## Test Conditions
DESIREE-FIRE Intermediate Scale Test Number 1 - Circuit Simulator Data Only
Test Date: | 2010-02-23
DCSim DAQ Start Time | 12:09
DCSim Time for Synchronization | 13:03
Heat Source Synchronization | 0:02 | hour:minutes:seconds
Heat Source DAQ Start Time | 13:01
Fire Time | 13:56
Offset | 1:47 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 6420 | seconds
Heat Source Offset | 0:55 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 3299 | seconds
Heat Source Stop Time | 15:09
Test Duration | 1:13 | hour:minutes:seconds
| 4380 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 2, 3, and 4 represents the conduit temperature 3', 5', and 7' down the conduit located in B Position. These are labeled as "B Position - Conduit - 3'", "B Position - Conduit - Middle", " B Position - Conduit - 7'", respectively.
MOV 2 | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 8, 9, and 10 represents the air temperature 3', 5', and 7' down the tray located in D Position. These are labeled as "D Position - 3'", "D Position - Middle", "D Position - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-1.2188 | 123.3078 | -61.6653 | 61.4685 | 0.01358 | -0.0074298 | 0.0079339 | 0.066174 | -0.018267 | -0.029463 | -0.024955 | -0.00054937 | -0.0080321 | 0.063335 | 0.041947 | -0.019435 | -0.0148 | -0.014819 | -0.12817 | 61.4044 | -61.7432 | 61.4365 | -61.5189 | -61.9354 | -61.9354 | -0.15564 | 61.4136 | -61.7111 | 61.4685 | -61.7111 | -61.7386 | -61.6974 | -0.07782 | -0.064087 | -0.032044 | 0.14648 | -0.27008 | -0.27008 | -0.19226 | -0.19226 | -0.045777 | -0.054932 | 0 | -0.045777 | -0.032044 | -0.073242 | 0.013733 | -0.027465 | 0.2243 | 123.1796 | 0 | 123.1796 | 123.1476 | 123.1247 | 123.0698 | 123.0789 | -123.2117 | -123.1796 | 123.1018 | 123.1338 | 61.5372 | 61.5097
0.53125 | 123.2941 | -61.6425 | 61.5738 | 0.01358 | -0.011489 | 0.0081477 | 0.064251 | -0.021471 | -0.032667 | -0.023033 | 0.0055542 | -0.0069641 | 0.063762 | 0.047501 | -0.023067 | -0.013945 | -0.011401 | -0.004578 | 61.4731 | -61.647 | 61.5692 | -61.3495 | -61.7569 | -61.7798 | 0 | 61.4594 | -61.6608 | 61.5509 | -61.5692 | -61.615 | -61.6333 | -0.004578 | -0.10071 | -0.004578 | 0.29297 | -0.13733 | -0.11444 | -0.13275 | -0.10986 | -0.018311 | -0.11444 | -0.022889 | 0.073242 | 0.009155 | 0.027466 | 0.027466 | 0.045777 | 0.29755 | 123.2162 | 0.091553 | 123.2117 | 123.1201 | 123.1201 | 123.1155 | 123.1018 | -123.2208 | -123.2346 | 123.2117 | 123.1934 | 61.6379 | 61.6425
2.2188 | 123.3902 | -61.647 | 61.4868 | 0.028839 | -0.0093524 | 0.0081477 | 0.064892 | -0.01784 | -0.028395 | -0.02346 | 0.014709 | -0.0086731 | 0.062481 | 0.048997 | -0.018154 | -0.01245 | -0.016742 | -0.064087 | 61.3861 | -61.7157 | 61.5738 | -61.3358 | -61.7844 | -61.8027 | 0.009155 | 61.3495 | -61.6882 | 61.5738 | -61.5692 | -61.5921 | -61.6333 | -0.068664 | -0.10071 | 0.086976 | 0.31128 | -0.15564 | -0.13733 | -0.086975 | -0.068665 | -0.041198 | -0.13733 | 0.086976 | 0.07782 | 0.013733 | 0.054932 | 0.054931 | 0.09613 | 0.37994 | 123.2895 | 0.11902 | 123.262 | 123.1018 | 123.0377 | 123.0331 | 122.9965 | -123.2025 | -123.175 | 123.2208 | 123.2208 | 61.5829 | 61.6562
3.9844 | 123.3444 | -61.6425 | 61.5143 | 0.02121 | -0.007857 | 0.0085749 | 0.067456 | -0.018053 | -0.030104 | -0.02346 | 0.0055542 | -0.0073913 | 0.062694 | 0.040665 | -0.022212 | -0.013732 | -0.016101 | -0.027466 | 61.4456 | -61.7065 | 61.5555 | -61.3815 | -61.7935 | -61.8301 | 0.004578 | 61.4319 | -61.6653 | 61.5601 | -61.5692 | -61.6013 | -61.6196 | -0.064087 | -0.068664 | 0.041199 | 0.26093 | -0.18768 | -0.15106 | -0.1236 | -0.086975 | -0.022888 | -0.082397 | 0.045777 | 0.073242 | 0.022888 | 0.041199 | 0.045776 | 0.064087 | 0.32501 | 123.262 | 0.09613 | 123.2254 | 123.1522 | 123.0972 | 123.0881 | 123.0743 | -123.2208 | -123.1796 | 123.1979 | 123.2025 | 61.615 | 61.647
5.6562 | 123.2941 | -61.615 | 61.5829 | 0.0059509 | -0.0089252 | 0.0077203 | 0.06297 | -0.021258 | -0.029463 | -0.021965 | -0.003601 | -0.010596 | 0.060558 | 0.051346 | -0.024349 | -0.012877 | -0.012469 | 0.018311 | 61.4594 | -61.6425 | 61.5875 | -61.322 | -61.7249 | -61.7661 | 0.022888 | 61.4456 | -61.6058 | 61.5692 | -61.5555 | -61.5784 | -61.6241 | -0.027466 | -0.1236 | 0.004577 | 0.29297 | -0.15106 | -0.10986 | -0.1236 | -0.082398 | 0.009155 | -0.13733 | -0.013733 | 0.059509 | -0.009156 | 0.036621 | -0.018311 | 0.027466 | 0.32044 | 123.23 | 0.050354 | 123.175 | 123.1018 | 123.0515 | 123.0743 | 123.0606 | -123.2254 | -123.1888 | 123.2025 | 123.1842 | 61.6333 | 61.6379
7.4062 | 123.4085 | -61.5967 | 61.5234 | 0.0059509 | -0.010848 | 0.0081477 | 0.063611 | -0.02318 | -0.029676 | -0.022819 | -0.00054937 | -0.011237 | 0.06184 | 0.044938 | -0.021144 | -0.014373 | -0.01076 | -0.068665 | 61.4182 | -61.6562 | 61.5875 | -61.3403 | -61.734 | -61.7615 | 0.027466 | 61.409 | -61.6013 | 61.6241 | -61.4822 | -61.5143 | -61.5509 | -0.059509 | -0.10529 | 0.064087 | 0.25635 | -0.16479 | -0.13733 | -0.10529 | -0.07782 | -0.004577 | -0.11444 | 0.10071 | 0.11444 | 0.045777 | 0.082398 | 0.050354 | 0.086975 | 0.31586 | 123.2437 | 0.11902 | 123.2254 | 123.0743 | 123.0103 | 123.0148 | 123.0057 | -123.1796 | -123.1247 | 123.1842 | 123.2208 | 61.528 | 61.6241
9.1562 | 123.3444 | -61.6516 | 61.496 | 0.02121 | -0.011061 | 0.0066523 | 0.066174 | -0.016344 | -0.030958 | -0.026023 | 0.0025024 | -0.0084595 | 0.060772 | 0.046647 | -0.019649 | -0.013945 | -0.01781 | -0.068665 | 61.3998 | -61.6928 | 61.5372 | -61.3724 | -61.7798 | -61.7889 | -0.036621 | 61.3815 | -61.6653 | 61.5601 | -61.5692 | -61.5875 | -61.615 | -0.041199 | -0.096131 | 0.041198 | 0.27924 | -0.13733 | -0.12817 | -0.09613 | -0.086975 | -0.013733 | -0.11444 | 0.064087 | 0.082397 | 0.036621 | 0.064087 | 0.050354 | 0.07782 | 0.32044 | 123.23 | 0.09613 | 123.2254 | 123.0927 | 123.0469 | 123.0515 | 123.0331 | -123.1888 | -123.1613 | 123.1888 | 123.2117 | 61.5829 | 61.615
10.9062 | 123.2574 | -61.6745 | 61.5234 | 0.0059509 | -0.010421 | 0.0068659 | 0.069378 | -0.017412 | -0.031385 | -0.02581 | 0.0025024 | -0.0071777 | 0.062481 | 0.04387 | -0.020503 | -0.011595 | -0.015033 | -0.1236 | 61.3861 | -61.7432 | 61.4502 | -61.4914 | -61.9125 | -61.9125 | -0.16479 | 61.409 | -61.702 | 61.4502 | -61.7111 | -61.734 | -61.7157 | -0.068664 | -0.13733 | -0.073242 | 0.18311 | -0.23804 | -0.23804 | -0.16937 | -0.16937 | -0.027465 | -0.11444 | -0.073242 | -0.036621 | -0.041198 | -0.059509 | -0.013733 | -0.032044 | 0.25177 | 123.1934 | -0.009156 | 123.1522 | 123.1293 | 123.111 | 123.0606 | 123.0835 | -123.2666 | -123.2254 | 123.1247 | 123.1247 | 61.5509 | 61.5097
12.6094 | 123.3536 | -61.6287 | 61.4914 | 0.02121 | -0.0097796 | 0.0083613 | 0.066174 | -0.015703 | -0.031813 | -0.024314 | -0.003601 | -0.0095275 | 0.060772 | 0.054551 | -0.018367 | -0.013518 | -0.016955 | -0.086975 | 61.4044 | -61.6653 | 61.5417 | -61.3907 | -61.7935 | -61.821 | -0.054932 | 61.3861 | -61.6379 | 61.5555 | -61.5692 | -61.5784 | -61.6058 | -0.036621 | -0.086975 | 0.050354 | 0.23804 | -0.19226 | -0.16479 | -0.15564 | -0.12817 | -0.009155 | -0.10529 | 0.064087 | 0.059509 | 0.022888 | 0.050354 | 0.032043 | 0.059509 | 0.27466 | 123.2071 | 0.068664 | 123.1934 | 123.0698 | 123.024 | 123.0331 | 123.0148 | -123.1567 | -123.1293 | 123.1705 | 123.1842 | 61.5417 | 61.5738
14.3438 | 123.3032 | -61.6379 | 61.5005 | 0.0059509 | -0.0070026 | 0.0083613 | 0.067242 | -0.017412 | -0.029676 | -0.02581 | 0.0025024 | -0.0065369 | 0.060985 | 0.040665 | -0.022212 | -0.012877 | -0.017383 | -0.032043 | 61.4456 | -61.6928 | 61.5417 | -61.3632 | -61.7889 | -61.8118 | 0.009155 | 61.4227 | -61.6562 | 61.5463 | -61.5738 | -61.615 | -61.6241 | -0.054932 | -0.054931 | 0.041199 | 0.27466 | -0.17395 | -0.15106 | -0.11902 | -0.09613 | -0.018311 | -0.07782 | 0.045777 | 0.064086 | 0.013732 | 0.022888 | 0.032043 | 0.041199 | 0.32959 | 123.2346 | 0.082397 | 123.2025 | 123.1384 | 123.0789 | 123.0835 | 123.0606 | -123.1934 | -123.1567 | 123.1796 | 123.1842 | 61.6058 | 61.647
16.0469 | 123.3582 | -61.6196 | 61.5097 | 0.0059509 | -0.0093524 | 0.0087885 | 0.064038 | -0.021898 | -0.028181 | -0.025383 | 0.0055542 | -0.0088867 | 0.064617 | 0.04152 | -0.019649 | -0.013518 | -0.016314 | -0.073242 | 61.409 | -61.6562 | 61.5234 | -61.377 | -61.7798 | -61.7981 | -0.041199 | 61.3815 | -61.6562 | 61.5601 | -61.5326 | -61.5646 | -61.5875 | -0.036621 | -0.10071 | 0.013732 | 0.24262 | -0.17853 | -0.16022 | -0.14191 | -0.1236 | -0.036621 | -0.12817 | 0.050354 | 0.086975 | 0.032044 | 0.054932 | 0.068665 | 0.091553 | 0.27924 | 123.1796 | 0.1236 | 123.2162 | 123.0652 | 123.0377 | 123.0286 | 123.0011 | -123.1659 | -123.1659 | 123.143 | 123.1796 | 61.5463 | 61.5784
17.8125 | 123.3124 | -61.6791 | 61.4594 | 0.0059509 | -0.0087116 | 0.010284 | 0.06596 | -0.019121 | -0.029463 | -0.024101 | 0.0025024 | -0.0063233 | 0.064617 | 0.045151 | -0.020076 | -0.012877 | -0.016742 | -0.13275 | 61.4044 | -61.7157 | 61.4456 | -61.4731 | -61.8942 | -61.8896 | -0.10986 | 61.3632 | -61.6791 | 61.5051 | -61.647 | -61.6791 | -61.6562 | -0.036621 | -0.054932 | -0.013733 | 0.20599 | -0.21057 | -0.21515 | -0.17395 | -0.17853 | 0 | -0.096131 | 0.045776 | 0.032043 | 0.022888 | 0 | 0.022888 | 0 | 0.24262 | 123.1613 | 0.032043 | 123.1842 | 123.1201 | 123.0423 | 123.0835 | 123.0423 | -123.175 | -123.1384 | 123.1247 | 123.1842 | 61.5463 | 61.5692
19.5781 | 123.3536 | -61.6516 | 61.441 | 0.01358 | -0.0097796 | 0.0087885 | 0.065533 | -0.018267 | -0.02989 | -0.022605 | 0.011658 | -0.0076049 | 0.063762 | 0.048356 | -0.021358 | -0.012236 | -0.01311 | -0.059509 | 61.3861 | -61.6882 | 61.5738 | -61.3266 | -61.7844 | -61.7844 | 0.022888 | 61.3312 | -61.6653 | 61.5692 | -61.5555 | -61.5784 | -61.6058 | -0.036621 | -0.054932 | 0.13275 | 0.32501 | -0.13275 | -0.13275 | -0.096131 | -0.096131 | -0.013733 | -0.10986 | 0.12817 | 0.09613 | 0.045776 | 0.073242 | 0.059509 | 0.086975 | 0.36163 | 123.262 | 0.10986 | 123.2346 | 123.0743 | 122.9965 | 123.0377 | 122.9828 | -123.1293 | -123.1064 | 123.2254 | 123.2208 | 61.5921 | 61.6745
21.3281 | 123.3353 | -61.5738 | 61.528 | 0.0059509 | -0.010207 | 0.0085749 | 0.062756 | -0.021044 | -0.028181 | -0.02346 | -0.003601 | -0.0095275 | 0.061412 | 0.046433 | -0.021144 | -0.013945 | -0.016955 | 0.013733 | 61.409 | -61.6379 | 61.6196 | -61.2625 | -61.6745 | -61.7157 | 0.064087 | 61.4227 | -61.5738 | 61.6104 | -61.4777 | -61.5143 | -61.5417 | -0.064086 | -0.11902 | 0.091553 | 0.31128 | -0.14191 | -0.10071 | -0.07782 | -0.036622 | 0 | -0.10529 | 0.082398 | 0.096131 | 0.032044 | 0.05951 | 0.032044 | 0.05951 | 0.37537 | 123.2574 | 0.096131 | 123.1842 | 123.0469 | 122.9965 | 122.9828 | 122.9965 | -123.1659 | -123.1018 | 123.1934 | 123.1842 | 61.5875 | 61.6379
23.0938 | 123.3765 | -61.6241 | 61.4456 | 0.01358 | -0.0093524 | 0.0083613 | 0.063183 | -0.019549 | -0.028608 | -0.024742 | 0.0025024 | -0.0088867 | 0.062908 | 0.04451 | -0.018794 | -0.013518 | -0.011187 | -0.073242 | 61.3586 | -61.7203 | 61.5509 | -61.3358 | -61.7935 | -61.8118 | 0.009155 | 61.3266 | -61.6653 | 61.5738 | -61.5555 | -61.5829 | -61.6058 | -0.09613 | -0.086975 | 0.10528 | 0.28839 | -0.18768 | -0.16937 | -0.091553 | -0.073242 | -0.041198 | -0.11902 | 0.12817 | 0.068665 | 0.018311 | 0.041199 | 0.059509 | 0.082397 | 0.38452 | 123.2712 | 0.10986 | 123.2391 | 123.0789 | 122.9919 | 122.9828 | 122.9507 | -123.1659 | -123.111 | 123.175 | 123.1979 | 61.5509 | 61.6333
24.8438 | 123.2849 | -61.5967 | 61.5417 | 0.044098 | -0.0091388 | 0.0079339 | 0.065747 | -0.016771 | -0.031172 | -0.022178 | 0.0055542 | -0.0071777 | 0.062694 | 0.045151 | -0.022426 | -0.014586 | -0.01546 | -0.032043 | 61.4868 | -61.6974 | 61.5143 | -61.3998 | -61.7935 | -61.7981 | -0.054932 | 61.4594 | -61.6287 | 61.5234 | -61.5784 | -61.6196 | -61.615 | -0.10071 | -0.054932 | -0.027466 | 0.19684 | -0.20142 | -0.19684 | -0.10071 | -0.09613 | -0.032043 | -0.082397 | -0.018311 | 0.018311 | -0.01831 | -0.022888 | 0.013733 | 0.009155 | 0.29755 | 123.2117 | 0.050354 | 123.1522 | 123.1842 | 123.0881 | 123.0835 | 123.056 | -123.2391 | -123.1705 | 123.111 | 123.1201 | 61.5646 | 61.5417
26.5312 | 123.317 | -61.6013 | 61.496 | 0.02121 | -0.0089252 | 0.0083613 | 0.064465 | -0.01784 | -0.030958 | -0.021751 | 0.008606 | -0.0099549 | 0.06184 | 0.041306 | -0.019222 | -0.014159 | -0.013324 | -0.082397 | 61.3861 | -61.6699 | 61.5326 | -61.3312 | -61.7844 | -61.7981 | -0.036621 | 61.3724 | -61.6516 | 61.5646 | -61.5555 | -61.5829 | -61.5875 | -0.068665 | -0.10986 | 0.036621 | 0.27008 | -0.19684 | -0.18311 | -0.12817 | -0.11444 | -0.050354 | -0.1236 | 0.068664 | 0.045776 | 0.013733 | 0.01831 | 0.064087 | 0.068664 | 0.33875 | 123.2025 | 0.09613 | 123.2162 | 123.056 | 123.024 | 122.9874 | 122.9736 | -123.1659 | -123.1476 | 123.1338 | 123.1659 | 61.5189 | 61.5646
28.2969 | 123.317 | -61.6287 | 61.4868 | 0.036468 | -0.0087116 | 0.0087885 | 0.066601 | -0.020403 | -0.029249 | -0.025169 | 0.008606 | -0.0080321 | 0.062481 | 0.047074 | -0.021572 | -0.015441 | -0.013537 | -0.073242 | 61.3724 | -61.6745 | 61.5463 | -61.3312 | -61.7935 | -61.7889 | -0.018311 | 61.3541 | -61.6425 | 61.5509 | -61.5646 | -61.5784 | -61.6013 | -0.045777 | -0.11444 | 0.05951 | 0.29755 | -0.16022 | -0.16479 | -0.11444 | -0.11902 | -0.013733 | -0.13275 | 0.064087 | 0.064087 | 0.027466 | 0.050354 | 0.041199 | 0.064087 | 0.34332 | 123.2208 | 0.07782 | 123.1934 | 123.0469 | 122.9965 | 123.0011 | 122.9828 | -123.1613 | -123.1293 | 123.175 | 123.1796 | 61.5555 | 61.6104
30.0625 | 123.2574 | -61.6653 | 61.5005 | 0.01358 | -0.008498 | 0.0087885 | 0.065533 | -0.01848 | -0.026899 | -0.024528 | 0.0025024 | -0.0061095 | 0.06419 | 0.043656 | -0.02029 | -0.012236 | -0.016955 | -0.11444 | 61.4227 | -61.734 | 61.4136 | -61.5097 | -61.908 | -61.9263 | -0.13733 | 61.3953 | -61.6928 | 61.4502 | -61.6837 | -61.7249 | -61.6791 | -0.068665 | -0.07782 | -0.086975 | 0.15564 | -0.26093 | -0.24262 | -0.19226 | -0.17395 | -0.027466 | -0.10529 | -0.050354 | -0.018311 | -0.013733 | -0.05951 | 0.013733 | -0.032044 | 0.2243 | 123.1476 | 0.009155 | 123.143 | 123.1567 | 123.0881 | 123.0881 | 123.0606 | -123.2346 | -123.1934 | 123.0789 | 123.1155 | 61.5509 | 61.528
31.75 | 123.3856 | -61.6241 | 61.4273 | -0.0016786 | -0.007857 | 0.0094293 | 0.065106 | -0.014208 | -0.029249 | -0.022178 | -0.00054937 | -0.0076049 | 0.062267 | 0.048997 | -0.019222 | -0.01245 | -0.012469 | -0.10529 | 61.3861 | -61.6882 | 61.5051 | -61.3724 | -61.8073 | -61.8347 | -0.018311 | 61.3312 | -61.6653 | 61.5692 | -61.5463 | -61.6013 | -61.5875 | -0.064086 | -0.041199 | 0.07782 | 0.25177 | -0.21057 | -0.1831 | -0.14648 | -0.11902 | -0.041198 | -0.09613 | 0.14191 | 0.07782 | 0.036622 | 0.022889 | 0.07782 | 0.064087 | 0.31586 | 123.1934 | 0.11902 | 123.2346 | 123.0743 | 122.9965 | 123.0103 | 122.9553 | -123.1155 | -123.0927 | 123.1293 | 123.1934 | 61.5189 | 61.6058
33.5156 | 123.2986 | -61.6196 | 61.4731 | 0.01358 | -0.010421 | 0.0094293 | 0.062329 | -0.022539 | -0.030958 | -0.026023 | 0.0025024 | -0.0093139 | 0.062053 | 0.054764 | -0.021785 | -0.013945 | -0.01781 | -0.091553 | 61.3953 | -61.6699 | 61.5234 | -61.3495 | -61.7798 | -61.7889 | -0.041199 | 61.3724 | -61.6196 | 61.5372 | -61.5509 | -61.5921 | -61.5875 | -0.050354 | -0.077819 | 0.050354 | 0.27008 | -0.16937 | -0.16022 | -0.11902 | -0.10986 | 0 | -0.10071 | 0.064087 | 0.068665 | 0.032044 | 0.027466 | 0.032044 | 0.027466 | 0.32043 | 123.1934 | 0.068665 | 123.1567 | 123.0652 | 122.9919 | 123.0148 | 122.9919 | -123.143 | -123.0927 | 123.143 | 123.1567 | 61.528 | 61.5784
35.2188 | 123.23 | -61.6974 | 61.4868 | -0.0016786 | -0.010421 | 0.010284 | 0.068097 | -0.01549 | -0.030317 | -0.02581 | 0.0025024 | -0.0076049 | 0.063762 | 0.042588 | -0.02029 | -0.0148 | -0.017383 | -0.14648 | 61.4319 | -61.7294 | 61.4136 | -61.496 | -61.8988 | -61.8988 | -0.16022 | 61.3815 | -61.6928 | 61.4456 | -61.6745 | -61.7157 | -61.6791 | -0.032043 | -0.054931 | -0.073242 | 0.20142 | -0.20142 | -0.20142 | -0.16937 | -0.16937 | 0.004578 | -0.10528 | -0.041198 | 0.022888 | 0.018311 | -0.01831 | 0.013733 | -0.022888 | 0.23346 | 123.143 | 0.01831 | 123.1384 | 123.1613 | 123.0743 | 123.1293 | 123.0789 | -123.2162 | -123.1796 | 123.111 | 123.143 | 61.5509 | 61.5372
36.9844 | 123.3215 | -61.6241 | 61.4502 | 0.02121 | -0.0093524 | 0.0090021 | 0.063824 | -0.018908 | -0.027967 | -0.025596 | 0.008606 | -0.0097411 | 0.062694 | 0.04387 | -0.019863 | -0.013091 | -0.015246 | -0.059509 | 61.3815 | -61.6928 | 61.5463 | -61.3129 | -61.7477 | -61.7706 | 0.022888 | 61.3449 | -61.6608 | 61.5509 | -61.5463 | -61.5738 | -61.5875 | -0.068664 | -0.068664 | 0.096131 | 0.31128 | -0.14648 | -0.1236 | -0.07782 | -0.054932 | -0.036621 | -0.10529 | 0.10071 | 0.07782 | 0.036622 | 0.050354 | 0.073243 | 0.086975 | 0.37994 | 123.2391 | 0.11444 | 123.2117 | 123.0743 | 123.0057 | 123.0057 | 122.9691 | -123.143 | -123.111 | 123.1705 | 123.175 | 61.5646 | 61.647
38.7344 | 123.3398 | -61.6379 | 61.4182 | 0.01358 | -0.006148 | 0.0090021 | 0.066815 | -0.017199 | -0.026045 | -0.024955 | 0.008606 | -0.0088867 | 0.063762 | 0.040452 | -0.019649 | -0.011382 | -0.014605 | -0.059509 | 61.377 | -61.7065 | 61.5646 | -61.3174 | -61.7432 | -61.7798 | 0.027466 | 61.3449 | -61.6653 | 61.5601 | -61.528 | -61.5738 | -61.5784 | -0.068665 | -0.041199 | 0.14648 | 0.32043 | -0.14191 | -0.10529 | -0.073242 | -0.036621 | -0.027466 | -0.073242 | 0.14191 | 0.10986 | 0.059509 | 0.064086 | 0.086975 | 0.091552 | 0.3891 | 123.2712 | 0.13733 | 123.2254 | 123.0835 | 123.0103 | 123.0148 | 122.9828 | -123.1247 | -123.0835 | 123.2025 | 123.1979 | 61.5784 | 61.6653
40.4219 | 123.3307 | -61.6196 | 61.4227 | 0.0059509 | -0.0089252 | 0.0083613 | 0.065533 | -0.020403 | -0.029036 | -0.022819 | 0.0025024 | -0.0076049 | 0.062053 | 0.050919 | -0.02029 | -0.014159 | -0.014819 | -0.10071 | 61.3815 | -61.7203 | 61.5234 | -61.3632 | -61.8073 | -61.8347 | -0.018311 | 61.322 | -61.6516 | 61.5646 | -61.5555 | -61.5875 | -61.5875 | -0.10071 | -0.041198 | 0.10071 | 0.25635 | -0.21515 | -0.18768 | -0.11444 | -0.086975 | -0.032043 | -0.10071 | 0.14191 | 0.064087 | 0.032044 | 0.032044 | 0.064087 | 0.064087 | 0.35706 | 123.2437 | 0.09613 | 123.2162 | 123.1018 | 122.9736 | 123.0011 | 122.9416 | -123.143 | -123.0743 | 123.143 | 123.1842 | 61.5189 | 61.6013
42.1875 | 123.3398 | -61.6287 | 61.4731 | 0.036468 | -0.0063616 | 0.010284 | 0.06532 | -0.019335 | -0.027327 | -0.021751 | 0.008606 | -0.0084595 | 0.065471 | 0.052415 | -0.019649 | -0.012236 | -0.015887 | -0.050354 | 61.3358 | -61.6882 | 61.5509 | -61.2991 | -61.7706 | -61.7798 | 0.018311 | 61.3129 | -61.6837 | 61.5463 | -61.5417 | -61.5646 | -61.5875 | -0.059509 | -0.13733 | 0.07782 | 0.32959 | -0.15106 | -0.14191 | -0.091553 | -0.082398 | -0.054932 | -0.16022 | 0.073243 | 0.086975 | 0.041199 | 0.064087 | 0.096131 | 0.11902 | 0.3891 | 123.2391 | 0.14191 | 123.23 | 123.024 | 122.9965 | 122.9645 | 122.9416 | -123.1613 | -123.1567 | 123.1796 | 123.175 | 61.5784 | 61.647
43.9531 | 123.3032 | -61.6196 | 61.4685 | 0.036468 | -0.0089252 | 0.0096429 | 0.064892 | -0.018694 | -0.028608 | -0.021324 | 0.0055542 | -0.0097411 | 0.060131 | 0.04387 | -0.022853 | -0.012664 | -0.010974 | -0.09613 | 61.3724 | -61.6837 | 61.5189 | -61.3266 | -61.7615 | -61.7752 | -0.032043 | 61.3724 | -61.6425 | 61.5417 | -61.5555 | -61.5555 | -61.5829 | -0.064087 | -0.096131 | 0.050354 | 0.29297 | -0.15564 | -0.14191 | -0.091553 | -0.07782 | -0.022888 | -0.096131 | 0.073242 | 0.064087 | 0.036621 | 0.064087 | 0.059509 | 0.086975 | 0.35706 | 123.2025 | 0.086975 | 123.1842 | 123.056 | 123.0148 | 122.9919 | 122.9919 | -123.1522 | -123.111 | 123.1384 | 123.1613 | 61.5234 | 61.5875
45.7031 | 123.23 | -61.615 | 61.5326 | 0.0059509 | -0.0091388 | 0.0083613 | 0.065747 | -0.018908 | -0.027967 | -0.022605 | -0.003601 | -0.0071777 | 0.063762 | 0.046647 | -0.024135 | -0.014373 | -0.012683 | -0.022888 | 61.4456 | -61.615 | 61.5372 | -61.3541 | -61.7477 | -61.7798 | -0.032043 | 61.4548 | -61.6058 | 61.5189 | -61.5372 | -61.5829 | -61.6058 | 0 | -0.086975 | 0.004577 | 0.26093 | -0.16479 | -0.13275 | -0.16479 | -0.13275 | 0.009155 | -0.07782 | -0.013733 | 0.07782 | 0.009155 | 0.032043 | 0 | 0.022888 | 0.26093 | 123.1522 | 0.068665 | 123.1247 | 123.0606 | 123.0606 | 123.0606 | 123.0698 | -123.1476 | -123.1384 | 123.1522 | 123.1338 | 61.5921 | 61.5829
47.4062 | 123.2666 | -61.6196 | 61.5143 | 0.036468 | -0.006789 | 0.011352 | 0.065533 | -0.021258 | -0.027967 | -0.022392 | 0.0055542 | -0.0071777 | 0.060344 | 0.040238 | -0.021572 | -0.013304 | -0.014819 | -0.018311 | 61.4914 | -61.6699 | 61.5143 | -61.3678 | -61.7661 | -61.7844 | -0.027466 | 61.4273 | -61.6562 | 61.5326 | -61.5463 | -61.6013 | -61.5875 | -0.050354 | -0.022888 | 0 | 0.25177 | -0.16479 | -0.14648 | -0.11444 | -0.09613 | -0.036621 | -0.086975 | 0.018311 | 0.073242 | 0.032044 | 0.018311 | 0.068665 | 0.054932 | 0.30212 | 123.1842 | 0.10986 | 123.1888 | 123.1613 | 123.0835 | 123.111 | 123.0469 | -123.1842 | -123.1705 | 123.1338 | 123.1522 | 61.6013 | 61.5921
49.1719 | 123.3398 | -61.5967 | 61.4822 | 0.0059509 | -0.010207 | 0.0070795 | 0.065106 | -0.022112 | -0.030958 | -0.02346 | 0.0025024 | -0.0099549 | 0.060985 | 0.043015 | -0.023281 | -0.01245 | -0.014392 | -0.068665 | 61.3815 | -61.6699 | 61.5509 | -61.2946 | -61.6974 | -61.7386 | 0.032043 | 61.3953 | -61.5967 | 61.6013 | -61.4548 | -61.4731 | -61.5143 | -0.073242 | -0.10071 | 0.068664 | 0.30212 | -0.14191 | -0.10071 | -0.068664 | -0.027466 | 0 | -0.086975 | 0.11902 | 0.14191 | 0.082398 | 0.1236 | 0.082398 | 0.1236 | 0.37537 | 123.2208 | 0.14191 | 123.1979 | 123.0515 | 122.9919 | 122.9782 | 122.9919 | -123.1522 | -123.0789 | 123.1476 | 123.1979 | 61.528 | 61.6287
50.9219 | 123.23 | -61.5921 | 61.5784 | -0.0093076 | -0.0091388 | 0.0077203 | 0.064465 | -0.020189 | -0.029676 | -0.021537 | -0.00054937 | -0.010169 | 0.061626 | 0.040452 | -0.02499 | -0.014373 | -0.015246 | -0.059509 | 61.4868 | -61.6379 | 61.5005 | -61.3678 | -61.7477 | -61.7706 | -0.054932 | 61.441 | -61.5967 | 61.4914 | -61.5646 | -61.6104 | -61.5967 | -0.045776 | -0.091553 | -0.07782 | 0.2243 | -0.17853 | -0.15564 | -0.13275 | -0.10986 | -0.004578 | -0.13733 | -0.086975 | 0.027466 | -0.004578 | -0.018311 | 0 | -0.013733 | 0.27008 | 123.1384 | 0.032044 | 123.0881 | 123.1247 | 123.0377 | 123.0789 | 123.0331 | -123.2162 | -123.175 | 123.0927 | 123.0835 | 61.5326 | 61.5372
52.625 | 123.2849 | -61.5921 | 61.5051 | 0.028839 | -0.0087116 | 0.0081477 | 0.067029 | -0.017412 | -0.029249 | -0.021965 | 0.0055542 | -0.0078185 | 0.062267 | 0.044297 | -0.02264 | -0.015227 | -0.015887 | -0.009155 | 61.4731 | -61.6608 | 61.5143 | -61.3495 | -61.7615 | -61.7935 | -0.045776 | 61.4319 | -61.6058 | 61.5143 | -61.5509 | -61.5784 | -61.5875 | -0.068665 | -0.032044 | 0.009155 | 0.24261 | -0.20142 | -0.16937 | -0.13275 | -0.10071 | -0.013733 | -0.073242 | 0.009155 | 0.041199 | 0.004578 | 0.013733 | 0.018311 | 0.027466 | 0.31128 | 123.175 | 0.054932 | 123.1201 | 123.1338 | 123.0377 | 123.0652 | 123.024 | -123.1659 | -123.111 | 123.1064 | 123.1064 | 61.5829 | 61.5463
54.375 | 123.3032 | -61.5967 | 61.4639 | 0.02121 | -0.0082842 | 0.0098565 | 0.064038 | -0.01784 | -0.029676 | -0.021965 | 0.008606 | -0.0076049 | 0.062694 | 0.043015 | -0.017513 | -0.013091 | -0.018237 | -0.07782 | 61.3632 | -61.6699 | 61.5417 | -61.2991 | -61.7523 | -61.7615 | 0.013733 | 61.322 | -61.6287 | 61.5463 | -61.5326 | -61.5555 | -61.5784 | -0.073242 | -0.10071 | 0.07782 | 0.29755 | -0.16479 | -0.15564 | -0.091553 | -0.082397 | -0.032043 | -0.14191 | 0.082398 | 0.064087 | 0.018311 | 0.041199 | 0.050354 | 0.073242 | 0.37079 | 123.2117 | 0.09613 | 123.175 | 123.0331 | 122.9507 | 122.9599 | 122.9187 | -123.1338 | -123.0927 | 123.1384 | 123.143 | 61.5189 | 61.6104
56.125 | 123.349 | -61.5555 | 61.5097 | -0.0016786 | -0.011275 | 0.0079339 | 0.062329 | -0.022539 | -0.031813 | -0.023033 | 0.0025024 | -0.0097411 | 0.062053 | 0.046647 | -0.019863 | -0.0148 | -0.016742 | 0.013733 | 61.3724 | -61.6333 | 61.6241 | -61.2213 | -61.6425 | -61.6791 | 0.09613 | 61.3998 | -61.5555 | 61.6241 | -61.4136 | -61.4548 | -61.4822 | -0.07782 | -0.13733 | 0.11444 | 0.33417 | -0.1236 | -0.086975 | -0.045776 | -0.009155 | 0 | -0.10986 | 0.11444 | 0.14191 | 0.073242 | 0.10071 | 0.073242 | 0.10071 | 0.41199 | 123.2574 | 0.14191 | 123.1796 | 123.0057 | 122.9553 | 122.9279 | 122.9553 | -123.143 | -123.0652 | 123.1796 | 123.1796 | 61.5692 | 61.6516
57.8906 | 123.1888 | -61.6562 | 61.4868 | 0.01358 | -0.0063616 | 0.0092157 | 0.06596 | -0.015703 | -0.030104 | -0.024101 | -0.00054937 | -0.0073913 | 0.061412 | 0.045792 | -0.020717 | -0.013518 | -0.014819 | -0.10986 | 61.3998 | -61.7111 | 61.441 | -61.4594 | -61.8896 | -61.8942 | -0.15564 | 61.3815 | -61.6516 | 61.4365 | -61.6562 | -61.6837 | -61.6745 | -0.054932 | -0.086975 | -0.045776 | 0.19684 | -0.23804 | -0.23346 | -0.18311 | -0.17853 | 0.004578 | -0.10528 | -0.050354 | 0 | -0.018311 | -0.027466 | -0.022889 | -0.032044 | 0.25177 | 123.1522 | -0.004578 | 123.0881 | 123.111 | 123.0331 | 123.056 | 123.0377 | -123.1979 | -123.1384 | 123.0972 | 123.0927 | 61.5463 | 61.5005
59.5781 | 123.3398 | -61.5784 | 61.4639 | -0.0093076 | -0.010207 | 0.0075067 | 0.064251 | -0.019121 | -0.029463 | -0.026878 | -0.003601 | -0.0097411 | 0.060558 | 0.052201 | -0.019863 | -0.013732 | -0.016528 | -0.018311 | 61.4227 | -61.6104 | 61.5875 | -61.235 | -61.6653 | -61.6837 | 0.068665 | 61.3495 | -61.5738 | 61.6241 | -61.4273 | -61.4548 | -61.4914 | -0.032044 | -0.041199 | 0.1236 | 0.34332 | -0.10529 | -0.086975 | -0.073242 | -0.054931 | 0.004577 | -0.11444 | 0.16022 | 0.15106 | 0.086975 | 0.1236 | 0.082398 | 0.11902 | 0.37537 | 123.1979 | 0.14648 | 123.1979 | 123.0331 | 122.9233 | 123.0011 | 122.9279 | -123.0743 | -123.0377 | 123.1659 | 123.2025 | 61.5601 | 61.647
61.3281 | 123.2025 | -61.6562 | 61.4594 | -0.0016786 | -0.0093524 | 0.0094293 | 0.066601 | -0.020189 | -0.02989 | -0.024528 | -0.00054937 | -0.0056823 | 0.062908 | 0.050278 | -0.019008 | -0.013304 | -0.018664 | -0.14648 | 61.4227 | -61.6974 | 61.3861 | -61.4685 | -61.8896 | -61.8942 | -0.14648 | 61.3724 | -61.6745 | 61.4273 | -61.6562 | -61.6928 | -61.6608 | -0.041199 | -0.036622 | -0.073243 | 0.18768 | -0.23804 | -0.23346 | -0.19684 | -0.19226 | -0.018311 | -0.086976 | -0.032044 | 0 | -0.004578 | -0.036621 | 0.013733 | -0.01831 | 0.22888 | 123.0835 | 0.018311 | 123.1018 | 123.1201 | 123.0469 | 123.0789 | 123.0286 | -123.1567 | -123.1339 | 123.0423 | 123.0835 | 61.5097 | 61.5097
63.1094 | 123.3444 | -61.5417 | 61.5051 | -0.0016786 | -0.011061 | 0.0085749 | 0.064465 | -0.019121 | -0.030104 | -0.025169 | -0.00054937 | -0.0095275 | 0.060131 | 0.048356 | -0.022426 | -0.014159 | -0.014819 | -0.004578 | 61.3861 | -61.615 | 61.6196 | -61.2122 | -61.6333 | -61.6882 | 0.09613 | 61.3998 | -61.5692 | 61.5967 | -61.409 | -61.4456 | -61.4868 | -0.073242 | -0.11902 | 0.11444 | 0.32959 | -0.14648 | -0.091553 | -0.073242 | -0.018311 | -0.027466 | -0.10529 | 0.091553 | 0.13275 | 0.054932 | 0.09613 | 0.082398 | 0.1236 | 0.40283 | 123.2346 | 0.16022 | 123.1659 | 123.0011 | 122.9691 | 122.9279 | 122.9416 | -123.1201 | -123.0743 | 123.1613 | 123.1384 | 61.5372 | 61.6379
64.7969 | 123.2254 | -61.5646 | 61.5143 | 0.0059509 | -0.011061 | 0.0072931 | 0.062115 | -0.019121 | -0.028822 | -0.024314 | -0.003601 | -0.0088867 | 0.063762 | 0.038956 | -0.020503 | -0.014373 | -0.013965 | 0.009155 | 61.409 | -61.6104 | 61.5646 | -61.2671 | -61.6791 | -61.7249 | 0.018311 | 61.3815 | -61.5692 | 61.5234 | -61.5051 | -61.5509 | -61.5692 | -0.045777 | -0.10529 | 0.050354 | 0.29755 | -0.16022 | -0.11444 | -0.11444 | -0.068664 | -0.004578 | -0.13275 | 0.009155 | 0.059509 | -0.004578 | 0.013733 | 0 | 0.018311 | 0.34332 | 123.175 | 0.064087 | 123.0927 | 123.0194 | 122.9507 | 122.9736 | 122.9462 | -123.1247 | -123.0835 | 123.1293 | 123.0881 | 61.5738 | 61.5829
66.5469 | 123.3398 | -61.5417 | 61.4868 | -0.0016786 | -0.009566 | 0.0096429 | 0.063611 | -0.019762 | -0.032667 | -0.022178 | -0.00054937 | -0.0086731 | 0.062267 | 0.049637 | -0.019222 | -0.013732 | -0.01311 | -0.009155 | 61.3953 | -61.5921 | 61.6058 | -61.2122 | -61.6379 | -61.6699 | 0.10986 | 61.3907 | -61.5692 | 61.6287 | -61.3998 | -61.4456 | -61.5005 | -0.050354 | -0.091552 | 0.11902 | 0.32959 | -0.12817 | -0.09613 | -0.07782 | -0.045776 | -0.027466 | -0.09613 | 0.14191 | 0.14191 | 0.041199 | 0.09613 | 0.068665 | 0.1236 | 0.37994 | 123.1979 | 0.16937 | 123.1979 | 122.9874 | 122.9599 | 122.937 | 122.9324 | -123.0789 | -123.056 | 123.1476 | 123.1705 | 61.5326 | 61.6516
68.25 | 123.3353 | -61.5463 | 61.4868 | 0.0059509 | -0.011489 | 0.0077203 | 0.061688 | -0.018267 | -0.029036 | -0.022392 | 0.0025024 | -0.0097411 | 0.060558 | 0.041092 | -0.020076 | -0.01245 | -0.015887 | -0.013733 | 61.3724 | -61.6104 | 61.6058 | -61.1984 | -61.6333 | -61.6562 | 0.10986 | 61.3861 | -61.5784 | 61.6104 | -61.409 | -61.4319 | -61.496 | -0.064087 | -0.11444 | 0.11902 | 0.3479 | -0.10986 | -0.086975 | -0.045776 | -0.022888 | -0.032043 | -0.10071 | 0.1236 | 0.13733 | 0.050354 | 0.11444 | 0.082397 | 0.14648 | 0.41199 | 123.2162 | 0.16937 | 123.1888 | 122.9828 | 122.9645 | 122.9187 | 122.9324 | -123.0972 | -123.0652 | 123.1522 | 123.1567 | 61.5326 | 61.6562
70 | 123.3307 | -61.5463 | 61.4822 | -0.0016786 | -0.012343 | 0.0049433 | 0.063397 | -0.021258 | -0.031172 | -0.023246 | 0.0025024 | -0.0093139 | 0.063549 | 0.050278 | -0.020717 | -0.013518 | -0.013751 | -0.004578 | 61.3953 | -61.6013 | 61.5967 | -61.2213 | -61.6516 | -61.6653 | 0.10529 | 61.3815 | -61.5875 | 61.6196 | -61.3998 | -61.4273 | -61.4639 | -0.054931 | -0.086975 | 0.11444 | 0.32501 | -0.11902 | -0.10529 | -0.064087 | -0.050354 | -0.041198 | -0.10071 | 0.13733 | 0.14648 | 0.082398 | 0.11902 | 0.1236 | 0.16022 | 0.37994 | 123.1979 | 0.18768 | 123.2071 | 122.9965 | 122.9691 | 122.9416 | 122.9279 | -123.0835 | -123.0698 | 123.143 | 123.1659 | 61.5417 | 61.6516
71.6719 | 123.3307 | -61.6287 | 61.3861 | -0.0016786 | -0.0087116 | 0.0077203 | 0.066388 | -0.019549 | -0.028181 | -0.023674 | 0.0025024 | -0.0082459 | 0.062267 | 0.053696 | -0.018154 | -0.011595 | -0.016101 | -0.054932 | 61.322 | -61.647 | 61.5234 | -61.3174 | -61.7706 | -61.7752 | 0.009155 | 61.3037 | -61.6379 | 61.5601 | -61.5189 | -61.5463 | -61.5601 | -0.018311 | -0.064087 | 0.13733 | 0.31128 | -0.14648 | -0.14191 | -0.12817 | -0.1236 | -0.009155 | -0.082397 | 0.17395 | 0.10986 | 0.068664 | 0.082397 | 0.077819 | 0.091552 | 0.32959 | 123.1705 | 0.11902 | 123.1979 | 122.9691 | 122.9416 | 122.9507 | 122.9324 | -123.0331 | -123.024 | 123.1522 | 123.1888 | 61.5738 | 61.6379
73.4375 | 123.2117 | -61.6333 | 61.4502 | -0.0093076 | -0.0087116 | 0.0083613 | 0.067029 | -0.019549 | -0.029036 | -0.025596 | 0.0025024 | -0.0056823 | 0.063549 | 0.049424 | -0.020931 | -0.012877 | -0.01311 | -0.12817 | 61.3907 | -61.7111 | 61.3907 | -61.4594 | -61.8759 | -61.8713 | -0.13733 | 61.3586 | -61.6425 | 61.4502 | -61.6287 | -61.6653 | -61.6287 | -0.07782 | -0.059509 | -0.059509 | 0.17395 | -0.23804 | -0.24261 | -0.16022 | -0.16479 | -0.009155 | -0.091552 | 0 | 0.004578 | 0.004578 | -0.032043 | 0.013733 | -0.022888 | 0.25177 | 123.1018 | 0.013733 | 123.0927 | 123.1018 | 123.0011 | 123.024 | 122.9919 | -123.1613 | -123.0927 | 123.024 | 123.0835 | 61.5051 | 61.496
75.1875 | 123.2025 | -61.647 | 61.4502 | 0.0059509 | -0.0099932 | 0.0087885 | 0.066174 | -0.014849 | -0.031599 | -0.022605 | 0.0025024 | -0.0080321 | 0.062908 | 0.040665 | -0.02264 | -0.013732 | -0.015674 | -0.041199 | 61.4365 | -61.6562 | 61.496 | -61.3541 | -61.7844 | -61.8118 | -0.041199 | 61.3907 | -61.5967 | 61.4731 | -61.5738 | -61.6333 | -61.6104 | -0.009155 | -0.013733 | 0.045777 | 0.29297 | -0.1648 | -0.13733 | -0.15564 | -0.12817 | 0.050354 | -0.059509 | 0.022888 | 0.073242 | 0.036621 | 0.013733 | -0.013733 | -0.036621 | 0.30212 | 123.1522 | 0.022888 | 123.0698 | 123.0927 | 122.9874 | 123.0835 | 123.0377 | -123.1064 | -123.0469 | 123.143 | 123.1201 | 61.6058 | 61.6058
76.875 | 123.1705 | -61.6699 | 61.4777 | 0.0059509 | -0.0093524 | 0.0072931 | 0.065533 | -0.016344 | -0.028181 | -0.020897 | 0.0025024 | -0.0097411 | 0.062053 | 0.044083 | -0.02029 | -0.012877 | -0.015887 | -0.12817 | 61.3815 | -61.702 | 61.3907 | -61.4502 | -61.8668 | -61.8851 | -0.14648 | 61.3861 | -61.6379 | 61.4182 | -61.6516 | -61.702 | -61.6516 | -0.032043 | -0.09613 | -0.086975 | 0.21973 | -0.21515 | -0.19684 | -0.18311 | -0.16479 | 0.032044 | -0.091553 | -0.059509 | 0.018311 | 0.018311 | -0.032043 | -0.013733 | -0.064087 | 0.25177 | 123.0927 | -0.013733 | 123.056 | 123.0835 | 123.024 | 123.0515 | 123.056 | -123.1796 | -123.1155 | 123.0606 | 123.0881 | 61.5417 | 61.5234
78.6406 | 123.2712 | -61.6013 | 61.4548 | 0.02121 | -0.010848 | 0.0083613 | 0.062756 | -0.023821 | -0.029036 | -0.024101 | 0.0025024 | -0.0093139 | 0.062481 | 0.05156 | -0.021358 | -0.01245 | -0.012683 | -0.09613 | 61.3632 | -61.6425 | 61.4914 | -61.3174 | -61.7523 | -61.7615 | -0.041199 | 61.3312 | -61.6287 | 61.5234 | -61.5234 | -61.5417 | -61.5692 | -0.041199 | -0.091553 | 0.036621 | 0.28381 | -0.16022 | -0.15106 | -0.11902 | -0.10986 | -0.027466 | -0.1236 | 0.068664 | 0.07782 | 0.032043 | 0.059509 | 0.059509 | 0.086975 | 0.32501 | 123.1338 | 0.10529 | 123.1522 | 123.0057 | 122.9599 | 122.9645 | 122.9324 | -123.0972 | -123.0835 | 123.0927 | 123.1247 | 61.5051 | 61.5601
80.3906 | 123.2666 | -61.5417 | 61.5097 | 0.0059509 | -0.0097796 | 0.0072931 | 0.065106 | -0.015276 | -0.029463 | -0.025383 | 0.0025024 | -0.0091003 | 0.05949 | 0.048142 | -0.02264 | -0.013945 | -0.016314 | 0.013733 | 61.3724 | -61.6104 | 61.5829 | -61.2213 | -61.6562 | -61.6882 | 0.068665 | 61.3907 | -61.5646 | 61.5646 | -61.4365 | -61.4685 | -61.4868 | -0.068665 | -0.13733 | 0.073242 | 0.32043 | -0.14648 | -0.11444 | -0.077819 | -0.045776 | -0.022888 | -0.11902 | 0.054931 | 0.10529 | 0.054932 | 0.073242 | 0.07782 | 0.09613 | 0.3891 | 123.1934 | 0.12817 | 123.1293 | 122.9828 | 122.9553 | 122.9141 | 122.9324 | -123.1201 | -123.0743 | 123.1247 | 123.1064 | 61.5555 | 61.6104
82.1562 | 123.3215 | -61.5692 | 61.4685 | 0.0059509 | -0.013411 | 0.0068659 | 0.06297 | -0.022326 | -0.028395 | -0.024955 | 0.0025024 | -0.0084595 | 0.06483 | 0.048356 | -0.019649 | -0.0098864 | -0.010119 | -0.041199 | 61.3724 | -61.6333 | 61.5601 | -61.2488 | -61.6699 | -61.6699 | 0.045776 | 61.3861 | -61.5555 | 61.6013 | -61.409 | -61.4456 | -61.4777 | -0.064087 | -0.096131 | 0.091553 | 0.32044 | -0.10071 | -0.10071 | -0.036621 | -0.036621 | 0.013733 | -0.082398 | 0.13275 | 0.16022 | 0.091553 | 0.1236 | 0.07782 | 0.10986 | 0.38452 | 123.1934 | 0.14648 | 123.1567 | 123.0057 | 122.9416 | 122.9416 | 122.9553 | -123.1018 | -123.024 | 123.1293 | 123.1705 | 61.528 | 61.615
83.9219 | 123.1888 | -61.6287 | 61.4456 | 0.0059509 | -0.0091388 | 0.010711 | 0.06831 | -0.018267 | -0.031599 | -0.02111 | -0.00054937 | -0.0071777 | 0.062053 | 0.04451 | -0.019863 | -0.013304 | -0.01546 | -0.091553 | 61.3907 | -61.6745 | 61.4365 | -61.409 | -61.8393 | -61.8576 | -0.11444 | 61.3541 | -61.6379 | 61.4182 | -61.6241 | -61.6699 | -61.6425 | -0.045777 | -0.054932 | -0.009156 | 0.21973 | -0.22888 | -0.21057 | -0.1831 | -0.16479 | -0.009155 | -0.091553 | -0.027466 | 0.004577 | -0.013733 | -0.041199 | -0.004578 | -0.032044 | 0.2655 | 123.111 | 0.013732 | 123.056 | 123.0652 | 122.9919 | 123.0194 | 122.9828 | -123.1201 | -123.0835 | 123.0652 | 123.0469 | 61.5372 | 61.5143
85.6875 | 123.2483 | -61.6104 | 61.3953 | -0.0016786 | -0.0097796 | 0.0081477 | 0.063611 | -0.022967 | -0.030958 | -0.023033 | -0.00054937 | -0.0078185 | 0.062481 | 0.049424 | -0.02029 | -0.013304 | -0.014392 | -0.13733 | 61.3907 | -61.6745 | 61.4044 | -61.4136 | -61.8484 | -61.8439 | -0.07782 | 61.2991 | -61.6379 | 61.4731 | -61.5601 | -61.6013 | -61.5829 | -0.064087 | -0.004578 | 0.009155 | 0.19684 | -0.23346 | -0.23804 | -0.16937 | -0.17395 | -0.027465 | -0.096131 | 0.077819 | 0.050354 | 0.027466 | 0.009156 | 0.054931 | 0.036621 | 0.26093 | 123.0789 | 0.077819 | 123.111 | 123.0652 | 122.937 | 123.0011 | 122.9095 | -123.0698 | -123.0331 | 123.0148 | 123.0835 | 61.4731 | 61.5326
87.3906 | 123.2758 | -61.5829 | 61.4044 | 0.02121 | -0.0074298 | 0.0090021 | 0.064892 | -0.01848 | -0.029249 | -0.023033 | 0.008606 | -0.0078185 | 0.062481 | 0.046433 | -0.019649 | -0.013945 | -0.012469 | -0.064087 | 61.3312 | -61.6562 | 61.528 | -61.2762 | -61.7294 | -61.7294 | 0.013733 | 61.2991 | -61.6379 | 61.5234 | -61.5189 | -61.5509 | -61.5555 | -0.073242 | -0.073242 | 0.1236 | 0.3067 | -0.14648 | -0.14648 | -0.073242 | -0.073242 | -0.054931 | -0.10529 | 0.11902 | 0.064087 | 0.027466 | 0.032044 | 0.082397 | 0.086975 | 0.37994 | 123.1842 | 0.11902 | 123.1613 | 122.9874 | 122.937 | 122.9141 | 122.8821 | -123.0606 | -123.0423 | 123.111 | 123.1064 | 61.5189 | 61.5967
89.1406 | 123.1979 | -61.6516 | 61.4456 | 0.0059509 | -0.0087116 | 0.0079339 | 0.06596 | -0.021044 | -0.029249 | -0.023246 | 0.0055542 | -0.0093139 | 0.063549 | 0.051987 | -0.019649 | -0.011809 | -0.013751 | -0.13733 | 61.409 | -61.6837 | 61.3861 | -61.4731 | -61.8576 | -61.8713 | -0.14648 | 61.3586 | -61.647 | 61.4227 | -61.6425 | -61.6653 | -61.6379 | -0.032044 | -0.036621 | -0.05951 | 0.17853 | -0.21973 | -0.20599 | -0.18768 | -0.17395 | 0.004577 | -0.086975 | -0.022889 | 0.009155 | 0.013733 | -0.013733 | 0.009156 | -0.01831 | 0.21057 | 123.0698 | 0.004578 | 123.0698 | 123.0927 | 123.0057 | 123.0606 | 123.0103 | -123.1293 | -123.0927 | 123.0377 | 123.0743 | 61.5143 | 61.5051
90.9062 | 123.2712 | -61.5509 | 61.4594 | 0.01358 | -0.0091388 | 0.0085749 | 0.063183 | -0.021471 | -0.027327 | -0.024314 | -0.00054937 | -0.012732 | 0.05949 | 0.048569 | -0.019435 | -0.0101 | -0.012896 | -0.09613 | 61.3815 | -61.6379 | 61.4868 | -61.3083 | -61.734 | -61.7523 | -0.018311 | 61.3495 | -61.5875 | 61.5234 | -61.4639 | -61.496 | -61.5143 | -0.086975 | -0.07782 | 0.027465 | 0.24261 | -0.20142 | -0.18311 | -0.11444 | -0.096131 | -0.036621 | -0.10986 | 0.064086 | 0.086975 | 0.036621 | 0.054931 | 0.073242 | 0.091552 | 0.32959 | 123.1247 | 0.1236 | 123.111 | 123.0194 | 122.937 | 122.9324 | 122.9004 | -123.0972 | -123.0469 | 123.0377 | 123.0743 | 61.4548 | 61.5326
92.6094 | 123.2986 | -61.5601 | 61.4685 | 0.01358 | -0.011489 | 0.0092157 | 0.064038 | -0.019762 | -0.029036 | -0.023887 | 0.0025024 | -0.0097411 | 0.065044 | 0.050065 | -0.021358 | -0.013304 | -0.014178 | -0.064087 | 61.3815 | -61.6379 | 61.5143 | -61.2808 | -61.702 | -61.7111 | 0.013733 | 61.3632 | -61.5463 | 61.5829 | -61.4365 | -61.4639 | -61.4731 | -0.077819 | -0.086975 | 0.045776 | 0.27924 | -0.15106 | -0.14191 | -0.073243 | -0.064087 | 0.013733 | -0.10529 | 0.11444 | 0.1236 | 0.086976 | 0.096131 | 0.073243 | 0.082398 | 0.35706 | 123.1522 | 0.10986 | 123.1293 | 123.0194 | 122.9095 | 122.9416 | 122.9233 | -123.1064 | -123.0148 | 123.0743 | 123.143 | 61.496 | 61.5738
94.3594 | 123.2254 | -61.5921 | 61.4548 | 0.02121 | -0.009566 | 0.0081477 | 0.065106 | -0.019762 | -0.031385 | -0.025383 | 0.008606 | -0.0065369 | 0.062481 | 0.04451 | -0.02499 | -0.012877 | -0.014819 | -0.018311 | 61.4502 | -61.6562 | 61.496 | -61.3403 | -61.7294 | -61.7615 | 0 | 61.3861 | -61.6058 | 61.5143 | -61.5143 | -61.5417 | -61.5555 | -0.064087 | -0.004578 | 0.041199 | 0.25177 | -0.16937 | -0.13733 | -0.10529 | -0.073242 | -0.013733 | -0.068665 | 0.059509 | 0.07782 | 0.036621 | 0.050354 | 0.050354 | 0.064087 | 0.31586 | 123.1522 | 0.091553 | 123.1201 | 123.1064 | 122.9919 | 123.0423 | 122.9782 | -123.111 | -123.0606 | 123.0881 | 123.1064 | 61.5738 | 61.5921
96.1094 | 123.2162 | -61.5372 | 61.4822 | 0.02121 | -0.0080706 | 0.0090021 | 0.066388 | -0.020403 | -0.028395 | -0.023674 | 0.011658 | -0.0067505 | 0.065044 | 0.041947 | -0.022212 | -0.011595 | -0.013965 | -0.032043 | 61.4365 | -61.6379 | 61.4822 | -61.3403 | -61.7111 | -61.7523 | -0.036621 | 61.3861 | -61.6058 | 61.4914 | -61.5189 | -61.5646 | -61.5601 | -0.10071 | -0.045777 | 0 | 0.19684 | -0.21515 | -0.17395 | -0.11444 | -0.073243 | -0.068665 | -0.096131 | 0.009155 | 0.01831 | -0.022889 | -0.027466 | 0.045776 | 0.041199 | 0.29755 | 123.1201 | 0.086975 | 123.0972 | 123.0743 | 122.9919 | 122.9736 | 122.9233 | -123.1201 | -123.0881 | 123.0194 | 123.0286 | 61.5051 | 61.5005
97.8594 | 123.2529 | -61.5829 | 61.4319 | 0.036468 | -0.008498 | 0.0077203 | 0.064465 | -0.021898 | -0.02989 | -0.023674 | 0.008606 | -0.010169 | 0.064617 | 0.051133 | -0.019435 | -0.011595 | -0.015887 | -0.07782 | 61.3495 | -61.6562 | 61.4868 | -61.2991 | -61.7157 | -61.7477 | -0.022888 | 61.3403 | -61.5967 | 61.5189 | -61.5051 | -61.5509 | -61.5509 | -0.073242 | -0.082398 | 0.054931 | 0.28381 | -0.1648 | -0.13275 | -0.091553 | -0.059509 | -0.013733 | -0.091553 | 0.086975 | 0.07782 | 0.032044 | 0.032044 | 0.045777 | 0.045777 | 0.35706 | 123.143 | 0.091553 | 123.1155 | 123.0057 | 122.937 | 122.9324 | 122.9233 | -123.0881 | -123.0286 | 123.0698 | 123.1018 | 61.5051 | 61.5601
99.6094 | 123.2483 | -61.5829 | 61.4365 | 0.01358 | -0.0089252 | 0.0092157 | 0.064251 | -0.020617 | -0.029036 | -0.021965 | 0.0055542 | -0.0082459 | 0.061412 | 0.044724 | -0.021144 | -0.012236 | -0.014605 | -0.064087 | 61.3541 | -61.615 | 61.4822 | -61.322 | -61.734 | -61.7386 | -0.041199 | 61.3403 | -61.5784 | 61.5097 | -61.5005 | -61.5234 | -61.5463 | -0.032043 | -0.082397 | 0.045777 | 0.26093 | -0.15564 | -0.15106 | -0.1236 | -0.11902 | 0.004578 | -0.09613 | 0.073243 | 0.082398 | 0.036621 | 0.05951 | 0.032043 | 0.054932 | 0.29297 | 123.0972 | 0.07782 | 123.0881 | 122.9691 | 122.9187 | 122.937 | 122.9233 | -123.0515 | -123.0148 | 123.0652 | 123.0927 | 61.5189 | 61.5417
101.375 | 123.1659 | -61.5829 | 61.5234 | 0.0059509 | -0.0087116 | 0.0053705 | 0.064038 | -0.018053 | -0.030531 | -0.026878 | 0.0025024 | -0.0061095 | 0.062481 | 0.043656 | -0.02264 | -0.013091 | -0.015887 | -0.054932 | 61.4456 | -61.6287 | 61.4685 | -61.3449 | -61.734 | -61.7523 | -0.050354 | 61.441 | -61.5555 | 61.4731 | -61.528 | -61.5646 | -61.5646 | -0.045776 | -0.077819 | -0.054931 | 0.23804 | -0.16937 | -0.15106 | -0.1236 | -0.10529 | 0.027466 | -0.082397 | -0.050354 | 0.054932 | 0.018311 | 0.018311 | -0.009155 | -0.009155 | 0.28381 | 123.0972 | 0.027466 | 123.0286 | 123.0743 | 122.9965 | 123.0286 | 123.024 | -123.1522 | -123.0789 | 123.0515 | 123.056 | 61.528 | 61.5326
103.0781 | 123.2208 | -61.5829 | 61.4685 | 0.0059509 | -0.0080706 | 0.0087885 | 0.066174 | -0.022539 | -0.028608 | -0.023887 | -0.00054937 | -0.0061095 | 0.062053 | 0.04686 | -0.020076 | -0.012664 | -0.016742 | -0.009155 | 61.409 | -61.6333 | 61.5005 | -61.3174 | -61.7249 | -61.7386 | 0.013733 | 61.377 | -61.6104 | 61.5143 | -61.5143 | -61.5509 | -61.5326 | -0.050354 | -0.059509 | 0.032043 | 0.2655 | -0.15564 | -0.14191 | -0.10528 | -0.091553 | -0.027466 | -0.091553 | 0.045776 | 0.068665 | 0.050354 | 0.032044 | 0.07782 | 0.05951 | 0.31586 | 123.1338 | 0.096131 | 123.1247 | 123.0423 | 122.9874 | 122.9919 | 122.9599 | -123.1018 | -123.0789 | 123.0835 | 123.0972 | 61.5738 | 61.5967
104.8125 | 123.2895 | -61.5921 | 61.3998 | 0.01358 | -0.007857 | 0.0081477 | 0.063183 | -0.016131 | -0.030104 | -0.023246 | -0.00054937 | -0.0097411 | 0.06419 | 0.046219 | -0.013668 | -0.01245 | -0.012256 | -0.059509 | 61.3037 | -61.6287 | 61.4868 | -61.29 | -61.7432 | -61.7432 | -0.009155 | 61.2717 | -61.6287 | 61.528 | -61.4868 | -61.5234 | -61.528 | -0.036621 | -0.09613 | 0.086975 | 0.30212 | -0.15106 | -0.15106 | -0.11444 | -0.11444 | -0.036621 | -0.12817 | 0.12817 | 0.10529 | 0.064087 | 0.068665 | 0.10071 | 0.10529 | 0.33875 | 123.1155 | 0.14191 | 123.1567 | 122.9324 | 122.9004 | 122.8958 | 122.8638 | -123.0286 | -123.0286 | 123.0789 | 123.1201 | 61.5326 | 61.5829
106.5625 | 123.1796 | -61.5601 | 61.4914 | 0.02121 | -0.009566 | 0.010925 | 0.066601 | -0.021044 | -0.028608 | -0.019188 | 0.014709 | -0.0082459 | 0.061626 | 0.041947 | -0.023494 | -0.013518 | -0.018878 | -0.032043 | 61.4502 | -61.647 | 61.4548 | -61.3403 | -61.7249 | -61.7432 | -0.045776 | 61.3953 | -61.6013 | 61.4822 | -61.5097 | -61.5372 | -61.5509 | -0.086975 | -0.041199 | -0.036621 | 0.21973 | -0.1831 | -0.16479 | -0.09613 | -0.07782 | -0.041198 | -0.09613 | -0.009155 | 0.050354 | 0.009156 | 0.022889 | 0.050354 | 0.064087 | 0.3067 | 123.1018 | 0.091552 | 123.0835 | 123.0972 | 122.9965 | 123.0103 | 122.9553 | -123.1384 | -123.0927 | 123.0148 | 123.0423 | 61.528 | 61.5143
108.2812 | 123.2895 | -61.5784 | 61.3678 | 0.01358 | -0.0070026 | 0.010284 | 0.066815 | -0.01848 | -0.029676 | -0.02581 | 0.0055542 | -0.0093139 | 0.062908 | 0.042588 | -0.020076 | -0.011382 | -0.017169 | -0.091553 | 61.3266 | -61.6608 | 61.4685 | -61.3174 | -61.7477 | -61.7615 | 0.004578 | 61.2625 | -61.5967 | 61.5326 | -61.4868 | -61.5326 | -61.5143 | -0.082398 | -0.041199 | 0.10071 | 0.26093 | -0.18311 | -0.16937 | -0.10071 | -0.086975 | -0.018311 | -0.10529 | 0.16479 | 0.091553 | 0.064087 | 0.045776 | 0.082398 | 0.064087 | 0.34332 | 123.1293 | 0.10986 | 123.1293 | 122.9874 | 122.8592 | 122.905 | 122.8409 | -123.0286 | -122.9645 | 123.0469 | 123.111 | 61.4868 | 61.5829
110.0312 | 123.2071 | -61.5829 | 61.4456 | 0.01358 | -0.0072162 | 0.0085749 | 0.06532 | -0.017626 | -0.02989 | -0.020256 | 0.0055542 | -0.0080321 | 0.060985 | 0.042588 | -0.022212 | -0.013304 | -0.014178 | -0.027466 | 61.4182 | -61.6425 | 61.4777 | -61.3037 | -61.7294 | -61.7661 | 0.004578 | 61.3678 | -61.5921 | 61.496 | -61.5051 | -61.5326 | -61.528 | -0.059509 | -0.027466 | 0.032043 | 0.27924 | -0.18311 | -0.14648 | -0.1236 | -0.086975 | -0.009155 | -0.07782 | 0.050354 | 0.07782 | 0.054932 | 0.050354 | 0.064087 | 0.059509 | 0.33875 | 123.1201 | 0.086975 | 123.0881 | 123.0606 | 122.9599 | 123.0011 | 122.9507 | -123.0881 | -123.0377 | 123.0606 | 123.0789 | 61.5555 | 61.5875
111.7969 | 123.2986 | -61.5234 | 61.4365 | 0.01358 | -0.010848 | 0.0081477 | 0.063611 | -0.020617 | -0.031385 | -0.025596 | -0.00054937 | -0.0097411 | 0.062694 | 0.047501 | -0.02029 | -0.012664 | -0.012896 | -0.018311 | 61.3495 | -61.5738 | 61.5555 | -61.2122 | -61.6196 | -61.6516 | 0.11444 | 61.3449 | -61.5463 | 61.5967 | -61.3815 | -61.4044 | -61.4548 | -0.050355 | -0.086975 | 0.11902 | 0.31128 | -0.12817 | -0.096131 | -0.077819 | -0.045776 | -0.022889 | -0.091552 | 0.16022 | 0.14191 | 0.068664 | 0.11902 | 0.091553 | 0.14191 | 0.36163 | 123.1293 | 0.16479 | 123.143 | 122.9233 | 122.8912 | 122.8729 | 122.8683 | -123.0103 | -122.9828 | 123.0789 | 123.1201 | 61.5051 | 61.6379
113.4844 | 123.1293 | -61.5555 | 61.5143 | 0.0059509 | -0.0089252 | 0.0077203 | 0.065533 | -0.021685 | -0.030958 | -0.023246 | 0.0055542 | -0.0063233 | 0.064403 | 0.04387 | -0.023708 | -0.014586 | -0.012683 | -0.013733 | 61.409 | -61.5967 | 61.4685 | -61.3266 | -61.7203 | -61.7432 | -0.022888 | 61.3907 | -61.5555 | 61.4731 | -61.5051 | -61.528 | -61.5646 | -0.041199 | -0.10529 | -0.045776 | 0.22888 | -0.18768 | -0.16479 | -0.14648 | -0.1236 | 0 | -0.1236 | -0.041199 | 0.050354 | -0.009155 | 0.027466 | -0.009155 | 0.027466 | 0.27008 | 123.0652 | 0.050354 | 123.0286 | 123.0057 | 122.9462 | 122.9645 | 122.9462 | -123.111 | -123.0698 | 123.024 | 123.0286 | 61.5417 | 61.5326
115.25 | 123.1476 | -61.5417 | 61.5463 | -0.0016786 | -0.0097796 | 0.0079339 | 0.06596 | -0.018267 | -0.030104 | -0.024742 | -0.003601 | -0.0082459 | 0.064403 | 0.046433 | -0.022853 | -0.014586 | -0.014819 | -0.013733 | 61.3953 | -61.5921 | 61.496 | -61.3037 | -61.6882 | -61.7249 | -0.013733 | 61.3907 | -61.5189 | 61.4685 | -61.5097 | -61.5372 | -61.5555 | -0.050354 | -0.15106 | -0.050354 | 0.23804 | -0.18311 | -0.14648 | -0.13275 | -0.09613 | 0.022888 | -0.15564 | -0.07782 | 0.032043 | -0.013733 | 0.004578 | -0.036621 | -0.01831 | 0.28839 | 123.0881 | 0.009155 | 122.9874 | 122.9874 | 122.9095 | 122.937 | 122.9324 | -123.1384 | -123.0652 | 123.0377 | 123.0103 | 61.528 | 61.528
117.0156 | 123.1476 | -61.5601 | 61.5143 | -0.0016786 | -0.0089252 | 0.0090021 | 0.064465 | -0.025103 | -0.030958 | -0.023033 | -0.00054937 | -0.0088867 | 0.061626 | 0.040452 | -0.023067 | -0.011809 | -0.014392 | 0.009155 | 61.3861 | -61.5829 | 61.5097 | -61.2625 | -61.6608 | -61.6974 | 0 | 61.4044 | -61.5372 | 61.4868 | -61.4868 | -61.5234 | -61.5417 | -0.022888 | -0.12817 | -0.004577 | 0.29755 | -0.13733 | -0.10071 | -0.11444 | -0.07782 | 0.022889 | -0.10986 | -0.027466 | 0.073243 | 0.018311 | 0.036622 | -0.004578 | 0.013733 | 0.32043 | 123.0927 | 0.050354 | 123.024 | 122.9691 | 122.9416 | 122.9462 | 122.9645 | -123.0972 | -123.0515 | 123.0698 | 123.0469 | 61.5692 | 61.5601
118.7812 | 123.2666 | -61.5234 | 61.441 | 0.0059509 | -0.0091388 | 0.0087885 | 0.064038 | -0.022753 | -0.028395 | -0.026023 | -0.00054937 | -0.0088867 | 0.062908 | 0.040024 | -0.02029 | -0.013091 | -0.017596 | -0.059509 | 61.3358 | -61.615 | 61.5189 | -61.2579 | -61.6608 | -61.6562 | 0.032043 | 61.3495 | -61.5601 | 61.5738 | -61.3953 | -61.4227 | -61.4639 | -0.091553 | -0.10529 | 0.07782 | 0.2655 | -0.13275 | -0.13733 | -0.041199 | -0.045777 | -0.036622 | -0.091553 | 0.13275 | 0.12817 | 0.059509 | 0.10071 | 0.096131 | 0.13733 | 0.35705 | 123.1338 | 0.1648 | 123.1339 | 122.9507 | 122.9095 | 122.8592 | 122.8729 | -123.056 | -123.0011 | 123.0423 | 123.0972 | 61.4639 | 61.5555
120.4688 | 123.2162 | -61.5555 | 61.4227 | 0.02121 | -0.0080706 | 0.0087885 | 0.063824 | -0.021258 | -0.028822 | -0.021324 | 0.008606 | -0.0071777 | 0.06184 | 0.04152 | -0.018367 | -0.012023 | -0.015033 | -0.082397 | 61.3358 | -61.6241 | 61.4777 | -61.2991 | -61.7203 | -61.7294 | -0.032043 | 61.3312 | -61.5875 | 61.496 | -61.5051 | -61.5326 | -61.5463 | -0.068665 | -0.086975 | 0.054932 | 0.25635 | -0.17395 | -0.16479 | -0.10528 | -0.09613 | -0.032043 | -0.091552 | 0.073243 | 0.050354 | 0.009155 | 0.022888 | 0.041198 | 0.054931 | 0.32501 | 123.1018 | 0.082397 | 123.0835 | 122.9599 | 122.9187 | 122.8912 | 122.8867 | -123.0469 | -123.0103 | 123.0331 | 123.0515 | 61.4731 | 61.5234
122.1562 | 123.1705 | -61.5463 | 61.496 | 0.036468 | -0.006148 | 0.0053705 | 0.065106 | -0.016131 | -0.033094 | -0.024742 | 0.008606 | -0.0071777 | 0.062694 | 0.04152 | -0.021144 | -0.0148 | -0.015033 | -0.045776 | 61.4319 | -61.6241 | 61.4548 | -61.3312 | -61.7294 | -61.7523 | -0.059509 | 61.4136 | -61.5875 | 61.4639 | -61.5234 | -61.5555 | -61.5417 | -0.07782 | -0.064087 | -0.041199 | 0.21515 | -0.20599 | -0.1831 | -0.12817 | -0.10528 | -0.041198 | -0.082398 | -0.032044 | 0.022889 | 0.004578 | -0.009155 | 0.045776 | 0.032043 | 0.29297 | 123.0789 | 0.064087 | 123.0515 | 123.056 | 123.0011 | 122.9782 | 122.9599 | -123.1201 | -123.0835 | 123.0011 | 123.0103 | 61.5006 | 61.4868
123.8594 | 123.1338 | -61.6333 | 61.3998 | 0.01358 | -0.0074298 | 0.0092157 | 0.065747 | -0.021258 | -0.028822 | -0.025383 | 0.0025024 | -0.0048279 | 0.063121 | 0.045579 | -0.021785 | -0.013304 | -0.017596 | -0.13275 | 61.3907 | -61.6699 | 61.3449 | -61.4594 | -61.8576 | -61.853 | -0.16022 | 61.3266 | -61.6196 | 61.3998 | -61.615 | -61.6653 | -61.6104 | -0.036621 | -0.009155 | -0.054931 | 0.17395 | -0.21973 | -0.2243 | -0.1831 | -0.18768 | 0.013733 | -0.073242 | 0 | 0.018311 | 0.022888 | -0.032043 | 0.009155 | -0.045776 | 0.21057 | 123.0148 | 0.004578 | 123.0194 | 123.0606 | 122.9462 | 123.024 | 122.9599 | -123.0698 | -123.0194 | 122.9782 | 123.0331 | 61.5006 | 61.4731
125.625 | 123.1522 | -61.6058 | 61.4136 | -0.0016786 | -0.0089252 | 0.0096429 | 0.067029 | -0.021044 | -0.030104 | -0.024955 | 0.0025024 | -0.0091003 | 0.062908 | 0.045579 | -0.019649 | -0.010955 | -0.018664 | -0.13733 | 61.3724 | -61.6608 | 61.3586 | -61.4273 | -61.8393 | -61.8576 | -0.13733 | 61.3358 | -61.6333 | 61.409 | -61.5967 | -61.647 | -61.6013 | -0.054932 | -0.041199 | -0.054931 | 0.17853 | -0.25177 | -0.23346 | -0.19684 | -0.17853 | -0.027466 | -0.07782 | -0.004577 | 0.009155 | 0.004578 | -0.041199 | 0.032044 | -0.013733 | 0.23346 | 123.0194 | 0.036621 | 123.0423 | 123.0331 | 122.9691 | 122.9782 | 122.9416 | -123.0743 | -123.0469 | 122.9645 | 123.0148 | 61.4685 | 61.4685
127.3438 | 123.1522 | -61.5921 | 61.4044 | 0.0059509 | -0.0074298 | 0.0094293 | 0.067029 | -0.020189 | -0.029463 | -0.023674 | 0.0025024 | -0.0073913 | 0.060985 | 0.043656 | -0.019222 | -0.011595 | -0.016314 | -0.1236 | 61.3495 | -61.6653 | 61.3449 | -61.4273 | -61.853 | -61.853 | -0.14191 | 61.3403 | -61.6241 | 61.3953 | -61.6058 | -61.6516 | -61.6013 | -0.073242 | -0.054932 | -0.059509 | 0.16479 | -0.26093 | -0.26093 | -0.18768 | -0.18768 | -0.032044 | -0.064087 | -0.009155 | -0.013733 | -0.009155 | -0.059509 | 0.022889 | -0.027465 | 0.23804 | 123.0103 | 0.018311 | 123.0194 | 123.0148 | 122.9645 | 122.9416 | 122.9324 | -123.0698 | -123.0286 | 122.937 | 122.9874 | 61.4685 | 61.4502
129.1094 | 123.1705 | -61.5555 | 61.4685 | 0.0059509 | -0.008498 | 0.0087885 | 0.066601 | -0.018053 | -0.029676 | -0.02111 | 0.011658 | -0.0095275 | 0.061626 | 0.037034 | -0.021572 | -0.012236 | -0.016955 | -0.022888 | 61.4365 | -61.647 | 61.4548 | -61.3129 | -61.7157 | -61.7523 | -0.032043 | 61.3632 | -61.5738 | 61.4868 | -61.5005 | -61.5326 | -61.5326 | -0.091553 | -0.032044 | -0.013733 | 0.24262 | -0.19684 | -0.16022 | -0.10529 | -0.068664 | -0.018311 | -0.10529 | 0.01831 | 0.054932 | 0.022888 | 0.022888 | 0.041199 | 0.041199 | 0.33417 | 123.1018 | 0.073243 | 123.0606 | 123.0835 | 122.937 | 122.9919 | 122.9187 | -123.1155 | -123.0423 | 123.0103 | 123.0423 | 61.5326 | 61.5234
130.7969 | 123.2574 | -61.5692 | 61.3678 | -0.0016786 | -0.0091388 | 0.0081477 | 0.066174 | -0.016344 | -0.027754 | -0.020897 | 0.0055542 | -0.010169 | 0.06419 | 0.045151 | -0.019008 | -0.010741 | -0.015033 | -0.07782 | 61.3174 | -61.6608 | 61.5005 | -61.2396 | -61.7065 | -61.7203 | 0.018311 | 61.2671 | -61.6013 | 61.5097 | -61.4639 | -61.4914 | -61.5051 | -0.091553 | -0.050354 | 0.13275 | 0.32959 | -0.15106 | -0.13733 | -0.059509 | -0.045776 | -0.032043 | -0.10071 | 0.14191 | 0.10529 | 0.064087 | 0.07782 | 0.09613 | 0.10986 | 0.42114 | 123.1613 | 0.13733 | 123.111 | 122.9782 | 122.8683 | 122.8867 | 122.8363 | -123.0286 | -122.9691 | 123.0698 | 123.0789 | 61.4914 | 61.5875
132.7344 | 123.23 | -61.5829 | 61.377 | -0.0016786 | -0.0091388 | 0.0087885 | 0.066601 | -0.018053 | -0.030958 | -0.025169 | 0.0025024 | -0.0069641 | 0.06483 | 0.047074 | -0.018581 | -0.012664 | -0.015033 | -0.13733 | 61.3266 | -61.6699 | 61.3953 | -61.3541 | -61.7798 | -61.8027 | -0.068665 | 61.2717 | -61.5967 | 61.5005 | -61.5189 | -61.5372 | -61.5189 | -0.086975 | -0.050354 | 0.018311 | 0.22888 | -0.21973 | -0.19684 | -0.13275 | -0.10986 | -0.013733 | -0.10529 | 0.1236 | 0.064087 | 0.064087 | 0.045777 | 0.07782 | 0.05951 | 0.31586 | 123.0652 | 0.07782 | 123.0972 | 122.9965 | 122.8683 | 122.9095 | 122.8546 | -123.0469 | -122.9736 | 122.9782 | 123.0835 | 61.4456 | 61.5143
134.5469 | 123.2025 | -61.5372 | 61.441 | 0.01358 | -0.01277 | 0.0072931 | 0.064465 | -0.017626 | -0.029463 | -0.025169 | 0.0055542 | -0.0091003 | 0.059703 | 0.044083 | -0.021358 | -0.012236 | -0.011401 | -0.07782 | 61.3266 | -61.6333 | 61.4548 | -61.29 | -61.7249 | -61.7294 | -0.045776 | 61.2991 | -61.5646 | 61.4914 | -61.5005 | -61.5097 | -61.5326 | -0.096131 | -0.11444 | 0.013733 | 0.24719 | -0.19226 | -0.18768 | -0.09613 | -0.091553 | -0.027466 | -0.14191 | 0.050354 | 0.036621 | 0.004577 | 0.027465 | 0.032043 | 0.054931 | 0.34332 | 123.0881 | 0.064087 | 123.056 | 122.9599 | 122.8638 | 122.8638 | 122.8363 | -123.0743 | -123.0057 | 122.9919 | 123.0286 | 61.4594 | 61.4914
136.25 | 123.2483 | -61.5005 | 61.4365 | -0.0016786 | -0.011061 | 0.0083613 | 0.062115 | -0.019976 | -0.030531 | -0.022819 | 0.0025024 | -0.0095275 | 0.060344 | 0.047501 | -0.021572 | -0.011809 | -0.018237 | 0.013733 | 61.3586 | -61.5692 | 61.5646 | -61.1618 | -61.6013 | -61.6287 | 0.10986 | 61.3312 | -61.5097 | 61.5784 | -61.3815 | -61.3907 | -61.4502 | -0.068665 | -0.077819 | 0.12817 | 0.33875 | -0.12817 | -0.10071 | -0.059509 | -0.032043 | -0.009156 | -0.10529 | 0.14191 | 0.11902 | 0.050354 | 0.10986 | 0.05951 | 0.11902 | 0.40741 | 123.1338 | 0.12817 | 123.0881 | 122.9279 | 122.8409 | 122.8592 | 122.8317 | -123.0057 | -122.9462 | 123.0652 | 123.0789 | 61.5143 | 61.6104
137.9844 | 123.1155 | -61.5463 | 61.496 | 0.0059509 | -0.0087116 | 0.0057977 | 0.062329 | -0.021685 | -0.030531 | -0.02346 | -0.0066528 | -0.0076049 | 0.060772 | 0.044938 | -0.024135 | -0.013304 | -0.012683 | -0.064087 | 61.4273 | -61.5829 | 61.4273 | -61.3266 | -61.7157 | -61.7386 | -0.041199 | 61.3998 | -61.5509 | 61.4594 | -61.5051 | -61.5189 | -61.5143 | -0.036621 | -0.068665 | -0.068665 | 0.21973 | -0.19226 | -0.16937 | -0.15564 | -0.13275 | -0.004577 | -0.096131 | -0.036621 | 0.041199 | 0.032044 | 0.027466 | 0.036621 | 0.032043 | 0.25635 | 123.0103 | 0.045776 | 123.0103 | 123.0103 | 122.9507 | 122.9736 | 122.9462 | -123.0789 | -123.0469 | 122.9736 | 123.0057 | 61.4822 | 61.5051
139.7188 | 123.1476 | -61.5692 | 61.4227 | 0.0059509 | -0.0097796 | 0.0083613 | 0.064038 | -0.016131 | -0.030317 | -0.021751 | 0.0025024 | -0.0076049 | 0.062694 | 0.043229 | -0.019008 | -0.014373 | -0.016528 | -0.036621 | 61.377 | -61.647 | 61.4731 | -61.3037 | -61.7249 | -61.7386 | 0 | 61.3495 | -61.5646 | 61.4594 | -61.5189 | -61.5417 | -61.5509 | -0.07782 | -0.045776 | 0.050354 | 0.2655 | -0.16937 | -0.15564 | -0.091552 | -0.07782 | 0.004578 | -0.073242 | 0.036622 | 0.050354 | 0.018311 | 0.027466 | 0.013733 | 0.022888 | 0.34332 | 123.1201 | 0.045776 | 123.024 | 123.024 | 122.9141 | 122.9462 | 122.9187 | -123.0698 | -122.9874 | 123.0423 | 123.0286 | 61.5326 | 61.5692
141.4062 | 123.1705 | -61.528 | 61.4731 | 0.0059509 | -0.010207 | 0.0075067 | 0.062543 | -0.024889 | -0.030745 | -0.023674 | -0.00054937 | -0.0073913 | 0.061199 | 0.042801 | -0.021572 | -0.015013 | -0.012896 | 0.009155 | 61.3586 | -61.5646 | 61.5326 | -61.1938 | -61.6058 | -61.647 | 0.050354 | 61.3632 | -61.5005 | 61.5143 | -61.4319 | -61.4548 | -61.4731 | -0.036621 | -0.11444 | 0.05951 | 0.33417 | -0.11902 | -0.07782 | -0.082398 | -0.041199 | 0.027466 | -0.10986 | 0.041199 | 0.09613 | 0.054932 | 0.073242 | 0.027466 | 0.045776 | 0.37079 | 123.0972 | 0.068664 | 123.0148 | 122.9233 | 122.8638 | 122.8867 | 122.8912 | -123.0377 | -122.9736 | 123.0606 | 123.0423 | 61.5372 | 61.5784
143.0781 | 123.1659 | -61.5601 | 61.4227 | 0.0059509 | -0.0089252 | 0.0092157 | 0.065106 | -0.015917 | -0.028822 | -0.022605 | 0.008606 | -0.0071777 | 0.064403 | 0.043442 | -0.020931 | -0.012664 | -0.015246 | -0.041199 | 61.3953 | -61.6287 | 61.4502 | -61.2854 | -61.702 | -61.7386 | -0.009155 | 61.3541 | -61.5601 | 61.4548 | -61.4868 | -61.5326 | -61.5143 | -0.068664 | -0.027465 | 0.027466 | 0.27466 | -0.17853 | -0.14191 | -0.10986 | -0.073242 | 0 | -0.068664 | 0.032044 | 0.073243 | 0.045777 | 0.027466 | 0.045777 | 0.027466 | 0.34332 | 123.0789 | 0.073243 | 123.0148 | 123.024 | 122.9141 | 122.9553 | 122.9141 | -123.0515 | -122.9828 | 123.0103 | 123.0148 | 61.5189 | 61.5509
144.75 | 123.1293 | -61.5967 | 61.3815 | 0.0059509 | -0.0091388 | 0.0070795 | 0.066601 | -0.015703 | -0.030958 | -0.027732 | 0.0025024 | -0.0078185 | 0.062908 | 0.048142 | -0.019649 | -0.01245 | -0.012683 | -0.14191 | 61.3541 | -61.6608 | 61.3449 | -61.409 | -61.8301 | -61.8256 | -0.1236 | 61.2946 | -61.6425 | 61.4182 | -61.5829 | -61.6333 | -61.5967 | -0.064087 | -0.027466 | -0.036621 | 0.18768 | -0.22888 | -0.23346 | -0.16479 | -0.16937 | -0.045776 | -0.086975 | 0.036621 | 0.013733 | 0 | -0.036621 | 0.045776 | 0.009155 | 0.25177 | 123.0057 | 0.059509 | 123.0606 | 123.0148 | 122.937 | 122.9507 | 122.8912 | -123.0423 | -123.024 | 122.9416 | 123.0148 | 61.4548 | 61.4731
146.4375 | 123.23 | -61.528 | 61.4594 | -0.0093076 | -0.010421 | 0.0090021 | 0.063397 | -0.020189 | -0.029676 | -0.025596 | 0.0025024 | -0.0099549 | 0.061626 | 0.055405 | -0.021358 | -0.012236 | -0.016314 | 0.018311 | 61.3632 | -61.5509 | 61.5509 | -61.1526 | -61.6058 | -61.6333 | 0.086975 | 61.3449 | -61.5189 | 61.5601 | -61.377 | -61.4136 | -61.441 | -0.022888 | -0.096131 | 0.091552 | 0.37537 | -0.10529 | -0.07782 | -0.082398 | -0.054932 | 0.009155 | -0.11444 | 0.10071 | 0.15106 | 0.086975 | 0.11444 | 0.07782 | 0.10529 | 0.39825 | 123.1018 | 0.14191 | 123.0789 | 122.9141 | 122.8638 | 122.8912 | 122.8729 | -123.0103 | -122.9782 | 123.0789 | 123.0881 | 61.5463 | 61.615
148.1562 | 123.2758 | -61.4868 | 61.4365 | 0.01358 | -0.01277 | 0.01007 | 0.061688 | -0.02553 | -0.032881 | -0.023674 | -0.00054937 | -0.0091003 | 0.062267 | 0.041092 | -0.018794 | -0.012664 | -0.016314 | -0.009155 | 61.3586 | -61.5692 | 61.5555 | -61.1755 | -61.5875 | -61.6287 | 0.1236 | 61.3129 | -61.4868 | 61.5921 | -61.3358 | -61.377 | -61.409 | -0.082398 | -0.077819 | 0.11902 | 0.31128 | -0.14191 | -0.10071 | -0.059509 | -0.01831 | 0 | -0.1236 | 0.15564 | 0.15106 | 0.077819 | 0.10986 | 0.077819 | 0.10986 | 0.39368 | 123.1247 | 0.15106 | 123.0789 | 122.9279 | 122.7997 | 122.8455 | 122.7997 | -123.0057 | -122.9233 | 123.0423 | 123.0789 | 61.4777 | 61.6104
149.875 | 123.1155 | -61.5646 | 61.4777 | -0.0016786 | -0.0097796 | 0.0077203 | 0.065533 | -0.022753 | -0.029249 | -0.025169 | 0.014709 | -0.0078185 | 0.061412 | 0.039384 | -0.02264 | -0.013945 | -0.016314 | -0.054932 | 61.4182 | -61.5738 | 61.4182 | -61.3037 | -61.6928 | -61.7203 | -0.036621 | 61.3998 | -61.5509 | 61.4548 | -61.5143 | -61.5463 | -61.5326 | -0.009156 | -0.059509 | -0.059509 | 0.26093 | -0.15564 | -0.12817 | -0.14648 | -0.11902 | 0.013733 | -0.07782 | -0.022888 | 0.050354 | 0.032043 | 0.01831 | 0.01831 | 0.004577 | 0.27008 | 122.9919 | 0.036621 | 123.0057 | 122.9919 | 122.9507 | 122.9828 | 122.9645 | -123.0515 | -123.0286 | 122.9828 | 123.0194 | 61.5097 | 61.528
151.5625 | 123.143 | -61.6058 | 61.3678 | -0.0093076 | -0.010207 | 0.0075067 | 0.066388 | -0.015276 | -0.030531 | -0.024314 | 0.0025024 | -0.0086731 | 0.06419 | 0.047288 | -0.020076 | -0.012236 | -0.014819 | -0.14191 | 61.377 | -61.6425 | 61.3541 | -61.4044 | -61.8118 | -61.8301 | -0.13275 | 61.29 | -61.6058 | 61.4136 | -61.5692 | -61.6058 | -61.5738 | -0.036621 | 0.009155 | -0.013733 | 0.20142 | -0.2243 | -0.20599 | -0.18768 | -0.16937 | 0 | -0.07782 | 0.045776 | 0.036621 | 0.032043 | 0 | 0.032043 | 0 | 0.23804 | 122.9965 | 0.036621 | 123.0194 | 123.0194 | 122.8958 | 122.9828 | 122.8958 | -123.0103 | -122.9736 | 122.9599 | 123.0194 | 61.4639 | 61.4731
153.2344 | 123.175 | -61.5646 | 61.3632 | 0.044098 | -0.011702 | 0.01007 | 0.064038 | -0.013781 | -0.030317 | -0.022605 | 0.011658 | -0.0088867 | 0.062267 | 0.048997 | -0.017726 | -0.010955 | -0.010547 | -0.041199 | 61.3083 | -61.6013 | 61.4822 | -61.2213 | -61.6837 | -61.7111 | 0.027466 | 61.2762 | -61.5829 | 61.4868 | -61.4731 | -61.5143 | -61.5143 | -0.036621 | -0.054931 | 0.11902 | 0.34332 | -0.14648 | -0.11902 | -0.10986 | -0.082398 | -0.018311 | -0.086975 | 0.1236 | 0.091553 | 0.050354 | 0.050354 | 0.068665 | 0.068665 | 0.37994 | 123.0835 | 0.10986 | 123.0698 | 122.9095 | 122.8592 | 122.8729 | 122.8409 | -122.9645 | -122.9462 | 123.0469 | 123.0515 | 61.5234 | 61.5921
154.9062 | 123.262 | -61.4914 | 61.4227 | 0.02121 | -0.010421 | 0.0075067 | 0.062543 | -0.019121 | -0.028608 | -0.021965 | 0.0055542 | -0.0086731 | 0.06419 | 0.043656 | -0.019649 | -0.011809 | -0.01546 | -0.004578 | 61.3586 | -61.5875 | 61.5326 | -61.171 | -61.5967 | -61.6333 | 0.10986 | 61.3358 | -61.5143 | 61.5829 | -61.3358 | -61.3815 | -61.4136 | -0.09613 | -0.064086 | 0.10986 | 0.32043 | -0.14191 | -0.10529 | -0.045777 | -0.009156 | -0.022888 | -0.086975 | 0.16022 | 0.15564 | 0.07782 | 0.10986 | 0.10071 | 0.13275 | 0.41656 | 123.1201 | 0.17853 | 123.0972 | 122.9462 | 122.85 | 122.85 | 122.8271 | -123.0103 | -122.937 | 123.024 | 123.0743 | 61.4868 | 61.6013
156.5938 | 123.111 | -61.5555 | 61.3815 | 0.0059509 | -0.0074298 | 0.0096429 | 0.066388 | -0.015703 | -0.029249 | -0.022605 | -0.00054937 | -0.0065369 | 0.062267 | 0.047715 | -0.022212 | -0.013518 | -0.016101 | -0.036621 | 61.3861 | -61.5921 | 61.4456 | -61.2991 | -61.7111 | -61.7615 | -0.036621 | 61.3358 | -61.5646 | 61.441 | -61.5463 | -61.5829 | -61.5601 | -0.036621 | 0.004577 | 0.064087 | 0.25635 | -0.20599 | -0.15564 | -0.16937 | -0.11902 | -0.009155 | -0.045777 | 0.059509 | 0.009155 | -0.004578 | -0.027466 | 0.004577 | -0.018311 | 0.29297 | 123.0377 | 0.01831 | 123.0057 | 122.9782 | 122.9004 | 122.9416 | 122.8912 | -122.9736 | -122.9462 | 123.0011 | 122.9965 | 61.5189 | 61.5189
158.3281 | 123.143 | -61.5372 | 61.4319 | 0.02121 | -0.0076434 | 0.010284 | 0.064679 | -0.01549 | -0.029036 | -0.02581 | 0.008606 | -0.0082459 | 0.06419 | 0.045792 | -0.022853 | -0.012023 | -0.017169 | -0.032043 | 61.3953 | -61.6196 | 61.4456 | -61.29 | -61.7065 | -61.7065 | -0.013733 | 61.3403 | -61.5601 | 61.4639 | -61.4731 | -61.5234 | -61.5097 | -0.082398 | -0.036621 | 0.013733 | 0.24719 | -0.16937 | -0.16937 | -0.086975 | -0.086975 | -0.022889 | -0.091553 | 0.032043 | 0.064087 | 0.027465 | 0.013733 | 0.050354 | 0.036622 | 0.32959 | 123.0652 | 0.086976 | 123.024 | 123.0148 | 122.9004 | 122.9324 | 122.8775 | -123.0515 | -122.9919 | 122.9828 | 123.0011 | 61.5051 | 61.5234
160.0156 | 123.2346 | -61.5601 | 61.3495 | 0.01358 | -0.010848 | 0.0081477 | 0.065106 | -0.019335 | -0.032026 | -0.024528 | 0.0025024 | -0.0063233 | 0.062053 | 0.046433 | -0.017726 | -0.0101 | -0.017169 | -0.09613 | 61.3129 | -61.6287 | 61.4594 | -61.29 | -61.7249 | -61.7386 | -0.018311 | 61.2534 | -61.5921 | 61.496 | -61.4639 | -61.5005 | -61.4731 | -0.068664 | -0.036621 | 0.10986 | 0.27008 | -0.17853 | -0.16479 | -0.10986 | -0.096131 | -0.032043 | -0.09613 | 0.14648 | 0.096131 | 0.086976 | 0.05951 | 0.11902 | 0.091553 | 0.33875 | 123.0881 | 0.12817 | 123.0881 | 122.9416 | 122.8455 | 122.8729 | 122.8134 | -122.9782 | -122.9416 | 123.0194 | 123.056 | 61.4639 | 61.5417
161.6875 | 123.1613 | -61.5234 | 61.3953 | 0.02121 | -0.0093524 | 0.01242 | 0.063824 | -0.016771 | -0.027754 | -0.024314 | 0.0055542 | -0.0084595 | 0.062267 | 0.048569 | -0.019435 | -0.013518 | -0.01781 | -0.068665 | 61.3358 | -61.615 | 61.4273 | -61.2762 | -61.6882 | -61.7065 | -0.027466 | 61.2991 | -61.5829 | 61.4639 | -61.4685 | -61.496 | -61.4914 | -0.091553 | -0.05951 | 0.032043 | 0.24719 | -0.18311 | -0.16479 | -0.091553 | -0.073242 | -0.05951 | -0.096131 | 0.068664 | 0.054931 | 0.032043 | 0.027465 | 0.091553 | 0.086975 | 0.33874 | 123.0423 | 0.11444 | 123.0469 | 122.9507 | 122.8821 | 122.8592 | 122.8226 | -123.0103 | -122.9782 | 122.9507 | 122.9874 | 61.4548 | 61.496
163.4219 | 123.1659 | -61.528 | 61.4182 | 0.02121 | -0.0074298 | 0.011352 | 0.064038 | -0.016558 | -0.028608 | -0.022178 | 0.0025024 | -0.0095275 | 0.063549 | 0.050065 | -0.019008 | -0.012236 | -0.011615 | -0.082397 | 61.322 | -61.6241 | 61.4502 | -61.2808 | -61.6882 | -61.6882 | -0.054932 | 61.322 | -61.5646 | 61.4639 | -61.4594 | -61.4914 | -61.5189 | -0.096131 | -0.096131 | 0.032043 | 0.24719 | -0.16022 | -0.16022 | -0.064086 | -0.064086 | -0.036621 | -0.096131 | 0.045776 | 0.068664 | 0.009155 | 0.036621 | 0.045776 | 0.073242 | 0.34332 | 123.0743 | 0.10529 | 123.0286 | 122.9462 | 122.8867 | 122.85 | 122.85 | -123.0423 | -122.9828 | 122.9782 | 122.9919 | 61.4456 | 61.4731
165.1562 | 123.1659 | -61.5555 | 61.3907 | 0.02121 | -0.0059344 | 0.0098565 | 0.06596 | -0.014849 | -0.029463 | -0.022605 | 0.0055542 | -0.0093139 | 0.06483 | 0.050919 | -0.019435 | -0.012877 | -0.016101 | -0.073242 | 61.3174 | -61.6379 | 61.4548 | -61.2534 | -61.6974 | -61.7111 | 0.018311 | 61.2808 | -61.5646 | 61.4731 | -61.4777 | -61.5051 | -61.4914 | -0.082397 | -0.073242 | 0.064087 | 0.30212 | -0.15564 | -0.14191 | -0.073243 | -0.05951 | -0.009155 | -0.10986 | 0.082397 | 0.07782 | 0.064087 | 0.050354 | 0.073242 | 0.059509 | 0.38452 | 123.0927 | 0.086975 | 123.0377 | 122.9553 | 122.8455 | 122.8729 | 122.8363 | -123.0286 | -122.9553 | 123.0103 | 123.0286 | 61.4822 | 61.5738
166.9375 | 123.23 | -61.5051 | 61.4227 | -0.0016786 | -0.0076434 | 0.0092157 | 0.067669 | -0.019762 | -0.032454 | -0.02346 | -0.00054937 | -0.010382 | 0.061199 | 0.050706 | -0.021144 | -0.012664 | -0.016528 | -0.013733 | 61.3724 | -61.5326 | 61.5372 | -61.1572 | -61.5875 | -61.615 | 0.10071 | 61.3174 | -61.5189 | 61.5601 | -61.3495 | -61.3632 | -61.409 | -0.027466 | -0.050354 | 0.11444 | 0.3479 | -0.10986 | -0.082397 | -0.082397 | -0.054931 | -0.013733 | -0.10528 | 0.13733 | 0.15564 | 0.09613 | 0.14191 | 0.10986 | 0.15564 | 0.37537 | 123.0698 | 0.16937 | 123.0789 | 122.905 | 122.8363 | 122.8775 | 122.8226 | -122.9553 | -122.9416 | 123.0423 | 123.0652 | 61.4914 | 61.6058
168.8281 | 123.0972 | -61.5234 | 61.4731 | 0.036468 | -0.0076434 | 0.0090021 | 0.066174 | -0.01848 | -0.030531 | -0.024101 | 0.0025024 | -0.0058959 | 0.062481 | 0.04387 | -0.02499 | -0.014586 | -0.018664 | -0.032043 | 61.3953 | -61.6333 | 61.4273 | -61.3129 | -61.6974 | -61.7065 | -0.050354 | 61.4136 | -61.5509 | 61.4365 | -61.5051 | -61.528 | -61.5005 | -0.10986 | -0.077819 | -0.045776 | 0.21057 | -0.18311 | -0.17395 | -0.073242 | -0.064087 | -0.027466 | -0.059509 | -0.036621 | 0.01831 | 0.022888 | -0.004578 | 0.050354 | 0.022888 | 0.32044 | 123.0606 | 0.045776 | 122.9874 | 123.0286 | 122.9645 | 122.9187 | 122.937 | -123.1064 | -123.024 | 122.9507 | 122.9599 | 61.4914 | 61.4731
170.8281 | 123.1659 | -61.4914 | 61.4594 | 0.01358 | -0.0091388 | 0.0079339 | 0.063611 | -0.01784 | -0.02989 | -0.024955 | 0.0025024 | -0.010169 | 0.061412 | 0.047501 | -0.023067 | -0.014586 | -0.013537 | 0.013733 | 61.3678 | -61.5646 | 61.528 | -61.1893 | -61.5875 | -61.615 | 0.064087 | 61.3449 | -61.5005 | 61.496 | -61.3861 | -61.4227 | -61.4456 | -0.073242 | -0.091553 | 0.068664 | 0.30212 | -0.1236 | -0.09613 | -0.050354 | -0.022888 | -0.009155 | -0.11444 | 0.036621 | 0.10529 | 0.045776 | 0.068665 | 0.054931 | 0.07782 | 0.37537 | 123.0927 | 0.11444 | 122.9965 | 122.9324 | 122.8455 | 122.8592 | 122.8363 | -123.024 | -122.9599 | 123.0194 | 122.9874 | 61.5051 | 61.5555
173.0156 | 123.1796 | -61.5326 | 61.409 | 0.01358 | -0.011702 | 0.0068659 | 0.064251 | -0.018908 | -0.030317 | -0.02111 | -0.00054937 | -0.0093139 | 0.061626 | 0.051987 | -0.021358 | -0.01245 | -0.012896 | -0.091553 | 61.3312 | -61.6104 | 61.4365 | -61.2808 | -61.6882 | -61.7065 | -0.041199 | 61.3174 | -61.528 | 61.4731 | -61.441 | -61.4594 | -61.4731 | -0.07782 | -0.07782 | 0.027465 | 0.25177 | -0.17395 | -0.15564 | -0.09613 | -0.077819 | 0.004578 | -0.091553 | 0.064086 | 0.091553 | 0.05951 | 0.073242 | 0.054932 | 0.068664 | 0.32959 | 123.0469 | 0.086975 | 123.0011 | 122.9416 | 122.8455 | 122.8638 | 122.85 | -123.0194 | -122.937 | 122.9691 | 123.0057 | 61.441 | 61.4914
174.7656 | 123.1384 | -61.5509 | 61.4319 | 0.01358 | -0.0080706 | 0.0083613 | 0.067456 | -0.018694 | -0.030958 | -0.024955 | 0.0055542 | -0.0039733 | 0.061199 | 0.031266 | -0.021999 | -0.013518 | -0.016742 | -0.022888 | 61.377 | -61.6058 | 61.441 | -61.2854 | -61.702 | -61.6974 | 0 | 61.322 | -61.5555 | 61.4548 | -61.4731 | -61.5143 | -61.4914 | -0.054932 | -0.054932 | 0.009155 | 0.2655 | -0.14648 | -0.15106 | -0.091553 | -0.09613 | -0.004578 | -0.10986 | 0.022888 | 0.07782 | 0.059509 | 0.036621 | 0.064087 | 0.041199 | 0.32043 | 123.0469 | 0.082398 | 123.0103 | 122.9828 | 122.8775 | 122.9279 | 122.8729 | -123.0377 | -122.9874 | 122.9919 | 123.0057 | 61.528 | 61.5509
176.7656 | 123.143 | -61.5417 | 61.3724 | 0.02121 | -0.0091388 | 0.0081477 | 0.064465 | -0.01784 | -0.028822 | -0.023033 | 0.0025024 | -0.010382 | 0.061199 | 0.052201 | -0.017513 | -0.013518 | -0.016101 | -0.09613 | 61.3174 | -61.5829 | 61.4502 | -61.2808 | -61.6928 | -61.7157 | -0.054932 | 61.2991 | -61.5372 | 61.4594 | -61.4777 | -61.4914 | -61.4868 | -0.041199 | -0.054931 | 0.07782 | 0.26093 | -0.17395 | -0.15106 | -0.13275 | -0.10986 | 0.004578 | -0.073242 | 0.086976 | 0.064087 | 0.054932 | 0.050354 | 0.050354 | 0.045776 | 0.30212 | 123.0331 | 0.059509 | 122.9965 | 122.9004 | 122.8363 | 122.8592 | 122.8409 | -122.9553 | -122.9095 | 122.9919 | 123.0011 | 61.4456 | 61.4868
179.6094 | 123.0789 | -61.5738 | 61.3815 | -0.0016786 | -0.0065754 | 0.010925 | 0.06532 | -0.019549 | -0.030745 | -0.022392 | 0.0025024 | -0.0052551 | 0.063762 | 0.04387 | -0.020503 | -0.013091 | -0.018023 | -0.041199 | 61.3632 | -61.6013 | 61.409 | -61.2946 | -61.7249 | -61.7477 | -0.041199 | 61.3174 | -61.5829 | 61.409 | -61.5372 | -61.6058 | -61.5646 | -0.027465 | -0.018311 | 0.027466 | 0.27924 | -0.17395 | -0.15106 | -0.14649 | -0.1236 | -0.009155 | -0.064087 | 0.027466 | 0.036622 | 0.009156 | -0.032043 | 0.018311 | -0.022888 | 0.3067 | 123.0103 | 0.045777 | 122.9919 | 122.9645 | 122.9004 | 122.937 | 122.8912 | -122.9828 | -122.9645 | 122.9828 | 122.9828 | 61.5326 | 61.5326
181.3125 | 123.1201 | -61.5372 | 61.4227 | 0.044098 | -0.0070026 | 0.0081477 | 0.06596 | -0.018694 | -0.029463 | -0.021965 | 0.008606 | -0.0071777 | 0.062481 | 0.040024 | -0.021999 | -0.012236 | -0.018237 | -0.018311 | 61.377 | -61.6013 | 61.4319 | -61.2534 | -61.6791 | -61.7157 | 0 | 61.3724 | -61.5555 | 61.4594 | -61.4685 | -61.5097 | -61.496 | -0.064087 | -0.045776 | 0.009156 | 0.28381 | -0.17853 | -0.14191 | -0.11444 | -0.07782 | -0.018311 | -0.050354 | 0.036622 | 0.068664 | 0.041198 | 0.027465 | 0.059509 | 0.045776 | 0.3479 | 123.0331 | 0.086975 | 123.0148 | 122.9782 | 122.9279 | 122.9141 | 122.9095 | -123.024 | -122.9782 | 122.9691 | 122.9965 | 61.5189 | 61.5372
183 | 123.0606 | -61.5005 | 61.4502 | 0.0059509 | -0.011489 | 0.0077203 | 0.064038 | -0.020403 | -0.030104 | -0.022605 | 0.0025024 | -0.0086731 | 0.06419 | 0.046219 | -0.024776 | -0.011595 | -0.016101 | -0.07782 | 61.4044 | -61.5692 | 61.4182 | -61.2991 | -61.6745 | -61.6974 | -0.054932 | 61.3724 | -61.5005 | 61.409 | -61.4777 | -61.5097 | -61.5097 | -0.068665 | -0.045776 | -0.032043 | 0.20142 | -0.19684 | -0.17395 | -0.12817 | -0.10529 | 0 | -0.07782 | -0.041198 | 0.022888 | -0.009156 | -0.009156 | -0.009156 | -0.009156 | 0.27008 | 122.9874 | 0.022888 | 122.9095 | 122.9736 | 122.8729 | 122.905 | 122.8729 | -123.0194 | -122.9507 | 122.9187 | 122.9095 | 61.4227 | 61.4456
184.7188 | 123.1155 | -61.528 | 61.4365 | 0.01358 | -0.0087116 | 0.0075067 | 0.064038 | -0.01848 | -0.02989 | -0.021324 | 0.0055542 | -0.0076049 | 0.063762 | 0.046006 | -0.020503 | -0.013732 | -0.018237 | -0.032043 | 61.3586 | -61.6013 | 61.4365 | -61.2717 | -61.6653 | -61.6882 | 0 | 61.3312 | -61.5417 | 61.4456 | -61.4639 | -61.5005 | -61.4822 | -0.073242 | -0.077819 | 0 | 0.25635 | -0.16022 | -0.13733 | -0.086975 | -0.064087 | -0.013733 | -0.10529 | 0.009156 | 0.064087 | 0.045776 | 0.027466 | 0.059509 | 0.041199 | 0.32959 | 123.0377 | 0.07782 | 122.9874 | 122.9599 | 122.8729 | 122.8867 | 122.8592 | -123.0377 | -122.9782 | 122.9645 | 122.9736 | 61.496 | 61.528
186.4062 | 123.0789 | -61.5143 | 61.4456 | 0.036468 | -0.007857 | 0.0090021 | 0.064465 | -0.018267 | -0.033735 | -0.025596 | 0.011658 | -0.0080321 | 0.063335 | 0.044083 | -0.020717 | -0.015013 | -0.014178 | -0.041199 | 61.4319 | -61.6058 | 61.3998 | -61.2946 | -61.6882 | -61.7157 | -0.050354 | 61.3724 | -61.5463 | 61.4319 | -61.4822 | -61.5051 | -61.4914 | -0.091553 | -0.013733 | -0.045777 | 0.21973 | -0.20142 | -0.17395 | -0.10986 | -0.082397 | -0.032044 | -0.073243 | -0.013733 | 0.032043 | 0.022888 | 0.009155 | 0.054932 | 0.041199 | 0.31128 | 123.0057 | 0.064087 | 122.9782 | 123.0377 | 122.9187 | 122.9462 | 122.8867 | -123.0515 | -122.9919 | 122.9141 | 122.9462 | 61.4731 | 61.4639
188.0938 | 123.1979 | -61.4685 | 61.4136 | 0.0059509 | -0.013198 | 0.0083613 | 0.063397 | -0.026171 | -0.029036 | -0.021965 | 0.0025024 | -0.0099549 | 0.062694 | 0.04686 | -0.020931 | -0.011809 | -0.016955 | -0.027466 | 61.3266 | -61.5417 | 61.4868 | -61.1801 | -61.5875 | -61.6104 | 0.07782 | 61.2991 | -61.4868 | 61.5417 | -61.3449 | -61.3953 | -61.4136 | -0.073242 | -0.086975 | 0.073242 | 0.28839 | -0.14191 | -0.11902 | -0.068665 | -0.045776 | -0.01831 | -0.11444 | 0.12817 | 0.1236 | 0.054932 | 0.073242 | 0.073242 | 0.091552 | 0.36163 | 123.0286 | 0.14191 | 123.0286 | 122.8683 | 122.7859 | 122.7951 | 122.7676 | -122.9553 | -122.9004 | 122.9553 | 123.0103 | 61.441 | 61.5463
189.7812 | 123.0606 | -61.5051 | 61.4731 | -0.0093076 | -0.007857 | 0.0090021 | 0.064038 | -0.023394 | -0.028395 | -0.026237 | -0.003601 | -0.0078185 | 0.06483 | 0.040665 | -0.023281 | -0.012664 | -0.01781 | -0.027466 | 61.4182 | -61.5555 | 61.4273 | -61.2625 | -61.6699 | -61.6928 | -0.032043 | 61.3861 | -61.5143 | 61.4319 | -61.4594 | -61.4822 | -61.5051 | -0.050354 | -0.054931 | -0.045776 | 0.24262 | -0.18768 | -0.16479 | -0.13733 | -0.11444 | -0.009155 | -0.086975 | -0.041198 | 0.045776 | 0 | 0.022888 | 0.009155 | 0.032043 | 0.29297 | 122.9828 | 0.054931 | 122.9462 | 122.9736 | 122.9004 | 122.9233 | 122.8912 | -123.0286 | -122.9874 | 122.9324 | 122.937 | 61.4777 | 61.4731
191.4531 | 123.1293 | -61.5234 | 61.3998 | 0.01358 | -0.0093524 | 0.0055841 | 0.065106 | -0.014849 | -0.030317 | -0.022819 | 0.0025024 | -0.0076049 | 0.063762 | 0.043229 | -0.021999 | -0.012023 | -0.014605 | -0.022888 | 61.3861 | -61.5967 | 61.4227 | -61.2579 | -61.6791 | -61.7249 | 0.004578 | 61.3358 | -61.5417 | 61.441 | -61.4639 | -61.4914 | -61.4777 | -0.073243 | -0.013733 | 0.022888 | 0.2655 | -0.20142 | -0.15564 | -0.12817 | -0.082397 | -0.018311 | -0.064087 | 0.041199 | 0.059509 | 0.045776 | 0.032043 | 0.064087 | 0.050354 | 0.33874 | 123.0194 | 0.07782 | 122.9828 | 122.9828 | 122.8775 | 122.9095 | 122.8592 | -122.9965 | -122.9416 | 122.9462 | 122.9645 | 61.5005 | 61.528
193.1406 | 123.0743 | -61.5005 | 61.4731 | 0.028839 | -0.010634 | 0.0090021 | 0.065747 | -0.019762 | -0.028395 | -0.02346 | 0.008606 | -0.0073913 | 0.065471 | 0.04451 | -0.022853 | -0.013091 | -0.016528 | -0.050354 | 61.4136 | -61.6013 | 61.3998 | -61.29 | -61.702 | -61.6974 | -0.041199 | 61.3724 | -61.5234 | 61.4227 | -61.4914 | -61.5097 | -61.4914 | -0.10071 | -0.059509 | -0.073242 | 0.21057 | -0.19684 | -0.20142 | -0.096131 | -0.10071 | -0.022888 | -0.10071 | -0.050354 | 0.009155 | 0.009155 | -0.009156 | 0.032043 | 0.013732 | 0.31128 | 123.0011 | 0.032043 | 122.9462 | 123.0148 | 122.8958 | 122.9141 | 122.8729 | -123.0743 | -122.9965 | 122.9004 | 122.9233 | 61.4502 | 61.4594
194.875 | 123.1567 | -61.4868 | 61.4365 | -0.0016786 | -0.0089252 | 0.0092157 | 0.062543 | -0.019976 | -0.02754 | -0.023033 | -0.00054937 | -0.0080321 | 0.061199 | 0.050278 | -0.020503 | -0.01245 | -0.015246 | 0.018311 | 61.3358 | -61.5463 | 61.5372 | -61.1572 | -61.5646 | -61.5921 | 0.07782 | 61.3449 | -61.5005 | 61.528 | -61.3358 | -61.3861 | -61.4044 | -0.05951 | -0.10071 | 0.10071 | 0.32959 | -0.10529 | -0.07782 | -0.045776 | -0.01831 | -0.013733 | -0.091552 | 0.091553 | 0.15106 | 0.082397 | 0.10071 | 0.09613 | 0.11444 | 0.3891 | 123.0835 | 0.16479 | 123.0286 | 122.8821 | 122.8455 | 122.8226 | 122.8317 | -122.9828 | -122.937 | 123.024 | 123.0148 | 61.5051 | 61.5646
196.5625 | 123.1384 | -61.5143 | 61.4044 | 0.02121 | -0.0093524 | 0.0079339 | 0.06532 | -0.018694 | -0.029676 | -0.022819 | 0.0055542 | -0.0080321 | 0.061412 | 0.050919 | -0.018581 | -0.01245 | -0.017169 | -0.082397 | 61.2991 | -61.5967 | 61.4182 | -61.2625 | -61.6882 | -61.6882 | -0.036621 | 61.2762 | -61.5372 | 61.4685 | -61.4502 | -61.4777 | -61.496 | -0.082398 | -0.10529 | 0.013733 | 0.25177 | -0.17395 | -0.17395 | -0.091552 | -0.091552 | -0.022888 | -0.12817 | 0.064087 | 0.064087 | 0.01831 | 0.036621 | 0.041198 | 0.059509 | 0.33417 | 123.0148 | 0.086975 | 123.0057 | 122.8958 | 122.8134 | 122.8134 | 122.7905 | -123.0011 | -122.9416 | 122.9324 | 122.9828 | 61.4319 | 61.4777
198.2344 | 123.0606 | -61.496 | 61.4639 | 0.01358 | -0.0089252 | 0.0087885 | 0.066388 | -0.020189 | -0.031385 | -0.024314 | 0.0025024 | -0.0088867 | 0.062481 | 0.044938 | -0.023921 | -0.012664 | -0.017596 | -0.050354 | 61.377 | -61.5326 | 61.4136 | -61.2762 | -61.6745 | -61.6974 | -0.032043 | 61.3861 | -61.5005 | 61.4227 | -61.4594 | -61.4868 | -61.496 | -0.036621 | -0.086975 | -0.050354 | 0.21973 | -0.20142 | -0.17853 | -0.16479 | -0.14191 | -0.004577 | -0.07782 | -0.041199 | 0.036621 | 0 | 0.009156 | 0.004577 | 0.013733 | 0.25635 | 122.9462 | 0.041198 | 122.9233 | 122.9095 | 122.8867 | 122.8729 | 122.8821 | -122.9965 | -122.9645 | 122.9095 | 122.9187 | 61.4456 | 61.4639
199.9219 | 123.1476 | -61.5005 | 61.377 | 0.028839 | -0.0072162 | 0.0079339 | 0.066601 | -0.019335 | -0.032026 | -0.024528 | 0.0055542 | -0.0097411 | 0.062908 | 0.051774 | -0.018367 | -0.010741 | -0.015674 | -0.086975 | 61.3174 | -61.6013 | 61.4227 | -61.2625 | -61.6745 | -61.6791 | -0.036621 | 61.29 | -61.5326 | 61.4502 | -61.4639 | -61.4777 | -61.4868 | -0.10071 | -0.059509 | 0.045776 | 0.23804 | -0.17853 | -0.17395 | -0.07782 | -0.073243 | -0.032044 | -0.086975 | 0.073242 | 0.036621 | 0.013733 | 0.022888 | 0.045777 | 0.054932 | 0.33874 | 123.024 | 0.068665 | 122.9828 | 122.9187 | 122.8226 | 122.818 | 122.7905 | -122.9782 | -122.9095 | 122.9233 | 122.9507 | 61.4136 | 61.4639
201.625 | 123.1293 | -61.4594 | 61.4319 | 0.0059509 | -0.007857 | 0.0098565 | 0.063183 | -0.019121 | -0.032454 | -0.024101 | -0.00054937 | -0.011237 | 0.062053 | 0.043229 | -0.020717 | -0.011595 | -0.016528 | 0.022888 | 61.3266 | -61.5509 | 61.5189 | -61.171 | -61.5738 | -61.6013 | 0.073242 | 61.322 | -61.4822 | 61.5189 | -61.3815 | -61.3907 | -61.4227 | -0.091552 | -0.10529 | 0.086975 | 0.28839 | -0.14191 | -0.11444 | -0.050354 | -0.022889 | -0.022888 | -0.10986 | 0.086975 | 0.07782 | 0.036622 | 0.068665 | 0.05951 | 0.091553 | 0.37994 | 123.0698 | 0.10071 | 123.0011 | 122.8775 | 122.8043 | 122.7859 | 122.7814 | -122.9828 | -122.9141 | 122.9782 | 122.9782 | 61.4822 | 61.5326
203.3281 | 123.0286 | -61.5463 | 61.3953 | 0.01358 | -0.0076434 | 0.0094293 | 0.06596 | -0.018694 | -0.028822 | -0.026023 | -0.00054937 | -0.0061095 | 0.060344 | 0.048997 | -0.020717 | -0.012877 | -0.014392 | -0.10986 | 61.3266 | -61.6058 | 61.3403 | -61.3678 | -61.7889 | -61.8027 | -0.14191 | 61.2991 | -61.5692 | 61.3541 | -61.5646 | -61.5967 | -61.5555 | -0.059509 | -0.068665 | -0.054932 | 0.17853 | -0.25635 | -0.24261 | -0.19684 | -0.1831 | -0.022888 | -0.096131 | -0.041199 | -0.01831 | -0.009155 | -0.050354 | 0.013733 | -0.027466 | 0.23804 | 122.9462 | 0.004578 | 122.9233 | 122.9324 | 122.8683 | 122.8729 | 122.8455 | -123.0011 | -122.9645 | 122.8867 | 122.9004 | 61.4365 | 61.4044
205.0156 | 123.143 | -61.5234 | 61.3266 | 0.028839 | -0.0087116 | 0.0085749 | 0.06596 | -0.018267 | -0.028822 | -0.023246 | 0.008606 | -0.0073913 | 0.065471 | 0.047074 | -0.018794 | -0.010527 | -0.017169 | -0.054932 | 61.2762 | -61.6104 | 61.4456 | -61.2076 | -61.6562 | -61.6653 | 0.018311 | 61.2534 | -61.5692 | 61.4548 | -61.4365 | -61.4777 | -61.4639 | -0.086976 | -0.050354 | 0.11902 | 0.31586 | -0.14191 | -0.13275 | -0.054931 | -0.045776 | -0.045777 | -0.073242 | 0.12817 | 0.086975 | 0.059509 | 0.045776 | 0.10529 | 0.091553 | 0.40283 | 123.056 | 0.13275 | 123.024 | 122.8867 | 122.8226 | 122.7997 | 122.7768 | -122.937 | -122.8958 | 122.9691 | 122.9782 | 61.4685 | 61.5417
206.7188 | 123.1705 | -61.5326 | 61.3632 | 0.01358 | -0.0091388 | 0.0090021 | 0.066174 | -0.021258 | -0.02989 | -0.025596 | 0.0025024 | -0.0097411 | 0.06419 | 0.050706 | -0.017513 | -0.012236 | -0.016742 | -0.09613 | 61.2808 | -61.6379 | 61.3953 | -61.2579 | -61.7203 | -61.7477 | -0.018311 | 61.2625 | -61.5646 | 61.4548 | -61.4319 | -61.496 | -61.4502 | -0.10529 | -0.082397 | 0.032044 | 0.27466 | -0.21515 | -0.18768 | -0.10986 | -0.082398 | -0.032043 | -0.10071 | 0.091553 | 0.10071 | 0.082398 | 0.036621 | 0.11444 | 0.068664 | 0.37994 | 123.0331 | 0.13275 | 123.0194 | 122.9187 | 122.8271 | 122.8134 | 122.7951 | -123.0011 | -122.9279 | 122.9279 | 122.9874 | 61.4365 | 61.5143
208.4688 | 123.056 | -61.5784 | 61.3907 | 0.01358 | -0.0093524 | 0.0085749 | 0.066388 | -0.019335 | -0.029036 | -0.026237 | 0.0025024 | -0.0071777 | 0.061412 | 0.048783 | -0.020076 | -0.0094592 | -0.013965 | -0.13733 | 61.3358 | -61.615 | 61.2991 | -61.4044 | -61.8118 | -61.8027 | -0.14648 | 61.2808 | -61.5738 | 61.3495 | -61.5646 | -61.6104 | -61.5555 | -0.036621 | -0.054932 | -0.091553 | 0.17395 | -0.2243 | -0.23346 | -0.18768 | -0.19684 | 0.004577 | -0.10986 | -0.041199 | 0.013733 | 0.022888 | -0.032044 | 0.018311 | -0.036621 | 0.21057 | 122.9141 | 0.009156 | 122.9233 | 122.9507 | 122.8546 | 122.9141 | 122.8592 | -123.0057 | -122.9645 | 122.8775 | 122.9279 | 61.441 | 61.4319
210.1719 | 123.056 | -61.5875 | 61.3632 | 0.01358 | -0.0063616 | 0.0087885 | 0.066174 | -0.017626 | -0.028181 | -0.021324 | 0.0025024 | -0.0082459 | 0.063121 | 0.043656 | -0.02029 | -0.011809 | -0.011401 | -0.14191 | 61.3449 | -61.6241 | 61.3037 | -61.3998 | -61.8027 | -61.8027 | -0.16022 | 61.3083 | -61.5875 | 61.3495 | -61.5692 | -61.6013 | -61.5326 | -0.036622 | -0.01831 | -0.059509 | 0.18768 | -0.21515 | -0.21515 | -0.17853 | -0.17853 | 0 | -0.054931 | -0.013733 | 0.01831 | 0.054931 | -0.013733 | 0.054931 | -0.013733 | 0.22431 | 122.9279 | 0.01831 | 122.937 | 122.9691 | 122.8958 | 122.9324 | 122.8958 | -122.9874 | -122.9507 | 122.8912 | 122.937 | 61.4456 | 61.4273
211.9062 | 123.0881 | -61.5005 | 61.409 | 0.028839 | -0.0070026 | 0.0081477 | 0.06596 | -0.016771 | -0.031813 | -0.022605 | 0.008606 | -0.0067505 | 0.060772 | 0.043015 | -0.022212 | -0.011595 | -0.015674 | -0.027466 | 61.3495 | -61.6013 | 61.4182 | -61.2396 | -61.6745 | -61.6882 | 0.004578 | 61.3083 | -61.5692 | 61.4319 | -61.441 | -61.4914 | -61.4777 | -0.10071 | -0.05951 | 0.009155 | 0.26093 | -0.18768 | -0.17395 | -0.086975 | -0.073243 | -0.068665 | -0.10071 | 0.022888 | 0.059509 | 0.022888 | 0.009155 | 0.091553 | 0.07782 | 0.36163 | 123.0194 | 0.12817 | 123.0011 | 122.9507 | 122.8775 | 122.85 | 122.8088 | -123.0103 | -122.9782 | 122.9187 | 122.9324 | 61.4731 | 61.5051
213.5781 | 123.1522 | -61.4731 | 61.3907 | 0.0059509 | -0.010207 | 0.0090021 | 0.064679 | -0.021685 | -0.031172 | -0.023887 | 0.0025024 | -0.0093139 | 0.06419 | 0.055832 | -0.019222 | -0.012236 | -0.015887 | -0.064087 | 61.322 | -61.5509 | 61.441 | -61.2122 | -61.6379 | -61.647 | 0.018311 | 61.2625 | -61.5097 | 61.4914 | -61.3724 | -61.3861 | -61.4044 | -0.07782 | -0.068665 | 0.050354 | 0.26093 | -0.17395 | -0.16479 | -0.096131 | -0.086975 | -0.036622 | -0.12817 | 0.10071 | 0.10071 | 0.068664 | 0.086975 | 0.10529 | 0.1236 | 0.33874 | 122.9919 | 0.13733 | 123.0011 | 122.8729 | 122.7722 | 122.7951 | 122.7356 | -122.9416 | -122.9004 | 122.9141 | 122.9645 | 61.409 | 61.4914
215.2812 | 123.0835 | -61.5051 | 61.4319 | 0.028839 | -0.006789 | 0.0085749 | 0.063824 | -0.019549 | -0.029463 | -0.026023 | 0.008606 | -0.0084595 | 0.06419 | 0.03682 | -0.023494 | -0.013304 | -0.017169 | -0.018311 | 61.3724 | -61.5829 | 61.4044 | -61.2717 | -61.6562 | -61.6745 | -0.032043 | 61.3358 | -61.5326 | 61.4319 | -61.4502 | -61.4822 | -61.4685 | -0.07782 | -0.05951 | -0.027466 | 0.23346 | -0.16937 | -0.15106 | -0.091553 | -0.073242 | -0.027466 | -0.096131 | 0 | 0.054932 | 0.036621 | 0.022888 | 0.064087 | 0.050354 | 0.31128 | 122.9874 | 0.082398 | 122.9645 | 122.9553 | 122.8683 | 122.8775 | 122.8409 | -123.0148 | -122.9645 | 122.9095 | 122.937 | 61.4868 | 61.4731
217.0156 | 123.0515 | -61.5097 | 61.4502 | -0.0093076 | -0.009566 | 0.010498 | 0.064038 | -0.01848 | -0.030317 | -0.022605 | 0.011658 | -0.0071777 | 0.064617 | 0.043656 | -0.023281 | -0.012877 | -0.015033 | -0.054932 | 61.4136 | -61.528 | 61.3907 | -61.2717 | -61.6562 | -61.6837 | -0.041199 | 61.3678 | -61.528 | 61.3953 | -61.4685 | -61.5005 | -61.4914 | -0.01831 | -0.036621 | -0.059509 | 0.23804 | -0.17395 | -0.14648 | -0.15564 | -0.12817 | -0.01831 | -0.082397 | -0.054931 | 0.041199 | 0.018311 | 0.009156 | 0.036621 | 0.027466 | 0.25635 | 122.9187 | 0.059509 | 122.9233 | 122.9416 | 122.8958 | 122.9233 | 122.8775 | -122.9782 | -122.9782 | 122.9004 | 122.905 | 61.4548 | 61.4685
218.7031 | 123.1659 | -61.5143 | 61.3037 | 0.0059509 | -0.0087116 | 0.0094293 | 0.06596 | -0.018694 | -0.027754 | -0.025383 | 0.0055542 | -0.0078185 | 0.064617 | 0.050492 | -0.015804 | -0.011809 | -0.014605 | -0.059509 | 61.29 | -61.5829 | 61.4227 | -61.2259 | -61.6745 | -61.6974 | -0.018311 | 61.2259 | -61.5555 | 61.4685 | -61.4273 | -61.4594 | -61.441 | -0.068665 | -0.013733 | 0.11902 | 0.28839 | -0.18311 | -0.16022 | -0.11444 | -0.091553 | -0.041199 | -0.07782 | 0.16479 | 0.086975 | 0.073242 | 0.054931 | 0.11444 | 0.09613 | 0.35706 | 123.0057 | 0.12817 | 123.024 | 122.8729 | 122.7814 | 122.8043 | 122.7402 | -122.8867 | -122.8592 | 122.937 | 122.9828 | 61.4548 | 61.496
220.4062 | 123.0743 | -61.5509 | 61.3449 | 0.0059509 | -0.0074298 | 0.0090021 | 0.066174 | -0.019762 | -0.029463 | -0.023246 | -0.00054937 | -0.0065369 | 0.060558 | 0.043015 | -0.018581 | -0.011595 | -0.012256 | -0.15106 | 61.29 | -61.6241 | 61.3129 | -61.3678 | -61.7798 | -61.7661 | -0.11444 | 61.2717 | -61.5738 | 61.3632 | -61.5463 | -61.5601 | -61.5326 | -0.073243 | -0.054932 | -0.032044 | 0.1831 | -0.21515 | -0.22888 | -0.14191 | -0.15564 | -0.022889 | -0.073243 | 0.01831 | 0.004577 | 0.01831 | -0.009156 | 0.041199 | 0.013733 | 0.25635 | 122.937 | 0.027466 | 122.937 | 122.9141 | 122.8455 | 122.8409 | 122.8226 | -122.9691 | -122.9187 | 122.8638 | 122.9141 | 61.3998 | 61.4365
222.0938 | 123.1522 | -61.4685 | 61.4136 | 0.01358 | -0.007857 | 0.0081477 | 0.063611 | -0.01848 | -0.031172 | -0.023674 | -0.003601 | -0.0076049 | 0.062694 | 0.044297 | -0.021144 | -0.012236 | -0.014178 | 0.018311 | 61.3174 | -61.5097 | 61.528 | -61.1206 | -61.5646 | -61.6013 | 0.11902 | 61.2762 | -61.4594 | 61.5143 | -61.3266 | -61.3678 | -61.3815 | -0.041199 | -0.09613 | 0.11444 | 0.3479 | -0.13275 | -0.09613 | -0.091552 | -0.054931 | 0.009155 | -0.13733 | 0.10071 | 0.14191 | 0.086975 | 0.10071 | 0.07782 | 0.091553 | 0.3891 | 123.0377 | 0.13275 | 122.9736 | 122.8271 | 122.7356 | 122.7859 | 122.7448 | -122.9233 | -122.8729 | 122.9965 | 122.9828 | 61.4868 | 61.5875
223.7969 | 123.0515 | -61.5143 | 61.3953 | 0.01358 | -0.0057208 | 0.0085749 | 0.06532 | -0.022539 | -0.030317 | -0.022178 | 0.0025024 | -0.0071777 | 0.063335 | 0.043015 | -0.019435 | -0.013091 | -0.02016 | -0.041199 | 61.3358 | -61.5738 | 61.3998 | -61.2625 | -61.6974 | -61.702 | -0.022888 | 61.3174 | -61.5234 | 61.409 | -61.4731 | -61.5234 | -61.5097 | -0.05951 | -0.05951 | 0.004577 | 0.25177 | -0.18768 | -0.18311 | -0.12817 | -0.1236 | -0.009155 | -0.07782 | 0.013733 | 0.041199 | 0.004577 | -0.009155 | 0.013732 | 0 | 0.31128 | 122.9736 | 0.050354 | 122.9324 | 122.9095 | 122.8409 | 122.85 | 122.8317 | -122.9691 | -122.9187 | 122.9141 | 122.9233 | 61.4731 | 61.4914
225.4688 | 123.0881 | -61.4548 | 61.4319 | 0.0059509 | -0.0070026 | 0.0094293 | 0.062543 | -0.019549 | -0.030317 | -0.02346 | -0.003601 | -0.0069641 | 0.062267 | 0.05156 | -0.02264 | -0.013732 | -0.015033 | 0.013733 | 61.3312 | -61.5372 | 61.4731 | -61.1618 | -61.5601 | -61.6013 | 0.064087 | 61.3129 | -61.4777 | 61.4685 | -61.3678 | -61.4136 | -61.4182 | -0.082397 | -0.10071 | 0.041198 | 0.29297 | -0.14648 | -0.10529 | -0.064087 | -0.022889 | -0.022888 | -0.11902 | 0.036621 | 0.086975 | 0.036621 | 0.041199 | 0.059509 | 0.064087 | 0.37537 | 123.0103 | 0.10986 | 122.9462 | 122.8683 | 122.7905 | 122.7859 | 122.7676 | -122.9691 | -122.9095 | 122.9279 | 122.9233 | 61.4685 | 61.5189
227.2031 | 123.1155 | -61.4548 | 61.4044 | 0.01358 | -0.011061 | 0.0075067 | 0.063611 | -0.020189 | -0.02989 | -0.022392 | -0.00054937 | -0.010169 | 0.063762 | 0.045151 | -0.018794 | -0.011382 | -0.016528 | -0.07782 | 61.3403 | -61.5646 | 61.4044 | -61.2305 | -61.6379 | -61.6608 | -0.013733 | 61.2808 | -61.5189 | 61.4731 | -61.3907 | -61.3998 | -61.4182 | -0.10986 | -0.064087 | 0 | 0.2243 | -0.20599 | -0.1831 | -0.096131 | -0.073242 | -0.064087 | -0.1236 | 0.068664 | 0.064087 | 0.036621 | 0.054932 | 0.10071 | 0.11902 | 0.33417 | 122.9691 | 0.12817 | 122.9919 | 122.905 | 122.7997 | 122.7951 | 122.7356 | -122.9691 | -122.9233 | 122.8592 | 122.9279 | 61.377 | 61.441
228.9375 | 123.0331 | -61.5326 | 61.3724 | 0.0059509 | -0.0087116 | 0.0094293 | 0.064679 | -0.018694 | -0.028181 | -0.027305 | -0.003601 | -0.0076049 | 0.062053 | 0.03917 | -0.021358 | -0.0148 | -0.01781 | -0.1236 | 61.3403 | -61.6241 | 61.322 | -61.3861 | -61.7935 | -61.7935 | -0.17853 | 61.2854 | -61.5601 | 61.3449 | -61.5738 | -61.6058 | -61.5463 | -0.091553 | -0.032043 | -0.050354 | 0.14648 | -0.26093 | -0.26093 | -0.16937 | -0.16937 | -0.027466 | -0.086975 | -0.027465 | -0.041199 | -0.013733 | -0.073242 | 0.013733 | -0.045776 | 0.23804 | 122.9462 | -0.013733 | 122.905 | 122.9645 | 122.8455 | 122.8729 | 122.818 | -122.9965 | -122.9324 | 122.8546 | 122.8775 | 61.409 | 61.3541
230.6562 | 123.0606 | -61.5005 | 61.4182 | 0.02121 | -0.0080706 | 0.0096429 | 0.065533 | -0.019549 | -0.030745 | -0.022605 | 0.0055542 | -0.0054687 | 0.063335 | 0.045792 | -0.022853 | -0.012236 | -0.012683 | -0.027466 | 61.3815 | -61.5692 | 61.4044 | -61.2488 | -61.6425 | -61.6791 | -0.018311 | 61.3403 | -61.528 | 61.441 | -61.4502 | -61.4868 | -61.4548 | -0.068665 | -0.036621 | -0.013733 | 0.25177 | -0.17853 | -0.14191 | -0.10986 | -0.073242 | -0.027466 | -0.07782 | 0.022888 | 0.050354 | 0.045776 | 0.013733 | 0.073242 | 0.041199 | 0.32044 | 122.9736 | 0.07782 | 122.9691 | 122.9507 | 122.8683 | 122.8821 | 122.8409 | -122.9874 | -122.9462 | 122.905 | 122.9416 | 61.4731 | 61.4822
232.3438 | 123.0698 | -61.5234 | 61.4136 | 0.01358 | -0.0091388 | 0.0092157 | 0.065533 | -0.019549 | -0.030745 | -0.021965 | 0.008606 | -0.0063233 | 0.063976 | 0.040879 | -0.021572 | -0.013304 | -0.016101 | -0.041199 | 61.3953 | -61.5555 | 61.4136 | -61.2579 | -61.6333 | -61.6745 | -0.027466 | 61.3815 | -61.5005 | 61.4227 | -61.441 | -61.4731 | -61.4548 | -0.032044 | -0.01831 | 0 | 0.2655 | -0.15106 | -0.10986 | -0.11902 | -0.07782 | 0.022888 | -0.032043 | 0.009155 | 0.082397 | 0.068664 | 0.050354 | 0.045776 | 0.027466 | 0.29755 | 122.9691 | 0.059509 | 122.9233 | 122.9507 | 122.8821 | 122.9187 | 122.905 | -122.9691 | -122.9141 | 122.937 | 122.9462 | 61.4822 | 61.496
234.0312 | 123.0469 | -61.5189 | 61.4182 | 0.0059509 | -0.0097796 | 0.010498 | 0.063397 | -0.017199 | -0.030745 | -0.021324 | 0.011658 | -0.0073913 | 0.062481 | 0.046647 | -0.022212 | -0.013304 | -0.01546 | -0.054932 | 61.3678 | -61.6013 | 61.3815 | -61.2579 | -61.6196 | -61.6653 | -0.041199 | 61.3312 | -61.5097 | 61.4136 | -61.4548 | -61.4777 | -61.4548 | -0.082397 | -0.050354 | -0.036621 | 0.26092 | -0.14648 | -0.10071 | -0.064087 | -0.018311 | 0.009155 | -0.086975 | -0.004578 | 0.064087 | 0.064087 | 0.041199 | 0.054932 | 0.032044 | 0.34332 | 122.9828 | 0.054932 | 122.9233 | 122.9691 | 122.8409 | 122.8867 | 122.85 | -123.0194 | -122.9279 | 122.9004 | 122.9324 | 61.4639 | 61.4777
235.7031 | 123.111 | -61.4822 | 61.3998 | 0.01358 | -0.010634 | 0.0085749 | 0.062543 | -0.020403 | -0.030104 | -0.024742 | 0.0025024 | -0.0086731 | 0.063121 | 0.042801 | -0.020717 | -0.012023 | -0.011828 | -0.10071 | 61.3083 | -61.5555 | 61.4136 | -61.2305 | -61.6287 | -61.6653 | -0.013733 | 61.2625 | -61.496 | 61.4731 | -61.3815 | -61.3861 | -61.409 | -0.073242 | -0.091552 | 0.013733 | 0.25177 | -0.1831 | -0.14648 | -0.10986 | -0.073242 | -0.013733 | -0.13733 | 0.073242 | 0.10071 | 0.073242 | 0.096131 | 0.086975 | 0.10986 | 0.32501 | 122.9691 | 0.11444 | 122.9691 | 122.8638 | 122.7585 | 122.7905 | 122.7448 | -122.9553 | -122.8958 | 122.8958 | 122.9553 | 61.3815 | 61.4685
237.4062 | 123.1338 | -61.528 | 61.3083 | 0.028839 | -0.008498 | 0.010284 | 0.065747 | -0.019976 | -0.030104 | -0.021751 | 0.0055542 | -0.0099549 | 0.063335 | 0.047715 | -0.019435 | -0.010741 | -0.019519 | -0.059509 | 61.2671 | -61.6013 | 61.4365 | -61.1938 | -61.647 | -61.6516 | 0.018311 | 61.2259 | -61.5143 | 61.4502 | -61.4044 | -61.4365 | -61.4456 | -0.073242 | -0.041199 | 0.12817 | 0.33417 | -0.1236 | -0.11902 | -0.050354 | -0.045777 | 0.013733 | -0.082398 | 0.14191 | 0.1236 | 0.082397 | 0.091553 | 0.068664 | 0.07782 | 0.40741 | 123.0377 | 0.10986 | 122.9645 | 122.8683 | 122.7402 | 122.7951 | 122.7539 | -122.9095 | -122.8226 | 122.9645 | 122.9782 | 61.4685 | 61.5463
239.0938 | 123.1293 | -61.4868 | 61.377 | 0.01358 | -0.010207 | 0.0077203 | 0.062115 | -0.021471 | -0.030317 | -0.023674 | -0.00054937 | -0.0086731 | 0.062053 | 0.054337 | -0.020076 | -0.011809 | -0.011401 | -0.091553 | 61.322 | -61.5372 | 61.3998 | -61.2305 | -61.6379 | -61.647 | -0.013733 | 61.2808 | -61.5051 | 61.4502 | -61.377 | -61.3998 | -61.4044 | -0.050354 | -0.054932 | 0.022888 | 0.25635 | -0.16022 | -0.15106 | -0.10986 | -0.10071 | -0.018311 | -0.09613 | 0.073242 | 0.10986 | 0.082397 | 0.086975 | 0.10071 | 0.10529 | 0.3067 | 122.937 | 0.12817 | 122.9553 | 122.8592 | 122.7859 | 122.8088 | 122.7676 | -122.9141 | -122.8821 | 122.8867 | 122.937 | 61.3953 | 61.4731
240.7969 | 123.1338 | -61.5143 | 61.3403 | -0.0016786 | -0.0080706 | 0.011566 | 0.065106 | -0.019549 | -0.028395 | -0.024955 | 0.0055542 | -0.0099549 | 0.060772 | 0.05156 | -0.017513 | -0.0094592 | -0.016101 | -0.064087 | 61.2442 | -61.5829 | 61.4182 | -61.2167 | -61.6608 | -61.6974 | 0 | 61.2259 | -61.5417 | 61.4456 | -61.4182 | -61.4273 | -61.441 | -0.068665 | -0.09613 | 0.07782 | 0.29755 | -0.18311 | -0.14648 | -0.11444 | -0.07782 | -0.027466 | -0.11444 | 0.10529 | 0.09613 | 0.073242 | 0.086975 | 0.10071 | 0.11444 | 0.36621 | 123.0011 | 0.1236 | 122.9874 | 122.8271 | 122.7676 | 122.7585 | 122.7402 | -122.9233 | -122.8821 | 122.9324 | 122.9599 | 61.4502 | 61.5143
242.5 | 123.143 | -61.4456 | 61.3815 | 0.01358 | -0.0089252 | 0.0070795 | 0.065533 | -0.023394 | -0.029676 | -0.022178 | 0.0055542 | -0.010596 | 0.062481 | 0.049637 | -0.021785 | -0.010527 | -0.014819 | 0.004578 | 61.2991 | -61.5234 | 61.5189 | -61.0977 | -61.528 | -61.5692 | 0.11444 | 61.3129 | -61.4639 | 61.5143 | -61.2991 | -61.3403 | -61.3815 | -0.077819 | -0.082398 | 0.13733 | 0.3479 | -0.1236 | -0.082397 | -0.045777 | -0.004578 | -0.01831 | -0.068665 | 0.13275 | 0.14649 | 0.064087 | 0.10529 | 0.082397 | 0.1236 | 0.42572 | 123.0423 | 0.1648 | 122.9782 | 122.8226 | 122.7768 | 122.7448 | 122.7585 | -122.905 | -122.8455 | 122.9645 | 122.9599 | 61.4502 | 61.5601
244.1875 | 123.0835 | -61.5097 | 61.3678 | 0.0059509 | -0.010848 | 0.0075067 | 0.064465 | -0.021898 | -0.030317 | -0.023674 | 0.0055542 | -0.0086731 | 0.063762 | 0.04387 | -0.021572 | -0.010741 | -0.015033 | -0.091553 | 61.29 | -61.5601 | 61.409 | -61.2259 | -61.6516 | -61.6699 | -0.032043 | 61.2854 | -61.5005 | 61.4182 | -61.4365 | -61.4594 | -61.4502 | -0.050354 | -0.07782 | 0.041199 | 0.28381 | -0.16022 | -0.14191 | -0.10986 | -0.091552 | 0.009156 | -0.082398 | 0.050354 | 0.073243 | 0.05951 | 0.050354 | 0.050354 | 0.041198 | 0.33417 | 122.9691 | 0.064087 | 122.9187 | 122.85 | 122.7859 | 122.7997 | 122.7951 | -122.9279 | -122.8683 | 122.9187 | 122.9279 | 61.4182 | 61.4777
245.9219 | 123.143 | -61.5051 | 61.3174 | 0.01358 | -0.009566 | 0.0083613 | 0.064679 | -0.017199 | -0.02754 | -0.025383 | 0.0025024 | -0.0084595 | 0.062481 | 0.050278 | -0.019649 | -0.0096728 | -0.019732 | -0.068665 | 61.2762 | -61.6104 | 61.3953 | -61.2259 | -61.6562 | -61.6699 | -0.013733 | 61.2259 | -61.5097 | 61.441 | -61.3953 | -61.4594 | -61.4182 | -0.10529 | -0.041199 | 0.07782 | 0.27924 | -0.16479 | -0.15106 | -0.059509 | -0.045776 | -0.004578 | -0.091553 | 0.1236 | 0.10986 | 0.086975 | 0.045776 | 0.091553 | 0.050354 | 0.38452 | 123.0057 | 0.11444 | 122.9507 | 122.8867 | 122.7356 | 122.7814 | 122.731 | -122.9279 | -122.8271 | 122.9004 | 122.9462 | 61.4365 | 61.4914
247.6094 | 123.143 | -61.441 | 61.3861 | -0.0093076 | -0.008498 | 0.0070795 | 0.062329 | -0.02083 | -0.029463 | -0.024955 | 0.0025024 | -0.0065369 | 0.060985 | 0.043442 | -0.021144 | -0.010314 | -0.013965 | -0.009155 | 61.2946 | -61.5143 | 61.5097 | -61.1069 | -61.5189 | -61.5646 | 0.11902 | 61.2991 | -61.4456 | 61.5143 | -61.3083 | -61.3312 | -61.3678 | -0.073242 | -0.091552 | 0.1236 | 0.33417 | -0.1236 | -0.07782 | -0.050354 | -0.004578 | -0.004578 | -0.086975 | 0.12817 | 0.13275 | 0.073242 | 0.10986 | 0.07782 | 0.11444 | 0.40741 | 123.024 | 0.13733 | 122.9599 | 122.8088 | 122.7448 | 122.7356 | 122.7402 | -122.9004 | -122.8317 | 122.9507 | 122.9553 | 61.4319 | 61.5601
249.3125 | 122.9874 | -61.5372 | 61.3815 | 0.0059509 | -0.0048664 | 0.0079339 | 0.065533 | -0.016558 | -0.028608 | -0.023246 | 0.0055542 | -0.0058959 | 0.062694 | 0.043442 | -0.021358 | -0.012664 | -0.015033 | -0.10071 | 61.322 | -61.6013 | 61.3174 | -61.3403 | -61.7569 | -61.7661 | -0.15106 | 61.2946 | -61.5555 | 61.322 | -61.5417 | -61.5921 | -61.528 | -0.064087 | -0.05951 | -0.064087 | 0.19684 | -0.22888 | -0.21973 | -0.1648 | -0.15564 | -0.018311 | -0.086975 | -0.05951 | -0.004578 | 0.009155 | -0.054932 | 0.027466 | -0.036621 | 0.26093 | 122.9187 | 0.013733 | 122.8775 | 122.9233 | 122.85 | 122.8592 | 122.8317 | -122.9828 | -122.937 | 122.8546 | 122.8592 | 61.4365 | 61.3861
251.0156 | 122.9965 | -61.5189 | 61.322 | 0.0059509 | -0.0063616 | 0.0077203 | 0.066174 | -0.014849 | -0.029036 | -0.024101 | 0.0025024 | -0.0058959 | 0.061199 | 0.044938 | -0.020503 | -0.012023 | -0.019305 | -0.082397 | 61.322 | -61.5875 | 61.3449 | -61.2762 | -61.7157 | -61.7386 | -0.091553 | 61.2488 | -61.5234 | 61.3495 | -61.5097 | -61.5601 | -61.5189 | -0.068664 | 0 | 0.022889 | 0.24261 | -0.21973 | -0.19684 | -0.15106 | -0.12817 | -0.004577 | -0.073242 | 0.027466 | 0.009155 | 0 | -0.041199 | 0.004577 | -0.036622 | 0.31128 | 122.9324 | 0.013732 | 122.8729 | 122.9095 | 122.7722 | 122.8409 | 122.7676 | -122.9095 | -122.8455 | 122.8638 | 122.8683 | 61.4365 | 61.4273
252.7031 | 123.1201 | -61.4227 | 61.3998 | 0.0059509 | -0.0091388 | 0.0083613 | 0.062329 | -0.020189 | -0.029676 | -0.02346 | 0.0025024 | -0.0099549 | 0.063976 | 0.045365 | -0.022426 | -0.010955 | -0.014392 | -0.009155 | 61.322 | -61.5372 | 61.496 | -61.1069 | -61.528 | -61.5784 | 0.10986 | 61.29 | -61.441 | 61.4914 | -61.2946 | -61.3449 | -61.3632 | -0.11444 | -0.07782 | 0.096131 | 0.31586 | -0.15564 | -0.10529 | -0.041199 | 0.009155 | -0.018311 | -0.10986 | 0.091553 | 0.12817 | 0.059509 | 0.077819 | 0.07782 | 0.09613 | 0.4303 | 123.0331 | 0.14648 | 122.9324 | 122.8592 | 122.731 | 122.7447 | 122.7127 | -122.937 | -122.8409 | 122.9187 | 122.9141 | 61.4136 | 61.5326
254.4062 | 123.0698 | -61.4685 | 61.3586 | 0.02121 | -0.007857 | 0.01007 | 0.066388 | -0.018267 | -0.029036 | -0.025596 | 0.0055542 | -0.0069641 | 0.062908 | 0.057969 | -0.021358 | -0.012236 | -0.015887 | -0.082397 | 61.2946 | -61.5692 | 61.4044 | -61.2305 | -61.6608 | -61.6562 | -0.041199 | 61.2488 | -61.5143 | 61.4182 | -61.4182 | -61.441 | -61.4365 | -0.10071 | -0.064087 | 0.045776 | 0.23804 | -0.18768 | -0.19226 | -0.086975 | -0.091553 | -0.045776 | -0.10986 | 0.059509 | 0.050354 | 0.032044 | 0.027466 | 0.07782 | 0.073242 | 0.33875 | 122.9736 | 0.09613 | 122.9324 | 122.8638 | 122.7631 | 122.7631 | 122.7173 | -122.9279 | -122.8729 | 122.8729 | 122.8867 | 61.3861 | 61.4273
256.0938 | 122.9828 | -61.5646 | 61.3632 | 0.0059509 | -0.0072162 | 0.0090021 | 0.06532 | -0.020189 | -0.030317 | -0.023887 | 0.0025024 | -0.0061095 | 0.064617 | 0.042161 | -0.021572 | -0.012023 | -0.016742 | -0.10529 | 61.322 | -61.5967 | 61.3037 | -61.3632 | -61.7706 | -61.7661 | -0.13733 | 61.2808 | -61.5509 | 61.3174 | -61.5601 | -61.6013 | -61.5372 | -0.032044 | -0.041199 | -0.059509 | 0.20142 | -0.20142 | -0.20599 | -0.16937 | -0.17395 | 0.013733 | -0.082397 | -0.045776 | 0.004577 | 0.027466 | -0.036621 | 0.013733 | -0.050354 | 0.23346 | 122.9004 | -0.009156 | 122.8683 | 122.9187 | 122.8317 | 122.8867 | 122.8455 | -122.9599 | -122.9141 | 122.8683 | 122.8821 | 61.4594 | 61.4273
257.8594 | 123.0789 | -61.5051 | 61.3312 | 0.0059509 | -0.0076434 | 0.0085749 | 0.066174 | -0.015276 | -0.029676 | -0.022819 | -0.00054937 | -0.0091003 | 0.063762 | 0.045365 | -0.020076 | -0.011382 | -0.015246 | -0.14191 | 61.2534 | -61.5921 | 61.3174 | -61.3083 | -61.7477 | -61.7432 | -0.07782 | 61.2259 | -61.5417 | 61.3998 | -61.441 | -61.4914 | -61.4639 | -0.086975 | -0.07782 | -0.013733 | 0.19684 | -0.23804 | -0.24262 | -0.15106 | -0.15564 | -0.036621 | -0.10529 | 0.068664 | 0.064087 | 0.041199 | 0.013733 | 0.07782 | 0.050354 | 0.28381 | 122.9095 | 0.10071 | 122.9416 | 122.8455 | 122.7676 | 122.7585 | 122.731 | -122.9233 | -122.8729 | 122.8226 | 122.905 | 61.3632 | 61.4273
259.5469 | 123.0515 | -61.4822 | 61.3861 | 0.01358 | -0.0057208 | 0.011138 | 0.066815 | -0.021258 | -0.032667 | -0.025169 | 0.008606 | -0.0065369 | 0.065258 | 0.048356 | -0.022853 | -0.012236 | -0.016955 | -0.027466 | 61.3358 | -61.5692 | 61.3953 | -61.2305 | -61.6425 | -61.6562 | 0.013733 | 61.29 | -61.5097 | 61.4182 | -61.4273 | -61.4639 | -61.4319 | -0.086975 | -0.050354 | 0.009156 | 0.25177 | -0.17395 | -0.16022 | -0.086975 | -0.073242 | -0.027466 | -0.09613 | 0.032044 | 0.054932 | 0.050354 | 0.018311 | 0.07782 | 0.045777 | 0.33875 | 122.9645 | 0.082398 | 122.9279 | 122.905 | 122.7997 | 122.818 | 122.7722 | -122.9553 | -122.8958 | 122.8775 | 122.9004 | 61.4548 | 61.496
261.2812 | 122.9874 | -61.5372 | 61.3174 | 0.0059509 | -0.0087116 | 0.0079339 | 0.064892 | -0.018908 | -0.027113 | -0.024314 | -0.00054937 | -0.0071777 | 0.06718 | 0.053055 | -0.018581 | -0.010527 | -0.01546 | -0.16022 | 61.3129 | -61.5967 | 61.2671 | -61.3495 | -61.7706 | -61.7752 | -0.17395 | 61.2579 | -61.5417 | 61.3129 | -61.5417 | -61.5784 | -61.5234 | -0.05951 | -0.004578 | -0.050354 | 0.18768 | -0.23804 | -0.23346 | -0.17853 | -0.17395 | -0.004578 | -0.059509 | -0.004578 | -0.004578 | 0.013733 | -0.041199 | 0.018311 | -0.036621 | 0.24719 | 122.8638 | 0 | 122.8546 | 122.9095 | 122.7997 | 122.85 | 122.7951 | -122.9141 | -122.8592 | 122.8043 | 122.85 | 61.377 | 61.3632
262.9844 | 123.1247 | -61.4914 | 61.2991 | 0.0059509 | -0.0080706 | 0.0087885 | 0.062756 | -0.017412 | -0.029249 | -0.023674 | 0.0025024 | -0.0091003 | 0.063335 | 0.045579 | -0.019435 | -0.011168 | -0.016314 | -0.068665 | 61.235 | -61.5784 | 61.3953 | -61.2122 | -61.6516 | -61.6791 | -0.009155 | 61.1938 | -61.5234 | 61.4456 | -61.3998 | -61.4502 | -61.4227 | -0.086975 | -0.064087 | 0.096131 | 0.27924 | -0.18768 | -0.16022 | -0.10071 | -0.073242 | -0.032043 | -0.10528 | 0.14649 | 0.091553 | 0.068665 | 0.041199 | 0.10071 | 0.073242 | 0.36621 | 122.9736 | 0.1236 | 122.9691 | 122.8134 | 122.7173 | 122.7264 | 122.6852 | -122.8775 | -122.8226 | 122.8867 | 122.937 | 61.4227 | 61.4822
264.6875 | 123.0743 | -61.5051 | 61.3312 | 0.028839 | -0.0076434 | 0.010498 | 0.064679 | -0.021258 | -0.029249 | -0.022392 | 0.008606 | -0.0099549 | 0.063549 | 0.043015 | -0.018154 | -0.0092456 | -0.011401 | -0.068665 | 61.2717 | -61.5692 | 61.4227 | -61.1801 | -61.615 | -61.6287 | 0.032043 | 61.2213 | -61.528 | 61.4182 | -61.3998 | -61.441 | -61.4273 | -0.064087 | -0.05951 | 0.091552 | 0.32501 | -0.1236 | -0.10986 | -0.059509 | -0.045776 | -0.022888 | -0.10986 | 0.086975 | 0.10529 | 0.07782 | 0.064087 | 0.10071 | 0.086975 | 0.3891 | 122.9919 | 0.12817 | 122.9462 | 122.8409 | 122.7493 | 122.7768 | 122.7264 | -122.9004 | -122.8592 | 122.9279 | 122.9233 | 61.4365 | 61.5372
266.375 | 123.111 | -61.5005 | 61.3129 | 0.0059509 | -0.0072162 | 0.0083613 | 0.063183 | -0.015917 | -0.028608 | -0.025383 | 0.0055542 | -0.0073913 | 0.065044 | 0.048783 | -0.019222 | -0.012236 | -0.015887 | -0.068665 | 61.2488 | -61.5967 | 61.4044 | -61.2213 | -61.6516 | -61.6699 | 0.022888 | 61.203 | -61.528 | 61.441 | -61.3907 | -61.4319 | -61.4182 | -0.096131 | -0.064087 | 0.091553 | 0.27924 | -0.16937 | -0.15106 | -0.073242 | -0.054931 | -0.027466 | -0.10986 | 0.12817 | 0.10986 | 0.082397 | 0.068664 | 0.10986 | 0.09613 | 0.37537 | 123.0011 | 0.13733 | 122.9691 | 122.8455 | 122.731 | 122.7493 | 122.7036 | -122.9095 | -122.8409 | 122.905 | 122.9416 | 61.4319 | 61.5234
268.0625 | 123.0743 | -61.4594 | 61.3861 | 0.0059509 | -0.0097796 | 0.010284 | 0.060834 | -0.018267 | -0.033094 | -0.02581 | 0.0025024 | -0.0084595 | 0.063121 | 0.046647 | -0.021785 | -0.011382 | -0.015033 | -0.07782 | 61.2762 | -61.5692 | 61.377 | -61.2305 | -61.6241 | -61.6379 | -0.022888 | 61.2534 | -61.4914 | 61.441 | -61.3724 | -61.3953 | -61.4044 | -0.10986 | -0.10986 | -0.009155 | 0.22888 | -0.17853 | -0.1648 | -0.068664 | -0.054932 | -0.032043 | -0.13275 | 0.054932 | 0.086976 | 0.054932 | 0.064087 | 0.086975 | 0.09613 | 0.33875 | 122.9462 | 0.11902 | 122.9324 | 122.8455 | 122.7448 | 122.7356 | 122.7127 | -122.9553 | -122.8775 | 122.8363 | 122.9004 | 61.3815 | 61.4365
269.75 | 122.9874 | -61.4594 | 61.4273 | 0.0059509 | -0.0099932 | 0.0087885 | 0.063611 | -0.022539 | -0.03224 | -0.024742 | -0.00054937 | -0.0058959 | 0.063549 | 0.051987 | -0.024135 | -0.0148 | -0.015246 | -0.018311 | 61.3403 | -61.5143 | 61.3998 | -61.2167 | -61.6196 | -61.6287 | -0.027466 | 61.3312 | -61.4868 | 61.3861 | -61.4365 | -61.4594 | -61.4456 | -0.054931 | -0.086975 | -0.027466 | 0.24262 | -0.16937 | -0.16022 | -0.11444 | -0.10529 | -0.027465 | -0.09613 | -0.041199 | 0.022889 | 0.013733 | 0 | 0.041198 | 0.027465 | 0.29755 | 122.9141 | 0.050354 | 122.8729 | 122.8546 | 122.818 | 122.7997 | 122.7905 | -122.9416 | -122.9141 | 122.8592 | 122.8455 | 61.441 | 61.4319
271.4531 | 123.1064 | -61.5189 | 61.3129 | 0.0059509 | -0.010634 | 0.0081477 | 0.064251 | -0.024675 | -0.029463 | -0.024742 | 0.0025024 | -0.0097411 | 0.060985 | 0.047715 | -0.018794 | -0.009032 | -0.013965 | -0.068665 | 61.2213 | -61.5509 | 61.3953 | -61.203 | -61.6425 | -61.6699 | -0.004578 | 61.203 | -61.5234 | 61.4502 | -61.4182 | -61.4273 | -61.4136 | -0.032043 | -0.091553 | 0.082398 | 0.31586 | -0.15106 | -0.1236 | -0.11902 | -0.091553 | -0.004577 | -0.10986 | 0.13733 | 0.10071 | 0.10529 | 0.091553 | 0.10986 | 0.09613 | 0.3479 | 122.9462 | 0.10529 | 122.9736 | 122.7722 | 122.7264 | 122.7402 | 122.7219 | -122.8638 | -122.8363 | 122.9141 | 122.9691 | 61.4502 | 61.5143
273.1562 | 123.1064 | -61.4456 | 61.3678 | 0.01358 | -0.010848 | 0.0087885 | 0.062115 | -0.02318 | -0.031599 | -0.022178 | -0.003601 | -0.0099549 | 0.062481 | 0.044083 | -0.020717 | -0.011382 | -0.013965 | -0.009155 | 61.3037 | -61.5143 | 61.4822 | -61.0886 | -61.5051 | -61.5509 | 0.11444 | 61.29 | -61.441 | 61.496 | -61.29 | -61.3358 | -61.3449 | -0.068664 | -0.064087 | 0.11444 | 0.35706 | -0.10528 | -0.059509 | -0.036621 | 0.009155 | 0.004578 | -0.07782 | 0.12817 | 0.15564 | 0.10071 | 0.10986 | 0.09613 | 0.10529 | 0.42572 | 122.9965 | 0.15106 | 122.937 | 122.818 | 122.731 | 122.7493 | 122.7356 | -122.8821 | -122.8088 | 122.9279 | 122.9416 | 61.4365 | 61.5601
274.9062 | 123.0927 | -61.5097 | 61.3129 | 0.0059509 | -0.0089252 | 0.0077203 | 0.064038 | -0.020403 | -0.02989 | -0.022392 | -0.00054937 | -0.0080321 | 0.062908 | 0.049424 | -0.018794 | -0.010955 | -0.017169 | -0.15106 | 61.2854 | -61.5967 | 61.322 | -61.2854 | -61.7157 | -61.702 | -0.082397 | 61.2259 | -61.5234 | 61.3907 | -61.4365 | -61.4502 | -61.441 | -0.086975 | -0.027466 | 0.009155 | 0.2243 | -0.19226 | -0.20599 | -0.10529 | -0.11902 | -0.013732 | -0.086975 | 0.07782 | 0.073243 | 0.068665 | 0.05951 | 0.082397 | 0.073242 | 0.31128 | 122.9187 | 0.086975 | 122.9141 | 122.8821 | 122.7493 | 122.7951 | 122.7356 | -122.9095 | -122.8363 | 122.8317 | 122.9004 | 61.3586 | 61.4273
276.5938 | 123.0927 | -61.5143 | 61.3129 | -0.0016786 | -0.0082842 | 0.01007 | 0.063183 | -0.019976 | -0.02989 | -0.023674 | 0.0025024 | -0.0084595 | 0.062481 | 0.043656 | -0.019008 | -0.0094592 | -0.014605 | -0.11902 | 61.2579 | -61.6013 | 61.3495 | -61.2442 | -61.6699 | -61.702 | -0.041199 | 61.1938 | -61.5417 | 61.4227 | -61.4044 | -61.4365 | -61.4182 | -0.086975 | -0.054931 | 0.036621 | 0.27008 | -0.18768 | -0.15564 | -0.10071 | -0.068665 | -0.027466 | -0.11902 | 0.10986 | 0.10986 | 0.09613 | 0.07782 | 0.1236 | 0.10529 | 0.35705 | 122.9507 | 0.13733 | 122.9645 | 122.8592 | 122.7356 | 122.7722 | 122.7081 | -122.9141 | -122.8546 | 122.8638 | 122.937 | 61.3953 | 61.4731
278.2812 | 123.0881 | -61.4182 | 61.377 | 0.01358 | -0.0099932 | 0.0066523 | 0.064251 | -0.023607 | -0.032454 | -0.024742 | 0.0025024 | -0.0093139 | 0.063335 | 0.046433 | -0.022853 | -0.0101 | -0.017383 | 0.013733 | 61.3037 | -61.5143 | 61.496 | -61.0703 | -61.5051 | -61.5555 | 0.091553 | 61.2534 | -61.4365 | 61.5005 | -61.2671 | -61.3266 | -61.3541 | -0.09613 | -0.073242 | 0.11902 | 0.3479 | -0.13733 | -0.086975 | -0.041199 | 0.009155 | -0.01831 | -0.1236 | 0.1236 | 0.15106 | 0.064087 | 0.091553 | 0.082397 | 0.10986 | 0.44403 | 123.0103 | 0.16937 | 122.937 | 122.818 | 122.6898 | 122.7219 | 122.6715 | -122.8912 | -122.8134 | 122.9141 | 122.9187 | 61.4319 | 61.5097
279.9688 | 123.024 | -61.4731 | 61.3998 | 0.02121 | -0.009566 | 0.0068659 | 0.064251 | -0.021044 | -0.029676 | -0.021537 | 0.014709 | -0.0054687 | 0.062908 | 0.040024 | -0.023281 | -0.013091 | -0.019946 | -0.027466 | 61.3541 | -61.5509 | 61.3724 | -61.2259 | -61.615 | -61.6333 | -0.050354 | 61.3358 | -61.5097 | 61.3861 | -61.4273 | -61.4594 | -61.4273 | -0.07782 | -0.045776 | -0.027466 | 0.24719 | -0.16022 | -0.14191 | -0.082398 | -0.064087 | -0.036622 | -0.064087 | -0.013733 | 0.045776 | 0.045776 | 0.013732 | 0.082398 | 0.050354 | 0.32501 | 122.9233 | 0.082398 | 122.8958 | 122.905 | 122.8455 | 122.8271 | 122.8088 | -122.9507 | -122.9095 | 122.8455 | 122.8592 | 61.4456 | 61.4227
281.6562 | 123.0881 | -61.4273 | 61.3586 | -0.0016786 | -0.007857 | 0.0085749 | 0.062115 | -0.024889 | -0.029463 | -0.025383 | -0.003601 | -0.0086731 | 0.062267 | 0.04152 | -0.021572 | -0.012023 | -0.017169 | 0.009155 | 61.2671 | -61.4914 | 61.4822 | -61.0886 | -61.5097 | -61.5646 | 0.10529 | 61.29 | -61.4731 | 61.5051 | -61.2808 | -61.3129 | -61.3449 | -0.064087 | -0.091553 | 0.1236 | 0.33874 | -0.13733 | -0.082398 | -0.073242 | -0.018311 | -0.045776 | -0.068665 | 0.14648 | 0.14648 | 0.082397 | 0.11444 | 0.12817 | 0.16022 | 0.40283 | 122.9736 | 0.19226 | 122.9782 | 122.7585 | 122.7631 | 122.6944 | 122.7173 | -122.85 | -122.8317 | 122.9095 | 122.9324 | 61.4365 | 61.5326
283.3594 | 123.0652 | -61.4044 | 61.3586 | 0.0059509 | -0.0080706 | 0.0079339 | 0.064251 | -0.020617 | -0.029249 | -0.024742 | -0.00054937 | -0.0084595 | 0.062908 | 0.046647 | -0.019863 | -0.013732 | -0.018664 | 0.004578 | 61.3037 | -61.5051 | 61.4731 | -61.1023 | -61.5189 | -61.5463 | 0.082397 | 61.2671 | -61.4365 | 61.4731 | -61.3129 | -61.322 | -61.3541 | -0.10071 | -0.054932 | 0.11444 | 0.30212 | -0.14191 | -0.11444 | -0.041199 | -0.013733 | -0.032043 | -0.091553 | 0.11444 | 0.091553 | 0.050354 | 0.082398 | 0.082397 | 0.11444 | 0.40283 | 122.9782 | 0.1236 | 122.9095 | 122.8088 | 122.7036 | 122.7081 | 122.6715 | -122.8638 | -122.7951 | 122.8775 | 122.8775 | 61.409 | 61.4868
285.0625 | 123.111 | -61.441 | 61.3541 | 0.01358 | -0.0093524 | 0.0077203 | 0.062329 | -0.024462 | -0.030317 | -0.022819 | -0.003601 | -0.0084595 | 0.060131 | 0.04451 | -0.021999 | -0.013732 | -0.014819 | -0.009155 | 61.2671 | -61.5097 | 61.4685 | -61.0748 | -61.5189 | -61.5417 | 0.1236 | 61.2534 | -61.4227 | 61.5005 | -61.29 | -61.3174 | -61.3541 | -0.068665 | -0.086975 | 0.11444 | 0.36621 | -0.10071 | -0.07782 | -0.032043 | -0.009155 | 0.018311 | -0.10071 | 0.14648 | 0.15106 | 0.086975 | 0.1236 | 0.068664 | 0.10528 | 0.43488 | 122.9782 | 0.13275 | 122.9233 | 122.7768 | 122.6761 | 122.7081 | 122.6944 | -122.8638 | -122.7768 | 122.9095 | 122.9416 | 61.4319 | 61.5646
286.7656 | 123.111 | -61.4365 | 61.3449 | -0.0016786 | -0.011061 | 0.0075067 | 0.06297 | -0.022539 | -0.02989 | -0.022605 | 0.0055542 | -0.0093139 | 0.061626 | 0.050706 | -0.019222 | -0.012877 | -0.016101 | -0.009155 | 61.2854 | -61.5051 | 61.4594 | -61.1023 | -61.5143 | -61.5555 | 0.10529 | 61.2396 | -61.4502 | 61.5051 | -61.2808 | -61.29 | -61.3266 | -0.068665 | -0.05951 | 0.11444 | 0.33417 | -0.11902 | -0.07782 | -0.050354 | -0.009155 | -0.013733 | -0.10529 | 0.16022 | 0.15564 | 0.10986 | 0.14648 | 0.1236 | 0.16022 | 0.40283 | 122.9645 | 0.16937 | 122.9553 | 122.7905 | 122.6898 | 122.7219 | 122.6761 | -122.85 | -122.7951 | 122.8958 | 122.9416 | 61.4273 | 61.5417
288.4531 | 122.9599 | -61.5372 | 61.3632 | 0.0059509 | -0.0080706 | 0.0094293 | 0.06596 | -0.019335 | -0.030958 | -0.025383 | 0.0025024 | -0.0069641 | 0.063121 | 0.041947 | -0.020931 | -0.012023 | -0.01311 | -0.064087 | 61.3312 | -61.5601 | 61.322 | -61.29 | -61.7294 | -61.7294 | -0.10529 | 61.2717 | -61.5417 | 61.3403 | -61.5097 | -61.5326 | -61.5143 | -0.022889 | -0.032043 | -0.041199 | 0.24719 | -0.19226 | -0.19226 | -0.16937 | -0.16937 | -0.004578 | -0.091553 | -0.022888 | 0.027465 | 0.022888 | 0.004577 | 0.027466 | 0.009155 | 0.27008 | 122.8821 | 0.032043 | 122.8821 | 122.8912 | 122.8134 | 122.8683 | 122.8088 | -122.9233 | -122.905 | 122.8592 | 122.8775 | 61.4731 | 61.4319
290.1719 | 122.9645 | -61.5326 | 61.322 | -0.0016786 | -0.0076434 | 0.010284 | 0.064679 | -0.019762 | -0.031813 | -0.025596 | -0.00054937 | -0.0073913 | 0.063976 | 0.039811 | -0.018154 | -0.0094592 | -0.014178 | -0.12817 | 61.2808 | -61.5829 | 61.2762 | -61.3358 | -61.7477 | -61.7569 | -0.12817 | 61.2488 | -61.5372 | 61.3312 | -61.5097 | -61.5417 | -61.5005 | -0.050354 | -0.041198 | -0.045776 | 0.19684 | -0.2243 | -0.21515 | -0.17395 | -0.1648 | -0.004577 | -0.073242 | 0.009156 | 0.022888 | 0.032044 | -0.009155 | 0.036621 | -0.004578 | 0.24719 | 122.8592 | 0.027465 | 122.8683 | 122.8638 | 122.7859 | 122.8134 | 122.7814 | -122.905 | -122.8592 | 122.8088 | 122.8638 | 61.4044 | 61.4044
291.9219 | 123.0331 | -61.4731 | 61.3449 | 0.02121 | -0.0089252 | 0.0075067 | 0.063397 | -0.019121 | -0.030104 | -0.02346 | 0.0055542 | -0.0073913 | 0.062481 | 0.047074 | -0.019863 | -0.010741 | -0.014178 | -0.086975 | 61.2762 | -61.5463 | 61.3632 | -61.2259 | -61.615 | -61.6379 | -0.013733 | 61.2579 | -61.5005 | 61.3953 | -61.4044 | -61.4365 | -61.4182 | -0.073243 | -0.068665 | 0.01831 | 0.24719 | -0.16479 | -0.14191 | -0.091552 | -0.068664 | -0.027466 | -0.086975 | 0.050354 | 0.068664 | 0.054931 | 0.036621 | 0.082397 | 0.064087 | 0.32044 | 122.9095 | 0.09613 | 122.8958 | 122.8226 | 122.7585 | 122.7493 | 122.731 | -122.8912 | -122.8455 | 122.8363 | 122.8683 | 61.3861 | 61.4594
293.6562 | 122.9599 | -61.4685 | 61.4044 | 0.01358 | -0.009566 | 0.0077203 | 0.065106 | -0.016344 | -0.031385 | -0.022178 | 0.011658 | -0.0065369 | 0.06419 | 0.053483 | -0.022426 | -0.014586 | -0.014819 | -0.050354 | 61.3495 | -61.5372 | 61.3678 | -61.2488 | -61.6241 | -61.6379 | -0.045776 | 61.3358 | -61.4777 | 61.3586 | -61.4456 | -61.4731 | -61.441 | -0.068664 | -0.054932 | -0.036621 | 0.21973 | -0.16937 | -0.15564 | -0.10071 | -0.086976 | -0.009155 | -0.068665 | -0.045776 | 0.022888 | 0.027466 | -0.004577 | 0.036621 | 0.004578 | 0.28839 | 122.905 | 0.032043 | 122.8363 | 122.8867 | 122.8134 | 122.818 | 122.8043 | -122.9416 | -122.8821 | 122.8363 | 122.8271 | 61.4182 | 61.4227
295.3438 | 123.024 | -61.4685 | 61.3129 | 0.036468 | -0.0097796 | 0.0087885 | 0.065106 | -0.016985 | -0.030317 | -0.023033 | 0.0055542 | -0.0078185 | 0.064403 | 0.040879 | -0.019649 | -0.010527 | -0.015246 | -0.082397 | 61.2534 | -61.5692 | 61.3861 | -61.1938 | -61.6196 | -61.6425 | 0 | 61.203 | -61.5051 | 61.3953 | -61.3953 | -61.4273 | -61.4136 | -0.10071 | -0.059509 | 0.073242 | 0.27466 | -0.17395 | -0.15106 | -0.073242 | -0.050354 | -0.036621 | -0.10986 | 0.082398 | 0.073242 | 0.054932 | 0.041199 | 0.091553 | 0.07782 | 0.37537 | 122.9553 | 0.10986 | 122.9004 | 122.8226 | 122.7081 | 122.7219 | 122.6715 | -122.8821 | -122.818 | 122.8546 | 122.8638 | 61.3861 | 61.4685
297.0312 | 123.0606 | -61.4319 | 61.3541 | 0.0059509 | -0.009566 | 0.0085749 | 0.062329 | -0.020403 | -0.029249 | -0.02111 | -0.003601 | -0.0088867 | 0.062481 | 0.044938 | -0.020931 | -0.011595 | -0.017383 | 0.009155 | 61.3083 | -61.5005 | 61.4777 | -61.084 | -61.5097 | -61.5417 | 0.10071 | 61.2671 | -61.4273 | 61.4777 | -61.29 | -61.3083 | -61.3541 | -0.068664 | -0.045776 | 0.1236 | 0.3479 | -0.10986 | -0.07782 | -0.041199 | -0.009156 | 0.004578 | -0.086975 | 0.1236 | 0.14191 | 0.07782 | 0.1236 | 0.073242 | 0.11902 | 0.41656 | 122.9782 | 0.13733 | 122.905 | 122.8088 | 122.6944 | 122.7402 | 122.699 | -122.8546 | -122.7814 | 122.9095 | 122.9095 | 61.441 | 61.5326
298.75 | 122.9965 | -61.5417 | 61.3129 | 0.0059509 | -0.0080706 | 0.0081477 | 0.066388 | -0.021258 | -0.033094 | -0.02111 | -0.00054937 | -0.0048279 | 0.062267 | 0.050919 | -0.020717 | -0.011595 | -0.015246 | -0.13275 | 61.2854 | -61.5921 | 61.2671 | -61.3174 | -61.734 | -61.7294 | -0.10071 | 61.2076 | -61.5143 | 61.3403 | -61.4822 | -61.496 | -61.4639 | -0.050354 | -0.027466 | -0.045776 | 0.2243 | -0.18768 | -0.19226 | -0.13733 | -0.14191 | 0.027466 | -0.10529 | 0.027466 | 0.059509 | 0.07782 | 0.045776 | 0.050354 | 0.01831 | 0.27466 | 122.8592 | 0.032043 | 122.8546 | 122.8775 | 122.7219 | 122.8271 | 122.7493 | -122.905 | -122.8271 | 122.8088 | 122.8821 | 61.409 | 61.441
300.4531 | 123.0469 | -61.4822 | 61.3037 | 0.036468 | -0.0082842 | 0.0098565 | 0.063397 | -0.019976 | -0.029036 | -0.024101 | 0.011658 | -0.0086731 | 0.06483 | 0.044083 | -0.02029 | -0.0101 | -0.015887 | -0.064087 | 61.2488 | -61.5509 | 61.3953 | -61.1572 | -61.615 | -61.6196 | 0.032043 | 61.235 | -61.4914 | 61.4136 | -61.3861 | -61.4273 | -61.4182 | -0.068664 | -0.054932 | 0.091553 | 0.32501 | -0.13733 | -0.13275 | -0.068665 | -0.064087 | -0.009155 | -0.068665 | 0.10986 | 0.096131 | 0.064087 | 0.054932 | 0.073242 | 0.064087 | 0.39368 | 122.9462 | 0.10529 | 122.905 | 122.7997 | 122.7264 | 122.731 | 122.7173 | -122.8546 | -122.7951 | 122.8775 | 122.8958 | 61.4182 | 61.5143
302.1562 | 123.0194 | -61.4685 | 61.2946 | 0.02121 | -0.008498 | 0.0094293 | 0.063824 | -0.017199 | -0.030745 | -0.022178 | 0.011658 | -0.0063233 | 0.06419 | 0.046006 | -0.019649 | -0.010741 | -0.020373 | -0.07782 | 61.2167 | -61.5417 | 61.3907 | -61.1801 | -61.6196 | -61.6287 | 0.004578 | 61.2167 | -61.4914 | 61.4182 | -61.3907 | -61.409 | -61.4136 | -0.073242 | -0.07782 | 0.09613 | 0.28839 | -0.16022 | -0.15106 | -0.086975 | -0.07782 | -0.022888 | -0.07782 | 0.1236 | 0.07782 | 0.054932 | 0.059509 | 0.07782 | 0.082397 | 0.36163 | 122.9324 | 0.10071 | 122.9095 | 122.7585 | 122.7081 | 122.6852 | 122.6852 | -122.8363 | -122.7859 | 122.8592 | 122.8867 | 61.3907 | 61.4731
303.9062 | 122.9416 | -61.4456 | 61.3953 | -0.0016786 | -0.011275 | 0.0068659 | 0.064038 | -0.02083 | -0.02989 | -0.026237 | 0.014709 | -0.0054687 | 0.063976 | 0.037461 | -0.023281 | -0.013304 | -0.014605 | -0.059509 | 61.3129 | -61.496 | 61.3403 | -61.2396 | -61.6241 | -61.6379 | -0.036621 | 61.3449 | -61.4914 | 61.3541 | -61.4319 | -61.4502 | -61.4319 | -0.050354 | -0.082398 | -0.054932 | 0.20599 | -0.19226 | -0.17853 | -0.14191 | -0.12817 | -0.045776 | -0.050354 | -0.041199 | 0.013733 | 0.013733 | -0.004577 | 0.059509 | 0.041199 | 0.25635 | 122.8363 | 0.059509 | 122.8455 | 122.8088 | 122.8363 | 122.7585 | 122.7905 | -122.8912 | -122.8867 | 122.7859 | 122.7997 | 61.3861 | 61.409
305.5938 | 122.9553 | -61.4548 | 61.4136 | 0.0059509 | -0.0063616 | 0.0075067 | 0.062329 | -0.019976 | -0.031813 | -0.024742 | -0.00054937 | -0.0063233 | 0.063335 | 0.038956 | -0.02264 | -0.013518 | -0.017596 | -0.045776 | 61.3174 | -61.5005 | 61.3541 | -61.2213 | -61.615 | -61.6196 | -0.054932 | 61.3449 | -61.4502 | 61.3632 | -61.4182 | -61.4319 | -61.4456 | -0.045776 | -0.09613 | -0.059509 | 0.23346 | -0.16479 | -0.16022 | -0.11902 | -0.11444 | 0.004578 | -0.068664 | -0.050354 | 0.036621 | 0.009155 | 0.022888 | 0.004577 | 0.01831 | 0.27924 | 122.8546 | 0.032043 | 122.8134 | 122.818 | 122.7951 | 122.7722 | 122.7997 | -122.9141 | -122.8638 | 122.8088 | 122.818 | 61.409 | 61.3998
307.2969 | 122.9553 | -61.4273 | 61.3953 | -0.0016786 | -0.0089252 | 0.0070795 | 0.062756 | -0.020617 | -0.031813 | -0.024101 | 0.0025024 | -0.0076049 | 0.062053 | 0.040238 | -0.021572 | -0.012236 | -0.015246 | 0 | 61.3083 | -61.4914 | 61.409 | -61.1481 | -61.5646 | -61.5921 | 0 | 61.2991 | -61.4456 | 61.377 | -61.3724 | -61.4227 | -61.4182 | -0.064087 | -0.086975 | 0.013733 | 0.27924 | -0.16479 | -0.13733 | -0.10071 | -0.073242 | -0.018311 | -0.096131 | -0.018311 | 0.054932 | 0.009155 | 0.004578 | 0.027466 | 0.022889 | 0.34332 | 122.9004 | 0.073243 | 122.8226 | 122.7997 | 122.7448 | 122.7356 | 122.7264 | -122.8867 | -122.8409 | 122.8363 | 122.8043 | 61.4273 | 61.4273
308.9844 | 122.9553 | -61.4273 | 61.3861 | 0.02121 | -0.0070026 | 0.0066523 | 0.065533 | -0.019549 | -0.031172 | -0.021324 | 0.008606 | -0.0050415 | 0.064617 | 0.041947 | -0.021144 | -0.012236 | -0.019305 | -0.036621 | 61.3312 | -61.528 | 61.3495 | -61.2534 | -61.6196 | -61.6516 | -0.054932 | 61.3037 | -61.4685 | 61.3541 | -61.409 | -61.441 | -61.4182 | -0.10071 | -0.054931 | -0.036621 | 0.17395 | -0.2243 | -0.19226 | -0.1236 | -0.091553 | -0.041199 | -0.082397 | -0.032043 | 0.01831 | 0.009155 | -0.013733 | 0.050354 | 0.027466 | 0.27466 | 122.8775 | 0.059509 | 122.8226 | 122.8592 | 122.7722 | 122.7585 | 122.731 | -122.9141 | -122.8546 | 122.7768 | 122.7814 | 61.3907 | 61.3724
310.6875 | 122.9324 | -61.5051 | 61.3358 | 0.0059509 | -0.0057208 | 0.010284 | 0.066815 | -0.019549 | -0.029249 | -0.02346 | 0.0025024 | -0.0073913 | 0.061626 | 0.041306 | -0.019222 | -0.012236 | -0.017383 | -0.086975 | 61.2946 | -61.5601 | 61.2854 | -61.2762 | -61.6928 | -61.7203 | -0.091553 | 61.2488 | -61.5143 | 61.3037 | -61.4868 | -61.5417 | -61.4685 | -0.054932 | -0.041198 | -0.050354 | 0.22888 | -0.21515 | -0.18768 | -0.16022 | -0.13275 | -0.009155 | -0.086975 | -0.032043 | 0.018311 | 0.036621 | -0.036621 | 0.045776 | -0.027466 | 0.28381 | 122.8455 | 0.027466 | 122.818 | 122.8546 | 122.7631 | 122.7997 | 122.7539 | -122.8958 | -122.85 | 122.7905 | 122.8088 | 61.4182 | 61.4136
312.3906 | 122.9691 | -61.5189 | 61.2671 | -0.0016786 | -0.0082842 | 0.0079339 | 0.06596 | -0.019762 | -0.026899 | -0.021751 | 0.0025024 | -0.0067505 | 0.064403 | 0.041733 | -0.019008 | -0.0096728 | -0.015246 | -0.15106 | 61.2808 | -61.5784 | 61.2625 | -61.3083 | -61.7203 | -61.7386 | -0.13275 | 61.2305 | -61.5097 | 61.3174 | -61.4777 | -61.528 | -61.4822 | -0.059509 | 0.013733 | -0.004578 | 0.21057 | -0.21973 | -0.20142 | -0.16022 | -0.14191 | 0.009155 | -0.036621 | 0.050354 | 0.041199 | 0.036621 | -0.009155 | 0.027466 | -0.01831 | 0.27008 | 122.8409 | 0.032044 | 122.8271 | 122.8592 | 122.7402 | 122.7997 | 122.7493 | -122.8455 | -122.7768 | 122.7814 | 122.8363 | 61.3678 | 61.3861
314.0781 | 123.0698 | -61.4731 | 61.2671 | -0.0016786 | -0.008498 | 0.0083613 | 0.065106 | -0.018694 | -0.029036 | -0.023033 | 0.0055542 | -0.0086731 | 0.062481 | 0.043229 | -0.017726 | -0.010314 | -0.014819 | -0.064087 | 61.235 | -61.5417 | 61.3724 | -61.1847 | -61.6379 | -61.647 | -0.004578 | 61.1572 | -61.5097 | 61.4273 | -61.377 | -61.3998 | -61.3953 | -0.068665 | -0.032044 | 0.10528 | 0.28839 | -0.17395 | -0.16479 | -0.10529 | -0.09613 | -0.036622 | -0.10986 | 0.16022 | 0.09613 | 0.077819 | 0.073242 | 0.11444 | 0.10986 | 0.35706 | 122.9141 | 0.13275 | 122.937 | 122.7768 | 122.6669 | 122.7081 | 122.6303 | -122.8088 | -122.7768 | 122.8455 | 122.9004 | 61.409 | 61.4685
315.7656 | 123.0011 | -61.441 | 61.322 | 0.028839 | -0.0082842 | 0.0094293 | 0.064251 | -0.018053 | -0.029249 | -0.02346 | 0.0055542 | -0.0086731 | 0.062694 | 0.048142 | -0.017726 | -0.011809 | -0.016101 | -0.07782 | 61.2396 | -61.5555 | 61.3632 | -61.1755 | -61.6241 | -61.6287 | -0.013733 | 61.2122 | -61.4868 | 61.3907 | -61.3861 | -61.4182 | -61.3953 | -0.11444 | -0.082397 | 0.041199 | 0.2655 | -0.18768 | -0.18311 | -0.073242 | -0.068665 | -0.045776 | -0.10986 | 0.068665 | 0.054932 | 0.045776 | 0.022888 | 0.091552 | 0.068664 | 0.37994 | 122.9187 | 0.10071 | 122.8775 | 122.7951 | 122.699 | 122.6807 | 122.6532 | -122.8775 | -122.8088 | 122.8043 | 122.8317 | 61.3632 | 61.4273
317.4531 | 123.0606 | -61.409 | 61.3678 | -0.0093076 | -0.011061 | 0.0098565 | 0.064038 | -0.018908 | -0.026686 | -0.022605 | 0.0025024 | -0.0080321 | 0.062694 | 0.042588 | -0.02264 | -0.010527 | -0.017383 | 0 | 61.2717 | -61.4685 | 61.4639 | -61.0565 | -61.4914 | -61.5326 | 0.11444 | 61.2076 | -61.4273 | 61.4914 | -61.2717 | -61.29 | -61.3174 | -0.059509 | -0.096131 | 0.09613 | 0.35248 | -0.1236 | -0.082397 | -0.064087 | -0.022888 | -0.01831 | -0.16022 | 0.1236 | 0.13733 | 0.091553 | 0.11902 | 0.10986 | 0.13733 | 0.41199 | 122.9324 | 0.15564 | 122.9187 | 122.7402 | 122.6349 | 122.6807 | 122.6166 | -122.8363 | -122.7951 | 122.8729 | 122.9004 | 61.409 | 61.5234
319.1406 | 122.9233 | -61.4456 | 61.3861 | 0.0059509 | -0.0074298 | 0.0079339 | 0.062543 | -0.021044 | -0.032454 | -0.023246 | 0.0025024 | -0.0084595 | 0.062908 | 0.03917 | -0.021999 | -0.011809 | -0.012896 | -0.009155 | 61.2946 | -61.4731 | 61.3907 | -61.1664 | -61.5784 | -61.5829 | -0.013733 | 61.2946 | -61.4502 | 61.3815 | -61.3861 | -61.4273 | -61.4044 | -0.027465 | -0.091552 | 0.004578 | 0.27924 | -0.13733 | -0.13275 | -0.10986 | -0.10529 | -0.004577 | -0.091552 | -0.004577 | 0.05951 | 0.041199 | 0.018311 | 0.045776 | 0.022888 | 0.3067 | 122.8638 | 0.064087 | 122.8317 | 122.7676 | 122.7448 | 122.7402 | 122.7402 | -122.8592 | -122.8363 | 122.8363 | 122.8271 | 61.4365 | 61.4319
320.8281 | 122.9645 | -61.4594 | 61.3495 | 0.028839 | -0.0087116 | 0.010711 | 0.065106 | -0.018908 | -0.029676 | -0.022178 | 0.0055542 | -0.0084595 | 0.06483 | 0.035752 | -0.020503 | -0.013304 | -0.014178 | -0.027466 | 61.3266 | -61.5509 | 61.3678 | -61.2213 | -61.5875 | -61.6287 | -0.013733 | 61.2991 | -61.4639 | 61.377 | -61.3815 | -61.4182 | -61.409 | -0.091552 | -0.022888 | 0.018311 | 0.23804 | -0.16937 | -0.12817 | -0.07782 | -0.036621 | -0.004577 | -0.050354 | 0.027466 | 0.07782 | 0.050354 | 0.041199 | 0.054931 | 0.045776 | 0.32959 | 122.9187 | 0.082397 | 122.8409 | 122.8775 | 122.7631 | 122.7859 | 122.7585 | -122.9004 | -122.8134 | 122.8271 | 122.8363 | 61.4319 | 61.4456
322.5625 | 123.056 | -61.4777 | 61.2579 | 0.0059509 | -0.0070026 | 0.0094293 | 0.064465 | -0.019549 | -0.029676 | -0.022392 | 0.011658 | -0.0091003 | 0.063549 | 0.051133 | -0.019435 | -0.0094592 | -0.015246 | -0.068665 | 61.2076 | -61.5372 | 61.3907 | -61.1526 | -61.5967 | -61.615 | 0.013733 | 61.1893 | -61.5189 | 61.4044 | -61.3541 | -61.3998 | -61.3815 | -0.059509 | -0.050354 | 0.13275 | 0.32501 | -0.13733 | -0.11902 | -0.07782 | -0.05951 | -0.041199 | -0.068665 | 0.14648 | 0.1236 | 0.09613 | 0.07782 | 0.13733 | 0.11902 | 0.38452 | 122.9279 | 0.16479 | 122.9233 | 122.7448 | 122.7081 | 122.6852 | 122.6669 | -122.7951 | -122.7768 | 122.8683 | 122.8821 | 61.409 | 61.4914
324.2656 | 123.0148 | -61.4502 | 61.2946 | 0.044098 | -0.0080706 | 0.010711 | 0.063183 | -0.01549 | -0.030104 | -0.022605 | 0.011658 | -0.0086731 | 0.061412 | 0.048783 | -0.02029 | -0.011809 | -0.014178 | -0.07782 | 61.2442 | -61.5463 | 61.3632 | -61.1664 | -61.615 | -61.6287 | 0 | 61.2076 | -61.496 | 61.3953 | -61.377 | -61.4182 | -61.4044 | -0.096131 | -0.050354 | 0.068664 | 0.28381 | -0.17853 | -0.16479 | -0.082397 | -0.068664 | -0.045777 | -0.086975 | 0.10071 | 0.073242 | 0.045776 | 0.032043 | 0.091553 | 0.07782 | 0.37994 | 122.9095 | 0.11902 | 122.8912 | 122.7905 | 122.7036 | 122.6944 | 122.6578 | -122.8409 | -122.7905 | 122.8134 | 122.8455 | 61.3724 | 61.4502
325.9844 | 122.9416 | -61.4136 | 61.3953 | 0.0059509 | -0.007857 | 0.0079339 | 0.063611 | -0.018053 | -0.029676 | -0.025169 | 0.0025024 | -0.0093139 | 0.062694 | 0.044297 | -0.022212 | -0.010741 | -0.013537 | 0.013733 | 61.3174 | -61.4548 | 61.4182 | -61.1298 | -61.5189 | -61.5692 | 0.041199 | 61.29 | -61.4319 | 61.4044 | -61.3541 | -61.3861 | -61.3998 | -0.041199 | -0.07782 | 0.022888 | 0.28381 | -0.15564 | -0.10529 | -0.11444 | -0.064087 | -0.018311 | -0.10529 | 0.009155 | 0.059509 | 0.013733 | 0.027466 | 0.032044 | 0.045777 | 0.32501 | 122.8729 | 0.07782 | 122.8363 | 122.7722 | 122.7219 | 122.731 | 122.7036 | -122.85 | -122.8271 | 122.8317 | 122.818 | 61.4273 | 61.4548
327.6719 | 123.0148 | -61.4639 | 61.2488 | 0.028839 | -0.008498 | 0.0090021 | 0.063824 | -0.020403 | -0.02989 | -0.023033 | 0.014709 | -0.0084595 | 0.063762 | 0.050492 | -0.019863 | -0.011382 | -0.016742 | -0.068665 | 61.2305 | -61.5463 | 61.3861 | -61.1389 | -61.5784 | -61.6013 | 0.036621 | 61.1893 | -61.4822 | 61.409 | -61.3724 | -61.3998 | -61.3953 | -0.082398 | -0.01831 | 0.13733 | 0.32501 | -0.13733 | -0.11444 | -0.054931 | -0.032043 | -0.018311 | -0.059509 | 0.16022 | 0.091553 | 0.068664 | 0.064087 | 0.086975 | 0.082398 | 0.40741 | 122.9324 | 0.10986 | 122.8912 | 122.7768 | 122.6715 | 122.6944 | 122.6532 | -122.7951 | -122.731 | 122.85 | 122.8729 | 61.3953 | 61.5005
329.375 | 122.9691 | -61.4868 | 61.3586 | 0.0059509 | -0.0072162 | 0.0098565 | 0.064679 | -0.016131 | -0.028608 | -0.023674 | 0.0025024 | -0.0069641 | 0.062481 | 0.042588 | -0.021999 | -0.012236 | -0.015674 | -0.018311 | 61.3037 | -61.5326 | 61.3632 | -61.2076 | -61.6058 | -61.6104 | 0.004578 | 61.2808 | -61.4914 | 61.3861 | -61.377 | -61.4182 | -61.3998 | -0.045777 | -0.054932 | 0.004577 | 0.27923 | -0.1236 | -0.11902 | -0.07782 | -0.073242 | -0.004578 | -0.07782 | 0.027465 | 0.10986 | 0.086975 | 0.068664 | 0.091553 | 0.073242 | 0.32501 | 122.8958 | 0.11444 | 122.8775 | 122.8363 | 122.7722 | 122.7905 | 122.7676 | -122.8912 | -122.85 | 122.85 | 122.8729 | 61.4685 | 61.4914
331.0781 | 122.9324 | -61.5005 | 61.3266 | 0.01358 | -0.009566 | 0.010711 | 0.063611 | -0.015917 | -0.029249 | -0.021965 | -0.003601 | -0.0069641 | 0.062908 | 0.045365 | -0.019435 | -0.013518 | -0.014178 | -0.13733 | 61.2488 | -61.5601 | 61.2396 | -61.3266 | -61.734 | -61.7432 | -0.14191 | 61.2442 | -61.5097 | 61.2946 | -61.5051 | -61.5326 | -61.4731 | -0.05951 | -0.07782 | -0.086975 | 0.17395 | -0.24262 | -0.23346 | -0.1831 | -0.17395 | -0.009156 | -0.082397 | -0.032043 | -0.004578 | 0.027466 | -0.032044 | 0.036622 | -0.022888 | 0.23346 | 122.7997 | 0.004578 | 122.8043 | 122.8088 | 122.7539 | 122.7493 | 122.7448 | -122.8867 | -122.8363 | 122.7402 | 122.7951 | 61.3632 | 61.3586
332.7812 | 123.0194 | -61.4731 | 61.3083 | 0.028839 | -0.0072162 | 0.011779 | 0.064892 | -0.016771 | -0.02989 | -0.023674 | 0.014709 | -0.0080321 | 0.063549 | 0.053055 | -0.02029 | -0.010314 | -0.014605 | -0.050354 | 61.2259 | -61.5509 | 61.3724 | -61.1435 | -61.5784 | -61.6058 | 0.027466 | 61.203 | -61.496 | 61.3998 | -61.3632 | -61.3953 | -61.3815 | -0.07782 | -0.082398 | 0.064086 | 0.32959 | -0.13275 | -0.10529 | -0.054932 | -0.027466 | -0.022889 | -0.10529 | 0.091552 | 0.10986 | 0.091552 | 0.077819 | 0.11444 | 0.10071 | 0.40741 | 122.9233 | 0.13275 | 122.8958 | 122.7768 | 122.699 | 122.699 | 122.6761 | -122.8592 | -122.8043 | 122.8455 | 122.8729 | 61.4227 | 61.5005
334.5 | 123.0194 | -61.4319 | 61.3495 | 0.01358 | -0.010848 | 0.0081477 | 0.063824 | -0.018694 | -0.030531 | -0.02346 | -0.00054937 | -0.0091003 | 0.065044 | 0.047288 | -0.020717 | -0.008391 | -0.013324 | -0.086975 | 61.2442 | -61.5326 | 61.3312 | -61.1893 | -61.5967 | -61.6058 | -0.018311 | 61.2167 | -61.4685 | 61.3953 | -61.3403 | -61.3541 | -61.3678 | -0.10071 | -0.10529 | -0.01831 | 0.24262 | -0.17395 | -0.16479 | -0.073242 | -0.064087 | -0.036621 | -0.13275 | 0.045777 | 0.091553 | 0.064087 | 0.07782 | 0.10071 | 0.11444 | 0.34332 | 122.8638 | 0.12817 | 122.8638 | 122.7768 | 122.6852 | 122.6761 | 122.6486 | -122.8821 | -122.818 | 122.7631 | 122.8271 | 61.3449 | 61.4136
336.2188 | 122.9691 | -61.4456 | 61.3449 | 0.02121 | -0.008498 | 0.0081477 | 0.065106 | -0.019549 | -0.029676 | -0.024101 | 0.011658 | -0.0061095 | 0.060985 | 0.040879 | -0.023067 | -0.011595 | -0.013751 | -0.018311 | 61.3403 | -61.5326 | 61.3586 | -61.1984 | -61.5692 | -61.5967 | -0.022888 | 61.3129 | -61.4868 | 61.3541 | -61.3861 | -61.4273 | -61.3907 | -0.086975 | -0.004578 | 0.013733 | 0.24719 | -0.15106 | -0.1236 | -0.064087 | -0.036621 | -0.041198 | -0.032044 | 0.009155 | 0.05951 | 0.054932 | 0.018311 | 0.09613 | 0.059509 | 0.33417 | 122.8912 | 0.10071 | 122.8409 | 122.8729 | 122.7997 | 122.7859 | 122.7585 | -122.8775 | -122.8317 | 122.8043 | 122.7997 | 61.4273 | 61.4227
337.9062 | 123.0423 | -61.4456 | 61.2671 | 0.0059509 | -0.0089252 | 0.01007 | 0.064038 | -0.02318 | -0.02989 | -0.023246 | -0.00054937 | -0.0091003 | 0.061626 | 0.050706 | -0.017085 | -0.011382 | -0.012256 | -0.11902 | 61.2305 | -61.5463 | 61.3312 | -61.2076 | -61.647 | -61.647 | -0.022888 | 61.1847 | -61.5189 | 61.3907 | -61.3815 | -61.4044 | -61.3861 | -0.10071 | -0.036621 | 0.064087 | 0.23804 | -0.20142 | -0.20142 | -0.10071 | -0.10071 | -0.073242 | -0.082398 | 0.1236 | 0.064087 | 0.05951 | 0.041199 | 0.13275 | 0.11444 | 0.33875 | 122.8775 | 0.13733 | 122.9095 | 122.7768 | 122.7036 | 122.6761 | 122.6303 | -122.8134 | -122.7859 | 122.7768 | 122.8363 | 61.3266 | 61.4227
339.5938 | 123.0423 | -61.3724 | 61.3449 | 0.01358 | -0.011489 | 0.0098565 | 0.064038 | -0.02083 | -0.030531 | -0.026237 | -0.00054937 | -0.0084595 | 0.06419 | 0.047501 | -0.02264 | -0.013945 | -0.018023 | 0.004578 | 61.2579 | -61.4868 | 61.4456 | -61.0519 | -61.4639 | -61.5189 | 0.10529 | 61.2305 | -61.4136 | 61.4639 | -61.2534 | -61.29 | -61.3129 | -0.11444 | -0.086975 | 0.10071 | 0.32043 | -0.14648 | -0.091553 | -0.032044 | 0.022888 | -0.041199 | -0.11444 | 0.11902 | 0.11902 | 0.059509 | 0.082397 | 0.10071 | 0.1236 | 0.43487 | 122.9324 | 0.16022 | 122.8775 | 122.7448 | 122.644 | 122.6303 | 122.6028 | -122.8317 | -122.7585 | 122.818 | 122.8363 | 61.377 | 61.4777
341.2812 | 122.9553 | -61.4594 | 61.3403 | 0.01358 | -0.008498 | 0.0092157 | 0.067456 | -0.023394 | -0.030104 | -0.024955 | 0.0055542 | -0.0069641 | 0.063121 | 0.044938 | -0.023708 | -0.01245 | -0.014819 | -0.032043 | 61.3312 | -61.5372 | 61.3495 | -61.1847 | -61.5967 | -61.6013 | -0.009155 | 61.29 | -61.4777 | 61.3586 | -61.3861 | -61.4136 | -61.3815 | -0.077819 | -0.009155 | 0.009155 | 0.27466 | -0.14191 | -0.13733 | -0.064087 | -0.05951 | -0.01831 | -0.050354 | 0.018311 | 0.073243 | 0.07782 | 0.045777 | 0.09613 | 0.064087 | 0.35248 | 122.8867 | 0.091553 | 122.8363 | 122.8683 | 122.7676 | 122.7905 | 122.7493 | -122.8775 | -122.818 | 122.8088 | 122.818 | 61.4273 | 61.4502
343 | 122.9095 | -61.4868 | 61.2991 | 0.02121 | -0.0087116 | 0.0083613 | 0.065106 | -0.014635 | -0.029676 | -0.025169 | -0.00054937 | -0.0067505 | 0.06419 | 0.047928 | -0.02029 | -0.012023 | -0.014819 | -0.15564 | 61.2579 | -61.5326 | 61.2305 | -61.3266 | -61.7432 | -61.7294 | -0.15564 | 61.2259 | -61.5189 | 61.2762 | -61.5005 | -61.528 | -61.4685 | -0.045777 | -0.041198 | -0.068664 | 0.16022 | -0.24262 | -0.25635 | -0.19684 | -0.21057 | -0.032044 | -0.073242 | -0.022888 | -0.013733 | 0.01831 | -0.041199 | 0.050354 | -0.009155 | 0.20599 | 122.7631 | 0.018311 | 122.7951 | 122.7905 | 122.7448 | 122.7448 | 122.7127 | -122.8317 | -122.818 | 122.7173 | 122.7631 | 61.3312 | 61.3312
344.6875 | 122.8912 | -61.5189 | 61.2991 | 0.0059509 | -0.0089252 | 0.0079339 | 0.064892 | -0.013567 | -0.027967 | -0.023674 | 0.0025024 | -0.0073913 | 0.064403 | 0.048356 | -0.018154 | -0.012023 | -0.015033 | -0.14648 | 61.2762 | -61.5646 | 61.203 | -61.3312 | -61.7294 | -61.7203 | -0.16022 | 61.235 | -61.5234 | 61.2671 | -61.496 | -61.5417 | -61.4639 | -0.045776 | -0.022888 | -0.09613 | 0.18768 | -0.20142 | -0.21057 | -0.15564 | -0.16479 | -0.004577 | -0.064087 | -0.032043 | 0.022888 | 0.054932 | -0.022888 | 0.059509 | -0.018311 | 0.23346 | 122.7676 | 0.027465 | 122.7905 | 122.8409 | 122.7585 | 122.7951 | 122.7539 | -122.8638 | -122.8226 | 122.7219 | 122.7859 | 61.3724 | 61.3586
346.375 | 123.024 | -61.4731 | 61.2625 | 0.01358 | -0.0091388 | 0.0087885 | 0.065747 | -0.014208 | -0.029249 | -0.025169 | 0.0025024 | -0.0071777 | 0.061412 | 0.042161 | -0.018367 | -0.010955 | -0.013537 | -0.12817 | 61.2259 | -61.5646 | 61.2808 | -61.2305 | -61.6562 | -61.6745 | -0.073242 | 61.1481 | -61.4777 | 61.3678 | -61.3861 | -61.4044 | -61.3907 | -0.091553 | -0.036621 | 0.018311 | 0.24261 | -0.20142 | -0.18311 | -0.10986 | -0.091553 | -0.004578 | -0.11444 | 0.10529 | 0.086975 | 0.082397 | 0.068664 | 0.086975 | 0.073242 | 0.33417 | 122.8455 | 0.091553 | 122.8455 | 122.7905 | 122.6257 | 122.699 | 122.6212 | -122.8271 | -122.7402 | 122.7539 | 122.8409 | 61.3449 | 61.3998
348.0625 | 122.9736 | -61.4685 | 61.3083 | 0.028839 | -0.007857 | 0.0085749 | 0.065533 | -0.015703 | -0.029676 | -0.025169 | 0.0055542 | -0.0093139 | 0.062267 | 0.04152 | -0.019649 | -0.010314 | -0.015887 | -0.086975 | 61.2396 | -61.5326 | 61.3449 | -61.1435 | -61.5967 | -61.6241 | -0.009155 | 61.2076 | -61.4914 | 61.3678 | -61.3724 | -61.409 | -61.3953 | -0.064087 | -0.068665 | 0.036621 | 0.32501 | -0.15564 | -0.12817 | -0.091553 | -0.064087 | -0.022888 | -0.10071 | 0.059509 | 0.096131 | 0.073242 | 0.059509 | 0.09613 | 0.082397 | 0.3891 | 122.8775 | 0.11902 | 122.8592 | 122.7722 | 122.699 | 122.7081 | 122.6761 | -122.8409 | -122.7997 | 122.8134 | 122.8363 | 61.3815 | 61.4594
349.75 | 123.0057 | -61.4777 | 61.2717 | 0.0059509 | -0.0097796 | 0.0098565 | 0.064679 | -0.017199 | -0.027967 | -0.023674 | -0.00054937 | -0.0052551 | 0.062053 | 0.044938 | -0.020503 | -0.010741 | -0.019946 | -0.13275 | 61.2488 | -61.5509 | 61.2808 | -61.2579 | -61.6745 | -61.6837 | -0.059509 | 61.1938 | -61.5097 | 61.377 | -61.409 | -61.4365 | -61.3907 | -0.073242 | -0.022888 | 0.009156 | 0.21973 | -0.20599 | -0.19684 | -0.13275 | -0.1236 | -0.032044 | -0.077819 | 0.10529 | 0.068664 | 0.086975 | 0.041199 | 0.11902 | 0.073243 | 0.29297 | 122.8317 | 0.10071 | 122.8867 | 122.7997 | 122.7036 | 122.7264 | 122.6715 | -122.8226 | -122.7814 | 122.7585 | 122.8546 | 61.3449 | 61.4182
351.4844 | 122.9919 | -61.377 | 61.3495 | 0.0059509 | -0.0072162 | 0.0072931 | 0.063183 | -0.01784 | -0.031172 | -0.023887 | 0.0025024 | -0.0082459 | 0.064403 | 0.051987 | -0.024349 | -0.012023 | -0.01546 | 0.009155 | 61.2671 | -61.4822 | 61.4319 | -61.0794 | -61.4914 | -61.5372 | 0.07782 | 61.2534 | -61.409 | 61.4456 | -61.2762 | -61.2946 | -61.2991 | -0.10529 | -0.082397 | 0.082398 | 0.29755 | -0.16022 | -0.11444 | -0.054931 | -0.009155 | -0.032044 | -0.09613 | 0.096131 | 0.10071 | 0.07782 | 0.082397 | 0.10986 | 0.11444 | 0.40283 | 122.9141 | 0.13275 | 122.8546 | 122.7493 | 122.6624 | 122.644 | 122.6303 | -122.8317 | -122.7585 | 122.8088 | 122.8226 | 61.3861 | 61.4548
353.2969 | 122.9828 | -61.4639 | 61.3037 | 0.028839 | -0.0072162 | 0.0098565 | 0.065106 | -0.019335 | -0.028181 | -0.024314 | 0.011658 | -0.0084595 | 0.063976 | 0.051346 | -0.021358 | -0.011382 | -0.017383 | -0.086975 | 61.2213 | -61.5234 | 61.3541 | -61.1526 | -61.5921 | -61.6013 | -0.027466 | 61.203 | -61.4685 | 61.3724 | -61.377 | -61.3907 | -61.3998 | -0.059509 | -0.082398 | 0.050354 | 0.31128 | -0.13733 | -0.12817 | -0.07782 | -0.068665 | -0.004578 | -0.10071 | 0.068664 | 0.086975 | 0.064087 | 0.073242 | 0.068665 | 0.07782 | 0.37079 | 122.8775 | 0.091553 | 122.8409 | 122.7448 | 122.6715 | 122.6852 | 122.6669 | -122.8271 | -122.7722 | 122.818 | 122.8363 | 61.377 | 61.4365
355.0938 | 123.0011 | -61.4502 | 61.2808 | 0.02121 | -0.0052936 | 0.012847 | 0.063824 | -0.016558 | -0.027754 | -0.022605 | 0.0055542 | -0.0063233 | 0.062053 | 0.048997 | -0.018794 | -0.0075366 | -0.012896 | -0.068665 | 61.2076 | -61.5646 | 61.3586 | -61.1389 | -61.5921 | -61.6058 | 0.018311 | 61.1847 | -61.4914 | 61.3724 | -61.3586 | -61.3815 | -61.377 | -0.11444 | -0.073242 | 0.07782 | 0.31128 | -0.15564 | -0.14191 | -0.041199 | -0.027466 | -0.041199 | -0.096131 | 0.091552 | 0.091552 | 0.073242 | 0.068664 | 0.11444 | 0.10986 | 0.42572 | 122.9233 | 0.13275 | 122.8638 | 122.7722 | 122.6761 | 122.6578 | 122.6349 | -122.8455 | -122.7722 | 122.8088 | 122.8226 | 61.3815 | 61.4685
356.7969 | 122.937 | -61.441 | 61.3358 | 0.028839 | -0.0074298 | 0.0087885 | 0.064251 | -0.020189 | -0.029676 | -0.02111 | 0.0055542 | -0.0046143 | 0.063549 | 0.044297 | -0.023281 | -0.013304 | -0.015246 | -0.032043 | 61.3266 | -61.528 | 61.3358 | -61.1847 | -61.5692 | -61.6013 | 0.018311 | 61.2808 | -61.4731 | 61.3724 | -61.3678 | -61.4136 | -61.3953 | -0.086975 | -0.009155 | 0 | 0.25635 | -0.16022 | -0.12817 | -0.073242 | -0.041199 | -0.032043 | -0.054931 | 0.036621 | 0.073242 | 0.045776 | 0.027466 | 0.077819 | 0.059509 | 0.34332 | 122.8638 | 0.10529 | 122.8455 | 122.8546 | 122.7539 | 122.7676 | 122.7219 | -122.8638 | -122.8088 | 122.7768 | 122.8134 | 61.409 | 61.4594
358.5469 | 122.8867 | -61.4319 | 61.3724 | -0.0093076 | -0.009566 | 0.0072931 | 0.066815 | -0.020189 | -0.03224 | -0.022178 | 0.011658 | -0.0076049 | 0.063335 | 0.050065 | -0.024562 | -0.015227 | -0.014819 | -0.059509 | 61.322 | -61.4914 | 61.3312 | -61.1938 | -61.5738 | -61.5829 | -0.027466 | 61.3129 | -61.4777 | 61.3266 | -61.3907 | -61.4227 | -61.3998 | -0.059509 | -0.050354 | -0.041198 | 0.23804 | -0.15106 | -0.14191 | -0.091553 | -0.082398 | -0.045776 | -0.059509 | -0.045776 | 0.041199 | 0.032044 | 0.009156 | 0.07782 | 0.054932 | 0.29755 | 122.8226 | 0.086975 | 122.8043 | 122.8134 | 122.7905 | 122.7539 | 122.7448 | -122.8638 | -122.85 | 122.7631 | 122.7585 | 61.3724 | 61.4044
360.2656 | 122.9462 | -61.4548 | 61.3266 | 0.028839 | -0.007857 | 0.0098565 | 0.064892 | -0.016985 | -0.03224 | -0.022819 | 0.008606 | -0.0069641 | 0.063121 | 0.038956 | -0.021144 | -0.013304 | -0.018023 | -0.036621 | 61.3403 | -61.5417 | 61.3266 | -61.1893 | -61.5921 | -61.5967 | -0.013733 | 61.2625 | -61.4685 | 61.3678 | -61.3632 | -61.4044 | -61.3815 | -0.086975 | 0.013733 | 0 | 0.2655 | -0.14191 | -0.13733 | -0.054932 | -0.050354 | -0.013733 | -0.064087 | 0.041199 | 0.091553 | 0.073242 | 0.050354 | 0.086975 | 0.064087 | 0.35248 | 122.8683 | 0.10529 | 122.8363 | 122.8821 | 122.731 | 122.7951 | 122.7173 | -122.8683 | -122.7951 | 122.7814 | 122.8226 | 61.4182 | 61.441
362.0312 | 122.9599 | -61.3815 | 61.3678 | -0.0016786 | -0.0097796 | 0.0072931 | 0.061474 | -0.020617 | -0.028395 | -0.022392 | 0.0025024 | -0.0078185 | 0.060558 | 0.044938 | -0.021785 | -0.01245 | -0.018023 | 0.004578 | 61.2579 | -61.4639 | 61.4136 | -61.0703 | -61.5005 | -61.528 | 0.068665 | 61.2396 | -61.4182 | 61.4136 | -61.2854 | -61.3174 | -61.322 | -0.082397 | -0.10986 | 0.045776 | 0.31128 | -0.14648 | -0.11902 | -0.064087 | -0.036621 | -0.036621 | -0.12817 | 0.045776 | 0.096131 | 0.05951 | 0.064087 | 0.096131 | 0.10071 | 0.39368 | 122.8775 | 0.13275 | 122.8317 | 122.7219 | 122.6578 | 122.6395 | 122.6212 | -122.8317 | -122.7859 | 122.7951 | 122.7951 | 61.3861 | 61.4502
363.7344 | 123.0103 | -61.377 | 61.3174 | 0.0059509 | -0.0097796 | 0.0066523 | 0.06297 | -0.020189 | -0.029463 | -0.026237 | 0.0025024 | -0.0086731 | 0.062053 | 0.041733 | -0.018581 | -0.011168 | -0.019305 | -0.082397 | 61.2396 | -61.496 | 61.3495 | -61.1389 | -61.5555 | -61.5829 | 0.018311 | 61.2076 | -61.4273 | 61.4182 | -61.2991 | -61.3129 | -61.322 | -0.11902 | -0.07782 | 0.032043 | 0.23804 | -0.20599 | -0.17853 | -0.086975 | -0.059509 | -0.050354 | -0.10986 | 0.10071 | 0.07782 | 0.054932 | 0.064087 | 0.10529 | 0.11444 | 0.35706 | 122.8455 | 0.12817 | 122.8455 | 122.7356 | 122.6349 | 122.6166 | 122.5845 | -122.8134 | -122.7448 | 122.7264 | 122.7951 | 61.2946 | 61.3953
365.5 | 122.8638 | -61.4777 | 61.2854 | 0.0059509 | -0.0087116 | 0.0075067 | 0.06532 | -0.016558 | -0.028608 | -0.023674 | 0.0055542 | -0.0069641 | 0.063335 | 0.040238 | -0.019222 | -0.010955 | -0.01546 | -0.12817 | 61.2854 | -61.5417 | 61.2396 | -61.3037 | -61.7157 | -61.7111 | -0.16022 | 61.2259 | -61.4777 | 61.2396 | -61.5234 | -61.5417 | -61.4731 | -0.064087 | 0 | -0.045776 | 0.17395 | -0.23346 | -0.23804 | -0.16937 | -0.17395 | 0 | -0.059509 | -0.045776 | -0.045776 | 0.004578 | -0.064087 | 0.004578 | -0.064087 | 0.23804 | 122.7814 | -0.045776 | 122.7173 | 122.8271 | 122.7036 | 122.7631 | 122.7036 | -122.8271 | -122.7631 | 122.7173 | 122.7173 | 61.3495 | 61.3174
367.2188 | 122.9279 | -61.4273 | 61.3358 | 0.02121 | -0.0091388 | 0.0087885 | 0.065747 | -0.018267 | -0.032667 | -0.020897 | 0.0055542 | -0.0071777 | 0.063549 | 0.035966 | -0.020931 | -0.011382 | -0.014178 | -0.027466 | 61.3449 | -61.5005 | 61.3266 | -61.1847 | -61.5601 | -61.6013 | -0.022888 | 61.2946 | -61.4685 | 61.3632 | -61.3632 | -61.4044 | -61.3632 | -0.073242 | 0.009156 | -0.009155 | 0.24262 | -0.17395 | -0.13275 | -0.10071 | -0.05951 | -0.041199 | -0.041198 | 0.027466 | 0.064087 | 0.064087 | 0.022888 | 0.10529 | 0.064087 | 0.31586 | 122.8271 | 0.10529 | 122.8317 | 122.8455 | 122.7631 | 122.7722 | 122.7219 | -122.8363 | -122.8043 | 122.7539 | 122.7905 | 61.3998 | 61.4044
368.9219 | 122.9919 | -61.4273 | 61.2396 | -0.0016786 | -0.0089252 | 0.010284 | 0.061261 | -0.016558 | -0.02989 | -0.023887 | 0.014709 | -0.0093139 | 0.063121 | 0.043229 | -0.018367 | -0.008391 | -0.013965 | -0.09613 | 61.1847 | -61.5372 | 61.3403 | -61.1389 | -61.5921 | -61.5921 | 0.009155 | 61.1664 | -61.496 | 61.3953 | -61.3358 | -61.3724 | -61.3586 | -0.10986 | -0.054932 | 0.10071 | 0.28839 | -0.16479 | -0.16479 | -0.054932 | -0.054932 | -0.068665 | -0.073242 | 0.15564 | 0.091553 | 0.068664 | 0.054932 | 0.13733 | 0.1236 | 0.39825 | 122.8775 | 0.16022 | 122.8912 | 122.7219 | 122.6624 | 122.612 | 122.5937 | -122.7768 | -122.7356 | 122.7676 | 122.8226 | 61.3312 | 61.4365
370.7031 | 122.9507 | -61.4182 | 61.2717 | 0.02121 | -0.007857 | 0.0096429 | 0.063397 | -0.016985 | -0.031172 | -0.02346 | 0.008606 | -0.0088867 | 0.061626 | 0.044938 | -0.018154 | -0.010955 | -0.015033 | -0.068665 | 61.2167 | -61.528 | 61.3403 | -61.1389 | -61.5829 | -61.5967 | -0.004578 | 61.203 | -61.4777 | 61.3678 | -61.3632 | -61.3815 | -61.3861 | -0.10986 | -0.054931 | 0.068665 | 0.27924 | -0.17853 | -0.16479 | -0.068665 | -0.054932 | -0.059509 | -0.068664 | 0.096131 | 0.054932 | 0.032044 | 0.036621 | 0.091553 | 0.09613 | 0.3891 | 122.8683 | 0.11444 | 122.8455 | 122.7448 | 122.6807 | 122.6349 | 122.6212 | -122.7997 | -122.7493 | 122.7585 | 122.7859 | 61.3495 | 61.4136
372.4688 | 122.9645 | -61.409 | 61.2671 | 0.01358 | -0.0087116 | 0.0087885 | 0.06596 | -0.016771 | -0.030531 | -0.025383 | 0.0055542 | -0.0071777 | 0.063335 | 0.050492 | -0.021358 | -0.010314 | -0.01311 | -0.091553 | 61.2396 | -61.5234 | 61.3129 | -61.1755 | -61.5829 | -61.615 | -0.041199 | 61.203 | -61.441 | 61.3495 | -61.3678 | -61.3907 | -61.3724 | -0.11444 | -0.027466 | 0.045776 | 0.23346 | -0.20599 | -0.17395 | -0.091553 | -0.05951 | -0.032043 | -0.064087 | 0.082397 | 0.041199 | 0.036622 | 0.018311 | 0.068665 | 0.050354 | 0.3479 | 122.8363 | 0.073242 | 122.7905 | 122.7631 | 122.644 | 122.6486 | 122.612 | -122.7905 | -122.7081 | 122.7219 | 122.7585 | 61.3174 | 61.3678
374.1875 | 122.9599 | -61.4273 | 61.2991 | 0.0059509 | -0.0080706 | 0.0098565 | 0.064251 | -0.019549 | -0.028608 | -0.024101 | 0.0055542 | -0.0088867 | 0.063121 | 0.042374 | -0.017513 | -0.0088184 | -0.014605 | -0.07782 | 61.2259 | -61.5189 | 61.3312 | -61.1664 | -61.5921 | -61.6013 | -0.027466 | 61.1938 | -61.4685 | 61.3541 | -61.3586 | -61.3953 | -61.377 | -0.091553 | -0.073242 | 0.032044 | 0.26093 | -0.17395 | -0.16479 | -0.082397 | -0.073242 | -0.041199 | -0.10528 | 0.054932 | 0.068664 | 0.050354 | 0.032043 | 0.091553 | 0.073242 | 0.35248 | 122.85 | 0.10986 | 122.8226 | 122.7448 | 122.6624 | 122.6532 | 122.6212 | -122.818 | -122.7676 | 122.7585 | 122.7814 | 61.3495 | 61.3998
375.875 | 122.9141 | -61.4044 | 61.377 | 0.0059509 | -0.009566 | 0.0096429 | 0.06297 | -0.022967 | -0.031599 | -0.024955 | -0.003601 | -0.0080321 | 0.063976 | 0.040665 | -0.021999 | -0.011595 | -0.018237 | 0.013733 | 61.2717 | -61.4639 | 61.4044 | -61.0748 | -61.4822 | -61.528 | 0.054932 | 61.2946 | -61.409 | 61.3815 | -61.3037 | -61.3449 | -61.3586 | -0.059509 | -0.10529 | 0.027466 | 0.32959 | -0.1236 | -0.07782 | -0.064087 | -0.018311 | -0.004578 | -0.082397 | 0.004578 | 0.10071 | 0.045776 | 0.059509 | 0.050354 | 0.064087 | 0.3891 | 122.8683 | 0.10529 | 122.7905 | 122.7356 | 122.7036 | 122.6761 | 122.699 | -122.8409 | -122.7859 | 122.8088 | 122.7859 | 61.4182 | 61.4594
377.5938 | 122.9965 | -61.377 | 61.3312 | 0.01358 | -0.008498 | 0.0096429 | 0.064251 | -0.019549 | -0.029463 | -0.021751 | 0.0055542 | -0.012305 | 0.063976 | 0.047928 | -0.020503 | -0.0101 | -0.014178 | -0.073242 | 61.2396 | -61.4777 | 61.3495 | -61.1389 | -61.5326 | -61.5601 | 0.013733 | 61.2122 | -61.4365 | 61.4227 | -61.2808 | -61.2991 | -61.3129 | -0.10071 | -0.091553 | 0.01831 | 0.23804 | -0.18311 | -0.15564 | -0.082398 | -0.054932 | -0.059509 | -0.11902 | 0.091552 | 0.09613 | 0.064087 | 0.07782 | 0.1236 | 0.13733 | 0.33874 | 122.8271 | 0.15564 | 122.8592 | 122.7173 | 122.6486 | 122.6166 | 122.5891 | -122.8088 | -122.7676 | 122.7264 | 122.7997 | 61.3037 | 61.3907
379.375 | 122.9141 | -61.4319 | 61.3129 | 0.01358 | -0.0076434 | 0.0083613 | 0.064465 | -0.02083 | -0.030317 | -0.024955 | 0.008606 | -0.0063233 | 0.062694 | 0.045579 | -0.022212 | -0.012023 | -0.019946 | -0.027466 | 61.3174 | -61.5005 | 61.3312 | -61.1664 | -61.5738 | -61.5875 | 0.004578 | 61.2808 | -61.4548 | 61.3586 | -61.3541 | -61.3953 | -61.3678 | -0.068664 | 0.004578 | 0.018311 | 0.2655 | -0.15564 | -0.14191 | -0.086975 | -0.073243 | -0.022888 | -0.032043 | 0.045777 | 0.07782 | 0.064087 | 0.036621 | 0.086975 | 0.059509 | 0.33417 | 122.8317 | 0.10071 | 122.8134 | 122.818 | 122.7356 | 122.7493 | 122.7127 | -122.8134 | -122.7676 | 122.7631 | 122.7905 | 61.4044 | 61.4365
381.0781 | 122.8409 | -61.4868 | 61.2946 | 0.0059509 | -0.0072162 | 0.01007 | 0.066388 | -0.01549 | -0.02989 | -0.023887 | -0.00054937 | -0.0065369 | 0.063549 | 0.039597 | -0.02029 | -0.014159 | -0.01546 | -0.09613 | 61.2671 | -61.5463 | 61.2442 | -61.2625 | -61.6974 | -61.6882 | -0.10529 | 61.2259 | -61.4914 | 61.2625 | -61.4731 | -61.4914 | -61.4548 | -0.05951 | -0.027466 | -0.050354 | 0.2243 | -0.20142 | -0.21057 | -0.14191 | -0.15106 | -0.004578 | -0.068665 | -0.032044 | 0.013733 | 0.032043 | -0.004578 | 0.036621 | 0 | 0.28381 | 122.7905 | 0.018311 | 122.7539 | 122.8134 | 122.7173 | 122.7539 | 122.7127 | -122.8409 | -122.7859 | 122.731 | 122.7493 | 61.3907 | 61.3815
382.8594 | 122.9965 | -61.377 | 61.3129 | -0.0016786 | -0.010634 | 0.0085749 | 0.063611 | -0.019976 | -0.02989 | -0.023033 | 0.0025024 | -0.0078185 | 0.062481 | 0.04686 | -0.020931 | -0.011382 | -0.010974 | -0.004578 | 61.2534 | -61.4273 | 61.441 | -61.0519 | -61.4594 | -61.5005 | 0.10071 | 61.2213 | -61.3815 | 61.4456 | -61.235 | -61.2625 | -61.2854 | -0.050354 | -0.059509 | 0.12817 | 0.32501 | -0.1236 | -0.082398 | -0.073242 | -0.032044 | -0.004578 | -0.091553 | 0.13275 | 0.14191 | 0.091553 | 0.11444 | 0.096131 | 0.11902 | 0.37537 | 122.8683 | 0.14649 | 122.8271 | 122.6807 | 122.6028 | 122.6303 | 122.5983 | -122.7402 | -122.6944 | 122.818 | 122.8226 | 61.3724 | 61.4777
384.625 | 122.8729 | -61.3998 | 61.3907 | -0.0016786 | -0.0065754 | 0.0072931 | 0.064038 | -0.023821 | -0.030531 | -0.024528 | -0.003601 | -0.0052551 | 0.062908 | 0.040024 | -0.023067 | -0.013945 | -0.01546 | -0.059509 | 61.322 | -61.4868 | 61.3083 | -61.1801 | -61.5784 | -61.5921 | -0.032043 | 61.3083 | -61.4365 | 61.322 | -61.3724 | -61.3907 | -61.3907 | -0.086975 | -0.068665 | -0.082397 | 0.21973 | -0.19226 | -0.17853 | -0.10529 | -0.091553 | -0.036621 | -0.082397 | -0.068665 | 0.027466 | 0.009155 | 0.009155 | 0.045776 | 0.045776 | 0.3067 | 122.7951 | 0.064087 | 122.7585 | 122.8088 | 122.7448 | 122.7219 | 122.7081 | -122.8775 | -122.8271 | 122.7081 | 122.7219 | 61.3403 | 61.3678
386.3438 | 122.9919 | -61.4502 | 61.2488 | 0.01358 | -0.0093524 | 0.0092157 | 0.065533 | -0.014208 | -0.030745 | -0.023246 | -0.00054937 | -0.0084595 | 0.062267 | 0.041306 | -0.018581 | -0.01245 | -0.019519 | -0.082397 | 61.1664 | -61.528 | 61.3266 | -61.1572 | -61.5875 | -61.5967 | -0.013733 | 61.1572 | -61.4548 | 61.3815 | -61.3541 | -61.3861 | -61.3586 | -0.07782 | -0.082397 | 0.07782 | 0.29297 | -0.14648 | -0.13733 | -0.068665 | -0.059509 | -0.004578 | -0.091552 | 0.13275 | 0.09613 | 0.091552 | 0.064087 | 0.09613 | 0.068665 | 0.37079 | 122.8546 | 0.10071 | 122.8363 | 122.6944 | 122.612 | 122.6166 | 122.6074 | -122.7768 | -122.7036 | 122.7768 | 122.8317 | 61.3678 | 61.4365
388.125 | 122.85 | -61.3998 | 61.377 | 0.0059509 | -0.0091388 | 0.0072931 | 0.062756 | -0.016771 | -0.030317 | -0.021751 | 0.0025024 | -0.0076049 | 0.063121 | 0.04921 | -0.024349 | -0.012664 | -0.013751 | -0.068665 | 61.2762 | -61.4822 | 61.2991 | -61.1801 | -61.5692 | -61.5875 | -0.036621 | 61.3083 | -61.4365 | 61.322 | -61.3724 | -61.3998 | -61.3815 | -0.082398 | -0.10071 | -0.07782 | 0.21973 | -0.18768 | -0.16937 | -0.10529 | -0.086975 | -0.036621 | -0.068664 | -0.054932 | 0.027466 | 0.01831 | 0 | 0.054931 | 0.036621 | 0.30212 | 122.7814 | 0.064087 | 122.7585 | 122.7585 | 122.7448 | 122.6761 | 122.7081 | -122.8592 | -122.8134 | 122.699 | 122.7219 | 61.3312 | 61.3632
389.8281 | 122.8363 | -61.4868 | 61.2946 | 0.01358 | -0.0076434 | 0.0087885 | 0.064038 | -0.01848 | -0.029463 | -0.026023 | 0.0025024 | -0.0071777 | 0.062267 | 0.047928 | -0.018154 | -0.012236 | -0.016314 | -0.10986 | 61.2671 | -61.528 | 61.2122 | -61.2762 | -61.702 | -61.7065 | -0.15564 | 61.2122 | -61.4914 | 61.2534 | -61.4868 | -61.528 | -61.4594 | -0.041199 | -0.027466 | -0.082398 | 0.21057 | -0.21973 | -0.21515 | -0.17853 | -0.17395 | -0.004578 | -0.082398 | -0.041199 | 0 | 0.027465 | -0.041199 | 0.032043 | -0.036621 | 0.25177 | 122.7402 | 0.004578 | 122.7448 | 122.7951 | 122.7036 | 122.7539 | 122.699 | -122.8226 | -122.7859 | 122.699 | 122.7402 | 61.377 | 61.3312
391.5625 | 122.8821 | -61.4594 | 61.2808 | 0.01358 | -0.0082842 | 0.0092157 | 0.064465 | -0.01848 | -0.030745 | -0.026023 | -0.00054937 | -0.0054687 | 0.064617 | 0.04921 | -0.018367 | -0.010741 | -0.014819 | -0.14191 | 61.2488 | -61.5372 | 61.203 | -61.2762 | -61.6882 | -61.6974 | -0.13275 | 61.2259 | -61.4868 | 61.2671 | -61.4639 | -61.4914 | -61.441 | -0.077819 | -0.032044 | -0.07782 | 0.18311 | -0.23804 | -0.22888 | -0.16022 | -0.15106 | -0.027465 | -0.054932 | -0.013733 | -0.004577 | 0.018311 | -0.032043 | 0.045776 | -0.004578 | 0.26093 | 122.7402 | 0.022888 | 122.7539 | 122.7859 | 122.7127 | 122.7081 | 122.6852 | -122.818 | -122.7676 | 122.6624 | 122.7264 | 61.3174 | 61.3266
393.2812 | 122.8683 | -61.4319 | 61.3037 | 0.01358 | -0.0063616 | 0.0094293 | 0.065106 | -0.021471 | -0.031599 | -0.024314 | 0.0055542 | -0.0071777 | 0.061626 | 0.04387 | -0.016017 | -0.011382 | -0.018451 | -0.050354 | 61.2762 | -61.4777 | 61.3037 | -61.1755 | -61.5875 | -61.6058 | -0.027466 | 61.2305 | -61.4227 | 61.3358 | -61.3724 | -61.4365 | -61.3907 | -0.045776 | -0.027466 | 0 | 0.25635 | -0.17395 | -0.15564 | -0.12817 | -0.10986 | 0.009156 | -0.073242 | 0.032043 | 0.05951 | 0.041199 | -0.004577 | 0.032043 | -0.013733 | 0.30212 | 122.7814 | 0.050354 | 122.7585 | 122.7539 | 122.6532 | 122.7081 | 122.6624 | -122.7814 | -122.7264 | 122.7356 | 122.7676 | 61.3815 | 61.4044
395.0469 | 122.905 | -61.4273 | 61.322 | 0.0059509 | -0.0063616 | 0.0072931 | 0.063183 | -0.020617 | -0.03224 | -0.025169 | 0.0025024 | -0.0095275 | 0.065258 | 0.045792 | -0.020076 | -0.010741 | -0.017383 | -0.022888 | 61.29 | -61.4822 | 61.3174 | -61.1389 | -61.5555 | -61.5921 | -0.004578 | 61.235 | -61.4731 | 61.3586 | -61.3312 | -61.3907 | -61.3724 | -0.054932 | -0.032043 | -0.004577 | 0.28839 | -0.16479 | -0.12817 | -0.10986 | -0.073242 | -0.045776 | -0.086975 | 0.036622 | 0.09613 | 0.054932 | 0.036621 | 0.10071 | 0.082397 | 0.34332 | 122.7997 | 0.14191 | 122.8317 | 122.7722 | 122.7081 | 122.7173 | 122.6624 | -122.8043 | -122.7951 | 122.7448 | 122.7859 | 61.4044 | 61.4227
396.75 | 122.9233 | -61.4182 | 61.2854 | 0.02121 | -0.0089252 | 0.0092157 | 0.062329 | -0.019121 | -0.030531 | -0.023887 | 0.0055542 | -0.0093139 | 0.062481 | 0.057328 | -0.019008 | -0.010527 | -0.012469 | -0.086975 | 61.2259 | -61.5097 | 61.3129 | -61.1435 | -61.5738 | -61.5921 | -0.022888 | 61.203 | -61.4502 | 61.3541 | -61.3403 | -61.3815 | -61.3586 | -0.091553 | -0.059509 | 0.027466 | 0.27466 | -0.17395 | -0.15564 | -0.082397 | -0.064087 | -0.032043 | -0.082397 | 0.068665 | 0.07782 | 0.059509 | 0.036621 | 0.091552 | 0.068664 | 0.36621 | 122.8226 | 0.10986 | 122.8043 | 122.7356 | 122.6532 | 122.644 | 122.6212 | -122.7951 | -122.7356 | 122.731 | 122.7722 | 61.3312 | 61.3953
398.5312 | 122.9828 | -61.4227 | 61.235 | 0.0059509 | -0.0070026 | 0.0094293 | 0.066174 | -0.02083 | -0.02989 | -0.021537 | 0.017761 | -0.0091003 | 0.063549 | 0.041092 | -0.016872 | -0.011595 | -0.01311 | -0.068665 | 61.1893 | -61.5234 | 61.3449 | -61.116 | -61.5509 | -61.5738 | 0.022888 | 61.1801 | -61.4685 | 61.377 | -61.322 | -61.3586 | -61.3403 | -0.10071 | -0.045776 | 0.10986 | 0.3067 | -0.15106 | -0.12817 | -0.050355 | -0.027466 | -0.045777 | -0.054931 | 0.14191 | 0.10071 | 0.082397 | 0.064086 | 0.12817 | 0.10986 | 0.40741 | 122.8683 | 0.14648 | 122.8455 | 122.7127 | 122.6486 | 122.612 | 122.6028 | -122.7585 | -122.7036 | 122.7676 | 122.7997 | 61.3541 | 61.4456
400.25 | 122.9828 | -61.441 | 61.2305 | 0.0059509 | -0.0072162 | 0.0090021 | 0.064251 | -0.019335 | -0.029036 | -0.023887 | -0.00054937 | -0.0088867 | 0.063549 | 0.050065 | -0.015377 | -0.011382 | -0.015033 | -0.064087 | 61.1984 | -61.5143 | 61.3174 | -61.1572 | -61.5829 | -61.5967 | -0.004578 | 61.116 | -61.4502 | 61.3861 | -61.3312 | -61.3678 | -61.3586 | -0.073242 | -0.032044 | 0.086975 | 0.28381 | -0.15564 | -0.14191 | -0.082398 | -0.068665 | -0.009155 | -0.11444 | 0.15564 | 0.10986 | 0.082397 | 0.073242 | 0.091552 | 0.082397 | 0.35706 | 122.8317 | 0.11902 | 122.8363 | 122.7127 | 122.5662 | 122.6395 | 122.5571 | -122.7448 | -122.6807 | 122.7585 | 122.8271 | 61.377 | 61.4365
401.9531 | 122.9233 | -61.4273 | 61.2854 | 0.028839 | -0.0076434 | 0.0092157 | 0.064679 | -0.021898 | -0.030317 | -0.025169 | 0.0025024 | -0.010169 | 0.061412 | 0.046006 | -0.019008 | -0.0088184 | -0.011828 | -0.086975 | 61.2259 | -61.5097 | 61.2991 | -61.1664 | -61.5692 | -61.5829 | -0.050354 | 61.1664 | -61.4456 | 61.3403 | -61.3449 | -61.3724 | -61.3449 | -0.082398 | -0.059509 | 0.013733 | 0.26093 | -0.15564 | -0.14191 | -0.073242 | -0.059509 | -0.018311 | -0.11902 | 0.054932 | 0.082397 | 0.082397 | 0.054932 | 0.10071 | 0.073243 | 0.34332 | 122.8088 | 0.10071 | 122.7859 | 122.7356 | 122.612 | 122.6532 | 122.5937 | -122.7951 | -122.731 | 122.7264 | 122.7676 | 61.3403 | 61.377
403.7344 | 122.9279 | -61.4227 | 61.2991 | 0.01358 | -0.0082842 | 0.0072931 | 0.064892 | -0.017626 | -0.028608 | -0.022392 | 0.0025024 | -0.0076049 | 0.063549 | 0.044724 | -0.020076 | -0.010527 | -0.015674 | -0.09613 | 61.2122 | -61.5005 | 61.3037 | -61.1664 | -61.5738 | -61.5784 | -0.054932 | 61.1755 | -61.4319 | 61.3449 | -61.3678 | -61.3861 | -61.3586 | -0.07782 | -0.086975 | 0.004578 | 0.25635 | -0.15564 | -0.15106 | -0.07782 | -0.073243 | -0.009156 | -0.1236 | 0.045777 | 0.054931 | 0.064086 | 0.036621 | 0.073242 | 0.045777 | 0.33417 | 122.8043 | 0.064087 | 122.7768 | 122.7127 | 122.6074 | 122.6349 | 122.5983 | -122.7997 | -122.731 | 122.7264 | 122.7676 | 61.3266 | 61.3678
405.5 | 122.9462 | -61.4502 | 61.2259 | 0.01358 | -0.007857 | 0.0096429 | 0.064892 | -0.015276 | -0.029249 | -0.023033 | 0.0055542 | -0.0058959 | 0.060985 | 0.043442 | -0.017085 | -0.012236 | -0.016955 | -0.15106 | 61.2305 | -61.5509 | 61.2259 | -61.2259 | -61.6653 | -61.6653 | -0.07782 | 61.1618 | -61.4639 | 61.322 | -61.3724 | -61.409 | -61.3724 | -0.10071 | 0.004578 | 0 | 0.2243 | -0.21515 | -0.21515 | -0.11444 | -0.11444 | -0.013733 | -0.064087 | 0.09613 | 0.07782 | 0.07782 | 0.041198 | 0.091553 | 0.054931 | 0.32501 | 122.7768 | 0.091553 | 122.7859 | 122.7814 | 122.6257 | 122.6807 | 122.612 | -122.7768 | -122.6898 | 122.6761 | 122.7722 | 61.2991 | 61.3724
407.2344 | 122.937 | -61.3541 | 61.3266 | 0.0059509 | -0.009566 | 0.0062249 | 0.06297 | -0.019549 | -0.030745 | -0.023246 | -0.00054937 | -0.0095275 | 0.063121 | 0.048356 | -0.02264 | -0.011168 | -0.016742 | 0.009155 | 61.2396 | -61.4365 | 61.3998 | -61.0474 | -61.4594 | -61.4914 | 0.082397 | 61.2305 | -61.3815 | 61.409 | -61.2442 | -61.2854 | -61.2808 | -0.082397 | -0.086975 | 0.073242 | 0.3067 | -0.13733 | -0.10529 | -0.054932 | -0.022889 | -0.027466 | -0.09613 | 0.082398 | 0.10986 | 0.073242 | 0.068665 | 0.10071 | 0.096131 | 0.3891 | 122.8363 | 0.13733 | 122.7905 | 122.6761 | 122.612 | 122.5937 | 122.5845 | -122.7631 | -122.7081 | 122.7539 | 122.7631 | 61.3632 | 61.4365
409.0156 | 122.8317 | -61.4182 | 61.3724 | -0.0016786 | -0.0087116 | 0.0066523 | 0.064892 | -0.021044 | -0.031172 | -0.023674 | 0.0055542 | -0.0086731 | 0.063762 | 0.039597 | -0.023494 | -0.013518 | -0.013751 | -0.045776 | 61.3129 | -61.4548 | 61.2854 | -61.171 | -61.5646 | -61.5875 | -0.041199 | 61.2717 | -61.3815 | 61.3129 | -61.3541 | -61.3861 | -61.3724 | -0.036621 | -0.059509 | -0.086975 | 0.24719 | -0.16937 | -0.14648 | -0.13275 | -0.10986 | 0.036621 | -0.10071 | -0.059509 | 0.064087 | 0.045777 | 0.032044 | 0.009156 | -0.004577 | 0.28381 | 122.7402 | 0.027466 | 122.6944 | 122.7676 | 122.6532 | 122.731 | 122.6898 | -122.8271 | -122.7539 | 122.7036 | 122.731 | 61.3724 | 61.377
410.7969 | 122.905 | -61.4182 | 61.2946 | 0.028839 | -0.011275 | 0.0098565 | 0.06297 | -0.020189 | -0.027327 | -0.024314 | 0.008606 | -0.0093139 | 0.062267 | 0.047928 | -0.020717 | -0.013518 | -0.015674 | -0.09613 | 61.2259 | -61.496 | 61.2946 | -61.171 | -61.5692 | -61.5921 | -0.050354 | 61.2076 | -61.4548 | 61.3358 | -61.3403 | -61.3632 | -61.3541 | -0.07782 | -0.068665 | 0 | 0.24719 | -0.17395 | -0.15106 | -0.09613 | -0.073242 | -0.036621 | -0.086975 | 0.041198 | 0.07782 | 0.064087 | 0.054932 | 0.10071 | 0.091553 | 0.32501 | 122.7905 | 0.11444 | 122.7905 | 122.7219 | 122.6624 | 122.644 | 122.6257 | -122.7905 | -122.7493 | 122.7127 | 122.7539 | 61.322 | 61.3678
412.5938 | 122.9782 | -61.4182 | 61.2076 | 0.01358 | -0.0065754 | 0.0079339 | 0.06532 | -0.018694 | -0.028608 | -0.023887 | 0.0025024 | -0.0097411 | 0.063335 | 0.04451 | -0.019649 | -0.0086048 | -0.016101 | -0.068665 | 61.1526 | -61.5097 | 61.3312 | -61.1343 | -61.5738 | -61.5921 | -0.018311 | 61.1481 | -61.4365 | 61.3678 | -61.3403 | -61.3586 | -61.3403 | -0.091553 | -0.054932 | 0.1236 | 0.28381 | -0.17395 | -0.15564 | -0.082397 | -0.064087 | -0.01831 | -0.05951 | 0.16022 | 0.07782 | 0.07782 | 0.059509 | 0.09613 | 0.077819 | 0.37537 | 122.8409 | 0.09613 | 122.8043 | 122.6624 | 122.5845 | 122.5708 | 122.5662 | -122.7173 | -122.644 | 122.7493 | 122.7859 | 61.3495 | 61.3998
414.3125 | 122.9599 | -61.4456 | 61.2396 | 0.01358 | -0.0074298 | 0.010925 | 0.06532 | -0.018908 | -0.030531 | -0.022605 | -0.00054937 | -0.0088867 | 0.064403 | 0.044083 | -0.017513 | -0.0079638 | -0.016314 | -0.09613 | 61.1984 | -61.5143 | 61.3037 | -61.1618 | -61.6013 | -61.6104 | 0 | 61.1435 | -61.4548 | 61.3495 | -61.3541 | -61.3586 | -61.3266 | -0.068664 | -0.041199 | 0.064087 | 0.28381 | -0.16479 | -0.15564 | -0.096131 | -0.086975 | -0.009155 | -0.09613 | 0.10986 | 0.091553 | 0.11902 | 0.086975 | 0.12817 | 0.09613 | 0.35248 | 122.818 | 0.10071 | 122.8043 | 122.7127 | 122.5983 | 122.644 | 122.5891 | -122.7539 | -122.6944 | 122.7493 | 122.7951 | 61.3495 | 61.4456
416.0781 | 122.9507 | -61.4456 | 61.2396 | -0.0016786 | -0.0072162 | 0.0092157 | 0.068738 | -0.016771 | -0.02989 | -0.02346 | 0.0025024 | -0.0065369 | 0.062267 | 0.047501 | -0.018154 | -0.0096728 | -0.014392 | -0.13275 | 61.235 | -61.5234 | 61.2396 | -61.2076 | -61.6425 | -61.647 | -0.054932 | 61.1572 | -61.4639 | 61.322 | -61.3403 | -61.3907 | -61.3586 | -0.077819 | -0.004578 | 0 | 0.23804 | -0.20142 | -0.19684 | -0.1236 | -0.11902 | -0.01831 | -0.082397 | 0.082397 | 0.10529 | 0.086975 | 0.054932 | 0.10529 | 0.073242 | 0.31586 | 122.7631 | 0.1236 | 122.7859 | 122.7585 | 122.6212 | 122.6807 | 122.6028 | -122.7631 | -122.7036 | 122.6852 | 122.7676 | 61.3129 | 61.3907
417.8438 | 122.9187 | -61.409 | 61.2671 | 0.0059509 | -0.0097796 | 0.0081477 | 0.065106 | -0.019335 | -0.02989 | -0.023674 | 0.0055542 | -0.0073913 | 0.062481 | 0.04921 | -0.020717 | -0.009032 | -0.017596 | -0.086975 | 61.203 | -61.5097 | 61.3083 | -61.1618 | -61.5692 | -61.5692 | -0.032043 | 61.1755 | -61.4456 | 61.3449 | -61.3449 | -61.3632 | -61.3495 | -0.10071 | -0.064087 | 0.041199 | 0.24719 | -0.16022 | -0.16022 | -0.059509 | -0.059509 | -0.036621 | -0.091553 | 0.07782 | 0.064087 | 0.05951 | 0.045777 | 0.096131 | 0.082398 | 0.3479 | 122.818 | 0.10071 | 122.7905 | 122.7127 | 122.6212 | 122.612 | 122.5845 | -122.7768 | -122.7127 | 122.7173 | 122.7539 | 61.322 | 61.377
419.6406 | 122.9507 | -61.3632 | 61.3083 | 0.02121 | -0.0097796 | 0.0062249 | 0.063397 | -0.021044 | -0.029036 | -0.025596 | -0.00054937 | -0.0091003 | 0.06184 | 0.04152 | -0.023708 | -0.011382 | -0.015033 | 0.009155 | 61.235 | -61.4548 | 61.409 | -61.0245 | -61.4639 | -61.4914 | 0.091553 | 61.2076 | -61.3953 | 61.4182 | -61.2259 | -61.2717 | -61.2579 | -0.091553 | -0.073243 | 0.10071 | 0.33874 | -0.12817 | -0.10071 | -0.036621 | -0.009155 | -0.032044 | -0.10071 | 0.10986 | 0.13733 | 0.10528 | 0.091553 | 0.13733 | 0.1236 | 0.4303 | 122.8638 | 0.16937 | 122.8134 | 122.6898 | 122.6028 | 122.5983 | 122.5708 | -122.7631 | -122.7036 | 122.7722 | 122.7814 | 61.3724 | 61.4548
421.3438 | 122.8912 | -61.4685 | 61.2579 | -0.0016786 | -0.0087116 | 0.0083613 | 0.065106 | -0.01848 | -0.029036 | -0.024101 | -0.00054937 | -0.0067505 | 0.062053 | 0.046219 | -0.019435 | -0.013304 | -0.014819 | -0.12817 | 61.2442 | -61.5234 | 61.2076 | -61.2671 | -61.6837 | -61.6791 | -0.10986 | 61.1664 | -61.4731 | 61.2762 | -61.4044 | -61.441 | -61.4044 | -0.054931 | -0.013733 | -0.050354 | 0.20142 | -0.21057 | -0.21515 | -0.15564 | -0.16022 | -0.004577 | -0.091553 | 0.01831 | 0.064087 | 0.064087 | 0.027466 | 0.068664 | 0.032043 | 0.25635 | 122.731 | 0.068664 | 122.7493 | 122.7676 | 122.6395 | 122.7127 | 122.6349 | -122.7814 | -122.731 | 122.6761 | 122.7448 | 61.3403 | 61.3586
423.125 | 122.9462 | -61.441 | 61.2305 | 0.01358 | -0.0072162 | 0.0096429 | 0.068738 | -0.017626 | -0.028395 | -0.022392 | -0.00054937 | -0.0086731 | 0.062053 | 0.047288 | -0.01794 | -0.010314 | -0.016101 | -0.11902 | 61.2076 | -61.5417 | 61.2671 | -61.1893 | -61.6241 | -61.6196 | -0.027466 | 61.1481 | -61.4639 | 61.3449 | -61.3449 | -61.3678 | -61.3266 | -0.10071 | -0.022888 | 0.036621 | 0.25177 | -0.17853 | -0.18311 | -0.07782 | -0.082398 | -0.022888 | -0.082398 | 0.11444 | 0.09613 | 0.11444 | 0.073242 | 0.13733 | 0.09613 | 0.35248 | 122.8088 | 0.11902 | 122.8088 | 122.7493 | 122.612 | 122.6486 | 122.5891 | -122.7722 | -122.6944 | 122.7081 | 122.7859 | 61.322 | 61.4136
424.8906 | 122.8775 | -61.409 | 61.322 | 0.01358 | -0.007857 | 0.0068659 | 0.065533 | -0.018053 | -0.027754 | -0.023674 | 0.008606 | -0.0061095 | 0.063549 | 0.041733 | -0.023494 | -0.010527 | -0.01781 | -0.036621 | 61.2671 | -61.4868 | 61.322 | -61.1435 | -61.5601 | -61.5692 | 0.018311 | 61.2167 | -61.441 | 61.3403 | -61.3358 | -61.3861 | -61.3403 | -0.077819 | -0.054931 | 0 | 0.2655 | -0.16022 | -0.15106 | -0.082398 | -0.073243 | -0.032043 | -0.10529 | 0.018311 | 0.073243 | 0.068665 | 0.022889 | 0.10071 | 0.054932 | 0.34332 | 122.8088 | 0.10529 | 122.7814 | 122.7539 | 122.6578 | 122.6761 | 122.6257 | -122.8088 | -122.7631 | 122.731 | 122.7493 | 61.3724 | 61.4273
426.6719 | 122.9187 | -61.441 | 61.235 | 0.0059509 | -0.0076434 | 0.0079339 | 0.06532 | -0.021044 | -0.028822 | -0.023887 | 0.0025024 | -0.0067505 | 0.063549 | 0.041306 | -0.019435 | -0.011168 | -0.014819 | -0.14648 | 61.2122 | -61.5417 | 61.2213 | -61.2213 | -61.6608 | -61.6608 | -0.068665 | 61.1481 | -61.4594 | 61.3266 | -61.3678 | -61.3998 | -61.3541 | -0.10071 | -0.022888 | -0.013733 | 0.21973 | -0.21973 | -0.21973 | -0.11902 | -0.11902 | -0.018311 | -0.086975 | 0.091553 | 0.073242 | 0.086975 | 0.041199 | 0.10529 | 0.05951 | 0.32043 | 122.7631 | 0.091553 | 122.7859 | 122.7539 | 122.6074 | 122.6532 | 122.5891 | -122.7768 | -122.6944 | 122.6624 | 122.7676 | 61.2946 | 61.3724
428.3906 | 122.9233 | -61.4365 | 61.2305 | 0.01358 | -0.0080706 | 0.0094293 | 0.064892 | -0.018053 | -0.030745 | -0.022178 | 0.0025024 | -0.0082459 | 0.063762 | 0.045365 | -0.019863 | -0.011595 | -0.009692 | -0.16022 | 61.1938 | -61.5509 | 61.2396 | -61.2167 | -61.6287 | -61.6425 | -0.082397 | 61.1526 | -61.4594 | 61.3266 | -61.3678 | -61.4182 | -61.3678 | -0.11444 | -0.036621 | 0.009155 | 0.21973 | -0.20599 | -0.19226 | -0.091553 | -0.07782 | -0.022889 | -0.07782 | 0.09613 | 0.068664 | 0.068664 | 0.01831 | 0.091553 | 0.041199 | 0.33417 | 122.7905 | 0.091553 | 122.7859 | 122.7448 | 122.612 | 122.6303 | 122.5891 | -122.7814 | -122.6898 | 122.6761 | 122.7631 | 61.2762 | 61.3541
430.1094 | 122.8867 | -61.4136 | 61.2808 | 0.01358 | -0.011061 | 0.0092157 | 0.063824 | -0.019762 | -0.028395 | -0.022819 | 0.008606 | -0.0078185 | 0.062267 | 0.042588 | -0.020503 | -0.0101 | -0.019732 | -0.086975 | 61.2167 | -61.4731 | 61.2854 | -61.1526 | -61.5646 | -61.5829 | -0.041199 | 61.171 | -61.4273 | 61.3174 | -61.3358 | -61.3586 | -61.3449 | -0.059509 | -0.064087 | 0.004577 | 0.26093 | -0.16937 | -0.15106 | -0.10986 | -0.091553 | -0.013733 | -0.10986 | 0.036621 | 0.07782 | 0.068664 | 0.054931 | 0.082397 | 0.068664 | 0.32043 | 122.7585 | 0.091553 | 122.7448 | 122.6898 | 122.5983 | 122.6303 | 122.5845 | -122.7539 | -122.7081 | 122.699 | 122.731 | 61.3266 | 61.3724
431.875 | 122.9279 | -61.3495 | 61.3174 | -0.0016786 | -0.0097796 | 0.0068659 | 0.06297 | -0.020189 | -0.032454 | -0.021324 | 0.0025024 | -0.0078185 | 0.060772 | 0.050065 | -0.020717 | -0.011809 | -0.012042 | 0.009155 | 61.2305 | -61.441 | 61.3953 | -61.0382 | -61.4502 | -61.4822 | 0.091553 | 61.2167 | -61.3678 | 61.409 | -61.2396 | -61.2579 | -61.2717 | -0.091553 | -0.086975 | 0.07782 | 0.31128 | -0.13275 | -0.10071 | -0.041199 | -0.009155 | -0.018311 | -0.10071 | 0.091553 | 0.10986 | 0.07782 | 0.091552 | 0.096131 | 0.10986 | 0.40283 | 122.8363 | 0.12817 | 122.7768 | 122.6715 | 122.5845 | 122.58 | 122.5662 | -122.7585 | -122.6852 | 122.7448 | 122.7585 | 61.3586 | 61.441
433.6719 | 122.8134 | -61.4319 | 61.2671 | 0.01358 | -0.006148 | 0.011138 | 0.065106 | -0.015917 | -0.030317 | -0.026664 | 0.0055542 | -0.0052551 | 0.062694 | 0.04921 | -0.020717 | -0.010741 | -0.013965 | -0.10529 | 61.2305 | -61.5051 | 61.2122 | -61.2488 | -61.6516 | -61.6653 | -0.11902 | 61.1847 | -61.4639 | 61.2396 | -61.4502 | -61.4914 | -61.4182 | -0.073242 | -0.036621 | -0.054932 | 0.18311 | -0.23346 | -0.21973 | -0.16022 | -0.14648 | -0.032043 | -0.082398 | -0.027466 | -0.01831 | 0.013733 | -0.059509 | 0.045776 | -0.027466 | 0.25635 | 122.7173 | 0.013733 | 122.7036 | 122.7356 | 122.6486 | 122.6624 | 122.6166 | -122.7722 | -122.731 | 122.644 | 122.6715 | 61.3266 | 61.3129
435.3906 | 122.9553 | -61.4273 | 61.1984 | 0.0059509 | -0.0091388 | 0.0096429 | 0.064465 | -0.013994 | -0.028608 | -0.022605 | 0.0025024 | -0.0093139 | 0.06483 | 0.045151 | -0.018794 | -0.0094592 | -0.016742 | -0.07782 | 61.1618 | -61.5005 | 61.3083 | -61.1298 | -61.5692 | -61.5784 | 0.004578 | 61.116 | -61.4365 | 61.3495 | -61.322 | -61.3495 | -61.3266 | -0.073242 | -0.036621 | 0.10986 | 0.29755 | -0.15106 | -0.14191 | -0.07782 | -0.068665 | -0.009155 | -0.082397 | 0.15106 | 0.10529 | 0.10071 | 0.07782 | 0.10986 | 0.086975 | 0.37079 | 122.8088 | 0.11444 | 122.7859 | 122.6624 | 122.5525 | 122.5891 | 122.5433 | -122.699 | -122.6349 | 122.7356 | 122.7768 | 61.3495 | 61.4319
437.1719 | 122.8134 | -61.441 | 61.2534 | -0.0016786 | -0.0057208 | 0.0083613 | 0.065533 | -0.015917 | -0.030531 | -0.025169 | 0.0025024 | -0.0069641 | 0.063335 | 0.043656 | -0.021572 | -0.011382 | -0.016528 | -0.09613 | 61.2442 | -61.5051 | 61.203 | -61.2305 | -61.6562 | -61.6837 | -0.12817 | 61.2167 | -61.4456 | 61.2396 | -61.4456 | -61.496 | -61.4182 | -0.064087 | -0.009155 | -0.050354 | 0.21057 | -0.24262 | -0.21515 | -0.17853 | -0.15106 | -0.004578 | -0.036621 | -0.013733 | -0.004578 | 0.022888 | -0.054932 | 0.027466 | -0.050354 | 0.27466 | 122.7081 | 0 | 122.6852 | 122.7493 | 122.6624 | 122.6852 | 122.6578 | -122.7585 | -122.699 | 122.644 | 122.6807 | 61.3449 | 61.3129
438.9531 | 122.8592 | -61.3861 | 61.2991 | 0.036468 | -0.0076434 | 0.0085749 | 0.066388 | -0.016985 | -0.030531 | -0.021537 | 0.008606 | -0.0054687 | 0.063549 | 0.040452 | -0.023494 | -0.011595 | -0.017383 | -0.041199 | 61.2991 | -61.4822 | 61.2854 | -61.1526 | -61.5372 | -61.5692 | -0.018311 | 61.2442 | -61.4273 | 61.3449 | -61.322 | -61.3632 | -61.3266 | -0.096131 | 0 | -0.013733 | 0.23346 | -0.18311 | -0.15106 | -0.086975 | -0.054931 | -0.041199 | -0.054931 | 0.045777 | 0.064087 | 0.059509 | 0.022888 | 0.10071 | 0.064087 | 0.32959 | 122.7676 | 0.10529 | 122.7722 | 122.7814 | 122.6715 | 122.6852 | 122.6303 | -122.7814 | -122.7264 | 122.6715 | 122.731 | 61.3449 | 61.3678
440.6719 | 122.8912 | -61.409 | 61.2717 | 0.01358 | -0.0074298 | 0.0077203 | 0.065106 | -0.022967 | -0.031813 | -0.022392 | 0.0055542 | -0.0091003 | 0.063121 | 0.045151 | -0.020076 | -0.010955 | -0.013751 | -0.086975 | 61.2305 | -61.4822 | 61.2854 | -61.1298 | -61.5555 | -61.5646 | -0.041199 | 61.1664 | -61.4319 | 61.3129 | -61.3312 | -61.3541 | -61.3312 | -0.073242 | -0.041198 | 0.013733 | 0.27924 | -0.15564 | -0.14648 | -0.082397 | -0.073242 | -0.022888 | -0.10529 | 0.041199 | 0.07782 | 0.07782 | 0.054932 | 0.10071 | 0.07782 | 0.35248 | 122.7676 | 0.10071 | 122.7448 | 122.7127 | 122.5983 | 122.6395 | 122.5754 | -122.7539 | -122.7036 | 122.6944 | 122.7219 | 61.322 | 61.3678
442.375 | 122.8409 | -61.3907 | 61.3312 | 0.01358 | -0.0072162 | 0.0066523 | 0.065106 | -0.020403 | -0.030531 | -0.024955 | 0.008606 | -0.0076049 | 0.064617 | 0.040879 | -0.021785 | -0.011382 | -0.013537 | -0.036621 | 61.3083 | -61.4731 | 61.2762 | -61.171 | -61.5463 | -61.5646 | -0.041199 | 61.2671 | -61.3998 | 61.3266 | -61.3358 | -61.3724 | -61.3312 | -0.082397 | -0.022888 | -0.054932 | 0.21973 | -0.17395 | -0.15564 | -0.091553 | -0.073243 | -0.009155 | -0.064087 | -0.004578 | 0.054932 | 0.059509 | 0.018311 | 0.068664 | 0.027466 | 0.30212 | 122.7493 | 0.064087 | 122.7264 | 122.7814 | 122.6669 | 122.699 | 122.6578 | -122.8043 | -122.731 | 122.6669 | 122.7173 | 61.3541 | 61.3495
444.1406 | 122.8134 | -61.3861 | 61.3495 | 0.0059509 | -0.0097796 | 0.0092157 | 0.065747 | -0.021471 | -0.030745 | -0.024528 | -0.00054937 | -0.0078185 | 0.060344 | 0.041092 | -0.023067 | -0.013732 | -0.013751 | -0.073242 | 61.3129 | -61.4502 | 61.2671 | -61.1664 | -61.5417 | -61.5692 | -0.050354 | 61.2854 | -61.3815 | 61.2854 | -61.3403 | -61.3724 | -61.3541 | -0.064087 | -0.036621 | -0.082397 | 0.21973 | -0.18311 | -0.15564 | -0.11902 | -0.091553 | 0.004577 | -0.064087 | -0.064087 | 0.045776 | 0.032043 | 0.013733 | 0.027466 | 0.009156 | 0.28381 | 122.7173 | 0.041199 | 122.6669 | 122.7631 | 122.6669 | 122.699 | 122.6715 | -122.7997 | -122.731 | 122.6532 | 122.6715 | 61.3129 | 61.3358
445.9062 | 122.9279 | -61.3174 | 61.2991 | 0.0059509 | -0.006789 | 0.0098565 | 0.06297 | -0.018908 | -0.031172 | -0.025169 | -0.00054937 | -0.010596 | 0.062908 | 0.047715 | -0.020076 | -0.011382 | -0.02016 | 0.013733 | 61.2396 | -61.3861 | 61.3815 | -61.0291 | -61.441 | -61.4731 | 0.09613 | 61.171 | -61.3541 | 61.409 | -61.2167 | -61.2396 | -61.235 | -0.068664 | -0.059509 | 0.082398 | 0.28839 | -0.15564 | -0.1236 | -0.086975 | -0.054932 | -0.036621 | -0.12817 | 0.10986 | 0.10071 | 0.082398 | 0.07782 | 0.11902 | 0.11444 | 0.35706 | 122.7676 | 0.13733 | 122.7631 | 122.6257 | 122.525 | 122.5571 | 122.4884 | -122.6852 | -122.6532 | 122.699 | 122.7264 | 61.3312 | 61.4136
447.6719 | 122.9416 | -61.3358 | 61.2762 | 0.01358 | -0.011275 | 0.0087885 | 0.06297 | -0.023394 | -0.032667 | -0.023674 | 0.0055542 | -0.0078185 | 0.060344 | 0.042588 | -0.021144 | -0.011595 | -0.01546 | -0.059509 | 61.2076 | -61.4639 | 61.3403 | -61.0794 | -61.4731 | -61.4914 | 0.050354 | 61.1755 | -61.3907 | 61.3953 | -61.2396 | -61.2534 | -61.2534 | -0.12817 | -0.068664 | 0.064087 | 0.25635 | -0.15564 | -0.13733 | -0.027466 | -0.009155 | -0.054932 | -0.10071 | 0.11902 | 0.09613 | 0.082397 | 0.082397 | 0.13733 | 0.13733 | 0.38452 | 122.8043 | 0.15106 | 122.7859 | 122.6715 | 122.5662 | 122.5433 | 122.5113 | -122.7402 | -122.6669 | 122.6761 | 122.731 | 61.2762 | 61.3861
449.4531 | 122.85 | -61.3724 | 61.2991 | -0.0016786 | -0.0070026 | 0.011138 | 0.067242 | -0.021685 | -0.029249 | -0.023887 | 0.008606 | -0.0063233 | 0.062694 | 0.041947 | -0.021999 | -0.0096728 | -0.018878 | -0.036621 | 61.2625 | -61.4777 | 61.3083 | -61.1206 | -61.5417 | -61.5692 | 0.022888 | 61.1893 | -61.4136 | 61.3266 | -61.3174 | -61.3724 | -61.3586 | -0.10529 | -0.036621 | 0.009156 | 0.25177 | -0.19684 | -0.16937 | -0.091553 | -0.064087 | -0.041199 | -0.10986 | 0.027466 | 0.054931 | 0.013732 | 0 | 0.054931 | 0.041199 | 0.35706 | 122.7859 | 0.09613 | 122.7402 | 122.7402 | 122.6028 | 122.6349 | 122.5616 | -122.7768 | -122.7127 | 122.6807 | 122.699 | 61.3358 | 61.3953
451.1719 | 122.8775 | -61.441 | 61.2305 | 0.0059509 | -0.0059344 | 0.0096429 | 0.065747 | -0.020403 | -0.030317 | -0.025383 | 0.0025024 | -0.0063233 | 0.063762 | 0.042801 | -0.02029 | -0.0081774 | -0.017596 | -0.13733 | 61.2305 | -61.5097 | 61.2076 | -61.2305 | -61.6653 | -61.6745 | -0.09613 | 61.1755 | -61.4548 | 61.29 | -61.3953 | -61.409 | -61.3678 | -0.068665 | 0 | -0.022888 | 0.21057 | -0.23346 | -0.2243 | -0.1648 | -0.15564 | -0.013733 | -0.054932 | 0.059509 | 0.045776 | 0.073242 | 0.032043 | 0.086975 | 0.045776 | 0.27924 | 122.7173 | 0.059509 | 122.7448 | 122.7402 | 122.6303 | 122.6715 | 122.6166 | -122.7402 | -122.6852 | 122.6486 | 122.731 | 61.3037 | 61.3449
452.9375 | 122.937 | -61.3358 | 61.29 | 0.0059509 | -0.0091388 | 0.0068659 | 0.064038 | -0.019976 | -0.029249 | -0.023674 | 0.0025024 | -0.0073913 | 0.06184 | 0.053696 | -0.021358 | -0.012023 | -0.014392 | 0.004578 | 61.2259 | -61.4227 | 61.3861 | -61.0245 | -61.4319 | -61.4731 | 0.11444 | 61.1984 | -61.3495 | 61.4136 | -61.2076 | -61.2488 | -61.2442 | -0.086975 | -0.064087 | 0.09613 | 0.31128 | -0.13733 | -0.096131 | -0.050354 | -0.009156 | -0.013733 | -0.091553 | 0.1236 | 0.12817 | 0.091552 | 0.086975 | 0.10529 | 0.10071 | 0.39825 | 122.8088 | 0.14191 | 122.7631 | 122.6486 | 122.5479 | 122.5616 | 122.5342 | -122.7127 | -122.6395 | 122.7219 | 122.7493 | 61.3403 | 61.4502
454.6562 | 122.9095 | -61.3358 | 61.2854 | 0.0059509 | -0.008498 | 0.0090021 | 0.06297 | -0.016131 | -0.030317 | -0.025169 | -0.00054937 | -0.011237 | 0.061412 | 0.046433 | -0.021572 | -0.0098864 | -0.014392 | -0.009155 | 61.2259 | -61.4227 | 61.3998 | -60.997 | -61.409 | -61.4502 | 0.11444 | 61.1984 | -61.3449 | 61.4044 | -61.203 | -61.235 | -61.2534 | -0.086975 | -0.059509 | 0.11444 | 0.33875 | -0.11444 | -0.073243 | -0.027466 | 0.013732 | -0.009156 | -0.086975 | 0.11902 | 0.13275 | 0.082397 | 0.10071 | 0.091553 | 0.10986 | 0.42572 | 122.8226 | 0.14191 | 122.7493 | 122.6486 | 122.5433 | 122.5616 | 122.5342 | -122.7081 | -122.6303 | 122.7356 | 122.7402 | 61.3266 | 61.4502
456.3594 | 122.9187 | -61.3358 | 61.3037 | -0.0016786 | -0.0087116 | 0.0092157 | 0.064038 | -0.022326 | -0.029249 | -0.023033 | 0.0025024 | -0.0088867 | 0.064403 | 0.04387 | -0.02264 | -0.0092456 | -0.01781 | -0.004578 | 61.2122 | -61.4227 | 61.3861 | -61.0062 | -61.4273 | -61.4639 | 0.10071 | 61.2076 | -61.377 | 61.409 | -61.2076 | -61.2488 | -61.235 | -0.086975 | -0.091553 | 0.082397 | 0.32959 | -0.12817 | -0.091553 | -0.041199 | -0.004578 | -0.041199 | -0.09613 | 0.10529 | 0.12817 | 0.10071 | 0.086975 | 0.14191 | 0.12817 | 0.41656 | 122.8088 | 0.16937 | 122.7859 | 122.6349 | 122.5845 | 122.5479 | 122.5433 | -122.7264 | -122.6807 | 122.7219 | 122.7448 | 61.3312 | 61.4365
458.125 | 122.8088 | -61.3724 | 61.3174 | -0.0093076 | -0.0072162 | 0.0085749 | 0.06532 | -0.018694 | -0.032667 | -0.024528 | 0.0055542 | -0.0080321 | 0.059703 | 0.045365 | -0.021358 | -0.011809 | -0.014605 | -0.009155 | 61.2625 | -61.4273 | 61.3037 | -61.1114 | -61.5189 | -61.528 | 0.013733 | 61.2488 | -61.3907 | 61.2991 | -61.3266 | -61.3541 | -61.3358 | -0.054932 | -0.054932 | -0.013733 | 0.26093 | -0.15564 | -0.14648 | -0.10071 | -0.091553 | -0.018311 | -0.068665 | -0.018311 | 0.045776 | 0.036621 | 0.01831 | 0.054932 | 0.036621 | 0.31586 | 122.731 | 0.064087 | 122.6898 | 122.6898 | 122.6395 | 122.6349 | 122.6212 | -122.7448 | -122.7081 | 122.6761 | 122.6715 | 61.3632 | 61.3861
459.8281 | 122.8088 | -61.3632 | 61.322 | -0.0016786 | -0.0097796 | 0.010284 | 0.064465 | -0.023821 | -0.030531 | -0.026878 | 0.0055542 | -0.0069641 | 0.062053 | 0.042801 | -0.021572 | -0.013518 | -0.016528 | -0.022888 | 61.2762 | -61.4319 | 61.2854 | -61.1343 | -61.528 | -61.5509 | -0.032043 | 61.2717 | -61.3632 | 61.3037 | -61.3312 | -61.3678 | -61.3495 | -0.068665 | -0.045776 | -0.036621 | 0.22888 | -0.18768 | -0.1648 | -0.11902 | -0.09613 | 0 | -0.050354 | -0.01831 | 0.032043 | 0.013733 | -0.004578 | 0.013733 | -0.004578 | 0.29755 | 122.7173 | 0.032043 | 122.6669 | 122.7081 | 122.6349 | 122.6395 | 122.6349 | -122.7539 | -122.6852 | 122.6486 | 122.6669 | 61.3403 | 61.3312
461.5938 | 122.9141 | -61.3541 | 61.2808 | -0.0016786 | -0.009566 | 0.0081477 | 0.063611 | -0.021685 | -0.031813 | -0.023674 | 0.0055542 | -0.0091003 | 0.062694 | 0.04686 | -0.020717 | -0.011809 | -0.015246 | 0 | 61.2213 | -61.4182 | 61.3815 | -61.0107 | -61.4365 | -61.4685 | 0.082397 | 61.2122 | -61.3678 | 61.4136 | -61.2167 | -61.2488 | -61.2671 | -0.064087 | -0.05951 | 0.10071 | 0.34332 | -0.11444 | -0.082397 | -0.050354 | -0.01831 | -0.013733 | -0.068665 | 0.13275 | 0.13733 | 0.086975 | 0.10529 | 0.10071 | 0.11902 | 0.40741 | 122.7997 | 0.15106 | 122.7814 | 122.6395 | 122.58 | 122.5754 | 122.5662 | -122.699 | -122.6486 | 122.7356 | 122.7676 | 61.3541 | 61.4365
463.3125 | 122.8958 | -61.3724 | 61.2213 | 0.028839 | -0.007857 | 0.0090021 | 0.066388 | -0.014422 | -0.02989 | -0.025596 | 0.014709 | -0.0080321 | 0.063976 | 0.040452 | -0.018154 | -0.010741 | -0.016955 | -0.059509 | 61.1526 | -61.4731 | 61.3129 | -61.0977 | -61.5372 | -61.5555 | 0.032043 | 61.1389 | -61.4182 | 61.3541 | -61.3129 | -61.3495 | -61.3174 | -0.10071 | -0.068664 | 0.091553 | 0.27466 | -0.18311 | -0.1648 | -0.082398 | -0.064087 | -0.045777 | -0.082397 | 0.13275 | 0.059509 | 0.054931 | 0.022888 | 0.10071 | 0.068665 | 0.37537 | 122.7859 | 0.10529 | 122.7722 | 122.6257 | 122.5571 | 122.525 | 122.5113 | -122.6944 | -122.6395 | 122.6852 | 122.7264 | 61.3129 | 61.4044
465.0938 | 122.7997 | -61.3632 | 61.3037 | 0.0059509 | -0.010207 | 0.0077203 | 0.064251 | -0.022967 | -0.029676 | -0.025596 | 0.0025024 | -0.0063233 | 0.064403 | 0.042801 | -0.020931 | -0.011809 | -0.015674 | 0.009155 | 61.2625 | -61.4227 | 61.3266 | -61.1023 | -61.4914 | -61.5234 | 0.013733 | 61.2488 | -61.3907 | 61.3083 | -61.2991 | -61.3358 | -61.322 | -0.059509 | -0.041199 | 0.022888 | 0.26093 | -0.16022 | -0.12817 | -0.10071 | -0.068665 | -0.027466 | -0.054932 | 0.004578 | 0.064087 | 0.041199 | 0.027466 | 0.068665 | 0.054932 | 0.32043 | 122.7493 | 0.091553 | 122.699 | 122.6852 | 122.6395 | 122.6257 | 122.612 | -122.7264 | -122.6944 | 122.6898 | 122.6715 | 61.3724 | 61.377
466.7969 | 122.9187 | -61.3953 | 61.2167 | 0.028839 | -0.0074298 | 0.012207 | 0.066174 | -0.02083 | -0.028822 | -0.023033 | 0.011658 | -0.0080321 | 0.063335 | 0.04921 | -0.017299 | -0.0092456 | -0.018451 | -0.068665 | 61.1755 | -61.5005 | 61.3037 | -61.084 | -61.5326 | -61.5463 | 0.032043 | 61.1389 | -61.4456 | 61.3541 | -61.3083 | -61.3449 | -61.3174 | -0.10529 | -0.041199 | 0.086975 | 0.31128 | -0.15106 | -0.13733 | -0.045777 | -0.032044 | -0.050354 | -0.07782 | 0.13733 | 0.086975 | 0.07782 | 0.050354 | 0.12817 | 0.10071 | 0.41656 | 122.8043 | 0.13733 | 122.7997 | 122.6761 | 122.5845 | 122.5708 | 122.5342 | -122.7173 | -122.6624 | 122.699 | 122.7493 | 61.3266 | 61.4273
468.5625 | 122.8317 | -61.3678 | 61.2991 | 0.01358 | -0.006789 | 0.0090021 | 0.065106 | -0.014422 | -0.030104 | -0.022605 | 0.011658 | -0.0078185 | 0.064617 | 0.044297 | -0.021999 | -0.011595 | -0.013751 | -0.036621 | 61.2854 | -61.4731 | 61.2762 | -61.1572 | -61.5097 | -61.5417 | -0.027466 | 61.2579 | -61.3998 | 61.3083 | -61.3174 | -61.3541 | -61.3037 | -0.10529 | -0.013733 | -0.022888 | 0.21057 | -0.17395 | -0.14191 | -0.068665 | -0.036622 | -0.032043 | -0.041198 | 0.009156 | 0.050354 | 0.064087 | 0.013733 | 0.09613 | 0.045776 | 0.31586 | 122.7493 | 0.082397 | 122.7081 | 122.7585 | 122.6578 | 122.6532 | 122.6257 | -122.7722 | -122.699 | 122.644 | 122.6761 | 61.3312 | 61.3403
470.2812 | 122.8592 | -61.4136 | 61.2946 | 0.02121 | -0.0093524 | 0.011993 | 0.067669 | -0.019335 | -0.028181 | -0.022605 | 0.0055542 | -0.0054687 | 0.063335 | 0.042588 | -0.018581 | -0.01245 | -0.017596 | -0.027466 | 61.29 | -61.4685 | 61.2717 | -61.1526 | -61.5234 | -61.5692 | 0.009155 | 61.2259 | -61.4044 | 61.3174 | -61.322 | -61.3541 | -61.322 | -0.054932 | -0.004578 | -0.022889 | 0.26093 | -0.15564 | -0.10986 | -0.10071 | -0.054931 | 0.009155 | -0.068665 | 0.022888 | 0.091553 | 0.091553 | 0.059509 | 0.082398 | 0.050354 | 0.31586 | 122.7402 | 0.082398 | 122.7219 | 122.7585 | 122.6303 | 122.7036 | 122.6395 | -122.7631 | -122.699 | 122.6852 | 122.731 | 61.3861 | 61.4227
472.0469 | 122.905 | -61.3495 | 61.2534 | 0.01358 | -0.010207 | 0.0087885 | 0.064679 | -0.021685 | -0.02989 | -0.022392 | 0.0025024 | -0.011664 | 0.063976 | 0.050919 | -0.019008 | -0.011168 | -0.014605 | -0.09613 | 61.203 | -61.4639 | 61.2854 | -61.1023 | -61.5097 | -61.5189 | -0.004578 | 61.1801 | -61.409 | 61.3678 | -61.2442 | -61.2671 | -61.2717 | -0.11444 | -0.050354 | 0.032043 | 0.24719 | -0.16937 | -0.16022 | -0.054932 | -0.045777 | -0.05951 | -0.073242 | 0.11444 | 0.10529 | 0.07782 | 0.082397 | 0.13733 | 0.14191 | 0.36163 | 122.7493 | 0.16479 | 122.7768 | 122.6669 | 122.5891 | 122.5525 | 122.5296 | -122.7173 | -122.6624 | 122.6349 | 122.7173 | 61.2534 | 61.3449
473.8281 | 122.7905 | -61.3953 | 61.3358 | 0.01358 | -0.0080706 | 0.0062249 | 0.06596 | -0.020189 | -0.028608 | -0.02346 | 0.011658 | -0.0058959 | 0.062267 | 0.043015 | -0.023921 | -0.011595 | -0.016955 | -0.064087 | 61.2671 | -61.441 | 61.2396 | -61.1572 | -61.5326 | -61.528 | -0.041199 | 61.2762 | -61.3815 | 61.2946 | -61.3312 | -61.3678 | -61.322 | -0.045776 | -0.068664 | -0.09613 | 0.23804 | -0.13275 | -0.13733 | -0.086975 | -0.091553 | 0.013733 | -0.059509 | -0.041198 | 0.064087 | 0.073243 | 0.027466 | 0.05951 | 0.013733 | 0.28381 | 122.6807 | 0.050354 | 122.6761 | 122.7081 | 122.6578 | 122.6624 | 122.6715 | -122.7768 | -122.7173 | 122.6349 | 122.6898 | 61.3312 | 61.3541
475.625 | 122.9233 | -61.322 | 61.2442 | 0.0059509 | -0.010421 | 0.0072931 | 0.063824 | -0.022539 | -0.030317 | -0.025169 | -0.00054937 | -0.0093139 | 0.060558 | 0.054123 | -0.019435 | -0.011382 | -0.012683 | -0.027466 | 61.2167 | -61.4273 | 61.3724 | -61.0153 | -61.4319 | -61.4548 | 0.09613 | 61.1664 | -61.3541 | 61.4365 | -61.1847 | -61.2213 | -61.235 | -0.10529 | -0.027466 | 0.12817 | 0.3067 | -0.13275 | -0.10986 | -0.027466 | -0.004578 | -0.032044 | -0.07782 | 0.19226 | 0.13733 | 0.086975 | 0.10071 | 0.11902 | 0.13275 | 0.41199 | 122.7997 | 0.16937 | 122.7905 | 122.644 | 122.5204 | 122.5388 | 122.4884 | -122.6715 | -122.5983 | 122.6944 | 122.7585 | 61.2946 | 61.4182
477.4062 | 122.8638 | -61.3724 | 61.235 | 0.028839 | -0.009566 | 0.0068659 | 0.064038 | -0.01848 | -0.029676 | -0.021965 | 0.011658 | -0.0097411 | 0.062694 | 0.047501 | -0.019863 | -0.010527 | -0.013537 | -0.073242 | 61.1801 | -61.4777 | 61.29 | -61.0977 | -61.5417 | -61.5372 | -0.013733 | 61.1343 | -61.4319 | 61.3266 | -61.322 | -61.3358 | -61.3266 | -0.10529 | -0.054931 | 0.054932 | 0.27466 | -0.1648 | -0.16937 | -0.059509 | -0.064087 | -0.05951 | -0.10071 | 0.091553 | 0.050354 | 0.045776 | 0.036621 | 0.10529 | 0.096131 | 0.37994 | 122.7676 | 0.10986 | 122.7585 | 122.6578 | 122.5662 | 122.5525 | 122.5067 | -122.7127 | -122.6669 | 122.6624 | 122.699 | 61.2991 | 61.3586
479.125 | 122.7631 | -61.4456 | 61.2579 | -0.0016786 | -0.008498 | 0.0081477 | 0.064892 | -0.020189 | -0.031172 | -0.02346 | 0.008606 | -0.0069641 | 0.062481 | 0.045792 | -0.018367 | -0.011382 | -0.019091 | -0.11444 | 61.2122 | -61.496 | 61.1847 | -61.2671 | -61.6425 | -61.6699 | -0.16479 | 61.1893 | -61.4227 | 61.2122 | -61.441 | -61.4777 | -61.409 | -0.050354 | -0.045777 | -0.073243 | 0.17853 | -0.2243 | -0.19684 | -0.17395 | -0.14648 | 0.022889 | -0.068665 | -0.045777 | 0.004578 | 0.036621 | -0.032043 | 0.013732 | -0.054932 | 0.22888 | 122.6807 | -0.018311 | 122.6349 | 122.7081 | 122.612 | 122.6578 | 122.6349 | -122.7539 | -122.6807 | 122.6303 | 122.6578 | 61.3312 | 61.2808
480.875 | 122.8592 | -61.3998 | 61.2442 | 0.01358 | -0.007857 | 0.0085749 | 0.064892 | -0.019121 | -0.028608 | -0.02581 | 0.0055542 | -0.0082459 | 0.063976 | 0.04387 | -0.018367 | -0.010527 | -0.017596 | -0.086975 | 61.1801 | -61.4502 | 61.2717 | -61.1114 | -61.5555 | -61.5463 | -0.032043 | 61.1481 | -61.4273 | 61.3129 | -61.322 | -61.3358 | -61.3083 | -0.050354 | -0.064087 | 0.027465 | 0.28839 | -0.14648 | -0.15564 | -0.096131 | -0.10529 | -0.027466 | -0.096131 | 0.068664 | 0.07782 | 0.091552 | 0.064087 | 0.11902 | 0.091553 | 0.33875 | 122.7219 | 0.10529 | 122.7402 | 122.6303 | 122.5754 | 122.58 | 122.5479 | -122.6944 | -122.6715 | 122.6715 | 122.7127 | 61.3129 | 61.3678
482.5938 | 122.8775 | -61.3724 | 61.2671 | 0.0059509 | -0.007857 | 0.0072931 | 0.064679 | -0.019762 | -0.031813 | -0.023674 | 0.008606 | -0.0084595 | 0.062267 | 0.056473 | -0.02029 | -0.0092456 | -0.017383 | -0.091553 | 61.2213 | -61.4639 | 61.2579 | -61.1435 | -61.528 | -61.5555 | -0.050354 | 61.1435 | -61.377 | 61.3083 | -61.3174 | -61.3358 | -61.2991 | -0.091553 | -0.045777 | -0.009155 | 0.22888 | -0.18311 | -0.15564 | -0.091553 | -0.064087 | -0.004578 | -0.1236 | 0.041199 | 0.054931 | 0.073242 | 0.036621 | 0.07782 | 0.041199 | 0.32043 | 122.7219 | 0.059509 | 122.6852 | 122.6852 | 122.5204 | 122.5937 | 122.5159 | -122.731 | -122.644 | 122.6303 | 122.6807 | 61.2808 | 61.322
484.3125 | 122.7951 | -61.4136 | 61.2396 | 0.01358 | -0.0072162 | 0.0098565 | 0.065533 | -0.019549 | -0.029249 | -0.024528 | 0.0055542 | -0.0058959 | 0.063976 | 0.039811 | -0.020503 | -0.011809 | -0.015674 | -0.036621 | 61.2213 | -61.4822 | 61.2762 | -61.1435 | -61.5692 | -61.5829 | -0.022888 | 61.1801 | -61.4044 | 61.29 | -61.3678 | -61.4136 | -61.3678 | -0.068665 | -0.018311 | 0.036621 | 0.27008 | -0.16937 | -0.15564 | -0.10071 | -0.086975 | 0.009155 | -0.059509 | 0.050354 | 0.045776 | 0.045776 | 0 | 0.036621 | -0.009155 | 0.33875 | 122.7585 | 0.036621 | 122.6944 | 122.7036 | 122.5845 | 122.6349 | 122.5937 | -122.7219 | -122.644 | 122.6898 | 122.7036 | 61.377 | 61.3907
486.0938 | 122.8088 | -61.3541 | 61.322 | 0.0059509 | -0.0072162 | 0.0085749 | 0.064892 | -0.02083 | -0.030531 | -0.023887 | 0.0055542 | -0.0095275 | 0.063335 | 0.04451 | -0.024135 | -0.013518 | -0.01311 | -0.004578 | 61.2305 | -61.4227 | 61.3129 | -61.0703 | -61.4777 | -61.5005 | 0.004578 | 61.2671 | -61.3632 | 61.2946 | -61.3037 | -61.3312 | -61.3037 | -0.068664 | -0.091552 | -0.009155 | 0.28381 | -0.14648 | -0.1236 | -0.07782 | -0.054932 | -0.009155 | -0.054931 | -0.027465 | 0.050354 | 0.050354 | 0.022888 | 0.059509 | 0.032043 | 0.35248 | 122.7356 | 0.059509 | 122.6578 | 122.6532 | 122.6303 | 122.5845 | 122.6212 | -122.7447 | -122.6852 | 122.6669 | 122.6486 | 61.3495 | 61.3586
487.8594 | 122.7676 | -61.3403 | 61.2991 | 0.01358 | -0.0076434 | 0.0081477 | 0.065747 | -0.024035 | -0.030317 | -0.025169 | 0.0025024 | -0.0082459 | 0.062053 | 0.040879 | -0.022212 | -0.012023 | -0.013324 | 0.009155 | 61.2396 | -61.4136 | 61.2991 | -61.0886 | -61.4868 | -61.5326 | 0 | 61.2259 | -61.3541 | 61.2991 | -61.3083 | -61.3403 | -61.3129 | -0.073242 | -0.059509 | 0 | 0.25177 | -0.19226 | -0.14648 | -0.11902 | -0.073242 | -0.013733 | -0.073242 | 0 | 0.032043 | 0.027466 | 0 | 0.041199 | 0.013733 | 0.32501 | 122.7127 | 0.045776 | 122.6532 | 122.6532 | 122.58 | 122.58 | 122.5662 | -122.7127 | -122.6532 | 122.6395 | 122.6395 | 61.3495 | 61.3403
489.5781 | 122.9141 | -61.3312 | 61.2671 | -0.0016786 | -0.0097796 | 0.0094293 | 0.064251 | -0.021685 | -0.030531 | -0.021965 | 0.0025024 | -0.0097411 | 0.066112 | 0.043442 | -0.019008 | -0.011168 | -0.018023 | -0.041199 | 61.1938 | -61.4365 | 61.3403 | -61.0336 | -61.4365 | -61.4639 | 0.07782 | 61.1893 | -61.3495 | 61.3998 | -61.203 | -61.2396 | -61.235 | -0.10529 | -0.073242 | 0.073242 | 0.29755 | -0.13275 | -0.10529 | -0.027466 | 0 | -0.01831 | -0.07782 | 0.13275 | 0.12817 | 0.096131 | 0.091553 | 0.11444 | 0.10986 | 0.40283 | 122.7768 | 0.14648 | 122.7493 | 122.6303 | 122.5388 | 122.525 | 122.5204 | -122.7036 | -122.6166 | 122.6715 | 122.731 | 61.29 | 61.409
491.2969 | 122.8271 | -61.3632 | 61.2854 | 0.01358 | -0.006789 | 0.0081477 | 0.066601 | -0.016771 | -0.030958 | -0.021324 | 0.0055542 | -0.0063233 | 0.064403 | 0.041092 | -0.020503 | -0.010955 | -0.014819 | -0.022888 | 61.2671 | -61.4594 | 61.2808 | -61.1252 | -61.5326 | -61.5555 | 0.009155 | 61.2259 | -61.4182 | 61.3266 | -61.2946 | -61.3358 | -61.2991 | -0.096131 | -0.01831 | -0.004577 | 0.23804 | -0.19226 | -0.16937 | -0.09613 | -0.073242 | -0.054932 | -0.059509 | 0.041199 | 0.068664 | 0.064087 | 0.027466 | 0.11902 | 0.082398 | 0.33417 | 122.7402 | 0.1236 | 122.7448 | 122.7264 | 122.644 | 122.6303 | 122.5891 | -122.7448 | -122.7036 | 122.644 | 122.6898 | 61.3403 | 61.3724
493.0625 | 122.7631 | -61.4136 | 61.2762 | -0.0016786 | -0.0070026 | 0.0085749 | 0.065747 | -0.019549 | -0.031385 | -0.025596 | -0.00054937 | -0.0093139 | 0.062481 | 0.03917 | -0.019863 | -0.008391 | -0.016314 | -0.11444 | 61.1938 | -61.4914 | 61.1755 | -61.2213 | -61.6241 | -61.647 | -0.13733 | 61.171 | -61.4456 | 61.2213 | -61.4227 | -61.4594 | -61.3998 | -0.07782 | -0.082397 | -0.10071 | 0.19226 | -0.23346 | -0.21057 | -0.15564 | -0.13275 | -0.032044 | -0.10529 | -0.054932 | -0.009155 | 0.013733 | -0.045777 | 0.045777 | -0.013733 | 0.27008 | 122.6669 | 0.022889 | 122.6669 | 122.6852 | 122.6166 | 122.6074 | 122.5845 | -122.7676 | -122.7219 | 122.5891 | 122.6349 | 61.2991 | 61.2762
494.8594 | 122.8958 | -61.3403 | 61.2671 | 0.01358 | -0.010207 | 0.0081477 | 0.064251 | -0.018908 | -0.031385 | -0.026237 | 0.0025024 | -0.0097411 | 0.062908 | 0.044938 | -0.020717 | -0.010741 | -0.015674 | -0.068665 | 61.1893 | -61.4594 | 61.29 | -61.084 | -61.4822 | -61.496 | 0.027466 | 61.171 | -61.3815 | 61.377 | -61.2167 | -61.2442 | -61.2396 | -0.11902 | -0.07782 | 0.022888 | 0.25635 | -0.15564 | -0.14191 | -0.036621 | -0.022888 | -0.041199 | -0.096131 | 0.10986 | 0.1236 | 0.10071 | 0.09613 | 0.14191 | 0.13733 | 0.37537 | 122.7493 | 0.1648 | 122.7585 | 122.6486 | 122.5525 | 122.5296 | 122.5113 | -122.7264 | -122.6486 | 122.6303 | 122.7173 | 61.2717 | 61.3678
496.6406 | 122.7905 | -61.4136 | 61.2671 | 0.0059509 | -0.0076434 | 0.011566 | 0.067029 | -0.018053 | -0.030317 | -0.023674 | 0.0055542 | -0.0048279 | 0.063762 | 0.042374 | -0.019435 | -0.012236 | -0.017169 | -0.054932 | 61.2259 | -61.4685 | 61.235 | -61.1572 | -61.5875 | -61.6013 | -0.050354 | 61.1984 | -61.4044 | 61.2534 | -61.3907 | -61.4319 | -61.3632 | -0.054932 | -0.041199 | -0.032044 | 0.25635 | -0.18768 | -0.17395 | -0.13275 | -0.11902 | 0.009155 | -0.068665 | -0.013733 | 0.022888 | 0.050354 | -0.018311 | 0.041199 | -0.027466 | 0.31128 | 122.7036 | 0.013733 | 122.6578 | 122.6944 | 122.6028 | 122.6395 | 122.612 | -122.7356 | -122.6715 | 122.6486 | 122.6669 | 61.3586 | 61.3632
498.3438 | 122.9141 | -61.3266 | 61.2625 | 0.0059509 | -0.0091388 | 0.0081477 | 0.064465 | -0.021471 | -0.03224 | -0.026237 | 0.0025024 | -0.010169 | 0.062053 | 0.05156 | -0.02029 | -0.0098864 | -0.015674 | -0.022888 | 61.2076 | -61.3998 | 61.3312 | -61.0336 | -61.4273 | -61.4594 | 0.07782 | 61.1755 | -61.3815 | 61.3953 | -61.1938 | -61.2259 | -61.2259 | -0.073242 | -0.054931 | 0.068665 | 0.29297 | -0.13275 | -0.10071 | -0.05951 | -0.027466 | -0.054932 | -0.086975 | 0.13275 | 0.13275 | 0.10071 | 0.10071 | 0.15564 | 0.15564 | 0.36621 | 122.731 | 0.18768 | 122.7768 | 122.6074 | 122.5571 | 122.5342 | 122.5021 | -122.6624 | -122.644 | 122.6578 | 122.7219 | 61.3037 | 61.4044
500.125 | 122.8912 | -61.377 | 61.1893 | 0.0059509 | -0.010207 | 0.0077203 | 0.064251 | -0.019976 | -0.030317 | -0.022819 | -0.003601 | -0.0080321 | 0.062481 | 0.040238 | -0.014522 | -0.0094592 | -0.016742 | -0.068665 | 61.1023 | -61.4868 | 61.2762 | -61.0931 | -61.5417 | -61.5601 | -0.009155 | 61.0931 | -61.4182 | 61.3358 | -61.3083 | -61.322 | -61.2946 | -0.10986 | -0.086975 | 0.086975 | 0.28381 | -0.18311 | -0.16479 | -0.073243 | -0.054932 | -0.041199 | -0.09613 | 0.14648 | 0.068664 | 0.082397 | 0.054932 | 0.1236 | 0.096131 | 0.39368 | 122.7631 | 0.10986 | 122.7539 | 122.5891 | 122.5113 | 122.4792 | 122.4701 | -122.6761 | -122.6074 | 122.6532 | 122.7127 | 61.3083 | 61.3678
501.8906 | 122.7448 | -61.3998 | 61.2671 | 0.0059509 | -0.0072162 | 0.0077203 | 0.067883 | -0.020403 | -0.028822 | -0.024742 | 0.0025024 | -0.0054687 | 0.063976 | 0.038102 | -0.019863 | -0.010955 | -0.016314 | -0.068665 | 61.2076 | -61.4685 | 61.1938 | -61.1938 | -61.6013 | -61.6287 | -0.082397 | 61.1664 | -61.4365 | 61.2442 | -61.4044 | -61.441 | -61.3724 | -0.068665 | -0.059509 | -0.073242 | 0.20599 | -0.22888 | -0.20142 | -0.16022 | -0.13275 | -0.036621 | -0.10071 | -0.022888 | -0.004578 | 0.027466 | -0.041199 | 0.064087 | -0.004578 | 0.27466 | 122.6624 | 0.032043 | 122.6807 | 122.6761 | 122.6028 | 122.6074 | 122.5662 | -122.7356 | -122.7036 | 122.5937 | 122.644 | 61.3312 | 61.3174
503.6719 | 122.7951 | -61.3678 | 61.2717 | 0.0059509 | -0.0089252 | 0.010284 | 0.065747 | -0.018908 | -0.030531 | -0.021965 | -0.003601 | -0.0071777 | 0.063335 | 0.044938 | -0.021358 | -0.011809 | -0.015887 | -0.027466 | 61.2213 | -61.4502 | 61.2625 | -61.116 | -61.5417 | -61.5463 | -0.013733 | 61.1847 | -61.3907 | 61.2946 | -61.322 | -61.377 | -61.3266 | -0.082397 | -0.050354 | -0.009155 | 0.25177 | -0.17853 | -0.17395 | -0.096131 | -0.091553 | -0.022888 | -0.086975 | 0.022889 | 0.045777 | 0.041199 | -0.009155 | 0.064087 | 0.013733 | 0.33417 | 122.7127 | 0.068665 | 122.6852 | 122.6715 | 122.5754 | 122.5891 | 122.5525 | -122.7219 | -122.6624 | 122.6303 | 122.6624 | 61.3403 | 61.3541
505.3906 | 122.8088 | -61.3449 | 61.2762 | -0.0016786 | -0.0048664 | 0.0087885 | 0.062756 | -0.02083 | -0.030531 | -0.024742 | -0.00054937 | -0.0093139 | 0.061199 | 0.044083 | -0.024562 | -0.0096728 | -0.015033 | 0 | 61.2076 | -61.3861 | 61.3312 | -61.0291 | -61.4227 | -61.4456 | 0.036621 | 61.1938 | -61.3586 | 61.3403 | -61.2534 | -61.2946 | -61.2762 | -0.041198 | -0.068664 | 0.054932 | 0.31586 | -0.10071 | -0.077819 | -0.05951 | -0.036621 | -0.013733 | -0.082397 | 0.064087 | 0.091553 | 0.068665 | 0.050354 | 0.082398 | 0.064087 | 0.35706 | 122.7173 | 0.10529 | 122.699 | 122.5937 | 122.5525 | 122.5525 | 122.5388 | -122.6624 | -122.6349 | 122.6761 | 122.6852 | 61.3449 | 61.3815
507.1094 | 122.8226 | -61.3724 | 61.2854 | 0.028839 | -0.0059344 | 0.0092157 | 0.064465 | -0.021044 | -0.028608 | -0.026023 | 0.011658 | -0.0052551 | 0.063549 | 0.040024 | -0.022212 | -0.011809 | -0.017169 | -0.032043 | 61.2808 | -61.4365 | 61.2671 | -61.116 | -61.5189 | -61.5372 | -0.027466 | 61.2259 | -61.3724 | 61.3083 | -61.2946 | -61.3266 | -61.29 | -0.064087 | -0.004577 | -0.01831 | 0.25635 | -0.1648 | -0.14648 | -0.10071 | -0.082398 | 0 | -0.059509 | 0.022889 | 0.077819 | 0.082397 | 0.045776 | 0.082397 | 0.045776 | 0.32043 | 122.7036 | 0.077819 | 122.6807 | 122.7173 | 122.5983 | 122.6532 | 122.5983 | -122.7219 | -122.6578 | 122.6395 | 122.6807 | 61.3403 | 61.3449
508.8906 | 122.7722 | -61.3403 | 61.3083 | 0.0059509 | -0.0097796 | 0.0068659 | 0.06532 | -0.023607 | -0.03224 | -0.021965 | 0.0025024 | -0.0080321 | 0.063335 | 0.044083 | -0.021785 | -0.0094592 | -0.016314 | 0.009155 | 61.2305 | -61.3998 | 61.3129 | -61.0519 | -61.4502 | -61.4914 | 0.036621 | 61.203 | -61.3266 | 61.3174 | -61.2625 | -61.2854 | -61.2762 | -0.059509 | -0.07782 | 0.004577 | 0.28839 | -0.15106 | -0.10986 | -0.091553 | -0.050354 | 0.013733 | -0.10529 | 0.009155 | 0.07782 | 0.064087 | 0.054932 | 0.050354 | 0.041199 | 0.3479 | 122.7127 | 0.064087 | 122.644 | 122.6303 | 122.5296 | 122.5708 | 122.5433 | -122.7081 | -122.6349 | 122.6532 | 122.6578 | 61.3495 | 61.377
510.6875 | 122.8592 | -61.3678 | 61.2213 | 0.028839 | -0.0065754 | 0.010284 | 0.06596 | -0.016131 | -0.030958 | -0.024528 | 0.008606 | -0.0054687 | 0.063335 | 0.04921 | -0.016658 | -0.008391 | -0.012896 | -0.073242 | 61.1618 | -61.496 | 61.2946 | -61.0703 | -61.5051 | -61.528 | 0.022888 | 61.0977 | -61.4227 | 61.3358 | -61.2717 | -61.3083 | -61.2717 | -0.12817 | -0.059509 | 0.073243 | 0.29755 | -0.16022 | -0.13733 | -0.032043 | -0.009155 | -0.054931 | -0.1236 | 0.11444 | 0.096131 | 0.096131 | 0.059509 | 0.15106 | 0.11444 | 0.42572 | 122.7905 | 0.15106 | 122.7585 | 122.6578 | 122.5204 | 122.5296 | 122.4655 | -122.7173 | -122.644 | 122.6624 | 122.7036 | 61.2946 | 61.3907
512.4688 | 122.7585 | -61.3632 | 61.3266 | -0.0016786 | -0.0089252 | 0.0075067 | 0.064679 | -0.019976 | -0.032026 | -0.022392 | 0.0025024 | -0.0086731 | 0.063335 | 0.04686 | -0.02029 | -0.011595 | -0.017383 | 0 | 61.2259 | -61.409 | 61.2671 | -61.0886 | -61.496 | -61.5143 | -0.013733 | 61.2213 | -61.3403 | 61.2946 | -61.3037 | -61.322 | -61.3083 | -0.045777 | -0.10071 | -0.059509 | 0.27466 | -0.15106 | -0.13275 | -0.10529 | -0.086975 | 0.022888 | -0.10529 | -0.032043 | 0.059509 | 0.054931 | 0.041199 | 0.032043 | 0.018311 | 0.32043 | 122.6761 | 0.036621 | 122.6349 | 122.6349 | 122.5616 | 122.5891 | 122.5845 | -122.7356 | -122.6669 | 122.6303 | 122.6578 | 61.3632 | 61.3495
514.1719 | 122.7402 | -61.4182 | 61.2442 | 0.0059509 | -0.0063616 | 0.0077203 | 0.065533 | -0.020189 | -0.030531 | -0.023674 | 0.0025024 | -0.0069641 | 0.064403 | 0.043229 | -0.018794 | -0.01245 | -0.013537 | -0.10529 | 61.2122 | -61.4822 | 61.1755 | -61.2167 | -61.647 | -61.6379 | -0.13733 | 61.1801 | -61.4319 | 61.2213 | -61.409 | -61.4548 | -61.3861 | -0.064087 | -0.032044 | -0.068665 | 0.20142 | -0.21973 | -0.22888 | -0.15564 | -0.16479 | -0.013733 | -0.064087 | -0.022889 | 0.009155 | 0.032044 | -0.036621 | 0.045777 | -0.022888 | 0.2655 | 122.6578 | 0.022888 | 122.6532 | 122.6944 | 122.612 | 122.6303 | 122.5983 | -122.7264 | -122.6761 | 122.5937 | 122.6395 | 61.3129 | 61.2808
515.9375 | 122.7859 | -61.3678 | 61.2488 | 0.02121 | -0.011275 | 0.0098565 | 0.06532 | -0.021685 | -0.02989 | -0.021537 | 0.008606 | -0.0078185 | 0.062908 | 0.04387 | -0.020931 | -0.0098864 | -0.01546 | -0.045776 | 61.1938 | -61.4502 | 61.2579 | -61.1298 | -61.5372 | -61.5601 | -0.027466 | 61.1664 | -61.3815 | 61.29 | -61.3403 | -61.3861 | -61.322 | -0.082397 | -0.054931 | 0.009156 | 0.23804 | -0.19226 | -0.16937 | -0.10986 | -0.086975 | -0.013733 | -0.082397 | 0.041199 | 0.027466 | 0.045777 | -0.01831 | 0.05951 | -0.004577 | 0.32043 | 122.7081 | 0.041199 | 122.6715 | 122.644 | 122.5479 | 122.5616 | 122.5342 | -122.699 | -122.6303 | 122.6257 | 122.6578 | 61.322 | 61.3403
517.6875 | 122.7631 | -61.409 | 61.2579 | 0.01358 | -0.006789 | 0.0098565 | 0.064679 | -0.01549 | -0.029249 | -0.021965 | 0.0055542 | -0.0052551 | 0.065685 | 0.04921 | -0.021144 | -0.011382 | -0.016955 | -0.054932 | 61.2122 | -61.4639 | 61.2167 | -61.1572 | -61.5738 | -61.5829 | -0.059509 | 61.1572 | -61.4273 | 61.2396 | -61.3815 | -61.4273 | -61.3541 | -0.054931 | -0.045777 | -0.041199 | 0.25177 | -0.17395 | -0.16479 | -0.11902 | -0.10986 | -0.01831 | -0.10071 | -0.018311 | 0.027466 | 0.054932 | -0.01831 | 0.073242 | 0 | 0.3067 | 122.6807 | 0.045776 | 122.6669 | 122.6761 | 122.5845 | 122.6212 | 122.5662 | -122.7219 | -122.6852 | 122.6257 | 122.6486 | 61.3541 | 61.3495
519.4688 | 122.8775 | -61.3907 | 61.1572 | -0.0016786 | -0.0087116 | 0.010284 | 0.064679 | -0.019335 | -0.030317 | -0.023246 | 0.0025024 | -0.0084595 | 0.061412 | 0.047288 | -0.018581 | -0.009032 | -0.016955 | -0.091553 | 61.1481 | -61.4685 | 61.2488 | -61.1069 | -61.528 | -61.5463 | -0.018311 | 61.0977 | -61.4365 | 61.3312 | -61.2946 | -61.322 | -61.2762 | -0.07782 | -0.009156 | 0.091552 | 0.28381 | -0.15564 | -0.13733 | -0.07782 | -0.059509 | -0.045776 | -0.05951 | 0.17395 | 0.09613 | 0.11444 | 0.068665 | 0.16022 | 0.11444 | 0.36163 | 122.7173 | 0.14191 | 122.7676 | 122.6166 | 122.5342 | 122.5388 | 122.4884 | -122.6257 | -122.5937 | 122.6395 | 122.7219 | 61.2991 | 61.3724
521.1875 | 122.7951 | -61.3815 | 61.2488 | 0.028839 | -0.008498 | 0.0079339 | 0.064038 | -0.016771 | -0.030317 | -0.021965 | 0.008606 | -0.0054687 | 0.063762 | 0.043656 | -0.020717 | -0.010741 | -0.013537 | -0.027466 | 61.29 | -61.4456 | 61.2534 | -61.1206 | -61.4914 | -61.5372 | -0.022888 | 61.2259 | -61.3998 | 61.3037 | -61.2854 | -61.3495 | -61.2808 | -0.064087 | 0.041199 | 0.004578 | 0.26093 | -0.15564 | -0.10986 | -0.091552 | -0.045776 | -0.01831 | -0.022888 | 0.054932 | 0.096131 | 0.10071 | 0.032044 | 0.11902 | 0.050354 | 0.32501 | 122.699 | 0.11444 | 122.7036 | 122.7356 | 122.6257 | 122.6715 | 122.6074 | -122.6944 | -122.6486 | 122.6349 | 122.6852 | 61.3541 | 61.3586
522.9531 | 122.8638 | -61.3632 | 61.1755 | 0.036468 | -0.004439 | 0.011993 | 0.064038 | -0.01314 | -0.030317 | -0.024101 | 0.0055542 | -0.0082459 | 0.063549 | 0.054337 | -0.017513 | -0.0077502 | -0.018023 | -0.064087 | 61.1389 | -61.4594 | 61.2717 | -61.0519 | -61.5097 | -61.5326 | 0.032043 | 61.116 | -61.3953 | 61.3403 | -61.2762 | -61.3129 | -61.2808 | -0.096131 | -0.036621 | 0.09613 | 0.31128 | -0.16937 | -0.14648 | -0.073242 | -0.050354 | -0.032044 | -0.059509 | 0.16479 | 0.086975 | 0.082397 | 0.050354 | 0.11444 | 0.082398 | 0.40741 | 122.731 | 0.11902 | 122.7356 | 122.5983 | 122.5113 | 122.5021 | 122.4792 | -122.6349 | -122.5708 | 122.6349 | 122.7036 | 61.2991 | 61.3953
524.6719 | 122.7997 | -61.3174 | 61.2762 | 0.0059509 | -0.0082842 | 0.0077203 | 0.064465 | -0.022539 | -0.032026 | -0.020683 | 0.0025024 | -0.0061095 | 0.063335 | 0.046647 | -0.023067 | -0.0101 | -0.013537 | 0.004578 | 61.2167 | -61.409 | 61.322 | -61.0153 | -61.4319 | -61.4639 | 0.036621 | 61.1984 | -61.3495 | 61.3174 | -61.2579 | -61.2762 | -61.2671 | -0.091553 | -0.059509 | 0.045776 | 0.30212 | -0.14648 | -0.11444 | -0.054931 | -0.022888 | -0.032043 | -0.07782 | 0.041199 | 0.059509 | 0.050354 | 0.041199 | 0.082397 | 0.073242 | 0.39368 | 122.731 | 0.091552 | 122.6669 | 122.6257 | 122.5479 | 122.5342 | 122.5159 | -122.6852 | -122.6257 | 122.6395 | 122.6349 | 61.322 | 61.3541
526.3906 | 122.8821 | -61.3861 | 61.1801 | 0.0059509 | -0.0089252 | 0.0083613 | 0.063611 | -0.019976 | -0.031599 | -0.023033 | -0.00054937 | -0.0095275 | 0.063762 | 0.04686 | -0.018794 | -0.0092456 | -0.017596 | -0.07782 | 61.1252 | -61.4594 | 61.2579 | -61.116 | -61.5234 | -61.5555 | 0.004578 | 61.0794 | -61.4273 | 61.3083 | -61.2854 | -61.3129 | -61.29 | -0.073243 | -0.054932 | 0.07782 | 0.27008 | -0.16937 | -0.13733 | -0.09613 | -0.064086 | -0.041199 | -0.10071 | 0.12817 | 0.10071 | 0.09613 | 0.073242 | 0.13733 | 0.11444 | 0.34332 | 122.7173 | 0.14191 | 122.7356 | 122.5845 | 122.5067 | 122.5113 | 122.4655 | -122.6395 | -122.6074 | 122.644 | 122.6944 | 61.3083 | 61.3907
528.1719 | 122.7448 | -61.4182 | 61.2488 | 0.01358 | -0.006789 | 0.0079339 | 0.063824 | -0.022753 | -0.02989 | -0.023246 | 0.0025024 | -0.0056823 | 0.065258 | 0.044938 | -0.019222 | -0.010741 | -0.018237 | -0.13275 | 61.2167 | -61.5005 | 61.1298 | -61.2396 | -61.6333 | -61.6562 | -0.13733 | 61.1298 | -61.4182 | 61.203 | -61.409 | -61.4365 | -61.3724 | -0.082397 | -0.032043 | -0.11902 | 0.17853 | -0.23804 | -0.21515 | -0.15564 | -0.13275 | 0 | -0.11902 | -0.045776 | 0.009155 | 0.045777 | -0.01831 | 0.045777 | -0.01831 | 0.26093 | 122.6303 | 0.009155 | 122.6212 | 122.7173 | 122.5479 | 122.6349 | 122.5479 | -122.7493 | -122.6669 | 122.5479 | 122.6212 | 61.2854 | 61.2808
529.9688 | 122.8546 | -61.3678 | 61.1984 | 0.0059509 | -0.007857 | 0.0094293 | 0.064251 | -0.017412 | -0.027327 | -0.022819 | 0.011658 | -0.0091003 | 0.065685 | 0.047288 | -0.018794 | -0.011595 | -0.013537 | -0.068665 | 61.1343 | -61.4639 | 61.2671 | -61.0703 | -61.496 | -61.5189 | 0.036621 | 61.1114 | -61.4319 | 61.3312 | -61.2671 | -61.3037 | -61.2717 | -0.09613 | -0.064087 | 0.068665 | 0.29755 | -0.15106 | -0.12817 | -0.054932 | -0.032044 | -0.064087 | -0.086975 | 0.13275 | 0.10071 | 0.096131 | 0.064087 | 0.16022 | 0.12817 | 0.39368 | 122.731 | 0.16479 | 122.7631 | 122.5983 | 122.5433 | 122.5021 | 122.4792 | -122.6624 | -122.6303 | 122.6349 | 122.699 | 61.2991 | 61.4044
531.7344 | 122.8592 | -61.3586 | 61.171 | 0.0059509 | -0.0065754 | 0.0085749 | 0.064679 | -0.016131 | -0.026045 | -0.026023 | 0.0025024 | -0.0076049 | 0.06419 | 0.043656 | -0.018367 | -0.0092456 | -0.016742 | -0.12817 | 61.1481 | -61.4685 | 61.1893 | -61.171 | -61.5692 | -61.5784 | -0.045776 | 61.1252 | -61.3998 | 61.29 | -61.3129 | -61.3358 | -61.2854 | -0.10986 | -0.022888 | 0.018311 | 0.18768 | -0.21973 | -0.21057 | -0.10986 | -0.10071 | -0.041198 | -0.045776 | 0.11902 | 0.045777 | 0.073243 | 0.022889 | 0.11444 | 0.064087 | 0.29755 | 122.6578 | 0.086975 | 122.6898 | 122.6166 | 122.525 | 122.5067 | 122.4838 | -122.6395 | -122.5708 | 122.5479 | 122.6486 | 61.2305 | 61.3129
533.4531 | 122.7264 | -61.3861 | 61.2625 | 0.0059509 | -0.006789 | 0.01007 | 0.066601 | -0.016985 | -0.030531 | -0.025169 | 0.0025024 | -0.0080321 | 0.061199 | 0.04152 | -0.020717 | -0.0101 | -0.019305 | -0.07782 | 61.203 | -61.4731 | 61.1938 | -61.1847 | -61.5921 | -61.6104 | -0.086975 | 61.1618 | -61.4273 | 61.2122 | -61.3998 | -61.4456 | -61.3724 | -0.086975 | -0.059509 | -0.068664 | 0.20142 | -0.22431 | -0.20599 | -0.13733 | -0.11902 | -0.041199 | -0.10071 | -0.050354 | -0.013733 | 0.013733 | -0.05951 | 0.054932 | -0.018311 | 0.28839 | 122.6669 | 0.027466 | 122.6395 | 122.6761 | 122.5891 | 122.5891 | 122.5479 | -122.7356 | -122.6898 | 122.58 | 122.5983 | 61.3083 | 61.2991
535.1875 | 122.8226 | -61.3449 | 61.235 | 0.028839 | -0.011061 | 0.0094293 | 0.063824 | -0.019121 | -0.029463 | -0.023674 | 0.0055542 | -0.0099549 | 0.063549 | 0.049637 | -0.019649 | -0.0092456 | -0.018023 | -0.11902 | 61.1938 | -61.4639 | 61.2396 | -61.1114 | -61.5005 | -61.5417 | -0.054932 | 61.1206 | -61.3815 | 61.2854 | -61.2991 | -61.3129 | -61.29 | -0.11902 | -0.041198 | 0.004578 | 0.23346 | -0.19684 | -0.15564 | -0.07782 | -0.036621 | -0.036621 | -0.11444 | 0.050354 | 0.045777 | 0.054932 | 0.032044 | 0.091553 | 0.068665 | 0.35248 | 122.7036 | 0.082398 | 122.6669 | 122.6578 | 122.5021 | 122.5388 | 122.4655 | -122.699 | -122.6166 | 122.5845 | 122.6303 | 61.2259 | 61.29
536.9375 | 122.8455 | -61.2762 | 61.2671 | -0.0016786 | -0.0070026 | 0.0090021 | 0.066174 | -0.024462 | -0.031172 | -0.025169 | 0.0025024 | -0.0078185 | 0.06483 | 0.042161 | -0.021144 | -0.0092456 | -0.014819 | 0.013733 | 61.1893 | -61.3907 | 61.3449 | -60.9695 | -61.3907 | -61.4365 | 0.10986 | 61.1755 | -61.3358 | 61.4044 | -61.1618 | -61.203 | -61.203 | -0.11444 | -0.07782 | 0.07782 | 0.3067 | -0.16022 | -0.11444 | -0.045776 | 0 | -0.059509 | -0.091553 | 0.13733 | 0.11444 | 0.073242 | 0.073242 | 0.13275 | 0.13275 | 0.42114 | 122.7356 | 0.17395 | 122.7402 | 122.58 | 122.5113 | 122.4655 | 122.4518 | -122.6578 | -122.6028 | 122.6212 | 122.6807 | 61.29 | 61.3861
538.7188 | 122.8546 | -61.3815 | 61.1618 | 0.01358 | -0.0063616 | 0.0090021 | 0.063611 | -0.022112 | -0.031385 | -0.024528 | -0.00054937 | -0.0063233 | 0.060985 | 0.04152 | -0.018367 | -0.0088184 | -0.011828 | -0.082397 | 61.1252 | -61.4868 | 61.2534 | -61.1023 | -61.5143 | -61.5463 | 0.004578 | 61.1023 | -61.4136 | 61.3174 | -61.2808 | -61.3129 | -61.2717 | -0.10528 | -0.036621 | 0.091553 | 0.27924 | -0.16479 | -0.13275 | -0.05951 | -0.027466 | -0.032043 | -0.059509 | 0.15564 | 0.10071 | 0.10986 | 0.068665 | 0.14191 | 0.10071 | 0.38452 | 122.7402 | 0.13275 | 122.731 | 122.612 | 122.5159 | 122.5067 | 122.4838 | -122.6486 | -122.5754 | 122.6349 | 122.699 | 61.2991 | 61.3861
540.5 | 122.8683 | -61.2854 | 61.2579 | -0.0093076 | -0.0091388 | 0.0087885 | 0.062115 | -0.020403 | -0.030317 | -0.023033 | -0.00054937 | -0.0091003 | 0.063762 | 0.050492 | -0.021572 | -0.012023 | -0.016955 | 0.009155 | 61.171 | -61.409 | 61.3495 | -60.9695 | -61.3953 | -61.4319 | 0.09613 | 61.1618 | -61.3358 | 61.3953 | -61.1664 | -61.203 | -61.203 | -0.1236 | -0.086976 | 0.091552 | 0.31586 | -0.14648 | -0.10986 | -0.022888 | 0.013733 | -0.050354 | -0.096131 | 0.13733 | 0.11902 | 0.082397 | 0.082397 | 0.13275 | 0.13275 | 0.43945 | 122.7585 | 0.16937 | 122.731 | 122.58 | 122.4976 | 122.4564 | 122.4472 | -122.6669 | -122.5937 | 122.6349 | 122.6807 | 61.2946 | 61.3815
542.2188 | 122.7814 | -61.3449 | 61.2808 | 0.028839 | -0.0072162 | 0.0096429 | 0.063824 | -0.023821 | -0.02989 | -0.023033 | 0.0055542 | -0.0078185 | 0.064617 | 0.040879 | -0.020503 | -0.012023 | -0.015033 | -0.018311 | 61.2717 | -61.4365 | 61.2442 | -61.116 | -61.4868 | -61.5143 | -0.013733 | 61.235 | -61.3724 | 61.2946 | -61.2762 | -61.3358 | -61.2808 | -0.091552 | -0.009156 | -0.036621 | 0.22888 | -0.16937 | -0.14191 | -0.07782 | -0.050354 | -0.027465 | -0.045777 | 0.013733 | 0.068665 | 0.064087 | 0.009156 | 0.091552 | 0.036621 | 0.32043 | 122.6807 | 0.09613 | 122.6669 | 122.7081 | 122.6074 | 122.6166 | 122.58 | -122.7173 | -122.6532 | 122.5891 | 122.6395 | 61.3266 | 61.3312
544 | 122.8134 | -61.3861 | 61.1847 | -0.0016786 | -0.0087116 | 0.0083613 | 0.064465 | -0.022967 | -0.030531 | -0.022819 | -0.00054937 | -0.0078185 | 0.06483 | 0.044724 | -0.016872 | -0.0101 | -0.014819 | -0.12817 | 61.1755 | -61.5005 | 61.1481 | -61.2076 | -61.5967 | -61.615 | -0.091553 | 61.1206 | -61.4182 | 61.2625 | -61.3312 | -61.3632 | -61.2991 | -0.11444 | -0.009155 | -0.036621 | 0.17853 | -0.22888 | -0.21057 | -0.11444 | -0.096131 | -0.032044 | -0.064087 | 0.07782 | 0.054931 | 0.086975 | 0.022888 | 0.11902 | 0.054932 | 0.29297 | 122.6486 | 0.086975 | 122.6807 | 122.6761 | 122.5388 | 122.5616 | 122.5067 | -122.6852 | -122.6028 | 122.5342 | 122.6486 | 61.2579 | 61.2946
545.7031 | 122.8409 | -61.3266 | 61.2534 | 0.01358 | -0.0093524 | 0.0081477 | 0.065747 | -0.024889 | -0.030104 | -0.025383 | 0.0025024 | -0.0095275 | 0.063976 | 0.044297 | -0.021572 | -0.0092456 | -0.014819 | -0.082397 | 61.1664 | -61.441 | 61.2442 | -61.1023 | -61.4777 | -61.5097 | -0.018311 | 61.1435 | -61.3678 | 61.3312 | -61.2396 | -61.2442 | -61.2213 | -0.11444 | -0.086975 | -0.009155 | 0.2243 | -0.18311 | -0.15106 | -0.068665 | -0.036621 | -0.041199 | -0.10986 | 0.07782 | 0.086975 | 0.10529 | 0.082397 | 0.14648 | 0.1236 | 0.33875 | 122.6852 | 0.12817 | 122.699 | 122.6074 | 122.5113 | 122.493 | 122.4701 | -122.6944 | -122.6212 | 122.5708 | 122.6578 | 61.2442 | 61.3083
547.4844 | 122.8271 | -61.3632 | 61.1984 | 0.036468 | -0.0099932 | 0.0094293 | 0.064679 | -0.016771 | -0.028822 | -0.021965 | 0.0055542 | -0.0091003 | 0.063976 | 0.043229 | -0.018367 | -0.0101 | -0.018664 | -0.07782 | 61.1252 | -61.4502 | 61.2717 | -61.0519 | -61.5051 | -61.5143 | 0.018311 | 61.1069 | -61.4136 | 61.2991 | -61.2854 | -61.3129 | -61.29 | -0.086975 | -0.073242 | 0.073242 | 0.31128 | -0.15106 | -0.14191 | -0.064087 | -0.054932 | -0.050354 | -0.091552 | 0.10071 | 0.07782 | 0.073242 | 0.050354 | 0.1236 | 0.10071 | 0.39825 | 122.7219 | 0.12817 | 122.7127 | 122.5754 | 122.5204 | 122.4884 | 122.4701 | -122.6486 | -122.612 | 122.6349 | 122.6624 | 61.2854 | 61.3815
549.2031 | 122.85 | -61.2854 | 61.2762 | 0.0059509 | -0.007857 | 0.0079339 | 0.061902 | -0.019976 | -0.030317 | -0.024314 | -0.00054937 | -0.0076049 | 0.062694 | 0.048783 | -0.023281 | -0.012236 | -0.018664 | 0.009155 | 61.1801 | -61.3998 | 61.3266 | -60.9879 | -61.3953 | -61.4319 | 0.082397 | 61.1801 | -61.3174 | 61.3724 | -61.1847 | -61.2213 | -61.2076 | -0.11444 | -0.09613 | 0.050354 | 0.29755 | -0.14648 | -0.10986 | -0.032044 | 0.004577 | -0.032044 | -0.09613 | 0.09613 | 0.10071 | 0.077819 | 0.064087 | 0.10986 | 0.096131 | 0.41199 | 122.7264 | 0.13275 | 122.6898 | 122.58 | 122.4976 | 122.4655 | 122.4655 | -122.6761 | -122.5937 | 122.612 | 122.6578 | 61.2946 | 61.3678
550.9844 | 122.7676 | -61.3632 | 61.2396 | 0.01358 | -0.007857 | 0.0085749 | 0.065533 | -0.016771 | -0.028822 | -0.022178 | 0.0025024 | -0.0069641 | 0.063549 | 0.041306 | -0.021572 | -0.010527 | -0.014605 | -0.022888 | 61.1984 | -61.4319 | 61.2488 | -61.0977 | -61.4868 | -61.5189 | 0.009155 | 61.171 | -61.3953 | 61.2717 | -61.2991 | -61.3495 | -61.2854 | -0.068665 | -0.041199 | 0.009155 | 0.2655 | -0.15564 | -0.1236 | -0.086975 | -0.054931 | -0.032044 | -0.068665 | 0.032043 | 0.064087 | 0.07782 | 0.013733 | 0.10986 | 0.045777 | 0.33417 | 122.6807 | 0.096131 | 122.6669 | 122.6303 | 122.5662 | 122.5616 | 122.5342 | -122.6715 | -122.6349 | 122.612 | 122.6349 | 61.3403 | 61.3724
552.75 | 122.8409 | -61.3129 | 61.2625 | -0.0016786 | -0.0097796 | 0.0081477 | 0.064892 | -0.019121 | -0.030317 | -0.023674 | -0.00054937 | -0.0097411 | 0.062481 | 0.045579 | -0.017513 | -0.010955 | -0.013537 | -0.064087 | 61.171 | -61.4136 | 61.2671 | -61.0382 | -61.4365 | -61.4685 | 0.027466 | 61.1435 | -61.3358 | 61.3632 | -61.1938 | -61.2213 | -61.2076 | -0.10071 | -0.091553 | 0.004578 | 0.27466 | -0.15564 | -0.1236 | -0.054932 | -0.022888 | -0.022888 | -0.11902 | 0.10071 | 0.11902 | 0.10529 | 0.091553 | 0.12817 | 0.11444 | 0.37537 | 122.6807 | 0.14191 | 122.699 | 122.5845 | 122.4792 | 122.4838 | 122.4564 | -122.6761 | -122.5983 | 122.58 | 122.6761 | 61.2488 | 61.3403
554.5312 | 122.7402 | -61.3953 | 61.2076 | -0.0016786 | -0.0093524 | 0.0098565 | 0.06831 | -0.019549 | -0.02989 | -0.022178 | 0.0025024 | -0.0054687 | 0.066112 | 0.040024 | -0.019435 | -0.011809 | -0.013324 | -0.1236 | 61.1755 | -61.4777 | 61.1252 | -61.2259 | -61.6333 | -61.6379 | -0.14648 | 61.1481 | -61.4227 | 61.1984 | -61.3907 | -61.4273 | -61.3358 | -0.082397 | -0.032044 | -0.082398 | 0.16937 | -0.24261 | -0.23804 | -0.16022 | -0.15564 | -0.027465 | -0.05951 | -0.009156 | 0.004578 | 0.05951 | -0.032043 | 0.086975 | -0.004578 | 0.25177 | 122.6028 | 0.032043 | 122.6212 | 122.6532 | 122.5708 | 122.5708 | 122.5433 | -122.6852 | -122.6303 | 122.5204 | 122.5937 | 61.2717 | 61.2488
556.25 | 122.7676 | -61.3174 | 61.2671 | 0.01358 | -0.004439 | 0.0085749 | 0.066388 | -0.019335 | -0.02989 | -0.023246 | 0.011658 | -0.0076049 | 0.06184 | 0.043229 | -0.023494 | -0.011382 | -0.017383 | -0.036621 | 61.2488 | -61.4456 | 61.2259 | -61.116 | -61.5097 | -61.5189 | -0.032043 | 61.2259 | -61.3861 | 61.2762 | -61.2762 | -61.322 | -61.2762 | -0.12817 | -0.018311 | -0.041199 | 0.20142 | -0.20142 | -0.19226 | -0.073242 | -0.064087 | -0.068664 | -0.041199 | 0.009155 | 0.041199 | 0.041199 | -0.004577 | 0.10986 | 0.064087 | 0.32959 | 122.6715 | 0.10986 | 122.6624 | 122.6944 | 122.612 | 122.5662 | 122.5433 | -122.7127 | -122.6532 | 122.5433 | 122.5937 | 61.2808 | 61.2854
558.0156 | 122.7585 | -61.3403 | 61.2808 | 0.0059509 | -0.0070026 | 0.0096429 | 0.065106 | -0.019762 | -0.029249 | -0.026023 | 0.0055542 | -0.0058959 | 0.06419 | 0.043442 | -0.018154 | -0.0098864 | -0.013965 | -0.036621 | 61.2396 | -61.4594 | 61.2259 | -61.0977 | -61.4868 | -61.5005 | -0.041199 | 61.1984 | -61.3586 | 61.2854 | -61.2717 | -61.3174 | -61.29 | -0.11902 | -0.041199 | -0.054932 | 0.24261 | -0.16022 | -0.14648 | -0.041198 | -0.027465 | -0.018311 | -0.082398 | 0.004577 | 0.068665 | 0.050354 | 0.022888 | 0.068665 | 0.041199 | 0.36163 | 122.6852 | 0.086976 | 122.644 | 122.699 | 122.5571 | 122.58 | 122.5388 | -122.7402 | -122.6395 | 122.5662 | 122.6257 | 61.3037 | 61.2991
559.7812 | 122.7997 | -61.3632 | 61.1664 | 0.028839 | -0.0097796 | 0.010284 | 0.064679 | -0.017412 | -0.029036 | -0.024528 | 0.008606 | -0.0097411 | 0.062481 | 0.049424 | -0.018154 | -0.0096728 | -0.015033 | -0.068665 | 61.116 | -61.441 | 61.2625 | -61.0336 | -61.4777 | -61.5005 | 0.027466 | 61.084 | -61.4044 | 61.3083 | -61.2762 | -61.3129 | -61.2625 | -0.07782 | -0.050354 | 0.09613 | 0.32959 | -0.13733 | -0.11444 | -0.059509 | -0.036621 | -0.041199 | -0.082398 | 0.14191 | 0.086975 | 0.10071 | 0.050354 | 0.14191 | 0.091553 | 0.40741 | 122.7036 | 0.12817 | 122.7127 | 122.5571 | 122.4884 | 122.4792 | 122.4472 | -122.6074 | -122.5708 | 122.6257 | 122.6715 | 61.2946 | 61.3907
561.5 | 122.7127 | -61.3907 | 61.2305 | 0.0059509 | -0.0074298 | 0.0077203 | 0.065533 | -0.016985 | -0.028608 | -0.022178 | -0.00054937 | -0.0058959 | 0.062694 | 0.041947 | -0.022212 | -0.011168 | -0.015033 | -0.059509 | 61.203 | -61.4319 | 61.1664 | -61.1664 | -61.5738 | -61.6058 | -0.073242 | 61.1618 | -61.3953 | 61.2076 | -61.3678 | -61.4136 | -61.3541 | -0.041199 | -0.027466 | -0.064087 | 0.2243 | -0.21515 | -0.18311 | -0.17395 | -0.14191 | -0.004578 | -0.068665 | -0.022888 | 0.022888 | 0.036621 | -0.022888 | 0.041199 | -0.01831 | 0.2655 | 122.5983 | 0.027466 | 122.6028 | 122.6349 | 122.5571 | 122.5937 | 122.5525 | -122.6624 | -122.6257 | 122.5571 | 122.5983 | 61.3312 | 61.3174
563.2656 | 122.7127 | -61.3266 | 61.3174 | -0.0093076 | -0.0093524 | 0.0096429 | 0.064251 | -0.017412 | -0.030745 | -0.024742 | 0.0025024 | -0.0076049 | 0.064617 | 0.040238 | -0.021572 | -0.010955 | -0.015887 | -0.050354 | 61.2167 | -61.3907 | 61.203 | -61.0977 | -61.4822 | -61.5143 | -0.041199 | 61.2213 | -61.3678 | 61.2625 | -61.2991 | -61.3129 | -61.29 | -0.064087 | -0.10071 | -0.11444 | 0.22888 | -0.18768 | -0.15564 | -0.1236 | -0.091553 | -0.041199 | -0.096131 | -0.054932 | 0.027466 | 0.036621 | 0.013733 | 0.07782 | 0.054932 | 0.29297 | 122.5937 | 0.068665 | 122.6303 | 122.6074 | 122.5891 | 122.5433 | 122.5479 | -122.7081 | -122.6852 | 122.5296 | 122.5891 | 61.2762 | 61.2854
565.0312 | 122.8409 | -61.2991 | 61.2488 | -0.0016786 | -0.0087116 | 0.011993 | 0.065533 | -0.018694 | -0.029036 | -0.024101 | -0.00054937 | -0.010596 | 0.065258 | 0.038315 | -0.021358 | -0.009032 | -0.020373 | 0.009155 | 61.1847 | -61.377 | 61.322 | -60.9467 | -61.3861 | -61.4182 | 0.10071 | 61.1526 | -61.29 | 61.3907 | -61.1572 | -61.1938 | -61.1893 | -0.07782 | -0.064087 | 0.073242 | 0.35248 | -0.11902 | -0.086975 | -0.041199 | -0.009155 | 0.009155 | -0.09613 | 0.14191 | 0.14191 | 0.10986 | 0.10528 | 0.10071 | 0.09613 | 0.4303 | 122.699 | 0.13275 | 122.6807 | 122.5616 | 122.4426 | 122.4838 | 122.4518 | -122.6257 | -122.5388 | 122.6212 | 122.6898 | 61.3083 | 61.3998
566.7969 | 122.8363 | -61.2991 | 61.2305 | 0.02121 | -0.011275 | 0.0072931 | 0.063611 | -0.022967 | -0.028608 | -0.024314 | -0.00054937 | -0.0091003 | 0.063976 | 0.04921 | -0.018367 | -0.0086048 | -0.014605 | -0.045776 | 61.1893 | -61.3907 | 61.2808 | -61.0291 | -61.4227 | -61.441 | 0.045776 | 61.1389 | -61.3358 | 61.3632 | -61.1801 | -61.1938 | -61.203 | -0.091553 | -0.041199 | 0.050354 | 0.27008 | -0.14191 | -0.1236 | -0.050354 | -0.032043 | -0.036621 | -0.091553 | 0.13275 | 0.11902 | 0.09613 | 0.10528 | 0.13275 | 0.14191 | 0.36163 | 122.6715 | 0.15564 | 122.699 | 122.58 | 122.4747 | 122.4884 | 122.438 | -122.6212 | -122.5662 | 122.58 | 122.6624 | 61.2534 | 61.3449
568.5156 | 122.731 | -61.3495 | 61.2122 | 0.0059509 | -0.008498 | 0.0094293 | 0.066815 | -0.017199 | -0.027754 | -0.024955 | -0.00054937 | -0.0071777 | 0.06483 | 0.036179 | -0.018154 | -0.011809 | -0.015246 | -0.027466 | 61.2076 | -61.4227 | 61.2167 | -61.1069 | -61.5097 | -61.528 | 0 | 61.1618 | -61.3815 | 61.2625 | -61.3083 | -61.3495 | -61.3083 | -0.073242 | -0.004577 | 0.004578 | 0.24261 | -0.17853 | -0.16022 | -0.10529 | -0.086976 | -0.032044 | -0.050354 | 0.050354 | 0.041198 | 0.041198 | 0 | 0.073242 | 0.032044 | 0.31586 | 122.6395 | 0.073242 | 122.644 | 122.6303 | 122.5433 | 122.5571 | 122.5113 | -122.6349 | -122.5937 | 122.5662 | 122.612 | 61.322 | 61.3495
570.2344 | 122.85 | -61.3174 | 61.2213 | 0.0059509 | -0.011275 | 0.0070795 | 0.063397 | -0.016771 | -0.031385 | -0.022178 | -0.00054937 | -0.0088867 | 0.062908 | 0.053055 | -0.021144 | -0.010955 | -0.017169 | -0.027466 | 61.1572 | -61.3998 | 61.3083 | -61.0062 | -61.4044 | -61.4182 | 0.073242 | 61.116 | -61.3266 | 61.3724 | -61.1847 | -61.1893 | -61.203 | -0.082397 | -0.064086 | 0.086976 | 0.31128 | -0.10071 | -0.086975 | -0.018311 | -0.004578 | -0.009155 | -0.10529 | 0.15106 | 0.13275 | 0.11444 | 0.12817 | 0.1236 | 0.13733 | 0.39368 | 122.7081 | 0.14191 | 122.699 | 122.5571 | 122.4426 | 122.4747 | 122.4335 | -122.6212 | -122.5479 | 122.6257 | 122.6898 | 61.29 | 61.3907
572 | 122.6898 | -61.377 | 61.2122 | 0.01358 | -0.0082842 | 0.011352 | 0.06532 | -0.020617 | -0.027967 | -0.024101 | -0.00054937 | -0.0088867 | 0.062481 | 0.038743 | -0.020503 | -0.011809 | -0.01311 | -0.10986 | 61.171 | -61.4594 | 61.1435 | -61.1984 | -61.6058 | -61.6287 | -0.14191 | 61.1481 | -61.3998 | 61.1984 | -61.3953 | -61.4502 | -61.3815 | -0.082398 | -0.041199 | -0.068664 | 0.17853 | -0.25177 | -0.22888 | -0.16937 | -0.14648 | -0.022888 | -0.064087 | -0.013733 | -0.018311 | -0.004578 | -0.073242 | 0.01831 | -0.050354 | 0.26093 | 122.6028 | 0.004577 | 122.5983 | 122.6303 | 122.5479 | 122.5479 | 122.525 | -122.6715 | -122.612 | 122.5204 | 122.5754 | 61.2671 | 61.235
573.7188 | 122.7402 | -61.3449 | 61.2534 | 0.036468 | -0.0080706 | 0.010925 | 0.06596 | -0.021471 | -0.029676 | -0.024955 | 0.011658 | -0.0041869 | 0.066326 | 0.043015 | -0.021572 | -0.010527 | -0.013324 | -0.032043 | 61.2717 | -61.4227 | 61.2259 | -61.1069 | -61.4594 | -61.5051 | -0.004578 | 61.2167 | -61.3815 | 61.2717 | -61.2671 | -61.3129 | -61.2625 | -0.077819 | 0.01831 | -0.027466 | 0.23804 | -0.16022 | -0.11444 | -0.082398 | -0.036622 | -0.036621 | -0.036621 | 0.01831 | 0.07782 | 0.082398 | 0.032044 | 0.11902 | 0.068665 | 0.31586 | 122.6486 | 0.11444 | 122.6532 | 122.6944 | 122.5983 | 122.6166 | 122.5616 | -122.6761 | -122.6349 | 122.5708 | 122.6166 | 61.3129 | 61.3403
575.5 | 122.7493 | -61.3449 | 61.2534 | 0.02121 | -0.0091388 | 0.0083613 | 0.064892 | -0.019549 | -0.030104 | -0.02346 | 0.0055542 | -0.0071777 | 0.065471 | 0.042161 | -0.021785 | -0.011809 | -0.015674 | -0.027466 | 61.1984 | -61.4319 | 61.2396 | -61.0748 | -61.4822 | -61.5189 | 0 | 61.1481 | -61.3815 | 61.2854 | -61.2946 | -61.3174 | -61.2579 | -0.086975 | -0.054932 | -0.013733 | 0.27008 | -0.17395 | -0.13733 | -0.086975 | -0.050354 | -0.036621 | -0.10529 | 0.032043 | 0.050354 | 0.086975 | 0.027466 | 0.1236 | 0.064087 | 0.35706 | 122.6715 | 0.086975 | 122.6669 | 122.6303 | 122.5296 | 122.5433 | 122.493 | -122.6852 | -122.6349 | 122.5845 | 122.6303 | 61.3174 | 61.3449
577.2031 | 122.7127 | -61.3358 | 61.2671 | -0.0016786 | -0.0087116 | 0.0094293 | 0.064465 | -0.019976 | -0.032454 | -0.024528 | 0.014709 | -0.0076049 | 0.065685 | 0.04686 | -0.021572 | -0.0101 | -0.015674 | -0.050354 | 61.2534 | -61.4182 | 61.203 | -61.1069 | -61.4777 | -61.5097 | -0.041199 | 61.2305 | -61.3907 | 61.2579 | -61.2946 | -61.3174 | -61.2717 | -0.082398 | -0.013733 | -0.064087 | 0.22888 | -0.17395 | -0.14191 | -0.091553 | -0.059509 | -0.054932 | -0.036621 | -0.009155 | 0.041198 | 0.064087 | 0.01831 | 0.11902 | 0.073242 | 0.31128 | 122.6212 | 0.09613 | 122.6486 | 122.6715 | 122.6212 | 122.5891 | 122.5662 | -122.6852 | -122.6578 | 122.5388 | 122.5937 | 61.2854 | 61.2946
578.9688 | 122.8455 | -61.3037 | 61.235 | -0.0016786 | -0.011061 | 0.0075067 | 0.062543 | -0.021898 | -0.028395 | -0.021965 | -0.003601 | -0.0095275 | 0.06419 | 0.046006 | -0.020931 | -0.0094592 | -0.014819 | -0.032043 | 61.1847 | -61.377 | 61.29 | -60.997 | -61.3953 | -61.4273 | 0.068665 | 61.1389 | -61.3174 | 61.3724 | -61.1664 | -61.1938 | -61.1755 | -0.073242 | -0.050354 | 0.054932 | 0.3067 | -0.1236 | -0.091553 | -0.050354 | -0.018311 | -0.013733 | -0.09613 | 0.13733 | 0.13733 | 0.12817 | 0.10986 | 0.14191 | 0.1236 | 0.37994 | 122.6669 | 0.15106 | 122.6898 | 122.5616 | 122.4564 | 122.4884 | 122.4426 | -122.612 | -122.5525 | 122.5937 | 122.6761 | 61.2717 | 61.3724
580.75 | 122.8134 | -61.2808 | 61.2488 | 0.01358 | -0.0089252 | 0.0085749 | 0.064251 | -0.019121 | -0.031172 | -0.023246 | -0.00054937 | -0.0091003 | 0.062908 | 0.040024 | -0.020076 | -0.012236 | -0.017596 | 0.018311 | 61.1664 | -61.3861 | 61.3266 | -60.9787 | -61.3815 | -61.4044 | 0.07782 | 61.1618 | -61.322 | 61.3586 | -61.1481 | -61.1893 | -61.1893 | -0.10529 | -0.082397 | 0.07782 | 0.30212 | -0.1236 | -0.10071 | -0.018311 | 0.004577 | -0.041198 | -0.086975 | 0.10986 | 0.13275 | 0.091553 | 0.091553 | 0.13275 | 0.13275 | 0.40741 | 122.7127 | 0.17395 | 122.6807 | 122.5525 | 122.4838 | 122.4472 | 122.4426 | -122.6349 | -122.5708 | 122.6074 | 122.6395 | 61.2991 | 61.3586
582.5312 | 122.8409 | -61.29 | 61.2167 | 0.0059509 | -0.0070026 | 0.0081477 | 0.063824 | -0.020617 | -0.029676 | -0.024101 | 0.0025024 | -0.011237 | 0.063335 | 0.051133 | -0.020717 | -0.010955 | -0.016955 | 0.004578 | 61.1572 | -61.3907 | 61.3174 | -60.9512 | -61.3678 | -61.3861 | 0.10986 | 61.1481 | -61.3174 | 61.3815 | -61.1389 | -61.1755 | -61.1755 | -0.10071 | -0.059509 | 0.10071 | 0.33874 | -0.09613 | -0.07782 | 0.004578 | 0.022888 | -0.027466 | -0.068665 | 0.1648 | 0.15106 | 0.11444 | 0.11444 | 0.14191 | 0.14191 | 0.43945 | 122.7081 | 0.17853 | 122.699 | 122.5479 | 122.4655 | 122.4472 | 122.438 | -122.6074 | -122.5342 | 122.6074 | 122.6715 | 61.2946 | 61.3998
584.25 | 122.7036 | -61.3953 | 61.2213 | 0.0059509 | -0.0074298 | 0.0077203 | 0.066388 | -0.016344 | -0.030104 | -0.023887 | -0.00054937 | -0.0069641 | 0.062053 | 0.049424 | -0.019863 | -0.011168 | -0.018451 | -0.068665 | 61.1984 | -61.4365 | 61.1755 | -61.1664 | -61.5738 | -61.5875 | -0.091553 | 61.1481 | -61.3861 | 61.2076 | -61.3586 | -61.3998 | -61.3358 | -0.041198 | -0.022888 | -0.045776 | 0.22888 | -0.19226 | -0.17853 | -0.15106 | -0.13733 | 0.009156 | -0.073242 | -0.013732 | 0.036621 | 0.05951 | -0.004577 | 0.050354 | -0.013733 | 0.27008 | 122.612 | 0.027465 | 122.5937 | 122.6349 | 122.5342 | 122.5937 | 122.5433 | -122.6578 | -122.6074 | 122.5708 | 122.6028 | 61.3266 | 61.3037
586.0156 | 122.6898 | -61.3266 | 61.2808 | 0.01358 | -0.0055072 | 0.0072931 | 0.064679 | -0.021471 | -0.032026 | -0.021324 | 0.0025024 | -0.0063233 | 0.063549 | 0.040024 | -0.02499 | -0.012023 | -0.016955 | -0.064087 | 61.2442 | -61.3907 | 61.2076 | -61.116 | -61.4914 | -61.5097 | -0.022888 | 61.2213 | -61.3449 | 61.2534 | -61.2808 | -61.3129 | -61.2717 | -0.064087 | -0.036621 | -0.073242 | 0.21057 | -0.18311 | -0.16479 | -0.11902 | -0.10071 | -0.018311 | -0.05951 | -0.027466 | 0.045776 | 0.054932 | 0.013733 | 0.073243 | 0.032044 | 0.27466 | 122.5983 | 0.064087 | 122.5983 | 122.6349 | 122.5662 | 122.5708 | 122.5479 | -122.6715 | -122.6257 | 122.5342 | 122.58 | 61.2625 | 61.3037
587.7812 | 122.8043 | -61.3403 | 61.171 | -0.0016786 | -0.0091388 | 0.010925 | 0.064679 | -0.016558 | -0.030317 | -0.024314 | 0.0025024 | -0.0093139 | 0.066112 | 0.045151 | -0.017726 | -0.010314 | -0.017169 | -0.1236 | 61.1343 | -61.4456 | 61.1984 | -61.116 | -61.5234 | -61.5326 | -0.018311 | 61.0657 | -61.4044 | 61.2991 | -61.2579 | -61.3083 | -61.2488 | -0.10529 | -0.036621 | 0.027466 | 0.2243 | -0.19226 | -0.18311 | -0.086975 | -0.077819 | -0.064087 | -0.10529 | 0.12817 | 0.082397 | 0.091553 | 0.032043 | 0.15564 | 0.09613 | 0.32959 | 122.644 | 0.14648 | 122.7036 | 122.58 | 122.4701 | 122.4747 | 122.406 | -122.6166 | -122.5754 | 122.5388 | 122.6395 | 61.2167 | 61.322
589.5 | 122.818 | -61.2946 | 61.2167 | 0.01358 | -0.0097796 | 0.0092157 | 0.062115 | -0.02318 | -0.028822 | -0.025383 | -0.003601 | -0.0080321 | 0.063335 | 0.04686 | -0.019222 | -0.0088184 | -0.014392 | -0.073242 | 61.1343 | -61.3861 | 61.2534 | -61.0474 | -61.4456 | -61.4639 | 0.018311 | 61.1298 | -61.3449 | 61.3403 | -61.1801 | -61.2076 | -61.1847 | -0.091552 | -0.082398 | 0.036621 | 0.24719 | -0.16937 | -0.15106 | -0.07782 | -0.05951 | -0.050354 | -0.086975 | 0.1236 | 0.11444 | 0.10986 | 0.086975 | 0.16022 | 0.13733 | 0.33875 | 122.6395 | 0.16479 | 122.6852 | 122.5204 | 122.4747 | 122.4289 | 122.4243 | -122.6028 | -122.5616 | 122.5479 | 122.6349 | 61.2213 | 61.3129
591.2188 | 122.7905 | -61.3358 | 61.1572 | 0.044098 | -0.0063616 | 0.0087885 | 0.066815 | -0.018267 | -0.027327 | -0.022392 | 0.011658 | -0.0080321 | 0.066326 | 0.042588 | -0.016872 | -0.010955 | -0.017383 | -0.059509 | 61.116 | -61.4273 | 61.2488 | -61.0428 | -61.4777 | -61.4868 | 0.036621 | 61.084 | -61.377 | 61.2991 | -61.2396 | -61.2808 | -61.235 | -0.091553 | -0.041199 | 0.091552 | 0.29297 | -0.15106 | -0.14191 | -0.059509 | -0.050354 | -0.041199 | -0.073243 | 0.14191 | 0.09613 | 0.10071 | 0.054931 | 0.14191 | 0.09613 | 0.38452 | 122.6761 | 0.13733 | 122.6761 | 122.5433 | 122.4609 | 122.4518 | 122.4197 | -122.5845 | -122.5342 | 122.5845 | 122.6349 | 61.2762 | 61.3724
593 | 122.731 | -61.3266 | 61.2076 | 0.02121 | -0.0093524 | 0.0087885 | 0.065747 | -0.019762 | -0.031599 | -0.022819 | 0.0055542 | -0.0073913 | 0.063549 | 0.047074 | -0.021999 | -0.0101 | -0.015887 | -0.036621 | 61.2122 | -61.4044 | 61.235 | -61.0886 | -61.4822 | -61.5097 | 0.013733 | 61.1572 | -61.3632 | 61.2762 | -61.29 | -61.322 | -61.2717 | -0.07782 | 0.004577 | 0.027465 | 0.23804 | -0.18311 | -0.15564 | -0.10529 | -0.07782 | -0.036621 | -0.050354 | 0.068664 | 0.036621 | 0.054932 | 0.004578 | 0.091553 | 0.041199 | 0.31586 | 122.6395 | 0.073242 | 122.6395 | 122.6166 | 122.5204 | 122.5388 | 122.4838 | -122.612 | -122.5708 | 122.5616 | 122.6028 | 61.29 | 61.3403
594.7656 | 122.818 | -61.2625 | 61.2259 | -0.0016786 | -0.010207 | 0.0075067 | 0.062756 | -0.021685 | -0.031813 | -0.024314 | 0.0025024 | -0.0097411 | 0.063549 | 0.042588 | -0.022853 | -0.0094592 | -0.015246 | 0 | 61.2076 | -61.3678 | 61.3358 | -60.9558 | -61.3724 | -61.3998 | 0.10986 | 61.1572 | -61.3129 | 61.3678 | -61.1389 | -61.1755 | -61.1801 | -0.10529 | -0.01831 | 0.10986 | 0.3067 | -0.13733 | -0.10986 | -0.032043 | -0.004577 | -0.050354 | -0.068664 | 0.14191 | 0.1236 | 0.082397 | 0.086975 | 0.13275 | 0.13733 | 0.41199 | 122.7036 | 0.17395 | 122.6807 | 122.5754 | 122.4701 | 122.4701 | 122.4197 | -122.5937 | -122.5388 | 122.5983 | 122.6303 | 61.2625 | 61.3724
596.5625 | 122.7127 | -61.3678 | 61.1893 | 0.02121 | -0.0082842 | 0.0081477 | 0.068738 | -0.014635 | -0.027967 | -0.024314 | 0.0025024 | -0.0082459 | 0.063121 | 0.042374 | -0.019008 | -0.0101 | -0.018023 | -0.12817 | 61.1847 | -61.4639 | 61.116 | -61.1938 | -61.615 | -61.6104 | -0.10529 | 61.1069 | -61.3815 | 61.2076 | -61.3678 | -61.409 | -61.3174 | -0.09613 | -0.004578 | -0.073242 | 0.17395 | -0.24262 | -0.24719 | -0.14648 | -0.15106 | -0.013733 | -0.082397 | 0.018311 | 0 | 0.050354 | -0.041199 | 0.064087 | -0.027466 | 0.27008 | 122.58 | 0.013733 | 122.5891 | 122.6486 | 122.4884 | 122.5525 | 122.4747 | -122.6532 | -122.5708 | 122.4838 | 122.5754 | 61.2396 | 61.2625
598.2812 | 122.7997 | -61.2671 | 61.2396 | 0.01358 | -0.006148 | 0.0090021 | 0.064465 | -0.024248 | -0.031172 | -0.021751 | 0.0055542 | -0.010809 | 0.060985 | 0.048783 | -0.018581 | -0.0096728 | -0.020373 | -0.064087 | 61.1664 | -61.3907 | 61.235 | -61.0565 | -61.4273 | -61.4502 | 0.009155 | 61.1252 | -61.3037 | 61.3312 | -61.1893 | -61.2076 | -61.1984 | -0.1236 | -0.073242 | -0.004578 | 0.21057 | -0.1831 | -0.16022 | -0.059509 | -0.036621 | -0.036621 | -0.11444 | 0.091553 | 0.07782 | 0.068665 | 0.059509 | 0.10529 | 0.09613 | 0.33417 | 122.6257 | 0.11444 | 122.6349 | 122.5571 | 122.4289 | 122.4335 | 122.3923 | -122.6303 | -122.5433 | 122.5021 | 122.5983 | 61.203 | 61.2762
600.0469 | 122.7219 | -61.3449 | 61.2122 | 0.01358 | -0.0063616 | 0.0092157 | 0.066388 | -0.016985 | -0.030745 | -0.022819 | 0.008606 | -0.0052551 | 0.067394 | 0.043015 | -0.022212 | -0.012877 | -0.016955 | -0.027466 | 61.171 | -61.4365 | 61.2259 | -61.0657 | -61.5051 | -61.496 | 0.022888 | 61.1618 | -61.3495 | 61.2717 | -61.2717 | -61.3266 | -61.2534 | -0.091552 | -0.041199 | 0.013733 | 0.27924 | -0.15106 | -0.16022 | -0.05951 | -0.068665 | -0.004577 | -0.050354 | 0.059509 | 0.073243 | 0.091553 | 0.018311 | 0.09613 | 0.022888 | 0.37079 | 122.6624 | 0.07782 | 122.6212 | 122.6074 | 122.5113 | 122.5159 | 122.5067 | -122.6486 | -122.5616 | 122.5708 | 122.6166 | 61.3174 | 61.3678
601.8281 | 122.7173 | -61.3815 | 61.1893 | 0.0059509 | -0.0074298 | 0.0092157 | 0.06596 | -0.017626 | -0.031385 | -0.026237 | 0.0055542 | -0.0086731 | 0.062267 | 0.044938 | -0.019649 | -0.012023 | -0.012683 | -0.15106 | 61.1801 | -61.4456 | 61.1069 | -61.203 | -61.6013 | -61.5967 | -0.1236 | 61.1389 | -61.3953 | 61.203 | -61.3678 | -61.409 | -61.322 | -0.064087 | -0.009155 | -0.082397 | 0.17853 | -0.21515 | -0.21973 | -0.15106 | -0.15564 | -0.013733 | -0.050354 | 0.013733 | 0.013733 | 0.05951 | -0.027466 | 0.073243 | -0.013733 | 0.24262 | 122.5525 | 0.027466 | 122.5983 | 122.6257 | 122.5342 | 122.5616 | 122.5204 | -122.6349 | -122.5845 | 122.4884 | 122.5845 | 61.2305 | 61.2579
603.6094 | 122.7493 | -61.3083 | 61.2442 | 0.0059509 | -0.0089252 | 0.0085749 | 0.063397 | -0.021685 | -0.030317 | -0.022819 | 0.008606 | -0.0097411 | 0.062481 | 0.046219 | -0.023067 | -0.0101 | -0.015033 | 0.009155 | 61.1938 | -61.3541 | 61.2991 | -60.9833 | -61.377 | -61.4227 | 0.07782 | 61.171 | -61.3174 | 61.3174 | -61.1801 | -61.2259 | -61.2076 | -0.045776 | -0.050354 | 0.054931 | 0.32501 | -0.11444 | -0.068664 | -0.068664 | -0.022888 | -0.009155 | -0.073243 | 0.073242 | 0.12817 | 0.10071 | 0.082398 | 0.10986 | 0.091553 | 0.37079 | 122.6532 | 0.13733 | 122.6349 | 122.5479 | 122.4884 | 122.5021 | 122.4792 | -122.5983 | -122.5616 | 122.6074 | 122.6257 | 61.3174 | 61.3861
605.3281 | 122.6715 | -61.3724 | 61.2259 | 0.0059509 | -0.0076434 | 0.0092157 | 0.066601 | -0.016771 | -0.035017 | -0.021537 | 0.0025024 | -0.0058959 | 0.062053 | 0.047501 | -0.019863 | -0.0096728 | -0.014605 | -0.13733 | 61.1847 | -61.4319 | 61.1023 | -61.2442 | -61.615 | -61.6241 | -0.14191 | 61.1206 | -61.3815 | 61.1801 | -61.3861 | -61.4136 | -61.3358 | -0.05951 | -0.041199 | -0.1236 | 0.12817 | -0.25177 | -0.24262 | -0.19226 | -0.1831 | -0.009156 | -0.10529 | -0.045776 | -0.013733 | 0.036621 | -0.041199 | 0.045777 | -0.032043 | 0.18768 | 122.5342 | -0.004577 | 122.5616 | 122.6166 | 122.5021 | 122.5571 | 122.493 | -122.6578 | -122.6074 | 122.4747 | 122.5525 | 61.235 | 61.2305
607.0938 | 122.7173 | -61.3266 | 61.2579 | 0.028839 | -0.0059344 | 0.0092157 | 0.063397 | -0.01784 | -0.029249 | -0.021537 | 0.011658 | -0.0071777 | 0.064617 | 0.045792 | -0.020931 | -0.011809 | -0.013965 | -0.054932 | 61.2625 | -61.3907 | 61.2076 | -61.0977 | -61.4914 | -61.5005 | -0.032043 | 61.1938 | -61.3403 | 61.2442 | -61.2717 | -61.2854 | -61.2396 | -0.064087 | 0.004577 | -0.050354 | 0.22888 | -0.17395 | -0.16479 | -0.10986 | -0.10071 | -0.013733 | -0.064087 | -0.013733 | 0.054932 | 0.086975 | 0.041199 | 0.10071 | 0.054932 | 0.29297 | 122.5983 | 0.068665 | 122.5845 | 122.6532 | 122.5342 | 122.5891 | 122.5204 | -122.6486 | -122.5983 | 122.5342 | 122.5708 | 61.2717 | 61.2946
608.8594 | 122.6761 | -61.2946 | 61.2762 | 0.0059509 | -0.0082842 | 0.0081477 | 0.063611 | -0.021898 | -0.030745 | -0.023674 | 0.0025024 | -0.0088867 | 0.06419 | 0.034043 | -0.023067 | -0.01245 | -0.014178 | -0.068665 | 61.2305 | -61.3815 | 61.1847 | -61.1023 | -61.4822 | -61.5005 | -0.036621 | 61.2076 | -61.3358 | 61.2396 | -61.2808 | -61.3129 | -61.2488 | -0.086975 | -0.045776 | -0.091553 | 0.19226 | -0.20599 | -0.18768 | -0.11902 | -0.10071 | -0.041198 | -0.068664 | -0.036621 | 0.013733 | 0.045777 | -0.01831 | 0.086975 | 0.022888 | 0.27924 | 122.5662 | 0.054931 | 122.5754 | 122.612 | 122.5433 | 122.525 | 122.5021 | -122.6578 | -122.612 | 122.4792 | 122.5342 | 61.2259 | 61.2579
610.6562 | 122.8043 | -61.2808 | 61.2259 | -0.0016786 | -0.0087116 | 0.0072931 | 0.063397 | -0.016131 | -0.03224 | -0.026878 | 0.0025024 | -0.0093139 | 0.063549 | 0.046433 | -0.020717 | -0.0098864 | -0.016955 | 0.009155 | 61.1847 | -61.3403 | 61.3129 | -60.9558 | -61.377 | -61.3953 | 0.10986 | 61.1389 | -61.2946 | 61.3495 | -61.1298 | -61.1893 | -61.1755 | -0.059509 | -0.041199 | 0.086975 | 0.32501 | -0.11444 | -0.09613 | -0.054932 | -0.036621 | -0.013733 | -0.086975 | 0.1236 | 0.15106 | 0.10529 | 0.091553 | 0.11902 | 0.10529 | 0.38452 | 122.6532 | 0.16479 | 122.644 | 122.525 | 122.4335 | 122.4655 | 122.4197 | -122.5662 | -122.5204 | 122.5937 | 122.6303 | 61.29 | 61.3907
612.375 | 122.7264 | -61.3495 | 61.2259 | 0.0059509 | -0.0076434 | 0.0085749 | 0.064679 | -0.020403 | -0.029249 | -0.024528 | 0.0025024 | -0.0067505 | 0.063762 | 0.041306 | -0.019435 | -0.0101 | -0.01546 | -0.036621 | 61.1938 | -61.377 | 61.2213 | -61.0794 | -61.4914 | -61.5005 | -0.004578 | 61.1526 | -61.3266 | 61.2534 | -61.2808 | -61.3312 | -61.2946 | -0.027466 | -0.032043 | -0.004578 | 0.27008 | -0.15106 | -0.14191 | -0.1236 | -0.11444 | 0.022888 | -0.073242 | 0.027466 | 0.068664 | 0.054931 | 0.01831 | 0.032043 | -0.004578 | 0.29755 | 122.5983 | 0.045776 | 122.58 | 122.5708 | 122.4792 | 122.5433 | 122.5021 | -122.6028 | -122.5525 | 122.5708 | 122.6028 | 61.3129 | 61.3449
614.1562 | 122.7219 | -61.3129 | 61.2396 | 0.02121 | -0.0093524 | 0.0092157 | 0.065106 | -0.017412 | -0.031385 | -0.020469 | 0.008606 | -0.0065369 | 0.062694 | 0.037461 | -0.021785 | -0.011382 | -0.01781 | -0.045776 | 61.235 | -61.3998 | 61.2167 | -61.0977 | -61.4594 | -61.4822 | -0.009155 | 61.1755 | -61.3586 | 61.2534 | -61.2534 | -61.29 | -61.2396 | -0.086975 | -0.004578 | -0.022888 | 0.21515 | -0.16937 | -0.14648 | -0.082398 | -0.05951 | -0.045777 | -0.064087 | 0.013733 | 0.059509 | 0.073242 | 0.022888 | 0.11902 | 0.068665 | 0.30212 | 122.6166 | 0.10529 | 122.612 | 122.6349 | 122.5342 | 122.5479 | 122.4884 | -122.6395 | -122.5983 | 122.5296 | 122.5662 | 61.2671 | 61.3037
615.9531 | 122.699 | -61.3129 | 61.2625 | 0.028839 | -0.0065754 | 0.0098565 | 0.064038 | -0.015917 | -0.031385 | -0.023033 | 0.0055542 | -0.0080321 | 0.065685 | 0.045365 | -0.020931 | -0.011382 | -0.011828 | -0.036621 | 61.2534 | -61.409 | 61.1847 | -61.1114 | -61.4594 | -61.496 | -0.022888 | 61.2213 | -61.3495 | 61.2488 | -61.2534 | -61.29 | -61.2396 | -0.096131 | -0.009155 | -0.07782 | 0.20142 | -0.18311 | -0.14648 | -0.086975 | -0.050354 | -0.036621 | -0.041199 | -0.013733 | 0.059509 | 0.073242 | 0.022888 | 0.10986 | 0.059509 | 0.29755 | 122.5937 | 0.09613 | 122.5983 | 122.6624 | 122.5708 | 122.5662 | 122.5342 | -122.6715 | -122.612 | 122.4976 | 122.5616 | 61.2762 | 61.29
617.7344 | 122.7173 | -61.2946 | 61.29 | 0.036468 | -0.007857 | 0.0085749 | 0.062329 | -0.020403 | -0.031385 | -0.02581 | 0.008606 | -0.0048279 | 0.062908 | 0.038102 | -0.020503 | -0.010955 | -0.014819 | -0.032043 | 61.2534 | -61.3953 | 61.1938 | -61.1069 | -61.4868 | -61.5097 | -0.041199 | 61.1984 | -61.3495 | 61.2488 | -61.2488 | -61.29 | -61.2442 | -0.10071 | -0.036621 | -0.09613 | 0.18768 | -0.21515 | -0.19226 | -0.11444 | -0.091552 | -0.054931 | -0.091553 | -0.041199 | 0.045777 | 0.050354 | 0.004578 | 0.10529 | 0.059509 | 0.28839 | 122.5891 | 0.10071 | 122.5983 | 122.6486 | 122.5479 | 122.5479 | 122.493 | -122.6852 | -122.6395 | 122.4884 | 122.5433 | 61.2625 | 61.2534
619.5 | 122.7448 | -61.3495 | 61.1618 | -0.0016786 | -0.0076434 | 0.010711 | 0.066174 | -0.022326 | -0.029036 | -0.023674 | -0.00054937 | -0.0071777 | 0.063762 | 0.04152 | -0.016658 | -0.0092456 | -0.014819 | -0.12817 | 61.171 | -61.4502 | 61.1114 | -61.1755 | -61.6013 | -61.5875 | -0.11444 | 61.0748 | -61.3861 | 61.2305 | -61.322 | -61.3541 | -61.2991 | -0.10071 | 0.009155 | -0.050354 | 0.17395 | -0.23804 | -0.25177 | -0.13733 | -0.15106 | -0.036621 | -0.086975 | 0.068665 | 0.027466 | 0.050354 | -0.004578 | 0.086975 | 0.032043 | 0.27466 | 122.5616 | 0.064087 | 122.6166 | 122.6212 | 122.4609 | 122.5204 | 122.4243 | -122.612 | -122.5479 | 122.4609 | 122.58 | 61.2213 | 61.235
621.2812 | 122.6532 | -61.3541 | 61.1893 | -0.0093076 | -0.00508 | 0.0085749 | 0.066601 | -0.016558 | -0.02989 | -0.020897 | 0.0025024 | -0.0073913 | 0.065899 | 0.043656 | -0.018794 | -0.010741 | -0.016101 | -0.064087 | 61.1755 | -61.4136 | 61.171 | -61.1206 | -61.5509 | -61.5646 | -0.07782 | 61.1114 | -61.377 | 61.203 | -61.3312 | -61.3678 | -61.3037 | -0.059509 | -0.013733 | -0.018311 | 0.23346 | -0.21057 | -0.19684 | -0.15106 | -0.13733 | -0.022888 | -0.07782 | 0.013733 | 0.022888 | 0.050354 | -0.013733 | 0.073242 | 0.009155 | 0.29297 | 122.5845 | 0.045776 | 122.58 | 122.5891 | 122.4884 | 122.5296 | 122.4655 | -122.6028 | -122.5662 | 122.525 | 122.5571 | 61.29 | 61.2762
622.9844 | 122.6807 | -61.377 | 61.1938 | 0.0059509 | -0.006148 | 0.010498 | 0.065533 | -0.017626 | -0.029463 | -0.026237 | 0.0025024 | -0.0088867 | 0.065685 | 0.045579 | -0.019649 | -0.010314 | -0.015033 | -0.14191 | 61.1572 | -61.4685 | 61.0794 | -61.2213 | -61.615 | -61.6013 | -0.15106 | 61.116 | -61.3907 | 61.1893 | -61.3678 | -61.4044 | -61.3266 | -0.091553 | -0.036621 | -0.11444 | 0.15564 | -0.2243 | -0.23804 | -0.13275 | -0.14648 | -0.013733 | -0.07782 | -0.004578 | 0.009155 | 0.050354 | -0.027466 | 0.064087 | -0.013733 | 0.24719 | 122.5479 | 0.022888 | 122.58 | 122.6257 | 122.5067 | 122.5342 | 122.493 | -122.6624 | -122.5845 | 122.4564 | 122.5662 | 61.235 | 61.2259
624.75 | 122.7173 | -61.3129 | 61.2625 | 0.02121 | -0.0091388 | 0.0083613 | 0.062756 | -0.015703 | -0.030745 | -0.024955 | 0.011658 | -0.0073913 | 0.063549 | 0.047288 | -0.019863 | -0.010527 | -0.016101 | -0.059509 | 61.2625 | -61.4227 | 61.1984 | -61.0886 | -61.4777 | -61.4914 | -0.036621 | 61.171 | -61.3358 | 61.2579 | -61.2579 | -61.3083 | -61.2259 | -0.10986 | 0 | -0.064087 | 0.2243 | -0.17853 | -0.16479 | -0.068665 | -0.054932 | -0.022888 | -0.091553 | -0.004577 | 0.054931 | 0.086975 | 0.004577 | 0.10986 | 0.027465 | 0.33417 | 122.6212 | 0.077819 | 122.5937 | 122.6852 | 122.5067 | 122.5754 | 122.4838 | -122.6852 | -122.5983 | 122.5113 | 122.5708 | 61.2534 | 61.2762
626.4531 | 122.7264 | -61.3586 | 61.1618 | -0.0093076 | -0.007857 | 0.0092157 | 0.064679 | -0.016985 | -0.030745 | -0.024101 | -0.003601 | -0.0086731 | 0.064617 | 0.045151 | -0.016872 | -0.0094592 | -0.015246 | -0.14191 | 61.1664 | -61.4502 | 61.1114 | -61.1755 | -61.5875 | -61.5784 | -0.10986 | 61.0931 | -61.409 | 61.2076 | -61.3266 | -61.3632 | -61.2854 | -0.091552 | 0.004578 | -0.050354 | 0.18311 | -0.21973 | -0.22888 | -0.12817 | -0.13733 | -0.050354 | -0.068664 | 0.045777 | 0.032044 | 0.073243 | -0.004577 | 0.1236 | 0.045777 | 0.27466 | 122.5616 | 0.082398 | 122.6166 | 122.6166 | 122.5021 | 122.525 | 122.4518 | -122.612 | -122.5708 | 122.4701 | 122.5662 | 61.2167 | 61.2488
628.1562 | 122.7036 | -61.2991 | 61.2488 | 0.01358 | -0.0074298 | 0.0094293 | 0.067029 | -0.022753 | -0.030317 | -0.026023 | 0.011658 | -0.0061095 | 0.062694 | 0.040452 | -0.019863 | -0.0096728 | -0.014605 | -0.045776 | 61.235 | -61.3907 | 61.1984 | -61.0794 | -61.441 | -61.4822 | -0.018311 | 61.1938 | -61.3266 | 61.2534 | -61.2488 | -61.2808 | -61.235 | -0.091553 | -0.013733 | -0.050354 | 0.21973 | -0.18311 | -0.14191 | -0.091553 | -0.050354 | -0.027466 | -0.054931 | 0.004578 | 0.050354 | 0.064087 | 0.01831 | 0.091553 | 0.045776 | 0.31128 | 122.5891 | 0.07782 | 122.58 | 122.6257 | 122.5204 | 122.5342 | 122.493 | -122.6395 | -122.5754 | 122.4976 | 122.5525 | 61.2534 | 61.2808
629.9531 | 122.7631 | -61.3403 | 61.1664 | 0.02121 | -0.0097796 | 0.0096429 | 0.063824 | -0.01549 | -0.031172 | -0.023033 | 0.0055542 | -0.0061095 | 0.063976 | 0.045792 | -0.018154 | -0.0071094 | -0.014605 | -0.07782 | 61.0977 | -61.4548 | 61.2396 | -61.0245 | -61.4456 | -61.4685 | 0.013733 | 61.0794 | -61.377 | 61.2717 | -61.2488 | -61.2717 | -61.2442 | -0.11444 | -0.068665 | 0.073242 | 0.31586 | -0.12817 | -0.10529 | -0.013733 | 0.009155 | -0.036621 | -0.086975 | 0.10529 | 0.091553 | 0.09613 | 0.068665 | 0.13275 | 0.10529 | 0.4303 | 122.6944 | 0.12817 | 122.6486 | 122.5525 | 122.4564 | 122.438 | 122.4197 | -122.6212 | -122.5433 | 122.58 | 122.612 | 61.2625 | 61.3541
631.7344 | 122.7356 | -61.2808 | 61.2488 | 0.0059509 | -0.0093524 | 0.0072931 | 0.062329 | -0.020189 | -0.028395 | -0.025383 | 0.0025024 | -0.0095275 | 0.065471 | 0.053055 | -0.020717 | -0.0094592 | -0.015674 | 0 | 61.1755 | -61.3586 | 61.2991 | -60.9879 | -61.3678 | -61.4044 | 0.068665 | 61.1481 | -61.3083 | 61.3129 | -61.1938 | -61.2167 | -61.2076 | -0.07782 | -0.073242 | 0.050354 | 0.29297 | -0.1236 | -0.086975 | -0.045776 | -0.009155 | -0.027466 | -0.10071 | 0.064087 | 0.086975 | 0.073242 | 0.064087 | 0.10071 | 0.091553 | 0.37079 | 122.6578 | 0.11444 | 122.6212 | 122.5342 | 122.4564 | 122.4564 | 122.4289 | -122.6074 | -122.5571 | 122.58 | 122.5937 | 61.2808 | 61.3495
633.4375 | 122.6624 | -61.377 | 61.2122 | -0.0016786 | -0.0080706 | 0.0087885 | 0.066815 | -0.01848 | -0.028181 | -0.022178 | 0.008606 | -0.0082459 | 0.062694 | 0.040452 | -0.019649 | -0.010955 | -0.017169 | -0.10071 | 61.1481 | -61.441 | 61.1114 | -61.1984 | -61.6013 | -61.5921 | -0.13733 | 61.1206 | -61.3907 | 61.1618 | -61.3815 | -61.4182 | -61.3312 | -0.064087 | -0.064087 | -0.10071 | 0.17853 | -0.21515 | -0.2243 | -0.15106 | -0.16022 | -0.013733 | -0.091553 | -0.050354 | -0.004578 | 0.045776 | -0.041199 | 0.059509 | -0.027466 | 0.24262 | 122.5525 | 0.009155 | 122.5525 | 122.5891 | 122.5113 | 122.525 | 122.4976 | -122.6532 | -122.6028 | 122.4884 | 122.5388 | 61.2762 | 61.2396
635.1406 | 122.6669 | -61.3632 | 61.1984 | 0.0059509 | -0.006789 | 0.01007 | 0.067456 | -0.016985 | -0.029676 | -0.027732 | -0.00054937 | -0.0063233 | 0.06419 | 0.041306 | -0.020076 | -0.0098864 | -0.012896 | -0.082397 | 61.1526 | -61.3861 | 61.1343 | -61.1343 | -61.5555 | -61.5738 | -0.07782 | 61.116 | -61.3861 | 61.1801 | -61.3403 | -61.377 | -61.3037 | -0.022888 | -0.045776 | -0.064087 | 0.22888 | -0.21057 | -0.19226 | -0.18768 | -0.16937 | -0.022888 | -0.082397 | -0.01831 | 0.022888 | 0.059509 | -0.013733 | 0.082397 | 0.009155 | 0.25177 | 122.5204 | 0.045776 | 122.5662 | 122.5388 | 122.5021 | 122.5159 | 122.4792 | -122.5845 | -122.5845 | 122.4976 | 122.5433 | 61.2808 | 61.2854
636.9062 | 122.7402 | -61.3129 | 61.2167 | 0.02121 | -0.0074298 | 0.01007 | 0.063611 | -0.019121 | -0.029676 | -0.023246 | 0.0055542 | -0.010809 | 0.063762 | 0.04451 | -0.019435 | -0.0098864 | -0.011615 | -0.086975 | 61.1481 | -61.3815 | 61.1938 | -61.0657 | -61.4731 | -61.496 | -0.032043 | 61.084 | -61.3632 | 61.2488 | -61.2442 | -61.2717 | -61.235 | -0.068665 | -0.068665 | -0.022888 | 0.24719 | -0.18311 | -0.16022 | -0.11444 | -0.091552 | -0.050354 | -0.13275 | 0.032043 | 0.068664 | 0.07782 | 0.041199 | 0.12817 | 0.091553 | 0.31586 | 122.5754 | 0.11902 | 122.612 | 122.5296 | 122.4472 | 122.4609 | 122.3969 | -122.5983 | -122.58 | 122.5067 | 122.5616 | 61.2259 | 61.2808
638.6875 | 122.6624 | -61.3678 | 61.1801 | 0.0059509 | -0.0057208 | 0.010498 | 0.06596 | -0.016344 | -0.030104 | -0.023246 | -0.00054937 | -0.0048279 | 0.063335 | 0.041092 | -0.019649 | -0.0096728 | -0.02016 | -0.13733 | 61.1618 | -61.441 | 61.0931 | -61.2122 | -61.6013 | -61.5921 | -0.13733 | 61.0977 | -61.3861 | 61.1618 | -61.3586 | -61.3907 | -61.3129 | -0.073242 | -0.018311 | -0.086975 | 0.15564 | -0.2243 | -0.23346 | -0.15106 | -0.16022 | -0.01831 | -0.082398 | -0.018311 | 0.009155 | 0.054932 | -0.022888 | 0.073242 | -0.004578 | 0.22888 | 122.5342 | 0.027465 | 122.5479 | 122.6028 | 122.4838 | 122.5296 | 122.4655 | -122.6212 | -122.5662 | 122.4609 | 122.5296 | 61.2305 | 61.2305
640.4844 | 122.7951 | -61.2671 | 61.203 | -0.0016786 | -0.010634 | 0.0094293 | 0.061047 | -0.025103 | -0.031599 | -0.024314 | 0.0025024 | -0.011023 | 0.062053 | 0.040238 | -0.02029 | -0.0075366 | -0.015246 | -0.050354 | 61.1435 | -61.3724 | 61.2488 | -60.997 | -61.3953 | -61.4044 | 0.045776 | 61.1252 | -61.3037 | 61.3358 | -61.1435 | -61.1572 | -61.1435 | -0.10528 | -0.059509 | 0.045776 | 0.27008 | -0.13733 | -0.12817 | -0.032044 | -0.022889 | -0.036621 | -0.07782 | 0.13275 | 0.1236 | 0.1236 | 0.10986 | 0.16022 | 0.14648 | 0.37537 | 122.6212 | 0.16022 | 122.6395 | 122.5159 | 122.4289 | 122.4106 | 122.3923 | -122.5754 | -122.5067 | 122.5159 | 122.6028 | 61.2167 | 61.3129
642.1875 | 122.699 | -61.3174 | 61.2396 | 0.028839 | -0.0080706 | 0.0070795 | 0.065533 | -0.019976 | -0.031599 | -0.02581 | 0.011658 | -0.0088867 | 0.063976 | 0.043656 | -0.022426 | -0.010741 | -0.014819 | -0.036621 | 61.2305 | -61.3953 | 61.1801 | -61.0931 | -61.441 | -61.4777 | -0.027466 | 61.1801 | -61.3312 | 61.2396 | -61.2488 | -61.2854 | -61.2305 | -0.07782 | -0.009155 | -0.059509 | 0.2243 | -0.16022 | -0.1236 | -0.082397 | -0.045776 | -0.013733 | -0.059509 | 0 | 0.068665 | 0.086975 | 0.032044 | 0.10071 | 0.045777 | 0.30212 | 122.5754 | 0.082398 | 122.5708 | 122.6257 | 122.5113 | 122.5479 | 122.4976 | -122.6349 | -122.5708 | 122.4976 | 122.5571 | 61.2808 | 61.29
643.8906 | 122.6852 | -61.3312 | 61.235 | 0.0059509 | -0.0065754 | 0.0096429 | 0.064892 | -0.021685 | -0.03224 | -0.023033 | 0.0025024 | -0.0071777 | 0.06419 | 0.037034 | -0.018794 | -0.012877 | -0.017596 | -0.036621 | 61.1938 | -61.4227 | 61.1984 | -61.0611 | -61.4868 | -61.5051 | -0.018311 | 61.1481 | -61.3312 | 61.2305 | -61.2854 | -61.3403 | -61.2717 | -0.091552 | -0.041198 | -0.036621 | 0.27008 | -0.17395 | -0.15564 | -0.082398 | -0.064087 | 0 | -0.086975 | -0.004577 | 0.045777 | 0.05951 | -0.009155 | 0.05951 | -0.009155 | 0.36163 | 122.6212 | 0.045777 | 122.5616 | 122.6166 | 122.4792 | 122.525 | 122.4792 | -122.6578 | -122.5662 | 122.5296 | 122.5616 | 61.2946 | 61.3129
645.6094 | 122.6578 | -61.3037 | 61.2717 | -0.0093076 | -0.0074298 | 0.0075067 | 0.063183 | -0.019976 | -0.031599 | -0.023887 | 0.0055542 | -0.0091003 | 0.064403 | 0.041306 | -0.020931 | -0.011168 | -0.015887 | -0.022888 | 61.1847 | -61.3815 | 61.2122 | -61.0519 | -61.441 | -61.4502 | -0.027466 | 61.1801 | -61.322 | 61.235 | -61.2579 | -61.2762 | -61.2396 | -0.07782 | -0.086975 | -0.059509 | 0.25177 | -0.14648 | -0.13733 | -0.068664 | -0.059509 | -0.01831 | -0.091552 | -0.036621 | 0.045776 | 0.064087 | 0.027466 | 0.082397 | 0.045776 | 0.32959 | 122.5937 | 0.064086 | 122.5571 | 122.5662 | 122.5021 | 122.4884 | 122.4838 | -122.6532 | -122.5937 | 122.5159 | 122.5388 | 61.2808 | 61.2762
647.3281 | 122.644 | -61.3586 | 61.1847 | 0.0059509 | -0.0076434 | 0.010284 | 0.06596 | -0.020403 | -0.027967 | -0.02346 | 0.0055542 | -0.0069641 | 0.060772 | 0.034257 | -0.020076 | -0.0098864 | -0.016742 | -0.086975 | 61.1664 | -61.4182 | 61.1343 | -61.1435 | -61.5601 | -61.5875 | -0.10529 | 61.1069 | -61.3815 | 61.1801 | -61.3495 | -61.3861 | -61.3129 | -0.059509 | -0.01831 | -0.050354 | 0.21515 | -0.22888 | -0.20142 | -0.16937 | -0.14191 | -0.022888 | -0.077819 | -0.004577 | 0.009156 | 0.045777 | -0.027465 | 0.068665 | -0.004577 | 0.27466 | 122.5525 | 0.032044 | 122.5616 | 122.5845 | 122.4884 | 122.525 | 122.4655 | -122.6028 | -122.5662 | 122.493 | 122.5388 | 61.2717 | 61.2534
649.0938 | 122.6532 | -61.3632 | 61.1938 | -0.0016786 | -0.0076434 | 0.0070795 | 0.063824 | -0.017199 | -0.028822 | -0.023033 | -0.00054937 | -0.0067505 | 0.062481 | 0.041092 | -0.019863 | -0.010741 | -0.016955 | -0.11444 | 61.1435 | -61.4502 | 61.1023 | -61.171 | -61.5646 | -61.5829 | -0.15564 | 61.1114 | -61.377 | 61.1618 | -61.3586 | -61.3861 | -61.3174 | -0.086975 | -0.050354 | -0.091553 | 0.19226 | -0.21973 | -0.20142 | -0.13275 | -0.11444 | -0.013733 | -0.082398 | -0.032044 | 0.004577 | 0.045776 | -0.022888 | 0.059509 | -0.009155 | 0.27924 | 122.5525 | 0.01831 | 122.5388 | 122.5937 | 122.4884 | 122.5067 | 122.4747 | -122.644 | -122.5708 | 122.4655 | 122.525 | 61.2488 | 61.2076
650.875 | 122.7448 | -61.3129 | 61.1847 | 0.0059509 | -0.0097796 | 0.010498 | 0.064038 | -0.016985 | -0.028608 | -0.025169 | 0.011658 | -0.0086731 | 0.063976 | 0.046647 | -0.017513 | -0.0094592 | -0.017383 | -0.09613 | 61.1389 | -61.3998 | 61.1893 | -61.0703 | -61.4639 | -61.496 | -0.041199 | 61.0657 | -61.3449 | 61.2534 | -61.2534 | -61.2671 | -61.2442 | -0.086975 | -0.045776 | 0.004578 | 0.24262 | -0.18311 | -0.15106 | -0.096131 | -0.064087 | -0.032044 | -0.11902 | 0.068665 | 0.059509 | 0.068664 | 0.045776 | 0.10071 | 0.07782 | 0.32959 | 122.5891 | 0.091553 | 122.5983 | 122.5388 | 122.4106 | 122.4518 | 122.3785 | -122.5845 | -122.5296 | 122.5021 | 122.5662 | 61.2167 | 61.2717
652.6875 | 122.6715 | -61.3129 | 61.2534 | 0.02121 | -0.0074298 | 0.0066523 | 0.06596 | -0.022112 | -0.032454 | -0.022392 | 0.011658 | -0.0076049 | 0.063335 | 0.03447 | -0.02264 | -0.012023 | -0.018237 | -0.027466 | 61.2167 | -61.4044 | 61.1664 | -61.0886 | -61.4639 | -61.4639 | -0.036621 | 61.1938 | -61.3312 | 61.2305 | -61.2534 | -61.2946 | -61.235 | -0.091553 | -0.036621 | -0.086975 | 0.2243 | -0.15106 | -0.15106 | -0.059509 | -0.059509 | -0.018311 | -0.059509 | -0.022888 | 0.059509 | 0.07782 | 0.01831 | 0.096131 | 0.036621 | 0.31586 | 122.5708 | 0.07782 | 122.5616 | 122.6212 | 122.525 | 122.5296 | 122.5067 | -122.6578 | -122.5845 | 122.4792 | 122.5433 | 61.2854 | 61.2762
654.4688 | 122.7173 | -61.2991 | 61.1893 | 0.036468 | -0.0099932 | 0.0077203 | 0.064251 | -0.019976 | -0.029676 | -0.024528 | 0.0055542 | -0.0097411 | 0.062908 | 0.038743 | -0.019863 | -0.0092456 | -0.018878 | -0.073242 | 61.1206 | -61.3998 | 61.1847 | -61.0474 | -61.4777 | -61.4822 | -0.027466 | 61.0931 | -61.3541 | 61.2396 | -61.2259 | -61.2717 | -61.2305 | -0.10071 | -0.068665 | -0.004578 | 0.25177 | -0.18311 | -0.17853 | -0.082398 | -0.07782 | -0.054932 | -0.09613 | 0.050354 | 0.073242 | 0.068664 | 0.027466 | 0.1236 | 0.082398 | 0.35248 | 122.5845 | 0.12817 | 122.5937 | 122.5204 | 122.4472 | 122.4197 | 122.3923 | -122.5891 | -122.5433 | 122.4838 | 122.5388 | 61.2259 | 61.2717
656.1875 | 122.6486 | -61.3724 | 61.171 | 0.0059509 | -0.0093524 | 0.0096429 | 0.066174 | -0.020403 | -0.030104 | -0.025383 | -0.003601 | -0.0078185 | 0.062908 | 0.044938 | -0.021144 | -0.012877 | -0.014178 | -0.14191 | 61.1755 | -61.4365 | 61.084 | -61.2167 | -61.615 | -61.5967 | -0.15106 | 61.0931 | -61.3815 | 61.171 | -61.3724 | -61.3907 | -61.3083 | -0.064087 | 0.004578 | -0.086975 | 0.15564 | -0.22431 | -0.24262 | -0.16022 | -0.17853 | -0.009156 | -0.077819 | 0 | 0 | 0.064086 | -0.018311 | 0.073242 | -0.009155 | 0.21973 | 122.5204 | 0.009156 | 122.5525 | 122.612 | 122.4747 | 122.5479 | 122.4655 | -122.6074 | -122.5525 | 122.4564 | 122.5433 | 61.2305 | 61.2213
657.9688 | 122.7219 | -61.3037 | 61.203 | 0.01358 | -0.0093524 | 0.0072931 | 0.064465 | -0.020403 | -0.030317 | -0.024955 | 0.0025024 | -0.0088867 | 0.064403 | 0.054123 | -0.016017 | -0.010314 | -0.014392 | -0.086975 | 61.1252 | -61.4044 | 61.1938 | -61.0703 | -61.4594 | -61.496 | -0.032043 | 61.1023 | -61.3403 | 61.2534 | -61.2442 | -61.2625 | -61.2259 | -0.10071 | -0.07782 | -0.009155 | 0.23346 | -0.19226 | -0.15564 | -0.091553 | -0.054932 | -0.036621 | -0.10071 | 0.050354 | 0.059509 | 0.07782 | 0.041199 | 0.11444 | 0.07782 | 0.33417 | 122.5983 | 0.09613 | 122.5937 | 122.5296 | 122.4426 | 122.4289 | 122.406 | -122.6074 | -122.5433 | 122.4976 | 122.5571 | 61.2167 | 61.2717
659.6719 | 122.7173 | -61.3174 | 61.1664 | 0.036468 | -0.0074298 | 0.0090021 | 0.065747 | -0.019549 | -0.029249 | -0.023887 | 0.0055542 | -0.0088867 | 0.063121 | 0.048569 | -0.019222 | -0.0088184 | -0.014819 | -0.073242 | 61.1114 | -61.4182 | 61.2076 | -61.0336 | -61.4502 | -61.4685 | -0.013733 | 61.0931 | -61.3495 | 61.2442 | -61.2488 | -61.2717 | -61.235 | -0.10071 | -0.054932 | 0.041199 | 0.28381 | -0.15106 | -0.13275 | -0.050354 | -0.032043 | -0.032043 | -0.073242 | 0.07782 | 0.068665 | 0.082398 | 0.045777 | 0.11444 | 0.07782 | 0.38452 | 122.6257 | 0.10071 | 122.5937 | 122.5296 | 122.4426 | 122.4289 | 122.4106 | -122.5845 | -122.5159 | 122.525 | 122.5616 | 61.2442 | 61.3037
661.375 | 122.7951 | -61.2396 | 61.1938 | 0.0059509 | -0.0087116 | 0.0075067 | 0.065106 | -0.022967 | -0.033949 | -0.026664 | 0.008606 | -0.0088867 | 0.063335 | 0.050065 | -0.020076 | -0.01245 | -0.015674 | -0.004578 | 61.1435 | -61.3678 | 61.2717 | -60.9375 | -61.3495 | -61.3678 | 0.1236 | 61.1252 | -61.29 | 61.3541 | -61.1023 | -61.1481 | -61.1252 | -0.12817 | -0.050354 | 0.077819 | 0.30212 | -0.12817 | -0.10986 | 0 | 0.018311 | -0.050354 | -0.068665 | 0.16022 | 0.13733 | 0.11444 | 0.091553 | 0.16479 | 0.14191 | 0.4303 | 122.6395 | 0.18768 | 122.644 | 122.5113 | 122.4152 | 122.3831 | 122.3648 | -122.5616 | -122.4838 | 122.5113 | 122.5937 | 61.235 | 61.3632
663.1562 | 122.6669 | -61.3495 | 61.1435 | 0.0059509 | -0.0080706 | 0.010284 | 0.06596 | -0.019976 | -0.030104 | -0.024314 | 0.0025024 | -0.0063233 | 0.062481 | 0.050065 | -0.018794 | -0.0098864 | -0.013537 | -0.12817 | 61.1389 | -61.4182 | 61.0977 | -61.1664 | -61.5646 | -61.5692 | -0.11902 | 61.084 | -61.4182 | 61.1938 | -61.3358 | -61.3861 | -61.2808 | -0.068665 | -0.004578 | -0.045777 | 0.18311 | -0.21973 | -0.21515 | -0.15106 | -0.14648 | -0.068665 | -0.05951 | 0.050354 | 0.013733 | 0.068664 | -0.036621 | 0.13733 | 0.032044 | 0.25177 | 122.5159 | 0.082398 | 122.612 | 122.5571 | 122.5021 | 122.4884 | 122.4335 | -122.5616 | -122.5616 | 122.4472 | 122.5433 | 61.2213 | 61.2305
664.9375 | 122.7081 | -61.3129 | 61.1938 | 0.01358 | -0.0052936 | 0.0096429 | 0.062115 | -0.024035 | -0.030531 | -0.026023 | 0.0025024 | -0.0091003 | 0.063762 | 0.053483 | -0.02264 | -0.0094592 | -0.011401 | -0.086975 | 61.1481 | -61.3998 | 61.1938 | -61.0703 | -61.4594 | -61.5005 | -0.050354 | 61.1069 | -61.3403 | 61.2305 | -61.2396 | -61.2854 | -61.2259 | -0.086975 | -0.045777 | 0 | 0.24262 | -0.18768 | -0.14648 | -0.10071 | -0.05951 | -0.027466 | -0.086975 | 0.036621 | 0.073242 | 0.086975 | 0.027466 | 0.11444 | 0.054932 | 0.32959 | 122.5937 | 0.10071 | 122.5708 | 122.5479 | 122.4472 | 122.4609 | 122.4197 | -122.5937 | -122.5342 | 122.5067 | 122.5433 | 61.2259 | 61.2625
666.6406 | 122.6944 | -61.3312 | 61.1801 | 0.0059509 | -0.0089252 | 0.0092157 | 0.064251 | -0.02083 | -0.030317 | -0.023887 | 0.0025024 | -0.0054687 | 0.06184 | 0.046219 | -0.020503 | -0.011809 | -0.013965 | -0.14191 | 61.1481 | -61.4319 | 61.1114 | -61.1755 | -61.5509 | -61.5692 | -0.11902 | 61.1114 | -61.3678 | 61.2122 | -61.2991 | -61.3449 | -61.2717 | -0.10071 | -0.032044 | -0.068665 | 0.15564 | -0.23804 | -0.21973 | -0.13733 | -0.11902 | -0.036621 | -0.068665 | 0.032043 | 0.032044 | 0.05951 | -0.013733 | 0.096131 | 0.022888 | 0.25635 | 122.5433 | 0.068665 | 122.58 | 122.58 | 122.4792 | 122.4792 | 122.4426 | -122.612 | -122.5479 | 122.4426 | 122.5433 | 61.1893 | 61.2122
668.375 | 122.6852 | -61.2991 | 61.1755 | 0.02121 | -0.006789 | 0.01007 | 0.063397 | -0.018908 | -0.028608 | -0.022178 | 0.0055542 | -0.0076049 | 0.063335 | 0.037888 | -0.019649 | -0.010955 | -0.012256 | -0.027466 | 61.1847 | -61.409 | 61.203 | -61.0519 | -61.4594 | -61.4822 | 0.004578 | 61.1252 | -61.3174 | 61.2442 | -61.2305 | -61.2717 | -61.2213 | -0.10986 | 0.009155 | 0.027466 | 0.24719 | -0.18311 | -0.16022 | -0.073242 | -0.050354 | -0.018311 | -0.050354 | 0.068665 | 0.068664 | 0.07782 | 0.027466 | 0.096131 | 0.045777 | 0.35706 | 122.612 | 0.086975 | 122.5616 | 122.5937 | 122.4426 | 122.4838 | 122.4243 | -122.5845 | -122.493 | 122.5021 | 122.5433 | 61.2717 | 61.3037
670.1406 | 122.644 | -61.3449 | 61.1801 | 0.02121 | -0.0055072 | 0.0094293 | 0.065106 | -0.017199 | -0.030104 | -0.023246 | 0.0055542 | -0.0065369 | 0.062694 | 0.043442 | -0.023281 | -0.011595 | -0.016955 | -0.036621 | 61.1893 | -61.3907 | 61.1938 | -61.0703 | -61.4639 | -61.5005 | -0.013733 | 61.1252 | -61.3358 | 61.2076 | -61.2762 | -61.3312 | -61.2488 | -0.045776 | 0.009155 | 0.013733 | 0.27466 | -0.15564 | -0.11902 | -0.10986 | -0.073242 | 0.009156 | -0.054932 | 0.027466 | 0.068665 | 0.096131 | 0.013733 | 0.086975 | 0.004577 | 0.32044 | 122.5845 | 0.059509 | 122.5433 | 122.58 | 122.4609 | 122.5342 | 122.4701 | -122.5708 | -122.5159 | 122.5388 | 122.5525 | 61.3083 | 61.3312
671.9375 | 122.6532 | -61.2808 | 61.2625 | 0.036468 | -0.0076434 | 0.0087885 | 0.065747 | -0.021685 | -0.030317 | -0.022392 | 0.008606 | -0.0069641 | 0.065471 | 0.041306 | -0.022426 | -0.010741 | -0.01311 | -0.027466 | 61.2122 | -61.3953 | 61.1755 | -61.0703 | -61.4548 | -61.4731 | -0.045776 | 61.1893 | -61.3403 | 61.2213 | -61.2488 | -61.29 | -61.2305 | -0.11444 | -0.050354 | -0.086975 | 0.21057 | -0.19226 | -0.17395 | -0.077819 | -0.059509 | -0.059509 | -0.073242 | -0.041199 | 0.032044 | 0.050354 | -0.009155 | 0.10986 | 0.050354 | 0.32501 | 122.5708 | 0.091553 | 122.5616 | 122.6074 | 122.5296 | 122.493 | 122.4701 | -122.6578 | -122.6028 | 122.4564 | 122.5021 | 61.2534 | 61.235
673.7344 | 122.7859 | -61.2579 | 61.203 | -0.0016786 | -0.0082842 | 0.0081477 | 0.065747 | -0.017199 | -0.031385 | -0.022392 | 0.0055542 | -0.010596 | 0.061412 | 0.048569 | -0.02029 | -0.011809 | -0.015033 | -0.036621 | 61.1481 | -61.3312 | 61.2396 | -60.9695 | -61.3541 | -61.409 | 0.073242 | 61.0931 | -61.3037 | 61.322 | -61.1298 | -61.1526 | -61.1481 | -0.073242 | -0.054932 | 0.036621 | 0.28839 | -0.15106 | -0.09613 | -0.07782 | -0.022888 | -0.045776 | -0.10986 | 0.11902 | 0.12817 | 0.10986 | 0.10529 | 0.15564 | 0.15106 | 0.36163 | 122.5708 | 0.17395 | 122.6257 | 122.4792 | 122.3969 | 122.406 | 122.3511 | -122.5342 | -122.5067 | 122.4976 | 122.58 | 61.2213 | 61.3312
675.5312 | 122.7768 | -61.3312 | 61.1023 | -0.0016786 | -0.0091388 | 0.0092157 | 0.06297 | -0.021471 | -0.029036 | -0.023674 | -0.00054937 | -0.0084595 | 0.065258 | 0.047288 | -0.019008 | -0.009032 | -0.01781 | -0.068665 | 61.0977 | -61.4044 | 61.1984 | -61.0336 | -61.4548 | -61.4868 | 0 | 61.0428 | -61.3586 | 61.2579 | -61.2167 | -61.2671 | -61.2122 | -0.073242 | -0.004578 | 0.09613 | 0.29755 | -0.15564 | -0.1236 | -0.082397 | -0.050354 | -0.027466 | -0.059509 | 0.15564 | 0.11444 | 0.11902 | 0.064087 | 0.14648 | 0.091553 | 0.37079 | 122.6028 | 0.14191 | 122.6166 | 122.5021 | 122.4014 | 122.4289 | 122.374 | -122.5067 | -122.4609 | 122.5296 | 122.5891 | 61.2625 | 61.3312
677.25 | 122.7402 | -61.2946 | 61.1206 | 0.044098 | -0.0063616 | 0.0083613 | 0.066601 | -0.017626 | -0.026045 | -0.024955 | 0.008606 | -0.0080321 | 0.063762 | 0.043656 | -0.018154 | -0.0092456 | -0.014392 | -0.064087 | 61.0886 | -61.4319 | 61.2259 | -61.0153 | -61.4365 | -61.4548 | 0.013733 | 61.0565 | -61.3632 | 61.2671 | -61.2122 | -61.235 | -61.2076 | -0.13733 | -0.032043 | 0.10529 | 0.27924 | -0.16022 | -0.14191 | -0.022888 | -0.004577 | -0.068664 | -0.064086 | 0.14649 | 0.082398 | 0.086975 | 0.05951 | 0.15564 | 0.12817 | 0.41656 | 122.6578 | 0.15106 | 122.6303 | 122.5204 | 122.4197 | 122.3831 | 122.3511 | -122.5525 | -122.4838 | 122.5204 | 122.5616 | 61.2305 | 61.3083
678.9688 | 122.7539 | -61.3129 | 61.1252 | 0.01358 | -0.0082842 | 0.01007 | 0.063611 | -0.019549 | -0.028608 | -0.023887 | 0.014709 | -0.0076049 | 0.063549 | 0.048569 | -0.019863 | -0.008391 | -0.016742 | -0.07782 | 61.0703 | -61.4044 | 61.2167 | -61.0199 | -61.4456 | -61.4731 | 0.041199 | 61.0474 | -61.3586 | 61.2671 | -61.1984 | -61.2579 | -61.2122 | -0.091553 | -0.054932 | 0.091553 | 0.29297 | -0.16022 | -0.13275 | -0.068664 | -0.041199 | -0.045777 | -0.07782 | 0.14191 | 0.11444 | 0.10071 | 0.054931 | 0.14648 | 0.10071 | 0.38452 | 122.6212 | 0.16022 | 122.6257 | 122.4747 | 122.406 | 122.3831 | 122.3602 | -122.5296 | -122.4838 | 122.5296 | 122.58 | 61.235 | 61.3541
680.75 | 122.7539 | -61.3312 | 61.1206 | 0.0059509 | -0.0072162 | 0.0092157 | 0.066601 | -0.016344 | -0.029676 | -0.021965 | 0.0055542 | -0.0082459 | 0.063549 | 0.043442 | -0.018794 | -0.0086048 | -0.014819 | -0.073242 | 61.0657 | -61.4136 | 61.2122 | -61.0199 | -61.441 | -61.4548 | 0.032043 | 61.0611 | -61.3632 | 61.2625 | -61.2167 | -61.2396 | -61.203 | -0.082397 | -0.054931 | 0.091553 | 0.31128 | -0.1236 | -0.10986 | -0.041199 | -0.027466 | -0.032043 | -0.059509 | 0.14191 | 0.11444 | 0.12817 | 0.091553 | 0.16022 | 0.1236 | 0.39368 | 122.6257 | 0.14648 | 122.6257 | 122.4792 | 122.4243 | 122.3969 | 122.3923 | -122.5342 | -122.4838 | 122.5433 | 122.5937 | 61.2579 | 61.3632
682.5469 | 122.6349 | -61.3174 | 61.1801 | 0.0059509 | -0.009566 | 0.0090021 | 0.06596 | -0.01784 | -0.029676 | -0.022605 | 0.0055542 | -0.0073913 | 0.064617 | 0.031907 | -0.020717 | -0.0096728 | -0.018878 | -0.068665 | 61.1755 | -61.4044 | 61.1526 | -61.1252 | -61.5509 | -61.5646 | -0.07782 | 61.1114 | -61.3541 | 61.1618 | -61.3312 | -61.3632 | -61.29 | -0.086975 | -0.004578 | -0.027466 | 0.19226 | -0.24719 | -0.23346 | -0.16022 | -0.14648 | -0.036621 | -0.068665 | -0.018311 | -0.013733 | 0.027466 | -0.045776 | 0.064087 | -0.009155 | 0.27924 | 122.5571 | 0.022888 | 122.5159 | 122.58 | 122.4655 | 122.493 | 122.4289 | -122.5845 | -122.5342 | 122.4701 | 122.4792 | 61.2488 | 61.2396
684.2656 | 122.6395 | -61.3403 | 61.1618 | -0.0016786 | -0.0089252 | 0.0096429 | 0.066815 | -0.01784 | -0.030958 | -0.023887 | -0.003601 | -0.0069641 | 0.066112 | 0.04152 | -0.019649 | -0.010527 | -0.010974 | -0.13733 | 61.1618 | -61.441 | 61.0748 | -61.1755 | -61.5875 | -61.5875 | -0.14191 | 61.1114 | -61.3815 | 61.1389 | -61.3495 | -61.3907 | -61.2991 | -0.10071 | 0 | -0.086975 | 0.16479 | -0.24719 | -0.24719 | -0.14648 | -0.14648 | -0.041199 | -0.050354 | -0.022888 | -0.009155 | 0.041199 | -0.050354 | 0.082398 | -0.009155 | 0.2655 | 122.5159 | 0.032044 | 122.5204 | 122.6028 | 122.493 | 122.5021 | 122.4518 | -122.6028 | -122.5433 | 122.4152 | 122.4792 | 61.203 | 61.1984
686.0312 | 122.6669 | -61.2854 | 61.2213 | 0.02121 | -0.0091388 | 0.0087885 | 0.065533 | -0.015703 | -0.029249 | -0.022605 | 0.008606 | -0.0058959 | 0.065258 | 0.045365 | -0.022212 | -0.010527 | -0.014605 | -0.018311 | 61.235 | -61.3861 | 61.1847 | -61.0565 | -61.4365 | -61.4777 | -0.022888 | 61.1664 | -61.3266 | 61.2442 | -61.2259 | -61.2762 | -61.1984 | -0.10071 | 0.013733 | -0.036621 | 0.22888 | -0.19226 | -0.15106 | -0.091553 | -0.050354 | -0.041199 | -0.054931 | 0.022889 | 0.059509 | 0.086975 | 0.009155 | 0.12817 | 0.050354 | 0.32959 | 122.5708 | 0.10071 | 122.5708 | 122.6212 | 122.493 | 122.5204 | 122.4518 | -122.6074 | -122.5479 | 122.4701 | 122.5296 | 61.2671 | 61.2625
687.8125 | 122.7493 | -61.2579 | 61.203 | 0.0059509 | -0.010421 | 0.0083613 | 0.062756 | -0.022539 | -0.031813 | -0.027305 | 0.0025024 | -0.0069641 | 0.064403 | 0.049424 | -0.019649 | -0.010314 | -0.016955 | -0.059509 | 61.1435 | -61.3678 | 61.2442 | -60.9787 | -61.3678 | -61.3907 | 0.041199 | 61.1023 | -61.3129 | 61.3129 | -61.1389 | -61.1435 | -61.1298 | -0.10986 | -0.059509 | 0.041199 | 0.27924 | -0.13275 | -0.10986 | -0.022888 | 0 | -0.054931 | -0.10071 | 0.10986 | 0.11902 | 0.12817 | 0.11444 | 0.1831 | 0.16937 | 0.3891 | 122.612 | 0.17395 | 122.6257 | 122.5113 | 122.4152 | 122.4014 | 122.3602 | -122.5708 | -122.5159 | 122.5021 | 122.5708 | 61.1984 | 61.2991
689.5781 | 122.644 | -61.2991 | 61.2534 | 0.036468 | -0.0070026 | 0.0060113 | 0.065747 | -0.017412 | -0.030958 | -0.02346 | 0.008606 | -0.0095275 | 0.062481 | 0.03917 | -0.021144 | -0.013945 | -0.015033 | -0.027466 | 61.2488 | -61.3724 | 61.171 | -61.0657 | -61.4548 | -61.4731 | -0.045776 | 61.1801 | -61.3129 | 61.2122 | -61.2442 | -61.2808 | -61.2213 | -0.073242 | -0.004578 | -0.082398 | 0.23346 | -0.17395 | -0.15564 | -0.10071 | -0.082398 | -0.013733 | -0.073242 | -0.041199 | 0.054931 | 0.07782 | 0.01831 | 0.091553 | 0.032043 | 0.3067 | 122.5433 | 0.068664 | 122.525 | 122.6212 | 122.493 | 122.5479 | 122.4792 | -122.6257 | -122.5662 | 122.4701 | 122.5113 | 61.2717 | 61.2534
691.2812 | 122.7219 | -61.2991 | 61.1664 | 0.02121 | -0.0059344 | 0.0083613 | 0.063611 | -0.018694 | -0.031599 | -0.022178 | 0.011658 | -0.0073913 | 0.063549 | 0.049637 | -0.01794 | -0.0096728 | -0.014819 | -0.091553 | 61.1114 | -61.3724 | 61.1938 | -61.0336 | -61.4731 | -61.4685 | -0.022888 | 61.0748 | -61.3495 | 61.2305 | -61.2259 | -61.2534 | -61.2076 | -0.073242 | -0.054932 | 0.027466 | 0.2655 | -0.16937 | -0.17395 | -0.096131 | -0.10071 | -0.050354 | -0.091553 | 0.064087 | 0.073242 | 0.091552 | 0.045776 | 0.14191 | 0.09613 | 0.33874 | 122.5662 | 0.1236 | 122.58 | 122.4838 | 122.4243 | 122.4106 | 122.374 | -122.5388 | -122.5159 | 122.493 | 122.5296 | 61.2076 | 61.2762
693.0781 | 122.6395 | -61.2625 | 61.2717 | 0.0059509 | -0.0074298 | 0.0087885 | 0.066601 | -0.024675 | -0.030531 | -0.024314 | 0.0055542 | -0.0080321 | 0.064617 | 0.039811 | -0.023921 | -0.0086048 | -0.014605 | -0.054932 | 61.203 | -61.3724 | 61.1755 | -61.0794 | -61.4365 | -61.4685 | -0.032043 | 61.1847 | -61.3037 | 61.2122 | -61.2396 | -61.2579 | -61.2259 | -0.10986 | -0.068664 | -0.09613 | 0.1831 | -0.20599 | -0.17395 | -0.096131 | -0.064087 | -0.041199 | -0.086975 | -0.059509 | 0.022888 | 0.036621 | 0.004577 | 0.07782 | 0.045776 | 0.29297 | 122.5479 | 0.064087 | 122.5159 | 122.5754 | 122.4884 | 122.4655 | 122.4472 | -122.644 | -122.5754 | 122.438 | 122.4747 | 61.2076 | 61.2305
694.8594 | 122.6761 | -61.2946 | 61.2076 | 0.02121 | -0.0080706 | 0.0083613 | 0.066388 | -0.019335 | -0.027754 | -0.023246 | 0.0055542 | -0.0076049 | 0.064617 | 0.036606 | -0.019008 | -0.0092456 | -0.016528 | -0.032043 | 61.171 | -61.3815 | 61.1938 | -61.0245 | -61.441 | -61.4594 | 0.018311 | 61.1114 | -61.3266 | 61.235 | -61.2396 | -61.2946 | -61.2213 | -0.086975 | -0.036622 | -0.013733 | 0.27008 | -0.16479 | -0.14648 | -0.07782 | -0.059509 | -0.032043 | -0.096131 | 0.027465 | 0.054932 | 0.073243 | 0 | 0.10529 | 0.032043 | 0.35706 | 122.5754 | 0.086975 | 122.5616 | 122.5525 | 122.438 | 122.4655 | 122.406 | -122.5891 | -122.5342 | 122.4884 | 122.5296 | 61.2625 | 61.3129
696.5781 | 122.7448 | -61.2534 | 61.1801 | -0.0016786 | -0.0070026 | 0.0087885 | 0.063824 | -0.019335 | -0.031599 | -0.023033 | 0.0025024 | -0.010809 | 0.065685 | 0.043656 | -0.019649 | -0.0086048 | -0.017596 | -0.036621 | 61.1481 | -61.3724 | 61.2534 | -60.965 | -61.3541 | -61.377 | 0.068665 | 61.0886 | -61.29 | 61.3129 | -61.1069 | -61.1664 | -61.1343 | -0.11902 | -0.032044 | 0.073242 | 0.28839 | -0.1236 | -0.10071 | -0.004578 | 0.01831 | -0.036621 | -0.091553 | 0.13275 | 0.14648 | 0.11902 | 0.086975 | 0.15564 | 0.1236 | 0.40741 | 122.6257 | 0.1831 | 122.6028 | 122.5204 | 122.3785 | 122.4014 | 122.3419 | -122.5525 | -122.4701 | 122.5067 | 122.5662 | 61.2167 | 61.322
698.3594 | 122.7539 | -61.2259 | 61.203 | -0.0016786 | -0.0099932 | 0.0098565 | 0.063397 | -0.022753 | -0.032026 | -0.024101 | -0.00054937 | -0.0095275 | 0.063335 | 0.043656 | -0.02029 | -0.0094592 | -0.017169 | 0 | 61.1343 | -61.3358 | 61.2946 | -60.9238 | -61.322 | -61.3586 | 0.10529 | 61.0977 | -61.2534 | 61.3358 | -61.084 | -61.1206 | -61.1343 | -0.10986 | -0.068665 | 0.091553 | 0.30212 | -0.13275 | -0.09613 | -0.022889 | 0.013733 | -0.027466 | -0.10529 | 0.13275 | 0.14191 | 0.091553 | 0.10529 | 0.11902 | 0.13275 | 0.41199 | 122.6303 | 0.16937 | 122.5891 | 122.4701 | 122.3511 | 122.3602 | 122.3236 | -122.5388 | -122.4564 | 122.5204 | 122.5616 | 61.2259 | 61.3312
700.0781 | 122.612 | -61.2625 | 61.2488 | -0.0016786 | -0.006789 | 0.0070795 | 0.066388 | -0.01784 | -0.030745 | -0.024528 | 0.017761 | -0.0065369 | 0.06419 | 0.042374 | -0.021999 | -0.011809 | -0.01311 | -0.054932 | 61.2076 | -61.3312 | 61.1755 | -61.0565 | -61.4136 | -61.4548 | -0.022888 | 61.203 | -61.3083 | 61.2167 | -61.2488 | -61.2762 | -61.2305 | -0.068665 | -0.041198 | -0.073242 | 0.20599 | -0.19226 | -0.15106 | -0.1236 | -0.082397 | -0.045777 | -0.045776 | -0.032043 | 0.013733 | 0.032043 | -0.013733 | 0.07782 | 0.032044 | 0.27466 | 122.5067 | 0.05951 | 122.525 | 122.5388 | 122.5113 | 122.4701 | 122.4655 | -122.58 | -122.5571 | 122.438 | 122.4792 | 61.2076 | 61.2396
701.8438 | 122.7448 | -61.2808 | 61.1252 | 0.036468 | -0.004439 | 0.0096429 | 0.06532 | -0.017199 | -0.028395 | -0.022819 | 0.011658 | -0.0080321 | 0.063976 | 0.040452 | -0.019222 | -0.0098864 | -0.018237 | -0.054932 | 61.0748 | -61.4044 | 61.2076 | -60.997 | -61.4273 | -61.4685 | 0.022888 | 61.0474 | -61.3312 | 61.2854 | -61.2076 | -61.2259 | -61.1938 | -0.1236 | -0.050354 | 0.082398 | 0.28381 | -0.18768 | -0.14648 | -0.064087 | -0.022888 | -0.050354 | -0.07782 | 0.16022 | 0.073242 | 0.086975 | 0.054932 | 0.13733 | 0.10529 | 0.40741 | 122.612 | 0.1236 | 122.6166 | 122.4792 | 122.3785 | 122.3557 | 122.3282 | -122.5296 | -122.4564 | 122.4884 | 122.5662 | 61.2259 | 61.3037
703.6406 | 122.7448 | -61.235 | 61.1984 | -0.0016786 | -0.010634 | 0.0098565 | 0.062756 | -0.020617 | -0.028181 | -0.021751 | 0.0025024 | -0.0088867 | 0.060985 | 0.043229 | -0.02029 | -0.009032 | -0.013537 | -0.045776 | 61.1343 | -61.3495 | 61.2396 | -60.9604 | -61.3678 | -61.3815 | 0.068665 | 61.0977 | -61.2762 | 61.3174 | -61.116 | -61.1618 | -61.1435 | -0.11444 | -0.064087 | 0.041199 | 0.27466 | -0.14649 | -0.13275 | -0.032044 | -0.018311 | -0.041199 | -0.10071 | 0.11902 | 0.11902 | 0.091552 | 0.073242 | 0.13275 | 0.11444 | 0.3891 | 122.5891 | 0.16022 | 122.5937 | 122.4838 | 122.374 | 122.3694 | 122.3328 | -122.5479 | -122.4747 | 122.4747 | 122.5525 | 61.1893 | 61.3037
705.3438 | 122.6715 | -61.29 | 61.2259 | 0.028839 | -0.0055072 | 0.0077203 | 0.06596 | -0.020189 | -0.029676 | -0.023674 | 0.008606 | -0.0056823 | 0.063335 | 0.039811 | -0.021572 | -0.01245 | -0.014605 | -0.013733 | 61.2122 | -61.3678 | 61.1938 | -61.0428 | -61.4182 | -61.4548 | -0.013733 | 61.1618 | -61.3037 | 61.2213 | -61.2122 | -61.2671 | -61.203 | -0.07782 | -0.013733 | -0.032043 | 0.24719 | -0.1648 | -0.12817 | -0.086975 | -0.050354 | -0.013733 | -0.064087 | -0.004578 | 0.07782 | 0.086975 | 0.022888 | 0.10071 | 0.036621 | 0.32501 | 122.5616 | 0.091553 | 122.525 | 122.58 | 122.4655 | 122.5021 | 122.4518 | -122.5937 | -122.5296 | 122.4838 | 122.5113 | 61.2762 | 61.2762
707.1094 | 122.7036 | -61.2808 | 61.1572 | 0.01358 | -0.009566 | 0.0090021 | 0.063397 | -0.021685 | -0.026472 | -0.025383 | 0.0025024 | -0.0076049 | 0.062267 | 0.04921 | -0.019649 | -0.010741 | -0.014819 | -0.10529 | 61.1526 | -61.3632 | 61.1618 | -61.0519 | -61.4456 | -61.4639 | -0.064087 | 61.0748 | -61.3129 | 61.235 | -61.2076 | -61.2396 | -61.1938 | -0.082397 | -0.004578 | 0.004577 | 0.22888 | -0.18311 | -0.1648 | -0.10071 | -0.082398 | -0.032043 | -0.082398 | 0.077819 | 0.073242 | 0.086975 | 0.041199 | 0.11902 | 0.073242 | 0.31128 | 122.525 | 0.10529 | 122.5479 | 122.5159 | 122.3877 | 122.4335 | 122.3557 | -122.5204 | -122.4701 | 122.4426 | 122.5159 | 61.1755 | 61.2167
708.8906 | 122.7402 | -61.2854 | 61.1252 | 0.0059509 | -0.0070026 | 0.0087885 | 0.063824 | -0.01549 | -0.027327 | -0.024101 | 0.011658 | -0.0084595 | 0.063335 | 0.042161 | -0.015377 | -0.0086048 | -0.012896 | -0.059509 | 61.0703 | -61.3815 | 61.2259 | -60.997 | -61.441 | -61.4456 | 0.022888 | 61.0428 | -61.3495 | 61.2625 | -61.1893 | -61.2488 | -61.1984 | -0.096131 | -0.054932 | 0.10071 | 0.28839 | -0.16022 | -0.15564 | -0.064087 | -0.059509 | -0.064087 | -0.082397 | 0.13733 | 0.09613 | 0.086975 | 0.036621 | 0.15106 | 0.10071 | 0.38452 | 122.6074 | 0.16022 | 122.612 | 122.4518 | 122.3923 | 122.3557 | 122.3282 | -122.5067 | -122.4747 | 122.5113 | 122.5479 | 61.2259 | 61.3083
710.6094 | 122.6624 | -61.29 | 61.1893 | 0.028839 | -0.0087116 | 0.011352 | 0.065533 | -0.016985 | -0.031172 | -0.021324 | 0.011658 | -0.0069641 | 0.063762 | 0.040024 | -0.020931 | -0.011595 | -0.015246 | -0.032043 | 61.171 | -61.3953 | 61.1938 | -61.0336 | -61.4227 | -61.4502 | 0 | 61.1481 | -61.3037 | 61.2488 | -61.203 | -61.2671 | -61.2076 | -0.10529 | -0.018311 | 0.004578 | 0.25635 | -0.16022 | -0.13275 | -0.054931 | -0.027465 | -0.013733 | -0.041199 | 0.059509 | 0.086975 | 0.082397 | 0.022888 | 0.09613 | 0.036621 | 0.36163 | 122.5891 | 0.10071 | 122.5525 | 122.5662 | 122.4518 | 122.4609 | 122.438 | -122.5845 | -122.493 | 122.4838 | 122.5388 | 61.2579 | 61.29
712.3281 | 122.6166 | -61.3037 | 61.171 | 0.01358 | -0.007857 | 0.0096429 | 0.066815 | -0.019549 | -0.031599 | -0.024101 | 0.0055542 | -0.0073913 | 0.06419 | 0.040024 | -0.019222 | -0.0101 | -0.018664 | -0.064087 | 61.1389 | -61.3724 | 61.1206 | -61.0886 | -61.5417 | -61.5326 | -0.086975 | 61.0886 | -61.3449 | 61.1572 | -61.3129 | -61.3495 | -61.2717 | -0.068664 | -0.032043 | -0.050354 | 0.21515 | -0.22888 | -0.23804 | -0.16022 | -0.16937 | -0.041199 | -0.082397 | -0.013732 | -0.009155 | 0.032044 | -0.045776 | 0.073243 | -0.004577 | 0.28381 | 122.493 | 0.032044 | 122.5021 | 122.5113 | 122.4335 | 122.4426 | 122.3923 | -122.5433 | -122.5159 | 122.4243 | 122.4609 | 61.2396 | 61.2167
714.1094 | 122.7722 | -61.2396 | 61.1664 | -0.0016786 | -0.0093524 | 0.0070795 | 0.063397 | -0.019121 | -0.030317 | -0.024101 | 0.0025024 | -0.0097411 | 0.063549 | 0.047288 | -0.02029 | -0.0098864 | -0.011828 | -0.022888 | 61.1389 | -61.3266 | 61.2625 | -60.9375 | -61.3312 | -61.3678 | 0.082397 | 61.1069 | -61.2671 | 61.3449 | -61.1069 | -61.1343 | -61.1206 | -0.086975 | -0.027466 | 0.09613 | 0.30212 | -0.12817 | -0.091553 | -0.041199 | -0.004578 | -0.027466 | -0.059509 | 0.17853 | 0.13275 | 0.11902 | 0.10529 | 0.14649 | 0.13275 | 0.3891 | 122.5891 | 0.16022 | 122.612 | 122.4655 | 122.374 | 122.3785 | 122.3465 | -122.493 | -122.4335 | 122.5021 | 122.5845 | 61.2167 | 61.322
715.875 | 122.6898 | -61.2808 | 61.1389 | 0.02121 | -0.007857 | 0.0083613 | 0.065106 | -0.018053 | -0.028822 | -0.023887 | 0.014709 | -0.0067505 | 0.06419 | 0.047928 | -0.01794 | -0.0096728 | -0.016314 | -0.068665 | 61.0977 | -61.3861 | 61.1893 | -61.0107 | -61.4456 | -61.4548 | -0.004578 | 61.0565 | -61.3174 | 61.2442 | -61.203 | -61.235 | -61.2076 | -0.10529 | -0.041199 | 0.050354 | 0.27008 | -0.17395 | -0.1648 | -0.068665 | -0.05951 | -0.036621 | -0.082397 | 0.10529 | 0.07782 | 0.073242 | 0.045777 | 0.10986 | 0.082398 | 0.37537 | 122.5754 | 0.11444 | 122.5616 | 122.4838 | 122.374 | 122.3785 | 122.3373 | -122.525 | -122.4564 | 122.4701 | 122.525 | 61.2122 | 61.2762
717.6562 | 122.6944 | -61.2213 | 61.1938 | -0.0016786 | -0.0074298 | 0.0083613 | 0.063183 | -0.017199 | -0.031385 | -0.024101 | 0.0025024 | -0.0086731 | 0.063976 | 0.04387 | -0.021144 | -0.009032 | -0.017169 | 0.009155 | 61.1526 | -61.3266 | 61.2671 | -60.9283 | -61.3358 | -61.3724 | 0.068665 | 61.1069 | -61.2671 | 61.2946 | -61.1114 | -61.1526 | -61.1435 | -0.10529 | -0.041199 | 0.073242 | 0.29297 | -0.15106 | -0.11444 | -0.045776 | -0.009155 | -0.045777 | -0.086975 | 0.10071 | 0.10986 | 0.077819 | 0.068664 | 0.1236 | 0.11444 | 0.39825 | 122.5937 | 0.15564 | 122.5616 | 122.4792 | 122.374 | 122.374 | 122.3282 | -122.5204 | -122.4609 | 122.4884 | 122.5159 | 61.2305 | 61.29
719.375 | 122.731 | -61.2854 | 61.0977 | 0.0059509 | -0.008498 | 0.011352 | 0.06532 | -0.01784 | -0.029463 | -0.024528 | 0.0025024 | -0.0095275 | 0.063762 | 0.044083 | -0.017299 | -0.0094592 | -0.016101 | -0.09613 | 61.0977 | -61.3907 | 61.1664 | -61.0519 | -61.4685 | -61.4822 | -0.004578 | 61.0107 | -61.3403 | 61.2579 | -61.2213 | -61.2534 | -61.1755 | -0.10529 | 0 | 0.068665 | 0.23346 | -0.19684 | -0.18311 | -0.091553 | -0.07782 | -0.054932 | -0.086975 | 0.16022 | 0.064087 | 0.10986 | 0.032043 | 0.16479 | 0.086975 | 0.33875 | 122.5571 | 0.11902 | 122.5983 | 122.4884 | 122.3511 | 122.3831 | 122.2961 | -122.4884 | -122.438 | 122.4518 | 122.5433 | 61.1893 | 61.2808
721.1406 | 122.5845 | -61.3358 | 61.1572 | 0.0059509 | -0.006789 | 0.0096429 | 0.066601 | -0.018267 | -0.031172 | -0.02581 | 0.0055542 | -0.0073913 | 0.065044 | 0.040452 | -0.020503 | -0.010955 | -0.020587 | -0.15564 | 61.1252 | -61.4182 | 61.0657 | -61.1801 | -61.5784 | -61.5692 | -0.14648 | 61.0931 | -61.3541 | 61.1481 | -61.3403 | -61.3678 | -61.2854 | -0.082398 | -0.032044 | -0.091553 | 0.15564 | -0.23346 | -0.24262 | -0.15106 | -0.16022 | -0.018311 | -0.064087 | -0.009156 | -0.004578 | 0.050354 | -0.032044 | 0.068665 | -0.013733 | 0.23804 | 122.4838 | 0.013733 | 122.5021 | 122.5433 | 122.4472 | 122.4609 | 122.4289 | -122.5754 | -122.5113 | 122.4014 | 122.4838 | 61.1801 | 61.1893
722.9219 | 122.5754 | -61.3358 | 61.1755 | 0.01358 | -0.0080706 | 0.0094293 | 0.066388 | -0.021044 | -0.030531 | -0.022392 | 0.0025024 | -0.0054687 | 0.061412 | 0.046219 | -0.021144 | -0.0096728 | -0.015887 | -0.11902 | 61.1023 | -61.4319 | 61.0886 | -61.1435 | -61.5372 | -61.5509 | -0.14648 | 61.1069 | -61.3449 | 61.1389 | -61.3266 | -61.377 | -61.29 | -0.096131 | -0.073242 | -0.086975 | 0.19226 | -0.21515 | -0.20142 | -0.11902 | -0.10529 | -0.009156 | -0.068664 | -0.036621 | 0.009155 | 0.045776 | -0.041199 | 0.054932 | -0.032043 | 0.28839 | 122.5204 | 0.018311 | 122.4838 | 122.5342 | 122.4518 | 122.438 | 122.4426 | -122.6074 | -122.5204 | 122.4243 | 122.4747 | 61.2167 | 61.1893
724.7031 | 122.6578 | -61.3312 | 61.1298 | -0.0016786 | -0.0080706 | 0.0096429 | 0.064679 | -0.024035 | -0.029249 | -0.024528 | -0.00054937 | -0.0078185 | 0.060772 | 0.045579 | -0.020076 | -0.0081774 | -0.017596 | -0.12817 | 61.1206 | -61.3861 | 61.0703 | -61.1343 | -61.5646 | -61.5463 | -0.10071 | 61.0474 | -61.3724 | 61.1847 | -61.2717 | -61.3083 | -61.235 | -0.054931 | -0.009156 | -0.05951 | 0.19684 | -0.21515 | -0.23346 | -0.16022 | -0.17853 | -0.041198 | -0.082398 | 0.054931 | 0.05951 | 0.096131 | 0.022888 | 0.13733 | 0.064086 | 0.25177 | 122.4564 | 0.10071 | 122.5571 | 122.5067 | 122.4197 | 122.4518 | 122.3785 | -122.5159 | -122.5021 | 122.4014 | 122.5159 | 61.203 | 61.2305
726.4844 | 122.7264 | -61.2122 | 61.1755 | 0.0059509 | -0.010207 | 0.0087885 | 0.065533 | -0.019976 | -0.031385 | -0.023246 | -0.00054937 | -0.0095275 | 0.06184 | 0.045579 | -0.021785 | -0.010527 | -0.017596 | -0.009155 | 61.0977 | -61.3266 | 61.2671 | -60.8826 | -61.2991 | -61.3312 | 0.091553 | 61.0886 | -61.235 | 61.3083 | -61.0794 | -61.116 | -61.1069 | -0.11444 | -0.07782 | 0.091553 | 0.32959 | -0.11902 | -0.086975 | -0.004578 | 0.027466 | -0.022888 | -0.086975 | 0.13275 | 0.13275 | 0.10529 | 0.09613 | 0.12817 | 0.11902 | 0.44403 | 122.5937 | 0.15564 | 122.5433 | 122.4243 | 122.3236 | 122.3099 | 122.3007 | -122.5021 | -122.4106 | 122.4792 | 122.5204 | 61.203 | 61.3037
728.1875 | 122.5662 | -61.3312 | 61.1938 | 0.0059509 | -0.0072162 | 0.0090021 | 0.065533 | -0.021685 | -0.031172 | -0.024314 | 0.0055542 | -0.0069641 | 0.06184 | 0.048569 | -0.01794 | -0.0096728 | -0.014178 | -0.086975 | 61.1435 | -61.409 | 61.0977 | -61.116 | -61.528 | -61.5509 | -0.11902 | 61.0977 | -61.3266 | 61.1343 | -61.322 | -61.3678 | -61.2762 | -0.07782 | -0.050354 | -0.096131 | 0.21515 | -0.21973 | -0.19684 | -0.14191 | -0.11902 | 0.004578 | -0.096131 | -0.05951 | 0.009156 | 0.054932 | -0.036621 | 0.050354 | -0.041199 | 0.29297 | 122.5067 | 0.004578 | 122.4609 | 122.5525 | 122.4243 | 122.4747 | 122.4289 | -122.6028 | -122.5204 | 122.4289 | 122.4655 | 61.2442 | 61.2122
729.9688 | 122.6624 | -61.2808 | 61.1893 | 0.01358 | -0.0097796 | 0.010284 | 0.066388 | -0.021258 | -0.030745 | -0.022819 | 0.014709 | -0.0069641 | 0.065258 | 0.045151 | -0.020076 | -0.012664 | -0.014178 | -0.027466 | 61.1435 | -61.3632 | 61.1755 | -61.0199 | -61.4227 | -61.4594 | 0.009155 | 61.116 | -61.29 | 61.2305 | -61.203 | -61.2488 | -61.1847 | -0.082397 | -0.045776 | -0.013733 | 0.26093 | -0.17853 | -0.14191 | -0.096131 | -0.059509 | -0.009155 | -0.073242 | 0.041199 | 0.07782 | 0.096131 | 0.032044 | 0.10529 | 0.041199 | 0.34332 | 122.5388 | 0.086975 | 122.5204 | 122.5067 | 122.406 | 122.4243 | 122.3969 | -122.5525 | -122.4792 | 122.4564 | 122.5113 | 61.2534 | 61.29
731.7344 | 122.5891 | -61.2442 | 61.2488 | -0.0016786 | -0.0082842 | 0.0092157 | 0.064892 | -0.015276 | -0.031599 | -0.024101 | 0.011658 | -0.0065369 | 0.065044 | 0.045792 | -0.022212 | -0.010527 | -0.014819 | -0.036621 | 61.2122 | -61.3678 | 61.1481 | -61.0336 | -61.4182 | -61.4502 | -0.041199 | 61.1481 | -61.3037 | 61.1984 | -61.235 | -61.2488 | -61.2076 | -0.1236 | -0.036621 | -0.10071 | 0.21057 | -0.20599 | -0.17395 | -0.082397 | -0.050354 | -0.059509 | -0.10071 | -0.050354 | 0.009156 | 0.036621 | -0.004577 | 0.09613 | 0.054932 | 0.33417 | 122.5159 | 0.068665 | 122.5021 | 122.58 | 122.4518 | 122.4564 | 122.3923 | -122.6166 | -122.5525 | 122.3923 | 122.4426 | 61.2076 | 61.203
733.5156 | 122.6761 | -61.2488 | 61.171 | 0.02121 | -0.0087116 | 0.0092157 | 0.062329 | -0.021044 | -0.028395 | -0.025383 | 0.0055542 | -0.0082459 | 0.063335 | 0.045365 | -0.021358 | -0.0071094 | -0.015246 | -0.086975 | 61.116 | -61.3678 | 61.1526 | -61.0474 | -61.441 | -61.4548 | -0.054932 | 61.0748 | -61.3129 | 61.2488 | -61.1755 | -61.2213 | -61.1801 | -0.11902 | -0.054931 | -0.01831 | 0.20142 | -0.20599 | -0.19226 | -0.086975 | -0.073242 | -0.064087 | -0.09613 | 0.07782 | 0.073242 | 0.068664 | 0.027466 | 0.13275 | 0.091553 | 0.32044 | 122.5204 | 0.13733 | 122.5616 | 122.4838 | 122.3877 | 122.3648 | 122.3236 | -122.5388 | -122.4838 | 122.4014 | 122.4976 | 61.1618 | 61.1938
735.2188 | 122.6486 | -61.235 | 61.1435 | 0.036468 | -0.010421 | 0.0096429 | 0.064679 | -0.019976 | -0.028608 | -0.021965 | 0.0055542 | -0.0091003 | 0.06419 | 0.041306 | -0.018794 | -0.010527 | -0.015887 | -0.10986 | 61.0931 | -61.3815 | 61.1481 | -61.0245 | -61.4365 | -61.441 | -0.054932 | 61.0611 | -61.2946 | 61.2213 | -61.2076 | -61.2396 | -61.1893 | -0.14649 | -0.050354 | 0.004577 | 0.21057 | -0.20599 | -0.20142 | -0.059509 | -0.054931 | -0.05951 | -0.082398 | 0.077819 | 0.027465 | 0.045776 | -0.004578 | 0.10529 | 0.054932 | 0.35706 | 122.5296 | 0.086975 | 122.5159 | 122.4747 | 122.3557 | 122.3282 | 122.2961 | -122.525 | -122.4381 | 122.3831 | 122.4564 | 61.1252 | 61.1801
737 | 122.7219 | -61.2122 | 61.1847 | -0.0016786 | -0.008498 | 0.0081477 | 0.063824 | -0.02083 | -0.02989 | -0.023033 | -0.003601 | -0.0082459 | 0.063762 | 0.04451 | -0.02029 | -0.011595 | -0.015674 | 0.013733 | 61.1298 | -61.3129 | 61.2625 | -60.9055 | -61.3129 | -61.3541 | 0.10529 | 61.0931 | -61.2717 | 61.322 | -61.0886 | -61.1252 | -61.1114 | -0.10071 | -0.054931 | 0.07782 | 0.3067 | -0.14191 | -0.10071 | -0.041199 | 0 | -0.059509 | -0.091552 | 0.13733 | 0.1236 | 0.10071 | 0.086975 | 0.16022 | 0.14648 | 0.40741 | 122.5754 | 0.1831 | 122.5937 | 122.4426 | 122.3648 | 122.3419 | 122.3053 | -122.4976 | -122.4564 | 122.4747 | 122.5342 | 61.2259 | 61.3174
738.7812 | 122.6212 | -61.2762 | 61.1847 | 0.02121 | -0.0070026 | 0.01007 | 0.066601 | -0.021685 | -0.030317 | -0.026237 | 0.008606 | -0.0052551 | 0.064617 | 0.042588 | -0.02029 | -0.011595 | -0.020373 | -0.022888 | 61.2122 | -61.3724 | 61.171 | -61.0474 | -61.3998 | -61.4548 | -0.013733 | 61.1389 | -61.3129 | 61.2305 | -61.203 | -61.2579 | -61.1984 | -0.09613 | 0.027466 | -0.013733 | 0.22888 | -0.17853 | -0.1236 | -0.082398 | -0.027466 | -0.036621 | -0.045776 | 0.045777 | 0.073242 | 0.07782 | 0.01831 | 0.11444 | 0.054931 | 0.32501 | 122.5433 | 0.10986 | 122.5433 | 122.5845 | 122.4518 | 122.4884 | 122.4152 | -122.5571 | -122.4976 | 122.4472 | 122.5067 | 61.2534 | 61.2625
740.5625 | 122.6761 | -61.2762 | 61.1481 | 0.036468 | -0.0082842 | 0.0096429 | 0.06532 | -0.01848 | -0.03224 | -0.023887 | 0.011658 | -0.0082459 | 0.065044 | 0.049424 | -0.018154 | -0.010314 | -0.017596 | -0.082397 | 61.0977 | -61.377 | 61.1847 | -61.0153 | -61.4273 | -61.4456 | 0.009155 | 61.0428 | -61.2946 | 61.235 | -61.2076 | -61.2396 | -61.1984 | -0.10071 | -0.050354 | 0.036621 | 0.26093 | -0.16937 | -0.15106 | -0.068665 | -0.050354 | -0.018311 | -0.10529 | 0.086975 | 0.068664 | 0.07782 | 0.036621 | 0.096131 | 0.054932 | 0.36163 | 122.5616 | 0.086975 | 122.5296 | 122.4747 | 122.3373 | 122.374 | 122.319 | -122.525 | -122.4426 | 122.4609 | 122.5113 | 61.1938 | 61.2854
742.2656 | 122.7127 | -61.2396 | 61.1481 | -0.0093076 | -0.009566 | 0.0094293 | 0.064038 | -0.019549 | -0.032667 | -0.024955 | -0.00054937 | -0.0099549 | 0.063121 | 0.043656 | -0.019435 | -0.010527 | -0.016742 | -0.068665 | 61.1298 | -61.3632 | 61.1847 | -60.9833 | -61.377 | -61.409 | 0.004578 | 61.0886 | -61.2808 | 61.2808 | -61.1389 | -61.1481 | -61.1252 | -0.1236 | -0.01831 | 0.036621 | 0.25635 | -0.16937 | -0.13733 | -0.045777 | -0.013733 | -0.041199 | -0.059509 | 0.13275 | 0.10071 | 0.11444 | 0.091553 | 0.15564 | 0.13275 | 0.37994 | 122.5479 | 0.14191 | 122.5616 | 122.493 | 122.3694 | 122.3694 | 122.3282 | -122.5113 | -122.4289 | 122.4243 | 122.5204 | 61.171 | 61.2442
744.0469 | 122.5891 | -61.2625 | 61.235 | -0.0016786 | -0.0082842 | 0.0070795 | 0.066388 | -0.018694 | -0.032667 | -0.029014 | 0.017761 | -0.0076049 | 0.064403 | 0.038102 | -0.02264 | -0.011809 | -0.018664 | -0.036621 | 61.1847 | -61.3495 | 61.1526 | -61.0519 | -61.4136 | -61.4273 | -0.009155 | 61.1984 | -61.2808 | 61.1938 | -61.235 | -61.2671 | -61.203 | -0.086975 | -0.050354 | -0.082397 | 0.21057 | -0.16479 | -0.15106 | -0.07782 | -0.064087 | -0.018311 | -0.036621 | -0.041198 | 0.027466 | 0.059509 | -0.004578 | 0.07782 | 0.013733 | 0.29755 | 122.5021 | 0.045777 | 122.4747 | 122.5342 | 122.4792 | 122.4472 | 122.4609 | -122.5845 | -122.5159 | 122.4152 | 122.4564 | 61.2259 | 61.2534
745.8125 | 122.5937 | -61.2305 | 61.2442 | 0.0059509 | -0.0080706 | 0.0094293 | 0.065533 | -0.020617 | -0.033308 | -0.021324 | 0.0025024 | -0.0082459 | 0.064403 | 0.04921 | -0.021144 | -0.010955 | -0.017383 | -0.050354 | 61.1526 | -61.3083 | 61.1572 | -61.0382 | -61.4136 | -61.4502 | -0.036621 | 61.1755 | -61.2854 | 61.1984 | -61.2167 | -61.2305 | -61.2122 | -0.07782 | -0.091553 | -0.086975 | 0.19226 | -0.21973 | -0.1831 | -0.14191 | -0.10528 | -0.054931 | -0.068665 | -0.045777 | 0.013733 | 0.018311 | 0 | 0.073242 | 0.054931 | 0.27008 | 122.4655 | 0.068664 | 122.4838 | 122.4609 | 122.4609 | 122.3831 | 122.406 | -122.5525 | -122.5296 | 122.3877 | 122.4289 | 61.1801 | 61.1938
747.5938 | 122.6257 | -61.2625 | 61.2122 | 0.02121 | -0.006148 | 0.0077203 | 0.066174 | -0.020403 | -0.029676 | -0.024314 | 0.0055542 | -0.0071777 | 0.063335 | 0.044724 | -0.019649 | -0.012023 | -0.017596 | -0.032043 | 61.1893 | -61.3495 | 61.1801 | -61.0153 | -61.4182 | -61.4456 | 0.018311 | 61.1298 | -61.2717 | 61.235 | -61.2122 | -61.2442 | -61.1664 | -0.086975 | -0.022888 | -0.032043 | 0.24719 | -0.18311 | -0.15564 | -0.096131 | -0.068665 | -0.009155 | -0.082397 | 0.022888 | 0.050354 | 0.09613 | 0.01831 | 0.10529 | 0.027465 | 0.33417 | 122.5296 | 0.059509 | 122.5067 | 122.5388 | 122.4014 | 122.4518 | 122.3923 | -122.5616 | -122.4838 | 122.4426 | 122.4976 | 61.2305 | 61.2808
749.3125 | 122.6807 | -61.2854 | 61.116 | 0.02121 | -0.0089252 | 0.010711 | 0.06532 | -0.018267 | -0.028608 | -0.023246 | 0.0055542 | -0.0071777 | 0.06419 | 0.044297 | -0.016017 | -0.0088184 | -0.014392 | -0.045776 | 61.084 | -61.3632 | 61.1984 | -60.9833 | -61.4136 | -61.4319 | 0.027466 | 61.0336 | -61.3312 | 61.2534 | -61.1847 | -61.235 | -61.1893 | -0.07782 | -0.032044 | 0.082397 | 0.30212 | -0.14648 | -0.12817 | -0.068665 | -0.050354 | -0.045777 | -0.082398 | 0.13733 | 0.10071 | 0.09613 | 0.050354 | 0.14191 | 0.096131 | 0.37994 | 122.5616 | 0.14648 | 122.5845 | 122.4472 | 122.3648 | 122.3694 | 122.319 | -122.4792 | -122.4472 | 122.4838 | 122.5388 | 61.2396 | 61.3129
751.0938 | 122.5937 | -61.2305 | 61.2305 | 0.0059509 | -0.0070026 | 0.0090021 | 0.064679 | -0.019335 | -0.030317 | -0.024101 | -0.00054937 | -0.0082459 | 0.063121 | 0.046219 | -0.021144 | -0.010741 | -0.016314 | -0.013733 | 61.1572 | -61.3174 | 61.171 | -61.0107 | -61.377 | -61.4227 | -0.013733 | 61.1664 | -61.2717 | 61.2122 | -61.1938 | -61.2396 | -61.1984 | -0.086975 | -0.073242 | -0.05951 | 0.21973 | -0.19226 | -0.14648 | -0.10528 | -0.059509 | -0.041198 | -0.064087 | -0.018311 | 0.036621 | 0.032044 | -0.009155 | 0.073242 | 0.032043 | 0.3067 | 122.4884 | 0.077819 | 122.4838 | 122.4747 | 122.438 | 122.3877 | 122.3969 | -122.5479 | -122.5021 | 122.4014 | 122.4426 | 61.2167 | 61.2167
752.7969 | 122.5845 | -61.2579 | 61.2442 | -0.0016786 | -0.0074298 | 0.0087885 | 0.063611 | -0.022112 | -0.030958 | -0.023033 | 0.0025024 | -0.0080321 | 0.063549 | 0.045365 | -0.022212 | -0.011595 | -0.016742 | -0.022888 | 61.1893 | -61.3449 | 61.171 | -61.0199 | -61.409 | -61.4319 | -0.022888 | 61.1481 | -61.2579 | 61.203 | -61.2076 | -61.235 | -61.1984 | -0.086975 | -0.054932 | -0.073243 | 0.23804 | -0.17395 | -0.15106 | -0.086975 | -0.064087 | 0 | -0.096131 | -0.041199 | 0.050354 | 0.05951 | 0.022889 | 0.05951 | 0.022889 | 0.32501 | 122.5159 | 0.050354 | 122.4609 | 122.5342 | 122.406 | 122.4472 | 122.406 | -122.5891 | -122.5021 | 122.4289 | 122.4609 | 61.235 | 61.235
754.5156 | 122.7173 | -61.203 | 61.1664 | 0.0059509 | -0.0089252 | 0.0072931 | 0.062756 | -0.022753 | -0.030958 | -0.026664 | 0.0025024 | -0.0084595 | 0.063549 | 0.054123 | -0.019435 | -0.0081774 | -0.018878 | -0.013733 | 61.1069 | -61.3403 | 61.2671 | -60.8871 | -61.2762 | -61.3358 | 0.091553 | 61.0748 | -61.2442 | 61.3312 | -61.0565 | -61.1114 | -61.1023 | -0.13733 | -0.059509 | 0.10071 | 0.31586 | -0.13275 | -0.073242 | 0.004578 | 0.064087 | -0.041199 | -0.091553 | 0.16479 | 0.14648 | 0.10071 | 0.091553 | 0.14191 | 0.13275 | 0.45319 | 122.6074 | 0.18768 | 122.5754 | 122.4472 | 122.319 | 122.3099 | 122.2778 | -122.5067 | -122.4106 | 122.4701 | 122.5342 | 61.1893 | 61.2946
756.2656 | 122.6532 | -61.2762 | 61.1343 | 0.01358 | -0.0087116 | 0.0096429 | 0.065533 | -0.019976 | -0.030104 | -0.020469 | 0.0025024 | -0.0067505 | 0.062908 | 0.042374 | -0.014949 | -0.0096728 | -0.01546 | -0.13733 | 61.0886 | -61.3861 | 61.084 | -61.1114 | -61.528 | -61.5463 | -0.10071 | 61.0428 | -61.3403 | 61.1984 | -61.2488 | -61.2717 | -61.2259 | -0.10986 | -0.045776 | -0.050354 | 0.1648 | -0.27008 | -0.25177 | -0.16022 | -0.14191 | -0.064087 | -0.091552 | 0.064087 | 0.027466 | 0.050354 | 0.004578 | 0.11444 | 0.068665 | 0.27466 | 122.4701 | 0.091553 | 122.5388 | 122.4747 | 122.3831 | 122.3648 | 122.319 | -122.5204 | -122.4747 | 122.3602 | 122.4747 | 61.1389 | 61.1755
757.9844 | 122.612 | -61.2717 | 61.1389 | 0.01358 | -0.007857 | 0.010284 | 0.064038 | -0.016771 | -0.030745 | -0.023674 | 0.0025024 | -0.0050415 | 0.06483 | 0.047715 | -0.020076 | -0.0098864 | -0.015246 | -0.027466 | 61.1389 | -61.3403 | 61.1664 | -61.0245 | -61.4227 | -61.4548 | -0.004578 | 61.0886 | -61.2808 | 61.203 | -61.2305 | -61.2717 | -61.2122 | -0.068665 | 0 | 0.027466 | 0.24719 | -0.18311 | -0.15106 | -0.11444 | -0.082397 | -0.009156 | -0.050354 | 0.064087 | 0.041198 | 0.059509 | 0 | 0.068665 | 0.009156 | 0.31586 | 122.5067 | 0.050354 | 122.4838 | 122.4792 | 122.3694 | 122.4106 | 122.3602 | -122.4792 | -122.4197 | 122.438 | 122.4747 | 61.2442 | 61.2671
759.6875 | 122.7081 | -61.2991 | 61.0565 | -0.0016786 | -0.0076434 | 0.0092157 | 0.06297 | -0.01549 | -0.028608 | -0.022178 | 0.0055542 | -0.0091003 | 0.063976 | 0.048142 | -0.01794 | -0.0086048 | -0.014605 | -0.073242 | 61.0703 | -61.3724 | 61.171 | -61.0107 | -61.4273 | -61.4594 | -0.004578 | 61.0153 | -61.3266 | 61.2488 | -61.1755 | -61.2213 | -61.1893 | -0.073242 | 0.013732 | 0.11444 | 0.28839 | -0.16022 | -0.12817 | -0.086976 | -0.054932 | -0.027466 | -0.041199 | 0.19226 | 0.1236 | 0.10986 | 0.07782 | 0.13733 | 0.10529 | 0.36163 | 122.5433 | 0.15106 | 122.5754 | 122.4426 | 122.3419 | 122.3694 | 122.3145 | -122.4289 | -122.3831 | 122.4701 | 122.5479 | 61.2259 | 61.2946
761.4688 | 122.6212 | -61.2671 | 61.1755 | 0.01358 | -0.0065754 | 0.0092157 | 0.066174 | -0.018694 | -0.030317 | -0.025169 | 0.0055542 | -0.0071777 | 0.064617 | 0.045579 | -0.021144 | -0.0088184 | -0.011615 | -0.036621 | 61.1343 | -61.3541 | 61.1755 | -61.0016 | -61.4044 | -61.441 | 0.036621 | 61.1023 | -61.2946 | 61.235 | -61.1984 | -61.2442 | -61.1984 | -0.086975 | -0.041199 | 0 | 0.2655 | -0.17395 | -0.13733 | -0.086975 | -0.050354 | -0.027466 | -0.073242 | 0.059509 | 0.068665 | 0.068665 | 0.022888 | 0.096131 | 0.050354 | 0.35248 | 122.5296 | 0.096131 | 122.5296 | 122.4884 | 122.3969 | 122.4014 | 122.3694 | -122.5296 | -122.4701 | 122.4426 | 122.5021 | 61.2305 | 61.3037
763.1875 | 122.7036 | -61.2167 | 61.1664 | 0.0059509 | -0.0091388 | 0.0092157 | 0.063824 | -0.020617 | -0.030958 | -0.023033 | 0.0025024 | -0.0099549 | 0.064403 | 0.047501 | -0.019863 | -0.0094592 | -0.013965 | -0.086975 | 61.1114 | -61.3403 | 61.1755 | -60.997 | -61.3632 | -61.409 | -0.004578 | 61.0794 | -61.2534 | 61.2854 | -61.116 | -61.1526 | -61.116 | -0.1236 | -0.054932 | 0.009155 | 0.21973 | -0.19226 | -0.14648 | -0.068665 | -0.022888 | -0.036621 | -0.086975 | 0.11902 | 0.10071 | 0.10071 | 0.064087 | 0.13733 | 0.10071 | 0.34332 | 122.5159 | 0.13733 | 122.5388 | 122.4518 | 122.3328 | 122.3282 | 122.2961 | -122.5067 | -122.4197 | 122.3923 | 122.5021 | 61.1298 | 61.2122
764.8906 | 122.7081 | -61.203 | 61.1755 | 0.0059509 | -0.0089252 | 0.0075067 | 0.062543 | -0.018694 | -0.030104 | -0.023674 | 0.008606 | -0.0082459 | 0.062481 | 0.043015 | -0.021358 | -0.0088184 | -0.014819 | 0.013733 | 61.116 | -61.2854 | 61.2579 | -60.8871 | -61.2991 | -61.3403 | 0.11902 | 61.0748 | -61.2488 | 61.3174 | -61.0703 | -61.1114 | -61.0977 | -0.082397 | -0.059509 | 0.082398 | 0.31586 | -0.13733 | -0.09613 | -0.054932 | -0.013733 | -0.045776 | -0.10071 | 0.14191 | 0.13275 | 0.10529 | 0.091553 | 0.15106 | 0.13733 | 0.39825 | 122.5433 | 0.17853 | 122.5662 | 122.4014 | 122.3236 | 122.319 | 122.2778 | -122.4609 | -122.4243 | 122.4609 | 122.5204 | 61.2167 | 61.322
766.6719 | 122.58 | -61.3083 | 61.1389 | 0.0059509 | -0.0059344 | 0.010711 | 0.066601 | -0.016131 | -0.02989 | -0.023674 | 0.0025024 | -0.0073913 | 0.06419 | 0.037888 | -0.020503 | -0.011809 | -0.019519 | -0.11444 | 61.116 | -61.3998 | 61.0382 | -61.1801 | -61.5646 | -61.5784 | -0.14191 | 61.0748 | -61.322 | 61.1343 | -61.3174 | -61.3678 | -61.2579 | -0.091552 | -0.022888 | -0.10071 | 0.12817 | -0.27008 | -0.25635 | -0.17853 | -0.16479 | -0.013732 | -0.064087 | -0.004578 | -0.009155 | 0.050354 | -0.059509 | 0.064086 | -0.045777 | 0.21973 | 122.438 | 0.004577 | 122.4564 | 122.5159 | 122.3969 | 122.4243 | 122.3831 | -122.5388 | -122.4609 | 122.3465 | 122.4426 | 61.1938 | 61.1664
768.3906 | 122.6715 | -61.2671 | 61.1023 | 0.02121 | -0.0055072 | 0.011566 | 0.06532 | -0.01784 | -0.029676 | -0.022392 | 0.008606 | -0.0086731 | 0.063549 | 0.049637 | -0.015163 | -0.0096728 | -0.011615 | -0.07782 | 61.0886 | -61.3815 | 61.1984 | -60.9695 | -61.3998 | -61.4319 | 0.032043 | 61.0474 | -61.3358 | 61.235 | -61.1618 | -61.2259 | -61.1847 | -0.11444 | -0.013733 | 0.09613 | 0.29755 | -0.16479 | -0.13275 | -0.050354 | -0.01831 | -0.068664 | -0.054932 | 0.13275 | 0.10529 | 0.082398 | 0.041199 | 0.15106 | 0.10986 | 0.41199 | 122.58 | 0.17395 | 122.5708 | 122.4701 | 122.3831 | 122.3557 | 122.3145 | -122.4838 | -122.438 | 122.4655 | 122.5021 | 61.1893 | 61.2991
770.1562 | 122.5433 | -61.2991 | 61.1572 | 0.0059509 | -0.006148 | 0.0098565 | 0.066174 | -0.021685 | -0.029463 | -0.026664 | 0.0025024 | -0.0069641 | 0.065471 | 0.044724 | -0.019008 | -0.0088184 | -0.014392 | -0.1236 | 61.1389 | -61.3953 | 61.0519 | -61.1526 | -61.5326 | -61.5509 | -0.16937 | 61.0703 | -61.3495 | 61.1252 | -61.3083 | -61.3495 | -61.2717 | -0.096131 | -0.018311 | -0.10529 | 0.14648 | -0.25177 | -0.23346 | -0.15564 | -0.13733 | -0.050354 | -0.086976 | -0.032044 | -0.009156 | 0.027466 | -0.050354 | 0.07782 | 0 | 0.24262 | 122.4472 | 0.041198 | 122.4747 | 122.5342 | 122.4197 | 122.438 | 122.3694 | -122.5525 | -122.5067 | 122.3511 | 122.4243 | 61.1755 | 61.1298
771.9219 | 122.58 | -61.2946 | 61.171 | -0.0016786 | -0.0072162 | 0.0070795 | 0.064679 | -0.02083 | -0.031172 | -0.025169 | 0.0025024 | -0.0076049 | 0.063335 | 0.045151 | -0.020931 | -0.010314 | -0.014819 | -0.050354 | 61.1526 | -61.3541 | 61.1298 | -61.0519 | -61.4685 | -61.4777 | -0.045776 | 61.084 | -61.3083 | 61.1664 | -61.2579 | -61.3174 | -61.235 | -0.059509 | -0.01831 | -0.041198 | 0.24262 | -0.1831 | -0.17395 | -0.1236 | -0.11444 | -0.013733 | -0.086975 | -0.004577 | 0.036621 | 0.05951 | -0.022888 | 0.073243 | -0.009155 | 0.30212 | 122.4838 | 0.050354 | 122.4747 | 122.5067 | 122.3923 | 122.4472 | 122.3785 | -122.525 | -122.4792 | 122.4243 | 122.4609 | 61.2442 | 61.2488
773.7188 | 122.644 | -61.2808 | 61.1389 | 0.028839 | -0.0065754 | 0.0079339 | 0.062543 | -0.022753 | -0.027754 | -0.022605 | 0.0055542 | -0.010169 | 0.06483 | 0.042801 | -0.018581 | -0.010314 | -0.016101 | -0.09613 | 61.0703 | -61.3678 | 61.1664 | -60.9924 | -61.4044 | -61.4273 | -0.032043 | 61.0474 | -61.2946 | 61.2122 | -61.1984 | -61.2259 | -61.171 | -0.086975 | -0.068665 | 0.027466 | 0.28839 | -0.14648 | -0.1236 | -0.059509 | -0.036621 | -0.013733 | -0.091553 | 0.073242 | 0.082398 | 0.10986 | 0.054932 | 0.1236 | 0.068665 | 0.37537 | 122.5342 | 0.096131 | 122.5067 | 122.438 | 122.3419 | 122.3511 | 122.3282 | -122.5067 | -122.4335 | 122.4472 | 122.493 | 61.1847 | 61.2488
775.5 | 122.612 | -61.2213 | 61.1847 | 0.0059509 | -0.0082842 | 0.0085749 | 0.066815 | -0.01848 | -0.032881 | -0.022605 | 0.008606 | -0.0065369 | 0.062694 | 0.037888 | -0.019435 | -0.010527 | -0.015033 | -0.018311 | 61.1893 | -61.3495 | 61.1572 | -60.997 | -61.3953 | -61.4456 | 0.009155 | 61.1023 | -61.29 | 61.2259 | -61.1938 | -61.2305 | -61.1618 | -0.12817 | 0.004578 | -0.027465 | 0.2243 | -0.22431 | -0.17395 | -0.096131 | -0.045777 | -0.068665 | -0.082397 | 0.041199 | 0.027465 | 0.059509 | -0.009156 | 0.12817 | 0.059509 | 0.35248 | 122.5067 | 0.09613 | 122.5159 | 122.5388 | 122.3923 | 122.4106 | 122.3236 | -122.5342 | -122.4747 | 122.3785 | 122.4472 | 61.203 | 61.2305
777.2031 | 122.5754 | -61.3083 | 61.1526 | 0.0059509 | -0.0072162 | 0.0094293 | 0.065106 | -0.020403 | -0.032454 | -0.024742 | 0.0025024 | -0.0061095 | 0.065471 | 0.041733 | -0.017299 | -0.0098864 | -0.013537 | -0.14648 | 61.1389 | -61.3861 | 61.0428 | -61.1664 | -61.5509 | -61.5326 | -0.13733 | 61.0931 | -61.3358 | 61.116 | -61.3174 | -61.3495 | -61.2625 | -0.077819 | -0.013733 | -0.10986 | 0.14191 | -0.2243 | -0.24261 | -0.14648 | -0.16479 | -0.027465 | -0.059509 | -0.036621 | -0.009155 | 0.045777 | -0.041198 | 0.073242 | -0.013733 | 0.21973 | 122.4289 | 0.01831 | 122.4518 | 122.525 | 122.4289 | 122.4472 | 122.4014 | -122.5388 | -122.4884 | 122.3511 | 122.4243 | 61.1618 | 61.171
778.9844 | 122.7036 | -61.1847 | 61.1755 | 0.0059509 | -0.0074298 | 0.0081477 | 0.064465 | -0.019976 | -0.028608 | -0.021537 | 0.0055542 | -0.0082459 | 0.061412 | 0.048569 | -0.021999 | -0.010741 | -0.019305 | -0.004578 | 61.1069 | -61.2762 | 61.2534 | -60.878 | -61.2808 | -61.3312 | 0.10529 | 61.0886 | -61.2396 | 61.3083 | -61.0703 | -61.0977 | -61.0977 | -0.091553 | -0.068664 | 0.07782 | 0.3067 | -0.14648 | -0.096131 | -0.054932 | -0.004578 | -0.054932 | -0.086975 | 0.13275 | 0.11444 | 0.086975 | 0.086975 | 0.14191 | 0.14191 | 0.39825 | 122.5296 | 0.16937 | 122.5479 | 122.3831 | 122.3282 | 122.2916 | 122.2733 | -122.4518 | -122.4152 | 122.438 | 122.493 | 61.1801 | 61.29
780.7656 | 122.5754 | -61.2946 | 61.1389 | -0.0016786 | -0.0055072 | 0.0087885 | 0.064892 | -0.018908 | -0.028822 | -0.025169 | -0.00054937 | -0.0084595 | 0.06483 | 0.045792 | -0.019863 | -0.008391 | -0.019519 | -0.13275 | 61.1114 | -61.4136 | 61.0565 | -61.1252 | -61.5555 | -61.5326 | -0.13733 | 61.0748 | -61.3037 | 61.1389 | -61.3037 | -61.3403 | -61.2488 | -0.11902 | -0.027466 | -0.082397 | 0.16937 | -0.23804 | -0.26093 | -0.11902 | -0.14191 | -0.009155 | -0.064087 | 0 | -0.009155 | 0.045777 | -0.045776 | 0.054932 | -0.036621 | 0.28839 | 122.4701 | 0 | 122.4426 | 122.525 | 122.3785 | 122.406 | 122.3694 | -122.5525 | -122.4426 | 122.3511 | 122.4335 | 61.1618 | 61.1572
782.5625 | 122.5754 | -61.235 | 61.2305 | 0.01358 | -0.007857 | 0.0081477 | 0.065747 | -0.019335 | -0.030531 | -0.019615 | 0.0055542 | -0.0099549 | 0.063335 | 0.042161 | -0.022853 | -0.010741 | -0.011401 | -0.013733 | 61.1664 | -61.2946 | 61.1801 | -60.9695 | -61.3541 | -61.4044 | -0.004578 | 61.1572 | -61.2442 | 61.1893 | -61.1801 | -61.2213 | -61.1755 | -0.05951 | -0.064087 | -0.050354 | 0.2655 | -0.16937 | -0.11902 | -0.10986 | -0.059509 | -0.009156 | -0.073242 | -0.041199 | 0.054931 | 0.059509 | 0.013733 | 0.068665 | 0.022889 | 0.32501 | 122.4747 | 0.064087 | 122.4335 | 122.4609 | 122.4014 | 122.4014 | 122.3923 | -122.525 | -122.4747 | 122.4152 | 122.4243 | 61.2213 | 61.2305
784.2812 | 122.6807 | -61.2213 | 61.171 | 0.0059509 | -0.008498 | 0.0079339 | 0.06297 | -0.018908 | -0.030317 | -0.022605 | 0.0055542 | -0.010169 | 0.061626 | 0.041733 | -0.019649 | -0.011168 | -0.015246 | -0.082397 | 61.1023 | -61.3449 | 61.1801 | -60.9741 | -61.3586 | -61.3953 | 0.009155 | 61.0611 | -61.2534 | 61.2808 | -61.1114 | -61.1298 | -61.1069 | -0.1236 | -0.068664 | 0.009156 | 0.24719 | -0.17395 | -0.13733 | -0.050354 | -0.013733 | -0.032044 | -0.10986 | 0.10986 | 0.10986 | 0.11444 | 0.091552 | 0.14648 | 0.1236 | 0.37079 | 122.525 | 0.14191 | 122.5342 | 122.4472 | 122.3145 | 122.3236 | 122.2824 | -122.5159 | -122.4243 | 122.4014 | 122.5021 | 61.1389 | 61.2305
786.0625 | 122.6669 | -61.2259 | 61.171 | 0.02121 | -0.0089252 | 0.0081477 | 0.064251 | -0.018694 | -0.030958 | -0.023033 | 0.0025024 | -0.0093139 | 0.062053 | 0.043015 | -0.017513 | -0.0101 | -0.014819 | -0.086975 | 61.116 | -61.3449 | 61.1618 | -61.0016 | -61.3861 | -61.4182 | -0.009155 | 61.0519 | -61.2625 | 61.235 | -61.1389 | -61.171 | -61.1343 | -0.11902 | -0.054931 | -0.009155 | 0.2243 | -0.19226 | -0.16022 | -0.073242 | -0.041198 | -0.036621 | -0.11902 | 0.064087 | 0.086975 | 0.091553 | 0.054932 | 0.12817 | 0.091553 | 0.34332 | 122.5067 | 0.1236 | 122.4976 | 122.4609 | 122.3145 | 122.3419 | 122.2778 | -122.5159 | -122.4335 | 122.3877 | 122.4609 | 61.1389 | 61.2167
787.8281 | 122.6852 | -61.2991 | 61.0886 | 0.02121 | -0.008498 | 0.011138 | 0.063397 | -0.018694 | -0.029463 | -0.026451 | 0.0025024 | -0.010596 | 0.062267 | 0.046647 | -0.016872 | -0.0088184 | -0.016742 | -0.07782 | 61.0428 | -61.3678 | 61.1618 | -61.0062 | -61.4319 | -61.441 | -0.009155 | 61.0153 | -61.3129 | 61.2396 | -61.1618 | -61.2076 | -61.1572 | -0.068665 | -0.045776 | 0.073242 | 0.29297 | -0.14191 | -0.13275 | -0.073242 | -0.064087 | -0.013733 | -0.073242 | 0.15106 | 0.13733 | 0.14191 | 0.091552 | 0.15564 | 0.10529 | 0.36163 | 122.5296 | 0.15106 | 122.5525 | 122.4106 | 122.3282 | 122.3419 | 122.3145 | -122.4564 | -122.4014 | 122.4609 | 122.5388 | 61.2213 | 61.29
789.6094 | 122.7081 | -61.1984 | 61.1572 | 0.0059509 | -0.010848 | 0.0081477 | 0.065106 | -0.016985 | -0.028608 | -0.027092 | 0.0025024 | -0.0076049 | 0.064403 | 0.041733 | -0.022853 | -0.0088184 | -0.018237 | -0.013733 | 61.1069 | -61.3129 | 61.2488 | -60.9009 | -61.2991 | -61.3358 | 0.10071 | 61.0931 | -61.2671 | 61.3083 | -61.0703 | -61.084 | -61.0794 | -0.11444 | -0.050354 | 0.091552 | 0.29755 | -0.13733 | -0.10071 | -0.022888 | 0.013733 | -0.068665 | -0.064087 | 0.15106 | 0.12817 | 0.11902 | 0.11444 | 0.18768 | 0.18311 | 0.41199 | 122.5616 | 0.19684 | 122.5754 | 122.4197 | 122.3602 | 122.3053 | 122.2916 | -122.4701 | -122.4243 | 122.4472 | 122.5067 | 61.1847 | 61.2991
791.3281 | 122.6624 | -61.1847 | 61.1938 | 0.02121 | -0.008498 | 0.0098565 | 0.063824 | -0.017626 | -0.031172 | -0.024955 | -0.003601 | -0.010596 | 0.062481 | 0.042161 | -0.019649 | -0.0098864 | -0.01546 | 0.004578 | 61.1298 | -61.2991 | 61.2579 | -60.9055 | -61.2991 | -61.3449 | 0.091553 | 61.1023 | -61.2442 | 61.2991 | -61.084 | -61.1114 | -61.116 | -0.11444 | -0.064087 | 0.064087 | 0.27923 | -0.16022 | -0.11444 | -0.045777 | 0 | -0.05951 | -0.091553 | 0.10528 | 0.10071 | 0.068664 | 0.073242 | 0.12817 | 0.13275 | 0.39368 | 122.5571 | 0.16022 | 122.5433 | 122.4289 | 122.3465 | 122.3145 | 122.287 | -122.493 | -122.4381 | 122.4426 | 122.4838 | 61.1893 | 61.2762
793.1094 | 122.5891 | -61.2991 | 61.1298 | -0.0093076 | -0.0097796 | 0.010498 | 0.066815 | -0.018694 | -0.031813 | -0.027519 | 0.0025024 | -0.0052551 | 0.06419 | 0.038529 | -0.018154 | -0.0079638 | -0.016528 | -0.12817 | 61.1206 | -61.3724 | 61.0519 | -61.1252 | -61.5143 | -61.5234 | -0.11444 | 61.0474 | -61.3403 | 61.1435 | -61.2946 | -61.3403 | -61.2396 | -0.073242 | -0.009156 | -0.07782 | 0.17395 | -0.2243 | -0.21515 | -0.15106 | -0.14191 | -0.041199 | -0.082398 | 0.013733 | 0.004577 | 0.059509 | -0.041199 | 0.10071 | 0 | 0.24719 | 122.4243 | 0.045776 | 122.4838 | 122.493 | 122.3877 | 122.4197 | 122.3465 | -122.5021 | -122.4701 | 122.3511 | 122.4426 | 61.171 | 61.1847
794.8906 | 122.5616 | -61.2442 | 61.1664 | 0.02121 | -0.0052936 | 0.01007 | 0.066174 | -0.018908 | -0.031599 | -0.02346 | 0.011658 | -0.0058959 | 0.064403 | 0.045151 | -0.019222 | -0.009032 | -0.015674 | -0.027466 | 61.1206 | -61.3586 | 61.1755 | -60.9879 | -61.409 | -61.4456 | 0.032043 | 61.1206 | -61.29 | 61.1984 | -61.1847 | -61.235 | -61.1801 | -0.11444 | -0.045777 | 0.009155 | 0.25635 | -0.20142 | -0.16479 | -0.086975 | -0.050354 | -0.045776 | -0.045777 | 0.032043 | 0.05951 | 0.064087 | 0.009156 | 0.10986 | 0.054932 | 0.37079 | 122.5342 | 0.10529 | 122.4884 | 122.4792 | 122.4106 | 122.3648 | 122.3648 | -122.525 | -122.4564 | 122.4197 | 122.4426 | 61.2167 | 61.2762
796.6562 | 122.5616 | -61.2717 | 61.2213 | 0.01358 | -0.0091388 | 0.0090021 | 0.064251 | -0.023821 | -0.030531 | -0.026023 | 0.017761 | -0.0073913 | 0.065471 | 0.047288 | -0.024349 | -0.011382 | -0.010119 | -0.050354 | 61.2122 | -61.3403 | 61.1526 | -61.0245 | -61.3953 | -61.4182 | -0.050354 | 61.1526 | -61.2808 | 61.1893 | -61.2076 | -61.2396 | -61.1801 | -0.068665 | -0.009155 | -0.068664 | 0.24719 | -0.14648 | -0.1236 | -0.07782 | -0.054932 | -0.009156 | -0.068664 | -0.032043 | 0.064086 | 0.091552 | 0.032043 | 0.10071 | 0.041199 | 0.31586 | 122.493 | 0.073242 | 122.4701 | 122.5525 | 122.4335 | 122.4838 | 122.4243 | -122.5616 | -122.5021 | 122.4243 | 122.4609 | 61.2213 | 61.2213
798.4219 | 122.5616 | -61.2259 | 61.235 | 0.0059509 | -0.0089252 | 0.0087885 | 0.064038 | -0.018908 | -0.030317 | -0.022178 | 0.0025024 | -0.0078185 | 0.063335 | 0.048997 | -0.021999 | -0.01245 | -0.018237 | -0.07782 | 61.1801 | -61.3358 | 61.1343 | -61.0336 | -61.3907 | -61.4319 | -0.045776 | 61.1526 | -61.2396 | 61.1893 | -61.1984 | -61.2259 | -61.1755 | -0.10986 | -0.054931 | -0.10071 | 0.19226 | -0.20599 | -0.1648 | -0.096131 | -0.054932 | -0.013733 | -0.082397 | -0.045776 | 0.027466 | 0.050354 | 0 | 0.064087 | 0.013733 | 0.30212 | 122.4701 | 0.041199 | 122.4289 | 122.5159 | 122.3923 | 122.406 | 122.3785 | -122.5708 | -122.4747 | 122.3602 | 122.4152 | 61.1481 | 61.1801
800.1406 | 122.6715 | -61.2854 | 61.0931 | 0.0059509 | -0.0082842 | 0.0094293 | 0.06596 | -0.020189 | -0.02754 | -0.024955 | 0.0025024 | -0.0084595 | 0.062908 | 0.04686 | -0.014736 | -0.009032 | -0.016742 | -0.1236 | 61.0703 | -61.377 | 61.1023 | -61.0291 | -61.4685 | -61.4685 | -0.027466 | 61.0062 | -61.3083 | 61.2305 | -61.1755 | -61.2305 | -61.1572 | -0.091553 | -0.022889 | 0.009155 | 0.25635 | -0.18311 | -0.18311 | -0.091553 | -0.091553 | -0.022889 | -0.086975 | 0.13733 | 0.10986 | 0.12817 | 0.054931 | 0.15106 | 0.07782 | 0.3479 | 122.4792 | 0.13275 | 122.5388 | 122.4472 | 122.3145 | 122.3557 | 122.2916 | -122.4701 | -122.4014 | 122.3877 | 122.5159 | 61.1618 | 61.2579
801.9219 | 122.5479 | -61.2259 | 61.2122 | 0.0059509 | -0.0072162 | 0.0072931 | 0.066174 | -0.024889 | -0.033522 | -0.025383 | 0.014709 | -0.0065369 | 0.066753 | 0.046219 | -0.023708 | -0.013304 | -0.01546 | -0.068665 | 61.1801 | -61.3312 | 61.1343 | -61.0107 | -61.3861 | -61.409 | -0.041199 | 61.171 | -61.2808 | 61.1893 | -61.1984 | -61.2259 | -61.1801 | -0.10529 | -0.032043 | -0.07782 | 0.21515 | -0.18311 | -0.16022 | -0.07782 | -0.054931 | -0.054932 | -0.041199 | -0.022888 | 0.027466 | 0.045776 | 0 | 0.10071 | 0.054932 | 0.32043 | 122.4655 | 0.082398 | 122.4701 | 122.5113 | 122.4518 | 122.406 | 122.3969 | -122.5433 | -122.493 | 122.3602 | 122.4152 | 61.1572 | 61.1847
803.7031 | 122.6715 | -61.2122 | 61.1618 | -0.0016786 | -0.0089252 | 0.010711 | 0.064465 | -0.021685 | -0.02989 | -0.02581 | 0.0025024 | -0.010809 | 0.063335 | 0.043015 | -0.01794 | -0.0096728 | -0.019091 | -0.036621 | 61.116 | -61.3129 | 61.2167 | -60.9055 | -61.3037 | -61.3312 | 0.07782 | 61.0611 | -61.2167 | 61.3083 | -61.0657 | -61.1023 | -61.0931 | -0.10071 | -0.045776 | 0.054932 | 0.3067 | -0.11902 | -0.091553 | -0.018311 | 0.009155 | -0.004578 | -0.10071 | 0.14649 | 0.14648 | 0.11902 | 0.10986 | 0.1236 | 0.11444 | 0.40741 | 122.5296 | 0.15106 | 122.525 | 122.4289 | 122.2778 | 122.3282 | 122.2733 | -122.4747 | -122.3785 | 122.4289 | 122.5204 | 61.1755 | 61.29
805.4844 | 122.6028 | -61.3312 | 61.1114 | 0.02121 | -0.0093524 | 0.0077203 | 0.066174 | -0.018267 | -0.028608 | -0.022819 | 0.0025024 | -0.0052551 | 0.064403 | 0.041733 | -0.019008 | -0.010527 | -0.013537 | -0.11902 | 61.116 | -61.3907 | 61.0703 | -61.1023 | -61.5143 | -61.5234 | -0.10071 | 61.0474 | -61.3129 | 61.1664 | -61.2625 | -61.29 | -61.203 | -0.059509 | 0.004578 | -0.041199 | 0.22888 | -0.19226 | -0.18311 | -0.13275 | -0.1236 | 0.018311 | -0.064087 | 0.054932 | 0.068665 | 0.12817 | 0.041199 | 0.10986 | 0.022888 | 0.28839 | 122.4609 | 0.050354 | 122.4792 | 122.5067 | 122.3602 | 122.4472 | 122.3785 | -122.5021 | -122.4243 | 122.4014 | 122.4976 | 61.2122 | 61.2305
807.1875 | 122.6807 | -61.2442 | 61.0977 | 0.0059509 | -0.0074298 | 0.011566 | 0.065106 | -0.018908 | -0.030745 | -0.02111 | 0.0055542 | -0.0069641 | 0.062694 | 0.044083 | -0.01794 | -0.0086048 | -0.018237 | -0.068665 | 61.0611 | -61.3724 | 61.1618 | -60.9924 | -61.4136 | -61.4319 | 0.004578 | 61.0062 | -61.3083 | 61.2396 | -61.1801 | -61.2122 | -61.1481 | -0.12817 | -0.036621 | 0.064087 | 0.25177 | -0.18768 | -0.16937 | -0.05951 | -0.041199 | -0.064087 | -0.091552 | 0.14191 | 0.064087 | 0.096131 | 0.032044 | 0.16022 | 0.096131 | 0.37994 | 122.5342 | 0.12817 | 122.5479 | 122.4335 | 122.3145 | 122.3053 | 122.2504 | -122.4701 | -122.406 | 122.406 | 122.4838 | 61.1755 | 61.2488
808.9531 | 122.6715 | -61.203 | 61.1481 | 0.0059509 | -0.010207 | 0.0094293 | 0.065106 | -0.018267 | -0.030958 | -0.022605 | 0.0025024 | -0.0080321 | 0.063121 | 0.044724 | -0.020503 | -0.0081774 | -0.018451 | -0.013733 | 61.1298 | -61.3129 | 61.2122 | -60.9055 | -61.3037 | -61.3174 | 0.09613 | 61.0703 | -61.2167 | 61.2991 | -61.0794 | -61.0977 | -61.084 | -0.10986 | -0.01831 | 0.064087 | 0.29755 | -0.11444 | -0.10071 | -0.004578 | 0.009155 | -0.013733 | -0.07782 | 0.15106 | 0.1236 | 0.11902 | 0.10529 | 0.13275 | 0.11902 | 0.40741 | 122.525 | 0.13733 | 122.5159 | 122.4426 | 122.287 | 122.3328 | 122.2733 | -122.4609 | -122.3648 | 122.4152 | 122.5021 | 61.1893 | 61.2991
810.6719 | 122.6532 | -61.2213 | 61.1618 | 0.01358 | -0.0097796 | 0.0090021 | 0.063824 | -0.021685 | -0.029036 | -0.023887 | 0.0055542 | -0.0073913 | 0.063335 | 0.047928 | -0.019863 | -0.010314 | -0.015887 | -0.073242 | 61.0794 | -61.3541 | 61.1435 | -60.997 | -61.3815 | -61.409 | -0.018311 | 61.0748 | -61.2625 | 61.2442 | -61.1252 | -61.1526 | -61.116 | -0.13275 | -0.082397 | -0.01831 | 0.2243 | -0.18768 | -0.16022 | -0.054932 | -0.027466 | -0.041199 | -0.086975 | 0.082398 | 0.09613 | 0.10529 | 0.068664 | 0.14648 | 0.10986 | 0.35706 | 122.4976 | 0.13733 | 122.5067 | 122.4335 | 122.3373 | 122.3007 | 122.2961 | -122.5159 | -122.4243 | 122.3648 | 122.4655 | 61.1481 | 61.203
812.375 | 122.6624 | -61.2579 | 61.0748 | -0.0016786 | -0.0070026 | 0.0096429 | 0.064465 | -0.016771 | -0.029249 | -0.024528 | -0.00054937 | -0.0071777 | 0.062694 | 0.039597 | -0.018154 | -0.0092456 | -0.018023 | -0.073242 | 61.0428 | -61.3724 | 61.1481 | -61.0062 | -61.4227 | -61.441 | -0.004578 | 61.0016 | -61.2808 | 61.235 | -61.171 | -61.2213 | -61.1526 | -0.11444 | -0.032043 | 0.073242 | 0.25177 | -0.1831 | -0.16479 | -0.068665 | -0.050354 | -0.022888 | -0.073242 | 0.16022 | 0.086976 | 0.10529 | 0.036622 | 0.12817 | 0.05951 | 0.36621 | 122.5204 | 0.10986 | 122.5159 | 122.4152 | 122.2824 | 122.3007 | 122.2595 | -122.4472 | -122.3557 | 122.406 | 122.493 | 61.1847 | 61.2534
814.1094 | 122.6807 | -61.2717 | 61.0748 | 0.01358 | -0.0087116 | 0.0092157 | 0.063397 | -0.017199 | -0.028181 | -0.022819 | -0.00054937 | -0.0080321 | 0.064403 | 0.048569 | -0.017085 | -0.0096728 | -0.014392 | -0.059509 | 61.0565 | -61.3678 | 61.1618 | -61.0016 | -61.3998 | -61.4273 | 0.009155 | 61.0062 | -61.2991 | 61.2442 | -61.1664 | -61.203 | -61.1526 | -0.096131 | -0.01831 | 0.086975 | 0.27008 | -0.15564 | -0.12817 | -0.059509 | -0.032043 | -0.027466 | -0.068664 | 0.16937 | 0.10529 | 0.11902 | 0.068664 | 0.14648 | 0.09613 | 0.36621 | 122.5296 | 0.13275 | 122.5433 | 122.4243 | 122.3053 | 122.3282 | 122.2778 | -122.4426 | -122.374 | 122.4335 | 122.5159 | 61.2122 | 61.2808
815.8281 | 122.6303 | -61.2579 | 61.1069 | 0.028839 | -0.006789 | 0.011352 | 0.064679 | -0.017199 | -0.028822 | -0.023246 | 0.008606 | -0.0067505 | 0.062267 | 0.051133 | -0.018581 | -0.0094592 | -0.015674 | -0.07782 | 61.0748 | -61.3586 | 61.1984 | -60.9604 | -61.3815 | -61.4136 | 0.013733 | 61.0382 | -61.3129 | 61.2305 | -61.1755 | -61.2122 | -61.1526 | -0.10071 | -0.032044 | 0.091552 | 0.29755 | -0.15564 | -0.1236 | -0.054931 | -0.022888 | -0.054931 | -0.068665 | 0.1236 | 0.082398 | 0.10529 | 0.045777 | 0.16022 | 0.10071 | 0.39825 | 122.5571 | 0.13733 | 122.5433 | 122.4335 | 122.3511 | 122.3328 | 122.2961 | -122.4655 | -122.4197 | 122.4564 | 122.4884 | 61.1801 | 61.2717
817.5469 | 122.6807 | -61.1938 | 61.1481 | 0.0059509 | -0.011061 | 0.0092157 | 0.063183 | -0.019762 | -0.033308 | -0.025169 | -0.003601 | -0.0097411 | 0.060985 | 0.052201 | -0.023708 | -0.0098864 | -0.011615 | -0.018311 | 61.1206 | -61.3037 | 61.2442 | -60.8917 | -61.2717 | -61.3266 | 0.09613 | 61.0703 | -61.235 | 61.3129 | -61.0565 | -61.0657 | -61.0748 | -0.10986 | -0.027466 | 0.096131 | 0.30212 | -0.13275 | -0.077819 | -0.022888 | 0.032044 | -0.041198 | -0.07782 | 0.16479 | 0.13733 | 0.11902 | 0.12817 | 0.16022 | 0.16937 | 0.41199 | 122.5479 | 0.17853 | 122.5479 | 122.4243 | 122.3053 | 122.3145 | 122.2641 | -122.4518 | -122.3831 | 122.4381 | 122.5067 | 61.1755 | 61.29
819.2656 | 122.6761 | -61.2762 | 61.0657 | 0.0059509 | -0.0076434 | 0.0092157 | 0.063183 | -0.01784 | -0.029676 | -0.025596 | 0.0025024 | -0.0091003 | 0.06483 | 0.044297 | -0.01794 | -0.007323 | -0.01781 | -0.059509 | 61.0519 | -61.3632 | 61.1664 | -60.9879 | -61.4182 | -61.4365 | 0.013733 | 60.9879 | -61.2946 | 61.235 | -61.1572 | -61.2076 | -61.1481 | -0.086975 | -0.013733 | 0.10071 | 0.28839 | -0.16022 | -0.14191 | -0.073242 | -0.054932 | -0.018311 | -0.07782 | 0.16937 | 0.11902 | 0.12817 | 0.068664 | 0.14648 | 0.086975 | 0.37537 | 122.5296 | 0.13733 | 122.5296 | 122.4152 | 122.2824 | 122.3282 | 122.2641 | -122.4289 | -122.3602 | 122.4426 | 122.5113 | 61.2167 | 61.29
821.0469 | 122.5754 | -61.2305 | 61.1618 | 0.036468 | -0.0087116 | 0.0083613 | 0.067242 | -0.016131 | -0.030745 | -0.026878 | 0.0055542 | -0.0063233 | 0.063762 | 0.04152 | -0.021785 | -0.0094592 | -0.015674 | -0.018311 | 61.1755 | -61.3129 | 61.171 | -61.0016 | -61.3724 | -61.4182 | -0.018311 | 61.116 | -61.2579 | 61.2076 | -61.1755 | -61.2305 | -61.1435 | -0.082397 | 0.013733 | 0.009155 | 0.22888 | -0.18768 | -0.14191 | -0.10529 | -0.059509 | -0.027466 | -0.045776 | 0.045777 | 0.054932 | 0.086975 | 0 | 0.11444 | 0.027466 | 0.31128 | 122.4838 | 0.082398 | 122.4655 | 122.4884 | 122.374 | 122.406 | 122.3465 | -122.4747 | -122.4197 | 122.4014 | 122.4381 | 61.2122 | 61.2122
822.8125 | 122.5525 | -61.2213 | 61.1755 | 0.028839 | -0.006789 | 0.0075067 | 0.065747 | -0.022967 | -0.030745 | -0.023033 | 0.0055542 | -0.0071777 | 0.062694 | 0.047288 | -0.023067 | -0.013732 | -0.015674 | -0.050354 | 61.1847 | -61.3312 | 61.1206 | -61.0153 | -61.3998 | -61.4273 | -0.045776 | 61.1298 | -61.2625 | 61.1847 | -61.2076 | -61.2259 | -61.1664 | -0.10986 | 0.009155 | -0.054932 | 0.20599 | -0.20599 | -0.17853 | -0.09613 | -0.068664 | -0.041199 | -0.045776 | 0.009155 | 0.013732 | 0.054931 | -0.004578 | 0.09613 | 0.036621 | 0.31586 | 122.4518 | 0.054931 | 122.4472 | 122.5159 | 122.3923 | 122.406 | 122.3511 | -122.5067 | -122.438 | 122.3419 | 122.406 | 61.171 | 61.1755
824.5938 | 122.612 | -61.2167 | 61.1389 | 0.028839 | -0.010848 | 0.011993 | 0.064251 | -0.018267 | -0.029036 | -0.023674 | 0.008606 | -0.0080321 | 0.062267 | 0.04451 | -0.019222 | -0.0079638 | -0.016955 | -0.068665 | 61.0748 | -61.377 | 61.1572 | -60.9604 | -61.409 | -61.409 | 0.004578 | 61.0245 | -61.2854 | 61.2167 | -61.171 | -61.2167 | -61.1664 | -0.16022 | -0.064087 | 0.018311 | 0.25635 | -0.19226 | -0.19226 | -0.032044 | -0.032044 | -0.068664 | -0.11444 | 0.07782 | 0.045777 | 0.050354 | 0 | 0.11902 | 0.068664 | 0.41656 | 122.5342 | 0.11444 | 122.5021 | 122.4518 | 122.3099 | 122.2916 | 122.2412 | -122.5159 | -122.4243 | 122.374 | 122.4335 | 61.1481 | 61.2213
826.375 | 122.5433 | -61.2762 | 61.1526 | -0.0016786 | -0.0074298 | 0.0087885 | 0.06831 | -0.017626 | -0.02989 | -0.026451 | 0.0025024 | -0.0054687 | 0.064403 | 0.044724 | -0.020931 | -0.011382 | -0.011401 | -0.068665 | 61.1298 | -61.3358 | 61.0748 | -61.0794 | -61.4731 | -61.5051 | -0.10529 | 61.084 | -61.2946 | 61.1252 | -61.2625 | -61.3129 | -61.2259 | -0.059509 | -0.022888 | -0.07782 | 0.19684 | -0.22888 | -0.19684 | -0.16937 | -0.13733 | -0.018311 | -0.068665 | -0.027466 | 0.013733 | 0.050354 | -0.036621 | 0.068665 | -0.01831 | 0.25635 | 122.4106 | 0.032044 | 122.4197 | 122.4655 | 122.3785 | 122.406 | 122.3602 | -122.4884 | -122.4472 | 122.3511 | 122.4014 | 61.2076 | 61.171
828.0938 | 122.5845 | -61.2396 | 61.1664 | 0.028839 | -0.0065754 | 0.0079339 | 0.064679 | -0.01848 | -0.029249 | -0.022178 | 0.008606 | -0.0067505 | 0.06419 | 0.04686 | -0.021144 | -0.010955 | -0.016528 | -0.022888 | 61.1618 | -61.3586 | 61.1572 | -60.9879 | -61.3861 | -61.409 | 0.009155 | 61.1023 | -61.2762 | 61.1938 | -61.1618 | -61.2122 | -61.1572 | -0.11902 | -0.004578 | -0.009155 | 0.25177 | -0.16937 | -0.14648 | -0.050354 | -0.027465 | -0.036621 | -0.064087 | 0.027466 | 0.07782 | 0.082397 | 0.027466 | 0.11902 | 0.064087 | 0.37079 | 122.5159 | 0.11444 | 122.4701 | 122.5204 | 122.3785 | 122.4014 | 122.3419 | -122.525 | -122.4426 | 122.3969 | 122.4335 | 61.2167 | 61.2488
829.8594 | 122.5204 | -61.2076 | 61.2259 | 0.0059509 | -0.0093524 | 0.0083613 | 0.065106 | -0.019976 | -0.031599 | -0.022605 | 0.0025024 | -0.0080321 | 0.062694 | 0.038529 | -0.023067 | -0.011168 | -0.015246 | -0.064087 | 61.1893 | -61.3083 | 61.1206 | -61.0291 | -61.3815 | -61.4227 | -0.032043 | 61.1435 | -61.2259 | 61.1755 | -61.1847 | -61.235 | -61.1664 | -0.10071 | -0.036621 | -0.10529 | 0.17853 | -0.21515 | -0.17395 | -0.11444 | -0.073242 | -0.01831 | -0.082397 | -0.050354 | 0.022889 | 0.041199 | -0.027465 | 0.059509 | -0.009155 | 0.27924 | 122.4289 | 0.041199 | 122.4014 | 122.4976 | 122.3694 | 122.3969 | 122.3511 | -122.5342 | -122.4518 | 122.3282 | 122.3831 | 61.1435 | 61.1755
831.6406 | 122.6349 | -61.2213 | 61.1526 | 0.01358 | -0.007857 | 0.0092157 | 0.064251 | -0.024248 | -0.031172 | -0.024955 | -0.00054937 | -0.0082459 | 0.063335 | 0.046433 | -0.017726 | -0.0096728 | -0.014392 | -0.09613 | 61.0794 | -61.322 | 61.1389 | -60.9787 | -61.377 | -61.409 | -0.013733 | 61.0565 | -61.2762 | 61.2305 | -61.116 | -61.1664 | -61.1206 | -0.10071 | -0.073242 | -0.013733 | 0.24261 | -0.18768 | -0.15564 | -0.086976 | -0.054932 | -0.054932 | -0.09613 | 0.07782 | 0.10529 | 0.10071 | 0.054931 | 0.15564 | 0.10986 | 0.34332 | 122.4609 | 0.16022 | 122.5067 | 122.4014 | 122.3328 | 122.3007 | 122.2778 | -122.4747 | -122.4289 | 122.3602 | 122.4518 | 61.1252 | 61.2076
833.4062 | 122.6578 | -61.2442 | 61.0886 | 0.0059509 | -0.0070026 | 0.01007 | 0.064679 | -0.014422 | -0.02989 | -0.020683 | 0.020813 | -0.0076049 | 0.062694 | 0.042801 | -0.017513 | -0.0088184 | -0.017169 | -0.082397 | 61.0336 | -61.3541 | 61.1801 | -60.965 | -61.3861 | -61.4227 | 0.022888 | 61.0153 | -61.29 | 61.2396 | -61.1343 | -61.1893 | -61.1435 | -0.10986 | -0.054932 | 0.091553 | 0.27924 | -0.17853 | -0.14191 | -0.068664 | -0.032043 | -0.045776 | -0.073242 | 0.15106 | 0.10986 | 0.10071 | 0.054932 | 0.14648 | 0.10071 | 0.3891 | 122.5342 | 0.15564 | 122.5296 | 122.3877 | 122.3053 | 122.2778 | 122.2595 | -122.4426 | -122.3785 | 122.4243 | 122.4838 | 61.1618 | 61.2671
835.1094 | 122.5708 | -61.2442 | 61.1847 | 0.036468 | -0.0093524 | 0.0085749 | 0.06532 | -0.013994 | -0.031385 | -0.023246 | 0.014709 | -0.0065369 | 0.065044 | 0.042801 | -0.020076 | -0.011168 | -0.012469 | -0.022888 | 61.1801 | -61.3403 | 61.1664 | -61.0016 | -61.3541 | -61.409 | -0.018311 | 61.1298 | -61.2488 | 61.1984 | -61.1801 | -61.203 | -61.1572 | -0.09613 | -0.004577 | -0.01831 | 0.24262 | -0.16479 | -0.10986 | -0.068665 | -0.013733 | -0.004577 | -0.054931 | 0.013733 | 0.064087 | 0.086975 | 0.041199 | 0.091552 | 0.045776 | 0.33874 | 122.5067 | 0.068664 | 122.4472 | 122.5204 | 122.3785 | 122.4243 | 122.374 | -122.525 | -122.4335 | 122.4106 | 122.4426 | 61.2213 | 61.2259
836.8906 | 122.6852 | -61.1801 | 61.1481 | 0.01358 | -0.0093524 | 0.0085749 | 0.062329 | -0.020189 | -0.031172 | -0.025596 | 0.0025024 | -0.0093139 | 0.063335 | 0.044297 | -0.016658 | -0.0098864 | -0.014605 | -0.032043 | 61.116 | -61.29 | 61.2213 | -60.878 | -61.29 | -61.3266 | 0.10071 | 61.0611 | -61.203 | 61.3129 | -61.0382 | -61.0703 | -61.0565 | -0.10986 | -0.032043 | 0.073242 | 0.30212 | -0.14648 | -0.10986 | -0.036621 | 0 | -0.022888 | -0.086975 | 0.16479 | 0.14191 | 0.1236 | 0.10986 | 0.14648 | 0.13275 | 0.41199 | 122.5113 | 0.1648 | 122.5159 | 122.406 | 122.2641 | 122.2961 | 122.2412 | -122.438 | -122.3511 | 122.4014 | 122.493 | 61.1481 | 61.2808
838.6094 | 122.6761 | -61.1984 | 61.1252 | 0.01358 | -0.009566 | 0.0092157 | 0.064679 | -0.019335 | -0.031385 | -0.024528 | 0.0055542 | -0.0099549 | 0.06184 | 0.040665 | -0.02029 | -0.0094592 | -0.013751 | -0.041199 | 61.0977 | -61.2946 | 61.2122 | -60.9055 | -61.29 | -61.3403 | 0.068665 | 61.0794 | -61.2305 | 61.2808 | -61.0611 | -61.0794 | -61.0565 | -0.096131 | -0.027466 | 0.086975 | 0.29297 | -0.14191 | -0.091553 | -0.045776 | 0.004578 | -0.032044 | -0.045776 | 0.15564 | 0.13733 | 0.14191 | 0.11902 | 0.17395 | 0.15106 | 0.3891 | 122.5067 | 0.16937 | 122.5113 | 122.3923 | 122.3099 | 122.2961 | 122.2778 | -122.4197 | -122.3557 | 122.4106 | 122.4792 | 61.1572 | 61.2671
840.3125 | 122.5662 | -61.2305 | 61.1526 | 0.01358 | -0.007857 | 0.0087885 | 0.06596 | -0.021471 | -0.032026 | -0.024314 | 0.0055542 | -0.0056823 | 0.064617 | 0.034684 | -0.021999 | -0.011809 | -0.017383 | -0.032043 | 61.1435 | -61.3495 | 61.1481 | -60.997 | -61.3907 | -61.4273 | 0.018311 | 61.084 | -61.2579 | 61.1938 | -61.1984 | -61.2213 | -61.1801 | -0.11902 | -0.009155 | -0.004578 | 0.23346 | -0.19684 | -0.16022 | -0.07782 | -0.041199 | -0.027466 | -0.068665 | 0.041199 | 0.032044 | 0.050354 | 0.009156 | 0.07782 | 0.036622 | 0.35248 | 122.4976 | 0.05951 | 122.4518 | 122.493 | 122.3419 | 122.374 | 122.3145 | -122.5021 | -122.4106 | 122.3785 | 122.4243 | 61.1984 | 61.2488
842.0312 | 122.5983 | -61.2534 | 61.1389 | 0.02121 | -0.009566 | 0.0090021 | 0.064251 | -0.021685 | -0.030531 | -0.026023 | 0.0055542 | -0.0095275 | 0.062908 | 0.042161 | -0.019008 | -0.0092456 | -0.017596 | -0.09613 | 61.0794 | -61.3174 | 61.1252 | -60.9924 | -61.3953 | -61.4044 | -0.045776 | 61.0611 | -61.2762 | 61.1893 | -61.1755 | -61.2167 | -61.1481 | -0.064087 | -0.059509 | -0.013733 | 0.26093 | -0.15106 | -0.14191 | -0.086975 | -0.07782 | -0.022888 | -0.07782 | 0.050354 | 0.07782 | 0.10529 | 0.036621 | 0.12817 | 0.059509 | 0.32501 | 122.4426 | 0.10071 | 122.4655 | 122.3969 | 122.3373 | 122.3328 | 122.3145 | -122.4564 | -122.4152 | 122.3785 | 122.4426 | 61.1572 | 61.2076
843.8125 | 122.5845 | -61.2808 | 61.1023 | 0.0059509 | -0.0074298 | 0.0083613 | 0.065747 | -0.020403 | -0.030104 | -0.02581 | 0.008606 | -0.0071777 | 0.065685 | 0.042801 | -0.016872 | -0.011382 | -0.016955 | -0.14191 | 61.084 | -61.3541 | 61.0519 | -61.0931 | -61.5005 | -61.5097 | -0.09613 | 61.0565 | -61.3174 | 61.1664 | -61.2488 | -61.2671 | -61.1938 | -0.073242 | -0.018311 | -0.050354 | 0.18768 | -0.22888 | -0.21973 | -0.15564 | -0.14648 | -0.036621 | -0.045776 | 0.064087 | 0.032044 | 0.086975 | 0.013733 | 0.1236 | 0.050354 | 0.26093 | 122.406 | 0.068665 | 122.4838 | 122.438 | 122.374 | 122.3648 | 122.3373 | -122.4564 | -122.4197 | 122.3328 | 122.4472 | 61.1389 | 61.1847
845.6094 | 122.6486 | -61.2625 | 61.0565 | 0.0059509 | -0.007857 | 0.011566 | 0.068097 | -0.019335 | -0.030745 | -0.024101 | 0.0025024 | -0.0086731 | 0.06419 | 0.041092 | -0.017513 | -0.0081774 | -0.014819 | -0.09613 | 61.0703 | -61.3312 | 61.1206 | -61.0199 | -61.4182 | -61.4502 | -0.027466 | 61.0062 | -61.3174 | 61.2396 | -61.1526 | -61.2122 | -61.1481 | -0.068665 | 0.013732 | 0.064086 | 0.24262 | -0.18768 | -0.15564 | -0.11902 | -0.086975 | -0.054932 | -0.050354 | 0.1831 | 0.10986 | 0.11444 | 0.050354 | 0.16937 | 0.10529 | 0.31128 | 122.4518 | 0.1648 | 122.5571 | 122.4014 | 122.3236 | 122.3328 | 122.2687 | -122.3877 | -122.374 | 122.3831 | 122.5021 | 61.1664 | 61.235
847.3125 | 122.6486 | -61.1893 | 61.1435 | 0.01358 | -0.010848 | 0.0072931 | 0.064038 | -0.018053 | -0.030531 | -0.023246 | 0.0055542 | -0.0093139 | 0.064617 | 0.047288 | -0.021358 | -0.010527 | -0.014392 | -0.045776 | 61.0886 | -61.2854 | 61.1984 | -60.8917 | -61.2808 | -61.3129 | 0.082397 | 61.0657 | -61.235 | 61.2946 | -61.0611 | -61.0931 | -61.0703 | -0.09613 | -0.054932 | 0.054931 | 0.29755 | -0.1236 | -0.091553 | -0.027466 | 0.004577 | -0.045776 | -0.07782 | 0.15106 | 0.12817 | 0.11902 | 0.09613 | 0.16479 | 0.14191 | 0.39368 | 122.4838 | 0.17395 | 122.5296 | 122.374 | 122.3007 | 122.2778 | 122.2549 | -122.4289 | -122.3785 | 122.3877 | 122.4838 | 61.1435 | 61.2717
849.0938 | 122.5479 | -61.2122 | 61.1664 | 0.028839 | -0.0052936 | 0.01007 | 0.065106 | -0.017412 | -0.028395 | -0.024314 | 0.014709 | -0.0084595 | 0.063121 | 0.042588 | -0.021785 | -0.0096728 | -0.016101 | -0.032043 | 61.1755 | -61.3358 | 61.1206 | -61.0153 | -61.377 | -61.409 | -0.032043 | 61.1343 | -61.2488 | 61.1847 | -61.1847 | -61.2122 | -61.1481 | -0.1236 | 0.009155 | -0.045777 | 0.19684 | -0.19684 | -0.16479 | -0.073243 | -0.041199 | -0.036621 | -0.032044 | 0.01831 | 0.027466 | 0.064087 | 0 | 0.10071 | 0.036621 | 0.32043 | 122.4564 | 0.064087 | 122.4335 | 122.5113 | 122.3831 | 122.3877 | 122.3465 | -122.5021 | -122.4152 | 122.3328 | 122.3969 | 61.1801 | 61.1801
850.875 | 122.6212 | -61.203 | 61.1023 | 0.02121 | -0.010634 | 0.01007 | 0.064038 | -0.021471 | -0.029676 | -0.024314 | -0.00054937 | -0.0095275 | 0.061626 | 0.045579 | -0.019435 | -0.0088184 | -0.014605 | -0.091553 | 61.0977 | -61.3358 | 61.1298 | -60.9924 | -61.3907 | -61.409 | -0.032043 | 61.0428 | -61.2625 | 61.2167 | -61.1435 | -61.171 | -61.116 | -0.13275 | -0.004578 | 0.027466 | 0.21057 | -0.20599 | -0.18768 | -0.073243 | -0.054932 | -0.059509 | -0.059509 | 0.11444 | 0.059509 | 0.086975 | 0.032044 | 0.14648 | 0.091553 | 0.34332 | 122.4655 | 0.11902 | 122.4792 | 122.4335 | 122.3053 | 122.3007 | 122.2458 | -122.438 | -122.3648 | 122.3328 | 122.4197 | 61.1115 | 61.171
852.6406 | 122.5937 | -61.2396 | 61.1206 | 0.01358 | -0.0072162 | 0.01007 | 0.064892 | -0.015703 | -0.030745 | -0.024101 | 0.0055542 | -0.0082459 | 0.06483 | 0.049637 | -0.018581 | -0.010741 | -0.015246 | -0.091553 | 61.0794 | -61.3449 | 61.1389 | -60.9558 | -61.3861 | -61.4136 | -0.050354 | 61.0199 | -61.2854 | 61.1938 | -61.1893 | -61.203 | -61.1618 | -0.10529 | -0.041198 | 0.018311 | 0.28381 | -0.17395 | -0.14648 | -0.068664 | -0.041198 | -0.045776 | -0.10071 | 0.073243 | 0.050354 | 0.07782 | 0.036621 | 0.1236 | 0.082397 | 0.3891 | 122.4838 | 0.09613 | 122.4792 | 122.4243 | 122.3053 | 122.319 | 122.2595 | -122.4655 | -122.406 | 122.3785 | 122.4335 | 61.1481 | 61.1893
854.3594 | 122.5754 | -61.203 | 61.1801 | 0.036468 | -0.0055072 | 0.0096429 | 0.066815 | -0.02318 | -0.029463 | -0.026023 | 0.008606 | -0.0065369 | 0.063976 | 0.037247 | -0.021785 | -0.0098864 | -0.017169 | -0.032043 | 61.1664 | -61.3129 | 61.1618 | -61.0016 | -61.3632 | -61.409 | -0.004578 | 61.1206 | -61.2442 | 61.1893 | -61.1755 | -61.203 | -61.1343 | -0.10986 | -0.013733 | -0.018311 | 0.20142 | -0.20599 | -0.16022 | -0.096131 | -0.050354 | -0.041199 | -0.05951 | 0.009155 | 0.027466 | 0.068665 | 0 | 0.10986 | 0.041199 | 0.31128 | 122.4747 | 0.068665 | 122.4335 | 122.4792 | 122.3648 | 122.3694 | 122.3236 | -122.493 | -122.4243 | 122.3648 | 122.3923 | 61.171 | 61.1984
856.1719 | 122.525 | -61.2717 | 61.1526 | 0.01358 | -0.006789 | 0.0092157 | 0.066388 | -0.019549 | -0.030104 | -0.025596 | 0.0025024 | -0.0078185 | 0.065471 | 0.045365 | -0.018154 | -0.010314 | -0.016101 | -0.073242 | 61.116 | -61.3403 | 61.0977 | -61.0245 | -61.4502 | -61.4731 | -0.041199 | 61.0794 | -61.2671 | 61.1343 | -61.2396 | -61.2854 | -61.2259 | -0.068665 | -0.036621 | -0.054932 | 0.24719 | -0.20142 | -0.17853 | -0.13275 | -0.10986 | 0.004577 | -0.073242 | -0.018311 | 0.032043 | 0.045776 | -0.013733 | 0.041199 | -0.01831 | 0.31586 | 122.438 | 0.027466 | 122.4014 | 122.4564 | 122.3465 | 122.3877 | 122.3511 | -122.493 | -122.4197 | 122.3694 | 122.406 | 61.1984 | 61.2305
857.875 | 122.5113 | -61.2671 | 61.1389 | 0.01358 | -0.0070026 | 0.0094293 | 0.066601 | -0.012926 | -0.029676 | -0.020897 | 0.0025024 | -0.0065369 | 0.064617 | 0.041947 | -0.018794 | -0.008391 | -0.01311 | -0.07782 | 61.1252 | -61.3678 | 61.0703 | -61.0565 | -61.4731 | -61.5051 | -0.082397 | 61.0611 | -61.3037 | 61.1298 | -61.2534 | -61.2946 | -61.2167 | -0.10071 | -0.013733 | -0.068665 | 0.21057 | -0.23804 | -0.20599 | -0.13733 | -0.10529 | -0.036621 | -0.07782 | -0.009155 | 0.013733 | 0.050354 | -0.027466 | 0.086975 | 0.009155 | 0.31128 | 122.438 | 0.050354 | 122.4335 | 122.493 | 122.3648 | 122.3923 | 122.3282 | -122.5067 | -122.4426 | 122.3373 | 122.3969 | 61.1893 | 61.1847
859.6406 | 122.644 | -61.2534 | 61.0611 | -0.0016786 | -0.0070026 | 0.0085749 | 0.064038 | -0.018053 | -0.031813 | -0.023246 | 0.014709 | -0.0073913 | 0.065471 | 0.048569 | -0.019435 | -0.0086048 | -0.013965 | -0.068665 | 61.0565 | -61.3403 | 61.1618 | -60.9512 | -61.3815 | -61.4136 | 0.013733 | 61.0245 | -61.322 | 61.2259 | -61.1389 | -61.1664 | -61.1298 | -0.086975 | -0.004577 | 0.10071 | 0.30212 | -0.16022 | -0.12817 | -0.073242 | -0.041199 | -0.068664 | -0.036621 | 0.16479 | 0.11444 | 0.1236 | 0.086975 | 0.19226 | 0.15564 | 0.3891 | 122.5021 | 0.1831 | 122.5479 | 122.3969 | 122.3465 | 122.3099 | 122.2778 | -122.4014 | -122.3831 | 122.4152 | 122.4792 | 61.1847 | 61.2671
861.3594 | 122.5204 | -61.2579 | 61.1206 | -0.0016786 | -0.0080706 | 0.0066523 | 0.066388 | -0.016771 | -0.029249 | -0.022819 | 0.0025024 | -0.0067505 | 0.063976 | 0.04451 | -0.020503 | -0.0081774 | -0.018023 | -0.15564 | 61.1206 | -61.377 | 61.0199 | -61.1069 | -61.5005 | -61.5143 | -0.13275 | 61.0565 | -61.3083 | 61.1252 | -61.2625 | -61.2991 | -61.235 | -0.11902 | 0 | -0.10071 | 0.15106 | -0.25635 | -0.24261 | -0.13733 | -0.1236 | -0.050354 | -0.064086 | 0.004578 | -0.004577 | 0.022889 | -0.041198 | 0.073243 | 0.009156 | 0.27008 | 122.3969 | 0.045777 | 122.4335 | 122.4976 | 122.3648 | 122.3785 | 122.3145 | -122.4976 | -122.4289 | 122.2778 | 122.3831 | 61.1023 | 61.1252
863.125 | 122.5616 | -61.2625 | 61.1114 | -0.0016786 | -0.0059344 | 0.0070795 | 0.066174 | -0.018053 | -0.029249 | -0.025596 | -0.003601 | -0.0084595 | 0.064617 | 0.04451 | -0.019435 | -0.0088184 | -0.017383 | -0.14648 | 61.1206 | -61.3541 | 61.0336 | -61.0794 | -61.4822 | -61.5189 | -0.11902 | 61.0474 | -61.29 | 61.1435 | -61.2762 | -61.2808 | -61.2122 | -0.091553 | 0.009155 | -0.07782 | 0.1831 | -0.25635 | -0.21973 | -0.16479 | -0.12817 | -0.027466 | -0.064087 | 0.032044 | -0.013733 | 0.050354 | -0.018311 | 0.07782 | 0.009155 | 0.27466 | 122.3877 | 0.013733 | 122.4335 | 122.4747 | 122.3373 | 122.3831 | 122.3099 | -122.4655 | -122.4014 | 122.2961 | 122.406 | 61.116 | 61.1435
864.9062 | 122.5159 | -61.2305 | 61.1938 | 0.01358 | -0.0087116 | 0.0094293 | 0.062329 | -0.017626 | -0.031599 | -0.021751 | 0.0025024 | -0.0071777 | 0.062694 | 0.042588 | -0.023281 | -0.0098864 | -0.016742 | -0.036621 | 61.1572 | -61.2717 | 61.1298 | -60.9604 | -61.3632 | -61.3998 | -0.022888 | 61.1389 | -61.2396 | 61.1893 | -61.1664 | -61.1893 | -61.1572 | -0.041198 | -0.036621 | -0.064087 | 0.27008 | -0.16937 | -0.13275 | -0.12817 | -0.091553 | -0.009155 | -0.054932 | -0.004578 | 0.064087 | 0.073242 | 0.041199 | 0.082397 | 0.050354 | 0.31128 | 122.4014 | 0.073242 | 122.4289 | 122.4289 | 122.3785 | 122.3877 | 122.3694 | -122.4655 | -122.4335 | 122.3602 | 122.4197 | 61.1938 | 61.2076
866.625 | 122.5296 | -61.2946 | 61.116 | 0.0059509 | -0.0063616 | 0.01007 | 0.065533 | -0.015917 | -0.031385 | -0.023246 | 0.008606 | -0.0067505 | 0.062908 | 0.041733 | -0.019222 | -0.010314 | -0.015674 | -0.13733 | 61.1023 | -61.3586 | 61.0245 | -61.1069 | -61.5097 | -61.5097 | -0.13733 | 61.0565 | -61.3266 | 61.1114 | -61.2762 | -61.2991 | -61.2167 | -0.064087 | -0.013733 | -0.091553 | 0.18768 | -0.21515 | -0.21515 | -0.15106 | -0.15106 | -0.032043 | -0.059509 | -0.004578 | 0.018311 | 0.07782 | -0.004577 | 0.10986 | 0.027466 | 0.25177 | 122.3831 | 0.050354 | 122.438 | 122.4609 | 122.3831 | 122.3969 | 122.3511 | -122.4747 | -122.4426 | 122.319 | 122.406 | 61.1572 | 61.1572
868.3281 | 122.5021 | -61.2671 | 61.1481 | 0.01358 | -0.0063616 | 0.01007 | 0.06532 | -0.017412 | -0.029463 | -0.022392 | 0.0025024 | -0.0065369 | 0.064403 | 0.042801 | -0.019863 | -0.0101 | -0.014605 | -0.12817 | 61.1069 | -61.3678 | 61.0336 | -61.1206 | -61.496 | -61.5234 | -0.15564 | 61.0657 | -61.2946 | 61.0931 | -61.2762 | -61.3129 | -61.2076 | -0.10071 | -0.041198 | -0.11444 | 0.14649 | -0.25635 | -0.22888 | -0.15564 | -0.12817 | -0.027466 | -0.082397 | -0.054931 | -0.009155 | 0.059509 | -0.045776 | 0.086975 | -0.01831 | 0.24719 | 122.4014 | 0.018311 | 122.3877 | 122.4747 | 122.3602 | 122.374 | 122.3328 | -122.5159 | -122.4426 | 122.3007 | 122.3602 | 61.1389 | 61.1115
870.1094 | 122.5845 | -61.2167 | 61.1206 | 0.02121 | -0.006789 | 0.0096429 | 0.064251 | -0.019549 | -0.028608 | -0.023887 | 0.011658 | -0.0086731 | 0.063121 | 0.048997 | -0.019008 | -0.010314 | -0.01781 | -0.091553 | 61.0657 | -61.3495 | 61.1252 | -60.9467 | -61.377 | -61.3907 | -0.004578 | 61.0474 | -61.29 | 61.2122 | -61.1526 | -61.1938 | -61.1343 | -0.13275 | -0.054931 | 0.004578 | 0.27008 | -0.17395 | -0.16022 | -0.041199 | -0.027466 | -0.073242 | -0.073242 | 0.091553 | 0.064087 | 0.082398 | 0.022888 | 0.15564 | 0.09613 | 0.40283 | 122.4747 | 0.13733 | 122.5021 | 122.4152 | 122.3373 | 122.2824 | 122.2641 | -122.4701 | -122.4106 | 122.3419 | 122.4289 | 61.1252 | 61.2122
871.8906 | 122.6028 | -61.2259 | 61.116 | 0.028839 | -0.0082842 | 0.0094293 | 0.064038 | -0.015703 | -0.029463 | -0.023887 | 0.014709 | -0.0078185 | 0.06419 | 0.048142 | -0.021144 | -0.010955 | -0.012683 | -0.086975 | 61.0519 | -61.322 | 61.1343 | -60.9467 | -61.3861 | -61.4136 | 0.009155 | 61.0382 | -61.2671 | 61.2122 | -61.1481 | -61.1755 | -61.1389 | -0.09613 | -0.064087 | 0.01831 | 0.27924 | -0.18768 | -0.16022 | -0.091553 | -0.064087 | -0.041199 | -0.07782 | 0.09613 | 0.07782 | 0.086975 | 0.050354 | 0.12817 | 0.091553 | 0.37537 | 122.4564 | 0.11902 | 122.4792 | 122.374 | 122.3053 | 122.2778 | 122.2641 | -122.438 | -122.3831 | 122.3602 | 122.438 | 61.1389 | 61.235
873.6875 | 122.4838 | -61.2762 | 61.1298 | 0.0059509 | -0.0076434 | 0.012207 | 0.064892 | -0.021685 | -0.029036 | -0.022178 | 0.0025024 | -0.0073913 | 0.064403 | 0.045792 | -0.021144 | -0.011382 | -0.017596 | -0.11444 | 61.1023 | -61.3586 | 61.0382 | -61.1114 | -61.5005 | -61.496 | -0.15106 | 61.0657 | -61.3083 | 61.1023 | -61.2762 | -61.3083 | -61.2259 | -0.082398 | -0.027466 | -0.091553 | 0.1648 | -0.21973 | -0.2243 | -0.13733 | -0.14191 | -0.032044 | -0.064087 | -0.027466 | 0 | 0.050354 | -0.032044 | 0.082398 | 0 | 0.24719 | 122.3969 | 0.032044 | 122.4106 | 122.4609 | 122.374 | 122.3785 | 122.3419 | -122.4884 | -122.4381 | 122.3145 | 122.3785 | 61.1618 | 61.1252
875.4062 | 122.5845 | -61.2213 | 61.1206 | 0.0059509 | -0.0091388 | 0.0085749 | 0.064038 | -0.01784 | -0.029249 | -0.022605 | 0.011658 | -0.011237 | 0.063121 | 0.047501 | -0.021785 | -0.0096728 | -0.013537 | -0.091553 | 61.0794 | -61.3129 | 61.1298 | -60.9695 | -61.3678 | -61.3953 | -0.054932 | 61.0291 | -61.2579 | 61.1893 | -61.1572 | -61.1801 | -61.116 | -0.091553 | -0.041198 | 0.009156 | 0.25177 | -0.17395 | -0.14648 | -0.082398 | -0.054932 | -0.036622 | -0.091552 | 0.068665 | 0.064086 | 0.10529 | 0.041198 | 0.14191 | 0.07782 | 0.34332 | 122.4426 | 0.10071 | 122.4472 | 122.3923 | 122.287 | 122.3007 | 122.2504 | -122.4335 | -122.3785 | 122.3511 | 122.4106 | 61.1298 | 61.1664
877.125 | 122.6303 | -61.2488 | 61.0565 | 0.0059509 | -0.0080706 | 0.01007 | 0.062543 | -0.016985 | -0.028395 | -0.02346 | -0.003601 | -0.0086731 | 0.061412 | 0.048142 | -0.016445 | -0.0081774 | -0.012469 | -0.064087 | 61.0474 | -61.3403 | 61.1435 | -60.965 | -61.3861 | -61.4044 | -0.009155 | 60.997 | -61.2854 | 61.2213 | -61.1481 | -61.1801 | -61.1298 | -0.091553 | -0.009156 | 0.086975 | 0.28381 | -0.15564 | -0.13733 | -0.064087 | -0.045776 | -0.036621 | -0.05951 | 0.16479 | 0.10071 | 0.11902 | 0.068664 | 0.15564 | 0.10529 | 0.37537 | 122.4838 | 0.13733 | 122.5067 | 122.3877 | 122.2824 | 122.2961 | 122.2458 | -122.3969 | -122.3419 | 122.3923 | 122.4701 | 61.1847 | 61.2396
878.9062 | 122.6028 | -61.2122 | 61.0748 | 0.028839 | -0.0076434 | 0.01242 | 0.065533 | -0.016344 | -0.027754 | -0.02346 | 0.011658 | -0.0078185 | 0.064617 | 0.046006 | -0.018794 | -0.0081774 | -0.016314 | -0.064087 | 61.0428 | -61.3312 | 61.1618 | -60.9329 | -61.3541 | -61.3861 | 0.045776 | 61.0336 | -61.2625 | 61.2213 | -61.1298 | -61.1847 | -61.1298 | -0.11902 | -0.032043 | 0.086975 | 0.27924 | -0.17395 | -0.14191 | -0.054931 | -0.022888 | -0.050354 | -0.041199 | 0.14648 | 0.082397 | 0.082397 | 0.027466 | 0.13275 | 0.07782 | 0.39825 | 122.493 | 0.13275 | 122.4838 | 122.374 | 122.2961 | 122.2549 | 122.2458 | -122.406 | -122.3373 | 122.374 | 122.4335 | 61.1481 | 61.2579
880.6406 | 122.5021 | -61.2259 | 61.116 | 0.0059509 | -0.006789 | 0.011566 | 0.066174 | -0.021898 | -0.028395 | -0.023887 | 0.0025024 | -0.0065369 | 0.066326 | 0.046647 | -0.018581 | -0.008391 | -0.013965 | -0.13733 | 61.116 | -61.3724 | 61.0291 | -61.0886 | -61.496 | -61.5005 | -0.10529 | 61.0428 | -61.3129 | 61.1206 | -61.2579 | -61.3083 | -61.1984 | -0.14648 | 0 | -0.086975 | 0.13733 | -0.27466 | -0.27008 | -0.12817 | -0.1236 | -0.086975 | -0.073242 | 0.004577 | -0.032044 | 0.027466 | -0.082398 | 0.11444 | 0.004577 | 0.28381 | 122.4014 | 0.054931 | 122.4335 | 122.4884 | 122.3557 | 122.3419 | 122.2687 | -122.4884 | -122.4289 | 122.2549 | 122.3465 | 61.0886 | 61.1206
882.4062 | 122.5067 | -61.1938 | 61.2213 | -0.0093076 | -0.0089252 | 0.0077203 | 0.062756 | -0.019549 | -0.031172 | -0.021965 | 0.0025024 | -0.0071777 | 0.068035 | 0.044297 | -0.023921 | -0.01245 | -0.015246 | -0.073242 | 61.171 | -61.2808 | 61.1023 | -60.9924 | -61.377 | -61.4044 | -0.036621 | 61.1572 | -61.2167 | 61.171 | -61.1801 | -61.1847 | -61.1343 | -0.086975 | -0.050354 | -0.11902 | 0.20142 | -0.21057 | -0.1831 | -0.1236 | -0.09613 | -0.022888 | -0.064086 | -0.050354 | 0.013733 | 0.05951 | 0.009156 | 0.082398 | 0.032044 | 0.28839 | 122.3831 | 0.036621 | 122.3877 | 122.4518 | 122.374 | 122.3648 | 122.3511 | -122.5021 | -122.438 | 122.2961 | 122.3648 | 61.1206 | 61.1572
884.125 | 122.5388 | -61.2808 | 61.1298 | -0.0016786 | -0.0076434 | 0.0087885 | 0.066601 | -0.02083 | -0.030745 | -0.025169 | 0.0025024 | -0.0063233 | 0.063549 | 0.04152 | -0.019008 | -0.007323 | -0.017169 | -0.13733 | 61.0977 | -61.3724 | 61.0245 | -61.0794 | -61.4777 | -61.496 | -0.11444 | 61.0382 | -61.2946 | 61.1435 | -61.2534 | -61.29 | -61.203 | -0.091552 | -0.032044 | -0.10529 | 0.20142 | -0.21515 | -0.19684 | -0.1236 | -0.10529 | -0.013733 | -0.091553 | 0.013733 | 0.027466 | 0.07782 | -0.009155 | 0.091553 | 0.004578 | 0.29297 | 122.3969 | 0.041199 | 122.4381 | 122.4701 | 122.3328 | 122.3785 | 122.319 | -122.5021 | -122.4243 | 122.3053 | 122.4243 | 61.1435 | 61.1664
885.8438 | 122.5525 | -61.2213 | 61.1984 | 0.028839 | -0.0091388 | 0.0083613 | 0.065747 | -0.016771 | -0.02989 | -0.023674 | 0.014709 | -0.0088867 | 0.063976 | 0.040024 | -0.021999 | -0.0096728 | -0.017383 | -0.045776 | 61.1572 | -61.3403 | 61.1389 | -61.0016 | -61.3724 | -61.3724 | -0.009155 | 61.1572 | -61.2259 | 61.1938 | -61.1526 | -61.1938 | -61.1252 | -0.11902 | -0.041198 | -0.059509 | 0.21973 | -0.15106 | -0.15106 | -0.032043 | -0.032043 | -0.004578 | -0.041198 | -0.004577 | 0.068664 | 0.09613 | 0.027465 | 0.10071 | 0.032043 | 0.33874 | 122.4792 | 0.073242 | 122.4197 | 122.4976 | 122.3831 | 122.3785 | 122.3785 | -122.5388 | -122.4243 | 122.3602 | 122.4152 | 61.1755 | 61.2122
887.625 | 122.5616 | -61.2167 | 61.1206 | 0.01358 | -0.010207 | 0.0094293 | 0.064251 | -0.021044 | -0.030958 | -0.022605 | 0.0055542 | -0.0095275 | 0.06419 | 0.046219 | -0.017726 | -0.0096728 | -0.015674 | -0.10529 | 61.0931 | -61.322 | 61.1252 | -60.9787 | -61.3632 | -61.3861 | -0.054932 | 61.0474 | -61.2442 | 61.1893 | -61.1526 | -61.1847 | -61.1343 | -0.10529 | -0.027465 | 0.004578 | 0.23804 | -0.16937 | -0.14648 | -0.064087 | -0.041199 | -0.027466 | -0.073242 | 0.068665 | 0.064087 | 0.082398 | 0.032044 | 0.10986 | 0.05951 | 0.34332 | 122.4472 | 0.091553 | 122.4335 | 122.4152 | 122.2916 | 122.3099 | 122.2641 | -122.4426 | -122.3648 | 122.3419 | 122.406 | 61.1114 | 61.1618
889.3281 | 122.5937 | -61.2213 | 61.116 | 0.036468 | -0.0052936 | 0.010498 | 0.063611 | -0.016558 | -0.028395 | -0.022178 | 0.011658 | -0.010169 | 0.062481 | 0.050278 | -0.018794 | -0.0088184 | -0.017169 | -0.07782 | 61.0703 | -61.3403 | 61.1389 | -60.9421 | -61.377 | -61.3861 | 0 | 61.0062 | -61.2762 | 61.1938 | -61.1343 | -61.1755 | -61.1206 | -0.11902 | -0.045777 | 0.022888 | 0.27923 | -0.16479 | -0.15564 | -0.045776 | -0.036621 | -0.054932 | -0.10986 | 0.07782 | 0.086975 | 0.10071 | 0.045776 | 0.15564 | 0.10071 | 0.39825 | 122.4792 | 0.14191 | 122.4701 | 122.4106 | 122.2824 | 122.2916 | 122.2275 | -122.4564 | -122.3923 | 122.3602 | 122.4152 | 61.1435 | 61.2213
891.125 | 122.58 | -61.2076 | 61.1389 | 0.0059509 | -0.006789 | 0.010711 | 0.064038 | -0.022967 | -0.031385 | -0.023033 | 0.0055542 | -0.0076049 | 0.062908 | 0.049424 | -0.018794 | -0.010314 | -0.013324 | -0.09613 | 61.0977 | -61.3174 | 61.1343 | -60.9741 | -61.3678 | -61.3953 | -0.050354 | 61.0565 | -61.2442 | 61.1938 | -61.1618 | -61.1801 | -61.1343 | -0.10986 | -0.041199 | -0.004578 | 0.23346 | -0.18768 | -0.16022 | -0.07782 | -0.050354 | -0.036621 | -0.082397 | 0.054932 | 0.045777 | 0.073243 | 0.027466 | 0.10986 | 0.064087 | 0.34332 | 122.4518 | 0.082398 | 122.4381 | 122.4152 | 122.3007 | 122.3053 | 122.2641 | -122.4564 | -122.3831 | 122.3419 | 122.4014 | 61.1115 | 61.1572
892.8906 | 122.6166 | -61.1938 | 61.1343 | 0.02121 | -0.0076434 | 0.0079339 | 0.064679 | -0.021044 | -0.029676 | -0.024528 | 0.0025024 | -0.0091003 | 0.062908 | 0.048997 | -0.019863 | -0.0094592 | -0.015246 | -0.09613 | 61.0794 | -61.3129 | 61.1298 | -60.9787 | -61.3449 | -61.3953 | -0.027466 | 61.0748 | -61.2534 | 61.2213 | -61.0977 | -61.1343 | -61.0886 | -0.11902 | -0.054931 | -0.004577 | 0.21515 | -0.20142 | -0.15106 | -0.082398 | -0.032044 | -0.059509 | -0.059509 | 0.086975 | 0.096131 | 0.10529 | 0.05951 | 0.16479 | 0.11902 | 0.33417 | 122.4426 | 0.15564 | 122.4747 | 122.3923 | 122.3282 | 122.2733 | 122.2687 | -122.4472 | -122.3877 | 122.3236 | 122.4152 | 61.0977 | 61.1664
894.5938 | 122.5113 | -61.1984 | 61.1801 | 0.028839 | -0.0070026 | 0.0090021 | 0.06596 | -0.020403 | -0.028822 | -0.022605 | 0.011658 | -0.0076049 | 0.064617 | 0.045792 | -0.020717 | -0.012664 | -0.021441 | -0.032043 | 61.1893 | -61.2946 | 61.1298 | -60.9924 | -61.3541 | -61.377 | -0.041199 | 61.1252 | -61.2396 | 61.1755 | -61.171 | -61.203 | -61.1343 | -0.096131 | 0.009155 | -0.050354 | 0.20599 | -0.17853 | -0.15564 | -0.082397 | -0.059509 | -0.041199 | -0.054932 | -0.004578 | 0.027466 | 0.064087 | -0.004578 | 0.10529 | 0.036621 | 0.30212 | 122.4243 | 0.068665 | 122.4152 | 122.4838 | 122.3648 | 122.3877 | 122.3236 | -122.4747 | -122.4197 | 122.3282 | 122.374 | 61.1664 | 61.1572
896.3125 | 122.5708 | -61.2213 | 61.1252 | 0.028839 | -0.0089252 | 0.0094293 | 0.063824 | -0.018267 | -0.030104 | -0.02346 | 0.011658 | -0.0076049 | 0.062481 | 0.056046 | -0.018794 | -0.011809 | -0.016101 | -0.091553 | 61.084 | -61.3083 | 61.1435 | -60.9695 | -61.3678 | -61.3907 | -0.036621 | 61.0565 | -61.2625 | 61.203 | -61.1389 | -61.1893 | -61.1298 | -0.086976 | -0.041199 | 0.018311 | 0.25177 | -0.16937 | -0.14648 | -0.082397 | -0.059509 | -0.041199 | -0.068664 | 0.07782 | 0.082397 | 0.091552 | 0.032043 | 0.13275 | 0.073242 | 0.33875 | 122.4518 | 0.1236 | 122.4655 | 122.3923 | 122.319 | 122.3053 | 122.2778 | -122.4335 | -122.3877 | 122.3648 | 122.4243 | 61.1298 | 61.1847
898.1094 | 122.5754 | -61.1801 | 61.1343 | 0.01358 | -0.0087116 | 0.0083613 | 0.062329 | -0.020189 | -0.031385 | -0.025169 | 0.0025024 | -0.0095275 | 0.062908 | 0.045365 | -0.018581 | -0.011809 | -0.011615 | -0.091553 | 61.0886 | -61.3083 | 61.1343 | -60.9695 | -61.3632 | -61.3724 | -0.032043 | 61.0336 | -61.2488 | 61.203 | -61.1572 | -61.1801 | -61.1298 | -0.12817 | -0.045776 | 0 | 0.21057 | -0.19226 | -0.1831 | -0.064086 | -0.054931 | -0.068664 | -0.10071 | 0.068665 | 0.022888 | 0.050354 | 0 | 0.11902 | 0.068664 | 0.33875 | 122.4426 | 0.091552 | 122.4518 | 122.3969 | 122.2824 | 122.2687 | 122.2137 | -122.4426 | -122.3831 | 122.3145 | 122.3831 | 61.0886 | 61.1481
899.875 | 122.4884 | -61.2579 | 61.1069 | 0.0059509 | -0.0059344 | 0.0098565 | 0.065747 | -0.019549 | -0.033308 | -0.019615 | -0.00054937 | -0.0061095 | 0.062694 | 0.038102 | -0.019863 | -0.011382 | -0.01311 | -0.11902 | 61.1069 | -61.3449 | 61.0336 | -61.1023 | -61.4914 | -61.5189 | -0.16937 | 61.0565 | -61.3266 | 61.1069 | -61.2717 | -61.2991 | -61.203 | -0.086975 | 0 | -0.073243 | 0.15564 | -0.26092 | -0.23346 | -0.17395 | -0.14648 | -0.068664 | -0.050354 | 0 | -0.013732 | 0.054932 | -0.041198 | 0.1236 | 0.027466 | 0.24262 | 122.3785 | 0.054932 | 122.4335 | 122.4518 | 122.3831 | 122.3648 | 122.3145 | -122.4518 | -122.4335 | 122.2916 | 122.3648 | 61.1389 | 61.0886
901.6094 | 122.4792 | -61.2854 | 61.1343 | 0.01358 | -0.0074298 | 0.010925 | 0.066174 | -0.01549 | -0.029036 | -0.023887 | 0.0025024 | -0.0088867 | 0.063976 | 0.043442 | -0.020503 | -0.011595 | -0.016314 | -0.14191 | 61.116 | -61.3449 | 61.0245 | -61.116 | -61.5005 | -61.5051 | -0.14648 | 61.0611 | -61.322 | 61.1023 | -61.2762 | -61.3083 | -61.2122 | -0.05951 | -0.01831 | -0.10986 | 0.16937 | -0.21973 | -0.21515 | -0.16022 | -0.15564 | -0.036621 | -0.073242 | -0.032043 | 0.009155 | 0.073242 | -0.022889 | 0.10986 | 0.013732 | 0.22888 | 122.3694 | 0.045776 | 122.4243 | 122.4609 | 122.3831 | 122.4014 | 122.3465 | -122.4792 | -122.4564 | 122.3099 | 122.3877 | 61.1435 | 61.1389
903.3281 | 122.5204 | -61.2259 | 61.1343 | 0.0059509 | -0.0076434 | 0.0085749 | 0.066601 | -0.022326 | -0.032026 | -0.024955 | 0.0025024 | -0.0056823 | 0.061626 | 0.04387 | -0.018581 | -0.0101 | -0.015033 | -0.036621 | 61.1298 | -61.2762 | 61.1389 | -60.9558 | -61.3632 | -61.3907 | -0.009155 | 61.084 | -61.235 | 61.1801 | -61.1755 | -61.2213 | -61.1435 | -0.050354 | -0.004577 | 0.004578 | 0.27008 | -0.1648 | -0.13733 | -0.11444 | -0.086975 | -0.009155 | -0.050354 | 0.045777 | 0.050354 | 0.082397 | 0.004578 | 0.091552 | 0.013733 | 0.32043 | 122.4152 | 0.059509 | 122.4152 | 122.406 | 122.319 | 122.3557 | 122.3099 | -122.4106 | -122.3694 | 122.3648 | 122.406 | 61.1893 | 61.2167
905.1094 | 122.5845 | -61.2213 | 61.1206 | 0.036468 | -0.0099932 | 0.0096429 | 0.063611 | -0.020189 | -0.030104 | -0.025169 | 0.008606 | -0.0088867 | 0.067821 | 0.04921 | -0.019649 | -0.010314 | -0.016314 | -0.07782 | 61.0611 | -61.3174 | 61.1343 | -60.9558 | -61.3632 | -61.3861 | -0.018311 | 61.0245 | -61.2534 | 61.1801 | -61.1435 | -61.1664 | -61.116 | -0.096131 | -0.059509 | 0.013733 | 0.2655 | -0.16479 | -0.14191 | -0.068664 | -0.045776 | -0.032044 | -0.09613 | 0.05951 | 0.077819 | 0.10529 | 0.054931 | 0.13733 | 0.086975 | 0.36163 | 122.4518 | 0.10986 | 122.4335 | 122.3785 | 122.2778 | 122.2824 | 122.2458 | -122.438 | -122.374 | 122.3557 | 122.4014 | 61.1435 | 61.203
906.875 | 122.493 | -61.1801 | 61.2213 | -0.0016786 | -0.0076434 | 0.0079339 | 0.064465 | -0.021471 | -0.03224 | -0.023033 | -0.00054937 | -0.0073913 | 0.063762 | 0.045151 | -0.024349 | -0.0101 | -0.016955 | -0.064087 | 61.1801 | -61.2762 | 61.1114 | -60.9833 | -61.3495 | -61.377 | -0.032043 | 61.1298 | -61.1984 | 61.1755 | -61.1389 | -61.1801 | -61.1206 | -0.09613 | -0.041198 | -0.10986 | 0.19684 | -0.19684 | -0.16937 | -0.10071 | -0.073242 | -0.01831 | -0.091552 | -0.045776 | 0.041199 | 0.05951 | 0 | 0.07782 | 0.01831 | 0.29297 | 122.3877 | 0.059509 | 122.374 | 122.4564 | 122.3282 | 122.3602 | 122.3099 | -122.4976 | -122.4197 | 122.2916 | 122.3557 | 61.116 | 61.1481
908.5938 | 122.612 | -61.1526 | 61.1526 | 0.0059509 | -0.0093524 | 0.0066523 | 0.06532 | -0.021044 | -0.032454 | -0.026451 | -0.003601 | -0.0080321 | 0.061199 | 0.048783 | -0.021785 | -0.0086048 | -0.014605 | -0.009155 | 61.0886 | -61.2488 | 61.2442 | -60.8322 | -61.2488 | -61.2808 | 0.09613 | 61.0703 | -61.1984 | 61.3037 | -61.0199 | -61.0565 | -61.0382 | -0.09613 | -0.064087 | 0.091553 | 0.32043 | -0.12817 | -0.09613 | -0.032044 | 0 | -0.045776 | -0.082398 | 0.15106 | 0.13275 | 0.11444 | 0.09613 | 0.16022 | 0.14191 | 0.41656 | 122.493 | 0.17853 | 122.5021 | 122.3373 | 122.2687 | 122.2412 | 122.2229 | -122.4014 | -122.3511 | 122.3969 | 122.4564 | 61.1435 | 61.2488
910.375 | 122.493 | -61.2717 | 61.1435 | 0.0059509 | -0.0063616 | 0.0092157 | 0.066388 | -0.018267 | -0.030104 | -0.024101 | -0.00054937 | -0.0080321 | 0.065258 | 0.038529 | -0.01794 | -0.010527 | -0.013965 | -0.13275 | 61.116 | -61.3358 | 61.0245 | -61.0931 | -61.4777 | -61.4777 | -0.1236 | 61.0657 | -61.29 | 61.1206 | -61.2671 | -61.29 | -61.1984 | -0.064087 | -0.027466 | -0.11902 | 0.17853 | -0.20599 | -0.20599 | -0.14191 | -0.14191 | -0.018311 | -0.07782 | -0.022889 | 0.004577 | 0.073242 | -0.018311 | 0.091553 | 0 | 0.24261 | 122.3602 | 0.022888 | 122.4106 | 122.4518 | 122.3557 | 122.3877 | 122.3373 | -122.4792 | -122.4335 | 122.2961 | 122.3923 | 61.1389 | 61.1481
912.1094 | 122.5388 | -61.2122 | 61.1343 | 0.01358 | -0.006789 | 0.0087885 | 0.066601 | -0.01784 | -0.030104 | -0.024955 | 0.0055542 | -0.0086731 | 0.064403 | 0.034897 | -0.018794 | -0.0098864 | -0.017169 | -0.041199 | 61.1526 | -61.3037 | 61.1481 | -60.9421 | -61.3358 | -61.3861 | 0.013733 | 61.0931 | -61.2396 | 61.2076 | -61.1572 | -61.1847 | -61.1435 | -0.091553 | 0.018311 | 0.013733 | 0.27008 | -0.17395 | -0.1236 | -0.082397 | -0.032043 | -0.027466 | -0.041198 | 0.073243 | 0.054931 | 0.068664 | 0.027466 | 0.09613 | 0.054932 | 0.36163 | 122.4518 | 0.082397 | 122.4472 | 122.4564 | 122.3328 | 122.3648 | 122.3053 | -122.438 | -122.374 | 122.3602 | 122.4197 | 61.171 | 61.2259
913.875 | 122.6166 | -61.1572 | 61.1389 | 0.0059509 | -0.010207 | 0.0096429 | 0.063183 | -0.022112 | -0.030104 | -0.02581 | 0.0055542 | -0.0093139 | 0.06419 | 0.041092 | -0.019649 | -0.010741 | -0.018878 | -0.036621 | 61.1069 | -61.2625 | 61.2122 | -60.878 | -61.2579 | -61.2991 | 0.07782 | 61.0611 | -61.2076 | 61.29 | -61.0153 | -61.0703 | -61.0382 | -0.10529 | -0.032043 | 0.073242 | 0.27924 | -0.14191 | -0.10071 | -0.036621 | 0.004577 | -0.050354 | -0.07782 | 0.15106 | 0.14191 | 0.11902 | 0.086976 | 0.16937 | 0.13733 | 0.38452 | 122.4747 | 0.19226 | 122.4976 | 122.3694 | 122.2687 | 122.2641 | 122.2183 | -122.4014 | -122.3465 | 122.3694 | 122.4472 | 61.1206 | 61.235
915.5938 | 122.525 | -61.2122 | 61.1755 | 0.02121 | -0.0072162 | 0.0092157 | 0.065106 | -0.022539 | -0.027754 | -0.022178 | 0.0025024 | -0.0063233 | 0.063121 | 0.040024 | -0.020503 | -0.010314 | -0.013324 | -0.032043 | 61.1481 | -61.2717 | 61.1389 | -60.9283 | -61.3495 | -61.3907 | 0.027466 | 61.0794 | -61.2396 | 61.1893 | -61.1481 | -61.1938 | -61.1114 | -0.059509 | -0.027466 | -0.036621 | 0.28381 | -0.17853 | -0.13733 | -0.11902 | -0.07782 | -0.027466 | -0.09613 | 0.013733 | 0.064087 | 0.10071 | 0.01831 | 0.12817 | 0.045776 | 0.34332 | 122.4106 | 0.091553 | 122.4289 | 122.4197 | 122.319 | 122.3602 | 122.2916 | -122.4472 | -122.4152 | 122.3511 | 122.4014 | 61.1801 | 61.2396
917.3594 | 122.5021 | -61.1755 | 61.2076 | 0.0059509 | -0.0097796 | 0.0081477 | 0.061902 | -0.021471 | -0.029463 | -0.02111 | 0.0025024 | -0.0099549 | 0.065044 | 0.04451 | -0.021144 | -0.0098864 | -0.015246 | -0.009155 | 61.1343 | -61.2671 | 61.1664 | -60.91 | -61.2991 | -61.3312 | 0 | 61.116 | -61.1801 | 61.1893 | -61.116 | -61.1526 | -61.1069 | -0.091553 | -0.073243 | -0.041199 | 0.2655 | -0.15564 | -0.1236 | -0.064087 | -0.032043 | -0.004578 | -0.091553 | -0.018311 | 0.059509 | 0.068664 | 0.022888 | 0.073242 | 0.027466 | 0.35706 | 122.4335 | 0.064087 | 122.3694 | 122.4014 | 122.2961 | 122.3099 | 122.2916 | -122.4747 | -122.3877 | 122.3419 | 122.3648 | 61.1664 | 61.1755
919.0781 | 122.4609 | -61.2671 | 61.1343 | 0.0059509 | -0.004439 | 0.010284 | 0.066388 | -0.013781 | -0.02989 | -0.024101 | 0.0025024 | -0.0073913 | 0.062267 | 0.043656 | -0.020717 | -0.010314 | -0.016101 | -0.12817 | 61.1114 | -61.3358 | 61.0336 | -61.084 | -61.4777 | -61.4822 | -0.15564 | 61.0336 | -61.3037 | 61.0931 | -61.2854 | -61.3129 | -61.2076 | -0.068664 | -0.022888 | -0.10071 | 0.18311 | -0.21515 | -0.21057 | -0.14648 | -0.14191 | -0.036621 | -0.10071 | -0.041198 | -0.01831 | 0.059509 | -0.045776 | 0.09613 | -0.009155 | 0.25177 | 122.3694 | 0.018311 | 122.3969 | 122.4472 | 122.3373 | 122.3785 | 122.3007 | -122.4701 | -122.438 | 122.3007 | 122.3602 | 61.1389 | 61.1115
920.8594 | 122.4884 | -61.1938 | 61.2122 | -0.0093076 | -0.011061 | 0.0083613 | 0.065747 | -0.021044 | -0.031385 | -0.02346 | 0.0025024 | -0.0078185 | 0.065258 | 0.045792 | -0.022426 | -0.012236 | -0.019732 | -0.041199 | 61.1526 | -61.2534 | 61.1481 | -60.9421 | -61.3358 | -61.3449 | -0.022888 | 61.1343 | -61.1984 | 61.1847 | -61.1298 | -61.1618 | -61.1252 | -0.059509 | -0.059509 | -0.064087 | 0.25177 | -0.15106 | -0.14191 | -0.091553 | -0.082397 | -0.004577 | -0.07782 | -0.027466 | 0.064087 | 0.068665 | 0.032044 | 0.073242 | 0.036621 | 0.31128 | 122.4014 | 0.068664 | 122.3831 | 122.406 | 122.3328 | 122.3465 | 122.3282 | -122.4655 | -122.4106 | 122.3419 | 122.3785 | 61.1526 | 61.171
922.5781 | 122.5708 | -61.1618 | 61.1618 | 0.02121 | -0.0097796 | 0.0096429 | 0.064465 | -0.018694 | -0.031813 | -0.023674 | 0.008606 | -0.0097411 | 0.065258 | 0.051133 | -0.017726 | -0.009032 | -0.014605 | -0.086975 | 61.084 | -61.2991 | 61.1389 | -60.9467 | -61.3266 | -61.3678 | -0.004578 | 61.0474 | -61.2213 | 61.2442 | -61.0794 | -61.1023 | -61.0657 | -0.13733 | -0.07782 | -0.022888 | 0.21515 | -0.20599 | -0.1648 | -0.068665 | -0.027466 | -0.059509 | -0.11444 | 0.082398 | 0.082397 | 0.09613 | 0.059509 | 0.15564 | 0.11902 | 0.35248 | 122.438 | 0.14191 | 122.4655 | 122.3831 | 122.2687 | 122.2458 | 122.2092 | -122.4609 | -122.3831 | 122.3007 | 122.406 | 61.0748 | 61.1572
924.2812 | 122.4976 | -61.1618 | 61.2167 | -0.0016786 | -0.0087116 | 0.0092157 | 0.06532 | -0.022753 | -0.029463 | -0.026664 | -0.003601 | -0.0076049 | 0.062908 | 0.043442 | -0.022853 | -0.0098864 | -0.015674 | -0.004578 | 61.1114 | -61.2396 | 61.1664 | -60.91 | -61.29 | -61.3312 | 0.018311 | 61.1252 | -61.1938 | 61.2076 | -61.116 | -61.1435 | -61.0977 | -0.07782 | -0.10529 | -0.050354 | 0.25177 | -0.16937 | -0.12817 | -0.091553 | -0.050354 | -0.032044 | -0.091553 | -0.009155 | 0.045776 | 0.064087 | 0.01831 | 0.096131 | 0.050354 | 0.32959 | 122.406 | 0.07782 | 122.4014 | 122.3511 | 122.319 | 122.2733 | 122.287 | -122.4564 | -122.4106 | 122.3282 | 122.3694 | 61.1572 | 61.1801
926.0469 | 122.4976 | -61.1847 | 61.1984 | 0.0059509 | -0.008498 | 0.0077203 | 0.065106 | -0.022967 | -0.032667 | -0.023674 | 0.0025024 | -0.0088867 | 0.06419 | 0.045579 | -0.019863 | -0.010314 | -0.015033 | 0 | 61.1298 | -61.2488 | 61.1755 | -60.9009 | -61.2946 | -61.3358 | 0.027466 | 61.1435 | -61.1847 | 61.203 | -61.0931 | -61.1526 | -61.116 | -0.064087 | -0.068664 | -0.022888 | 0.28381 | -0.15106 | -0.10986 | -0.086975 | -0.045777 | 0 | -0.054931 | 0.004578 | 0.091552 | 0.068664 | 0.032043 | 0.068664 | 0.032043 | 0.3479 | 122.4243 | 0.091552 | 122.3877 | 122.3785 | 122.3282 | 122.3145 | 122.3282 | -122.4472 | -122.3831 | 122.3602 | 122.3877 | 61.1847 | 61.2122
927.8125 | 122.6166 | -61.1343 | 61.1664 | 0.0059509 | -0.0093524 | 0.0098565 | 0.063183 | -0.019121 | -0.030745 | -0.024528 | 0.0025024 | -0.0097411 | 0.065258 | 0.04686 | -0.021785 | -0.0098864 | -0.017383 | -0.013733 | 61.1023 | -61.2488 | 61.235 | -60.7956 | -61.2213 | -61.2488 | 0.11444 | 61.084 | -61.1664 | 61.2946 | -60.997 | -61.0519 | -61.0291 | -0.11444 | -0.064087 | 0.068664 | 0.33875 | -0.11444 | -0.086975 | 0 | 0.027466 | -0.032044 | -0.082398 | 0.12817 | 0.13733 | 0.10529 | 0.082397 | 0.13733 | 0.11444 | 0.45319 | 122.4838 | 0.16937 | 122.4609 | 122.3511 | 122.2504 | 122.2366 | 122.2183 | -122.4152 | -122.3328 | 122.3694 | 122.4289 | 61.1206 | 61.2488
929.5781 | 122.5845 | -61.1481 | 61.1847 | 0.0059509 | -0.0097796 | 0.0098565 | 0.063611 | -0.021044 | -0.03224 | -0.024101 | -0.00054937 | -0.0099549 | 0.061626 | 0.048142 | -0.021358 | -0.0081774 | -0.01546 | 0.009155 | 61.116 | -61.2442 | 61.235 | -60.8459 | -61.2396 | -61.2808 | 0.091553 | 61.0886 | -61.1847 | 61.29 | -61.0336 | -61.0657 | -61.0153 | -0.096131 | -0.068664 | 0.050354 | 0.30212 | -0.13275 | -0.091553 | -0.036621 | 0.004578 | -0.036621 | -0.09613 | 0.10529 | 0.11444 | 0.13275 | 0.082397 | 0.16937 | 0.11902 | 0.39825 | 122.4792 | 0.15106 | 122.4747 | 122.3602 | 122.2733 | 122.2641 | 122.2366 | -122.4289 | -122.3694 | 122.3831 | 122.438 | 61.1572 | 61.2396
931.2969 | 122.5754 | -61.2213 | 61.0703 | -0.0016786 | -0.0091388 | 0.0087885 | 0.069165 | -0.020403 | -0.031385 | -0.023246 | 0.0025024 | -0.0071777 | 0.064617 | 0.049851 | -0.016231 | -0.0079638 | -0.014178 | -0.13733 | 61.0703 | -61.3266 | 61.0703 | -61.0199 | -61.4182 | -61.441 | -0.068665 | 61.0016 | -61.2534 | 61.1984 | -61.1526 | -61.1801 | -61.1023 | -0.10529 | 0 | 0 | 0.20142 | -0.21973 | -0.19684 | -0.11444 | -0.091553 | -0.032044 | -0.068664 | 0.12817 | 0.068664 | 0.11902 | 0.041198 | 0.15106 | 0.073242 | 0.3067 | 122.3969 | 0.10071 | 122.4518 | 122.3969 | 122.2549 | 122.2916 | 122.2229 | -122.3969 | -122.3236 | 122.2916 | 122.4197 | 61.084 | 61.1526
933.0781 | 122.6166 | -61.1298 | 61.1435 | -0.0016786 | -0.0080706 | 0.0098565 | 0.063611 | -0.024248 | -0.032026 | -0.025383 | 0.0025024 | -0.0091003 | 0.062267 | 0.044083 | -0.022212 | -0.0088184 | -0.018664 | -0.068665 | 61.1069 | -61.2671 | 61.1755 | -60.8871 | -61.2808 | -61.3174 | 0.018311 | 61.0703 | -61.1847 | 61.2762 | -61.0336 | -61.0611 | -61.0153 | -0.13733 | -0.036621 | 0.032043 | 0.24262 | -0.18768 | -0.15106 | -0.050354 | -0.013733 | -0.054931 | -0.073243 | 0.13275 | 0.096131 | 0.11444 | 0.068665 | 0.16937 | 0.1236 | 0.37994 | 122.4426 | 0.15106 | 122.4609 | 122.374 | 122.2549 | 122.2366 | 122.2 | -122.4106 | -122.3282 | 122.3053 | 122.406 | 61.0611 | 61.1481
934.8438 | 122.6212 | -61.1755 | 61.1435 | -0.0016786 | -0.0082842 | 0.0077203 | 0.065533 | -0.02083 | -0.030317 | -0.02581 | 0.0025024 | -0.0086731 | 0.062694 | 0.040452 | -0.017513 | -0.011168 | -0.016101 | -0.073242 | 61.0931 | -61.2717 | 61.1801 | -60.8963 | -61.2488 | -61.29 | 0.036621 | 61.0611 | -61.2076 | 61.2762 | -61.0199 | -61.0519 | -61.0153 | -0.09613 | -0.050354 | 0.036621 | 0.27924 | -0.11444 | -0.073242 | -0.018311 | 0.022888 | -0.032044 | -0.082398 | 0.13275 | 0.15564 | 0.16022 | 0.1236 | 0.19226 | 0.15564 | 0.37537 | 122.4518 | 0.18768 | 122.4838 | 122.3648 | 122.2687 | 122.2687 | 122.2366 | -122.4152 | -122.3511 | 122.3557 | 122.4518 | 61.1023 | 61.2122
936.625 | 122.4701 | -61.2534 | 61.116 | -0.0016786 | -0.0082842 | 0.01007 | 0.06596 | -0.021258 | -0.030104 | -0.025596 | 0.0025024 | -0.0046143 | 0.063335 | 0.040024 | -0.02029 | -0.0088184 | -0.014392 | -0.11444 | 61.1069 | -61.3129 | 61.0382 | -61.0794 | -61.4777 | -61.4914 | -0.13733 | 61.0703 | -61.2762 | 61.1252 | -61.2534 | -61.2854 | -61.1847 | -0.059509 | -0.009155 | -0.07782 | 0.17395 | -0.23804 | -0.2243 | -0.17853 | -0.16479 | -0.022888 | -0.045777 | 0.009155 | 0 | 0.068665 | -0.032043 | 0.091553 | -0.009155 | 0.23346 | 122.3511 | 0.022888 | 122.4014 | 122.4197 | 122.3465 | 122.3602 | 122.3236 | -122.4289 | -122.3923 | 122.2916 | 122.3785 | 61.1389 | 61.116
938.4062 | 122.5662 | -61.2213 | 61.084 | 0.0059509 | -0.0080706 | 0.01007 | 0.066174 | -0.016985 | -0.02989 | -0.025596 | -0.00054937 | -0.0078185 | 0.063549 | 0.049637 | -0.018794 | -0.0094592 | -0.013965 | -0.13733 | 61.0886 | -61.3312 | 61.0703 | -61.0107 | -61.4365 | -61.441 | -0.054932 | 61.0016 | -61.2717 | 61.203 | -61.1343 | -61.1755 | -61.0886 | -0.10986 | 0.004578 | -0.013733 | 0.21057 | -0.21973 | -0.21515 | -0.10986 | -0.10529 | -0.050354 | -0.082397 | 0.11902 | 0.086975 | 0.13275 | 0.045776 | 0.1831 | 0.09613 | 0.32043 | 122.4014 | 0.13733 | 122.4747 | 122.4197 | 122.2733 | 122.3099 | 122.2229 | -122.4152 | -122.3557 | 122.2916 | 122.4243 | 61.084 | 61.1664
940.1094 | 122.4792 | -61.2442 | 61.1664 | 0.02121 | -0.006148 | 0.0087885 | 0.065747 | -0.016985 | -0.028822 | -0.025169 | 0.0025024 | -0.0073913 | 0.06419 | 0.046006 | -0.019863 | -0.0094592 | -0.015887 | -0.059509 | 61.1114 | -61.2717 | 61.0931 | -60.997 | -61.4273 | -61.4227 | -0.068665 | 61.0703 | -61.2579 | 61.1343 | -61.1984 | -61.2442 | -61.1755 | -0.027465 | -0.054932 | -0.073242 | 0.24719 | -0.17853 | -0.1831 | -0.15106 | -0.15564 | -0.013733 | -0.096131 | -0.032044 | 0.045777 | 0.068665 | 0 | 0.082398 | 0.013733 | 0.27466 | 122.3648 | 0.05951 | 122.3923 | 122.3831 | 122.3282 | 122.3557 | 122.3145 | -122.438 | -122.4243 | 122.3373 | 122.3785 | 61.1847 | 61.1755
941.8906 | 122.5021 | -61.2213 | 61.1526 | 0.01358 | -0.0072162 | 0.0087885 | 0.066388 | -0.018053 | -0.02989 | -0.021751 | 0.0025024 | -0.0063233 | 0.065258 | 0.043229 | -0.021785 | -0.0088184 | -0.015246 | -0.041199 | 61.1481 | -61.3129 | 61.1435 | -60.9283 | -61.3312 | -61.3815 | -0.009155 | 61.0794 | -61.2122 | 61.203 | -61.1343 | -61.1801 | -61.1114 | -0.091553 | -0.004578 | -0.009155 | 0.29297 | -0.16022 | -0.10986 | -0.068665 | -0.018311 | 0.009155 | -0.073242 | 0.050354 | 0.086975 | 0.10986 | 0.041198 | 0.10071 | 0.032043 | 0.38452 | 122.4564 | 0.07782 | 122.4152 | 122.4609 | 122.2916 | 122.3694 | 122.3007 | -122.4655 | -122.3648 | 122.3648 | 122.4243 | 61.1801 | 61.2122
943.6875 | 122.4747 | -61.2396 | 61.1343 | 0.0059509 | -0.0063616 | 0.0090021 | 0.065533 | -0.015917 | -0.029249 | -0.025169 | -0.00054937 | -0.0078185 | 0.064403 | 0.042801 | -0.01794 | -0.0098864 | -0.018237 | -0.16022 | 61.1298 | -61.3266 | 61.0153 | -61.0886 | -61.4777 | -61.4777 | -0.16022 | 61.0611 | -61.2579 | 61.1298 | -61.2442 | -61.2717 | -61.1984 | -0.086975 | -0.004577 | -0.11902 | 0.15106 | -0.23804 | -0.23804 | -0.15106 | -0.15106 | -0.018311 | -0.073242 | -0.004577 | -0.004578 | 0.041199 | -0.032043 | 0.05951 | -0.013732 | 0.23804 | 122.3419 | 0.013733 | 122.3877 | 122.4564 | 122.319 | 122.3694 | 122.3007 | -122.4609 | -122.3923 | 122.2549 | 122.3694 | 61.0794 | 61.0794
945.4531 | 122.5067 | -61.2122 | 61.1389 | 0.01358 | -0.0057208 | 0.010711 | 0.065106 | -0.022326 | -0.030531 | -0.023033 | 0.0055542 | -0.0069641 | 0.064617 | 0.037034 | -0.019222 | -0.0101 | -0.012683 | -0.050354 | 61.1572 | -61.29 | 61.1435 | -60.9238 | -61.3403 | -61.3724 | 0 | 61.084 | -61.2076 | 61.1938 | -61.1206 | -61.1618 | -61.1069 | -0.07782 | 0.018311 | 0.004578 | 0.28839 | -0.16022 | -0.12817 | -0.082397 | -0.050354 | 0.004577 | -0.054932 | 0.054932 | 0.091553 | 0.10529 | 0.050354 | 0.10071 | 0.045777 | 0.36621 | 122.4335 | 0.086976 | 122.4014 | 122.4472 | 122.2916 | 122.3694 | 122.2961 | -122.4289 | -122.3465 | 122.3557 | 122.406 | 61.1618 | 61.2122
947.1875 | 122.5433 | -61.1664 | 61.1481 | 0.02121 | -0.0097796 | 0.0075067 | 0.062329 | -0.021258 | -0.030531 | -0.02346 | 0.0055542 | -0.0080321 | 0.06483 | 0.051133 | -0.02029 | -0.0088184 | -0.013965 | -0.09613 | 61.0886 | -61.2671 | 61.1206 | -60.9329 | -61.3358 | -61.3586 | -0.059509 | 61.0611 | -61.2259 | 61.203 | -61.116 | -61.1389 | -61.0794 | -0.10071 | -0.059509 | -0.027466 | 0.23346 | -0.19226 | -0.16937 | -0.091553 | -0.068664 | -0.059509 | -0.086975 | 0.054932 | 0.050354 | 0.086975 | 0.027466 | 0.14648 | 0.086975 | 0.33417 | 122.3877 | 0.10986 | 122.4289 | 122.3557 | 122.287 | 122.2549 | 122.2275 | -122.4152 | -122.374 | 122.287 | 122.3694 | 61.0703 | 61.1069
948.9688 | 122.5204 | -61.1572 | 61.1755 | 0.01358 | -0.007857 | 0.011352 | 0.06532 | -0.020189 | -0.029249 | -0.024955 | 0.0025024 | -0.0078185 | 0.061199 | 0.044724 | -0.02264 | -0.010527 | -0.019305 | -0.027466 | 61.1572 | -61.29 | 61.1389 | -60.9192 | -61.3266 | -61.3586 | 0.013733 | 61.0748 | -61.2167 | 61.2122 | -61.0886 | -61.1572 | -61.0886 | -0.13275 | -0.01831 | -0.036621 | 0.23804 | -0.20142 | -0.16937 | -0.068665 | -0.036621 | -0.059509 | -0.10071 | 0.036621 | 0.068665 | 0.068665 | 0 | 0.12817 | 0.059509 | 0.37079 | 122.4289 | 0.12817 | 122.4289 | 122.4472 | 122.2916 | 122.3145 | 122.2321 | -122.4655 | -122.3923 | 122.2961 | 122.3694 | 61.1298 | 61.171
950.7344 | 122.4701 | -61.203 | 61.1664 | -0.0016786 | -0.0057208 | 0.0092157 | 0.066388 | -0.01549 | -0.02989 | -0.021537 | 0.0055542 | -0.0069641 | 0.062908 | 0.043442 | -0.020503 | -0.010955 | -0.015887 | -0.068665 | 61.116 | -61.29 | 61.0977 | -60.965 | -61.3953 | -61.4273 | -0.07782 | 61.0611 | -61.2396 | 61.1389 | -61.203 | -61.2396 | -61.1618 | -0.086975 | -0.050354 | -0.068665 | 0.23804 | -0.2243 | -0.19226 | -0.13733 | -0.10529 | -0.036621 | -0.10529 | -0.027466 | 0 | 0.041199 | -0.036621 | 0.07782 | 0 | 0.32501 | 122.3877 | 0.036621 | 122.3785 | 122.406 | 122.3007 | 122.319 | 122.2641 | -122.4564 | -122.406 | 122.3007 | 122.3419 | 61.1343 | 61.1252
952.5 | 122.4884 | -61.2076 | 61.1481 | 0.0059509 | -0.0065754 | 0.010711 | 0.067029 | -0.016344 | -0.030958 | -0.022178 | 0.0025024 | -0.0067505 | 0.063335 | 0.048356 | -0.021572 | -0.0079638 | -0.013324 | -0.059509 | 61.1343 | -61.2808 | 61.116 | -60.9512 | -61.3632 | -61.3953 | -0.045776 | 61.0703 | -61.2396 | 61.1526 | -61.1801 | -61.2305 | -61.1435 | -0.073242 | -0.013733 | -0.032043 | 0.25635 | -0.18768 | -0.15564 | -0.11444 | -0.082397 | -0.032043 | -0.07782 | 0.004578 | 0.027466 | 0.064087 | -0.022888 | 0.09613 | 0.009155 | 0.32959 | 122.3969 | 0.059509 | 122.3923 | 122.4152 | 122.3099 | 122.3419 | 122.2778 | -122.4289 | -122.3877 | 122.3236 | 122.3602 | 61.1481 | 61.1618
954.2188 | 122.4792 | -61.1984 | 61.1526 | 0.01358 | -0.003371 | 0.0092157 | 0.065747 | -0.015703 | -0.030958 | -0.024742 | 0.0025024 | -0.0054687 | 0.063762 | 0.042801 | -0.019863 | -0.0098864 | -0.016314 | -0.041199 | 61.1389 | -61.2671 | 61.116 | -60.9329 | -61.3495 | -61.3815 | -0.013733 | 61.0931 | -61.2213 | 61.1893 | -61.1618 | -61.1938 | -61.1206 | -0.068665 | -0.013733 | -0.036621 | 0.2655 | -0.18311 | -0.15106 | -0.11444 | -0.082397 | -0.022888 | -0.059509 | 0.036621 | 0.036621 | 0.07782 | 0.004577 | 0.10071 | 0.027465 | 0.33417 | 122.3831 | 0.059509 | 122.4106 | 122.406 | 122.3145 | 122.3373 | 122.2916 | -122.4197 | -122.374 | 122.3145 | 122.3877 | 61.1572 | 61.1847
956 | 122.5891 | -61.203 | 61.0886 | 0.0059509 | -0.0091388 | 0.0098565 | 0.065106 | -0.021471 | -0.029463 | -0.023033 | 0.0025024 | -0.0097411 | 0.065258 | 0.04921 | -0.019008 | -0.010955 | -0.016742 | -0.1236 | 61.0703 | -61.2946 | 61.0931 | -60.9329 | -61.3861 | -61.3907 | -0.004578 | 61.0153 | -61.2259 | 61.2396 | -61.0931 | -61.1435 | -61.0703 | -0.091553 | -0.018311 | 0.004578 | 0.27008 | -0.18768 | -0.1831 | -0.09613 | -0.091552 | -0.022888 | -0.073242 | 0.15106 | 0.10986 | 0.13275 | 0.059509 | 0.15564 | 0.082397 | 0.36163 | 122.3877 | 0.13275 | 122.4655 | 122.3648 | 122.2412 | 122.2733 | 122.2183 | -122.3831 | -122.3145 | 122.2961 | 122.4426 | 61.0794 | 61.1984
957.7031 | 122.4335 | -61.2305 | 61.1618 | 0.0059509 | -0.006148 | 0.0081477 | 0.06596 | -0.021471 | -0.02754 | -0.028587 | 0.0025024 | -0.0080321 | 0.062694 | 0.042588 | -0.019008 | -0.010741 | -0.016314 | -0.1236 | 61.1389 | -61.3083 | 61.0245 | -61.0611 | -61.4502 | -61.4639 | -0.16022 | 61.0657 | -61.2808 | 61.116 | -61.2213 | -61.2717 | -61.1526 | -0.07782 | -0.022888 | -0.13733 | 0.16937 | -0.23346 | -0.21973 | -0.15564 | -0.14191 | -0.050354 | -0.09613 | -0.045776 | 0.009156 | 0.07782 | -0.041198 | 0.12817 | 0.009156 | 0.24719 | 122.3328 | 0.05951 | 122.3969 | 122.4472 | 122.3465 | 122.3694 | 122.2961 | -122.4701 | -122.4426 | 122.2549 | 122.3465 | 61.1069 | 61.0703
959.4844 | 122.4792 | -61.2167 | 61.1114 | 0.0059509 | -0.006789 | 0.0087885 | 0.063611 | -0.013994 | -0.031385 | -0.021537 | 0.0055542 | -0.0067505 | 0.063762 | 0.04686 | -0.021572 | -0.010314 | -0.014392 | -0.1236 | 61.1298 | -61.2854 | 61.0107 | -61.0703 | -61.4456 | -61.4685 | -0.1831 | 61.0565 | -61.2579 | 61.1343 | -61.2305 | -61.2579 | -61.1618 | -0.068664 | 0.018311 | -0.10071 | 0.14648 | -0.25177 | -0.22888 | -0.18311 | -0.16022 | -0.041199 | -0.054931 | 0.022888 | -0.013733 | 0.054932 | -0.041199 | 0.096131 | 0 | 0.21515 | 122.2961 | 0.027466 | 122.3923 | 122.4152 | 122.3145 | 122.3465 | 122.2733 | -122.3969 | -122.3694 | 122.2275 | 122.3511 | 61.0931 | 61.0336
961.2188 | 122.4701 | -61.1526 | 61.1893 | 0.01358 | -0.0072162 | 0.0079339 | 0.064679 | -0.021685 | -0.030317 | -0.024314 | 0.017761 | -0.0063233 | 0.06483 | 0.040452 | -0.023281 | -0.012236 | -0.016528 | -0.082397 | 61.1984 | -61.2305 | 61.1069 | -60.9375 | -61.29 | -61.3129 | -0.041199 | 61.171 | -61.1984 | 61.1847 | -61.1252 | -61.1481 | -61.0977 | -0.07782 | 0.009155 | -0.082397 | 0.21515 | -0.16022 | -0.13733 | -0.082397 | -0.059509 | -0.045776 | -0.018311 | -0.004578 | 0.027466 | 0.054932 | 0.004578 | 0.10071 | 0.050354 | 0.29297 | 122.3373 | 0.073242 | 122.3831 | 122.4289 | 122.3694 | 122.3511 | 122.3236 | -122.4197 | -122.3877 | 122.2595 | 122.3373 | 61.0703 | 61.1114
963 | 122.4747 | -61.1984 | 61.1389 | 0.0059509 | -0.0087116 | 0.0068659 | 0.067456 | -0.01848 | -0.031172 | -0.027305 | 0.0025024 | -0.0076049 | 0.065044 | 0.042161 | -0.018154 | -0.0096728 | -0.016528 | -0.14191 | 61.1298 | -61.3083 | 61.0291 | -61.0336 | -61.4365 | -61.4502 | -0.13275 | 61.0428 | -61.2625 | 61.1343 | -61.2076 | -61.235 | -61.1526 | -0.10986 | -0.009155 | -0.10986 | 0.16479 | -0.25177 | -0.23804 | -0.14191 | -0.12817 | -0.064087 | -0.09613 | -0.004578 | -0.009156 | 0.045776 | -0.036621 | 0.10986 | 0.027466 | 0.27466 | 122.3373 | 0.054931 | 122.3969 | 122.4381 | 122.3053 | 122.3282 | 122.2412 | -122.4472 | -122.4014 | 122.2275 | 122.3328 | 61.0565 | 61.0657
964.7188 | 122.4472 | -61.2076 | 61.116 | 0.01358 | -0.0070026 | 0.011352 | 0.063824 | -0.021471 | -0.030531 | -0.023887 | -0.00054937 | -0.0069641 | 0.063549 | 0.041306 | -0.019008 | -0.010741 | -0.015033 | -0.1236 | 61.1389 | -61.2946 | 61.0382 | -61.0336 | -61.4319 | -61.4502 | -0.15564 | 61.0977 | -61.2167 | 61.0931 | -61.2305 | -61.2671 | -61.1618 | -0.086975 | 0.022888 | -0.07782 | 0.17395 | -0.24261 | -0.2243 | -0.15564 | -0.13733 | -0.009155 | -0.018311 | -0.022888 | -0.022888 | 0.045777 | -0.059509 | 0.054932 | -0.050354 | 0.26093 | 122.3328 | -0.013733 | 122.3099 | 122.4335 | 122.3145 | 122.3465 | 122.3053 | -122.4106 | -122.3328 | 122.2458 | 122.3007 | 61.084 | 61.0519
966.4375 | 122.4747 | -61.1526 | 61.2213 | 0.0059509 | -0.0089252 | 0.011352 | 0.06596 | -0.021044 | -0.030317 | -0.021537 | 0.008606 | -0.0082459 | 0.066112 | 0.038956 | -0.021572 | -0.011809 | -0.016742 | -0.041199 | 61.2213 | -61.2534 | 61.1298 | -60.9329 | -61.3037 | -61.3403 | -0.045776 | 61.1755 | -61.1755 | 61.1847 | -61.1252 | -61.1481 | -61.0748 | -0.10071 | 0 | -0.091552 | 0.21973 | -0.18768 | -0.15106 | -0.086975 | -0.050354 | -0.022888 | -0.045776 | -0.036621 | 0.027466 | 0.07782 | 0.004578 | 0.10071 | 0.027466 | 0.32044 | 122.3831 | 0.050354 | 122.3602 | 122.4747 | 122.3511 | 122.374 | 122.3282 | -122.4747 | -122.3969 | 122.2824 | 122.3373 | 61.1114 | 61.1069
968.1406 | 122.5159 | -61.1572 | 61.1801 | 0.01358 | -0.0087116 | 0.0090021 | 0.066601 | -0.01549 | -0.031813 | -0.024101 | 0.0055542 | -0.0069641 | 0.06419 | 0.037247 | -0.019008 | -0.0098864 | -0.014178 | -0.045776 | 61.1435 | -61.2534 | 61.1389 | -60.9146 | -61.3129 | -61.3312 | 0.018311 | 61.1069 | -61.1847 | 61.235 | -61.0931 | -61.1252 | -61.084 | -0.09613 | -0.036621 | -0.041199 | 0.24262 | -0.17395 | -0.15564 | -0.07782 | -0.059509 | -0.027465 | -0.073242 | 0.054931 | 0.064087 | 0.073243 | 0.032044 | 0.10071 | 0.059509 | 0.33875 | 122.3923 | 0.091552 | 122.4197 | 122.3969 | 122.2916 | 122.3007 | 122.2641 | -122.4335 | -122.3648 | 122.2961 | 122.3923 | 61.1115 | 61.1755
969.8906 | 122.5983 | -61.1893 | 61.0703 | -0.0016786 | -0.006789 | 0.0096429 | 0.062543 | -0.021044 | -0.031813 | -0.021751 | 0.0055542 | -0.0099549 | 0.062481 | 0.048997 | -0.014522 | -0.0068958 | -0.012683 | -0.073242 | 61.0474 | -61.2671 | 61.1481 | -60.9146 | -61.322 | -61.3403 | 0.004578 | 61.0016 | -61.2167 | 61.2305 | -61.0703 | -61.1069 | -61.0519 | -0.07782 | -0.022888 | 0.07782 | 0.27466 | -0.15106 | -0.13275 | -0.073242 | -0.054931 | -0.027466 | -0.068664 | 0.16022 | 0.11902 | 0.13733 | 0.082397 | 0.16479 | 0.10986 | 0.35248 | 122.4152 | 0.14648 | 122.4472 | 122.3145 | 122.2183 | 122.2366 | 122.1909 | -122.3373 | -122.287 | 122.3373 | 122.4197 | 61.116 | 61.1938
971.6094 | 122.5891 | -61.1847 | 61.116 | 0.0059509 | -0.007857 | 0.0085749 | 0.064679 | -0.013781 | -0.030958 | -0.02581 | 0.0055542 | -0.0099549 | 0.061199 | 0.046219 | -0.014949 | -0.0077502 | -0.013751 | -0.10071 | 61.0657 | -61.2762 | 61.1481 | -60.91 | -61.3266 | -61.3586 | 0.004578 | 61.0107 | -61.235 | 61.235 | -61.0657 | -61.1298 | -61.0382 | -0.091553 | -0.050354 | 0.032043 | 0.27466 | -0.17395 | -0.14191 | -0.082398 | -0.050354 | -0.050354 | -0.10529 | 0.11902 | 0.11902 | 0.14648 | 0.054931 | 0.19684 | 0.10528 | 0.36621 | 122.4243 | 0.16937 | 122.4701 | 122.3419 | 122.2458 | 122.2504 | 122.1954 | -122.3923 | -122.3511 | 122.3328 | 122.4197 | 61.084 | 61.1893
973.3125 | 122.5845 | -61.1206 | 61.1481 | 0.02121 | -0.009566 | 0.0090021 | 0.061902 | -0.016985 | -0.031172 | -0.022819 | 0.0025024 | -0.010596 | 0.062053 | 0.049424 | -0.02029 | -0.0094592 | -0.013751 | -0.086975 | 61.1343 | -61.2396 | 61.1572 | -60.8871 | -61.2671 | -61.2854 | 0 | 61.0748 | -61.1664 | 61.2854 | -61.0107 | -61.0428 | -61.0062 | -0.11902 | -0.013733 | 0.009156 | 0.23346 | -0.1648 | -0.14649 | -0.045776 | -0.027466 | -0.045777 | -0.073242 | 0.13733 | 0.10986 | 0.11444 | 0.077819 | 0.16022 | 0.1236 | 0.35248 | 122.3969 | 0.15564 | 122.4518 | 122.374 | 122.2412 | 122.2549 | 122.1954 | -122.3877 | -122.3145 | 122.2778 | 122.406 | 61.0336 | 61.1206
975.0781 | 122.5433 | -61.1572 | 61.1298 | 0.028839 | -0.0059344 | 0.0098565 | 0.062756 | -0.018908 | -0.02754 | -0.022605 | 0.014709 | -0.0088867 | 0.062481 | 0.046647 | -0.019435 | -0.008391 | -0.01546 | -0.082397 | 61.0977 | -61.2854 | 61.1435 | -60.8734 | -61.3129 | -61.3312 | 0.013733 | 61.0428 | -61.1801 | 61.2305 | -61.084 | -61.116 | -61.0794 | -0.12817 | -0.032044 | 0.013733 | 0.28381 | -0.17395 | -0.15564 | -0.045777 | -0.027466 | -0.022888 | -0.086975 | 0.10071 | 0.073243 | 0.07782 | 0.041199 | 0.10071 | 0.064087 | 0.41199 | 122.4289 | 0.096131 | 122.4106 | 122.3831 | 122.2229 | 122.2549 | 122.2 | -122.4152 | -122.3099 | 122.3007 | 122.3877 | 61.0748 | 61.171
976.7969 | 122.4701 | -61.1069 | 61.2076 | 0.0059509 | -0.0080706 | 0.0090021 | 0.064679 | -0.016985 | -0.031385 | -0.027946 | 0.0025024 | -0.0091003 | 0.063976 | 0.042161 | -0.021144 | -0.012023 | -0.013537 | 0 | 61.1389 | -61.203 | 61.1984 | -60.8459 | -61.2305 | -61.2671 | 0.032043 | 61.1298 | -61.1526 | 61.2259 | -61.0657 | -61.0886 | -61.0565 | -0.09613 | -0.068665 | -0.009156 | 0.26093 | -0.16022 | -0.1236 | -0.064087 | -0.027466 | -0.045776 | -0.07782 | 0.01831 | 0.041199 | 0.050354 | 0.018311 | 0.09613 | 0.064087 | 0.35706 | 122.4014 | 0.086975 | 122.3785 | 122.3419 | 122.2824 | 122.2458 | 122.2366 | -122.4106 | -122.3602 | 122.3053 | 122.3328 | 61.1069 | 61.1389
978.5781 | 122.4655 | -61.1893 | 61.1526 | 0.01358 | -0.007857 | 0.011352 | 0.066174 | -0.016558 | -0.030531 | -0.024528 | 0.0055542 | -0.0065369 | 0.063762 | 0.040238 | -0.017726 | -0.010741 | -0.01546 | -0.15106 | 61.1114 | -61.2991 | 61.0336 | -61.0565 | -61.4365 | -61.441 | -0.14191 | 61.0931 | -61.2122 | 61.1206 | -61.203 | -61.2396 | -61.1526 | -0.10986 | -0.041199 | -0.11902 | 0.13275 | -0.25177 | -0.24719 | -0.14191 | -0.13733 | -0.022888 | -0.059509 | -0.032044 | -0.013733 | 0.036621 | -0.050354 | 0.059509 | -0.027466 | 0.24261 | 122.3328 | 0.009155 | 122.3328 | 122.4106 | 122.3053 | 122.3007 | 122.2824 | -122.4518 | -122.3648 | 122.2229 | 122.3099 | 61.0382 | 61.0474
980.2969 | 122.4701 | -61.1206 | 61.2534 | 0.0059509 | -0.0080706 | 0.0087885 | 0.063397 | -0.016985 | -0.028822 | -0.024742 | 0.014709 | -0.0082459 | 0.065685 | 0.04152 | -0.02264 | -0.012236 | -0.013965 | -0.054932 | 61.1893 | -61.2167 | 61.1618 | -60.91 | -61.2854 | -61.3358 | -0.036621 | 61.1847 | -61.171 | 61.1938 | -61.1069 | -61.1343 | -61.0657 | -0.096131 | -0.064087 | -0.091553 | 0.21057 | -0.21515 | -0.1648 | -0.11902 | -0.068664 | -0.050354 | -0.068665 | -0.059509 | 0.013732 | 0.054931 | -0.013733 | 0.10529 | 0.036621 | 0.3067 | 122.3785 | 0.064086 | 122.3648 | 122.406 | 122.3557 | 122.3099 | 122.3053 | -122.4701 | -122.4243 | 122.2824 | 122.3145 | 61.0657 | 61.084
982.0938 | 122.5388 | -61.1435 | 61.1526 | 0.02121 | -0.0089252 | 0.010284 | 0.062329 | -0.019121 | -0.028608 | -0.022819 | 0.0055542 | -0.0099549 | 0.064403 | 0.044938 | -0.019649 | -0.010314 | -0.016742 | -0.082397 | 61.1023 | -61.2442 | 61.1526 | -60.8826 | -61.3037 | -61.3174 | -0.018311 | 61.0519 | -61.1847 | 61.2122 | -61.0977 | -61.116 | -61.0565 | -0.10071 | -0.050354 | 0 | 0.26093 | -0.17395 | -0.16022 | -0.073242 | -0.059509 | -0.041198 | -0.10071 | 0.059509 | 0.045777 | 0.086975 | 0.027466 | 0.12817 | 0.068664 | 0.36163 | 122.3969 | 0.086975 | 122.3969 | 122.3465 | 122.2366 | 122.2458 | 122.1954 | -122.3969 | -122.3373 | 122.2961 | 122.3557 | 61.0611 | 61.1252
983.7969 | 122.5845 | -61.1481 | 61.1114 | -0.0016786 | -0.0074298 | 0.0087885 | 0.064251 | -0.02083 | -0.029676 | -0.024528 | 0.017761 | -0.0080321 | 0.065471 | 0.047928 | -0.018154 | -0.0077502 | -0.018023 | -0.086975 | 61.0748 | -61.2534 | 61.171 | -60.8551 | -61.3129 | -61.3174 | 0.022888 | 61.0336 | -61.2167 | 61.2579 | -61.0565 | -61.0886 | -61.0565 | -0.10529 | -0.036621 | 0.059509 | 0.29297 | -0.16937 | -0.16479 | -0.064087 | -0.059509 | -0.068665 | -0.07782 | 0.14649 | 0.091552 | 0.091552 | 0.059509 | 0.16022 | 0.12817 | 0.39825 | 122.4243 | 0.16022 | 122.4747 | 122.3282 | 122.2504 | 122.2229 | 122.1817 | -122.3648 | -122.3282 | 122.319 | 122.406 | 61.0611 | 61.171
985.5625 | 122.4838 | -61.1847 | 61.1481 | 0.0059509 | -0.0076434 | 0.0077203 | 0.06532 | -0.01549 | -0.031599 | -0.024528 | 0.0025024 | -0.0071777 | 0.063549 | 0.04921 | -0.019649 | -0.0086048 | -0.013751 | -0.14648 | 61.1114 | -61.2717 | 61.0428 | -61.0199 | -61.4044 | -61.4273 | -0.13733 | 61.0931 | -61.2259 | 61.1572 | -61.1847 | -61.2076 | -61.1298 | -0.086975 | -0.036621 | -0.10529 | 0.16479 | -0.24262 | -0.21973 | -0.15564 | -0.13275 | -0.041199 | -0.054931 | 0.009156 | 0 | 0.054931 | -0.022889 | 0.09613 | 0.01831 | 0.25177 | 122.3145 | 0.041199 | 122.3831 | 122.3831 | 122.319 | 122.2961 | 122.2778 | -122.4197 | -122.374 | 122.2275 | 122.3419 | 61.0382 | 61.0474
987.2812 | 122.5113 | -61.1618 | 61.0977 | 0.0059509 | -0.0093524 | 0.0094293 | 0.06831 | -0.017199 | -0.031599 | -0.025383 | 0.0025024 | -0.0069641 | 0.063335 | 0.047288 | -0.017726 | -0.0094592 | -0.016955 | -0.15106 | 61.1252 | -61.2991 | 61.0657 | -61.0062 | -61.3953 | -61.4044 | -0.10529 | 61.084 | -61.2396 | 61.1664 | -61.1343 | -61.1893 | -61.1023 | -0.13733 | 0.027466 | -0.032043 | 0.15564 | -0.24262 | -0.23346 | -0.10529 | -0.096131 | -0.07782 | -0.013733 | 0.068665 | 0.027466 | 0.059509 | -0.027466 | 0.13733 | 0.050354 | 0.29297 | 122.3648 | 0.10529 | 122.406 | 122.4243 | 122.3236 | 122.287 | 122.2458 | -122.3969 | -122.3373 | 122.2275 | 122.3282 | 61.0107 | 61.0565
988.9844 | 122.5571 | -61.1343 | 61.1572 | 0.02121 | -0.0070026 | 0.010711 | 0.064251 | -0.019976 | -0.028608 | -0.020897 | 0.011658 | -0.0069641 | 0.065685 | 0.047715 | -0.019008 | -0.011809 | -0.013965 | -0.073242 | 61.084 | -61.2717 | 61.1664 | -60.8688 | -61.2946 | -61.2991 | 0.013733 | 61.0474 | -61.1938 | 61.235 | -61.0748 | -61.1069 | -61.0519 | -0.13733 | -0.073243 | 0.009155 | 0.2655 | -0.16479 | -0.16022 | -0.027466 | -0.022889 | -0.05951 | -0.10986 | 0.077819 | 0.059509 | 0.082397 | 0.027465 | 0.14191 | 0.086975 | 0.40283 | 122.438 | 0.11902 | 122.4289 | 122.3557 | 122.2412 | 122.2183 | 122.1817 | -122.4289 | -122.3511 | 122.3007 | 122.3694 | 61.0611 | 61.1481
990.75 | 122.5296 | -61.1435 | 61.171 | 0.02121 | -0.0082842 | 0.0090021 | 0.062543 | -0.021258 | -0.028822 | -0.024314 | 0.0055542 | -0.0095275 | 0.066753 | 0.045365 | -0.020931 | -0.006682 | -0.014605 | -0.091553 | 61.1343 | -61.2305 | 61.1435 | -60.8963 | -61.2991 | -61.3129 | -0.041199 | 61.0977 | -61.1664 | 61.235 | -61.0565 | -61.084 | -61.0291 | -0.086975 | -0.036621 | -0.027465 | 0.24719 | -0.16937 | -0.15564 | -0.082397 | -0.068664 | -0.022888 | -0.073242 | 0.064087 | 0.086975 | 0.11444 | 0.05951 | 0.13733 | 0.082398 | 0.33417 | 122.374 | 0.10986 | 122.4014 | 122.3648 | 122.2641 | 122.2778 | 122.2412 | -122.4014 | -122.3373 | 122.287 | 122.3785 | 61.0519 | 61.1023
992.4688 | 122.4747 | -61.1298 | 61.235 | 0.028839 | -0.0074298 | 0.0085749 | 0.065747 | -0.019549 | -0.029676 | -0.022392 | 0.011658 | -0.0056823 | 0.063121 | 0.046647 | -0.021785 | -0.009032 | -0.015246 | -0.041199 | 61.2122 | -61.2396 | 61.1526 | -60.9146 | -61.2808 | -61.3129 | -0.036621 | 61.171 | -61.1572 | 61.2259 | -61.0794 | -61.1023 | -61.0245 | -0.10986 | -0.022888 | -0.082397 | 0.21515 | -0.1831 | -0.15106 | -0.073242 | -0.041199 | -0.027466 | -0.064087 | -0.009155 | 0.050354 | 0.10529 | 0.027466 | 0.13275 | 0.054932 | 0.32501 | 122.3923 | 0.07782 | 122.3831 | 122.4518 | 122.3282 | 122.3419 | 122.3007 | -122.4747 | -122.3923 | 122.2824 | 122.3557 | 61.0886 | 61.0931
994.1875 | 122.5342 | -61.1114 | 61.1801 | 0.028839 | -0.009566 | 0.0098565 | 0.06532 | -0.021044 | -0.03224 | -0.021324 | 0.0055542 | -0.0086731 | 0.062908 | 0.052628 | -0.019649 | -0.010314 | -0.018237 | -0.10071 | 61.1114 | -61.2213 | 61.1755 | -60.8551 | -61.29 | -61.2991 | -0.032043 | 61.0748 | -61.1664 | 61.2305 | -61.0748 | -61.0931 | -61.0291 | -0.10986 | -0.068665 | -0.004578 | 0.25635 | -0.18768 | -0.17853 | -0.07782 | -0.068665 | -0.054932 | -0.10529 | 0.050354 | 0.036621 | 0.082397 | 0.01831 | 0.13733 | 0.073242 | 0.36621 | 122.3969 | 0.091553 | 122.3969 | 122.3328 | 122.2412 | 122.2229 | 122.1863 | -122.4014 | -122.3465 | 122.287 | 122.3419 | 61.0107 | 61.0794
995.9531 | 122.58 | -61.1343 | 61.1114 | 0.01358 | -0.0063616 | 0.0087885 | 0.066388 | -0.014635 | -0.027754 | -0.02581 | 0.014709 | -0.0073913 | 0.065044 | 0.048142 | -0.017513 | -0.009032 | -0.017596 | -0.082397 | 61.0748 | -61.2488 | 61.2076 | -60.8414 | -61.2808 | -61.29 | 0.032043 | 61.0336 | -61.2167 | 61.2671 | -61.0336 | -61.084 | -61.0245 | -0.11444 | -0.036621 | 0.096131 | 0.29297 | -0.15564 | -0.14648 | -0.041199 | -0.032044 | -0.082398 | -0.07782 | 0.15564 | 0.10071 | 0.10986 | 0.050354 | 0.19226 | 0.13275 | 0.40741 | 122.4564 | 0.18311 | 122.4838 | 122.3236 | 122.2504 | 122.2092 | 122.168 | -122.3602 | -122.3282 | 122.3419 | 122.4014 | 61.0519 | 61.1664
997.7188 | 122.5342 | -61.1481 | 61.116 | 0.044098 | -0.0059344 | 0.011566 | 0.066174 | -0.019762 | -0.031599 | -0.022178 | 0.0055542 | -0.0078185 | 0.062694 | 0.045579 | -0.018367 | -0.008391 | -0.015033 | -0.068665 | 61.116 | -61.2579 | 61.1984 | -60.8322 | -61.2488 | -61.29 | 0.041199 | 61.0611 | -61.1893 | 61.2579 | -61.0336 | -61.0886 | -61.0474 | -0.10986 | 0 | 0.082397 | 0.31586 | -0.14191 | -0.10071 | -0.032043 | 0.009156 | -0.041199 | -0.054932 | 0.14191 | 0.11444 | 0.10071 | 0.059509 | 0.14191 | 0.10071 | 0.42572 | 122.4564 | 0.15564 | 122.4472 | 122.374 | 122.2504 | 122.2641 | 122.2092 | -122.374 | -122.3053 | 122.3465 | 122.406 | 61.0794 | 61.1893
999.4844 | 122.4243 | -61.171 | 61.1618 | 0.0059509 | -0.0059344 | 0.011138 | 0.064892 | -0.023607 | -0.029676 | -0.02346 | -0.00054937 | -0.0063233 | 0.063335 | 0.046433 | -0.019649 | -0.0088184 | -0.016528 | -0.12817 | 61.1572 | -61.2625 | 61.0931 | -61.0062 | -61.3861 | -61.409 | -0.15106 | 61.0977 | -61.1984 | 61.1389 | -61.1801 | -61.2259 | -61.1389 | -0.091553 | -0.004577 | -0.068664 | 0.16479 | -0.23804 | -0.21515 | -0.14648 | -0.1236 | -0.027466 | -0.064087 | -0.022888 | -0.009156 | 0.032043 | -0.054932 | 0.059509 | -0.027466 | 0.25635 | 122.3557 | 0.01831 | 122.3373 | 122.4197 | 122.2961 | 122.3282 | 122.2687 | -122.4243 | -122.3602 | 122.2641 | 122.3099 | 61.0428 | 61.0199
1001.2188 | 122.4335 | -61.1114 | 61.2488 | -0.0016786 | -0.007857 | 0.0072931 | 0.064465 | -0.01784 | -0.031385 | -0.025169 | 0.0025024 | -0.0088867 | 0.065044 | 0.044938 | -0.024562 | -0.010527 | -0.012683 | -0.068665 | 61.1755 | -61.1801 | 61.1618 | -60.8643 | -61.2671 | -61.2946 | -0.036621 | 61.203 | -61.1435 | 61.2076 | -61.0703 | -61.0886 | -61.0382 | -0.068665 | -0.073242 | -0.086975 | 0.24719 | -0.18311 | -0.15564 | -0.11444 | -0.086975 | -0.032044 | -0.045776 | -0.041198 | 0.041199 | 0.073242 | 0.022888 | 0.10529 | 0.054932 | 0.31586 | 122.3419 | 0.073243 | 122.3511 | 122.3557 | 122.3465 | 122.287 | 122.3145 | -122.4289 | -122.3923 | 122.2733 | 122.319 | 61.0428 | 61.0748
1002.9844 | 122.5204 | -61.1114 | 61.1572 | 0.01358 | -0.0099932 | 0.011352 | 0.06297 | -0.02318 | -0.030317 | -0.023033 | 0.0055542 | -0.0071777 | 0.062481 | 0.048783 | -0.020076 | -0.011168 | -0.016955 | -0.10529 | 61.1526 | -61.2167 | 61.1755 | -60.8643 | -61.2625 | -61.3037 | -0.054932 | 61.1114 | -61.1664 | 61.2488 | -61.0291 | -61.0565 | -61.0062 | -0.10529 | -0.004578 | 0.01831 | 0.24719 | -0.19226 | -0.15106 | -0.086975 | -0.045776 | -0.054932 | -0.045777 | 0.091552 | 0.082397 | 0.10528 | 0.054931 | 0.16022 | 0.10986 | 0.35248 | 122.3923 | 0.13733 | 122.4152 | 122.3694 | 122.2778 | 122.2641 | 122.2229 | -122.374 | -122.3236 | 122.287 | 122.3602 | 61.0062 | 61.0565
1004.7656 | 122.5708 | -61.1298 | 61.116 | 0.0059509 | -0.0063616 | 0.0094293 | 0.064679 | -0.019976 | -0.029676 | -0.02346 | -0.003601 | -0.0073913 | 0.063121 | 0.047501 | -0.019649 | -0.0092456 | -0.01311 | -0.13733 | 61.1206 | -61.2534 | 61.1618 | -60.8917 | -61.3174 | -61.3312 | -0.032043 | 61.0474 | -61.1847 | 61.2534 | -61.0382 | -61.084 | -60.997 | -0.1236 | 0.004577 | 0.045776 | 0.23804 | -0.20142 | -0.18768 | -0.07782 | -0.064087 | -0.054931 | -0.068665 | 0.13733 | 0.091553 | 0.13275 | 0.045777 | 0.18768 | 0.10071 | 0.36163 | 122.4152 | 0.14648 | 122.438 | 122.374 | 122.2321 | 122.2504 | 122.1771 | -122.3694 | -122.3007 | 122.2916 | 122.3831 | 60.9924 | 61.0977
1006.5312 | 122.4472 | -61.1664 | 61.1618 | 0.0059509 | -0.006789 | 0.0090021 | 0.066388 | -0.020403 | -0.027967 | -0.023887 | -0.00054937 | -0.0086731 | 0.062481 | 0.042801 | -0.020076 | -0.0096728 | -0.01546 | -0.13733 | 61.1572 | -61.2305 | 61.0748 | -61.0107 | -61.3953 | -61.4273 | -0.13733 | 61.1114 | -61.2122 | 61.1618 | -61.1572 | -61.2076 | -61.1069 | -0.064087 | -0.004577 | -0.086975 | 0.15564 | -0.26093 | -0.22888 | -0.19684 | -0.16479 | -0.045776 | -0.050354 | 0 | 0.009155 | 0.059509 | -0.041199 | 0.10529 | 0.004577 | 0.21973 | 122.3053 | 0.054931 | 122.374 | 122.3877 | 122.3236 | 122.3236 | 122.2778 | -122.3923 | -122.374 | 122.2412 | 122.3282 | 61.0291 | 61.0291
1008.3281 | 122.4426 | -61.1435 | 61.2122 | 0.02121 | -0.0072162 | 0.011138 | 0.067242 | -0.025103 | -0.029249 | -0.024101 | 0.0055542 | -0.0056823 | 0.063335 | 0.042374 | -0.019863 | -0.010314 | -0.017383 | -0.15106 | 61.1664 | -61.2488 | 61.0519 | -61.0107 | -61.377 | -61.3861 | -0.15106 | 61.1206 | -61.1755 | 61.1526 | -61.1526 | -61.1984 | -61.0977 | -0.10529 | -0.045776 | -0.16022 | 0.13275 | -0.24261 | -0.23346 | -0.13733 | -0.12817 | -0.032043 | -0.091553 | -0.059509 | -0.009155 | 0.045777 | -0.054931 | 0.07782 | -0.022888 | 0.23804 | 122.3007 | 0.022888 | 122.3282 | 122.4152 | 122.2961 | 122.3099 | 122.2641 | -122.4609 | -122.3877 | 122.1954 | 122.2961 | 60.9924 | 60.9924
1010.0469 | 122.5754 | -61.0519 | 61.203 | 0.01358 | -0.010421 | 0.0087885 | 0.061047 | -0.021685 | -0.030958 | -0.024742 | 0.0025024 | -0.0095275 | 0.06483 | 0.047928 | -0.020076 | -0.011168 | -0.016742 | -0.036621 | 61.1389 | -61.1618 | 61.3083 | -60.6903 | -61.1252 | -61.1664 | 0.086975 | 61.116 | -61.1069 | 61.3403 | -60.9146 | -60.9375 | -60.9283 | -0.10986 | -0.064087 | 0.10529 | 0.36163 | -0.11444 | -0.073242 | -0.004578 | 0.036621 | -0.054932 | -0.086975 | 0.13733 | 0.13733 | 0.1236 | 0.11444 | 0.17853 | 0.16937 | 0.4715 | 122.4701 | 0.19226 | 122.4472 | 122.3007 | 122.2229 | 122.1909 | 122.168 | -122.3648 | -122.3099 | 122.3602 | 122.3923 | 61.0153 | 61.1389
1011.8125 | 122.438 | -61.0931 | 61.2534 | 0.0059509 | -0.0089252 | 0.0094293 | 0.064465 | -0.019549 | -0.029036 | -0.024955 | 0.014709 | -0.0067505 | 0.06419 | 0.045365 | -0.023494 | -0.0096728 | -0.016955 | -0.068665 | 61.2076 | -61.1664 | 61.203 | -60.8505 | -61.2213 | -61.2579 | -0.018311 | 61.1984 | -61.116 | 61.235 | -61.0474 | -61.0794 | -61.0062 | -0.073242 | -0.045776 | -0.050354 | 0.24262 | -0.1648 | -0.12817 | -0.091553 | -0.054931 | -0.022888 | -0.054932 | -0.018311 | 0.045777 | 0.086975 | 0.013733 | 0.10986 | 0.036621 | 0.31586 | 122.3694 | 0.068665 | 122.3511 | 122.374 | 122.3145 | 122.3007 | 122.2916 | -122.4197 | -122.3694 | 122.2961 | 122.3282 | 61.0245 | 61.0748
1013.5312 | 122.4884 | -61.0977 | 61.235 | 0.028839 | -0.004439 | 0.0090021 | 0.064679 | -0.019976 | -0.029249 | -0.024955 | 0.0055542 | -0.0076049 | 0.064617 | 0.03682 | -0.020931 | -0.010527 | -0.013751 | -0.041199 | 61.1984 | -61.1618 | 61.2122 | -60.8459 | -61.235 | -61.2717 | 0.013733 | 61.1572 | -61.1343 | 61.2854 | -61.0107 | -61.0611 | -60.9924 | -0.064087 | -0.036621 | -0.022888 | 0.25177 | -0.17395 | -0.13733 | -0.10986 | -0.073242 | -0.036621 | -0.077819 | 0.050354 | 0.086975 | 0.10529 | 0.036621 | 0.14191 | 0.073242 | 0.31586 | 122.374 | 0.1236 | 122.4197 | 122.3602 | 122.2916 | 122.2961 | 122.2549 | -122.3969 | -122.3694 | 122.3099 | 122.3831 | 61.0565 | 61.1115
1015.25 | 122.4426 | -61.0748 | 61.2717 | 0.0059509 | -0.009566 | 0.0098565 | 0.064679 | -0.021044 | -0.029676 | -0.021751 | -0.00054937 | -0.0063233 | 0.06483 | 0.040238 | -0.02264 | -0.010955 | -0.01311 | -0.036621 | 61.2305 | -61.1435 | 61.2259 | -60.8002 | -61.1847 | -61.2213 | -0.013733 | 61.1847 | -61.0748 | 61.2488 | -61.0245 | -61.0611 | -61.0062 | -0.068665 | -0.041198 | -0.045776 | 0.27466 | -0.14648 | -0.10986 | -0.077819 | -0.041198 | 0 | -0.086975 | -0.022888 | 0.050354 | 0.068664 | 0.013733 | 0.068664 | 0.013733 | 0.34332 | 122.3694 | 0.050354 | 122.3236 | 122.374 | 122.2595 | 122.3053 | 122.2595 | -122.4152 | -122.3465 | 122.3007 | 122.3236 | 61.0382 | 61.0611
1017.0312 | 122.4426 | -61.116 | 61.1938 | 0.0059509 | -0.0076434 | 0.0098565 | 0.066815 | -0.01549 | -0.030317 | -0.023887 | -0.00054937 | -0.0063233 | 0.064403 | 0.043442 | -0.019435 | -0.0094592 | -0.016742 | -0.07782 | 61.1984 | -61.1938 | 61.1755 | -60.8688 | -61.2854 | -61.3037 | -0.054932 | 61.1435 | -61.1481 | 61.2122 | -61.0886 | -61.1343 | -61.0565 | -0.07782 | 0.004577 | -0.018311 | 0.24719 | -0.18768 | -0.16937 | -0.10986 | -0.091552 | -0.032043 | -0.050354 | 0.01831 | 0.027466 | 0.059509 | -0.01831 | 0.091552 | 0.013733 | 0.32501 | 122.3694 | 0.059509 | 122.3602 | 122.3923 | 122.2916 | 122.3145 | 122.2595 | -122.3877 | -122.3419 | 122.2916 | 122.3282 | 61.0382 | 61.0611
1018.8125 | 122.4884 | -61.0931 | 61.235 | 0.02121 | -0.008498 | 0.0087885 | 0.06532 | -0.017412 | -0.031172 | -0.023887 | 0.011658 | -0.0078185 | 0.063762 | 0.040024 | -0.020717 | -0.011168 | -0.01781 | -0.059509 | 61.2396 | -61.1755 | 61.2167 | -60.8505 | -61.203 | -61.235 | -0.018311 | 61.1984 | -61.0886 | 61.2579 | -61.0016 | -61.0474 | -60.9833 | -0.082397 | 0.004578 | -0.01831 | 0.24262 | -0.14191 | -0.10986 | -0.059509 | -0.027466 | 0.004578 | -0.036621 | 0.022889 | 0.091553 | 0.10986 | 0.045777 | 0.10529 | 0.041199 | 0.32501 | 122.3923 | 0.086975 | 122.3465 | 122.4152 | 122.287 | 122.3328 | 122.2916 | -122.4106 | -122.3236 | 122.3099 | 122.3511 | 61.0336 | 61.0748
1020.5469 | 122.438 | -61.0565 | 61.3037 | -0.0016786 | -0.0072162 | 0.010925 | 0.063611 | -0.019335 | -0.028822 | -0.023674 | 0.0055542 | -0.0073913 | 0.065685 | 0.04686 | -0.019649 | -0.011809 | -0.016955 | -0.045776 | 61.235 | -61.1343 | 61.2122 | -60.8185 | -61.203 | -61.2213 | -0.013733 | 61.1984 | -61.0703 | 61.2442 | -61.0107 | -61.0428 | -60.9879 | -0.077819 | -0.068665 | -0.091553 | 0.23804 | -0.16479 | -0.14648 | -0.086975 | -0.068665 | -0.013732 | -0.10529 | -0.059509 | 0.045777 | 0.068665 | 0.013733 | 0.082397 | 0.027465 | 0.31586 | 122.3465 | 0.059509 | 122.3145 | 122.3694 | 122.2687 | 122.2916 | 122.2549 | -122.438 | -122.374 | 122.2687 | 122.3007 | 61.0107 | 61.0428
1022.2812 | 122.4609 | -61.0657 | 61.2762 | 0.044098 | -0.0046526 | 0.0083613 | 0.065533 | -0.020403 | -0.028395 | -0.023887 | 0.008606 | -0.0056823 | 0.063976 | 0.047501 | -0.021785 | -0.010527 | -0.020587 | -0.068665 | 61.2579 | -61.1343 | 61.1984 | -60.8688 | -61.2213 | -61.2579 | -0.027466 | 61.1755 | -61.1069 | 61.2579 | -61.0062 | -61.0428 | -60.9695 | -0.068664 | -0.01831 | -0.07782 | 0.19684 | -0.19226 | -0.15564 | -0.1236 | -0.086975 | -0.041199 | -0.10071 | -0.01831 | 0.059509 | 0.096131 | 0.022888 | 0.13733 | 0.064087 | 0.2655 | 122.3328 | 0.10071 | 122.3648 | 122.3923 | 122.2824 | 122.3236 | 122.2412 | -122.4106 | -122.3831 | 122.2641 | 122.3236 | 60.997 | 61.0382
1024.0625 | 122.525 | -61.084 | 61.1847 | 0.028839 | -0.0074298 | 0.01007 | 0.064892 | -0.01848 | -0.028608 | -0.023887 | 0.0025024 | -0.0076049 | 0.065258 | 0.038529 | -0.018581 | -0.0079638 | -0.016742 | -0.10071 | 61.1435 | -61.171 | 61.235 | -60.7819 | -61.1893 | -61.2305 | 0.009155 | 61.084 | -61.1526 | 61.2946 | -60.9879 | -61.0291 | -60.9787 | -0.086975 | -0.041198 | 0.050354 | 0.30212 | -0.14648 | -0.10529 | -0.05951 | -0.018311 | -0.068665 | -0.10071 | 0.10986 | 0.09613 | 0.10529 | 0.054931 | 0.17395 | 0.1236 | 0.3891 | 122.406 | 0.16479 | 122.4472 | 122.3145 | 122.2366 | 122.2275 | 122.168 | -122.3557 | -122.3373 | 122.319 | 122.3785 | 60.9833 | 61.0931
1025.8438 | 122.5845 | -61.0107 | 61.235 | 0.01358 | -0.0076434 | 0.0075067 | 0.064679 | -0.019549 | -0.033094 | -0.02346 | 0.0025024 | -0.0099549 | 0.062053 | 0.050492 | -0.019649 | -0.011595 | -0.013751 | -0.050354 | 61.1755 | -61.1389 | 61.3037 | -60.6903 | -61.1069 | -61.1435 | 0.11902 | 61.1664 | -61.0428 | 61.377 | -60.878 | -60.91 | -60.9009 | -0.12817 | -0.059509 | 0.068665 | 0.32043 | -0.13275 | -0.096131 | -0.004578 | 0.032043 | -0.032044 | -0.068664 | 0.14191 | 0.13275 | 0.10986 | 0.10071 | 0.14191 | 0.13275 | 0.44861 | 122.4426 | 0.16479 | 122.4197 | 122.3145 | 122.2092 | 122.1863 | 122.1771 | -122.374 | -122.2778 | 122.3145 | 122.3877 | 60.9604 | 61.1298
1027.6406 | 122.438 | -61.0291 | 61.2717 | 0.036468 | -0.0070026 | 0.0098565 | 0.067242 | -0.022326 | -0.02989 | -0.021537 | 0.011658 | -0.0065369 | 0.063335 | 0.042801 | -0.022212 | -0.011595 | -0.016742 | -0.050354 | 61.2671 | -61.1526 | 61.2122 | -60.8505 | -61.1893 | -61.2534 | -0.041199 | 61.2213 | -61.0977 | 61.2625 | -61.0291 | -61.0474 | -60.9741 | -0.1236 | -0.004577 | -0.059509 | 0.17853 | -0.2243 | -0.16022 | -0.10071 | -0.036621 | -0.068664 | -0.050354 | -0.009155 | 0 | 0.054932 | -0.01831 | 0.1236 | 0.050354 | 0.30212 | 122.3648 | 0.068664 | 122.3602 | 122.4197 | 122.319 | 122.2961 | 122.2504 | -122.4243 | -122.3694 | 122.2412 | 122.2916 | 60.9787 | 60.9879
1029.3438 | 122.5754 | -61.0199 | 61.2625 | 0.0059509 | -0.0080706 | 0.0098565 | 0.064038 | -0.02318 | -0.030104 | -0.025383 | 0.0055542 | -0.0097411 | 0.06483 | 0.042161 | -0.019649 | -0.0096728 | -0.014605 | -0.032043 | 61.1893 | -61.0931 | 61.3266 | -60.6812 | -61.0794 | -61.1298 | 0.10986 | 61.1618 | -61.0611 | 61.377 | -60.8643 | -60.9055 | -60.8734 | -0.073243 | -0.073242 | 0.064087 | 0.33875 | -0.10986 | -0.05951 | -0.036621 | 0.013733 | -0.041199 | -0.10071 | 0.11444 | 0.15564 | 0.14648 | 0.11444 | 0.18768 | 0.15564 | 0.41199 | 122.4197 | 0.19684 | 122.438 | 122.2824 | 122.2229 | 122.2092 | 122.1817 | -122.3557 | -122.3236 | 122.3465 | 122.3969 | 60.9879 | 61.1298
1031.125 | 122.4426 | -61.1114 | 61.2076 | 0.01358 | -0.0055072 | 0.0092157 | 0.066388 | -0.017412 | -0.029676 | -0.023033 | 0.0025024 | -0.0061095 | 0.066326 | 0.038102 | -0.018154 | -0.0096728 | -0.016101 | -0.14648 | 61.203 | -61.1984 | 61.1069 | -60.9329 | -61.3403 | -61.3495 | -0.11902 | 61.1755 | -61.1343 | 61.2076 | -61.0977 | -61.1252 | -61.0291 | -0.086975 | -0.004578 | -0.10071 | 0.17853 | -0.23804 | -0.22888 | -0.15106 | -0.14191 | -0.022888 | -0.032044 | 0 | 0.013733 | 0.082397 | -0.013733 | 0.10529 | 0.009155 | 0.2655 | 122.3053 | 0.036621 | 122.3419 | 122.4014 | 122.3099 | 122.3145 | 122.287 | -122.406 | -122.3419 | 122.2183 | 122.319 | 60.965 | 60.9924
1032.8438 | 122.5571 | -60.9741 | 61.2671 | -0.0093076 | -0.0087116 | 0.01007 | 0.064251 | -0.021898 | -0.031172 | -0.019615 | 0.0025024 | -0.0093139 | 0.060558 | 0.04921 | -0.018794 | -0.0098864 | -0.016528 | -0.022888 | 61.1755 | -61.1023 | 61.3312 | -60.6766 | -61.0703 | -61.1252 | 0.10529 | 61.171 | -61.0336 | 61.3678 | -60.8505 | -60.8963 | -60.8688 | -0.12817 | -0.091553 | 0.064087 | 0.29755 | -0.15106 | -0.09613 | -0.022888 | 0.032044 | -0.059509 | -0.096131 | 0.10071 | 0.1236 | 0.10529 | 0.07782 | 0.1648 | 0.13733 | 0.42572 | 122.4335 | 0.18311 | 122.4014 | 122.2778 | 122.2046 | 122.1497 | 122.1451 | -122.3694 | -122.3007 | 122.3053 | 122.3419 | 60.9512 | 61.0794
1034.625 | 122.4701 | -61.0703 | 61.2488 | 0.02121 | -0.007857 | 0.01007 | 0.064251 | -0.01784 | -0.027754 | -0.022819 | 0.0055542 | -0.0061095 | 0.062053 | 0.044297 | -0.021358 | -0.0101 | -0.01546 | -0.045776 | 61.2625 | -61.1435 | 61.235 | -60.791 | -61.1938 | -61.235 | 0.018311 | 61.171 | -61.084 | 61.2991 | -60.9879 | -61.0428 | -60.9558 | -0.073243 | 0.013733 | -0.013733 | 0.27923 | -0.16479 | -0.1236 | -0.091552 | -0.050354 | -0.013733 | -0.07782 | 0.050354 | 0.082397 | 0.11444 | 0.027465 | 0.12817 | 0.041198 | 0.35248 | 122.3785 | 0.09613 | 122.3831 | 122.406 | 122.2549 | 122.3328 | 122.2412 | -122.3923 | -122.3328 | 122.3053 | 122.3694 | 61.0245 | 61.0886
1036.3438 | 122.4701 | -61.0611 | 61.2762 | 0.028839 | -0.0052936 | 0.0083613 | 0.064892 | -0.017412 | -0.028395 | -0.022605 | -0.00054937 | -0.0041869 | 0.063549 | 0.042374 | -0.020931 | -0.0092456 | -0.01076 | -0.073242 | 61.2488 | -61.1252 | 61.235 | -60.7864 | -61.1938 | -61.2122 | 0.022888 | 61.1755 | -61.0748 | 61.2946 | -60.9787 | -61.0336 | -60.965 | -0.064087 | -0.027466 | -0.041199 | 0.27466 | -0.15106 | -0.13275 | -0.086975 | -0.068665 | -0.013733 | -0.10071 | 0.018311 | 0.082397 | 0.09613 | 0.027466 | 0.10986 | 0.041199 | 0.33875 | 122.3602 | 0.09613 | 122.3694 | 122.374 | 122.2504 | 122.3099 | 122.2366 | -122.4014 | -122.3511 | 122.2961 | 122.3557 | 60.9879 | 61.084
1038.125 | 122.4976 | -61.0153 | 61.2671 | 0.036468 | -0.0063616 | 0.0098565 | 0.064465 | -0.01314 | -0.027327 | -0.025169 | 0.011658 | -0.0054687 | 0.063762 | 0.035538 | -0.020503 | -0.009032 | -0.014819 | -0.041199 | 61.2534 | -61.1343 | 61.2305 | -60.7773 | -61.1801 | -61.2167 | 0.022888 | 61.2076 | -61.0886 | 61.2991 | -60.9604 | -61.0062 | -60.9375 | -0.11902 | -0.013733 | -0.036621 | 0.23804 | -0.20142 | -0.16479 | -0.082398 | -0.045777 | -0.073242 | -0.059509 | 0.032043 | 0.054932 | 0.07782 | 0.009155 | 0.15106 | 0.082397 | 0.35706 | 122.3648 | 0.12817 | 122.3877 | 122.3877 | 122.2961 | 122.2687 | 122.2229 | -122.4014 | -122.3557 | 122.2458 | 122.3145 | 60.9741 | 61.0382
1039.9062 | 122.5571 | -61.0657 | 61.1664 | 0.059357 | -0.0076434 | 0.01242 | 0.064679 | -0.019976 | -0.028608 | -0.022819 | 0.014709 | -0.0082459 | 0.066753 | 0.051346 | -0.018154 | -0.0088184 | -0.013751 | -0.086975 | 61.1572 | -61.1435 | 61.2717 | -60.7452 | -61.1755 | -61.203 | 0.032043 | 61.0886 | -61.1114 | 61.3312 | -60.9421 | -60.9695 | -60.9192 | -0.07782 | -0.009155 | 0.10529 | 0.32044 | -0.13733 | -0.10986 | -0.059509 | -0.032043 | -0.045776 | -0.07782 | 0.16479 | 0.1236 | 0.14648 | 0.096131 | 0.19226 | 0.14191 | 0.39825 | 122.4152 | 0.16937 | 122.4426 | 122.3007 | 122.2 | 122.2229 | 122.1542 | -122.3099 | -122.2778 | 122.3373 | 122.3969 | 60.9787 | 61.0977
1041.6875 | 122.5525 | -61.0336 | 61.1893 | -0.0016786 | -0.009566 | 0.010711 | 0.064892 | -0.016131 | -0.029676 | -0.02346 | 0.0055542 | -0.010596 | 0.065044 | 0.045365 | -0.016017 | -0.0062548 | -0.012042 | -0.10071 | 61.1664 | -61.1572 | 61.2488 | -60.7864 | -61.2076 | -61.2213 | 0.027466 | 61.1114 | -61.084 | 61.3403 | -60.9421 | -60.9833 | -60.9192 | -0.1236 | -0.022888 | 0.059509 | 0.24719 | -0.18768 | -0.17395 | -0.064086 | -0.050354 | -0.050354 | -0.07782 | 0.15106 | 0.091552 | 0.11444 | 0.050354 | 0.16479 | 0.10071 | 0.37079 | 122.406 | 0.14191 | 122.4243 | 122.3236 | 122.1954 | 122.2 | 122.1451 | -122.3465 | -122.2733 | 122.2824 | 122.374 | 60.9329 | 61.0611
1043.4688 | 122.4243 | -61.1023 | 61.2305 | -0.0016786 | -0.0037982 | 0.01007 | 0.06596 | -0.020617 | -0.031172 | -0.026023 | 0.0025024 | -0.0071777 | 0.066539 | 0.039811 | -0.019222 | -0.0101 | -0.014605 | -0.15106 | 61.235 | -61.1664 | 61.1252 | -60.9238 | -61.3037 | -61.3266 | -0.14648 | 61.1526 | -61.0886 | 61.235 | -61.0794 | -61.1069 | -61.0016 | -0.064087 | 0.004577 | -0.10529 | 0.17853 | -0.2243 | -0.20142 | -0.16022 | -0.13733 | 0.013733 | -0.07782 | 0.004577 | 0.022888 | 0.10071 | -0.004578 | 0.086975 | -0.018311 | 0.24262 | 122.2916 | 0.009155 | 122.3236 | 122.4014 | 122.2412 | 122.3373 | 122.2549 | -122.3969 | -122.319 | 122.2275 | 122.3373 | 60.9512 | 60.9558
1045.1875 | 122.4518 | -61.0474 | 61.2625 | 0.02121 | -0.006789 | 0.0096429 | 0.06831 | -0.024462 | -0.030317 | -0.022819 | -0.00054937 | -0.0091003 | 0.065899 | 0.042161 | -0.020717 | -0.0081774 | -0.012042 | -0.086975 | 61.2762 | -61.1252 | 61.2213 | -60.8002 | -61.2213 | -61.2442 | -0.045776 | 61.1984 | -61.0657 | 61.2534 | -61.0199 | -61.0794 | -60.9924 | -0.07782 | 0.013733 | -0.041199 | 0.24719 | -0.19684 | -0.17395 | -0.11902 | -0.09613 | -0.018311 | -0.064087 | -0.009155 | 0.027466 | 0.054931 | -0.032044 | 0.073242 | -0.013733 | 0.32501 | 122.3465 | 0.045777 | 122.319 | 122.4014 | 122.2641 | 122.3236 | 122.2458 | -122.3877 | -122.3282 | 122.2687 | 122.3007 | 60.9604 | 61.0016
1046.9688 | 122.5067 | -61.0382 | 61.235 | 0.01358 | -0.0080706 | 0.01007 | 0.064251 | -0.02083 | -0.027327 | -0.027305 | 0.0025024 | -0.010169 | 0.064403 | 0.048783 | -0.019649 | -0.0079638 | -0.01311 | -0.12817 | 61.2076 | -61.1252 | 61.2396 | -60.7819 | -61.1572 | -61.203 | -0.045776 | 61.1481 | -61.0657 | 61.3083 | -60.9512 | -60.9741 | -60.9238 | -0.086975 | -0.027465 | 0.004578 | 0.25635 | -0.1648 | -0.11902 | -0.07782 | -0.032044 | -0.027466 | -0.086975 | 0.073243 | 0.086975 | 0.11444 | 0.064087 | 0.14191 | 0.091553 | 0.34332 | 122.3648 | 0.11444 | 122.374 | 122.3328 | 122.2137 | 122.2458 | 122.1863 | -122.3602 | -122.3007 | 122.2778 | 122.3465 | 60.91 | 60.9924
1048.75 | 122.4152 | -60.9695 | 61.3495 | 0.0059509 | -0.0046526 | 0.0083613 | 0.065533 | -0.019335 | -0.031385 | -0.021324 | 0.0025024 | -0.0082459 | 0.062694 | 0.044938 | -0.022426 | -0.0086048 | -0.01781 | -0.091553 | 61.2808 | -61.0703 | 61.2305 | -60.7636 | -61.1526 | -61.1938 | -0.018311 | 61.2534 | -61.0107 | 61.29 | -60.965 | -60.9924 | -60.9283 | -0.10071 | -0.068664 | -0.11902 | 0.20599 | -0.22431 | -0.18311 | -0.1236 | -0.082398 | -0.041199 | -0.09613 | -0.059509 | 0.004577 | 0.041198 | -0.022889 | 0.082397 | 0.01831 | 0.3067 | 122.3007 | 0.045776 | 122.3007 | 122.3511 | 122.2641 | 122.2504 | 122.2229 | -122.4197 | -122.3602 | 122.2 | 122.2595 | 60.878 | 60.9512
1050.5312 | 122.5525 | -60.9695 | 61.2991 | 0.0059509 | -0.0087116 | 0.0087885 | 0.06532 | -0.018908 | -0.033308 | -0.025383 | 0.0025024 | -0.0095275 | 0.063335 | 0.041092 | -0.02029 | -0.0088184 | -0.016101 | -0.050354 | 61.203 | -61.0886 | 61.3541 | -60.6262 | -61.0291 | -61.0794 | 0.10529 | 61.2076 | -60.9833 | 61.4273 | -60.8231 | -60.8459 | -60.8414 | -0.11902 | -0.09613 | 0.054932 | 0.34332 | -0.10986 | -0.05951 | 0.009155 | 0.059509 | -0.013733 | -0.091552 | 0.12817 | 0.14648 | 0.12817 | 0.1236 | 0.14191 | 0.13733 | 0.46234 | 122.4426 | 0.16022 | 122.4106 | 122.2916 | 122.1909 | 122.1725 | 122.1771 | -122.3877 | -122.2824 | 122.3236 | 122.3969 | 60.9192 | 61.0748
1052.3125 | 122.5067 | -60.9833 | 61.2671 | 0.02121 | -0.0059344 | 0.010284 | 0.063824 | -0.01848 | -0.031385 | -0.025169 | 0.008606 | -0.0080321 | 0.063121 | 0.047501 | -0.019649 | -0.010527 | -0.011615 | -0.10986 | 61.2122 | -61.116 | 61.2579 | -60.7681 | -61.1526 | -61.1893 | -0.045776 | 61.171 | -61.0428 | 61.3174 | -60.9329 | -60.9741 | -60.91 | -0.13275 | -0.054932 | -0.009155 | 0.21515 | -0.20599 | -0.16937 | -0.073242 | -0.036621 | -0.05951 | -0.096131 | 0.050354 | 0.050354 | 0.073242 | 0.009155 | 0.13275 | 0.068665 | 0.3479 | 122.374 | 0.10986 | 122.3602 | 122.3282 | 122.2137 | 122.1954 | 122.1542 | -122.3831 | -122.3099 | 122.2412 | 122.3007 | 60.8734 | 60.9375
1054.0312 | 122.5845 | -60.965 | 61.2854 | 0.0059509 | -0.0063616 | 0.0079339 | 0.062543 | -0.019549 | -0.030104 | -0.023887 | 0.0025024 | -0.0076049 | 0.063335 | 0.048356 | -0.02029 | -0.012664 | -0.016528 | -0.045776 | 61.235 | -61.0703 | 61.3495 | -60.6491 | -61.0519 | -61.0748 | 0.082397 | 61.2076 | -60.9741 | 61.4319 | -60.8093 | -60.8231 | -60.8185 | -0.10529 | -0.050354 | 0.064087 | 0.31586 | -0.10986 | -0.086975 | -0.004578 | 0.01831 | -0.009155 | -0.077819 | 0.14648 | 0.15564 | 0.14648 | 0.14191 | 0.15564 | 0.15106 | 0.42114 | 122.4197 | 0.16479 | 122.406 | 122.3053 | 122.1817 | 122.2 | 122.1725 | -122.3557 | -122.2595 | 122.3145 | 122.3969 | 60.9192 | 61.0474
1055.7344 | 122.4976 | -60.9833 | 61.2534 | 0.02121 | -0.0052936 | 0.01007 | 0.064038 | -0.018694 | -0.029463 | -0.02111 | 0.011658 | -0.0080321 | 0.06419 | 0.045792 | -0.019435 | -0.0088184 | -0.012896 | -0.1236 | 61.2259 | -61.0886 | 61.2671 | -60.7636 | -61.1572 | -61.1755 | -0.059509 | 61.1984 | -61.0703 | 61.3129 | -60.9421 | -60.9558 | -60.9055 | -0.10529 | -0.027466 | 0.013733 | 0.21973 | -0.19226 | -0.17395 | -0.086975 | -0.068665 | -0.086975 | -0.054932 | 0.059509 | 0.041198 | 0.077819 | 0.027465 | 0.16479 | 0.11444 | 0.32501 | 122.3557 | 0.12817 | 122.3831 | 122.3145 | 122.2687 | 122.2092 | 122.1817 | -122.3419 | -122.3236 | 122.2504 | 122.2961 | 60.8597 | 60.9238
1057.5 | 122.5433 | -60.9467 | 61.2854 | 0.0059509 | -0.0063616 | 0.0077203 | 0.064251 | -0.016771 | -0.031385 | -0.023674 | 0.0025024 | -0.0084595 | 0.062481 | 0.043442 | -0.020717 | -0.010314 | -0.016314 | -0.036621 | 61.2579 | -61.0519 | 61.3861 | -60.6354 | -61.0153 | -61.0611 | 0.10071 | 61.2442 | -60.9879 | 61.4273 | -60.8093 | -60.8322 | -60.8002 | -0.10529 | -0.027465 | 0.10071 | 0.31128 | -0.11444 | -0.068665 | -0.009155 | 0.036621 | -0.041199 | -0.041198 | 0.14191 | 0.13733 | 0.14648 | 0.11444 | 0.18768 | 0.15564 | 0.41656 | 122.438 | 0.17853 | 122.4152 | 122.3099 | 122.2321 | 122.2046 | 122.1909 | -122.3373 | -122.2733 | 122.3328 | 122.374 | 60.91 | 61.0474
1059.2188 | 122.406 | -61.0519 | 61.2854 | 0.0059509 | -0.006789 | 0.010284 | 0.066174 | -0.014635 | -0.030104 | -0.021537 | -0.003601 | -0.0069641 | 0.065471 | 0.044724 | -0.017513 | -0.0096728 | -0.013324 | -0.16479 | 61.2579 | -61.1252 | 61.171 | -60.8826 | -61.2625 | -61.2762 | -0.13733 | 61.203 | -61.0519 | 61.2488 | -61.0565 | -61.0794 | -60.9787 | -0.073242 | -0.027465 | -0.11444 | 0.16937 | -0.2243 | -0.21057 | -0.15106 | -0.13733 | 0 | -0.082397 | -0.036621 | -0.004578 | 0.073242 | -0.027466 | 0.073242 | -0.027466 | 0.24262 | 122.2961 | -0.004578 | 122.3007 | 122.3831 | 122.2549 | 122.3099 | 122.2549 | -122.4106 | -122.3373 | 122.2229 | 122.3007 | 60.8871 | 60.9146
1061 | 122.525 | -60.9833 | 61.2625 | 0.036468 | -0.0065754 | 0.011993 | 0.066174 | -0.01784 | -0.028822 | -0.02346 | 0.014709 | -0.0080321 | 0.063976 | 0.048356 | -0.019222 | -0.009032 | -0.012469 | -0.10986 | 61.203 | -61.0748 | 61.3129 | -60.6812 | -61.1435 | -61.1481 | 0.022888 | 61.1984 | -61.0748 | 61.3586 | -60.9192 | -60.9375 | -60.8917 | -0.091553 | -0.059509 | 0.050354 | 0.30212 | -0.1648 | -0.16022 | -0.073242 | -0.068665 | -0.091553 | -0.064087 | 0.096131 | 0.064087 | 0.091552 | 0.045776 | 0.1831 | 0.13733 | 0.39368 | 122.3877 | 0.15564 | 122.4335 | 122.2778 | 122.2733 | 122.1863 | 122.1817 | -122.3373 | -122.3373 | 122.2961 | 122.3419 | 60.8734 | 61.0062
1062.7656 | 122.5616 | -60.9604 | 61.2946 | -0.0016786 | -0.008498 | 0.0072931 | 0.063824 | -0.021044 | -0.033094 | -0.027305 | -0.00054937 | -0.0073913 | 0.063762 | 0.043656 | -0.020931 | -0.0077502 | -0.012683 | -0.09613 | 61.2488 | -61.0565 | 61.3449 | -60.6491 | -61.0519 | -61.0657 | 0.068665 | 61.2122 | -60.9787 | 61.4365 | -60.7956 | -60.8368 | -60.8139 | -0.096131 | -0.045777 | 0.050354 | 0.31128 | -0.10529 | -0.091553 | -0.009155 | 0.004578 | -0.018311 | -0.082398 | 0.14191 | 0.1648 | 0.14648 | 0.1236 | 0.16479 | 0.14191 | 0.40741 | 122.4014 | 0.18311 | 122.4152 | 122.3053 | 122.1909 | 122.2092 | 122.1725 | -122.3511 | -122.2733 | 122.3053 | 122.3969 | 60.8643 | 61.0291
1064.4688 | 122.4152 | -60.9604 | 61.3678 | 0.036468 | -0.0070026 | 0.0072931 | 0.065747 | -0.022539 | -0.030317 | -0.022178 | 0.011658 | -0.0082459 | 0.064403 | 0.040665 | -0.020503 | -0.0096728 | -0.012469 | -0.07782 | 61.3586 | -61.0703 | 61.2946 | -60.7452 | -61.1206 | -61.1572 | -0.041199 | 61.3266 | -61.0245 | 61.3266 | -60.9329 | -60.9558 | -60.8963 | -0.10986 | -0.009155 | -0.073242 | 0.21515 | -0.19684 | -0.16022 | -0.086976 | -0.050354 | -0.064087 | -0.041199 | -0.041199 | 0.027466 | 0.064087 | 0.004577 | 0.12817 | 0.068664 | 0.32501 | 122.3648 | 0.091553 | 122.3511 | 122.4289 | 122.3511 | 122.319 | 122.287 | -122.438 | -122.3923 | 122.2549 | 122.287 | 60.8826 | 60.9192
1066.1875 | 122.406 | -60.9467 | 61.3724 | 0.0059509 | -0.0087116 | 0.0092157 | 0.064038 | -0.016985 | -0.032454 | -0.025169 | 0.0025024 | -0.0084595 | 0.065258 | 0.041733 | -0.021785 | -0.013091 | -0.012042 | -0.10986 | 61.3037 | -61.0382 | 61.2808 | -60.7224 | -61.1069 | -61.1298 | -0.036621 | 61.3037 | -60.9695 | 61.3403 | -60.9055 | -60.9375 | -60.8734 | -0.091553 | -0.068664 | -0.091552 | 0.2243 | -0.18311 | -0.16022 | -0.091553 | -0.068665 | -0.022888 | -0.068664 | -0.032043 | 0.041198 | 0.073242 | 0.009155 | 0.09613 | 0.032043 | 0.31586 | 122.319 | 0.064086 | 122.3099 | 122.3419 | 122.2733 | 122.2504 | 122.2504 | -122.4106 | -122.3419 | 122.2275 | 122.287 | 60.8368 | 60.91
1067.8906 | 122.4518 | -60.9879 | 61.3266 | 0.02121 | -0.0063616 | 0.0087885 | 0.065106 | -0.015276 | -0.031172 | -0.020256 | 0.0025024 | -0.0073913 | 0.063121 | 0.039811 | -0.01794 | -0.011382 | -0.017383 | -0.073242 | 61.29 | -61.0382 | 61.3083 | -60.7178 | -61.1252 | -61.1572 | -0.009155 | 61.2305 | -61.0016 | 61.3449 | -60.9329 | -60.965 | -60.8963 | -0.050354 | -0.036621 | -0.01831 | 0.27008 | -0.16937 | -0.13733 | -0.11902 | -0.086975 | -0.013733 | -0.09613 | 0.018311 | 0.054932 | 0.091553 | 0.022888 | 0.10529 | 0.036621 | 0.32043 | 122.3465 | 0.068665 | 122.3465 | 122.3282 | 122.2321 | 122.2778 | 122.2183 | -122.3648 | -122.3282 | 122.2961 | 122.3328 | 60.9146 | 60.9787
1069.6094 | 122.4518 | -61.0291 | 61.2854 | 0.0059509 | -0.006789 | 0.0092157 | 0.069806 | -0.017626 | -0.028181 | -0.024101 | 0.0055542 | -0.0071777 | 0.063549 | 0.043229 | -0.017085 | -0.0096728 | -0.014605 | -0.16479 | 61.2808 | -61.0931 | 61.1984 | -60.8276 | -61.2213 | -61.2259 | -0.10986 | 61.1938 | -61.0382 | 61.3129 | -60.9924 | -61.0245 | -60.9375 | -0.064087 | -0.004577 | -0.086975 | 0.20142 | -0.19684 | -0.19226 | -0.13275 | -0.12817 | -0.009155 | -0.091552 | 0.027466 | 0.036621 | 0.091553 | 0.004578 | 0.10071 | 0.013733 | 0.2655 | 122.2916 | 0.045776 | 122.3511 | 122.374 | 122.2321 | 122.3099 | 122.2229 | -122.3785 | -122.3236 | 122.2275 | 122.3419 | 60.8643 | 60.9192
1071.3438 | 122.5525 | -60.9009 | 61.3129 | -0.0016786 | -0.0087116 | 0.0096429 | 0.064251 | -0.017412 | -0.030317 | -0.025169 | -0.00054937 | -0.0097411 | 0.062053 | 0.042801 | -0.018794 | -0.0094592 | -0.014605 | -0.07782 | 61.29 | -61.0199 | 61.3678 | -60.6125 | -61.0153 | -61.0519 | 0.07782 | 61.2396 | -60.9695 | 61.4685 | -60.7819 | -60.8093 | -60.7864 | -0.11902 | -0.022888 | 0.054932 | 0.28839 | -0.15106 | -0.11444 | -0.032044 | 0.004577 | -0.068664 | -0.073242 | 0.15564 | 0.11902 | 0.11444 | 0.091553 | 0.18311 | 0.16022 | 0.40741 | 122.3877 | 0.18768 | 122.438 | 122.3099 | 122.2092 | 122.1909 | 122.1405 | -122.3328 | -122.2824 | 122.2687 | 122.3694 | 60.8231 | 60.9787
1073.1406 | 122.406 | -60.9375 | 61.3678 | -0.0016786 | -0.0074298 | 0.0087885 | 0.062543 | -0.01784 | -0.032667 | -0.025383 | -0.00054937 | -0.0082459 | 0.063335 | 0.042161 | -0.022853 | -0.010527 | -0.017169 | -0.064087 | 61.3632 | -61.0291 | 61.3083 | -60.6903 | -61.0703 | -61.116 | -0.022888 | 61.3266 | -60.9512 | 61.3724 | -60.8734 | -60.9283 | -60.878 | -0.091553 | -0.004578 | -0.059509 | 0.24719 | -0.17853 | -0.13275 | -0.086975 | -0.041198 | -0.013733 | -0.041199 | 0.004577 | 0.064087 | 0.059509 | 0.009155 | 0.073242 | 0.022888 | 0.33874 | 122.3373 | 0.07782 | 122.3236 | 122.3923 | 122.2778 | 122.3007 | 122.2641 | -122.3969 | -122.319 | 122.2458 | 122.3099 | 60.8734 | 60.9146
1074.9219 | 122.4609 | -60.9833 | 61.2762 | 0.0059509 | -0.008498 | 0.01007 | 0.064465 | -0.021898 | -0.030104 | -0.024955 | 0.0025024 | -0.0073913 | 0.06483 | 0.045151 | -0.018794 | -0.0094592 | -0.018023 | -0.16022 | 61.29 | -61.084 | 61.235 | -60.791 | -61.1938 | -61.2213 | -0.11902 | 61.2259 | -61.0153 | 61.3312 | -60.9329 | -60.9741 | -60.8871 | -0.10071 | 0.013733 | -0.041199 | 0.19226 | -0.23804 | -0.21057 | -0.13733 | -0.10986 | -0.032044 | -0.050354 | 0.054932 | 0.050354 | 0.09613 | 0.009155 | 0.12817 | 0.041199 | 0.29297 | 122.319 | 0.082398 | 122.3465 | 122.374 | 122.2412 | 122.2733 | 122.2092 | -122.3602 | -122.2916 | 122.2183 | 122.3145 | 60.8231 | 60.8643
1076.6875 | 122.5433 | -60.9604 | 61.2534 | 0.01358 | -0.009566 | 0.01007 | 0.06532 | -0.024035 | -0.029463 | -0.025383 | 0.0025024 | -0.0076049 | 0.063121 | 0.048997 | -0.016017 | -0.010314 | -0.016528 | -0.1236 | 61.2534 | -61.0474 | 61.3174 | -60.6995 | -61.0977 | -61.1343 | 0.004578 | 61.2122 | -60.9604 | 61.4136 | -60.8643 | -60.8871 | -60.8276 | -0.086975 | 0 | 0.064087 | 0.26093 | -0.17395 | -0.13733 | -0.086975 | -0.050354 | 0 | -0.041199 | 0.16022 | 0.09613 | 0.13275 | 0.073242 | 0.13275 | 0.073242 | 0.3479 | 122.3648 | 0.09613 | 122.374 | 122.3007 | 122.1725 | 122.2137 | 122.1725 | -122.3007 | -122.2137 | 122.2778 | 122.374 | 60.8368 | 60.965
1078.4219 | 122.4884 | -60.9604 | 61.2991 | 0.0059509 | -0.0091388 | 0.0094293 | 0.06596 | -0.020617 | -0.02989 | -0.024955 | 0.0025024 | -0.0084595 | 0.06483 | 0.043229 | -0.017513 | -0.0075366 | -0.017596 | -0.17853 | 61.3174 | -61.0474 | 61.235 | -60.7636 | -61.1847 | -61.1847 | -0.064087 | 61.2213 | -60.9833 | 61.3815 | -60.8963 | -60.9238 | -60.8597 | -0.086975 | 0.018311 | -0.064087 | 0.19684 | -0.2243 | -0.2243 | -0.13733 | -0.13733 | -0.022888 | -0.07782 | 0.082398 | 0.064087 | 0.10071 | 0.036621 | 0.1236 | 0.059509 | 0.28381 | 122.2824 | 0.086975 | 122.3648 | 122.3648 | 122.2046 | 122.2778 | 122.1817 | -122.3465 | -122.2824 | 122.1954 | 122.3419 | 60.7819 | 60.8963
1080.1406 | 122.493 | -60.9238 | 61.3403 | 0.028839 | -0.0097796 | 0.010284 | 0.06297 | -0.018908 | -0.030531 | -0.022819 | 0.0055542 | -0.0067505 | 0.063549 | 0.040024 | -0.019863 | -0.0086048 | -0.012683 | -0.13275 | 61.2946 | -61.0382 | 61.3403 | -60.6674 | -61.0748 | -61.1023 | -0.041199 | 61.2579 | -60.9604 | 61.3998 | -60.8414 | -60.8826 | -60.8276 | -0.11444 | -0.045776 | 0 | 0.25635 | -0.17853 | -0.15106 | -0.064087 | -0.036621 | -0.036621 | -0.082397 | 0.059509 | 0.082397 | 0.09613 | 0.041199 | 0.13275 | 0.07782 | 0.37079 | 122.3785 | 0.11902 | 122.3602 | 122.3328 | 122.2183 | 122.2183 | 122.1817 | -122.3785 | -122.3007 | 122.2641 | 122.3236 | 60.791 | 60.8826
1081.9219 | 122.4197 | -60.8917 | 61.4319 | 0.0059509 | -0.0076434 | 0.0075067 | 0.066388 | -0.019549 | -0.029676 | -0.026023 | 0.0055542 | -0.010596 | 0.062267 | 0.048142 | -0.022212 | -0.010527 | -0.015887 | -0.027466 | 61.3541 | -60.9558 | 61.3907 | -60.6171 | -61.0016 | -61.0382 | 0.018311 | 61.3495 | -60.9055 | 61.4227 | -60.8414 | -60.8688 | -60.8185 | -0.064087 | -0.07782 | -0.041199 | 0.27466 | -0.14648 | -0.10986 | -0.082397 | -0.045776 | -0.013733 | -0.082398 | -0.009156 | 0.050354 | 0.073243 | 0.022889 | 0.086976 | 0.036622 | 0.33875 | 122.3465 | 0.064087 | 122.3282 | 122.3099 | 122.2549 | 122.2458 | 122.2412 | -122.3877 | -122.3373 | 122.2824 | 122.3145 | 60.8643 | 60.91
1083.6406 | 122.4152 | -60.91 | 61.4273 | 0.044098 | -0.0065754 | 0.0079339 | 0.06831 | -0.018267 | -0.033308 | -0.023246 | 0.008606 | -0.0065369 | 0.063976 | 0.048142 | -0.022426 | -0.0101 | -0.013537 | -0.073242 | 61.409 | -60.9833 | 61.3312 | -60.672 | -61.0428 | -61.0794 | -0.054932 | 61.3724 | -60.9467 | 61.3998 | -60.8505 | -60.8917 | -60.8185 | -0.073242 | -0.01831 | -0.09613 | 0.23804 | -0.16937 | -0.13275 | -0.096131 | -0.05951 | -0.036621 | -0.054932 | -0.027466 | 0.059509 | 0.091553 | 0.01831 | 0.12817 | 0.054931 | 0.31128 | 122.3145 | 0.09613 | 122.3465 | 122.3923 | 122.319 | 122.319 | 122.2824 | -122.4106 | -122.374 | 122.2412 | 122.3099 | 60.8368 | 60.8551
1085.4219 | 122.4472 | -60.9009 | 61.3953 | 0.036468 | -0.0057208 | 0.0085749 | 0.065533 | -0.018267 | -0.027967 | -0.021324 | 0.014709 | -0.0084595 | 0.062694 | 0.038956 | -0.02029 | -0.0094592 | -0.017383 | -0.064087 | 61.4227 | -60.997 | 61.377 | -60.6445 | -61.0153 | -61.0611 | -0.018311 | 61.3815 | -60.9283 | 61.4273 | -60.8231 | -60.878 | -60.7819 | -0.09613 | 0.027465 | -0.018311 | 0.25635 | -0.16022 | -0.11444 | -0.064087 | -0.018311 | -0.027466 | -0.013733 | 0.032043 | 0.07782 | 0.11902 | 0.022888 | 0.14648 | 0.050354 | 0.35248 | 122.374 | 0.10529 | 122.3557 | 122.4197 | 122.3099 | 122.3236 | 122.2824 | -122.3923 | -122.3236 | 122.2778 | 122.3282 | 60.8368 | 60.8826
1087.1406 | 122.5296 | -60.91 | 61.3174 | 0.01358 | -0.0074298 | 0.0096429 | 0.064465 | -0.017199 | -0.029249 | -0.025169 | -0.00054937 | -0.0086731 | 0.065044 | 0.041947 | -0.01559 | -0.0092456 | -0.014392 | -0.13733 | 61.2762 | -61.0062 | 61.377 | -60.6308 | -61.0291 | -61.0703 | 0 | 61.2259 | -60.9512 | 61.4594 | -60.8093 | -60.8597 | -60.7864 | -0.096131 | -0.041199 | 0.059509 | 0.27924 | -0.16022 | -0.11902 | -0.064086 | -0.022888 | -0.041199 | -0.091553 | 0.14191 | 0.10071 | 0.1236 | 0.050354 | 0.1648 | 0.091553 | 0.37537 | 122.3831 | 0.14191 | 122.4106 | 122.2824 | 122.1771 | 122.1863 | 122.1359 | -122.3236 | -122.2687 | 122.287 | 122.3694 | 60.7727 | 60.91
1088.9375 | 122.4609 | -60.8963 | 61.3998 | 0.036468 | -0.006148 | 0.011779 | 0.066388 | -0.019121 | -0.029036 | -0.020897 | 0.008606 | -0.0067505 | 0.062694 | 0.035111 | -0.022426 | -0.0101 | -0.013324 | -0.054932 | 61.4319 | -60.9741 | 61.3678 | -60.6445 | -61.0199 | -61.0382 | -0.013733 | 61.3403 | -60.9055 | 61.4456 | -60.8093 | -60.8459 | -60.7819 | -0.07782 | 0.032044 | -0.032043 | 0.25177 | -0.14191 | -0.1236 | -0.064087 | -0.045776 | -0.009156 | -0.059509 | 0.045777 | 0.086975 | 0.11444 | 0.050354 | 0.1236 | 0.05951 | 0.32959 | 122.3419 | 0.096131 | 122.3511 | 122.406 | 122.2458 | 122.3282 | 122.2366 | -122.374 | -122.3053 | 122.2641 | 122.3419 | 60.8414 | 60.8826
1090.7188 | 122.5021 | -60.9055 | 61.3312 | 0.0059509 | -0.008498 | 0.0098565 | 0.064465 | -0.019976 | -0.029463 | -0.022819 | 0.0025024 | -0.0082459 | 0.063762 | 0.045579 | -0.018794 | -0.007323 | -0.015674 | -0.19226 | 61.3403 | -61.0107 | 61.29 | -60.7224 | -61.1343 | -61.1572 | -0.086975 | 61.2579 | -60.9421 | 61.4319 | -60.8322 | -60.8688 | -60.7956 | -0.10529 | 0.009155 | -0.041199 | 0.18311 | -0.25177 | -0.22888 | -0.14648 | -0.1236 | -0.036621 | -0.073242 | 0.10071 | 0.073243 | 0.10986 | 0.036622 | 0.14649 | 0.073243 | 0.28839 | 122.3007 | 0.10986 | 122.374 | 122.3511 | 122.2 | 122.2458 | 122.1634 | -122.3419 | -122.2733 | 122.1954 | 122.3373 | 60.7132 | 60.8185
1092.4844 | 122.5479 | -60.8871 | 61.3358 | 0.0059509 | -0.0091388 | 0.0087885 | 0.06532 | -0.02083 | -0.028608 | -0.02346 | 0.0025024 | -0.0069641 | 0.063549 | 0.050278 | -0.016872 | -0.0088184 | -0.016528 | -0.10071 | 61.3358 | -60.9695 | 61.3907 | -60.5942 | -61.0382 | -61.0382 | 0.027466 | 61.2488 | -60.9055 | 61.4822 | -60.7773 | -60.8322 | -60.7498 | -0.082397 | 0 | 0.054932 | 0.29297 | -0.15106 | -0.15106 | -0.068665 | -0.068665 | -0.018311 | -0.086975 | 0.14648 | 0.10986 | 0.13733 | 0.054932 | 0.15564 | 0.073243 | 0.37537 | 122.3602 | 0.12817 | 122.3877 | 122.3053 | 122.1542 | 122.2229 | 122.1359 | -122.3053 | -122.2412 | 122.2778 | 122.3694 | 60.7864 | 60.9146
1094.2031 | 122.4472 | -60.8322 | 61.4456 | 0.028839 | -0.006789 | 0.0077203 | 0.065533 | -0.013353 | -0.029676 | -0.020042 | 0.008606 | -0.0050415 | 0.066112 | 0.044938 | -0.021785 | -0.0092456 | -0.014605 | -0.054932 | 61.4777 | -60.9375 | 61.3998 | -60.6171 | -60.9833 | -61.0245 | -0.013733 | 61.3907 | -60.91 | 61.4685 | -60.7956 | -60.8231 | -60.7452 | -0.10529 | 0.032043 | -0.045777 | 0.21515 | -0.19226 | -0.15106 | -0.086975 | -0.045776 | -0.07782 | -0.054932 | 0.022888 | 0.036621 | 0.086975 | 0.009155 | 0.1648 | 0.086975 | 0.32044 | 122.3373 | 0.11444 | 122.3785 | 122.4152 | 122.3007 | 122.3099 | 122.2229 | -122.3831 | -122.3557 | 122.2321 | 122.3007 | 60.7773 | 60.8185
1095.9844 | 122.4472 | -60.8871 | 61.3907 | 0.0059509 | -0.0072162 | 0.0098565 | 0.06297 | -0.019976 | -0.029463 | -0.024955 | 0.0025024 | -0.0078185 | 0.06483 | 0.044297 | -0.01794 | -0.008391 | -0.015674 | -0.16479 | 61.3998 | -60.965 | 61.3174 | -60.704 | -61.0931 | -61.1114 | -0.10071 | 61.3129 | -60.9283 | 61.4273 | -60.8597 | -60.8871 | -60.8139 | -0.07782 | 0.009155 | -0.073242 | 0.18311 | -0.2243 | -0.20599 | -0.14648 | -0.12817 | -0.041199 | -0.07782 | 0.036621 | 0.027466 | 0.073242 | 0 | 0.11444 | 0.041199 | 0.26093 | 122.2824 | 0.068665 | 122.3557 | 122.3648 | 122.2412 | 122.287 | 122.2 | -122.3557 | -122.319 | 122.2046 | 122.3145 | 60.7224 | 60.7864
1097.6875 | 122.438 | -60.8414 | 61.4182 | 0.01358 | -0.00508 | 0.0092157 | 0.067242 | -0.012285 | -0.027967 | -0.020897 | 0.0055542 | -0.0067505 | 0.063549 | 0.045365 | -0.018794 | -0.0096728 | -0.015887 | -0.07782 | 61.3998 | -60.91 | 61.4044 | -60.5942 | -60.9924 | -61.0382 | 0 | 61.3678 | -60.8643 | 61.4594 | -60.7956 | -60.8368 | -60.759 | -0.068664 | -0.018311 | -0.013733 | 0.24719 | -0.19684 | -0.15106 | -0.12817 | -0.082398 | -0.022888 | -0.050354 | 0.041199 | 0.045777 | 0.082398 | 0.004578 | 0.10529 | 0.027466 | 0.31586 | 122.3145 | 0.068665 | 122.3236 | 122.3099 | 122.2321 | 122.2412 | 122.2092 | -122.3282 | -122.2824 | 122.2458 | 122.3007 | 60.7635 | 60.8414
1099.4688 | 122.525 | -60.7681 | 61.4456 | 0.01358 | -0.0087116 | 0.0087885 | 0.062329 | -0.014849 | -0.032026 | -0.025169 | 0.0055542 | -0.011878 | 0.062481 | 0.044083 | -0.021572 | -0.0096728 | -0.016101 | -0.050354 | 61.409 | -60.9009 | 61.5189 | -60.4294 | -60.8459 | -60.8734 | 0.086975 | 61.3678 | -60.8002 | 61.5921 | -60.6445 | -60.6674 | -60.64 | -0.13275 | -0.036621 | 0.073242 | 0.33875 | -0.10529 | -0.07782 | 0.027466 | 0.054932 | -0.032044 | -0.07782 | 0.14648 | 0.1236 | 0.12817 | 0.10071 | 0.16022 | 0.13275 | 0.4715 | 122.4197 | 0.15564 | 122.3923 | 122.3099 | 122.168 | 122.1771 | 122.1359 | -122.3465 | -122.2458 | 122.287 | 122.3602 | 60.7178 | 60.8551
1101.1875 | 122.4106 | -60.8826 | 61.4319 | 0.0059509 | -0.0072162 | 0.0096429 | 0.06532 | -0.01784 | -0.030745 | -0.020897 | 0.0025024 | -0.0065369 | 0.064403 | 0.045151 | -0.018367 | -0.0088184 | -0.016528 | -0.16022 | 61.4273 | -60.9512 | 61.3037 | -60.7132 | -61.0931 | -61.1114 | -0.13275 | 61.3632 | -60.9009 | 61.409 | -60.8688 | -60.91 | -60.8093 | -0.068665 | -0.004578 | -0.12817 | 0.16937 | -0.22888 | -0.21057 | -0.16022 | -0.14191 | -0.018311 | -0.068665 | -0.022888 | 0.013733 | 0.073242 | -0.027466 | 0.091553 | -0.009155 | 0.23804 | 122.2549 | 0.032044 | 122.3099 | 122.3785 | 122.2641 | 122.3099 | 122.2458 | -122.3831 | -122.3328 | 122.1863 | 122.2916 | 60.7224 | 60.7498
1102.9688 | 122.3969 | -60.8643 | 61.4227 | 0.0059509 | -0.008498 | 0.0083613 | 0.066174 | -0.017199 | -0.030745 | -0.023246 | -0.00054937 | -0.0095275 | 0.065258 | 0.041947 | -0.019222 | -0.010955 | -0.013965 | -0.16937 | 61.3907 | -60.9695 | 61.3312 | -60.6857 | -61.0657 | -61.0977 | -0.15564 | 61.3861 | -60.8826 | 61.4044 | -60.878 | -60.9329 | -60.8185 | -0.10529 | -0.032043 | -0.091552 | 0.17853 | -0.23346 | -0.20142 | -0.12817 | -0.096131 | -0.01831 | -0.036621 | -0.01831 | -0.013733 | 0.045777 | -0.068664 | 0.064087 | -0.050354 | 0.28381 | 122.3007 | 0.004577 | 122.287 | 122.3602 | 122.2687 | 122.2549 | 122.2504 | -122.3923 | -122.3053 | 122.1954 | 122.2687 | 60.6949 | 60.7086
1104.75 | 122.3877 | -60.8688 | 61.4548 | 0.02121 | -0.009566 | 0.010498 | 0.067029 | -0.014422 | -0.029036 | -0.023033 | -0.00054937 | -0.0076049 | 0.064617 | 0.040665 | -0.019649 | -0.0092456 | -0.012896 | -0.16937 | 61.4227 | -60.9558 | 61.3358 | -60.6903 | -61.0794 | -61.1023 | -0.17395 | 61.3678 | -60.8871 | 61.4502 | -60.878 | -60.9009 | -60.791 | -0.086976 | -0.032044 | -0.11902 | 0.17853 | -0.23346 | -0.21057 | -0.14648 | -0.1236 | -0.018311 | -0.086975 | -0.004578 | -0.009156 | 0.077819 | -0.032044 | 0.09613 | -0.013733 | 0.2655 | 122.2916 | 0.009155 | 122.3373 | 122.3785 | 122.2549 | 122.2916 | 122.2366 | -122.4106 | -122.3419 | 122.2046 | 122.319 | 60.6995 | 60.6949
1106.5312 | 122.4426 | -60.7864 | 61.5005 | 0.01358 | -0.0080706 | 0.0094293 | 0.067242 | -0.021898 | -0.02989 | -0.022392 | 0.0055542 | -0.0048279 | 0.066326 | 0.040452 | -0.021572 | -0.0101 | -0.016528 | -0.07782 | 61.5189 | -60.8551 | 61.4319 | -60.5621 | -60.9238 | -60.9695 | -0.036621 | 61.4777 | -60.8231 | 61.5143 | -60.7315 | -60.7773 | -60.704 | -0.068665 | 0.018311 | -0.068664 | 0.2243 | -0.18311 | -0.13733 | -0.11444 | -0.068664 | -0.036621 | -0.022888 | 0.013733 | 0.054932 | 0.082397 | 0.009155 | 0.11902 | 0.045776 | 0.29297 | 122.287 | 0.091553 | 122.3373 | 122.374 | 122.3007 | 122.3053 | 122.2641 | -122.3557 | -122.3236 | 122.2183 | 122.3007 | 60.7086 | 60.7498
1108.2656 | 122.3969 | -60.8139 | 61.5005 | 0.01358 | -0.006148 | 0.011138 | 0.06596 | -0.016771 | -0.028822 | -0.024314 | -0.00054937 | -0.0069641 | 0.06419 | 0.050706 | -0.018154 | -0.009032 | -0.015887 | -0.14648 | 61.4639 | -60.8963 | 61.3953 | -60.6171 | -61.0199 | -61.0336 | -0.11444 | 61.4136 | -60.8643 | 61.4548 | -60.8139 | -60.8505 | -60.7361 | -0.082397 | -0.036621 | -0.10529 | 0.19684 | -0.21973 | -0.20599 | -0.13733 | -0.1236 | -0.050354 | -0.086975 | -0.045776 | 0 | 0.07782 | -0.036621 | 0.12817 | 0.013733 | 0.27924 | 122.2916 | 0.050354 | 122.319 | 122.3602 | 122.2778 | 122.2778 | 122.2275 | -122.3969 | -122.3648 | 122.2092 | 122.2687 | 60.6674 | 60.6995
1110.0469 | 122.4976 | -60.7544 | 61.5005 | 0.02121 | -0.0087116 | 0.0096429 | 0.064465 | -0.020189 | -0.030745 | -0.022819 | 0.0055542 | -0.0082459 | 0.066112 | 0.044938 | -0.018154 | -0.0081774 | -0.017383 | -0.13275 | 61.4456 | -60.8643 | 61.4685 | -60.5164 | -60.9146 | -60.9375 | -0.036621 | 61.3998 | -60.7727 | 61.5555 | -60.6812 | -60.6949 | -60.64 | -0.10986 | -0.054931 | -0.032043 | 0.23804 | -0.1831 | -0.16022 | -0.073242 | -0.050354 | -0.01831 | -0.10071 | 0.054932 | 0.073243 | 0.11444 | 0.05951 | 0.13275 | 0.07782 | 0.3479 | 122.3328 | 0.091553 | 122.3282 | 122.3099 | 122.1725 | 122.2 | 122.1542 | -122.3648 | -122.2733 | 122.2229 | 122.3099 | 60.6216 | 60.7178
1111.8125 | 122.4884 | -60.7407 | 61.4685 | 0.02121 | -0.006789 | 0.012634 | 0.066388 | -0.020189 | -0.028395 | -0.020683 | 0.0055542 | -0.0071777 | 0.062481 | 0.048783 | -0.018367 | -0.0096728 | -0.014178 | -0.10986 | 61.4365 | -60.8368 | 61.5189 | -60.4523 | -60.8871 | -60.8963 | 0.018311 | 61.3815 | -60.8047 | 61.5829 | -60.6674 | -60.704 | -60.6583 | -0.09613 | -0.032044 | 0.050354 | 0.28839 | -0.15564 | -0.14648 | -0.059509 | -0.050354 | -0.064087 | -0.086975 | 0.11444 | 0.073243 | 0.082398 | 0.036621 | 0.14648 | 0.10071 | 0.38452 | 122.3557 | 0.13733 | 122.3877 | 122.2733 | 122.1863 | 122.1771 | 122.1222 | -122.3053 | -122.2733 | 122.2595 | 122.3236 | 60.6308 | 60.759
1113.5938 | 122.4564 | -60.7681 | 61.4594 | 0.01358 | -0.0080706 | 0.0081477 | 0.066815 | -0.01549 | -0.030531 | -0.023246 | -0.00054937 | -0.0065369 | 0.065258 | 0.050919 | -0.018367 | -0.0098864 | -0.016101 | -0.16937 | 61.496 | -60.8963 | 61.4136 | -60.6033 | -60.9924 | -61.0153 | -0.09613 | 61.4182 | -60.8185 | 61.5463 | -60.7224 | -60.7727 | -60.6857 | -0.12817 | 0.036621 | -0.045777 | 0.16479 | -0.24719 | -0.22431 | -0.11902 | -0.096131 | -0.050354 | -0.041199 | 0.086975 | 0.045776 | 0.082397 | -0.004578 | 0.13275 | 0.045776 | 0.29297 | 122.3099 | 0.09613 | 122.3648 | 122.3923 | 122.2366 | 122.2641 | 122.1863 | -122.3557 | -122.2778 | 122.1817 | 122.3145 | 60.5988 | 60.672
1115.3125 | 122.4838 | -60.7361 | 61.5189 | 0.028839 | -0.010634 | 0.011779 | 0.063611 | -0.016771 | -0.029463 | -0.022819 | 0.011658 | -0.0091003 | 0.062694 | 0.048356 | -0.019008 | -0.0079638 | -0.013537 | -0.12817 | 61.4365 | -60.8505 | 61.5189 | -60.4568 | -60.878 | -60.8917 | -0.009155 | 61.4273 | -60.7727 | 61.5921 | -60.6583 | -60.6903 | -60.6308 | -0.11444 | -0.082398 | 0 | 0.27924 | -0.15564 | -0.14191 | -0.041199 | -0.027466 | -0.036621 | -0.091553 | 0.073242 | 0.07782 | 0.10529 | 0.045776 | 0.14191 | 0.082397 | 0.39368 | 122.3694 | 0.11444 | 122.3648 | 122.287 | 122.2 | 122.1725 | 122.1634 | -122.3694 | -122.2916 | 122.2549 | 122.3282 | 60.6079 | 60.7269
1117.1094 | 122.4014 | -60.7315 | 61.528 | 0.028839 | -0.006789 | 0.010711 | 0.067883 | -0.017199 | -0.030531 | -0.024955 | 0.0055542 | -0.0069641 | 0.066326 | 0.041092 | -0.019435 | -0.0096728 | -0.015887 | -0.07782 | 61.5234 | -60.8139 | 61.5051 | -60.5118 | -60.9238 | -60.9421 | -0.018311 | 61.4639 | -60.7681 | 61.528 | -60.7315 | -60.7773 | -60.6857 | -0.082398 | -0.004578 | -0.022888 | 0.21973 | -0.21057 | -0.19226 | -0.12817 | -0.10986 | -0.036621 | -0.064087 | 0 | 0 | 0.045776 | -0.045777 | 0.082397 | -0.009156 | 0.30212 | 122.319 | 0.036621 | 122.2961 | 122.3373 | 122.2321 | 122.2549 | 122.1954 | -122.3419 | -122.2961 | 122.2366 | 122.2595 | 60.6537 | 60.7132
1118.9062 | 122.3969 | -60.6857 | 61.6241 | 0.01358 | -0.0072162 | 0.0077203 | 0.064892 | -0.020617 | -0.030958 | -0.023887 | -0.00054937 | -0.0067505 | 0.063762 | 0.050706 | -0.02264 | -0.0101 | -0.011615 | -0.091553 | 61.5646 | -60.7636 | 61.5234 | -60.4797 | -60.8505 | -60.8734 | -0.027466 | 61.5463 | -60.7132 | 61.5646 | -60.6491 | -60.672 | -60.6171 | -0.07782 | -0.05951 | -0.10071 | 0.20599 | -0.18768 | -0.16479 | -0.10986 | -0.086975 | -0.027466 | -0.07782 | -0.05951 | 0.036621 | 0.068665 | 0.013733 | 0.096131 | 0.041199 | 0.28381 | 122.287 | 0.064087 | 122.2778 | 122.3282 | 122.2595 | 122.2504 | 122.2321 | -122.3877 | -122.3373 | 122.2092 | 122.2504 | 60.5942 | 60.6583
1120.6719 | 122.525 | -60.6583 | 61.5646 | 0.0059509 | -0.011061 | 0.0090021 | 0.064251 | -0.022967 | -0.03224 | -0.026023 | 0.0025024 | -0.0082459 | 0.063762 | 0.046006 | -0.018794 | -0.0094592 | -0.014178 | -0.09613 | 61.5234 | -60.7407 | 61.6013 | -60.3607 | -60.7681 | -60.7819 | 0.036621 | 61.4914 | -60.6857 | 61.6837 | -60.5301 | -60.5576 | -60.5209 | -0.082398 | -0.041199 | 0.036621 | 0.29755 | -0.1236 | -0.10986 | -0.041198 | -0.027465 | -0.027466 | -0.073242 | 0.11902 | 0.12817 | 0.13733 | 0.10071 | 0.16479 | 0.12817 | 0.37994 | 122.3419 | 0.15564 | 122.3694 | 122.2641 | 122.1771 | 122.1817 | 122.1497 | -122.3053 | -122.2504 | 122.2595 | 122.3419 | 60.5621 | 60.6949
1122.3906 | 122.5021 | -60.6491 | 61.5967 | 0.01358 | -0.0087116 | 0.0090021 | 0.061902 | -0.023394 | -0.030317 | -0.024528 | -0.00054937 | -0.010596 | 0.063762 | 0.047715 | -0.019649 | -0.007323 | -0.014605 | -0.12817 | 61.5417 | -60.7636 | 61.5601 | -60.4202 | -60.8047 | -60.8231 | -0.022888 | 61.5005 | -60.7086 | 61.6745 | -60.5713 | -60.5896 | -60.5484 | -0.11444 | -0.054932 | -0.036621 | 0.22888 | -0.17395 | -0.15564 | -0.059509 | -0.041199 | -0.059509 | -0.096131 | 0.07782 | 0.07782 | 0.10071 | 0.059509 | 0.16022 | 0.11902 | 0.34332 | 122.3236 | 0.13733 | 122.3831 | 122.3053 | 122.2092 | 122.1909 | 122.1497 | -122.3602 | -122.3053 | 122.2092 | 122.3236 | 60.5209 | 60.6262
1124.1719 | 122.4701 | -60.672 | 61.5601 | 0.02121 | -0.0076434 | 0.010711 | 0.067242 | -0.019976 | -0.028395 | -0.022605 | 0.011658 | -0.0082459 | 0.06184 | 0.046006 | -0.019649 | -0.0094592 | -0.017596 | -0.11444 | 61.5143 | -60.7636 | 61.5784 | -60.3973 | -60.8276 | -60.8459 | 0 | 61.4777 | -60.7132 | 61.6379 | -60.5942 | -60.6262 | -60.5576 | -0.091553 | -0.045777 | 0.01831 | 0.27466 | -0.17395 | -0.15564 | -0.082397 | -0.064087 | -0.041199 | -0.082398 | 0.077819 | 0.07782 | 0.11444 | 0.045776 | 0.15564 | 0.086975 | 0.36621 | 122.3419 | 0.11902 | 122.3511 | 122.2778 | 122.1909 | 122.1863 | 122.1497 | -122.3236 | -122.2733 | 122.2504 | 122.3099 | 60.5576 | 60.672
1125.875 | 122.5479 | -60.64 | 61.6104 | 0.0059509 | -0.0099932 | 0.0083613 | 0.063824 | -0.016985 | -0.030745 | -0.020469 | 0.0025024 | -0.0082459 | 0.06419 | 0.046006 | -0.021358 | -0.010741 | -0.016955 | -0.050354 | 61.5463 | -60.7224 | 61.6653 | -60.3058 | -60.6995 | -60.7361 | 0.086975 | 61.5326 | -60.64 | 61.7432 | -60.4797 | -60.4843 | -60.4706 | -0.082397 | -0.064087 | 0.054931 | 0.33417 | -0.09613 | -0.059509 | -0.013733 | 0.022888 | 0 | -0.07782 | 0.13275 | 0.16022 | 0.16937 | 0.15564 | 0.16937 | 0.15564 | 0.41657 | 122.3877 | 0.16022 | 122.3831 | 122.2687 | 122.1725 | 122.1863 | 122.1725 | -122.3328 | -122.2504 | 122.3053 | 122.3831 | 60.5896 | 60.7269
1127.6562 | 122.4335 | -60.6354 | 61.6562 | 0.02121 | -0.0065754 | 0.0090021 | 0.067242 | -0.019976 | -0.029036 | -0.02346 | 0.014709 | -0.0063233 | 0.063121 | 0.043442 | -0.020076 | -0.011382 | -0.018237 | -0.054932 | 61.6425 | -60.7224 | 61.6196 | -60.4019 | -60.7819 | -60.8139 | -0.009155 | 61.5692 | -60.6766 | 61.6562 | -60.5667 | -60.6125 | -60.5392 | -0.086975 | -0.013733 | -0.036621 | 0.23346 | -0.17853 | -0.14648 | -0.091553 | -0.059509 | -0.041199 | -0.086975 | 0 | 0.068665 | 0.09613 | 0.022888 | 0.13733 | 0.064087 | 0.32043 | 122.3419 | 0.10986 | 122.3328 | 122.3648 | 122.2458 | 122.2778 | 122.2046 | -122.3785 | -122.3328 | 122.2549 | 122.2916 | 60.5804 | 60.6262
1129.4531 | 122.493 | -60.5804 | 61.6608 | 0.0059509 | -0.008498 | 0.0083613 | 0.064465 | -0.018267 | -0.031813 | -0.023887 | 0.0025024 | -0.0097411 | 0.064403 | 0.046433 | -0.021999 | -0.010741 | -0.011828 | -0.041199 | 61.6013 | -60.6674 | 61.7065 | -60.2921 | -60.672 | -60.704 | 0.059509 | 61.5829 | -60.5942 | 61.7432 | -60.466 | -60.5026 | -60.466 | -0.086975 | -0.05951 | 0.045776 | 0.28839 | -0.1236 | -0.091553 | -0.036622 | -0.004578 | -0.013733 | -0.07782 | 0.082397 | 0.11444 | 0.11444 | 0.077819 | 0.12817 | 0.091552 | 0.37537 | 122.374 | 0.12817 | 122.3373 | 122.2687 | 122.1771 | 122.1817 | 122.1634 | -122.3282 | -122.2549 | 122.287 | 122.3236 | 60.5392 | 60.64
1131.1875 | 122.5159 | -60.5621 | 61.6653 | 0.0059509 | -0.0091388 | 0.0081477 | 0.063611 | -0.01848 | -0.031813 | -0.023033 | 0.0025024 | -0.0086731 | 0.06419 | 0.04387 | -0.021358 | -0.011382 | -0.014819 | -0.032043 | 61.615 | -60.6445 | 61.7386 | -60.2509 | -60.64 | -60.6903 | 0.086975 | 61.5921 | -60.585 | 61.7844 | -60.4248 | -60.4706 | -60.4294 | -0.082397 | -0.050354 | 0.073242 | 0.31128 | -0.12817 | -0.07782 | -0.045777 | 0.004577 | -0.022888 | -0.073242 | 0.11902 | 0.13733 | 0.13275 | 0.091553 | 0.15564 | 0.11444 | 0.39368 | 122.3831 | 0.16022 | 122.3694 | 122.2595 | 122.1771 | 122.1771 | 122.1542 | -122.3099 | -122.2504 | 122.3007 | 122.3465 | 60.5301 | 60.6491
1132.9688 | 122.3602 | -60.6354 | 61.6653 | 0.0059509 | -0.0070026 | 0.0094293 | 0.06532 | -0.018267 | -0.032026 | -0.024101 | 0.0055542 | -0.0061095 | 0.062481 | 0.041733 | -0.01794 | -0.0088184 | -0.013751 | -0.14191 | 61.615 | -60.7361 | 61.5509 | -60.4706 | -60.8459 | -60.8597 | -0.1236 | 61.6196 | -60.6628 | 61.6287 | -60.6537 | -60.6903 | -60.585 | -0.10071 | -0.050354 | -0.11444 | 0.16479 | -0.2243 | -0.21057 | -0.1236 | -0.10986 | -0.027466 | -0.045776 | -0.036621 | -0.018311 | 0.050354 | -0.054932 | 0.07782 | -0.027466 | 0.2655 | 122.287 | 0.009155 | 122.2916 | 122.3511 | 122.2824 | 122.2504 | 122.2549 | -122.4014 | -122.3282 | 122.1863 | 122.2641 | 60.4935 | 60.5118
1134.75 | 122.525 | -60.553 | 61.6837 | 0.02121 | -0.009566 | 0.010284 | 0.066601 | -0.01848 | -0.033308 | -0.026023 | 0.0025024 | -0.0093139 | 0.062481 | 0.046006 | -0.019863 | -0.009032 | -0.016742 | -0.10071 | 61.6425 | -60.64 | 61.7065 | -60.2692 | -60.6491 | -60.704 | 0.036621 | 61.615 | -60.585 | 61.8073 | -60.4111 | -60.434 | -60.3928 | -0.086975 | -0.041199 | 0.022888 | 0.28381 | -0.15106 | -0.09613 | -0.064087 | -0.009155 | -0.032043 | -0.068665 | 0.1236 | 0.14191 | 0.16022 | 0.11902 | 0.19226 | 0.15106 | 0.37079 | 122.3465 | 0.17395 | 122.3923 | 122.2824 | 122.2 | 122.1954 | 122.168 | -122.3236 | -122.2687 | 122.2595 | 122.3602 | 60.4523 | 60.5896
1136.4844 | 122.3785 | -60.585 | 61.6882 | -0.0016786 | -0.0055072 | 0.011138 | 0.066174 | -0.018908 | -0.028181 | -0.024314 | 0.0055542 | -0.0071777 | 0.063549 | 0.044938 | -0.019649 | -0.0092456 | -0.015033 | -0.09613 | 61.6791 | -60.6674 | 61.6379 | -60.3516 | -60.791 | -60.8047 | -0.068665 | 61.6333 | -60.6079 | 61.6882 | -60.5759 | -60.6308 | -60.5255 | -0.082397 | -0.009155 | -0.050354 | 0.23346 | -0.21973 | -0.20599 | -0.13733 | -0.1236 | -0.022888 | -0.054931 | 0 | 0.009155 | 0.059509 | -0.045776 | 0.082397 | -0.022888 | 0.31586 | 122.3053 | 0.032043 | 122.2961 | 122.3465 | 122.2412 | 122.2641 | 122.2183 | -122.3557 | -122.2961 | 122.2229 | 122.2733 | 60.4889 | 60.5164
1138.1875 | 122.4747 | -60.5621 | 61.6562 | 0.01358 | -0.0080706 | 0.010284 | 0.066174 | -0.015062 | -0.031599 | -0.024314 | 0.0025024 | -0.0065369 | 0.063549 | 0.047074 | -0.018794 | -0.0077502 | -0.013965 | -0.17395 | 61.6699 | -60.6583 | 61.6241 | -60.3561 | -60.7773 | -60.7819 | -0.07782 | 61.6058 | -60.6125 | 61.7706 | -60.4889 | -60.5301 | -60.434 | -0.09613 | 0.013733 | -0.032043 | 0.20599 | -0.21973 | -0.21515 | -0.1236 | -0.11902 | -0.050354 | -0.050354 | 0.11444 | 0.073242 | 0.12817 | 0.032044 | 0.17853 | 0.082398 | 0.30212 | 122.2824 | 0.1236 | 122.3831 | 122.3282 | 122.2183 | 122.2321 | 122.168 | -122.3145 | -122.2687 | 122.1863 | 122.3328 | 60.3882 | 60.4843
1139.9531 | 122.4747 | -60.4889 | 61.734 | 0.02121 | -0.0074298 | 0.011993 | 0.063397 | -0.022112 | -0.028395 | -0.026878 | 0.0055542 | -0.011023 | 0.065044 | 0.043229 | -0.019649 | -0.0094592 | -0.0208 | -0.1236 | 61.6882 | -60.5988 | 61.734 | -60.2417 | -60.6674 | -60.6812 | -0.013733 | 61.6516 | -60.5438 | 61.7889 | -60.4523 | -60.4614 | -60.4202 | -0.10986 | -0.045777 | 0 | 0.24719 | -0.19226 | -0.17853 | -0.082397 | -0.068664 | -0.054931 | -0.082398 | 0.054931 | 0.036621 | 0.068665 | 0.027466 | 0.1236 | 0.082397 | 0.35706 | 122.3328 | 0.091552 | 122.3328 | 122.287 | 122.1954 | 122.1771 | 122.1405 | -122.3328 | -122.2778 | 122.2229 | 122.2778 | 60.3653 | 60.4752
1141.7188 | 122.4197 | -60.5118 | 61.7523 | 0.01358 | -0.004439 | 0.010925 | 0.066815 | -0.016344 | -0.030317 | -0.02581 | 0.0055542 | -0.0069641 | 0.063335 | 0.036393 | -0.018367 | -0.0092456 | -0.015887 | -0.09613 | 61.7386 | -60.5804 | 61.7432 | -60.2692 | -60.6903 | -60.7178 | -0.045776 | 61.6974 | -60.5164 | 61.7569 | -60.4889 | -60.5164 | -60.4477 | -0.068664 | -0.013733 | -0.009155 | 0.24262 | -0.20599 | -0.17853 | -0.13733 | -0.10986 | -0.004577 | -0.054931 | 0.004578 | 0.022888 | 0.064087 | -0.004577 | 0.068664 | 0 | 0.31128 | 122.3236 | 0.027465 | 122.2733 | 122.319 | 122.2137 | 122.2504 | 122.2092 | -122.3328 | -122.2687 | 122.2549 | 122.2687 | 60.4156 | 60.466
1143.4375 | 122.5204 | -60.4202 | 61.8027 | 0.0059509 | -0.011061 | 0.0096429 | 0.064251 | -0.018908 | -0.031813 | -0.023674 | -0.00054937 | -0.0078185 | 0.062053 | 0.045151 | -0.018794 | -0.0092456 | -0.017169 | -0.11902 | 61.7523 | -60.5392 | 61.8073 | -60.173 | -60.5621 | -60.5759 | -0.004578 | 61.7203 | -60.4385 | 61.9125 | -60.3058 | -60.3333 | -60.2829 | -0.11902 | -0.050354 | 0.004578 | 0.24719 | -0.15564 | -0.14191 | -0.036621 | -0.022888 | -0.018311 | -0.082397 | 0.10986 | 0.11444 | 0.13733 | 0.086975 | 0.15564 | 0.10529 | 0.36621 | 122.3465 | 0.13275 | 122.3511 | 122.2916 | 122.1588 | 122.1725 | 122.1405 | -122.3419 | -122.2412 | 122.2275 | 122.3328 | 60.3012 | 60.4156
1145.1562 | 122.4747 | -60.4111 | 61.8256 | 0.01358 | -0.010207 | 0.011352 | 0.063611 | -0.01848 | -0.030104 | -0.023246 | 0.008606 | -0.0067505 | 0.063121 | 0.046219 | -0.02264 | -0.0098864 | -0.012469 | -0.10986 | 61.7752 | -60.5209 | 61.8073 | -60.1822 | -60.5713 | -60.5804 | -0.050354 | 61.7432 | -60.4523 | 61.8851 | -60.3424 | -60.3607 | -60.3012 | -0.10986 | -0.050354 | -0.018311 | 0.22888 | -0.16937 | -0.16022 | -0.059509 | -0.050354 | -0.041199 | -0.082398 | 0.059509 | 0.068665 | 0.10986 | 0.050354 | 0.15106 | 0.091553 | 0.33875 | 122.3282 | 0.10986 | 122.3373 | 122.2961 | 122.1954 | 122.1863 | 122.1542 | -122.3465 | -122.2778 | 122.2183 | 122.2961 | 60.3012 | 60.3607
1146.9219 | 122.4701 | -60.4111 | 61.821 | 0.02121 | -0.0087116 | 0.0094293 | 0.064038 | -0.01549 | -0.029249 | -0.023033 | 0.008606 | -0.0082459 | 0.062908 | 0.050706 | -0.019222 | -0.008391 | -0.015674 | -0.11444 | 61.7798 | -60.5072 | 61.8301 | -60.1501 | -60.553 | -60.5621 | -0.036621 | 61.7523 | -60.466 | 61.9034 | -60.3378 | -60.3607 | -60.2921 | -0.09613 | -0.041199 | 0.009155 | 0.26093 | -0.15106 | -0.14191 | -0.054932 | -0.045777 | -0.054931 | -0.068665 | 0.082397 | 0.073242 | 0.11902 | 0.050354 | 0.17395 | 0.10529 | 0.35706 | 122.3373 | 0.12817 | 122.3694 | 122.287 | 122.2183 | 122.1909 | 122.1634 | -122.3282 | -122.287 | 122.2412 | 122.3145 | 60.2966 | 60.3745
1148.6875 | 122.5204 | -60.2966 | 61.8896 | 0.0059509 | -0.0097796 | 0.010711 | 0.064038 | -0.020403 | -0.031599 | -0.024314 | 0.0055542 | -0.010596 | 0.062481 | 0.044938 | -0.023494 | -0.0092456 | -0.019519 | -0.082397 | 61.8347 | -60.4385 | 61.9263 | -60.054 | -60.4385 | -60.466 | 0.059509 | 61.8256 | -60.3653 | 62.0178 | -60.1959 | -60.228 | -60.1868 | -0.14191 | -0.054931 | 0.036622 | 0.24262 | -0.16937 | -0.14191 | -0.027465 | 0 | -0.068664 | -0.064086 | 0.12817 | 0.10071 | 0.10986 | 0.068665 | 0.17853 | 0.13733 | 0.38452 | 122.3648 | 0.16937 | 122.3831 | 122.2733 | 122.1909 | 122.1313 | 122.1222 | -122.3282 | -122.2549 | 122.2229 | 122.3145 | 60.2142 | 60.3561
1150.4844 | 122.5204 | -60.2737 | 61.9354 | 0.0059509 | -0.0089252 | 0.0072931 | 0.064251 | -0.017412 | -0.030531 | -0.022178 | 0.0025024 | -0.0069641 | 0.061412 | 0.048569 | -0.019435 | -0.011168 | -0.015033 | -0.041199 | 61.8805 | -60.3973 | 62.0041 | -59.9579 | -60.3561 | -60.4019 | 0.09613 | 61.8576 | -60.3104 | 62.0773 | -60.141 | -60.1593 | -60.1364 | -0.1236 | -0.054932 | 0.068664 | 0.31586 | -0.12817 | -0.082397 | -0.004578 | 0.041199 | -0.036621 | -0.07782 | 0.14191 | 0.13275 | 0.13733 | 0.11444 | 0.17395 | 0.15106 | 0.43945 | 122.4014 | 0.16937 | 122.3877 | 122.2778 | 122.168 | 122.1542 | 122.1313 | -122.3328 | -122.2458 | 122.2778 | 122.3511 | 60.2325 | 60.3699
1152.2031 | 122.5113 | -60.2737 | 61.8942 | 0.0059509 | -0.0080706 | 0.010711 | 0.064679 | -0.01784 | -0.030958 | -0.024314 | -0.00054937 | -0.0067505 | 0.062053 | 0.046647 | -0.020076 | -0.0081774 | -0.017596 | -0.091553 | 61.8805 | -60.4019 | 61.9766 | -60.0128 | -60.4523 | -60.4706 | 0.013733 | 61.8347 | -60.347 | 62.0407 | -60.2005 | -60.2417 | -60.1776 | -0.12817 | -0.013733 | 0.082398 | 0.26093 | -0.19684 | -0.17853 | -0.068664 | -0.050354 | -0.073242 | -0.059509 | 0.14648 | 0.073243 | 0.096131 | 0.032044 | 0.16937 | 0.10529 | 0.3891 | 122.3785 | 0.14648 | 122.3877 | 122.2824 | 122.1817 | 122.1542 | 122.1085 | -122.2961 | -122.2412 | 122.2504 | 122.3145 | 60.1822 | 60.2875
1153.9844 | 122.374 | -60.3241 | 61.9583 | 0.0059509 | -0.007857 | 0.0085749 | 0.065106 | -0.019762 | -0.027754 | -0.023887 | 0.0025024 | -0.0056823 | 0.062481 | 0.050492 | -0.018794 | -0.0096728 | -0.017596 | -0.16022 | 61.9629 | -60.4019 | 61.8439 | -60.1593 | -60.5667 | -60.5759 | -0.13275 | 61.9125 | -60.3333 | 61.9492 | -60.3195 | -60.3561 | -60.2509 | -0.07782 | 0.004578 | -0.11444 | 0.1648 | -0.25177 | -0.24261 | -0.17395 | -0.16479 | -0.009155 | -0.045776 | -0.009155 | 0.004578 | 0.073243 | -0.032043 | 0.082398 | -0.022888 | 0.24262 | 122.2458 | 0.013733 | 122.2824 | 122.3648 | 122.2458 | 122.287 | 122.2366 | -122.3602 | -122.2916 | 122.168 | 122.2733 | 60.1639 | 60.1913
1155.6875 | 122.5204 | -60.141 | 62.0407 | 0.01358 | -0.0089252 | 0.010284 | 0.062543 | -0.019121 | -0.032454 | -0.024955 | -0.00054937 | -0.010596 | 0.062053 | 0.045579 | -0.019863 | -0.0092456 | -0.016101 | -0.064087 | 61.9995 | -60.2509 | 62.114 | -59.8434 | -60.2509 | -60.2921 | 0.086975 | 61.9446 | -60.1776 | 62.1964 | -60.0266 | -60.0449 | -60.0128 | -0.10986 | -0.041198 | 0.073243 | 0.29755 | -0.15106 | -0.10986 | -0.041199 | 0 | -0.036621 | -0.09613 | 0.15564 | 0.11444 | 0.12817 | 0.09613 | 0.1648 | 0.13275 | 0.40741 | 122.3648 | 0.15106 | 122.374 | 122.2504 | 122.1222 | 122.1405 | 122.0856 | -122.2916 | -122.2183 | 122.2549 | 122.3373 | 60.0769 | 60.228
1157.4844 | 122.5067 | -60.1639 | 62.0178 | 0.01358 | -0.0089252 | 0.010498 | 0.064679 | -0.020403 | -0.031172 | -0.023033 | 0.0055542 | -0.0084595 | 0.063762 | 0.044724 | -0.018367 | -0.0096728 | -0.016742 | -0.09613 | 62.0041 | -60.26 | 62.0819 | -59.8846 | -60.3104 | -60.3516 | 0.009155 | 61.9354 | -60.228 | 62.1689 | -60.0677 | -60.1044 | -60.0449 | -0.096131 | -0.013733 | 0.064087 | 0.27923 | -0.18768 | -0.14648 | -0.091552 | -0.050354 | -0.064087 | -0.082397 | 0.15106 | 0.09613 | 0.11902 | 0.059509 | 0.18311 | 0.1236 | 0.37537 | 122.3419 | 0.16022 | 122.3969 | 122.2641 | 122.1634 | 122.168 | 122.0993 | -122.2778 | -122.2458 | 122.2458 | 122.3328 | 60.0677 | 60.173
1159.2031 | 122.3831 | -60.1181 | 62.1552 | 0.0059509 | -0.0048664 | 0.0092157 | 0.066174 | -0.019549 | -0.030317 | -0.023246 | 0.0025024 | -0.0067505 | 0.064403 | 0.049424 | -0.019863 | -0.009032 | -0.01546 | -0.15564 | 62.1185 | -60.2005 | 62.0499 | -59.9487 | -60.3561 | -60.3653 | -0.14191 | 62.0956 | -60.1593 | 62.1506 | -60.1181 | -60.1593 | -60.0632 | -0.082397 | -0.036621 | -0.10528 | 0.16937 | -0.24719 | -0.23804 | -0.1648 | -0.15564 | -0.041199 | -0.059509 | -0.004577 | 0 | 0.054932 | -0.041199 | 0.096131 | 0 | 0.25177 | 122.2504 | 0.041199 | 122.3099 | 122.319 | 122.2549 | 122.2366 | 122.2137 | -122.3557 | -122.3145 | 122.168 | 122.2687 | 59.9625 | 59.9762
1160.9844 | 122.493 | -60.0403 | 62.1597 | 0.044098 | -0.0074298 | 0.0085749 | 0.063824 | -0.021898 | -0.027113 | -0.02346 | 0.008606 | -0.0078185 | 0.06483 | 0.045792 | -0.021144 | -0.0068958 | -0.018451 | -0.082397 | 62.1414 | -60.141 | 62.2421 | -59.7198 | -60.1501 | -60.1776 | 0.054932 | 62.0956 | -60.0677 | 62.3016 | -59.935 | -59.9808 | -59.9167 | -0.10071 | -0.018311 | 0.082397 | 0.32043 | -0.13733 | -0.10986 | -0.036621 | -0.009155 | -0.027466 | -0.064087 | 0.14191 | 0.10529 | 0.1236 | 0.059509 | 0.15106 | 0.086975 | 0.42114 | 122.3831 | 0.13275 | 122.3694 | 122.2824 | 122.1634 | 122.1817 | 122.1359 | -122.3007 | -122.2275 | 122.2824 | 122.3419 | 59.9579 | 60.0952
1162.75 | 122.3419 | -60.0815 | 62.2009 | -0.0016786 | -0.0072162 | 0.01007 | 0.065106 | -0.014849 | -0.029463 | -0.02111 | 0.0025024 | -0.0065369 | 0.063762 | 0.03917 | -0.019435 | -0.0086048 | -0.01546 | -0.13733 | 62.1872 | -60.1501 | 62.0956 | -59.8984 | -60.2783 | -60.3012 | -0.13733 | 62.146 | -60.1227 | 62.1552 | -60.0815 | -60.1456 | -60.0174 | -0.068664 | -0.013733 | -0.10529 | 0.18311 | -0.21973 | -0.19684 | -0.15106 | -0.12817 | -0.041199 | -0.054932 | -0.045777 | 0 | 0.064087 | -0.064087 | 0.10529 | -0.022888 | 0.25177 | 122.2458 | 0.041199 | 122.2778 | 122.3373 | 122.2687 | 122.2687 | 122.2275 | -122.3511 | -122.3236 | 122.1771 | 122.2366 | 59.9442 | 59.9442
1164.5312 | 122.4426 | -59.967 | 62.2833 | 0.01358 | -0.0082842 | 0.010711 | 0.06532 | -0.021258 | -0.029676 | -0.02581 | 0.0055542 | -0.0086731 | 0.062053 | 0.03917 | -0.018794 | -0.0094592 | -0.018664 | -0.12817 | 62.2192 | -60.0403 | 62.2787 | -59.7153 | -60.1089 | -60.1181 | -0.045776 | 62.2055 | -59.9945 | 62.3474 | -59.8801 | -59.9258 | -59.8526 | -0.073242 | -0.064087 | -0.004577 | 0.25177 | -0.15106 | -0.14191 | -0.07782 | -0.068665 | -0.027466 | -0.07782 | 0.064087 | 0.086975 | 0.11444 | 0.041199 | 0.14191 | 0.068665 | 0.32501 | 122.319 | 0.11444 | 122.3419 | 122.2595 | 122.2 | 122.1863 | 122.1725 | -122.3236 | -122.2778 | 122.2458 | 122.3145 | 59.8389 | 59.9213
1166.2656 | 122.4747 | -59.9442 | 62.2467 | 0.036468 | -0.0074298 | 0.0096429 | 0.063824 | -0.016131 | -0.028181 | -0.024742 | 0.017761 | -0.0099549 | 0.062694 | 0.046219 | -0.020503 | -0.008391 | -0.011401 | -0.11444 | 62.1643 | -60.0861 | 62.2787 | -59.6786 | -60.1135 | -60.1227 | -0.018311 | 62.1643 | -60.0174 | 62.3291 | -59.8846 | -59.9167 | -59.8618 | -0.14191 | -0.082397 | 0.032044 | 0.2655 | -0.17853 | -0.16937 | -0.036621 | -0.027465 | -0.073242 | -0.082397 | 0.082398 | 0.059509 | 0.082398 | 0.027466 | 0.15564 | 0.10071 | 0.40741 | 122.3648 | 0.13275 | 122.3465 | 122.2504 | 122.1817 | 122.1085 | 122.1085 | -122.3328 | -122.2641 | 122.2229 | 122.2733 | 59.8297 | 59.9258
1168.0469 | 122.4792 | -59.8755 | 62.352 | 0.02121 | -0.011061 | 0.010925 | 0.064251 | -0.019121 | -0.030745 | -0.021324 | 0.0025024 | -0.0069641 | 0.063121 | 0.048783 | -0.021358 | -0.0098864 | -0.011187 | -0.10071 | 62.2787 | -59.9991 | 62.3245 | -59.642 | -60.0357 | -60.0586 | -0.013733 | 62.2513 | -59.9258 | 62.4298 | -59.7885 | -59.8114 | -59.7794 | -0.1236 | -0.073242 | -0.027466 | 0.23346 | -0.18311 | -0.16022 | -0.05951 | -0.036622 | -0.050354 | -0.10071 | 0.07782 | 0.086975 | 0.09613 | 0.064087 | 0.14648 | 0.11444 | 0.35706 | 122.3236 | 0.13733 | 122.3557 | 122.2778 | 122.1771 | 122.1542 | 122.1268 | -122.3511 | -122.2778 | 122.2 | 122.3053 | 59.7748 | 59.8618
1169.7656 | 122.5204 | -59.8251 | 62.3795 | 0.0059509 | -0.008498 | 0.0079339 | 0.062756 | -0.018267 | -0.031172 | -0.025169 | 0.0025024 | -0.0080321 | 0.063762 | 0.042161 | -0.020717 | -0.011595 | -0.016742 | -0.032043 | 62.3108 | -59.9213 | 62.4481 | -59.5047 | -59.9258 | -59.9579 | 0.10071 | 62.3062 | -59.848 | 62.5031 | -59.7061 | -59.7382 | -59.7107 | -0.096131 | -0.068665 | 0.068664 | 0.32043 | -0.13275 | -0.10071 | -0.036621 | -0.004577 | -0.022888 | -0.073243 | 0.1236 | 0.11902 | 0.11444 | 0.086975 | 0.13733 | 0.10986 | 0.41656 | 122.3694 | 0.14191 | 122.3511 | 122.2321 | 122.1542 | 122.1359 | 122.1313 | -122.3007 | -122.2275 | 122.2733 | 122.3282 | 59.7931 | 59.9258
1171.5 | 122.374 | -59.8251 | 62.4847 | -0.0016786 | -0.0080706 | 0.010711 | 0.065106 | -0.022753 | -0.033949 | -0.026023 | 0.014709 | -0.0067505 | 0.066112 | 0.04152 | -0.023921 | -0.010314 | -0.02016 | -0.086975 | 62.4435 | -59.9167 | 62.3932 | -59.5871 | -59.9396 | -59.9854 | -0.018311 | 62.4115 | -59.8526 | 62.4344 | -59.7931 | -59.8114 | -59.7473 | -0.091553 | -0.041199 | -0.091553 | 0.23804 | -0.16022 | -0.11444 | -0.068665 | -0.022888 | -0.027466 | -0.073242 | -0.050354 | 0.032043 | 0.07782 | 0.013733 | 0.10529 | 0.041199 | 0.32959 | 122.3099 | 0.059509 | 122.287 | 122.3602 | 122.2641 | 122.2687 | 122.2366 | -122.4014 | -122.3373 | 122.2183 | 122.2595 | 59.7382 | 59.8068
1173.2188 | 122.4609 | -59.7656 | 62.4664 | 0.02121 | -0.0093524 | 0.010925 | 0.064251 | -0.019762 | -0.031172 | -0.02111 | 0.008606 | -0.0067505 | 0.062053 | 0.048356 | -0.018367 | -0.011809 | -0.01546 | -0.11902 | 62.4115 | -59.848 | 62.4481 | -59.5276 | -59.9121 | -59.9442 | -0.050354 | 62.384 | -59.816 | 62.5168 | -59.7061 | -59.7427 | -59.6832 | -0.082397 | -0.054932 | -0.018311 | 0.23804 | -0.17853 | -0.14648 | -0.096131 | -0.064087 | -0.050354 | -0.082398 | 0.050354 | 0.059509 | 0.082397 | 0.022888 | 0.13275 | 0.073242 | 0.32043 | 122.2961 | 0.10986 | 122.3328 | 122.2595 | 122.2 | 122.1771 | 122.1497 | -122.3145 | -122.2824 | 122.2137 | 122.2824 | 59.6466 | 59.7153
1175 | 122.4243 | -59.7427 | 62.5168 | 0.02121 | -0.006789 | 0.0096429 | 0.066601 | -0.019762 | -0.031385 | -0.025169 | 0.0055542 | -0.0069641 | 0.062267 | 0.040238 | -0.018794 | -0.01245 | -0.018451 | -0.050354 | 62.4939 | -59.8251 | 62.4893 | -59.4864 | -59.8984 | -59.9167 | 0.027466 | 62.4298 | -59.7519 | 62.558 | -59.6924 | -59.7244 | -59.6603 | -0.082397 | -0.022889 | -0.027466 | 0.25635 | -0.17395 | -0.15564 | -0.091553 | -0.073242 | -0.009155 | -0.086975 | 0.041198 | 0.050354 | 0.082398 | 0.018311 | 0.091553 | 0.027466 | 0.33874 | 122.3145 | 0.059509 | 122.3099 | 122.319 | 122.1817 | 122.2366 | 122.1725 | -122.3419 | -122.2687 | 122.2321 | 122.3007 | 59.6924 | 59.7702
1176.7656 | 122.4014 | -59.6466 | 62.6221 | -0.0016786 | -0.0065754 | 0.0081477 | 0.066174 | -0.016771 | -0.031599 | -0.022392 | -0.00054937 | -0.0082459 | 0.064403 | 0.04686 | -0.021785 | -0.010314 | -0.017596 | -0.032043 | 62.5397 | -59.7427 | 62.5809 | -59.3765 | -59.761 | -59.816 | 0.018311 | 62.5122 | -59.7061 | 62.6083 | -59.5917 | -59.6375 | -59.5825 | -0.096131 | -0.082397 | -0.041198 | 0.27008 | -0.16937 | -0.11444 | -0.073242 | -0.01831 | -0.05951 | -0.10986 | -0.013733 | 0.054931 | 0.064086 | 0.009155 | 0.1236 | 0.068665 | 0.36621 | 122.3236 | 0.11444 | 122.3145 | 122.2824 | 122.2183 | 122.1863 | 122.1588 | -122.3648 | -122.3282 | 122.2275 | 122.2549 | 59.6146 | 59.6649
1178.5469 | 122.4518 | -59.5963 | 62.5992 | 0.01358 | -0.0072162 | 0.0087885 | 0.066601 | -0.019335 | -0.027754 | -0.023246 | 0.011658 | -0.0076049 | 0.062481 | 0.046647 | -0.018367 | -0.010955 | -0.014178 | -0.11902 | 62.5488 | -59.7107 | 62.5946 | -59.3674 | -59.7702 | -59.7794 | -0.045776 | 62.5214 | -59.6603 | 62.6953 | -59.5505 | -59.5779 | -59.5047 | -0.11444 | -0.050354 | -0.004578 | 0.22888 | -0.18311 | -0.17395 | -0.068665 | -0.05951 | -0.064087 | -0.07782 | 0.09613 | 0.045776 | 0.091552 | 0.01831 | 0.15564 | 0.082397 | 0.34332 | 122.3053 | 0.10986 | 122.3557 | 122.2595 | 122.1817 | 122.1451 | 122.1176 | -122.3099 | -122.2595 | 122.1909 | 122.2916 | 59.4772 | 59.5505
1180.2656 | 122.3648 | -59.5963 | 62.6816 | 0.0059509 | -0.0065754 | 0.011779 | 0.067456 | -0.016985 | -0.031599 | -0.022819 | 0.0055542 | -0.0069641 | 0.062267 | 0.043015 | -0.017726 | -0.0096728 | -0.014605 | -0.10986 | 62.6678 | -59.6512 | 62.6038 | -59.4131 | -59.8022 | -59.8343 | -0.10071 | 62.6221 | -59.6008 | 62.6541 | -59.5825 | -59.6283 | -59.5413 | -0.054932 | -0.013733 | -0.07782 | 0.1831 | -0.23804 | -0.20599 | -0.18311 | -0.15106 | -0.004578 | -0.05951 | -0.027466 | 0.013732 | 0.054931 | -0.032044 | 0.059509 | -0.027466 | 0.23804 | 122.2549 | 0.01831 | 122.2549 | 122.319 | 122.2229 | 122.2641 | 122.2183 | -122.3328 | -122.2824 | 122.2 | 122.2504 | 59.4864 | 59.4955
1182.0469 | 122.4472 | -59.5322 | 62.6816 | 0.036468 | -0.0072162 | 0.01007 | 0.064679 | -0.016985 | -0.029249 | -0.022392 | 0.0055542 | -0.0099549 | 0.066539 | 0.047501 | -0.01794 | -0.007323 | -0.019946 | -0.1236 | 62.6587 | -59.642 | 62.6953 | -59.2667 | -59.6924 | -59.7061 | -0.013733 | 62.5809 | -59.5505 | 62.7548 | -59.491 | -59.5184 | -59.4498 | -0.10986 | -0.022889 | 0.013732 | 0.2655 | -0.17395 | -0.16022 | -0.064087 | -0.050354 | -0.01831 | -0.10071 | 0.073242 | 0.041199 | 0.082398 | 0.013733 | 0.10071 | 0.032043 | 0.37537 | 122.3373 | 0.059509 | 122.3053 | 122.3007 | 122.1313 | 122.1909 | 122.113 | -122.3236 | -122.2321 | 122.2275 | 122.287 | 59.4086 | 59.5184
1183.7344 | 122.3694 | -59.5001 | 62.7869 | -0.0016786 | -0.0048664 | 0.010498 | 0.066174 | -0.022326 | -0.031172 | -0.020683 | -0.00054937 | -0.0063233 | 0.064403 | 0.047501 | -0.019649 | -0.0092456 | -0.018664 | -0.13275 | 62.7457 | -59.6008 | 62.6907 | -59.3124 | -59.7198 | -59.7244 | -0.10071 | 62.709 | -59.5184 | 62.7548 | -59.5047 | -59.5505 | -59.4406 | -0.10071 | -0.041198 | -0.09613 | 0.18768 | -0.2243 | -0.21973 | -0.1236 | -0.11902 | -0.018311 | -0.07782 | -0.032043 | -0.004578 | 0.059509 | -0.050354 | 0.07782 | -0.032043 | 0.28839 | 122.2916 | 0.013733 | 122.2733 | 122.3465 | 122.2275 | 122.2458 | 122.2092 | -122.3877 | -122.3053 | 122.1909 | 122.2549 | 59.3674 | 59.3994
1185.5156 | 122.5067 | -59.3079 | 62.8738 | -0.0016786 | -0.008498 | 0.01007 | 0.064679 | -0.021044 | -0.030531 | -0.022392 | -0.00054937 | -0.0095275 | 0.06419 | 0.047288 | -0.021144 | -0.010955 | -0.01546 | -0.07782 | 62.851 | -59.4177 | 62.9379 | -59.0149 | -59.4177 | -59.4635 | 0.073242 | 62.8006 | -59.3491 | 63.0341 | -59.1797 | -59.198 | -59.1797 | -0.10986 | -0.022888 | 0.064087 | 0.29297 | -0.15564 | -0.10986 | -0.045776 | 0 | -0.041199 | -0.073242 | 0.16022 | 0.12817 | 0.12817 | 0.10986 | 0.16937 | 0.15106 | 0.40283 | 122.3557 | 0.16937 | 122.3831 | 122.2687 | 122.1497 | 122.1588 | 122.1085 | -122.2916 | -122.2229 | 122.2458 | 122.3419 | 59.23 | 59.3811
1187.2344 | 122.4197 | -59.2896 | 62.9242 | 0.01358 | -0.006148 | 0.010284 | 0.067456 | -0.01848 | -0.030317 | -0.021965 | 0.008606 | -0.0073913 | 0.063976 | 0.039597 | -0.019435 | -0.010741 | -0.017596 | -0.082397 | 62.9608 | -59.3857 | 62.9379 | -59.0286 | -59.4406 | -59.4543 | 0.032043 | 62.8967 | -59.3079 | 63.002 | -59.2209 | -59.2758 | -59.1843 | -0.09613 | 0.036621 | 0.013733 | 0.26093 | -0.16479 | -0.15106 | -0.068665 | -0.054932 | -0.01831 | -0.027465 | 0.07782 | 0.068665 | 0.10529 | 0.013733 | 0.1236 | 0.032043 | 0.35706 | 122.3236 | 0.086975 | 122.3099 | 122.3465 | 122.2046 | 122.2504 | 122.1863 | -122.3099 | -122.2321 | 122.2275 | 122.2916 | 59.2072 | 59.3216
1188.9531 | 122.3877 | -59.2941 | 62.9471 | 0.01358 | -0.0065754 | 0.011779 | 0.066388 | -0.016771 | -0.031813 | -0.023674 | 0.0055542 | -0.0082459 | 0.064617 | 0.043015 | -0.018794 | -0.011382 | -0.016742 | -0.19684 | 62.97 | -59.3994 | 62.8693 | -59.1339 | -59.5093 | -59.5184 | -0.11902 | 62.9059 | -59.3216 | 62.9929 | -59.2712 | -59.317 | -59.2163 | -0.10529 | 0.022888 | -0.07782 | 0.16022 | -0.22431 | -0.21515 | -0.11902 | -0.10986 | -0.027466 | -0.041199 | 0.045776 | 0.022888 | 0.077819 | -0.022889 | 0.10528 | 0.004577 | 0.2655 | 122.2687 | 0.050354 | 122.3145 | 122.3694 | 122.2275 | 122.2641 | 122.2 | -122.3465 | -122.2687 | 122.1634 | 122.287 | 59.0973 | 59.1751
1190.6719 | 122.438 | -59.1843 | 63.0341 | 0.036468 | -0.0097796 | 0.011138 | 0.064679 | -0.018694 | -0.029463 | -0.024101 | 0.011658 | -0.0086731 | 0.06419 | 0.040879 | -0.019222 | -0.0098864 | -0.014605 | -0.15564 | 63.002 | -59.2484 | 63.0615 | -58.8913 | -59.3308 | -59.3353 | 0.022888 | 62.9562 | -59.2072 | 63.1302 | -59.0836 | -59.1202 | -59.0927 | -0.064087 | -0.032044 | 0.027465 | 0.29297 | -0.15106 | -0.14648 | -0.086975 | -0.082398 | -0.022888 | -0.07782 | 0.09613 | 0.10071 | 0.091553 | 0.064087 | 0.11444 | 0.086975 | 0.35706 | 122.3099 | 0.1236 | 122.3373 | 122.2504 | 122.1634 | 122.1863 | 122.1405 | -122.2824 | -122.2412 | 122.2458 | 122.3145 | 59.0286 | 59.2072
1192.4531 | 122.4518 | -59.0836 | 63.0936 | 0.028839 | -0.0082842 | 0.010498 | 0.065533 | -0.019762 | -0.030104 | -0.023246 | 0.011658 | -0.0069641 | 0.06483 | 0.042801 | -0.018581 | -0.010527 | -0.013965 | -0.20599 | 63.089 | -59.198 | 63.1577 | -58.7952 | -59.2163 | -59.2484 | 0.032043 | 63.0524 | -59.1522 | 63.2172 | -59.0057 | -59.0332 | -58.9691 | -0.11444 | -0.004578 | 0.064087 | 0.28839 | -0.16479 | -0.13275 | -0.050354 | -0.018311 | -0.068665 | -0.041199 | 0.1236 | 0.07782 | 0.11444 | 0.050354 | 0.18311 | 0.11902 | 0.40283 | 122.3557 | 0.14648 | 122.3694 | 122.287 | 122.2046 | 122.1725 | 122.1359 | -122.2916 | -122.2458 | 122.2412 | 122.3007 | 58.8776 | 59.1156
1194.1875 | 122.438 | -59.0378 | 63.1622 | 0.02121 | -0.009566 | 0.010498 | 0.06532 | -0.02553 | -0.029676 | -0.022392 | 0.008606 | -0.0071777 | 0.065685 | 0.048356 | -0.019649 | -0.010955 | -0.015033 | -0.25177 | 63.1119 | -59.1385 | 63.1531 | -58.7997 | -59.198 | -59.2209 | -0.027466 | 63.0981 | -59.0927 | 63.2446 | -58.9828 | -59.0149 | -58.9645 | -0.10071 | -0.050354 | -0.009155 | 0.23804 | -0.1831 | -0.16022 | -0.082397 | -0.059509 | -0.054931 | -0.064086 | 0.082398 | 0.054932 | 0.073242 | 0.022888 | 0.12817 | 0.077819 | 0.33875 | 122.2916 | 0.10986 | 122.3373 | 122.2504 | 122.1909 | 122.1497 | 122.1359 | -122.3007 | -122.2549 | 122.1909 | 122.2824 | 58.786 | 59.0103
1195.9688 | 122.4976 | -58.8181 | 63.3591 | 0.0059509 | -0.0091388 | 0.0094293 | 0.064465 | -0.019762 | -0.030745 | -0.023033 | 0.0055542 | -0.0076049 | 0.066112 | 0.050706 | -0.021999 | -0.008391 | -0.018023 | -0.27924 | 63.3453 | -58.9417 | 63.3682 | -58.5892 | -58.9828 | -58.992 | 0.004578 | 63.2904 | -58.8638 | 63.4781 | -58.7311 | -58.7448 | -58.7036 | -0.1236 | -0.013733 | 0.009155 | 0.22888 | -0.17395 | -0.1648 | -0.050354 | -0.041199 | -0.045777 | -0.068665 | 0.11902 | 0.086975 | 0.11444 | 0.073242 | 0.16022 | 0.11902 | 0.35248 | 122.3099 | 0.13275 | 122.3419 | 122.287 | 122.1542 | 122.1634 | 122.1085 | -122.3007 | -122.2229 | 122.1863 | 122.2961 | 58.5388 | 58.8226
1197.7344 | 122.4152 | -58.7082 | 63.5422 | 0.02121 | -0.0057208 | 0.0098565 | 0.067456 | -0.020403 | -0.029463 | -0.020897 | 0.011658 | -0.0069641 | 0.065258 | 0.040452 | -0.020931 | -0.0098864 | -0.015246 | -0.27466 | 63.5422 | -58.8043 | 63.5147 | -58.4656 | -58.8272 | -58.8959 | 0.013733 | 63.5239 | -58.7173 | 63.588 | -58.6441 | -58.6716 | -58.5983 | -0.09613 | 0 | -0.027466 | 0.24262 | -0.18768 | -0.11902 | -0.091553 | -0.022888 | -0.009155 | -0.01831 | 0.045777 | 0.064087 | 0.10986 | 0.036621 | 0.11902 | 0.045776 | 0.33875 | 122.319 | 0.073242 | 122.3053 | 122.3465 | 122.2412 | 122.2504 | 122.2321 | -122.3465 | -122.2595 | 122.2229 | 122.2961 | 58.4335 | 58.7219
1199.4688 | 122.406 | -58.5526 | 63.6932 | 0.02121 | -0.0076434 | 0.01007 | 0.066601 | -0.015703 | -0.028608 | -0.021751 | 0.008606 | -0.0071777 | 0.063335 | 0.042161 | -0.019222 | -0.0094592 | -0.015246 | -0.32959 | 63.6932 | -58.6395 | 63.6795 | -58.3145 | -58.6945 | -58.7219 | 0.032043 | 63.6612 | -58.58 | 63.7436 | -58.4885 | -58.5251 | -58.4518 | -0.086975 | 0 | -0.013733 | 0.23804 | -0.16937 | -0.14191 | -0.082398 | -0.054932 | -0.027466 | -0.032043 | 0.050354 | 0.064087 | 0.10071 | 0.027466 | 0.12817 | 0.054932 | 0.32501 | 122.319 | 0.091553 | 122.3236 | 122.3328 | 122.2412 | 122.2458 | 122.2137 | -122.3328 | -122.2733 | 122.2321 | 122.2961 | 58.223 | 58.5846
1201.25 | 122.4518 | -58.5342 | 63.6475 | 0.01358 | -0.0076434 | 0.0087885 | 0.066174 | -0.021471 | -0.030958 | -0.021965 | 0.0025024 | -0.0078185 | 0.063335 | 0.050278 | -0.021785 | -0.0098864 | -0.018023 | -0.48523 | 63.6292 | -58.6578 | 63.6475 | -58.3054 | -58.7036 | -58.7173 | -0.022888 | 63.5971 | -58.5846 | 63.7436 | -58.4473 | -58.4793 | -58.4473 | -0.1236 | -0.018311 | 0 | 0.22888 | -0.1831 | -0.16937 | -0.059509 | -0.045776 | -0.050354 | -0.050354 | 0.09613 | 0.086975 | 0.086975 | 0.054932 | 0.13733 | 0.10529 | 0.35248 | 122.3053 | 0.13733 | 122.3282 | 122.287 | 122.1817 | 122.1634 | 122.1313 | -122.3053 | -122.2321 | 122.1817 | 122.2778 | 58.049 | 58.5114
1203.0312 | 122.3602 | -58.5022 | 63.7665 | 0.01358 | -0.0074298 | 0.0096429 | 0.064251 | -0.01549 | -0.030531 | -0.024101 | 0.0055542 | -0.0061095 | 0.063976 | 0.053055 | -0.017085 | -0.0101 | -0.017596 | -0.56305 | 63.7619 | -58.5846 | 63.6429 | -58.3603 | -58.7402 | -58.7448 | -0.1236 | 63.6932 | -58.5617 | 63.7436 | -58.5159 | -58.5434 | -58.4473 | -0.082398 | -0.004577 | -0.1236 | 0.14191 | -0.24262 | -0.23804 | -0.16022 | -0.15564 | -0.05951 | -0.073242 | -0.022888 | -0.013733 | 0.054931 | -0.041199 | 0.11444 | 0.018311 | 0.2243 | 122.2275 | 0.045777 | 122.3053 | 122.3465 | 122.2549 | 122.2641 | 122.1954 | -122.3511 | -122.3282 | 122.1451 | 122.2458 | 57.9391 | 58.3786
1204.7344 | 122.4792 | -58.4198 | 63.7527 | 0.0059509 | -0.007857 | 0.010711 | 0.06532 | -0.017412 | -0.027754 | -0.02346 | 0.0025024 | -0.0080321 | 0.064617 | 0.042161 | -0.016445 | -0.0079638 | -0.015033 | -0.67749 | 63.7711 | -58.5342 | 63.7711 | -58.2092 | -58.6075 | -58.6121 | -0.045776 | 63.6795 | -58.4564 | 63.8901 | -58.342 | -58.3832 | -58.2962 | -0.11444 | 0.01831 | 0.01831 | 0.21057 | -0.19226 | -0.18768 | -0.07782 | -0.073242 | -0.036621 | -0.073243 | 0.13733 | 0.07782 | 0.1236 | 0.036621 | 0.16022 | 0.073242 | 0.32501 | 122.3053 | 0.11444 | 122.3465 | 122.3053 | 122.1359 | 122.1909 | 122.0993 | -122.287 | -122.2092 | 122.1909 | 122.3099 | 57.7423 | 58.374
1206.5156 | 122.493 | -58.3145 | 63.8535 | 0.0059509 | -0.0080706 | 0.010925 | 0.065106 | -0.016985 | -0.030531 | -0.024742 | -0.00054937 | -0.0065369 | 0.065899 | 0.041092 | -0.019222 | -0.007323 | -0.015887 | -0.75989 | 63.8672 | -58.4335 | 63.8855 | -58.0948 | -58.5114 | -58.5251 | 0 | 63.7848 | -58.3923 | 63.9862 | -58.2413 | -58.2825 | -58.2138 | -0.11902 | 0.013732 | 0.032043 | 0.21973 | -0.21057 | -0.19684 | -0.091552 | -0.07782 | -0.07782 | -0.068665 | 0.13275 | 0.073242 | 0.10071 | 0.032043 | 0.17853 | 0.10986 | 0.33874 | 122.319 | 0.15106 | 122.3785 | 122.3007 | 122.1771 | 122.1817 | 122.0993 | -122.287 | -122.2458 | 122.2 | 122.3007 | 57.5546 | 58.3145
1208.2969 | 122.3648 | -58.2367 | 64.0411 | 0.0059509 | -0.0065754 | 0.0075067 | 0.064465 | -0.019976 | -0.030531 | -0.023674 | 0.0025024 | -0.0086731 | 0.062908 | 0.040879 | -0.024562 | -0.010955 | -0.015033 | -0.83313 | 64.0411 | -58.2916 | 63.9633 | -58.0078 | -58.3878 | -58.4152 | -0.013733 | 64.032 | -58.2596 | 64.0228 | -58.1863 | -58.2138 | -58.1543 | -0.054932 | 0 | -0.07782 | 0.22888 | -0.17853 | -0.15106 | -0.1236 | -0.09613 | -0.022889 | -0.009156 | -0.018311 | 0.050354 | 0.082397 | 0.022888 | 0.10529 | 0.045777 | 0.28381 | 122.2549 | 0.073243 | 122.2824 | 122.3328 | 122.2916 | 122.2778 | 122.2687 | -122.3328 | -122.3007 | 122.2 | 122.2595 | 57.4036 | 58.223
1210.0312 | 122.5159 | -58.1039 | 64.064 | 0.0059509 | -0.0099932 | 0.0092157 | 0.06297 | -0.023821 | -0.033522 | -0.021324 | 0.0055542 | -0.0078185 | 0.060558 | 0.045579 | -0.021144 | -0.0094592 | -0.01546 | -0.91095 | 64.0182 | -58.223 | 64.1327 | -57.7972 | -58.2138 | -58.2458 | 0.10529 | 64.0091 | -58.1451 | 64.2014 | -57.9941 | -58.0307 | -57.9987 | -0.11902 | -0.045776 | 0.068664 | 0.3067 | -0.14191 | -0.10986 | -0.022889 | 0.009155 | -0.041199 | -0.054932 | 0.13733 | 0.10986 | 0.10529 | 0.073242 | 0.14648 | 0.11444 | 0.42572 | 122.3557 | 0.15106 | 122.3465 | 122.2412 | 122.1542 | 122.1222 | 122.113 | -122.287 | -122.2092 | 122.2366 | 122.3053 | 57.193 | 58.2092
1211.7969 | 122.3602 | -58.0719 | 64.2517 | 0.02121 | -0.0082842 | 0.0075067 | 0.064465 | -0.019121 | -0.031813 | -0.024742 | 0.0025024 | -0.0073913 | 0.063121 | 0.044724 | -0.024135 | -0.012236 | -0.014392 | -1.1261 | 64.1968 | -58.1451 | 64.1235 | -57.8476 | -58.2275 | -58.2321 | -0.009155 | 64.1922 | -58.0673 | 64.183 | -58.0261 | -58.049 | -57.9987 | -0.073243 | -0.054932 | -0.12817 | 0.2243 | -0.16022 | -0.15564 | -0.086975 | -0.082397 | 0.004577 | -0.059509 | -0.068665 | 0.045776 | 0.073242 | 0.022888 | 0.068665 | 0.018311 | 0.29755 | 122.2687 | 0.041199 | 122.2504 | 122.3419 | 122.2595 | 122.2687 | 122.2641 | -122.3969 | -122.319 | 122.1954 | 122.2549 | 56.9458 | 58.0627
1213.5938 | 122.374 | -58.0307 | 64.2288 | 0.0059509 | -0.006789 | 0.01007 | 0.066815 | -0.017199 | -0.031599 | -0.024314 | 0.0055542 | -0.0088867 | 0.065044 | 0.048569 | -0.017085 | -0.009032 | -0.014605 | -1.387 | 64.2288 | -58.0994 | 64.1052 | -57.8567 | -58.2642 | -58.255 | -0.10529 | 64.1556 | -58.0536 | 64.2334 | -58.0307 | -58.0673 | -57.9529 | -0.068664 | 0 | -0.1236 | 0.17395 | -0.2243 | -0.23346 | -0.15564 | -0.16479 | -0.022888 | -0.073242 | 0.004577 | 0 | 0.07782 | -0.036621 | 0.10071 | -0.013733 | 0.24262 | 122.2046 | 0.022888 | 122.287 | 122.3282 | 122.2092 | 122.2595 | 122.1863 | -122.3282 | -122.2824 | 122.1359 | 122.2641 | 56.6437 | 57.9254
1215.3125 | 122.4197 | -57.8751 | 64.357 | 0.02121 | -0.0055072 | 0.0096429 | 0.062756 | -0.018694 | -0.033735 | -0.023674 | 0.008606 | -0.0046143 | 0.063762 | 0.043229 | -0.018367 | -0.010741 | -0.016314 | -1.4923 | 64.3341 | -57.9895 | 64.3204 | -57.637 | -58.0307 | -58.0536 | 0.032043 | 64.2883 | -57.9117 | 64.4028 | -57.8293 | -57.8659 | -57.7881 | -0.11444 | -0.022889 | -0.036621 | 0.23804 | -0.17853 | -0.15564 | -0.064087 | -0.041199 | -0.036621 | -0.068665 | 0.045776 | 0.045776 | 0.086975 | 0.009155 | 0.1236 | 0.045776 | 0.35248 | 122.3099 | 0.082397 | 122.3145 | 122.3236 | 122.2 | 122.2092 | 122.1634 | -122.3465 | -122.2687 | 122.1954 | 122.2778 | 56.3828 | 57.9071
1217.0781 | 122.406 | -57.8384 | 64.389 | 0.0059509 | -0.007857 | 0.0087885 | 0.06596 | -0.019976 | -0.027754 | -0.023887 | 0.008606 | -0.0071777 | 0.064403 | 0.044083 | -0.018367 | -0.011595 | -0.017596 | -1.7303 | 64.3936 | -57.9346 | 64.3616 | -57.5958 | -58.017 | -58.0124 | 0.027466 | 64.3158 | -57.8796 | 64.4394 | -57.7972 | -57.8247 | -57.7606 | -0.09613 | 0.004578 | -0.027466 | 0.24262 | -0.17395 | -0.17853 | -0.07782 | -0.082398 | -0.041199 | -0.073242 | 0.050354 | 0.041199 | 0.07782 | 0.013733 | 0.11902 | 0.054932 | 0.33875 | 122.2961 | 0.082398 | 122.319 | 122.3282 | 122.1954 | 122.2321 | 122.1542 | -122.3236 | -122.2687 | 122.2 | 122.2778 | 56.1081 | 57.8659
1218.8438 | 122.3557 | -57.7103 | 64.5538 | 0.0059509 | -0.0080706 | 0.0068659 | 0.063397 | -0.018053 | -0.032026 | -0.020897 | 0.014709 | -0.0071777 | 0.065471 | 0.042588 | -0.023067 | -0.012023 | -0.016101 | -1.9958 | 64.5172 | -57.8476 | 64.4257 | -57.5134 | -57.9117 | -57.9346 | -0.032043 | 64.5172 | -57.756 | 64.5264 | -57.7011 | -57.7286 | -57.6599 | -0.13733 | -0.036621 | -0.12817 | 0.19684 | -0.2243 | -0.20142 | -0.086975 | -0.064087 | -0.045776 | -0.036621 | -0.027466 | 0.009155 | 0.050354 | -0.018311 | 0.09613 | 0.027465 | 0.33417 | 122.2733 | 0.054931 | 122.2824 | 122.3648 | 122.2733 | 122.2275 | 122.2275 | -122.4014 | -122.3099 | 122.1359 | 122.2366 | 55.7144 | 57.6782
1220.5781 | 122.3785 | -57.6965 | 64.5264 | 0.0059509 | -0.0055072 | 0.0094293 | 0.065533 | -0.015062 | -0.02989 | -0.02581 | -0.00054937 | -0.0067505 | 0.062694 | 0.045579 | -0.016445 | -0.0088184 | -0.01546 | -2.33 | 64.5447 | -57.7927 | 64.4394 | -57.5089 | -57.93 | -57.9391 | -0.10071 | 64.4714 | -57.7377 | 64.5538 | -57.6828 | -57.7286 | -57.6233 | -0.096131 | 0.018311 | -0.086975 | 0.18768 | -0.24262 | -0.23346 | -0.14648 | -0.13733 | -0.041199 | -0.054931 | 0.027466 | 0.013733 | 0.073242 | -0.032044 | 0.11444 | 0.009155 | 0.28381 | 122.2321 | 0.054932 | 122.2916 | 122.3373 | 122.2092 | 122.2412 | 122.168 | -122.319 | -122.2641 | 122.1359 | 122.2504 | 55.3665 | 57.5958
1222.3594 | 122.4747 | -57.5226 | 64.6225 | 0.01358 | -0.008498 | 0.011566 | 0.062115 | -0.018908 | -0.031599 | -0.023246 | 0.0055542 | -0.0080321 | 0.063549 | 0.047501 | -0.021999 | -0.0096728 | -0.014178 | -2.4628 | 64.5859 | -57.637 | 64.7003 | -57.2205 | -57.6416 | -57.6874 | 0.10071 | 64.5676 | -57.5546 | 64.7644 | -57.431 | -57.4585 | -57.4356 | -0.11444 | -0.036622 | 0.077819 | 0.30212 | -0.1648 | -0.11902 | -0.050354 | -0.004578 | -0.032043 | -0.054932 | 0.14191 | 0.091553 | 0.086975 | 0.064087 | 0.11902 | 0.09613 | 0.41656 | 122.3373 | 0.1236 | 122.319 | 122.2229 | 122.1222 | 122.1085 | 122.0901 | -122.2595 | -122.1771 | 122.2229 | 122.287 | 55.0598 | 57.6233
1224.1406 | 122.374 | -57.5226 | 64.7461 | 0.02121 | -0.0046526 | 0.0092157 | 0.064465 | -0.021685 | -0.031813 | -0.024314 | 0.008606 | -0.0071777 | 0.065685 | 0.044083 | -0.020076 | -0.010527 | -0.016528 | -2.8244 | 64.7552 | -57.6279 | 64.6362 | -57.3166 | -57.6828 | -57.7011 | -0.036621 | 64.6774 | -57.55 | 64.7278 | -57.4905 | -57.5089 | -57.4585 | -0.10529 | 0.009155 | -0.10986 | 0.20599 | -0.17853 | -0.16022 | -0.073242 | -0.054931 | -0.027466 | -0.068665 | -0.018311 | 0.032043 | 0.064087 | 0.013733 | 0.091553 | 0.041199 | 0.31128 | 122.2641 | 0.059509 | 122.2778 | 122.3831 | 122.2275 | 122.2778 | 122.2 | -122.374 | -122.2961 | 122.1588 | 122.2504 | 54.6982 | 57.486
1225.9219 | 122.3602 | -57.4493 | 64.8056 | 0.0059509 | -0.0065754 | 0.0098565 | 0.06532 | -0.022112 | -0.030104 | -0.02346 | 0.0025024 | -0.0058959 | 0.06184 | 0.043656 | -0.018794 | -0.0079638 | -0.014392 | -3.2181 | 64.7873 | -57.518 | 64.6957 | -57.2617 | -57.6599 | -57.6874 | -0.11902 | 64.7369 | -57.4539 | 64.8193 | -57.4356 | -57.4768 | -57.3807 | -0.068664 | -0.018311 | -0.10986 | 0.18768 | -0.23804 | -0.21057 | -0.16937 | -0.14191 | -0.004577 | -0.068665 | 0.013733 | 0.013733 | 0.068665 | -0.027466 | 0.073242 | -0.022889 | 0.25635 | 122.2137 | 0.01831 | 122.2733 | 122.3053 | 122.1909 | 122.2366 | 122.1863 | -122.3236 | -122.2595 | 122.1451 | 122.2687 | 54.2313 | 57.3303
1227.7031 | 122.3877 | -56.8588 | 65.3229 | 0.01358 | -0.0055072 | 0.0085749 | 0.066388 | -0.015703 | -0.028822 | -0.023033 | 0.0025024 | -0.0071777 | 0.065685 | 0.040879 | -0.020076 | -0.010527 | -0.016955 | -3.4195 | 65.419 | -56.9275 | 65.3641 | -56.5659 | -56.9962 | -57.0236 | -0.018311 | 65.3549 | -56.8405 | 65.4648 | -56.7902 | -56.8588 | -56.8909 | -0.068664 | 0.09613 | 0.041199 | 0.29297 | -0.16479 | -0.13733 | -0.096131 | -0.068665 | 0.018311 | 0.032043 | 0.14191 | 0.068665 | -0.032043 | 0 | -0.050354 | -0.018311 | 0.36163 | 122.2916 | 0.050354 | 122.3053 | 122.3465 | 122.1954 | 122.2778 | 122.2137 | -122.2504 | -122.1634 | 122.2229 | 122.3236 | 53.4393 | 56.8405
1229.4219 | 122.3373 | -56.6711 | 65.5701 | 0.0059509 | -0.0040118 | 0.011138 | 0.066815 | -0.020189 | -0.028608 | -0.023246 | 0.0055542 | -0.0099549 | 0.065044 | 0.042801 | -0.019222 | -0.009032 | -0.017596 | -3.7628 | 65.5838 | -56.7398 | 65.4785 | -56.4697 | -56.9 | -56.9 | -0.10071 | 65.5289 | -56.6986 | 65.5563 | -56.6757 | -56.7123 | -56.6254 | -0.068664 | 0.013733 | -0.091552 | 0.20142 | -0.22888 | -0.22888 | -0.16022 | -0.16022 | -0.027465 | -0.041198 | -0.013733 | -0.004577 | 0.045777 | -0.041198 | 0.073242 | -0.013733 | 0.27008 | 122.2183 | 0.022888 | 122.2549 | 122.3236 | 122.2275 | 122.2549 | 122.2 | -122.3099 | -122.2687 | 122.1497 | 122.2275 | 52.9083 | 56.5704
1231.2188 | 122.3969 | -56.5063 | 65.744 | 0.044098 | -0.0074298 | 0.0085749 | 0.064679 | -0.02083 | -0.030745 | -0.025169 | 0.011658 | -0.0061095 | 0.065899 | 0.03917 | -0.021785 | -0.008391 | -0.013537 | -4.0054 | 65.7944 | -56.5979 | 65.6708 | -56.2775 | -56.6803 | -56.694 | -0.018311 | 65.7166 | -56.5567 | 65.7486 | -56.4606 | -56.5109 | -56.4148 | -0.091552 | 0.050354 | -0.073243 | 0.22888 | -0.18768 | -0.17395 | -0.096131 | -0.082398 | -0.050354 | -0.027466 | 0.004577 | 0.045777 | 0.091553 | -0.004577 | 0.14191 | 0.045777 | 0.32043 | 122.2687 | 0.096131 | 122.3053 | 122.3923 | 122.2733 | 122.3007 | 122.2229 | -122.3419 | -122.3007 | 122.1771 | 122.2549 | 52.5009 | 56.488
1233 | 122.5067 | -56.1493 | 66.0095 | 0.0059509 | -0.0074298 | 0.0081477 | 0.064038 | -0.019549 | -0.031813 | -0.024101 | 0.0025024 | -0.011237 | 0.062053 | 0.048356 | -0.020076 | -0.0077502 | -0.016955 | -4.2938 | 65.9958 | -56.2683 | 66.0416 | -55.838 | -56.2958 | -56.3095 | 0.09613 | 65.918 | -56.1996 | 66.1469 | -56.0394 | -56.0623 | -56.0394 | -0.11902 | -0.013732 | 0.032044 | 0.31128 | -0.16022 | -0.14648 | -0.041198 | -0.027465 | -0.050354 | -0.091552 | 0.13733 | 0.10986 | 0.10986 | 0.086975 | 0.16022 | 0.13733 | 0.4303 | 122.3099 | 0.16022 | 122.3465 | 122.2641 | 122.1176 | 122.1451 | 122.0673 | -122.2778 | -122.2092 | 122.1909 | 122.2961 | 51.8555 | 56.2454
1234.7656 | 122.3648 | -56.1081 | 66.1606 | -0.0016786 | -0.007857 | 0.0098565 | 0.066388 | -0.016985 | -0.029036 | -0.025383 | 0.0025024 | -0.0071777 | 0.060985 | 0.037888 | -0.02029 | -0.0096728 | -0.017596 | -4.7516 | 66.124 | -56.1996 | 66.0187 | -55.925 | -56.3461 | -56.3553 | -0.10986 | 66.069 | -56.1172 | 66.1148 | -56.1127 | -56.1539 | -56.0486 | -0.091553 | -0.036621 | -0.14191 | 0.1831 | -0.24719 | -0.23804 | -0.15564 | -0.14648 | -0.009156 | -0.091552 | -0.045776 | -0.004578 | 0.059509 | -0.045777 | 0.068665 | -0.036621 | 0.27466 | 122.2183 | 0.004578 | 122.2321 | 122.3236 | 122.1863 | 122.2321 | 122.1771 | -122.3602 | -122.2778 | 122.1268 | 122.2229 | 51.3565 | 55.9982
1236.5625 | 122.4289 | -56.044 | 66.1606 | 0.028839 | -0.0097796 | 0.011138 | 0.06532 | -0.019121 | -0.028822 | -0.022605 | 0.011658 | -0.0099549 | 0.063976 | 0.051133 | -0.018794 | -0.0088184 | -0.016101 | -5.0262 | 66.1469 | -56.1172 | 66.1652 | -55.7693 | -56.1905 | -56.2042 | -0.009155 | 66.1057 | -56.0486 | 66.2384 | -56.0028 | -56.0257 | -55.9525 | -0.073243 | -0.013732 | 0.004578 | 0.27466 | -0.16022 | -0.14648 | -0.086975 | -0.073242 | -0.004578 | -0.054931 | 0.07782 | 0.041198 | 0.091552 | 0.01831 | 0.09613 | 0.022888 | 0.3479 | 122.2824 | 0.045776 | 122.287 | 122.2641 | 122.1542 | 122.1909 | 122.1497 | -122.2778 | -122.2092 | 122.2092 | 122.2824 | 51.0178 | 56.0349
1238.2969 | 122.493 | -55.9845 | 66.1972 | 0.02121 | -0.008498 | 0.010925 | 0.06532 | -0.021898 | -0.029036 | -0.023246 | 0.0025024 | -0.0088867 | 0.064403 | 0.046006 | -0.016231 | -0.0077502 | -0.014819 | -5.3284 | 66.1606 | -56.0761 | 66.2109 | -55.719 | -56.1539 | -56.1722 | 0 | 66.0919 | -56.0257 | 66.3437 | -55.9158 | -55.9433 | -55.8792 | -0.091553 | -0.036622 | 0.013732 | 0.2655 | -0.18768 | -0.16937 | -0.09613 | -0.07782 | -0.041199 | -0.10529 | 0.14648 | 0.068664 | 0.10529 | 0.041199 | 0.14649 | 0.082398 | 0.35706 | 122.287 | 0.10986 | 122.3694 | 122.2366 | 122.1176 | 122.1451 | 122.0764 | -122.2733 | -122.2229 | 122.1954 | 122.3282 | 50.6561 | 55.9845
1240.0781 | 122.493 | -55.9387 | 66.2384 | 0.0059509 | -0.010421 | 0.0081477 | 0.06297 | -0.020617 | -0.031385 | -0.02346 | 0.0025024 | -0.0086731 | 0.065899 | 0.046006 | -0.020503 | -0.007323 | -0.018023 | -5.5664 | 66.2018 | -56.0349 | 66.3116 | -55.5954 | -56.0257 | -56.0486 | 0.07782 | 66.156 | -55.9799 | 66.362 | -55.8243 | -55.8655 | -55.8289 | -0.09613 | -0.036621 | 0.073243 | 0.34332 | -0.10986 | -0.086975 | -0.013733 | 0.009155 | -0.041198 | -0.082397 | 0.1236 | 0.11444 | 0.10986 | 0.073242 | 0.15106 | 0.11444 | 0.43945 | 122.3465 | 0.15564 | 122.3419 | 122.2366 | 122.1359 | 122.1405 | 122.0947 | -122.2733 | -122.2183 | 122.2504 | 122.3007 | 50.3723 | 56.0165
1241.7812 | 122.5113 | -55.9296 | 66.2704 | 0.0059509 | -0.0087116 | 0.0079339 | 0.064892 | -0.019976 | -0.031385 | -0.026023 | 0.0025024 | -0.010169 | 0.065899 | 0.04686 | -0.020076 | -0.0092456 | -0.013537 | -5.8456 | 66.2201 | -56.0303 | 66.3208 | -55.5725 | -56.0028 | -56.0394 | 0.11444 | 66.188 | -55.9433 | 66.3757 | -55.8289 | -55.8426 | -55.8151 | -0.10071 | -0.050354 | 0.050354 | 0.35705 | -0.10986 | -0.073243 | -0.009156 | 0.027465 | -0.013733 | -0.082398 | 0.10528 | 0.10071 | 0.11444 | 0.086975 | 0.12817 | 0.10071 | 0.45776 | 122.3511 | 0.11444 | 122.319 | 122.2504 | 122.1313 | 122.1497 | 122.1176 | -122.3007 | -122.2137 | 122.2504 | 122.3053 | 50.0839 | 56.044
1243.5781 | 122.3648 | -55.8563 | 66.394 | 0.02121 | -0.0087116 | 0.0079339 | 0.065533 | -0.017412 | -0.031172 | -0.024955 | 0.017761 | -0.0065369 | 0.062481 | 0.035325 | -0.020931 | -0.0088184 | -0.014819 | -6.2714 | 66.3849 | -55.9891 | 66.275 | -55.6732 | -56.0669 | -56.0761 | -0.041199 | 66.3391 | -55.9296 | 66.3483 | -55.8655 | -55.8838 | -55.8105 | -0.13275 | -0.009155 | -0.11902 | 0.18311 | -0.21973 | -0.21057 | -0.086975 | -0.07782 | -0.073242 | -0.054932 | -0.045776 | -0.009156 | 0.045776 | -0.027466 | 0.11902 | 0.045776 | 0.31586 | 122.2641 | 0.064086 | 122.2778 | 122.374 | 122.2687 | 122.2412 | 122.1954 | -122.3831 | -122.3236 | 122.1313 | 122.2046 | 49.585 | 55.8151
1245.2969 | 122.4426 | -55.8701 | 66.3345 | 0.01358 | -0.010207 | 0.0090021 | 0.064251 | -0.025103 | -0.030104 | -0.023033 | 0.0055542 | -0.0082459 | 0.062267 | 0.046006 | -0.020503 | -0.009032 | -0.012469 | -6.5598 | 66.2979 | -55.9616 | 66.3116 | -55.6183 | -56.0349 | -56.0532 | -0.054932 | 66.2613 | -55.9067 | 66.4078 | -55.806 | -55.838 | -55.7785 | -0.091553 | -0.036621 | -0.022888 | 0.25177 | -0.18311 | -0.1648 | -0.091553 | -0.073242 | -0.036621 | -0.073242 | 0.073242 | 0.064087 | 0.091553 | 0.032043 | 0.12817 | 0.068664 | 0.34332 | 122.2733 | 0.10071 | 122.3145 | 122.2595 | 122.168 | 122.168 | 122.1313 | -122.2961 | -122.2412 | 122.1817 | 122.2778 | 49.3103 | 55.8151
1247.0781 | 122.3419 | -56.044 | 66.2384 | -0.0093076 | -0.0076434 | 0.0096429 | 0.067242 | -0.016558 | -0.031599 | -0.025383 | 0.0025024 | -0.0065369 | 0.062908 | 0.040665 | -0.018154 | -0.0098864 | -0.016955 | -6.8665 | 66.2109 | -56.0989 | 66.1057 | -55.8517 | -56.2866 | -56.2592 | -0.12817 | 66.1423 | -56.0349 | 66.1835 | -56.0623 | -56.0989 | -55.9799 | -0.054932 | -0.027466 | -0.13275 | 0.19226 | -0.21515 | -0.24261 | -0.16022 | -0.18768 | 0.009155 | -0.09613 | -0.054931 | -0.018311 | 0.064087 | -0.054932 | 0.054932 | -0.064087 | 0.24719 | 122.2046 | -0.027466 | 122.2183 | 122.3099 | 122.1771 | 122.2549 | 122.1863 | -122.3373 | -122.2733 | 122.1497 | 122.2275 | 49.1776 | 55.9158
1248.7812 | 122.319 | -55.8517 | 66.3803 | -0.0016786 | -0.006148 | 0.0092157 | 0.064251 | -0.017412 | -0.029036 | -0.024955 | 0.0025024 | -0.0063233 | 0.06419 | 0.04387 | -0.019649 | -0.011809 | -0.014819 | -7.077 | 66.4124 | -55.9387 | 66.2933 | -55.6641 | -56.0852 | -56.1035 | -0.16479 | 66.3254 | -55.9158 | 66.3528 | -55.9067 | -55.9433 | -55.8609 | -0.086975 | 0.032044 | -0.086975 | 0.18768 | -0.25177 | -0.23346 | -0.16479 | -0.14648 | -0.064087 | -0.054932 | -0.027466 | -0.054931 | -0.009155 | -0.091552 | 0.054932 | -0.027465 | 0.27466 | 122.2321 | 0.009156 | 122.2687 | 122.3511 | 122.2412 | 122.2641 | 122.1771 | -122.319 | -122.2961 | 122.1451 | 122.2046 | 48.7747 | 55.687
1250.5781 | 122.4701 | -52.977 | 69.191 | -0.0016786 | -0.0087116 | 0.0075067 | 0.060406 | -0.025103 | -0.028822 | -0.026878 | 0.0025024 | -0.011878 | 0.063549 | 0.049637 | -0.02029 | -0.0098864 | -0.018237 | -6.5552 | 69.1498 | -53.0777 | 69.2551 | -52.6566 | -53.0823 | -53.1143 | 0.1236 | 69.1223 | -52.9999 | 69.31 | -52.8809 | -52.9221 | -52.89 | -0.10071 | -0.041199 | 0.064087 | 0.32044 | -0.13733 | -0.10529 | -0.036621 | -0.004577 | -0.022888 | -0.068665 | 0.11902 | 0.096131 | 0.086975 | 0.054932 | 0.10986 | 0.07782 | 0.42114 | 122.3328 | 0.11902 | 122.3099 | 122.2275 | 122.1222 | 122.1268 | 122.0993 | -122.2687 | -122.1909 | 122.2321 | 122.287 | 46.4218 | 53.1006
1252.2812 | 122.3328 | -51.9928 | 70.2942 | -0.0016786 | -0.0082842 | 0.010711 | 0.066174 | -0.019762 | -0.030104 | -0.024314 | 0.0025024 | -0.0061095 | 0.062694 | 0.042374 | -0.017726 | -0.0077502 | -0.016742 | -6.5643 | 70.2667 | -52.0386 | 70.166 | -51.8051 | -52.2263 | -52.2263 | -0.091553 | 70.2347 | -51.9974 | 70.2347 | -52.034 | -52.0706 | -51.9699 | -0.045776 | -0.027465 | -0.12817 | 0.18768 | -0.23346 | -0.23346 | -0.18768 | -0.18768 | -0.004577 | -0.059509 | -0.059509 | -0.041199 | 0.022888 | -0.07782 | 0.027465 | -0.073243 | 0.23346 | 122.2046 | -0.036622 | 122.2321 | 122.3053 | 122.2321 | 122.2595 | 122.2275 | -122.3328 | -122.2916 | 122.1588 | 122.2275 | 45.4285 | 51.9012
1254.0625 | 122.3602 | -51.2558 | 71.022 | 0.044098 | -0.006789 | 0.0098565 | 0.063824 | -0.017199 | -0.030317 | -0.024314 | 0.011658 | -0.0056823 | 0.063121 | 0.040024 | -0.021358 | -0.011168 | -0.014392 | -6.5506 | 70.9991 | -51.3565 | 70.8939 | -51.0361 | -51.4481 | -51.4618 | -0.027466 | 70.9351 | -51.2878 | 70.9534 | -51.2695 | -51.3107 | -51.2146 | -0.10071 | -0.022888 | -0.12817 | 0.21973 | -0.20599 | -0.19226 | -0.10529 | -0.091553 | -0.032044 | -0.086975 | -0.068665 | -0.013733 | 0.041198 | -0.054932 | 0.073242 | -0.022888 | 0.32043 | 122.2504 | 0.018311 | 122.2412 | 122.3557 | 122.2229 | 122.2549 | 122.1909 | -122.3785 | -122.3099 | 122.1497 | 122.2092 | 44.7052 | 51.2283
1255.8281 | 122.3328 | -49.8734 | 72.4182 | -0.0016786 | -0.0059344 | 0.0081477 | 0.064251 | -0.01784 | -0.033094 | -0.022819 | 0.0025024 | -0.0080321 | 0.06483 | 0.045151 | -0.021785 | -0.010314 | -0.013751 | -6.3812 | 72.3862 | -49.9283 | 72.3175 | -49.649 | -50.0473 | -50.0793 | 0 | 72.3312 | -49.8779 | 72.3633 | -49.8734 | -49.8962 | -49.855 | -0.054932 | -0.032044 | -0.10071 | 0.2243 | -0.20599 | -0.17395 | -0.15106 | -0.11902 | -0.004578 | -0.086975 | -0.054932 | 0 | 0.01831 | -0.022888 | 0.022888 | -0.01831 | 0.27924 | 122.2458 | 0.004578 | 122.2412 | 122.3145 | 122.2092 | 122.2595 | 122.2046 | -122.3465 | -122.2961 | 122.1909 | 122.2366 | 43.4921 | 49.8734
1257.5469 | 122.4838 | -49.4705 | 72.7112 | -0.0093076 | -0.0076434 | 0.0094293 | 0.062543 | -0.017626 | -0.031599 | -0.025383 | 0.0025024 | -0.0082459 | 0.065471 | 0.051133 | -0.021144 | -0.0086048 | -0.017596 | -6.4545 | 72.6471 | -49.5804 | 72.7249 | -49.1959 | -49.6078 | -49.6353 | 0.11444 | 72.6105 | -49.5117 | 72.8027 | -49.4156 | -49.4339 | -49.3927 | -0.10986 | -0.064087 | 0.013733 | 0.27466 | -0.16479 | -0.13733 | -0.054932 | -0.027466 | -0.041199 | -0.10071 | 0.091552 | 0.054932 | 0.07782 | 0.036621 | 0.11902 | 0.07782 | 0.38452 | 122.3053 | 0.096131 | 122.3145 | 122.2275 | 122.1222 | 122.1176 | 122.081 | -122.2916 | -122.2229 | 122.1954 | 122.2733 | 43.0161 | 49.585
1259.3125 | 122.438 | -48.4085 | 73.7869 | 0.028839 | -0.0082842 | 0.01007 | 0.062756 | -0.019335 | -0.031599 | -0.022392 | 0.0055542 | -0.0097411 | 0.061199 | 0.043015 | -0.017299 | -0.0096728 | -0.016101 | -6.3675 | 73.7228 | -48.5046 | 73.7412 | -48.2162 | -48.6191 | -48.6237 | 0.009155 | 73.7137 | -48.4543 | 73.8419 | -48.4131 | -48.4222 | -48.3719 | -0.096131 | -0.064087 | -0.045776 | 0.19226 | -0.21515 | -0.21057 | -0.11902 | -0.11444 | -0.045777 | -0.073242 | 0.054932 | -0.004578 | 0.036621 | -0.013733 | 0.082398 | 0.032044 | 0.28839 | 122.2458 | 0.041199 | 122.2961 | 122.2275 | 122.168 | 122.1313 | 122.1222 | -122.2916 | -122.2412 | 122.1497 | 122.2504 | 42.041 | 48.4177
1261.0938 | 122.3373 | -47.6028 | 74.6704 | -0.0016786 | -0.0048664 | 0.0092157 | 0.069378 | -0.018267 | -0.032454 | -0.023887 | -0.00054937 | -0.0063233 | 0.062481 | 0.044938 | -0.016658 | -0.0088184 | -0.016528 | -6.2714 | 74.6429 | -47.612 | 74.6017 | -47.3785 | -47.7951 | -47.7585 | -0.045776 | 74.6063 | -47.58 | 74.6246 | -47.6761 | -47.7081 | -47.5983 | -0.009156 | -0.027466 | -0.068664 | 0.2243 | -0.15564 | -0.19226 | -0.14648 | -0.1831 | 0.022888 | -0.064087 | -0.045776 | -0.073242 | 0.004577 | -0.10529 | -0.018311 | -0.12817 | 0.23346 | 122.2137 | -0.09613 | 122.2046 | 122.2549 | 122.1863 | 122.2458 | 122.2092 | -122.2824 | -122.2504 | 122.2046 | 122.2275 | 41.3315 | 47.5571
1262.8125 | 122.3419 | -46.5729 | 75.6775 | 0.02121 | -0.0076434 | 0.0098565 | 0.06596 | -0.017626 | -0.029036 | -0.023033 | 0.0055542 | -0.0084595 | 0.066112 | 0.044297 | -0.019863 | -0.0098864 | -0.016314 | -6.2439 | 75.6958 | -46.6553 | 75.5356 | -46.4539 | -46.843 | -46.8384 | -0.086975 | 75.6134 | -46.5637 | 75.6454 | -46.6461 | -46.6736 | -46.5683 | -0.082397 | 0.018311 | -0.14191 | 0.11902 | -0.2655 | -0.27008 | -0.18311 | -0.18768 | 0.009155 | -0.064087 | -0.032043 | -0.073242 | 0.004578 | -0.10071 | -0.004577 | -0.10986 | 0.20142 | 122.1909 | -0.082397 | 122.2092 | 122.3511 | 122.1771 | 122.2687 | 122.1863 | -122.3328 | -122.2412 | 122.1085 | 122.2183 | 40.329 | 46.4859
1264.6094 | 122.374 | -46.4264 | 75.8194 | 0.028839 | -0.00508 | 0.011352 | 0.064465 | -0.014422 | -0.030531 | -0.023674 | 0.014709 | -0.0052551 | 0.063335 | 0.04451 | -0.021144 | -0.0096728 | -0.01781 | -6.3126 | 75.8194 | -46.5408 | 75.6912 | -46.2753 | -46.6553 | -46.6736 | 0.022888 | 75.7736 | -46.4722 | 75.7828 | -46.4813 | -46.5134 | -46.4355 | -0.11444 | 0 | -0.12817 | 0.15106 | -0.24719 | -0.22888 | -0.13275 | -0.11444 | -0.045776 | -0.045776 | -0.036621 | -0.054931 | -0.009155 | -0.086975 | 0.036621 | -0.041199 | 0.2655 | 122.2321 | -0.009155 | 122.2549 | 122.3602 | 122.2458 | 122.2458 | 122.2 | -122.3602 | -122.2916 | 122.1176 | 122.2092 | 40.1138 | 46.4493
1266.3438 | 122.4472 | -45.9961 | 76.1581 | 0.01358 | -0.0070026 | 0.010284 | 0.066174 | -0.017412 | -0.031813 | -0.023246 | 0.0025024 | -0.0091003 | 0.06184 | 0.047501 | -0.016017 | -0.0088184 | -0.014392 | -6.3766 | 76.1673 | -46.0922 | 76.1719 | -45.7809 | -46.2021 | -46.225 | 0.045776 | 76.0666 | -46.019 | 76.2817 | -45.9778 | -46.0281 | -45.9457 | -0.09613 | 0.009155 | 0.013733 | 0.21515 | -0.22888 | -0.20599 | -0.13275 | -0.10986 | -0.022888 | -0.091553 | 0.1236 | 0.018311 | 0.050354 | -0.032043 | 0.073242 | -0.009155 | 0.31128 | 122.2641 | 0.041199 | 122.3007 | 122.2595 | 122.0856 | 122.1634 | 122.0627 | -122.2504 | -122.1771 | 122.168 | 122.2778 | 39.6194 | 46.0419
1268.1094 | 122.4518 | -45.3964 | 76.7899 | 0.0059509 | -0.0055072 | 0.0098565 | 0.066388 | -0.018267 | -0.029036 | -0.024955 | 0.0055542 | -0.0082459 | 0.06483 | 0.048569 | -0.01794 | -0.006682 | -0.016101 | -6.3446 | 76.8082 | -45.4971 | 76.7578 | -45.2087 | -45.639 | -45.6299 | 0.027466 | 76.712 | -45.4102 | 76.8814 | -45.3918 | -45.4376 | -45.3323 | -0.10071 | 0.018311 | -0.032044 | 0.18768 | -0.23346 | -0.24262 | -0.13275 | -0.14191 | -0.013733 | -0.07782 | 0.091553 | 0.004577 | 0.064087 | -0.041199 | 0.07782 | -0.027466 | 0.28839 | 122.2549 | 0.01831 | 122.2916 | 122.3053 | 122.1222 | 122.2046 | 122.1085 | -122.287 | -122.2 | 122.1542 | 122.2778 | 39.0518 | 45.4239
1269.7969 | 122.4655 | -45.1355 | 77.0691 | 0.01358 | -0.0057208 | 0.0092157 | 0.063611 | -0.018267 | -0.030745 | -0.024955 | -0.00054937 | -0.0091003 | 0.06419 | 0.043442 | -0.021144 | -0.0081774 | -0.014392 | -6.1981 | 77.0142 | -45.2179 | 77.0966 | -44.8517 | -45.2957 | -45.2957 | 0.28839 | 76.9592 | -45.1447 | 77.1606 | -45.0668 | -45.1126 | -45.0897 | -0.082398 | -0.054932 | 0.027466 | 0.28381 | -0.16022 | -0.16022 | -0.077819 | -0.077819 | -0.009155 | -0.10986 | 0.091553 | 0.068665 | 0.045776 | 0.022888 | 0.054931 | 0.032043 | 0.36621 | 122.3145 | 0.07782 | 122.3053 | 122.2321 | 122.1039 | 122.1497 | 122.0947 | -122.287 | -122.2137 | 122.2321 | 122.2961 | 38.9374 | 45.4239
1271.5781 | 122.4655 | -44.014 | 78.1631 | 0.01358 | -0.0082842 | 0.0081477 | 0.065106 | -0.02083 | -0.033735 | -0.022819 | 0.0025024 | -0.0084595 | 0.063549 | 0.047715 | -0.021144 | -0.0101 | -0.012042 | -6.0471 | 78.1311 | -44.1055 | 78.1906 | -43.7347 | -44.1467 | -44.1788 | 0.11902 | 78.0807 | -44.0414 | 78.2959 | -43.9453 | -43.9682 | -43.9545 | -0.091553 | -0.032043 | 0.027466 | 0.27924 | -0.1648 | -0.13275 | -0.073242 | -0.041199 | -0.027466 | -0.082397 | 0.13275 | 0.068665 | 0.059509 | 0.045776 | 0.086975 | 0.073242 | 0.37079 | 122.2961 | 0.096131 | 122.3373 | 122.2366 | 122.1222 | 122.1451 | 122.0947 | -122.2687 | -122.2046 | 122.2046 | 122.3099 | 37.9669 | 44.133
1273.3594 | 122.3419 | -43.428 | 78.8498 | 0.0059509 | -0.0065754 | 0.0085749 | 0.064251 | -0.016771 | -0.032454 | -0.028801 | 0.0025024 | -0.0086731 | 0.063549 | 0.044083 | -0.021785 | -0.011382 | -0.01781 | -6.0059 | 78.7582 | -43.4784 | 78.717 | -43.2404 | -43.6157 | -43.6478 | -0.022888 | 78.7308 | -43.4372 | 78.7445 | -43.4875 | -43.5196 | -43.4647 | -0.050354 | -0.091552 | -0.13275 | 0.18768 | -0.21973 | -0.18768 | -0.16937 | -0.13733 | -0.009155 | -0.11902 | -0.10528 | -0.059509 | -0.036621 | -0.091552 | -0.027466 | -0.082397 | 0.23804 | 122.1954 | -0.050354 | 122.1817 | 122.2366 | 122.168 | 122.1863 | 122.1588 | -122.3282 | -122.287 | 122.1451 | 122.1725 | 37.4222 | 43.4052
1275.0625 | 122.4609 | -42.9474 | 79.2709 | 0.0059509 | -0.0099932 | 0.0079339 | 0.064251 | -0.021044 | -0.030745 | -0.026664 | -0.00054937 | -0.0076049 | 0.065044 | 0.044083 | -0.019435 | -0.0098864 | -0.0084104 | -5.8823 | 79.184 | -43.0161 | 79.2572 | -42.6636 | -43.0984 | -43.1305 | 0.24719 | 79.1611 | -42.9474 | 79.3167 | -42.9153 | -42.9565 | -42.9153 | -0.068664 | -0.086975 | -0.013733 | 0.28381 | -0.18311 | -0.15106 | -0.11444 | -0.082398 | 0 | -0.10986 | 0.045776 | 0.032044 | 0.032044 | -0.009155 | 0.032044 | -0.009155 | 0.35248 | 122.2733 | 0.032044 | 122.2641 | 122.2 | 122.1085 | 122.1313 | 122.1085 | -122.287 | -122.2183 | 122.2046 | 122.2641 | 37.0651 | 43.1946
1276.8281 | 122.4609 | -43.396 | 78.7903 | 0.01358 | -0.010421 | 0.0085749 | 0.065106 | -0.018694 | -0.031385 | -0.023033 | 0.0025024 | -0.0063233 | 0.063976 | 0.047501 | -0.019222 | -0.0086048 | -0.015887 | -6.2897 | 78.7262 | -43.5104 | 78.7582 | -43.1671 | -43.5745 | -43.5791 | 0.15106 | 78.717 | -43.4372 | 78.8864 | -43.3456 | -43.3777 | -43.3411 | -0.11444 | -0.064087 | -0.032043 | 0.22888 | -0.18311 | -0.17853 | -0.068665 | -0.064087 | -0.041199 | -0.073242 | 0.096131 | 0.050354 | 0.054932 | 0.01831 | 0.096131 | 0.059509 | 0.34332 | 122.2687 | 0.091553 | 122.3236 | 122.2366 | 122.1542 | 122.1222 | 122.113 | -122.3007 | -122.2275 | 122.1542 | 122.2824 | 37.1063 | 43.5471
1278.625 | 122.4014 | -42.8375 | 79.3304 | 0.028839 | -0.0065754 | 0.0092157 | 0.067029 | -0.016131 | -0.027754 | -0.024955 | 0.011658 | -0.0076049 | 0.065471 | 0.045151 | -0.017513 | -0.0088184 | -0.017169 | -6.3217 | 79.303 | -42.9382 | 79.3304 | -42.6041 | -43.0618 | -43.0527 | 0.050354 | 79.2801 | -42.9108 | 79.3854 | -42.8879 | -42.9291 | -42.8513 | -0.10071 | -0.027465 | 0 | 0.23346 | -0.21515 | -0.22431 | -0.11444 | -0.1236 | -0.073243 | -0.050354 | 0.054932 | -0.050354 | -0.013733 | -0.091553 | 0.05951 | -0.01831 | 0.33417 | 122.2687 | 0.022889 | 122.2961 | 122.2412 | 122.1909 | 122.1405 | 122.1176 | -122.2687 | -122.2412 | 122.168 | 122.2229 | 36.5158 | 42.8879
1280.4062 | 122.4014 | -43.9362 | 78.2913 | 0.02121 | -0.006148 | 0.0087885 | 0.067456 | -0.016558 | -0.029463 | -0.025596 | 0.0055542 | -0.0065369 | 0.062908 | 0.042801 | -0.020717 | -0.0101 | -0.015246 | -6.9077 | 78.2959 | -44.0369 | 78.241 | -43.6981 | -44.1467 | -44.1696 | 0.086975 | 78.2639 | -43.9682 | 78.2959 | -43.9682 | -44.0002 | -43.9453 | -0.10071 | 0.004577 | -0.050354 | 0.23804 | -0.23346 | -0.21057 | -0.13275 | -0.10986 | -0.032044 | -0.027466 | 0.004577 | -0.032044 | -0.009155 | -0.064087 | 0.022889 | -0.032043 | 0.33874 | 122.2778 | 0 | 122.2641 | 122.3328 | 122.2321 | 122.2321 | 122.2 | -122.3282 | -122.2595 | 122.1771 | 122.2321 | 37.0285 | 44.0231
1282.125 | 122.3785 | -43.2129 | 78.9871 | 0.02121 | -0.0074298 | 0.0092157 | 0.065106 | -0.01784 | -0.030958 | -0.027092 | 0.0025024 | -0.0058959 | 0.064617 | 0.037034 | -0.021358 | -0.0094592 | -0.016955 | -6.665 | 79.1199 | -43.1351 | 78.923 | -43.0069 | -43.4372 | -43.4418 | 0.16479 | 79.01 | -43.1946 | 79.0237 | -43.2632 | -43.2587 | -43.1946 | 0.07782 | 0.13275 | -0.064087 | 0.20599 | -0.22888 | -0.2243 | -0.3067 | -0.30212 | 0.018311 | 0.022888 | 0.036621 | -0.050354 | 0.018311 | -0.045776 | 0 | -0.064087 | 0.12817 | 122.0581 | -0.068665 | 122.2183 | 122.2549 | 122.2046 | 122.3328 | 122.2229 | -122.1222 | -122.1817 | 122.1359 | 122.2366 | 36.5479 | 43.3777
1283.8906 | 122.4564 | -42.8009 | 79.3625 | 0.0059509 | -0.004439 | 0.01242 | 0.064679 | -0.021685 | -0.030104 | -0.020897 | 0.0055542 | -0.0084595 | 0.062267 | 0.04387 | -0.017085 | -0.0071094 | -0.015033 | -6.9397 | 79.3579 | -42.9062 | 79.335 | -42.5995 | -43.0389 | -43.0618 | 0.036621 | 79.2847 | -42.8558 | 79.454 | -42.8055 | -42.8375 | -42.746 | -0.10529 | -0.004578 | -0.027466 | 0.20142 | -0.26093 | -0.23804 | -0.15564 | -0.13275 | -0.054932 | -0.07782 | 0.091553 | -0.004578 | 0.054931 | -0.036621 | 0.10986 | 0.018311 | 0.3067 | 122.2412 | 0.050354 | 122.3099 | 122.2641 | 122.1405 | 122.1588 | 122.0856 | -122.2687 | -122.2183 | 122.1359 | 122.2549 | 35.8612 | 42.8375
1285.6719 | 122.3236 | -42.5583 | 79.6555 | -0.0093076 | -0.0059344 | 0.010284 | 0.067029 | -0.015703 | -0.030104 | -0.022605 | 0.0025024 | -0.0067505 | 0.063335 | 0.042801 | -0.021358 | -0.007323 | -0.017596 | -6.9122 | 79.6692 | -42.627 | 79.5593 | -42.3843 | -42.8329 | -42.8558 | -0.041199 | 79.6005 | -42.5949 | 79.6097 | -42.6819 | -42.7322 | -42.627 | -0.068664 | 0.013732 | -0.096131 | 0.17395 | -0.29755 | -0.27466 | -0.22888 | -0.20599 | -0.036621 | -0.054932 | -0.045777 | -0.1236 | -0.068664 | -0.17395 | -0.032043 | -0.13733 | 0.24262 | 122.1863 | -0.086975 | 122.2046 | 122.2961 | 122.1954 | 122.2275 | 122.1588 | -122.2824 | -122.2504 | 122.1176 | 122.168 | 35.6461 | 42.5171
1287.4062 | 122.3236 | -42.2928 | 79.9622 | 0.0059509 | -0.0070026 | 0.0094293 | 0.067029 | -0.019335 | -0.030958 | -0.024528 | -0.00054937 | -0.0061095 | 0.065044 | 0.040665 | -0.021144 | -0.0068958 | -0.016742 | -6.9489 | 79.9255 | -42.3981 | 79.7882 | -42.1738 | -42.5949 | -42.6041 | -0.11902 | 79.8569 | -42.3203 | 79.8798 | -42.3843 | -42.4347 | -42.334 | -0.10529 | -0.036621 | -0.17395 | 0.11902 | -0.31128 | -0.30212 | -0.20599 | -0.19684 | -0.027465 | -0.10529 | -0.082397 | -0.091552 | -0.041198 | -0.14191 | -0.013733 | -0.11444 | 0.2243 | 122.1863 | -0.064087 | 122.2 | 122.3236 | 122.1771 | 122.2183 | 122.1497 | -122.3602 | -122.2824 | 122.081 | 122.1725 | 35.3439 | 42.1738
1289.1875 | 122.3007 | -41.8442 | 80.4199 | -0.0016786 | -0.0063616 | 0.0090021 | 0.06596 | -0.01549 | -0.030104 | -0.02346 | -0.00054937 | -0.0065369 | 0.062267 | 0.036179 | -0.020076 | -0.0077502 | -0.015033 | -6.8481 | 80.4382 | -41.8991 | 80.2368 | -41.684 | -42.128 | -42.1188 | -0.091553 | 80.3421 | -41.8533 | 80.3329 | -41.954 | -41.9861 | -41.8854 | -0.054932 | 0.01831 | -0.18311 | 0.16022 | -0.27466 | -0.28381 | -0.21973 | -0.22888 | -0.009156 | -0.07782 | -0.086975 | -0.10986 | -0.041199 | -0.14191 | -0.032043 | -0.13275 | 0.21515 | 122.1359 | -0.10071 | 122.1863 | 122.3373 | 122.1954 | 122.2824 | 122.1863 | -122.319 | -122.2733 | 122.081 | 122.1771 | 34.996 | 41.7526
1290.9688 | 122.319 | -41.153 | 81.134 | 0.0059509 | -0.0074298 | 0.0098565 | 0.065533 | -0.022326 | -0.030317 | -0.024528 | 0.0025024 | -0.0050415 | 0.065044 | 0.041733 | -0.019863 | -0.0092456 | -0.016742 | -6.1386 | 81.1066 | -41.2033 | 80.9555 | -41.0019 | -41.4276 | -41.4413 | -0.10529 | 81.0608 | -41.153 | 81.0242 | -41.2445 | -41.2949 | -41.1987 | -0.050354 | -0.027466 | -0.17853 | 0.15106 | -0.28839 | -0.27466 | -0.23804 | -0.2243 | 0 | -0.073242 | -0.10986 | -0.091553 | -0.045776 | -0.14191 | -0.045776 | -0.14191 | 0.20142 | 122.1588 | -0.091553 | 122.1771 | 122.3099 | 122.2137 | 122.2595 | 122.2137 | -122.3373 | -122.287 | 122.1085 | 122.1771 | 35.0143 | 41.0477
1292.6875 | 122.3785 | -41.2857 | 80.9601 | 0.02121 | -0.00508 | 0.011779 | 0.064465 | -0.017199 | -0.02989 | -0.022605 | 0.0055542 | -0.0069641 | 0.063549 | 0.043656 | -0.023921 | -0.0094592 | -0.015887 | -5.9006 | 80.9601 | -41.391 | 80.8456 | -41.0522 | -41.478 | -41.4963 | 0.073242 | 80.896 | -41.3406 | 80.9372 | -41.3132 | -41.3773 | -41.304 | -0.10529 | 0 | -0.11444 | 0.23346 | -0.21057 | -0.19226 | -0.10529 | -0.086975 | -0.054931 | -0.064087 | -0.022888 | -0.027465 | -0.01831 | -0.091552 | 0.036621 | -0.036621 | 0.33875 | 122.2366 | 0.027466 | 122.2778 | 122.3511 | 122.2366 | 122.2458 | 122.1817 | -122.3511 | -122.3007 | 122.1313 | 122.2229 | 35.3851 | 41.3589
1294.4688 | 122.4014 | -35.463 | 86.7783 | 0.0059509 | -0.0059344 | 0.01007 | 0.06062 | -0.021471 | -0.032026 | -0.026023 | 0.0025024 | -0.0082459 | 0.062908 | 0.044297 | -0.020503 | -0.010527 | -0.011187 | -3.4698 | 86.7188 | -35.5042 | 86.7416 | -35.1974 | -35.5957 | -35.6461 | 0.1236 | 86.673 | -35.463 | 86.7828 | -35.4538 | -35.495 | -35.463 | -0.041198 | -0.059509 | -0.036621 | 0.2655 | -0.1831 | -0.13275 | -0.14191 | -0.091553 | 0 | -0.10529 | 0.004578 | 0.009156 | 0 | -0.032043 | 0 | -0.032043 | 0.3067 | 122.2458 | 0.009156 | 122.2458 | 122.2229 | 122.1359 | 122.1817 | 122.1359 | -122.2824 | -122.2412 | 122.2046 | 122.2458 | 31.9931 | 35.5865
1296.2031 | 122.374 | -35.3531 | 86.8835 | 0.0059509 | -0.0074298 | 0.0096429 | 0.063183 | -0.016131 | -0.029463 | -0.02346 | 0.0025024 | -0.0088867 | 0.062481 | 0.048783 | -0.021144 | -0.0096728 | -0.016742 | -3.2593 | 86.8378 | -35.4126 | 86.8011 | -35.1151 | -35.5133 | -35.5316 | 0.10986 | 86.792 | -35.3485 | 86.8698 | -35.4034 | -35.4492 | -35.3989 | -0.05951 | -0.045776 | -0.082398 | 0.23804 | -0.17853 | -0.16022 | -0.11902 | -0.10071 | 0.004577 | -0.091553 | -0.013733 | -0.050354 | -0.045777 | -0.096131 | -0.050354 | -0.10071 | 0.29755 | 122.2137 | -0.054931 | 122.2183 | 122.2504 | 122.1405 | 122.1909 | 122.1451 | -122.2961 | -122.2321 | 122.1542 | 122.2229 | 32.0938 | 35.463
1297.9688 | 122.4426 | -35.0739 | 87.1033 | 0.0059509 | -0.0074298 | 0.0081477 | 0.062756 | -0.021258 | -0.030531 | -0.024528 | 0.0055542 | -0.0080321 | 0.062694 | 0.038956 | -0.019649 | -0.0081774 | -0.018237 | -3.0899 | 87.0666 | -35.1562 | 87.0804 | -34.8312 | -35.2615 | -35.2707 | 0.16022 | 87.0392 | -35.1334 | 87.1445 | -35.0784 | -35.1379 | -35.1059 | -0.082397 | -0.036621 | -0.022888 | 0.24262 | -0.19684 | -0.18768 | -0.11444 | -0.10529 | -0.059509 | -0.064086 | 0.041199 | -0.004577 | -0.032043 | -0.064086 | 0.027466 | -0.004577 | 0.32501 | 122.2366 | 0.054932 | 122.2778 | 122.2229 | 122.1725 | 122.1405 | 122.113 | -122.2595 | -122.2366 | 122.1542 | 122.2183 | 31.9839 | 35.2341
1299.6719 | 122.4152 | -34.8267 | 87.3734 | 0.0059509 | -0.009566 | 0.01007 | 0.064465 | -0.020403 | -0.032667 | -0.024742 | -0.00054937 | -0.0080321 | 0.063121 | 0.040879 | -0.020076 | -0.0101 | -0.019305 | -2.8564 | 87.3322 | -34.9136 | 87.3276 | -34.5932 | -35.0006 | -35.0372 | 0.13733 | 87.2818 | -34.8587 | 87.3779 | -34.8495 | -34.8999 | -34.8633 | -0.086975 | -0.041199 | -0.045776 | 0.23346 | -0.21057 | -0.17395 | -0.1236 | -0.086975 | -0.032044 | -0.091553 | 0.004578 | -0.022888 | -0.036621 | -0.073242 | -0.004577 | -0.041198 | 0.32043 | 122.2412 | 0.009156 | 122.2366 | 122.2458 | 122.1405 | 122.1588 | 122.1085 | -122.287 | -122.2321 | 122.1542 | 122.2046 | 31.9702 | 34.964
1301.4688 | 122.3328 | -34.584 | 87.6663 | 0.036468 | -0.0052936 | 0.0098565 | 0.067883 | -0.017626 | -0.031385 | -0.023246 | 0.014709 | -0.0054687 | 0.062267 | 0.042161 | -0.020717 | -0.012236 | -0.016955 | -2.8519 | 87.6434 | -34.671 | 87.4924 | -34.465 | -34.8221 | -34.8587 | 0.050354 | 87.6022 | -34.6207 | 87.5885 | -34.7122 | -34.758 | -34.6619 | -0.086976 | -0.022888 | -0.17395 | 0.11902 | -0.27466 | -0.23804 | -0.18768 | -0.15106 | -0.036622 | -0.064087 | -0.07782 | -0.12817 | -0.07782 | -0.17395 | -0.041198 | -0.13733 | 0.20599 | 122.1634 | -0.091552 | 122.2092 | 122.3145 | 122.2229 | 122.2275 | 122.1863 | -122.3373 | -122.287 | 122.0764 | 122.1725 | 31.7322 | 34.6344
1303.1875 | 122.3282 | -33.522 | 88.7741 | 0.01358 | -0.0097796 | 0.0096429 | 0.064679 | -0.022539 | -0.032454 | -0.024742 | 0.0055542 | -0.0073913 | 0.062908 | 0.041733 | -0.02029 | -0.011168 | -0.016528 | -2.2156 | 88.7146 | -33.5999 | 88.5635 | -33.3847 | -33.7646 | -33.7646 | 0.018311 | 88.6917 | -33.5358 | 88.6414 | -33.6227 | -33.6548 | -33.6044 | -0.07782 | -0.059509 | -0.21057 | 0.13733 | -0.24261 | -0.24261 | -0.16479 | -0.16479 | -0.013733 | -0.082398 | -0.13275 | -0.10071 | -0.082397 | -0.13275 | -0.068664 | -0.11902 | 0.21515 | 122.1634 | -0.086975 | 122.1771 | 122.3145 | 122.2275 | 122.2366 | 122.2137 | -122.374 | -122.3099 | 122.0856 | 122.1634 | 31.3065 | 33.5403
1304.9531 | 122.4518 | -32.9453 | 89.2227 | 0.01358 | -0.006789 | 0.0090021 | 0.064038 | -0.019976 | -0.030745 | -0.026023 | -0.00054937 | -0.0084595 | 0.062267 | 0.046006 | -0.020503 | -0.0086048 | -0.019091 | -1.9638 | 89.1953 | -33.0322 | 89.209 | -32.7026 | -33.1055 | -33.1146 | 0.1831 | 89.122 | -32.9636 | 89.3051 | -32.9498 | -33.0093 | -32.9727 | -0.086976 | -0.027466 | -0.013733 | 0.24261 | -0.16937 | -0.16022 | -0.082397 | -0.073242 | -0.018311 | -0.10071 | 0.082398 | -0.004578 | -0.027466 | -0.064087 | -0.009155 | -0.045776 | 0.32959 | 122.2412 | 0.013733 | 122.2687 | 122.2275 | 122.0856 | 122.1405 | 122.0673 | -122.2549 | -122.1863 | 122.1542 | 122.2504 | 30.9814 | 33.1284
1306.7344 | 122.4106 | -33.3252 | 88.8657 | 0.028839 | -0.0059344 | 0.011352 | 0.066815 | -0.016558 | -0.029463 | -0.022605 | 0.011658 | -0.0086731 | 0.062908 | 0.050492 | -0.016658 | -0.010741 | -0.016314 | -1.9821 | 88.8565 | -33.4076 | 88.8474 | -33.078 | -33.5083 | -33.5175 | 0.09613 | 88.7878 | -33.3572 | 88.9069 | -33.3755 | -33.4305 | -33.3572 | -0.082398 | -0.009156 | -0.018311 | 0.24719 | -0.19226 | -0.18311 | -0.10986 | -0.10071 | -0.032044 | -0.07782 | 0.041198 | -0.050354 | -0.032044 | -0.10529 | 0 | -0.073242 | 0.32959 | 122.2549 | -0.01831 | 122.2641 | 122.2641 | 122.1451 | 122.1817 | 122.113 | -122.2733 | -122.2229 | 122.1725 | 122.2321 | 31.3431 | 33.4213
1308.4531 | 122.374 | -32.8949 | 89.3417 | 0.028839 | -0.0048664 | 0.010284 | 0.066815 | -0.016558 | -0.030531 | -0.024314 | 0.0055542 | -0.0056823 | 0.065044 | 0.040024 | -0.019435 | -0.0094592 | -0.017169 | -1.6571 | 89.3555 | -32.9681 | 89.2456 | -32.7118 | -33.1146 | -33.1238 | 0.11902 | 89.2685 | -32.9041 | 89.3326 | -32.9498 | -33.0231 | -32.9407 | -0.073243 | 0.013733 | -0.096131 | 0.1831 | -0.22888 | -0.21973 | -0.15564 | -0.14648 | -0.009156 | -0.073242 | -0.009155 | -0.054932 | -0.045777 | -0.12817 | -0.036621 | -0.11902 | 0.25635 | 122.2137 | -0.045776 | 122.2366 | 122.3236 | 122.1725 | 122.2504 | 122.1634 | -122.3099 | -122.2458 | 122.1405 | 122.2275 | 31.2378 | 33.0139
1310.2344 | 122.4197 | -32.9544 | 89.2456 | 0.036468 | -0.0042254 | 0.010925 | 0.064892 | -0.01784 | -0.028181 | -0.021751 | 0.011658 | -0.0078185 | 0.063976 | 0.046219 | -0.017085 | -0.010527 | -0.01546 | -1.6434 | 89.2776 | -32.959 | 89.2456 | -32.6614 | -33.0963 | -33.1055 | 0.14191 | 89.2181 | -32.9498 | 89.2181 | -33.0505 | -33.0963 | -33.0093 | -0.004577 | 0.032044 | 0 | 0.29297 | -0.15106 | -0.14191 | -0.14648 | -0.13733 | 0.004578 | -0.027465 | -0.027465 | -0.09613 | -0.054931 | -0.14191 | -0.059509 | -0.14648 | 0.29755 | 122.2046 | -0.10071 | 122.168 | 122.2366 | 122.168 | 122.2321 | 122.1725 | -122.2046 | -122.1954 | 122.2 | 122.1725 | 31.311 | 33.0963
1312.0312 | 122.4564 | -34.1309 | 88.06 | 0.01358 | -0.011489 | 0.010925 | 0.063611 | -0.019976 | -0.032667 | -0.02581 | 0.0025024 | -0.0071777 | 0.063335 | 0.043229 | -0.017726 | -0.009032 | -0.015246 | -2.3987 | 88.0005 | -34.2682 | 87.9639 | -33.9523 | -34.346 | -34.3689 | 0.064087 | 87.9456 | -34.1721 | 88.092 | -34.1492 | -34.1949 | -34.1446 | -0.13733 | -0.05951 | -0.096131 | 0.17853 | -0.23804 | -0.21515 | -0.10071 | -0.07782 | -0.041199 | -0.11444 | 0.032043 | -0.018311 | -0.013733 | -0.064087 | 0.027466 | -0.022888 | 0.31586 | 122.2321 | 0.022888 | 122.2641 | 122.2687 | 122.1176 | 122.1313 | 122.0764 | -122.3282 | -122.2321 | 122.0947 | 122.2229 | 31.7322 | 34.1949
1313.8125 | 122.3969 | -34.8267 | 87.3505 | 0.02121 | -0.0082842 | 0.011779 | 0.062543 | -0.018908 | -0.029676 | -0.022392 | 0.008606 | -0.0056823 | 0.064403 | 0.046219 | -0.018581 | -0.0077502 | -0.018878 | -1.9821 | 87.3459 | -34.9091 | 87.3001 | -34.639 | -35.0647 | -35.0464 | 0.027466 | 87.2955 | -34.8587 | 87.3779 | -34.9136 | -34.9503 | -34.8816 | -0.082398 | -0.004578 | -0.050354 | 0.18768 | -0.21973 | -0.23804 | -0.13733 | -0.15564 | -0.032044 | -0.054932 | 0.027466 | -0.086975 | -0.054932 | -0.1236 | -0.022888 | -0.091552 | 0.27008 | 122.2092 | -0.054931 | 122.2366 | 122.2549 | 122.1542 | 122.1725 | 122.1222 | -122.2595 | -122.2092 | 122.1268 | 122.2046 | 32.8445 | 34.8541
1315.6094 | 122.2961 | -34.8083 | 87.4283 | 0.0059509 | -0.0048664 | 0.0087885 | 0.066388 | -0.023394 | -0.029249 | -0.023246 | 0.0055542 | -0.0048279 | 0.063121 | 0.037247 | -0.018794 | -0.0088184 | -0.02315 | -1.9363 | 87.4374 | -34.8724 | 87.2498 | -34.6985 | -35.1196 | -35.1288 | -0.041199 | 87.3871 | -34.8587 | 87.3367 | -34.9686 | -35.0143 | -34.8953 | -0.064087 | 0.009155 | -0.17853 | 0.10986 | -0.32043 | -0.31128 | -0.25635 | -0.24719 | -0.050354 | -0.041199 | -0.091553 | -0.16022 | -0.086975 | -0.20599 | -0.036621 | -0.15564 | 0.17395 | 122.1222 | -0.10986 | 122.1954 | 122.3099 | 122.2458 | 122.2458 | 122.1954 | -122.3007 | -122.287 | 122.0581 | 122.1451 | 32.872 | 34.7672
1317.3281 | 122.3648 | -34.0576 | 88.147 | 0.0059509 | -0.0087116 | 0.0081477 | 0.063397 | -0.022326 | -0.031813 | -0.020469 | 0.0055542 | -0.0065369 | 0.063335 | 0.040238 | -0.019863 | -0.010741 | -0.012256 | -1.4053 | 88.147 | -34.1125 | 88.1287 | -33.7875 | -34.1904 | -34.2316 | 0.086975 | 88.1104 | -34.0805 | 88.1424 | -34.1263 | -34.1675 | -34.0805 | -0.054932 | 0 | -0.018311 | 0.27008 | -0.17395 | -0.13275 | -0.11902 | -0.07782 | -0.022888 | -0.036621 | -0.004578 | -0.068665 | -0.022888 | -0.10986 | 0 | -0.086975 | 0.32501 | 122.2412 | -0.045777 | 122.2229 | 122.2595 | 122.1909 | 122.2046 | 122.168 | -122.2595 | -122.2275 | 122.1863 | 122.2 | 32.6523 | 34.1446
1319.0938 | 122.4609 | -34.2453 | 87.9272 | 0.0059509 | -0.0055072 | 0.0085749 | 0.067456 | -0.019335 | -0.030317 | -0.024955 | -0.00054937 | -0.0065369 | 0.063335 | 0.038315 | -0.013668 | -0.0096728 | -0.016314 | -1.5839 | 87.9044 | -34.3323 | 87.9044 | -33.9935 | -34.4559 | -34.4604 | 0.073242 | 87.8586 | -34.2773 | 88.0005 | -34.2819 | -34.3277 | -34.2407 | -0.086975 | -0.022888 | -0.022888 | 0.25177 | -0.21515 | -0.21057 | -0.12817 | -0.1236 | -0.032044 | -0.068664 | 0.073242 | -0.036621 | 0.004577 | -0.082398 | 0.036621 | -0.050354 | 0.33875 | 122.2366 | -0.004577 | 122.2778 | 122.2366 | 122.1359 | 122.1497 | 122.1039 | -122.2595 | -122.2046 | 122.1497 | 122.2458 | 32.6614 | 34.3185
1320.8594 | 122.4243 | -33.9844 | 88.1927 | 0.01358 | -0.006148 | 0.010925 | 0.063397 | -0.020617 | -0.03224 | -0.022819 | 0.0025024 | -0.0086731 | 0.066539 | 0.041947 | -0.02264 | -0.010314 | -0.01546 | -1.9135 | 88.2065 | -34.0805 | 88.1195 | -33.7967 | -34.1995 | -34.2178 | 0.036621 | 88.1058 | -34.021 | 88.2065 | -34.0576 | -34.0851 | -34.021 | -0.09613 | 0.013733 | -0.073242 | 0.18768 | -0.23346 | -0.21515 | -0.13733 | -0.11902 | -0.036621 | -0.086975 | 0.013733 | -0.073242 | -0.036621 | -0.10071 | 0 | -0.064087 | 0.28381 | 122.2 | -0.036621 | 122.2275 | 122.287 | 122.1268 | 122.1909 | 122.0901 | -122.2733 | -122.2137 | 122.1039 | 122.1909 | 32.0709 | 34.021
1322.6406 | 122.3053 | -34.4879 | 87.7213 | -0.0016786 | -0.0072162 | 0.0081477 | 0.066601 | -0.02083 | -0.032454 | -0.022392 | -0.00054937 | -0.0071777 | 0.062908 | 0.036393 | -0.022853 | -0.011382 | -0.014392 | -2.2842 | 87.7945 | -34.5245 | 87.5931 | -34.2911 | -34.7076 | -34.7168 | -0.013733 | 87.7029 | -34.5016 | 87.6617 | -34.5886 | -34.6344 | -34.5474 | -0.036621 | 0.073243 | -0.12817 | 0.19684 | -0.22888 | -0.21973 | -0.19226 | -0.18311 | -0.013733 | -0.01831 | -0.059509 | -0.10071 | -0.059509 | -0.14648 | -0.045776 | -0.13275 | 0.23346 | 122.1176 | -0.086975 | 122.1634 | 122.319 | 122.2046 | 122.2824 | 122.1909 | -122.2458 | -122.2229 | 122.081 | 122.1497 | 32.2037 | 34.4742
1324.3594 | 122.4243 | -34.0988 | 88.0234 | 0.0059509 | -0.008498 | 0.0098565 | 0.06297 | -0.019762 | -0.030104 | -0.025169 | -0.00054937 | -0.0091003 | 0.062267 | 0.046006 | -0.021144 | -0.008391 | -0.014178 | -2.4582 | 88.0234 | -34.2041 | 88.028 | -33.847 | -34.2957 | -34.3231 | 0.15106 | 87.9822 | -34.1721 | 88.1012 | -34.1309 | -34.1812 | -34.1537 | -0.10529 | 0 | 0.004578 | 0.25177 | -0.2243 | -0.19684 | -0.11902 | -0.091552 | -0.073242 | -0.041198 | 0.07782 | -0.032043 | -0.054932 | -0.082397 | 0.01831 | -0.009155 | 0.35706 | 122.2321 | 0.041199 | 122.2733 | 122.2275 | 122.1542 | 122.1222 | 122.081 | -122.2275 | -122.1954 | 122.1268 | 122.2 | 31.6406 | 34.2499
1326.125 | 122.3282 | -34.4604 | 87.7991 | 0.0059509 | -0.008498 | 0.0096429 | 0.064892 | -0.018908 | -0.030531 | -0.023887 | 0.0055542 | -0.0076049 | 0.06419 | 0.043442 | -0.023494 | -0.011382 | -0.015887 | -2.861 | 87.7625 | -34.5337 | 87.6251 | -34.2728 | -34.6848 | -34.7076 | 0.013733 | 87.7716 | -34.4971 | 87.6801 | -34.5566 | -34.6115 | -34.5291 | -0.073242 | -0.036621 | -0.17395 | 0.18768 | -0.24719 | -0.2243 | -0.17395 | -0.15106 | -0.036621 | -0.027466 | -0.11902 | -0.096131 | -0.068665 | -0.15106 | -0.032044 | -0.11444 | 0.26093 | 122.1588 | -0.05951 | 122.1771 | 122.2961 | 122.2687 | 122.2229 | 122.2321 | -122.3328 | -122.2961 | 122.0856 | 122.1405 | 31.5994 | 34.4742
1327.8281 | 122.3282 | -36.5891 | 85.6796 | 0.0059509 | -0.0063616 | 0.0096429 | 0.063824 | -0.019121 | -0.032881 | -0.021751 | 0.0025024 | -0.0080321 | 0.064403 | 0.046647 | -0.02264 | -0.011168 | -0.015033 | -4.2114 | 85.4828 | -36.7905 | 85.4507 | -36.4014 | -36.8088 | -36.8362 | -0.16479 | 85.5789 | -36.6028 | 85.5927 | -36.6577 | -36.6989 | -36.676 | -0.20142 | -0.19684 | -0.22888 | 0.18768 | -0.24719 | -0.21973 | -0.045777 | -0.018311 | -0.013733 | -0.10071 | -0.086975 | -0.068665 | -0.086975 | -0.10986 | -0.073242 | -0.096131 | 0.3891 | 122.2412 | -0.054932 | 122.1954 | 122.2733 | 122.1817 | 122.0718 | 122.168 | -122.4701 | -122.2824 | 122.0398 | 122.1817 | 32.3776 | 36.4243
1329.6094 | 122.406 | -36.5479 | 85.6384 | 0.028839 | -0.00508 | 0.011352 | 0.066174 | -0.019549 | -0.029463 | -0.024955 | 0.011658 | -0.0076049 | 0.065471 | 0.043656 | -0.016445 | -0.0101 | -0.016528 | -4.3076 | 85.6201 | -36.5982 | 85.6064 | -36.232 | -36.7401 | -36.7355 | 0.082397 | 85.556 | -36.5845 | 85.6705 | -36.5982 | -36.6348 | -36.5707 | -0.050354 | -0.018311 | -0.032044 | 0.31586 | -0.18768 | -0.19226 | -0.13733 | -0.14191 | -0.036621 | -0.082398 | 0.032043 | -0.050354 | -0.022888 | -0.086975 | 0.013733 | -0.050354 | 0.36621 | 122.2046 | -0.013733 | 122.2549 | 122.2183 | 122.1405 | 122.168 | 122.1039 | -122.2366 | -122.2229 | 122.1542 | 122.2183 | 32.2403 | 36.6302
1331.3281 | 122.319 | -37.2391 | 84.9792 | 0.02121 | -0.0052936 | 0.012207 | 0.067029 | -0.018053 | -0.029676 | -0.024101 | 0.0055542 | -0.0052551 | 0.06184 | 0.042161 | -0.017513 | -0.008391 | -0.016955 | -4.9301 | 85.0937 | -37.207 | 84.8923 | -36.969 | -37.4496 | -37.4817 | -0.013733 | 84.9289 | -37.2482 | 84.9426 | -37.3444 | -37.3764 | -37.2894 | 0.032044 | 0.11444 | -0.086975 | 0.27008 | -0.24261 | -0.21057 | -0.27466 | -0.24262 | -0.009155 | -0.050354 | -0.036621 | -0.10529 | -0.050354 | -0.13733 | -0.041199 | -0.12817 | 0.23804 | 122.0993 | -0.09613 | 122.1909 | 122.3007 | 122.1771 | 122.3328 | 122.168 | -122.1863 | -122.2275 | 122.1313 | 122.1817 | 32.309 | 37.2253
1333.125 | 122.3145 | -37.1017 | 85.1486 | -0.0016786 | -0.0065754 | 0.0083613 | 0.065747 | -0.024675 | -0.031599 | -0.027092 | 0.0025024 | -0.0084595 | 0.063335 | 0.048356 | -0.022426 | -0.0101 | -0.015887 | -5.2734 | 85.1395 | -37.1887 | 84.9655 | -36.8729 | -37.3352 | -37.3398 | -0.004578 | 85.0754 | -37.1292 | 85.0571 | -37.1841 | -37.2345 | -37.1475 | -0.086975 | -0.009156 | -0.18311 | 0.22888 | -0.23804 | -0.23346 | -0.15106 | -0.14648 | -0.027465 | -0.073243 | -0.091553 | -0.082397 | -0.045776 | -0.13275 | -0.018311 | -0.10529 | 0.31586 | 122.1542 | -0.054932 | 122.1863 | 122.3282 | 122.2046 | 122.2412 | 122.1771 | -122.3373 | -122.2778 | 122.0673 | 122.1588 | 31.8283 | 37.0972
1334.8438 | 122.3557 | -36.3831 | 85.8582 | 0.02121 | -0.0072162 | 0.01007 | 0.066388 | -0.024035 | -0.031385 | -0.023246 | 0.014709 | -0.0073913 | 0.063335 | 0.044297 | -0.020076 | -0.0092456 | -0.013965 | -5.0903 | 85.881 | -36.4197 | 85.7483 | -36.113 | -36.5662 | -36.5845 | 0.018311 | 85.8032 | -36.3831 | 85.8582 | -36.4151 | -36.4746 | -36.3876 | -0.036621 | 0.022888 | -0.10986 | 0.27008 | -0.20142 | -0.1831 | -0.1648 | -0.14648 | 0 | -0.054931 | 0 | -0.032043 | -0.004577 | -0.091552 | -0.004577 | -0.091552 | 0.3067 | 122.168 | -0.032043 | 122.2412 | 122.3007 | 122.1863 | 122.2641 | 122.1863 | -122.2778 | -122.2412 | 122.1313 | 122.2412 | 31.2927 | 36.4014
1336.625 | 122.4518 | -35.6277 | 86.5173 | 0.0059509 | -0.0089252 | 0.0090021 | 0.062329 | -0.018694 | -0.030104 | -0.024742 | -0.00054937 | -0.0078185 | 0.063976 | 0.048142 | -0.019863 | -0.0092456 | -0.015674 | -5.0629 | 86.4944 | -35.7239 | 86.5265 | -35.2936 | -35.7742 | -35.7925 | 0.16022 | 86.4487 | -35.6598 | 86.6226 | -35.6094 | -35.6461 | -35.6049 | -0.09613 | -0.022888 | 0.009155 | 0.33417 | -0.16479 | -0.14648 | -0.068665 | -0.050354 | -0.032043 | -0.068665 | 0.10529 | 0.018311 | 0.022889 | -0.01831 | 0.054932 | 0.013733 | 0.4303 | 122.2504 | 0.050354 | 122.2824 | 122.2183 | 122.1085 | 122.1222 | 122.0764 | -122.2412 | -122.1771 | 122.1542 | 122.2504 | 30.5649 | 35.788
1338.3594 | 122.3328 | -34.9045 | 87.3459 | 0.036468 | -0.006148 | 0.0092157 | 0.066601 | -0.015703 | -0.030531 | -0.023246 | 0.008606 | -0.0069641 | 0.063335 | 0.048997 | -0.018367 | -0.009032 | -0.019732 | -4.953 | 87.2864 | -35.0601 | 87.1399 | -34.7168 | -35.1288 | -35.1517 | 0.022888 | 87.1948 | -34.996 | 87.3688 | -34.8633 | -35.0143 | -34.964 | -0.15564 | -0.059509 | -0.20599 | 0.18768 | -0.24719 | -0.2243 | -0.091552 | -0.068664 | -0.091553 | -0.15106 | 0.022888 | 0.041199 | -0.059509 | -0.10986 | 0.032044 | -0.01831 | 0.34332 | 122.2 | 0.13275 | 122.3648 | 122.3465 | 122.1909 | 122.1909 | 122.0993 | -122.406 | -122.3419 | 122.0444 | 122.2733 | 29.9515 | 34.9274
1340.1406 | 122.2778 | -32.6111 | 89.653 | -0.0016786 | -0.0046526 | 0.010284 | 0.066601 | -0.02083 | -0.031813 | -0.026237 | -0.00054937 | -0.0065369 | 0.063121 | 0.041733 | -0.018367 | -0.0094592 | -0.014392 | -3.9368 | 89.6439 | -32.6569 | 89.4424 | -32.4326 | -32.8766 | -32.8903 | -0.054932 | 89.566 | -32.6111 | 89.5432 | -32.7301 | -32.7942 | -32.6797 | -0.045776 | -0.009155 | -0.21057 | 0.17853 | -0.27924 | -0.2655 | -0.23346 | -0.21973 | 0 | -0.086975 | -0.10986 | -0.11902 | -0.068665 | -0.18311 | -0.068665 | -0.18311 | 0.2243 | 122.0993 | -0.11902 | 122.1542 | 122.3007 | 122.1771 | 122.2549 | 122.1771 | -122.3099 | -122.2641 | 122.0535 | 122.1542 | 28.6743 | 32.5562
1341.8438 | 122.406 | -32.0206 | 90.1794 | 0.01358 | -0.0091388 | 0.010498 | 0.063183 | -0.018267 | -0.030317 | -0.021537 | 0.0025024 | -0.0086731 | 0.065258 | 0.044297 | -0.01794 | -0.0079638 | -0.01546 | -3.8635 | 90.1566 | -32.0618 | 90.0925 | -31.723 | -32.1854 | -32.1991 | 0.068665 | 90.0879 | -32.0343 | 90.2069 | -32.0251 | -32.0709 | -32.016 | -0.041199 | -0.022888 | -0.086975 | 0.29755 | -0.17853 | -0.16479 | -0.13733 | -0.1236 | -0.013733 | -0.091552 | 0.027466 | -0.004577 | 0.004578 | -0.050354 | 0.018311 | -0.036621 | 0.33875 | 122.1542 | 0.009156 | 122.2412 | 122.2183 | 122.1222 | 122.1771 | 122.1085 | -122.2412 | -122.2137 | 122.113 | 122.2275 | 28.157 | 32.0892
1343.625 | 122.3923 | -29.6402 | 92.5323 | 0.036468 | -0.0076434 | 0.012634 | 0.06532 | -0.015703 | -0.028822 | -0.021965 | 0.011658 | -0.0069641 | 0.062908 | 0.055619 | -0.017513 | -0.006682 | -0.015887 | -2.6917 | 92.4957 | -29.7318 | 92.4912 | -29.3289 | -29.8187 | -29.8233 | 0.23804 | 92.4362 | -29.6722 | 92.5827 | -29.686 | -29.7501 | -29.6906 | -0.091552 | -0.036621 | -0.041199 | 0.31128 | -0.1831 | -0.17853 | -0.091553 | -0.086976 | -0.032043 | -0.096131 | 0.050354 | -0.045776 | -0.050354 | -0.10986 | -0.018311 | -0.07782 | 0.40283 | 122.2229 | -0.013733 | 122.2549 | 122.2275 | 122.1085 | 122.1359 | 122.0764 | -122.2641 | -122.2046 | 122.1313 | 122.2229 | 26.9485 | 29.8782
1345.3438 | 122.4152 | -27.5116 | 94.6335 | 0.0059509 | -0.0072162 | 0.0087885 | 0.064679 | -0.019976 | -0.032454 | -0.02346 | -0.00054937 | -0.0082459 | 0.063121 | 0.049424 | -0.016231 | -0.009032 | -0.016742 | -1.6022 | 94.6381 | -27.6123 | 94.574 | -27.2415 | -27.681 | -27.713 | 0.16937 | 94.5694 | -27.5345 | 94.7021 | -27.5528 | -27.6215 | -27.5253 | -0.10071 | 0.004578 | -0.059509 | 0.27008 | -0.20142 | -0.16937 | -0.10071 | -0.068664 | -0.022888 | -0.064087 | 0.068664 | -0.041198 | -0.013733 | -0.10986 | 0.009155 | -0.086975 | 0.37079 | 122.1863 | -0.01831 | 122.2366 | 122.2504 | 122.1039 | 122.1497 | 122.081 | -122.2458 | -122.168 | 122.0856 | 122.2137 | 25.9094 | 27.681
1347.125 | 122.2916 | -25.7263 | 96.5561 | 0.02121 | -0.0063616 | 0.0094293 | 0.06532 | -0.019549 | -0.031172 | -0.024955 | 0.0025024 | -0.0061095 | 0.065899 | 0.040879 | -0.022212 | -0.010314 | -0.014392 | -0.79193 | 96.5149 | -25.7767 | 96.3364 | -25.4929 | -25.9048 | -25.9323 | 0.07782 | 96.492 | -25.7401 | 96.405 | -25.8133 | -25.882 | -25.7996 | -0.050354 | -0.041198 | -0.21973 | 0.23346 | -0.20599 | -0.17853 | -0.15564 | -0.12817 | -0.013733 | -0.064087 | -0.15106 | -0.086975 | -0.073243 | -0.15564 | -0.05951 | -0.14191 | 0.28381 | 122.113 | -0.073242 | 122.1451 | 122.2916 | 122.2321 | 122.2412 | 122.2183 | -122.3328 | -122.2961 | 122.0627 | 122.1313 | 24.9344 | 25.8041
1348.8438 | 122.3099 | -24.5636 | 97.6364 | 0.0059509 | -0.007857 | 0.0098565 | 0.063183 | -0.018908 | -0.030317 | -0.026451 | -0.00054937 | -0.0080321 | 0.062694 | 0.043229 | -0.020076 | -0.010314 | -0.014819 | -0.15106 | 97.6181 | -24.6094 | 97.5586 | -24.2386 | -24.6597 | -24.7055 | 0.11902 | 97.5632 | -24.5316 | 97.5998 | -24.6368 | -24.7009 | -24.6414 | -0.045776 | -0.018311 | -0.07782 | 0.32501 | -0.14191 | -0.09613 | -0.09613 | -0.050354 | 0.032044 | -0.073243 | -0.036622 | -0.073242 | -0.077819 | -0.13733 | -0.10986 | -0.16937 | 0.37079 | 122.168 | -0.10529 | 122.1313 | 122.2275 | 122.0947 | 122.1817 | 122.1268 | -122.2458 | -122.168 | 122.1222 | 122.1634 | 24.4125 | 24.6826
1350.6406 | 122.3648 | -27.5162 | 94.6381 | 0.028839 | -0.0074298 | 0.010284 | 0.06596 | -0.017412 | -0.028608 | -0.022392 | 0.0025024 | -0.0084595 | 0.064403 | 0.051133 | -0.017726 | -0.0077502 | -0.017169 | -2.211 | 94.6198 | -27.6169 | 94.5282 | -27.2461 | -27.7039 | -27.7496 | 0.018311 | 94.5374 | -27.5848 | 94.6152 | -27.6031 | -27.6718 | -27.6031 | -0.10071 | -0.018311 | -0.10986 | 0.27008 | -0.23346 | -0.18768 | -0.13275 | -0.086975 | -0.068665 | -0.10071 | -0.022889 | -0.086975 | -0.086975 | -0.15564 | -0.01831 | -0.086975 | 0.37079 | 122.1451 | -0.01831 | 122.2 | 122.2366 | 122.1222 | 122.1359 | 122.0535 | -122.2549 | -122.2229 | 122.0444 | 122.1313 | 25.3052 | 27.5345
1352.3594 | 122.287 | -29.0176 | 93.2236 | -0.0093076 | -0.0052936 | 0.0083613 | 0.066388 | -0.019121 | -0.031385 | -0.026451 | 0.0025024 | -0.0058959 | 0.063762 | 0.03917 | -0.019649 | -0.009032 | -0.016101 | -3.2455 | 93.251 | -29.0268 | 93.0817 | -28.7247 | -29.2145 | -29.2374 | 0.027466 | 93.1961 | -28.9948 | 93.1366 | -29.1275 | -29.2191 | -29.1046 | -0.009155 | 0.027466 | -0.14191 | 0.29297 | -0.21973 | -0.19684 | -0.21057 | -0.18768 | 0.022888 | -0.027466 | -0.086975 | -0.10986 | -0.086975 | -0.20142 | -0.10986 | -0.2243 | 0.30212 | 122.1085 | -0.13275 | 122.1313 | 122.2778 | 122.1909 | 122.2687 | 122.2137 | -122.2504 | -122.2183 | 122.0993 | 122.1542 | 25.7721 | 29.0451
1354.125 | 122.2824 | -31.2607 | 90.9348 | 0.01358 | -0.0057208 | 0.011993 | 0.067029 | -0.019762 | -0.028822 | -0.02346 | 0.008606 | -0.0067505 | 0.06483 | 0.040238 | -0.017726 | -0.0094592 | -0.014392 | -4.9026 | 90.9485 | -31.3202 | 90.802 | -30.9402 | -31.3751 | -31.3568 | 0.19226 | 90.9622 | -31.1691 | 90.8707 | -31.3751 | -31.4529 | -31.3522 | -0.059509 | 0.013733 | -0.13275 | 0.32043 | -0.096131 | -0.11444 | -0.036622 | -0.054932 | 0.091553 | 0.027466 | -0.064086 | -0.11444 | -0.091553 | -0.19226 | -0.18311 | -0.28381 | 0.37994 | 122.1222 | -0.20599 | 122.0398 | 122.2687 | 122.1313 | 122.2092 | 122.2229 | -122.2549 | -122.1039 | 122.0627 | 122.1313 | 26.358 | 31.4529
1355.8906 | 122.3785 | -54.1397 | 67.9825 | 0.02121 | -0.0082842 | 0.010925 | 0.067883 | -0.018908 | -0.027327 | -0.021751 | 0.0055542 | -0.0061095 | 0.066539 | 0.040879 | -0.020717 | -0.008391 | -0.015674 | -19.8807 | 68.042 | -54.2358 | 67.9596 | -53.6087 | -54.2587 | -54.277 | -0.18768 | 67.9596 | -54.1992 | 67.9916 | -54.1489 | -54.2175 | -54.158 | -0.096131 | 0.059509 | -0.022888 | 0.53101 | -0.13733 | -0.11902 | -0.041199 | -0.022888 | -0.05951 | -0.022888 | 0.009155 | -0.009156 | -0.018311 | -0.07782 | 0.041199 | -0.01831 | 0.62714 | 122.1954 | 0.050354 | 122.1909 | 122.2778 | 122.1588 | 122.1817 | 122.0993 | -122.2183 | -122.1817 | 122.0993 | 122.1313 | 34.259 | 53.952
1357.6094 | 122.3877 | -80.0766 | 41.9861 | 0.0059509 | -0.0089252 | 0.011352 | 0.065747 | -0.020189 | -0.029463 | -0.024314 | -0.00054937 | -0.0071777 | 0.064617 | 0.044297 | -0.017513 | -0.008391 | -0.015887 | -36.882 | 41.8991 | -80.2963 | 41.9449 | -79.3488 | -80.1636 | -80.2322 | 0.53558 | 41.9128 | -80.1682 | 42.16 | -79.8935 | -79.9347 | -79.8569 | -0.21973 | -0.086975 | -0.041199 | 0.72784 | -0.15564 | -0.086975 | 0.064087 | 0.13275 | -0.091553 | -0.073242 | 0.17395 | 0.1831 | 0.21973 | 0.14191 | 0.31128 | 0.23346 | 0.94757 | 122.2412 | 0.27466 | 122.3282 | 122.1954 | 122.081 | 121.9757 | 121.9894 | -122.2824 | -122.1542 | 122.0215 | 122.2366 | 43.1946 | 80.6122
1359.4062 | 122.287 | -45.3827 | 76.7578 | 0.0059509 | -0.0072162 | 0.011138 | 0.067456 | -0.017412 | -0.029676 | -0.023246 | 0.0055542 | -0.0061095 | 0.063335 | 0.04921 | -0.018794 | -0.0081774 | -0.014392 | -14.7446 | 76.7899 | -45.4468 | 76.6022 | -44.9982 | -45.6253 | -45.6207 | -0.082397 | 76.6754 | -45.4056 | 76.7029 | -45.5521 | -45.5475 | -45.4239 | -0.064087 | 0.032044 | -0.15564 | 0.38452 | -0.23804 | -0.24262 | -0.17395 | -0.17853 | -0.022889 | -0.082397 | -0.054931 | -0.16937 | -0.041199 | -0.1648 | -0.01831 | -0.14191 | 0.44861 | 122.0489 | -0.14648 | 122.1085 | 122.2366 | 122.081 | 122.1725 | 122.0581 | -122.2046 | -122.1634 | 121.9849 | 122.0856 | 30.6381 | 45.3003
1361.1875 | 122.287 | -105.5603 | 16.5024 | 0.036468 | -0.0059344 | 0.010711 | 0.067669 | -0.01784 | -0.028181 | -0.023033 | 0.008606 | -0.0052551 | 0.063976 | 0.041306 | -0.021785 | -0.0077502 | -0.01781 | -54.1672 | 16.5848 | -105.6473 | 16.4703 | -104.5029 | -105.4733 | -105.5832 | -0.53558 | 16.4886 | -105.661 | 16.571 | -105.2628 | -105.3131 | -105.249 | -0.086975 | 0.082398 | -0.032043 | 1.0574 | -0.022888 | 0.086975 | 0.064087 | 0.17395 | -0.10071 | -0.013733 | 0.068665 | 0.29755 | 0.31128 | 0.24719 | 0.41199 | 0.3479 | 1.1444 | 122.1176 | 0.39826 | 122.2321 | 122.2321 | 122.1497 | 122.1451 | 122.049 | -122.1497 | -122.1634 | 122.0306 | 122.1313 | 51.3931 | 105.0247
1362.9219 | 122.3236 | -114.0381 | 8.0521 | -0.0093076 | -0.0080706 | 0.012634 | 0.065106 | -0.022326 | -0.029249 | -0.021965 | 0.0055542 | -0.0091003 | 0.062694 | 0.043656 | -0.020076 | -0.0101 | -0.018023 | -60.0586 | 8.0154 | -114.0564 | 8.0612 | -112.706 | -113.7955 | -113.9008 | -0.23346 | 8.0246 | -114.0839 | 8.107 | -113.5574 | -113.6307 | -113.6032 | -0.01831 | -0.036621 | 0.009155 | 1.3321 | 0.13733 | 0.24262 | 0.15564 | 0.26093 | -0.045776 | -0.027466 | 0.054932 | 0.48065 | 0.43488 | 0.40741 | 0.48065 | 0.45319 | 1.3504 | 122.1176 | 0.52643 | 122.1909 | 122.0718 | 122.1085 | 122.0535 | 122.0627 | -122.1085 | -122.1359 | 122.0993 | 122.1451 | 53.9795 | 113.8046
1364.7031 | 122.1817 | -115.6631 | 6.4178 | 0.01358 | -0.0052936 | 0.01007 | 0.067883 | -0.020189 | -0.030531 | -0.022819 | 0.0055542 | -0.0073913 | 0.062694 | 0.046006 | -0.019649 | -0.007323 | -0.018023 | -61.8393 | 6.3766 | -115.7501 | 6.2347 | -114.5096 | -115.5991 | -115.6769 | -0.35706 | 6.4133 | -115.741 | 6.3309 | -115.361 | -115.4251 | -115.3107 | -0.086975 | -0.041199 | -0.18311 | 1.1536 | -0.013733 | 0.064087 | 0.073242 | 0.15106 | -0.07782 | -0.004578 | -0.086975 | 0.30212 | 0.35248 | 0.23804 | 0.4303 | 0.31586 | 1.2405 | 121.9849 | 0.37994 | 122.0718 | 122.1268 | 122.1542 | 122.0398 | 122.0764 | -122.168 | -122.1588 | 121.8979 | 121.994 | 53.8239 | 115.3061
1366.5 | 122.2366 | -116.3773 | 5.6625 | -0.0016786 | -0.0076434 | 0.01007 | 0.063824 | -0.01848 | -0.029676 | -0.020897 | 0.0025024 | -0.0097411 | 0.063762 | 0.046433 | -0.020931 | -0.0077502 | -0.012256 | -62.9425 | 5.5893 | -116.4413 | 5.6396 | -115.0131 | -116.1301 | -116.2537 | -0.16022 | 5.6396 | -116.3864 | 5.69 | -115.9287 | -115.9836 | -115.9424 | -0.064087 | -0.073243 | -0.022889 | 1.3641 | 0.1236 | 0.24719 | 0.18768 | 0.31128 | -0.009156 | -0.022889 | 0.027465 | 0.44861 | 0.43487 | 0.39368 | 0.44403 | 0.40283 | 1.4282 | 122.081 | 0.45776 | 122.0764 | 122.0306 | 122.0261 | 121.9666 | 122.0169 | -122.1039 | -122.049 | 122.0169 | 122.0673 | 53.4348 | 116.217
1368.2188 | 122.1313 | -116.8808 | 5.1865 | 0.01358 | -0.0082842 | 0.0083613 | 0.067456 | -0.022539 | -0.030531 | -0.021751 | 0.0025024 | -0.0082459 | 0.062694 | 0.047288 | -0.019863 | -0.0088184 | -0.015887 | -64.1556 | 5.1178 | -116.9632 | 4.9759 | -115.6311 | -116.7068 | -116.8396 | -0.28839 | 5.1498 | -116.9128 | 5.0537 | -116.5237 | -116.5924 | -116.5283 | -0.082398 | -0.068664 | -0.21057 | 1.2497 | 0.041198 | 0.17395 | 0.1236 | 0.25635 | -0.032044 | -0.036621 | -0.13275 | 0.35706 | 0.35248 | 0.28839 | 0.38452 | 0.32044 | 1.3321 | 121.9391 | 0.3891 | 121.9666 | 122.081 | 122.0627 | 121.9986 | 122.0306 | -122.1497 | -122.0993 | 121.8567 | 121.9345 | 52.7252 | 116.5924
1370 | 122.1176 | -117.0593 | 4.9805 | 0.044098 | -0.0070026 | 0.01007 | 0.067029 | -0.019762 | -0.030317 | -0.022178 | 0.008606 | -0.0067505 | 0.062694 | 0.040452 | -0.019008 | -0.0101 | -0.014605 | -64.8468 | 4.9438 | -117.1783 | 4.7882 | -115.8096 | -116.8762 | -117.0044 | -0.23346 | 4.9759 | -117.1463 | 4.8614 | -116.6931 | -116.7664 | -116.684 | -0.11902 | -0.036621 | -0.19226 | 1.2497 | 0.054931 | 0.1831 | 0.17395 | 0.30212 | -0.086975 | -0.004578 | -0.11902 | 0.36621 | 0.37537 | 0.29297 | 0.46234 | 0.37994 | 1.3687 | 121.9666 | 0.45319 | 122.0078 | 122.1222 | 122.1222 | 122.0032 | 122.0352 | -122.1588 | -122.1268 | 121.8475 | 121.9208 | 52.2125 | 116.8259
1371.7188 | 122.1451 | -116.4047 | 5.2734 | 0.036468 | -0.0074298 | 0.013916 | 0.067029 | -0.015917 | -0.028608 | -0.020683 | 0.011658 | -0.0069641 | 0.068889 | 0.053269 | -0.015804 | -0.009032 | -0.013324 | -65.1398 | 4.7928 | -117.1738 | 4.7928 | -114.6515 | -115.7822 | -115.9012 | -0.16937 | 5.7129 | -116.7664 | 4.8706 | -116.684 | -116.716 | -115.8371 | -0.76904 | -0.48065 | -0.48065 | 1.7532 | 0.50354 | 0.62256 | 1.2726 | 1.3916 | -0.36163 | 0.43945 | -0.40283 | -0.27924 | 0.56763 | -0.31128 | 0.92926 | 0.050354 | 2.5223 | 121.9666 | 0.082397 | 121.637 | 121.9666 | 122.4792 | 121.1975 | 122.1176 | -122.4472 | -122.0398 | 121.1975 | 121.2753 | 51.265 | 116.2354
1373.5 | 122.2321 | -117.1555 | 4.7607 | 0.01358 | -0.004439 | 0.01242 | 0.065106 | -0.019976 | -0.030745 | -0.022392 | 0.0025024 | -0.0086731 | 0.063335 | 0.047928 | -0.016017 | -0.007323 | -0.019732 | -65.6662 | 4.6692 | -117.2836 | 4.5136 | -115.9882 | -117.0822 | -117.1829 | -0.009155 | 4.6143 | -117.2241 | 4.8294 | -116.7389 | -116.8213 | -116.7114 | -0.12817 | -0.091553 | -0.24719 | 1.1673 | -0.027465 | 0.073243 | 0.10071 | 0.20142 | -0.068664 | -0.14648 | 0.068665 | 0.41656 | 0.44403 | 0.33417 | 0.51269 | 0.40283 | 1.2955 | 121.7972 | 0.48523 | 122.0535 | 121.9528 | 121.8384 | 121.8246 | 121.7697 | -122.0444 | -121.9849 | 121.669 | 121.9849 | 51.4893 | 117.1463
1375.2188 | 122.1405 | -87.8311 | 34.0805 | 0.01358 | -0.0059344 | 0.011138 | 0.066174 | -0.015917 | -0.030104 | -0.022605 | 0.0055542 | -0.0084595 | 0.062053 | 0.041947 | -0.016658 | -0.008391 | -0.015887 | -45.8038 | 33.815 | -88.0783 | 34.0668 | -86.7599 | -87.7945 | -87.8632 | 0.66834 | 33.9111 | -87.8906 | 34.2636 | -87.5381 | -87.5839 | -87.5198 | -0.24719 | -0.2655 | -0.013733 | 1.0712 | -0.032043 | 0.036621 | 0.21515 | 0.28381 | -0.059509 | -0.16937 | 0.18311 | 0.29297 | 0.31128 | 0.24719 | 0.37079 | 0.3067 | 1.3184 | 122.1451 | 0.35248 | 122.1542 | 121.8933 | 121.8018 | 121.6461 | 121.7422 | -122.1588 | -121.9711 | 121.8979 | 122.0947 | 42.0273 | 88.4995
1376.9844 | 122.0856 | -93.8736 | 28.0655 | 0.0059509 | -0.0052936 | 0.0098565 | 0.067029 | -0.021258 | -0.031599 | -0.027092 | -0.00054937 | -0.0041869 | 0.065899 | 0.044297 | -0.016658 | -0.0094592 | -0.012042 | -50.2716 | 28.1387 | -93.8873 | 28.1113 | -92.7017 | -93.7271 | -93.8049 | -3.6758 | 28.1204 | -93.8095 | 28.1479 | -93.6584 | -93.7592 | -93.6539 | -0.013733 | 0.073242 | 0.045776 | 1.1719 | 0.068664 | 0.14648 | 0.082397 | 0.16022 | 0.064087 | 0.054931 | 0.082397 | 0.21515 | 0.21973 | 0.11444 | 0.15564 | 0.050354 | 1.1856 | 121.9986 | 0.15106 | 121.9574 | 122.0261 | 121.9299 | 122.0123 | 121.994 | -121.9528 | -121.875 | 121.9849 | 122.0215 | 43.602 | 90.1978
1378.7656 | 122.049 | -79.6326 | 42.3386 | 0.01358 | -0.006789 | 0.0085749 | 0.066815 | -0.019976 | -0.031172 | -0.023246 | 0.0025024 | -0.0082459 | 0.06483 | 0.037034 | -0.01794 | -0.0088184 | -0.011828 | -40.7547 | 42.2379 | -79.7882 | 42.1829 | -78.7216 | -79.6829 | -79.715 | 0.082397 | 42.247 | -79.6646 | 42.3523 | -79.4952 | -79.5273 | -79.4357 | -0.15564 | -0.10071 | -0.15564 | 0.91095 | -0.082398 | -0.050354 | 0.073242 | 0.10529 | -0.032044 | -0.091553 | 0.013733 | 0.13733 | 0.19684 | 0.10529 | 0.22888 | 0.13733 | 1.0666 | 121.9711 | 0.16937 | 122.0169 | 122.0261 | 121.9116 | 121.8704 | 121.8796 | -122.1268 | -122.0032 | 121.8155 | 121.9849 | 38.8779 | 79.715
1380.5469 | 122.1909 | -76.7395 | 45.1263 | 0.01358 | -0.0087116 | 0.01242 | 0.06532 | -0.019335 | -0.027754 | -0.023674 | 0.0025024 | -0.0099549 | 0.062694 | 0.043442 | -0.015377 | -0.007323 | -0.019305 | -38.6856 | 45.1218 | -76.8631 | 45.1813 | -75.6958 | -76.712 | -76.7944 | 0.15106 | 45.0577 | -76.8036 | 45.3003 | -76.5518 | -76.593 | -76.5152 | -0.1236 | -0.004578 | 0.054931 | 1.0437 | -0.054932 | 0.027466 | 0.068664 | 0.15106 | -0.064087 | -0.068665 | 0.17395 | 0.18768 | 0.2243 | 0.14648 | 0.28839 | 0.21057 | 1.1673 | 122.0444 | 0.25177 | 122.1039 | 121.9849 | 121.8613 | 121.8613 | 121.7972 | -121.9894 | -121.9299 | 121.9208 | 122.0398 | 38.0539 | 76.8906
1382.2812 | 122.2046 | -84.5993 | 37.2574 | 0.01358 | -0.0074298 | 0.010498 | 0.065533 | -0.014849 | -0.027113 | -0.020897 | 0.014709 | -0.0065369 | 0.066967 | 0.046433 | -0.017726 | -0.0088184 | -0.015246 | -44.2703 | 37.1979 | -84.7824 | 37.262 | -83.4549 | -84.4391 | -84.5352 | 0.30212 | 37.2116 | -84.668 | 37.262 | -84.5535 | -84.4711 | -84.3109 | -0.18311 | -0.059509 | 0.004578 | 1.1444 | 0.064087 | 0.16022 | 0.24719 | 0.34332 | -0.068665 | -0.045776 | 0.004578 | 0.045776 | 0.28839 | 0.12817 | 0.35706 | 0.19684 | 1.3275 | 122.0444 | 0.11444 | 121.9299 | 121.9803 | 121.8796 | 121.7972 | 121.8109 | -122.0398 | -121.9254 | 121.8613 | 121.8613 | 40.329 | 84.9014
1384.0625 | 122.0856 | -95.7092 | 26.1749 | 0.0059509 | -0.0037982 | 0.010925 | 0.066601 | -0.01848 | -0.029463 | -0.02346 | 0.0055542 | -0.0078185 | 0.064617 | 0.040879 | -0.019222 | -0.0088184 | -0.015887 | -52.4002 | 26.0651 | -96.0159 | 25.9644 | -94.6426 | -95.7321 | -95.8649 | -0.25177 | 26.0696 | -95.8878 | 26.207 | -95.5307 | -95.6223 | -95.4758 | -0.3067 | -0.10986 | -0.21057 | 1.0666 | -0.15564 | -0.022888 | 0.15106 | 0.28381 | -0.17853 | -0.10529 | 0.032043 | 0.17853 | 0.23346 | 0.086976 | 0.41199 | 0.2655 | 1.3733 | 121.9803 | 0.35706 | 122.0947 | 122.081 | 121.9574 | 121.7743 | 121.7789 | -122.1909 | -122.0627 | 121.6736 | 121.9162 | 43.309 | 95.4575
1385.8281 | 121.9437 | -84.4666 | 37.4222 | -0.0016786 | -0.007857 | 0.0098565 | 0.06532 | -0.02083 | -0.030531 | -0.022819 | 0.0025024 | -0.0093139 | 0.063762 | 0.037247 | -0.023494 | -0.010314 | -0.013537 | -44.3253 | 37.3169 | -84.6085 | 37.0102 | -83.4869 | -84.343 | -84.4803 | -1.3412 | 37.2253 | -84.6405 | 37.4634 | -84.1553 | -84.4437 | -84.2514 | -0.14191 | -0.10528 | -0.41199 | 0.97962 | -0.013733 | 0.1236 | 0.12817 | 0.2655 | -0.17395 | -0.19684 | 0.041199 | 0.31128 | 0.21515 | 0.022888 | 0.3891 | 0.19684 | 1.1215 | 121.6187 | 0.48523 | 122.1039 | 121.9254 | 121.8658 | 121.7834 | 121.6919 | -122.0306 | -122.0627 | 121.4767 | 121.9299 | 40.1413 | 83.1253
1387.6094 | 121.9345 | -68.7424 | 53.0365 | 0.036468 | -0.0048664 | 0.012207 | 0.065533 | -0.017412 | -0.026472 | -0.021751 | 0.0055542 | -0.0088867 | 0.067821 | 0.049851 | -0.017726 | -0.011168 | -0.013965 | -33.0826 | 53.8513 | -68.0328 | 52.5696 | -67.8223 | -68.9941 | -69.5801 | -2.6276 | 51.8738 | -69.9783 | 52.8488 | -68.4402 | -68.4036 | -68.4357 | 0.70953 | 0.81482 | -0.46692 | 0.92011 | -0.83771 | -0.25177 | -1.5472 | -0.9613 | -1.236 | -1.1627 | -0.18768 | 0.30212 | 0.3067 | 0.33875 | 1.5427 | 1.5747 | 0.21057 | 120.6024 | 1.5381 | 122.8271 | 121.8842 | 121.8521 | 122.5937 | 120.6162 | -121.0693 | -123.0148 | 121.312 | 121.5912 | 35.6598 | 66.1148
1389.3281 | 121.8201 | -87.2635 | 34.3231 | 0.01358 | -0.0072162 | 0.012207 | 0.067242 | -0.014849 | -0.027327 | -0.023033 | 0.0025024 | -0.0056823 | 0.062481 | 0.043442 | -0.020076 | -0.0086048 | -0.015674 | -46.7056 | 33.6273 | -88.1882 | 33.4076 | -86.7416 | -87.9272 | -88.3301 | 0.42572 | 33.6273 | -87.7945 | 34.2224 | -86.911 | -86.9339 | -87.0621 | -0.92468 | -0.6958 | -0.91553 | 0.52185 | -1.0666 | -0.66376 | -0.14191 | 0.26093 | -0.53101 | -0.6958 | -0.10071 | 0.35248 | 0.20142 | 0.32959 | 0.73242 | 0.8606 | 1.4465 | 121.5958 | 0.88348 | 122.0169 | 121.8155 | 121.4218 | 120.8908 | 120.8908 | -122.5113 | -122.1176 | 120.6711 | 121.4859 | 40.5579 | 87.6892
1391.1094 | 121.7651 | -83.876 | 37.5412 | 0.01358 | -0.0070026 | 0.0096429 | 0.064679 | -0.021258 | -0.027327 | -0.022605 | 0.0055542 | -0.0088867 | 0.064617 | 0.042588 | -0.021785 | -0.0092456 | -0.018878 | -44.4672 | 37.4451 | -84.1553 | 37.5961 | -82.6904 | -84.2834 | -84.4528 | -1.0483 | 37.207 | -84.0546 | 37.8662 | -83.6105 | -83.551 | -83.5648 | -0.27923 | -0.096131 | 0.054931 | 1.1856 | -0.57678 | -0.40741 | -0.29755 | -0.12817 | -0.17853 | -0.33417 | 0.32501 | 0.2655 | 0.31128 | 0.32501 | 0.48981 | 0.50354 | 1.4648 | 121.7514 | 0.44403 | 121.9208 | 121.6003 | 121.2616 | 121.3211 | 121.0831 | -121.6965 | -121.5958 | 121.4722 | 121.7422 | 39.4089 | 82.8278
1392.8125 | 121.9208 | -71.3928 | 49.8459 | 0.044098 | -0.0065754 | 0.0090021 | 0.067669 | -0.020403 | -0.028181 | -0.024528 | 0.014709 | -0.0061095 | 0.062908 | 0.045151 | -0.020076 | -0.011595 | -0.014819 | -33.3801 | 52.1439 | -69.7403 | 58.5526 | -62.6862 | -65.1443 | -65.4099 | 2.7695 | 56.2775 | -65.7898 | 49.8001 | -71.7133 | -71.814 | -70.8481 | 1.6525 | 2.298 | 8.7067 | 8.7067 | 5.983 | 6.2485 | 4.3304 | 4.5959 | 5.603 | 6.4316 | -0.045776 | -0.32044 | 0.54474 | -0.42114 | -5.0583 | -6.0242 | 7.0541 | 128.2928 | -5.9235 | 115.5899 | 121.8842 | 122.0673 | 123.5367 | 127.6703 | -119.5862 | -115.6357 | 129.9454 | 121.1929 | 38.0127 | 74.1623
1394.5938 | 121.907 | -54.5792 | 67.2775 | 0.028839 | -0.0059344 | 0.011779 | 0.064038 | -0.015917 | -0.029676 | -0.020897 | 0.008606 | -0.0097411 | 0.066539 | 0.052201 | -0.020931 | -0.0098864 | -0.016955 | -22.1512 | 66.9983 | -54.5471 | 67.4835 | -53.2471 | -54.071 | -54.5197 | 2.6093 | 67.0395 | -54.6112 | 67.1677 | -54.3777 | -54.5883 | -54.364 | 0.032044 | -0.27924 | 0.20599 | 1.3321 | 0.05951 | 0.50812 | 0.027466 | 0.47607 | -0.032043 | -0.23804 | -0.10986 | 0.20142 | 0.21515 | -0.009155 | 0.24719 | 0.022888 | 1.3 | 122.0306 | 0.23346 | 121.7789 | 121.5454 | 121.6507 | 121.5775 | 121.6187 | -121.8246 | -121.8887 | 122.0627 | 121.7468 | 32.428 | 57.1884
1396.3125 | 121.9757 | -120.1813 | 1.4694 | 0.0059509 | -0.006148 | 0.013275 | 0.066174 | -0.016558 | -0.02754 | -0.020683 | 0.014709 | -0.0065369 | 0.065044 | 0.044297 | -0.016231 | -0.0081774 | -0.015033 | -69.9829 | 1.4099 | -120.3094 | 1.4282 | -118.2678 | -119.8288 | -120.0531 | -0.27924 | 1.4603 | -120.3415 | 1.4923 | -119.7739 | -119.8746 | -119.8013 | -0.12817 | -0.059509 | -0.041198 | 1.9135 | 0.12817 | 0.35248 | 0.25635 | 0.48065 | -0.16022 | -0.009155 | 0.022889 | 0.40741 | 0.37994 | 0.3067 | 0.54016 | 0.46692 | 2.0416 | 121.7377 | 0.56763 | 121.8338 | 121.7194 | 121.8018 | 121.5912 | 121.6415 | -121.7789 | -121.8109 | 121.6095 | 121.6736 | 50.1984 | 119.902
1398.0938 | 122.0261 | -120.5566 | 1.3458 | -0.0093076 | -0.0046526 | 0.014556 | 0.066815 | -0.018908 | -0.028608 | -0.02346 | 0.0055542 | -0.0088867 | 0.065044 | 0.052415 | -0.022853 | -0.0101 | -0.01311 | -70.2621 | 1.268 | -120.6482 | 1.2405 | -118.5333 | -120.1492 | -120.3781 | -0.23346 | 1.3046 | -120.6436 | 1.2405 | -120.1675 | -120.2545 | -120.1813 | -0.091552 | -0.07782 | -0.10529 | 2.0233 | 0.17853 | 0.40741 | 0.27008 | 0.49896 | -0.086975 | -0.041199 | -0.10529 | 0.3891 | 0.37537 | 0.30212 | 0.46234 | 0.3891 | 2.1149 | 121.8887 | 0.47607 | 121.8842 | 121.9162 | 121.9482 | 121.8246 | 121.8613 | -121.994 | -121.9894 | 121.7972 | 121.7972 | 50.2945 | 120.3232
1399.8594 | 122.0993 | -120.6619 | 1.2909 | -0.0016786 | -0.0065754 | 0.012847 | 0.067242 | -0.021258 | -0.026472 | -0.022178 | 0.0025024 | -0.0073913 | 0.066326 | 0.040024 | -0.016658 | -0.0068958 | -0.019305 | -70.3262 | 1.2405 | -120.7855 | 1.1032 | -118.6432 | -120.3506 | -120.5521 | -0.29297 | 1.2772 | -120.7489 | 1.2177 | -120.2774 | -120.3598 | -120.2408 | -0.1236 | -0.050354 | -0.18768 | 2.0187 | 0.10986 | 0.31128 | 0.23346 | 0.43488 | -0.086975 | -0.013733 | -0.073243 | 0.38452 | 0.42114 | 0.30212 | 0.50812 | 0.3891 | 2.1423 | 121.8887 | 0.4715 | 121.9666 | 122.0261 | 122.0261 | 121.9025 | 121.9391 | -122.0764 | -122.0398 | 121.7651 | 121.8796 | 50.3357 | 120.369
1401.5781 | 122.1313 | -120.7672 | 1.1719 | 0.028839 | -0.0063616 | 0.013275 | 0.067242 | -0.015703 | -0.026686 | -0.02111 | 0.011658 | -0.0097411 | 0.066326 | 0.046006 | -0.018794 | -0.0079638 | -0.016314 | -70.6467 | 1.1124 | -120.8771 | 1.1307 | -118.5699 | -120.3186 | -120.5475 | -0.19684 | 1.1765 | -120.8359 | 1.1765 | -120.3552 | -120.4193 | -120.3415 | -0.10986 | -0.059509 | -0.041199 | 2.1973 | 0.21973 | 0.44861 | 0.32959 | 0.55847 | -0.068664 | 0.004578 | 0.004578 | 0.41199 | 0.42572 | 0.3479 | 0.49438 | 0.41656 | 2.3071 | 122.0078 | 0.48065 | 122.0123 | 121.9894 | 122.0123 | 121.8796 | 121.9437 | -122.049 | -122.0078 | 121.8979 | 121.9437 | 50.1205 | 120.5704
1403.3594 | 122.2 | -120.7626 | 1.1948 | 0.0059509 | -0.006148 | 0.016479 | 0.066174 | -0.014849 | -0.024336 | -0.020897 | 0.008606 | -0.0080321 | 0.065899 | 0.046219 | -0.01559 | -0.0071094 | -0.016101 | -70.2438 | 1.1261 | -120.8496 | 1.1398 | -118.4647 | -120.314 | -120.575 | -0.17395 | 1.181 | -120.8633 | 1.2131 | -120.3094 | -120.4056 | -120.3278 | -0.086975 | -0.068664 | -0.054931 | 2.298 | 0.18768 | 0.44861 | 0.27466 | 0.53558 | -0.10071 | -0.013733 | 0.018311 | 0.45319 | 0.43488 | 0.35706 | 0.53558 | 0.45776 | 2.3849 | 121.9894 | 0.55389 | 122.0764 | 121.9757 | 122.0444 | 121.8887 | 121.9437 | -122.0444 | -122.0581 | 121.9025 | 121.9757 | 50.5188 | 120.5887
1405.0625 | 122.1405 | -120.8221 | 1.149 | 0.02121 | -0.0076434 | 0.011352 | 0.064465 | -0.01848 | -0.026258 | -0.024101 | 0.0055542 | -0.0095275 | 0.064403 | 0.052201 | -0.021144 | -0.0092456 | -0.010974 | -70.578 | 1.1032 | -120.9686 | 1.0437 | -118.5196 | -120.3918 | -120.6299 | -0.27924 | 1.1261 | -120.9366 | 1.1032 | -120.4468 | -120.5338 | -120.4239 | -0.14648 | -0.045777 | -0.10529 | 2.3026 | 0.19226 | 0.4303 | 0.33874 | 0.57678 | -0.11444 | -0.022888 | -0.045777 | 0.37537 | 0.39825 | 0.28839 | 0.51269 | 0.40283 | 2.449 | 122.0123 | 0.48981 | 122.0398 | 122.0718 | 122.0627 | 121.9254 | 121.9482 | -122.1176 | -122.0856 | 121.8658 | 121.9254 | 50.2441 | 120.5429
1406.8281 | 122.2046 | -120.8038 | 1.1581 | 0.0059509 | -0.00508 | 0.013488 | 0.068097 | -0.018267 | -0.026258 | -0.021751 | -0.00054937 | -0.0069641 | 0.063976 | 0.044083 | -0.018581 | -0.0075366 | -0.017383 | -70.7291 | 1.0941 | -120.9549 | 1.0574 | -118.4418 | -120.3598 | -120.6345 | -0.19684 | 1.1353 | -120.9137 | 1.1765 | -120.4102 | -120.4926 | -120.3873 | -0.15106 | -0.064087 | -0.10071 | 2.3621 | 0.16937 | 0.44403 | 0.32043 | 0.59509 | -0.10986 | -0.022888 | 0.018311 | 0.39368 | 0.41656 | 0.31128 | 0.52643 | 0.42114 | 2.5131 | 122.0123 | 0.50354 | 122.0901 | 122.0489 | 122.049 | 121.8979 | 121.9391 | -122.113 | -122.0718 | 121.8613 | 121.9803 | 50.0748 | 120.607
1408.6094 | 122.113 | -120.9778 | 1.0574 | 0.01358 | -0.0070026 | 0.012847 | 0.067883 | -0.016985 | -0.026472 | -0.02111 | -0.00054937 | -0.0076049 | 0.065471 | 0.044083 | -0.022212 | -0.0077502 | -0.013751 | -71.4066 | 0.99792 | -121.1243 | 0.85144 | -118.6203 | -120.5978 | -120.813 | -0.31586 | 1.0437 | -121.0648 | 0.92468 | -120.6665 | -120.7489 | -120.6116 | -0.14648 | -0.059509 | -0.20599 | 2.3575 | 0.16479 | 0.37994 | 0.31128 | 0.52643 | -0.086975 | -0.013733 | -0.13275 | 0.31128 | 0.36621 | 0.22888 | 0.45319 | 0.31586 | 2.504 | 121.9757 | 0.39825 | 121.9894 | 122.1222 | 122.1085 | 121.9757 | 122.0215 | -122.1817 | -122.1222 | 121.8292 | 121.9025 | 49.5712 | 120.6619
1410.3125 | 122.1954 | -121.0373 | 0.98419 | 0.01358 | -0.0072162 | 0.012847 | 0.065747 | -0.015276 | -0.025618 | -0.021965 | 0.0055542 | -0.0099549 | 0.06419 | 0.053483 | -0.020076 | -0.0094592 | -0.016528 | -71.1594 | 0.90637 | -121.1472 | 0.84686 | -118.4784 | -120.5292 | -120.7993 | -0.27466 | 0.94299 | -121.1243 | 0.92468 | -120.639 | -120.7123 | -120.6345 | -0.10986 | -0.07782 | -0.13733 | 2.5589 | 0.23804 | 0.50812 | 0.3479 | 0.61798 | -0.086976 | -0.041199 | -0.059509 | 0.39825 | 0.40283 | 0.32501 | 0.48981 | 0.41199 | 2.6688 | 121.994 | 0.48523 | 122.049 | 122.0535 | 122.0673 | 121.9437 | 121.9803 | -122.1313 | -122.1085 | 121.8842 | 121.962 | 49.8779 | 120.7626
1412.0938 | 122.1222 | -121.0648 | 1.0117 | 0.02121 | -0.0025164 | 0.01007 | 0.068951 | -0.017199 | -0.027113 | -0.023033 | 0.017761 | -0.0063233 | 0.064403 | 0.041306 | -0.021144 | -0.011382 | -0.014819 | -71.9009 | 0.97961 | -121.1929 | 0.79651 | -118.4509 | -120.5475 | -120.813 | -0.27466 | 1.0071 | -121.1472 | 0.86517 | -120.7077 | -120.7809 | -120.6665 | -0.12817 | -0.032044 | -0.21515 | 2.6138 | 0.25177 | 0.51727 | 0.37994 | 0.64545 | -0.082398 | -0.004578 | -0.14648 | 0.35706 | 0.39825 | 0.28381 | 0.48065 | 0.36621 | 2.742 | 121.9894 | 0.43945 | 122.0123 | 122.1725 | 122.1542 | 122.0444 | 122.0718 | -122.2046 | -122.1588 | 121.8613 | 121.9299 | 49.1638 | 120.7901
1413.8906 | 122.1268 | -121.0739 | 1.0117 | 0.02121 | -0.004439 | 0.013275 | 0.068951 | -0.016771 | -0.028181 | -0.023887 | 0.0025024 | -0.0073913 | 0.064403 | 0.04451 | -0.018581 | -0.011595 | -0.016314 | -72.171 | 0.9613 | -121.1655 | 0.8606 | -118.3319 | -120.5383 | -120.8176 | -0.21515 | 1.0025 | -121.1472 | 0.90179 | -120.694 | -120.7809 | -120.6757 | -0.091552 | -0.050354 | -0.15106 | 2.742 | 0.25635 | 0.53558 | 0.3479 | 0.62714 | -0.073242 | -0.009156 | -0.10986 | 0.37994 | 0.39826 | 0.29297 | 0.4715 | 0.36621 | 2.8336 | 122.0261 | 0.45319 | 122.0489 | 122.1268 | 122.1497 | 122.0352 | 122.0764 | -122.1771 | -122.1588 | 121.9345 | 121.9757 | 48.9029 | 120.8588
1415.6094 | 122.1222 | -121.1884 | 0.90179 | -0.0016786 | -0.0052936 | 0.014129 | 0.068097 | -0.016771 | -0.025618 | -0.020042 | 0.0025024 | -0.0080321 | 0.065899 | 0.04451 | -0.020076 | -0.0098864 | -0.014819 | -72.8622 | 0.85144 | -121.2616 | 0.68207 | -118.4463 | -120.694 | -120.9778 | -0.32044 | 0.89722 | -121.2524 | 0.78278 | -120.8359 | -120.9045 | -120.7901 | -0.073243 | -0.050354 | -0.21973 | 2.742 | 0.21057 | 0.49438 | 0.28381 | 0.56763 | -0.064087 | -0.004577 | -0.11902 | 0.35248 | 0.39825 | 0.28381 | 0.46234 | 0.3479 | 2.8152 | 121.9437 | 0.41657 | 122.0352 | 122.113 | 122.1497 | 122.0398 | 122.0856 | -122.1634 | -122.1542 | 121.8704 | 121.9711 | 48.3261 | 120.8679
1417.375 | 122.1634 | -121.7148 | 0.3891 | 0.02121 | -0.0042254 | 0.012847 | 0.067242 | -0.019762 | -0.024763 | -0.020256 | 0.0025024 | -0.0091003 | 0.065899 | 0.044297 | -0.020931 | -0.011595 | -0.017596 | -73.5489 | 0.31128 | -121.8475 | 0.21515 | -118.7851 | -121.106 | -121.4172 | -0.19684 | 0.35706 | -121.7743 | 0.29297 | -121.312 | -121.4127 | -121.3028 | -0.13275 | -0.07782 | -0.17395 | 2.9297 | 0.29755 | 0.60883 | 0.4303 | 0.74158 | -0.059509 | -0.032043 | -0.09613 | 0.40283 | 0.41199 | 0.30212 | 0.4715 | 0.36163 | 3.0624 | 122.0627 | 0.46234 | 122.0673 | 122.1588 | 122.1313 | 122.0261 | 122.0718 | -122.2366 | -122.1634 | 121.9299 | 122.0078 | 48.1659 | 121.5179
1419.1562 | 122.168 | -121.8018 | 0.28839 | 0.01358 | -0.0037982 | 0.013488 | 0.068738 | -0.015917 | -0.026899 | -0.021537 | 0.0055542 | -0.0088867 | 0.064403 | 0.045151 | -0.017726 | -0.009032 | -0.017596 | -74.2447 | 0.23346 | -121.907 | 0.073242 | -118.8721 | -121.257 | -121.55 | -0.30212 | 0.28381 | -121.8613 | 0.16022 | -121.4401 | -121.5271 | -121.3989 | -0.10528 | -0.054932 | -0.21515 | 2.9297 | 0.25177 | 0.54474 | 0.35706 | 0.65002 | -0.059509 | -0.004578 | -0.12817 | 0.36163 | 0.40283 | 0.27466 | 0.46234 | 0.33417 | 3.035 | 121.9803 | 0.42114 | 122.0215 | 122.1405 | 122.1451 | 122.0352 | 122.0856 | -122.1954 | -122.1497 | 121.875 | 121.962 | 47.5571 | 121.4996
1420.9219 | 122.1405 | -121.8246 | 0.29755 | 0.02121 | -0.0046526 | 0.013916 | 0.067456 | -0.019762 | -0.02754 | -0.019828 | 0.0025024 | -0.0084595 | 0.062053 | 0.045365 | -0.019863 | -0.0088184 | -0.014819 | -74.3774 | 0.2243 | -121.9345 | 0.059509 | -118.8309 | -121.2662 | -121.5637 | -0.32501 | 0.27008 | -121.8979 | 0.15106 | -121.4676 | -121.5546 | -121.4401 | -0.10986 | -0.073242 | -0.23804 | 2.9938 | 0.26093 | 0.55847 | 0.37079 | 0.66833 | -0.073242 | -0.027465 | -0.14648 | 0.35706 | 0.38452 | 0.27008 | 0.45776 | 0.34332 | 3.1036 | 121.994 | 0.4303 | 122.0489 | 122.1588 | 122.168 | 122.049 | 122.0947 | -122.2321 | -122.1954 | 121.8842 | 121.9757 | 47.4472 | 121.4996
1422.7031 | 122.2366 | -121.8063 | 0.26093 | 0.01358 | -0.0048664 | 0.016052 | 0.065747 | -0.018053 | -0.028181 | -0.020042 | 0.0025024 | -0.0078185 | 0.065258 | 0.046006 | -0.017513 | -0.0088184 | -0.016314 | -74.4141 | 0.2243 | -121.9345 | 0.091553 | -118.6707 | -121.2067 | -121.4996 | -0.26093 | 0.25635 | -121.8796 | 0.21973 | -121.3943 | -121.4813 | -121.3715 | -0.12817 | -0.036621 | -0.16937 | 3.1357 | 0.3067 | 0.59967 | 0.43488 | 0.72784 | -0.073243 | -0.004577 | -0.041198 | 0.41199 | 0.43488 | 0.32501 | 0.50812 | 0.39825 | 3.2639 | 122.0261 | 0.48523 | 122.0993 | 122.1588 | 122.1359 | 122.0306 | 122.0627 | -122.1954 | -122.1405 | 121.8979 | 122.0261 | 47.3923 | 121.5454
1424.5156 | 122.2549 | -121.7926 | 0.24261 | 0.01358 | -0.0055072 | 0.014984 | 0.065533 | -0.023607 | -0.024336 | -0.020042 | 0.0025024 | -0.0086731 | 0.061199 | 0.045151 | -0.022212 | -0.0094592 | -0.016101 | -74.8947 | 0.17395 | -121.907 | 0.1831 | -118.4509 | -121.0464 | -121.4035 | -0.16479 | 0.23804 | -121.875 | 0.23804 | -121.3394 | -121.4218 | -121.3486 | -0.11444 | -0.068665 | -0.05951 | 3.3417 | 0.3891 | 0.74616 | 0.50354 | 0.8606 | -0.082397 | -0.004578 | -0.004578 | 0.45319 | 0.44403 | 0.37079 | 0.52643 | 0.45319 | 3.4561 | 122.0901 | 0.53558 | 122.113 | 122.081 | 122.113 | 121.9666 | 122.0306 | -122.1497 | -122.1176 | 121.9757 | 122.0306 | 46.8979 | 121.6278
1426.2812 | 122.1954 | -121.8109 | 0.27924 | 0.02121 | -0.0031574 | 0.013488 | 0.070874 | -0.021258 | -0.02519 | -0.018333 | 0.0055542 | -0.0069641 | 0.063976 | 0.037888 | -0.019649 | -0.0092456 | -0.012896 | -74.6567 | 0.23346 | -121.9162 | 0.16022 | -118.4509 | -121.0831 | -121.4264 | -0.1831 | 0.27008 | -121.875 | 0.21057 | -121.3943 | -121.4859 | -121.376 | -0.10529 | -0.045777 | -0.11902 | 3.36 | 0.38452 | 0.72784 | 0.48981 | 0.83313 | -0.064087 | -0.009155 | -0.068665 | 0.41657 | 0.43488 | 0.32501 | 0.49896 | 0.3891 | 3.4653 | 122.0764 | 0.48065 | 122.0856 | 122.1497 | 122.1451 | 122.0444 | 122.081 | -122.1954 | -122.1542 | 121.9711 | 122.0215 | 47.1542 | 121.6278
1428 | 122.2595 | -121.7926 | 0.2655 | 0.01358 | -0.0020892 | 0.014556 | 0.067242 | -0.017626 | -0.02519 | -0.020042 | 0.0025024 | -0.0076049 | 0.06419 | 0.05156 | -0.019435 | -0.008391 | -0.014819 | -74.8718 | 0.21515 | -121.9162 | 0.16022 | -118.3731 | -121.0464 | -121.431 | -0.21973 | 0.24261 | -121.8842 | 0.25177 | -121.3715 | -121.4401 | -121.3211 | -0.1236 | -0.050354 | -0.10529 | 3.4195 | 0.36163 | 0.74616 | 0.48523 | 0.86975 | -0.091552 | -0.022888 | -0.013733 | 0.42114 | 0.4715 | 0.35248 | 0.56305 | 0.44403 | 3.5431 | 122.0764 | 0.5127 | 122.1359 | 122.1313 | 122.1268 | 122.0078 | 122.0352 | -122.1817 | -122.1497 | 121.9528 | 122.0444 | 46.9208 | 121.5729
1429.7188 | 122.1771 | -121.8292 | 0.29755 | 0.036468 | -0.003371 | 0.013061 | 0.068738 | -0.018908 | -0.027113 | -0.017906 | 0.011658 | -0.0080321 | 0.066326 | 0.044297 | -0.024135 | -0.0096728 | -0.014392 | -76.9592 | 0.24719 | -121.9574 | 0.086975 | -118.4235 | -121.0236 | -121.4722 | -0.26093 | 0.29297 | -121.8887 | 0.14648 | -121.4493 | -121.5363 | -121.4218 | -0.12817 | -0.050354 | -0.21057 | 3.4058 | 0.35706 | 0.80566 | 0.48523 | 0.93384 | -0.059509 | -0.004577 | -0.15106 | 0.37994 | 0.40741 | 0.29297 | 0.46692 | 0.35248 | 3.5339 | 122.0444 | 0.43945 | 122.0352 | 122.2046 | 122.1817 | 122.0764 | 122.1222 | -122.2549 | -122.1863 | 121.9162 | 121.9757 | 44.87 | 121.5683
1431.5156 | 122.1497 | -121.8063 | 0.31586 | 0.01358 | -0.00508 | 0.011779 | 0.067242 | -0.021044 | -0.025404 | -0.021537 | 0.0055542 | -0.0067505 | 0.06419 | 0.042801 | -0.022426 | -0.0088184 | -0.015033 | -77.449 | 0.21973 | -121.8933 | 0.11444 | -118.3228 | -121.0052 | -121.4401 | -0.2655 | 0.28839 | -121.8842 | 0.17853 | -121.4401 | -121.5088 | -121.4401 | -0.086976 | -0.09613 | -0.20142 | 3.4836 | 0.36621 | 0.80109 | 0.45319 | 0.88806 | -0.07782 | -0.027466 | -0.13733 | 0.36621 | 0.36621 | 0.29755 | 0.44403 | 0.37537 | 3.5706 | 122.0078 | 0.44403 | 122.0627 | 122.113 | 122.1725 | 122.0261 | 122.0947 | -122.2092 | -122.2 | 121.9208 | 121.9849 | 44.3573 | 121.5408
1433.2344 | 122.2366 | -121.7972 | 0.3067 | -0.0016786 | -0.00508 | 0.01477 | 0.066174 | -0.022753 | -0.024977 | -0.019828 | -0.00054937 | -0.0097411 | 0.063121 | 0.047074 | -0.020931 | -0.0101 | -0.013537 | -77.8931 | 0.20142 | -121.8979 | 0.20142 | -118.1396 | -120.8771 | -121.3348 | -0.17395 | 0.24261 | -121.8384 | 0.24719 | -121.3577 | -121.4264 | -121.3623 | -0.10071 | -0.10529 | -0.10529 | 3.6575 | 0.46234 | 0.9201 | 0.56305 | 1.0208 | -0.041199 | -0.064087 | -0.05951 | 0.43945 | 0.43487 | 0.37079 | 0.47607 | 0.41199 | 3.7582 | 122.0993 | 0.48065 | 122.0856 | 122.0993 | 122.081 | 121.9986 | 122.0398 | -122.2046 | -122.1451 | 121.9986 | 122.0444 | 43.9041 | 121.6232
1434.9375 | 122.1588 | -121.8018 | 0.32501 | 0.01358 | -0.00508 | 0.013916 | 0.068097 | -0.021258 | -0.026045 | -0.024101 | 0.0055542 | -0.0084595 | 0.065685 | 0.047074 | -0.021572 | -0.011595 | -0.016528 | -78.0579 | 0.24261 | -121.9208 | 0.10071 | -118.1854 | -120.9641 | -121.4127 | -0.26093 | 0.28839 | -121.8842 | 0.16479 | -121.4539 | -121.5317 | -121.4264 | -0.11902 | -0.082397 | -0.2243 | 3.6163 | 0.3891 | 0.83771 | 0.50812 | 0.95673 | -0.082397 | -0.036621 | -0.16022 | 0.3479 | 0.37537 | 0.27008 | 0.45776 | 0.35248 | 3.7354 | 122.0215 | 0.4303 | 122.049 | 122.1634 | 122.1725 | 122.0444 | 122.0901 | -122.2458 | -122.2092 | 121.9025 | 121.9666 | 43.7439 | 121.5408
1436.7188 | 122.2824 | -121.7606 | 0.28381 | 0.01358 | -0.0023028 | 0.017761 | 0.068951 | -0.016558 | -0.023909 | -0.021324 | 0.011658 | -0.0086731 | 0.06419 | 0.049637 | -0.016872 | -0.006682 | -0.016742 | -78.717 | 0.20599 | -121.8613 | 0.23346 | -117.9657 | -120.8496 | -121.2891 | -0.16022 | 0.26093 | -121.8292 | 0.30212 | -121.3303 | -121.3989 | -121.3165 | -0.10071 | -0.077819 | -0.050354 | 3.7949 | 0.4715 | 0.91095 | 0.5722 | 1.0117 | -0.068665 | -0.022888 | 0.018311 | 0.4303 | 0.44403 | 0.36163 | 0.5127 | 0.4303 | 3.8956 | 122.0947 | 0.49896 | 122.1313 | 122.0673 | 122.0901 | 121.9666 | 122.0215 | -122.1451 | -122.113 | 121.994 | 122.0627 | 43.0435 | 121.6003
1438.5 | 122.168 | -121.8155 | 0.31586 | 0.01358 | -0.00273 | 0.014984 | 0.068738 | -0.021685 | -0.025618 | -0.02111 | 0.0025024 | -0.0091003 | 0.065471 | 0.037461 | -0.021358 | -0.0101 | -0.016955 | -79.0558 | 0.23346 | -121.9208 | 0.13733 | -118.0023 | -120.8542 | -121.3348 | -0.25635 | 0.27008 | -121.8658 | 0.17395 | -121.431 | -121.4996 | -121.4218 | -0.10529 | -0.082398 | -0.17853 | 3.8132 | 0.48065 | 0.9613 | 0.58594 | 1.0666 | -0.050354 | -0.045776 | -0.14191 | 0.38452 | 0.39368 | 0.31586 | 0.44403 | 0.36621 | 3.9185 | 122.0581 | 0.43488 | 122.0398 | 122.1542 | 122.1359 | 122.0489 | 122.0856 | -122.2366 | -122.1817 | 121.9528 | 121.9894 | 42.7597 | 121.5591
1440.2812 | 122.0947 | -121.2479 | 0.87433 | 0.0059509 | -0.006148 | 0.013916 | 0.068951 | -0.023394 | -0.024763 | -0.021751 | -0.00054937 | -0.0086731 | 0.065258 | 0.041947 | -0.02264 | -0.0088184 | -0.018237 | -79.184 | 0.78735 | -121.3669 | 0.67291 | -117.4118 | -120.3003 | -120.7672 | -0.21973 | 0.85602 | -121.3074 | 0.73242 | -120.8725 | -120.9457 | -120.845 | -0.11902 | -0.086975 | -0.20142 | 3.8361 | 0.48065 | 0.94757 | 0.59967 | 1.0666 | -0.059509 | -0.018311 | -0.14191 | 0.37537 | 0.40283 | 0.30212 | 0.46234 | 0.36163 | 3.9551 | 122.0398 | 0.43488 | 122.0398 | 122.1542 | 122.1634 | 122.0352 | 122.1039 | -122.2412 | -122.1817 | 121.9208 | 121.9803 | 42.0639 | 121.0281
1442.0469 | 122.1451 | -119.87 | 2.0782 | 0.01358 | -0.0040118 | 0.01712 | 0.069806 | -0.021044 | -0.023909 | -0.021751 | -0.00054937 | -0.0082459 | 0.062908 | 0.047501 | -0.014308 | -0.0088184 | -0.020587 | -78.5797 | 2.0187 | -119.9295 | 2.0325 | -115.9058 | -118.8034 | -119.3253 | -0.17853 | 2.0508 | -119.8975 | 2.124 | -119.3985 | -119.4855 | -119.371 | -0.059509 | -0.059509 | -0.045776 | 3.9642 | 0.54474 | 1.0666 | 0.60425 | 1.1261 | -0.027466 | -0.027466 | 0.045776 | 0.4715 | 0.49896 | 0.38452 | 0.52643 | 0.41199 | 4.0237 | 121.962 | 0.49896 | 122.0215 | 121.9482 | 121.9482 | 121.8887 | 121.9208 | -122.0078 | -121.9757 | 121.9025 | 121.994 | 41.2903 | 119.6915
1443.7656 | 122.1588 | -121.2021 | 0.75531 | 0.01358 | -0.0059344 | 0.013275 | 0.069378 | -0.019335 | -0.024977 | -0.019828 | -0.00054937 | -0.0097411 | 0.063762 | 0.056046 | -0.018367 | -0.010527 | -0.01311 | -79.7058 | 0.6958 | -121.312 | 0.64087 | -117.16 | -120.195 | -120.6619 | -0.28839 | 0.71869 | -121.2708 | 0.72327 | -120.7718 | -120.8359 | -120.7718 | -0.10986 | -0.059509 | -0.11444 | 4.0421 | 0.54016 | 1.0071 | 0.65002 | 1.1169 | -0.068665 | -0.036621 | -0.032043 | 0.4303 | 0.4303 | 0.36621 | 0.49896 | 0.43488 | 4.1519 | 121.9528 | 0.49896 | 121.994 | 122.0078 | 121.9894 | 121.8979 | 121.9208 | -122.0673 | -122.0261 | 121.843 | 121.9254 | 41.4963 | 120.9137
1445.5469 | 121.9299 | -118.9453 | 2.8702 | 0.02121 | -0.00508 | 0.015838 | 0.069592 | -0.02318 | -0.024549 | -0.019401 | 0.0025024 | -0.0093139 | 0.06483 | 0.050492 | -0.018794 | -0.0094592 | -0.015033 | -77.8244 | 2.7969 | -119.0689 | 2.7557 | -114.8483 | -117.8741 | -118.3777 | -0.26093 | 2.8336 | -119.0048 | 2.8198 | -118.5379 | -118.6203 | -118.5013 | -0.1236 | -0.073242 | -0.11444 | 4.097 | 0.56763 | 1.0712 | 0.69122 | 1.1948 | -0.05951 | -0.036621 | -0.050354 | 0.40741 | 0.44403 | 0.32501 | 0.50354 | 0.38452 | 4.2206 | 121.8246 | 0.46692 | 121.8246 | 121.8658 | 121.8384 | 121.7422 | 121.7789 | -121.9391 | -121.875 | 121.701 | 121.7651 | 41.1209 | 118.6844
1447.3281 | 121.8292 | -119.0826 | 2.6871 | 0.01358 | -0.0035846 | 0.016052 | 0.068524 | -0.017626 | -0.024977 | -0.019615 | 0.0055542 | -0.0067505 | 0.06419 | 0.047074 | -0.021999 | -0.0101 | -0.013965 | -78.2455 | 2.6001 | -119.2017 | 2.5452 | -114.9536 | -117.984 | -118.5425 | -0.27008 | 2.6596 | -119.1513 | 2.5452 | -118.7531 | -118.808 | -118.7119 | -0.11902 | -0.086975 | -0.14191 | 4.129 | 0.54016 | 1.0986 | 0.65918 | 1.2177 | -0.068664 | -0.027466 | -0.14191 | 0.32959 | 0.37079 | 0.27466 | 0.43945 | 0.34332 | 4.248 | 121.7468 | 0.39825 | 121.6965 | 121.8018 | 121.8109 | 121.6827 | 121.7422 | -121.8887 | -121.8384 | 121.6278 | 121.6278 | 40.8371 | 118.8126
1449.0469 | 121.907 | -119.1467 | 2.5269 | 0.0059509 | -0.0035846 | 0.013916 | 0.069165 | -0.022326 | -0.023481 | -0.018333 | -0.00054937 | -0.0091003 | 0.062694 | 0.04152 | -0.018367 | -0.0092456 | -0.014392 | -78.4424 | 2.449 | -119.2932 | 2.4811 | -114.8483 | -117.9749 | -118.5287 | -0.09613 | 2.4902 | -119.22 | 2.5543 | -118.7027 | -118.7485 | -118.6844 | -0.14648 | -0.077819 | -0.045776 | 4.2984 | 0.61798 | 1.1719 | 0.76447 | 1.3184 | -0.073242 | -0.036621 | 0.027466 | 0.44403 | 0.46234 | 0.39825 | 0.53558 | 0.4715 | 4.4449 | 121.7743 | 0.51727 | 121.7743 | 121.7422 | 121.7102 | 121.5958 | 121.637 | -121.8201 | -121.7468 | 121.6278 | 121.701 | 40.7043 | 119.0506
1450.8281 | 121.6049 | -117.9977 | 3.6484 | 0.0059509 | -0.00508 | 0.012847 | 0.071515 | -0.019335 | -0.024549 | -0.018119 | 0.017761 | -0.0067505 | 0.06483 | 0.04152 | -0.020717 | -0.010955 | -0.01546 | -78.0807 | 3.5934 | -118.1625 | 3.3691 | -113.9557 | -116.8304 | -117.6086 | -0.23346 | 3.5385 | -118.1213 | 3.6118 | -117.7048 | -117.7734 | -117.6224 | -0.16479 | -0.054931 | -0.27923 | 4.0421 | 0.3891 | 1.1673 | 0.55389 | 1.3321 | -0.1236 | -0.10986 | -0.036621 | 0.29297 | 0.37537 | 0.22431 | 0.49896 | 0.3479 | 4.2068 | 121.5317 | 0.41656 | 121.7331 | 121.756 | 121.6599 | 121.5912 | 121.5363 | -121.8109 | -121.7697 | 121.3669 | 121.6095 | 39.917 | 117.7643
1452.5938 | 121.7056 | -118.9819 | 2.6642 | -0.0016786 | -0.0018756 | 0.014343 | 0.071942 | -0.020189 | -0.023695 | -0.017265 | 0.0025024 | -0.0069641 | 0.063121 | 0.038529 | -0.018794 | -0.008391 | -0.015887 | -80.2551 | 2.5909 | -119.0735 | 2.504 | -114.5462 | -117.8696 | -118.3731 | -0.25177 | 2.6367 | -119.0369 | 2.5543 | -118.634 | -118.7073 | -118.5928 | -0.091552 | -0.073243 | -0.16022 | 4.4357 | 0.60883 | 1.1124 | 0.70038 | 1.2039 | -0.054931 | -0.027466 | -0.10986 | 0.3479 | 0.3891 | 0.27466 | 0.44403 | 0.32959 | 4.5273 | 121.5775 | 0.40283 | 121.5912 | 121.6644 | 121.6736 | 121.5729 | 121.6187 | -121.7377 | -121.7011 | 121.4859 | 121.5363 | 38.7268 | 118.7302
1454.375 | 121.7377 | -118.9453 | 2.6688 | 0.02121 | -0.00273 | 0.016265 | 0.071087 | -0.017412 | -0.021131 | -0.018333 | 0.0055542 | -0.0088867 | 0.064617 | 0.048783 | -0.018581 | -0.0096728 | -0.016101 | -79.097 | 2.5909 | -119.101 | 2.5269 | -114.386 | -117.7643 | -118.3319 | -0.20142 | 2.6367 | -119.046 | 2.5909 | -118.5883 | -118.6523 | -118.5471 | -0.15564 | -0.07782 | -0.14191 | 4.5593 | 0.6134 | 1.181 | 0.76904 | 1.3367 | -0.10071 | -0.032043 | -0.07782 | 0.35706 | 0.39825 | 0.29297 | 0.49896 | 0.39368 | 4.715 | 121.6278 | 0.45776 | 121.637 | 121.6919 | 121.6827 | 121.5363 | 121.582 | -121.7697 | -121.7148 | 121.4722 | 121.5363 | 39.8483 | 118.7439
1456.1562 | 121.6919 | -118.9453 | 2.5955 | 0.036468 | -0.0040118 | 0.018829 | 0.06831 | -0.019762 | -0.019423 | -0.018333 | 0.0055542 | -0.0086731 | 0.065471 | 0.048569 | -0.017085 | -0.008391 | -0.017169 | -79.2847 | 2.5497 | -119.0323 | 2.5497 | -114.2029 | -117.6865 | -118.2724 | -0.07782 | 2.5681 | -119.0277 | 2.6001 | -118.5471 | -118.634 | -118.5333 | -0.086976 | -0.045776 | -0.045776 | 4.7424 | 0.67291 | 1.2588 | 0.75989 | 1.3458 | -0.082398 | -0.027466 | 0.004578 | 0.39825 | 0.41199 | 0.31128 | 0.49438 | 0.39368 | 4.8294 | 121.582 | 0.48065 | 121.6278 | 121.582 | 121.5958 | 121.4951 | 121.5134 | -121.6278 | -121.6232 | 121.4951 | 121.5454 | 39.6606 | 118.8675
1457.9219 | 121.7514 | -119.0964 | 2.4261 | 0.0059509 | -0.0025164 | 0.016479 | 0.071087 | -0.019121 | -0.0222 | -0.018547 | 0.0055542 | -0.0084595 | 0.063762 | 0.048783 | -0.016231 | -0.0077502 | -0.01781 | -79.6051 | 2.3621 | -119.22 | 2.3483 | -114.2899 | -117.7734 | -118.4326 | -0.24261 | 2.4078 | -119.1559 | 2.4399 | -118.6798 | -118.7622 | -118.6386 | -0.1236 | -0.064086 | -0.077819 | 4.8065 | 0.66376 | 1.3229 | 0.78735 | 1.4465 | -0.059509 | -0.01831 | 0.013733 | 0.41656 | 0.45776 | 0.33417 | 0.51727 | 0.39368 | 4.9301 | 121.5683 | 0.47607 | 121.5958 | 121.582 | 121.5637 | 121.4584 | 121.5042 | -121.6461 | -121.582 | 121.4447 | 121.5363 | 39.4913 | 118.8538
1459.7031 | 121.637 | -119.6274 | 1.9089 | 0.028839 | -0.0018756 | 0.016052 | 0.071942 | -0.019121 | -0.020491 | -0.019188 | 0.011658 | -0.0071777 | 0.064403 | 0.040024 | -0.021785 | -0.0092456 | -0.016742 | -80.0217 | 1.8585 | -119.7739 | 1.7624 | -114.6652 | -118.2037 | -118.9224 | -0.21515 | 1.8723 | -119.7052 | 1.8265 | -119.2337 | -119.3161 | -119.1971 | -0.14648 | -0.050354 | -0.14649 | 4.9622 | 0.70496 | 1.4236 | 0.85144 | 1.5701 | -0.07782 | -0.036622 | -0.082398 | 0.39368 | 0.4303 | 0.31128 | 0.50812 | 0.3891 | 5.1086 | 121.5363 | 0.4715 | 121.5317 | 121.6324 | 121.5775 | 121.4859 | 121.4996 | -121.6827 | -121.6141 | 121.3898 | 121.4539 | 39.6057 | 119.4122
1461.4375 | 121.4859 | -119.8196 | 1.6754 | 0.036468 | -0.0037982 | 0.015625 | 0.069165 | -0.020189 | -0.021345 | -0.01641 | 0.017761 | -0.0082459 | 0.063976 | 0.041306 | -0.022212 | -0.0101 | -0.015246 | -80.4016 | 1.6434 | -119.957 | 1.4969 | -114.7293 | -118.3365 | -119.0826 | -0.26093 | 1.6754 | -119.8883 | 1.5335 | -119.4489 | -119.5358 | -119.4168 | -0.13733 | -0.032043 | -0.17853 | 5.0903 | 0.737 | 1.4832 | 0.87433 | 1.6205 | -0.068665 | 0 | -0.14191 | 0.37079 | 0.40283 | 0.28381 | 0.4715 | 0.35248 | 5.2277 | 121.4539 | 0.43945 | 121.4218 | 121.6003 | 121.5637 | 121.463 | 121.4951 | -121.6324 | -121.5637 | 121.3165 | 121.3531 | 39.418 | 119.5587
1463.2188 | 121.344 | -120.4697 | 0.86975 | 0.0059509 | -0.0025164 | 0.016693 | 0.07301 | -0.019762 | -0.01985 | -0.01641 | -0.00054937 | -0.0080321 | 0.06483 | 0.043229 | -0.019435 | -0.0092456 | -0.015674 | -81.6467 | 0.7782 | -120.4971 | 0.65002 | -115.329 | -118.9407 | -119.7372 | -0.29755 | 0.87433 | -120.52 | 0.72784 | -120.1447 | -120.2408 | -120.0668 | -0.027465 | -0.091553 | -0.21973 | 5.1407 | 0.73242 | 1.5289 | 0.75989 | 1.5564 | -0.050354 | 0.004578 | -0.14191 | 0.32501 | 0.40283 | 0.22888 | 0.45319 | 0.27924 | 5.1682 | 121.1472 | 0.37537 | 121.2479 | 121.2753 | 121.3943 | 121.2479 | 121.344 | -121.3669 | -121.3898 | 121.1197 | 121.1975 | 38.8229 | 120.1721
1465 | 121.3623 | -118.8675 | 2.3117 | 0.028839 | -0.0037982 | 0.01712 | 0.069165 | -0.020403 | -0.017927 | -0.017692 | 0.014709 | -0.0097411 | 0.064617 | 0.047074 | -0.019008 | -0.0079638 | -0.014392 | -80.0766 | 2.2293 | -118.9957 | 2.2568 | -113.4155 | -117.2287 | -118.0298 | -0.20599 | 2.298 | -118.9362 | 2.3071 | -118.4601 | -118.5379 | -118.428 | -0.12817 | -0.082398 | -0.054932 | 5.452 | 0.83771 | 1.6388 | 0.96588 | 1.767 | -0.068664 | -0.013733 | -0.004578 | 0.40741 | 0.43945 | 0.32959 | 0.50812 | 0.39825 | 5.5801 | 121.2524 | 0.47607 | 121.2433 | 121.225 | 121.2341 | 121.0968 | 121.1655 | -121.3074 | -121.2479 | 121.1243 | 121.1746 | 38.7909 | 118.6615
1466.7188 | 121.701 | -121.4401 | 0.13275 | -0.0016786 | -0.0048664 | 0.015625 | 0.069165 | -0.023394 | -0.018568 | -0.018333 | 0.0055542 | -0.0084595 | 0.062481 | 0.048783 | -0.019863 | -0.0060412 | -0.013751 | -82.2418 | 0.032043 | -121.5179 | 0.064087 | -115.6494 | -119.4626 | -120.488 | -0.14191 | 0.086975 | -121.4493 | 0.11902 | -120.9274 | -121.0052 | -120.932 | -0.077819 | -0.10071 | -0.068664 | 5.7907 | 0.95215 | 1.9775 | 1.03 | 2.0554 | -0.009155 | -0.045776 | -0.013732 | 0.5127 | 0.50812 | 0.43488 | 0.51727 | 0.44403 | 5.8685 | 121.582 | 0.52185 | 121.5683 | 121.55 | 121.5363 | 121.4722 | 121.5271 | -121.6507 | -121.582 | 121.5042 | 121.5591 | 39.1983 | 121.2982
1468.5 | 121.7239 | -121.5454 | 0.16937 | 0.036468 | -0.0040118 | 0.016052 | 0.069592 | -0.020617 | -0.017714 | -0.017051 | 0.011658 | -0.0080321 | 0.06184 | 0.045365 | -0.020717 | -0.010314 | -0.019091 | -83.3862 | 0.086975 | -121.669 | -0.050354 | -115.773 | -119.3253 | -120.6757 | -0.2655 | 0.14191 | -121.6415 | -0.004578 | -121.138 | -121.2341 | -121.106 | -0.1236 | -0.082398 | -0.21973 | 5.7724 | 0.86975 | 2.2202 | 0.99335 | 2.3438 | -0.096131 | -0.027466 | -0.17395 | 0.40741 | 0.43945 | 0.31128 | 0.53558 | 0.40741 | 5.896 | 121.6187 | 0.50354 | 121.637 | 121.756 | 121.7834 | 121.6324 | 121.6873 | -121.8384 | -121.8109 | 121.4951 | 121.5408 | 38.1592 | 121.2799
1470.2812 | 121.8109 | -121.582 | 0.13733 | 0.0059509 | -0.00273 | 0.018615 | 0.07301 | -0.015917 | -0.0078869 | -0.01641 | 0.0055542 | -0.0091003 | 0.065899 | 0.03682 | -0.019008 | -0.0088184 | -0.016314 | -83.345 | 0.07782 | -121.6827 | -0.041199 | -115.6128 | -117.9428 | -120.7169 | -0.29755 | 0.10529 | -121.6461 | 0.073242 | -121.2112 | -121.2662 | -121.1334 | -0.10071 | -0.059509 | -0.17853 | 5.9692 | 0.86517 | 3.6392 | 0.96588 | 3.7399 | -0.064087 | -0.032043 | -0.064087 | 0.37079 | 0.44861 | 0.31586 | 0.5127 | 0.37994 | 6.0699 | 121.6415 | 0.43488 | 121.7194 | 121.7606 | 121.7514 | 121.6599 | 121.6873 | -121.8201 | -121.7834 | 121.5408 | 121.6553 | 38.237 | 121.2845
1472 | 121.8704 | -121.5271 | 0.21515 | 0.01358 | -0.0052936 | 0.018829 | 0.069378 | -0.019762 | 0.070726 | -0.015342 | 0.0025024 | -0.0088867 | 0.062053 | 0.043656 | -0.020931 | -0.009032 | -0.017383 | -77.8793 | 0.15564 | -121.6461 | 0.091553 | -115.3519 | -106.0318 | -120.5338 | -0.30212 | 0.21057 | -121.6003 | 0.15106 | -121.1151 | -121.2067 | -121.0785 | -0.11902 | -0.059509 | -0.1236 | 6.1752 | 0.99335 | 15.4953 | 1.1124 | 15.6143 | -0.073242 | -0.004578 | -0.064087 | 0.41199 | 0.44861 | 0.32044 | 0.52185 | 0.39368 | 6.2943 | 121.7377 | 0.48523 | 121.7514 | 121.8018 | 121.8109 | 121.6827 | 121.7377 | -121.8613 | -121.8155 | 121.6187 | 121.6782 | 43.6478 | 121.225
1473.7812 | 121.8979 | -121.55 | 0.19226 | 0.036468 | -0.00038018 | 0.018829 | 0.072583 | -0.019335 | 0.047869 | -0.016838 | 0.008606 | -0.0093139 | 0.065044 | 0.052628 | -0.018154 | -0.007323 | -0.017169 | -78.3463 | 0.10529 | -121.6919 | 0.10529 | -115.2283 | -109.9777 | -120.5383 | -0.25635 | 0.17395 | -121.6187 | 0.15564 | -121.1655 | -121.2204 | -121.1105 | -0.14191 | -0.086975 | -0.086975 | 6.3217 | 1.0117 | 11.5723 | 1.1536 | 11.7142 | -0.068664 | -0.018311 | -0.036621 | 0.38452 | 0.43945 | 0.32959 | 0.50812 | 0.39825 | 6.4636 | 121.7972 | 0.45319 | 121.7743 | 121.7972 | 121.7926 | 121.6553 | 121.7239 | -121.8842 | -121.8109 | 121.6553 | 121.7056 | 43.2037 | 121.2936
1475.5 | 121.875 | -121.3028 | 0.49439 | 0.01358 | -0.0010212 | 0.020538 | 0.072156 | -0.01784 | 0.33092 | -0.015983 | 0.0055542 | -0.0071777 | 0.064617 | 0.040879 | -0.020503 | -0.0098864 | -0.009692 | -61.6425 | 0.43945 | -121.3852 | 0.35248 | -114.6378 | -61.2946 | -120.2316 | -0.17395 | 0.48523 | -121.3486 | 0.42114 | -120.8771 | -120.9641 | -120.8359 | -0.082398 | -0.054932 | -0.14191 | 6.665 | 1.0712 | 60.0082 | 1.1536 | 60.0906 | -0.045777 | -0.009156 | -0.073242 | 0.42572 | 0.46692 | 0.33875 | 0.5127 | 0.38452 | 6.7474 | 121.7377 | 0.4715 | 121.7697 | 121.8246 | 121.8338 | 121.7422 | 121.788 | -121.8796 | -121.843 | 121.6553 | 121.7239 | 59.6603 | 121.1288
1477.2656 | 121.8704 | -121.1197 | 0.6546 | 0.01358 | -0.0020892 | 0.01947 | 0.070019 | -0.022326 | 0.48708 | -0.015556 | 0.008606 | -0.0054687 | 0.065471 | 0.04451 | -0.018154 | -0.010314 | -0.016955 | -54.8538 | 0.58136 | -121.2296 | 0.5127 | -114.1617 | -40.9103 | -119.9432 | -0.19226 | 0.62714 | -121.2112 | 0.56763 | -120.7352 | -120.8176 | -120.6894 | -0.10986 | -0.073242 | -0.14191 | 6.958 | 1.1765 | 80.2094 | 1.2863 | 80.3192 | -0.091553 | -0.027466 | -0.086975 | 0.38452 | 0.4303 | 0.30212 | 0.52185 | 0.39368 | 7.0679 | 121.7422 | 0.47607 | 121.7789 | 121.8109 | 121.8384 | 121.7011 | 121.7468 | -121.8842 | -121.8658 | 121.6324 | 121.6873 | 66.2659 | 120.9274
1479.0469 | 121.8384 | -121.0327 | 0.74158 | 0.02121 | -0.0035846 | 0.022674 | 0.070447 | -0.021685 | 0.58364 | -0.017479 | 0.0025024 | -0.0071777 | 0.064403 | 0.04921 | -0.019222 | -0.009032 | -0.018237 | -49.1455 | 0.66376 | -121.1288 | 0.51727 | -113.5254 | -26.152 | -119.8563 | -0.32501 | 0.71869 | -121.1014 | 0.60883 | -120.7123 | -120.7947 | -120.6299 | -0.09613 | -0.07782 | -0.2243 | 7.5073 | 1.1765 | 94.8807 | 1.2726 | 94.9768 | -0.068664 | -0.022888 | -0.13275 | 0.32043 | 0.40283 | 0.23804 | 0.4715 | 0.3067 | 7.6035 | 121.6461 | 0.3891 | 121.7102 | 121.7926 | 121.8201 | 121.6965 | 121.7514 | -121.8704 | -121.843 | 121.55 | 121.6415 | 71.8872 | 120.7077
1480.7656 | 121.9574 | -120.9641 | 0.7782 | 0.01358 | -0.00508 | 0.021606 | 0.068097 | -0.022326 | 0.62999 | -0.018974 | -0.0066528 | -0.011023 | 0.065258 | 0.047501 | -0.019008 | -0.0092456 | -0.012469 | -45.9366 | 0.69122 | -121.0373 | 0.67291 | -112.0926 | -18.0313 | -119.6686 | -0.25177 | 0.72784 | -121.0281 | 0.76446 | -120.5154 | -120.575 | -120.4926 | -0.073242 | -0.086975 | -0.10528 | 8.8715 | 1.2955 | 102.9327 | 1.3687 | 103.006 | -0.064087 | -0.050354 | -0.013733 | 0.44861 | 0.4715 | 0.3891 | 0.53558 | 0.45319 | 8.9447 | 121.7102 | 0.5127 | 121.7926 | 121.7285 | 121.756 | 121.6553 | 121.6919 | -121.8155 | -121.8063 | 121.637 | 121.7285 | 75.0275 | 120.7123
1482.5469 | 121.843 | -120.9732 | 0.80109 | 0.02121 | -0.0040118 | 0.022247 | 0.070233 | -0.014849 | 0.64366 | -0.013633 | 0.011658 | -0.0073913 | 0.064617 | 0.041306 | -0.021144 | -0.009032 | -0.016528 | -40.0864 | 0.7782 | -121.0739 | 0.61798 | -110.9985 | -15.8524 | -119.6411 | -0.26093 | 0.82398 | -121.0556 | 0.68665 | -120.5933 | -120.6482 | -120.5246 | -0.10071 | -0.022888 | -0.1831 | 9.9747 | 1.3321 | 105.1209 | 1.4328 | 105.2216 | -0.082397 | 0.022889 | -0.11444 | 0.37994 | 0.44861 | 0.32501 | 0.53101 | 0.40741 | 10.0754 | 121.6919 | 0.46234 | 121.7422 | 121.8521 | 121.8796 | 121.7514 | 121.7972 | -121.875 | -121.8567 | 121.5912 | 121.6599 | 80.8868 | 120.7123
1484.2656 | 121.8796 | -120.9732 | 0.80109 | -0.0016786 | -0.0014484 | 0.024169 | 0.066815 | -0.016985 | 0.64623 | -0.012992 | -0.00054937 | -0.0099549 | 0.066112 | 0.048569 | -0.020503 | -0.0098864 | -0.015887 | -39.3814 | 0.72784 | -121.0144 | 0.737 | -110.3394 | -14.5798 | -119.4992 | -0.20142 | 0.76904 | -121.0144 | 0.737 | -120.5521 | -120.6162 | -120.5246 | -0.041198 | -0.073242 | -0.064086 | 10.6339 | 1.474 | 106.3934 | 1.5152 | 106.4346 | -0.041198 | -0.032043 | -0.064086 | 0.42114 | 0.44861 | 0.35706 | 0.48981 | 0.39825 | 10.675 | 121.7514 | 0.46234 | 121.7514 | 121.7422 | 121.7834 | 121.7011 | 121.7422 | -121.8155 | -121.8155 | 121.7102 | 121.7102 | 81.5918 | 120.7718
1486.0312 | 121.8475 | -120.9732 | 0.8194 | 0.01358 | -0.0037982 | 0.023742 | 0.06596 | -0.019335 | 0.64516 | -0.018119 | -0.00054937 | -0.0091003 | 0.063976 | 0.047074 | -0.02029 | -0.0086048 | -0.018023 | -39.679 | 0.72327 | -121.019 | 0.69122 | -109.964 | -13.8977 | -119.4534 | -0.2243 | 0.77362 | -121.0419 | 0.70038 | -120.5704 | -120.6528 | -120.5338 | -0.045776 | -0.09613 | -0.12817 | 11.0092 | 1.5198 | 107.0755 | 1.5656 | 107.1213 | -0.068664 | -0.045776 | -0.11902 | 0.40283 | 0.43945 | 0.32044 | 0.50812 | 0.3891 | 11.055 | 121.7102 | 0.4715 | 121.7422 | 121.7422 | 121.8155 | 121.6965 | 121.7468 | -121.8384 | -121.8613 | 121.6644 | 121.6736 | 81.2943 | 120.7489
1487.75 | 121.8613 | -120.9412 | 0.85144 | 0.036468 | -0.0014484 | 0.023315 | 0.070447 | -0.018908 | 0.649 | -0.016838 | 0.011658 | -0.0050415 | 0.064403 | 0.043229 | -0.018154 | -0.0094592 | -0.014819 | -39.9216 | 0.79651 | -121.0098 | 0.65002 | -109.6344 | -13.0554 | -119.426 | -0.26093 | 0.83313 | -121.0144 | 0.72327 | -120.5612 | -120.6299 | -120.5017 | -0.068665 | -0.054931 | -0.20142 | 11.3068 | 1.5152 | 107.8857 | 1.5839 | 107.9544 | -0.073242 | -0.01831 | -0.12817 | 0.37994 | 0.43945 | 0.31128 | 0.51269 | 0.38452 | 11.3754 | 121.6599 | 0.45319 | 121.7377 | 121.8063 | 121.8475 | 121.7377 | 121.7743 | -121.8613 | -121.8658 | 121.5912 | 121.6644 | 81.0196 | 120.6802
1489.5469 | 121.8201 | -120.9412 | 0.85602 | 0.0059509 | -0.0040118 | 0.023101 | 0.069806 | -0.022539 | 0.64559 | -0.013633 | 0.0025024 | -0.0080321 | 0.065685 | 0.040024 | -0.023281 | -0.0088184 | -0.017596 | -39.6973 | 0.80109 | -120.9961 | 0.65002 | -108.9981 | -12.5702 | -119.3802 | -0.26093 | 0.85602 | -121.0327 | 0.70496 | -120.5933 | -120.6482 | -120.5338 | -0.054932 | -0.054932 | -0.20599 | 11.9431 | 1.561 | 108.371 | 1.6159 | 108.4259 | -0.091553 | 0 | -0.15106 | 0.3479 | 0.40741 | 0.29297 | 0.49896 | 0.38452 | 11.998 | 121.6461 | 0.43945 | 121.7377 | 121.7972 | 121.8887 | 121.7422 | 121.7972 | -121.8521 | -121.8887 | 121.5912 | 121.6461 | 81.2439 | 120.6802
1491.3281 | 121.8658 | -120.932 | 0.87891 | 0.01358 | -0.0020892 | 0.02481 | 0.068738 | -0.022539 | 0.64729 | -0.011924 | 0.008606 | -0.0069641 | 0.065044 | 0.038529 | -0.019649 | -0.010314 | -0.018664 | -38.9465 | 0.79651 | -120.9915 | 0.737 | -108.815 | -12.0346 | -119.252 | -0.19684 | 0.83313 | -120.9595 | 0.78278 | -120.5154 | -120.5795 | -120.4697 | -0.059509 | -0.082397 | -0.14191 | 12.117 | 1.68 | 108.8974 | 1.7395 | 108.9569 | -0.027466 | -0.045776 | -0.09613 | 0.41657 | 0.46234 | 0.35248 | 0.48981 | 0.37994 | 12.1765 | 121.7285 | 0.44403 | 121.7422 | 121.788 | 121.7926 | 121.7285 | 121.7651 | -121.8704 | -121.8384 | 121.669 | 121.7148 | 81.9855 | 120.7352
1493.0312 | 121.9345 | -120.9045 | 0.82855 | 0.0059509 | -0.0023028 | 0.026947 | 0.06831 | -0.017626 | 0.64601 | -0.011711 | 0.0025024 | -0.0080321 | 0.062481 | 0.053483 | -0.017726 | -0.009032 | -0.016955 | -39.3448 | 0.76904 | -120.9503 | 0.70496 | -108.3847 | -11.7645 | -119.1925 | -0.24719 | 0.78735 | -120.9824 | 0.84686 | -120.4742 | -120.5521 | -120.4102 | -0.045776 | -0.059509 | -0.1236 | 12.5198 | 1.712 | 109.14 | 1.7578 | 109.1858 | -0.07782 | -0.041198 | 0.018311 | 0.4303 | 0.49438 | 0.35248 | 0.5722 | 0.4303 | 12.5656 | 121.6553 | 0.50812 | 121.8292 | 121.7194 | 121.7697 | 121.6736 | 121.6919 | -121.7789 | -121.8109 | 121.6095 | 121.7514 | 81.5598 | 120.6573
1494.8125 | 121.962 | -120.8908 | 0.81482 | 0.0059509 | -0.0014484 | 0.02716 | 0.067242 | -0.018908 | 0.64388 | -0.013847 | 0.0055542 | -0.0093139 | 0.062481 | 0.040879 | -0.017085 | -0.0092456 | -0.016528 | -39.0884 | 0.75531 | -120.9229 | 0.77362 | -107.7484 | -11.4075 | -119.0048 | -0.21057 | 0.77362 | -120.9686 | 0.8606 | -120.4514 | -120.5429 | -120.401 | -0.032044 | -0.059509 | -0.041198 | 13.1424 | 1.886 | 109.4833 | 1.918 | 109.5154 | -0.07782 | -0.041198 | 0.045777 | 0.43945 | 0.48981 | 0.3479 | 0.56763 | 0.42572 | 13.1744 | 121.6965 | 0.51727 | 121.8292 | 121.6782 | 121.7422 | 121.6461 | 121.6644 | -121.7377 | -121.7834 | 121.6644 | 121.7514 | 81.8024 | 120.6802
1496.6094 | 121.8338 | -120.9229 | 0.84686 | 0.0059509 | -0.0023028 | 0.026733 | 0.069806 | -0.017626 | 0.64302 | -0.010429 | 0.0055542 | -0.0084595 | 0.06483 | 0.04387 | -0.016658 | -0.008391 | -0.0092648 | -39.8804 | 0.79193 | -120.9961 | 0.63629 | -107.428 | -11.2198 | -119.0277 | -0.32959 | 0.84686 | -120.9595 | 0.72784 | -120.5841 | -120.6619 | -120.5109 | -0.073242 | -0.054932 | -0.21057 | 13.4949 | 1.8951 | 109.7031 | 1.9684 | 109.7763 | -0.036621 | 0 | -0.11902 | 0.33875 | 0.41199 | 0.26093 | 0.44861 | 0.29755 | 13.5681 | 121.6324 | 0.37537 | 121.6873 | 121.788 | 121.8063 | 121.7148 | 121.7697 | -121.843 | -121.8063 | 121.5591 | 121.6507 | 81.0425 | 120.5933
1498.3906 | 121.907 | -120.9457 | 0.83313 | 0.0059509 | -0.0014484 | 0.026306 | 0.069806 | -0.023394 | 0.64409 | -0.0087201 | 0.008606 | -0.0091003 | 0.066753 | 0.050065 | -0.021785 | -0.007323 | -0.016742 | -39.9033 | 0.77362 | -120.9457 | 0.72784 | -106.8237 | -10.9131 | -118.8126 | -0.28839 | 0.81024 | -120.9824 | 0.7782 | -120.5109 | -120.5704 | -120.4651 | 0 | -0.059509 | -0.10529 | 14.122 | 2.1332 | 110.0327 | 2.1332 | 110.0327 | -0.036621 | -0.022888 | -0.054932 | 0.43488 | 0.48065 | 0.37537 | 0.51727 | 0.41199 | 14.122 | 121.6736 | 0.4715 | 121.7606 | 121.7194 | 121.7926 | 121.7194 | 121.756 | -121.7789 | -121.8155 | 121.6736 | 121.7239 | 81.0425 | 120.6573
1500.1562 | 121.9574 | -120.8817 | 0.83313 | 0.0059509 | -0.0029438 | 0.028656 | 0.068097 | -0.020403 | 0.64195 | -0.0087201 | -0.00054937 | -0.0071777 | 0.062053 | 0.049424 | -0.021785 | -0.010955 | -0.016955 | -38.7955 | 0.75989 | -120.9412 | 0.79193 | -106.4209 | -10.5423 | -118.5883 | -0.15564 | 0.80109 | -120.9503 | 0.84686 | -120.4239 | -120.5063 | -120.4147 | -0.059509 | -0.073242 | -0.041199 | 14.4608 | 2.2934 | 110.3394 | 2.3529 | 110.3989 | -0.068664 | -0.032044 | 0.013733 | 0.45776 | 0.46692 | 0.37537 | 0.53558 | 0.44403 | 14.5203 | 121.7331 | 0.52643 | 121.7972 | 121.7011 | 121.7514 | 121.6415 | 121.6827 | -121.7743 | -121.7834 | 121.6736 | 121.7285 | 82.0862 | 120.726
1501.8594 | 121.8155 | -120.9229 | 0.87433 | 0.0059509 | -0.0029438 | 0.027801 | 0.069165 | -0.019335 | 0.6396 | -0.0070111 | 0.0055542 | -0.0095275 | 0.059917 | 0.048142 | -0.022853 | -0.0096728 | -0.016528 | -39.0839 | 0.76904 | -121.019 | 0.6958 | -106.192 | -10.4919 | -118.5516 | -0.27924 | 0.82398 | -120.9595 | 0.72327 | -120.5612 | -120.6207 | -120.52 | -0.09613 | -0.10529 | -0.17853 | 14.7308 | 2.3712 | 110.4309 | 2.4673 | 110.527 | -0.036621 | -0.050354 | -0.15106 | 0.36163 | 0.40283 | 0.30212 | 0.43945 | 0.33875 | 14.827 | 121.7148 | 0.39826 | 121.6827 | 121.788 | 121.7834 | 121.6919 | 121.7468 | -121.8933 | -121.8338 | 121.6187 | 121.6461 | 81.839 | 120.6436
1503.6406 | 121.907 | -120.9 | 0.83771 | 0.02121 | -0.004439 | 0.029083 | 0.069165 | -0.018053 | 0.63918 | -0.0089337 | 0.0025024 | -0.0095275 | 0.063335 | 0.048997 | -0.01794 | -0.0075366 | -0.012042 | -39.1708 | 0.75989 | -120.9778 | 0.72327 | -105.835 | -10.35 | -118.4326 | -0.28839 | 0.79651 | -120.9778 | 0.79651 | -120.4788 | -120.5429 | -120.4605 | -0.07782 | -0.07782 | -0.11444 | 15.065 | 2.4673 | 110.5499 | 2.5452 | 110.6277 | -0.07782 | -0.041199 | -0.041199 | 0.42114 | 0.43945 | 0.35706 | 0.51727 | 0.43488 | 15.1428 | 121.7011 | 0.49896 | 121.7743 | 121.7377 | 121.7743 | 121.6599 | 121.6965 | -121.8155 | -121.8155 | 121.6232 | 121.6965 | 81.7291 | 120.6116
1505.4219 | 121.8613 | -120.932 | 0.85144 | 0.028839 | -0.00059378 | 0.032501 | 0.070874 | -0.018053 | 0.63426 | -0.0070111 | 0.008606 | -0.0076049 | 0.066753 | 0.04451 | -0.020717 | -0.011382 | -0.011187 | -40.947 | 0.79193 | -121.0052 | 0.70953 | -105.1346 | -10.1852 | -118.2404 | -0.2243 | 0.83313 | -120.9915 | 0.7782 | -120.52 | -120.5887 | -120.4742 | -0.073242 | -0.059509 | -0.14191 | 15.7974 | 2.6917 | 110.7468 | 2.7649 | 110.82 | -0.059509 | -0.01831 | -0.073242 | 0.41199 | 0.45776 | 0.34332 | 0.51727 | 0.40283 | 15.8707 | 121.7148 | 0.4715 | 121.7697 | 121.7972 | 121.8246 | 121.7239 | 121.7651 | -121.8567 | -121.843 | 121.6415 | 121.7102 | 79.985 | 120.7077
1507.1875 | 121.8933 | -120.8817 | 0.85602 | -0.0016786 | -0.0010212 | 0.033569 | 0.069806 | -0.025103 | 0.63512 | -0.0031659 | 0.008606 | -0.0082459 | 0.063335 | 0.047501 | -0.020503 | -0.010955 | -0.017383 | -40.86 | 0.75073 | -120.9503 | 0.78278 | -104.3747 | -9.993 | -117.9886 | -0.19684 | 0.81024 | -120.9549 | 0.79193 | -120.4697 | -120.5292 | -120.4468 | -0.068664 | -0.10529 | -0.073242 | 16.507 | 2.8931 | 110.8887 | 2.9617 | 110.9573 | -0.073242 | -0.045776 | -0.064087 | 0.41199 | 0.43488 | 0.35248 | 0.50812 | 0.42572 | 16.5756 | 121.7331 | 0.48523 | 121.7468 | 121.701 | 121.7651 | 121.6324 | 121.6919 | -121.8063 | -121.8109 | 121.6644 | 121.6736 | 80.0217 | 120.6848
1508.9844 | 121.9666 | -120.8405 | 0.84686 | 0.01358 | -0.0010212 | 0.031646 | 0.068738 | -0.019549 | 0.63063 | -0.0033795 | 0.0055542 | -0.0099549 | 0.063549 | 0.042374 | -0.018367 | -0.010314 | -0.015887 | -41.6061 | 0.75989 | -120.9549 | 0.80566 | -104.1092 | -9.906 | -117.5125 | -0.16479 | 0.79651 | -120.9503 | 0.86517 | -120.3873 | -120.4742 | -120.3735 | -0.11444 | -0.086975 | -0.041199 | 16.7313 | 3.3279 | 110.9344 | 3.4424 | 111.0489 | -0.10986 | -0.050354 | 0.01831 | 0.45319 | 0.46692 | 0.36621 | 0.57678 | 0.47607 | 16.8457 | 121.7606 | 0.56305 | 121.8155 | 121.7148 | 121.7468 | 121.6003 | 121.637 | -121.8018 | -121.7972 | 121.6461 | 121.7056 | 79.2343 | 120.6757
1510.7656 | 121.8658 | -120.8725 | 0.87433 | 0.02121 | -0.00038018 | 0.033355 | 0.072583 | -0.019976 | 0.62978 | -0.00081607 | 0.011658 | -0.0061095 | 0.063976 | 0.04451 | -0.019649 | -0.011168 | -0.017169 | -45.3873 | 0.8194 | -120.9412 | 0.75531 | -103.7201 | -10.0754 | -117.3798 | -0.19684 | 0.84228 | -120.9412 | 0.81024 | -120.4926 | -120.5612 | -120.4514 | -0.068664 | -0.054932 | -0.11902 | 17.1524 | 3.4927 | 110.7971 | 3.5614 | 110.8658 | -0.068664 | -0.032044 | -0.064087 | 0.37994 | 0.42114 | 0.31128 | 0.48981 | 0.37994 | 17.2211 | 121.6965 | 0.44861 | 121.7514 | 121.7606 | 121.7834 | 121.6919 | 121.7148 | -121.8155 | -121.8155 | 121.6278 | 121.6827 | 75.4852 | 120.6757
1512.5469 | 121.8979 | -120.8633 | 0.84228 | 0.036468 | 0.00047422 | 0.035278 | 0.071728 | -0.017626 | 0.62892 | 0.0040973 | 0.014709 | -0.0073913 | 0.065685 | 0.046006 | -0.017726 | -0.0092456 | -0.012896 | -44.5908 | 0.79193 | -120.9274 | 0.80566 | -103.2028 | -10.0067 | -116.7618 | -0.2243 | 0.82855 | -120.9503 | 0.85144 | -120.4605 | -120.5338 | -120.4193 | -0.064087 | -0.050354 | -0.036621 | 17.6605 | 4.1016 | 110.8566 | 4.1656 | 110.9207 | -0.086975 | -0.013733 | 0.009155 | 0.40283 | 0.44403 | 0.32959 | 0.531 | 0.41656 | 17.7246 | 121.7331 | 0.48981 | 121.8018 | 121.7194 | 121.7789 | 121.6553 | 121.6919 | -121.7697 | -121.7926 | 121.669 | 121.7148 | 76.2726 | 120.639
1514.2656 | 121.8018 | -120.9091 | 0.90179 | 0.01358 | -0.0012348 | 0.032714 | 0.072156 | -0.019121 | 0.62401 | 0.0096515 | 0.014709 | -0.0080321 | 0.06419 | 0.041306 | -0.022212 | -0.010314 | -0.017596 | -44.4855 | 0.85144 | -120.9641 | 0.6958 | -102.7634 | -10.0891 | -115.8508 | -0.29755 | 0.90179 | -120.9641 | 0.74616 | -120.5154 | -120.6024 | -120.4651 | -0.054931 | -0.050354 | -0.20599 | 18.1458 | 5.0583 | 110.82 | 5.1132 | 110.8749 | -0.054931 | 0 | -0.15564 | 0.39368 | 0.44403 | 0.3067 | 0.49896 | 0.36163 | 18.2007 | 121.6599 | 0.44861 | 121.7102 | 121.8155 | 121.8658 | 121.7606 | 121.8109 | -121.8658 | -121.8658 | 121.6049 | 121.6553 | 76.4236 | 120.6116
1516.0312 | 121.8842 | -121.5317 | 0.27924 | 0.028839 | -0.001662 | 0.045745 | 0.0020871 | 0.059706 | 0.069445 | -0.020897 | 0.008606 | -0.0063233 | 0.065899 | 0.046006 | -0.019863 | -0.010955 | -0.016742 | -40.5624 | 0.2243 | -121.6599 | -94.1528 | 0.24261 | -2.4811 | -15.9897 | -0.24719 | 0.26093 | -121.5958 | 0.1831 | -121.1426 | -121.2067 | -121.0693 | -0.12817 | -0.054932 | -94.4321 | 121.7743 | 105.542 | 119.0506 | 105.6702 | 119.1788 | -0.064087 | -0.018311 | -0.096131 | 0.3891 | 0.46234 | 0.32501 | 0.52643 | 0.3891 | 121.9025 | 27.507 | 0.45319 | 121.7789 | 121.8842 | 121.8567 | 121.756 | 121.7926 | -121.9391 | -121.875 | 27.3788 | 121.7148 | 80.9692 | 121.2845
1517.7969 | 121.875 | -121.5363 | 0.30212 | -0.0016786 | -0.0025164 | 0.045959 | 0.0012325 | 0.055433 | 0.070086 | -0.021751 | 0.0055542 | -0.0088867 | 0.065044 | 0.044297 | -0.021358 | -0.0096728 | -0.016742 | -42.952 | 0.21515 | -121.6644 | -94.043 | 0.23804 | -2.7969 | -16.5207 | -0.28381 | 0.26093 | -121.6461 | 0.14191 | -121.1746 | -121.2616 | -121.138 | -0.12817 | -0.086975 | -94.3451 | 121.7743 | 105.0156 | 118.7393 | 105.1437 | 118.8675 | -0.10986 | -0.041199 | -0.16022 | 0.36163 | 0.39825 | 0.27466 | 0.50812 | 0.38452 | 121.9025 | 27.6215 | 0.4715 | 121.788 | 121.8796 | 121.907 | 121.7514 | 121.7972 | -121.9666 | -121.9482 | 27.4933 | 121.6782 | 78.5843 | 121.2524
1519.5156 | 122.0078 | -121.5134 | 0.2655 | 0.028839 | -0.00273 | 0.049591 | -4.906e-05 | 0.060346 | 0.073504 | -0.022819 | 0.014709 | -0.0071777 | 0.065471 | 0.044724 | -0.015377 | -0.0077502 | -0.016314 | -41.4597 | 0.20142 | -121.6232 | -93.0542 | 0.37537 | -2.7786 | -16.5619 | -0.21515 | 0.23346 | -121.5912 | 0.27924 | -121.0785 | -121.1517 | -121.0327 | -0.10986 | -0.064087 | -93.3197 | 121.8887 | 104.9515 | 118.7347 | 105.0613 | 118.8446 | -0.07782 | -0.032044 | 0.013733 | 0.43488 | 0.48065 | 0.36163 | 0.55847 | 0.43945 | 121.9986 | 28.569 | 0.5127 | 121.8704 | 121.8246 | 121.8246 | 121.7148 | 121.7468 | -121.8887 | -121.8567 | 28.4592 | 121.7926 | 80.0537 | 121.2982
1521.2969 | 121.8933 | -121.5866 | 0.30212 | -0.0016786 | -0.00038018 | 0.045959 | 0.0010189 | 0.05522 | 0.069872 | -0.023033 | 0.0025024 | -0.0069641 | 0.065685 | 0.038315 | -0.023494 | -0.010314 | -0.013751 | -40.2145 | 0.22888 | -121.6782 | -92.9901 | 0.22888 | -2.8931 | -16.4429 | -0.32044 | 0.3067 | -121.6415 | 0.13275 | -121.2067 | -121.2753 | -121.1426 | -0.091553 | -0.073242 | -93.2922 | 121.8155 | 105.1437 | 118.6935 | 105.2353 | 118.7851 | -0.054932 | 0.004578 | -0.16937 | 0.37994 | 0.44403 | 0.31128 | 0.49896 | 0.36621 | 121.907 | 28.6881 | 0.43488 | 121.7743 | 121.907 | 121.9482 | 121.8155 | 121.8933 | -121.9803 | -121.9437 | 28.5965 | 121.7194 | 81.3721 | 121.2662
1523.0625 | 122.0444 | -121.5225 | 0.30212 | 0.0059509 | -0.0018756 | 0.04895 | 0.0010189 | 0.057356 | 0.069872 | -0.026023 | 0.0025024 | -0.0093139 | 0.063549 | 0.042588 | -0.019435 | -0.010741 | -0.02016 | -38.3057 | 0.20599 | -121.6461 | -92.7109 | 0.40283 | -2.7557 | -16.0904 | -0.16937 | 0.25635 | -121.5958 | 0.28381 | -121.019 | -121.1014 | -121.0327 | -0.1236 | -0.09613 | -93.013 | 121.9254 | 105.4321 | 118.7668 | 105.5557 | 118.8904 | -0.073242 | -0.045776 | -0.018311 | 0.50354 | 0.48981 | 0.42114 | 0.56305 | 0.49439 | 122.049 | 28.9352 | 0.57678 | 121.8796 | 121.8521 | 121.8521 | 121.7285 | 121.7789 | -121.9482 | -121.8979 | 28.8116 | 121.8063 | 83.2169 | 121.3531
1524.8438 | 122.0261 | -121.5225 | 0.28381 | -0.0093076 | -0.0031574 | 0.048522 | 0.00059174 | 0.056715 | 0.069658 | -0.021324 | 0.008606 | -0.0071777 | 0.06718 | 0.041306 | -0.014308 | -0.0062548 | -0.016742 | -38.0859 | 0.24261 | -121.6232 | -92.6056 | 0.29755 | -2.7924 | -16.6351 | -0.24719 | 0.26093 | -121.6232 | 0.29755 | -121.1105 | -121.1884 | -121.0281 | -0.10071 | -0.041198 | -92.8894 | 121.8201 | 104.8874 | 118.7302 | 104.9881 | 118.8309 | -0.10071 | -0.022888 | 0.013733 | 0.41199 | 0.49438 | 0.33417 | 0.59509 | 0.43488 | 121.9208 | 29.0176 | 0.5127 | 121.9208 | 121.8658 | 121.8842 | 121.7651 | 121.7834 | -121.907 | -121.907 | 28.9169 | 121.8201 | 83.4366 | 121.2753
1526.5625 | 121.9894 | -121.5454 | 0.28839 | 0.028839 | -0.00038018 | 0.050018 | -0.00026266 | 0.056288 | 0.072222 | -0.021965 | 0.014709 | -0.0073913 | 0.062267 | 0.044724 | -0.018367 | -0.0081774 | -0.013965 | -38.0447 | 0.2243 | -121.6415 | -92.5735 | 0.35706 | -2.7328 | -16.7862 | -0.29755 | 0.27924 | -121.6141 | 0.25635 | -121.1426 | -121.2021 | -121.1105 | -0.096131 | -0.064087 | -92.8619 | 121.9025 | 104.7592 | 118.8126 | 104.8553 | 118.9087 | -0.068665 | -0.009155 | -0.032043 | 0.40283 | 0.43488 | 0.34332 | 0.50354 | 0.41199 | 121.9986 | 29.068 | 0.4715 | 121.8704 | 121.8658 | 121.8933 | 121.7697 | 121.8246 | -121.9299 | -121.9025 | 28.9719 | 121.8018 | 83.5007 | 121.2479
1528.3281 | 122.0627 | -121.5179 | 0.28381 | -0.0016786 | -0.0029438 | 0.049377 | -0.0026127 | 0.059492 | 0.071154 | -0.020897 | 0.0055542 | -0.0078185 | 0.06184 | 0.054337 | -0.019863 | -0.0094592 | -0.012896 | -46.2433 | 0.21057 | -121.6553 | -92.5095 | 0.39825 | -2.6962 | -17.07 | -0.18768 | 0.24261 | -121.5683 | 0.32044 | -121.051 | -121.1105 | -121.019 | -0.13733 | -0.073242 | -92.7933 | 121.9162 | 104.4479 | 118.8217 | 104.5853 | 118.959 | -0.050354 | -0.041198 | 0.036622 | 0.46692 | 0.49896 | 0.40741 | 0.54932 | 0.45776 | 122.0535 | 29.1458 | 0.51727 | 121.8887 | 121.8658 | 121.8109 | 121.7285 | 121.7606 | -121.9391 | -121.8521 | 29.0085 | 121.8384 | 75.2747 | 121.3303
1530.0469 | 122.0535 | -121.5546 | 0.28381 | 0.036468 | 4.7022e-05 | 0.055572 | 0.0018735 | 0.058851 | 0.073931 | -0.022178 | 0.017761 | -0.0065369 | 0.064617 | 0.04686 | -0.016445 | -0.0088184 | -0.019305 | -45.7993 | 0.21515 | -121.6415 | -91.5619 | 0.40283 | -2.7054 | -16.9281 | -0.21057 | 0.28381 | -121.5958 | 0.29755 | -121.1105 | -121.1746 | -121.0602 | -0.086976 | -0.068664 | -91.8457 | 121.9574 | 104.6265 | 118.8492 | 104.7134 | 118.9362 | -0.041199 | 0 | 0.013733 | 0.44403 | 0.49438 | 0.37994 | 0.53558 | 0.42114 | 122.0444 | 30.0797 | 0.48523 | 121.8933 | 121.8567 | 121.8796 | 121.7697 | 121.8384 | -121.9254 | -121.8796 | 29.9927 | 121.8521 | 75.7553 | 121.344
1531.8125 | 122.0673 | -121.5317 | 0.3067 | 0.01358 | 0.0015424 | 0.056427 | -0.0011173 | 0.059706 | 0.071795 | -0.021537 | 0.0025024 | -0.0073913 | 0.064403 | 0.04451 | -0.017513 | -0.0096728 | -0.016528 | -45.369 | 0.22888 | -121.637 | -87.5061 | 0.36621 | -2.7695 | -16.6168 | -0.22888 | 0.25635 | -121.6003 | 0.32501 | -121.0968 | -121.1838 | -121.0464 | -0.10529 | -0.07782 | -87.8128 | 121.8979 | 104.9149 | 118.7622 | 105.0201 | 118.8675 | -0.068665 | -0.050354 | 0.01831 | 0.43488 | 0.48523 | 0.3479 | 0.55389 | 0.41656 | 122.0032 | 34.1309 | 0.50354 | 121.9254 | 121.8658 | 121.8567 | 121.7606 | 121.788 | -121.9437 | -121.907 | 34.0256 | 121.8567 | 76.1627 | 121.3028
1533.5938 | 122.0627 | -121.5546 | 0.3067 | 0.02121 | 4.7022e-05 | 0.058349 | -0.0013309 | 0.056288 | 0.070726 | -0.023887 | 0.0025024 | -0.0091003 | 0.063549 | 0.044083 | -0.019863 | -0.0081774 | -0.013537 | -47.1085 | 0.2243 | -121.6736 | -80.2689 | 0.43488 | -2.6871 | -15.3534 | -0.19226 | 0.27008 | -121.582 | 0.30212 | -121.0648 | -121.1197 | -121.0556 | -0.11902 | -0.082398 | -80.5756 | 121.9894 | 106.2012 | 118.8675 | 106.3202 | 118.9865 | -0.027466 | -0.036621 | -0.004578 | 0.48981 | 0.49896 | 0.43487 | 0.52643 | 0.46234 | 122.1085 | 41.4047 | 0.51727 | 121.8842 | 121.8979 | 121.8521 | 121.7789 | 121.8246 | -121.9803 | -121.8887 | 41.2857 | 121.8567 | 74.4461 | 121.3623
1535.375 | 122.0856 | -121.5271 | 0.29755 | 0.0059509 | 0.00068782 | 0.063476 | -0.00047626 | 0.05586 | 0.072435 | -0.022819 | 0.0025024 | -0.0076049 | 0.06483 | 0.046647 | -0.017513 | -0.0077502 | -0.019946 | -44.7556 | 0.21973 | -121.6507 | -79.4357 | 0.38452 | -2.7008 | -15.1062 | -0.23804 | 0.27008 | -121.6049 | 0.32501 | -121.1014 | -121.1884 | -121.0419 | -0.1236 | -0.077819 | -79.7333 | 121.9116 | 106.4209 | 118.8263 | 106.5445 | 118.9499 | -0.077819 | -0.027465 | 0.027466 | 0.42572 | 0.48523 | 0.33875 | 0.56305 | 0.41656 | 122.0352 | 42.215 | 0.50354 | 121.9299 | 121.8704 | 121.875 | 121.7468 | 121.7972 | -121.9482 | -121.9025 | 42.0914 | 121.8521 | 76.7715 | 121.2891
1537.1406 | 121.9528 | -121.5683 | 0.32959 | 0.01358 | 0.00026062 | 0.063903 | 0.0035825 | 0.060774 | 0.072008 | -0.023246 | 0.0025024 | -0.0073913 | 0.064617 | 0.040024 | -0.018794 | -0.010955 | -0.014605 | -43.1488 | 0.27924 | -121.7148 | -78.9413 | 0.23804 | -2.7786 | -15.0238 | -0.36163 | 0.3067 | -121.6919 | 0.19684 | -121.2433 | -121.312 | -121.1517 | -0.14648 | -0.050354 | -79.2709 | 121.8063 | 106.5445 | 118.7897 | 106.691 | 118.9362 | -0.1236 | -0.022888 | -0.13275 | 0.32501 | 0.41657 | 0.25635 | 0.54016 | 0.37994 | 121.9528 | 42.7734 | 0.44861 | 121.8887 | 121.994 | 121.9986 | 121.8475 | 121.875 | -122.0444 | -122.0215 | 42.627 | 121.7651 | 78.4195 | 121.2067
1538.8594 | 122.0901 | -121.5591 | 0.28381 | 0.0059509 | 0.007951 | 0.061767 | 0.00080534 | 0.059919 | 0.070299 | -0.024101 | -0.00054937 | -0.0086731 | 0.06483 | 0.048356 | -0.016872 | -0.007323 | -0.018451 | 0.16479 | 0.2243 | -121.6827 | -78.8956 | 0.35706 | -2.5864 | -14.6622 | -0.23804 | 0.23804 | -121.637 | 0.31128 | -121.1243 | -121.2067 | -121.0556 | -0.1236 | -0.059509 | -79.1794 | 121.9162 | 106.897 | 118.9728 | 107.0206 | 119.0964 | -0.07782 | -0.045776 | 0.027466 | 0.43488 | 0.50354 | 0.35248 | 0.58136 | 0.4303 | 122.0398 | 42.7872 | 0.51269 | 121.9482 | 121.907 | 121.875 | 121.7834 | 121.7972 | -121.9666 | -121.9208 | 42.6636 | 121.8704 | 121.7239 | 121.3211
1540.6406 | 122.0627 | -121.6003 | 0.29297 | 0.01358 | 0.0081646 | 0.06134 | -0.0019717 | 0.05522 | 0.069231 | -0.022605 | 0.0025024 | -0.0099549 | 0.063549 | 0.043442 | -0.021785 | -0.009032 | -0.017383 | 0.13275 | 0.23346 | -121.7239 | -77.9892 | 0.32501 | -2.7054 | -14.5203 | -0.3067 | 0.26093 | -121.669 | 0.25177 | -121.1609 | -121.2067 | -121.1151 | -0.1236 | -0.05951 | -78.2822 | 121.9254 | 107.0801 | 118.895 | 107.2037 | 119.0186 | -0.068664 | -0.032044 | -0.041199 | 0.43945 | 0.48523 | 0.39368 | 0.55389 | 0.46234 | 122.049 | 43.7347 | 0.50812 | 121.9208 | 121.9574 | 121.9299 | 121.8338 | 121.8613 | -122.0169 | -121.962 | 43.6111 | 121.8521 | 121.7331 | 121.2936
1542.4219 | 121.994 | -121.6324 | 0.32501 | 0.028839 | 0.0056012 | 0.063049 | -0.0015445 | 0.054365 | 0.069658 | -0.022178 | 0.008606 | -0.0069641 | 0.06419 | 0.042161 | -0.023281 | -0.010314 | -0.019091 | 0.14191 | 0.28381 | -121.7743 | -77.1423 | 0.26093 | -2.6184 | -14.2319 | -0.32959 | 0.30212 | -121.7056 | 0.17853 | -121.2296 | -121.3074 | -121.1563 | -0.14191 | -0.041199 | -77.4673 | 121.8933 | 107.4005 | 119.014 | 107.5424 | 119.1559 | -0.073242 | -0.022888 | -0.14648 | 0.40283 | 0.47607 | 0.32501 | 0.54932 | 0.39825 | 122.0352 | 44.632 | 0.47607 | 121.8842 | 122.0581 | 122.0078 | 121.9162 | 121.9345 | -122.0993 | -122.0306 | 44.4901 | 121.8109 | 121.7743 | 121.3028
1544.1875 | 121.9528 | -121.6599 | 0.29297 | 0.01358 | 0.07332 | 0.10663 | 0.0014463 | 0.059492 | 0.071154 | -0.022819 | 0.0055542 | -0.0073913 | 0.065044 | 0.047501 | -0.019649 | -0.0096728 | -0.015246 | 0.09613 | 0.21973 | -121.7606 | 0.059509 | 0.20599 | -2.5864 | -1.1948 | -0.36163 | 0.25635 | -121.7102 | 0.12817 | -121.3303 | -121.3806 | -121.2387 | -0.10071 | -0.073242 | -0.23346 | 121.8658 | 120.4651 | 119.0735 | 120.5658 | 119.1742 | -0.050354 | -0.036621 | -0.16479 | 0.32959 | 0.42114 | 0.27924 | 0.4715 | 0.32959 | 121.9666 | 121.8201 | 0.37994 | 121.8384 | 121.9803 | 121.9666 | 121.8796 | 121.9162 | -122.0535 | -122.0032 | 121.7194 | 121.788 | 121.756 | 121.2982
1545.9844 | 122.1085 | -121.6003 | 0.24719 | 0.0059509 | 0.069261 | 0.10513 | -0.0023989 | 0.052015 | 0.070513 | -0.022819 | 0.0055542 | -0.0097411 | 0.06419 | 0.050065 | -0.020931 | -0.0101 | -0.012896 | 0.11444 | 0.19684 | -121.7285 | 0.17395 | 0.37079 | -2.3941 | -1.0529 | -0.21973 | 0.22888 | -121.6736 | 0.27924 | -121.138 | -121.1929 | -121.1197 | -0.12817 | -0.050354 | -0.073242 | 121.9711 | 120.5475 | 119.2062 | 120.6757 | 119.3344 | -0.073242 | -0.01831 | 0.032044 | 0.46234 | 0.48065 | 0.40741 | 0.55389 | 0.48065 | 122.0993 | 121.9025 | 0.53558 | 121.9528 | 121.9254 | 121.9025 | 121.7972 | 121.8292 | -121.9757 | -121.9208 | 121.7743 | 121.8796 | 121.7148 | 121.3806
1547.7656 | 121.9666 | -121.669 | 0.27008 | 0.02121 | 0.072892 | 0.10834 | 0.00037814 | 0.056929 | 0.072649 | -0.022819 | 0.014709 | -0.0067505 | 0.065899 | 0.032548 | -0.022853 | -0.010955 | -0.016742 | 0.073242 | 0.24261 | -121.7972 | 0.054932 | 0.21973 | -2.5269 | -1.2039 | -0.29755 | 0.27466 | -121.7194 | 0.1236 | -121.3028 | -121.376 | -121.2112 | -0.12817 | -0.027466 | -0.21515 | 121.8887 | 120.4651 | 119.1422 | 120.5933 | 119.2703 | -0.050354 | 0.004577 | -0.14649 | 0.36621 | 0.45776 | 0.29297 | 0.50812 | 0.34332 | 122.0169 | 121.8521 | 0.41656 | 121.843 | 122.0398 | 121.994 | 121.9116 | 121.9437 | -122.0673 | -121.9894 | 121.7239 | 121.7926 | 121.7422 | 121.3715
1549.5625 | 121.9757 | -121.6736 | 0.27924 | -0.0093076 | 0.07097 | 0.10599 | -0.00069006 | 0.05586 | 0.070513 | -0.02111 | 0.0025024 | -0.0082459 | 0.065258 | 0.043015 | -0.022426 | -0.011809 | -0.01546 | 0.10986 | 0.19226 | -121.7651 | 0.11444 | 0.27008 | -2.4673 | -1.1536 | -0.29297 | 0.24261 | -121.7285 | 0.14648 | -121.2799 | -121.3531 | -121.2341 | -0.091553 | -0.086975 | -0.16479 | 121.9437 | 120.52 | 119.2062 | 120.6116 | 119.2978 | -0.054932 | -0.036621 | -0.13275 | 0.39368 | 0.43945 | 0.32044 | 0.49438 | 0.37537 | 122.0352 | 121.8796 | 0.44861 | 121.875 | 121.9574 | 121.9711 | 121.8658 | 121.9162 | -122.0444 | -122.0078 | 121.788 | 121.8201 | 121.7834 | 121.3806
1551.2969 | 122.0078 | -121.7651 | 0.16022 | 0.028839 | 0.16625 | 0.10962 | 0.0010189 | 0.054792 | 0.074144 | -0.02346 | 0.008606 | -0.0071777 | 0.063762 | 0.038315 | -0.019222 | -0.0098864 | -0.017383 | -0.027466 | 0.10071 | -121.9116 | -0.036621 | 0.13733 | -0.21973 | -1.2177 | -0.24719 | 0.13733 | -121.8246 | 0.07782 | -121.3669 | -121.4539 | -121.3303 | -0.14648 | -0.059509 | -0.19684 | 121.9025 | 120.5475 | 121.5454 | 120.694 | 121.6919 | -0.059509 | -0.022888 | -0.082397 | 0.39825 | 0.43488 | 0.31128 | 0.49439 | 0.37079 | 122.0489 | 121.875 | 0.45776 | 121.9025 | 122.0123 | 121.962 | 121.8658 | 121.9025 | -122.0718 | -121.9849 | 121.7285 | 121.843 | 121.7377 | 121.5179
1553.0781 | 121.9849 | -121.788 | 0.15106 | -0.0016786 | 0.1733 | 0.10919 | 0.00080534 | 0.052442 | 0.074999 | -0.02346 | 0.0025024 | -0.0065369 | 0.063976 | 0.045365 | -0.02029 | -0.011168 | -0.016955 | -0.036621 | 0.068665 | -121.9025 | -0.073242 | 0.10529 | -0.073242 | -1.2543 | -0.29755 | 0.11902 | -121.843 | 0.022888 | -121.4355 | -121.5225 | -121.3669 | -0.11444 | -0.082397 | -0.2243 | 121.8933 | 120.5338 | 121.7148 | 120.6482 | 121.8292 | -0.054932 | -0.032043 | -0.12817 | 0.35248 | 0.42114 | 0.2655 | 0.47607 | 0.32044 | 122.0078 | 121.8292 | 0.40741 | 121.8658 | 121.9711 | 121.962 | 121.8567 | 121.907 | -122.0535 | -121.994 | 121.7148 | 121.8109 | 121.7514 | 121.4905
1554.7812 | 122.081 | -121.7514 | 0.10986 | 0.0059509 | 0.17244 | 0.11069 | -0.0017581 | 0.053511 | 0.072649 | -0.021965 | 0.0055542 | -0.010169 | 0.065685 | 0.043656 | -0.019008 | -0.0079638 | -0.019732 | -0.054932 | 0.036621 | -121.8658 | -0.009155 | 0.16937 | 0.041199 | -0.39368 | -0.27466 | 0.064087 | -121.8384 | 0.11902 | -121.3074 | -121.3715 | -121.2708 | -0.11444 | -0.073242 | -0.11902 | 121.9208 | 121.3577 | 121.7926 | 121.4722 | 121.907 | -0.086975 | -0.045776 | 0.009156 | 0.44403 | 0.48065 | 0.37994 | 0.56763 | 0.46692 | 122.0352 | 121.8567 | 0.53101 | 121.9574 | 121.9025 | 121.9025 | 121.788 | 121.8155 | -121.9757 | -121.9482 | 121.7422 | 121.8704 | 121.6965 | 121.4767
1556.5781 | 122.1085 | -121.7651 | 0.11902 | 0.036468 | 0.17522 | 0.11304 | 0.0014463 | 0.059706 | 0.074999 | -0.020469 | 0.008606 | -0.0097411 | 0.063976 | 0.051346 | -0.017299 | -0.008391 | -0.015033 | 0.009155 | 0.064087 | -121.8658 | 0.041199 | 0.22888 | 0.032043 | -0.37079 | -0.2243 | 0.082397 | -121.8521 | 0.13733 | -121.3211 | -121.3943 | -121.257 | -0.10071 | -0.054932 | -0.07782 | 121.994 | 121.3943 | 121.7972 | 121.4951 | 121.8979 | -0.086975 | -0.036622 | 0.01831 | 0.44403 | 0.50812 | 0.37079 | 0.59509 | 0.45776 | 122.0947 | 121.907 | 0.53101 | 121.9894 | 121.9299 | 121.9345 | 121.8292 | 121.8475 | -121.9849 | -121.9711 | 121.8063 | 121.9025 | 121.7743 | 121.5408
1558.3594 | 121.9574 | -120.163 | 1.6937 | 0.036468 | 0.23503 | 1.2655 | -0.00047626 | 0.055006 | 0.070513 | -0.02111 | 0.0055542 | -0.0071777 | 0.064617 | 0.040238 | -0.019863 | -0.0096728 | -0.015887 | 1.4374 | 1.6159 | -120.2591 | 1.4053 | 1.5564 | 1.5106 | 0.80566 | -0.37537 | 1.6479 | -120.2774 | 1.5656 | -119.7464 | -119.8288 | -119.7189 | -0.09613 | -0.07782 | -0.28839 | 121.7194 | 120.9686 | 121.6736 | 121.0648 | 121.7697 | -0.11444 | -0.045777 | -0.12817 | 0.41657 | 0.44403 | 0.33417 | 0.55847 | 0.44861 | 121.8155 | 121.6644 | 0.53101 | 121.843 | 121.875 | 121.9254 | 121.7789 | 121.8109 | -121.9528 | -121.9711 | 121.5683 | 121.7285 | 121.6003 | 119.7876
1560.1406 | 122.0581 | -121.7743 | 0.09613 | -0.0016786 | -0.0057208 | -0.036072 | -0.0023989 | -0.017199 | -0.026686 | -0.02581 | 0.0025024 | -0.0084595 | 0.06483 | 0.051774 | -0.015804 | -0.0094592 | -0.018023 | 0.027466 | 0.027466 | -0.054932 | 0.059509 | 0.19226 | 0.064087 | 0.082397 | -0.23346 | 0.068665 | -121.8521 | 0.10986 | -121.2982 | -121.3898 | -121.2708 | 121.7194 | -0.068664 | -0.036621 | 121.9666 | 121.8567 | 121.8384 | 0.13733 | 0.11902 | -0.07782 | -0.027465 | 0.013733 | 0.47607 | 0.50354 | 0.38452 | 0.58136 | 0.46234 | 0.24719 | 0.11444 | 0.55389 | 121.962 | 0.082398 | 121.9208 | 121.8018 | 121.843 | -0.15106 | -121.9482 | 121.8338 | 121.8842 | 121.8018 | 121.5408
1561.8594 | 122.0123 | -121.8384 | 0.10986 | 0.028839 | -0.004439 | -0.036072 | -0.0011173 | -0.016985 | -0.029036 | -0.021751 | 0.008606 | -0.0069641 | 0.063762 | 0.049637 | -0.023281 | -0.0092456 | -0.016314 | -0.004578 | 0.064087 | -0.10071 | -0.004578 | 0.10986 | 0.027466 | 0.027466 | -0.24719 | 0.086975 | -121.875 | 0.036621 | -121.4081 | -121.4676 | -121.3577 | 121.7377 | -0.045776 | -0.11444 | 121.9482 | 121.8658 | 121.8658 | 0.12817 | 0.12817 | -0.036621 | -0.022888 | -0.073242 | 0.4303 | 0.48065 | 0.37079 | 0.51727 | 0.40741 | 0.21057 | 0.09613 | 0.46692 | 121.9116 | 0.1648 | 121.962 | 121.9025 | 121.9254 | -0.21057 | -121.9849 | 121.8338 | 121.875 | 121.8338 | 121.5912
1563.6406 | 121.962 | -121.8658 | 0.1236 | 0.01358 | -0.0025164 | -0.033722 | 0.00080534 | -0.015276 | -0.028822 | -0.024101 | 0.0055542 | -0.0071777 | 0.063549 | 0.044938 | -0.019649 | -0.0077502 | -0.015246 | -0.059509 | 0.059509 | -0.07782 | -0.073242 | 0.059509 | -0.045776 | -0.027466 | -0.35248 | 0.07782 | -121.9162 | -0.022888 | -121.4996 | -121.5775 | -121.4172 | 121.788 | -0.064087 | -0.19684 | 121.9254 | 121.8384 | 121.8201 | 0.050354 | 0.032044 | -0.050354 | -0.045776 | -0.14648 | 0.36621 | 0.44861 | 0.28839 | 0.49896 | 0.33875 | 0.13733 | 0.004578 | 0.41657 | 121.8933 | 0.13733 | 121.994 | 121.9254 | 121.9437 | -0.20142 | -122.0398 | 121.7926 | 121.843 | 121.8063 | 121.5134
1565.4219 | 122.0581 | -121.8521 | 0.086975 | 0.02121 | -0.0031574 | -0.0365 | -0.0015445 | -0.012926 | -0.02989 | -0.024314 | 0.0025024 | -0.0069641 | 0.062267 | 0.041092 | -0.019863 | -0.008391 | -0.01546 | -0.022888 | 0.050354 | -0.10071 | -0.013733 | 0.1236 | 0.022888 | 0.036621 | -0.25177 | 0.086975 | -121.9482 | 0.022888 | -121.4401 | -121.5088 | -121.376 | 121.7514 | -0.036621 | -0.10071 | 121.9757 | 121.8887 | 121.875 | 0.13733 | 0.1236 | -0.09613 | 0 | -0.064087 | 0.41199 | 0.47607 | 0.34332 | 0.5722 | 0.43945 | 0.2243 | 0.086975 | 0.50812 | 121.9711 | 0.15106 | 122.0352 | 121.9025 | 121.9391 | -0.18768 | -122.0352 | 121.8384 | 121.875 | 121.8292 | 121.6003
1567.2031 | 122.0673 | -121.8567 | 0.11444 | 0.02121 | -0.0035846 | -0.035218 | -0.00047626 | -0.016771 | -0.027113 | -0.023246 | 0.008606 | -0.0093139 | 0.06419 | 0.045151 | -0.018154 | -0.010527 | -0.018023 | -0.004578 | 0.045776 | -0.073242 | -0.013733 | 0.11902 | 0.032043 | 0.032043 | -0.23804 | 0.10071 | -121.9162 | 0.022888 | -121.4539 | -121.5225 | -121.3898 | 121.7834 | -0.068665 | -0.12817 | 121.9757 | 121.8887 | 121.8887 | 0.10529 | 0.10529 | -0.05951 | -0.013733 | -0.091553 | 0.40283 | 0.46692 | 0.33417 | 0.52643 | 0.39368 | 0.19226 | 0.059509 | 0.46234 | 121.9391 | 0.11902 | 122.0169 | 121.9025 | 121.9574 | -0.18768 | -122.0306 | 121.843 | 121.8796 | 121.8521 | 121.6187
1569.0156 | 122.049 | -121.8613 | 0.10529 | 0.028839 | -0.00273 | -0.035645 | 0.0014463 | -0.022967 | -0.028608 | -0.024742 | 0.008606 | -0.0067505 | 0.063121 | 0.04387 | -0.020076 | -0.0088184 | -0.013751 | -0.041199 | 0.07782 | -0.11902 | -0.036621 | 0.07782 | 0.036621 | 0.013733 | -0.29297 | 0.091553 | -121.9574 | 0.013733 | -121.4676 | -121.55 | -121.4172 | 121.7422 | -0.027466 | -0.14191 | 121.9391 | 121.875 | 121.8979 | 0.13275 | 0.15564 | -0.09613 | -0.013733 | -0.091553 | 0.39368 | 0.44403 | 0.31128 | 0.54016 | 0.40741 | 0.19684 | 0.082398 | 0.48981 | 121.9711 | 0.19684 | 122.049 | 121.9391 | 121.9528 | -0.22431 | -122.0627 | 121.8246 | 121.875 | 121.8201 | 121.5683
1570.8125 | 122.0215 | -121.8658 | 0.14191 | 0.01358 | -0.0042254 | -0.033936 | 0.00059174 | -0.014849 | -0.030745 | -0.026023 | -0.00054937 | -0.0071777 | 0.06483 | 0.046433 | -0.017726 | -0.0071094 | -0.015887 | -0.059509 | 0.045776 | -0.073242 | -0.07782 | 0.041199 | -0.041199 | -0.054932 | -0.38452 | 0.10529 | -121.9345 | -0.050354 | -121.5591 | -121.6232 | -121.4447 | 121.7926 | -0.096131 | -0.21973 | 121.907 | 121.8109 | 121.8246 | 0.01831 | 0.032043 | -0.068664 | -0.036621 | -0.19226 | 0.3067 | 0.42114 | 0.24261 | 0.48981 | 0.31128 | 0.11444 | -0.004578 | 0.37537 | 121.8842 | 0.11902 | 122.0398 | 121.9116 | 121.9711 | -0.21515 | -122.0764 | 121.788 | 121.8155 | 121.8063 | 121.4813
1572.5156 | 122.1497 | -121.8887 | 0.09613 | 0.01358 | -0.0059344 | -0.03714 | -0.0017581 | -0.018267 | -0.028822 | -0.021537 | 0.0025024 | -0.0099549 | 0.063976 | 0.043015 | -0.020076 | -0.0094592 | -0.012042 | -0.050354 | 0.041199 | -0.082397 | -0.009155 | 0.14648 | 0.059509 | 0.064087 | -0.31128 | 0.059509 | -121.9116 | 0.073242 | -121.4264 | -121.4813 | -121.376 | 121.8063 | -0.054931 | -0.10528 | 122.0352 | 121.9528 | 121.9482 | 0.14648 | 0.14191 | -0.022888 | -0.036621 | -0.022888 | 0.46234 | 0.5127 | 0.40741 | 0.53558 | 0.4303 | 0.22888 | 0.073242 | 0.48523 | 121.9849 | 0.1236 | 121.9711 | 121.9299 | 121.9482 | -0.17853 | -122.0078 | 121.8796 | 121.962 | 121.8384 | 121.5775
1574.2969 | 122.1039 | -121.8933 | 0.10986 | 0.0059509 | -0.0018756 | -0.034577 | -0.0015445 | -0.018053 | -0.030745 | -0.022178 | 0.0055542 | -0.0078185 | 0.066539 | 0.047074 | -0.020717 | -0.0096728 | -0.01546 | 0.004578 | 0.032043 | -0.073242 | 0.032043 | 0.1831 | 0.10986 | 0.091553 | -0.24261 | 0.054932 | -121.9025 | 0.036621 | -121.4447 | -121.5042 | -121.4218 | 121.8201 | -0.07782 | -0.07782 | 122.0764 | 121.9849 | 122.0032 | 0.16479 | 0.18311 | -0.009155 | -0.054931 | -0.073242 | 0.44861 | 0.4715 | 0.3891 | 0.48065 | 0.39826 | 0.25635 | 0.10529 | 0.45776 | 121.9391 | 0.10529 | 121.9574 | 121.9254 | 121.9482 | -0.18311 | -122.0123 | 121.9254 | 121.9299 | 121.8979 | 121.6507
1576.0312 | 122.1268 | -121.8887 | 0.086975 | 0.028839 | -0.0042254 | -0.034577 | 0.00016454 | -0.019549 | -0.02754 | -0.022819 | 0.0025024 | -0.0084595 | 0.065258 | 0.049424 | -0.01794 | -0.0079638 | -0.013324 | 0.004578 | 0.032043 | -0.059509 | 0.027466 | 0.16479 | 0.064087 | 0.068665 | -0.31128 | 0.064087 | -121.9162 | 0.050354 | -121.4813 | -121.5363 | -121.3989 | 121.8292 | -0.054932 | -0.059509 | 122.0535 | 121.9574 | 121.9528 | 0.12817 | 0.1236 | -0.027466 | -0.022888 | -0.036621 | 0.40741 | 0.48981 | 0.35248 | 0.51727 | 0.37994 | 0.2243 | 0.086975 | 0.43488 | 121.9666 | 0.091552 | 121.9803 | 121.9208 | 121.9528 | -0.14648 | -122.0032 | 121.9162 | 121.9391 | 121.8933 | 121.5775
1577.8125 | 122.1542 | -121.8704 | 0.082397 | 0.036468 | -0.0035846 | -0.035645 | 0.00016454 | -0.012713 | -0.027327 | -0.023674 | 0.0055542 | -0.0088867 | 0.062908 | 0.043656 | -0.01794 | -0.0081774 | -0.015246 | 0.027466 | 0.032043 | -0.07782 | 0.073242 | 0.20599 | 0.082397 | 0.07782 | -0.23346 | 0.050354 | -121.9116 | 0.09613 | -121.431 | -121.5042 | -121.376 | 121.7926 | -0.050354 | -0.009155 | 122.0764 | 121.9482 | 121.9528 | 0.15564 | 0.16022 | -0.041199 | -0.032043 | 0.013733 | 0.43945 | 0.49438 | 0.36621 | 0.53558 | 0.40741 | 0.28381 | 0.15106 | 0.48065 | 122.0078 | 0.10986 | 121.962 | 121.9025 | 121.9208 | -0.16022 | -121.994 | 121.9437 | 121.9666 | 121.8979 | 121.637
1579.6094 | 122.1863 | -121.8704 | 0.082397 | 0.0059509 | -0.003371 | -0.035004 | -0.00069006 | -0.019121 | -0.029249 | -0.020897 | 0.014709 | -0.0069641 | 0.06483 | 0.048997 | -0.015804 | -0.0062548 | -0.016955 | 0.013733 | 0.009155 | -0.050354 | 0.059509 | 0.19684 | 0.082397 | 0.091553 | -0.24719 | 0.073242 | -121.9528 | 0.10071 | -121.4401 | -121.4996 | -121.3806 | 121.8201 | -0.073242 | -0.022888 | 122.0673 | 121.962 | 121.9528 | 0.14191 | 0.13275 | -0.082398 | -0.009155 | 0.018311 | 0.4303 | 0.48981 | 0.37079 | 0.5722 | 0.45319 | 0.24719 | 0.10986 | 0.5127 | 122.0535 | 0.059509 | 122.0261 | 121.8796 | 121.9437 | -0.13275 | -122.0352 | 121.9299 | 121.9711 | 121.8842 | 121.6232
1581.3438 | 122.1176 | -121.9208 | 0.10529 | 0.02121 | -0.0035846 | -0.034791 | -0.00026266 | -0.015917 | -0.02989 | -0.023887 | 0.0055542 | -0.0052551 | 0.06419 | 0.047501 | -0.021785 | -0.010527 | -0.016314 | -0.004578 | 0.068665 | -0.086975 | -0.022888 | 0.11902 | 0.004578 | 0.041199 | -0.25635 | 0.07782 | -121.9711 | 0.018311 | -121.5225 | -121.5775 | -121.4401 | 121.8338 | -0.036621 | -0.12817 | 122.0398 | 121.962 | 121.9254 | 0.12817 | 0.091553 | -0.050354 | -0.027466 | -0.086975 | 0.39825 | 0.48065 | 0.34332 | 0.53101 | 0.39368 | 0.20599 | 0.064087 | 0.44861 | 121.9894 | 0.15564 | 122.049 | 121.9894 | 121.9986 | -0.19226 | -122.0764 | 121.8979 | 121.9391 | 121.9162 | 121.6644
1583.1094 | 122.113 | -121.907 | 0.091553 | 0.028839 | -0.0040118 | -0.036286 | 0.00059174 | -0.01848 | -0.030745 | -0.021537 | 0.008606 | -0.0084595 | 0.066753 | 0.041306 | -0.019649 | -0.010527 | -0.015674 | -0.018311 | 0.073242 | -0.082397 | -0.013733 | 0.10529 | 0.018311 | 0.032043 | -0.26093 | 0.09613 | -121.9849 | 0.022888 | -121.5363 | -121.5958 | -121.4355 | 121.8246 | -0.018311 | -0.10529 | 122.0123 | 121.9391 | 121.9254 | 0.11444 | 0.10071 | -0.07782 | 0.004577 | -0.068665 | 0.37079 | 0.4715 | 0.31128 | 0.54932 | 0.3891 | 0.18768 | 0.068664 | 0.44861 | 122.0078 | 0.15564 | 122.081 | 121.9803 | 122.0032 | -0.17395 | -122.0764 | 121.8933 | 121.9299 | 121.8887 | 121.6461
1584.8281 | 122.0581 | -121.9299 | 0.10986 | 0.01358 | -0.006148 | -0.036072 | 0.00080534 | -0.01784 | -0.028608 | -0.026664 | -0.003601 | -0.0067505 | 0.06483 | 0.047715 | -0.018154 | -0.008391 | -0.014392 | -0.068665 | 0.064087 | -0.073242 | -0.086975 | 0.032043 | -0.064087 | -0.032043 | -0.3891 | 0.10529 | -122.0078 | -0.041199 | -121.6141 | -121.6644 | -121.4951 | 121.8567 | -0.045776 | -0.19684 | 121.962 | 121.8979 | 121.8658 | 0.041199 | 0.009155 | -0.077819 | -0.004577 | -0.15106 | 0.31586 | 0.43488 | 0.2655 | 0.51269 | 0.34332 | 0.10529 | -0.013733 | 0.39368 | 121.9666 | 0.13733 | 122.113 | 121.994 | 122.0352 | -0.18311 | -122.1176 | 121.843 | 121.8887 | 121.8613 | 121.5408
1586.625 | 122.2 | -121.9254 | 0.086975 | 0.0059509 | -0.006148 | -0.036927 | 0.00037814 | -0.019121 | -0.027967 | -0.024314 | 0.0055542 | -0.0086731 | 0.061626 | 0.05156 | -0.020076 | -0.010527 | -0.016314 | -0.045776 | 0.032043 | -0.050354 | -0.022888 | 0.15106 | 0.059509 | 0.091553 | -0.31586 | 0.059509 | -121.962 | 0.068665 | -121.4584 | -121.5134 | -121.3989 | 121.875 | -0.054932 | -0.10986 | 122.0764 | 122.0169 | 121.9849 | 0.14191 | 0.10986 | -0.036621 | -0.027466 | -0.01831 | 0.46692 | 0.52643 | 0.41199 | 0.56305 | 0.44861 | 0.20142 | 0.027466 | 0.50354 | 122.0306 | 0.082397 | 122.0215 | 121.9574 | 121.9849 | -0.13733 | -122.0489 | 121.9025 | 121.994 | 121.8796 | 121.6095
1588.4062 | 122.2 | -121.8933 | 0.09613 | 0.0059509 | -0.0037982 | -0.035218 | -0.00026266 | -0.014635 | -0.028395 | -0.022178 | 0.011658 | -0.0080321 | 0.06718 | 0.050919 | -0.016872 | -0.0064684 | -0.01546 | 0.022888 | 0.041199 | -0.064087 | 0.064087 | 0.2243 | 0.068665 | 0.09613 | -0.23804 | 0.07782 | -121.9482 | 0.091553 | -121.463 | -121.5317 | -121.4127 | 121.8292 | -0.054931 | -0.032043 | 122.1176 | 121.9894 | 121.962 | 0.16022 | 0.13275 | -0.054931 | -0.01831 | -0.004577 | 0.4303 | 0.48065 | 0.36163 | 0.53558 | 0.41656 | 0.28839 | 0.12817 | 0.48523 | 122.0398 | 0.10529 | 122.0261 | 121.9345 | 121.9711 | -0.16022 | -122.0444 | 121.9574 | 121.9849 | 121.9162 | 121.6553
1590.1094 | 122.1725 | -121.9345 | 0.091553 | 0.036468 | -0.0035846 | -0.035431 | -0.00069006 | -0.018267 | -0.029249 | -0.024101 | 0.008606 | -0.010596 | 0.060985 | 0.045579 | -0.018154 | -0.0092456 | -0.011828 | -0.036621 | 0.041199 | -0.045776 | -0.004578 | 0.12817 | 0.027466 | 0.041199 | -0.36621 | 0.041199 | -121.9574 | 0.041199 | -121.5271 | -121.5775 | -121.4493 | 121.8887 | -0.050354 | -0.096131 | 122.0627 | 121.9757 | 121.962 | 0.086975 | 0.073242 | -0.022888 | -0.050354 | -0.050354 | 0.40741 | 0.48523 | 0.35706 | 0.50812 | 0.37994 | 0.17395 | 0.041198 | 0.4303 | 121.9986 | 0.086975 | 121.9986 | 121.9757 | 121.9757 | -0.13733 | -122.049 | 121.9299 | 121.9757 | 121.8979 | 121.5683
1591.8906 | 122.1497 | -121.9391 | 0.086975 | 0.0059509 | -0.0055072 | -0.035645 | -0.0028263 | -0.021471 | -0.030317 | -0.023674 | 0.0055542 | -0.0082459 | 0.062908 | 0.054123 | -0.022426 | -0.010527 | -0.014605 | 0 | 0.009155 | -0.036621 | 0.036621 | 0.1831 | 0.086975 | 0.082397 | -0.27008 | 0.064087 | -121.9803 | 0.027466 | -121.5225 | -121.5729 | -121.4584 | 121.9025 | -0.07782 | -0.050354 | 122.1222 | 122.0215 | 122.0261 | 0.11902 | 0.1236 | -0.041199 | -0.022888 | -0.059509 | 0.41657 | 0.48065 | 0.36621 | 0.52185 | 0.40741 | 0.21973 | 0.073242 | 0.45776 | 122.0078 | 0.045776 | 122.0444 | 121.9482 | 122.0032 | -0.1236 | -122.0673 | 121.9757 | 121.9666 | 121.9391 | 121.669
1593.6875 | 122.081 | -121.9711 | 0.12817 | 0.01358 | -0.0042254 | -0.035859 | -0.00090366 | -0.021044 | -0.031813 | -0.021537 | -0.00054937 | -0.0082459 | 0.067394 | 0.041733 | -0.020503 | -0.011595 | -0.02016 | -0.059509 | 0.036621 | -0.068665 | -0.073242 | 0.073242 | -0.009155 | 0.013733 | -0.3479 | 0.10071 | -121.9986 | -0.041199 | -121.5866 | -121.6553 | -121.5317 | 121.9025 | -0.091553 | -0.20142 | 122.0444 | 121.9849 | 121.962 | 0.082398 | 0.05951 | -0.027466 | -0.027466 | -0.16937 | 0.38452 | 0.43945 | 0.31586 | 0.46692 | 0.34332 | 0.14191 | -0.004577 | 0.41199 | 121.9574 | 0.10529 | 122.0993 | 122.0078 | 122.0718 | -0.19684 | -122.1268 | 121.8979 | 121.9299 | 121.9116 | 121.6232
1595.4062 | 122.2229 | -121.9116 | 0.068665 | 0.0059509 | -0.0025164 | -0.035859 | 0.0012325 | -0.013781 | -0.029463 | -0.022392 | 0.0055542 | -0.0078185 | 0.06419 | 0.044938 | -0.01559 | -0.0077502 | -0.013537 | 0.022888 | 0.013733 | -0.022888 | 0.059509 | 0.17853 | 0.064087 | 0.086975 | -0.23346 | 0.07782 | -121.9803 | 0.10071 | -121.4676 | -121.5591 | -121.4035 | 121.8887 | -0.054932 | -0.009156 | 122.0901 | 121.9986 | 121.9757 | 0.10986 | 0.086975 | -0.068665 | 0.009155 | 0.032043 | 0.44403 | 0.50812 | 0.35248 | 0.57678 | 0.42114 | 0.20142 | 0.082397 | 0.5127 | 122.081 | 0.036621 | 122.0581 | 121.9254 | 121.9894 | -0.091553 | -122.049 | 121.9711 | 122.0123 | 121.9345 | 121.6782
1597.125 | 122.0947 | -122.0032 | 0.12817 | 0.0059509 | -0.0031574 | -0.0365 | -0.00026266 | -0.019762 | -0.031172 | -0.023887 | -0.00054937 | -0.0052551 | 0.063549 | 0.038529 | -0.023921 | -0.010741 | -0.013537 | -0.073242 | 0.054932 | -0.073242 | -0.082397 | 0.059509 | -0.022888 | -0.013733 | -0.35706 | 0.091553 | -122.0306 | -0.059509 | -121.6095 | -121.6644 | -121.5454 | 121.9299 | -0.073242 | -0.21057 | 122.0627 | 121.9894 | 121.9803 | 0.059509 | 0.050354 | -0.027466 | -0.036621 | -0.18768 | 0.39368 | 0.45776 | 0.33875 | 0.48523 | 0.36621 | 0.13275 | -0.009155 | 0.42114 | 121.9711 | 0.12817 | 122.1222 | 122.0581 | 122.0947 | -0.20142 | -122.1588 | 121.9208 | 121.9437 | 121.9299 | 121.6461
1598.9219 | 122.1176 | -121.994 | 0.11444 | -0.0016786 | -0.006148 | -0.035218 | -0.00090366 | -0.019762 | -0.031172 | -0.023246 | 0.0055542 | -0.0086731 | 0.06419 | 0.048142 | -0.02264 | -0.0088184 | -0.01781 | -0.009155 | 0.036621 | -0.036621 | 0.009155 | 0.14648 | 0.059509 | 0.050354 | -0.29755 | 0.064087 | -122.0123 | -0.009155 | -121.5729 | -121.6415 | -121.5042 | 121.9574 | -0.07782 | -0.10529 | 122.1405 | 122.0444 | 122.0535 | 0.086975 | 0.09613 | -0.01831 | -0.050354 | -0.1236 | 0.42114 | 0.48981 | 0.35248 | 0.50812 | 0.37079 | 0.18311 | 0.045776 | 0.43945 | 122.0032 | 0.073242 | 122.0764 | 122.0306 | 122.0581 | -0.15106 | -122.1268 | 122.0032 | 121.9849 | 121.9849 | 121.6965
1600.7031 | 122.2275 | -121.9574 | 0.091553 | 0.0059509 | -0.0048664 | -0.035859 | -0.0013309 | -0.019976 | -0.028181 | -0.022819 | -0.00054937 | -0.010596 | 0.063762 | 0.044938 | -0.018794 | -0.010527 | -0.016528 | -0.045776 | 0.027466 | -0.050354 | -0.013733 | 0.14191 | 0.045776 | 0.068665 | -0.33875 | 0.045776 | -122.0306 | 0.073242 | -121.5042 | -121.55 | -121.4401 | 121.907 | -0.064087 | -0.10529 | 122.0993 | 122.0261 | 122.0032 | 0.11902 | 0.09613 | -0.073243 | -0.045777 | -0.018311 | 0.45319 | 0.51727 | 0.40741 | 0.59052 | 0.48065 | 0.19226 | 0.036621 | 0.52643 | 122.1039 | 0.07782 | 122.0764 | 121.9849 | 122.0032 | -0.14191 | -122.1222 | 121.9437 | 122.0306 | 121.9116 | 121.6187
1602.4375 | 122.2366 | -121.9574 | 0.082397 | 0.01358 | -0.00508 | -0.035645 | 0.0023007 | -0.019121 | -0.028181 | -0.025596 | 0.014709 | -0.0095275 | 0.065899 | 0.049637 | -0.019008 | -0.0062548 | -0.016101 | 0.022888 | 0.027466 | -0.059509 | 0.082397 | 0.21973 | 0.068665 | 0.10071 | -0.25635 | 0.050354 | -121.994 | 0.09613 | -121.4905 | -121.5729 | -121.4172 | 121.8979 | -0.054931 | 0 | 122.1771 | 122.0581 | 122.0261 | 0.16022 | 0.12817 | -0.036622 | -0.032043 | 0.013733 | 0.46692 | 0.54016 | 0.38452 | 0.57678 | 0.42114 | 0.27924 | 0.14191 | 0.50354 | 122.0901 | 0.086975 | 122.0444 | 121.9849 | 122.0078 | -0.14191 | -122.0764 | 122.0398 | 122.0535 | 121.9803 | 121.701
1604.2188 | 122.1725 | -121.9849 | 0.11444 | 0.02121 | -0.0031574 | -0.0365 | -0.0013309 | -0.017412 | -0.026899 | -0.023246 | 0.011658 | -0.0080321 | 0.065044 | 0.038102 | -0.019435 | -0.008391 | -0.016742 | -0.041199 | 0.068665 | -0.082397 | -0.045776 | 0.091553 | -0.004578 | 0.013733 | -0.32501 | 0.10071 | -122.0627 | 0.004578 | -121.5866 | -121.6599 | -121.5088 | 121.9025 | -0.045776 | -0.16022 | 122.0764 | 121.9986 | 121.9803 | 0.09613 | 0.077819 | -0.07782 | -0.013733 | -0.10986 | 0.39825 | 0.47607 | 0.32501 | 0.55389 | 0.40283 | 0.17395 | 0.036621 | 0.47607 | 122.0673 | 0.15106 | 122.1634 | 122.0535 | 122.0856 | -0.19684 | -122.1771 | 121.9391 | 121.9894 | 121.9437 | 121.6599
1606.0156 | 122.2504 | -121.9482 | 0.091553 | 0.0059509 | -0.004439 | -0.037568 | -0.0013309 | -0.019549 | -0.029036 | -0.024101 | 0.0025024 | -0.0099549 | 0.064403 | 0.04387 | -0.019649 | -0.0096728 | -0.013751 | -0.009155 | 0.009155 | -0.036621 | 0.068665 | 0.21973 | 0.10529 | 0.10529 | -0.2243 | 0.036621 | -122.0215 | 0.091553 | -121.4722 | -121.5454 | -121.4493 | 121.9116 | -0.082398 | -0.022888 | 122.168 | 122.0535 | 122.0535 | 0.14191 | 0.14191 | -0.073242 | -0.054932 | 0 | 0.47607 | 0.49896 | 0.40283 | 0.5722 | 0.47607 | 0.25635 | 0.10529 | 0.54932 | 122.113 | 0.045776 | 122.0581 | 121.9574 | 121.9849 | -0.12817 | -122.113 | 122.0169 | 122.0398 | 121.9391 | 121.7239
1607.7812 | 122.2687 | -121.9437 | 0.064087 | 0.0059509 | -0.0055072 | -0.0365 | -0.00047626 | -0.020403 | -0.02989 | -0.023246 | 0.0055542 | -0.0099549 | 0.065258 | 0.041092 | -0.019649 | -0.0088184 | -0.018878 | 0 | 0.013733 | -0.027466 | 0.059509 | 0.23346 | 0.1236 | 0.1236 | -0.21973 | 0.041199 | -122.0032 | 0.10529 | -121.4539 | -121.5271 | -121.4355 | 121.9162 | -0.050354 | -0.004578 | 122.1771 | 122.0673 | 122.0673 | 0.15106 | 0.15106 | -0.059509 | -0.022888 | 0.041199 | 0.48981 | 0.50812 | 0.41656 | 0.56763 | 0.47607 | 0.26093 | 0.086975 | 0.54932 | 122.1085 | 0.041199 | 122.0444 | 121.9574 | 121.9849 | -0.091553 | -122.0673 | 122.0032 | 122.049 | 121.9437 | 121.7239
1609.5 | 122.2549 | -121.9528 | 0.082397 | 0.044098 | -0.00059378 | -0.032654 | 0.0014463 | -0.02083 | -0.028395 | -0.021751 | 0.014709 | -0.0071777 | 0.064403 | 0.046433 | -0.018154 | -0.0096728 | -0.014392 | 0.041199 | 0.022888 | -0.032043 | 0.07782 | 0.21973 | 0.068665 | 0.09613 | -0.26093 | 0.054932 | -121.9894 | 0.09613 | -121.5179 | -121.5912 | -121.4447 | 121.9208 | -0.059509 | -0.004577 | 122.1725 | 122.049 | 122.0215 | 0.12817 | 0.10071 | -0.036621 | -0.027465 | 0.013733 | 0.43488 | 0.50812 | 0.36163 | 0.54474 | 0.39825 | 0.25177 | 0.10986 | 0.4715 | 122.0856 | 0.054931 | 122.0444 | 121.9757 | 122.0078 | -0.11444 | -122.0718 | 122.0306 | 122.049 | 121.994 | 121.6919
1611.2812 | 122.168 | -122.0078 | 0.10071 | 0.028839 | -0.0059344 | -0.036072 | -0.0011173 | -0.011858 | -0.030317 | -0.021965 | 0.011658 | -0.0065369 | 0.065685 | 0.043442 | -0.021572 | -0.010314 | -0.014392 | -0.032043 | 0.068665 | -0.07782 | -0.027466 | 0.10529 | 0.013733 | 0.027466 | -0.28381 | 0.10986 | -122.049 | 0.022888 | -121.5775 | -121.6644 | -121.5134 | 121.9299 | -0.032043 | -0.12817 | 122.113 | 122.0352 | 122.0215 | 0.10529 | 0.091553 | -0.041199 | 0.009155 | -0.07782 | 0.4303 | 0.49438 | 0.34332 | 0.53558 | 0.38452 | 0.18311 | 0.050354 | 0.4715 | 122.0718 | 0.14649 | 122.1588 | 122.0764 | 122.1176 | -0.17853 | -122.1497 | 121.9803 | 122.0306 | 121.9757 | 121.7239
1613.0781 | 122.2321 | -121.9711 | 0.09613 | 0.028839 | -0.0059344 | -0.033722 | -0.0013309 | -0.01784 | -0.028822 | -0.022178 | 0.008606 | -0.0054687 | 0.063121 | 0.045365 | -0.019008 | -0.0075366 | -0.016528 | -0.045776 | 0.032043 | -0.050354 | -0.013733 | 0.13275 | 0.027466 | 0.054932 | -0.36163 | 0.068665 | -122.049 | 0.036621 | -121.5683 | -121.637 | -121.5042 | 121.9208 | -0.064087 | -0.10986 | 122.1039 | 122.0261 | 121.9986 | 0.10529 | 0.07782 | -0.07782 | -0.027465 | -0.059509 | 0.40283 | 0.46692 | 0.33417 | 0.54474 | 0.41199 | 0.18311 | 0.036621 | 0.48065 | 122.0856 | 0.082397 | 122.1176 | 122.0032 | 122.0398 | -0.14648 | -122.1451 | 121.9574 | 122.0078 | 121.9254 | 121.6095
1614.7969 | 122.1451 | -122.0123 | 0.1236 | 0.036468 | -0.0031574 | -0.034363 | -0.00069006 | -0.018908 | -0.030317 | -0.025383 | 0.017761 | -0.0071777 | 0.065471 | 0.043015 | -0.021999 | -0.0086048 | -0.018664 | -0.054932 | 0.091553 | -0.082397 | -0.059509 | 0.068665 | -0.018311 | 0 | -0.33417 | 0.09613 | -122.0627 | -0.022888 | -121.6415 | -121.7148 | -121.55 | 121.9299 | -0.032043 | -0.1831 | 122.081 | 122.0123 | 121.994 | 0.082397 | 0.064086 | -0.050354 | -0.027466 | -0.14648 | 0.37079 | 0.46234 | 0.29755 | 0.5127 | 0.3479 | 0.15106 | 0.022888 | 0.42114 | 122.0398 | 0.17395 | 122.1588 | 122.1039 | 122.1085 | -0.20599 | -122.1863 | 121.9528 | 121.9894 | 121.9574 | 121.6782
1616.5938 | 122.1497 | -122.0261 | 0.10986 | 0.01358 | -0.0020892 | -0.032868 | -4.906e-05 | -0.017626 | -0.02754 | -0.027092 | -0.00054937 | -0.0063233 | 0.065899 | 0.043015 | -0.016658 | -0.0075366 | -0.017383 | -0.082397 | 0.059509 | -0.068665 | -0.082397 | 0.013733 | -0.073242 | -0.041199 | -0.42114 | 0.082397 | -122.0856 | -0.018311 | -121.6919 | -121.7331 | -121.5546 | 121.9574 | -0.050354 | -0.19226 | 122.0398 | 121.9849 | 121.9528 | 0.027466 | -0.004577 | -0.059509 | -0.027466 | -0.12817 | 0.33417 | 0.4715 | 0.29297 | 0.53101 | 0.35248 | 0.082398 | -0.013732 | 0.39368 | 122.0673 | 0.12817 | 122.168 | 122.0856 | 122.1085 | -0.17853 | -122.1954 | 121.9437 | 122.0078 | 121.9437 | 121.6049
1618.375 | 122.1497 | -122.0306 | 0.10986 | 0.036468 | -0.0025164 | -0.035859 | -0.0011173 | -0.021258 | -0.029249 | -0.020683 | 0.017761 | -0.0091003 | 0.065258 | 0.039811 | -0.020503 | -0.0077502 | -0.013751 | -0.064087 | 0.07782 | -0.09613 | -0.07782 | 0.059509 | -0.018311 | 0 | -0.37537 | 0.09613 | -122.0856 | -0.027466 | -121.6461 | -121.7102 | -121.5683 | 121.9345 | -0.032043 | -0.18768 | 122.0901 | 122.0306 | 122.0123 | 0.09613 | 0.077819 | -0.054931 | -0.013733 | -0.13733 | 0.38452 | 0.46234 | 0.32044 | 0.51727 | 0.37537 | 0.15564 | 0.01831 | 0.43945 | 122.0581 | 0.17395 | 122.1817 | 122.1085 | 122.1268 | -0.20599 | -122.1954 | 121.9528 | 122.0032 | 121.9666 | 121.6553
1620.1562 | 122.1405 | -122.0078 | 0.10986 | 0.01358 | -0.004439 | -0.034363 | 0.0020871 | -0.016131 | -0.029463 | -0.024101 | 0.0055542 | -0.0061095 | 0.065258 | 0.041306 | -0.020717 | -0.011382 | -0.019305 | -0.054932 | 0.059509 | -0.068665 | -0.086975 | 0.041199 | -0.064087 | -0.045776 | -0.41657 | 0.086975 | -122.0764 | -0.027466 | -121.701 | -121.7606 | -121.5729 | 121.9391 | -0.050354 | -0.19684 | 122.049 | 121.962 | 121.9437 | 0.022889 | 0.004578 | -0.068665 | -0.022888 | -0.13733 | 0.3067 | 0.43488 | 0.24719 | 0.50354 | 0.31586 | 0.10986 | -0.01831 | 0.37537 | 122.0489 | 0.12817 | 122.1634 | 122.0673 | 122.0947 | -0.17853 | -122.1863 | 121.9208 | 121.9803 | 121.9528 | 121.5912
1621.9375 | 122.1725 | -122.0535 | 0.11444 | 0.044098 | -0.0055072 | -0.03714 | 0.0010189 | -0.01848 | -0.029249 | -0.020256 | 0.014709 | -0.0073913 | 0.066967 | 0.041092 | -0.019435 | -0.009032 | -0.015674 | -0.064087 | 0.073242 | -0.10071 | -0.054932 | 0.073242 | -0.009155 | 0.009155 | -0.35248 | 0.10071 | -122.0627 | -0.013733 | -121.6232 | -121.6965 | -121.5408 | 121.9528 | -0.041199 | -0.16937 | 122.1268 | 122.0627 | 122.0444 | 0.10986 | 0.091553 | -0.009155 | -0.013733 | -0.12817 | 0.4303 | 0.51269 | 0.35706 | 0.52185 | 0.36621 | 0.17395 | 0.045776 | 0.43945 | 122.049 | 0.17395 | 122.1634 | 122.1268 | 122.1542 | -0.21515 | -122.1771 | 121.9986 | 122.0398 | 121.9894 | 121.701
1623.7188 | 122.2641 | -121.9894 | 0.082397 | -0.0016786 | -0.0057208 | -0.036927 | -0.0013309 | -0.016131 | -0.028822 | -0.023246 | 0.0055542 | -0.0091003 | 0.063762 | 0.047288 | -0.019649 | -0.0077502 | -0.01781 | -0.054932 | 0.027466 | -0.045776 | -0.018311 | 0.13733 | 0.045776 | 0.059509 | -0.36621 | 0.050354 | -122.0581 | 0.059509 | -121.5683 | -121.6095 | -121.5042 | 121.9437 | -0.054931 | -0.10071 | 122.1268 | 122.049 | 122.0352 | 0.10528 | 0.091552 | -0.068664 | -0.032043 | -0.022888 | 0.42114 | 0.48523 | 0.37994 | 0.55389 | 0.44861 | 0.18311 | 0.027465 | 0.48981 | 122.1176 | 0.073242 | 122.1085 | 122.0169 | 122.0398 | -0.12817 | -122.1405 | 121.9711 | 122.049 | 121.9345 | 121.6232
1625.4375 | 122.1771 | -122.0352 | 0.10071 | 0.0059509 | -0.004439 | -0.03415 | -4.906e-05 | -0.016131 | -0.02754 | -0.02346 | 0.0025024 | -0.0076049 | 0.063762 | 0.045151 | -0.018794 | -0.009032 | -0.012042 | -0.054932 | 0.064087 | -0.082397 | -0.082397 | 0.027466 | -0.064087 | -0.036621 | -0.40741 | 0.082397 | -122.0856 | -0.018311 | -121.6873 | -121.7514 | -121.5775 | 121.9528 | -0.036621 | -0.18311 | 122.0627 | 121.9986 | 121.9711 | 0.045776 | 0.01831 | -0.050354 | -0.018311 | -0.11902 | 0.3479 | 0.45776 | 0.28381 | 0.50812 | 0.33417 | 0.10986 | 0 | 0.39825 | 122.0673 | 0.14648 | 122.168 | 122.0993 | 122.1176 | -0.18311 | -122.1863 | 121.9528 | 122.0169 | 121.9803 | 121.6278
1627.2344 | 122.2412 | -122.0398 | 0.09613 | 0.0059509 | -0.0046526 | -0.033509 | -0.0026127 | -0.017412 | -0.02754 | -0.021537 | 0.0055542 | -0.0095275 | 0.06419 | 0.041306 | -0.019863 | -0.010314 | -0.011615 | 0.004578 | 0.022888 | -0.041199 | 0.027466 | 0.18768 | 0.082397 | 0.086975 | -0.27008 | 0.064087 | -122.0352 | 0.032043 | -121.582 | -121.6507 | -121.5363 | 121.9986 | -0.073242 | -0.068664 | 122.2275 | 122.1268 | 122.1222 | 0.12817 | 0.1236 | 0.004578 | -0.032043 | -0.064087 | 0.45776 | 0.50354 | 0.3891 | 0.49896 | 0.38452 | 0.22888 | 0.068665 | 0.45319 | 122.0673 | 0.064087 | 122.0993 | 122.0627 | 122.1039 | -0.13733 | -122.1313 | 122.0673 | 122.0718 | 122.0444 | 121.7697
1629.0312 | 122.3007 | -121.9803 | 0.068665 | 0.0059509 | -0.0063616 | -0.036072 | 0.00037814 | -0.017626 | -0.029036 | -0.022605 | -0.00054937 | -0.010169 | 0.064403 | 0.038956 | -0.019008 | -0.0079638 | -0.013751 | -0.036621 | 0.022888 | -0.045776 | 0.041199 | 0.16937 | 0.086975 | 0.10071 | -0.29755 | 0.041199 | -122.0673 | 0.091553 | -121.5271 | -121.5912 | -121.4859 | 121.9345 | -0.045777 | -0.027466 | 122.1497 | 122.081 | 122.0673 | 0.14648 | 0.13275 | -0.086975 | -0.027466 | 0.022888 | 0.45319 | 0.49439 | 0.3891 | 0.58136 | 0.47607 | 0.21515 | 0.086975 | 0.54016 | 122.1588 | 0.068664 | 122.1085 | 122.0032 | 122.0215 | -0.11444 | -122.1359 | 122.0215 | 122.0718 | 121.9437 | 121.6827
1630.8125 | 122.3053 | -121.994 | 0.068665 | -0.0016786 | -0.0046526 | -0.035218 | -0.0015445 | -0.018908 | -0.030317 | -0.022178 | 0.0025024 | -0.0091003 | 0.06184 | 0.05156 | -0.020076 | -0.0086048 | -0.01781 | -0.027466 | 0.027466 | -0.036621 | 0.027466 | 0.1831 | 0.10071 | 0.10986 | -0.27008 | 0.054932 | -122.081 | 0.086975 | -121.5408 | -121.5866 | -121.4676 | 121.9574 | -0.041199 | -0.041199 | 122.1771 | 122.1039 | 122.0947 | 0.14648 | 0.13733 | -0.086975 | -0.013733 | 0.01831 | 0.45319 | 0.52643 | 0.40741 | 0.6134 | 0.49439 | 0.21973 | 0.064087 | 0.54016 | 122.168 | 0.064087 | 122.1359 | 122.0215 | 122.049 | -0.10529 | -122.1497 | 122.0215 | 122.081 | 121.9666 | 121.7239
1632.5469 | 122.2916 | -121.9849 | 0.091553 | 0.02121 | -0.0042254 | -0.036927 | -0.0017581 | -0.017412 | -0.028608 | -0.02346 | 0.0025024 | -0.0099549 | 0.063121 | 0.052842 | -0.01794 | -0.0101 | -0.015246 | -0.045776 | 0.013733 | -0.045776 | 0.004578 | 0.12817 | 0.036621 | 0.068665 | -0.36163 | 0.059509 | -122.0764 | 0.059509 | -121.5775 | -121.6461 | -121.5088 | 121.9391 | -0.07782 | -0.086975 | 122.113 | 122.0535 | 122.0215 | 0.11444 | 0.082397 | -0.091553 | -0.032044 | -0.032044 | 0.40741 | 0.47607 | 0.33875 | 0.56763 | 0.4303 | 0.17395 | 0.050354 | 0.49896 | 122.1359 | 0.059509 | 122.1359 | 121.9986 | 122.0444 | -0.13733 | -122.168 | 121.9894 | 122.0444 | 121.9391 | 121.6232
1634.3281 | 122.2641 | -122.0078 | 0.086975 | 0.036468 | -0.001662 | -0.0318 | 0.0025143 | -0.01848 | -0.028181 | -0.021324 | 0.014709 | -0.0073913 | 0.064403 | 0.047715 | -0.017299 | -0.0081774 | -0.012256 | 0.009155 | 0.022888 | -0.027466 | 0.054932 | 0.21057 | 0.050354 | 0.082397 | -0.31128 | 0.068665 | -122.0764 | 0.054932 | -121.5912 | -121.6599 | -121.5317 | 121.9803 | -0.064087 | -0.032043 | 122.2183 | 122.0901 | 122.0581 | 0.10986 | 0.07782 | -0.068665 | -0.01831 | -0.032043 | 0.41656 | 0.47607 | 0.3479 | 0.54474 | 0.41656 | 0.23804 | 0.082398 | 0.48523 | 122.1313 | 0.050354 | 122.1451 | 122.0306 | 122.0764 | -0.11444 | -122.1634 | 122.0627 | 122.0627 | 122.0169 | 121.6965
1636.1094 | 122.1634 | -122.0444 | 0.11902 | -0.0016786 | -0.0020892 | -0.033509 | 0.0018735 | -0.016131 | -0.029463 | -0.022819 | 0.0025024 | -0.0069641 | 0.065258 | 0.042374 | -0.018794 | -0.008391 | -0.019946 | -0.054932 | 0.073242 | -0.064087 | -0.07782 | 0.027466 | -0.073242 | -0.054932 | -0.40741 | 0.073242 | -122.1222 | -0.045776 | -121.7331 | -121.788 | -121.6095 | 121.9803 | -0.045777 | -0.19684 | 122.0718 | 121.9894 | 121.9711 | 0.009155 | -0.009155 | -0.077819 | -0.045777 | -0.16479 | 0.31128 | 0.43488 | 0.25635 | 0.51269 | 0.33417 | 0.091553 | -0.013733 | 0.3891 | 122.0764 | 0.13733 | 122.1954 | 122.1176 | 122.1176 | -0.18311 | -122.2412 | 121.9666 | 121.9986 | 121.9894 | 121.637
1637.9062 | 122.2733 | -122.0215 | 0.082397 | 0.0059509 | -0.0029438 | -0.03714 | 0.00016454 | -0.016985 | -0.030317 | -0.022819 | 0.0025024 | -0.0093139 | 0.065258 | 0.04686 | -0.016445 | -0.0071094 | -0.019091 | -0.068665 | 0.045776 | -0.073242 | -0.036621 | 0.091553 | -0.013733 | 0.013733 | -0.36163 | 0.068665 | -122.0856 | 0.068665 | -121.6003 | -121.669 | -121.5317 | 121.9482 | -0.036621 | -0.11902 | 122.113 | 122.0352 | 122.0078 | 0.086975 | 0.059509 | -0.064087 | -0.013732 | -0.013732 | 0.42114 | 0.48981 | 0.35248 | 0.55389 | 0.41657 | 0.16479 | 0.036621 | 0.48523 | 122.1542 | 0.11902 | 122.1542 | 122.0673 | 122.0901 | -0.15564 | -122.168 | 121.9849 | 122.0901 | 121.9528 | 121.6599
1639.7031 | 122.3145 | -122.0215 | 0.086975 | 0.0059509 | -0.003371 | -0.036713 | -0.0034671 | -0.02318 | -0.029249 | -0.021965 | -0.00054937 | -0.0093139 | 0.066967 | 0.040238 | -0.019008 | -0.008391 | -0.017596 | -0.013733 | 0.013733 | -0.027466 | 0.054932 | 0.21973 | 0.11902 | 0.10529 | -0.25635 | 0.036621 | -122.081 | 0.09613 | -121.5454 | -121.6141 | -121.5179 | 121.994 | -0.073242 | -0.032043 | 122.2412 | 122.1268 | 122.1405 | 0.13275 | 0.14649 | -0.05951 | -0.050354 | 0.009155 | 0.47607 | 0.50354 | 0.40741 | 0.56305 | 0.46692 | 0.24719 | 0.082398 | 0.53558 | 122.1771 | 0.041199 | 122.1176 | 122.0352 | 122.0581 | -0.11444 | -122.168 | 122.0764 | 122.1176 | 122.0078 | 121.7651
1641.4219 | 122.319 | -122.0398 | 0.082397 | 0.0059509 | -0.0031574 | -0.036072 | -0.0015445 | -0.020617 | -0.028822 | -0.02581 | 0.0055542 | -0.0091003 | 0.065899 | 0.044724 | -0.020076 | -0.0064684 | -0.014819 | 0.009155 | 0.013733 | -0.027466 | 0.059509 | 0.22888 | 0.11444 | 0.10071 | -0.24261 | 0.054932 | -122.0627 | 0.07782 | -121.5454 | -121.6187 | -121.4951 | 122.0123 | -0.068664 | -0.022888 | 122.2687 | 122.1405 | 122.1542 | 0.12817 | 0.14191 | -0.022888 | -0.027465 | -0.004577 | 0.49438 | 0.54474 | 0.42114 | 0.56763 | 0.44403 | 0.25635 | 0.086975 | 0.51727 | 122.1405 | 0.041199 | 122.1176 | 122.0535 | 122.0947 | -0.10986 | -122.1451 | 122.0993 | 122.1176 | 122.049 | 121.7972
1643.2031 | 122.2733 | -122.0764 | 0.091553 | 0.0059509 | -0.0035846 | -0.034791 | -0.0011173 | -0.019121 | -0.028608 | -0.023246 | -0.00054937 | -0.0067505 | 0.06419 | 0.045579 | -0.018581 | -0.011595 | -0.02016 | 0.009155 | 0.004578 | -0.041199 | 0.041199 | 0.19226 | 0.086975 | 0.07782 | -0.27466 | 0.045776 | -122.0947 | 0.036621 | -121.6049 | -121.6644 | -121.55 | 122.0352 | -0.086975 | -0.050354 | 122.2687 | 122.1542 | 122.1634 | 0.11902 | 0.12817 | -0.018311 | -0.045777 | -0.054932 | 0.4715 | 0.52643 | 0.41199 | 0.54474 | 0.4303 | 0.23346 | 0.082398 | 0.48981 | 122.1313 | 0.045777 | 122.1405 | 122.081 | 122.1222 | -0.13275 | -122.1863 | 122.1176 | 122.113 | 122.0856 | 121.8018
1645 | 122.2092 | -122.0535 | 0.10529 | 0.0059509 | -0.0040118 | -0.036713 | -4.906e-05 | -0.018053 | -0.029036 | -0.022605 | 0.0025024 | -0.0058959 | 0.065471 | 0.052415 | -0.02029 | -0.010955 | -0.015246 | -0.013733 | 0.004578 | -0.045776 | 0.022888 | 0.15564 | 0.045776 | 0.064087 | -0.33875 | 0.068665 | -122.0993 | -0.018311 | -121.6599 | -121.7194 | -121.5958 | 122.0078 | -0.10071 | -0.082398 | 122.2092 | 122.1176 | 122.0993 | 0.10986 | 0.091552 | -0.045776 | -0.036621 | -0.1236 | 0.39368 | 0.45776 | 0.33417 | 0.50354 | 0.37994 | 0.20142 | 0.068664 | 0.43945 | 122.081 | 0.050354 | 122.168 | 122.0581 | 122.1222 | -0.15106 | -122.2046 | 122.0764 | 122.0352 | 122.0398 | 121.7148
1646.7969 | 122.2778 | -122.0444 | 0.073242 | 0.044098 | -0.0046526 | -0.032441 | 0.0010189 | -0.016344 | -0.030531 | -0.02346 | 0.011658 | -0.0063233 | 0.065685 | 0.045151 | -0.017513 | -0.010741 | -0.016528 | -0.009155 | 0.022888 | -0.041199 | 0.032043 | 0.17853 | 0.050354 | 0.059509 | -0.35248 | 0.045776 | -122.0947 | 0.045776 | -121.6415 | -121.6919 | -121.5454 | 122.0032 | -0.050354 | -0.041199 | 122.2229 | 122.1039 | 122.0947 | 0.10071 | 0.091553 | -0.050354 | -0.027466 | -0.027466 | 0.40283 | 0.49896 | 0.35248 | 0.54932 | 0.40283 | 0.21973 | 0.073242 | 0.45319 | 122.1405 | 0.064087 | 122.1405 | 122.0673 | 122.0901 | -0.11444 | -122.168 | 122.0764 | 122.0901 | 122.0352 | 121.6919
1648.5156 | 122.2549 | -122.049 | 0.10071 | 0.02121 | -0.0040118 | -0.035431 | 0.0020871 | -0.020617 | -0.02754 | -0.021537 | 0.008606 | -0.0069641 | 0.064403 | 0.050706 | -0.02029 | -0.0088184 | -0.015246 | -0.027466 | 0.059509 | -0.082397 | -0.009155 | 0.11902 | 0.009155 | 0.032043 | -0.31128 | 0.091553 | -122.1039 | 0.018311 | -121.6507 | -121.7285 | -121.5866 | 121.9666 | -0.041199 | -0.10986 | 122.168 | 122.081 | 122.0581 | 0.11444 | 0.091552 | -0.054932 | -0.009155 | -0.082397 | 0.39825 | 0.46234 | 0.32043 | 0.51727 | 0.37537 | 0.20142 | 0.073242 | 0.45319 | 122.1222 | 0.14191 | 122.1954 | 122.1085 | 122.1405 | -0.18311 | -122.2046 | 122.0398 | 122.0673 | 122.0215 | 121.7377
1650.2812 | 122.3511 | -122.0581 | 0.068665 | 0.02121 | -0.0042254 | -0.036286 | -0.0034671 | -0.021471 | -0.030745 | -0.019615 | 0.008606 | -0.0084595 | 0.063976 | 0.047715 | -0.019649 | -0.008391 | -0.011828 | -0.027466 | 0.018311 | -0.041199 | 0.027466 | 0.17853 | 0.07782 | 0.09613 | -0.31128 | 0.041199 | -122.1039 | 0.10529 | -121.5729 | -121.637 | -121.5042 | 122.0169 | -0.050354 | -0.041199 | 122.2366 | 122.1542 | 122.1359 | 0.13733 | 0.11902 | -0.045777 | -0.027466 | 0.036621 | 0.48523 | 0.55389 | 0.42114 | 0.59967 | 0.46692 | 0.21973 | 0.068665 | 0.53101 | 122.2092 | 0.05951 | 122.1451 | 122.0764 | 122.0993 | -0.10986 | -122.1725 | 122.0856 | 122.1634 | 122.0306 | 121.7468
1652.0781 | 122.2046 | -122.0673 | 0.10071 | 0.0059509 | -0.0048664 | -0.033295 | 0.0020871 | -0.013781 | -0.027113 | -0.026451 | -0.00054937 | -0.0073913 | 0.063976 | 0.03917 | -0.017726 | -0.0094592 | -0.02016 | -0.036621 | 0.041199 | -0.054932 | -0.050354 | 0.064087 | -0.036621 | -0.013733 | -0.38452 | 0.07782 | -122.1222 | -0.013733 | -121.7239 | -121.8063 | -121.6278 | 122.0123 | -0.059509 | -0.15106 | 122.1313 | 122.0535 | 122.0306 | 0.041199 | 0.018311 | -0.054931 | -0.022888 | -0.11444 | 0.34332 | 0.43945 | 0.26093 | 0.49438 | 0.31586 | 0.11902 | 0.004578 | 0.39825 | 122.1085 | 0.096131 | 122.2 | 122.1085 | 122.1451 | -0.15564 | -122.2229 | 122.0169 | 122.0535 | 122.0306 | 121.6827
1653.7969 | 122.3465 | -122.0535 | 0.086975 | 0.0059509 | -0.0031574 | -0.035859 | -0.00069006 | -0.019121 | -0.029036 | -0.022605 | 0.0025024 | -0.0093139 | 0.064403 | 0.042801 | -0.019435 | -0.0094592 | -0.018451 | -0.013733 | 0.009155 | -0.013733 | 0.050354 | 0.25177 | 0.13733 | 0.11444 | -0.28381 | 0.054932 | -122.0993 | 0.10529 | -121.5591 | -121.6278 | -121.5408 | 122.0398 | -0.07782 | -0.036621 | 122.3053 | 122.168 | 122.1909 | 0.12817 | 0.15106 | -0.045776 | -0.032043 | 0.018311 | 0.49438 | 0.51269 | 0.42572 | 0.55847 | 0.4715 | 0.2655 | 0.064087 | 0.54016 | 122.2046 | 0.022888 | 122.1542 | 122.0627 | 122.1085 | -0.10071 | -122.1863 | 122.1039 | 122.1588 | 122.0398 | 121.7697
1655.5781 | 122.2687 | -122.0581 | 0.082397 | 0.01358 | -0.0042254 | -0.035859 | 0.0018735 | -0.016985 | -0.027113 | -0.023033 | -0.00054937 | -0.0073913 | 0.06419 | 0.041092 | -0.017513 | -0.0092456 | -0.014392 | -0.068665 | 0.045776 | -0.064087 | -0.054932 | 0.059509 | -0.054932 | -0.018311 | -0.38452 | 0.050354 | -122.1039 | 0.036621 | -121.6644 | -121.7194 | -121.5683 | 121.994 | -0.036621 | -0.13733 | 122.1176 | 122.0398 | 122.0032 | 0.045776 | 0.009155 | -0.045777 | -0.032043 | -0.045776 | 0.39368 | 0.48981 | 0.33875 | 0.53558 | 0.38452 | 0.1236 | 0.009155 | 0.43945 | 122.1405 | 0.10986 | 122.1542 | 122.1039 | 122.1085 | -0.14648 | -122.1863 | 122.0032 | 122.0947 | 121.9894 | 121.6736
1657.3594 | 122.2961 | -122.0444 | 0.082397 | 0.02121 | -0.0037982 | -0.032868 | -0.00026266 | -0.016558 | -0.027113 | -0.025383 | 0.0025024 | -0.0095275 | 0.065471 | 0.043229 | -0.018154 | -0.0088184 | -0.018451 | -0.045776 | 0.027466 | -0.032043 | -0.004578 | 0.13275 | 0.041199 | 0.050354 | -0.40283 | 0.059509 | -122.1222 | 0.032043 | -121.6461 | -121.6919 | -121.5729 | 122.0123 | -0.054931 | -0.086975 | 122.1771 | 122.0947 | 122.0856 | 0.082397 | 0.073242 | -0.077819 | -0.022888 | -0.050354 | 0.39825 | 0.4715 | 0.35248 | 0.54932 | 0.4303 | 0.16479 | 0.027465 | 0.47607 | 122.1542 | 0.059509 | 122.1817 | 122.0718 | 122.1039 | -0.11444 | -122.2046 | 122.0398 | 122.0764 | 121.9986 | 121.6415
1659.0781 | 122.3648 | -122.0352 | 0.10529 | 0.01358 | -0.0052936 | -0.036713 | -0.0023989 | -0.020189 | -0.032667 | -0.022178 | 0.0025024 | -0.0084595 | 0.063335 | 0.053483 | -0.01794 | -0.0092456 | -0.013965 | 0.013733 | 0.018311 | -0.022888 | 0.068665 | 0.21973 | 0.11902 | 0.10986 | -0.25635 | 0.050354 | -122.0947 | 0.09613 | -121.5775 | -121.637 | -121.5454 | 122.0123 | -0.086975 | -0.036621 | 122.2549 | 122.1451 | 122.1542 | 0.13275 | 0.14191 | -0.05951 | -0.054932 | -0.009156 | 0.45776 | 0.48981 | 0.39825 | 0.54932 | 0.45776 | 0.24261 | 0.091553 | 0.51727 | 122.1909 | 0.041199 | 122.1451 | 122.0535 | 122.0856 | -0.12817 | -122.2 | 122.1039 | 122.1313 | 122.049 | 121.7789
1660.8594 | 122.2229 | -122.1039 | 0.11902 | 0.02121 | -0.0035846 | -0.035645 | -0.00090366 | -0.017626 | -0.030104 | -0.023887 | 0.0055542 | -0.0069641 | 0.063762 | 0.042801 | -0.02264 | -0.0088184 | -0.016528 | -0.027466 | 0.018311 | -0.045776 | -0.018311 | 0.11902 | 0.027466 | 0.013733 | -0.37079 | 0.07782 | -122.1268 | -0.032043 | -121.6965 | -121.7789 | -121.6324 | 122.0581 | -0.10071 | -0.13733 | 122.2229 | 122.1176 | 122.1313 | 0.059509 | 0.073242 | -0.022888 | -0.041199 | -0.15106 | 0.40741 | 0.4715 | 0.32501 | 0.49438 | 0.3479 | 0.16479 | 0.027465 | 0.4303 | 122.0947 | 0.064087 | 122.2046 | 122.1222 | 122.1817 | -0.16479 | -122.2458 | 122.0856 | 122.0718 | 122.0764 | 121.7331
1662.6562 | 122.3877 | -122.0947 | 0.086975 | -0.0016786 | -0.0059344 | -0.036927 | -0.0015445 | -0.018053 | -0.02989 | -0.023887 | 0.0055542 | -0.0073913 | 0.065258 | 0.045792 | -0.020503 | -0.0096728 | -0.017383 | 0 | 0 | -0.032043 | 0.045776 | 0.21515 | 0.11444 | 0.10529 | -0.2655 | 0.041199 | -122.0901 | 0.10071 | -121.5729 | -121.6415 | -121.5317 | 122.0627 | -0.086975 | -0.041199 | 122.3099 | 122.2 | 122.2092 | 0.13733 | 0.14648 | 0.004578 | -0.045776 | 0.013733 | 0.52185 | 0.56305 | 0.45319 | 0.55847 | 0.44861 | 0.24719 | 0.077819 | 0.51727 | 122.1909 | 0.032043 | 122.1313 | 122.0947 | 122.1359 | -0.11902 | -122.1771 | 122.1405 | 122.1954 | 122.0947 | 121.8292
1664.375 | 122.2961 | -122.0627 | 0.10071 | 0.0059509 | -0.0055072 | -0.033936 | 0.0018735 | -0.014849 | -0.028608 | -0.029014 | -0.00054937 | -0.0058959 | 0.062694 | 0.045151 | -0.016017 | -0.0092456 | -0.01546 | -0.054932 | 0.041199 | -0.054932 | -0.050354 | 0.059509 | -0.050354 | -0.018311 | -0.39368 | 0.068665 | -122.0947 | 0.032043 | -121.6873 | -121.756 | -121.6049 | 122.0078 | -0.059509 | -0.15106 | 122.1222 | 122.0444 | 122.0123 | 0.036621 | 0.004578 | -0.032044 | -0.032043 | -0.068665 | 0.37537 | 0.45776 | 0.3067 | 0.48981 | 0.33875 | 0.11444 | 0.004578 | 0.40741 | 122.1268 | 0.096131 | 122.1634 | 122.1039 | 122.1313 | -0.15564 | -122.1954 | 122.0123 | 122.0947 | 122.0078 | 121.669
1666.1406 | 122.3465 | -122.081 | 0.082397 | 0.0059509 | -0.0048664 | -0.037354 | 0.00037814 | -0.02083 | -0.028395 | -0.023887 | 0.0025024 | -0.0078185 | 0.06419 | 0.041733 | -0.022853 | -0.0077502 | -0.013965 | -0.004578 | 0.004578 | -0.013733 | 0.073242 | 0.20599 | 0.10986 | 0.10071 | -0.27008 | 0.059509 | -122.1039 | 0.073242 | -121.6003 | -121.6736 | -121.55 | 122.0673 | -0.077819 | -0.009155 | 122.287 | 122.1817 | 122.1909 | 0.11444 | 0.1236 | -0.022888 | -0.022888 | -0.009155 | 0.48065 | 0.53101 | 0.40741 | 0.55389 | 0.4303 | 0.21973 | 0.086975 | 0.50354 | 122.1771 | 0.018311 | 122.1634 | 122.0856 | 122.1405 | -0.09613 | -122.1863 | 122.1542 | 122.1542 | 122.0764 | 121.8109
1667.8594 | 122.2549 | -122.0947 | 0.09613 | 0.01358 | -0.0063616 | -0.035218 | 0.0018735 | -0.01848 | -0.029249 | -0.022605 | -0.003601 | -0.0035461 | 0.066326 | 0.04451 | -0.017726 | -0.0062548 | -0.016528 | -0.07782 | 0.073242 | -0.059509 | -0.086975 | 0.054932 | -0.045776 | -0.022888 | -0.42572 | 0.07782 | -122.1405 | -0.004578 | -121.7285 | -121.8063 | -121.6232 | 122.0352 | -0.022888 | -0.1831 | 122.1497 | 122.0718 | 122.049 | 0.036621 | 0.013733 | -0.045776 | -0.01831 | -0.10071 | 0.36621 | 0.4715 | 0.28839 | 0.51727 | 0.33417 | 0.11444 | -0.027466 | 0.41199 | 122.1359 | 0.13275 | 122.2183 | 122.168 | 122.1725 | -0.15564 | -122.2366 | 122.0078 | 122.0901 | 122.0169 | 121.669
1669.6406 | 122.3648 | -122.0627 | 0.091553 | -0.0016786 | -0.004439 | -0.038636 | -0.0011173 | -0.017412 | -0.029036 | -0.021751 | -0.00054937 | -0.0086731 | 0.064403 | 0.044938 | -0.023067 | -0.0092456 | -0.018023 | 0 | 0.013733 | -0.022888 | 0.068665 | 0.21515 | 0.10986 | 0.10986 | -0.28839 | 0.050354 | -122.1176 | 0.07782 | -121.6095 | -121.6965 | -121.5546 | 122.0398 | -0.07782 | -0.022888 | 122.2778 | 122.1725 | 122.1725 | 0.13275 | 0.13275 | -0.054932 | -0.041199 | -0.013733 | 0.45319 | 0.50812 | 0.36621 | 0.56305 | 0.42114 | 0.23804 | 0.091553 | 0.50812 | 122.1954 | 0.036621 | 122.168 | 122.0764 | 122.113 | -0.11444 | -122.2092 | 122.1313 | 122.1405 | 122.0627 | 121.7743
1671.3594 | 122.3282 | -122.0673 | 0.07782 | 0.02121 | -0.0037982 | -0.0365 | -0.00026266 | -0.017199 | -0.029249 | -0.020469 | 0.008606 | -0.0073913 | 0.063121 | 0.046647 | -0.018794 | -0.0071094 | -0.015033 | -0.027466 | 0.018311 | -0.036621 | 0 | 0.15106 | 0.036621 | 0.059509 | -0.39825 | 0.064087 | -122.113 | 0.041199 | -121.6782 | -121.7468 | -121.5958 | 122.0306 | -0.059509 | -0.07782 | 122.2183 | 122.1268 | 122.1039 | 0.09613 | 0.073242 | -0.045776 | -0.013733 | -0.036621 | 0.3891 | 0.4715 | 0.32044 | 0.51727 | 0.36621 | 0.18768 | 0.036621 | 0.43488 | 122.1542 | 0.054932 | 122.1771 | 122.0856 | 122.1313 | -0.11444 | -122.1909 | 122.0673 | 122.1085 | 122.0398 | 121.669
1673.1406 | 122.2458 | -122.1039 | 0.11902 | 0.028839 | -0.0025164 | -0.036713 | -0.00026266 | -0.017199 | -0.028608 | -0.024742 | 0.011658 | -0.0076049 | 0.06718 | 0.042588 | -0.021572 | -0.010741 | -0.01781 | -0.091553 | 0.054932 | -0.068665 | -0.059509 | 0.068665 | 0.009155 | 0 | -0.38452 | 0.1236 | -122.1725 | -0.027466 | -121.756 | -121.8155 | -121.6599 | 122.0352 | -0.064087 | -0.17853 | 122.1725 | 122.1039 | 122.113 | 0.068665 | 0.07782 | -0.068664 | 0.004577 | -0.14649 | 0.3479 | 0.44403 | 0.28839 | 0.51269 | 0.35706 | 0.13733 | 0.009156 | 0.41656 | 122.1451 | 0.1236 | 122.2961 | 122.1588 | 122.2275 | -0.18768 | -122.2916 | 122.0444 | 122.0764 | 122.0123 | 121.7194
1674.8594 | 122.3923 | -122.0764 | 0.064087 | 0.0059509 | -0.00508 | -0.037354 | -0.0019717 | -0.023607 | -0.030745 | -0.020897 | 0.0055542 | -0.0082459 | 0.065258 | 0.043442 | -0.019008 | -0.0101 | -0.016101 | -0.022888 | 0.009155 | -0.022888 | 0.054932 | 0.19684 | 0.10529 | 0.091553 | -0.3067 | 0.059509 | -122.0993 | 0.09613 | -121.5912 | -121.6507 | -121.55 | 122.0535 | -0.054932 | -0.009155 | 122.2733 | 122.168 | 122.1817 | 0.11444 | 0.12817 | -0.022888 | -0.004578 | 0.032043 | 0.48523 | 0.52643 | 0.42572 | 0.54932 | 0.44861 | 0.21973 | 0.07782 | 0.50812 | 122.1954 | 0.032043 | 122.1588 | 122.0856 | 122.1359 | -0.086975 | -122.1634 | 122.1313 | 122.1725 | 122.0535 | 121.7697
1676.6406 | 122.3328 | -122.0947 | 0.086975 | 0.02121 | -0.0059344 | -0.036072 | 0.0016599 | -0.015276 | -0.030531 | -0.022178 | 0.0055542 | -0.0093139 | 0.063762 | 0.043442 | -0.018581 | -0.0062548 | -0.012896 | -0.059509 | 0.045776 | -0.054932 | -0.041199 | 0.09613 | -0.022888 | 0 | -0.41199 | 0.068665 | -122.1451 | 0.064087 | -121.6736 | -121.7514 | -121.5775 | 122.0398 | -0.041199 | -0.12817 | 122.1909 | 122.0947 | 122.0718 | 0.054932 | 0.032044 | -0.050354 | -0.01831 | -0.022888 | 0.42114 | 0.51727 | 0.34332 | 0.56763 | 0.39368 | 0.15106 | 0.013733 | 0.4715 | 122.2092 | 0.10071 | 122.2137 | 122.1405 | 122.1634 | -0.14191 | -122.2321 | 122.0535 | 122.1588 | 122.0352 | 121.6827
1678.4375 | 122.3923 | -122.0764 | 0.082397 | 0.0059509 | -0.0059344 | -0.033936 | -0.0013309 | -0.01848 | -0.029463 | -0.023246 | 0.0055542 | -0.0099549 | 0.063976 | 0.042374 | -0.020076 | -0.0071094 | -0.013965 | 0.004578 | 0.027466 | -0.027466 | 0.086975 | 0.24719 | 0.14648 | 0.10986 | -0.29755 | 0.041199 | -122.1405 | 0.09613 | -121.6141 | -121.6644 | -121.5546 | 122.0489 | -0.054931 | 0.004578 | 122.3236 | 122.1863 | 122.2229 | 0.13733 | 0.17395 | -0.064087 | -0.041198 | 0.013733 | 0.46234 | 0.52185 | 0.41199 | 0.58594 | 0.47607 | 0.27466 | 0.11444 | 0.52643 | 122.2366 | 0.054932 | 122.1817 | 122.1039 | 122.1176 | -0.10986 | -122.2229 | 122.1634 | 122.1725 | 122.081 | 121.7789
1680.2188 | 122.3328 | -122.113 | 0.091553 | 0.028839 | -0.0052936 | -0.036927 | -0.0011173 | -0.019976 | -0.029036 | -0.022819 | 0.011658 | -0.0086731 | 0.063335 | 0.04686 | -0.018367 | -0.010955 | -0.012896 | -0.050354 | 0.018311 | -0.050354 | -0.009155 | 0.13733 | 0.036621 | 0.041199 | -0.42114 | 0.064087 | -122.1588 | 0.041199 | -121.701 | -121.7468 | -121.6003 | 122.0627 | -0.073242 | -0.10071 | 122.2504 | 122.1542 | 122.1497 | 0.091553 | 0.086975 | -0.045776 | -0.027466 | -0.050354 | 0.41199 | 0.5127 | 0.36621 | 0.55847 | 0.41199 | 0.18768 | 0.041199 | 0.45776 | 122.2 | 0.068665 | 122.2229 | 122.1313 | 122.1771 | -0.14191 | -122.2504 | 122.1039 | 122.1542 | 122.0627 | 121.6919
1682.0156 | 122.2412 | -122.1313 | 0.10986 | 0.0059509 | -0.004439 | -0.033722 | 0.0016599 | -0.01784 | -0.031172 | -0.019401 | 0.0055542 | -0.0058959 | 0.063549 | 0.03682 | -0.018154 | -0.0101 | -0.015033 | -0.07782 | 0.050354 | -0.054932 | -0.091553 | 0.009155 | -0.068665 | -0.050354 | -0.4715 | 0.07782 | -122.1634 | -0.013733 | -121.788 | -121.8521 | -121.6599 | 122.0764 | -0.059509 | -0.20142 | 122.1405 | 122.081 | 122.0627 | 0.004578 | -0.013733 | -0.032043 | -0.032043 | -0.1236 | 0.34332 | 0.4715 | 0.27924 | 0.50354 | 0.31128 | 0.064087 | -0.036621 | 0.37537 | 122.1497 | 0.10529 | 122.2412 | 122.1817 | 122.2092 | -0.16479 | -122.2733 | 122.0398 | 122.1176 | 122.0535 | 121.6599
1683.7344 | 122.3923 | -122.0764 | 0.073242 | 0.0059509 | -0.0065754 | -0.03714 | -0.0013309 | -0.017412 | -0.029676 | -0.023674 | 0.0025024 | -0.010382 | 0.064403 | 0.043229 | -0.021144 | -0.0081774 | -0.016955 | -0.009155 | 0 | -0.022888 | 0.064087 | 0.23804 | 0.13275 | 0.10529 | -0.3067 | 0.041199 | -122.113 | 0.09613 | -121.6095 | -121.6782 | -121.5637 | 122.0535 | -0.073242 | -0.009155 | 122.3145 | 122.1817 | 122.2092 | 0.12817 | 0.15564 | -0.036621 | -0.032043 | 0.022888 | 0.46692 | 0.51269 | 0.39825 | 0.54932 | 0.43488 | 0.26093 | 0.086975 | 0.50354 | 122.2092 | 0.022888 | 122.1542 | 122.0764 | 122.1176 | -0.09613 | -122.1863 | 122.1405 | 122.1725 | 122.0673 | 121.7697
1685.5 | 122.3007 | -122.1039 | 0.10071 | 0.028839 | -0.0029438 | -0.036072 | 0.00080534 | -0.018908 | -0.028181 | -0.023033 | 0.008606 | -0.0065369 | 0.065471 | 0.040665 | -0.019649 | -0.0096728 | -0.015246 | -0.018311 | 0.050354 | -0.050354 | -0.004578 | 0.1236 | 0.032043 | 0.036621 | -0.3479 | 0.07782 | -122.1725 | 0.041199 | -121.7148 | -121.7743 | -121.6187 | 122.0535 | -0.050354 | -0.10529 | 122.2275 | 122.1405 | 122.1359 | 0.086975 | 0.082397 | -0.068664 | -0.022888 | -0.059509 | 0.3891 | 0.48523 | 0.32959 | 0.55389 | 0.39825 | 0.17395 | 0.045776 | 0.45776 | 122.2137 | 0.10071 | 122.2504 | 122.1542 | 122.1817 | -0.15106 | -122.2733 | 122.0993 | 122.1451 | 122.0856 | 121.756
1687.2812 | 122.3465 | -122.1176 | 0.082397 | 0.028839 | -0.003371 | -0.035004 | -0.00047626 | -0.01848 | -0.026686 | -0.023674 | 0.014709 | -0.0073913 | 0.066326 | 0.05156 | -0.017513 | -0.010955 | -0.014819 | -0.004578 | 0.032043 | -0.036621 | 0.027466 | 0.20142 | 0.073242 | 0.09613 | -0.37537 | 0.045776 | -122.1542 | 0.082397 | -121.6782 | -121.7468 | -121.6049 | 122.081 | -0.050354 | -0.054931 | 122.319 | 122.2137 | 122.1909 | 0.13275 | 0.10986 | -0.036621 | -0.036621 | 0 | 0.43945 | 0.5127 | 0.37079 | 0.54932 | 0.40741 | 0.23804 | 0.064087 | 0.47607 | 122.2366 | 0.068664 | 122.2 | 122.1497 | 122.1634 | -0.11902 | -122.2366 | 122.1451 | 122.2 | 122.113 | 121.7422
1689.0625 | 122.2641 | -122.1451 | 0.10986 | -0.0016786 | -0.0040118 | -0.037354 | 0.00037814 | -0.016771 | -0.028822 | -0.024101 | 0.011658 | -0.0080321 | 0.066539 | 0.046647 | -0.021572 | -0.011595 | -0.015674 | -0.091553 | 0.054932 | -0.073242 | -0.07782 | 0.050354 | -0.013733 | 0 | -0.42114 | 0.10986 | -122.2137 | -0.032043 | -121.7743 | -121.8246 | -121.6736 | 122.0718 | -0.054931 | -0.18768 | 122.1954 | 122.1451 | 122.1313 | 0.073242 | 0.059509 | -0.068664 | 0 | -0.14191 | 0.37079 | 0.4715 | 0.32044 | 0.54016 | 0.3891 | 0.1236 | -0.004578 | 0.43945 | 122.1817 | 0.12817 | 122.3236 | 122.2 | 122.2549 | -0.18311 | -122.3236 | 122.0673 | 122.113 | 122.0535 | 121.7239
1690.8438 | 122.3328 | -122.1085 | 0.10071 | 0.01358 | -0.0029438 | -0.034791 | 0.0014463 | -0.019121 | -0.02754 | -0.024314 | 0.0055542 | -0.0091003 | 0.066326 | 0.04451 | -0.018367 | -0.0058276 | -0.013537 | -0.073242 | 0.054932 | -0.041199 | -0.059509 | 0.064087 | -0.032043 | -0.013733 | -0.45319 | 0.086975 | -122.168 | 0.054932 | -121.7194 | -121.7834 | -121.6232 | 122.0673 | -0.045776 | -0.16022 | 122.1725 | 122.0947 | 122.0764 | 0.027466 | 0.009156 | -0.05951 | -0.013733 | -0.045776 | 0.3891 | 0.48523 | 0.32501 | 0.54474 | 0.38452 | 0.10529 | -0.01831 | 0.44861 | 122.2229 | 0.096131 | 122.2549 | 122.1634 | 122.1954 | -0.14191 | -122.2687 | 122.0489 | 122.1634 | 122.0352 | 121.6553
1692.5625 | 122.3465 | -122.1222 | 0.082397 | 0.028839 | -0.0042254 | -0.0365 | -0.0013309 | -0.014849 | -0.028608 | -0.022605 | 0.011658 | -0.0082459 | 0.063121 | 0.047715 | -0.019649 | -0.0086048 | -0.014178 | -0.022888 | 0.036621 | -0.045776 | -0.004578 | 0.14648 | 0.041199 | 0.059509 | -0.42114 | 0.050354 | -122.1634 | 0.036621 | -121.6873 | -121.7606 | -121.6232 | 122.0764 | -0.045776 | -0.086975 | 122.2687 | 122.1817 | 122.1634 | 0.10528 | 0.086975 | -0.041199 | -0.032043 | -0.045776 | 0.43488 | 0.49896 | 0.36163 | 0.54016 | 0.40283 | 0.19226 | 0.041198 | 0.47607 | 122.2 | 0.082397 | 122.2137 | 122.1588 | 122.1725 | -0.12817 | -122.2458 | 122.1176 | 122.1588 | 122.0993 | 121.701
1694.3281 | 122.3648 | -122.1085 | 0.091553 | 0.02121 | -0.00508 | -0.033082 | -0.0019717 | -0.021044 | -0.027327 | -0.023887 | 0.008606 | -0.0091003 | 0.062908 | 0.047501 | -0.017513 | -0.0079638 | -0.013537 | -0.041199 | 0.045776 | -0.036621 | -0.004578 | 0.11444 | 0.032043 | 0.054932 | -0.43945 | 0.054932 | -122.1313 | 0.045776 | -121.701 | -121.7606 | -121.6049 | 122.0718 | -0.045777 | -0.096131 | 122.2229 | 122.1634 | 122.1405 | 0.091553 | 0.068664 | -0.022889 | -0.036621 | -0.045777 | 0.40741 | 0.50354 | 0.3479 | 0.52643 | 0.37079 | 0.15106 | 0.032043 | 0.4303 | 122.1771 | 0.082397 | 122.1863 | 122.1542 | 122.1634 | -0.12817 | -122.2229 | 122.1039 | 122.1542 | 122.0673 | 121.669
1696.1094 | 122.2549 | -122.168 | 0.11444 | 0.02121 | -0.0014484 | -0.034363 | 0.0031551 | -0.015917 | -0.029036 | -0.022392 | 0.0025024 | -0.0071777 | 0.065471 | 0.050278 | -0.018794 | -0.0086048 | -0.013965 | -0.045776 | 0.045776 | -0.059509 | -0.064087 | 0.041199 | -0.050354 | -0.050354 | -0.47607 | 0.082397 | -122.1634 | -0.036621 | -121.8201 | -121.8887 | -121.6736 | 122.1085 | -0.068665 | -0.17853 | 122.2092 | 122.1176 | 122.1176 | 0.009155 | 0.009155 | 0.004578 | -0.032044 | -0.15106 | 0.3479 | 0.49438 | 0.27924 | 0.48981 | 0.27466 | 0.10071 | -0.004578 | 0.34332 | 122.1268 | 0.10528 | 122.2458 | 122.2137 | 122.2504 | -0.17395 | -122.2778 | 122.1039 | 122.1313 | 122.1222 | 121.6919
1697.8906 | 122.3236 | -122.1359 | 0.068665 | 0.0059509 | -0.0040118 | -0.036072 | -0.00047626 | -0.019976 | -0.029463 | -0.020042 | -0.00054937 | -0.0093139 | 0.065471 | 0.04387 | -0.017299 | -0.0079638 | -0.015674 | -0.073242 | 0.050354 | -0.050354 | -0.064087 | 0.068665 | -0.045776 | -0.013733 | -0.45319 | 0.059509 | -122.1909 | 0.032043 | -121.7514 | -121.8063 | -121.6232 | 122.0856 | -0.018311 | -0.13275 | 122.2046 | 122.1222 | 122.0901 | 0.036621 | 0.004578 | -0.054932 | -0.009156 | -0.036622 | 0.38452 | 0.51269 | 0.32959 | 0.56763 | 0.38452 | 0.11902 | -0.013733 | 0.43945 | 122.2229 | 0.10071 | 122.2504 | 122.1863 | 122.1954 | -0.11902 | -122.2595 | 122.0718 | 122.168 | 122.0627 | 121.6827
1699.6719 | 122.3969 | -122.1222 | 0.086975 | 0.01358 | -0.0055072 | -0.036072 | -0.00026266 | -0.016131 | -0.028822 | -0.021324 | 0.008606 | -0.0095275 | 0.065044 | 0.049637 | -0.019863 | -0.0092456 | -0.018878 | -0.041199 | 0.018311 | -0.045776 | -0.004578 | 0.15564 | 0.059509 | 0.064087 | -0.41657 | 0.059509 | -122.1725 | 0.068665 | -121.6782 | -121.7194 | -121.5958 | 122.0764 | -0.068664 | -0.091553 | 122.2778 | 122.1863 | 122.1817 | 0.10986 | 0.10528 | -0.050354 | -0.027466 | -0.01831 | 0.44403 | 0.52643 | 0.40283 | 0.57678 | 0.45319 | 0.20142 | 0.041198 | 0.49438 | 122.2412 | 0.064087 | 122.2321 | 122.1405 | 122.1817 | -0.13275 | -122.2595 | 122.1176 | 122.1909 | 122.081 | 121.7056
1701.4531 | 122.319 | -122.1451 | 0.091553 | 0.01358 | -0.0025164 | -0.035218 | -4.906e-05 | -0.01784 | -0.027327 | -0.023033 | 0.0055542 | -0.0073913 | 0.065899 | 0.038956 | -0.018367 | -0.0088184 | -0.019305 | -0.009155 | 0.064087 | -0.050354 | 0.009155 | 0.13275 | 0.018311 | 0.027466 | -0.3479 | 0.07782 | -122.1725 | 0.022888 | -121.7422 | -121.8063 | -121.6415 | 122.0947 | -0.027466 | -0.082398 | 122.2778 | 122.1725 | 122.1634 | 0.07782 | 0.068665 | -0.027465 | -0.013733 | -0.068665 | 0.40283 | 0.50354 | 0.33875 | 0.531 | 0.36621 | 0.18311 | 0.059509 | 0.4303 | 122.1954 | 0.11444 | 122.2504 | 122.2092 | 122.2229 | -0.14191 | -122.2641 | 122.1542 | 122.168 | 122.1359 | 121.7972
1703.1719 | 122.3785 | -122.1405 | 0.09613 | -0.0016786 | -0.0037982 | -0.035645 | -0.0015445 | -0.021685 | -0.028822 | -0.022819 | 0.008606 | -0.0086731 | 0.065471 | 0.045365 | -0.020503 | -0.0077502 | -0.014819 | 0.009155 | 0.013733 | -0.013733 | 0.050354 | 0.20599 | 0.10529 | 0.10986 | -0.33417 | 0.054932 | -122.1542 | 0.073242 | -121.6782 | -121.7194 | -121.6095 | 122.1268 | -0.082397 | -0.045776 | 122.3465 | 122.2504 | 122.2458 | 0.1236 | 0.11902 | -0.013733 | -0.041198 | -0.022888 | 0.46234 | 0.53101 | 0.42114 | 0.54474 | 0.43488 | 0.21973 | 0.064087 | 0.47607 | 122.2275 | 0.027466 | 122.2092 | 122.1542 | 122.1954 | -0.10986 | -122.2504 | 122.1909 | 122.2137 | 122.1497 | 121.8063
1704.9375 | 122.287 | -122.1817 | 0.1236 | -0.0016786 | -0.0070026 | -0.0365 | 0.0012325 | -0.016985 | -0.030745 | -0.026237 | 0.0025024 | -0.0061095 | 0.066753 | 0.042801 | -0.021572 | -0.010527 | -0.019519 | -0.064087 | 0.054932 | -0.059509 | -0.073242 | 0.059509 | -0.009155 | 0 | -0.4303 | 0.10986 | -122.2412 | -0.041199 | -121.7834 | -121.8567 | -121.6965 | 122.1222 | -0.068664 | -0.19684 | 122.2412 | 122.1817 | 122.1725 | 0.059509 | 0.050354 | -0.059509 | -0.013733 | -0.16479 | 0.39826 | 0.48523 | 0.32501 | 0.54474 | 0.38452 | 0.11902 | -0.013733 | 0.45776 | 122.2 | 0.11444 | 122.3511 | 122.2366 | 122.2916 | -0.1831 | -122.3648 | 122.1085 | 122.1405 | 122.1176 | 121.7514
1706.7188 | 122.4152 | -122.1405 | 0.086975 | 0.01358 | -0.0042254 | -0.036286 | -0.0026127 | -0.020617 | -0.030317 | -0.020469 | 0.0055542 | -0.0086731 | 0.063762 | 0.041733 | -0.019222 | -0.010741 | -0.015033 | 0.022888 | 0.004578 | -0.013733 | 0.064087 | 0.22888 | 0.14191 | 0.10986 | -0.31586 | 0.050354 | -122.1451 | 0.10986 | -121.6324 | -121.7148 | -121.5958 | 122.1268 | -0.082397 | -0.022888 | 122.3694 | 122.2504 | 122.2824 | 0.1236 | 0.15564 | -0.004578 | -0.036621 | 0.022888 | 0.50812 | 0.54474 | 0.42572 | 0.54932 | 0.4303 | 0.24261 | 0.07782 | 0.5127 | 122.2549 | 0.018311 | 122.1954 | 122.1451 | 122.1909 | -0.10071 | -122.2321 | 122.2046 | 122.2504 | 122.1634 | 121.8246
1708.5 | 122.4106 | -122.1268 | 0.09613 | 0.01358 | -0.003371 | -0.035859 | -0.0026127 | -0.018908 | -0.029463 | -0.024528 | -0.00054937 | -0.0078185 | 0.062481 | 0.048569 | -0.018581 | -0.0064684 | -0.013965 | -0.027466 | 0.022888 | -0.027466 | 0 | 0.15106 | 0.073242 | 0.059509 | -0.44403 | 0.068665 | -122.1725 | 0.07782 | -121.6827 | -121.7377 | -121.5912 | 122.0993 | -0.073242 | -0.09613 | 122.2778 | 122.1863 | 122.2 | 0.086975 | 0.10071 | -0.045776 | -0.027465 | -0.01831 | 0.44403 | 0.53558 | 0.3891 | 0.58136 | 0.43487 | 0.17853 | 0.027466 | 0.48981 | 122.2504 | 0.050354 | 122.2412 | 122.1497 | 122.1954 | -0.1236 | -122.2687 | 122.1268 | 122.2046 | 122.0993 | 121.6827
1710.2031 | 122.2916 | -122.168 | 0.10071 | -0.0016786 | -0.00273 | -0.034363 | 0.00037814 | -0.019335 | -0.030317 | -0.021537 | -0.00054937 | -0.0067505 | 0.065471 | 0.050278 | -0.021999 | -0.010527 | -0.014819 | -0.07782 | 0.045776 | -0.045776 | -0.068665 | 0.073242 | -0.009155 | 0 | -0.4715 | 0.086975 | -122.1771 | -0.032043 | -121.7789 | -121.8475 | -121.7148 | 122.1222 | -0.054932 | -0.16937 | 122.2412 | 122.168 | 122.1588 | 0.045776 | 0.036621 | -0.009155 | -0.013733 | -0.13275 | 0.3891 | 0.45319 | 0.32044 | 0.46234 | 0.32959 | 0.11902 | -0.022889 | 0.39825 | 122.1451 | 0.091552 | 122.2641 | 122.2137 | 122.2549 | -0.14648 | -122.2778 | 122.0993 | 122.1359 | 122.0901 | 121.6965
1711.9688 | 122.3053 | -122.168 | 0.11444 | 0.0059509 | -0.0042254 | -0.037354 | -0.0011173 | -0.020189 | -0.030531 | -0.023246 | 0.0025024 | -0.0086731 | 0.066753 | 0.040665 | -0.023921 | -0.0098864 | -0.01781 | -0.054932 | 0.041199 | -0.045776 | -0.07782 | 0.07782 | 0 | -0.009155 | -0.46234 | 0.07782 | -122.2092 | -0.032043 | -121.7926 | -121.8521 | -121.6873 | 122.1222 | -0.073242 | -0.19226 | 122.2458 | 122.1588 | 122.168 | 0.036621 | 0.045776 | -0.041198 | -0.036621 | -0.14648 | 0.37537 | 0.48065 | 0.31586 | 0.52185 | 0.35705 | 0.1236 | -0.032044 | 0.41656 | 122.1771 | 0.086975 | 122.287 | 122.2092 | 122.2458 | -0.16022 | -122.3236 | 122.0901 | 122.1359 | 122.113 | 121.7056
1713.7344 | 122.374 | -122.1542 | 0.091553 | 0.01358 | -0.003371 | -0.035004 | 0.0016599 | -0.021471 | -0.028181 | -0.023674 | 0.0055542 | -0.0099549 | 0.063549 | 0.045579 | -0.017299 | -0.009032 | -0.016528 | -0.027466 | 0.027466 | -0.050354 | 0 | 0.13733 | 0.041199 | 0.059509 | -0.45776 | 0.054932 | -122.1817 | 0.054932 | -121.7285 | -121.7834 | -121.6507 | 122.1039 | -0.064087 | -0.091553 | 122.2916 | 122.2137 | 122.1954 | 0.10986 | 0.091553 | -0.027466 | -0.036621 | -0.036621 | 0.42572 | 0.50354 | 0.37079 | 0.53101 | 0.39826 | 0.18768 | 0.050354 | 0.45319 | 122.2366 | 0.07782 | 122.2366 | 122.1817 | 122.2092 | -0.14191 | -122.2733 | 122.1542 | 122.2092 | 122.1268 | 121.6965
1715.5156 | 122.4197 | -122.1313 | 0.073242 | 0.0059509 | -0.006148 | -0.035645 | 0.00059174 | -0.022753 | -0.030104 | -0.022819 | 0.0055542 | -0.0078185 | 0.063335 | 0.047501 | -0.01794 | -0.0101 | -0.010333 | 0.022888 | 0.022888 | -0.013733 | 0.068665 | 0.2243 | 0.11444 | 0.11444 | -0.33417 | 0.041199 | -122.1634 | 0.09613 | -121.6599 | -121.7148 | -121.6049 | 122.1176 | -0.050354 | -0.004577 | 122.3557 | 122.2458 | 122.2458 | 0.12817 | 0.12817 | -0.032043 | -0.032043 | 0.022888 | 0.4715 | 0.52643 | 0.41657 | 0.55847 | 0.44861 | 0.23804 | 0.082398 | 0.50354 | 122.2595 | 0.036621 | 122.2046 | 122.1542 | 122.1725 | -0.086975 | -122.2366 | 122.2 | 122.2275 | 122.1542 | 121.7972
1717.2344 | 122.3053 | -122.168 | 0.11902 | 0.0059509 | -0.0010212 | -0.036286 | 0.0027279 | -0.017626 | -0.028181 | -0.021537 | 0.0055542 | -0.0063233 | 0.063549 | 0.037675 | -0.017085 | -0.0088184 | -0.015887 | -0.032043 | 0.036621 | -0.054932 | -0.032043 | 0.082397 | -0.027466 | -0.022888 | -0.45776 | 0.082397 | -122.1954 | 0 | -121.8109 | -121.8887 | -121.7056 | 122.113 | -0.082398 | -0.15106 | 122.2504 | 122.1451 | 122.1405 | 0.032044 | 0.027466 | -0.027466 | -0.036622 | -0.11902 | 0.35706 | 0.46234 | 0.27924 | 0.48981 | 0.3067 | 0.13733 | 0.022889 | 0.38452 | 122.1954 | 0.091553 | 122.2778 | 122.2046 | 122.2504 | -0.17395 | -122.3145 | 122.1359 | 122.168 | 122.1359 | 121.7102
1719.0312 | 122.438 | -122.1497 | 0.086975 | 0.01358 | -0.0040118 | -0.036072 | -0.00090366 | -0.021898 | -0.030317 | -0.022178 | 0.0025024 | -0.0093139 | 0.063762 | 0.044724 | -0.020503 | -0.007323 | -0.013324 | -0.009155 | 0.027466 | -0.009155 | 0.054932 | 0.21973 | 0.13275 | 0.11902 | -0.3479 | 0.041199 | -122.1863 | 0.09613 | -121.6553 | -121.7285 | -121.6003 | 122.1405 | -0.059509 | -0.032043 | 122.3694 | 122.2687 | 122.2824 | 0.12817 | 0.14191 | -0.036621 | -0.045776 | 0.009155 | 0.49439 | 0.54932 | 0.42114 | 0.58594 | 0.45776 | 0.22888 | 0.064087 | 0.53101 | 122.2824 | 0.036621 | 122.2275 | 122.1771 | 122.1909 | -0.09613 | -122.2733 | 122.2046 | 122.2458 | 122.1405 | 121.8018
1720.8125 | 122.3007 | -122.1725 | 0.10529 | 0.0059509 | -0.0020892 | -0.034577 | 0.00059174 | -0.018267 | -0.02754 | -0.023033 | 0.0025024 | -0.0063233 | 0.065685 | 0.035752 | -0.018581 | -0.0094592 | -0.016742 | -0.032043 | 0.045776 | -0.059509 | -0.045776 | 0.086975 | -0.027466 | -0.018311 | -0.46234 | 0.059509 | -122.2092 | -0.009155 | -121.8201 | -121.8842 | -121.7102 | 122.113 | -0.05951 | -0.15106 | 122.2595 | 122.1542 | 122.1451 | 0.041198 | 0.032043 | -0.036621 | -0.045777 | -0.11444 | 0.35248 | 0.46234 | 0.28839 | 0.49896 | 0.32501 | 0.14648 | 0.013733 | 0.3891 | 122.2 | 0.10528 | 122.2687 | 122.2183 | 122.2321 | -0.16479 | -122.3145 | 122.1268 | 122.1634 | 122.1405 | 121.7102
1722.5312 | 122.4609 | -122.1405 | 0.073242 | -0.0016786 | -0.0037982 | -0.035645 | 0.0012325 | -0.020403 | -0.028822 | -0.018974 | 0.0025024 | -0.0080321 | 0.065258 | 0.045151 | -0.020076 | -0.0098864 | -0.015674 | -0.018311 | 0.022888 | -0.045776 | 0.036621 | 0.19684 | 0.10071 | 0.10529 | -0.39825 | 0.041199 | -122.2 | 0.09613 | -121.6644 | -121.7194 | -121.5912 | 122.0947 | -0.050354 | -0.036621 | 122.3373 | 122.2458 | 122.2412 | 0.15106 | 0.14648 | -0.059509 | -0.032043 | 0.022888 | 0.47607 | 0.54932 | 0.42114 | 0.60882 | 0.48065 | 0.24261 | 0.082397 | 0.53558 | 122.2961 | 0.068664 | 122.2412 | 122.1634 | 122.1817 | -0.11902 | -122.2733 | 122.1771 | 122.2366 | 122.1222 | 121.7422
1724.3125 | 122.2916 | -122.1909 | 0.091553 | 0.0059509 | -0.0031574 | -0.035004 | 0.00080534 | -0.01848 | -0.028822 | -0.025169 | 0.0055542 | -0.0078185 | 0.066967 | 0.045365 | -0.020503 | -0.0081774 | -0.02016 | -0.059509 | 0.073242 | -0.045776 | -0.07782 | 0.013733 | -0.045776 | -0.045776 | -0.54932 | 0.086975 | -122.2229 | -0.045776 | -121.8521 | -121.9208 | -121.7285 | 122.1451 | -0.018311 | -0.16937 | 122.2046 | 122.1451 | 122.1451 | 0 | 0 | -0.032043 | -0.004578 | -0.13733 | 0.33874 | 0.46234 | 0.27008 | 0.49438 | 0.30212 | 0.059509 | -0.032044 | 0.37079 | 122.1771 | 0.11902 | 122.3099 | 122.2641 | 122.2778 | -0.13733 | -122.3145 | 122.113 | 122.1451 | 122.1313 | 121.6415
1726.0312 | 122.3923 | -122.1588 | 0.09613 | 0.02121 | -0.0065754 | -0.035004 | 0.00059174 | -0.021685 | -0.028395 | -0.023033 | 0.0055542 | -0.0084595 | 0.06483 | 0.048783 | -0.019222 | -0.008391 | -0.01311 | -0.036621 | 0.032043 | -0.022888 | 0 | 0.15106 | 0.045776 | 0.059509 | -0.47607 | 0.059509 | -122.2092 | 0.045776 | -121.7468 | -121.8155 | -121.6599 | 122.1359 | -0.064087 | -0.09613 | 122.3099 | 122.2183 | 122.2046 | 0.082397 | 0.068664 | -0.050354 | -0.036621 | -0.050354 | 0.41199 | 0.49896 | 0.34332 | 0.54932 | 0.39368 | 0.17395 | 0.022888 | 0.46234 | 122.2549 | 0.054931 | 122.2687 | 122.1909 | 122.2183 | -0.11902 | -122.3053 | 122.1588 | 122.2046 | 122.1222 | 121.6827
1727.8125 | 122.3282 | -122.2137 | 0.10529 | 0.044098 | -0.0046526 | -0.0365 | 0.00037814 | -0.019762 | -0.029463 | -0.023674 | 0.014709 | -0.0067505 | 0.065044 | 0.041306 | -0.020076 | -0.0098864 | -0.014605 | -0.045776 | 0.073242 | -0.064087 | -0.054932 | 0.064087 | -0.004578 | 0.022888 | -0.4715 | 0.10071 | -122.2549 | -0.032043 | -121.8063 | -121.8613 | -121.6965 | 122.1497 | -0.032044 | -0.16022 | 122.2778 | 122.2366 | 122.2092 | 0.086975 | 0.059509 | -0.041199 | -0.004578 | -0.13733 | 0.40741 | 0.51727 | 0.35248 | 0.55847 | 0.39368 | 0.12817 | 0.009155 | 0.44861 | 122.2229 | 0.13733 | 122.3557 | 122.287 | 122.3145 | -0.16937 | -122.3602 | 122.1588 | 122.1817 | 122.168 | 121.7422
1729.5938 | 122.4472 | -122.1634 | 0.086975 | 0.0059509 | -0.003371 | -0.034363 | 0.0012325 | -0.01549 | -0.02989 | -0.027519 | 0.0025024 | -0.0082459 | 0.063335 | 0.047928 | -0.017299 | -0.0068958 | -0.014605 | -0.013733 | 0.018311 | -0.022888 | 0.050354 | 0.17395 | 0.07782 | 0.068665 | -0.40741 | 0.041199 | -122.2458 | 0.11444 | -121.7056 | -121.7697 | -121.6187 | 122.1405 | -0.068664 | -0.036621 | 122.3373 | 122.2321 | 122.2412 | 0.091553 | 0.10071 | -0.082398 | -0.045776 | 0.027466 | 0.45776 | 0.54474 | 0.39368 | 0.62714 | 0.47608 | 0.19684 | 0.073242 | 0.54016 | 122.3602 | 0.041199 | 122.287 | 122.1817 | 122.2046 | -0.10986 | -122.3328 | 122.2137 | 122.2778 | 122.1497 | 121.756
1731.375 | 122.3145 | -122.1909 | 0.11902 | 0.02121 | -0.0029438 | -0.035859 | -0.0011173 | -0.021044 | -0.028822 | -0.021965 | -0.00054937 | -0.0067505 | 0.067394 | 0.040879 | -0.023708 | -0.0096728 | -0.015033 | -0.073242 | 0.050354 | -0.064087 | -0.086975 | 0.059509 | -0.009155 | -0.009155 | -0.5127 | 0.07782 | -122.2183 | -0.041199 | -121.8292 | -121.875 | -121.7285 | 122.1268 | -0.068665 | -0.20599 | 122.2504 | 122.1817 | 122.1817 | 0.054932 | 0.054932 | -0.027466 | -0.041199 | -0.16022 | 0.36163 | 0.46234 | 0.31586 | 0.48981 | 0.34332 | 0.1236 | -0.022888 | 0.3891 | 122.1771 | 0.11444 | 122.2961 | 122.2412 | 122.2687 | -0.18311 | -122.3373 | 122.1039 | 122.1497 | 122.1176 | 121.6782
1733.1094 | 122.374 | -122.2 | 0.10986 | 0.02121 | -0.001662 | -0.032868 | 0.0020871 | -0.020403 | -0.029463 | -0.019401 | 0.0055542 | -0.0065369 | 0.065471 | 0.041947 | -0.018581 | -0.010741 | -0.019305 | 0 | 0.050354 | -0.050354 | 0 | 0.14191 | 0.036621 | 0.036621 | -0.40283 | 0.068665 | -122.2458 | 0.045776 | -121.7697 | -121.8613 | -121.6644 | 122.1497 | -0.059509 | -0.10986 | 122.3419 | 122.2366 | 122.2366 | 0.086975 | 0.086975 | -0.045777 | -0.041198 | -0.064087 | 0.4303 | 0.53558 | 0.33875 | 0.58136 | 0.38452 | 0.19226 | 0.050354 | 0.47608 | 122.2916 | 0.10071 | 122.3145 | 122.2504 | 122.2687 | -0.16022 | -122.3557 | 122.2 | 122.2458 | 122.2 | 121.7972
1734.8906 | 122.3236 | -122.168 | 0.091553 | 0.0059509 | -0.0018756 | -0.033722 | 0.0016599 | -0.015062 | -0.028181 | -0.021965 | -0.00054937 | -0.0052551 | 0.063976 | 0.044938 | -0.018794 | -0.0101 | -0.016955 | -0.050354 | 0.041199 | -0.054932 | -0.045776 | 0.086975 | -0.022888 | -0.032043 | -0.48523 | 0.068665 | -122.2412 | -0.004578 | -121.8155 | -121.8887 | -121.7056 | 122.113 | -0.050354 | -0.13733 | 122.2549 | 122.1359 | 122.1451 | 0.022889 | 0.032044 | -0.073242 | -0.022888 | -0.096131 | 0.35248 | 0.46234 | 0.27924 | 0.53558 | 0.35248 | 0.14191 | 0.009156 | 0.42572 | 122.2366 | 0.096131 | 122.3099 | 122.2092 | 122.2366 | -0.14649 | -122.3328 | 122.1222 | 122.1634 | 122.1176 | 121.6827
1736.6719 | 122.3053 | -122.2046 | 0.11902 | 0.0059509 | -0.0012348 | -0.033722 | -0.00069006 | -0.015703 | -0.027967 | -0.020897 | 0.008606 | -0.0093139 | 0.064617 | 0.045579 | -0.018154 | -0.0096728 | -0.013537 | -0.045776 | 0.059509 | -0.050354 | -0.09613 | 0.018311 | -0.068665 | -0.059509 | -0.56763 | 0.07782 | -122.2366 | -0.018311 | -121.8658 | -121.9482 | -121.7468 | 122.1542 | -0.05951 | -0.21515 | 122.2229 | 122.1451 | 122.1359 | -0.009155 | -0.018311 | -0.032043 | -0.041199 | -0.13733 | 0.33875 | 0.45776 | 0.25635 | 0.48981 | 0.28839 | 0.068665 | -0.045776 | 0.37079 | 122.2183 | 0.10986 | 122.3145 | 122.2641 | 122.2824 | -0.16937 | -122.3557 | 122.1085 | 122.1863 | 122.1588 | 121.637
1738.4531 | 122.4243 | -122.1634 | 0.054932 | 0.028839 | -0.0048664 | -0.034577 | 0.00080534 | -0.015917 | -0.025618 | -0.021324 | 0.017761 | -0.0084595 | 0.066326 | 0.049851 | -0.019863 | -0.0062548 | -0.013324 | 0 | 0.022888 | -0.027466 | 0.036621 | 0.21973 | 0.086975 | 0.07782 | -0.43488 | 0.045776 | -122.2137 | 0.064087 | -121.7331 | -121.8018 | -121.6599 | 122.1359 | -0.032044 | -0.018311 | 122.3831 | 122.2412 | 122.2504 | 0.10529 | 0.11444 | -0.050354 | -0.009156 | 0.009155 | 0.4303 | 0.50354 | 0.36163 | 0.55389 | 0.41199 | 0.24719 | 0.064087 | 0.48065 | 122.2778 | 0.050354 | 122.2595 | 122.1863 | 122.2092 | -0.082398 | -122.2687 | 122.2 | 122.2275 | 122.1634 | 121.7285
1740.2188 | 122.4106 | -122.1817 | 0.091553 | 0.02121 | -0.0046526 | -0.035859 | -0.0026127 | -0.019976 | -0.028822 | -0.020256 | 0.0055542 | -0.0091003 | 0.064403 | 0.042588 | -0.018367 | -0.0077502 | -0.014605 | -0.036621 | 0.027466 | -0.022888 | 0 | 0.13733 | 0.032043 | 0.054932 | -0.53101 | 0.059509 | -122.2275 | 0.045776 | -121.7606 | -121.8246 | -121.6644 | 122.1588 | -0.064087 | -0.091553 | 122.319 | 122.2366 | 122.2137 | 0.07782 | 0.054931 | -0.045776 | -0.032044 | -0.045777 | 0.42114 | 0.51727 | 0.35706 | 0.56305 | 0.40283 | 0.16022 | 0.022888 | 0.46692 | 122.2733 | 0.050354 | 122.287 | 122.2092 | 122.2412 | -0.11444 | -122.319 | 122.1817 | 122.2275 | 122.1451 | 121.6507
1742 | 122.3282 | -122.2137 | 0.10986 | 0.0059509 | -0.001662 | -0.0365 | 0.00016454 | -0.019549 | -0.02754 | -0.024955 | 0.0025024 | -0.0056823 | 0.06419 | 0.046647 | -0.020503 | -0.0098864 | -0.015033 | -0.068665 | 0.050354 | -0.068665 | -0.091553 | 0 | -0.073242 | -0.059509 | -0.57678 | 0.07782 | -122.2687 | -0.027466 | -121.8567 | -121.9345 | -121.7285 | 122.1451 | -0.059509 | -0.20142 | 122.2137 | 122.1542 | 122.1405 | 0.009156 | -0.004577 | -0.054932 | -0.032043 | -0.13733 | 0.35706 | 0.48523 | 0.27924 | 0.54016 | 0.33417 | 0.068665 | -0.022888 | 0.41199 | 122.2412 | 0.11902 | 122.3465 | 122.2641 | 122.2916 | -0.17853 | -122.3785 | 122.1222 | 122.1863 | 122.1451 | 121.637
1743.7188 | 122.4426 | -122.1451 | 0.086975 | 0.01358 | -0.0065754 | -0.035431 | -0.0026127 | -0.022539 | -0.029463 | -0.020897 | -0.00054937 | -0.0080321 | 0.065044 | 0.052415 | -0.022426 | -0.0098864 | -0.019305 | 0.013733 | 0.022888 | -0.018311 | 0.050354 | 0.21057 | 0.10529 | 0.086975 | -0.41199 | 0.036621 | -122.2229 | 0.064087 | -121.7194 | -121.7697 | -121.6461 | 122.1268 | -0.064087 | -0.036621 | 122.3557 | 122.2321 | 122.2504 | 0.10529 | 0.1236 | -0.077819 | -0.050354 | -0.022888 | 0.42572 | 0.49896 | 0.37537 | 0.57678 | 0.45319 | 0.22888 | 0.068665 | 0.50354 | 122.287 | 0.041199 | 122.2595 | 122.168 | 122.1817 | -0.10529 | -122.3099 | 122.1954 | 122.2092 | 122.1588 | 121.7331
1745.5156 | 122.4106 | -122.1954 | 0.068665 | 0.01358 | -0.0031574 | -0.034577 | -0.00090366 | -0.019335 | -0.027754 | -0.023033 | 0.008606 | -0.0084595 | 0.066326 | 0.048356 | -0.019435 | -0.0088184 | -0.012042 | -0.041199 | 0.027466 | -0.036621 | -0.009155 | 0.12817 | 0.041199 | 0.054932 | -0.54474 | 0.054932 | -122.2641 | 0.041199 | -121.7697 | -121.8292 | -121.6644 | 122.1588 | -0.041199 | -0.07782 | 122.3236 | 122.2504 | 122.2366 | 0.091553 | 0.07782 | -0.068664 | -0.013733 | -0.027466 | 0.42572 | 0.53101 | 0.36621 | 0.59967 | 0.43488 | 0.1648 | 0.027466 | 0.49439 | 122.3053 | 0.064087 | 122.319 | 122.2229 | 122.2504 | -0.10529 | -122.3328 | 122.1863 | 122.2366 | 122.1542 | 121.6507
1747.2344 | 122.3831 | -122.2137 | 0.10071 | 0.044098 | -0.003371 | -0.036286 | 0.0029415 | -0.018267 | -0.029036 | -0.022819 | 0.011658 | -0.0044007 | 0.06483 | 0.037888 | -0.022853 | -0.0092456 | -0.017383 | -0.013733 | 0.068665 | -0.059509 | -0.022888 | 0.091553 | 0.036621 | 0.022888 | -0.4715 | 0.091553 | -122.2412 | 0.018311 | -121.7789 | -121.8475 | -121.6873 | 122.1542 | -0.032043 | -0.1236 | 122.3053 | 122.2366 | 122.2504 | 0.082397 | 0.09613 | -0.027466 | -0.009155 | -0.082397 | 0.43488 | 0.52643 | 0.36621 | 0.55389 | 0.39368 | 0.15106 | 0.036621 | 0.46234 | 122.2595 | 0.12817 | 122.3328 | 122.2824 | 122.3053 | -0.16022 | -122.3419 | 122.1909 | 122.2321 | 122.2 | 121.7422
1749.0156 | 122.3923 | -122.2092 | 0.09613 | 0.036468 | -0.001662 | -0.036927 | 0.00016454 | -0.016131 | -0.029249 | -0.023246 | 0.008606 | -0.0065369 | 0.065258 | 0.047074 | -0.019863 | -0.011382 | -0.014392 | -0.022888 | 0.054932 | -0.054932 | -0.004578 | 0.09613 | 0.032043 | 0.018311 | -0.46234 | 0.091553 | -122.2549 | 0.018311 | -121.7972 | -121.8475 | -121.6965 | 122.1542 | -0.041198 | -0.10071 | 122.3053 | 122.2275 | 122.2412 | 0.073243 | 0.086975 | -0.045777 | -0.004577 | -0.077819 | 0.41199 | 0.51269 | 0.36163 | 0.55847 | 0.40741 | 0.15106 | 0.050354 | 0.45776 | 122.2733 | 0.10986 | 122.3465 | 122.2641 | 122.3007 | -0.15106 | -122.3511 | 122.2046 | 122.2275 | 122.1863 | 121.7468
1750.7188 | 122.438 | -122.1588 | 0.07782 | -0.0016786 | -0.0040118 | -0.036927 | -4.906e-05 | -0.013994 | -0.028822 | -0.023887 | 0.0025024 | -0.0086731 | 0.06419 | 0.040879 | -0.017299 | -0.0077502 | -0.016955 | -0.041199 | 0.032043 | -0.032043 | -0.018311 | 0.10986 | -0.009155 | 0.018311 | -0.50812 | 0.032043 | -122.2549 | 0.10071 | -121.7651 | -121.8155 | -121.6415 | 122.1268 | -0.045777 | -0.096131 | 122.2687 | 122.1771 | 122.1497 | 0.050354 | 0.022888 | -0.096131 | -0.045777 | 0.022888 | 0.39368 | 0.51727 | 0.34332 | 0.6134 | 0.43945 | 0.14191 | 0.013732 | 0.48981 | 122.3557 | 0.064086 | 122.287 | 122.1909 | 122.1909 | -0.10986 | -122.3328 | 122.1405 | 122.2595 | 122.1176 | 121.6507
1752.5 | 122.438 | -122.1817 | 0.07782 | 0.028839 | -0.004439 | -0.034791 | -0.0017581 | -0.016558 | -0.028822 | -0.022178 | 0.011658 | -0.010809 | 0.06483 | 0.048142 | -0.017085 | -0.007323 | -0.013751 | 0.018311 | 0.018311 | -0.009155 | 0.059509 | 0.21057 | 0.086975 | 0.091553 | -0.44403 | 0.045776 | -122.2275 | 0.07782 | -121.7468 | -121.8338 | -121.6507 | 122.1725 | -0.059509 | -0.018311 | 122.3923 | 122.2733 | 122.2687 | 0.10071 | 0.09613 | -0.045776 | -0.032044 | 0 | 0.43488 | 0.53101 | 0.3479 | 0.57678 | 0.39368 | 0.21973 | 0.068664 | 0.48065 | 122.3053 | 0.027466 | 122.2733 | 122.2 | 122.2275 | -0.086975 | -122.3053 | 122.2412 | 122.2595 | 122.2 | 121.7377
1754.2812 | 122.3511 | -122.2183 | 0.11902 | 0.0059509 | -0.003371 | -0.037354 | -0.00047626 | -0.021898 | -0.026472 | -0.024101 | 0.0055542 | -0.0061095 | 0.062694 | 0.04921 | -0.023921 | -0.0081774 | -0.017383 | -0.027466 | 0.032043 | -0.036621 | -0.050354 | 0.09613 | 0.004578 | 0.004578 | -0.52185 | 0.068665 | -122.2458 | -0.027466 | -121.8292 | -121.8933 | -121.7514 | 122.1817 | -0.086976 | -0.16937 | 122.3145 | 122.2229 | 122.2229 | 0.041199 | 0.041199 | -0.027466 | -0.050354 | -0.14649 | 0.3891 | 0.46692 | 0.32501 | 0.49439 | 0.35248 | 0.13275 | -0.013733 | 0.41657 | 122.2183 | 0.068664 | 122.3145 | 122.2504 | 122.287 | -0.15564 | -122.3648 | 122.168 | 122.1909 | 122.1909 | 121.6965
1756 | 122.3557 | -122.2137 | 0.10986 | 0.0059509 | -0.0063616 | -0.037995 | -0.00047626 | -0.016558 | -0.029036 | -0.021537 | 0.0025024 | -0.0058959 | 0.063549 | 0.041733 | -0.022212 | -0.009032 | -0.013751 | -0.018311 | 0.027466 | -0.036621 | -0.036621 | 0.11902 | 0.045776 | 0.027466 | -0.5127 | 0.07782 | -122.2595 | -0.018311 | -121.8246 | -121.8887 | -121.7422 | 122.1771 | -0.082397 | -0.14648 | 122.3328 | 122.2412 | 122.2595 | 0.064087 | 0.082397 | -0.045776 | -0.032043 | -0.12817 | 0.3891 | 0.4715 | 0.32501 | 0.51727 | 0.37079 | 0.15564 | 0 | 0.43488 | 122.2412 | 0.064087 | 122.3373 | 122.2412 | 122.2916 | -0.14648 | -122.3694 | 122.1771 | 122.1954 | 122.1954 | 121.7011
1757.7656 | 122.3831 | -122.2412 | 0.10529 | -0.0016786 | -0.00508 | -0.038422 | -0.0023989 | -0.016558 | -0.028181 | -0.025169 | 0.0055542 | -0.0082459 | 0.06419 | 0.04451 | -0.02029 | -0.0092456 | -0.014392 | -0.004578 | 0.009155 | -0.027466 | -0.009155 | 0.15564 | 0.054932 | 0.045776 | -0.48981 | 0.068665 | -122.2504 | 0.009155 | -121.8201 | -121.8567 | -121.7468 | 122.2137 | -0.096131 | -0.11444 | 122.3969 | 122.287 | 122.2961 | 0.073242 | 0.082398 | -0.009155 | -0.036621 | -0.096131 | 0.42114 | 0.49439 | 0.38452 | 0.50354 | 0.39368 | 0.18311 | 0.018311 | 0.4303 | 122.2595 | 0.036621 | 122.319 | 122.2504 | 122.3099 | -0.13275 | -122.3557 | 122.2321 | 122.2504 | 122.2366 | 121.7514
1759.5469 | 122.4792 | -122.1771 | 0.068665 | 0.0059509 | -0.0072162 | -0.035645 | 0.00016454 | -0.021258 | -0.027327 | -0.02346 | 0.0025024 | -0.0097411 | 0.066326 | 0.045365 | -0.016872 | -0.009032 | -0.015887 | 0.013733 | 0 | -0.004578 | 0.086975 | 0.25177 | 0.11902 | 0.11444 | -0.42572 | 0.045776 | -122.2046 | 0.10071 | -121.701 | -121.7606 | -121.6507 | 122.1725 | -0.068665 | 0.01831 | 122.4289 | 122.2916 | 122.2961 | 0.11902 | 0.1236 | -0.027466 | -0.022889 | 0.032043 | 0.47607 | 0.52643 | 0.41657 | 0.55389 | 0.44403 | 0.25635 | 0.091553 | 0.50354 | 122.3053 | 0.004578 | 122.2504 | 122.1771 | 122.2229 | -0.073243 | -122.2733 | 122.2641 | 122.2778 | 122.1909 | 121.7514
1761.3281 | 122.374 | -122.2321 | 0.10986 | -0.0016786 | -0.0037982 | -0.035859 | 0.00080534 | -0.021258 | -0.030317 | -0.026451 | 0.014709 | -0.0080321 | 0.065685 | 0.043229 | -0.021999 | -0.011595 | -0.014605 | -0.064087 | 0.041199 | -0.059509 | -0.091553 | 0.050354 | -0.009155 | 0.018311 | -0.54474 | 0.091553 | -122.2641 | -0.022888 | -121.8658 | -121.9025 | -121.7651 | 122.1725 | -0.068664 | -0.20142 | 122.2824 | 122.2504 | 122.2229 | 0.07782 | 0.050354 | -0.032043 | -0.01831 | -0.13275 | 0.36621 | 0.46692 | 0.32959 | 0.49896 | 0.36163 | 0.10986 | -0.032044 | 0.39825 | 122.2412 | 0.10071 | 122.3557 | 122.2733 | 122.3236 | -0.16937 | -122.374 | 122.1405 | 122.2092 | 122.168 | 121.6873
1763.0469 | 122.3602 | -122.2137 | 0.10529 | 0.01358 | -0.0055072 | -0.034791 | 0.0029415 | -0.015062 | -0.027754 | -0.024742 | 0.0025024 | -0.0067505 | 0.064617 | 0.043229 | -0.016658 | -0.0088184 | -0.015887 | -0.054932 | 0.041199 | -0.045776 | -0.091553 | 0.027466 | -0.064087 | -0.027466 | -0.60425 | 0.068665 | -122.2733 | -0.009155 | -121.8796 | -121.9528 | -121.7331 | 122.168 | -0.064087 | -0.19684 | 122.2412 | 122.1863 | 122.1497 | 0.01831 | -0.018311 | -0.059509 | -0.036621 | -0.11444 | 0.33417 | 0.48065 | 0.26093 | 0.54016 | 0.32043 | 0.073242 | -0.045777 | 0.39368 | 122.2641 | 0.086975 | 122.3419 | 122.2549 | 122.2824 | -0.15106 | -122.3785 | 122.1222 | 122.2046 | 122.1588 | 121.6095
1764.8281 | 122.3831 | -122.2504 | 0.10071 | -0.0093076 | -0.0042254 | -0.035218 | -0.00047626 | -0.021471 | -0.026899 | -0.023674 | 0.0025024 | -0.0080321 | 0.065471 | 0.049851 | -0.020717 | -0.010527 | -0.016101 | -0.032043 | 0.009155 | -0.032043 | -0.013733 | 0.13733 | 0.064087 | 0.050354 | -0.51727 | 0.064087 | -122.2549 | -0.018311 | -121.8292 | -121.8842 | -121.7468 | 122.2183 | -0.091553 | -0.11444 | 122.3877 | 122.3007 | 122.3145 | 0.082397 | 0.09613 | -0.004578 | -0.036621 | -0.11902 | 0.42114 | 0.50354 | 0.36621 | 0.50812 | 0.37079 | 0.16937 | 0.01831 | 0.42572 | 122.2366 | 0.041198 | 122.319 | 122.2595 | 122.3145 | -0.13275 | -122.3557 | 122.2366 | 122.2321 | 122.2183 | 121.7331
1766.6094 | 122.4106 | -122.2183 | 0.10529 | 0.01358 | -0.001662 | -0.036927 | 0.0014463 | -0.018267 | -0.02989 | -0.022178 | 0.008606 | -0.0069641 | 0.064617 | 0.040665 | -0.018367 | -0.0079638 | -0.019305 | -0.004578 | 0.041199 | -0.050354 | -0.018311 | 0.14191 | 0.032043 | 0.018311 | -0.48065 | 0.068665 | -122.2595 | 0.032043 | -121.8109 | -121.8796 | -121.7194 | 122.168 | -0.064087 | -0.1236 | 122.3602 | 122.2366 | 122.2504 | 0.068665 | 0.082397 | -0.041198 | -0.036621 | -0.073243 | 0.40741 | 0.49896 | 0.33875 | 0.54016 | 0.37994 | 0.19226 | 0.032043 | 0.44861 | 122.2916 | 0.091553 | 122.3282 | 122.2595 | 122.287 | -0.15564 | -122.3648 | 122.2 | 122.2504 | 122.2137 | 121.7377
1768.3906 | 122.4838 | -122.1725 | 0.082397 | 0.0059509 | -0.0035846 | -0.034791 | -0.00047626 | -0.018267 | -0.028181 | -0.023246 | 0.0055542 | -0.0093139 | 0.064617 | 0.04451 | -0.01559 | -0.0077502 | -0.01546 | 0 | 0 | -0.022888 | 0.045776 | 0.18768 | 0.064087 | 0.073242 | -0.49896 | 0.018311 | -122.2412 | 0.11902 | -121.7422 | -121.8063 | -121.6324 | 122.1497 | -0.082397 | -0.036621 | 122.3602 | 122.2458 | 122.2366 | 0.09613 | 0.086975 | -0.068665 | -0.064086 | 0.036622 | 0.4303 | 0.54016 | 0.36621 | 0.60883 | 0.43488 | 0.21057 | 0.068664 | 0.49896 | 122.3602 | 0.022888 | 122.2595 | 122.1725 | 122.1909 | -0.10528 | -122.3236 | 122.2183 | 122.2916 | 122.1725 | 121.6736
1770.1094 | 122.4838 | -122.2229 | 0.09613 | 0.0059509 | -0.00508 | -0.035431 | -0.00090366 | -0.020403 | -0.02989 | -0.022392 | -0.00054937 | -0.0082459 | 0.062053 | 0.052415 | -0.020076 | -0.0081774 | -0.014392 | -0.009155 | -0.004578 | -0.036621 | 0.022888 | 0.19684 | 0.10529 | 0.10071 | -0.49439 | 0.045776 | -122.2458 | 0.10529 | -121.7239 | -121.7834 | -121.6507 | 122.1863 | -0.10071 | -0.073242 | 122.4197 | 122.3236 | 122.3282 | 0.13733 | 0.14191 | -0.022889 | -0.050354 | 0.009156 | 0.49896 | 0.5722 | 0.43945 | 0.59509 | 0.46234 | 0.23346 | 0.059509 | 0.52185 | 122.3511 | 0.032043 | 122.2916 | 122.2183 | 122.2687 | -0.13275 | -122.3419 | 122.2458 | 122.3282 | 122.2137 | 121.7285
1771.875 | 122.4655 | -122.2 | 0.086975 | 0.028839 | -0.0052936 | -0.036072 | -0.00090366 | -0.021044 | -0.030745 | -0.02346 | 0.0025024 | -0.0078185 | 0.06419 | 0.046219 | -0.019008 | -0.009032 | -0.016955 | -0.041199 | 0.013733 | -0.036621 | -0.013733 | 0.12817 | 0.041199 | 0.064087 | -0.59052 | 0.054932 | -122.2458 | 0.054932 | -121.7789 | -121.8246 | -121.6782 | 122.1634 | -0.073242 | -0.10071 | 122.3282 | 122.2641 | 122.2412 | 0.10071 | 0.07782 | -0.045777 | -0.032043 | -0.032043 | 0.42114 | 0.52185 | 0.37537 | 0.56763 | 0.42114 | 0.1648 | 0.022888 | 0.46692 | 122.3007 | 0.050354 | 122.3007 | 122.2137 | 122.2549 | -0.1236 | -122.3328 | 122.1863 | 122.2549 | 122.1588 | 121.6095
1773.5938 | 122.493 | -122.2092 | 0.082397 | 0.01358 | -0.0059344 | -0.037995 | -0.0013309 | -0.019121 | -0.029036 | -0.020897 | 0.0025024 | -0.0065369 | 0.066112 | 0.050065 | -0.019435 | -0.0075366 | -0.01546 | 0.004578 | 0 | -0.022888 | 0.064087 | 0.25177 | 0.11902 | 0.14191 | -0.45776 | 0.036621 | -122.2412 | 0.09613 | -121.7194 | -121.7651 | -121.637 | 122.1863 | -0.082397 | -0.01831 | 122.4609 | 122.3511 | 122.3282 | 0.16479 | 0.14191 | -0.032044 | -0.045776 | 0.013733 | 0.48981 | 0.5722 | 0.44403 | 0.60425 | 0.47607 | 0.27466 | 0.086975 | 0.52185 | 122.3373 | 0.022888 | 122.2778 | 122.2092 | 122.2458 | -0.10528 | -122.3236 | 122.2733 | 122.3053 | 122.2137 | 121.7514
1775.375 | 122.4884 | -122.1909 | 0.09613 | 0.02121 | -0.003371 | -0.036072 | -0.0015445 | -0.016344 | -0.030531 | -0.024101 | 0.0025024 | -0.0073913 | 0.064403 | 0.048569 | -0.019649 | -0.0098864 | -0.016742 | 0.004578 | -0.013733 | -0.009155 | 0.054932 | 0.20142 | 0.09613 | 0.10071 | -0.48065 | 0.045776 | -122.2687 | 0.082397 | -121.7606 | -121.8063 | -121.6736 | 122.1817 | -0.10986 | -0.041198 | 122.3923 | 122.2916 | 122.287 | 0.10986 | 0.10528 | -0.07782 | -0.050354 | -0.013733 | 0.4303 | 0.51727 | 0.38452 | 0.59509 | 0.46234 | 0.21057 | 0.064087 | 0.50812 | 122.3511 | -0.004578 | 122.3145 | 122.1771 | 122.2366 | -0.10528 | -122.3648 | 122.2458 | 122.2733 | 122.1954 | 121.7102
1777.1562 | 122.4335 | -122.2229 | 0.091553 | 0.02121 | -0.0037982 | -0.035218 | 0.00016454 | -0.021258 | -0.026686 | -0.021324 | 0.0055542 | -0.0050415 | 0.063762 | 0.042161 | -0.01559 | -0.0075366 | -0.017383 | -0.045776 | 0.054932 | -0.045776 | -0.068665 | 0.054932 | -0.036621 | -0.027466 | -0.61798 | 0.073242 | -122.2778 | 0.036621 | -121.8475 | -121.8933 | -121.7239 | 122.1771 | -0.036621 | -0.16022 | 122.2778 | 122.1954 | 122.1863 | 0.01831 | 0.009155 | -0.054932 | -0.018311 | -0.054932 | 0.37537 | 0.49896 | 0.32959 | 0.55389 | 0.38452 | 0.10071 | -0.022889 | 0.4303 | 122.3145 | 0.10071 | 122.3511 | 122.2778 | 122.2961 | -0.13733 | -122.3694 | 122.1542 | 122.2595 | 122.1771 | 121.6049
1778.875 | 122.3602 | -122.2366 | 0.12817 | 0.01358 | -0.00273 | -0.035004 | 0.0020871 | -0.018908 | -0.028181 | -0.026664 | 0.0025024 | -0.0073913 | 0.065258 | 0.041733 | -0.017726 | -0.0088184 | -0.015674 | -0.041199 | 0.032043 | -0.045776 | -0.054932 | 0.064087 | -0.045776 | -0.054932 | -0.62256 | 0.07782 | -122.2961 | -0.004578 | -121.8887 | -121.962 | -121.7651 | 122.1909 | -0.096131 | -0.18311 | 122.3007 | 122.1817 | 122.1909 | -0.009156 | 0 | -0.05951 | -0.050354 | -0.13275 | 0.3479 | 0.4715 | 0.27466 | 0.53101 | 0.33417 | 0.10986 | -0.009156 | 0.40741 | 122.2916 | 0.077819 | 122.374 | 122.2687 | 122.3145 | -0.17395 | -122.4243 | 122.1817 | 122.2321 | 122.1954 | 121.6141
1780.6406 | 122.4655 | -122.2321 | 0.091553 | 0.01358 | -0.0035846 | -0.035859 | 0.00016454 | -0.015703 | -0.027113 | -0.024101 | 0.0025024 | -0.0080321 | 0.065685 | 0.044297 | -0.017513 | -0.0092456 | -0.016955 | -0.059509 | 0.027466 | -0.054932 | -0.050354 | 0.091553 | -0.045776 | -0.004578 | -0.59967 | 0.064087 | -122.2778 | 0.064087 | -121.8109 | -121.8704 | -121.701 | 122.1771 | -0.064087 | -0.14191 | 122.3236 | 122.2275 | 122.1863 | 0.050354 | 0.009156 | -0.045776 | -0.027466 | -0.027466 | 0.42114 | 0.53101 | 0.36163 | 0.57678 | 0.40741 | 0.14649 | 0.004578 | 0.46692 | 122.3419 | 0.082398 | 122.3419 | 122.2595 | 122.2961 | -0.14649 | -122.3694 | 122.1817 | 122.2961 | 122.1725 | 121.6324
1782.4062 | 122.5113 | -122.2 | 0.07782 | 0.0059509 | -0.0040118 | -0.033936 | -0.00047626 | -0.016131 | -0.025618 | -0.02346 | 0.0025024 | -0.0071777 | 0.065471 | 0.041306 | -0.017513 | -0.0068958 | -0.016528 | -0.009155 | 0.027466 | -0.027466 | 0.032043 | 0.16022 | 0.054932 | 0.059509 | -0.54016 | 0.041199 | -122.2458 | 0.10529 | -121.7651 | -121.8384 | -121.6415 | 122.1725 | -0.050354 | -0.045777 | 122.3602 | 122.2595 | 122.2549 | 0.086975 | 0.082398 | -0.045777 | -0.036621 | 0.027466 | 0.43488 | 0.55847 | 0.36163 | 0.60425 | 0.40741 | 0.18768 | 0.059509 | 0.48065 | 122.3511 | 0.054932 | 122.287 | 122.2275 | 122.2412 | -0.10529 | -122.3236 | 122.2321 | 122.3053 | 122.1909 | 121.6599
1784.1406 | 122.3648 | -122.2641 | 0.1236 | 0.0059509 | -0.0023028 | -0.035218 | 0.0010189 | -0.015703 | -0.028822 | -0.024742 | 0.0025024 | -0.0084595 | 0.06419 | 0.041306 | -0.02029 | -0.007323 | -0.013324 | -0.068665 | 0.041199 | -0.045776 | -0.059509 | 0.041199 | -0.045776 | -0.050354 | -0.65002 | 0.091553 | -122.287 | -0.041199 | -121.9254 | -121.9711 | -121.7834 | 122.2183 | -0.082397 | -0.1831 | 122.3053 | 122.2137 | 122.2183 | -0.004578 | 0 | -0.022888 | -0.032043 | -0.16479 | 0.33875 | 0.48065 | 0.29297 | 0.50354 | 0.31586 | 0.086975 | -0.013733 | 0.36163 | 122.2458 | 0.086975 | 122.3785 | 122.3053 | 122.3557 | -0.16937 | -122.4106 | 122.2046 | 122.2229 | 122.1954 | 121.6141
1785.9062 | 122.3831 | -122.2549 | 0.10529 | 0.0059509 | -0.0020892 | -0.035218 | -0.0019717 | -0.024462 | -0.031385 | -0.021537 | 0.0055542 | -0.0095275 | 0.063976 | 0.045579 | -0.021785 | -0.009032 | -0.017596 | -0.027466 | 0.036621 | -0.032043 | -0.027466 | 0.11902 | 0.032043 | 0.018311 | -0.62256 | 0.073242 | -122.3007 | -0.022888 | -121.8613 | -121.9208 | -121.7743 | 122.2229 | -0.068665 | -0.13275 | 122.374 | 122.2733 | 122.287 | 0.050354 | 0.064086 | -0.045776 | -0.032044 | -0.12817 | 0.39368 | 0.48065 | 0.33417 | 0.52643 | 0.37994 | 0.15106 | 0.004577 | 0.43945 | 122.2778 | 0.068664 | 122.374 | 122.2916 | 122.3282 | -0.13733 | -122.406 | 122.2275 | 122.2321 | 122.2275 | 121.6324
1787.6094 | 122.4747 | -122.2183 | 0.082397 | 0.028839 | -0.0010212 | -0.034577 | -4.906e-05 | -0.016985 | -0.027327 | -0.027519 | 0.011658 | -0.0082459 | 0.063976 | 0.046433 | -0.01559 | -0.0079638 | -0.015033 | 0.013733 | 0.027466 | -0.032043 | 0.054932 | 0.2243 | 0.086975 | 0.10986 | -0.54932 | 0.068665 | -122.2549 | 0.10071 | -121.7972 | -121.8475 | -121.6965 | 122.1863 | -0.054931 | -0.027465 | 122.4426 | 122.3282 | 122.3053 | 0.14191 | 0.11902 | -0.036621 | -0.013732 | 0.018311 | 0.42114 | 0.52185 | 0.37079 | 0.55847 | 0.40741 | 0.25635 | 0.086975 | 0.45776 | 122.3557 | 0.059509 | 122.3236 | 122.2458 | 122.287 | -0.11444 | -122.3373 | 122.2733 | 122.319 | 122.2321 | 121.669
1789.3906 | 122.3694 | -122.2824 | 0.09613 | 0.0059509 | -0.00273 | -0.036072 | -4.906e-05 | -0.015276 | -0.026686 | -0.020256 | 0.0055542 | -0.0056823 | 0.063976 | 0.041092 | -0.019435 | -0.009032 | -0.016314 | -0.036621 | 0.041199 | -0.045776 | -0.091553 | -0.013733 | -0.082397 | -0.045776 | -0.67291 | 0.068665 | -122.2961 | -0.018311 | -121.9208 | -121.9757 | -121.7789 | 122.2366 | -0.054931 | -0.18768 | 122.2687 | 122.2366 | 122.2 | 0 | -0.036621 | -0.013733 | -0.027465 | -0.11444 | 0.36163 | 0.50354 | 0.3067 | 0.51727 | 0.32044 | 0.032043 | -0.045777 | 0.37537 | 122.2778 | 0.086975 | 122.3648 | 122.3236 | 122.3511 | -0.14191 | -122.3923 | 122.1909 | 122.2641 | 122.2458 | 121.6095
1791.1094 | 122.4243 | -122.2641 | 0.086975 | 0.01358 | -0.0018756 | -0.034577 | 0.0018735 | -0.022539 | -0.027754 | -0.025169 | 0.0055542 | -0.0080321 | 0.064403 | 0.04686 | -0.01559 | -0.0081774 | -0.014605 | -0.068665 | 0.045776 | -0.064087 | -0.068665 | 0.059509 | -0.054932 | -0.018311 | -0.67749 | 0.073242 | -122.2961 | 0.013733 | -121.8704 | -121.9208 | -121.7422 | 122.2 | -0.041199 | -0.15564 | 122.3236 | 122.2458 | 122.2092 | 0.045776 | 0.009155 | -0.032044 | -0.013733 | -0.073242 | 0.39368 | 0.52185 | 0.34332 | 0.55389 | 0.37537 | 0.1236 | -0.004578 | 0.42572 | 122.3099 | 0.10986 | 122.3694 | 122.3099 | 122.3373 | -0.15106 | -122.3831 | 122.1954 | 122.2778 | 122.1954 | 121.5866
1792.875 | 122.4197 | -122.2504 | 0.10986 | 0.028839 | -0.0037982 | -0.0365 | -0.0017581 | -0.019121 | -0.029249 | -0.025596 | 0.011658 | -0.0080321 | 0.065899 | 0.03682 | -0.023708 | -0.0101 | -0.010547 | -0.045776 | 0.068665 | -0.068665 | -0.068665 | 0.073242 | -0.004578 | 0 | -0.60883 | 0.09613 | -122.3373 | -0.018311 | -121.843 | -121.9162 | -121.7377 | 122.1817 | -0.041198 | -0.17853 | 122.3236 | 122.2504 | 122.2458 | 0.068665 | 0.064087 | -0.086975 | -0.013733 | -0.12817 | 0.40741 | 0.51269 | 0.33417 | 0.59967 | 0.42114 | 0.14191 | 0 | 0.49438 | 122.319 | 0.13733 | 122.4335 | 122.319 | 122.3465 | -0.17853 | -122.4472 | 122.1817 | 122.2321 | 122.2046 | 121.6415
1794.6562 | 122.406 | -122.2595 | 0.10529 | 0.0059509 | -0.0018756 | -0.035645 | -0.0019717 | -0.016771 | -0.028395 | -0.020256 | 0.0025024 | -0.0067505 | 0.063762 | 0.03917 | -0.019222 | -0.009032 | -0.018664 | -0.009155 | 0.027466 | -0.045776 | -0.032043 | 0.10071 | 0.004578 | -0.004578 | -0.6134 | 0.073242 | -122.2733 | 0.009155 | -121.8796 | -121.9345 | -121.7743 | 122.2137 | -0.07782 | -0.13733 | 122.3602 | 122.2549 | 122.2641 | 0.041198 | 0.050354 | -0.013733 | -0.032044 | -0.096131 | 0.37994 | 0.48523 | 0.32501 | 0.49896 | 0.33874 | 0.14648 | 0.013733 | 0.39368 | 122.2824 | 0.073242 | 122.3465 | 122.287 | 122.3328 | -0.15106 | -122.3785 | 122.2275 | 122.2687 | 122.2504 | 121.6461
1796.4375 | 122.3877 | -122.2687 | 0.10986 | 0.028839 | -0.0042254 | -0.034791 | 0.00080534 | -0.016771 | -0.02989 | -0.023033 | 0.014709 | -0.0095275 | 0.065899 | 0.040024 | -0.023921 | -0.008391 | -0.013751 | -0.082397 | 0.068665 | -0.068665 | -0.073242 | 0.068665 | 0 | 0 | -0.65002 | 0.082397 | -122.319 | -0.022888 | -121.8796 | -121.9437 | -121.7651 | 122.2 | -0.041198 | -0.18311 | 122.3373 | 122.2687 | 122.2687 | 0.068665 | 0.068665 | -0.050354 | -0.027466 | -0.13275 | 0.3891 | 0.50354 | 0.32501 | 0.55389 | 0.37537 | 0.13733 | -0.004577 | 0.43945 | 122.2961 | 0.13733 | 122.4014 | 122.3373 | 122.3511 | -0.17853 | -122.4289 | 122.1954 | 122.2458 | 122.1863 | 121.6187
1798.2188 | 122.4701 | -122.2549 | 0.082397 | 0.02121 | -0.0037982 | -0.035218 | -0.0017581 | -0.021258 | -0.028822 | -0.021751 | 0.011658 | -0.0097411 | 0.063335 | 0.046219 | -0.019649 | -0.0071094 | -0.019305 | -0.036621 | 0.004578 | -0.027466 | -0.009155 | 0.13733 | 0.036621 | 0.059509 | -0.67749 | 0.041199 | -122.2687 | 0.041199 | -121.8292 | -121.8796 | -121.7194 | 122.2275 | -0.077819 | -0.091552 | 122.3923 | 122.3145 | 122.2916 | 0.086975 | 0.064087 | -0.013733 | -0.041198 | -0.041198 | 0.42572 | 0.53558 | 0.37537 | 0.54932 | 0.3891 | 0.16479 | 0.018311 | 0.43945 | 122.3099 | 0.032044 | 122.3099 | 122.2595 | 122.2961 | -0.10986 | -122.3511 | 122.2458 | 122.2961 | 122.2183 | 121.5775
1800 | 122.374 | -122.2549 | 0.10529 | 0.01358 | -0.0012348 | -0.035218 | -0.0017581 | -0.013567 | -0.027327 | -0.02346 | -0.00054937 | -0.0065369 | 0.065044 | 0.04387 | -0.020717 | -0.009032 | -0.018237 | -0.054932 | 0.045776 | -0.036621 | -0.082397 | 0.027466 | -0.054932 | -0.041199 | -0.72327 | 0.068665 | -122.3007 | -0.032043 | -121.9162 | -121.9894 | -121.788 | 122.2183 | -0.05951 | -0.18768 | 122.2824 | 122.2137 | 122.2 | -0.004578 | -0.018311 | -0.045776 | -0.036621 | -0.13733 | 0.33874 | 0.46692 | 0.2655 | 0.51269 | 0.31128 | 0.064087 | -0.045776 | 0.38452 | 122.2687 | 0.082397 | 122.3694 | 122.3007 | 122.3236 | -0.14191 | -122.406 | 122.1725 | 122.2229 | 122.2 | 121.5317
1801.7656 | 122.3969 | -122.2687 | 0.10071 | 0.0059509 | -0.0020892 | -0.035645 | 0.0012325 | -0.019121 | -0.029463 | -0.021324 | 0.0025024 | -0.0082459 | 0.063976 | 0.04921 | -0.017299 | -0.0101 | -0.017383 | -0.07782 | 0.064087 | -0.036621 | -0.082397 | 0.009155 | -0.064087 | -0.068665 | -0.71869 | 0.07782 | -122.3099 | -0.013733 | -121.9299 | -121.9757 | -121.7926 | 122.2321 | -0.036621 | -0.18311 | 122.2778 | 122.2 | 122.2046 | -0.032044 | -0.027466 | -0.041198 | -0.022888 | -0.11444 | 0.33875 | 0.47607 | 0.29297 | 0.51727 | 0.33417 | 0.045776 | -0.045776 | 0.37994 | 122.2961 | 0.10071 | 122.3877 | 122.3328 | 122.3465 | -0.13733 | -122.4106 | 122.1863 | 122.2549 | 122.1909 | 121.55
1803.5469 | 122.406 | -122.2778 | 0.11902 | 0.0059509 | -0.0037982 | -0.035431 | -0.0015445 | -0.02083 | -0.027967 | -0.023033 | 0.0055542 | -0.0088867 | 0.064403 | 0.038529 | -0.022426 | -0.010314 | -0.014605 | -0.10071 | 0.054932 | -0.054932 | -0.086975 | 0.068665 | -0.004578 | -0.013733 | -0.68665 | 0.091553 | -122.3419 | -0.041199 | -121.9025 | -121.9482 | -121.8063 | 122.2229 | -0.064087 | -0.20599 | 122.3465 | 122.2641 | 122.2733 | 0.041199 | 0.050354 | -0.064087 | -0.027466 | -0.16022 | 0.37537 | 0.4715 | 0.32959 | 0.53558 | 0.39368 | 0.1236 | -0.032043 | 0.43945 | 122.3007 | 0.10986 | 122.4335 | 122.3328 | 122.3694 | -0.17395 | -122.4609 | 122.1909 | 122.2366 | 122.1771 | 121.5912
1805.25 | 122.4884 | -122.2321 | 0.091553 | 0.044098 | -0.00273 | -0.035218 | -0.0011173 | -0.014635 | -0.02754 | -0.025383 | 0.011658 | -0.0073913 | 0.06483 | 0.04387 | -0.01794 | -0.0081774 | -0.01311 | -0.004578 | 0.009155 | -0.018311 | 0.032043 | 0.17853 | 0.064087 | 0.091553 | -0.62714 | 0.041199 | -122.319 | 0.064087 | -121.8201 | -121.8979 | -121.7331 | 122.2137 | -0.082398 | -0.05951 | 122.4106 | 122.3236 | 122.2961 | 0.10986 | 0.082398 | -0.086975 | -0.050354 | -0.027466 | 0.41199 | 0.49896 | 0.33417 | 0.58594 | 0.42114 | 0.19684 | 0.050354 | 0.49896 | 122.3831 | 0.027466 | 122.3602 | 122.2412 | 122.2733 | -0.10986 | -122.4106 | 122.2641 | 122.2961 | 122.2275 | 121.6049
1807.0312 | 122.4106 | -122.2778 | 0.12817 | 0.02121 | -0.0012348 | -0.036713 | 0.0010189 | -0.018267 | -0.027327 | -0.023887 | 0.008606 | -0.0082459 | 0.065258 | 0.040238 | -0.020717 | -0.010741 | -0.014819 | -0.054932 | 0.073242 | -0.068665 | -0.073242 | 0.073242 | 0.009155 | 0.013733 | -0.67291 | 0.091553 | -122.3282 | -0.032043 | -121.9025 | -121.962 | -121.7834 | 122.2092 | -0.054932 | -0.20142 | 122.3511 | 122.2916 | 122.287 | 0.082398 | 0.07782 | -0.050354 | -0.036621 | -0.16022 | 0.37537 | 0.49439 | 0.31586 | 0.54474 | 0.36621 | 0.14191 | -0.004577 | 0.42572 | 122.2961 | 0.14191 | 122.4197 | 122.3511 | 122.3694 | -0.19684 | -122.4564 | 122.2046 | 122.2458 | 122.2229 | 121.6049
1808.8125 | 122.3831 | -122.2778 | 0.091553 | 0.0059509 | -0.0040118 | -0.032868 | 0.00037814 | -0.017626 | -0.02754 | -0.024742 | 0.0055542 | -0.0076049 | 0.06483 | 0.042588 | -0.019008 | -0.0096728 | -0.014605 | -0.068665 | 0.050354 | -0.036621 | -0.091553 | 0.022888 | -0.073242 | -0.041199 | -0.76446 | 0.086975 | -122.3328 | -0.009155 | -121.9482 | -121.9894 | -121.7972 | 122.2412 | -0.041199 | -0.18311 | 122.3007 | 122.2366 | 122.2046 | -0.004578 | -0.036621 | -0.054932 | -0.004578 | -0.10071 | 0.32959 | 0.48065 | 0.28839 | 0.53558 | 0.34332 | 0.059509 | -0.054932 | 0.38452 | 122.3236 | 0.086975 | 122.4197 | 122.3282 | 122.3648 | -0.12817 | -122.4243 | 122.1863 | 122.2687 | 122.2092 | 121.5134
1810.5312 | 122.4289 | -122.287 | 0.1236 | 0.0059509 | -0.003371 | -0.037354 | 0.0016599 | -0.02318 | -0.028395 | -0.024101 | 0.0025024 | -0.0078185 | 0.065258 | 0.043015 | -0.018581 | -0.009032 | -0.016101 | -0.086975 | 0.050354 | -0.064087 | -0.09613 | 0.050354 | -0.045776 | -0.009155 | -0.70953 | 0.082397 | -122.3282 | 0.004578 | -121.9025 | -121.9757 | -121.7789 | 122.2229 | -0.073242 | -0.21973 | 122.3373 | 122.2778 | 122.2412 | 0.054932 | 0.018311 | -0.041199 | -0.041199 | -0.11902 | 0.38452 | 0.50812 | 0.31128 | 0.54932 | 0.35248 | 0.11444 | -0.032043 | 0.42572 | 122.3328 | 0.11444 | 122.4106 | 122.3373 | 122.3694 | -0.18768 | -122.4518 | 122.1909 | 122.2916 | 122.2 | 121.5775
1812.3125 | 122.374 | -122.2916 | 0.10529 | 0.01358 | -0.0020892 | -0.036713 | -0.00026266 | -0.016985 | -0.029249 | -0.027946 | 0.0055542 | -0.0088867 | 0.066326 | 0.044938 | -0.017085 | -0.0088184 | -0.016101 | -0.059509 | 0.064087 | -0.041199 | -0.10071 | 0.022888 | -0.059509 | -0.059509 | -0.75989 | 0.082397 | -122.3419 | -0.022888 | -121.9391 | -122.0078 | -121.7972 | 122.2504 | -0.041199 | -0.20599 | 122.3145 | 122.2321 | 122.2321 | -0.01831 | -0.01831 | -0.050354 | -0.022889 | -0.12817 | 0.35248 | 0.49439 | 0.28381 | 0.54474 | 0.33417 | 0.064087 | -0.059509 | 0.40283 | 122.319 | 0.10529 | 122.4243 | 122.3557 | 122.374 | -0.14649 | -122.4472 | 122.1909 | 122.2687 | 122.2321 | 121.5317
1814.0938 | 122.4014 | -122.3053 | 0.13275 | -0.0016786 | -0.003371 | -0.037781 | -0.0019717 | -0.020189 | -0.030104 | -0.022605 | -0.00054937 | -0.0095275 | 0.06483 | 0.040024 | -0.020076 | -0.009032 | -0.018878 | -0.064087 | 0.032043 | -0.041199 | -0.073242 | 0.07782 | -0.009155 | 0 | -0.70496 | 0.07782 | -122.2961 | -0.036621 | -121.8933 | -121.9528 | -121.8063 | 122.2641 | -0.10071 | -0.20599 | 122.3831 | 122.3053 | 122.2961 | 0.041199 | 0.032044 | 0.009155 | -0.054931 | -0.16937 | 0.41199 | 0.49896 | 0.35248 | 0.48981 | 0.34332 | 0.11902 | -0.032043 | 0.40283 | 122.2595 | 0.073242 | 122.374 | 122.3373 | 122.3831 | -0.17395 | -122.4289 | 122.2321 | 122.2687 | 122.2412 | 121.6003
1815.7969 | 122.4518 | -122.2687 | 0.10986 | 0.01358 | -0.0023028 | -0.036072 | 0.00080534 | -0.015276 | -0.028181 | -0.02111 | 0.020813 | -0.0091003 | 0.068035 | 0.038315 | -0.019435 | -0.0096728 | -0.015887 | -0.032043 | 0.054932 | -0.068665 | -0.045776 | 0.068665 | 0.018311 | 0.018311 | -0.66834 | 0.091553 | -122.2916 | 0.004578 | -121.875 | -121.9299 | -121.7697 | 122.2 | -0.054931 | -0.15564 | 122.3373 | 122.287 | 122.287 | 0.086976 | 0.086976 | -0.022888 | -0.01831 | -0.10529 | 0.39368 | 0.49896 | 0.33875 | 0.52185 | 0.36163 | 0.13733 | 0.022889 | 0.41657 | 122.2961 | 0.1236 | 122.3831 | 122.3236 | 122.3602 | -0.17853 | -122.4014 | 122.2229 | 122.2733 | 122.2366 | 121.6003
1817.5781 | 122.4609 | -122.2641 | 0.10529 | 0.02121 | -0.0020892 | -0.034791 | 0.00059174 | -0.018694 | -0.030104 | -0.023033 | 0.008606 | -0.0061095 | 0.065258 | 0.042161 | -0.021358 | -0.009032 | -0.016955 | -0.009155 | 0.050354 | -0.041199 | -0.022888 | 0.10071 | 0.032043 | 0.032043 | -0.64087 | 0.07782 | -122.3328 | 0.041199 | -121.8521 | -121.9116 | -121.7514 | 122.2229 | -0.054932 | -0.12817 | 122.3648 | 122.2961 | 122.2961 | 0.073242 | 0.073242 | -0.068665 | -0.027466 | -0.064087 | 0.41199 | 0.5127 | 0.35248 | 0.58136 | 0.42114 | 0.14191 | 0.018311 | 0.48065 | 122.374 | 0.091553 | 122.4106 | 122.3145 | 122.3419 | -0.14649 | -122.4381 | 122.2412 | 122.3053 | 122.2549 | 121.6232
1819.3594 | 122.493 | -122.2412 | 0.09613 | 0.01358 | -0.0035846 | -0.03714 | -0.0011173 | -0.021044 | -0.028395 | -0.023887 | 0.0055542 | -0.0099549 | 0.063976 | 0.044724 | -0.015804 | -0.0071094 | -0.016101 | -0.041199 | 0.013733 | -0.036621 | -0.009155 | 0.12817 | 0.036621 | 0.045776 | -0.72784 | 0.041199 | -122.3053 | 0.054932 | -121.8246 | -121.907 | -121.7285 | 122.2046 | -0.082397 | -0.10528 | 122.3694 | 122.287 | 122.2778 | 0.082397 | 0.073242 | -0.064087 | -0.054931 | -0.041198 | 0.41657 | 0.5127 | 0.33417 | 0.57678 | 0.39825 | 0.1648 | 0.027466 | 0.48065 | 122.3602 | 0.050354 | 122.3465 | 122.2549 | 122.2824 | -0.13275 | -122.4014 | 122.2321 | 122.2961 | 122.2 | 121.5134
1821.1406 | 122.406 | -122.2961 | 0.13733 | 0.0059509 | -0.0018756 | -0.033509 | 0.0012325 | -0.013781 | -0.027113 | -0.022178 | 0.0055542 | -0.0071777 | 0.067394 | 0.042588 | -0.020931 | -0.0088184 | -0.018023 | -0.054932 | 0.050354 | -0.045776 | -0.091553 | 0.018311 | -0.059509 | -0.045776 | -0.78278 | 0.07782 | -122.319 | -0.045776 | -121.9482 | -122.0169 | -121.8063 | 122.2504 | -0.086975 | -0.22888 | 122.3145 | 122.2504 | 122.2366 | 0 | -0.013733 | -0.022888 | -0.059509 | -0.18311 | 0.3479 | 0.48981 | 0.27924 | 0.5127 | 0.30212 | 0.064087 | -0.045777 | 0.37079 | 122.2733 | 0.09613 | 122.3969 | 122.3465 | 122.374 | -0.18311 | -122.4564 | 122.2046 | 122.2504 | 122.2412 | 121.5134
1822.8594 | 122.5342 | -122.2778 | 0.068665 | 0.01358 | -0.0037982 | -0.036072 | -0.0034671 | -0.02083 | -0.029676 | -0.02346 | 0.0055542 | -0.0093139 | 0.065258 | 0.047928 | -0.019222 | -0.0096728 | -0.018878 | -0.036621 | 0.004578 | -0.032043 | 0.004578 | 0.15106 | 0.054932 | 0.054932 | -0.70496 | 0.045776 | -122.3007 | 0.073242 | -121.7926 | -121.8567 | -121.7056 | 122.2458 | -0.064087 | -0.064087 | 122.4289 | 122.3328 | 122.3328 | 0.086975 | 0.086975 | -0.022888 | -0.022889 | 0.004577 | 0.48523 | 0.5722 | 0.42114 | 0.59509 | 0.44403 | 0.18311 | 0.036621 | 0.50812 | 122.374 | 0.036621 | 122.3465 | 122.2824 | 122.3236 | -0.10071 | -122.3694 | 122.2824 | 122.3511 | 122.2412 | 121.5729
1824.6406 | 122.3831 | -122.2916 | 0.10986 | 0.0059509 | -0.00059378 | -0.035004 | -0.00090366 | -0.019976 | -0.026472 | -0.022605 | -0.003601 | -0.0076049 | 0.066112 | 0.045792 | -0.018367 | -0.010741 | -0.016955 | -0.059509 | 0.041199 | -0.032043 | -0.086975 | 0.045776 | -0.045776 | -0.059509 | -0.7782 | 0.082397 | -122.3328 | -0.027466 | -121.9437 | -122.0215 | -121.8109 | 122.2595 | -0.068664 | -0.19684 | 122.3373 | 122.2321 | 122.2458 | -0.027466 | -0.013733 | -0.041199 | -0.027466 | -0.13733 | 0.3479 | 0.48065 | 0.27008 | 0.52185 | 0.31128 | 0.077819 | -0.054932 | 0.3891 | 122.3053 | 0.073242 | 122.4152 | 122.3328 | 122.374 | -0.14191 | -122.4426 | 122.2046 | 122.2641 | 122.2321 | 121.5134
1826.4219 | 122.4197 | -122.287 | 0.10529 | 0.0059509 | -0.0018756 | -0.036286 | 0.00037814 | -0.015703 | -0.029463 | -0.022605 | 0.0055542 | -0.0063233 | 0.065258 | 0.037675 | -0.018794 | -0.0081774 | -0.014605 | -0.032043 | 0.022888 | -0.041199 | -0.073242 | 0.064087 | -0.045776 | -0.027466 | -0.75989 | 0.068665 | -122.3373 | -0.018311 | -121.9299 | -122.0078 | -121.8155 | 122.2458 | -0.082398 | -0.17853 | 122.3511 | 122.2595 | 122.2412 | 0.013733 | -0.004577 | -0.050354 | -0.036621 | -0.1236 | 0.35706 | 0.4715 | 0.27924 | 0.52185 | 0.32959 | 0.10529 | -0.032043 | 0.40741 | 122.319 | 0.064087 | 122.406 | 122.3099 | 122.3557 | -0.14649 | -122.4426 | 122.2137 | 122.2687 | 122.2549 | 121.5271
1828.2031 | 122.4243 | -122.2961 | 0.09613 | 0.01358 | -0.0042254 | -0.037781 | -0.00026266 | -0.015062 | -0.029463 | -0.020897 | 0.014709 | -0.0078185 | 0.063762 | 0.04451 | -0.021572 | -0.011809 | -0.014819 | -0.091553 | 0.036621 | -0.036621 | -0.086975 | 0.059509 | -0.004578 | -0.004578 | -0.74616 | 0.10071 | -122.3648 | -0.050354 | -121.9208 | -121.9757 | -121.8018 | 122.2595 | -0.059509 | -0.1831 | 122.3557 | 122.2916 | 122.2916 | 0.032043 | 0.032043 | -0.068664 | 0.004578 | -0.14648 | 0.37537 | 0.49438 | 0.32044 | 0.56305 | 0.3891 | 0.09613 | -0.050354 | 0.44403 | 122.3145 | 0.073242 | 122.4655 | 122.3328 | 122.3969 | -0.13275 | -122.4609 | 122.2092 | 122.2458 | 122.2046 | 121.55
1830 | 122.4289 | -122.2961 | 0.11902 | 0.0059509 | -0.00273 | -0.037995 | -0.0017581 | -0.016771 | -0.030317 | -0.023674 | 0.020813 | -0.0078185 | 0.064403 | 0.042374 | -0.021144 | -0.010314 | -0.016742 | -0.086975 | 0.045776 | -0.050354 | -0.073242 | 0.068665 | 0.013733 | 0.013733 | -0.75531 | 0.10071 | -122.3648 | -0.041199 | -121.9254 | -121.9803 | -121.8109 | 122.2458 | -0.073243 | -0.19226 | 122.3648 | 122.3099 | 122.3099 | 0.064087 | 0.064087 | -0.068664 | -0.018311 | -0.16022 | 0.37079 | 0.48523 | 0.31586 | 0.55389 | 0.38452 | 0.11902 | -0.022888 | 0.43945 | 122.3236 | 0.09613 | 122.4655 | 122.3419 | 122.3969 | -0.16937 | -122.4838 | 122.2229 | 122.2549 | 122.2092 | 121.5408
1831.7812 | 122.4609 | -122.2733 | 0.10529 | 0.01358 | -0.0025164 | -0.034791 | 0.00016454 | -0.012713 | -0.02754 | -0.024955 | 0.0055542 | -0.0071777 | 0.067394 | 0.040665 | -0.02029 | -0.010314 | -0.016101 | -0.013733 | 0.045776 | -0.068665 | -0.027466 | 0.10986 | 0.032043 | 0.013733 | -0.67749 | 0.091553 | -122.3236 | 0.022888 | -121.8613 | -121.9345 | -121.756 | 122.2046 | -0.05951 | -0.13275 | 122.3831 | 122.287 | 122.3053 | 0.082398 | 0.10071 | -0.050354 | -0.013733 | -0.082398 | 0.41199 | 0.51727 | 0.33874 | 0.56763 | 0.3891 | 0.17853 | 0.041199 | 0.46234 | 122.3465 | 0.11444 | 122.4152 | 122.319 | 122.3648 | -0.17395 | -122.4289 | 122.2458 | 122.2961 | 122.2595 | 121.5958
1833.5625 | 122.5342 | -122.2321 | 0.068665 | 0.036468 | -0.003371 | -0.034577 | -0.0028263 | -0.018908 | -0.028608 | -0.020042 | 0.011658 | -0.0082459 | 0.066539 | 0.050065 | -0.017726 | -0.009032 | -0.015246 | 0.018311 | 0 | -0.009155 | 0.059509 | 0.20142 | 0.073242 | 0.09613 | -0.70953 | 0.045776 | -122.3053 | 0.07782 | -121.8384 | -121.8842 | -121.7514 | 122.2229 | -0.068665 | -0.009156 | 122.4335 | 122.3282 | 122.3053 | 0.10528 | 0.082397 | -0.073242 | -0.022889 | 0.009155 | 0.39368 | 0.48065 | 0.3479 | 0.55389 | 0.42114 | 0.21057 | 0.068664 | 0.46692 | 122.3831 | 0.009155 | 122.3511 | 122.2321 | 122.2778 | -0.07782 | -122.374 | 122.2916 | 122.3099 | 122.2504 | 121.5225
1835.3438 | 122.4518 | -122.2824 | 0.10986 | 0.0059509 | -0.0023028 | -0.035431 | 0.0020871 | -0.015703 | -0.029676 | -0.021324 | 0.0025024 | -0.0065369 | 0.063976 | 0.042588 | -0.018794 | -0.0077502 | -0.0208 | -0.009155 | 0.036621 | -0.050354 | -0.022888 | 0.10986 | 0.027466 | 0.013733 | -0.70953 | 0.064087 | -122.3602 | 0.022888 | -121.875 | -121.9666 | -121.7697 | 122.2321 | -0.073242 | -0.13275 | 122.3923 | 122.2961 | 122.3099 | 0.064087 | 0.07782 | -0.077819 | -0.045776 | -0.086975 | 0.40741 | 0.5127 | 0.31586 | 0.59052 | 0.39368 | 0.16022 | 0.027466 | 0.48523 | 122.3831 | 0.086975 | 122.4243 | 122.319 | 122.3465 | -0.16022 | -122.4701 | 122.2595 | 122.3053 | 122.2733 | 121.5729
1837.0625 | 122.438 | -122.2824 | 0.10529 | 0.0059509 | -0.0055072 | -0.035218 | -0.0015445 | -0.021898 | -0.029036 | -0.022605 | -0.00054937 | -0.0084595 | 0.066112 | 0.040452 | -0.020931 | -0.0094592 | -0.015887 | -0.041199 | 0.022888 | -0.054932 | -0.059509 | 0.086975 | 0.018311 | 0.022888 | -0.79193 | 0.073242 | -122.3419 | -0.032043 | -121.9162 | -121.9666 | -121.8292 | 122.2275 | -0.082398 | -0.16479 | 122.3694 | 122.3053 | 122.3007 | 0.07782 | 0.073243 | -0.059509 | -0.032044 | -0.13733 | 0.36621 | 0.45319 | 0.31586 | 0.5127 | 0.37537 | 0.14191 | -0.004577 | 0.42572 | 122.3099 | 0.07782 | 122.4152 | 122.3053 | 122.3557 | -0.16022 | -122.4472 | 122.2229 | 122.2504 | 122.2412 | 121.4905
1838.8594 | 122.5479 | -122.2687 | 0.086975 | 0.0059509 | -0.0029438 | -0.033295 | -0.00047626 | -0.01848 | -0.027327 | -0.022819 | -0.00054937 | -0.0086731 | 0.065258 | 0.050919 | -0.016658 | -0.0077502 | -0.016101 | -0.068665 | 0.041199 | -0.022888 | -0.018311 | 0.10071 | 0 | 0.036621 | -0.76446 | 0.050354 | -122.3099 | 0.082397 | -121.8475 | -121.8887 | -121.7285 | 122.2458 | -0.045776 | -0.10529 | 122.3694 | 122.3053 | 122.2687 | 0.059509 | 0.022888 | -0.041198 | -0.036621 | -0.004578 | 0.42114 | 0.54016 | 0.37994 | 0.58136 | 0.42114 | 0.1236 | 0.004577 | 0.46234 | 122.3923 | 0.064087 | 122.3602 | 122.3099 | 122.319 | -0.10986 | -122.3969 | 122.2504 | 122.3511 | 122.2 | 121.5042
1840.6406 | 122.4884 | -122.3053 | 0.10986 | 0.02121 | -0.004439 | -0.034363 | -0.0011173 | -0.016985 | -0.028608 | -0.022819 | 0.008606 | -0.0086731 | 0.063121 | 0.045151 | -0.019222 | -0.0096728 | -0.01781 | -0.009155 | 0.054932 | -0.054932 | -0.027466 | 0.11902 | 0.022888 | 0.027466 | -0.72784 | 0.082397 | -122.3465 | 0.041199 | -121.8704 | -121.9437 | -121.7697 | 122.2504 | -0.054931 | -0.13733 | 122.4243 | 122.3328 | 122.3282 | 0.082398 | 0.07782 | -0.041199 | -0.027466 | -0.068664 | 0.43488 | 0.53558 | 0.36163 | 0.57678 | 0.40283 | 0.17395 | 0.027466 | 0.47607 | 122.3877 | 0.10986 | 122.4289 | 122.3602 | 122.3877 | -0.16479 | -122.4564 | 122.2778 | 122.3465 | 122.2961 | 121.5775
1842.4219 | 122.5616 | -122.2733 | 0.086975 | 0.02121 | -0.0042254 | -0.035859 | -0.00047626 | -0.015703 | -0.02754 | -0.022605 | 0.0025024 | -0.011237 | 0.065044 | 0.041947 | -0.018154 | -0.0086048 | -0.016101 | -0.041199 | 0.013733 | -0.022888 | -0.013733 | 0.13275 | 0.050354 | 0.064087 | -0.81024 | 0.036621 | -122.3145 | 0.059509 | -121.8384 | -121.8842 | -121.7331 | 122.2504 | -0.073242 | -0.10071 | 122.406 | 122.3373 | 122.3236 | 0.086975 | 0.073242 | -0.041199 | -0.050354 | -0.027466 | 0.43487 | 0.54016 | 0.3891 | 0.58136 | 0.4303 | 0.15564 | 0.009155 | 0.47607 | 122.374 | 0.036621 | 122.3511 | 122.287 | 122.3099 | -0.10986 | -122.4014 | 122.2595 | 122.3328 | 122.2321 | 121.463
1844.1406 | 122.5296 | -122.2824 | 0.10071 | 0.0059509 | -0.0031574 | -0.0365 | -0.0028263 | -0.017412 | -0.030531 | -0.023033 | 0.008606 | -0.011237 | 0.063976 | 0.044083 | -0.018581 | -0.0086048 | -0.014392 | -0.036621 | 0.022888 | -0.009155 | -0.022888 | 0.13275 | 0.041199 | 0.050354 | -0.82398 | 0.054932 | -122.3282 | 0.050354 | -121.8613 | -121.907 | -121.7606 | 122.2733 | -0.07782 | -0.1236 | 122.4152 | 122.3328 | 122.3236 | 0.059509 | 0.050354 | -0.045776 | -0.045776 | -0.050354 | 0.42114 | 0.52185 | 0.37537 | 0.56763 | 0.42114 | 0.14191 | -0.013733 | 0.46692 | 122.3785 | 0.032043 | 122.3831 | 122.3053 | 122.3373 | -0.10986 | -122.4289 | 122.2595 | 122.3328 | 122.2458 | 121.4584
1845.9062 | 122.5708 | -122.2641 | 0.091553 | 0.01358 | -0.0040118 | -0.035004 | -0.00026266 | -0.022753 | -0.028822 | -0.023033 | 0.0025024 | -0.0091003 | 0.063121 | 0.046006 | -0.021144 | -0.010741 | -0.015033 | 0.004578 | -0.004578 | 0 | 0.073242 | 0.21515 | 0.10986 | 0.10986 | -0.70953 | 0.027466 | -122.319 | 0.091553 | -121.788 | -121.8521 | -121.7194 | 122.2641 | -0.096131 | -0.018311 | 122.4792 | 122.374 | 122.374 | 0.10986 | 0.10986 | -0.054932 | -0.064087 | 0 | 0.47607 | 0.54474 | 0.41199 | 0.59967 | 0.46692 | 0.21515 | 0.073242 | 0.53101 | 122.4106 | -0.004578 | 122.3465 | 122.2595 | 122.2916 | -0.091553 | -122.4106 | 122.3373 | 122.3557 | 122.2687 | 121.5546
1847.6875 | 122.5616 | -122.2733 | 0.054932 | 0.01358 | -0.00273 | -0.035859 | 0.0023007 | -0.017412 | -0.029249 | -0.024101 | 0.0025024 | -0.0073913 | 0.06483 | 0.045365 | -0.015377 | -0.0077502 | -0.016101 | -0.027466 | 0.004578 | -0.036621 | 0.004578 | 0.15106 | 0.041199 | 0.050354 | -0.78735 | 0.032043 | -122.3099 | 0.11444 | -121.8292 | -121.8933 | -121.7194 | 122.2366 | -0.050354 | -0.050354 | 122.4243 | 122.3236 | 122.3145 | 0.086975 | 0.07782 | -0.036621 | -0.022889 | 0.059509 | 0.44403 | 0.55389 | 0.37994 | 0.59052 | 0.41656 | 0.18768 | 0.041199 | 0.48065 | 122.4243 | 0.041199 | 122.3419 | 122.2778 | 122.3053 | -0.091553 | -122.3648 | 122.2778 | 122.3877 | 122.2458 | 121.4859
1849.3906 | 122.5067 | -122.2778 | 0.09613 | 0.0059509 | -0.0035846 | -0.035645 | -0.0028263 | -0.019335 | -0.02989 | -0.020469 | -0.003601 | -0.0088867 | 0.065471 | 0.041092 | -0.021785 | -0.0098864 | -0.011401 | 0 | 0.022888 | 0.013733 | 0.032043 | 0.18768 | 0.086975 | 0.082397 | -0.75989 | 0.050354 | -122.3511 | 0.032043 | -121.8521 | -121.9116 | -121.7651 | 122.2916 | -0.073242 | -0.064087 | 122.4655 | 122.3602 | 122.3648 | 0.068664 | 0.073242 | -0.073242 | -0.045776 | -0.064087 | 0.42572 | 0.5127 | 0.36621 | 0.58594 | 0.43945 | 0.17395 | 0.01831 | 0.49896 | 122.3831 | 0.009155 | 122.4014 | 122.3007 | 122.3282 | -0.082397 | -122.4472 | 122.3099 | 122.3099 | 122.2778 | 121.5179
1851.1875 | 122.4426 | -122.3236 | 0.11902 | 0.01358 | -0.0046526 | -0.037995 | 0.0010189 | -0.020403 | -0.029676 | -0.024314 | 0.011658 | -0.0061095 | 0.063976 | 0.039384 | -0.021144 | -0.0101 | -0.01546 | -0.09613 | 0.032043 | -0.059509 | -0.086975 | 0.050354 | 0 | 0.018311 | -0.85602 | 0.10986 | -122.3877 | -0.036621 | -121.9482 | -121.9894 | -121.8246 | 122.2641 | -0.086976 | -0.20599 | 122.374 | 122.3419 | 122.3236 | 0.07782 | 0.059509 | -0.064087 | -0.009156 | -0.15564 | 0.37537 | 0.49896 | 0.33417 | 0.56305 | 0.39825 | 0.10986 | -0.027466 | 0.43945 | 122.3511 | 0.091552 | 122.4976 | 122.3557 | 122.4335 | -0.17853 | -122.5067 | 122.2366 | 122.287 | 122.2275 | 121.4676
1852.9688 | 122.5159 | -122.2961 | 0.07782 | 0.01358 | -0.0048664 | -0.0365 | -0.0013309 | -0.020189 | -0.027967 | -0.024101 | 0.011658 | -0.0093139 | 0.063549 | 0.050278 | -0.01794 | -0.0086048 | -0.021228 | -0.036621 | 0.009155 | -0.009155 | 0 | 0.13733 | 0.032043 | 0.041199 | -0.86517 | 0.054932 | -122.3419 | 0.036621 | -121.875 | -121.9345 | -121.7789 | 122.287 | -0.068665 | -0.07782 | 122.4335 | 122.3373 | 122.3282 | 0.050354 | 0.041198 | -0.045776 | -0.022888 | -0.041199 | 0.42114 | 0.51727 | 0.36163 | 0.56305 | 0.40741 | 0.14648 | 0.009155 | 0.46692 | 122.3785 | 0.01831 | 122.3969 | 122.3053 | 122.3511 | -0.086975 | -122.4197 | 122.2961 | 122.3328 | 122.2595 | 121.431
1854.75 | 122.5891 | -122.2916 | 0.07782 | -0.0016786 | -0.0048664 | -0.034791 | -0.0011173 | -0.019335 | -0.028608 | -0.023674 | 0.008606 | -0.0099549 | 0.063762 | 0.045365 | -0.018794 | -0.0098864 | -0.018023 | 0.004578 | -0.004578 | 0 | 0.073242 | 0.23804 | 0.11444 | 0.11902 | -0.72784 | 0.018311 | -122.3099 | 0.10986 | -121.7743 | -121.8292 | -121.7056 | 122.2916 | -0.082398 | -0.004578 | 122.5296 | 122.4106 | 122.406 | 0.11902 | 0.11444 | -0.01831 | -0.059509 | 0.032043 | 0.51727 | 0.58594 | 0.46234 | 0.60425 | 0.48065 | 0.23804 | 0.073242 | 0.53558 | 122.4197 | -0.004578 | 122.3282 | 122.287 | 122.3099 | -0.07782 | -122.3877 | 122.3648 | 122.4014 | 122.2961 | 121.5637
1856.4688 | 122.5662 | -122.2595 | 0.082397 | 0.0059509 | -0.0040118 | -0.035004 | 0.0014463 | -0.015917 | -0.028181 | -0.025383 | 0.0025024 | -0.0063233 | 0.063762 | 0.048997 | -0.015377 | -0.0075366 | -0.015887 | -0.032043 | 0.032043 | -0.032043 | 0.009155 | 0.12817 | 0.022888 | 0.036621 | -0.81024 | 0.050354 | -122.3007 | 0.086975 | -121.8292 | -121.9025 | -121.7194 | 122.2275 | -0.050354 | -0.073242 | 122.3877 | 122.2961 | 122.2824 | 0.068664 | 0.054931 | -0.041199 | -0.032043 | 0.004578 | 0.4303 | 0.54016 | 0.35706 | 0.58136 | 0.39825 | 0.16022 | 0.041198 | 0.4715 | 122.3877 | 0.064086 | 122.3511 | 122.2916 | 122.3099 | -0.11444 | -122.3831 | 122.2687 | 122.3465 | 122.2275 | 121.4493
1858.25 | 122.4518 | -122.3373 | 0.10529 | 0.0059509 | -0.0023028 | -0.035431 | -0.00026266 | -0.018267 | -0.030104 | -0.02111 | 0.020813 | -0.0058959 | 0.064403 | 0.038315 | -0.023067 | -0.0096728 | -0.014178 | -0.091553 | 0.045776 | -0.050354 | -0.064087 | 0.068665 | -0.009155 | -0.004578 | -0.87433 | 0.091553 | -122.3785 | -0.032043 | -121.9574 | -121.994 | -121.8338 | 122.287 | -0.05951 | -0.16937 | 122.406 | 122.3328 | 122.3282 | 0.045776 | 0.041199 | -0.041199 | -0.013733 | -0.13733 | 0.37994 | 0.50354 | 0.34332 | 0.54474 | 0.38452 | 0.11902 | -0.013733 | 0.42114 | 122.3465 | 0.09613 | 122.4701 | 122.3831 | 122.4289 | -0.15564 | -122.4838 | 122.2733 | 122.3053 | 122.2458 | 121.463
1860.0469 | 122.5754 | -122.287 | 0.068665 | 0.01358 | -0.0052936 | -0.035004 | 0.00059174 | -0.018267 | -0.027967 | -0.024101 | 0.0025024 | -0.0088867 | 0.063762 | 0.047928 | -0.015163 | -0.008391 | -0.016314 | -0.054932 | 0.027466 | -0.018311 | -0.009155 | 0.13275 | 0.013733 | 0.032043 | -0.84686 | 0.032043 | -122.3007 | 0.10986 | -121.8292 | -121.8979 | -121.7239 | 122.2687 | -0.041199 | -0.07782 | 122.4197 | 122.319 | 122.3007 | 0.050354 | 0.032044 | -0.013733 | -0.036622 | 0.041198 | 0.45776 | 0.56305 | 0.3891 | 0.57678 | 0.40283 | 0.15106 | 0.009156 | 0.4715 | 122.4106 | 0.045777 | 122.3328 | 122.3145 | 122.319 | -0.086976 | -122.3694 | 122.2778 | 122.3969 | 122.2321 | 121.4401
1861.7656 | 122.5388 | -122.2961 | 0.054932 | 0.02121 | -0.00273 | -0.032654 | -0.00026266 | -0.020189 | -0.027967 | -0.022605 | 0.014709 | -0.0097411 | 0.06184 | 0.049424 | -0.015804 | -0.0077502 | -0.017383 | 0.009155 | 0.009155 | 0 | 0.073242 | 0.20599 | 0.07782 | 0.086975 | -0.82855 | 0.054932 | -122.319 | 0.09613 | -121.8475 | -121.907 | -121.7514 | 122.2961 | -0.045777 | 0.01831 | 122.5021 | 122.3831 | 122.374 | 0.086975 | 0.07782 | -0.022888 | 0 | 0.041198 | 0.44861 | 0.54474 | 0.3891 | 0.56763 | 0.41199 | 0.20599 | 0.073242 | 0.4715 | 122.4152 | 0.009155 | 122.374 | 122.3053 | 122.3511 | -0.054932 | -122.374 | 122.3694 | 122.3923 | 122.3053 | 121.4676
1863.5469 | 122.58 | -122.2916 | 0.068665 | 0.01358 | 4.7022e-05 | -0.033722 | -0.00026266 | -0.018053 | -0.026899 | -0.023033 | 0.0025024 | -0.0088867 | 0.066539 | 0.050065 | -0.016017 | -0.0077502 | -0.015674 | 0.022888 | 0 | 0.004578 | 0.050354 | 0.17395 | 0.068665 | 0.073242 | -0.8194 | 0.050354 | -122.3557 | 0.12817 | -121.8292 | -121.8796 | -121.7239 | 122.2961 | -0.068665 | -0.018311 | 122.4655 | 122.3648 | 122.3602 | 0.068664 | 0.064087 | -0.064087 | -0.018311 | 0.059509 | 0.46234 | 0.56763 | 0.41199 | 0.63171 | 0.47607 | 0.16937 | 0.045776 | 0.52643 | 122.4838 | -0.004578 | 122.406 | 122.2916 | 122.3419 | -0.064087 | -122.4243 | 122.3419 | 122.4197 | 122.3145 | 121.4722
1865.3438 | 122.5754 | -122.3007 | 0.068665 | 0.01358 | -0.0014484 | -0.035004 | -0.00047626 | -0.01549 | -0.026899 | -0.020469 | 0.017761 | -0.0058959 | 0.066539 | 0.058396 | -0.016231 | -0.007323 | -0.01781 | 0.018311 | -0.013733 | 0.009155 | 0.073242 | 0.21973 | 0.082397 | 0.09613 | -0.84686 | 0.054932 | -122.3099 | 0.11444 | -121.8109 | -121.8887 | -121.7194 | 122.3099 | -0.082398 | 0.004577 | 122.5204 | 122.3969 | 122.3831 | 0.086975 | 0.073242 | -0.009155 | -0.013733 | 0.045776 | 0.48981 | 0.58136 | 0.41199 | 0.59052 | 0.42114 | 0.21057 | 0.064087 | 0.49896 | 122.4243 | -0.022888 | 122.3648 | 122.287 | 122.3557 | -0.05951 | -122.3785 | 122.374 | 122.4152 | 122.319 | 121.4539
1867.0625 | 122.4976 | -122.3282 | 0.10986 | 0.044098 | -0.0023028 | -0.035859 | 0.0012325 | -0.019549 | -0.029676 | -0.023674 | 0.008606 | -0.0065369 | 0.06718 | 0.042374 | -0.022212 | -0.010527 | -0.018023 | -0.050354 | 0.082397 | -0.059509 | -0.050354 | 0.064087 | 0.018311 | 0.013733 | -0.9201 | 0.10071 | -122.3831 | -0.004578 | -121.9116 | -121.962 | -121.7972 | 122.2687 | -0.027466 | -0.16022 | 122.3923 | 122.3419 | 122.3465 | 0.073242 | 0.07782 | -0.054932 | -0.009155 | -0.11444 | 0.41657 | 0.53101 | 0.36621 | 0.58594 | 0.42114 | 0.1236 | 0.009155 | 0.4715 | 122.3785 | 0.14191 | 122.4838 | 122.4106 | 122.4289 | -0.16937 | -122.493 | 122.2778 | 122.3236 | 122.2778 | 121.4081
1868.8438 | 122.4243 | -122.3328 | 0.086975 | -0.0016786 | -0.001662 | -0.032227 | 0.0018735 | -0.019335 | -0.026045 | -0.02346 | -0.00054937 | -0.0061095 | 0.06718 | 0.03917 | -0.019649 | -0.0077502 | -0.015033 | -0.059509 | 0.054932 | -0.068665 | -0.07782 | 0.013733 | -0.059509 | -0.054932 | -1.0254 | 0.054932 | -122.3557 | -0.027466 | -121.994 | -122.0627 | -121.8567 | 122.2641 | -0.032043 | -0.16479 | 122.3465 | 122.2778 | 122.2733 | 0.013733 | 0.009156 | -0.022888 | -0.032043 | -0.11444 | 0.33875 | 0.47607 | 0.27008 | 0.49896 | 0.29297 | 0.082398 | -0.009155 | 0.36163 | 122.3282 | 0.1236 | 122.4106 | 122.3877 | 122.3877 | -0.15564 | -122.4426 | 122.2549 | 122.3053 | 122.2733 | 121.3074
1870.625 | 122.5296 | -122.3007 | 0.086975 | 0.0059509 | -0.0020892 | -0.035645 | -0.0021853 | -0.016985 | -0.028181 | -0.02111 | 0.011658 | -0.0086731 | 0.065899 | 0.04451 | -0.019435 | -0.010314 | -0.016955 | -0.041199 | 0.022888 | -0.004578 | -0.013733 | 0.1236 | 0.036621 | 0.032043 | -0.99792 | 0.041199 | -122.3328 | 0.054932 | -121.8658 | -121.9437 | -121.7789 | 122.2961 | -0.064087 | -0.10071 | 122.4243 | 122.3328 | 122.3373 | 0.036621 | 0.041199 | -0.032044 | -0.045776 | -0.032043 | 0.43488 | 0.52185 | 0.35706 | 0.55389 | 0.3891 | 0.12817 | -0.009155 | 0.46692 | 122.3877 | 0.027466 | 122.374 | 122.3236 | 122.3419 | -0.091553 | -122.4197 | 122.287 | 122.3557 | 122.2595 | 121.3028
1872.3906 | 122.5937 | -122.2504 | 0.064087 | 0.02121 | -0.0063616 | -0.035218 | -0.0017581 | -0.02083 | -0.029463 | -0.020469 | 0.0055542 | -0.0088867 | 0.064403 | 0.046647 | -0.019435 | -0.0094592 | -0.016314 | -0.013733 | 0 | -0.013733 | 0.050354 | 0.20142 | 0.086975 | 0.10071 | -0.90637 | 0.036621 | -122.3282 | 0.091553 | -121.8063 | -121.8613 | -121.7194 | 122.2366 | -0.064087 | -0.013733 | 122.4518 | 122.3511 | 122.3373 | 0.11444 | 0.10071 | -0.07782 | -0.027466 | 0.027466 | 0.44403 | 0.53101 | 0.3891 | 0.60883 | 0.46692 | 0.21515 | 0.064087 | 0.52185 | 122.4197 | 0.013733 | 122.3648 | 122.2504 | 122.287 | -0.07782 | -122.3923 | 122.3007 | 122.3419 | 122.2366 | 121.344
1874.1719 | 122.5296 | -122.287 | 0.068665 | 0.028839 | -0.00273 | -0.035431 | -0.00090366 | -0.018267 | -0.024977 | -0.020469 | 0.011658 | -0.0082459 | 0.063335 | 0.04686 | -0.017299 | -0.0068958 | -0.016314 | -0.027466 | 0.013733 | -0.004578 | 0.027466 | 0.16937 | 0.059509 | 0.054932 | -0.97961 | 0.054932 | -122.3694 | 0.045776 | -121.8842 | -121.9482 | -121.7834 | 122.2824 | -0.054932 | -0.041199 | 122.4564 | 122.3419 | 122.3465 | 0.05951 | 0.064087 | -0.082398 | -0.013733 | -0.022889 | 0.40283 | 0.50354 | 0.33875 | 0.58594 | 0.42114 | 0.17395 | 0.032044 | 0.48523 | 122.4152 | 0.018311 | 122.4243 | 122.3007 | 122.3419 | -0.073243 | -122.438 | 122.3145 | 122.3328 | 122.2595 | 121.3074
1875.8906 | 122.6028 | -122.2916 | 0.082397 | 0.02121 | -0.006148 | -0.036072 | -0.0034671 | -0.022967 | -0.02989 | -0.024742 | 0.0025024 | -0.0088867 | 0.064617 | 0.041092 | -0.021785 | -0.0096728 | -0.015887 | 0 | 0 | 0 | 0.064087 | 0.2243 | 0.11902 | 0.11902 | -0.87891 | 0.013733 | -122.3282 | 0.086975 | -121.7972 | -121.8613 | -121.7239 | 122.2916 | -0.082397 | -0.01831 | 122.5159 | 122.4106 | 122.4106 | 0.11902 | 0.11902 | -0.036621 | -0.068664 | 0.004578 | 0.49439 | 0.56763 | 0.4303 | 0.60425 | 0.46692 | 0.2243 | 0.064087 | 0.53101 | 122.4152 | 0 | 122.3419 | 122.2916 | 122.3053 | -0.082397 | -122.4106 | 122.3557 | 122.3785 | 122.2916 | 121.4127
1877.6719 | 122.4655 | -122.3328 | 0.11444 | 0.0059509 | -0.00059378 | -0.033936 | -0.00026266 | -0.016985 | -0.027754 | -0.021751 | 0.0025024 | -0.0061095 | 0.065899 | 0.040665 | -0.017726 | -0.0101 | -0.01311 | -0.064087 | 0.036621 | -0.032043 | -0.082397 | 0.032043 | -0.054932 | -0.064087 | -1.0986 | 0.091553 | -122.3465 | -0.041199 | -122.0032 | -122.0673 | -121.8613 | 122.3007 | -0.07782 | -0.19684 | 122.3648 | 122.2687 | 122.2778 | -0.032044 | -0.022889 | -0.013733 | -0.022888 | -0.15564 | 0.32959 | 0.4715 | 0.2655 | 0.48523 | 0.27924 | 0.064086 | -0.050354 | 0.34332 | 122.3053 | 0.068664 | 122.4381 | 122.3694 | 122.4243 | -0.14648 | -122.4609 | 122.2504 | 122.2916 | 122.2687 | 121.2341
1879.4531 | 122.5433 | -122.2778 | 0.082397 | 0.028839 | -0.003371 | -0.033936 | -0.00090366 | -0.01784 | -0.027327 | -0.025383 | 0.0055542 | -0.0076049 | 0.065471 | 0.050919 | -0.018367 | -0.0088184 | -0.013751 | -0.018311 | 0.027466 | -0.018311 | 0.018311 | 0.16022 | 0.045776 | 0.059509 | -1.0345 | 0.050354 | -122.3511 | 0.054932 | -121.8796 | -121.9437 | -121.7834 | 122.2595 | -0.054931 | -0.064086 | 122.438 | 122.3373 | 122.3236 | 0.07782 | 0.064087 | -0.073242 | -0.032043 | -0.027465 | 0.39825 | 0.49439 | 0.33417 | 0.56763 | 0.40741 | 0.17853 | 0.036622 | 0.4715 | 122.406 | 0.045777 | 122.4014 | 122.3053 | 122.3282 | -0.10071 | -122.4335 | 122.2961 | 122.3328 | 122.2595 | 121.2433
1881.25 | 122.612 | -122.3099 | 0.073242 | 0.0059509 | -0.004439 | -0.0365 | -0.00047626 | -0.021685 | -0.02989 | -0.023887 | 0.0025024 | -0.010169 | 0.063762 | 0.046647 | -0.021144 | -0.0088184 | -0.01781 | -0.013733 | 0.004578 | -0.009155 | 0.032043 | 0.1831 | 0.09613 | 0.10529 | -0.98877 | 0.064087 | -122.3328 | 0.091553 | -121.8246 | -121.8887 | -121.7422 | 122.3007 | -0.068664 | -0.041199 | 122.493 | 122.4152 | 122.406 | 0.11444 | 0.10528 | -0.022889 | -0.009155 | 0.018311 | 0.48523 | 0.56763 | 0.42114 | 0.59051 | 0.44403 | 0.19226 | 0.041198 | 0.50812 | 122.4243 | 0.013733 | 122.3969 | 122.3145 | 122.374 | -0.082397 | -122.406 | 122.3419 | 122.4014 | 122.2961 | 121.3211
1883.0312 | 122.4335 | -122.3557 | 0.1236 | -0.0016786 | -0.0031574 | -0.033722 | 0.00037814 | -0.014208 | -0.030104 | -0.023887 | 0.0025024 | -0.0076049 | 0.066967 | 0.044083 | -0.018794 | -0.010955 | -0.016101 | -0.059509 | 0.041199 | -0.009155 | -0.064087 | 0.045776 | -0.054932 | -0.032043 | -1.1307 | 0.082397 | -122.3602 | -0.045776 | -122.0078 | -122.0673 | -121.843 | 122.3465 | -0.082397 | -0.18768 | 122.4014 | 122.3236 | 122.3007 | -0.022888 | -0.045777 | -0.004577 | -0.041199 | -0.16937 | 0.3479 | 0.5127 | 0.28839 | 0.51727 | 0.29297 | 0.054931 | -0.054932 | 0.35248 | 122.3145 | 0.050354 | 122.4426 | 122.3969 | 122.438 | -0.13275 | -122.4838 | 122.2916 | 122.3099 | 122.2961 | 121.225
1884.8125 | 122.525 | -122.3007 | 0.068665 | 0.0059509 | -0.0031574 | -0.034363 | 0.0012325 | -0.018908 | -0.029036 | -0.023674 | 0.011658 | -0.0099549 | 0.065258 | 0.047074 | -0.01794 | -0.0086048 | -0.014605 | -0.045776 | 0.009155 | -0.027466 | 0 | 0.12817 | 0.045776 | 0.064087 | -1.1078 | 0.059509 | -122.3602 | 0.050354 | -121.9025 | -121.9437 | -121.8063 | 122.2733 | -0.05951 | -0.068665 | 122.4289 | 122.3648 | 122.3465 | 0.091553 | 0.073242 | -0.059509 | -0.009156 | -0.018311 | 0.39825 | 0.49438 | 0.35706 | 0.55389 | 0.41656 | 0.15564 | 0.027466 | 0.45776 | 122.4106 | 0.036621 | 122.4197 | 122.3099 | 122.3602 | -0.096131 | -122.4289 | 122.3007 | 122.3511 | 122.2549 | 121.1929
1886.6094 | 122.5983 | -122.2687 | 0.059509 | 0.01358 | -0.00038018 | -0.03714 | 0.0012325 | -0.014635 | -0.027754 | -0.024101 | 0.020813 | -0.0082459 | 0.06419 | 0.04686 | -0.017726 | -0.008391 | -0.012469 | 0.027466 | 0 | -0.013733 | 0.073242 | 0.20599 | 0.082397 | 0.09613 | -1.0391 | 0.045776 | -122.3373 | 0.11444 | -121.843 | -121.8887 | -121.7331 | 122.2549 | -0.059509 | 0.013733 | 122.4747 | 122.3648 | 122.3511 | 0.10986 | 0.09613 | -0.068664 | -0.013733 | 0.054932 | 0.42572 | 0.53558 | 0.37994 | 0.60425 | 0.44861 | 0.21973 | 0.086975 | 0.49438 | 122.4518 | 0.013733 | 122.3831 | 122.2687 | 122.3145 | -0.073242 | -122.3969 | 122.3419 | 122.3831 | 122.2961 | 121.2296
1888.3281 | 122.5571 | -122.3099 | 0.073242 | 0.028839 | -0.00038018 | -0.033082 | 0.0014463 | -0.015917 | -0.025831 | -0.023033 | 0.008606 | -0.0069641 | 0.064403 | 0.048569 | -0.017299 | -0.007323 | -0.018237 | 0 | 0.013733 | -0.018311 | 0.036621 | 0.19684 | 0.064087 | 0.07782 | -1.1169 | 0.041199 | -122.3328 | 0.064087 | -121.875 | -121.9574 | -121.7926 | 122.2916 | -0.059509 | -0.036621 | 122.5067 | 122.3877 | 122.374 | 0.096131 | 0.082398 | -0.022889 | -0.032043 | -0.009155 | 0.43488 | 0.51727 | 0.35248 | 0.54016 | 0.37537 | 0.21515 | 0.054932 | 0.45776 | 122.3969 | 0.032044 | 122.374 | 122.3236 | 122.3511 | -0.091553 | -122.406 | 122.3465 | 122.374 | 122.3099 | 121.1929
1890.1094 | 122.5525 | -122.3373 | 0.10071 | 0.02121 | -0.0063616 | -0.0365 | -0.00069006 | -0.013353 | -0.028608 | -0.020897 | 0.008606 | -0.0073913 | 0.06483 | 0.048356 | -0.019222 | -0.010314 | -0.016101 | -0.045776 | 0.027466 | -0.041199 | 0 | 0.1236 | 0.032043 | 0.050354 | -1.1856 | 0.036621 | -122.3602 | 0.036621 | -121.8842 | -121.9437 | -121.788 | 122.2961 | -0.073242 | -0.10071 | 122.4609 | 122.3877 | 122.3694 | 0.091553 | 0.073242 | -0.022888 | -0.064087 | -0.064087 | 0.45319 | 0.54932 | 0.39368 | 0.5722 | 0.41656 | 0.16479 | 0.041199 | 0.47607 | 122.3969 | 0.068665 | 122.3969 | 122.3648 | 122.374 | -0.14191 | -122.4609 | 122.3373 | 122.374 | 122.2916 | 121.1517
1891.9062 | 122.5067 | -122.3099 | 0.10986 | 0.02121 | -0.00273 | -0.035431 | 0.0020871 | -0.016558 | -0.02989 | -0.024314 | 0.0055542 | -0.0050415 | 0.063549 | 0.037461 | -0.018581 | -0.0096728 | -0.012256 | -0.018311 | 0.054932 | -0.036621 | 0.009155 | 0.1236 | 0.036621 | 0.041199 | -1.1215 | 0.082397 | -122.3648 | 0.009155 | -121.9299 | -122.0032 | -121.8338 | 122.2733 | -0.054931 | -0.10071 | 122.4335 | 122.3511 | 122.3465 | 0.07782 | 0.073242 | -0.054932 | -0.027466 | -0.10071 | 0.37994 | 0.47607 | 0.3067 | 0.53101 | 0.36163 | 0.16022 | 0.045776 | 0.43488 | 122.374 | 0.091553 | 122.4472 | 122.3648 | 122.3923 | -0.14648 | -122.4747 | 122.319 | 122.319 | 122.2916 | 121.1884
1893.625 | 122.58 | -122.3099 | 0.086975 | -0.0016786 | -0.0037982 | -0.036072 | 0.00016454 | -0.020189 | -0.027327 | -0.023246 | 0.0025024 | -0.0095275 | 0.065471 | 0.045365 | -0.019435 | -0.011168 | -0.013965 | 0 | -0.004578 | 0.004578 | 0.082397 | 0.20142 | 0.11902 | 0.10071 | -1.0941 | 0.036621 | -122.3419 | 0.09613 | -121.8201 | -121.907 | -121.7743 | 122.3145 | -0.091553 | -0.004578 | 122.5113 | 122.4106 | 122.4289 | 0.09613 | 0.11444 | -0.032044 | -0.050354 | 0.009155 | 0.48981 | 0.53558 | 0.40283 | 0.56763 | 0.43488 | 0.19684 | 0.077819 | 0.52185 | 122.438 | -0.009156 | 122.3785 | 122.3053 | 122.3465 | -0.082397 | -122.4289 | 122.3923 | 122.406 | 122.3099 | 121.2158
1895.4062 | 122.5525 | -122.3145 | 0.073242 | 0.01358 | -0.0037982 | -0.033295 | -0.0013309 | -0.020403 | -0.027967 | -0.022178 | 0.0025024 | -0.0099549 | 0.067607 | 0.050278 | -0.01794 | -0.0086048 | -0.017596 | -0.036621 | 0.027466 | -0.013733 | 0.009155 | 0.14191 | 0.032043 | 0.059509 | -1.2405 | 0.041199 | -122.374 | 0.032043 | -121.907 | -121.962 | -121.7972 | 122.3007 | -0.045776 | -0.064087 | 122.4564 | 122.374 | 122.3465 | 0.073242 | 0.045776 | -0.059509 | -0.032043 | -0.041199 | 0.40741 | 0.51727 | 0.35248 | 0.57678 | 0.41199 | 0.15564 | 0.022888 | 0.46692 | 122.406 | 0.041199 | 122.4152 | 122.3419 | 122.3557 | -0.086975 | -122.4472 | 122.3236 | 122.3465 | 122.2778 | 121.0739
1897.1875 | 122.5021 | -122.3373 | 0.10529 | 0.051727 | -0.0014484 | -0.035004 | 0.0020871 | -0.020617 | -0.025831 | -0.024101 | 0.017761 | -0.0067505 | 0.065044 | 0.040879 | -0.020503 | -0.011595 | -0.015887 | -0.059509 | 0.045776 | -0.054932 | -0.059509 | 0.059509 | -0.004578 | -0.004578 | -1.2634 | 0.091553 | -122.3969 | -0.027466 | -121.9528 | -122.0032 | -121.8246 | 122.2824 | -0.05951 | -0.16479 | 122.3969 | 122.3328 | 122.3328 | 0.050354 | 0.050354 | -0.05951 | -0.013733 | -0.13275 | 0.38452 | 0.51269 | 0.33417 | 0.5722 | 0.39368 | 0.11444 | -0.004577 | 0.44403 | 122.3694 | 0.10071 | 122.4884 | 122.3831 | 122.4289 | -0.16022 | -122.5021 | 122.2778 | 122.3099 | 122.2778 | 121.0739
1898.9062 | 122.5571 | -122.3557 | 0.091553 | 0.01358 | -0.003371 | -0.03415 | -4.906e-05 | -0.015917 | -0.029036 | -0.020897 | 0.0055542 | -0.0093139 | 0.065258 | 0.04451 | -0.018367 | -0.0098864 | -0.018023 | -0.036621 | 0.018311 | -0.027466 | 0 | 0.13275 | 0.045776 | 0.045776 | -1.3275 | 0.045776 | -122.3602 | 0.032043 | -121.8842 | -121.9666 | -121.8063 | 122.3282 | -0.073242 | -0.091553 | 122.4884 | 122.4014 | 122.4014 | 0.073242 | 0.073242 | -0.004577 | -0.045777 | -0.05951 | 0.4715 | 0.54932 | 0.3891 | 0.55389 | 0.39368 | 0.16022 | 0.027466 | 0.47607 | 122.3923 | 0.045777 | 122.406 | 122.374 | 122.4014 | -0.11902 | -122.4518 | 122.3557 | 122.3877 | 122.319 | 121.0281
1900.6875 | 122.5067 | -122.3282 | 0.091553 | 0.01358 | -0.0025164 | -0.032441 | 0.00059174 | -0.015276 | -0.028181 | -0.023674 | 0.008606 | -0.0061095 | 0.068676 | 0.048142 | -0.020503 | -0.0088184 | -0.017169 | -0.018311 | 0.050354 | -0.032043 | -0.004578 | 0.12817 | 0.032043 | 0.036621 | -1.2405 | 0.07782 | -122.3969 | 0.032043 | -121.9345 | -121.9803 | -121.8063 | 122.2961 | -0.041199 | -0.096131 | 122.4564 | 122.3648 | 122.3602 | 0.068664 | 0.064086 | -0.068665 | -0.013733 | -0.05951 | 0.39368 | 0.52185 | 0.3479 | 0.59052 | 0.41656 | 0.16022 | 0.027465 | 0.46234 | 122.4289 | 0.082397 | 122.4747 | 122.3785 | 122.406 | -0.1236 | -122.4884 | 122.3236 | 122.3602 | 122.3099 | 121.0876
1902.4688 | 122.5754 | -122.3236 | 0.068665 | 0.028839 | -0.0029438 | -0.034791 | -0.00026266 | -0.017626 | -0.027754 | -0.024742 | 0.014709 | -0.0078185 | 0.065044 | 0.046219 | -0.017085 | -0.0077502 | -0.014605 | -0.009155 | 0.009155 | -0.009155 | 0.036621 | 0.16479 | 0.050354 | 0.064087 | -1.3412 | 0.045776 | -122.374 | 0.045776 | -121.907 | -121.9666 | -121.7926 | 122.3145 | -0.05951 | -0.032044 | 122.4884 | 122.3877 | 122.374 | 0.073242 | 0.059509 | -0.050354 | -0.022889 | -0.022889 | 0.41656 | 0.531 | 0.35705 | 0.58136 | 0.40741 | 0.17395 | 0.045776 | 0.46692 | 122.4197 | 0.01831 | 122.4197 | 122.3328 | 122.3694 | -0.07782 | -122.4426 | 122.3602 | 122.3694 | 122.3145 | 120.9824
1904.1875 | 122.5662 | -122.3145 | 0.07782 | 0.02121 | -0.0042254 | -0.033722 | 0.00037814 | -0.020617 | -0.026686 | -0.021537 | 0.0055542 | -0.0071777 | 0.066539 | 0.047715 | -0.019649 | -0.008391 | -0.015033 | -0.036621 | 0.013733 | -0.018311 | -0.004578 | 0.11902 | 0.032043 | 0.050354 | -1.4145 | 0.050354 | -122.3602 | 0.050354 | -121.8842 | -121.9482 | -121.788 | 122.2961 | -0.064087 | -0.082398 | 122.4335 | 122.3648 | 122.3465 | 0.068665 | 0.050354 | -0.045776 | -0.027466 | -0.027466 | 0.4303 | 0.52643 | 0.36621 | 0.5722 | 0.41199 | 0.13733 | 0.013733 | 0.47607 | 122.4106 | 0.032044 | 122.4106 | 122.3282 | 122.3648 | -0.096131 | -122.438 | 122.3099 | 122.3648 | 122.2778 | 120.9
1905.9688 | 122.5891 | -122.3236 | 0.07782 | 0.02121 | -0.0042254 | -0.033936 | -0.0021853 | -0.01784 | -0.026686 | -0.02346 | -0.00054937 | -0.0084595 | 0.063762 | 0.04451 | -0.018794 | -0.010314 | -0.017169 | -0.032043 | 0.013733 | -0.022888 | 0 | 0.14191 | 0.064087 | 0.064087 | -1.4008 | 0.032043 | -122.374 | 0.064087 | -121.8521 | -121.9162 | -121.7789 | 122.3007 | -0.064087 | -0.07782 | 122.4655 | 122.3877 | 122.3877 | 0.086975 | 0.086975 | -0.050354 | -0.045777 | -0.013733 | 0.4715 | 0.54474 | 0.40741 | 0.59509 | 0.45776 | 0.16479 | 0.022888 | 0.52185 | 122.438 | 0.036621 | 122.406 | 122.3373 | 122.3557 | -0.10071 | -122.4518 | 122.3236 | 122.3877 | 122.2916 | 120.9229
1907.75 | 122.612 | -122.3053 | 0.073242 | 0.01358 | -0.0037982 | -0.035431 | 0.0020871 | -0.01549 | -0.026686 | -0.018547 | 0.014709 | -0.0076049 | 0.065685 | 0.04686 | -0.016017 | -0.010741 | -0.019091 | 0.018311 | 0.009155 | -0.018311 | 0.091553 | 0.21973 | 0.086975 | 0.09613 | -1.3641 | 0.041199 | -122.3602 | 0.10071 | -121.8613 | -121.9162 | -121.7468 | 122.287 | -0.064087 | 0.018311 | 122.525 | 122.4014 | 122.3923 | 0.11444 | 0.10529 | -0.054931 | -0.032043 | 0.027466 | 0.44403 | 0.55847 | 0.3891 | 0.6134 | 0.44403 | 0.23804 | 0.10986 | 0.49896 | 122.4609 | 0.027466 | 122.4014 | 122.3145 | 122.3465 | -0.091553 | -122.4335 | 122.3969 | 122.406 | 122.3236 | 120.9412
1909.4688 | 122.5479 | -122.3328 | 0.07782 | 0.01358 | -0.003371 | -0.035004 | -0.0015445 | -0.01848 | -0.027113 | -0.021537 | 0.008606 | -0.0086731 | 0.066753 | 0.044297 | -0.021358 | -0.0094592 | -0.013751 | -0.054932 | 0.009155 | -0.018311 | 0 | 0.13733 | 0.050354 | 0.045776 | -1.5198 | 0.054932 | -122.3877 | 0.036621 | -121.8979 | -121.9711 | -121.8063 | 122.3145 | -0.068665 | -0.07782 | 122.4701 | 122.3785 | 122.3831 | 0.064087 | 0.068665 | -0.054931 | -0.022888 | -0.041199 | 0.43488 | 0.52643 | 0.36163 | 0.58136 | 0.41656 | 0.15564 | 0.018311 | 0.48981 | 122.4243 | 0.027466 | 122.4426 | 122.3419 | 122.3877 | -0.096131 | -122.4655 | 122.3328 | 122.3694 | 122.2778 | 120.813
1911.2656 | 122.6166 | -122.319 | 0.07782 | 0.02121 | -0.0035846 | -0.036072 | -0.00090366 | -0.022112 | -0.030531 | -0.025596 | 0.0025024 | -0.0084595 | 0.063121 | 0.050492 | -0.019222 | -0.0088184 | -0.014178 | 0.009155 | -0.013733 | 0.013733 | 0.086975 | 0.23346 | 0.10071 | 0.10986 | -1.4236 | 0.045776 | -122.3465 | 0.09613 | -121.8018 | -121.8887 | -121.756 | 122.3328 | -0.091553 | 0.009155 | 122.5525 | 122.4289 | 122.4197 | 0.09613 | 0.086975 | -0.027466 | -0.032044 | 0.01831 | 0.51727 | 0.56305 | 0.4303 | 0.59052 | 0.45776 | 0.21973 | 0.073242 | 0.54474 | 122.4426 | -0.027466 | 122.3923 | 122.3053 | 122.3648 | -0.064087 | -122.4243 | 122.406 | 122.4152 | 122.3282 | 120.8954
1912.9688 | 122.4747 | -122.3557 | 0.11444 | 0.0059509 | -0.0023028 | -0.0365 | 0.0020871 | -0.016985 | -0.029249 | -0.022178 | 0.0055542 | -0.0078185 | 0.066753 | 0.041733 | -0.020076 | -0.0086048 | -0.012896 | -0.041199 | 0.032043 | -0.041199 | -0.036621 | 0.091553 | -0.009155 | -0.018311 | -1.5793 | 0.059509 | -122.3877 | 0.004578 | -121.9803 | -122.0581 | -121.8613 | 122.3145 | -0.082398 | -0.15106 | 122.4472 | 122.3373 | 122.3465 | 0.022888 | 0.032044 | -0.032043 | -0.054932 | -0.10986 | 0.37537 | 0.49439 | 0.29755 | 0.52643 | 0.32959 | 0.13275 | 0.004578 | 0.40741 | 122.3923 | 0.073242 | 122.4472 | 122.3877 | 122.4152 | -0.15564 | -122.5021 | 122.319 | 122.3602 | 122.3145 | 120.7764
1914.75 | 122.6074 | -122.2961 | 0.082397 | 0.0059509 | -0.0042254 | -0.03415 | 0.0016599 | -0.015276 | -0.029463 | -0.020042 | 0.017761 | -0.0058959 | 0.065258 | 0.044724 | -0.015163 | -0.0077502 | -0.009692 | 0.004578 | 0.013733 | -0.004578 | 0.064087 | 0.19226 | 0.073242 | 0.09613 | -1.5335 | 0.041199 | -122.3694 | 0.10529 | -121.8384 | -121.9208 | -121.7606 | 122.2916 | -0.068664 | -0.01831 | 122.4884 | 122.3923 | 122.3694 | 0.10071 | 0.07782 | -0.073242 | -0.041198 | 0.022889 | 0.45776 | 0.53558 | 0.37537 | 0.60883 | 0.44861 | 0.19684 | 0.068665 | 0.53101 | 122.4747 | 0.018311 | 122.4106 | 122.3099 | 122.3373 | -0.086975 | -122.4518 | 122.3602 | 122.4014 | 122.3007 | 120.7626
1916.5469 | 122.5616 | -122.3282 | 0.064087 | 0.036468 | -0.004439 | -0.034363 | -0.0013309 | -0.018908 | -0.027754 | -0.025169 | 0.008606 | -0.010169 | 0.062481 | 0.050919 | -0.019008 | -0.010314 | -0.014819 | -0.022888 | 0.004578 | -0.009155 | 0.027466 | 0.16937 | 0.041199 | 0.068665 | -1.6663 | 0.045776 | -122.3648 | 0.036621 | -121.9116 | -121.962 | -121.8109 | 122.319 | -0.059509 | -0.036621 | 122.4976 | 122.3969 | 122.3694 | 0.07782 | 0.050354 | -0.036621 | -0.018311 | -0.027466 | 0.41657 | 0.51727 | 0.36621 | 0.55389 | 0.40283 | 0.17853 | 0.036621 | 0.45319 | 122.4014 | 0.013733 | 122.4106 | 122.3328 | 122.374 | -0.073242 | -122.4289 | 122.3557 | 122.3648 | 122.3053 | 120.6619
1918.2656 | 122.5937 | -122.3282 | 0.073242 | 0.02121 | -0.0065754 | -0.035645 | 0.00016454 | -0.01848 | -0.030317 | -0.021324 | -0.00054937 | -0.010596 | 0.06184 | 0.05156 | -0.018367 | -0.0096728 | -0.016314 | -0.022888 | 0.018311 | 0 | 0.036621 | 0.1831 | 0.09613 | 0.091553 | -1.68 | 0.027466 | -122.3602 | 0.091553 | -121.843 | -121.8933 | -121.7606 | 122.3282 | -0.054931 | -0.036621 | 122.5113 | 122.4197 | 122.4243 | 0.091553 | 0.09613 | -0.032043 | -0.045776 | 0.018311 | 0.48523 | 0.56763 | 0.43488 | 0.59967 | 0.46692 | 0.1831 | 0.036621 | 0.51727 | 122.4518 | 0.018311 | 122.3877 | 122.3465 | 122.3557 | -0.073242 | -122.4335 | 122.3648 | 122.4197 | 122.3053 | 120.6482
1920.0469 | 122.5479 | -122.319 | 0.10986 | 0.0059509 | -0.0035846 | -0.0365 | -0.0032535 | -0.020189 | -0.028181 | -0.023033 | 0.008606 | -0.0063233 | 0.065258 | 0.042801 | -0.022426 | -0.009032 | -0.016528 | 0.004578 | 0 | -0.022888 | 0.027466 | 0.17853 | 0.091553 | 0.07782 | -1.6983 | 0.050354 | -122.3602 | 0.004578 | -121.9116 | -121.9803 | -121.8338 | 122.2961 | -0.10986 | -0.082397 | 122.4976 | 122.3969 | 122.4106 | 0.10071 | 0.11444 | -0.041198 | -0.059509 | -0.10529 | 0.40741 | 0.48523 | 0.33874 | 0.52643 | 0.37994 | 0.20142 | 0.050354 | 0.44861 | 122.3648 | 0.022888 | 122.4106 | 122.319 | 122.3694 | -0.13275 | -122.4701 | 122.3465 | 122.3236 | 122.3236 | 120.6207
1921.8281 | 122.6212 | -122.3282 | 0.064087 | 0.02121 | -0.00508 | -0.033509 | -4.906e-05 | -0.016771 | -0.026472 | -0.022605 | 0.0025024 | -0.0063233 | 0.064403 | 0.049851 | -0.014949 | -0.0101 | -0.020373 | 0.013733 | -0.004578 | 0.004578 | 0.054932 | 0.19684 | 0.064087 | 0.082397 | -1.767 | 0.022888 | -122.374 | 0.11902 | -121.8658 | -121.9299 | -121.7468 | 122.3328 | -0.068665 | -0.009155 | 122.525 | 122.4106 | 122.3923 | 0.077819 | 0.059509 | -0.045776 | -0.041199 | 0.054932 | 0.46234 | 0.58136 | 0.39825 | 0.62714 | 0.44403 | 0.19226 | 0.050354 | 0.50812 | 122.493 | -0.009156 | 122.3969 | 122.3236 | 122.3511 | -0.059509 | -122.438 | 122.3831 | 122.4472 | 122.3419 | 120.5612
1923.5469 | 122.6028 | -122.3419 | 0.086975 | 0.02121 | -0.0029438 | -0.036072 | -0.00047626 | -0.018694 | -0.030958 | -0.025169 | -0.00054937 | -0.0093139 | 0.063335 | 0.043656 | -0.023067 | -0.0096728 | -0.012469 | 0.004578 | 0 | -0.013733 | 0.059509 | 0.21515 | 0.11902 | 0.10529 | -1.7944 | 0.041199 | -122.3602 | 0.086975 | -121.8475 | -121.9254 | -121.7789 | 122.3282 | -0.086975 | -0.027466 | 122.5571 | 122.4472 | 122.4609 | 0.11902 | 0.13275 | -0.01831 | -0.045776 | 0 | 0.49439 | 0.56305 | 0.41657 | 0.58136 | 0.43488 | 0.22888 | 0.073242 | 0.5127 | 122.4472 | 0.013733 | 122.4014 | 122.3419 | 122.3831 | -0.10071 | -122.4472 | 122.4014 | 122.4289 | 122.3465 | 120.5475
1925.3281 | 122.5937 | -122.3145 | 0.054932 | 0.028839 | -0.00273 | -0.033295 | -4.906e-05 | -0.017199 | -0.027327 | -0.023674 | 0.011658 | -0.0082459 | 0.063335 | 0.053055 | -0.017085 | -0.008391 | -0.01546 | 0.009155 | 0 | 0 | 0.050354 | 0.20599 | 0.064087 | 0.10529 | -1.8631 | 0.054932 | -122.3831 | 0.086975 | -121.8887 | -121.9574 | -121.788 | 122.3145 | -0.054932 | -0.004578 | 122.5204 | 122.4197 | 122.3785 | 0.10529 | 0.064087 | -0.068665 | 0 | 0.032043 | 0.42572 | 0.52643 | 0.35706 | 0.59509 | 0.42572 | 0.20599 | 0.050354 | 0.49438 | 122.4701 | 0 | 122.438 | 122.3145 | 122.3694 | -0.054932 | -122.438 | 122.3648 | 122.4014 | 122.3236 | 120.4514
1927.125 | 122.5204 | -122.3602 | 0.11902 | 0.01358 | -0.004439 | -0.034791 | 0.00037814 | -0.014208 | -0.030104 | -0.020256 | 0.0055542 | -0.0073913 | 0.063549 | 0.043229 | -0.017085 | -0.0094592 | -0.018664 | -0.064087 | 0.036621 | -0.032043 | -0.073242 | 0.064087 | -0.054932 | -0.027466 | -2.0325 | 0.073242 | -122.3923 | 0.022888 | -121.9574 | -122.0535 | -121.8292 | 122.3282 | -0.082398 | -0.19226 | 122.4243 | 122.3328 | 122.3053 | 0.004577 | -0.022889 | -0.032044 | -0.045777 | -0.096131 | 0.40283 | 0.53101 | 0.3067 | 0.56305 | 0.33875 | 0.09613 | -0.041199 | 0.43488 | 122.4152 | 0.068664 | 122.4655 | 122.3969 | 122.4335 | -0.15106 | -122.5113 | 122.287 | 122.3831 | 122.2961 | 120.3278
1928.8438 | 122.6303 | -122.3282 | 0.064087 | 0.01358 | -0.0048664 | -0.035218 | -0.0026127 | -0.021471 | -0.028822 | -0.023033 | -0.00054937 | -0.0065369 | 0.062481 | 0.044297 | -0.021785 | -0.0094592 | -0.014178 | -0.013733 | -0.013733 | 0 | 0.050354 | 0.23346 | 0.1236 | 0.1236 | -1.9592 | 0.041199 | -122.3511 | 0.11444 | -121.8155 | -121.8887 | -121.7651 | 122.3282 | -0.07782 | -0.013733 | 122.5616 | 122.4518 | 122.4518 | 0.1236 | 0.1236 | -0.022888 | -0.022888 | 0.050354 | 0.5127 | 0.56305 | 0.43945 | 0.58594 | 0.46234 | 0.23346 | 0.050354 | 0.53558 | 122.4655 | -0.013733 | 122.3923 | 122.3145 | 122.3694 | -0.064087 | -122.4152 | 122.3785 | 122.4426 | 122.3145 | 120.369
1930.625 | 122.4884 | -122.3328 | 0.10986 | 0.02121 | -0.0010212 | -0.035004 | 0.0016599 | -0.018053 | -0.028181 | -0.021751 | 0.0025024 | -0.0063233 | 0.06483 | 0.045151 | -0.019222 | -0.0098864 | -0.013751 | -0.027466 | 0.022888 | -0.032043 | -0.041199 | 0.09613 | -0.013733 | -0.009155 | -2.124 | 0.073242 | -122.4106 | 0 | -121.9757 | -122.0627 | -121.875 | 122.3007 | -0.086975 | -0.15106 | 122.4289 | 122.3236 | 122.319 | 0.022888 | 0.01831 | -0.077819 | -0.036621 | -0.10986 | 0.35706 | 0.45776 | 0.27008 | 0.53558 | 0.3479 | 0.12817 | -0.009156 | 0.43488 | 122.4106 | 0.054931 | 122.4838 | 122.3557 | 122.406 | -0.14191 | -122.5204 | 122.2916 | 122.3328 | 122.3053 | 120.2087
1932.3594 | 122.6028 | -122.3236 | 0.059509 | 0.036468 | -0.0042254 | -0.035218 | -0.0011173 | -0.013567 | -0.026472 | -0.02111 | 0.014709 | -0.0067505 | 0.065258 | 0.047928 | -0.014736 | -0.0068958 | -0.017169 | 0.013733 | 0.027466 | -0.013733 | 0.082397 | 0.23804 | 0.091553 | 0.09613 | -2.124 | 0.041199 | -122.3694 | 0.10529 | -121.8567 | -121.9345 | -121.7697 | 122.3099 | -0.032043 | 0.022888 | 122.5616 | 122.4197 | 122.4152 | 0.10986 | 0.10529 | -0.045777 | -0.01831 | 0.045777 | 0.46692 | 0.55389 | 0.3891 | 0.59967 | 0.43488 | 0.25177 | 0.09613 | 0.5127 | 122.4747 | 0.041199 | 122.4106 | 122.3511 | 122.3648 | -0.073242 | -122.4289 | 122.406 | 122.4289 | 122.3373 | 120.1996
1934.1406 | 122.5571 | -122.3557 | 0.10529 | 0.01358 | -0.0018756 | -0.036072 | 0.00080534 | -0.01314 | -0.027754 | -0.022819 | 0.0055542 | -0.0071777 | 0.065044 | 0.040452 | -0.021144 | -0.0092456 | -0.014178 | -0.013733 | 0.036621 | -0.036621 | -0.004578 | 0.1236 | 0.027466 | 0.022888 | -2.1744 | 0.091553 | -122.406 | 0.036621 | -121.9116 | -122.0078 | -121.8292 | 122.319 | -0.068665 | -0.10986 | 122.4792 | 122.3785 | 122.3831 | 0.059509 | 0.064087 | -0.050354 | -0.013733 | -0.068665 | 0.44403 | 0.52643 | 0.3479 | 0.57678 | 0.39826 | 0.16022 | 0.032043 | 0.49439 | 122.4426 | 0.073242 | 122.4976 | 122.3923 | 122.4472 | -0.14191 | -122.5113 | 122.3511 | 122.3923 | 122.3419 | 120.1813
1935.9062 | 122.5388 | -122.3785 | 0.10529 | 0.01358 | -0.0025164 | -0.035431 | -0.0013309 | -0.015917 | -0.029249 | -0.022392 | 0.014709 | -0.0073913 | 0.066967 | 0.047928 | -0.021358 | -0.0081774 | -0.011401 | -0.054932 | 0.045776 | -0.041199 | -0.041199 | 0.064087 | 0.013733 | 0.018311 | -2.3254 | 0.073242 | -122.3969 | 0 | -121.9345 | -122.0261 | -121.8338 | 122.3373 | -0.05951 | -0.14649 | 122.4426 | 122.3969 | 122.3923 | 0.05951 | 0.054932 | -0.018311 | -0.032044 | -0.10529 | 0.44403 | 0.54474 | 0.35248 | 0.56305 | 0.37079 | 0.10529 | 0 | 0.46234 | 122.3969 | 0.086975 | 122.4701 | 122.4243 | 122.4518 | -0.14649 | -122.5021 | 122.3373 | 122.3785 | 122.3236 | 120.0531
1937.6406 | 122.5983 | -122.3236 | 0.082397 | 0.0059509 | -0.0023028 | -0.03415 | -4.906e-05 | -0.018267 | -0.02754 | -0.024742 | 0.0025024 | -0.0091003 | 0.063762 | 0.056046 | -0.017085 | -0.0077502 | -0.016742 | -0.068665 | 0.041199 | -0.041199 | -0.027466 | 0.11902 | 0 | 0.013733 | -2.3941 | 0.050354 | -122.3694 | 0.091553 | -121.8933 | -121.9666 | -121.7789 | 122.2824 | -0.041198 | -0.10986 | 122.4426 | 122.3373 | 122.3236 | 0.054932 | 0.041199 | -0.045777 | -0.032043 | 0.009156 | 0.4303 | 0.54474 | 0.35705 | 0.59051 | 0.40283 | 0.16022 | 0.013733 | 0.47607 | 122.4609 | 0.082398 | 122.4197 | 122.3648 | 122.374 | -0.1236 | -122.4518 | 122.2961 | 122.4152 | 122.2549 | 119.9295
1939.4375 | 122.5479 | -122.3694 | 0.091553 | 0.02121 | -0.0023028 | -0.035004 | -0.00047626 | -0.017626 | -0.029676 | -0.022605 | 0.008606 | -0.0050415 | 0.066539 | 0.042588 | -0.019435 | -0.0094592 | -0.018023 | 0.004578 | 0.050354 | -0.032043 | -0.018311 | 0.15106 | 0.036621 | 0.041199 | -2.3941 | 0.068665 | -122.374 | 0.036621 | -121.9299 | -122.0078 | -121.8246 | 122.3373 | -0.041199 | -0.10986 | 122.5204 | 122.4106 | 122.406 | 0.073242 | 0.068664 | -0.004577 | -0.022888 | -0.054932 | 0.43945 | 0.54474 | 0.36163 | 0.54932 | 0.36621 | 0.18311 | 0.013732 | 0.44403 | 122.4106 | 0.082397 | 122.4426 | 122.4197 | 122.438 | -0.1236 | -122.4655 | 122.3511 | 122.406 | 122.374 | 119.9753
1941.1719 | 122.5388 | -122.3877 | 0.10529 | 0.051727 | -0.0037982 | -0.036286 | 0.00037814 | -0.014849 | -0.029036 | -0.021751 | 0.014709 | -0.0076049 | 0.068462 | 0.042588 | -0.021999 | -0.0094592 | -0.011615 | -0.054932 | 0.054932 | -0.068665 | -0.045776 | 0.091553 | 0.013733 | 0.018311 | -2.5406 | 0.073242 | -122.4106 | 0.009155 | -121.9437 | -122.0169 | -121.8338 | 122.319 | -0.050354 | -0.15106 | 122.4792 | 122.406 | 122.4014 | 0.086976 | 0.082398 | -0.022888 | -0.032044 | -0.096131 | 0.44403 | 0.55389 | 0.37079 | 0.57678 | 0.39368 | 0.16022 | 0.022889 | 0.46692 | 122.4197 | 0.1236 | 122.4838 | 122.4426 | 122.4609 | -0.17395 | -122.5159 | 122.3419 | 122.3969 | 122.3328 | 119.8471
1942.9688 | 122.6303 | -122.3419 | 0.09613 | -0.0016786 | -0.0040118 | -0.03415 | -0.0013309 | -0.018053 | -0.028608 | -0.024101 | 0.0025024 | -0.011237 | 0.062694 | 0.043442 | -0.020717 | -0.0096728 | -0.016314 | -0.013733 | 0 | -0.004578 | 0.050354 | 0.21973 | 0.1236 | 0.10986 | -2.5131 | 0.036621 | -122.3648 | 0.10986 | -121.8475 | -121.9116 | -121.7789 | 122.3373 | -0.09613 | -0.045776 | 122.5616 | 122.4518 | 122.4655 | 0.11444 | 0.12817 | -0.022888 | -0.059509 | 0.013733 | 0.49439 | 0.56305 | 0.4303 | 0.58594 | 0.45319 | 0.22431 | 0.054932 | 0.51727 | 122.4747 | 0.004578 | 122.4014 | 122.3419 | 122.3785 | -0.10071 | -122.4609 | 122.3923 | 122.4518 | 122.3282 | 119.8288
1944.6875 | 122.6166 | -122.3282 | 0.068665 | 0.0059509 | -0.0040118 | -0.034791 | 0.00059174 | -0.013567 | -0.030104 | -0.02346 | 0.0055542 | -0.0058959 | 0.063762 | 0.043656 | -0.017299 | -0.0096728 | -0.014392 | -0.013733 | 0.013733 | -0.018311 | 0.032043 | 0.17853 | 0.054932 | 0.07782 | -2.6413 | 0.022888 | -122.3648 | 0.10529 | -121.8613 | -121.962 | -121.7606 | 122.3099 | -0.054932 | -0.036622 | 122.5067 | 122.406 | 122.3831 | 0.096131 | 0.073243 | -0.036621 | -0.045777 | 0.036621 | 0.46692 | 0.56763 | 0.36621 | 0.60425 | 0.40283 | 0.19684 | 0.050354 | 0.50354 | 122.4701 | 0.032044 | 122.3877 | 122.3419 | 122.3511 | -0.086976 | -122.4335 | 122.3602 | 122.4335 | 122.3145 | 119.6869
1946.4688 | 122.5479 | -122.3694 | 0.11444 | 0.01358 | -0.0029438 | -0.035218 | 0.00037814 | -0.015062 | -0.029036 | -0.024314 | 0.0025024 | -0.0067505 | 0.065044 | 0.04686 | -0.018154 | -0.0068958 | -0.019732 | -0.059509 | 0.022888 | -0.041199 | -0.068665 | 0.050354 | -0.041199 | -0.022888 | -2.7924 | 0.073242 | -122.3877 | 0.032043 | -121.9711 | -122.0444 | -121.8613 | 122.3282 | -0.091553 | -0.18311 | 122.4197 | 122.3465 | 122.3282 | 0.018311 | 0 | -0.01831 | -0.041199 | -0.082398 | 0.39825 | 0.50812 | 0.32501 | 0.52643 | 0.34332 | 0.091553 | -0.027466 | 0.41656 | 122.4197 | 0.064087 | 122.4609 | 122.3923 | 122.4426 | -0.15564 | -122.5021 | 122.3007 | 122.4014 | 122.3099 | 119.577
1948.1875 | 122.5388 | -122.3648 | 0.10529 | 0.028839 | -0.001662 | -0.036072 | -0.00090366 | -0.016985 | -0.02989 | -0.022819 | 0.014709 | -0.0063233 | 0.066753 | 0.04686 | -0.022212 | -0.010527 | -0.015246 | -0.018311 | 0.041199 | -0.050354 | -0.059509 | 0.07782 | 0.022888 | 0.013733 | -2.8244 | 0.091553 | -122.4106 | 0 | -121.9345 | -122.0306 | -121.8384 | 122.3145 | -0.064087 | -0.16479 | 122.4426 | 122.3785 | 122.3877 | 0.064087 | 0.073242 | -0.045776 | -0.013733 | -0.10529 | 0.4303 | 0.52643 | 0.33417 | 0.5722 | 0.37994 | 0.12817 | -0.009155 | 0.47607 | 122.4106 | 0.091553 | 122.5021 | 122.406 | 122.4564 | -0.15564 | -122.5159 | 122.3053 | 122.3648 | 122.3465 | 119.5404
1949.9688 | 122.5021 | -122.374 | 0.09613 | -0.0093076 | -0.0040118 | -0.035859 | -0.00026266 | -0.016131 | -0.029676 | -0.021537 | 0.0025024 | -0.0080321 | 0.063549 | 0.046433 | -0.024562 | -0.0101 | -0.018451 | -0.041199 | 0.018311 | -0.022888 | -0.050354 | 0.091553 | 0.022888 | 0.022888 | -2.9388 | 0.059509 | -122.406 | -0.009155 | -121.962 | -122.0444 | -121.8842 | 122.3511 | -0.077819 | -0.14648 | 122.4655 | 122.3969 | 122.3969 | 0.045776 | 0.045776 | -0.032044 | -0.036621 | -0.10528 | 0.41199 | 0.48981 | 0.32959 | 0.52185 | 0.36163 | 0.11444 | -0.027466 | 0.44403 | 122.3969 | 0.041199 | 122.4655 | 122.3923 | 122.4335 | -0.11902 | -122.5021 | 122.3236 | 122.3648 | 122.3328 | 119.4351
1951.75 | 122.4976 | -122.3969 | 0.10986 | 0.036468 | -0.00273 | -0.035218 | 0.0018735 | -0.017626 | -0.028181 | -0.026237 | 0.017761 | -0.0071777 | 0.06419 | 0.038315 | -0.019863 | -0.0092456 | -0.01546 | -0.054932 | 0.059509 | -0.064087 | -0.073242 | 0.068665 | 0.009155 | 0.013733 | -3.0441 | 0.10529 | -122.438 | -0.018311 | -121.9803 | -122.0718 | -121.8796 | 122.3328 | -0.050354 | -0.18311 | 122.4655 | 122.4106 | 122.406 | 0.07782 | 0.073242 | -0.041198 | -0.004577 | -0.12817 | 0.41656 | 0.51727 | 0.32501 | 0.55847 | 0.36621 | 0.13275 | -0.009155 | 0.45776 | 122.4197 | 0.1236 | 122.5433 | 122.4564 | 122.5021 | -0.17395 | -122.5479 | 122.3236 | 122.3785 | 122.3419 | 119.3527
1953.5156 | 122.5479 | -122.3831 | 0.10529 | 0.044098 | -0.00273 | -0.035218 | -0.0013309 | -0.013353 | -0.029036 | -0.020897 | 0.008606 | -0.0056823 | 0.066753 | 0.037888 | -0.02029 | -0.010527 | -0.016955 | -0.059509 | 0.050354 | -0.064087 | -0.064087 | 0.064087 | 0.004578 | 0 | -3.0808 | 0.091553 | -122.4335 | -0.018311 | -121.9391 | -122.0123 | -121.8567 | 122.319 | -0.054932 | -0.16937 | 122.4472 | 122.3831 | 122.3877 | 0.064087 | 0.068665 | -0.050354 | -0.013733 | -0.1236 | 0.44403 | 0.52643 | 0.37079 | 0.57678 | 0.42114 | 0.12817 | 0 | 0.49438 | 122.4152 | 0.11444 | 122.525 | 122.4335 | 122.4747 | -0.16937 | -122.5388 | 122.319 | 122.3648 | 122.3236 | 119.3024
1955.2969 | 122.525 | -122.3969 | 0.10529 | 0.028839 | -0.0046526 | -0.036713 | 0.00059174 | -0.018053 | -0.028822 | -0.023887 | 0.014709 | -0.0065369 | 0.066539 | 0.037461 | -0.020717 | -0.0098864 | -0.013537 | -0.054932 | 0.045776 | -0.073242 | -0.059509 | 0.054932 | -0.004578 | 0 | -3.1586 | 0.09613 | -122.4106 | -0.013733 | -121.9757 | -122.0535 | -121.8658 | 122.3236 | -0.05951 | -0.16479 | 122.4518 | 122.3969 | 122.3923 | 0.073242 | 0.068664 | -0.013732 | -0.009156 | -0.11902 | 0.42114 | 0.53101 | 0.34332 | 0.54474 | 0.35706 | 0.12817 | 0.013733 | 0.43488 | 122.3969 | 0.11902 | 122.5067 | 122.4426 | 122.493 | -0.17853 | -122.5159 | 122.3373 | 122.3831 | 122.3419 | 119.2383
1957.0781 | 122.5113 | -122.3877 | 0.10986 | 0.01358 | -0.0059344 | -0.035645 | -0.00047626 | -0.016344 | -0.027754 | -0.021324 | 0.014709 | -0.0071777 | 0.065899 | 0.040238 | -0.019649 | -0.010741 | -0.015674 | -0.068665 | 0.050354 | -0.064087 | -0.086975 | 0.059509 | 0.004578 | 0.009155 | -3.273 | 0.091553 | -122.4243 | -0.027466 | -121.9849 | -122.049 | -121.875 | 122.3236 | -0.059509 | -0.19684 | 122.4472 | 122.3969 | 122.3923 | 0.073242 | 0.068665 | -0.036621 | -0.01831 | -0.13733 | 0.40283 | 0.51269 | 0.33874 | 0.54932 | 0.37537 | 0.1236 | -0.022888 | 0.43945 | 122.3969 | 0.11444 | 122.5159 | 122.438 | 122.4792 | -0.17395 | -122.5342 | 122.3007 | 122.3602 | 122.319 | 119.1147
1958.8438 | 122.6349 | -122.374 | 0.073242 | 0.0059509 | -0.0048664 | -0.035218 | -0.0036807 | -0.020403 | -0.029036 | -0.022605 | 0.011658 | -0.0093139 | 0.062481 | 0.048569 | -0.017299 | -0.0098864 | -0.014819 | 0 | -0.004578 | -0.009155 | 0.054932 | 0.21515 | 0.1236 | 0.10529 | -3.2455 | 0.032043 | -122.3877 | 0.09613 | -121.8567 | -121.9299 | -121.7972 | 122.3648 | -0.07782 | -0.01831 | 122.5891 | 122.4792 | 122.4976 | 0.11444 | 0.13275 | -0.013733 | -0.041199 | 0.022888 | 0.51727 | 0.57678 | 0.44403 | 0.59051 | 0.45776 | 0.2243 | 0.064087 | 0.53101 | 122.4838 | 0.004577 | 122.4197 | 122.3694 | 122.406 | -0.082397 | -122.4609 | 122.4289 | 122.4701 | 122.374 | 119.1284
1960.5625 | 122.58 | -122.3557 | 0.086975 | 0.044098 | -0.0020892 | -0.035431 | 0.00016454 | -0.013567 | -0.029676 | -0.024101 | 0.017761 | -0.0093139 | 0.065044 | 0.046647 | -0.017726 | -0.0081774 | -0.018023 | 0.004578 | 0.009155 | -0.004578 | 0.050354 | 0.20599 | 0.09613 | 0.09613 | -3.3783 | 0.036621 | -122.3785 | 0.09613 | -121.907 | -121.9849 | -121.8155 | 122.3511 | -0.07782 | -0.036621 | 122.5616 | 122.4518 | 122.4518 | 0.10071 | 0.10071 | -0.022888 | -0.050354 | 0.009155 | 0.44861 | 0.54016 | 0.37079 | 0.56305 | 0.39368 | 0.21057 | 0.054932 | 0.4715 | 122.4747 | 0.013733 | 122.4152 | 122.3648 | 122.3923 | -0.091553 | -122.4655 | 122.406 | 122.4518 | 122.3602 | 118.9774
1962.3438 | 122.5708 | -122.3785 | 0.10986 | 0.02121 | -0.0018756 | -0.035004 | 0.0023007 | -0.014635 | -0.029463 | -0.021965 | 0.014709 | -0.0067505 | 0.065258 | 0.037034 | -0.019008 | -0.0079638 | -0.016314 | -0.022888 | 0.054932 | -0.050354 | -0.050354 | 0.068665 | 0.018311 | 0.009155 | -3.5156 | 0.082397 | -122.4289 | 0.027466 | -121.9437 | -122.0123 | -121.8338 | 122.3282 | -0.054931 | -0.16022 | 122.4472 | 122.3877 | 122.3969 | 0.059509 | 0.068665 | -0.050354 | -0.027466 | -0.082397 | 0.43488 | 0.54474 | 0.36621 | 0.59509 | 0.41657 | 0.11902 | 0 | 0.48523 | 122.4564 | 0.10529 | 122.5113 | 122.4335 | 122.4609 | -0.16022 | -122.5388 | 122.3282 | 122.406 | 122.3557 | 118.8629
1964.0781 | 122.5616 | -122.3694 | 0.091553 | 0.028839 | -0.0014484 | -0.033936 | -4.906e-05 | -0.016131 | -0.028822 | -0.023033 | 0.0025024 | -0.0065369 | 0.065258 | 0.042374 | -0.017299 | -0.0086048 | -0.015887 | -0.018311 | 0.032043 | -0.045776 | -0.018311 | 0.11902 | 0.027466 | 0.018311 | -3.6026 | 0.073242 | -122.406 | 0.027466 | -121.9254 | -122.0261 | -121.8521 | 122.3236 | -0.05951 | -0.10986 | 122.4884 | 122.3877 | 122.3969 | 0.064087 | 0.073242 | -0.036621 | -0.018311 | -0.064087 | 0.44403 | 0.51727 | 0.34332 | 0.55389 | 0.37994 | 0.16479 | 0.027465 | 0.48065 | 122.4335 | 0.077819 | 122.4792 | 122.4014 | 122.4426 | -0.13733 | -122.4976 | 122.3511 | 122.3969 | 122.3511 | 118.7668
1965.8594 | 122.6349 | -122.3282 | 0.064087 | -0.0016786 | -0.0029438 | -0.034791 | -0.0019717 | -0.019976 | -0.029463 | -0.023246 | 0.008606 | -0.0093139 | 0.063121 | 0.04921 | -0.019649 | -0.0081774 | -0.018023 | 0 | -0.018311 | 0.009155 | 0.050354 | 0.22888 | 0.1236 | 0.10986 | -3.6484 | 0.036621 | -122.3785 | 0.091553 | -121.8567 | -121.9299 | -121.7743 | 122.3373 | -0.082398 | -0.013733 | 122.5571 | 122.438 | 122.4518 | 0.10071 | 0.11444 | -0.050354 | -0.027466 | 0.027466 | 0.4715 | 0.55389 | 0.39825 | 0.60425 | 0.44861 | 0.21973 | 0.041199 | 0.52185 | 122.4701 | -0.027466 | 122.4152 | 122.3099 | 122.3648 | -0.054932 | -122.4426 | 122.3785 | 122.4197 | 122.3282 | 118.6798
1967.6562 | 122.6166 | -122.3648 | 0.07782 | 0.0059509 | -0.003371 | -0.033936 | -0.00026266 | -0.022112 | -0.029463 | -0.021751 | 0.0055542 | -0.0099549 | 0.069103 | 0.046433 | -0.01559 | -0.0071094 | -0.017383 | -0.045776 | 0.013733 | -0.022888 | -0.027466 | 0.11444 | 0.018311 | 0.027466 | -3.8498 | 0.036621 | -122.3969 | 0.10071 | -121.9025 | -121.9757 | -121.788 | 122.3419 | -0.064087 | -0.10529 | 122.4792 | 122.3923 | 122.3831 | 0.050354 | 0.041199 | -0.032044 | -0.041199 | 0.022888 | 0.46234 | 0.57678 | 0.3891 | 0.60883 | 0.42114 | 0.13733 | -0.004578 | 0.49438 | 122.4976 | 0.036621 | 122.4335 | 122.3785 | 122.4014 | -0.10071 | -122.4747 | 122.3373 | 122.4655 | 122.319 | 118.515
1969.3906 | 122.5525 | -122.3969 | 0.09613 | 0.036468 | -0.0020892 | -0.033082 | 0.00059174 | -0.019335 | -0.029249 | -0.020897 | 0.017761 | -0.0052551 | 0.066112 | 0.04152 | -0.021358 | -0.009032 | -0.016101 | -0.059509 | 0.054932 | -0.054932 | -0.054932 | 0.068665 | -0.004578 | 0.004578 | -3.9368 | 0.07782 | -122.4472 | -0.009155 | -121.9666 | -122.0352 | -121.8658 | 122.3419 | -0.041198 | -0.15106 | 122.4655 | 122.4014 | 122.3923 | 0.05951 | 0.050354 | -0.050354 | -0.01831 | -0.10528 | 0.4303 | 0.53101 | 0.36163 | 0.58136 | 0.41199 | 0.1236 | 0 | 0.48065 | 122.438 | 0.10986 | 122.525 | 122.4518 | 122.4747 | -0.15106 | -122.5433 | 122.3419 | 122.3877 | 122.3373 | 118.4601
1971.1562 | 122.5159 | -122.374 | 0.091553 | 0.01358 | -0.00273 | -0.035859 | -0.0023989 | -0.020189 | -0.029463 | -0.022605 | 0.0025024 | -0.0086731 | 0.066112 | 0.041733 | -0.018154 | -0.0098864 | -0.016314 | -0.036621 | 0.022888 | -0.036621 | -0.045776 | 0.07782 | -0.032043 | -0.018311 | -4.0649 | 0.059509 | -122.4106 | 0 | -121.9894 | -122.081 | -121.8842 | 122.3373 | -0.068665 | -0.13733 | 122.4518 | 122.3557 | 122.3419 | 0.01831 | 0.004578 | -0.036621 | -0.032044 | -0.091553 | 0.38452 | 0.48981 | 0.29297 | 0.52643 | 0.32959 | 0.11444 | -0.009155 | 0.42114 | 122.4106 | 0.059509 | 122.4701 | 122.3969 | 122.4335 | -0.12817 | -122.5021 | 122.3282 | 122.374 | 122.3373 | 118.309
1972.9375 | 122.5342 | -122.3923 | 0.086975 | 0.0059509 | -0.003371 | -0.035859 | -0.0013309 | -0.015703 | -0.028822 | -0.02346 | 0.0025024 | -0.0088867 | 0.063549 | 0.048142 | -0.023067 | -0.011382 | -0.014392 | -0.068665 | 0.018311 | -0.022888 | -0.07782 | 0.07782 | -0.018311 | -0.004578 | -4.2297 | 0.073242 | -122.438 | -0.027466 | -121.9849 | -122.0673 | -121.8842 | 122.3694 | -0.068664 | -0.16479 | 122.4701 | 122.3877 | 122.374 | 0.01831 | 0.004577 | -0.045776 | -0.013733 | -0.11444 | 0.40741 | 0.50812 | 0.32501 | 0.55389 | 0.37079 | 0.10071 | -0.054932 | 0.45319 | 122.4106 | 0.041199 | 122.5113 | 122.4106 | 122.4655 | -0.10986 | -122.525 | 122.3145 | 122.3648 | 122.3236 | 118.1625
1974.7188 | 122.612 | -122.3602 | 0.091553 | 0.02121 | -0.0042254 | -0.035004 | -0.00090366 | -0.015062 | -0.028181 | -0.020897 | 0.0055542 | -0.0076049 | 0.063762 | 0.050492 | -0.018154 | -0.0081774 | -0.017596 | -0.032043 | 0.018311 | -0.027466 | -0.013733 | 0.12817 | 0.054932 | 0.054932 | -4.2938 | 0.041199 | -122.3969 | 0.054932 | -121.9025 | -121.9849 | -121.8063 | 122.3328 | -0.073242 | -0.10529 | 122.4884 | 122.4152 | 122.4152 | 0.082398 | 0.082398 | -0.036622 | -0.050354 | -0.036621 | 0.45776 | 0.55389 | 0.37537 | 0.59052 | 0.41199 | 0.15564 | 0.013733 | 0.49438 | 122.4518 | 0.045777 | 122.4381 | 122.3785 | 122.4014 | -0.11902 | -122.4884 | 122.3465 | 122.4152 | 122.3282 | 118.0664
1976.4375 | 122.5204 | -122.4014 | 0.091553 | 0.01358 | -0.0018756 | -0.033509 | 0.00037814 | -0.016558 | -0.029249 | -0.024742 | 0.0025024 | -0.0082459 | 0.065471 | 0.038315 | -0.018367 | -0.0094592 | -0.014178 | -0.064087 | 0.036621 | -0.036621 | -0.09613 | 0.004578 | -0.073242 | -0.054932 | -4.4586 | 0.068665 | -122.406 | -0.022888 | -122.0123 | -122.0993 | -121.8933 | 122.3648 | -0.054932 | -0.18768 | 122.406 | 122.3465 | 122.3282 | -0.018311 | -0.036621 | -0.004578 | -0.022888 | -0.11444 | 0.3891 | 0.50812 | 0.30212 | 0.5127 | 0.3067 | 0.041199 | -0.059509 | 0.39368 | 122.3831 | 0.073242 | 122.4747 | 122.438 | 122.4701 | -0.12817 | -122.4976 | 122.3053 | 122.3785 | 122.3373 | 117.9428
1978.2344 | 122.6395 | -122.3465 | 0.064087 | -0.0016786 | -0.0010212 | -0.035431 | 0.0010189 | -0.019121 | -0.02754 | -0.023033 | 0.0055542 | -0.0097411 | 0.062481 | 0.04152 | -0.014736 | -0.0086048 | -0.012042 | -0.022888 | 0.013733 | -0.027466 | 0.013733 | 0.15564 | 0.041199 | 0.059509 | -4.454 | 0.027466 | -122.3831 | 0.10529 | -121.8933 | -121.962 | -121.7743 | 122.319 | -0.050354 | -0.050354 | 122.5021 | 122.406 | 122.3877 | 0.086975 | 0.068665 | -0.036621 | -0.036621 | 0.041199 | 0.45319 | 0.5722 | 0.38452 | 0.60883 | 0.42114 | 0.18311 | 0.041199 | 0.48981 | 122.4884 | 0.041199 | 122.4106 | 122.3602 | 122.374 | -0.091553 | -122.4472 | 122.3602 | 122.4518 | 122.3236 | 117.8925
1980 | 122.6257 | -122.3511 | 0.086975 | 0.01358 | -0.00508 | -0.035859 | -0.0028263 | -0.020617 | -0.029249 | -0.023674 | 0.008606 | -0.0091003 | 0.065685 | 0.049851 | -0.019222 | -0.007323 | -0.016528 | -0.050354 | -0.009155 | -0.004578 | -0.018311 | 0.11444 | 0.041199 | 0.059509 | -4.6371 | 0.032043 | -122.4106 | 0.064087 | -121.9116 | -121.9528 | -121.8246 | 122.3465 | -0.09613 | -0.10529 | 122.4655 | 122.4106 | 122.3923 | 0.064087 | 0.045777 | -0.059509 | -0.054932 | -0.022888 | 0.43945 | 0.52643 | 0.39825 | 0.58594 | 0.45776 | 0.11902 | -0.013733 | 0.49896 | 122.4747 | -0.004577 | 122.4426 | 122.3419 | 122.3831 | -0.091553 | -122.4976 | 122.3328 | 122.4152 | 122.3007 | 117.7139
1981.7656 | 122.6532 | -122.3557 | 0.054932 | 0.036468 | -0.0025164 | -0.032868 | 0.00059174 | -0.013781 | -0.026899 | -0.02346 | 0.011658 | -0.0078185 | 0.066112 | 0.04686 | -0.015377 | -0.006682 | -0.018237 | 0.032043 | 0.009155 | -0.009155 | 0.086975 | 0.21057 | 0.086975 | 0.09613 | -4.7699 | 0.036621 | -122.3923 | 0.10986 | -121.8704 | -121.9482 | -121.7926 | 122.3465 | -0.045777 | 0.032043 | 122.5662 | 122.4518 | 122.4426 | 0.10528 | 0.09613 | -0.036621 | -0.018311 | 0.054931 | 0.48523 | 0.56305 | 0.40741 | 0.59967 | 0.44403 | 0.21973 | 0.09613 | 0.52185 | 122.5021 | 0.01831 | 122.4289 | 122.3648 | 122.3923 | -0.064087 | -122.4472 | 122.4426 | 122.4655 | 122.3877 | 117.5858
1983.5625 | 122.5388 | -122.3969 | 0.11444 | 0.0059509 | -0.0031574 | -0.036072 | -0.00047626 | -0.01848 | -0.028181 | -0.026878 | 0.0025024 | -0.0063233 | 0.065044 | 0.039597 | -0.022212 | -0.010314 | -0.015033 | -0.086975 | 0.036621 | -0.054932 | -0.059509 | 0.054932 | 0.009155 | -0.004578 | -4.9759 | 0.073242 | -122.4197 | -0.027466 | -121.9894 | -122.0673 | -121.907 | 122.3419 | -0.07782 | -0.17395 | 122.4518 | 122.3923 | 122.406 | 0.050354 | 0.064087 | -0.022888 | -0.041199 | -0.14191 | 0.40741 | 0.48981 | 0.32959 | 0.5127 | 0.35248 | 0.10986 | -0.004577 | 0.4303 | 122.3923 | 0.091553 | 122.493 | 122.4335 | 122.4701 | -0.16937 | -122.5342 | 122.3373 | 122.3694 | 122.3099 | 117.421
1985.2812 | 122.6486 | -122.3648 | 0.064087 | 0.044098 | -0.0040118 | -0.032654 | 0.0018735 | -0.012926 | -0.026686 | -0.022605 | 0.020813 | -0.0071777 | 0.065471 | 0.046647 | -0.017299 | -0.007323 | -0.016742 | 0.050354 | 0 | -0.013733 | 0.07782 | 0.21973 | 0.091553 | 0.09613 | -4.9347 | 0.050354 | -122.4014 | 0.10071 | -121.875 | -121.9711 | -121.788 | 122.3511 | -0.064087 | 0.013733 | 122.5845 | 122.4609 | 122.4564 | 0.10986 | 0.10529 | -0.036621 | -0.013733 | 0.036621 | 0.48981 | 0.57678 | 0.39368 | 0.6134 | 0.4303 | 0.23346 | 0.091553 | 0.52643 | 122.5021 | 0.013733 | 122.4518 | 122.3648 | 122.4152 | -0.07782 | -122.4655 | 122.4426 | 122.4655 | 122.4152 | 117.4301
1987.0781 | 122.6669 | -122.3694 | 0.064087 | 0.01358 | -0.0042254 | -0.034577 | -0.00090366 | -0.019976 | -0.026258 | -0.026023 | 0.0025024 | -0.0088867 | 0.067394 | 0.044297 | -0.02029 | -0.0071094 | -0.014178 | -0.022888 | 0 | -0.013733 | 0.018311 | 0.16937 | 0.07782 | 0.082397 | -5.1041 | 0.036621 | -122.4106 | 0.07782 | -121.8613 | -121.9391 | -121.8063 | 122.3557 | -0.064087 | -0.045776 | 122.5388 | 122.4518 | 122.4472 | 0.09613 | 0.091553 | -0.041198 | -0.027466 | 0.013733 | 0.50812 | 0.56305 | 0.4303 | 0.60425 | 0.4715 | 0.18311 | 0.032044 | 0.54932 | 122.4884 | 0.013733 | 122.4472 | 122.3694 | 122.406 | -0.07782 | -122.4747 | 122.3877 | 122.4472 | 122.3465 | 117.2653
1988.7812 | 122.5296 | -122.3923 | 0.11444 | 0.028839 | -0.004439 | -0.0365 | 0.0016599 | -0.021044 | -0.02754 | -0.02346 | 0.011658 | -0.0080321 | 0.066326 | 0.038743 | -0.020503 | -0.011382 | -0.019305 | -0.059509 | 0.059509 | -0.041199 | -0.068665 | 0.068665 | -0.004578 | -0.009155 | -5.2872 | 0.086975 | -122.4609 | -0.032043 | -121.9986 | -122.081 | -121.8796 | 122.3511 | -0.054932 | -0.18311 | 122.4609 | 122.3831 | 122.3877 | 0.032044 | 0.036621 | -0.068664 | -0.027466 | -0.14648 | 0.39368 | 0.5127 | 0.31128 | 0.58136 | 0.37994 | 0.10986 | -0.027466 | 0.46234 | 122.4289 | 0.10071 | 122.5479 | 122.4518 | 122.4792 | -0.15564 | -122.5754 | 122.3236 | 122.3602 | 122.3328 | 117.1051
1990.5625 | 122.5891 | -122.3831 | 0.091553 | -0.0016786 | -0.004439 | -0.035431 | -0.00090366 | -0.015917 | -0.02754 | -0.022819 | 0.0055542 | -0.0084595 | 0.065471 | 0.051987 | -0.021999 | -0.0096728 | -0.01546 | 0.004578 | -0.013733 | -0.013733 | 0.045776 | 0.19226 | 0.091553 | 0.082397 | -5.3696 | 0.041199 | -122.406 | 0.032043 | -121.9162 | -121.9849 | -121.8475 | 122.3694 | -0.10529 | -0.045777 | 122.5754 | 122.4655 | 122.4747 | 0.09613 | 0.10529 | -0.022888 | -0.050354 | -0.05951 | 0.46692 | 0.53558 | 0.39825 | 0.55847 | 0.42114 | 0.20599 | 0.059509 | 0.48981 | 122.438 | 0 | 122.4472 | 122.3694 | 122.4243 | -0.10529 | -122.4976 | 122.4289 | 122.4152 | 122.3877 | 117.0135
1992.2812 | 122.5616 | -122.3923 | 0.10071 | 0.0059509 | -0.0031574 | -0.035004 | -0.0019717 | -0.021258 | -0.028608 | -0.024742 | 0.0055542 | -0.0093139 | 0.065044 | 0.044083 | -0.022212 | -0.0098864 | -0.017596 | 0.004578 | 0 | -0.018311 | 0.009155 | 0.16479 | 0.068665 | 0.054932 | -5.4977 | 0.064087 | -122.438 | 0.004578 | -121.9666 | -122.0215 | -121.875 | 122.374 | -0.10071 | -0.091553 | 122.5571 | 122.4472 | 122.4609 | 0.073243 | 0.086976 | -0.045776 | -0.036621 | -0.09613 | 0.42572 | 0.51727 | 0.37079 | 0.56305 | 0.41657 | 0.18311 | 0.027466 | 0.4715 | 122.4426 | 0.018311 | 122.5021 | 122.3923 | 122.4564 | -0.11902 | -122.5388 | 122.4014 | 122.3969 | 122.3969 | 116.8945
1994.0625 | 122.6486 | -122.374 | 0.086975 | 0.0059509 | -0.003371 | -0.035218 | -0.0032535 | -0.020403 | -0.029249 | -0.023887 | 0.0055542 | -0.0095275 | 0.062481 | 0.049851 | -0.019435 | -0.0088184 | -0.013751 | -0.050354 | 0.013733 | 0 | 0.018311 | 0.14648 | 0.068665 | 0.082397 | -5.6854 | 0.036621 | -122.4243 | 0.07782 | -121.875 | -121.9482 | -121.8109 | 122.374 | -0.073242 | -0.068664 | 122.5204 | 122.4564 | 122.4426 | 0.082397 | 0.068665 | -0.050354 | -0.050354 | -0.009155 | 0.49896 | 0.56305 | 0.42572 | 0.6134 | 0.47607 | 0.14648 | 0.018311 | 0.54932 | 122.5021 | 0.013733 | 122.4609 | 122.3877 | 122.4106 | -0.086975 | -122.5113 | 122.3923 | 122.4518 | 122.3236 | 116.6885
1995.8281 | 122.6532 | -122.3923 | 0.082397 | -0.0016786 | -0.004439 | -0.037781 | -0.0019717 | -0.02083 | -0.030745 | -0.021751 | -0.00054937 | -0.0080321 | 0.064403 | 0.047928 | -0.020076 | -0.009032 | -0.016955 | -0.013733 | 0.004578 | -0.004578 | 0.045776 | 0.1831 | 0.086975 | 0.091553 | -5.7404 | 0.036621 | -122.3831 | 0.086975 | -121.8704 | -121.9345 | -121.788 | 122.3877 | -0.077819 | -0.036621 | 122.5754 | 122.4838 | 122.4792 | 0.096131 | 0.091553 | 0.009155 | -0.045776 | 0.004578 | 0.52185 | 0.60425 | 0.45776 | 0.59509 | 0.44861 | 0.18768 | 0.050354 | 0.5127 | 122.4701 | 0.009156 | 122.4197 | 122.3969 | 122.4289 | -0.086975 | -122.4655 | 122.438 | 122.4792 | 122.3785 | 116.6519
1997.5469 | 122.6349 | -122.3602 | 0.07782 | 0.01358 | -0.0048664 | -0.035645 | -0.0030399 | -0.014422 | -0.029036 | -0.022392 | 0.0055542 | -0.0078185 | 0.065044 | 0.038743 | -0.019435 | -0.0101 | -0.016528 | -0.027466 | 0.009155 | -0.018311 | 0.004578 | 0.14191 | 0.064087 | 0.068665 | -5.8685 | 0.041199 | -122.4106 | 0.07782 | -121.8796 | -121.9666 | -121.8063 | 122.3419 | -0.068665 | -0.073242 | 122.5021 | 122.4289 | 122.4243 | 0.086976 | 0.082398 | -0.050354 | -0.036621 | 0 | 0.48065 | 0.55389 | 0.39368 | 0.60425 | 0.44403 | 0.16022 | 0.022889 | 0.53101 | 122.4884 | 0.027466 | 122.4518 | 122.3694 | 122.4014 | -0.096131 | -122.4884 | 122.3648 | 122.438 | 122.3328 | 116.4917
1999.3281 | 122.5433 | -122.3969 | 0.1236 | 0.0059509 | -0.004439 | -0.0365 | -0.00090366 | -0.018053 | -0.029249 | -0.023674 | 0.011658 | -0.0054687 | 0.064403 | 0.035966 | -0.021572 | -0.010527 | -0.019519 | -0.07782 | 0.036621 | -0.050354 | -0.054932 | 0.073242 | 0.004578 | 0.004578 | -6.0242 | 0.091553 | -122.4701 | -0.045776 | -121.994 | -122.0673 | -121.9025 | 122.3465 | -0.086975 | -0.17853 | 122.4701 | 122.4014 | 122.4014 | 0.054932 | 0.054932 | -0.073242 | -0.032043 | -0.16937 | 0.40283 | 0.49438 | 0.32959 | 0.56763 | 0.40283 | 0.1236 | -0.004578 | 0.47607 | 122.4243 | 0.086975 | 122.5616 | 122.4335 | 122.4884 | -0.17395 | -122.5937 | 122.3419 | 122.3511 | 122.319 | 116.3727
2001.0469 | 122.6212 | -122.3923 | 0.07782 | 0.02121 | -0.00508 | -0.035004 | -0.0021853 | -0.01848 | -0.027967 | -0.024101 | 0.008606 | -0.0091003 | 0.062908 | 0.047501 | -0.01794 | -0.008391 | -0.017596 | -0.036621 | 0.004578 | 0 | -0.004578 | 0.1236 | 0.032043 | 0.050354 | -6.189 | 0.041199 | -122.4106 | 0.045776 | -121.9208 | -121.9986 | -121.8384 | 122.3923 | -0.073242 | -0.082398 | 122.5159 | 122.4426 | 122.4243 | 0.050354 | 0.032043 | -0.01831 | -0.036621 | -0.032044 | 0.4715 | 0.55389 | 0.39368 | 0.5722 | 0.41199 | 0.1236 | -0.004578 | 0.48981 | 122.4564 | 0.004578 | 122.4518 | 122.3969 | 122.4335 | -0.07782 | -122.4884 | 122.3877 | 122.438 | 122.3557 | 116.2033
2002.8281 | 122.5616 | -122.406 | 0.09613 | 0.0059509 | -0.0046526 | -0.035645 | -0.0017581 | -0.016771 | -0.032026 | -0.02346 | -0.00054937 | -0.0071777 | 0.063121 | 0.043015 | -0.019649 | -0.010741 | -0.016742 | 0.009155 | -0.004578 | -0.009155 | 0.013733 | 0.16022 | 0.07782 | 0.073242 | -6.2531 | 0.068665 | -122.4335 | 0.018311 | -121.9437 | -122.0352 | -121.8704 | 122.3969 | -0.10071 | -0.082397 | 122.5662 | 122.4792 | 122.4838 | 0.082397 | 0.086975 | -0.027466 | -0.027465 | -0.077819 | 0.46234 | 0.53558 | 0.37079 | 0.56305 | 0.39825 | 0.16937 | 0.022888 | 0.48981 | 122.4518 | 0.004577 | 122.5021 | 122.4014 | 122.4747 | -0.10528 | -122.5296 | 122.4197 | 122.4243 | 122.4152 | 116.153
2004.6094 | 122.6624 | -122.3648 | 0.073242 | -0.0016786 | -0.0052936 | -0.033936 | -0.0011173 | -0.01848 | -0.029036 | -0.024528 | 0.0025024 | -0.011878 | 0.063762 | 0.045579 | -0.018581 | -0.0094592 | -0.014605 | -0.032043 | 0.013733 | -0.013733 | 0.018311 | 0.16479 | 0.068665 | 0.082397 | -6.4178 | 0.050354 | -122.4243 | 0.086975 | -121.875 | -121.9482 | -121.8063 | 122.3511 | -0.059509 | -0.054931 | 122.5296 | 122.4472 | 122.4335 | 0.09613 | 0.082398 | -0.059509 | -0.022888 | 0.013733 | 0.48981 | 0.55847 | 0.41657 | 0.61798 | 0.47607 | 0.17853 | 0.032044 | 0.54932 | 122.5113 | 0.027466 | 122.4747 | 122.3785 | 122.4152 | -0.086975 | -122.4976 | 122.3831 | 122.4518 | 122.3328 | 115.947
2006.3906 | 122.5388 | -122.406 | 0.11444 | 0.0059509 | -0.0037982 | -0.036072 | 0.0018735 | -0.015703 | -0.028395 | -0.021965 | 0.0025024 | -0.0037597 | 0.066326 | 0.043229 | -0.016017 | -0.010527 | -0.019732 | -0.050354 | 0.041199 | -0.027466 | -0.09613 | 0.032043 | -0.064087 | -0.036621 | -6.6605 | 0.059509 | -122.4335 | -0.013733 | -122.0261 | -122.1085 | -121.8887 | 122.3785 | -0.073242 | -0.21057 | 122.438 | 122.3694 | 122.3419 | -0.009155 | -0.036621 | -0.027466 | -0.054932 | -0.12817 | 0.37994 | 0.51727 | 0.29755 | 0.54474 | 0.32501 | 0.059509 | -0.068664 | 0.40741 | 122.4197 | 0.068665 | 122.493 | 122.4472 | 122.4655 | -0.14191 | -122.5479 | 122.3099 | 122.3923 | 122.3557 | 115.7455
2008.1719 | 122.6166 | -122.3831 | 0.054932 | 0.028839 | -0.0048664 | -0.035645 | -0.0011173 | -0.019549 | -0.027754 | -0.019401 | 0.0055542 | -0.0088867 | 0.065899 | 0.044297 | -0.015804 | -0.0088184 | -0.014178 | -0.022888 | 0.018311 | 0 | 0.018311 | 0.16937 | 0.036621 | 0.059509 | -6.7383 | 0.041199 | -122.4518 | 0.050354 | -121.9391 | -122.0123 | -121.8475 | 122.3831 | -0.036621 | -0.036621 | 122.5525 | 122.4426 | 122.4197 | 0.059509 | 0.036621 | -0.068664 | -0.013733 | -0.004578 | 0.44403 | 0.53558 | 0.37079 | 0.60425 | 0.43945 | 0.16937 | 0.018311 | 0.51269 | 122.5021 | 0.018311 | 122.493 | 122.4014 | 122.4243 | -0.054932 | -122.5067 | 122.4014 | 122.4335 | 122.3602 | 115.6448
2009.9531 | 122.5708 | -122.3785 | 0.09613 | 0.02121 | -0.0023028 | -0.0365 | 0.0023007 | -0.015276 | -0.030104 | -0.024314 | 0.0055542 | -0.0056823 | 0.063549 | 0.040452 | -0.020076 | -0.008391 | -0.016955 | -0.027466 | 0.041199 | -0.027466 | 0.004578 | 0.13275 | 0.027466 | 0.018311 | -6.8665 | 0.050354 | -122.4335 | 0.022888 | -121.962 | -122.0535 | -121.875 | 122.3511 | -0.054931 | -0.091552 | 122.5113 | 122.3969 | 122.406 | 0.045777 | 0.054932 | -0.054932 | -0.045776 | -0.073242 | 0.41657 | 0.50354 | 0.32501 | 0.55847 | 0.37994 | 0.16022 | 0.032044 | 0.4715 | 122.4564 | 0.068665 | 122.4838 | 122.4197 | 122.4289 | -0.1236 | -122.5296 | 122.3831 | 122.4014 | 122.3511 | 115.5121
2011.6719 | 122.6669 | -122.374 | 0.059509 | 0.0059509 | -0.0012348 | -0.032868 | -4.906e-05 | -0.015917 | -0.03224 | -0.025169 | 0.0025024 | -0.0084595 | 0.063121 | 0.043229 | -0.014949 | -0.0049732 | -0.018451 | 0.004578 | 0.018311 | 0.009155 | 0.050354 | 0.18768 | 0.050354 | 0.073242 | -7.045 | 0.032043 | -122.406 | 0.11902 | -121.8842 | -121.9482 | -121.7926 | 122.3831 | -0.041198 | -0.009155 | 122.5616 | 122.4472 | 122.4243 | 0.064087 | 0.041199 | -0.032044 | -0.027466 | 0.05951 | 0.48981 | 0.58136 | 0.42572 | 0.6134 | 0.45776 | 0.17853 | 0.041199 | 0.52185 | 122.525 | 0.009156 | 122.438 | 122.3923 | 122.406 | -0.050354 | -122.4655 | 122.4243 | 122.493 | 122.3785 | 115.329
2013.4688 | 122.5342 | -122.4197 | 0.11444 | 0.01358 | -0.0037982 | -0.035431 | -0.00047626 | -0.018908 | -0.031813 | -0.020256 | 0.008606 | -0.0080321 | 0.065258 | 0.043656 | -0.021358 | -0.0096728 | -0.016314 | -0.036621 | 0.018311 | -0.022888 | -0.036621 | 0.091553 | 0 | 0.013733 | -7.3151 | 0.064087 | -122.4564 | -0.027466 | -121.9986 | -122.081 | -121.9208 | 122.3969 | -0.09613 | -0.15106 | 122.5113 | 122.4335 | 122.4197 | 0.036621 | 0.022888 | -0.036621 | -0.050354 | -0.14191 | 0.42114 | 0.49896 | 0.33875 | 0.53558 | 0.37537 | 0.11444 | -0.013733 | 0.45776 | 122.4289 | 0.041199 | 122.5204 | 122.4381 | 122.4838 | -0.13733 | -122.5708 | 122.3831 | 122.3923 | 122.3831 | 115.1047
2015.1875 | 122.6761 | -122.3694 | 0.059509 | 0.0059509 | -0.004439 | -0.03415 | -0.0013309 | -0.019762 | -0.030745 | -0.021324 | 0.0055542 | -0.0091003 | 0.06483 | 0.043015 | -0.019649 | -0.0079638 | -0.014819 | -0.013733 | 0.004578 | 0 | 0.041199 | 0.20599 | 0.10529 | 0.10529 | -7.3471 | 0.036621 | -122.4335 | 0.10071 | -121.8704 | -121.9391 | -121.788 | 122.3694 | -0.054931 | -0.01831 | 122.5754 | 122.4747 | 122.4747 | 0.10529 | 0.10529 | -0.064087 | -0.022888 | 0.041199 | 0.49896 | 0.58136 | 0.4303 | 0.64545 | 0.49438 | 0.20599 | 0.041199 | 0.56305 | 122.5342 | 0.004578 | 122.4701 | 122.374 | 122.406 | -0.059509 | -122.493 | 122.4106 | 122.4701 | 122.3557 | 115.0223
2016.9531 | 122.5937 | -122.4197 | 0.10529 | 0.036468 | -0.0035846 | -0.035859 | 0.0016599 | -0.016131 | -0.028395 | -0.021324 | 0.011658 | -0.0067505 | 0.066539 | 0.038529 | -0.019649 | -0.0094592 | -0.016528 | -0.009155 | 0.050354 | -0.045776 | -0.027466 | 0.10986 | 0.027466 | 0.027466 | -7.5531 | 0.07782 | -122.4609 | 0.022888 | -121.9482 | -122.0444 | -121.8613 | 122.374 | -0.054932 | -0.13275 | 122.5296 | 122.4472 | 122.4472 | 0.073242 | 0.073242 | -0.041198 | -0.027466 | -0.082398 | 0.4715 | 0.55847 | 0.37537 | 0.59967 | 0.41656 | 0.15564 | 0.01831 | 0.5127 | 122.4838 | 0.09613 | 122.5388 | 122.4701 | 122.4976 | -0.15106 | -122.5662 | 122.3923 | 122.4426 | 122.4106 | 114.8666
2018.7344 | 122.6761 | -122.374 | 0.068665 | 0.0059509 | -0.0040118 | -0.034363 | -0.00069006 | -0.018053 | -0.027967 | -0.022392 | 0.0055542 | -0.010169 | 0.065258 | 0.04451 | -0.019008 | -0.009032 | -0.017596 | -0.018311 | 0.004578 | -0.013733 | 0.041199 | 0.18768 | 0.091553 | 0.10529 | -7.7454 | 0.032043 | -122.4106 | 0.10071 | -121.875 | -121.9345 | -121.8063 | 122.3602 | -0.064087 | -0.027466 | 122.5616 | 122.4792 | 122.4655 | 0.11902 | 0.10529 | -0.036621 | -0.036622 | 0.032043 | 0.49896 | 0.56763 | 0.43945 | 0.60425 | 0.47607 | 0.20142 | 0.054932 | 0.53558 | 122.5113 | 0.018311 | 122.4426 | 122.3785 | 122.406 | -0.082398 | -122.4792 | 122.4152 | 122.4747 | 122.3557 | 114.6286
2020.5156 | 122.612 | -122.374 | 0.086975 | 0.036468 | -0.0025164 | -0.032441 | -4.906e-05 | -0.017412 | -0.028181 | -0.027092 | 0.0055542 | -0.0073913 | 0.065899 | 0.046219 | -0.019008 | -0.0088184 | -0.013537 | -0.022888 | 0.009155 | -0.004578 | 0.009155 | 0.13733 | 0.027466 | 0.041199 | -7.9834 | 0.036621 | -122.4472 | 0.041199 | -121.9482 | -122.0169 | -121.8475 | 122.3694 | -0.07782 | -0.07782 | 122.5113 | 122.4152 | 122.4014 | 0.045777 | 0.032044 | -0.073243 | -0.050354 | -0.045776 | 0.42572 | 0.52643 | 0.35706 | 0.59967 | 0.4303 | 0.14191 | 0.013733 | 0.49896 | 122.4884 | 0.013733 | 122.4838 | 122.3831 | 122.4106 | -0.091553 | -122.5342 | 122.3831 | 122.4152 | 122.3511 | 114.3906
2022.2344 | 122.6257 | -122.3923 | 0.07782 | 0.02121 | -0.0018756 | -0.03415 | 0.0018735 | -0.014208 | -0.028395 | -0.023246 | 0.011658 | -0.0071777 | 0.066326 | 0.048783 | -0.018794 | -0.0092456 | -0.013324 | -0.013733 | 0 | -0.004578 | 0.022888 | 0.14648 | 0.041199 | 0.059509 | -8.1161 | 0.050354 | -122.4243 | 0.050354 | -121.9345 | -122.0078 | -121.8613 | 122.3877 | -0.07782 | -0.054932 | 122.5388 | 122.4518 | 122.4335 | 0.064087 | 0.045777 | -0.032043 | -0.027466 | -0.027466 | 0.45776 | 0.53101 | 0.38452 | 0.56305 | 0.41657 | 0.15106 | 0.027466 | 0.48981 | 122.4747 | 0.004578 | 122.4747 | 122.3923 | 122.4426 | -0.082398 | -122.5021 | 122.4152 | 122.4426 | 122.3785 | 114.2761
2024.0312 | 122.6761 | -122.3557 | 0.068665 | -0.0016786 | -0.00273 | -0.037568 | -0.0015445 | -0.019762 | -0.029249 | -0.022178 | 0.008606 | -0.0084595 | 0.065685 | 0.045792 | -0.020076 | -0.0092456 | -0.015033 | -0.004578 | -0.004578 | -0.018311 | 0.045776 | 0.18768 | 0.10529 | 0.10529 | -8.1894 | 0.027466 | -122.4197 | 0.10986 | -121.8475 | -121.9254 | -121.8155 | 122.3373 | -0.073243 | -0.022889 | 122.5433 | 122.4609 | 122.4609 | 0.1236 | 0.1236 | -0.064087 | -0.041199 | 0.041198 | 0.50812 | 0.54016 | 0.4303 | 0.60425 | 0.49439 | 0.20599 | 0.064087 | 0.57221 | 122.5296 | 0.013733 | 122.4472 | 122.3511 | 122.3831 | -0.086976 | -122.4884 | 122.4014 | 122.4655 | 122.3511 | 114.1663
2025.7344 | 122.6166 | -122.374 | 0.068665 | 0.02121 | -0.0029438 | -0.036713 | -0.00026266 | -0.018267 | -0.028181 | -0.025383 | 0.008606 | -0.0078185 | 0.065471 | 0.044297 | -0.019222 | -0.008391 | -0.017169 | -0.022888 | 0.009155 | -0.018311 | 0 | 0.14648 | 0.054932 | 0.054932 | -8.4961 | 0.022888 | -122.4335 | 0.022888 | -121.9437 | -122.0123 | -121.8613 | 122.3557 | -0.05951 | -0.068665 | 122.5204 | 122.4289 | 122.4289 | 0.073243 | 0.073243 | -0.05951 | -0.045777 | -0.045777 | 0.4303 | 0.5127 | 0.36163 | 0.5722 | 0.42114 | 0.16479 | 0.018311 | 0.48981 | 122.4564 | 0.027466 | 122.4564 | 122.3831 | 122.3969 | -0.086976 | -122.5021 | 122.374 | 122.3969 | 122.3511 | 113.8779
2027.5156 | 122.58 | -122.4243 | 0.10529 | 0.036468 | -0.00080738 | -0.036286 | 0.0020871 | -0.016558 | -0.029249 | -0.022819 | 0.014709 | -0.0052551 | 0.065471 | 0.047928 | -0.018794 | -0.0077502 | -0.018664 | -0.050354 | 0.064087 | -0.050354 | -0.036621 | 0.086975 | 0.013733 | 0.032043 | -8.638 | 0.059509 | -122.4564 | 0.004578 | -121.9528 | -122.0444 | -121.8704 | 122.374 | -0.041199 | -0.14191 | 122.5113 | 122.4564 | 122.438 | 0.082397 | 0.064087 | -0.032044 | -0.045777 | -0.10071 | 0.4715 | 0.55389 | 0.37994 | 0.58594 | 0.41199 | 0.13733 | 0.013733 | 0.50354 | 122.4609 | 0.11444 | 122.5159 | 122.4884 | 122.4838 | -0.15564 | -122.5616 | 122.3877 | 122.4289 | 122.374 | 113.7863
2029.3281 | 122.6624 | -122.3648 | 0.059509 | 0.0059509 | -0.00273 | -0.034791 | -4.906e-05 | -0.018267 | -0.029676 | -0.022819 | 0.0055542 | -0.0082459 | 0.066112 | 0.040452 | -0.014949 | -0.0071094 | -0.016314 | -0.009155 | 0.022888 | -0.018311 | 0.050354 | 0.1831 | 0.059509 | 0.073242 | -8.7799 | 0.036621 | -122.4335 | 0.11902 | -121.8796 | -121.9757 | -121.7926 | 122.3465 | -0.036621 | -0.009155 | 122.5479 | 122.438 | 122.4243 | 0.091553 | 0.07782 | -0.068665 | -0.022888 | 0.05951 | 0.48523 | 0.5722 | 0.3891 | 0.64087 | 0.45776 | 0.20142 | 0.068665 | 0.55389 | 122.5525 | 0.041199 | 122.4701 | 122.3877 | 122.4014 | -0.07782 | -122.493 | 122.4152 | 122.4838 | 122.3557 | 113.5849
2031.0469 | 122.5296 | -122.4243 | 0.10529 | 0.02121 | -0.0025164 | -0.035859 | -0.00047626 | -0.014849 | -0.027327 | -0.022605 | -0.00054937 | -0.0071777 | 0.067394 | 0.042161 | -0.020717 | -0.012236 | -0.019946 | -0.045776 | 0.050354 | -0.036621 | -0.059509 | 0.045776 | -0.050354 | -0.036621 | -9.0729 | 0.068665 | -122.4426 | -0.032043 | -122.0169 | -122.113 | -121.9208 | 122.3877 | -0.054932 | -0.16479 | 122.4701 | 122.3877 | 122.374 | 0 | -0.013733 | -0.018311 | -0.036621 | -0.13733 | 0.40741 | 0.50354 | 0.31128 | 0.52185 | 0.32959 | 0.082397 | -0.022888 | 0.42572 | 122.4106 | 0.086975 | 122.5113 | 122.4747 | 122.493 | -0.14191 | -122.5479 | 122.3648 | 122.3923 | 122.3785 | 113.3514
2032.8281 | 122.5433 | -122.4197 | 0.10529 | 0.01358 | -0.0046526 | -0.036072 | 0.0010189 | -0.016131 | -0.030958 | -0.021324 | 0.0025024 | -0.0076049 | 0.065044 | 0.03682 | -0.023494 | -0.010527 | -0.012896 | -0.068665 | 0.009155 | -0.036621 | -0.068665 | 0.073242 | -0.004578 | -0.004578 | -9.2331 | 0.07782 | -122.4564 | -0.032043 | -121.9894 | -122.0627 | -121.9254 | 122.3831 | -0.096131 | -0.17395 | 122.493 | 122.4152 | 122.4152 | 0.032043 | 0.032043 | -0.036621 | -0.027466 | -0.13733 | 0.4303 | 0.49439 | 0.35706 | 0.53101 | 0.39368 | 0.10986 | -0.032044 | 0.46692 | 122.4243 | 0.045776 | 122.5342 | 122.4289 | 122.4976 | -0.14191 | -122.5616 | 122.3511 | 122.3877 | 122.3511 | 113.1866
2034.5938 | 122.5433 | -122.4335 | 0.09613 | -0.0016786 | -0.0018756 | -0.033722 | 0.0010189 | -0.018694 | -0.028395 | -0.021324 | -0.00054937 | -0.0050415 | 0.066326 | 0.04451 | -0.017299 | -0.0098864 | -0.018023 | -0.059509 | 0.041199 | -0.036621 | -0.054932 | 0.064087 | -0.054932 | -0.050354 | -9.4711 | 0.073242 | -122.4655 | -0.013733 | -122.0215 | -122.113 | -121.9116 | 122.3969 | -0.054931 | -0.15106 | 122.4976 | 122.3831 | 122.3785 | -0.013733 | -0.018311 | -0.032043 | -0.022888 | -0.10986 | 0.41199 | 0.52185 | 0.32043 | 0.55389 | 0.35248 | 0.10071 | -0.018311 | 0.44403 | 122.4518 | 0.07782 | 122.5388 | 122.4747 | 122.5067 | -0.13275 | -122.5616 | 122.3785 | 122.4197 | 122.374 | 112.9623
2036.3125 | 122.5433 | -122.438 | 0.1236 | 0.0059509 | -0.0031574 | -0.035004 | -4.906e-05 | -0.015703 | -0.028608 | -0.023887 | 0.008606 | -0.0080321 | 0.063549 | 0.043656 | -0.019222 | -0.010527 | -0.016314 | -0.050354 | 0.036621 | -0.027466 | -0.064087 | 0.068665 | -0.022888 | -0.027466 | -9.6497 | 0.082397 | -122.4609 | -0.009155 | -122.0123 | -122.1039 | -121.9254 | 122.4106 | -0.086975 | -0.18768 | 122.5067 | 122.4106 | 122.4152 | 0 | 0.004578 | -0.022888 | -0.041199 | -0.13275 | 0.42572 | 0.5127 | 0.33417 | 0.53558 | 0.35706 | 0.096131 | -0.036621 | 0.44861 | 122.4518 | 0.064087 | 122.5433 | 122.4747 | 122.5204 | -0.15106 | -122.5845 | 122.374 | 122.4289 | 122.3877 | 112.7884
2038.0938 | 122.612 | -122.3969 | 0.091553 | 0.028839 | -0.0035846 | -0.032654 | -0.0013309 | -0.021471 | -0.030531 | -0.021324 | 0.011658 | -0.0091003 | 0.064617 | 0.046647 | -0.018154 | -0.0092456 | -0.018023 | -0.050354 | 0.009155 | -0.009155 | 0.004578 | 0.15564 | 0.032043 | 0.059509 | -9.8511 | 0.041199 | -122.438 | 0.050354 | -121.9254 | -122.0078 | -121.8613 | 122.3877 | -0.082398 | -0.086975 | 122.5525 | 122.4564 | 122.4289 | 0.068664 | 0.041198 | -0.041198 | -0.050354 | -0.041199 | 0.4715 | 0.53558 | 0.3891 | 0.57678 | 0.4303 | 0.16479 | 0.013733 | 0.5127 | 122.4884 | 0.01831 | 122.4792 | 122.406 | 122.4381 | -0.10071 | -122.5296 | 122.4014 | 122.4472 | 122.3465 | 112.5458
2039.8125 | 122.5525 | -122.4335 | 0.1236 | 0.0059509 | -0.0035846 | -0.036286 | -0.00069006 | -0.018267 | -0.029036 | -0.023033 | 0.014709 | -0.0067505 | 0.065471 | 0.044297 | -0.018794 | -0.0081774 | -0.017169 | -0.07782 | 0.045776 | -0.059509 | -0.086975 | 0.07782 | 0 | 0.004578 | -10.0021 | 0.09613 | -122.4747 | -0.050354 | -121.994 | -122.0901 | -121.9162 | 122.374 | -0.07782 | -0.21057 | 122.5113 | 122.438 | 122.4335 | 0.064087 | 0.059509 | -0.041198 | -0.027466 | -0.17395 | 0.43945 | 0.51727 | 0.34332 | 0.55847 | 0.38452 | 0.13733 | -0.027466 | 0.48065 | 122.4243 | 0.10528 | 122.5708 | 122.4792 | 122.5296 | -0.1831 | -122.5983 | 122.3465 | 122.3831 | 122.3557 | 112.4313
2041.6094 | 122.5525 | -122.4289 | 0.082397 | -0.0016786 | -0.0020892 | -0.034791 | -0.00026266 | -0.018053 | -0.030958 | -0.026237 | 0.0025024 | -0.0056823 | 0.068462 | 0.03917 | -0.018794 | -0.0088184 | -0.016742 | -0.022888 | 0.032043 | -0.032043 | -0.027466 | 0.10529 | -0.009155 | -0.009155 | -10.1761 | 0.059509 | -122.4426 | -0.004578 | -121.9894 | -122.0764 | -121.8979 | 122.3969 | -0.050354 | -0.10986 | 122.5342 | 122.4197 | 122.4197 | 0.022888 | 0.022888 | -0.013733 | -0.022888 | -0.086975 | 0.43945 | 0.53101 | 0.35248 | 0.54474 | 0.36621 | 0.13733 | 0.004577 | 0.45319 | 122.438 | 0.064086 | 122.5021 | 122.4609 | 122.4884 | -0.11444 | -122.525 | 122.4014 | 122.4243 | 122.406 | 112.2528
2043.3438 | 122.5342 | -122.4243 | 0.11444 | 0.01358 | -0.0018756 | -0.033295 | 0.0020871 | -0.011644 | -0.028181 | -0.019828 | 0.008606 | -0.0067505 | 0.063976 | 0.044297 | -0.019649 | -0.0096728 | -0.013537 | -0.054932 | 0.045776 | -0.027466 | -0.091553 | 0.009155 | -0.068665 | -0.054932 | -10.5057 | 0.059509 | -122.4655 | -0.013733 | -122.0398 | -122.1222 | -121.9437 | 122.3969 | -0.068665 | -0.20599 | 122.4335 | 122.3694 | 122.3557 | -0.027466 | -0.041199 | -0.041199 | -0.054932 | -0.12817 | 0.38452 | 0.48065 | 0.30212 | 0.52185 | 0.34332 | 0.036621 | -0.064087 | 0.42572 | 122.4518 | 0.073242 | 122.525 | 122.4701 | 122.4838 | -0.14191 | -122.58 | 122.3328 | 122.4106 | 122.3694 | 111.9186
2045.1406 | 122.5937 | -122.4289 | 0.091553 | 0.028839 | -0.0023028 | -0.035645 | 0.00037814 | -0.016131 | -0.030531 | -0.020683 | 0.0025024 | -0.0084595 | 0.066539 | 0.048356 | -0.021144 | -0.0101 | -0.019091 | -0.009155 | 0.041199 | -0.050354 | -0.018311 | 0.13275 | 0.041199 | 0.036621 | -10.4919 | 0.068665 | -122.4609 | 0.045776 | -121.9345 | -122.0261 | -121.8613 | 122.3785 | -0.050354 | -0.10986 | 122.5616 | 122.4655 | 122.4701 | 0.086975 | 0.091553 | -0.032043 | -0.022888 | -0.045777 | 0.49438 | 0.56763 | 0.40283 | 0.59967 | 0.43488 | 0.18311 | 0.032043 | 0.52643 | 122.5067 | 0.091553 | 122.5296 | 122.4701 | 122.4976 | -0.14191 | -122.5525 | 122.4106 | 122.4747 | 122.4197 | 111.937
2046.9219 | 122.6807 | -122.3602 | 0.073242 | 0.01358 | -0.0018756 | -0.035004 | -0.0026127 | -0.018694 | -0.027754 | -0.022178 | 0.0025024 | -0.0099549 | 0.062053 | 0.046219 | -0.018154 | -0.0088184 | -0.01546 | -0.032043 | 0.009155 | -0.004578 | 0.004578 | 0.17853 | 0.086975 | 0.09613 | -10.7483 | 0.041199 | -122.4289 | 0.09613 | -121.8521 | -121.9482 | -121.8063 | 122.3557 | -0.064087 | -0.068664 | 122.5388 | 122.4564 | 122.4472 | 0.10071 | 0.091553 | -0.068665 | -0.032043 | 0.022888 | 0.50812 | 0.55389 | 0.41199 | 0.62256 | 0.48065 | 0.18311 | 0.009156 | 0.57678 | 122.525 | 0.013733 | 122.4701 | 122.3694 | 122.4014 | -0.07782 | -122.5021 | 122.3648 | 122.4564 | 122.3282 | 111.6119
2048.6875 | 122.6761 | -122.3694 | 0.064087 | 0.028839 | -0.0040118 | -0.034577 | 0.00059174 | -0.01848 | -0.028822 | -0.024955 | 0.0025024 | -0.010809 | 0.063121 | 0.043656 | -0.01794 | -0.007323 | -0.015246 | -0.032043 | 0.004578 | -0.004578 | -0.009155 | 0.15564 | 0.068665 | 0.082397 | -10.9909 | 0.036621 | -122.4518 | 0.086975 | -121.8658 | -121.9437 | -121.8063 | 122.3648 | -0.059509 | -0.073242 | 122.525 | 122.4518 | 122.438 | 0.086975 | 0.073243 | -0.082397 | -0.027466 | 0.022888 | 0.50354 | 0.56305 | 0.42572 | 0.64545 | 0.50812 | 0.16022 | -0.004577 | 0.58594 | 122.5388 | 0.009156 | 122.4884 | 122.374 | 122.406 | -0.068665 | -122.5159 | 122.3602 | 122.4564 | 122.3373 | 111.3785
2050.4844 | 122.6486 | -122.4106 | 0.073242 | 0.01358 | -0.0040118 | -0.035645 | 0.00037814 | -0.019121 | -0.027967 | -0.023887 | 0.008606 | -0.0082459 | 0.065044 | 0.053696 | -0.018154 | -0.009032 | -0.016955 | -0.036621 | 0.004578 | -0.018311 | -0.013733 | 0.1236 | 0.041199 | 0.045776 | -11.2244 | 0.050354 | -122.438 | 0.050354 | -121.9162 | -121.9849 | -121.8338 | 122.3923 | -0.068664 | -0.086975 | 122.5342 | 122.4564 | 122.4518 | 0.064087 | 0.05951 | -0.027466 | -0.022888 | -0.022888 | 0.49438 | 0.57678 | 0.42572 | 0.60425 | 0.45319 | 0.14191 | 0.004578 | 0.52185 | 122.4884 | 0.022889 | 122.4884 | 122.4152 | 122.4609 | -0.091553 | -122.5113 | 122.3969 | 122.4609 | 122.374 | 111.1862
2052.2031 | 122.5296 | -122.4426 | 0.10529 | 0.01358 | -0.003371 | -0.032227 | 0.00059174 | -0.017412 | -0.027754 | -0.021537 | 0.0025024 | -0.0069641 | 0.06483 | 0.042588 | -0.01794 | -0.010314 | -0.014178 | -0.059509 | 0.036621 | -0.013733 | -0.07782 | 0.018311 | -0.068665 | -0.032043 | -11.5494 | 0.059509 | -122.438 | -0.022888 | -122.0352 | -122.1085 | -121.8979 | 122.4289 | -0.068665 | -0.18311 | 122.4609 | 122.4106 | 122.374 | -0.01831 | -0.054932 | 0.004578 | -0.045777 | -0.12817 | 0.40741 | 0.54474 | 0.33417 | 0.54016 | 0.32959 | 0.032044 | -0.064087 | 0.40283 | 122.4152 | 0.050354 | 122.4976 | 122.4792 | 122.5021 | -0.11902 | -122.5433 | 122.3648 | 122.4197 | 122.3831 | 110.8932
2053.9844 | 122.5983 | -122.4106 | 0.10529 | 0.02121 | -0.0031574 | -0.035645 | 0.00080534 | -0.017412 | -0.02989 | -0.021324 | 0.0055542 | -0.0073913 | 0.06483 | 0.039597 | -0.019435 | -0.011382 | -0.016314 | 0.004578 | 0.041199 | -0.050354 | -0.018311 | 0.1236 | 0.036621 | 0.045776 | -11.5997 | 0.082397 | -122.4426 | 0.045776 | -121.9528 | -122.0306 | -121.875 | 122.3602 | -0.064087 | -0.1236 | 122.5342 | 122.4564 | 122.4472 | 0.09613 | 0.086975 | -0.032044 | -0.022889 | -0.05951 | 0.45776 | 0.53558 | 0.37994 | 0.56763 | 0.41199 | 0.17395 | 0.032043 | 0.48981 | 122.4884 | 0.091553 | 122.525 | 122.4518 | 122.493 | -0.15564 | -122.5479 | 122.3923 | 122.4564 | 122.4152 | 110.8109
2055.7344 | 122.6486 | -122.3831 | 0.086975 | 0.028839 | -0.001662 | -0.032868 | -0.0026127 | -0.019335 | -0.030317 | -0.020897 | 0.008606 | -0.0084595 | 0.067607 | 0.046647 | -0.016445 | -0.009032 | -0.014605 | 0.009155 | -0.009155 | -0.009155 | 0.050354 | 0.21057 | 0.068665 | 0.10529 | -11.8607 | 0.041199 | -122.4518 | 0.082397 | -121.9116 | -121.9757 | -121.8475 | 122.374 | -0.09613 | -0.036621 | 122.5937 | 122.4884 | 122.4518 | 0.11444 | 0.07782 | -0.068664 | -0.045776 | -0.004578 | 0.4715 | 0.53558 | 0.40741 | 0.60425 | 0.47607 | 0.21973 | 0.059509 | 0.54016 | 122.5342 | 0 | 122.493 | 122.374 | 122.4243 | -0.09613 | -122.5388 | 122.4335 | 122.4655 | 122.3923 | 110.5225
2057.4531 | 122.58 | -122.4289 | 0.11444 | 0.0059509 | -0.0037982 | -0.035218 | 0.0020871 | -0.016985 | -0.027113 | -0.020256 | 0.0055542 | -0.0067505 | 0.066539 | 0.043229 | -0.018794 | -0.0081774 | -0.015887 | -0.068665 | 0.027466 | -0.041199 | -0.082397 | 0.050354 | -0.059509 | -0.041199 | -12.1994 | 0.059509 | -122.4655 | 0 | -121.9894 | -122.081 | -121.8933 | 122.3877 | -0.086975 | -0.19684 | 122.4792 | 122.3877 | 122.3694 | 0 | -0.01831 | -0.036621 | -0.054932 | -0.11444 | 0.43945 | 0.53558 | 0.3479 | 0.5722 | 0.38452 | 0.091553 | -0.041198 | 0.47607 | 122.4655 | 0.068665 | 122.525 | 122.4564 | 122.4884 | -0.15564 | -122.58 | 122.3465 | 122.4289 | 122.3602 | 110.2295
2059.25 | 122.5708 | -122.4335 | 0.10986 | 0.044098 | -0.00273 | -0.034791 | -0.00026266 | -0.01314 | -0.030317 | -0.022605 | 0.011658 | -0.0071777 | 0.065685 | 0.047288 | -0.022212 | -0.011168 | -0.015246 | -0.054932 | 0.041199 | -0.054932 | -0.068665 | 0.059509 | -0.009155 | 0 | -12.4878 | 0.068665 | -122.4747 | -0.036621 | -121.9711 | -122.0627 | -121.8796 | 122.3785 | -0.068664 | -0.17853 | 122.493 | 122.4335 | 122.4243 | 0.054932 | 0.045777 | -0.041198 | -0.041198 | -0.14648 | 0.46234 | 0.55389 | 0.37079 | 0.59509 | 0.41199 | 0.11444 | -0.013733 | 0.50354 | 122.438 | 0.096131 | 122.5433 | 122.4747 | 122.5021 | -0.16479 | -122.5845 | 122.3648 | 122.3969 | 122.3785 | 109.9457
2061.0312 | 122.5525 | -122.4518 | 0.10529 | 0.02121 | -0.0040118 | -0.035218 | -0.0017581 | -0.016558 | -0.031599 | -0.026023 | 0.0025024 | -0.0082459 | 0.065258 | 0.044724 | -0.021999 | -0.010314 | -0.015033 | -0.07782 | 0.036621 | -0.041199 | -0.07782 | 0.068665 | -0.004578 | -0.004578 | -12.7716 | 0.07782 | -122.4655 | -0.041199 | -121.9666 | -122.0764 | -121.9116 | 122.4106 | -0.068665 | -0.18311 | 122.5204 | 122.4472 | 122.4472 | 0.036621 | 0.036621 | -0.013733 | -0.027466 | -0.14649 | 0.48523 | 0.54016 | 0.37537 | 0.55389 | 0.3891 | 0.10986 | -0.036621 | 0.49896 | 122.4243 | 0.07782 | 122.5433 | 122.4884 | 122.5296 | -0.14649 | -122.5708 | 122.374 | 122.4106 | 122.374 | 109.6802
2062.7344 | 122.699 | -122.4014 | 0.064087 | 0.01358 | -0.0048664 | -0.034577 | -0.0026127 | -0.021471 | -0.028608 | -0.025169 | -0.003601 | -0.0078185 | 0.064617 | 0.045365 | -0.017513 | -0.009032 | -0.015674 | 0.009155 | -0.009155 | 0.009155 | 0.050354 | 0.22888 | 0.11444 | 0.10986 | -12.9089 | 0.022888 | -122.438 | 0.11444 | -121.8246 | -121.9254 | -121.7972 | 122.4106 | -0.073242 | -0.013733 | 122.6303 | 122.5113 | 122.5159 | 0.10071 | 0.10529 | -0.036621 | -0.041199 | 0.050354 | 0.57678 | 0.60425 | 0.47607 | 0.64087 | 0.5127 | 0.21973 | 0.041199 | 0.6134 | 122.5525 | -0.01831 | 122.4609 | 122.3923 | 122.4243 | -0.054932 | -122.5021 | 122.4518 | 122.5159 | 122.4106 | 109.4925
2064.5469 | 122.6395 | -122.3969 | 0.064087 | 0.02121 | -0.0025164 | -0.0365 | -0.00047626 | -0.013353 | -0.028181 | -0.023674 | 0.011658 | -0.0076049 | 0.065685 | 0.051346 | -0.015377 | -0.0088184 | -0.019519 | 0.022888 | 0 | 0.004578 | 0.027466 | 0.20142 | 0.050354 | 0.082397 | -13.2797 | 0.050354 | -122.4655 | 0.059509 | -121.8933 | -121.994 | -121.8475 | 122.4014 | -0.064087 | -0.036621 | 122.5983 | 122.4792 | 122.4472 | 0.077819 | 0.045776 | -0.068664 | -0.013733 | -0.004578 | 0.50354 | 0.54932 | 0.40283 | 0.61798 | 0.4715 | 0.19684 | 0.022888 | 0.5722 | 122.525 | -0.004578 | 122.5159 | 122.3969 | 122.4472 | -0.059509 | -122.5296 | 122.4243 | 122.4564 | 122.4197 | 109.1171
2066.2812 | 122.6166 | -122.3923 | 0.082397 | 0.028839 | -0.0037982 | -0.035218 | -0.00026266 | -0.020189 | -0.027327 | -0.023887 | 0.008606 | -0.0082459 | 0.065258 | 0.048142 | -0.017085 | -0.011168 | -0.013965 | -0.032043 | 0 | 0 | -0.013733 | 0.14648 | 0.059509 | 0.050354 | -13.6688 | 0.045776 | -122.4655 | 0.045776 | -121.9116 | -122.0215 | -121.8521 | 122.3923 | -0.082397 | -0.09613 | 122.5388 | 122.4426 | 122.4518 | 0.050354 | 0.059509 | -0.073242 | -0.036621 | -0.036621 | 0.48065 | 0.54016 | 0.37079 | 0.6134 | 0.44403 | 0.14648 | -0.013733 | 0.55389 | 122.5113 | 0 | 122.5113 | 122.3923 | 122.438 | -0.082397 | -122.5479 | 122.3785 | 122.438 | 122.3602 | 108.7234
2068.0781 | 122.6166 | -122.4426 | 0.10986 | 0.028839 | -0.0014484 | -0.035218 | 0.0016599 | -0.014208 | -0.028395 | -0.024528 | 0.008606 | -0.0067505 | 0.06483 | 0.046006 | -0.017513 | -0.0096728 | -0.018237 | 0.009155 | 0.018311 | -0.050354 | 0.004578 | 0.12817 | 0.027466 | 0.032043 | -13.8519 | 0.064087 | -122.4518 | 0.036621 | -121.9208 | -122.0352 | -121.8567 | 122.3923 | -0.091552 | -0.10529 | 122.5708 | 122.4747 | 122.4701 | 0.082397 | 0.07782 | -0.009155 | -0.045776 | -0.073242 | 0.52185 | 0.58594 | 0.40741 | 0.59509 | 0.41656 | 0.17853 | 0.054932 | 0.53101 | 122.4884 | 0.068665 | 122.5159 | 122.4609 | 122.5067 | -0.16022 | -122.5616 | 122.4472 | 122.4792 | 122.4518 | 108.5907
2069.7812 | 122.5891 | -122.4106 | 0.091553 | 0.02121 | -0.0012348 | -0.036286 | -4.906e-05 | -0.013567 | -0.028181 | -0.021537 | 0.011658 | -0.0086731 | 0.066112 | 0.045151 | -0.018367 | -0.0092456 | -0.015246 | 0 | 0.032043 | -0.032043 | 0 | 0.13733 | 0.027466 | 0.013733 | -14.1861 | 0.045776 | -122.4609 | 0.045776 | -121.9345 | -122.0398 | -121.8887 | 122.3785 | -0.05951 | -0.091553 | 122.5479 | 122.4243 | 122.438 | 0.045776 | 0.059509 | -0.050354 | -0.045777 | -0.045777 | 0.47607 | 0.52185 | 0.37079 | 0.5722 | 0.42114 | 0.16937 | 0.032043 | 0.52643 | 122.5067 | 0.064086 | 122.5067 | 122.4426 | 122.4564 | -0.1236 | -122.5525 | 122.4106 | 122.4564 | 122.4106 | 108.2245
2071.5781 | 122.6624 | -122.4106 | 0.068665 | 0.036468 | -0.00508 | -0.033936 | -4.906e-05 | -0.016771 | -0.030531 | -0.022392 | 0.011658 | -0.0095275 | 0.065471 | 0.050706 | -0.018367 | -0.010527 | -0.014605 | -0.032043 | 0 | 0 | 0.018311 | 0.16479 | 0.041199 | 0.064087 | -14.6255 | 0.041199 | -122.4564 | 0.050354 | -121.9025 | -121.9986 | -121.8658 | 122.4106 | -0.068665 | -0.050354 | 122.5754 | 122.4747 | 122.4518 | 0.064087 | 0.041199 | -0.045777 | -0.027466 | -0.018311 | 0.50812 | 0.54474 | 0.41199 | 0.59052 | 0.45776 | 0.16479 | 0.018311 | 0.55389 | 122.5067 | 0 | 122.4976 | 122.4106 | 122.4518 | -0.068665 | -122.525 | 122.4289 | 122.4609 | 122.3785 | 107.785
2073.3594 | 122.6898 | -122.374 | 0.07782 | 0.02121 | -0.0018756 | -0.03415 | -0.00069006 | -0.013994 | -0.028608 | -0.023674 | 0.0025024 | -0.0067505 | 0.066326 | 0.051133 | -0.016872 | -0.009032 | -0.018878 | -0.032043 | 0.022888 | -0.009155 | 0.004578 | 0.14191 | 0.032043 | 0.036621 | -14.8315 | 0.036621 | -122.4426 | 0.10529 | -121.8704 | -121.9711 | -121.8155 | 122.3648 | -0.054932 | -0.073242 | 122.5159 | 122.4106 | 122.406 | 0.045776 | 0.041198 | -0.068665 | -0.041199 | 0.027466 | 0.50354 | 0.55847 | 0.40283 | 0.62714 | 0.4715 | 0.15106 | 0.013733 | 0.5722 | 122.5479 | 0.032043 | 122.4792 | 122.3969 | 122.4106 | -0.086975 | -122.5204 | 122.3785 | 122.4792 | 122.3419 | 107.5424
2075.0781 | 122.5616 | -122.4289 | 0.09613 | 0.0059509 | -0.0020892 | -0.033509 | 0.0033689 | -0.011004 | -0.029463 | -0.024314 | 0.0055542 | -0.0076049 | 0.06483 | 0.04387 | -0.019649 | -0.0086048 | -0.014178 | -0.082397 | 0.027466 | -0.041199 | -0.07782 | 0.041199 | -0.064087 | -0.032043 | -15.2298 | 0.059509 | -122.4838 | -0.018311 | -121.994 | -122.0947 | -121.9116 | 122.3877 | -0.068664 | -0.17395 | 122.4701 | 122.3969 | 122.3648 | 0.009156 | -0.022888 | -0.054932 | -0.036621 | -0.11444 | 0.43488 | 0.51727 | 0.33417 | 0.5722 | 0.3891 | 0.082398 | -0.036621 | 0.48981 | 122.4655 | 0.068665 | 122.5433 | 122.4564 | 122.4884 | -0.13733 | -122.58 | 122.3511 | 122.4106 | 122.3465 | 107.1991
2076.8594 | 122.5754 | -122.4335 | 0.11444 | 0.01358 | -0.0031574 | -0.035431 | -0.0015445 | -0.016131 | -0.029249 | -0.025383 | -0.00054937 | -0.0069641 | 0.065471 | 0.048356 | -0.022426 | -0.0101 | -0.015033 | -0.073242 | 0.027466 | -0.045776 | -0.073242 | 0.07782 | -0.004578 | 0.013733 | -15.5365 | 0.068665 | -122.4701 | -0.032043 | -121.9482 | -122.0581 | -121.9254 | 122.3877 | -0.086975 | -0.18768 | 122.5113 | 122.4472 | 122.4289 | 0.059509 | 0.041198 | -0.036621 | -0.045776 | -0.14648 | 0.48523 | 0.50812 | 0.37537 | 0.54474 | 0.41199 | 0.1236 | -0.027466 | 0.52185 | 122.4381 | 0.073242 | 122.5388 | 122.4609 | 122.5021 | -0.16022 | -122.5845 | 122.3602 | 122.4014 | 122.3602 | 106.897
2078.6406 | 122.612 | -122.4289 | 0.10986 | 0.028839 | -0.0010212 | -0.034363 | 0.0012325 | -0.017412 | -0.027327 | -0.021751 | 0.014709 | -0.0069641 | 0.066112 | 0.04387 | -0.018581 | -0.010527 | -0.018237 | -0.027466 | 0.054932 | -0.064087 | -0.041199 | 0.091553 | 0.036621 | 0.022888 | -15.8615 | 0.073242 | -122.4884 | 0.032043 | -121.907 | -122.0215 | -121.8796 | 122.3648 | -0.054931 | -0.15106 | 122.5204 | 122.4518 | 122.4655 | 0.086975 | 0.10071 | -0.059509 | -0.036621 | -0.07782 | 0.52185 | 0.54932 | 0.40741 | 0.60883 | 0.46692 | 0.15564 | 0.022888 | 0.58136 | 122.5204 | 0.11902 | 122.5616 | 122.4838 | 122.5021 | -0.17395 | -122.5983 | 122.3877 | 122.4609 | 122.4014 | 106.5674
2080.375 | 122.5754 | -122.4564 | 0.10071 | 0.051727 | -0.0023028 | -0.0365 | -0.00047626 | -0.015703 | -0.027754 | -0.021324 | 0.014709 | -0.0084595 | 0.065685 | 0.038956 | -0.02029 | -0.0086048 | -0.018237 | -0.059509 | 0.068665 | -0.045776 | -0.054932 | 0.073242 | 0.009155 | 0.004578 | -16.2872 | 0.09613 | -122.5067 | -0.022888 | -121.9528 | -122.0627 | -121.9116 | 122.4106 | -0.032043 | -0.15564 | 122.5296 | 122.4609 | 122.4655 | 0.050354 | 0.054931 | -0.050354 | -0.004578 | -0.1236 | 0.50354 | 0.54474 | 0.39368 | 0.59509 | 0.44403 | 0.11902 | -0.009156 | 0.55389 | 122.4838 | 0.11444 | 122.6028 | 122.525 | 122.5525 | -0.14648 | -122.6074 | 122.4014 | 122.4335 | 122.3969 | 106.1691
2082.1562 | 122.6715 | -122.4106 | 0.064087 | 0.028839 | -0.0025164 | -0.0318 | 0.0012325 | -0.021258 | -0.026899 | -0.024528 | 0.014709 | -0.0080321 | 0.066539 | 0.056046 | -0.016017 | -0.0094592 | -0.015246 | 0.027466 | 0.018311 | 0.004578 | 0.073242 | 0.2243 | 0.07782 | 0.091553 | -16.5848 | 0.045776 | -122.4518 | 0.09613 | -121.8567 | -121.9757 | -121.8384 | 122.4152 | -0.045776 | 0.009155 | 122.6349 | 122.5021 | 122.4884 | 0.086975 | 0.073242 | -0.041199 | -0.018311 | 0.032043 | 0.55389 | 0.5722 | 0.43488 | 0.6134 | 0.47607 | 0.21973 | 0.068664 | 0.59509 | 122.5479 | 0.013733 | 122.4976 | 122.4289 | 122.4564 | -0.059509 | -122.5159 | 122.4838 | 122.5067 | 122.438 | 105.8258
2083.9531 | 122.6028 | -122.4243 | 0.086975 | 0.02121 | -0.0031574 | -0.035645 | -0.00069006 | -0.01314 | -0.029036 | -0.021965 | 0.0055542 | -0.0061095 | 0.06483 | 0.042801 | -0.017726 | -0.0068958 | -0.015033 | -0.064087 | 0.027466 | -0.018311 | -0.073242 | 0.073242 | -0.027466 | -0.027466 | -17.0883 | 0.054932 | -122.4792 | 0.009155 | -121.9528 | -122.0581 | -121.8887 | 122.406 | -0.059509 | -0.16022 | 122.4976 | 122.3969 | 122.3969 | -0.009155 | -0.009155 | -0.054932 | -0.032043 | -0.07782 | 0.4715 | 0.53558 | 0.36621 | 0.59051 | 0.42114 | 0.091553 | -0.054931 | 0.52643 | 122.4884 | 0.045777 | 122.5342 | 122.4518 | 122.4792 | -0.10529 | -122.5662 | 122.3511 | 122.4335 | 122.3602 | 105.336
2085.6562 | 122.6212 | -122.4197 | 0.086975 | 0.01358 | -0.004439 | -0.035645 | 0.00037814 | -0.018267 | -0.027967 | -0.024528 | 0.0025024 | -0.0069641 | 0.063335 | 0.045365 | -0.015163 | -0.009032 | -0.016314 | -0.054932 | 0.032043 | -0.018311 | -0.054932 | 0.07782 | -0.036621 | -0.013733 | -17.5735 | 0.041199 | -122.4609 | 0.050354 | -121.8979 | -122.0352 | -121.875 | 122.4014 | -0.054932 | -0.14191 | 122.4976 | 122.406 | 122.3831 | 0.004578 | -0.01831 | -0.041198 | -0.045776 | -0.036621 | 0.52185 | 0.54474 | 0.38452 | 0.58594 | 0.42572 | 0.096131 | -0.036621 | 0.56305 | 122.5113 | 0.050354 | 122.5021 | 122.4518 | 122.4609 | -0.10529 | -122.5479 | 122.3648 | 122.4701 | 122.3648 | 104.8462
2087.4375 | 122.5479 | -122.438 | 0.091553 | 0.0059509 | -0.0012348 | -0.035004 | 0.0014463 | -0.016558 | -0.028181 | -0.020042 | 0.0055542 | -0.0076049 | 0.065685 | 0.044724 | -0.019222 | -0.0081774 | -0.015887 | -0.064087 | 0.045776 | -0.022888 | -0.068665 | 0.036621 | -0.050354 | -0.036621 | -18.0176 | 0.068665 | -122.4792 | -0.036621 | -121.9803 | -122.0947 | -121.9162 | 122.4152 | -0.045777 | -0.16022 | 122.4747 | 122.4014 | 122.3877 | -0.013733 | -0.027466 | -0.041199 | -0.022888 | -0.12817 | 0.45776 | 0.52185 | 0.34332 | 0.56305 | 0.38452 | 0.059509 | -0.045777 | 0.49896 | 122.4426 | 0.068664 | 122.5479 | 122.4838 | 122.5067 | -0.11444 | -122.5708 | 122.3694 | 122.4014 | 122.374 | 104.4205
2089.1719 | 122.6852 | -122.4152 | 0.07782 | 0.0059509 | -0.0059344 | -0.036072 | -0.0028263 | -0.020403 | -0.031599 | -0.024528 | 0.011658 | -0.0084595 | 0.065685 | 0.04686 | -0.018794 | -0.0086048 | -0.014178 | -0.032043 | 0 | -0.013733 | 0.013733 | 0.1831 | 0.086975 | 0.09613 | -18.3243 | 0.041199 | -122.4335 | 0.082397 | -121.8018 | -121.9162 | -121.8201 | 122.4014 | -0.07782 | -0.064087 | 122.5983 | 122.5113 | 122.5021 | 0.10986 | 0.10071 | -0.018311 | -0.036621 | 0.004577 | 0.6134 | 0.59509 | 0.49896 | 0.6134 | 0.51727 | 0.19684 | 0.027466 | 0.63171 | 122.5159 | 0.013733 | 122.4747 | 122.4152 | 122.4564 | -0.091553 | -122.5113 | 122.4289 | 122.4976 | 122.3831 | 104.0909
2090.9531 | 122.58 | -122.4243 | 0.09613 | 0.02121 | -0.0037982 | -0.036072 | -0.00047626 | -0.01848 | -0.027967 | -0.021537 | 0.008606 | -0.0078185 | 0.066539 | 0.044297 | -0.021785 | -0.0096728 | -0.018451 | -0.009155 | 0.036621 | -0.013733 | -0.013733 | 0.11902 | 0.027466 | 0.013733 | -18.7866 | 0.073242 | -122.4701 | 0.009155 | -121.9116 | -122.0398 | -121.875 | 122.4106 | -0.059509 | -0.10986 | 122.5433 | 122.438 | 122.4518 | 0.027466 | 0.041199 | -0.045777 | -0.022888 | -0.086975 | 0.5127 | 0.54932 | 0.38452 | 0.59509 | 0.4303 | 0.13275 | 0 | 0.55847 | 122.4792 | 0.050354 | 122.5433 | 122.4609 | 122.4976 | -0.10986 | -122.5662 | 122.4106 | 122.4335 | 122.4152 | 103.6377
2092.7344 | 122.6166 | -122.4335 | 0.091553 | 0.01358 | -0.003371 | -0.033509 | 0.00037814 | -0.014422 | -0.029036 | -0.024955 | 0.0055542 | -0.0069641 | 0.066539 | 0.046006 | -0.020717 | -0.0088184 | -0.015887 | -0.004578 | 0.018311 | -0.018311 | -0.009155 | 0.11444 | 0.022888 | 0.022888 | -19.2215 | 0.054932 | -122.4655 | 0.027466 | -121.9025 | -122.0352 | -121.8842 | 122.4152 | -0.073242 | -0.10071 | 122.5479 | 122.4564 | 122.4564 | 0.041199 | 0.041199 | -0.032043 | -0.036621 | -0.064087 | 0.53101 | 0.54932 | 0.39825 | 0.58136 | 0.4303 | 0.13275 | 0.009156 | 0.56305 | 122.493 | 0.036622 | 122.5204 | 122.4518 | 122.4884 | -0.10986 | -122.5571 | 122.4243 | 122.4609 | 122.4289 | 103.212
2094.5312 | 122.6532 | -122.438 | 0.082397 | 0.028839 | -0.0052936 | -0.033936 | -0.0017581 | -0.021044 | -0.028181 | -0.022392 | 0.0055542 | -0.0084595 | 0.064617 | 0.048997 | -0.020503 | -0.0101 | -0.013965 | -0.041199 | 0.013733 | -0.018311 | -0.022888 | 0.13275 | 0.036621 | 0.041199 | -19.7754 | 0.045776 | -122.4564 | 0.050354 | -121.8658 | -121.9849 | -121.8521 | 122.4197 | -0.068664 | -0.10528 | 122.5708 | 122.4792 | 122.4747 | 0.05951 | 0.054932 | -0.018311 | -0.036621 | -0.032043 | 0.5722 | 0.58594 | 0.45319 | 0.60425 | 0.4715 | 0.15106 | -0.004577 | 0.59052 | 122.5067 | 0.032044 | 122.5021 | 122.4518 | 122.4838 | -0.10071 | -122.5388 | 122.4152 | 122.4884 | 122.3969 | 102.6627
2096.25 | 122.7036 | -122.3969 | 0.07782 | 0.0059509 | -0.0040118 | -0.037781 | -0.0021853 | -0.016771 | -0.02989 | -0.021324 | 0.0025024 | -0.011023 | 0.065685 | 0.045792 | -0.020931 | -0.0094592 | -0.019305 | 0.027466 | -0.004578 | 0.004578 | 0.059509 | 0.24261 | 0.11902 | 0.10986 | -20.1004 | 0.013733 | -122.4655 | 0.09613 | -121.7926 | -121.9116 | -121.8246 | 122.4014 | -0.082398 | -0.018311 | 122.6395 | 122.5067 | 122.5159 | 0.10529 | 0.11444 | -0.068664 | -0.064087 | 0.01831 | 0.60425 | 0.5722 | 0.48523 | 0.64087 | 0.55389 | 0.23804 | 0.054931 | 0.67291 | 122.5616 | -0.009156 | 122.4792 | 122.3923 | 122.4106 | -0.073242 | -122.5433 | 122.4564 | 122.493 | 122.4243 | 102.2964
2098.0312 | 122.699 | -122.3969 | 0.064087 | 0.0059509 | -0.0010212 | -0.034363 | 0.00059174 | -0.01848 | -0.026472 | -0.024101 | 0.0055542 | -0.0069641 | 0.064617 | 0.048783 | -0.016445 | -0.0075366 | -0.015246 | 0.004578 | 0.009155 | 0.009155 | 0.032043 | 0.16937 | 0.064087 | 0.073242 | -20.5765 | 0.018311 | -122.4289 | 0.11902 | -121.8155 | -121.9437 | -121.8018 | 122.406 | -0.054932 | -0.032044 | 122.5662 | 122.4701 | 122.4609 | 0.064087 | 0.054932 | -0.032043 | -0.045776 | 0.054932 | 0.58136 | 0.59509 | 0.45319 | 0.62714 | 0.48523 | 0.16022 | 0.022888 | 0.6134 | 122.5479 | 0 | 122.4472 | 122.406 | 122.4152 | -0.054932 | -122.493 | 122.4289 | 122.5159 | 122.4014 | 101.8204
2099.7344 | 122.6349 | -122.406 | 0.082397 | 0.028839 | -0.0031574 | -0.036072 | -0.0017581 | -0.015062 | -0.02754 | -0.024314 | 0.0025024 | -0.0084595 | 0.065471 | 0.049851 | -0.022853 | -0.0098864 | -0.016955 | 0.004578 | -0.004578 | 0.009155 | 0.050354 | 0.19226 | 0.10071 | 0.07782 | -21.1441 | 0.032043 | -122.4747 | 0.022888 | -121.8521 | -121.9711 | -121.875 | 122.4152 | -0.086975 | -0.032043 | 122.5983 | 122.4838 | 122.5067 | 0.068665 | 0.091553 | -0.068664 | -0.050354 | -0.059509 | 0.55389 | 0.53101 | 0.43488 | 0.59967 | 0.50354 | 0.18311 | 0.041199 | 0.62256 | 122.4976 | -0.013733 | 122.5067 | 122.4014 | 122.438 | -0.073242 | -122.5571 | 122.4564 | 122.4289 | 122.4106 | 101.2619
2101.5312 | 122.6807 | -122.4014 | 0.064087 | 0.0059509 | -0.001662 | -0.034363 | -4.906e-05 | -0.017199 | -0.028822 | -0.02346 | 0.011658 | -0.0067505 | 0.063976 | 0.044724 | -0.016658 | -0.0075366 | -0.014605 | 0.022888 | -0.009155 | 0.018311 | 0.054932 | 0.21973 | 0.07782 | 0.10071 | -21.5973 | 0.050354 | -122.4838 | 0.11444 | -121.7972 | -121.9254 | -121.8063 | 122.4197 | -0.073242 | -0.009155 | 122.6212 | 122.5021 | 122.4792 | 0.082397 | 0.059509 | -0.082398 | -0.013733 | 0.050354 | 0.60425 | 0.59509 | 0.47607 | 0.67749 | 0.55847 | 0.20142 | 0.036621 | 0.68665 | 122.5983 | -0.027466 | 122.5342 | 122.3923 | 122.4518 | -0.045776 | -122.5479 | 122.4564 | 122.5159 | 122.4243 | 100.8041
2103.3125 | 122.699 | -122.4197 | 0.068665 | 0.01358 | -0.004439 | -0.033936 | -0.0015445 | -0.019335 | -0.029036 | -0.022819 | 0.0025024 | -0.0086731 | 0.065258 | 0.047928 | -0.019008 | -0.0079638 | -0.014819 | -0.036621 | -0.013733 | 0.022888 | 0.022888 | 0.16479 | 0.10529 | 0.09613 | -22.197 | 0.027466 | -122.4609 | 0.082397 | -121.8018 | -121.9025 | -121.8201 | 122.4426 | -0.082398 | -0.045777 | 122.5845 | 122.5159 | 122.525 | 0.073242 | 0.082398 | -0.041198 | -0.041199 | 0.013732 | 0.61798 | 0.59967 | 0.51727 | 0.64087 | 0.55847 | 0.14191 | 0 | 0.65918 | 122.5433 | -0.036621 | 122.4884 | 122.406 | 122.4472 | -0.045777 | -122.5296 | 122.4426 | 122.5021 | 122.3831 | 100.2228
2105.0469 | 122.5983 | -122.4472 | 0.07782 | 0.01358 | -0.0014484 | -0.035431 | 0.0027279 | -0.01784 | -0.027967 | -0.022819 | 0.0055542 | -0.0084595 | 0.068676 | 0.04451 | -0.021572 | -0.0079638 | -0.016528 | 0 | 0.041199 | -0.018311 | -0.004578 | 0.1236 | 0.009155 | 0.032043 | -22.7737 | 0.068665 | -122.4609 | 0.022888 | -121.8933 | -122.0261 | -121.8842 | 122.4289 | -0.036621 | -0.082398 | 122.5708 | 122.4792 | 122.4564 | 0.050354 | 0.027466 | -0.013732 | -0.009155 | -0.054932 | 0.55389 | 0.56305 | 0.42114 | 0.57678 | 0.43488 | 0.14191 | 0.013733 | 0.56763 | 122.4838 | 0.05951 | 122.5296 | 122.4884 | 122.5159 | -0.096131 | -122.5388 | 122.4426 | 122.4701 | 122.4472 | 99.6735
2106.8125 | 122.699 | -122.4106 | 0.068665 | 0.0059509 | -0.0059344 | -0.036072 | -0.0026127 | -0.017412 | -0.029036 | -0.021965 | 0.0025024 | -0.0097411 | 0.063976 | 0.049851 | -0.019008 | -0.010314 | -0.012896 | 0 | 0 | -0.009155 | 0.068665 | 0.2243 | 0.12817 | 0.11444 | -23.1857 | 0.004578 | -122.4518 | 0.10529 | -121.7606 | -121.9025 | -121.8246 | 122.4014 | -0.068665 | 0 | 122.6349 | 122.525 | 122.5388 | 0.1236 | 0.13733 | -0.041199 | -0.064087 | 0.036621 | 0.65002 | 0.58594 | 0.50812 | 0.62714 | 0.54932 | 0.23346 | 0.07782 | 0.69122 | 122.5571 | 0.009155 | 122.4564 | 122.4106 | 122.4152 | -0.07782 | -122.5204 | 122.4792 | 122.5159 | 122.4106 | 99.2249
2108.5469 | 122.644 | -122.4197 | 0.07782 | 0.028839 | -0.0037982 | -0.033722 | -0.00026266 | -0.019549 | -0.028822 | -0.022178 | 0.011658 | -0.010382 | 0.06419 | 0.04387 | -0.018367 | -0.0092456 | -0.010333 | -0.036621 | 0.004578 | -0.018311 | 0.004578 | 0.14191 | 0.036621 | 0.054932 | -23.8037 | 0.041199 | -122.4701 | 0.022888 | -121.8658 | -121.9803 | -121.8613 | 122.4014 | -0.073242 | -0.073242 | 122.5616 | 122.4747 | 122.4564 | 0.073243 | 0.054932 | -0.050354 | -0.036621 | -0.054932 | 0.55389 | 0.55847 | 0.43945 | 0.60883 | 0.48981 | 0.16022 | 0.022889 | 0.60425 | 122.493 | 0.022889 | 122.5113 | 122.4243 | 122.4609 | -0.096131 | -122.5479 | 122.4243 | 122.4426 | 122.3831 | 98.616
2110.3281 | 122.6303 | -122.4289 | 0.11902 | 0.01358 | -0.0031574 | -0.033936 | -4.906e-05 | -0.020617 | -0.027113 | -0.024528 | 0.008606 | -0.0058959 | 0.06483 | 0.044297 | -0.018794 | -0.0092456 | -0.012683 | 0 | 0.050354 | -0.018311 | 0.004578 | 0.13275 | 0.027466 | 0.022888 | -24.234 | 0.073242 | -122.4838 | 0.036621 | -121.8521 | -121.9849 | -121.8567 | 122.4106 | -0.068665 | -0.11444 | 122.5616 | 122.4518 | 122.4564 | 0.041199 | 0.045777 | -0.054932 | -0.045777 | -0.082398 | 0.57678 | 0.5722 | 0.44403 | 0.62714 | 0.49896 | 0.15106 | 0.022889 | 0.63171 | 122.5204 | 0.068665 | 122.5571 | 122.4792 | 122.5021 | -0.13733 | -122.6028 | 122.4335 | 122.4655 | 122.4289 | 98.1949
2112.1094 | 122.7127 | -122.3785 | 0.059509 | 0.0059509 | -0.0035846 | -0.035004 | 0.00080534 | -0.01784 | -0.026045 | -0.022605 | 0.0025024 | -0.0076049 | 0.065685 | 0.045151 | -0.01559 | -0.007323 | -0.014392 | -0.018311 | 0.013733 | -0.013733 | 0.041199 | 0.14648 | 0.036621 | 0.050354 | -24.7467 | 0.036621 | -122.4701 | 0.10529 | -121.8109 | -121.9345 | -121.8018 | 122.3648 | -0.045776 | -0.01831 | 122.525 | 122.4289 | 122.4152 | 0.064087 | 0.050354 | -0.091553 | -0.022888 | 0.045777 | 0.56763 | 0.57678 | 0.44403 | 0.66833 | 0.53558 | 0.16022 | 0.054932 | 0.65918 | 122.5754 | 0.027466 | 122.5067 | 122.3923 | 122.4152 | -0.073242 | -122.5296 | 122.4197 | 122.4838 | 122.3602 | 97.6318
2113.8125 | 122.644 | -122.4426 | 0.07782 | 0.01358 | -0.003371 | -0.033722 | 0.0016599 | -0.017199 | -0.029036 | -0.023674 | 0.0055542 | -0.0076049 | 0.066326 | 0.040238 | -0.017299 | -0.0079638 | -0.01546 | -0.050354 | 0.050354 | -0.036621 | -0.054932 | 0.064087 | -0.036621 | -0.004578 | -25.2045 | 0.050354 | -122.4884 | 0.036621 | -121.8567 | -121.9986 | -121.8658 | 122.406 | -0.027466 | -0.13275 | 122.5067 | 122.438 | 122.406 | 0.032043 | 0 | -0.045776 | -0.027466 | -0.041199 | 0.58594 | 0.57678 | 0.44403 | 0.62256 | 0.48981 | 0.10071 | -0.018311 | 0.63171 | 122.525 | 0.086975 | 122.5388 | 122.493 | 122.493 | -0.11444 | -122.5662 | 122.3877 | 122.4792 | 122.3923 | 97.2382
2115.5938 | 122.5708 | -122.4335 | 0.091553 | 0.0059509 | -0.0012348 | -0.03415 | 0.0014463 | -0.016344 | -0.026472 | -0.020897 | 0.0055542 | -0.0065369 | 0.065685 | 0.042374 | -0.019435 | -0.0101 | -0.016314 | -0.036621 | 0.022888 | -0.009155 | -0.027466 | 0.10071 | -0.004578 | 0.004578 | -25.8911 | 0.054932 | -122.4792 | 0 | -121.8979 | -122.0535 | -121.907 | 122.4243 | -0.068665 | -0.11902 | 122.5342 | 122.438 | 122.4289 | 0.013733 | 0.004577 | -0.045776 | -0.036621 | -0.091553 | 0.53558 | 0.52643 | 0.37994 | 0.5722 | 0.42572 | 0.10986 | -0.018311 | 0.58136 | 122.4792 | 0.032043 | 122.5342 | 122.4564 | 122.4884 | -0.10071 | -122.5708 | 122.406 | 122.4335 | 122.3969 | 96.5424
2117.375 | 122.6212 | -122.438 | 0.10071 | 0.0059509 | -0.00273 | -0.035431 | 0.00059174 | -0.014422 | -0.030745 | -0.020469 | 0.011658 | -0.0061095 | 0.06718 | 0.042588 | -0.021144 | -0.011168 | -0.016314 | 0 | 0.032043 | -0.032043 | 0.009155 | 0.13733 | 0.032043 | 0.036621 | -26.2619 | 0.07782 | -122.4976 | 0.036621 | -121.8338 | -121.9894 | -121.8704 | 122.406 | -0.068665 | -0.091553 | 122.5754 | 122.4747 | 122.4701 | 0.068664 | 0.064086 | -0.05951 | -0.022888 | -0.064087 | 0.60425 | 0.56763 | 0.44861 | 0.62714 | 0.50812 | 0.16937 | 0.041198 | 0.66376 | 122.5342 | 0.064086 | 122.5754 | 122.4701 | 122.5159 | -0.13275 | -122.5983 | 122.4472 | 122.4747 | 122.438 | 96.1761
2119.1719 | 122.6486 | -122.4335 | 0.10986 | 0.01358 | -0.0046526 | -0.032227 | -0.0015445 | -0.016131 | -0.026899 | -0.022392 | 0.0055542 | -0.011237 | 0.065685 | 0.055405 | -0.019008 | -0.0081774 | -0.01781 | -0.045776 | 0.013733 | 0 | -0.009155 | 0.13733 | 0.054932 | 0.054932 | -26.8295 | 0.050354 | -122.4792 | 0.032043 | -121.8246 | -121.9574 | -121.8521 | 122.4335 | -0.09613 | -0.11902 | 122.5708 | 122.4884 | 122.4884 | 0.054932 | 0.054932 | -0.045776 | -0.059509 | -0.07782 | 0.60883 | 0.58136 | 0.47607 | 0.62714 | 0.52185 | 0.13733 | -0.009155 | 0.6546 | 122.5113 | 0.013733 | 122.5296 | 122.4472 | 122.4838 | -0.10986 | -122.5891 | 122.4243 | 122.4655 | 122.3877 | 95.6039
2120.9375 | 122.6166 | -122.4289 | 0.091553 | 0.02121 | -0.0018756 | -0.033509 | -0.0011173 | -0.013567 | -0.028822 | -0.019401 | 0.008606 | -0.0078185 | 0.065899 | 0.039384 | -0.020717 | -0.009032 | -0.014819 | 0.004578 | 0.041199 | -0.041199 | -0.013733 | 0.12817 | 0.041199 | 0.041199 | -27.1545 | 0.050354 | -122.4747 | 0.036621 | -121.8201 | -121.9711 | -121.875 | 122.3877 | -0.050354 | -0.10529 | 122.5571 | 122.4701 | 122.4701 | 0.082398 | 0.082398 | -0.045776 | -0.041199 | -0.054932 | 0.60883 | 0.55389 | 0.45776 | 0.59967 | 0.50354 | 0.16937 | 0.027466 | 0.6546 | 122.5113 | 0.082398 | 122.525 | 122.4701 | 122.4792 | -0.13275 | -122.5662 | 122.4152 | 122.4655 | 122.4335 | 95.2744
2122.6562 | 122.644 | -122.4197 | 0.054932 | 0.02121 | -0.0046526 | -0.033509 | -0.0015445 | -0.015917 | -0.025404 | -0.026878 | 0.0055542 | -0.0095275 | 0.064403 | 0.051346 | -0.017726 | -0.008391 | -0.013324 | -0.032043 | 0.018311 | 0.004578 | 0.004578 | 0.15106 | 0.041199 | 0.059509 | -27.5482 | 0.041199 | -122.4655 | 0.036621 | -121.8201 | -121.9437 | -121.8567 | 122.4243 | -0.036621 | -0.050354 | 122.5708 | 122.4792 | 122.4609 | 0.054931 | 0.036621 | -0.045776 | -0.013733 | -0.018311 | 0.59967 | 0.56305 | 0.47607 | 0.60883 | 0.52185 | 0.14648 | 0 | 0.64545 | 122.5021 | 0.013733 | 122.5067 | 122.4381 | 122.4609 | -0.050354 | -122.5204 | 122.4243 | 122.4564 | 122.3877 | 94.8715
2124.4531 | 122.6028 | -122.4518 | 0.10986 | 0.01358 | -0.0025164 | -0.036072 | -0.00069006 | -0.021898 | -0.027967 | -0.026237 | 0.0055542 | -0.0095275 | 0.066539 | 0.045579 | -0.020503 | -0.0096728 | -0.017596 | 0.004578 | 0 | 0 | 0.018311 | 0.15106 | 0.07782 | 0.064087 | -27.9556 | 0.064087 | -122.4701 | -0.004578 | -121.8338 | -121.9986 | -121.907 | 122.4518 | -0.10986 | -0.091552 | 122.6028 | 122.5159 | 122.5296 | 0.064087 | 0.07782 | -0.018311 | -0.045776 | -0.11444 | 0.61798 | 0.54474 | 0.45319 | 0.56305 | 0.4715 | 0.15106 | 0.018311 | 0.63629 | 122.4655 | 0 | 122.5342 | 122.4518 | 122.5159 | -0.10986 | -122.58 | 122.4701 | 122.4472 | 122.4564 | 94.4962
2126.2344 | 122.5571 | -122.4335 | 0.10529 | 0.0059509 | -0.0029438 | -0.035004 | 0.0016599 | -0.014635 | -0.028181 | -0.02581 | -0.00054937 | -0.0071777 | 0.066326 | 0.044083 | -0.017513 | -0.009032 | -0.016314 | -0.054932 | 0.032043 | -0.018311 | -0.082397 | 0.036621 | -0.054932 | -0.050354 | -28.4775 | 0.054932 | -122.4884 | -0.036621 | -121.9162 | -122.0627 | -121.9208 | 122.4152 | -0.073243 | -0.18768 | 122.4701 | 122.3831 | 122.3785 | -0.032043 | -0.036621 | -0.054931 | -0.050354 | -0.14191 | 0.51727 | 0.5127 | 0.37079 | 0.56763 | 0.42572 | 0.054932 | -0.064086 | 0.5722 | 122.4518 | 0.050354 | 122.5433 | 122.4655 | 122.4884 | -0.1236 | -122.5937 | 122.3511 | 122.3969 | 122.3785 | 93.956
2127.9375 | 122.6761 | -122.4152 | 0.082397 | 0.0059509 | -0.0035846 | -0.036072 | -0.00069006 | -0.016131 | -0.031813 | -0.021537 | 0.008606 | -0.0097411 | 0.063762 | 0.047074 | -0.017513 | -0.010527 | -0.013537 | 0.004578 | 0 | 0.018311 | 0.068665 | 0.21515 | 0.11902 | 0.1236 | -28.7018 | 0.041199 | -122.4289 | 0.09613 | -121.7377 | -121.8796 | -121.8338 | 122.4335 | -0.082397 | -0.013732 | 122.6303 | 122.5388 | 122.5342 | 0.10528 | 0.10071 | -0.013733 | -0.041198 | 0.013733 | 0.67749 | 0.58136 | 0.53558 | 0.59509 | 0.54932 | 0.19684 | 0.050354 | 0.69122 | 122.525 | -0.018311 | 122.4701 | 122.4152 | 122.4564 | -0.064086 | -122.5113 | 122.4838 | 122.5113 | 122.4197 | 93.7134
2129.7344 | 122.699 | -122.3831 | 0.068665 | 0.0059509 | -0.00508 | -0.0365 | -0.0021853 | -0.020617 | -0.029249 | -0.021965 | 0.0025024 | -0.0084595 | 0.063549 | 0.045365 | -0.019435 | -0.0088184 | -0.01546 | 0.013733 | -0.004578 | 0.004578 | 0.059509 | 0.23804 | 0.11902 | 0.11902 | -29.0634 | 0.018311 | -122.4518 | 0.10529 | -121.701 | -121.8613 | -121.7926 | 122.3877 | -0.073243 | -0.009156 | 122.6212 | 122.5021 | 122.5021 | 0.11444 | 0.11444 | -0.068664 | -0.050354 | 0.036621 | 0.68207 | 0.59051 | 0.52185 | 0.65918 | 0.59051 | 0.23346 | 0.054931 | 0.75073 | 122.5571 | -0.009156 | 122.4701 | 122.3785 | 122.4014 | -0.064087 | -122.5204 | 122.4426 | 122.4884 | 122.3969 | 93.3197
2131.5156 | 122.7036 | -122.3877 | 0.07782 | 0.01358 | -0.0042254 | -0.035431 | 0.00037814 | -0.017199 | -0.026258 | -0.022819 | 0.017761 | -0.0078185 | 0.066326 | 0.045579 | -0.016445 | -0.0088184 | -0.013751 | 0.036621 | -0.027466 | 0.018311 | 0.082397 | 0.22888 | 0.07782 | 0.10529 | -29.4571 | 0.027466 | -122.4884 | 0.10529 | -121.7331 | -121.907 | -121.8063 | 122.406 | -0.10529 | 0.004577 | 122.6166 | 122.493 | 122.4655 | 0.086975 | 0.059509 | -0.10071 | -0.050354 | 0.027466 | 0.6546 | 0.58136 | 0.48065 | 0.68207 | 0.58136 | 0.21057 | 0.064086 | 0.75531 | 122.5937 | -0.045777 | 122.5159 | 122.3602 | 122.4152 | -0.059509 | -122.5662 | 122.4701 | 122.493 | 122.4243 | 92.9306
2133.25 | 122.6486 | -122.4289 | 0.07782 | 0.036468 | -0.0057208 | -0.035431 | -4.906e-05 | -0.019121 | -0.028608 | -0.02346 | 0.008606 | -0.0071777 | 0.064617 | 0.049851 | -0.019222 | -0.0092456 | -0.01311 | 0.009155 | 0.004578 | -0.004578 | 0.036621 | 0.17853 | 0.073242 | 0.073242 | -29.9652 | 0.041199 | -122.4564 | 0.054932 | -121.8109 | -121.9437 | -121.8475 | 122.4243 | -0.073242 | -0.041199 | 122.6074 | 122.5021 | 122.5021 | 0.07782 | 0.07782 | -0.027466 | -0.036621 | -0.022888 | 0.61798 | 0.58136 | 0.48523 | 0.60883 | 0.5127 | 0.18311 | 0.041199 | 0.64545 | 122.5113 | 0.009156 | 122.4976 | 122.4335 | 122.4701 | -0.082398 | -122.5342 | 122.4655 | 122.4838 | 122.438 | 92.4637
2135.0312 | 122.6028 | -122.4564 | 0.09613 | -0.0016786 | -0.003371 | -0.035431 | 0.00037814 | -0.01549 | -0.029036 | -0.023033 | 0.008606 | -0.0071777 | 0.06718 | 0.041733 | -0.016445 | -0.0079638 | -0.016314 | -0.050354 | 0.027466 | -0.036621 | -0.064087 | 0.050354 | -0.045776 | -0.013733 | -30.336 | 0.059509 | -122.493 | 0.018311 | -121.8475 | -122.0078 | -121.8842 | 122.4197 | -0.068664 | -0.16022 | 122.5067 | 122.4426 | 122.4106 | 0.022888 | -0.009155 | -0.036621 | -0.036621 | -0.077819 | 0.60883 | 0.5722 | 0.44861 | 0.60883 | 0.48523 | 0.086975 | -0.027466 | 0.64545 | 122.5113 | 0.064087 | 122.5525 | 122.4838 | 122.5159 | -0.13275 | -122.5891 | 122.3923 | 122.4747 | 122.406 | 92.1204
2136.7344 | 122.6624 | -122.4106 | 0.07782 | 0.028839 | -0.0020892 | -0.033722 | 0.0014463 | -0.016771 | -0.026472 | -0.020042 | 0.011658 | -0.0061095 | 0.067394 | 0.04387 | -0.017085 | -0.0081774 | -0.014178 | 0.036621 | 0.018311 | -0.013733 | 0.073242 | 0.20599 | 0.082397 | 0.10071 | -30.6519 | 0.041199 | -122.4792 | 0.091553 | -121.756 | -121.9299 | -121.8338 | 122.3969 | -0.059509 | -0.004578 | 122.6166 | 122.5113 | 122.493 | 0.11444 | 0.09613 | -0.068665 | -0.036621 | 0.013733 | 0.6546 | 0.57678 | 0.48065 | 0.64545 | 0.54932 | 0.21973 | 0.086975 | 0.72327 | 122.5708 | 0.032044 | 122.5204 | 122.4289 | 122.4518 | -0.091553 | -122.5571 | 122.4838 | 122.5021 | 122.4472 | 91.7587
2138.5156 | 122.644 | -122.4106 | 0.09613 | 0.01358 | -0.0046526 | -0.035004 | 0.0012325 | -0.01784 | -0.027113 | -0.019615 | 0.0025024 | -0.0065369 | 0.065685 | 0.043656 | -0.016872 | -0.0094592 | -0.018664 | -0.059509 | 0.045776 | -0.018311 | -0.045776 | 0.068665 | -0.032043 | -0.013733 | -31.073 | 0.064087 | -122.4838 | 0.041199 | -121.8246 | -121.9666 | -121.843 | 122.3923 | -0.050354 | -0.14191 | 122.4792 | 122.3969 | 122.3785 | 0.004578 | -0.013732 | -0.073243 | -0.032043 | -0.054931 | 0.58594 | 0.56763 | 0.44403 | 0.64087 | 0.51727 | 0.086976 | -0.027465 | 0.65918 | 122.525 | 0.064087 | 122.5479 | 122.4564 | 122.4747 | -0.11444 | -122.58 | 122.3648 | 122.4518 | 122.3511 | 91.3376
2140.2969 | 122.6028 | -122.438 | 0.10071 | 0.028839 | -0.003371 | -0.033722 | 0.00016454 | -0.018053 | -0.028395 | -0.020469 | 0.008606 | -0.0061095 | 0.068035 | 0.042161 | -0.021358 | -0.0096728 | -0.017383 | -0.041199 | 0.027466 | -0.054932 | -0.032043 | 0.068665 | 0.018311 | 0.004578 | -31.4621 | 0.091553 | -122.5067 | -0.022888 | -121.8109 | -121.9711 | -121.8796 | 122.3831 | -0.073242 | -0.13275 | 122.5067 | 122.4426 | 122.4564 | 0.05951 | 0.073243 | -0.068665 | -0.009155 | -0.1236 | 0.62714 | 0.55847 | 0.46692 | 0.62714 | 0.53558 | 0.1236 | 0.022889 | 0.6958 | 122.4838 | 0.082398 | 122.5983 | 122.4655 | 122.5296 | -0.15564 | -122.6074 | 122.406 | 122.4152 | 122.3969 | 90.976
2142.0156 | 122.6898 | -122.4014 | 0.07782 | 0.0059509 | -0.0048664 | -0.035859 | -0.0013309 | -0.022967 | -0.02989 | -0.020256 | 0.008606 | -0.010596 | 0.063549 | 0.048356 | -0.019435 | -0.0079638 | -0.014392 | -0.032043 | 0.009155 | 0 | 0.013733 | 0.15564 | 0.068665 | 0.07782 | -31.8832 | 0.027466 | -122.4518 | 0.068665 | -121.7102 | -121.8704 | -121.8063 | 122.4014 | -0.068665 | -0.064087 | 122.5571 | 122.4792 | 122.4701 | 0.07782 | 0.068665 | -0.050354 | -0.050354 | -0.009155 | 0.69122 | 0.59509 | 0.53101 | 0.64545 | 0.58136 | 0.15564 | 0.013733 | 0.74158 | 122.5204 | 0.009155 | 122.4792 | 122.4106 | 122.4289 | -0.07782 | -122.5296 | 122.4152 | 122.4701 | 122.3694 | 90.5182
2143.7812 | 122.6166 | -122.4243 | 0.10529 | 0.02121 | -0.00016658 | -0.033936 | 0.00059174 | -0.018908 | -0.02754 | -0.023887 | 0.0055542 | -0.0061095 | 0.066967 | 0.040665 | -0.019649 | -0.0086048 | -0.015246 | 0 | 0.022888 | -0.018311 | 0 | 0.15106 | 0.041199 | 0.036621 | -32.2311 | 0.059509 | -122.4838 | 0.041199 | -121.7834 | -121.9482 | -121.8613 | 122.406 | -0.082398 | -0.10529 | 122.5754 | 122.4609 | 122.4655 | 0.054932 | 0.05951 | -0.05951 | -0.045777 | -0.064087 | 0.64087 | 0.56305 | 0.47607 | 0.62256 | 0.53558 | 0.16937 | 0.018311 | 0.70038 | 122.525 | 0.041199 | 122.5433 | 122.4472 | 122.4838 | -0.1236 | -122.5891 | 122.4243 | 122.4655 | 122.4243 | 90.1932
2145.5 | 122.6257 | -122.438 | 0.10529 | 0.01358 | -0.0020892 | -0.033082 | 0.0020871 | -0.017626 | -0.027754 | -0.023033 | 0.0055542 | -0.0071777 | 0.06718 | 0.047074 | -0.018794 | -0.0101 | -0.015674 | -0.027466 | 0.018311 | -0.036621 | 0.004578 | 0.14191 | 0.041199 | 0.045776 | -32.6386 | 0.050354 | -122.4884 | 0.050354 | -121.7651 | -121.9482 | -121.8567 | 122.4014 | -0.086975 | -0.10071 | 122.58 | 122.4838 | 122.4792 | 0.082397 | 0.07782 | -0.050354 | -0.054932 | -0.054932 | 0.67291 | 0.58136 | 0.48981 | 0.63171 | 0.54016 | 0.17853 | 0.041199 | 0.72327 | 122.5388 | 0.054932 | 122.5388 | 122.4564 | 122.4884 | -0.14191 | -122.5937 | 122.4426 | 122.4884 | 122.4106 | 89.7995
2147.2812 | 122.6898 | -122.3923 | 0.07782 | 0.044098 | -0.0010212 | -0.032013 | -0.0013309 | -0.015703 | -0.025831 | -0.023033 | 0.020813 | -0.0099549 | 0.065258 | 0.050492 | -0.016017 | -0.008391 | -0.012256 | 0.032043 | 0.022888 | -0.004578 | 0.068665 | 0.21973 | 0.086975 | 0.10986 | -32.991 | 0.041199 | -122.4884 | 0.10986 | -121.701 | -121.8613 | -121.8155 | 122.3877 | -0.054932 | -0.009155 | 122.612 | 122.5021 | 122.4792 | 0.11444 | 0.091553 | -0.09613 | -0.036621 | 0.032043 | 0.69122 | 0.57678 | 0.53101 | 0.67291 | 0.62714 | 0.22431 | 0.073243 | 0.78735 | 122.5983 | 0.027466 | 122.5296 | 122.4152 | 122.4335 | -0.082398 | -122.5662 | 122.4609 | 122.5021 | 122.4243 | 89.4012
2149 | 122.6349 | -122.4335 | 0.10529 | 0.01358 | -0.0037982 | -0.032227 | 0.00080534 | -0.015276 | -0.026899 | -0.024528 | 0.008606 | -0.0050415 | 0.066326 | 0.042374 | -0.020076 | -0.0092456 | -0.014392 | -0.004578 | 0.022888 | -0.018311 | -0.004578 | 0.14191 | 0.032043 | 0.041199 | -33.4671 | 0.059509 | -122.4884 | 0.045776 | -121.7606 | -121.9162 | -121.8567 | 122.4152 | -0.082398 | -0.10986 | 122.5754 | 122.4747 | 122.4655 | 0.05951 | 0.050354 | -0.054931 | -0.045777 | -0.05951 | 0.67291 | 0.57678 | 0.51727 | 0.63171 | 0.5722 | 0.16022 | 0.013733 | 0.72784 | 122.5342 | 0.041199 | 122.5479 | 122.4564 | 122.493 | -0.1236 | -122.5937 | 122.4289 | 122.4792 | 122.4289 | 88.9664
2150.7656 | 122.5479 | -122.4335 | 0.10986 | 0.0059509 | 0.00047422 | -0.034577 | 0.0016599 | -0.014849 | -0.029676 | -0.024101 | 0.0025024 | -0.0063233 | 0.067607 | 0.049424 | -0.018581 | -0.010955 | -0.011401 | -0.068665 | 0.050354 | -0.032043 | -0.07782 | 0.022888 | -0.068665 | -0.064087 | -33.9935 | 0.068665 | -122.4838 | -0.013733 | -121.8338 | -122.0123 | -121.9116 | 122.4014 | -0.059509 | -0.18768 | 122.4564 | 122.3694 | 122.3648 | -0.032044 | -0.036622 | -0.050354 | -0.041198 | -0.1236 | 0.59967 | 0.52185 | 0.42114 | 0.5722 | 0.4715 | 0.054931 | -0.045777 | 0.65002 | 122.4701 | 0.082397 | 122.5525 | 122.4838 | 122.5021 | -0.14191 | -122.5937 | 122.3557 | 122.4197 | 122.3648 | 88.4399
2152.5469 | 122.6074 | -122.4472 | 0.11444 | 0.028839 | -0.0029438 | -0.036927 | -4.906e-05 | -0.017626 | -0.028395 | -0.021965 | 0.014709 | -0.0065369 | 0.066967 | 0.046006 | -0.019649 | -0.0092456 | -0.017383 | -0.07782 | 0.068665 | -0.045776 | -0.059509 | 0.07782 | 0.027466 | 0.022888 | -34.2728 | 0.086975 | -122.5159 | -0.009155 | -121.7789 | -121.9482 | -121.875 | 122.4014 | -0.045776 | -0.17395 | 122.525 | 122.4701 | 122.4747 | 0.068664 | 0.073242 | -0.068664 | -0.027466 | -0.1236 | 0.66833 | 0.5722 | 0.49896 | 0.64087 | 0.56763 | 0.1236 | -0.013733 | 0.737 | 122.5067 | 0.11444 | 122.6028 | 122.5159 | 122.5342 | -0.16022 | -122.6303 | 122.3877 | 122.438 | 122.3694 | 88.1744
2154.2656 | 122.5891 | -122.4609 | 0.1236 | 0.051727 | -0.003371 | -0.035645 | -0.0017581 | -0.021044 | -0.028181 | -0.020256 | 0.014709 | -0.0082459 | 0.063121 | 0.044297 | -0.02029 | -0.010741 | -0.011187 | -0.059509 | 0.064087 | -0.032043 | -0.068665 | 0.073242 | 0.009155 | 0 | -34.8175 | 0.082397 | -122.4655 | -0.018311 | -121.8018 | -121.9482 | -121.8842 | 122.4289 | -0.059509 | -0.19226 | 122.5342 | 122.4609 | 122.4701 | 0.032043 | 0.041198 | -0.004578 | -0.041199 | -0.14191 | 0.65918 | 0.57678 | 0.5127 | 0.58136 | 0.51727 | 0.10529 | -0.036622 | 0.66376 | 122.4472 | 0.09613 | 122.5479 | 122.525 | 122.5433 | -0.15564 | -122.5891 | 122.3923 | 122.4426 | 122.4014 | 87.6434
2156.0469 | 122.5983 | -122.4289 | 0.11444 | -0.0016786 | -0.00038018 | -0.034363 | 0.00016454 | -0.016131 | -0.028181 | -0.025169 | 0.008606 | -0.0086731 | 0.067821 | 0.037247 | -0.018367 | -0.0088184 | -0.016314 | -0.013733 | 0.032043 | -0.013733 | -0.027466 | 0.10986 | 0.013733 | 0.004578 | -35.2707 | 0.050354 | -122.4838 | 0.009155 | -121.7789 | -121.9574 | -121.8933 | 122.4152 | -0.082398 | -0.14191 | 122.5388 | 122.4335 | 122.4426 | 0.018311 | 0.027466 | -0.054932 | -0.064087 | -0.10529 | 0.65002 | 0.53558 | 0.4715 | 0.59051 | 0.52643 | 0.1236 | -0.013733 | 0.70496 | 122.493 | 0.045776 | 122.5342 | 122.4609 | 122.4792 | -0.12817 | -122.5983 | 122.4014 | 122.438 | 122.4152 | 87.1582
2157.8281 | 122.6166 | -122.4426 | 0.09613 | 0.036468 | -0.0010212 | -0.035859 | -0.00069006 | -0.015917 | -0.027754 | -0.020042 | 0.0055542 | -0.0065369 | 0.065471 | 0.040879 | -0.017726 | -0.008391 | -0.015246 | -0.022888 | 0.045776 | -0.041199 | -0.032043 | 0.086975 | 0.032043 | 0.027466 | -35.7056 | 0.09613 | -122.4747 | 0.032043 | -121.7285 | -121.9208 | -121.8475 | 122.4014 | -0.050354 | -0.12817 | 122.5296 | 122.4701 | 122.4747 | 0.068665 | 0.073242 | -0.032043 | 0 | -0.064087 | 0.71411 | 0.59509 | 0.52185 | 0.62714 | 0.55389 | 0.12817 | 0.009156 | 0.74615 | 122.5067 | 0.086975 | 122.5708 | 122.4884 | 122.5388 | -0.13733 | -122.5708 | 122.4106 | 122.4747 | 122.4197 | 86.7371
2159.6406 | 122.6028 | -122.4472 | 0.09613 | 0.036468 | -0.0018756 | -0.036713 | -0.0015445 | -0.019121 | -0.029036 | -0.022605 | 0.017761 | -0.0071777 | 0.066539 | 0.04152 | -0.020503 | -0.0086048 | -0.017596 | -0.036621 | 0.064087 | -0.036621 | -0.050354 | 0.073242 | 0.027466 | 0.018311 | -36.0992 | 0.068665 | -122.4884 | 0.018311 | -121.7422 | -121.9299 | -121.8658 | 122.4106 | -0.032043 | -0.14648 | 122.5204 | 122.4655 | 122.4747 | 0.054932 | 0.064087 | -0.041198 | -0.027465 | -0.077819 | 0.70496 | 0.58136 | 0.51727 | 0.62256 | 0.55847 | 0.10986 | -0.013733 | 0.74615 | 122.5067 | 0.10071 | 122.5571 | 122.5113 | 122.5159 | -0.13275 | -122.5845 | 122.3969 | 122.4655 | 122.4106 | 86.348
2161.4375 | 122.6303 | -122.406 | 0.091553 | 0.0059509 | -0.0037982 | -0.034363 | -0.0017581 | -0.01848 | -0.030317 | -0.023033 | 0.0025024 | -0.010169 | 0.063549 | 0.043229 | -0.021572 | -0.009032 | -0.015674 | 0.009155 | 0 | -0.004578 | 0.032043 | 0.1831 | 0.10986 | 0.091553 | -36.5845 | 0.045776 | -122.4564 | 0.054932 | -121.7102 | -121.875 | -121.8521 | 122.4014 | -0.091553 | -0.05951 | 122.5891 | 122.4976 | 122.5159 | 0.096131 | 0.11444 | -0.050354 | -0.045777 | -0.036621 | 0.6958 | 0.55389 | 0.53101 | 0.60425 | 0.58136 | 0.18768 | 0.036621 | 0.74616 | 122.5113 | 0.004578 | 122.5021 | 122.406 | 122.4518 | -0.096131 | -122.5479 | 122.438 | 122.4609 | 122.4152 | 85.8215
2163.1719 | 122.6532 | -122.4106 | 0.091553 | 0.0059509 | -0.0048664 | -0.036286 | -0.0021853 | -0.017199 | -0.030745 | -0.021751 | 0.0025024 | -0.0095275 | 0.065044 | 0.042161 | -0.021572 | -0.011382 | -0.014392 | 0.018311 | -0.013733 | 0.018311 | 0.036621 | 0.20142 | 0.10986 | 0.091553 | -37.0193 | 0.032043 | -122.4564 | 0.045776 | -121.6827 | -121.8613 | -121.8521 | 122.4289 | -0.10529 | -0.054932 | 122.612 | 122.5021 | 122.5204 | 0.073242 | 0.091552 | -0.045777 | -0.05951 | -0.045777 | 0.72784 | 0.55847 | 0.54932 | 0.60425 | 0.59509 | 0.18311 | 0.01831 | 0.77362 | 122.5021 | -0.032044 | 122.4884 | 122.3969 | 122.4426 | -0.073242 | -122.5479 | 122.4472 | 122.4564 | 122.4289 | 85.3912
2164.9688 | 122.5708 | -122.4335 | 0.11902 | 0.02121 | -0.0042254 | -0.033936 | 0.00080534 | -0.016344 | -0.029036 | -0.022605 | 0.017761 | -0.0052551 | 0.065899 | 0.040452 | -0.023067 | -0.010527 | -0.015246 | -0.045776 | 0.036621 | -0.027466 | -0.07782 | 0.073242 | 0.013733 | 0.013733 | -37.5412 | 0.086975 | -122.5067 | -0.018311 | -121.7789 | -121.9345 | -121.9025 | 122.406 | -0.082398 | -0.19684 | 122.5067 | 122.4472 | 122.4472 | 0.041199 | 0.041199 | -0.073242 | -0.032044 | -0.13733 | 0.6546 | 0.53101 | 0.49896 | 0.60425 | 0.5722 | 0.10071 | -0.050354 | 0.72784 | 122.4884 | 0.064087 | 122.5937 | 122.4701 | 122.5204 | -0.14649 | -122.6257 | 122.3557 | 122.4152 | 122.3877 | 84.8923
2166.6875 | 122.7173 | -122.3831 | 0.07782 | 0.01358 | -0.0023028 | -0.033936 | -0.00026266 | -0.016985 | -0.029463 | -0.024314 | 0.020813 | -0.0082459 | 0.065044 | 0.042374 | -0.013881 | -0.0064684 | -0.019091 | 0.027466 | -0.013733 | 0.041199 | 0.054932 | 0.2243 | 0.09613 | 0.10986 | -37.8937 | 0.032043 | -122.4289 | 0.13733 | -121.6278 | -121.8246 | -121.7743 | 122.4243 | -0.091553 | -0.022888 | 122.6074 | 122.493 | 122.4792 | 0.068664 | 0.054931 | -0.045776 | -0.045777 | 0.059509 | 0.75531 | 0.60883 | 0.55847 | 0.6546 | 0.60425 | 0.18311 | 0.013733 | 0.80109 | 122.5662 | -0.054932 | 122.4609 | 122.3694 | 122.4152 | -0.036621 | -122.5067 | 122.438 | 122.5204 | 122.4106 | 84.4894
2168.4844 | 122.699 | -122.3694 | 0.10071 | 0.0059509 | -0.003371 | -0.034791 | 0.00016454 | -0.014422 | -0.028181 | -0.020683 | 0.017761 | -0.0078185 | 0.065258 | 0.049637 | -0.016017 | -0.0071094 | -0.017596 | 0.027466 | 0 | 0.032043 | 0.07782 | 0.21515 | 0.082397 | 0.11902 | -38.3743 | 0.059509 | -122.438 | 0.12817 | -121.6232 | -121.8292 | -121.788 | 122.4014 | -0.10071 | -0.022888 | 122.5845 | 122.4884 | 122.4518 | 0.086976 | 0.050354 | -0.068664 | -0.041199 | 0.027466 | 0.74615 | 0.58136 | 0.54016 | 0.65002 | 0.60883 | 0.18311 | 0.045777 | 0.81482 | 122.5662 | -0.032043 | 122.4976 | 122.3694 | 122.4289 | -0.068665 | -122.5388 | 122.4472 | 122.4976 | 122.3969 | 83.9951
2170.2344 | 122.6898 | -122.3969 | 0.073242 | 0.01358 | -0.0012348 | -0.036927 | 0.00080534 | -0.018908 | -0.029249 | -0.024101 | -0.00054937 | -0.0095275 | 0.063549 | 0.040879 | -0.018794 | -0.0077502 | -0.016101 | -0.004578 | 0.013733 | 0.013733 | 0.073242 | 0.21973 | 0.11444 | 0.11444 | -38.736 | 0.004578 | -122.4426 | 0.11444 | -121.6095 | -121.7972 | -121.7972 | 122.4106 | -0.059509 | 0 | 122.6166 | 122.5113 | 122.5113 | 0.10071 | 0.10071 | -0.045776 | -0.068664 | 0.041199 | 0.78735 | 0.59967 | 0.59967 | 0.64545 | 0.64545 | 0.20599 | 0.059509 | 0.83313 | 122.5571 | 0 | 122.4472 | 122.4106 | 122.4014 | -0.059509 | -122.5159 | 122.4701 | 122.5113 | 122.3923 | 83.6609
2172.0156 | 122.5708 | -122.4564 | 0.11902 | 0.0059509 | -0.00273 | -0.034577 | 0.0012325 | -0.018267 | -0.029676 | -0.024742 | 0.0025024 | -0.0076049 | 0.068462 | 0.040452 | -0.015804 | -0.008391 | -0.012896 | -0.054932 | 0.050354 | -0.022888 | -0.073242 | 0.032043 | -0.064087 | -0.018311 | -39.4363 | 0.059509 | -122.493 | -0.004578 | -121.7926 | -121.9528 | -121.8842 | 122.4335 | -0.068665 | -0.19226 | 122.4884 | 122.438 | 122.3923 | 0.004577 | -0.041199 | -0.036621 | -0.05951 | -0.1236 | 0.66376 | 0.5722 | 0.50354 | 0.60883 | 0.54016 | 0.054931 | -0.050354 | 0.70038 | 122.4884 | 0.073242 | 122.5525 | 122.5067 | 122.5159 | -0.14191 | -122.612 | 122.3831 | 122.4518 | 122.4014 | 83.02
2173.7812 | 122.5845 | -122.4289 | 0.10529 | 0.01358 | -0.0010212 | -0.034791 | -0.0013309 | -0.019335 | -0.029463 | -0.024955 | 0.0055542 | -0.0069641 | 0.065899 | 0.046433 | -0.020076 | -0.010741 | -0.016101 | 0.009155 | 0 | 0 | 0.004578 | 0.13733 | 0.064087 | 0.064087 | -39.6286 | 0.068665 | -122.4655 | 0.009155 | -121.7239 | -121.907 | -121.875 | 122.4289 | -0.10529 | -0.10071 | 122.5662 | 122.493 | 122.493 | 0.064087 | 0.064087 | -0.036621 | -0.036621 | -0.096131 | 0.70496 | 0.55389 | 0.52185 | 0.59051 | 0.55847 | 0.13733 | 0.004578 | 0.74158 | 122.4747 | 0 | 122.5342 | 122.4289 | 122.4976 | -0.10529 | -122.5708 | 122.4335 | 122.438 | 122.438 | 82.8003
2175.5 | 122.6074 | -122.4518 | 0.10529 | 0.0059509 | -0.0046526 | -0.034791 | 0.00037814 | -0.018267 | -0.02989 | -0.026664 | 0.0055542 | -0.0071777 | 0.06483 | 0.048142 | -0.021572 | -0.0081774 | -0.018023 | 0.004578 | 0.004578 | 0.022888 | 0.027466 | 0.18768 | 0.10529 | 0.086975 | -40.0406 | 0.050354 | -122.4655 | 0.045776 | -121.6736 | -121.8613 | -121.8475 | 122.4747 | -0.10071 | -0.07782 | 122.6395 | 122.5388 | 122.5571 | 0.064087 | 0.082398 | -0.013733 | -0.054932 | -0.05951 | 0.7782 | 0.60425 | 0.59051 | 0.61798 | 0.60425 | 0.16479 | 0.004578 | 0.79193 | 122.5113 | -0.01831 | 122.5159 | 122.4564 | 122.5021 | -0.082398 | -122.5708 | 122.4792 | 122.4976 | 122.4564 | 82.4112
2177.2188 | 122.6944 | -122.3602 | 0.059509 | 0.02121 | -0.0023028 | -0.033082 | 0.0010189 | -0.015703 | -0.029676 | -0.021965 | -0.00054937 | -0.0099549 | 0.06483 | 0.050706 | -0.01559 | -0.0079638 | -0.013751 | 0.045776 | -0.004578 | 0.022888 | 0.059509 | 0.19684 | 0.082397 | 0.09613 | -40.6265 | 0.050354 | -122.4564 | 0.13733 | -121.6095 | -121.8018 | -121.7743 | 122.3831 | -0.064087 | 0 | 122.5571 | 122.4564 | 122.4426 | 0.073242 | 0.059509 | -0.096131 | -0.009155 | 0.07782 | 0.75073 | 0.58594 | 0.55847 | 0.68207 | 0.6546 | 0.17395 | 0.036621 | 0.84686 | 122.5937 | -0.027466 | 122.5067 | 122.3557 | 122.4106 | -0.036621 | -122.5159 | 122.4197 | 122.4976 | 122.406 | 81.7337
2179 | 122.5983 | -122.4289 | 0.10529 | 0.028839 | -0.00273 | -0.033936 | -0.00047626 | -0.019549 | -0.028608 | -0.022819 | 0.008606 | -0.0067505 | 0.065899 | 0.040452 | -0.020503 | -0.0088184 | -0.017596 | 0 | 0.036621 | -0.004578 | 0.013733 | 0.15106 | 0.032043 | 0.050354 | -41.0934 | 0.064087 | -122.4564 | 0.045776 | -121.6919 | -121.8887 | -121.8567 | 122.4243 | -0.068665 | -0.091553 | 122.58 | 122.4792 | 122.4609 | 0.054932 | 0.036621 | -0.027466 | -0.041199 | -0.05951 | 0.737 | 0.5722 | 0.54016 | 0.59967 | 0.56763 | 0.15564 | 0.018311 | 0.76447 | 122.5021 | 0.041199 | 122.5204 | 122.4655 | 122.493 | -0.10986 | -122.5616 | 122.4426 | 122.4747 | 122.4289 | 81.3354
2180.7812 | 122.6624 | -122.4289 | 0.07782 | 0.01358 | -0.0042254 | -0.035004 | -0.0017581 | -0.016985 | -0.03224 | -0.023674 | 0.008606 | -0.010169 | 0.065899 | 0.046219 | -0.017085 | -0.0077502 | -0.011615 | -0.013733 | 0.013733 | -0.009155 | 0.004578 | 0.14648 | 0.064087 | 0.068665 | -41.5604 | 0.036621 | -122.4426 | 0.086975 | -121.6187 | -121.8018 | -121.8201 | 122.4197 | -0.064087 | -0.073242 | 122.5754 | 122.4976 | 122.493 | 0.07782 | 0.073242 | -0.013733 | -0.041199 | 0.009155 | 0.81024 | 0.60883 | 0.62714 | 0.62256 | 0.64087 | 0.15564 | 0.013733 | 0.82398 | 122.5296 | 0.022888 | 122.4792 | 122.4426 | 122.4655 | -0.086975 | -122.5204 | 122.4335 | 122.5159 | 122.4152 | 80.8685
2182.4844 | 122.5937 | -122.4106 | 0.11902 | 0.02121 | -0.0010212 | -0.035645 | 0.0018735 | -0.01549 | -0.027327 | -0.022392 | 0.0025024 | -0.0076049 | 0.067607 | 0.04451 | -0.018154 | -0.010314 | -0.016101 | 0.009155 | 0.036621 | -0.013733 | 0.004578 | 0.1236 | 0.018311 | 0.036621 | -41.954 | 0.059509 | -122.4655 | 0.018311 | -121.6965 | -121.8979 | -121.8613 | 122.3969 | -0.082398 | -0.11444 | 122.5342 | 122.4472 | 122.4289 | 0.050354 | 0.032044 | -0.054932 | -0.05951 | -0.10071 | 0.71411 | 0.54932 | 0.5127 | 0.60425 | 0.56763 | 0.13733 | 0.018311 | 0.76904 | 122.4838 | 0.050354 | 122.525 | 122.4472 | 122.4701 | -0.13275 | -122.5845 | 122.4152 | 122.4289 | 122.4197 | 80.4565
2184.2188 | 122.7081 | -122.3969 | 0.064087 | -0.0016786 | -0.0025164 | -0.034363 | -0.0017581 | -0.01784 | -0.029463 | -0.025169 | 0.0055542 | -0.0088867 | 0.063335 | 0.04686 | -0.018367 | -0.0077502 | -0.012469 | 0.004578 | 0.004578 | 0.018311 | 0.07782 | 0.23346 | 0.14191 | 0.1236 | -42.1967 | 0.041199 | -122.4197 | 0.11902 | -121.5591 | -121.7422 | -121.7697 | 122.4152 | -0.059509 | 0.013733 | 122.6303 | 122.5204 | 122.5388 | 0.10528 | 0.1236 | -0.022888 | -0.022888 | 0.054932 | 0.83771 | 0.62714 | 0.6546 | 0.65003 | 0.67749 | 0.21515 | 0.059509 | 0.8606 | 122.5388 | -0.013733 | 122.4609 | 122.4014 | 122.4381 | -0.045776 | -122.4838 | 122.4747 | 122.5159 | 122.4014 | 80.2002
2185.9688 | 122.6715 | -122.3785 | 0.10071 | 0.01358 | -0.0023028 | -0.034791 | 0.0023007 | -0.019976 | -0.030531 | -0.023033 | -0.00054937 | -0.0065369 | 0.065899 | 0.04451 | -0.017299 | -0.0096728 | -0.013324 | -0.054932 | 0.032043 | -0.027466 | -0.018311 | 0.09613 | -0.009155 | 0.013733 | -42.8284 | 0.050354 | -122.4655 | 0.09613 | -121.6232 | -121.8338 | -121.8201 | 122.3511 | -0.068665 | -0.11902 | 122.4747 | 122.3923 | 122.3694 | 0.041199 | 0.018311 | -0.086975 | -0.050354 | -0.004578 | 0.75531 | 0.55847 | 0.54474 | 0.64545 | 0.63171 | 0.1236 | 0.009155 | 0.84228 | 122.5616 | 0.059509 | 122.5159 | 122.4106 | 122.4289 | -0.12817 | -122.5662 | 122.3602 | 122.4747 | 122.3236 | 79.5502
2187.6875 | 122.6532 | -122.4152 | 0.09613 | 0.02121 | -0.004439 | -0.035431 | -0.0015445 | -0.015703 | -0.02989 | -0.023674 | 0.0055542 | -0.0086731 | 0.06718 | 0.042588 | -0.021572 | -0.0098864 | -0.016528 | -0.013733 | 0.022888 | 0.009155 | 0.004578 | 0.14191 | 0.045776 | 0.059509 | -43.3182 | 0.041199 | -122.4564 | 0.059509 | -121.6095 | -121.8018 | -121.8155 | 122.4243 | -0.073242 | -0.091552 | 122.5571 | 122.4747 | 122.4609 | 0.050354 | 0.036621 | -0.041199 | -0.054931 | -0.036621 | 0.80566 | 0.59967 | 0.6134 | 0.64087 | 0.6546 | 0.13275 | -0.004577 | 0.84686 | 122.5159 | 0.013733 | 122.4976 | 122.438 | 122.4564 | -0.086975 | -122.5525 | 122.4197 | 122.4747 | 122.4014 | 79.097
2189.4062 | 122.5937 | -122.4014 | 0.082397 | 0.0059509 | -0.0040118 | -0.031586 | -0.00047626 | -0.017626 | -0.029463 | -0.022178 | 0.0055542 | -0.0065369 | 0.06483 | 0.045579 | -0.017726 | -0.0079638 | -0.017596 | -0.036621 | 0.045776 | -0.013733 | -0.064087 | 0.064087 | -0.032043 | 0.009155 | -43.8309 | 0.073242 | -122.4701 | 0.027466 | -121.6782 | -121.8933 | -121.8384 | 122.3877 | -0.036621 | -0.14648 | 122.4655 | 122.4106 | 122.3694 | 0.022888 | -0.01831 | -0.068665 | -0.009155 | -0.054931 | 0.72327 | 0.56305 | 0.50812 | 0.63171 | 0.57678 | 0.07782 | -0.050354 | 0.79193 | 122.4976 | 0.059509 | 122.5433 | 122.4472 | 122.4747 | -0.09613 | -122.5525 | 122.3373 | 122.4289 | 122.3648 | 78.5706
2191.1094 | 122.6074 | -122.4243 | 0.11902 | 0.01358 | 0.00090162 | -0.0365 | 0.0020871 | -0.017412 | -0.027327 | -0.022819 | 0.008606 | -0.0071777 | 0.066753 | 0.043229 | -0.019008 | -0.008391 | -0.013537 | 0 | 0.045776 | -0.022888 | 0.013733 | 0.12817 | 0.054932 | 0.036621 | -44.1055 | 0.086975 | -122.4747 | 0.041199 | -121.6187 | -121.8292 | -121.8338 | 122.4014 | -0.073243 | -0.10529 | 122.5525 | 122.4609 | 122.4792 | 0.059509 | 0.07782 | -0.050354 | -0.032044 | -0.07782 | 0.80566 | 0.59052 | 0.59509 | 0.64087 | 0.64545 | 0.15106 | 0.036621 | 0.85602 | 122.5159 | 0.068664 | 122.5616 | 122.4701 | 122.5113 | -0.14191 | -122.5937 | 122.438 | 122.4655 | 122.4243 | 78.3188
2192.8438 | 122.58 | -122.4472 | 0.11444 | 0.0059509 | -0.00016658 | -0.034363 | 0.00080534 | -0.018908 | -0.028608 | -0.022819 | 0.0025024 | -0.0071777 | 0.065899 | 0.054551 | -0.020931 | -0.0092456 | -0.01546 | -0.045776 | 0.054932 | -0.022888 | -0.059509 | 0.054932 | -0.041199 | -0.013733 | -44.5908 | 0.068665 | -122.4518 | 0 | -121.6644 | -121.8887 | -121.843 | 122.4243 | -0.059509 | -0.17395 | 122.5021 | 122.4335 | 122.406 | 0.009155 | -0.018311 | -0.004577 | -0.045776 | -0.11444 | 0.78278 | 0.60425 | 0.55847 | 0.60882 | 0.56305 | 0.07782 | -0.036621 | 0.78735 | 122.4518 | 0.07782 | 122.5204 | 122.5021 | 122.5159 | -0.13733 | -122.5662 | 122.3877 | 122.4472 | 122.4014 | 77.8564
2194.5469 | 122.5433 | -122.4243 | 0.13733 | -0.0016786 | 0.00026062 | -0.033509 | 0.00016454 | -0.0095083 | -0.029036 | -0.020897 | 0.0025024 | -0.0061095 | 0.066539 | 0.044083 | -0.018154 | -0.0092456 | -0.022082 | -0.036621 | 0.036621 | -0.009155 | -0.068665 | 0.054932 | -0.050354 | -0.022888 | -44.9615 | 0.082397 | -122.4609 | -0.004578 | -121.6919 | -121.9208 | -121.875 | 122.4152 | -0.10071 | -0.20599 | 122.4792 | 122.4014 | 122.374 | -0.013733 | -0.041199 | -0.036621 | -0.054932 | -0.14191 | 0.73242 | 0.54932 | 0.50354 | 0.58594 | 0.54016 | 0.064087 | -0.05951 | 0.76904 | 122.4564 | 0.045776 | 122.5433 | 122.4609 | 122.5067 | -0.14648 | -122.5983 | 122.3557 | 122.4197 | 122.3877 | 77.4628
2196.25 | 121.907 | -121.6095 | 0.10529 | -0.67307 | 0.032518 | -0.034363 | 0.040967 | -0.018694 | -0.02989 | -0.023887 | 0.0055542 | -0.0080321 | 0.064403 | 0.041733 | -0.020931 | -0.010527 | -0.015033 | -0.009155 | 0.009155 | 0.022888 | 0.041199 | 0.16022 | 0.10529 | 0.07782 | -39.2899 | 0.054932 | -121.7056 | 0.027466 | -120.7947 | -121.0464 | -121.106 | 121.6324 | -0.096131 | -0.064087 | 121.7697 | 121.6873 | 121.7148 | 0.054932 | 0.082398 | -0.09613 | -0.050354 | -0.07782 | 0.81482 | 0.50354 | 0.56305 | 0.59967 | 0.65918 | 0.13733 | 0.018311 | 0.91095 | 121.7331 | -0.013733 | 121.7606 | 121.6187 | 121.6644 | -0.082398 | -121.8109 | 121.6507 | 121.637 | 121.6003 | 82.3196
2197.9531 | 122.4609 | -122.2641 | 0.12817 | 0.01358 | 0.025041 | -0.032013 | 0.044385 | -0.018267 | -0.030317 | -0.020897 | -0.00054937 | -0.0063233 | 0.066753 | 0.043015 | -0.018581 | -0.0094592 | -0.015246 | -0.059509 | 0.054932 | 0 | -0.07782 | 0.027466 | -0.045776 | 0 | -40.0681 | 0.07782 | -122.3053 | 0.013733 | -121.4767 | -121.7331 | -121.7239 | 122.2641 | -0.073242 | -0.20599 | 122.2916 | 122.2641 | 122.2183 | 0 | -0.045776 | -0.041199 | -0.050354 | -0.11444 | 0.78735 | 0.54016 | 0.53101 | 0.58136 | 0.5722 | 0.027466 | -0.07782 | 0.82855 | 122.319 | 0.054932 | 122.3831 | 122.319 | 122.3419 | -0.12817 | -122.4335 | 122.1863 | 122.2778 | 122.2046 | 82.196
2199.6875 | 122.5296 | -122.2778 | 0.10986 | 0.01358 | 0.030595 | -0.035004 | 0.043316 | -0.013781 | -0.029036 | -0.024742 | 0.008606 | -0.0069641 | 0.068035 | 0.048356 | -0.019435 | -0.0088184 | -0.016314 | 0.009155 | 0.050354 | -0.022888 | 0 | 0.14191 | 0.036621 | 0.036621 | -40.1825 | 0.082397 | -122.3373 | 0.073242 | -121.4127 | -121.6782 | -121.7102 | 122.2549 | -0.059509 | -0.10986 | 122.4197 | 122.3145 | 122.3145 | 0.059509 | 0.059509 | -0.059509 | -0.027466 | -0.036621 | 0.86517 | 0.56763 | 0.59967 | 0.62714 | 0.65918 | 0.16479 | 0.022888 | 0.92468 | 122.4106 | 0.073242 | 122.4197 | 122.3282 | 122.3602 | -0.13275 | -122.4472 | 122.2778 | 122.3511 | 122.287 | 82.0953
2201.3906 | 122.4976 | -122.3328 | 0.1236 | -0.0093076 | 0.028672 | -0.036072 | 0.042248 | -0.016344 | -0.03224 | -0.02346 | 0.008606 | -0.011878 | 0.064617 | 0.040879 | -0.021358 | -0.011168 | -0.014605 | -0.018311 | 0.018311 | 0 | -0.032043 | 0.1236 | 0.032043 | 0.032043 | -40.6723 | 0.059509 | -122.3419 | -0.004578 | -121.4676 | -121.7194 | -121.7789 | 122.3328 | -0.10528 | -0.15564 | 122.4564 | 122.3648 | 122.3648 | 0.032043 | 0.032043 | -0.009155 | -0.064087 | -0.12817 | 0.86517 | 0.55389 | 0.6134 | 0.56305 | 0.62256 | 0.1236 | -0.032043 | 0.87433 | 122.3373 | 0.018311 | 122.4014 | 122.3511 | 122.3923 | -0.1236 | -122.4655 | 122.3007 | 122.3282 | 122.3145 | 81.6605
2203.0938 | 122.5342 | -122.3328 | 0.11444 | 0.036468 | 0.028672 | -0.032868 | 0.043316 | -0.01549 | -0.028822 | -0.025383 | 0.014709 | -0.0071777 | 0.06419 | 0.042588 | -0.017726 | -0.0092456 | -0.014605 | -0.004578 | 0.054932 | -0.027466 | -0.022888 | 0.10071 | 0.041199 | 0.036621 | -40.892 | 0.073242 | -122.3831 | 0.059509 | -121.4218 | -121.701 | -121.7422 | 122.3053 | -0.059509 | -0.13733 | 122.4335 | 122.3694 | 122.374 | 0.064087 | 0.068665 | -0.050354 | -0.041199 | -0.054932 | 0.91095 | 0.59051 | 0.63171 | 0.64087 | 0.68207 | 0.12817 | 0.004578 | 0.9613 | 122.4426 | 0.082398 | 122.4564 | 122.3877 | 122.406 | -0.14191 | -122.4976 | 122.3099 | 122.3923 | 122.3282 | 81.4407
2204.8125 | 122.5571 | -122.3282 | 0.10986 | 0.02121 | 0.02675 | -0.0318 | 0.044598 | -0.015917 | -0.027754 | -0.023246 | 0.008606 | -0.0088867 | 0.066326 | 0.045151 | -0.018154 | -0.0088184 | -0.013537 | 0.009155 | 0.059509 | 0.004578 | 0 | 0.14648 | 0.032043 | 0.054932 | -41.1804 | 0.07782 | -122.3648 | 0.073242 | -121.4218 | -121.6873 | -121.7514 | 122.3328 | -0.050354 | -0.10986 | 122.4747 | 122.3831 | 122.3602 | 0.050354 | 0.027465 | -0.036621 | -0.032043 | -0.036621 | 0.90637 | 0.57678 | 0.64087 | 0.6134 | 0.67749 | 0.14191 | -0.004578 | 0.94299 | 122.438 | 0.054931 | 122.4426 | 122.3877 | 122.406 | -0.10529 | -122.4747 | 122.3282 | 122.4014 | 122.3373 | 81.1478
2206.6094 | 122.6303 | -122.3328 | 0.082397 | 0.01358 | 0.027177 | -0.034791 | 0.04118 | -0.017199 | -0.029249 | -0.022819 | 0.0055542 | -0.0078185 | 0.066539 | 0.046647 | -0.014308 | -0.0071094 | -0.016742 | -0.022888 | 0.036621 | 0.013733 | 0.018311 | 0.15106 | 0.050354 | 0.059509 | -41.7297 | 0.045776 | -122.3602 | 0.13275 | -121.3669 | -121.6415 | -121.6827 | 122.3465 | -0.045776 | -0.064086 | 122.4838 | 122.3923 | 122.3831 | 0.045776 | 0.036621 | -0.027465 | -0.036621 | 0.050354 | 0.96588 | 0.65002 | 0.69122 | 0.67749 | 0.71869 | 0.13733 | 0.004578 | 0.99335 | 122.493 | 0.022888 | 122.406 | 122.3694 | 122.3785 | -0.068664 | -122.4426 | 122.3511 | 122.4655 | 122.3099 | 80.603
2208.4219 | 122.5204 | -122.3648 | 0.12817 | 0.0059509 | 0.029527 | -0.035645 | 0.042889 | -0.01549 | -0.027754 | -0.02346 | 0.0025024 | -0.0080321 | 0.063762 | 0.042801 | -0.018794 | -0.010527 | -0.012683 | -0.041199 | 0.041199 | -0.027466 | -0.059509 | 0.036621 | -0.036621 | -0.022888 | -42.2653 | 0.07782 | -122.3923 | 0.018311 | -121.5042 | -121.788 | -121.8155 | 122.3373 | -0.086975 | -0.18768 | 122.4014 | 122.3419 | 122.3282 | 0.004578 | -0.009155 | -0.027466 | -0.050354 | -0.10986 | 0.8606 | 0.54932 | 0.57678 | 0.57678 | 0.60425 | 0.064087 | -0.032043 | 0.88806 | 122.4106 | 0.068665 | 122.4701 | 122.406 | 122.4426 | -0.15564 | -122.5204 | 122.3053 | 122.3831 | 122.3236 | 80.0995
2210.2344 | 122.5616 | -122.374 | 0.10529 | 0.02121 | 0.028032 | -0.035431 | 0.042035 | -0.018267 | -0.028181 | -0.020469 | -0.00054937 | -0.0084595 | 0.066967 | 0.041947 | -0.018581 | -0.009032 | -0.016528 | 0.004578 | 0.045776 | 0.004578 | 0.013733 | 0.14648 | 0.059509 | 0.054932 | -42.4805 | 0.059509 | -122.3694 | 0.045776 | -121.4172 | -121.7102 | -121.7651 | 122.3785 | -0.05951 | -0.091553 | 122.5204 | 122.4289 | 122.4335 | 0.050354 | 0.054931 | 0.004577 | -0.045777 | -0.05951 | 0.95673 | 0.60883 | 0.66376 | 0.60425 | 0.65918 | 0.14191 | 0.009155 | 0.95215 | 122.4152 | 0.041198 | 122.4289 | 122.4197 | 122.4335 | -0.10071 | -122.4747 | 122.3877 | 122.4197 | 122.3785 | 79.8935
2212.0312 | 122.612 | -122.3648 | 0.091553 | 0.02121 | 0.022691 | -0.033722 | 0.041821 | -0.018908 | -0.027967 | -0.019401 | 0.0055542 | -0.0091003 | 0.06718 | 0.043442 | -0.019222 | -0.0071094 | -0.015887 | -0.013733 | 0.009155 | 0.018311 | 0.022888 | 0.16479 | 0.068665 | 0.07782 | -42.9749 | 0.054932 | -122.374 | 0.086975 | -121.4035 | -121.6736 | -121.756 | 122.3831 | -0.082398 | -0.068665 | 122.5296 | 122.4426 | 122.4335 | 0.059509 | 0.050354 | -0.009155 | -0.036621 | -0.004578 | 0.9613 | 0.60883 | 0.69122 | 0.61798 | 0.70038 | 0.14648 | 0.004577 | 0.97046 | 122.4609 | -0.009156 | 122.4289 | 122.374 | 122.4197 | -0.073242 | -122.4655 | 122.3877 | 122.4518 | 122.3511 | 79.39
2213.8125 | 122.6257 | -122.3373 | 0.091553 | 0.01358 | 0.028459 | -0.033082 | 0.043103 | -0.01784 | -0.027754 | -0.023246 | 0.017761 | -0.0078185 | 0.065685 | 0.052842 | -0.018154 | -0.0071094 | -0.012896 | 0.018311 | 0.018311 | 0.022888 | 0.054932 | 0.21515 | 0.086975 | 0.10529 | -43.1992 | 0.050354 | -122.3831 | 0.09613 | -121.376 | -121.6415 | -121.7331 | 122.3602 | -0.073242 | -0.036621 | 122.5525 | 122.4426 | 122.4243 | 0.082398 | 0.064087 | -0.045777 | -0.041199 | 0.004577 | 0.9613 | 0.60425 | 0.6958 | 0.65002 | 0.74158 | 0.19226 | 0.032044 | 1.0071 | 122.4792 | -0.004577 | 122.4335 | 122.3557 | 122.3877 | -0.068665 | -122.4747 | 122.3923 | 122.4335 | 122.3557 | 79.1382
2215.625 | 122.5388 | -122.3785 | 0.13733 | -0.0016786 | 0.028032 | -0.034791 | 0.044171 | -0.014208 | -0.029676 | -0.02111 | 0.0025024 | -0.0054687 | 0.065899 | 0.04451 | -0.016872 | -0.0086048 | -0.0208 | -0.050354 | 0.027466 | -0.009155 | -0.068665 | 0.041199 | -0.045776 | -0.032043 | -43.8263 | 0.07782 | -122.4152 | 0 | -121.4859 | -121.756 | -121.8155 | 122.3694 | -0.10986 | -0.20599 | 122.4197 | 122.3465 | 122.3328 | -0.022888 | -0.036621 | -0.036621 | -0.059509 | -0.13733 | 0.89264 | 0.56305 | 0.62256 | 0.59967 | 0.65918 | 0.050354 | -0.05951 | 0.92926 | 122.4152 | 0.036621 | 122.493 | 122.406 | 122.4564 | -0.14648 | -122.5525 | 122.3099 | 122.3785 | 122.3282 | 78.5522
2217.3594 | 122.5433 | -122.3877 | 0.10529 | 0.01358 | 0.028672 | -0.035431 | 0.044171 | -0.019549 | -0.030745 | -0.021324 | 0.0055542 | -0.0071777 | 0.065899 | 0.046006 | -0.019222 | -0.0094592 | -0.015033 | 0.004578 | 0.036621 | 0.009155 | -0.013733 | 0.11902 | 0.032043 | 0.041199 | -44.0826 | 0.064087 | -122.3969 | 0.041199 | -121.4264 | -121.7285 | -121.7972 | 122.3969 | -0.068665 | -0.11902 | 122.5067 | 122.4289 | 122.4197 | 0.032044 | 0.022888 | -0.009156 | -0.041199 | -0.064087 | 0.9613 | 0.59051 | 0.65918 | 0.59967 | 0.66833 | 0.10986 | -0.022888 | 0.97046 | 122.4381 | 0.027466 | 122.4609 | 122.4243 | 122.4518 | -0.096131 | -122.5021 | 122.374 | 122.4289 | 122.3923 | 78.3051
2219.1406 | 122.5388 | -122.3969 | 0.1236 | 0.0059509 | 0.027177 | -0.035218 | 0.043957 | -0.016558 | -0.02989 | -0.020897 | 0.0025024 | -0.0052551 | 0.063762 | 0.039597 | -0.022853 | -0.008391 | -0.014392 | -0.073242 | 0.036621 | -0.013733 | -0.073242 | 0.086975 | 0.009155 | 0.009155 | -44.6869 | 0.082397 | -122.4335 | -0.022888 | -121.431 | -121.7056 | -121.8201 | 122.3831 | -0.086975 | -0.19684 | 122.4838 | 122.406 | 122.406 | 0.022888 | 0.022888 | -0.036621 | -0.041199 | -0.14648 | 0.96588 | 0.57678 | 0.69122 | 0.6134 | 0.72784 | 0.10071 | -0.059509 | 1.0025 | 122.4106 | 0.050354 | 122.5159 | 122.4335 | 122.4792 | -0.13733 | -122.5571 | 122.3236 | 122.374 | 122.3236 | 77.71
2220.9219 | 122.5388 | -122.406 | 0.10529 | 0.02121 | 0.026323 | -0.034363 | 0.043957 | -0.017412 | -0.02754 | -0.022178 | 0.0055542 | -0.0084595 | 0.065899 | 0.042161 | -0.017299 | -0.0075366 | -0.014605 | -0.013733 | 0.036621 | 0.004578 | -0.022888 | 0.11444 | 0 | 0.009155 | -44.9341 | 0.082397 | -122.3923 | 0.009155 | -121.431 | -121.7514 | -121.8201 | 122.4106 | -0.068665 | -0.12817 | 122.5204 | 122.4152 | 122.406 | 0.004577 | -0.004578 | 0.013733 | -0.022889 | -0.096131 | 0.97504 | 0.58594 | 0.6546 | 0.5722 | 0.64087 | 0.10986 | -0.027466 | 0.9613 | 122.4014 | 0.032043 | 122.4747 | 122.4426 | 122.4884 | -0.10071 | -122.4976 | 122.3831 | 122.4152 | 122.3923 | 77.4719
2222.7031 | 122.6578 | -122.3602 | 0.09613 | 0.0059509 | 0.026323 | -0.033295 | 0.040967 | -0.022967 | -0.030104 | -0.024528 | 0.0025024 | -0.0099549 | 0.063762 | 0.051774 | -0.017085 | -0.010741 | -0.016955 | -0.041199 | 0.027466 | 0.013733 | -0.009155 | 0.14648 | 0.068665 | 0.068665 | -45.3232 | 0.041199 | -122.4197 | 0.082397 | -121.344 | -121.6141 | -121.7468 | 122.374 | -0.068664 | -0.10528 | 122.5067 | 122.4289 | 122.4289 | 0.054932 | 0.054932 | -0.05951 | -0.054931 | -0.013733 | 1.0162 | 0.6134 | 0.74615 | 0.67291 | 0.80566 | 0.13275 | -0.022888 | 1.0757 | 122.5021 | 0.013733 | 122.4609 | 122.3877 | 122.4014 | -0.082397 | -122.5159 | 122.3511 | 122.4426 | 122.319 | 77.037
2224.4844 | 122.6074 | -122.3831 | 0.11902 | 0.02121 | 0.03145 | -0.035004 | 0.043744 | -0.015062 | -0.027327 | -0.026237 | 0.014709 | -0.0050415 | 0.067821 | 0.04387 | -0.018794 | -0.0096728 | -0.015246 | -0.018311 | 0.068665 | -0.018311 | -0.027466 | 0.091553 | 0.022888 | 0.022888 | -45.8405 | 0.086975 | -122.4518 | 0.027466 | -121.3852 | -121.6873 | -121.7789 | 122.3648 | -0.050354 | -0.14649 | 122.4747 | 122.406 | 122.406 | 0.041199 | 0.041199 | -0.068664 | -0.032044 | -0.091553 | 0.99792 | 0.60425 | 0.6958 | 0.67291 | 0.76447 | 0.10986 | -0.009155 | 1.0666 | 122.4792 | 0.086976 | 122.5388 | 122.4518 | 122.4701 | -0.13733 | -122.5708 | 122.3557 | 122.4106 | 122.3648 | 76.5427
2226.2188 | 122.644 | -122.3694 | 0.09613 | 0.044098 | 0.030381 | -0.033509 | 0.045025 | -0.015703 | -0.025618 | -0.024742 | 0.008606 | -0.0078185 | 0.064617 | 0.04451 | -0.016658 | -0.0081774 | -0.016101 | 0.032043 | 0.018311 | 0.009155 | 0.068665 | 0.21515 | 0.11444 | 0.12817 | -46.0968 | 0.027466 | -122.4014 | 0.11902 | -121.2845 | -121.6141 | -121.7285 | 122.3785 | -0.077819 | -0.027465 | 122.5845 | 122.4976 | 122.4838 | 0.11902 | 0.10529 | -0.032043 | -0.068664 | 0.022889 | 1.0849 | 0.64087 | 0.75531 | 0.67291 | 0.78735 | 0.20599 | 0.05951 | 1.1169 | 122.5204 | 0.009156 | 122.4289 | 122.3877 | 122.3969 | -0.086975 | -122.4976 | 122.438 | 122.4884 | 122.4014 | 76.2726
2227.9219 | 122.6486 | -122.3877 | 0.086975 | 0.02121 | 0.029527 | -0.034577 | 0.041394 | -0.02083 | -0.027113 | -0.023033 | 0.008606 | -0.0099549 | 0.065044 | 0.042588 | -0.017299 | -0.0081774 | -0.013537 | -0.022888 | 0.027466 | 0.013733 | -0.004578 | 0.14648 | 0.064087 | 0.064087 | -46.7651 | 0.041199 | -122.4243 | 0.082397 | -121.3074 | -121.6095 | -121.7331 | 122.4014 | -0.059509 | -0.091553 | 122.5342 | 122.4518 | 122.4518 | 0.050354 | 0.050354 | -0.036621 | -0.045776 | -0.004578 | 1.0803 | 0.6546 | 0.7782 | 0.69122 | 0.81482 | 0.13275 | -0.018311 | 1.1169 | 122.5067 | 0.013733 | 122.4655 | 122.4152 | 122.4289 | -0.073242 | -122.5113 | 122.3831 | 122.4701 | 122.3648 | 75.6226
2229.6406 | 122.5845 | -122.3831 | 0.11902 | 0.0059509 | 0.029954 | -0.036286 | 0.042035 | -0.016131 | -0.030104 | -0.024955 | 0.0055542 | -0.0067505 | 0.065471 | 0.039811 | -0.02029 | -0.0081774 | -0.012469 | 0.009155 | 0.027466 | 0.004578 | 0.032043 | 0.16479 | 0.082397 | 0.068665 | -47.4884 | 0.059509 | -122.4289 | 0.027466 | -121.3531 | -121.6736 | -121.8246 | 122.3877 | -0.091553 | -0.086976 | 122.5479 | 122.4518 | 122.4655 | 0.064087 | 0.077819 | -0.045776 | -0.05951 | -0.091553 | 1.03 | 0.55847 | 0.70953 | 0.60425 | 0.75531 | 0.16022 | 0.027465 | 1.0757 | 122.4564 | 0.022888 | 122.4884 | 122.4106 | 122.4426 | -0.11444 | -122.5479 | 122.4152 | 122.4106 | 122.3923 | 74.8947
2231.3594 | 122.6532 | -122.3694 | 0.10071 | 0.0059509 | 0.026964 | -0.036286 | 0.042676 | -0.021471 | -0.030317 | -0.026023 | 0.011658 | -0.011023 | 0.065258 | 0.048569 | -0.020931 | -0.0094592 | -0.013751 | 0.022888 | 0.013733 | 0.032043 | 0.082397 | 0.23346 | 0.13275 | 0.1236 | -47.731 | 0.050354 | -122.4152 | 0.11444 | -121.257 | -121.5729 | -121.7285 | 122.4014 | -0.086975 | -0.018311 | 122.6028 | 122.493 | 122.5021 | 0.091553 | 0.10071 | -0.045776 | -0.050354 | 0.013733 | 1.1124 | 0.64087 | 0.79651 | 0.68664 | 0.84229 | 0.20142 | 0.050354 | 1.1581 | 122.5296 | -0.01831 | 122.4655 | 122.3831 | 122.4197 | -0.068665 | -122.5159 | 122.4518 | 122.4838 | 122.3923 | 74.6384
2233.1406 | 122.644 | -122.3511 | 0.10071 | -0.0016786 | 0.026964 | -0.033722 | 0.045025 | -0.017626 | -0.029036 | -0.025169 | 0.0025024 | -0.0073913 | 0.06483 | 0.040665 | -0.018794 | -0.0088184 | -0.015887 | -0.041199 | 0.036621 | 0 | -0.013733 | 0.10071 | -0.004578 | 0.009155 | -48.4634 | 0.054932 | -122.4106 | 0.09613 | -121.3028 | -121.6324 | -121.7422 | 122.3511 | -0.064087 | -0.11444 | 122.4518 | 122.3602 | 122.3465 | 0.009155 | -0.004578 | -0.059509 | -0.045776 | -0.004578 | 1.0483 | 0.60882 | 0.71869 | 0.66833 | 0.7782 | 0.10071 | -0.013733 | 1.1078 | 122.5067 | 0.036621 | 122.4655 | 122.3877 | 122.406 | -0.10071 | -122.5113 | 122.3373 | 122.4472 | 122.3099 | 73.8876
2234.9219 | 122.5754 | -122.406 | 0.11444 | 0.02121 | 0.031022 | -0.03415 | 0.045025 | -0.015062 | -0.029036 | -0.023887 | 0.017761 | -0.0054687 | 0.067607 | 0.045792 | -0.020076 | -0.010741 | -0.01546 | -0.018311 | 0.073242 | -0.041199 | -0.036621 | 0.10529 | 0.036621 | 0.041199 | -49.1226 | 0.10071 | -122.4518 | 0.027466 | -121.3394 | -121.669 | -121.788 | 122.3648 | -0.041199 | -0.15106 | 122.5113 | 122.4472 | 122.4426 | 0.082398 | 0.07782 | -0.045776 | -0.013733 | -0.086975 | 1.0666 | 0.61798 | 0.737 | 0.66376 | 0.78278 | 0.14649 | 0.004578 | 1.1124 | 122.4792 | 0.11444 | 122.5525 | 122.4792 | 122.5067 | -0.15564 | -122.5662 | 122.3694 | 122.4335 | 122.3877 | 73.2834
2236.7188 | 122.6669 | -122.3557 | 0.10071 | 0.0059509 | 0.028245 | -0.034791 | 0.041394 | -0.017626 | -0.028608 | -0.022178 | 0.0025024 | -0.0078185 | 0.064617 | 0.048783 | -0.019435 | -0.0079638 | -0.017596 | 0.022888 | 0.009155 | 0.027466 | 0.082397 | 0.22888 | 0.11902 | 0.12817 | -49.5117 | 0.041199 | -122.3969 | 0.11902 | -121.225 | -121.55 | -121.7331 | 122.3831 | -0.091553 | -0.018311 | 122.5845 | 122.4838 | 122.4747 | 0.10071 | 0.091553 | -0.041199 | -0.059509 | 0.018311 | 1.1307 | 0.62256 | 0.80566 | 0.66376 | 0.84686 | 0.20142 | 0.054931 | 1.1719 | 122.5159 | -0.018311 | 122.4381 | 122.3648 | 122.3969 | -0.073242 | -122.4976 | 122.438 | 122.4747 | 122.3785 | 72.8439
2238.5156 | 122.6486 | -122.3694 | 0.09613 | 0.036468 | 0.029954 | -0.033509 | 0.043957 | -0.016344 | -0.027754 | -0.020683 | 0.008606 | -0.0095275 | 0.067821 | 0.040452 | -0.016658 | -0.0079638 | -0.017596 | 0.027466 | 0.022888 | 0.018311 | 0.086975 | 0.23346 | 0.10529 | 0.10529 | -49.9008 | 0.059509 | -122.4106 | 0.1236 | -121.2341 | -121.5729 | -121.7285 | 122.3877 | -0.073242 | -0.009155 | 122.6028 | 122.4747 | 122.4747 | 0.086975 | 0.086975 | -0.041198 | -0.036621 | 0.027466 | 1.1353 | 0.64087 | 0.79651 | 0.68207 | 0.83771 | 0.21515 | 0.068664 | 1.1765 | 122.5342 | 0.004577 | 122.4701 | 122.3923 | 122.4289 | -0.077819 | -122.5067 | 122.4564 | 122.493 | 122.3969 | 72.4686
2240.25 | 122.6715 | -122.3465 | 0.09613 | 0.0059509 | 0.028032 | -0.033082 | 0.041394 | -0.016771 | -0.027327 | -0.021751 | 0.017761 | -0.0058959 | 0.066753 | 0.052415 | -0.014095 | -0.008391 | -0.016101 | 0.036621 | 0.018311 | 0.045776 | 0.09613 | 0.24261 | 0.10071 | 0.11444 | -50.2304 | 0.045776 | -122.438 | 0.13275 | -121.2158 | -121.5591 | -121.6965 | 122.3923 | -0.077819 | 0 | 122.5891 | 122.4609 | 122.4472 | 0.068665 | 0.054932 | -0.091552 | -0.050354 | 0.036621 | 1.1307 | 0.65002 | 0.78735 | 0.74158 | 0.87891 | 0.19684 | 0.050354 | 1.2222 | 122.5708 | -0.027465 | 122.4838 | 122.3648 | 122.3923 | -0.050354 | -122.5342 | 122.4426 | 122.4792 | 122.3831 | 72.1161
2242.0312 | 122.5937 | -122.406 | 0.11902 | 0.028839 | 0.030595 | -0.035859 | 0.046521 | -0.020403 | -0.029249 | -0.022392 | 0.0055542 | -0.0073913 | 0.065685 | 0.048142 | -0.02029 | -0.0096728 | -0.013324 | -0.004578 | 0.068665 | -0.013733 | -0.009155 | 0.12817 | 0.045776 | 0.045776 | -50.56 | 0.10071 | -122.4197 | 0.054932 | -121.2753 | -121.6187 | -121.7789 | 122.3923 | -0.050354 | -0.12817 | 122.5342 | 122.4518 | 122.4518 | 0.059509 | 0.059509 | -0.013733 | -0.018311 | -0.064087 | 1.1307 | 0.62714 | 0.78735 | 0.64087 | 0.80109 | 0.14191 | 0.004578 | 1.1444 | 122.4747 | 0.082398 | 122.5204 | 122.4747 | 122.5067 | -0.13275 | -122.5388 | 122.3969 | 122.4609 | 122.4014 | 71.846
2243.7969 | 122.6532 | -122.3465 | 0.10986 | 0.02121 | 0.028672 | -0.033509 | 0.042035 | -0.018694 | -0.028822 | -0.022392 | 0.008606 | -0.0097411 | 0.06483 | 0.051987 | -0.019008 | -0.0079638 | -0.012683 | -0.041199 | 0.032043 | 0.027466 | 0.022888 | 0.15564 | 0.064087 | 0.073242 | -50.8896 | 0.041199 | -122.4152 | 0.082397 | -121.2296 | -121.5546 | -121.7514 | 122.374 | -0.07782 | -0.086975 | 122.5021 | 122.4197 | 122.4106 | 0.045776 | 0.036621 | -0.068664 | -0.068664 | -0.027466 | 1.1169 | 0.59509 | 0.79193 | 0.66376 | 0.8606 | 0.12817 | -0.004578 | 1.1856 | 122.4976 | 0.004577 | 122.4564 | 122.3785 | 122.3877 | -0.082397 | -122.525 | 122.3694 | 122.4289 | 122.3053 | 71.4569
2245.5312 | 122.6303 | -122.3694 | 0.09613 | 0.036468 | 0.029741 | -0.031586 | 0.042889 | -0.017626 | -0.026258 | -0.024955 | 0.008606 | -0.0084595 | 0.066967 | 0.047074 | -0.017299 | -0.0088184 | -0.013965 | 0.009155 | 0.018311 | 0.013733 | 0.054932 | 0.19684 | 0.082397 | 0.091553 | -51.384 | 0.032043 | -122.4106 | 0.07782 | -121.2341 | -121.5775 | -121.7514 | 122.3831 | -0.077819 | -0.041198 | 122.5662 | 122.4609 | 122.4518 | 0.07782 | 0.068664 | -0.041198 | -0.064087 | -0.01831 | 1.1353 | 0.61798 | 0.79193 | 0.65918 | 0.83313 | 0.18311 | 0.041199 | 1.1765 | 122.4884 | 0.004578 | 122.4426 | 122.3877 | 122.4014 | -0.082397 | -122.5067 | 122.4243 | 122.4472 | 122.3785 | 70.9854
2247.3125 | 122.5891 | -122.3694 | 0.13733 | 0.02121 | 0.031022 | -0.03415 | 0.045025 | -0.019762 | -0.028608 | -0.025383 | 0.0025024 | -0.0065369 | 0.065471 | 0.042161 | -0.020931 | -0.0088184 | -0.015674 | 0.018311 | 0.045776 | 0 | 0.022888 | 0.15106 | 0.059509 | 0.059509 | -52.0935 | 0.07782 | -122.4197 | 0.064087 | -121.2479 | -121.5912 | -121.7514 | 122.3694 | -0.091553 | -0.11444 | 122.5204 | 122.4289 | 122.4289 | 0.059509 | 0.059509 | -0.050354 | -0.059509 | -0.073242 | 1.1215 | 0.61798 | 0.7782 | 0.66834 | 0.82855 | 0.15106 | 0.022888 | 1.1719 | 122.4838 | 0.045776 | 122.4976 | 122.4152 | 122.4472 | -0.13733 | -122.5571 | 122.3923 | 122.4335 | 122.3877 | 70.2759
2249.0938 | 122.612 | -122.3785 | 0.11902 | 0.01358 | 0.031663 | -0.033936 | 0.042676 | -0.016558 | -0.027113 | -0.021965 | -0.00054937 | -0.0076049 | 0.066326 | 0.050919 | -0.016231 | -0.0086048 | -0.016528 | -0.036621 | 0.054932 | 0.004578 | -0.022888 | 0.086975 | -0.022888 | 0.004578 | -52.739 | 0.073242 | -122.3969 | 0.068665 | -121.2479 | -121.6003 | -121.7514 | 122.3831 | -0.064087 | -0.14191 | 122.4655 | 122.3831 | 122.3557 | 0 | -0.027466 | -0.018311 | -0.045777 | -0.050354 | 1.1307 | 0.62714 | 0.7782 | 0.64545 | 0.79651 | 0.082397 | -0.027466 | 1.149 | 122.4655 | 0.050354 | 122.4701 | 122.4335 | 122.4518 | -0.11444 | -122.5159 | 122.3557 | 122.4472 | 122.3419 | 69.6396
2250.875 | 122.5525 | -122.3969 | 0.14648 | 0.0059509 | 0.033159 | -0.034791 | 0.043103 | -0.019335 | -0.028608 | -0.024101 | 0.020813 | -0.0054687 | 0.066112 | 0.038743 | -0.02264 | -0.011382 | -0.018451 | -0.068665 | 0.068665 | -0.018311 | -0.027466 | 0.10071 | 0.041199 | 0.041199 | -53.0045 | 0.10986 | -122.4197 | -0.004578 | -121.2753 | -121.6095 | -121.788 | 122.3785 | -0.077819 | -0.17395 | 122.4976 | 122.4381 | 122.4381 | 0.05951 | 0.05951 | -0.022888 | -0.036621 | -0.15106 | 1.1215 | 0.60883 | 0.78735 | 0.63171 | 0.81024 | 0.11902 | -0.009155 | 1.1444 | 122.4152 | 0.086976 | 122.5296 | 122.4655 | 122.5067 | -0.16479 | -122.5662 | 122.3694 | 122.3923 | 122.3282 | 69.3924
2252.6562 | 122.5891 | -122.3602 | 0.15106 | 0.02121 | 0.032731 | -0.033722 | 0.045025 | -0.017412 | -0.026899 | -0.022178 | 0.008606 | -0.0071777 | 0.065685 | 0.03682 | -0.018794 | -0.0077502 | -0.01311 | 0.022888 | 0.054932 | 0.018311 | 0.018311 | 0.16937 | 0.059509 | 0.054932 | -53.3798 | 0.073242 | -122.3969 | 0.07782 | -121.2067 | -121.5591 | -121.7514 | 122.3785 | -0.09613 | -0.13275 | 122.5296 | 122.4152 | 122.4197 | 0.036621 | 0.041198 | -0.036622 | -0.07782 | -0.073242 | 1.1536 | 0.60883 | 0.80109 | 0.64545 | 0.83771 | 0.15106 | 0 | 1.1902 | 122.4747 | 0.036621 | 122.4701 | 122.4152 | 122.4335 | -0.13275 | -122.5479 | 122.3785 | 122.438 | 122.3831 | 68.9804
2254.3906 | 122.5616 | -122.3648 | 0.14648 | 0.036468 | 0.032731 | -0.035645 | 0.044598 | -0.017626 | -0.030531 | -0.020683 | 0.011658 | -0.0054687 | 0.065044 | 0.038743 | -0.019008 | -0.0086048 | -0.019732 | -0.036621 | 0.064087 | -0.027466 | -0.032043 | 0.091553 | 0.041199 | 0.036621 | -53.8422 | 0.09613 | -122.4335 | 0.004578 | -121.225 | -121.5546 | -121.7743 | 122.3373 | -0.082397 | -0.17853 | 122.4564 | 122.4014 | 122.406 | 0.064087 | 0.068665 | -0.068665 | -0.050354 | -0.14191 | 1.1398 | 0.59051 | 0.81024 | 0.65918 | 0.87891 | 0.11902 | -0.004577 | 1.2085 | 122.438 | 0.091553 | 122.5296 | 122.4289 | 122.4609 | -0.17395 | -122.58 | 122.3328 | 122.3694 | 122.3282 | 68.5226
2256.1875 | 122.5891 | -122.3694 | 0.11902 | -0.0016786 | 0.032304 | -0.036072 | 0.040326 | -0.018694 | -0.029676 | -0.021751 | 0.0025024 | -0.0086731 | 0.064403 | 0.038315 | -0.021144 | -0.0101 | -0.019091 | 0.018311 | 0.018311 | 0.032043 | 0.059509 | 0.20599 | 0.11902 | 0.091553 | -54.0298 | 0.045776 | -122.3969 | 0.068665 | -121.1655 | -121.5317 | -121.7514 | 122.4014 | -0.10071 | -0.05951 | 122.5754 | 122.4609 | 122.4884 | 0.05951 | 0.086976 | -0.027466 | -0.073243 | -0.050354 | 1.2039 | 0.61798 | 0.83771 | 0.64545 | 0.86517 | 0.17395 | 0.027466 | 1.2314 | 122.4655 | -0.013732 | 122.4426 | 122.3877 | 122.4152 | -0.086976 | -122.5159 | 122.4289 | 122.438 | 122.3877 | 68.3395
2257.9688 | 122.6669 | -122.3511 | 0.10071 | -0.0016786 | 0.032304 | -0.034577 | 0.042035 | -0.021685 | -0.029036 | -0.025169 | 0.0025024 | -0.0095275 | 0.064403 | 0.045792 | -0.019649 | -0.0096728 | -0.014178 | 0.013733 | 0.022888 | 0.041199 | 0.050354 | 0.21057 | 0.13275 | 0.1236 | -54.3182 | 0.036621 | -122.4014 | 0.13275 | -121.0785 | -121.4172 | -121.6782 | 122.3923 | -0.07782 | -0.050354 | 122.5616 | 122.4747 | 122.4838 | 0.082397 | 0.091552 | -0.050354 | -0.064087 | 0.032043 | 1.2726 | 0.67291 | 0.93384 | 0.72327 | 0.98419 | 0.16937 | 0.009155 | 1.3229 | 122.5342 | -0.018311 | 122.438 | 122.374 | 122.3877 | -0.059509 | -122.5021 | 122.4014 | 122.4838 | 122.3648 | 68.0328
2259.6875 | 122.5937 | -122.3465 | 0.13275 | 0.028839 | 0.034868 | -0.033722 | 0.043957 | -0.020403 | -0.030745 | -0.022178 | 0.008606 | -0.0054687 | 0.066753 | 0.043229 | -0.019649 | -0.0096728 | -0.012042 | 0.009155 | 0.07782 | -0.004578 | 0.009155 | 0.1236 | 0.068665 | 0.054932 | -54.8859 | 0.10071 | -122.3969 | 0.064087 | -121.1472 | -121.5134 | -121.7331 | 122.3419 | -0.054931 | -0.1236 | 122.4701 | 122.4014 | 122.4152 | 0.05951 | 0.073243 | -0.050354 | -0.032043 | -0.068664 | 1.1993 | 0.6134 | 0.83313 | 0.66376 | 0.88348 | 0.12817 | 0.013733 | 1.2497 | 122.4609 | 0.082398 | 122.4976 | 122.4243 | 122.4472 | -0.13733 | -122.5296 | 122.3557 | 122.4106 | 122.3557 | 67.4606
2261.4844 | 122.6166 | -122.3511 | 0.11902 | 0.028839 | 0.035936 | -0.032654 | 0.042889 | -0.015276 | -0.02519 | -0.024101 | 0.017761 | -0.0078185 | 0.068035 | 0.047501 | -0.016017 | -0.0081774 | -0.014178 | 0.045776 | 0.036621 | 0.045776 | 0.10071 | 0.24719 | 0.11444 | 0.11902 | -55.2292 | 0.064087 | -122.3648 | 0.13275 | -121.0968 | -121.4722 | -121.7056 | 122.3969 | -0.082398 | -0.018311 | 122.5983 | 122.4701 | 122.4655 | 0.073243 | 0.068665 | -0.013733 | -0.054932 | 0.013732 | 1.2543 | 0.64545 | 0.87891 | 0.65918 | 0.89264 | 0.20142 | 0.054932 | 1.268 | 122.4976 | -0.009155 | 122.4289 | 122.3877 | 122.4152 | -0.073243 | -122.4838 | 122.4518 | 122.4838 | 122.3969 | 67.1219
2263.2031 | 122.5708 | -122.3328 | 0.1236 | 0.0059509 | 0.040849 | -0.035645 | 0.044812 | -0.016985 | -0.028395 | -0.024101 | -0.00054937 | -0.0050415 | 0.065685 | 0.046433 | -0.017513 | -0.0075366 | -0.015674 | -0.009155 | 0.086975 | 0.018311 | -0.022888 | 0.10071 | -0.009155 | 0.009155 | -55.4901 | 0.10071 | -122.406 | 0.054932 | -121.17 | -121.5271 | -121.7331 | 122.3511 | -0.036621 | -0.14648 | 122.4335 | 122.3419 | 122.3236 | -0.009156 | -0.027466 | -0.073242 | -0.022888 | -0.068664 | 1.1627 | 0.59967 | 0.80566 | 0.67291 | 0.87891 | 0.082397 | -0.041199 | 1.236 | 122.4609 | 0.068664 | 122.5067 | 122.4197 | 122.4335 | -0.10528 | -122.5296 | 122.3099 | 122.3877 | 122.3236 | 66.8427
2264.9844 | 122.5983 | -122.3099 | 0.15564 | 0.028839 | 0.046403 | -0.033722 | 0.04588 | -0.016344 | -0.028181 | -0.019828 | 0.011658 | -0.0080321 | 0.066326 | 0.045151 | -0.018794 | -0.0094592 | -0.015674 | 0.059509 | 0.054932 | 0.064087 | 0.09613 | 0.25177 | 0.12817 | 0.14648 | -55.5954 | 0.086975 | -122.3557 | 0.14191 | -121.0236 | -121.3989 | -121.6553 | 122.374 | -0.10071 | -0.05951 | 122.5616 | 122.4564 | 122.438 | 0.082397 | 0.064087 | -0.045777 | -0.068665 | -0.013733 | 1.2863 | 0.6546 | 0.91095 | 0.70038 | 0.95673 | 0.18768 | 0.032043 | 1.3321 | 122.4976 | -0.009155 | 122.4426 | 122.3648 | 122.3969 | -0.091553 | -122.5113 | 122.406 | 122.4518 | 122.3694 | 66.7145
2266.7656 | 122.5525 | -121.9528 | 0.4303 | 0.01358 | 0.14894 | -0.035859 | 0.059125 | -0.019121 | -0.02989 | -0.020042 | 0.008606 | -0.0093139 | 0.065258 | 0.048997 | -0.019649 | -0.0079638 | -0.01546 | 0.28381 | 0.36163 | 0.33417 | 0.36621 | 0.48981 | 0.40741 | 0.49896 | -55.9708 | 0.46692 | -121.9482 | 0.4303 | -120.726 | -121.0236 | -121.3623 | 122.287 | -0.068665 | -0.064087 | 122.4426 | 122.4518 | 122.3602 | 0.1648 | 0.073243 | 0.004578 | 0.036621 | 0 | 1.2268 | 0.59051 | 0.92926 | 0.58594 | 0.92468 | 0.15564 | 0.032044 | 1.2222 | 122.3785 | 0.027466 | 122.4152 | 122.3145 | 122.4197 | -0.096131 | -122.3785 | 122.319 | 122.3831 | 122.2366 | 65.9821
2268.5625 | 120.3781 | -91.1728 | 28.5919 | 0.0059509 | 0.011583 | -0.0365 | 0.039044 | -0.019549 | -0.028608 | -0.024528 | 0.023865 | -0.0035461 | 0.065899 | 0.040665 | -0.023067 | -0.009032 | -0.015246 | -0.045776 | 0.082397 | -0.027466 | -0.004578 | 0.11902 | 0.050354 | 0.054932 | -34.4055 | 29.48 | -89.8819 | 29.5578 | -89.6942 | -89.415 | -90.065 | 91.1453 | -28.5095 | -28.5965 | 91.2918 | 91.2277 | 91.2231 | 0.082398 | 0.07782 | 1.2909 | 0.88806 | 0.96588 | 1.4786 | 1.1078 | 1.7578 | -0.18311 | 0.46692 | 0.14649 | 0.022888 | 0.18768 | 119.4397 | 0.10986 | 119.3619 | 91.2552 | 120.6528 | -28.6194 | -118.4738 | 91.1682 | 120.7306 | 91.127 | 56.7673
2270.3438 | 119.6548 | -104.686 | 14.6942 | 0.02121 | 0.015214 | -0.034363 | 0.036908 | -0.017199 | -0.030104 | -0.023033 | 0.017761 | -0.0076049 | 0.06483 | 0.045792 | -0.019222 | -0.010314 | -0.01546 | -0.009155 | 0.068665 | -0.013733 | 0.004578 | 0.1236 | 0.059509 | 0.073242 | -43.8492 | 14.5798 | -104.2374 | 15.0375 | -102.6901 | -103.363 | -104.068 | 104.6722 | -14.6255 | -14.6896 | 104.8096 | 104.7592 | 104.7455 | 0.086975 | 0.073242 | 0.44861 | -0.11444 | 0.34332 | 1.9958 | 0.61798 | 1.3229 | 0.16937 | 0.87433 | 0.13733 | 0.018311 | 1.5472 | 119.2749 | 0.082398 | 118.8171 | 104.7546 | 119.2657 | -14.7079 | -118.9316 | 104.6906 | 119.7235 | 104.6768 | 60.8368
2272.0625 | 119.9066 | -91.0217 | 28.8071 | 0.028839 | 0.014146 | -0.035218 | 0.035412 | -0.01549 | -0.029676 | -0.023246 | 0.011658 | -0.0056823 | 0.063549 | 0.043229 | -0.018154 | -0.009032 | -0.018664 | -0.050354 | 0.018311 | -0.050354 | -0.045776 | 0.10071 | 0.004578 | 0 | -36.0306 | 28.7247 | -91.0126 | 29.0497 | -89.7995 | -90.2206 | -90.6876 | 90.9714 | -28.7888 | -28.8528 | 91.1224 | 91.0217 | 91.0263 | 0.050354 | 0.054932 | 0.009156 | -0.082398 | 0.24262 | 1.2222 | 0.33417 | 0.80109 | 0.32501 | 0.79193 | 0.15106 | 0.004578 | 1.2131 | 120.0623 | 0.068665 | 119.7372 | 91.04 | 119.7464 | -28.8574 | -119.8196 | 90.976 | 120.0714 | 90.9714 | 54.9911
2273.8438 | 121.0831 | -120.7764 | 0.14191 | 0.0059509 | 0.012864 | -0.033936 | 0.032635 | -0.019549 | -0.028181 | -0.021537 | 0.0055542 | -0.010169 | 0.063549 | 0.048142 | -0.019863 | -0.0081774 | -0.014819 | -0.009155 | -0.027466 | -0.004578 | 0.013733 | 0.16937 | 0.086975 | 0.082397 | -55.1788 | 0.10529 | -120.8359 | 0.09613 | -119.4489 | -119.8608 | -120.2042 | 120.7718 | -0.16937 | -0.12817 | 120.9457 | 120.8588 | 120.8633 | 0.086975 | 0.091553 | -0.059509 | -0.036621 | -0.045777 | 1.3275 | 0.5722 | 0.91553 | 0.63171 | 0.97504 | 0.17395 | 0.018311 | 1.387 | 120.932 | -0.022888 | 120.9412 | 120.7489 | 120.8817 | -0.14649 | -120.9778 | 120.7901 | 120.8725 | 120.7672 | 65.5975
2275.625 | 121.4172 | -120.9274 | 0.25635 | 0.01358 | 0.012224 | -0.034363 | 0.034344 | -0.026384 | -0.028822 | -0.02581 | 0.0055542 | -0.0076049 | 0.065044 | 0.047928 | -0.018154 | -0.007323 | -0.01546 | -0.041199 | -0.009155 | -0.022888 | -0.027466 | 0.10986 | 0.027466 | 0.041199 | -55.7556 | 0.21515 | -120.9869 | 0.24261 | -119.5816 | -119.9799 | -120.2911 | 120.9045 | -0.2655 | -0.28381 | 121.0373 | 120.9686 | 120.9549 | 0.064087 | 0.050354 | -0.059509 | -0.041199 | -0.013733 | 1.3458 | 0.63629 | 0.94757 | 0.6958 | 1.0071 | 0.13275 | -0.004578 | 1.4053 | 121.2296 | 0.013733 | 121.2021 | 120.9183 | 121.1426 | -0.27924 | -121.2433 | 120.9 | 121.17 | 120.8862 | 65.1718
2277.4062 | 121.2341 | -120.5933 | 0.60425 | 0.0059509 | 0.015214 | -0.035431 | 0.035412 | -0.014849 | -0.027967 | -0.022605 | -0.00054937 | -0.0067505 | 0.064617 | 0.043229 | -0.020717 | -0.010314 | -0.012683 | -0.032043 | -0.022888 | -0.009155 | -0.032043 | 0.09613 | 0.009155 | 0.022888 | -54.5242 | 0.53101 | -120.6711 | 0.50354 | -119.2337 | -119.6594 | -119.989 | 120.5841 | -0.62714 | -0.63629 | 120.6894 | 120.6161 | 120.6024 | 0.032043 | 0.01831 | -0.07782 | -0.073242 | -0.10071 | 1.3596 | 0.60425 | 0.93384 | 0.68207 | 1.0117 | 0.10528 | -0.022888 | 1.4374 | 121.1746 | -0.013733 | 121.2021 | 120.5704 | 121.1243 | -0.6134 | -121.2753 | 120.5612 | 121.0968 | 120.5612 | 66.069
2279.1875 | 121.4767 | -121.0968 | 0.23804 | 0.02121 | 0.013719 | -0.036072 | 0.036694 | -0.019762 | -0.028395 | -0.023674 | 0.0055542 | -0.0078185 | 0.063549 | 0.046219 | -0.015377 | -0.0068958 | -0.014819 | -0.068665 | -0.004578 | -0.041199 | -0.068665 | 0.068665 | -0.032043 | 0 | -54.8126 | 0.24261 | -121.0968 | 0.27008 | -119.6503 | -120.1309 | -120.4514 | 121.0556 | -0.24261 | -0.3067 | 121.1655 | 121.0968 | 121.0648 | 0.041199 | 0.009156 | 0 | 0.004578 | 0.032044 | 1.4465 | 0.64545 | 0.96588 | 0.64545 | 0.96588 | 0.10986 | -0.027466 | 1.4465 | 121.3669 | 0.036621 | 121.3394 | 121.0922 | 121.3394 | -0.27924 | -121.3348 | 121.0281 | 121.3669 | 121.0281 | 66.2842
2280.8906 | 120.4102 | -119.8791 | 0.46234 | 0.01358 | 0.01436 | -0.034363 | 0.037762 | -0.016344 | -0.032026 | -0.021965 | 0.0025024 | -0.0080321 | 0.06483 | 0.043229 | -0.021358 | -0.0077502 | -0.015246 | -0.032043 | -0.036621 | -0.022888 | -0.013733 | 0.11444 | 0.045776 | 0.022888 | -55.7922 | 0.39825 | -119.8929 | 0.39368 | -118.5287 | -118.895 | -119.2657 | 119.8563 | -0.49896 | -0.47607 | 119.9936 | 119.902 | 119.9249 | 0.045776 | 0.068664 | -0.013733 | -0.064087 | -0.068664 | 1.3504 | 0.6134 | 0.98419 | 0.62714 | 0.99792 | 0.13733 | 0.009155 | 1.3641 | 120.2866 | -0.013733 | 120.2911 | 119.8425 | 120.2774 | -0.48523 | -120.3552 | 119.8654 | 120.2728 | 119.8471 | 64.0869
2282.6875 | 120.9915 | -120.6299 | 0.091553 | 0.0059509 | 0.012437 | -0.035431 | 0.03648 | -0.01784 | -0.02989 | -0.020683 | 0.0025024 | -0.0086731 | 0.063976 | 0.037034 | -0.017085 | -0.0086048 | -0.018023 | -0.004578 | -0.022888 | 0.018311 | 0.041199 | 0.20599 | 0.10529 | 0.091553 | -56.0852 | 0.041199 | -120.6665 | 0.14648 | -119.1696 | -119.5724 | -119.9707 | 120.6482 | -0.11444 | -0.050354 | 120.8359 | 120.7214 | 120.7352 | 0.073242 | 0.086975 | -0.036621 | -0.050354 | 0.054931 | 1.4603 | 0.65918 | 1.0574 | 0.6958 | 1.0941 | 0.18768 | 0.022888 | 1.4969 | 120.813 | -0.041199 | 120.7077 | 120.607 | 120.6711 | -0.073242 | -120.7581 | 120.6711 | 120.7764 | 120.6253 | 64.5447
2284.4688 | 119.5358 | -117.9291 | 1.5381 | 0.01358 | 0.014573 | -0.031586 | 0.037976 | -0.017626 | -0.027113 | -0.023033 | 0.0025024 | -0.0056823 | 0.062481 | 0.040024 | -0.018794 | -0.0075366 | -0.017383 | -0.064087 | 0.009155 | -0.032043 | -0.086975 | 0.018311 | -0.054932 | -0.045776 | -55.0415 | 1.4282 | -117.7002 | 1.4694 | -116.8533 | -116.7984 | -117.2562 | 117.897 | -1.5289 | -1.6251 | 117.9474 | 117.8833 | 117.8741 | -0.013733 | -0.022889 | 0.22888 | -0.10986 | -0.068665 | 1.0757 | 0.67291 | 1.1307 | 0.44403 | 0.90179 | 0.050354 | -0.054932 | 0.84686 | 119.1696 | 0.041198 | 119.1284 | 117.9382 | 119.3573 | -1.5701 | -119.2383 | 117.8421 | 119.3985 | 117.865 | 62.8876
2286.25 | 120.9732 | -120.0119 | 0.77362 | 0.01358 | 0.01201 | -0.033936 | 0.034131 | -0.015276 | -0.028181 | -0.018547 | 0.011658 | -0.0093139 | 0.065471 | 0.040665 | -0.018367 | -0.0071094 | -0.015033 | -0.050354 | -0.032043 | -0.022888 | -0.018311 | 0.11444 | 0.027466 | 0.032043 | -56.2134 | 0.65918 | -120.1447 | 0.67749 | -118.5471 | -118.9545 | -119.3848 | 119.989 | -0.80566 | -0.79193 | 120.1263 | 120.0439 | 120.0394 | 0.054931 | 0.050354 | -0.13275 | -0.11444 | -0.096131 | 1.4648 | 0.62714 | 1.0574 | 0.75989 | 1.1902 | 0.13733 | 0.004577 | 1.5976 | 120.8221 | -0.009155 | 120.8038 | 119.9799 | 120.6711 | -0.79651 | -120.9183 | 119.9936 | 120.6894 | 119.9615 | 63.7985
2288.0469 | 120.6482 | -119.9799 | 0.41657 | 0.044098 | 0.012437 | -0.033722 | 0.038189 | -0.01549 | -0.027113 | -0.02111 | 0.011658 | -0.0041869 | 0.065471 | 0.04921 | -0.017726 | -0.0092456 | -0.01546 | 0.018311 | -0.013733 | -0.022888 | 0.068665 | 0.20142 | 0.068665 | 0.082397 | -56.6986 | 0.34332 | -120.0623 | 0.45776 | -118.5471 | -118.9499 | -119.3344 | 119.957 | -0.4303 | -0.3479 | 120.1813 | 120.0623 | 120.0485 | 0.10528 | 0.091553 | -0.082398 | -0.073242 | 0.041199 | 1.4328 | 0.64545 | 1.03 | 0.72784 | 1.1124 | 0.2243 | 0.091553 | 1.5152 | 120.52 | 0.009155 | 120.4056 | 119.9661 | 120.3232 | -0.43945 | -120.4788 | 120.0485 | 120.4376 | 119.9982 | 63.2812
2289.7656 | 115.3198 | -113.7405 | 1.442 | 0.036468 | 0.016496 | -0.033722 | 0.035626 | -0.018908 | -0.030958 | -0.024101 | 0.0055542 | -0.0076049 | 0.062908 | 0.040238 | -0.021144 | -0.009032 | -0.015246 | -0.064087 | 0.036621 | -0.07782 | -0.064087 | 0.041199 | -0.004578 | -0.018311 | -53.54 | 1.4786 | -113.8275 | 1.2268 | -112.5687 | -112.7747 | -113.2599 | 113.6627 | -1.4053 | -1.506 | 113.7817 | 113.7222 | 113.736 | 0.059509 | 0.073242 | -0.086975 | 0.036621 | -0.21515 | 1.1719 | 0.48065 | 0.96588 | 0.56763 | 1.0529 | 0.11902 | 0.013733 | 1.2589 | 115.0543 | 0.11444 | 115.3061 | 113.7772 | 115.2191 | -1.5198 | -115.2695 | 113.6765 | 114.9673 | 113.6765 | 60.2005
2291.5469 | 117.2104 | -78.7308 | 38.8824 | 0.02121 | 0.010301 | -0.035431 | 0.034985 | -0.018694 | -0.031599 | -0.022819 | -0.00054937 | -0.0069641 | 0.063762 | 0.03917 | -0.018367 | -0.008391 | -0.014605 | 0 | -0.004578 | -0.036621 | -0.041199 | 0.082397 | -0.032043 | -0.027466 | -29.7226 | 38.2645 | -78.9734 | 38.8046 | -77.6367 | -77.8427 | -78.1677 | 78.6942 | -38.887 | -38.9236 | 78.8132 | 78.7033 | 78.6987 | 0.009155 | 0.004578 | -0.24262 | -0.61798 | -0.07782 | 1.0941 | 0.56305 | 0.88806 | 0.80566 | 1.1307 | 0.11902 | -0.004578 | 1.3367 | 117.778 | 0.032043 | 117.2379 | 78.7262 | 116.9952 | -38.9191 | -117.8558 | 78.6896 | 117.5354 | 78.7308 | 49.0082
2293.2656 | 118.3411 | -78.7857 | 39.1891 | 0.01358 | 0.013933 | -0.035859 | 0.036908 | -0.018053 | -0.02754 | -0.022605 | 0.008606 | -0.0069641 | 0.06419 | 0.035538 | -0.020076 | -0.009032 | -0.015246 | -0.032043 | 0.004578 | -0.054932 | -0.050354 | 0.086975 | -0.004578 | 0.009155 | -27.0218 | 39.7064 | -77.2751 | 40.1917 | -76.7075 | -77.5085 | -78.6072 | 78.7308 | -39.1846 | -39.2395 | 78.8727 | 78.7949 | 78.7811 | 0.064087 | 0.050354 | 1.5106 | 0.51727 | 1.0025 | 2.0782 | 0.17853 | 1.2772 | -1.3321 | -0.23346 | 0.14191 | 0.004578 | 0.56763 | 117.4667 | 0.05951 | 116.9815 | 78.7903 | 118.4921 | -39.2441 | -116.4642 | 78.7354 | 118.9774 | 78.7537 | 51.7639
2295.0469 | 119.9799 | -119.8975 | 0.11902 | -0.0016786 | 0.012864 | -0.03415 | 0.036267 | -0.016558 | -0.028822 | -0.02346 | 0.0025024 | -0.0076049 | 0.064617 | 0.043442 | -0.018367 | -0.0081774 | -0.012042 | -0.073242 | 0.027466 | -0.050354 | -0.10529 | 0.018311 | -0.07782 | -0.054932 | -56.3553 | 0.036621 | -119.9615 | -0.027466 | -118.4143 | -118.8492 | -119.2841 | 119.8471 | -0.091553 | -0.22431 | 119.9158 | 119.8425 | 119.8196 | -0.004578 | -0.027466 | -0.064087 | -0.082398 | -0.14649 | 1.4832 | 0.6134 | 1.0483 | 0.67749 | 1.1124 | 0.068665 | -0.054932 | 1.5472 | 119.9341 | 0.07782 | 119.9982 | 119.9249 | 119.9341 | -0.16937 | -120.0806 | 119.7922 | 119.87 | 119.8242 | 63.5422
2296.8438 | 120.3598 | -120.0851 | 0.068665 | 0.01358 | 0.015001 | -0.033082 | 0.037762 | -0.01848 | -0.025618 | -0.021965 | 0.0055542 | -0.0069641 | 0.065899 | 0.041092 | -0.014095 | -0.007323 | -0.016742 | 0.009155 | -0.027466 | -0.018311 | 0.050354 | 0.21057 | 0.086975 | 0.073242 | -56.5659 | 0.004578 | -120.1355 | 0.10071 | -118.4647 | -118.9087 | -119.426 | 120.0668 | -0.096131 | -0.018311 | 120.2957 | 120.1584 | 120.1721 | 0.091553 | 0.10529 | -0.050354 | -0.064087 | 0.032043 | 1.6205 | 0.65918 | 1.1765 | 0.70953 | 1.2268 | 0.22888 | 0.068665 | 1.6708 | 120.2362 | -0.009155 | 120.1401 | 120.0577 | 120.0897 | -0.086976 | -120.2042 | 120.1355 | 120.1859 | 120.0943 | 63.5193
2298.6406 | 120.4926 | -120.1767 | 0.054932 | 0.0059509 | 0.011369 | -0.035218 | 0.032208 | -0.018267 | -0.028608 | -0.024528 | 0.0055542 | -0.0082459 | 0.065685 | 0.053269 | -0.019008 | -0.0079638 | -0.017169 | -0.036621 | -0.022888 | -0.004578 | 0.027466 | 0.1831 | 0.10071 | 0.10071 | -57.0282 | -0.004578 | -120.2454 | 0.10071 | -118.5379 | -118.9636 | -119.5221 | 120.1721 | -0.07782 | -0.027466 | 120.3598 | 120.2774 | 120.2774 | 0.10529 | 0.10529 | -0.068664 | -0.05951 | 0.045776 | 1.6388 | 0.6546 | 1.2131 | 0.72327 | 1.2817 | 0.18768 | 0.032044 | 1.7075 | 120.3461 | -0.01831 | 120.2408 | 120.1538 | 120.1721 | -0.05951 | -120.3003 | 120.2042 | 120.2774 | 120.1401 | 63.1485
2300.3594 | 120.5063 | -120.2774 | 0.054932 | 0.02121 | 0.012224 | -0.032868 | 0.034558 | -0.015276 | -0.026686 | -0.022392 | 0.0055542 | -0.0082459 | 0.067821 | 0.050492 | -0.019649 | -0.0079638 | -0.01311 | -0.050354 | -0.013733 | -0.022888 | -0.032043 | 0.10986 | 0.032043 | 0.027466 | -57.5912 | 0.022888 | -120.3369 | 0.027466 | -118.6752 | -119.0735 | -119.6182 | 120.2545 | -0.068665 | -0.086975 | 120.3873 | 120.3049 | 120.3094 | 0.050354 | 0.054931 | -0.059509 | -0.032044 | -0.027466 | 1.6022 | 0.65918 | 1.2039 | 0.71869 | 1.2634 | 0.13275 | -0.009155 | 1.6617 | 120.3644 | 0.009155 | 120.3598 | 120.2637 | 120.3003 | -0.07782 | -120.3918 | 120.2454 | 120.3049 | 120.2271 | 62.6862
2302.1406 | 120.4742 | -120.3461 | 0.073242 | -0.0016786 | 0.012224 | -0.033295 | 0.038403 | -0.019762 | -0.028822 | -0.021537 | 0.0025024 | -0.0065369 | 0.065471 | 0.04152 | -0.016658 | -0.0092456 | -0.017169 | -0.086975 | 0.004578 | -0.054932 | -0.086975 | 0.009155 | -0.073242 | -0.059509 | -58.1543 | 0.059509 | -120.4056 | -0.032043 | -118.8171 | -119.2429 | -119.7464 | 120.2911 | -0.068664 | -0.16022 | 120.3552 | 120.2866 | 120.2728 | -0.004577 | -0.01831 | -0.05951 | -0.013733 | -0.10529 | 1.5289 | 0.59967 | 1.1032 | 0.65918 | 1.1627 | 0.064087 | -0.032043 | 1.5884 | 120.3735 | 0.05951 | 120.4651 | 120.3506 | 120.4056 | -0.12817 | -120.4788 | 120.2591 | 120.314 | 120.2591 | 62.1918
2303.8438 | 120.5109 | -120.2225 | 0.21973 | 0.01358 | 0.015001 | -0.032868 | 0.03584 | -0.01549 | -0.028822 | -0.023674 | 0.0055542 | -0.0052551 | 0.066326 | 0.042161 | -0.01794 | -0.0092456 | -0.015674 | -0.009155 | 0.009155 | -0.018311 | -0.022888 | 0.1236 | 0.018311 | 0.018311 | -58.4427 | 0.18768 | -120.2774 | 0.14648 | -118.6157 | -119.0231 | -119.5816 | 120.2042 | -0.21057 | -0.24261 | 120.3461 | 120.2408 | 120.2408 | 0.036622 | 0.036622 | -0.054932 | -0.032044 | -0.073243 | 1.6067 | 0.64087 | 1.1993 | 0.6958 | 1.2543 | 0.14191 | -0.004577 | 1.6617 | 120.4239 | 0.027466 | 120.4651 | 120.2316 | 120.4102 | -0.23804 | -120.4971 | 120.1996 | 120.369 | 120.2133 | 61.7798
2305.6406 | 120.5475 | -120.2728 | 0.25177 | 0.02121 | 0.015001 | -0.03415 | 0.03648 | -0.016558 | -0.029036 | -0.020469 | 0.0055542 | -0.0056823 | 0.065258 | 0.040879 | -0.019222 | -0.0088184 | -0.013751 | -0.073242 | 0.022888 | -0.032043 | -0.09613 | 0.027466 | -0.068665 | -0.050354 | -58.8913 | 0.19226 | -120.2957 | 0.13275 | -118.6707 | -119.0689 | -119.5953 | 120.2408 | -0.22888 | -0.3479 | 120.3003 | 120.2225 | 120.2042 | -0.018311 | -0.036622 | -0.022888 | -0.059509 | -0.11902 | 1.6022 | 0.67749 | 1.2039 | 0.70038 | 1.2268 | 0.059509 | -0.064087 | 1.6251 | 120.4285 | 0.054931 | 120.488 | 120.2957 | 120.4651 | -0.28381 | -120.5475 | 120.1767 | 120.4056 | 120.1996 | 61.3815
2307.3594 | 120.6573 | -120.4605 | 0.068665 | 0.02121 | 0.014573 | -0.0318 | 0.033703 | -0.016344 | -0.027967 | -0.023246 | 0.008606 | -0.0076049 | 0.066112 | 0.048142 | -0.01794 | -0.0075366 | -0.014605 | -0.064087 | 0.004578 | -0.022888 | -0.009155 | 0.13275 | 0.022888 | 0.032043 | -59.3353 | 0.013733 | -120.52 | 0.027466 | -118.7943 | -119.1971 | -119.7784 | 120.4376 | -0.064087 | -0.07782 | 120.5933 | 120.4926 | 120.4834 | 0.054931 | 0.045776 | -0.05951 | -0.054932 | -0.041199 | 1.6663 | 0.68207 | 1.2634 | 0.74158 | 1.3229 | 0.15564 | 0.013733 | 1.7258 | 120.5475 | 0.027466 | 120.5338 | 120.4651 | 120.4742 | -0.091553 | -120.5887 | 120.4514 | 120.488 | 120.3964 | 61.1252
2309.1406 | 120.6162 | -120.3461 | 0.21515 | -0.0093076 | 0.013719 | -0.033936 | 0.037121 | -0.013353 | -0.026472 | -0.023246 | -0.00054937 | -0.0061095 | 0.065899 | 0.04387 | -0.018581 | -0.008391 | -0.012683 | -0.082397 | 0.004578 | -0.032043 | -0.10986 | 0.009155 | -0.068665 | -0.050354 | -59.0561 | 0.16937 | -120.401 | 0.10529 | -118.8034 | -119.1834 | -119.7189 | 120.314 | -0.21057 | -0.32501 | 120.3552 | 120.2957 | 120.2774 | -0.018311 | -0.036622 | -0.054932 | -0.045776 | -0.10986 | 1.5427 | 0.62714 | 1.1627 | 0.68207 | 1.2177 | 0.041198 | -0.07782 | 1.5976 | 120.5063 | 0.036621 | 120.5704 | 120.3506 | 120.5154 | -0.24719 | -120.6161 | 120.2362 | 120.4514 | 120.2637 | 61.29
2310.9219 | 120.7306 | -120.4926 | 0.054932 | 0.036468 | 0.01436 | -0.033509 | 0.035199 | -0.017626 | -0.027967 | -0.024101 | 0.008606 | -0.0069641 | 0.06483 | 0.036393 | -0.021358 | -0.0060412 | -0.012896 | -0.032043 | -0.009155 | -0.018311 | 0.009155 | 0.16022 | 0.022888 | 0.050354 | -59.2209 | 0.009155 | -120.5475 | 0.041199 | -118.8721 | -119.252 | -119.838 | 120.4742 | -0.064087 | -0.045777 | 120.6528 | 120.5429 | 120.5154 | 0.068665 | 0.041199 | -0.054931 | -0.045777 | -0.013733 | 1.6205 | 0.6546 | 1.2405 | 0.70953 | 1.2955 | 0.17853 | 0.027466 | 1.6754 | 120.5887 | 0.009156 | 120.5566 | 120.4834 | 120.5017 | -0.073243 | -120.6024 | 120.5017 | 120.5338 | 120.4605 | 61.2717
2312.6406 | 120.7809 | -120.5521 | 0.068665 | -0.0016786 | 0.013719 | -0.035859 | 0.032635 | -0.020617 | -0.030531 | -0.024314 | 0.0055542 | -0.0084595 | 0.065258 | 0.049637 | -0.020717 | -0.0081774 | -0.012469 | -0.004578 | -0.022888 | -0.013733 | 0.018311 | 0.17395 | 0.086975 | 0.073242 | -59.3811 | 0 | -120.5887 | 0.032043 | -118.8721 | -119.2337 | -119.8746 | 120.5383 | -0.091553 | -0.050354 | 120.726 | 120.6253 | 120.639 | 0.086975 | 0.10071 | -0.036621 | -0.068665 | -0.036622 | 1.68 | 0.67749 | 1.3184 | 0.71411 | 1.355 | 0.18768 | 0.032044 | 1.7166 | 120.6207 | -0.009155 | 120.5887 | 120.5292 | 120.5521 | -0.082398 | -120.6573 | 120.5704 | 120.5841 | 120.5475 | 61.171
2314.4375 | 120.8633 | -120.5933 | 0.07782 | 0.0059509 | 0.011796 | -0.033082 | 0.032849 | -0.020403 | -0.029463 | -0.023246 | 0.008606 | -0.0086731 | 0.064617 | 0.052628 | -0.019435 | -0.007323 | -0.014392 | -0.045776 | -0.013733 | -0.013733 | 0.022888 | 0.17853 | 0.068665 | 0.07782 | -59.7656 | 0.009155 | -120.6162 | 0.086975 | -118.8263 | -119.1971 | -119.8563 | 120.5795 | -0.091553 | -0.054932 | 120.7718 | 120.6711 | 120.6619 | 0.091553 | 0.082398 | -0.022888 | -0.068665 | 0.009155 | 1.767 | 0.737 | 1.3962 | 0.75989 | 1.4191 | 0.19226 | 0.036621 | 1.7899 | 120.7031 | 0 | 120.6253 | 120.5795 | 120.6024 | -0.091553 | -120.694 | 120.6161 | 120.6802 | 120.5475 | 60.8276
2316.1562 | 120.8908 | -120.5841 | 0.064087 | 0.01358 | 0.015855 | -0.032654 | 0.034558 | -0.019335 | -0.027113 | -0.024314 | 0.017761 | -0.0061095 | 0.067607 | 0.046219 | -0.017513 | -0.008391 | -0.018878 | 0.004578 | -0.036621 | 0 | 0.064087 | 0.20142 | 0.059509 | 0.086975 | -60.141 | 0.013733 | -120.6253 | 0.10529 | -118.8721 | -119.2566 | -119.8837 | 120.5841 | -0.10071 | 0 | 120.7855 | 120.6711 | 120.6436 | 0.086975 | 0.059509 | -0.041199 | -0.050354 | 0.041199 | 1.712 | 0.70038 | 1.3275 | 0.74158 | 1.3687 | 0.20142 | 0.064087 | 1.7532 | 120.7306 | -0.036621 | 120.639 | 120.5475 | 120.5978 | -0.064087 | -120.6894 | 120.6482 | 120.6894 | 120.5887 | 60.4431
2317.9219 | 120.7169 | -120.0027 | 0.5722 | 0.01358 | 0.016069 | -0.0318 | 0.035626 | -0.016985 | -0.026472 | -0.023246 | 0.0025024 | -0.0076049 | 0.067821 | 0.04387 | -0.019008 | -0.006682 | -0.018023 | -0.036621 | -0.004578 | -0.004578 | -0.022888 | 0.10529 | 0.018311 | 0.032043 | -59.9075 | 0.4715 | -120.0943 | 0.52643 | -118.309 | -118.7302 | -119.3069 | 119.9982 | -0.57678 | -0.59509 | 120.108 | 120.0348 | 120.0211 | 0.036621 | 0.022889 | -0.091552 | -0.10071 | -0.045777 | 1.6937 | 0.6958 | 1.2726 | 0.78735 | 1.3641 | 0.10986 | -0.01831 | 1.7853 | 120.6207 | 0 | 120.5658 | 119.9982 | 120.4742 | -0.57678 | -120.6665 | 119.9799 | 120.5292 | 119.9661 | 60.0952
2319.7031 | 120.845 | -120.6619 | 0.09613 | 0.036468 | 0.015428 | -0.036286 | 0.034772 | -0.015703 | -0.02989 | -0.020897 | 0.011658 | -0.0050415 | 0.064617 | 0.042801 | -0.019222 | -0.0098864 | -0.016528 | -0.041199 | 0.036621 | -0.059509 | -0.036621 | 0.059509 | 0.009155 | 0.004578 | -60.1227 | 0.045776 | -120.6894 | 0 | -118.9499 | -119.3756 | -119.9844 | 120.6024 | -0.059509 | -0.13275 | 120.7214 | 120.6665 | 120.6711 | 0.064087 | 0.068664 | -0.027466 | -0.050354 | -0.09613 | 1.712 | 0.67749 | 1.2863 | 0.70496 | 1.3138 | 0.11902 | 0.022888 | 1.7395 | 120.6894 | 0.09613 | 120.7352 | 120.6985 | 120.7077 | -0.15564 | -120.7855 | 120.6253 | 120.6619 | 120.6207 | 60.5392
2321.4844 | 120.8496 | -120.694 | 0.10986 | 0.01358 | 0.013078 | -0.034577 | 0.034772 | -0.020403 | -0.031599 | -0.023033 | 0.0025024 | -0.0080321 | 0.066967 | 0.040665 | -0.020503 | -0.010955 | -0.012469 | -0.027466 | -0.018311 | -0.018311 | -0.013733 | 0.12817 | 0.050354 | 0.041199 | -60.4248 | 0.041199 | -120.7443 | -0.018311 | -118.959 | -119.3939 | -120.0485 | 120.6757 | -0.12817 | -0.1236 | 120.8221 | 120.7352 | 120.7443 | 0.05951 | 0.068665 | -0.050354 | -0.068664 | -0.12817 | 1.7349 | 0.64545 | 1.3 | 0.6958 | 1.3504 | 0.14649 | 0.004578 | 1.7853 | 120.726 | 0 | 120.7855 | 120.6757 | 120.7352 | -0.12817 | -120.8542 | 120.6802 | 120.6757 | 120.6665 | 60.2692
2323.25 | 120.845 | -120.7581 | 0.086975 | 0.02121 | 0.015641 | -0.036072 | 0.033063 | -0.019762 | -0.028822 | -0.024314 | 0.014709 | -0.0056823 | 0.068462 | 0.045579 | -0.020076 | -0.008391 | -0.015674 | -0.091553 | 0.022888 | -0.045776 | -0.10071 | 0.032043 | -0.027466 | 0.009155 | -60.4889 | 0.064087 | -120.7901 | -0.050354 | -119.0277 | -119.426 | -120.0897 | 120.7123 | -0.064087 | -0.18768 | 120.7901 | 120.7672 | 120.7306 | 0.054931 | 0.01831 | -0.032043 | -0.022888 | -0.13733 | 1.7303 | 0.66833 | 1.3321 | 0.70038 | 1.3641 | 0.077819 | -0.054932 | 1.7624 | 120.7397 | 0.068664 | 120.8542 | 120.7809 | 120.8221 | -0.13275 | -120.8771 | 120.6573 | 120.7077 | 120.6665 | 60.2692
2324.9844 | 121.0144 | -120.7306 | 0.064087 | 0.0059509 | 0.013719 | -0.036286 | 0.034558 | -0.019121 | -0.030317 | -0.026023 | 0.0025024 | -0.0065369 | 0.066112 | 0.050278 | -0.019222 | -0.0092456 | -0.017169 | -0.018311 | -0.050354 | 0 | 0.064087 | 0.22888 | 0.11444 | 0.10071 | -60.791 | 0.018311 | -120.7535 | 0.09613 | -118.8675 | -119.2932 | -119.9982 | 120.7306 | -0.11444 | 0 | 120.9595 | 120.8313 | 120.845 | 0.10071 | 0.11444 | -0.022888 | -0.045776 | 0.032043 | 1.8631 | 0.73242 | 1.4374 | 0.75531 | 1.4603 | 0.22888 | 0.064087 | 1.886 | 120.8496 | -0.050354 | 120.7718 | 120.6802 | 120.7489 | -0.064087 | -120.8176 | 120.7947 | 120.8267 | 120.7123 | 59.9396
2326.7656 | 120.9503 | -120.7809 | 0.091553 | 0.02121 | 0.016282 | -0.03415 | 0.03584 | -0.015917 | -0.028822 | -0.021751 | 0.0025024 | -0.0061095 | 0.06483 | 0.040452 | -0.015377 | -0.010955 | -0.017169 | -0.018311 | 0.004578 | -0.032043 | -0.013733 | 0.12817 | 0.032043 | 0.013733 | -61.2625 | 0.050354 | -120.8084 | 0.032043 | -118.9865 | -119.3985 | -120.0943 | 120.7489 | -0.086975 | -0.10529 | 120.9091 | 120.7947 | 120.813 | 0.045776 | 0.064086 | -0.027466 | -0.041199 | -0.05951 | 1.7944 | 0.68665 | 1.3824 | 0.71411 | 1.4099 | 0.16022 | 0.01831 | 1.8219 | 120.8405 | 0.036621 | 120.8588 | 120.7855 | 120.8313 | -0.1236 | -120.9 | 120.7672 | 120.813 | 120.7626 | 59.5184
2328.5625 | 121.0464 | -120.7397 | 0.086975 | 0.02121 | 0.015214 | -0.035645 | 0.035626 | -0.019335 | -0.028181 | -0.024955 | -0.00054937 | -0.0093139 | 0.064617 | 0.045579 | -0.019008 | -0.0077502 | -0.015033 | -0.009155 | -0.041199 | 0.004578 | 0.045776 | 0.21057 | 0.10529 | 0.09613 | -61.2625 | 0.004578 | -120.7901 | 0.091553 | -118.8812 | -119.2932 | -120.0348 | 120.7443 | -0.12817 | -0.041199 | 120.9503 | 120.8359 | 120.845 | 0.091552 | 0.10071 | -0.050354 | -0.082397 | 0.004578 | 1.8585 | 0.70496 | 1.4465 | 0.75531 | 1.4969 | 0.20599 | 0.041198 | 1.9089 | 120.8817 | -0.045777 | 120.7947 | 120.6985 | 120.7443 | -0.082397 | -120.8771 | 120.7855 | 120.8313 | 120.7306 | 59.4772
2330.2969 | 120.9961 | -120.8038 | 0.10071 | 0.02121 | 0.016496 | -0.03415 | 0.036267 | -0.021898 | -0.030317 | -0.024101 | 0.0025024 | -0.0082459 | 0.067394 | 0.035752 | -0.021785 | -0.0088184 | -0.014392 | -0.082397 | 0.013733 | -0.054932 | -0.086975 | 0.054932 | -0.013733 | -0.027466 | -61.7981 | 0.032043 | -120.8405 | -0.032043 | -119.0002 | -119.3985 | -120.1492 | 120.7489 | -0.086975 | -0.18768 | 120.8588 | 120.7764 | 120.7901 | 0.027466 | 0.041199 | -0.036621 | -0.068665 | -0.13275 | 1.8036 | 0.6546 | 1.4053 | 0.69122 | 1.442 | 0.10986 | -0.032043 | 1.8402 | 120.8084 | 0.068665 | 120.8725 | 120.8176 | 120.8359 | -0.15564 | -120.9412 | 120.7169 | 120.7718 | 120.7214 | 59.0057
2332.0781 | 120.9824 | -120.8038 | 0.068665 | 0.0059509 | 0.013719 | -0.034363 | 0.035626 | -0.019121 | -0.027327 | -0.021965 | 0.0025024 | -0.0041869 | 0.064617 | 0.04451 | -0.013881 | -0.0081774 | -0.015033 | -0.082397 | 0.022888 | -0.041199 | -0.086975 | 0.041199 | -0.059509 | -0.032043 | -61.9766 | 0.041199 | -120.8588 | 0.027466 | -118.9865 | -119.3756 | -120.1035 | 120.7626 | -0.045777 | -0.15564 | 120.845 | 120.7718 | 120.7443 | 0.009156 | -0.01831 | -0.054932 | -0.027466 | -0.041199 | 1.8173 | 0.70038 | 1.4282 | 0.75531 | 1.4832 | 0.082398 | -0.045776 | 1.8723 | 120.8862 | 0.064087 | 120.9 | 120.8267 | 120.845 | -0.10986 | -120.9274 | 120.7169 | 120.8313 | 120.7214 | 58.8272
2333.8594 | 121.0144 | -120.8496 | 0.086975 | 0.01358 | 0.015428 | -0.035218 | 0.038189 | -0.016344 | -0.028395 | -0.021751 | 0.0055542 | -0.0078185 | 0.065685 | 0.044083 | -0.017513 | -0.007323 | -0.015887 | -0.036621 | 0.004578 | -0.027466 | -0.018311 | 0.10986 | 0.013733 | 0.027466 | -62.6541 | 0.041199 | -120.8908 | 0.032043 | -118.959 | -119.3161 | -120.1401 | 120.8221 | -0.082397 | -0.10529 | 120.9595 | 120.8771 | 120.8633 | 0.054932 | 0.041199 | -0.041199 | -0.045776 | -0.054932 | 1.8906 | 0.70953 | 1.5335 | 0.75073 | 1.5747 | 0.13733 | 0.009155 | 1.9318 | 120.9229 | 0.032044 | 120.932 | 120.8542 | 120.8908 | -0.11444 | -120.9778 | 120.8313 | 120.8817 | 120.813 | 58.1955
2335.5781 | 121.1197 | -120.8221 | 0.068665 | 0.02121 | 0.013505 | -0.034577 | 0.035199 | -0.015276 | -0.030104 | -0.021537 | 0.0055542 | -0.0088867 | 0.065258 | 0.046006 | -0.019008 | -0.0077502 | -0.013751 | -0.064087 | -0.022888 | -0.036621 | -0.022888 | 0.11902 | 0.009155 | 0.045776 | -63.0661 | 0.032043 | -120.9091 | 0.059509 | -118.9316 | -119.2657 | -120.1172 | 120.7855 | -0.091553 | -0.091553 | 120.9412 | 120.8679 | 120.8313 | 0.082397 | 0.045776 | -0.086975 | -0.036622 | -0.009156 | 1.8906 | 0.70496 | 1.5564 | 0.79193 | 1.6434 | 0.15564 | 0.013733 | 1.9775 | 120.9686 | 0.013733 | 120.9412 | 120.7993 | 120.8542 | -0.10529 | -120.9778 | 120.7993 | 120.8817 | 120.7581 | 57.756
2337.3594 | 120.5383 | -120.9183 | 0.10529 | 0.0059509 | 0.012864 | -0.033722 | 0.036694 | -0.017199 | -0.029249 | -0.020897 | 0.008606 | -0.0056823 | 0.06718 | 0.041733 | -0.018581 | -0.0094592 | -0.016955 | -0.027466 | -0.013733 | 0.027466 | -0.045776 | 0.091553 | -0.009155 | -0.013733 | -62.9425 | 0.054932 | -120.9091 | 0 | -119.0048 | -119.339 | -120.195 | 120.9457 | -0.11902 | -0.15106 | 121.0098 | 120.9045 | 120.9091 | -0.041199 | -0.036621 | 0.009155 | -0.050354 | -0.10529 | 1.9135 | 0.72327 | 1.5793 | 0.71411 | 1.5701 | 0.064087 | -0.073242 | 1.9043 | 120.9091 | -0.041199 | 120.9641 | 120.9045 | 120.9732 | -0.07782 | -121.0144 | 120.8725 | 120.9183 | 120.8908 | 57.9758
2339.1406 | 121.1151 | -120.8771 | 0.07782 | 0.01358 | 0.013719 | -0.033295 | 0.036267 | -0.01784 | -0.029676 | -0.023033 | -0.00054937 | -0.0054687 | 0.066539 | 0.045579 | -0.017299 | -0.0068958 | -0.01546 | -0.068665 | 0.004578 | -0.018311 | -0.064087 | 0.064087 | -0.036621 | -0.004578 | -63.2721 | 0.036621 | -120.932 | 0.050354 | -118.9407 | -119.2062 | -120.1218 | 120.8588 | -0.073242 | -0.14191 | 120.9412 | 120.8725 | 120.8405 | 0.013733 | -0.01831 | -0.054932 | -0.041199 | -0.027466 | 1.9363 | 0.75531 | 1.6708 | 0.81024 | 1.7258 | 0.082398 | -0.045776 | 1.9913 | 120.9824 | 0.022889 | 120.9686 | 120.8817 | 120.9137 | -0.096131 | -121.0098 | 120.813 | 120.9274 | 120.8084 | 57.605
2340.8594 | 121.1288 | -120.8908 | 0.082397 | 0.02121 | 0.015855 | -0.03415 | 0.036267 | -0.017412 | -0.028822 | -0.021324 | 0.008606 | -0.0067505 | 0.065899 | 0.046647 | -0.02029 | -0.0096728 | -0.013965 | -0.045776 | -0.009155 | -0.022888 | -0.022888 | 0.12817 | 0.009155 | 0.027466 | -63.5651 | 0.045776 | -120.9366 | 0.032043 | -118.9407 | -119.22 | -120.1675 | 120.8679 | -0.091552 | -0.10528 | 121.019 | 120.9183 | 120.9 | 0.050354 | 0.032043 | -0.045776 | -0.036621 | -0.050354 | 1.9501 | 0.72327 | 1.6708 | 0.76904 | 1.7166 | 0.15106 | 0 | 1.9958 | 120.9686 | 0.013733 | 120.9824 | 120.8817 | 120.9366 | -0.10528 | -121.019 | 120.8679 | 120.9229 | 120.845 | 57.3257
2342.6406 | 121.0693 | -120.9457 | 0.073242 | 0.0059509 | 0.015641 | -0.033509 | 0.03584 | -0.016985 | -0.028395 | -0.021965 | 0.0055542 | -0.0071777 | 0.06718 | 0.045151 | -0.018794 | -0.005614 | -0.016528 | -0.073242 | 0 | -0.041199 | -0.11444 | 0.009155 | -0.068665 | -0.050354 | -63.9084 | 0.027466 | -121.0007 | -0.022888 | -119.0094 | -119.3069 | -120.2499 | 120.9045 | -0.073242 | -0.18768 | 120.9549 | 120.8954 | 120.8771 | -0.009155 | -0.027466 | -0.054931 | -0.045776 | -0.09613 | 1.9363 | 0.6958 | 1.6388 | 0.75073 | 1.6937 | 0.050354 | -0.073242 | 1.9913 | 120.9778 | 0.041199 | 121.0281 | 120.9457 | 120.9732 | -0.11444 | -121.0739 | 120.8313 | 120.9229 | 120.8725 | 57.0374
2344.4219 | 121.1838 | -120.9503 | 0.045776 | 0.036468 | 0.015214 | -0.033509 | 0.036908 | -0.015062 | -0.029036 | -0.020897 | 0.008606 | -0.0080321 | 0.066326 | 0.048142 | -0.016872 | -0.0071094 | -0.01311 | -0.022888 | -0.009155 | -0.009155 | 0 | 0.17395 | 0.027466 | 0.045776 | -64.1327 | 0.013733 | -121.0007 | 0.054932 | -118.895 | -119.1834 | -120.2179 | 120.9412 | -0.054931 | -0.045776 | 121.1243 | 120.9961 | 120.9778 | 0.054931 | 0.036621 | -0.050354 | -0.032043 | 0.009156 | 2.0554 | 0.73242 | 1.767 | 0.78278 | 1.8173 | 0.1831 | 0.009155 | 2.1057 | 121.0556 | 0 | 121.0144 | 120.9412 | 120.9641 | -0.054931 | -121.0464 | 120.9503 | 121.0052 | 120.9274 | 56.8176
2346.1406 | 121.0785 | -120.7626 | 0.24261 | 0.0059509 | 0.014573 | -0.034791 | 0.037335 | -0.01549 | -0.029676 | -0.02111 | 0.0055542 | -0.0052551 | 0.066967 | 0.04686 | -0.018367 | -0.0094592 | -0.01076 | -0.068665 | 0.009155 | -0.045776 | -0.10071 | 0.018311 | -0.073242 | -0.050354 | -64.3387 | 0.17395 | -120.813 | 0.12817 | -118.7485 | -119.0643 | -120.0485 | 120.7169 | -0.23346 | -0.34332 | 120.7809 | 120.7123 | 120.6894 | -0.004578 | -0.027466 | -0.050354 | -0.068665 | -0.11444 | 2.0142 | 0.71411 | 1.6983 | 0.76447 | 1.7487 | 0.064087 | -0.054932 | 2.0645 | 120.9412 | 0.054931 | 120.9869 | 120.7718 | 120.9366 | -0.28839 | -121.0556 | 120.6619 | 120.8908 | 120.694 | 56.424
2347.9219 | 121.2753 | -120.9778 | 0.068665 | -0.0016786 | 0.013292 | -0.034363 | 0.037762 | -0.010363 | -0.026899 | -0.024101 | 0.0055542 | -0.0067505 | 0.066753 | 0.050706 | -0.015163 | -0.0043322 | -0.016742 | 0.009155 | -0.032043 | 0.009155 | 0.045776 | 0.17395 | 0.045776 | 0.073242 | -64.6225 | -0.013733 | -121.0144 | 0.10986 | -118.8263 | -119.1193 | -120.1767 | 120.9869 | -0.10071 | -0.022889 | 121.1517 | 121.051 | 121.0236 | 0.064087 | 0.036621 | -0.036621 | -0.082398 | 0.041198 | 2.1515 | 0.80109 | 1.8585 | 0.83771 | 1.8951 | 0.16479 | 0.036621 | 2.1881 | 121.1243 | -0.041198 | 121.0007 | 120.9457 | 120.9641 | -0.05951 | -121.0831 | 121.0236 | 121.0876 | 120.9869 | 56.3553
2349.7031 | 121.1563 | -121.0373 | 0.10986 | 0.0059509 | 0.01436 | -0.034791 | 0.036053 | -0.017412 | -0.029249 | -0.022819 | 0.020813 | -0.0067505 | 0.066753 | 0.049424 | -0.021572 | -0.0094592 | -0.014605 | -0.059509 | 0.050354 | -0.073242 | -0.07782 | 0.068665 | -0.009155 | -0.004578 | -65.1581 | 0.045776 | -121.051 | -0.018311 | -118.9407 | -119.1971 | -120.2957 | 120.9641 | -0.059509 | -0.18768 | 121.106 | 121.0327 | 121.0281 | 0.068664 | 0.064087 | -0.013733 | -0.064087 | -0.12817 | 2.0966 | 0.74158 | 1.8402 | 0.75531 | 1.8539 | 0.14191 | -0.004578 | 2.1103 | 121.0327 | 0.1236 | 121.0968 | 121.0876 | 121.0831 | -0.18311 | -121.1609 | 120.9595 | 121.019 | 120.9778 | 55.8792
2351.4219 | 121.2158 | -121.0602 | 0.086975 | 0.036468 | 0.016069 | -0.035431 | 0.035626 | -0.016344 | -0.027754 | -0.021751 | 0.014709 | -0.0073913 | 0.068248 | 0.048569 | -0.02029 | -0.0101 | -0.014178 | -0.059509 | 0.022888 | -0.045776 | -0.050354 | 0.054932 | -0.004578 | 0 | -65.5609 | 0.059509 | -121.0739 | 0.004578 | -118.8675 | -119.1605 | -120.2728 | 121.0144 | -0.064087 | -0.13733 | 121.1151 | 121.0602 | 121.0556 | 0.045776 | 0.041198 | -0.013733 | -0.027466 | -0.082397 | 2.1927 | 0.78735 | 1.8997 | 0.80109 | 1.9135 | 0.10071 | -0.004578 | 2.2064 | 121.0785 | 0.068664 | 121.1334 | 121.0831 | 121.1197 | -0.13275 | -121.1609 | 121.0098 | 121.0648 | 121.0007 | 55.4993
2353.2031 | 121.2341 | -121.0602 | 0.091553 | 0.02121 | 0.01436 | -0.037781 | 0.036267 | -0.017199 | -0.030317 | -0.020469 | 0.0055542 | -0.0058959 | 0.068676 | 0.046006 | -0.021144 | -0.010527 | -0.011828 | -0.10529 | 0.004578 | -0.054932 | -0.10071 | 0.041199 | -0.036621 | -0.009155 | -66.1423 | 0.045776 | -121.1243 | -0.050354 | -118.9041 | -119.1467 | -120.3369 | 121.0052 | -0.086975 | -0.19226 | 121.1014 | 121.051 | 121.0236 | 0.045777 | 0.018311 | -0.064087 | -0.045777 | -0.14191 | 2.1561 | 0.72327 | 1.9135 | 0.78735 | 1.9775 | 0.096131 | -0.045776 | 2.2202 | 121.0739 | 0.05951 | 121.17 | 121.0648 | 121.106 | -0.14649 | -121.2158 | 120.9595 | 121.0098 | 120.9549 | 54.9179
2354.9062 | 121.2112 | -121.0739 | 0.068665 | 0.01358 | 0.013719 | -0.034791 | 0.034985 | -0.015276 | -0.029249 | -0.023674 | -0.00054937 | -0.0061095 | 0.064617 | 0.040665 | -0.016872 | -0.0092456 | -0.013324 | -0.041199 | 0.004578 | -0.041199 | -0.050354 | 0.10529 | -0.004578 | -0.013733 | -66.1148 | 0.041199 | -121.0876 | 0 | -118.8904 | -119.1422 | -120.3186 | 121.0327 | -0.064087 | -0.11902 | 121.1792 | 121.0602 | 121.0693 | 0.027466 | 0.036621 | -0.013732 | -0.027466 | -0.068665 | 2.1835 | 0.75531 | 1.9318 | 0.76904 | 1.9455 | 0.14649 | -0.009155 | 2.1973 | 121.0876 | 0.045777 | 121.1288 | 121.0785 | 121.1151 | -0.10986 | -121.1563 | 121.0236 | 121.0739 | 121.0327 | 54.9591
2356.6875 | 121.3715 | -121.051 | 0.054932 | 0.0059509 | 0.012224 | -0.034791 | 0.032208 | -0.019976 | -0.029676 | -0.022605 | 0.0025024 | -0.0071777 | 0.066112 | 0.046433 | -0.01794 | -0.005614 | -0.01546 | -0.041199 | -0.045776 | -0.013733 | 0.013733 | 0.16937 | 0.086975 | 0.09613 | -66.2155 | 0 | -121.106 | 0.10529 | -118.7256 | -118.9682 | -120.2271 | 121.0373 | -0.10071 | -0.041199 | 121.2204 | 121.1472 | 121.138 | 0.10986 | 0.10071 | -0.054932 | -0.054932 | 0.050354 | 2.3254 | 0.82397 | 2.0828 | 0.87891 | 2.1378 | 0.18311 | 0.027466 | 2.3804 | 121.2112 | -0.032043 | 121.106 | 121.0052 | 121.051 | -0.068665 | -121.1609 | 121.0648 | 121.1563 | 121.0098 | 54.8355
2358.4844 | 121.2387 | -121.1105 | 0.091553 | 0.0059509 | 0.015641 | -0.035859 | 0.032635 | -0.01784 | -0.027967 | -0.02346 | 0.0055542 | -0.0056823 | 0.066539 | 0.04387 | -0.020503 | -0.008391 | -0.0092648 | -0.013733 | -0.027466 | -0.004578 | -0.032043 | 0.13275 | 0.050354 | 0.041199 | -66.4261 | 0.022888 | -121.1334 | -0.018311 | -118.7943 | -119.046 | -120.3415 | 121.106 | -0.11902 | -0.1236 | 121.2433 | 121.1517 | 121.1609 | 0.045777 | 0.054932 | -0.022888 | -0.068665 | -0.10986 | 2.3163 | 0.76904 | 2.0645 | 0.79193 | 2.0874 | 0.13733 | -0.027465 | 2.3392 | 121.1151 | -0.022888 | 121.1563 | 121.0831 | 121.1334 | -0.096131 | -121.225 | 121.0785 | 121.0922 | 121.0968 | 54.6844
2360.2031 | 121.344 | -121.0419 | 0.07782 | 0.0059509 | 0.014146 | -0.034791 | 0.035199 | -0.014422 | -0.030745 | -0.024314 | 0.0055542 | -0.0056823 | 0.065044 | 0.048142 | -0.016658 | -0.0081774 | -0.01546 | 0 | -0.022888 | -0.013733 | 0.045776 | 0.19684 | 0.11902 | 0.086975 | -66.7648 | 0.004578 | -121.1243 | 0.09613 | -118.6752 | -118.927 | -120.2682 | 121.0281 | -0.10071 | -0.032044 | 121.2387 | 121.1288 | 121.1609 | 0.10071 | 0.13275 | -0.082398 | -0.073242 | 0.01831 | 2.3666 | 0.77362 | 2.1149 | 0.85602 | 2.1973 | 0.21057 | 0.059509 | 2.449 | 121.2204 | -0.009155 | 121.1288 | 121.019 | 121.0464 | -0.091553 | -121.2021 | 121.0876 | 121.138 | 121.0419 | 54.277
2361.9844 | 121.3074 | -121.1197 | 0.09613 | 0.02121 | 0.014146 | -0.034791 | 0.038189 | -0.018053 | -0.030745 | -0.023674 | 0.008606 | -0.0056823 | 0.068035 | 0.042801 | -0.018367 | -0.009032 | -0.016314 | -0.013733 | 0.009155 | -0.041199 | -0.022888 | 0.10529 | 0.009155 | 0.018311 | -66.9388 | 0.045776 | -121.1563 | 0.022888 | -118.7576 | -118.9865 | -120.3278 | 121.0785 | -0.086975 | -0.11902 | 121.225 | 121.138 | 121.1288 | 0.05951 | 0.050354 | -0.036621 | -0.050354 | -0.073242 | 2.3621 | 0.79193 | 2.1332 | 0.82855 | 2.1698 | 0.14649 | 0.018311 | 2.3987 | 121.1792 | 0.050354 | 121.2021 | 121.1288 | 121.1655 | -0.13733 | -121.2524 | 121.0968 | 121.1426 | 121.106 | 54.1809
2363.7656 | 121.4081 | -121.0831 | 0.068665 | 0.0059509 | 0.010728 | -0.035218 | 0.036267 | -0.024462 | -0.030531 | -0.023246 | 0.0025024 | -0.0088867 | 0.065899 | 0.042588 | -0.017513 | -0.0088184 | -0.015246 | -0.013733 | -0.022888 | -0.013733 | 0.059509 | 0.20599 | 0.09613 | 0.091553 | -67.0761 | 0 | -121.1334 | 0.11444 | -118.6157 | -118.84 | -120.2682 | 121.0693 | -0.091553 | -0.009156 | 121.2891 | 121.1746 | 121.1792 | 0.10529 | 0.10986 | -0.050354 | -0.068665 | 0.045776 | 2.4673 | 0.81482 | 2.243 | 0.86517 | 2.2934 | 0.21973 | 0.073242 | 2.5177 | 121.2479 | -0.009155 | 121.1334 | 121.0602 | 121.0831 | -0.082398 | -121.2021 | 121.1426 | 121.1975 | 121.0693 | 54.007
2365.5469 | 121.2799 | -121.0236 | 0.11444 | 0.036468 | 0.010942 | -0.033936 | 0.036053 | -0.01549 | -0.028608 | -0.020683 | 0.008606 | -0.0063233 | 0.068248 | 0.047501 | -0.015804 | -0.0081774 | -0.014178 | -0.045776 | 0.004578 | -0.004578 | 0 | 0.14648 | 0.032043 | 0.045776 | -67.5156 | 0.045776 | -121.0785 | 0.091553 | -118.6066 | -118.7988 | -120.2316 | 121.019 | -0.10986 | -0.11444 | 121.17 | 121.0693 | 121.0556 | 0.050354 | 0.036621 | -0.054931 | -0.068665 | -0.022888 | 2.417 | 0.79193 | 2.2247 | 0.84686 | 2.2797 | 0.15106 | 0.004578 | 2.4719 | 121.17 | 0.009156 | 121.1243 | 121.0281 | 121.0693 | -0.11902 | -121.1929 | 121.0236 | 121.1151 | 120.9778 | 53.508
2367.3281 | 119.902 | -119.6732 | 0.064087 | 0.0059509 | 0.011796 | -0.033295 | 0.036053 | -0.018694 | -0.029676 | -0.023033 | 0.0025024 | -0.0091003 | 0.066112 | 0.047074 | -0.014949 | -0.0062548 | -0.012896 | -0.036621 | -0.018311 | -0.018311 | 0.004578 | 0.1236 | 0.018311 | 0.045776 | -67.0395 | 0.018311 | -119.6686 | 0.09613 | -117.1829 | -117.3523 | -118.8126 | 119.6548 | -0.082398 | -0.059509 | 119.7968 | 119.7189 | 119.6915 | 0.064087 | 0.036622 | 0.004578 | -0.045776 | 0.032043 | 2.4902 | 0.8606 | 2.3209 | 0.85602 | 2.3163 | 0.14191 | 0.022889 | 2.4857 | 119.7647 | 0 | 119.6869 | 119.6548 | 119.6915 | -0.082398 | -119.7327 | 119.6777 | 119.7693 | 119.6365 | 52.6337
2369.0469 | 120.8405 | -120.7672 | 0.10071 | -0.0016786 | 0.015001 | -0.035431 | 0.036694 | -0.014635 | -0.02754 | -0.02111 | 0.0055542 | -0.0044007 | 0.068676 | 0.048142 | -0.017726 | -0.0079638 | -0.016528 | -0.07782 | 0.009155 | -0.036621 | -0.09613 | 0.004578 | -0.07782 | -0.068665 | -68.1519 | 0.045776 | -120.7672 | -0.013733 | -118.3136 | -118.483 | -119.9661 | 120.7306 | -0.091553 | -0.19684 | 120.7718 | 120.6985 | 120.6894 | -0.032044 | -0.041199 | 0 | -0.054932 | -0.11444 | 2.4536 | 0.80109 | 2.2842 | 0.80109 | 2.2842 | 0.041199 | -0.059509 | 2.4536 | 120.7535 | 0.045776 | 120.813 | 120.7764 | 120.813 | -0.13733 | -120.8679 | 120.6711 | 120.7535 | 120.6894 | 52.6154
2370.8438 | 121.0739 | -120.8038 | 0.068665 | 0.044098 | 0.014787 | -0.030945 | 0.036908 | -0.015062 | -0.026472 | -0.022819 | 0.017761 | -0.0080321 | 0.069744 | 0.056046 | -0.015163 | -0.0054004 | -0.014605 | 0.036621 | -0.027466 | -0.009155 | 0.054932 | 0.21057 | 0.07782 | 0.073242 | -68.4036 | 0.013733 | -120.8679 | 0.10986 | -118.2129 | -118.4143 | -119.9661 | 120.7947 | -0.096131 | -0.013733 | 121.0144 | 120.8771 | 120.8817 | 0.082397 | 0.086975 | -0.064087 | -0.054932 | 0.041198 | 2.5909 | 0.83771 | 2.3895 | 0.90179 | 2.4536 | 0.21973 | 0.064087 | 2.655 | 120.9778 | -0.018311 | 120.8817 | 120.7764 | 120.8176 | -0.07782 | -120.9366 | 120.8588 | 120.9137 | 120.8405 | 52.4002
2372.625 | 121.106 | -120.8633 | 0.073242 | 0.0059509 | 0.013078 | -0.035218 | 0.037335 | -0.015276 | -0.028608 | -0.021537 | -0.00054937 | -0.0071777 | 0.067607 | 0.044083 | -0.016445 | -0.0051868 | -0.013751 | -0.054932 | 0 | -0.036621 | -0.059509 | 0.073242 | -0.013733 | -0.004578 | -68.898 | 0.018311 | -120.9229 | 0.064087 | -118.277 | -118.4647 | -120.0439 | 120.8267 | -0.073242 | -0.13275 | 120.9366 | 120.8588 | 120.8496 | 0.032043 | 0.022888 | -0.05951 | -0.054931 | -0.009155 | 2.5864 | 0.8194 | 2.3987 | 0.87891 | 2.4582 | 0.10986 | -0.022888 | 2.6459 | 120.9869 | 0.036621 | 120.9412 | 120.8633 | 120.8817 | -0.10986 | -120.9961 | 120.8038 | 120.9274 | 120.8084 | 51.9653
2374.3594 | 121.1563 | -120.9045 | 0.082397 | 0.028839 | 0.01436 | -0.035218 | 0.034985 | -0.019976 | -0.028608 | -0.020897 | 0.011658 | -0.0058959 | 0.068676 | 0.053269 | -0.017299 | -0.0058276 | -0.013965 | -0.032043 | -0.018311 | 0 | 0.009155 | 0.14648 | 0.032043 | 0.059509 | -69.0765 | 0.004578 | -120.9778 | 0.036621 | -118.2587 | -118.4372 | -120.1035 | 120.9045 | -0.10071 | -0.073242 | 121.051 | 120.9641 | 120.9366 | 0.059509 | 0.032043 | -0.073242 | -0.077819 | -0.045776 | 2.6459 | 0.80109 | 2.4673 | 0.87433 | 2.5406 | 0.14648 | 0.009155 | 2.7191 | 121.0144 | -0.018311 | 120.9824 | 120.8862 | 120.9091 | -0.082397 | -121.0602 | 120.9137 | 120.9412 | 120.8725 | 51.828
2376.1406 | 121.2708 | -120.9274 | 0.07782 | 0.028839 | 0.012864 | -0.035859 | 0.034985 | -0.019121 | -0.029036 | -0.022178 | 0.0055542 | -0.0080321 | 0.066112 | 0.048569 | -0.020503 | -0.0079638 | -0.016955 | -0.013733 | -0.036621 | -0.022888 | 0.041199 | 0.20599 | 0.10071 | 0.10071 | -69.2184 | 0.009155 | -121.0007 | 0.10071 | -118.1717 | -118.3136 | -120.0485 | 120.9045 | -0.11444 | -0.036621 | 121.1334 | 121.0281 | 121.0281 | 0.1236 | 0.1236 | -0.073242 | -0.068665 | 0.022888 | 2.7557 | 0.87891 | 2.6138 | 0.95215 | 2.6871 | 0.22888 | 0.064087 | 2.829 | 121.1014 | -0.013733 | 121.0098 | 120.8908 | 120.9366 | -0.10071 | -121.0785 | 120.9686 | 121.0281 | 120.9137 | 51.709
2377.9219 | 121.1655 | -120.9869 | 0.082397 | -0.0016786 | 0.013719 | -0.035004 | 0.038403 | -0.013781 | -0.027113 | -0.025596 | 0.0025024 | -0.0050415 | 0.065685 | 0.043015 | -0.017085 | -0.006682 | -0.01311 | -0.07782 | 0.013733 | -0.032043 | -0.073242 | 0.054932 | -0.059509 | -0.036621 | -69.5618 | 0.032043 | -121.051 | 0.013733 | -118.277 | -118.428 | -120.1584 | 120.9549 | -0.068664 | -0.15564 | 121.0419 | 120.9503 | 120.9274 | -0.004578 | -0.027466 | -0.064087 | -0.050354 | -0.068664 | 2.71 | 0.82855 | 2.5589 | 0.89264 | 2.623 | 0.086975 | -0.041199 | 2.774 | 121.0648 | 0.045776 | 121.0831 | 121.0007 | 121.019 | -0.11444 | -121.1334 | 120.9137 | 121.0007 | 120.9091 | 51.4252
2379.7188 | 121.3165 | -121.0098 | 0.11444 | 0.044098 | 0.013719 | -0.032441 | 0.037549 | -0.015917 | -0.029676 | -0.023674 | 0.008606 | -0.0061095 | 0.066753 | 0.043015 | -0.019649 | -0.0068958 | -0.011828 | -0.032043 | 0.018311 | -0.036621 | -0.027466 | 0.10529 | 0.018311 | 0.018311 | -69.6579 | 0.064087 | -121.051 | 0.027466 | -118.0756 | -118.1854 | -120.0623 | 120.9732 | -0.09613 | -0.14191 | 121.1151 | 121.0281 | 121.0281 | 0.054932 | 0.054932 | -0.041198 | -0.050354 | -0.086975 | 2.9343 | 0.94757 | 2.8244 | 0.98877 | 2.8656 | 0.14191 | 0.009155 | 2.9755 | 121.0785 | 0.054932 | 121.1151 | 121.0281 | 121.0739 | -0.15106 | -121.1655 | 120.9824 | 121.0373 | 120.9778 | 51.3519
2381.4375 | 121.1655 | -121.0831 | 0.091553 | 0.0059509 | 0.013933 | -0.034363 | 0.033917 | -0.020617 | -0.030317 | -0.022819 | 0.0025024 | -0.0058959 | 0.069103 | 0.04451 | -0.023494 | -0.0098864 | -0.011615 | -0.10071 | 0.009155 | -0.050354 | -0.091553 | 0.050354 | -0.022888 | -0.022888 | -69.8776 | 0.036621 | -121.0922 | -0.054932 | -118.2358 | -118.3365 | -120.2133 | 121.0327 | -0.082398 | -0.18311 | 121.1334 | 121.0602 | 121.0602 | 0.027466 | 0.027466 | -0.009155 | -0.054932 | -0.14649 | 2.8473 | 0.86975 | 2.7466 | 0.87891 | 2.7557 | 0.10071 | -0.041199 | 2.8564 | 121.0373 | 0.059509 | 121.1288 | 121.0922 | 121.1197 | -0.14191 | -121.1838 | 120.9915 | 121.0281 | 120.9824 | 51.2054
2383.2188 | 121.2982 | -121.0876 | 0.082397 | 0.01358 | 0.014787 | -0.033722 | 0.036694 | -0.019121 | -0.030317 | -0.023033 | 0.008606 | -0.0061095 | 0.067394 | 0.047501 | -0.018581 | -0.007323 | -0.014392 | -0.050354 | -0.032043 | -0.009155 | -0.022888 | 0.11902 | 0.022888 | 0.050354 | -70.1111 | 0.018311 | -121.0922 | 0.032043 | -118.1259 | -118.1992 | -120.1721 | 121.0785 | -0.11444 | -0.10528 | 121.2067 | 121.138 | 121.1105 | 0.059509 | 0.032043 | -0.004578 | -0.064086 | -0.050354 | 2.9617 | 0.91553 | 2.8885 | 0.92011 | 2.8931 | 0.12817 | -0.013733 | 2.9663 | 121.1243 | -0.022888 | 121.1105 | 121.0556 | 121.106 | -0.091552 | -121.1746 | 121.0648 | 121.1197 | 121.0373 | 50.9766
2384.9219 | 121.2387 | -121.0922 | 0.082397 | 0.01358 | 0.01201 | -0.034363 | 0.037335 | -0.015062 | -0.029463 | -0.023674 | 0.008606 | -0.0041869 | 0.06483 | 0.043229 | -0.017513 | -0.009032 | -0.015674 | -0.07782 | 0 | -0.045776 | -0.10529 | 0.027466 | -0.064087 | -0.041199 | -70.2942 | 0.036621 | -121.1288 | -0.018311 | -118.1763 | -118.2358 | -120.2316 | 121.0464 | -0.082397 | -0.18768 | 121.1197 | 121.051 | 121.0281 | 0.004577 | -0.018311 | -0.036621 | -0.045776 | -0.10071 | 2.916 | 0.8606 | 2.8564 | 0.89722 | 2.8931 | 0.073242 | -0.05951 | 2.9526 | 121.1105 | 0.045776 | 121.1655 | 121.0922 | 121.1288 | -0.12817 | -121.2112 | 120.9869 | 121.0739 | 121.0144 | 50.798
2386.7031 | 121.2891 | -121.0648 | 0.09613 | 0.028839 | 0.014787 | -0.033722 | 0.038617 | -0.016558 | -0.028608 | -0.022178 | 0.0055542 | -0.0044007 | 0.068676 | 0.043442 | -0.017726 | -0.0051868 | -0.014392 | -0.054932 | -0.036621 | -0.009155 | -0.009155 | 0.11902 | 0.027466 | 0.050354 | -70.3583 | 0.022888 | -121.0831 | 0.050354 | -118.0115 | -118.0481 | -120.1447 | 121.0556 | -0.13275 | -0.10528 | 121.1838 | 121.1151 | 121.0922 | 0.059509 | 0.036621 | -0.018311 | -0.073242 | -0.045776 | 3.0533 | 0.9201 | 3.0167 | 0.93842 | 3.035 | 0.12817 | 0 | 3.0716 | 121.1334 | -0.027466 | 121.106 | 121.0281 | 121.0876 | -0.10528 | -121.1792 | 121.0556 | 121.1151 | 121.0098 | 50.7065
2388.5 | 120.4468 | -120.4056 | 0.10529 | 0.044098 | 0.01671 | -0.035431 | 0.033917 | -0.017626 | -0.030104 | -0.019615 | 0.011658 | -0.0026917 | 0.067607 | 0.037461 | -0.019649 | -0.0075366 | -0.011401 | -0.064087 | 0.022888 | -0.059509 | -0.07782 | 0.050354 | -0.009155 | -0.013733 | -70.0012 | 0.032043 | -120.4056 | -0.041199 | -117.2882 | -117.3065 | -119.4626 | 120.3461 | -0.082398 | -0.18311 | 120.4559 | 120.3918 | 120.3964 | 0.045776 | 0.050354 | 0 | -0.073243 | -0.14649 | 3.1174 | 0.94299 | 3.0991 | 0.94299 | 3.0991 | 0.10986 | -0.018311 | 3.1174 | 120.3644 | 0.082397 | 120.4376 | 120.4285 | 120.4376 | -0.16479 | -120.5109 | 120.3278 | 120.3644 | 120.3415 | 50.4044
2390.2969 | 121.051 | -120.9091 | 0.091553 | 0.028839 | 0.01436 | -0.035431 | 0.038403 | -0.019335 | -0.029463 | -0.023033 | 0.008606 | -0.0046143 | 0.066967 | 0.040879 | -0.020076 | -0.0071094 | -0.013751 | -0.054932 | 0.022888 | -0.064087 | -0.041199 | 0.082397 | -0.004578 | -0.004578 | -70.1889 | 0.045776 | -120.9274 | 0.004578 | -117.7048 | -117.7231 | -119.957 | 120.845 | -0.068665 | -0.13275 | 120.9915 | 120.9045 | 120.9045 | 0.059509 | 0.059509 | -0.01831 | -0.045777 | -0.086975 | 3.2043 | 0.95215 | 3.186 | 0.97046 | 3.2043 | 0.14648 | 0.022888 | 3.2227 | 120.932 | 0.086975 | 120.9732 | 120.932 | 120.9549 | -0.15564 | -121.019 | 120.8679 | 120.9137 | 120.8542 | 50.7202
2392.0625 | 121.1014 | -120.9778 | 0.10071 | 0.01358 | 0.013933 | -0.033509 | 0.034985 | -0.015917 | -0.028822 | -0.020469 | 0.0025024 | -0.0044007 | 0.066967 | 0.044724 | -0.016445 | -0.0060412 | -0.016742 | -0.073242 | 0.009155 | -0.054932 | -0.11444 | 0.022888 | -0.054932 | -0.045776 | -70.2347 | 0.032043 | -120.9824 | -0.013733 | -117.7414 | -117.746 | -120.0577 | 120.9229 | -0.091553 | -0.21515 | 121.0007 | 120.932 | 120.9229 | 0.009156 | 0 | -0.004578 | -0.068665 | -0.11444 | 3.2364 | 0.92011 | 3.2318 | 0.92468 | 3.2364 | 0.07782 | -0.059509 | 3.241 | 120.9686 | 0.064087 | 121.0144 | 120.9869 | 121.0098 | -0.15564 | -121.0831 | 120.8633 | 120.9641 | 120.9045 | 50.7431
2393.8594 | 121.2479 | -120.932 | 0.086975 | 0.01358 | 0.014146 | -0.035218 | 0.038617 | -0.01784 | -0.026045 | -0.02111 | 0.014709 | -0.0041869 | 0.065899 | 0.047928 | -0.017299 | -0.0058276 | -0.010333 | 0.027466 | -0.009155 | -0.018311 | 0.054932 | 0.19684 | 0.091553 | 0.086975 | -70.1202 | 0.036621 | -120.9961 | 0.11444 | -117.5629 | -117.5262 | -119.9753 | 120.9137 | -0.09613 | -0.032043 | 121.1288 | 121.019 | 121.0236 | 0.10529 | 0.10986 | -0.064087 | -0.050354 | 0.027466 | 3.3691 | 0.95673 | 3.4058 | 1.0208 | 3.4698 | 0.21515 | 0.073243 | 3.4332 | 121.1105 | 0.009156 | 121.0327 | 120.9229 | 120.9686 | -0.10529 | -121.0831 | 120.9869 | 121.0464 | 120.9595 | 50.8118
2395.5938 | 121.1746 | -121.0236 | 0.10986 | -0.0093076 | 0.014787 | -0.034363 | 0.034558 | -0.016344 | -0.02989 | -0.023246 | 0.0025024 | -0.0061095 | 0.068035 | 0.045792 | -0.021785 | -0.010314 | -0.013324 | -0.013733 | -0.013733 | -0.027466 | 0 | 0.15564 | 0.045776 | 0.050354 | -70.1111 | 0.013733 | -121.0831 | -0.009155 | -117.6086 | -117.5583 | -120.0943 | 120.9961 | -0.1236 | -0.10986 | 121.1792 | 121.0739 | 121.0693 | 0.07782 | 0.073242 | -0.059509 | -0.09613 | -0.11902 | 3.4149 | 0.92926 | 3.4653 | 0.98877 | 3.5248 | 0.18311 | 0.027466 | 3.4744 | 121.0739 | 0.013733 | 121.0968 | 121.0098 | 121.0373 | -0.13733 | -121.1929 | 121.0236 | 121.0144 | 121.0098 | 50.9125
2397.375 | 121.2067 | -121.0693 | 0.086975 | 0.01358 | 0.015641 | -0.033936 | 0.036908 | -0.01784 | -0.028608 | -0.025169 | 0.0025024 | -0.0029053 | 0.069744 | 0.039384 | -0.017513 | -0.007323 | -0.012256 | -0.036621 | 0.004578 | -0.032043 | -0.050354 | 0.086975 | -0.032043 | -0.027466 | -69.8685 | 0.045776 | -121.1197 | -0.018311 | -117.5995 | -117.5262 | -120.1263 | 121.0373 | -0.082397 | -0.13733 | 121.1563 | 121.0419 | 121.0373 | 0.004577 | 0 | -0.050354 | -0.041199 | -0.10529 | 3.4698 | 0.94299 | 3.5431 | 0.99335 | 3.5934 | 0.11902 | -0.018311 | 3.5202 | 121.1014 | 0.036621 | 121.1655 | 121.0739 | 121.1151 | -0.11902 | -121.2067 | 121.019 | 121.051 | 121.0327 | 51.2009
2399.1719 | 121.2021 | -120.9869 | 0.1831 | 0.0059509 | 0.013933 | -0.034791 | 0.036053 | -0.022967 | -0.030745 | -0.024101 | 0.0025024 | -0.0041869 | 0.071239 | 0.047288 | -0.02264 | -0.0086048 | -0.010119 | -0.068665 | -0.004578 | -0.022888 | -0.073242 | 0.07782 | -0.004578 | -0.022888 | -69.5435 | 0.1236 | -121.0373 | 0.050354 | -117.421 | -117.3065 | -120.0485 | 120.9641 | -0.18768 | -0.25635 | 121.0648 | 120.9641 | 120.9824 | 0 | 0.01831 | -0.050354 | -0.059509 | -0.13275 | 3.566 | 0.93841 | 3.6804 | 0.98877 | 3.7308 | 0.10071 | -0.050354 | 3.6163 | 121.0876 | 0.01831 | 121.1609 | 120.9824 | 121.1105 | -0.20599 | -121.2204 | 120.9137 | 121.0373 | 120.9183 | 51.4435
2400.9062 | 121.2387 | -121.1105 | 0.07782 | 0.0059509 | 0.012864 | -0.03415 | 0.037762 | -0.016985 | -0.029676 | -0.020042 | -0.00054937 | -0.0035461 | 0.066967 | 0.045151 | -0.015377 | -0.0071094 | -0.011828 | -0.032043 | 0.009155 | -0.027466 | -0.041199 | 0.086975 | -0.004578 | -0.013733 | -69.3329 | 0.050354 | -121.138 | -0.004578 | -117.4255 | -117.3431 | -120.1447 | 121.0831 | -0.068665 | -0.11902 | 121.1975 | 121.0968 | 121.106 | 0.013733 | 0.022888 | -0.027465 | -0.027466 | -0.082398 | 3.685 | 0.96588 | 3.7674 | 0.99335 | 3.7949 | 0.11444 | -0.013733 | 3.7125 | 121.1334 | 0.036621 | 121.1884 | 121.1197 | 121.1609 | -0.10529 | -121.2158 | 121.0693 | 121.106 | 121.0785 | 51.7776
2402.6875 | 121.3715 | -121.0602 | 0.050354 | 0.0059509 | 0.016496 | -0.0318 | 0.034772 | -0.018267 | -0.027967 | -0.020469 | 0.020813 | -0.0039733 | 0.068248 | 0.042161 | -0.016017 | -0.0043322 | -0.015033 | 0.027466 | -0.009155 | -0.018311 | 0.064087 | 0.19684 | 0.068665 | 0.086975 | -68.7515 | 0.027466 | -121.1426 | 0.10071 | -117.2195 | -117.1051 | -120.0439 | 121.0419 | -0.059509 | 0.013733 | 121.257 | 121.1472 | 121.1288 | 0.10529 | 0.086976 | -0.082397 | -0.022888 | 0.050354 | 3.8406 | 1.0162 | 3.9551 | 1.0986 | 4.0375 | 0.21515 | 0.082398 | 3.923 | 121.2433 | 0.009156 | 121.17 | 121.051 | 121.0876 | -0.068665 | -121.1929 | 121.1243 | 121.1609 | 121.0876 | 52.3087
2404.4844 | 121.3989 | -121.1288 | 0.073242 | -0.0016786 | 0.013505 | -0.036713 | 0.033063 | -0.021258 | -0.029676 | -0.02346 | 0.0055542 | -0.0046143 | 0.068676 | 0.051133 | -0.017513 | -0.006682 | -0.011615 | -0.022888 | -0.027466 | -0.004578 | 0 | 0.15564 | 0.068665 | 0.073242 | -68.5089 | 0.009155 | -121.17 | 0.073242 | -117.1371 | -116.9907 | -120.0485 | 121.1243 | -0.10071 | -0.073242 | 121.2845 | 121.2021 | 121.1975 | 0.07782 | 0.073243 | -0.041199 | -0.064087 | 0 | 3.9917 | 1.0803 | 4.1382 | 1.1215 | 4.1794 | 0.16022 | 0.004578 | 4.0329 | 121.2433 | -0.022888 | 121.1792 | 121.1014 | 121.138 | -0.07782 | -121.2433 | 121.1288 | 121.2021 | 121.106 | 52.6199
2406.2031 | 121.2662 | -121.1426 | 0.086975 | -0.0016786 | 0.01201 | -0.035218 | 0.039471 | -0.012285 | -0.027327 | -0.022819 | 0.0025024 | -0.0014099 | 0.069744 | 0.04921 | -0.015804 | -0.0081774 | -0.011828 | -0.086975 | 0.004578 | -0.036621 | -0.10071 | 0.004578 | -0.068665 | -0.059509 | -68.2983 | 0.041199 | -121.1975 | -0.041199 | -117.1829 | -117.0593 | -120.1492 | 121.106 | -0.082397 | -0.18768 | 121.1472 | 121.0831 | 121.0739 | -0.022888 | -0.032044 | -0.054932 | -0.045776 | -0.12817 | 3.9597 | 0.99335 | 4.0833 | 1.0483 | 4.1382 | 0.041199 | -0.064087 | 4.0146 | 121.1563 | 0.041199 | 121.2387 | 121.1472 | 121.1838 | -0.1236 | -121.2845 | 121.0419 | 121.1014 | 121.0556 | 52.8442
2407.9688 | 121.3623 | -121.1334 | 0.07782 | 0.028839 | 0.016282 | -0.036072 | 0.033917 | -0.014208 | -0.029036 | -0.020897 | 0.011658 | -0.0046143 | 0.069957 | 0.056901 | -0.017299 | -0.0060412 | -0.010547 | -0.045776 | -0.004578 | -0.004578 | -0.018311 | 0.14191 | 0.018311 | 0.041199 | -67.8772 | 0.018311 | -121.2067 | 0.036621 | -117.0044 | -116.8579 | -120.0943 | 121.1288 | -0.082398 | -0.096131 | 121.2753 | 121.1746 | 121.1517 | 0.045777 | 0.022889 | -0.073242 | -0.059509 | -0.041199 | 4.129 | 1.0391 | 4.2755 | 1.1124 | 4.3488 | 0.14649 | -0.013733 | 4.2023 | 121.2433 | 0 | 121.225 | 121.1288 | 121.1517 | -0.082398 | -121.2845 | 121.1151 | 121.17 | 121.0876 | 53.2562
2409.6875 | 121.344 | -121.1792 | 0.073242 | 0.02121 | 0.016496 | -0.033509 | 0.036267 | -0.01784 | -0.029249 | -0.021965 | 0.011658 | -0.0016235 | 0.069744 | 0.044297 | -0.019008 | -0.0062548 | -0.011828 | -0.013733 | 0.022888 | -0.022888 | -0.013733 | 0.13275 | 0.004578 | 0.027466 | -67.5201 | 0.022888 | -121.2158 | 0.027466 | -116.9312 | -116.7984 | -120.108 | 121.1563 | -0.050354 | -0.086975 | 121.3119 | 121.2067 | 121.1838 | 0.050354 | 0.027466 | -0.036621 | -0.050354 | -0.045776 | 4.248 | 1.0712 | 4.3808 | 1.1078 | 4.4174 | 0.15564 | 0.009155 | 4.2847 | 121.2433 | 0.045776 | 121.2387 | 121.2021 | 121.2021 | -0.09613 | -121.2891 | 121.1655 | 121.2067 | 121.1655 | 53.6591
2411.4844 | 121.4722 | -121.1563 | 0.064087 | 0.0059509 | 0.010728 | -0.035218 | 0.03349 | -0.016985 | -0.026472 | -0.023674 | 0.0025024 | -0.0033325 | 0.068035 | 0.04921 | -0.019649 | -0.005614 | -0.012256 | -0.018311 | -0.027466 | 0.004578 | 0.050354 | 0.23346 | 0.10529 | 0.10986 | -67.067 | 0.004578 | -121.1975 | 0.07782 | -116.7023 | -116.5466 | -120.0256 | 121.1609 | -0.091553 | -0.013733 | 121.3898 | 121.2662 | 121.2616 | 0.10529 | 0.10071 | -0.041199 | -0.059509 | 0.013733 | 4.454 | 1.1307 | 4.6097 | 1.1719 | 4.6509 | 0.22888 | 0.045776 | 4.4952 | 121.2753 | -0.032044 | 121.2021 | 121.1288 | 121.1609 | -0.059509 | -121.2616 | 121.2067 | 121.2341 | 121.138 | 54.0894
2413.2656 | 121.344 | -121.2112 | 0.082397 | -0.0016786 | 0.014787 | -0.034363 | 0.038189 | -0.017626 | -0.027113 | -0.022819 | 0.0025024 | -0.0001281 | 0.068676 | 0.046006 | -0.016658 | -0.0058276 | -0.0084104 | -0.082397 | 0.009155 | -0.041199 | -0.086975 | 0.022888 | -0.091553 | -0.059509 | -67.0074 | 0.041199 | -121.2524 | -0.022888 | -116.8533 | -116.6473 | -120.1492 | 121.17 | -0.073242 | -0.16937 | 121.2341 | 121.1517 | 121.1197 | -0.01831 | -0.050354 | -0.041198 | -0.041198 | -0.10528 | 4.3579 | 1.062 | 4.5639 | 1.1032 | 4.6051 | 0.064087 | -0.045776 | 4.3991 | 121.2296 | 0.050354 | 121.2936 | 121.2204 | 121.2524 | -0.1236 | -121.3348 | 121.1243 | 121.1884 | 121.1288 | 54.2038
2415.0469 | 121.3394 | -121.2341 | 0.10071 | 0.0059509 | 0.01436 | -0.033722 | 0.03349 | -0.022967 | -0.031599 | -0.024101 | 0.026916 | -0.0011963 | 0.072094 | 0.04451 | -0.021572 | -0.007323 | -0.010974 | -0.09613 | 0 | -0.050354 | -0.07782 | 0.050354 | -0.009155 | 0 | -66.6779 | 0.10071 | -121.2799 | -0.032043 | -116.7572 | -116.5009 | -120.163 | 121.1838 | -0.10071 | -0.17853 | 121.2845 | 121.2341 | 121.225 | 0.050354 | 0.041199 | -0.045776 | 0 | -0.13275 | 4.4769 | 1.0712 | 4.7333 | 1.1169 | 4.7791 | 0.10071 | -0.027466 | 4.5227 | 121.2479 | 0.050354 | 121.3806 | 121.2341 | 121.3348 | -0.15106 | -121.3806 | 121.1563 | 121.2021 | 121.138 | 54.5563
2416.75 | 121.4996 | -121.2021 | 0.059509 | 0.051727 | 0.015214 | -0.030732 | 0.038189 | -0.014422 | -0.026686 | -0.023887 | 0.011658 | -0.0026917 | 0.068676 | 0.051346 | -0.015804 | -0.0071094 | -0.011615 | 0.018311 | -0.032043 | -0.013733 | 0.068665 | 0.21515 | 0.073242 | 0.09613 | -66.4215 | 0.022888 | -121.2708 | 0.09613 | -116.5375 | -116.2994 | -120.0623 | 121.1884 | -0.091552 | 0.009156 | 121.4172 | 121.2982 | 121.2753 | 0.10986 | 0.086975 | -0.068665 | -0.036621 | 0.036621 | 4.6646 | 1.1398 | 4.9026 | 1.2085 | 4.9713 | 0.22888 | 0.082398 | 4.7333 | 121.3669 | -0.01831 | 121.2936 | 121.17 | 121.225 | -0.073242 | -121.3303 | 121.2708 | 121.2982 | 121.2204 | 54.7806
2418.5469 | 121.4355 | -121.2387 | 0.086975 | 0.02121 | 0.012864 | -0.035218 | 0.034558 | -0.017412 | -0.030531 | -0.021965 | 0.0055542 | -0.0046143 | 0.069316 | 0.045792 | -0.021144 | -0.0068958 | -0.013537 | -0.009155 | -0.018311 | -0.004578 | 0.018311 | 0.16022 | 0.091553 | 0.073242 | -66.4169 | 0.018311 | -121.2708 | 0.027466 | -116.5283 | -116.2491 | -120.1218 | 121.2341 | -0.10529 | -0.068664 | 121.3989 | 121.3119 | 121.3303 | 0.07782 | 0.096131 | -0.032044 | -0.068664 | -0.059509 | 4.7104 | 1.1169 | 4.9896 | 1.149 | 5.0217 | 0.16479 | 0.022889 | 4.7424 | 121.2982 | -0.013733 | 121.2891 | 121.2204 | 121.257 | -0.091553 | -121.3577 | 121.257 | 121.2662 | 121.2296 | 54.8218
2420.3281 | 121.5134 | -121.2296 | 0.07782 | 0.01358 | 0.014146 | -0.035859 | 0.031354 | -0.020189 | -0.029676 | -0.022605 | 0.0025024 | -0.0031189 | 0.072521 | 0.047288 | -0.017726 | -0.005614 | -0.014605 | 0 | -0.027466 | 0 | 0.041199 | 0.19226 | 0.091553 | 0.082397 | -66.2018 | -0.004578 | -121.2799 | 0.082397 | -116.4047 | -116.0889 | -120.0714 | 121.2296 | -0.10529 | -0.036621 | 121.4218 | 121.3119 | 121.3211 | 0.082397 | 0.091553 | -0.050354 | -0.082398 | 0.004577 | 4.8248 | 1.1581 | 5.1407 | 1.2085 | 5.191 | 0.19226 | 0.041199 | 4.8752 | 121.3623 | -0.027466 | 121.2753 | 121.2021 | 121.225 | -0.07782 | -121.3577 | 121.2708 | 121.3119 | 121.2296 | 55.0278
2422.0469 | 121.5179 | -121.2296 | 0.059509 | 0.02121 | 0.013292 | -0.032868 | 0.033917 | -0.017626 | -0.028608 | -0.019401 | 0.0055542 | -0.0007691 | 0.071025 | 0.048569 | -0.01559 | -0.0043322 | -0.0077694 | 0 | -0.036621 | 0.009155 | 0.041199 | 0.16022 | 0.045776 | 0.064087 | -66.1606 | 0.009155 | -121.2891 | 0.10986 | -116.3544 | -115.9882 | -120.0394 | 121.2387 | -0.09613 | -0.01831 | 121.3898 | 121.2936 | 121.2753 | 0.054932 | 0.036621 | -0.059509 | -0.050354 | 0.050354 | 4.8752 | 1.1902 | 5.2414 | 1.2497 | 5.3009 | 0.15106 | 0.032044 | 4.9347 | 121.3989 | -0.045776 | 121.2982 | 121.1929 | 121.2387 | -0.050354 | -121.3486 | 121.2708 | 121.3394 | 121.2296 | 55.069
2423.8281 | 121.4676 | -121.2708 | 0.10529 | 0.028839 | 0.015214 | -0.034791 | 0.037762 | -0.01848 | -0.032026 | -0.022605 | 0.008606 | -0.0007691 | 0.071025 | 0.04451 | -0.019008 | -0.007323 | -0.008624 | -0.004578 | 0.004578 | -0.045776 | -0.013733 | 0.10529 | 0.013733 | 0.018311 | -66.1469 | 0.045776 | -121.3257 | 0.032043 | -116.3773 | -115.9561 | -120.1126 | 121.225 | -0.10071 | -0.11902 | 121.376 | 121.2891 | 121.2845 | 0.064087 | 0.059509 | -0.054932 | -0.05951 | -0.073243 | 4.8935 | 1.1581 | 5.3146 | 1.2131 | 5.3696 | 0.15106 | 0.032043 | 4.9484 | 121.3577 | 0.050354 | 121.3715 | 121.2753 | 121.3165 | -0.15106 | -121.431 | 121.257 | 121.3028 | 121.2662 | 55.1239
2425.5625 | 121.4355 | -121.2982 | 0.10071 | 0.01358 | 0.013078 | -0.036927 | 0.035626 | -0.021044 | -0.028608 | -0.022819 | -0.00054937 | 8.55e-05 | 0.073589 | 0.040665 | -0.022426 | -0.0064684 | -0.012896 | -0.086975 | -0.004578 | -0.036621 | -0.086975 | 0.050354 | -0.032043 | -0.018311 | -66.1652 | 0.050354 | -121.3394 | -0.041199 | -116.3818 | -115.9378 | -120.163 | 121.2616 | -0.10529 | -0.18768 | 121.3486 | 121.2799 | 121.2662 | 0.01831 | 0.004578 | -0.041199 | -0.050354 | -0.14191 | 4.9164 | 1.1353 | 5.3604 | 1.1765 | 5.4016 | 0.086975 | -0.050354 | 4.9576 | 121.2982 | 0.032043 | 121.3898 | 121.2936 | 121.3486 | -0.13733 | -121.4401 | 121.2112 | 121.257 | 121.2112 | 55.1331
2427.3438 | 121.4127 | -121.3028 | 0.091553 | -0.0016786 | 0.015855 | -0.034363 | 0.037762 | -0.018053 | -0.025831 | -0.022392 | 0.0055542 | -0.0003417 | 0.071666 | 0.046006 | -0.016231 | -0.0054004 | -0.0094784 | -0.073242 | 0 | -0.054932 | -0.10529 | 0.004578 | -0.086975 | -0.068665 | -66.1743 | 0.054932 | -121.3623 | -0.018311 | -116.3315 | -115.86 | -120.1309 | 121.2479 | -0.091553 | -0.19684 | 121.3074 | 121.2341 | 121.2158 | -0.013733 | -0.032043 | -0.05951 | -0.036621 | -0.10986 | 4.9713 | 1.1719 | 5.4428 | 1.2314 | 5.5023 | 0.05951 | -0.050354 | 5.0308 | 121.344 | 0.054932 | 121.4172 | 121.3028 | 121.3577 | -0.14649 | -121.4539 | 121.1975 | 121.2845 | 121.2296 | 55.1285
2429.1406 | 121.5179 | -121.2982 | 0.10071 | 0.02121 | 0.016282 | -0.033295 | 0.035199 | -0.020617 | -0.027967 | -0.020042 | 0.008606 | 0.0005127 | 0.069957 | 0.049637 | -0.02029 | -0.007323 | -0.014392 | -0.041199 | 0.013733 | -0.050354 | -0.009155 | 0.11902 | 0.018311 | 0.018311 | -66.0873 | 0.041199 | -121.3623 | 0.045776 | -116.1896 | -115.6998 | -120.108 | 121.2479 | -0.086975 | -0.10986 | 121.4172 | 121.3165 | 121.3165 | 0.068665 | 0.068665 | -0.064087 | -0.059509 | -0.054932 | 5.1086 | 1.1902 | 5.5984 | 1.2543 | 5.6625 | 0.16937 | 0.041199 | 5.1727 | 121.4081 | 0.064087 | 121.4035 | 121.312 | 121.3394 | -0.15106 | -121.463 | 121.2891 | 121.344 | 121.257 | 55.2109
2430.9531 | 121.5042 | -121.3348 | 0.086975 | 0.0059509 | 0.015428 | -0.035645 | 0.036908 | -0.017412 | -0.028822 | -0.023033 | 0.0055542 | -0.0016235 | 0.071025 | 0.042801 | -0.016017 | -0.0058276 | -0.011187 | -0.082397 | 0.013733 | -0.036621 | -0.091553 | 0.036621 | -0.059509 | -0.032043 | -66.3025 | 0.022888 | -121.3486 | 0.018311 | -116.1804 | -115.654 | -120.1263 | 121.2982 | -0.073242 | -0.17853 | 121.3715 | 121.3028 | 121.2753 | 0.004578 | -0.022888 | -0.013733 | -0.064087 | -0.068664 | 5.1544 | 1.2085 | 5.6808 | 1.2222 | 5.6946 | 0.073242 | -0.054932 | 5.1682 | 121.3669 | 0.050354 | 121.3715 | 121.3486 | 121.3577 | -0.1236 | -121.4355 | 121.2433 | 121.3531 | 121.2524 | 55.0323
2432.6719 | 121.5042 | -121.3531 | 0.09613 | 0.028839 | 0.015001 | -0.035645 | 0.037762 | -0.019549 | -0.02754 | -0.022605 | 0.014709 | -0.0009827 | 0.071666 | 0.049637 | -0.017513 | -0.0064684 | -0.012042 | -0.064087 | 0.050354 | -0.059509 | -0.091553 | 0.041199 | -0.009155 | 0 | -66.4444 | 0.050354 | -121.4035 | -0.018311 | -116.1163 | -115.5579 | -120.1355 | 121.2936 | -0.045776 | -0.18768 | 121.3943 | 121.3531 | 121.344 | 0.059509 | 0.050354 | -0.050354 | -0.045776 | -0.11444 | 5.2368 | 1.2177 | 5.7953 | 1.268 | 5.8456 | 0.10071 | -0.032044 | 5.2872 | 121.3852 | 0.10986 | 121.4539 | 121.4035 | 121.4035 | -0.15564 | -121.4996 | 121.2616 | 121.3348 | 121.2891 | 54.9088
2434.4688 | 121.55 | -121.3348 | 0.09613 | 0.0059509 | 0.013505 | -0.035218 | 0.034131 | -0.021258 | -0.028608 | -0.025169 | 0.0055542 | -0.0026917 | 0.071025 | 0.051133 | -0.019649 | -0.0060412 | -0.011187 | -0.009155 | -0.027466 | -0.009155 | 0.022888 | 0.16937 | 0.073242 | 0.082397 | -66.4948 | 0.004578 | -121.376 | 0.032043 | -116.0019 | -115.3976 | -120.0943 | 121.3257 | -0.1236 | -0.073242 | 121.5042 | 121.4172 | 121.4081 | 0.091552 | 0.082397 | -0.041199 | -0.091552 | -0.064087 | 5.3329 | 1.2405 | 5.9372 | 1.2817 | 5.9784 | 0.17853 | 0.032043 | 5.3741 | 121.4081 | -0.018311 | 121.3806 | 121.3074 | 121.3394 | -0.10528 | -121.4722 | 121.3577 | 121.3669 | 121.3257 | 54.8401
2436.2656 | 121.5683 | -121.3394 | 0.082397 | 0.028839 | 0.013933 | -0.033509 | 0.035199 | -0.01784 | -0.029036 | -0.021324 | 0.0055542 | -0.0026917 | 0.070385 | 0.054551 | -0.016017 | -0.0043322 | -0.0094784 | -0.050354 | -0.013733 | -0.022888 | -0.013733 | 0.13275 | 0.022888 | 0.032043 | -66.7374 | 0.004578 | -121.3852 | 0.036621 | -115.947 | -115.3427 | -120.0943 | 121.3165 | -0.09613 | -0.09613 | 121.4722 | 121.3715 | 121.3623 | 0.054931 | 0.045776 | -0.045776 | -0.077819 | -0.045776 | 5.3925 | 1.2451 | 5.9967 | 1.2909 | 6.0425 | 0.15564 | 0.009155 | 5.4382 | 121.4218 | 0.009155 | 121.3898 | 121.3257 | 121.344 | -0.10528 | -121.4676 | 121.3257 | 121.376 | 121.2891 | 54.6021
2438.0625 | 121.6095 | -121.3211 | 0.059509 | -0.0016786 | 0.013933 | -0.035004 | 0.03648 | -0.011644 | -0.029036 | -0.024314 | 0.0055542 | -0.0011963 | 0.072734 | 0.044938 | -0.016231 | -0.0034778 | -0.0081968 | -0.059509 | 0.004578 | -0.027466 | -0.009155 | 0.11444 | 0.018311 | 0.027466 | -66.8472 | 0.004578 | -121.3577 | 0.086975 | -115.8417 | -115.2008 | -120.0302 | 121.2936 | -0.054931 | -0.068664 | 121.4355 | 121.3486 | 121.3394 | 0.054932 | 0.045777 | -0.036621 | -0.054931 | 0.027466 | 5.4794 | 1.2909 | 6.1203 | 1.3275 | 6.1569 | 0.14191 | 0.018311 | 5.5161 | 121.4447 | 0.032044 | 121.3623 | 121.3257 | 121.3257 | -0.086975 | -121.4172 | 121.312 | 121.4081 | 121.2616 | 54.4739
2439.8594 | 121.6324 | -121.3577 | 0.073242 | 0.0059509 | 0.010728 | -0.035859 | 0.035199 | -0.018053 | -0.027967 | -0.022819 | 0.0055542 | -0.0020507 | 0.069744 | 0.050706 | -0.018367 | -0.0041186 | -0.011401 | -0.004578 | -0.027466 | 0.004578 | 0.064087 | 0.21057 | 0.10986 | 0.10071 | -66.9708 | 0.018311 | -121.3806 | 0.091553 | -115.7364 | -115.0635 | -120.0439 | 121.3623 | -0.10071 | -0.009155 | 121.5683 | 121.4584 | 121.4676 | 0.09613 | 0.10529 | -0.022888 | -0.054931 | 0.018311 | 5.6213 | 1.3138 | 6.2942 | 1.3367 | 6.3171 | 0.20599 | 0.059509 | 5.6442 | 121.4722 | -0.032044 | 121.3989 | 121.3303 | 121.376 | -0.068664 | -121.4539 | 121.4218 | 121.4493 | 121.3531 | 54.3869
2441.5781 | 121.5775 | -121.3943 | 0.10071 | 0.036468 | 0.016282 | -0.034791 | 0.036053 | -0.012926 | -0.027327 | -0.024101 | 0.008606 | 0.0013673 | 0.071666 | 0.043015 | -0.01794 | -0.0043322 | -0.009692 | -0.018311 | 0.022888 | -0.064087 | -0.032043 | 0.10071 | 0.009155 | 0.009155 | -67.1539 | 0.036621 | -121.4035 | 0.022888 | -115.7639 | -115.0818 | -120.1035 | 121.3303 | -0.07782 | -0.13275 | 121.4951 | 121.4035 | 121.4035 | 0.073242 | 0.073242 | -0.009155 | -0.064087 | -0.07782 | 5.6305 | 1.2909 | 6.3126 | 1.3 | 6.3217 | 0.1648 | 0.032044 | 5.6396 | 121.4264 | 0.086975 | 121.4401 | 121.4172 | 121.431 | -0.1648 | -121.5042 | 121.3623 | 121.4172 | 121.376 | 54.2404
2443.3594 | 121.5637 | -121.3943 | 0.091553 | 0.02121 | 0.016069 | -0.032441 | 0.037121 | -0.015276 | -0.028822 | -0.020469 | 0.011658 | 0.0013673 | 0.072948 | 0.04921 | -0.016658 | -0.0043322 | -0.010119 | -0.027466 | 0.013733 | -0.036621 | -0.018311 | 0.11444 | 0.004578 | 0.013733 | -67.3553 | 0.032043 | -121.4172 | 0.032043 | -115.7318 | -115.0269 | -120.0989 | 121.3577 | -0.07782 | -0.10986 | 121.5088 | 121.4081 | 121.3989 | 0.050354 | 0.041199 | -0.022888 | -0.05951 | -0.05951 | 5.6625 | 1.2955 | 6.3675 | 1.3184 | 6.3904 | 0.15106 | 0.01831 | 5.6854 | 121.4493 | 0.050354 | 121.4493 | 121.4081 | 121.4264 | -0.12817 | -121.5088 | 121.376 | 121.4264 | 121.3669 | 54.039
2445.0938 | 121.5683 | -121.4172 | 0.091553 | 0.01358 | 0.013933 | -0.032227 | 0.036267 | -0.016558 | -0.02989 | -0.021537 | 0.0025024 | 0.0011535 | 0.072094 | 0.04686 | -0.016017 | -0.0019824 | -0.010119 | -0.082397 | 0 | -0.041199 | -0.10071 | 0.050354 | -0.073242 | -0.041199 | -67.4973 | 0.045776 | -121.4722 | -0.004578 | -115.6906 | -114.9719 | -120.1126 | 121.376 | -0.091553 | -0.19226 | 121.4676 | 121.376 | 121.344 | 0 | -0.032043 | -0.054932 | -0.045777 | -0.096131 | 5.7266 | 1.3046 | 6.4453 | 1.3596 | 6.5002 | 0.091553 | -0.059509 | 5.7816 | 121.4676 | 0.041199 | 121.5179 | 121.4172 | 121.463 | -0.13275 | -121.5637 | 121.3165 | 121.4127 | 121.3348 | 53.92
2446.8906 | 121.6187 | -121.4035 | 0.073242 | 0.01358 | 0.015214 | -0.036072 | 0.035626 | -0.01784 | -0.027967 | -0.022819 | 0.008606 | 0.0017945 | 0.072948 | 0.045792 | -0.020076 | -0.0034778 | -0.014178 | -0.027466 | 0.009155 | -0.027466 | -0.022888 | 0.12817 | 0.013733 | 0.018311 | -67.6941 | 0.027466 | -121.4676 | 0.036621 | -115.5762 | -114.8163 | -120.0851 | 121.376 | -0.064087 | -0.09613 | 121.5317 | 121.4218 | 121.4172 | 0.045777 | 0.041199 | -0.064087 | -0.045776 | -0.036621 | 5.8273 | 1.3184 | 6.5872 | 1.3824 | 6.6513 | 0.15564 | 0.004578 | 5.8914 | 121.5042 | 0.036621 | 121.4951 | 121.4127 | 121.431 | -0.10071 | -121.5408 | 121.3806 | 121.4401 | 121.376 | 53.7094
2448.6875 | 121.7148 | -121.4127 | 0.091553 | 0.0059509 | 0.013933 | -0.033509 | 0.033917 | -0.016558 | -0.028822 | -0.020897 | 0.0025024 | -0.0016235 | 0.070598 | 0.053269 | -0.019222 | -0.0058276 | -0.010547 | -0.013733 | -0.045776 | -0.004578 | 0.027466 | 0.18768 | 0.082397 | 0.086975 | -67.9321 | 0.013733 | -121.4264 | 0.032043 | -115.4663 | -114.679 | -120.0577 | 121.4081 | -0.13733 | -0.064087 | 121.6003 | 121.4996 | 121.4951 | 0.091553 | 0.086975 | -0.013733 | -0.07782 | -0.05951 | 5.9464 | 1.355 | 6.7337 | 1.3687 | 6.7474 | 0.19226 | 0.032044 | 5.9601 | 121.4584 | -0.041198 | 121.4401 | 121.3669 | 121.4264 | -0.096131 | -121.5179 | 121.4401 | 121.4447 | 121.3989 | 53.4805
2450.5 | 121.701 | -121.3898 | 0.054932 | 0.0059509 | 0.014146 | -0.032868 | 0.034772 | -0.020189 | -0.029036 | -0.020897 | 0.020813 | 0.0013673 | 0.072307 | 0.050706 | -0.016658 | -0.005614 | -0.0077694 | 0.032043 | -0.004578 | -0.004578 | 0.045776 | 0.20599 | 0.086975 | 0.09613 | -68.1335 | 0.018311 | -121.4447 | 0.10986 | -115.4022 | -114.5599 | -120.0073 | 121.3852 | -0.05951 | -0.009156 | 121.5958 | 121.4859 | 121.4767 | 0.10071 | 0.091553 | -0.054931 | -0.036621 | 0.054931 | 5.9875 | 1.3824 | 6.8298 | 1.4374 | 6.8848 | 0.21057 | 0.050354 | 6.0425 | 121.5546 | 0 | 121.463 | 121.3852 | 121.4081 | -0.05951 | -121.4996 | 121.4355 | 121.4996 | 121.4218 | 53.2562
2452.2969 | 121.5363 | -121.4676 | 0.086975 | 0.01358 | 0.015428 | -0.031373 | 0.036053 | -0.018908 | -0.027967 | -0.022605 | 0.0025024 | 0.0009399 | 0.071239 | 0.050065 | -0.017726 | -0.0017688 | -0.011401 | -0.086975 | 0.027466 | -0.027466 | -0.10071 | 0.004578 | -0.091553 | -0.068665 | -68.6691 | 0.050354 | -121.4996 | -0.027466 | -115.5075 | -114.6332 | -120.0989 | 121.4401 | -0.059509 | -0.18768 | 121.4722 | 121.3989 | 121.376 | -0.041199 | -0.064087 | -0.032044 | -0.036621 | -0.11444 | 5.9601 | 1.3687 | 6.8344 | 1.4008 | 6.8665 | 0.032044 | -0.073242 | 5.9921 | 121.4722 | 0.054932 | 121.55 | 121.4951 | 121.5179 | -0.11444 | -121.5866 | 121.3669 | 121.4401 | 121.3806 | 52.7985
2454.0938 | 121.6049 | -121.4447 | 0.086975 | -0.0016786 | 0.015001 | -0.036713 | 0.033917 | -0.021898 | -0.030317 | -0.021965 | 0.0055542 | 0.0002991 | 0.072734 | 0.048142 | -0.019649 | -0.003905 | -0.010547 | -0.022888 | -0.032043 | -0.013733 | 0 | 0.14648 | 0.059509 | 0.054932 | -68.7469 | 0.032043 | -121.4722 | 0.009155 | -115.3473 | -114.4592 | -120.0668 | 121.431 | -0.11902 | -0.086975 | 121.5912 | 121.4996 | 121.5042 | 0.068665 | 0.073242 | -0.027466 | -0.054932 | -0.07782 | 6.0974 | 1.3779 | 6.9855 | 1.4053 | 7.0129 | 0.16022 | 0.013733 | 6.1249 | 121.4813 | -0.01831 | 121.5042 | 121.4127 | 121.4767 | -0.10071 | -121.5591 | 121.4447 | 121.4539 | 121.4218 | 52.6978
2455.8125 | 114.9078 | -105.0705 | 9.9014 | 0.036468 | 0.012437 | -0.034791 | 0.037549 | -0.015062 | -0.029463 | -0.022178 | 0.008606 | 0.0024353 | 0.070812 | 0.045151 | -0.018581 | -0.0047594 | -0.0090512 | -0.045776 | 0.041199 | -0.050354 | -0.013733 | 0.082397 | 0.009155 | 0.018311 | -57.55 | 9.6085 | -105.5283 | 9.8282 | -99.5041 | -98.7122 | -103.83 | 105.0201 | -9.8602 | -9.9152 | 105.1529 | 105.0888 | 105.0797 | 0.068665 | 0.059509 | -0.45776 | -0.29297 | -0.073242 | 5.5664 | 1.2405 | 6.3583 | 1.6983 | 6.8161 | 0.13275 | 0.036621 | 6.0242 | 115.3564 | 0.091553 | 115.1367 | 105.1117 | 114.679 | -9.9518 | -115.4297 | 105.0568 | 114.8987 | 105.0247 | 47.5204
2457.5938 | 121.2662 | -120.9595 | 0.059509 | 0.01358 | 0.013505 | -0.032227 | 0.034985 | -0.017199 | -0.027754 | -0.021751 | 0.020813 | 0.0009399 | 0.073375 | 0.051774 | -0.016658 | -0.0028368 | -0.014178 | 0 | -0.022888 | 0 | 0.059509 | 0.20142 | 0.07782 | 0.10071 | -68.7469 | 0.018311 | -121.019 | 0.09613 | -114.7156 | -113.7909 | -119.5267 | 120.9595 | -0.082397 | 0 | 121.1609 | 121.0602 | 121.0373 | 0.10071 | 0.07782 | -0.059509 | -0.041198 | 0.036621 | 6.2439 | 1.4328 | 7.1686 | 1.4923 | 7.2281 | 0.20142 | 0.059509 | 6.3034 | 121.1151 | -0.022888 | 121.0373 | 120.9366 | 120.9778 | -0.059509 | -121.0785 | 121.019 | 121.0556 | 120.9595 | 52.2125
2459.3125 | 121.257 | -121.0876 | 0.09613 | 0.01358 | 0.014146 | -0.033082 | 0.037549 | -0.014635 | -0.027967 | -0.02346 | 0.0055542 | 0.0011535 | 0.07188 | 0.045792 | -0.017513 | -0.0032642 | -0.0056332 | -0.050354 | 0.004578 | -0.045776 | -0.064087 | 0.086975 | -0.027466 | -0.022888 | -69.0628 | 0.036621 | -121.1746 | 0 | -114.8575 | -113.887 | -119.7281 | 121.0419 | -0.091552 | -0.16022 | 121.1746 | 121.0648 | 121.0602 | 0.022888 | 0.01831 | -0.086976 | -0.059509 | -0.09613 | 6.2302 | 1.3596 | 7.2006 | 1.4465 | 7.2876 | 0.13275 | -0.018311 | 6.3171 | 121.1746 | 0.050354 | 121.2112 | 121.0922 | 121.1243 | -0.14191 | -121.2708 | 121.0236 | 121.0876 | 121.0373 | 52.0248
2461.1094 | 115.7547 | -109.1583 | 6.3904 | 0.028839 | 0.014146 | -0.033936 | 0.038189 | -0.017199 | -0.027754 | -0.020897 | 0.014709 | 0.0020081 | 0.06953 | 0.045151 | -0.018581 | -0.0041186 | -0.011828 | -0.018311 | 0.054932 | -0.032043 | -0.013733 | 0.10986 | 0 | -0.018311 | -60.3149 | 7.3059 | -109.1034 | 7.2189 | -102.3514 | -102.1362 | -107.9315 | 109.1263 | -6.3354 | -6.4041 | 109.2682 | 109.14 | 109.1583 | 0.013732 | 0.032043 | 0.054931 | 0.91553 | 0.82855 | 6.8069 | 1.2268 | 7.0221 | 1.1719 | 6.9672 | 0.14191 | 0.01831 | 6.752 | 116.3223 | 0.086975 | 116.4093 | 109.2133 | 116.4642 | -6.4224 | -115.4938 | 109.1446 | 116.3773 | 109.14 | 48.8434
2462.8281 | 121.0098 | -120.8679 | 0.10071 | -0.0093076 | 0.014146 | -0.034577 | 0.037549 | -0.016771 | -0.031172 | -0.023887 | 0.0055542 | 0.0030763 | 0.074871 | 0.055405 | -0.019222 | -0.0049732 | -0.0075558 | -0.07782 | 0.004578 | -0.032043 | -0.09613 | 0.036621 | -0.054932 | -0.041199 | -69.2871 | 0.050354 | -120.8862 | 0.013733 | -114.4272 | -113.4201 | -119.426 | 120.8359 | -0.09613 | -0.19684 | 120.9045 | 120.8267 | 120.813 | -0.009156 | -0.022889 | -0.01831 | -0.050354 | -0.086975 | 6.4407 | 1.442 | 7.4478 | 1.4603 | 7.4661 | 0.068664 | -0.064087 | 6.459 | 120.9 | 0.036621 | 120.9366 | 120.8725 | 120.9183 | -0.13275 | -120.9869 | 120.7718 | 120.8817 | 120.7901 | 51.5808
2464.625 | 121.1426 | -120.9915 | 0.091553 | 0.036468 | 0.01671 | -0.033722 | 0.03648 | -0.016771 | -0.027967 | -0.025169 | 0.008606 | 0.0022217 | 0.072521 | 0.05156 | -0.019435 | -0.0034778 | -0.0090512 | -0.018311 | 0 | -0.041199 | -0.032043 | 0.1236 | 0.018311 | 0.018311 | -69.4244 | 0.032043 | -121.019 | 0.018311 | -114.4455 | -113.3881 | -119.5084 | 120.9503 | -0.091553 | -0.1236 | 121.1151 | 121.0098 | 121.0098 | 0.05951 | 0.05951 | -0.027466 | -0.05951 | -0.073242 | 6.546 | 1.4832 | 7.6035 | 1.5106 | 7.6309 | 0.16479 | 0.009156 | 6.5735 | 121.0373 | 0.041199 | 121.051 | 120.9915 | 121.0236 | -0.13275 | -121.1105 | 120.9595 | 121.0098 | 120.9732 | 51.5671
2466.4219 | 121.1517 | -121.0556 | 0.11902 | 0.0059509 | 0.014787 | -0.033509 | 0.03349 | -0.018053 | -0.029463 | -0.021537 | -0.00054937 | 0.0035035 | 0.070385 | 0.04686 | -0.022212 | -0.0054004 | -0.0088376 | -0.09613 | 0.013733 | -0.045776 | -0.10986 | 0.059509 | -0.013733 | -0.027466 | -69.7586 | 0.059509 | -121.106 | -0.054932 | -114.473 | -113.3743 | -119.5953 | 121.0098 | -0.10529 | -0.22888 | 121.1151 | 121.0281 | 121.0419 | 0.01831 | 0.032043 | -0.050354 | -0.05951 | -0.17395 | 6.5826 | 1.4603 | 7.6813 | 1.5106 | 7.7316 | 0.10528 | -0.064087 | 6.633 | 121.051 | 0.059509 | 121.1655 | 121.0693 | 121.1151 | -0.16479 | -121.225 | 120.9457 | 121.0007 | 120.9595 | 51.297
2468.1562 | 121.3257 | -121.019 | 0.082397 | -0.0016786 | 0.013719 | -0.0365 | 0.033063 | -0.015062 | -0.029676 | -0.022392 | 0.0025024 | 0.0015809 | 0.07188 | 0.048569 | -0.018367 | -0.0041186 | -0.0094784 | -0.013733 | -0.022888 | 0.018311 | 0.032043 | 0.19226 | 0.10529 | 0.09613 | -69.8273 | -0.009155 | -121.0968 | 0.086975 | -114.3036 | -113.1363 | -119.5084 | 121.0373 | -0.10528 | -0.050354 | 121.2112 | 121.1151 | 121.1243 | 0.077819 | 0.086975 | -0.07782 | -0.091552 | 0.004578 | 6.7154 | 1.5106 | 7.8827 | 1.5884 | 7.9605 | 0.17395 | 0.013732 | 6.7932 | 121.1838 | -0.041199 | 121.0876 | 120.9961 | 121.0098 | -0.064086 | -121.1792 | 121.051 | 121.106 | 121.0052 | 51.1917
2469.9531 | 121.3028 | -121.0556 | 0.07782 | 0.028839 | 0.016282 | -0.033936 | 0.034344 | -0.013781 | -0.027327 | -0.022392 | 0.011658 | 0.0017945 | 0.075084 | 0.053696 | -0.017085 | -0.0026232 | -0.010333 | 0.018311 | -0.018311 | 0 | 0.041199 | 0.1831 | 0.050354 | 0.068665 | -70.0195 | 0.059509 | -121.1014 | 0.082397 | -114.2944 | -113.0722 | -119.5175 | 121.0556 | -0.096131 | -0.036621 | 121.2387 | 121.1243 | 121.106 | 0.068665 | 0.050354 | -0.045776 | -0.018311 | 0.004577 | 6.7612 | 1.5381 | 7.9834 | 1.5839 | 8.0292 | 0.1831 | 0.041199 | 6.8069 | 121.1838 | -0.018311 | 121.1609 | 121.0373 | 121.1151 | -0.07782 | -121.1792 | 121.0968 | 121.138 | 121.0739 | 51.0361
2471.75 | 120.9824 | -120.6024 | 0.10071 | 0.01358 | 0.014787 | -0.033722 | 0.035199 | -0.01784 | -0.028181 | -0.022178 | 0.0055542 | 0.0026489 | 0.07188 | 0.058396 | -0.016017 | -0.00091421 | -0.006915 | -0.059509 | 0.004578 | -0.032043 | -0.027466 | 0.10986 | -0.004578 | 0.018311 | -70.1065 | 0.032043 | -120.6757 | 0.11444 | -113.8275 | -112.587 | -119.0735 | 120.5704 | -0.09613 | -0.12817 | 120.7123 | 120.6207 | 120.5978 | 0.050354 | 0.027465 | -0.073242 | -0.068665 | 0.013733 | 6.7749 | 1.5289 | 8.0154 | 1.6022 | 8.0887 | 0.14191 | 0.004577 | 6.8481 | 120.7901 | 0.036621 | 120.7077 | 120.607 | 120.6345 | -0.13275 | -120.7764 | 120.575 | 120.7169 | 120.5429 | 50.4959
2473.5469 | 121.2204 | -120.8862 | 0.082397 | -0.0016786 | 0.010942 | -0.03415 | 0.034344 | -0.018694 | -0.028822 | -0.024742 | 0.008606 | -0.0005553 | 0.074016 | 0.037888 | -0.018794 | -0.0032642 | -0.008624 | -0.022888 | -0.032043 | -0.013733 | 0.027466 | 0.17395 | 0.064087 | 0.09613 | -70.4544 | -0.004578 | -120.9366 | 0.082397 | -113.9603 | -112.6785 | -119.3207 | 120.8725 | -0.11444 | -0.054931 | 121.0602 | 120.9824 | 120.9503 | 0.10986 | 0.07782 | -0.050354 | -0.086975 | 0 | 6.926 | 1.5656 | 8.2077 | 1.6159 | 8.2581 | 0.18768 | 0.041199 | 6.9763 | 121.019 | -0.01831 | 120.932 | 120.8542 | 120.8817 | -0.09613 | -121.019 | 120.9137 | 120.9686 | 120.8633 | 50.4318
2475.3281 | 121.0648 | -120.8679 | 0.19684 | 0.028839 | 0.016496 | -0.031373 | 0.034558 | -0.012499 | -0.028181 | -0.020256 | 0.0055542 | 0.0043579 | 0.073803 | 0.04686 | -0.018367 | -0.0032642 | -0.0099056 | -0.018311 | -0.013733 | -0.032043 | -0.004578 | 0.10071 | 0.009155 | 0.009155 | -70.7108 | 0.13275 | -120.8908 | 0.091553 | -113.9923 | -112.619 | -119.2657 | 120.8359 | -0.21057 | -0.20142 | 120.9686 | 120.8771 | 120.8771 | 0.041198 | 0.041198 | -0.022888 | -0.064087 | -0.10529 | 6.8756 | 1.6022 | 8.2489 | 1.6251 | 8.2718 | 0.13275 | 0.027465 | 6.8985 | 120.9824 | 0.01831 | 121.0236 | 120.8542 | 121.0007 | -0.22888 | -121.0876 | 120.8633 | 120.9595 | 120.8496 | 50.1572
2477.0469 | 121.1014 | -120.0668 | 0.78278 | 0.0059509 | 0.014146 | -0.034363 | 0.034344 | -0.017626 | -0.029249 | -0.019828 | 0.0055542 | 0.0005127 | 0.071025 | 0.051987 | -0.021144 | -0.002196 | -0.007983 | 0 | -0.032043 | 0 | 0.059509 | 0.20599 | 0.10071 | 0.091553 | -70.4407 | 0.53101 | -120.3506 | 1.1398 | -112.4817 | -111.6714 | -118.6523 | 120.0668 | -0.81482 | -0.72327 | 120.2728 | 120.1584 | 120.1675 | 0.091553 | 0.10071 | -0.28381 | -0.25177 | 0.35706 | 7.5851 | 1.4145 | 8.3954 | 1.6983 | 8.6792 | 0.20599 | 0.059509 | 7.869 | 121.4905 | -0.032043 | 120.8817 | 120.0348 | 120.5978 | -0.78278 | -121.1334 | 120.1263 | 121.2067 | 120.0668 | 49.6262
2478.8281 | 121.3257 | -121.0144 | 0.068665 | 0.01358 | 0.013292 | -0.033936 | 0.033703 | -0.019121 | -0.029463 | -0.021537 | 0.0025024 | 8.55e-05 | 0.073803 | 0.051987 | -0.021785 | -0.003905 | -0.0081968 | -0.004578 | -0.045776 | -0.004578 | 0.045776 | 0.2243 | 0.10071 | 0.10071 | -71.1273 | -0.009155 | -121.0419 | 0.07782 | -113.8138 | -112.381 | -119.3619 | 121.0098 | -0.11444 | -0.022889 | 121.2387 | 121.1151 | 121.1151 | 0.10529 | 0.10529 | -0.027466 | -0.07782 | 0.009155 | 7.2006 | 1.6525 | 8.6334 | 1.68 | 8.6609 | 0.22888 | 0.050354 | 7.2281 | 121.1197 | -0.041198 | 121.0327 | 120.9686 | 121.0052 | -0.073243 | -121.1105 | 121.0602 | 121.0922 | 121.0098 | 49.8871
2480.625 | 120.8954 | -119.6503 | 1.2726 | 0.0059509 | 0.015001 | -0.035859 | 0.035412 | -0.021044 | -0.030531 | -0.022178 | 0.0055542 | 0.0013673 | 0.072307 | 0.045365 | -0.020503 | -0.0054004 | -0.0081968 | -0.082397 | 0.009155 | -0.027466 | -0.082397 | 0.045776 | -0.018311 | -0.018311 | -70.2805 | 1.2177 | -119.632 | 1.1444 | -112.4634 | -110.9756 | -118.0161 | 119.6228 | -1.2634 | -1.355 | 119.696 | 119.632 | 119.632 | 0.009155 | 0.009155 | 0.018311 | -0.054932 | -0.12817 | 7.1869 | 1.6342 | 8.6746 | 1.6159 | 8.6563 | 0.073242 | -0.054931 | 7.1686 | 120.7764 | 0.036621 | 120.8496 | 119.6594 | 120.8679 | -1.3 | -120.9045 | 119.5679 | 120.7947 | 119.5679 | 49.3698
2482.3438 | 121.2479 | -120.9595 | 0.15564 | 0.028839 | 0.016069 | -0.033295 | 0.035626 | -0.019121 | -0.027754 | -0.018974 | 0.011658 | 0.0026489 | 0.073162 | 0.05391 | -0.018154 | -0.0032642 | -0.0073422 | -0.050354 | -0.013733 | -0.018311 | -0.004578 | 0.14648 | 0.050354 | 0.041199 | -71.4523 | 0.07782 | -121.0236 | 0.09613 | -113.6902 | -112.1109 | -119.2978 | 120.9412 | -0.16937 | -0.16022 | 121.106 | 121.0007 | 121.0098 | 0.05951 | 0.068665 | -0.064087 | -0.07782 | -0.05951 | 7.2693 | 1.6617 | 8.8486 | 1.7258 | 8.9127 | 0.16479 | 0.013733 | 7.3334 | 121.1197 | 0.004578 | 121.1014 | 120.9457 | 121.0373 | -0.17395 | -121.1792 | 120.9549 | 121.0556 | 120.9091 | 49.5071
2484.125 | 116.6702 | -116.4001 | 0.22888 | 0.01358 | 0.016282 | -0.032013 | 0.03648 | -0.018053 | -0.027754 | -0.02346 | 0.0055542 | 0.0043579 | 0.070812 | 0.044938 | -0.019649 | -0.0017688 | -0.0073422 | 0.09613 | 0 | -0.009155 | -0.041199 | 0.10529 | 0.027466 | 0.022888 | -68.8889 | 0.018311 | -116.4139 | 0.1831 | -109.4193 | -107.84 | -114.798 | 116.391 | -0.22888 | -0.27008 | 116.5054 | 116.423 | 116.4276 | 0.032043 | 0.036621 | -0.013733 | -0.21057 | -0.045777 | 6.9809 | 1.6022 | 8.5602 | 1.6159 | 8.5739 | 0.11444 | -0.032044 | 6.9946 | 116.597 | 0.009155 | 116.4322 | 116.4001 | 116.4185 | -0.23804 | -116.6428 | 116.3589 | 116.5833 | 116.4963 | 47.5113
2485.8594 | 120.3323 | -118.7073 | 1.7303 | -0.0016786 | 0.012224 | -0.0318 | 0.036908 | -0.015917 | -0.02989 | -0.024528 | 0.0025024 | 0.0028625 | 0.070598 | 0.04921 | -0.018154 | 0.00058099 | -0.0073422 | -0.045776 | 0.018311 | -0.032043 | -0.059509 | 0.045776 | -0.059509 | -0.045776 | -70.3125 | 1.6434 | -118.7805 | 1.68 | -111.3922 | -109.7626 | -117.0181 | 118.6752 | -1.712 | -1.7899 | 118.7531 | 118.6615 | 118.6478 | -0.013733 | -0.027466 | -0.073243 | -0.086975 | -0.050354 | 7.3151 | 1.6891 | 8.9447 | 1.7624 | 9.0179 | 0.077819 | -0.027466 | 7.3883 | 120.4605 | 0.050354 | 120.4239 | 118.7256 | 120.3506 | -1.7624 | -120.5109 | 118.6478 | 120.3873 | 118.6615 | 48.3948
2487.6406 | 120.9 | -120.1721 | 0.55847 | 0.01358 | 0.01436 | -0.037354 | 0.034131 | -0.021258 | -0.030531 | -0.020683 | 0.0055542 | 0.0041443 | 0.074657 | 0.054978 | -0.017513 | -0.0013416 | -0.0064878 | -0.022888 | -0.036621 | -0.009155 | 0.022888 | 0.16937 | 0.086975 | 0.086975 | -71.4203 | 0.48981 | -120.2316 | 0.5722 | -112.619 | -110.9024 | -118.4463 | 120.163 | -0.59509 | -0.53558 | 120.3415 | 120.2591 | 120.2591 | 0.09613 | 0.09613 | -0.059509 | -0.068665 | 0.013733 | 7.5531 | 1.7258 | 9.2697 | 1.7853 | 9.3292 | 0.17853 | 0.032043 | 7.6126 | 120.8038 | -0.027466 | 120.7214 | 120.1355 | 120.6619 | -0.56763 | -120.7901 | 120.195 | 120.7443 | 120.1492 | 48.7518
2489.4375 | 121.0739 | -120.7169 | 0.16479 | 0.01358 | 0.013078 | -0.036927 | 0.036267 | -0.019335 | -0.02989 | -0.024742 | 0.0025024 | 0.0030763 | 0.074016 | 0.055619 | -0.019008 | -0.0026232 | -0.003497 | -0.004578 | -0.036621 | -0.004578 | 0.050354 | 0.21973 | 0.11444 | 0.09613 | -71.9284 | 0.10986 | -120.6894 | 0.19226 | -113.0173 | -111.2274 | -118.9178 | 120.7123 | -0.20142 | -0.11444 | 120.9366 | 120.813 | 120.8313 | 0.10071 | 0.11902 | 0.027466 | -0.054932 | 0.027466 | 7.6996 | 1.799 | 9.4894 | 1.7715 | 9.462 | 0.22431 | 0.054932 | 7.6721 | 120.8817 | -0.032043 | 120.7993 | 120.6802 | 120.8267 | -0.16937 | -120.8542 | 120.7672 | 120.9091 | 120.7123 | 48.7885
2491.1719 | 120.3049 | -120.0485 | 0.11902 | 0.01358 | 0.013719 | -0.035431 | 0.034131 | -0.020403 | -0.027113 | -0.022178 | 0.008606 | 0.0028625 | 0.071239 | 0.054764 | -0.018367 | -0.0019824 | -0.005206 | -0.009155 | -0.032043 | 0.004578 | 0.041199 | 0.17853 | 0.086975 | 0.07782 | -71.8185 | 0.027466 | -120.0851 | 0.059509 | -112.381 | -110.5453 | -118.3044 | 120.0531 | -0.15106 | -0.07782 | 120.2271 | 120.1263 | 120.1355 | 0.073242 | 0.082397 | -0.036621 | -0.091553 | -0.05951 | 7.6675 | 1.7441 | 9.5032 | 1.7807 | 9.5398 | 0.17395 | 0.036621 | 7.7042 | 120.1447 | -0.036621 | 120.1126 | 120.0165 | 120.076 | -0.11444 | -120.2042 | 120.0897 | 120.108 | 120.0394 | 48.23
2492.9531 | 120.9732 | -120.6894 | 0.068665 | 0.02121 | 0.015855 | -0.032868 | 0.035199 | -0.018267 | -0.028395 | -0.025169 | 0.0055542 | 0.0017945 | 0.073375 | 0.060532 | -0.017299 | -0.0032642 | -0.009692 | 0.004578 | -0.041199 | -0.004578 | 0.068665 | 0.21973 | 0.10529 | 0.082397 | -72.3862 | 0.004578 | -120.7443 | 0.073242 | -112.9074 | -110.9756 | -118.927 | 120.6848 | -0.10986 | 0 | 120.9091 | 120.7718 | 120.7947 | 0.086975 | 0.10986 | -0.054932 | -0.064087 | 0.004577 | 7.782 | 1.7624 | 9.7137 | 1.8173 | 9.7687 | 0.22431 | 0.073243 | 7.8369 | 120.8176 | -0.036621 | 120.7489 | 120.6482 | 120.694 | -0.073243 | -120.813 | 120.7581 | 120.7626 | 120.694 | 48.3032
2494.6719 | 121.0327 | -120.7489 | 0.09613 | 0.028839 | 0.014787 | -0.033295 | 0.036267 | -0.013781 | -0.027754 | -0.021537 | 0.011658 | 0.0052125 | 0.074657 | 0.050919 | -0.016872 | -5.9806e-05 | -0.0047788 | -0.018311 | -0.009155 | -0.004578 | 0.004578 | 0.16022 | 0.036621 | 0.068665 | -72.6242 | 0.036621 | -120.8313 | 0.045776 | -113.0173 | -110.9711 | -119.0002 | 120.7443 | -0.10528 | -0.091552 | 120.9091 | 120.8176 | 120.7855 | 0.073243 | 0.041199 | -0.082398 | -0.059509 | -0.050354 | 7.7316 | 1.7487 | 9.7778 | 1.8311 | 9.8602 | 0.16479 | 0.009156 | 7.814 | 120.8771 | -0.004577 | 120.8679 | 120.7397 | 120.7855 | -0.10071 | -120.9274 | 120.7535 | 120.7947 | 120.7306 | 48.1247
2496.4531 | 120.6711 | -120.1401 | 0.35248 | 0.02121 | 0.013505 | -0.035645 | 0.035199 | -0.021044 | -0.028181 | -0.024742 | 0.008606 | 0.0013673 | 0.075298 | 0.046219 | -0.019008 | -0.00027341 | -0.0088376 | -0.036621 | -0.013733 | -0.013733 | -0.004578 | 0.11444 | 0.032043 | 0.050354 | -72.2809 | 0.3067 | -120.163 | 0.36621 | -112.2665 | -110.2341 | -118.3777 | 120.1263 | -0.36621 | -0.35706 | 120.2545 | 120.1904 | 120.1721 | 0.064087 | 0.045776 | -0.022888 | -0.045776 | 0.013733 | 7.8735 | 1.7624 | 9.906 | 1.7853 | 9.9289 | 0.12817 | 0.009155 | 7.8964 | 120.5292 | 0 | 120.4697 | 120.1263 | 120.4468 | -0.36621 | -120.5154 | 120.1355 | 120.5063 | 120.1035 | 47.8592
2498.25 | 120.8771 | -120.4605 | 0.22888 | 0.02121 | 0.013505 | -0.033295 | 0.035199 | -0.021258 | -0.02754 | -0.02111 | 0.014709 | 0.0054261 | 0.075084 | 0.053055 | -0.018794 | 0.00015379 | -0.0041378 | -0.009155 | 0.004578 | -0.004578 | 0.050354 | 0.18768 | 0.050354 | 0.07782 | -72.6654 | 0.17395 | -120.5612 | 0.23346 | -112.5229 | -110.3348 | -118.6295 | 120.4559 | -0.2243 | -0.17853 | 120.6482 | 120.5383 | 120.5109 | 0.082398 | 0.054932 | -0.10071 | -0.054932 | 0.004577 | 7.9376 | 1.8311 | 10.1257 | 1.9318 | 10.2264 | 0.19226 | 0.054932 | 8.0383 | 120.7947 | 0.009156 | 120.7352 | 120.4651 | 120.6345 | -0.23346 | -120.7901 | 120.5109 | 120.694 | 120.4514 | 47.7951
2500.0469 | 120.5521 | -120.2225 | 0.09613 | 0.028839 | 0.012437 | -0.035859 | 0.033063 | -0.016131 | -0.029249 | -0.024955 | 0.008606 | 0.0060669 | 0.075512 | 0.056473 | -0.01794 | -0.0013416 | -0.007983 | -0.054932 | -0.022888 | 0 | -0.004578 | 0.1236 | 0.022888 | 0.045776 | -72.8485 | 0.041199 | -120.3278 | 0.050354 | -112.294 | -110.0235 | -118.4326 | 120.2225 | -0.11902 | -0.10071 | 120.3461 | 120.2682 | 120.2454 | 0.045776 | 0.022888 | -0.10529 | -0.054931 | -0.045776 | 7.9285 | 1.7899 | 10.199 | 1.8951 | 10.3043 | 0.1236 | -0.004578 | 8.0338 | 120.3781 | -0.022888 | 120.369 | 120.1996 | 120.2637 | -0.09613 | -120.4239 | 120.2179 | 120.2728 | 120.1675 | 47.374
2501.7812 | 120.8221 | -120.5429 | 0.09613 | 0.01358 | 0.011583 | -0.033509 | 0.036267 | -0.01784 | -0.029036 | -0.02346 | 0.008606 | 0.0054261 | 0.074871 | 0.054978 | -0.019435 | -0.00070061 | -0.0067014 | -0.027466 | -0.009155 | -0.013733 | -0.004578 | 0.12817 | 0.018311 | 0.022888 | -73.1781 | 0.022888 | -120.5841 | 0.041199 | -112.4542 | -110.1471 | -118.6615 | 120.5292 | -0.10528 | -0.10071 | 120.6711 | 120.5658 | 120.5612 | 0.036621 | 0.032044 | -0.041198 | -0.073242 | -0.054931 | 8.0887 | 1.8814 | 10.3958 | 1.9226 | 10.437 | 0.14191 | 0.009155 | 8.1299 | 120.6253 | 0.004578 | 120.607 | 120.5338 | 120.5658 | -0.10986 | -120.6802 | 120.5383 | 120.5841 | 120.5154 | 47.3648
2503.5781 | 120.6985 | -120.1401 | 0.52643 | 0.0059509 | 0.011583 | -0.038209 | 0.035412 | -0.018053 | -0.027754 | -0.021324 | 0.0025024 | 0.0062805 | 0.076366 | 0.046006 | -0.020717 | -0.0028368 | -0.0041378 | -0.036621 | -0.027466 | -0.004578 | -0.036621 | 0.086975 | 0.004578 | 0.009155 | -73.1461 | 0.44861 | -120.1675 | 0.39825 | -112.0193 | -109.584 | -118.2678 | 120.1355 | -0.55389 | -0.56305 | 120.2271 | 120.1492 | 120.1447 | 0.013733 | 0.009156 | -0.027466 | -0.07782 | -0.12817 | 8.1207 | 1.8723 | 10.556 | 1.8997 | 10.5835 | 0.091553 | -0.032043 | 8.1482 | 120.5658 | -0.022888 | 120.6161 | 120.1126 | 120.5887 | -0.53101 | -120.694 | 120.1035 | 120.5383 | 120.1035 | 46.994
2505.3594 | 120.639 | -120.5292 | 0.09613 | 0.01358 | 0.014573 | -0.035218 | 0.036694 | -0.019335 | -0.029463 | -0.020683 | -0.00054937 | 0.0043579 | 0.073803 | 0.052842 | -0.021144 | -0.0017688 | -0.0043514 | -0.07782 | -0.009155 | -0.036621 | -0.07782 | 0.064087 | -0.018311 | -0.009155 | -73.5123 | 0.050354 | -120.575 | -0.054932 | -112.2711 | -109.8312 | -118.6203 | 120.4926 | -0.10528 | -0.17395 | 120.5933 | 120.52 | 120.5109 | 0.027466 | 0.01831 | -0.045776 | -0.045776 | -0.15106 | 8.2581 | 1.9089 | 10.6979 | 1.9547 | 10.7437 | 0.10071 | -0.041199 | 8.3038 | 120.52 | 0.027466 | 120.6253 | 120.52 | 120.5795 | -0.13275 | -120.6711 | 120.4514 | 120.4742 | 120.4514 | 47.0169
2507.1406 | 120.8496 | -120.6482 | 0.073242 | 0.028839 | 0.014146 | -0.032654 | 0.03648 | -0.018267 | -0.030104 | -0.024314 | 0.0055542 | 0.0084167 | 0.075939 | 0.051346 | -0.017513 | -0.0030506 | -0.005206 | -0.027466 | 0.009155 | -0.050354 | -0.018311 | 0.10529 | 0.022888 | 0.032043 | -73.7503 | 0.054932 | -120.7169 | 0.018311 | -112.2803 | -109.7855 | -118.7027 | 120.5978 | -0.064087 | -0.091553 | 120.7535 | 120.6802 | 120.6711 | 0.082397 | 0.073242 | -0.068665 | -0.01831 | -0.054931 | 8.3679 | 1.9455 | 10.8627 | 2.0142 | 10.9314 | 0.15564 | 0.032043 | 8.4366 | 120.7352 | 0.059509 | 120.7718 | 120.6573 | 120.7031 | -0.1236 | -120.7901 | 120.6299 | 120.6665 | 120.6207 | 46.8979
2508.9375 | 120.7123 | -120.5704 | 0.1236 | -0.0016786 | 0.013719 | -0.033722 | 0.037121 | -0.017199 | -0.027967 | -0.018547 | 0.0025024 | 0.0086305 | 0.076366 | 0.048142 | -0.018794 | -0.0017688 | -0.0049924 | -0.073242 | 0.009155 | -0.041199 | -0.082397 | 0.036621 | -0.068665 | -0.050354 | -73.8373 | 0.10071 | -120.6207 | 0.022888 | -112.2116 | -109.5749 | -118.5699 | 120.5292 | -0.11444 | -0.20599 | 120.607 | 120.52 | 120.5017 | -0.009155 | -0.027466 | -0.050354 | -0.022888 | -0.10071 | 8.3588 | 2.0004 | 10.9955 | 2.0508 | 11.0458 | 0.07782 | -0.041198 | 8.4091 | 120.6436 | 0.050354 | 120.7214 | 120.5795 | 120.6711 | -0.16479 | -120.7443 | 120.488 | 120.5933 | 120.4971 | 46.7331
2510.6562 | 121.0236 | -120.7214 | 0.068665 | 0.0059509 | 0.01436 | -0.032654 | 0.03648 | -0.01784 | -0.027327 | -0.023674 | 0.0025024 | 0.0052125 | 0.075298 | 0.05626 | -0.014736 | 0.0018628 | -0.0060604 | 0 | -0.036621 | 0.018311 | 0.054932 | 0.17853 | 0.041199 | 0.054932 | -73.9609 | 0.004578 | -120.7764 | 0.10986 | -112.1246 | -109.4513 | -118.6844 | 120.7397 | -0.10529 | -0.013733 | 120.9 | 120.7764 | 120.7626 | 0.036621 | 0.022888 | -0.054931 | -0.064087 | 0.041198 | 8.5968 | 2.037 | 11.2701 | 2.092 | 11.3251 | 0.16022 | 0.036621 | 8.6517 | 120.8862 | -0.054932 | 120.7809 | 120.6848 | 120.726 | -0.050354 | -120.845 | 120.7764 | 120.8313 | 120.7214 | 46.7606
2512.4375 | 115.9195 | -115.0864 | 0.48981 | 0.044098 | 0.015214 | -0.035218 | 0.036267 | -0.012285 | -0.030317 | -0.02346 | 0.0025024 | 0.0077759 | 0.072734 | 0.052842 | -0.019435 | -0.00048701 | -0.0077694 | 0.009155 | -0.054932 | -0.050354 | -0.004578 | 0.12817 | 0 | 0.004578 | -69.9509 | -0.1236 | -115.004 | -0.35706 | -106.041 | -103.45 | -111.5753 | 115.036 | -0.54474 | -0.49439 | 115.2145 | 115.0909 | 115.0864 | 0.054932 | 0.050354 | 0.082398 | -0.6134 | -0.84686 | 9.0454 | 3.511 | 11.6364 | 3.4287 | 11.554 | 0.17853 | 0.045776 | 8.963 | 114.6469 | -0.004578 | 114.8804 | 115.0314 | 114.9628 | -0.54016 | -115.4938 | 115.0818 | 114.7293 | 115.0955 | 45.1355
2514.1562 | 120.8359 | -120.4971 | 0.041199 | 0.02121 | 0.013505 | -0.033509 | 0.035626 | -0.016131 | -0.029036 | -0.025169 | 0.0025024 | 0.0058533 | 0.07658 | 0.056473 | -0.019649 | -0.0013416 | -0.0056332 | -0.018311 | -0.036621 | 0.009155 | 0.032043 | 0.21973 | 0.10529 | 0.11444 | -73.7549 | -0.013733 | -120.5658 | 0.10986 | -111.6486 | -108.8196 | -118.4006 | 120.5063 | -0.07782 | -0.009156 | 120.7169 | 120.6116 | 120.6024 | 0.10529 | 0.096131 | -0.068665 | -0.054932 | 0.068664 | 8.8486 | 2.0966 | 11.6776 | 2.1652 | 11.7462 | 0.21057 | 0.022888 | 8.9172 | 120.6757 | -0.045776 | 120.5521 | 120.4605 | 120.4834 | -0.032044 | -120.607 | 120.5292 | 120.607 | 120.4788 | 46.7422
2515.9531 | 120.8633 | -120.5795 | 0.10529 | 0.028839 | 0.013292 | -0.035218 | 0.036053 | -0.018267 | -0.02519 | -0.022392 | 0.008606 | 0.0062805 | 0.07658 | 0.052842 | -0.019863 | 0.001222 | -0.0039242 | -0.032043 | -0.013733 | -0.032043 | 0.004578 | 0.1236 | 0.027466 | 0.041199 | -74.1669 | 0.068665 | -120.5841 | 0.082397 | -111.6852 | -108.7967 | -118.4921 | 120.5475 | -0.11902 | -0.10071 | 120.7031 | 120.6207 | 120.607 | 0.073242 | 0.059509 | -0.004577 | -0.036621 | -0.022889 | 8.8943 | 2.0874 | 11.7828 | 2.092 | 11.7874 | 0.15564 | 0.036621 | 8.8989 | 120.6665 | 0.01831 | 120.6528 | 120.5658 | 120.6482 | -0.13733 | -120.6894 | 120.5841 | 120.6619 | 120.5475 | 46.4127
2517.7344 | 120.8588 | -120.5566 | 0.21057 | 0.02121 | 0.016069 | -0.033082 | 0.038403 | -0.014849 | -0.028608 | -0.020469 | 0.0025024 | 0.0099121 | 0.076366 | 0.054551 | -0.017299 | -0.00070061 | -0.0077694 | -0.032043 | -0.009155 | -0.041199 | -0.036621 | 0.11444 | -0.004578 | 0.004578 | -74.2355 | 0.15564 | -120.5612 | 0.13275 | -111.6623 | -108.6868 | -118.4372 | 120.5154 | -0.21973 | -0.24719 | 120.6711 | 120.5612 | 120.5521 | 0.045777 | 0.036621 | -0.004577 | -0.054931 | -0.07782 | 8.8943 | 2.1194 | 11.8698 | 2.124 | 11.8744 | 0.15564 | 0.004578 | 8.8989 | 120.694 | 0.032044 | 120.7169 | 120.5475 | 120.7123 | -0.25177 | -120.7718 | 120.52 | 120.6894 | 120.5246 | 46.3211
2519.5156 | 120.5841 | -120.3598 | 0.064087 | 0.028839 | 0.013933 | -0.033936 | 0.03584 | -0.020403 | -0.026472 | -0.020042 | 0.017761 | 0.0069215 | 0.076793 | 0.055192 | -0.019649 | 0.0031446 | -0.0039242 | -0.009155 | 0.018311 | -0.018311 | 0.054932 | 0.20142 | 0.059509 | 0.068665 | -74.2218 | -0.004578 | -120.4102 | 0.064087 | -111.2823 | -108.3069 | -118.2083 | 120.3415 | -0.045776 | -0.009155 | 120.5612 | 120.4285 | 120.4193 | 0.086976 | 0.07782 | -0.050354 | -0.068665 | 0 | 9.0775 | 2.1515 | 12.0529 | 2.2018 | 12.1033 | 0.21973 | 0.073243 | 9.1278 | 120.4742 | 0.036622 | 120.4056 | 120.3781 | 120.3552 | -0.082398 | -120.4742 | 120.4147 | 120.4239 | 120.3506 | 46.138
2521.2969 | 120.7947 | -120.5338 | 0.059509 | 0.044098 | 0.015001 | -0.032654 | 0.037549 | -0.013567 | -0.026899 | -0.020042 | 0.017761 | 0.0067077 | 0.075939 | 0.056901 | -0.016445 | 0.00079479 | -0.0011472 | 0.036621 | -0.018311 | 0 | 0.073242 | 0.21515 | 0.073242 | 0.086975 | -74.5193 | -0.009155 | -120.575 | 0.10071 | -111.3327 | -108.252 | -118.3228 | 120.5338 | -0.07782 | 0.013733 | 120.7489 | 120.6207 | 120.607 | 0.086975 | 0.073242 | -0.041199 | -0.068664 | 0.041199 | 9.201 | 2.211 | 12.2818 | 2.2522 | 12.323 | 0.21515 | 0.073242 | 9.2422 | 120.6757 | -0.018311 | 120.5658 | 120.5154 | 120.5246 | -0.059509 | -120.6345 | 120.607 | 120.6345 | 120.5704 | 46.0144
2523.0781 | 120.8542 | -120.5978 | 0.07782 | 0.01358 | 0.012864 | -0.033936 | 0.037121 | -0.020617 | -0.029249 | -0.021751 | 0.011658 | 0.0084167 | 0.075298 | 0.057328 | -0.018581 | 0.001222 | -0.0043514 | -0.054932 | -0.009155 | -0.013733 | -0.022888 | 0.12817 | 0.018311 | 0.036621 | -74.8856 | 0.013733 | -120.6711 | 0.036621 | -111.351 | -108.2108 | -118.4097 | 120.5841 | -0.086975 | -0.10071 | 120.726 | 120.6345 | 120.6161 | 0.050354 | 0.032044 | -0.073243 | -0.064087 | -0.041199 | 9.2468 | 2.1881 | 12.3871 | 2.2614 | 12.4603 | 0.14191 | -0.009155 | 9.3201 | 120.7077 | 0.004578 | 120.6848 | 120.5887 | 120.6116 | -0.091553 | -120.7489 | 120.575 | 120.6345 | 120.5429 | 45.7123
2524.8594 | 120.8542 | -120.694 | 0.11444 | 0.044098 | 0.016496 | -0.03415 | 0.037121 | -0.016558 | -0.02989 | -0.020683 | 0.011658 | 0.011621 | 0.077861 | 0.055405 | -0.021358 | 0.00058099 | -0.0064878 | -0.064087 | 0.032043 | -0.059509 | -0.059509 | 0.068665 | -0.009155 | 0.004578 | -76.4786 | 0.068665 | -120.7718 | -0.013733 | -111.676 | -108.3755 | -118.5059 | 120.6345 | -0.082398 | -0.17395 | 120.7626 | 120.6985 | 120.6848 | 0.064087 | 0.050354 | -0.07782 | -0.045776 | -0.12817 | 9.0179 | 2.1881 | 12.3184 | 2.2659 | 12.3962 | 0.12817 | 0 | 9.0958 | 120.7581 | 0.091552 | 120.8405 | 120.726 | 120.7626 | -0.17395 | -120.8862 | 120.6345 | 120.6802 | 120.6299 | 44.2154
2526.6562 | 120.9503 | -120.7214 | 0.07782 | 0.036468 | 0.016496 | -0.031373 | 0.03584 | -0.01549 | -0.02989 | -0.02111 | 0.011658 | 0.0088441 | 0.076152 | 0.057541 | -0.016872 | 0.0035718 | -0.0056332 | -0.004578 | -0.022888 | -0.009155 | 0.032043 | 0.18768 | 0.059509 | 0.059509 | -76.6113 | 0.022888 | -120.7855 | 0.041199 | -111.5891 | -108.2062 | -118.4875 | 120.7123 | -0.10071 | -0.045777 | 120.9091 | 120.7809 | 120.7809 | 0.068664 | 0.068664 | -0.064086 | -0.054932 | -0.036621 | 9.1324 | 2.2339 | 12.5153 | 2.298 | 12.5793 | 0.19684 | 0.041198 | 9.1965 | 120.8267 | -0.013733 | 120.8084 | 120.6985 | 120.7443 | -0.086975 | -120.8633 | 120.7535 | 120.7626 | 120.7169 | 44.1101
2528.4375 | 120.8817 | -120.7489 | 0.11902 | 0.0059509 | 0.015641 | -0.033295 | 0.037335 | -0.013567 | -0.028395 | -0.024101 | 0.0055542 | 0.011407 | 0.077648 | 0.054337 | -0.017513 | 0.0018628 | -0.0032834 | -0.059509 | 0.013733 | -0.036621 | -0.09613 | 0.009155 | -0.07782 | -0.073242 | -76.9089 | 0.027466 | -120.8176 | -0.036621 | -111.6531 | -108.2108 | -118.5699 | 120.7123 | -0.10529 | -0.21515 | 120.7581 | 120.6757 | 120.6711 | -0.036621 | -0.041199 | -0.068665 | -0.091553 | -0.15564 | 9.0958 | 2.179 | 12.5381 | 2.2476 | 12.6068 | 0.045776 | -0.059509 | 9.1644 | 120.7809 | 0.050354 | 120.845 | 120.7626 | 120.7764 | -0.15564 | -120.9366 | 120.6528 | 120.7123 | 120.6894 | 43.84
2530.1562 | 120.9503 | -120.8176 | 0.082397 | -0.0016786 | 0.01436 | -0.035431 | 0.034772 | -0.017199 | -0.029249 | -0.022178 | 0.0025024 | 0.0069215 | 0.078075 | 0.051133 | -0.021144 | -0.00048701 | -0.005206 | -0.036621 | -0.022888 | 0 | -0.027466 | 0.1236 | 0.036621 | 0.027466 | -76.9455 | 0.027466 | -120.813 | -0.032043 | -111.5067 | -107.9819 | -118.5516 | 120.8176 | -0.10528 | -0.10986 | 120.9412 | 120.845 | 120.8542 | 0.027466 | 0.036621 | 0.004578 | -0.054931 | -0.11444 | 9.3109 | 2.2659 | 12.8357 | 2.2614 | 12.8311 | 0.1236 | -0.027466 | 9.3063 | 120.7809 | -0.022888 | 120.8405 | 120.7947 | 120.845 | -0.082397 | -120.8954 | 120.7901 | 120.7855 | 120.7809 | 43.8721
2531.9531 | 121.0419 | -120.8038 | 0.086975 | 0.044098 | 0.016496 | -0.033936 | 0.039258 | -0.016558 | -0.025831 | -0.023887 | 0.017761 | 0.0092713 | 0.078502 | 0.059464 | -0.016658 | -0.0013416 | -0.0024288 | 0.004578 | -0.004578 | -0.013733 | 0.036621 | 0.17853 | 0.059509 | 0.073242 | -76.9959 | 0.004578 | -120.8633 | 0.050354 | -111.3831 | -107.7667 | -118.4921 | 120.7901 | -0.091553 | -0.050354 | 120.9824 | 120.8771 | 120.8633 | 0.086975 | 0.073242 | -0.059509 | -0.082397 | -0.036621 | 9.4208 | 2.3117 | 13.0371 | 2.3712 | 13.0966 | 0.19226 | 0.050354 | 9.4803 | 120.9137 | 0.009155 | 120.8679 | 120.7993 | 120.8084 | -0.10071 | -120.9503 | 120.8405 | 120.8542 | 120.8084 | 43.808
2533.7344 | 121.051 | -120.8267 | 0.064087 | 0.02121 | 0.012864 | -0.033509 | 0.035199 | -0.016985 | -0.027967 | -0.023033 | 0.011658 | 0.0096985 | 0.077007 | 0.054551 | -0.019649 | 0.0027174 | -0.006915 | -0.036621 | -0.018311 | 0.009155 | 0 | 0.1236 | 0.045776 | 0.045776 | -77.0279 | 0.032043 | -120.8862 | 0.036621 | -111.2961 | -107.5928 | -118.5013 | 120.8359 | -0.082398 | -0.064087 | 120.9503 | 120.8725 | 120.8725 | 0.036621 | 0.036621 | -0.059509 | -0.032044 | -0.027466 | 9.5306 | 2.3254 | 13.2339 | 2.3849 | 13.2935 | 0.11444 | -0.009155 | 9.5901 | 120.9229 | -0.027466 | 120.9183 | 120.8084 | 120.8588 | -0.054932 | -120.9503 | 120.8267 | 120.8633 | 120.7901 | 43.7988
2535.5312 | 121.0968 | -120.845 | 0.086975 | 0.036468 | 0.015001 | -0.034577 | 0.034985 | -0.021044 | -0.029676 | -0.024101 | 0.011658 | 0.0099121 | 0.078289 | 0.053696 | -0.017085 | 0.0025036 | -0.0028562 | -0.041199 | -0.018311 | -0.022888 | -0.004578 | 0.14648 | 0.032043 | 0.059509 | -77.1423 | 0.009155 | -120.9229 | 0.050354 | -111.2 | -107.4371 | -118.4921 | 120.8221 | -0.10529 | -0.091553 | 120.9915 | 120.9045 | 120.8771 | 0.082397 | 0.054931 | -0.07782 | -0.07782 | -0.036621 | 9.6451 | 2.3529 | 13.4079 | 2.4307 | 13.4857 | 0.16937 | 0.01831 | 9.7229 | 120.9732 | 0.004577 | 120.932 | 120.8267 | 120.8542 | -0.10986 | -121.0098 | 120.8405 | 120.8954 | 120.8038 | 43.7027
2537.3125 | 121.0373 | -120.8954 | 0.09613 | 0.01358 | 0.016282 | -0.03415 | 0.03883 | -0.016771 | -0.02989 | -0.022605 | 0.0055542 | 0.011621 | 0.078289 | 0.052201 | -0.016872 | 0.0016492 | -0.0015744 | -0.013733 | 0 | -0.013733 | -0.032043 | 0.091553 | -0.018311 | -0.013733 | -77.2751 | 0.036621 | -120.9137 | -0.004578 | -111.1954 | -107.3685 | -118.5379 | 120.8817 | -0.09613 | -0.12817 | 120.9869 | 120.8817 | 120.8771 | 0 | -0.004578 | -0.01831 | -0.059509 | -0.10071 | 9.7 | 2.3575 | 13.5269 | 2.3758 | 13.5452 | 0.10529 | -0.01831 | 9.7183 | 120.9091 | 0.013733 | 120.9503 | 120.8954 | 120.932 | -0.10986 | -121.0098 | 120.8633 | 120.8908 | 120.8817 | 43.6203
2539.0469 | 121.1792 | -120.8542 | 0.073242 | 0.0059509 | 0.016282 | -0.032654 | 0.03584 | -0.021044 | -0.028608 | -0.022178 | 0.023865 | 0.010553 | 0.077861 | 0.058396 | -0.01559 | 0.0031446 | -0.0032834 | 0.013733 | -0.027466 | 0.009155 | 0.045776 | 0.1831 | 0.054932 | 0.10986 | -77.2018 | 0.022888 | -120.9549 | 0.11444 | -110.939 | -107.103 | -118.428 | 120.8633 | -0.10071 | -0.027466 | 121.0373 | 120.9641 | 120.9091 | 0.10071 | 0.045777 | -0.10071 | -0.050354 | 0.041199 | 9.9152 | 2.4261 | 13.7512 | 2.5269 | 13.8519 | 0.17395 | 0.036621 | 10.0159 | 121.0693 | -0.036621 | 120.9778 | 120.8267 | 120.8771 | -0.064087 | -121.0281 | 120.9 | 120.9686 | 120.8679 | 43.6523
2540.8281 | 121.0693 | -120.9366 | 0.09613 | 0.0059509 | 0.011796 | -0.035004 | 0.035412 | -0.015276 | -0.030958 | -0.022178 | 0.0025024 | 0.01098 | 0.07957 | 0.05925 | -0.023921 | 0.00036739 | 0.00098903 | -0.07782 | 0.018311 | -0.036621 | -0.068665 | 0.064087 | -0.009155 | -0.013733 | -77.5681 | 0.054932 | -120.9686 | -0.050354 | -111.0306 | -107.0572 | -118.5379 | 120.9 | -0.077819 | -0.16479 | 121.0007 | 120.9229 | 120.9274 | 0.022888 | 0.027466 | -0.032044 | -0.041198 | -0.14648 | 9.906 | 2.3987 | 13.8794 | 2.4307 | 13.9114 | 0.10071 | -0.032044 | 9.938 | 120.9183 | 0.054932 | 121.0236 | 120.9549 | 120.9915 | -0.13275 | -121.0648 | 120.8679 | 120.8862 | 120.8588 | 43.3685
2542.6094 | 121.0739 | -120.9549 | 0.11444 | 0.0059509 | 0.013933 | -0.03415 | 0.039258 | -0.019335 | -0.029036 | -0.023246 | 0.0025024 | 0.012048 | 0.077221 | 0.059891 | -0.01559 | 0.0035718 | -0.0056332 | -0.082397 | 0.022888 | -0.018311 | -0.086975 | 0.013733 | -0.068665 | -0.036621 | -77.6871 | 0.050354 | -121.0098 | -0.018311 | -110.9436 | -106.9244 | -118.5013 | 120.9366 | -0.091553 | -0.20142 | 120.9686 | 120.9183 | 120.8862 | -0.01831 | -0.050354 | -0.054932 | -0.064087 | -0.13275 | 10.0113 | 2.4536 | 14.0305 | 2.5085 | 14.0854 | 0.032044 | -0.068664 | 10.0662 | 120.9915 | 0.041199 | 121.0602 | 120.9778 | 121.0052 | -0.13275 | -121.1243 | 120.8679 | 120.9366 | 120.8725 | 43.2678
2544.3906 | 121.1975 | -120.9274 | 0.064087 | 0.036468 | 0.015855 | -0.033936 | 0.037121 | -0.016771 | -0.026899 | -0.020042 | 0.020813 | 0.011407 | 0.081066 | 0.063096 | -0.016231 | 0.003999 | -0.0071286 | 0.004578 | 0 | 0 | 0.054932 | 0.20142 | 0.073242 | 0.091553 | -77.5955 | 0.018311 | -120.9915 | 0.09613 | -110.7651 | -106.6498 | -118.4372 | 120.9274 | -0.064087 | -0.009155 | 121.1288 | 121.019 | 121.0007 | 0.091553 | 0.073242 | -0.064087 | -0.045776 | 0.032043 | 10.1624 | 2.4902 | 14.2776 | 2.5543 | 14.3417 | 0.20142 | 0.054932 | 10.2264 | 121.0876 | 0 | 121.0098 | 120.9274 | 120.9457 | -0.064087 | -121.0556 | 120.9824 | 121.0236 | 120.932 | 43.3319
2546.1719 | 121.1838 | -120.9869 | 0.09613 | 0.02121 | 0.012864 | -0.0365 | 0.036908 | -0.018908 | -0.029249 | -0.024528 | 0.017761 | 0.012048 | 0.078716 | 0.055405 | -0.019008 | 0.0010084 | -0.0045652 | -0.036621 | 0.032043 | -0.059509 | -0.027466 | 0.07782 | 0.013733 | 0.009155 | -77.8702 | 0.054932 | -121.0648 | 0.013733 | -110.6964 | -106.5628 | -118.4509 | 120.9274 | -0.064087 | -0.1236 | 121.0648 | 120.9961 | 121.0007 | 0.068664 | 0.073242 | -0.07782 | -0.041198 | -0.082397 | 10.2905 | 2.536 | 14.4241 | 2.6138 | 14.502 | 0.13733 | 0.032043 | 10.3683 | 121.0785 | 0.091552 | 121.1197 | 121.019 | 121.0419 | -0.15564 | -121.1609 | 120.9595 | 121.0007 | 120.9503 | 43.1168
2547.8906 | 121.2891 | -120.9641 | 0.073242 | -0.0016786 | 0.014573 | -0.033082 | 0.034344 | -0.013994 | -0.030317 | -0.023246 | 0.0055542 | 0.010553 | 0.080639 | 0.057969 | -0.014522 | 0.0042126 | -0.0030698 | -0.009155 | -0.036621 | -0.004578 | 0.050354 | 0.19684 | 0.050354 | 0.068665 | -77.7008 | 0.004578 | -121.0007 | 0.10986 | -110.5499 | -106.3065 | -118.3685 | 120.9595 | -0.10986 | -0.022888 | 121.1609 | 121.0327 | 121.0144 | 0.073243 | 0.054932 | -0.036621 | -0.068664 | 0.036621 | 10.4141 | 2.5955 | 14.6576 | 2.6321 | 14.6942 | 0.20142 | 0.054932 | 10.4507 | 121.1105 | -0.032043 | 121.0052 | 120.9274 | 120.9686 | -0.07782 | -121.0739 | 121.0144 | 121.0739 | 120.9549 | 43.2632
2549.6719 | 121.257 | -121.019 | 0.07782 | 0.0059509 | 0.015214 | -0.032654 | 0.034344 | -0.017412 | -0.028181 | -0.023887 | 0.0055542 | 0.0092713 | 0.07957 | 0.054337 | -0.018154 | 0.0027174 | -0.0026426 | -0.009155 | -0.018311 | 0.022888 | 0.059509 | 0.19684 | 0.10071 | 0.07782 | -77.8198 | 0.018311 | -121.0236 | 0.064087 | -110.4767 | -106.1188 | -118.3777 | 121.0419 | -0.096131 | -0.018311 | 121.2158 | 121.0968 | 121.1197 | 0.054932 | 0.07782 | -0.004578 | -0.059509 | -0.013733 | 10.5423 | 2.6413 | 14.9002 | 2.6459 | 14.9048 | 0.17395 | 0.036621 | 10.5469 | 121.0876 | -0.041199 | 121.0419 | 121.0007 | 121.0373 | -0.054932 | -121.1014 | 121.0785 | 121.0831 | 121.0098 | 43.1992
2551.3906 | 121.2296 | -121.0464 | 0.073242 | 0.044098 | 0.01436 | -0.034363 | 0.037335 | -0.018694 | -0.029676 | -0.021537 | 0.011658 | 0.012689 | 0.080211 | 0.05925 | -0.017726 | 0.0025036 | -0.0028562 | -0.022888 | -0.004578 | -0.022888 | -0.013733 | 0.12817 | 0.032043 | 0.022888 | -77.9526 | 0.050354 | -121.0556 | 0.041199 | -110.3989 | -106.0226 | -118.396 | 121.0236 | -0.07782 | -0.086975 | 121.1746 | 121.0693 | 121.0785 | 0.045776 | 0.054931 | -0.009155 | -0.022888 | -0.032043 | 10.6476 | 2.6505 | 15.0238 | 2.6596 | 15.033 | 0.15106 | 0.009155 | 10.6567 | 121.0968 | 0.01831 | 121.106 | 121.0419 | 121.0968 | -0.09613 | -121.1288 | 121.0327 | 121.0876 | 121.0236 | 43.0939
2553.1719 | 121.2479 | -121.0602 | 0.082397 | 0.0059509 | 0.013933 | -0.033295 | 0.03584 | -0.018267 | -0.029249 | -0.023033 | 0.0055542 | 0.013116 | 0.077221 | 0.06395 | -0.016872 | 0.0031446 | -0.0013608 | -0.059509 | 0.013733 | -0.032043 | -0.07782 | 0.050354 | -0.041199 | -0.018311 | -78.0075 | 0.022888 | -121.0922 | 0.036621 | -110.321 | -105.8716 | -118.3823 | 121.0281 | -0.068664 | -0.16022 | 121.1105 | 121.0419 | 121.019 | 0.013732 | -0.009156 | -0.032043 | -0.059509 | -0.045776 | 10.7391 | 2.6779 | 15.1886 | 2.71 | 15.2206 | 0.082397 | -0.045777 | 10.7712 | 121.1288 | 0.045776 | 121.1151 | 121.0739 | 121.0831 | -0.11444 | -121.1746 | 120.9824 | 121.0968 | 121.0007 | 43.0527
2554.9688 | 121.2387 | -121.1105 | 0.11444 | 0.044098 | 0.015855 | -0.035645 | 0.037549 | -0.016131 | -0.028181 | -0.019828 | 0.020813 | 0.015893 | 0.080425 | 0.053269 | -0.019222 | 0.0016492 | -0.0030698 | -0.041199 | 0.036621 | -0.054932 | -0.068665 | 0.064087 | -0.013733 | -0.004578 | -78.1448 | 0.073242 | -121.1426 | -0.013733 | -110.202 | -105.7022 | -118.3685 | 121.0556 | -0.07782 | -0.18311 | 121.1746 | 121.106 | 121.0968 | 0.050354 | 0.041199 | -0.032043 | -0.041199 | -0.12817 | 10.9085 | 2.742 | 15.4083 | 2.774 | 15.4404 | 0.11902 | -0.013733 | 10.9406 | 121.1288 | 0.091553 | 121.2158 | 121.1472 | 121.1838 | -0.16937 | -121.257 | 121.0419 | 121.0968 | 121.0693 | 42.9657
2556.75 | 121.3669 | -121.0693 | 0.082397 | 0.01358 | 0.011369 | -0.036713 | 0.033917 | -0.020403 | -0.028822 | -0.022605 | -0.00054937 | 0.011407 | 0.078716 | 0.061814 | -0.020717 | 0.0025036 | -0.0026426 | -0.045776 | -0.032043 | 0.009155 | 0.013733 | 0.16022 | 0.07782 | 0.09613 | -78.1448 | 0.004578 | -121.0968 | 0.086975 | -109.996 | -105.4459 | -118.2724 | 121.0785 | -0.11444 | -0.068664 | 121.2296 | 121.1655 | 121.1472 | 0.086975 | 0.068665 | -0.027466 | -0.077819 | 0.004578 | 11.0733 | 2.7969 | 15.6235 | 2.8244 | 15.6509 | 0.15106 | 0.004578 | 11.1008 | 121.1838 | -0.041198 | 121.1014 | 121.0373 | 121.0739 | -0.073242 | -121.1792 | 121.0831 | 121.1563 | 121.0236 | 42.9245
2558.4688 | 121.3348 | -121.0693 | 0.073242 | 0.051727 | 0.014573 | -0.032654 | 0.037762 | -0.016344 | -0.026472 | -0.020897 | 0.011658 | 0.013971 | 0.080639 | 0.060319 | -0.01794 | 0.0059216 | -0.0030698 | -0.013733 | -0.004578 | -0.009155 | 0.041199 | 0.19226 | 0.068665 | 0.068665 | -78.1723 | 0.022888 | -121.1243 | 0.082397 | -109.9411 | -105.336 | -118.2907 | 121.0602 | -0.07782 | -0.032043 | 121.2616 | 121.138 | 121.138 | 0.07782 | 0.07782 | -0.054932 | -0.050354 | 0.009155 | 11.1282 | 2.7786 | 15.7333 | 2.8336 | 15.7883 | 0.20142 | 0.050354 | 11.1832 | 121.2067 | 0.004577 | 121.1472 | 121.0648 | 121.0922 | -0.082397 | -121.1975 | 121.1105 | 121.1517 | 121.0556 | 42.897
2560.2344 | 121.2936 | -121.1151 | 0.07782 | 0.028839 | 0.015428 | -0.033936 | 0.037762 | -0.017626 | -0.029036 | -0.024101 | 0.0055542 | 0.015253 | 0.081066 | 0.056901 | -0.019435 | 0.0037854 | -0.003497 | -0.009155 | 0.013733 | -0.032043 | -0.022888 | 0.10529 | -0.009155 | 0.004578 | -78.2272 | 0.041199 | -121.1334 | 0.009155 | -109.8816 | -105.2399 | -118.3365 | 121.0831 | -0.064087 | -0.10071 | 121.2204 | 121.1197 | 121.106 | 0.036621 | 0.022888 | -0.018311 | -0.036621 | -0.068665 | 11.2335 | 2.7786 | 15.8752 | 2.7969 | 15.8936 | 0.13733 | 0.009155 | 11.2518 | 121.1426 | 0.045776 | 121.1746 | 121.1288 | 121.1563 | -0.10986 | -121.2112 | 121.0922 | 121.1243 | 121.106 | 42.8879
2562.0312 | 121.2616 | -121.1243 | 0.10529 | 0.01358 | 0.016282 | -0.033082 | 0.037335 | -0.01549 | -0.027327 | -0.02346 | 0.008606 | 0.015466 | 0.083416 | 0.05861 | -0.018154 | 0.002931 | -0.00071997 | -0.064087 | 0.004578 | -0.027466 | -0.068665 | 0.064087 | -0.045776 | -0.045776 | -78.2776 | 0.032043 | -121.1792 | -0.018311 | -109.8038 | -105.1025 | -118.309 | 121.0968 | -0.10071 | -0.17395 | 121.1884 | 121.0785 | 121.0785 | -0.01831 | -0.01831 | -0.054931 | -0.073243 | -0.1236 | 11.3205 | 2.8152 | 16.0217 | 2.8702 | 16.0767 | 0.091553 | -0.041199 | 11.3754 | 121.1609 | 0.032044 | 121.2112 | 121.1288 | 121.1563 | -0.13275 | -121.2845 | 121.0556 | 121.106 | 121.0602 | 42.8467
2563.7969 | 121.3531 | -121.1288 | 0.073242 | 0.01358 | 0.014146 | -0.032227 | 0.036267 | -0.017199 | -0.026899 | -0.025383 | 0.0055542 | 0.015039 | 0.081493 | 0.057114 | -0.016658 | 0.0059216 | -0.0030698 | -0.07782 | 0.004578 | -0.018311 | -0.068665 | 0.064087 | -0.050354 | -0.032043 | -78.3829 | 0.027466 | -121.1929 | 0.022888 | -109.6619 | -104.8782 | -118.2449 | 121.1105 | -0.068664 | -0.14191 | 121.1929 | 121.0968 | 121.0785 | -0.013732 | -0.032043 | -0.064087 | -0.045776 | -0.050354 | 11.467 | 2.8839 | 16.2506 | 2.948 | 16.3147 | 0.082398 | -0.050354 | 11.5311 | 121.2158 | 0.022889 | 121.2204 | 121.1334 | 121.1563 | -0.091553 | -121.2662 | 121.0602 | 121.1517 | 121.051 | 42.746
2565.5312 | 121.3898 | -121.1517 | 0.082397 | 0.028839 | 0.01201 | -0.033722 | 0.034131 | -0.018053 | -0.025618 | -0.023246 | 0.008606 | 0.012262 | 0.079357 | 0.058396 | -0.020931 | 0.002931 | 0.0012028 | -0.050354 | -0.032043 | 0 | -0.009155 | 0.1236 | 0.027466 | 0.045776 | -78.3691 | -0.004578 | -121.1609 | 0.041199 | -109.4696 | -104.6631 | -118.1946 | 121.1517 | -0.11444 | -0.091552 | 121.2753 | 121.1975 | 121.1792 | 0.045776 | 0.027466 | -0.009156 | -0.086975 | -0.041198 | 11.6821 | 2.9572 | 16.4886 | 2.9663 | 16.4978 | 0.1236 | -0.009155 | 11.6913 | 121.2021 | -0.032043 | 121.1563 | 121.1197 | 121.1472 | -0.082397 | -121.2433 | 121.1426 | 121.1929 | 121.1014 | 42.7826
2567.3125 | 121.3623 | -121.1838 | 0.09613 | 0.044098 | 0.013292 | -0.035004 | 0.036694 | -0.018908 | -0.028395 | -0.022392 | 0.017761 | 0.016321 | 0.081707 | 0.059037 | -0.019008 | 0.00464 | -0.0026426 | -0.004578 | 0.022888 | -0.036621 | -0.009155 | 0.11444 | 0.013733 | 0.027466 | -78.4378 | 0.036621 | -121.1929 | 0.022888 | -109.4193 | -104.5486 | -118.2037 | 121.1472 | -0.073242 | -0.10528 | 121.2982 | 121.2112 | 121.1975 | 0.064087 | 0.050354 | -0.009155 | -0.059509 | -0.073242 | 11.7645 | 2.98 | 16.6351 | 2.9892 | 16.6443 | 0.15106 | 0.027466 | 11.7737 | 121.2158 | 0.059509 | 121.2296 | 121.2067 | 121.2204 | -0.13275 | -121.2891 | 121.1746 | 121.2067 | 121.1792 | 42.746
2569.0938 | 121.3303 | -121.17 | 0.10529 | -0.0016786 | 0.013719 | -0.033082 | 0.038189 | -0.016771 | -0.02989 | -0.023674 | 0.0025024 | 0.016962 | 0.078716 | 0.056687 | -0.017513 | 0.0048536 | 0.0012028 | -0.07782 | 0.027466 | -0.032043 | -0.09613 | -0.004578 | -0.091553 | -0.054932 | -78.5751 | 0.036621 | -121.2204 | -0.022888 | -109.3597 | -104.4342 | -118.2449 | 121.138 | -0.07782 | -0.20142 | 121.1655 | 121.1151 | 121.0785 | -0.022889 | -0.05951 | -0.050354 | -0.068665 | -0.12817 | 11.8103 | 2.9251 | 16.7358 | 2.9755 | 16.7862 | 0.027465 | -0.064087 | 11.8607 | 121.1975 | 0.059509 | 121.257 | 121.1975 | 121.2067 | -0.13733 | -121.3257 | 121.0739 | 121.1472 | 121.0922 | 42.5949
2570.8125 | 121.3943 | -121.1884 | 0.082397 | 0.028839 | 0.016069 | -0.032654 | 0.037549 | -0.017199 | -0.028395 | -0.024314 | 0.011658 | 0.016107 | 0.083202 | 0.057969 | -0.021572 | 0.003999 | -0.0024288 | -0.013733 | 0.009155 | -0.041199 | -0.022888 | 0.11902 | 0.013733 | 0.018311 | -78.5156 | 0.045776 | -121.2341 | 0.036621 | -109.1812 | -104.2191 | -118.1808 | 121.1472 | -0.073242 | -0.10528 | 121.3074 | 121.2067 | 121.2021 | 0.05951 | 0.054932 | -0.045777 | -0.036621 | -0.045776 | 12.0071 | 3.0075 | 16.9693 | 3.0533 | 17.0151 | 0.16022 | 0.018311 | 12.0529 | 121.2708 | 0.050354 | 121.2799 | 121.1975 | 121.2341 | -0.1236 | -121.3165 | 121.1655 | 121.225 | 121.1746 | 42.6727
2572.5938 | 121.3531 | -121.2296 | 0.11444 | 0.0059509 | 0.013505 | -0.033722 | 0.036694 | -0.015703 | -0.028181 | -0.022178 | 0.020813 | 0.017389 | 0.083629 | 0.054123 | -0.019435 | 0.0035718 | 0.0020572 | -0.068665 | 0.032043 | -0.068665 | -0.082397 | 0.064087 | 0 | 0.004578 | -78.566 | 0.086975 | -121.2845 | -0.041199 | -109.0759 | -104.1046 | -118.1808 | 121.1609 | -0.082398 | -0.19684 | 121.2936 | 121.2341 | 121.2296 | 0.073243 | 0.068665 | -0.054932 | -0.027466 | -0.15564 | 12.1536 | 3.0487 | 17.1249 | 3.1036 | 17.1799 | 0.13275 | -0.013732 | 12.2086 | 121.2433 | 0.10071 | 121.3715 | 121.2616 | 121.3165 | -0.18311 | -121.3989 | 121.1472 | 121.1884 | 121.1609 | 42.6636
2574.375 | 121.463 | -121.1929 | 0.068665 | -0.0016786 | 0.013292 | -0.032227 | 0.035199 | -0.020403 | -0.027113 | -0.021537 | 0.0025024 | 0.016107 | 0.081066 | 0.062241 | -0.020931 | 0.0048536 | 0.00034823 | 0 | -0.022888 | 0 | 0.032043 | 0.1831 | 0.082397 | 0.07782 | -78.5339 | 0.018311 | -121.2387 | 0.064087 | -108.815 | -103.8254 | -118.0801 | 121.1929 | -0.091553 | -0.036622 | 121.376 | 121.2708 | 121.2753 | 0.07782 | 0.082397 | -0.045776 | -0.050354 | -0.004578 | 12.3779 | 3.1128 | 17.3676 | 3.1586 | 17.4133 | 0.1831 | 0.032043 | 12.4237 | 121.3028 | -0.022888 | 121.257 | 121.17 | 121.2112 | -0.068665 | -121.3074 | 121.225 | 121.257 | 121.1929 | 42.659
2576.1562 | 121.4081 | -121.2433 | 0.10529 | 0.036468 | 0.01671 | -0.033082 | 0.033276 | -0.015062 | -0.026258 | -0.019615 | 0.023865 | 0.017603 | 0.082134 | 0.063309 | -0.018581 | 0.0035718 | 0.003339 | -0.054932 | 0.027466 | -0.059509 | -0.068665 | 0.054932 | 0.004578 | 0.004578 | -78.9001 | 0.082397 | -121.2845 | -0.013733 | -108.7875 | -103.7704 | -118.1213 | 121.1838 | -0.07782 | -0.17395 | 121.2982 | 121.2479 | 121.2479 | 0.064087 | 0.064087 | -0.041199 | -0.022889 | -0.11902 | 12.4557 | 3.1219 | 17.4728 | 3.1631 | 17.514 | 0.11444 | -0.009156 | 12.4969 | 121.2708 | 0.086975 | 121.3669 | 121.2708 | 121.3257 | -0.16479 | -121.3898 | 121.1746 | 121.2296 | 121.1884 | 42.3431
2577.875 | 121.5408 | -121.1838 | 0.091553 | 0.0059509 | 0.013078 | -0.034791 | 0.03349 | -0.016131 | -0.029463 | -0.021324 | 0.008606 | 0.015466 | 0.081279 | 0.067795 | -0.019435 | 0.00464 | 0.0014164 | -0.022888 | -0.022888 | 0.013733 | 0.064087 | 0.21973 | 0.11444 | 0.11444 | -78.6667 | 0.009155 | -121.2387 | 0.10986 | -108.5083 | -103.5004 | -118.0161 | 121.1975 | -0.11444 | -0.027466 | 121.4035 | 121.2982 | 121.2982 | 0.10071 | 0.10071 | -0.054931 | -0.082398 | 0.01831 | 12.6755 | 3.1677 | 17.6834 | 3.2227 | 17.7383 | 0.20599 | 0.050354 | 12.7304 | 121.3486 | -0.036621 | 121.2479 | 121.1609 | 121.1929 | -0.07782 | -121.3303 | 121.2479 | 121.2936 | 121.1609 | 42.5171
2579.6562 | 121.5134 | -121.1975 | 0.073242 | 0.01358 | 0.014146 | -0.034791 | 0.03584 | -0.018694 | -0.027754 | -0.020042 | 0.0025024 | 0.016321 | 0.081493 | 0.062668 | -0.014095 | 0.0061352 | 0.002698 | 0.027466 | -0.032043 | 0.009155 | 0.045776 | 0.18768 | 0.064087 | 0.068665 | -78.8956 | -0.013733 | -121.2387 | 0.10529 | -108.4488 | -103.3768 | -117.9794 | 121.2067 | -0.10529 | -0.027466 | 121.3852 | 121.2662 | 121.2616 | 0.05951 | 0.054932 | -0.041198 | -0.086975 | 0.032044 | 12.7487 | 3.2181 | 17.8207 | 3.2593 | 17.8619 | 0.17853 | 0.036621 | 12.7899 | 121.344 | -0.041198 | 121.225 | 121.1655 | 121.1838 | -0.064087 | -121.3119 | 121.2433 | 121.3028 | 121.225 | 42.3019
2581.4375 | 121.4127 | -121.2845 | 0.10071 | 0.01358 | 0.013719 | -0.033295 | 0.032208 | -0.021258 | -0.030317 | -0.020469 | 0.0055542 | 0.018457 | 0.082775 | 0.062455 | -0.021999 | 0.0052808 | -0.00050617 | -0.059509 | 0 | -0.018311 | -0.07782 | 0.068665 | -0.013733 | -0.004578 | -79.0604 | 0.050354 | -121.3165 | -0.036621 | -108.4671 | -103.3127 | -118.0847 | 121.2662 | -0.10071 | -0.17853 | 121.3531 | 121.2799 | 121.2708 | 0.013733 | 0.004578 | -0.032043 | -0.050354 | -0.13733 | 12.8174 | 3.1998 | 17.9718 | 3.2318 | 18.0038 | 0.086976 | -0.059509 | 12.8494 | 121.2799 | 0.018311 | 121.3669 | 121.2845 | 121.3348 | -0.11902 | -121.4172 | 121.2067 | 121.2479 | 121.225 | 42.2241
2583.2344 | 121.4401 | -121.2708 | 0.10071 | 0.01358 | 0.015001 | -0.035431 | 0.037549 | -0.014422 | -0.027967 | -0.024101 | 0.0055542 | 0.018671 | 0.083202 | 0.061387 | -0.017085 | 0.0048536 | 0.00163 | -0.064087 | 0.009155 | -0.032043 | -0.082397 | 0.032043 | -0.073242 | -0.036621 | -79.0466 | 0.036621 | -121.3165 | 0.009155 | -108.3023 | -103.1708 | -118.0435 | 121.2387 | -0.091553 | -0.18311 | 121.3028 | 121.2341 | 121.1975 | -0.004578 | -0.041199 | -0.045776 | -0.064087 | -0.091553 | 12.9684 | 3.2272 | 18.1 | 3.273 | 18.1458 | 0.064086 | -0.050354 | 13.0142 | 121.3257 | 0.041198 | 121.3531 | 121.2799 | 121.3074 | -0.13275 | -121.4172 | 121.1884 | 121.2799 | 121.2067 | 42.2241
2585.0312 | 121.55 | -121.2387 | 0.068665 | 0.0059509 | 0.013933 | -0.034577 | 0.034558 | -0.016771 | -0.028608 | -0.022605 | 0.0055542 | 0.019525 | 0.08427 | 0.0663 | -0.016658 | 0.0059216 | 0.002698 | -0.036621 | -0.013733 | 0 | 0.004578 | 0.15564 | 0.009155 | 0.045776 | -78.4882 | 0 | -121.2982 | 0.10071 | -108.11 | -102.7817 | -117.9245 | 121.2387 | -0.082398 | -0.064087 | 121.3943 | 121.2845 | 121.2479 | 0.045776 | 0.009155 | -0.05951 | -0.068665 | 0.032043 | 13.1287 | 3.3142 | 18.457 | 3.3737 | 18.5165 | 0.15564 | 0.004578 | 13.1882 | 121.3989 | -0.013733 | 121.2982 | 121.225 | 121.2387 | -0.068665 | -121.3669 | 121.2433 | 121.3394 | 121.2021 | 42.7505
2586.8281 | 121.4813 | -121.3028 | 0.091553 | 0.036468 | 0.015855 | -0.033936 | 0.037762 | -0.015917 | -0.028822 | -0.022605 | 0.014709 | 0.020593 | 0.083416 | 0.052415 | -0.018794 | 0.0050672 | 0.006116 | -0.009155 | 0.013733 | -0.032043 | -0.009155 | 0.12817 | 0.022888 | 0.027466 | -78.5614 | 0.027466 | -121.3348 | 0.045776 | -107.9956 | -102.6306 | -117.9337 | 121.2708 | -0.07782 | -0.10071 | 121.431 | 121.3303 | 121.3257 | 0.059509 | 0.054931 | -0.032044 | -0.064087 | -0.045777 | 13.3072 | 3.3691 | 18.6722 | 3.4012 | 18.7042 | 0.16022 | 0.022888 | 13.3392 | 121.3806 | 0.045776 | 121.3623 | 121.3165 | 121.3303 | -0.1236 | -121.4264 | 121.2936 | 121.3486 | 121.2936 | 42.7414
2588.5625 | 121.5729 | -121.2799 | 0.068665 | 0.0059509 | 0.010728 | -0.034363 | 0.032849 | -0.014208 | -0.027113 | -0.022819 | 0.008606 | 0.016107 | 0.083416 | 0.067155 | -0.017726 | 0.0067762 | 0.0022708 | -0.018311 | -0.041199 | 0.009155 | 0.050354 | 0.21973 | 0.11444 | 0.11902 | -78.4424 | -0.013733 | -121.3074 | 0.091553 | -107.7301 | -102.3376 | -117.8513 | 121.2891 | -0.10986 | -0.018311 | 121.4996 | 121.3989 | 121.3943 | 0.10986 | 0.10529 | -0.027466 | -0.082398 | 0.022888 | 13.5498 | 3.4286 | 18.9423 | 3.4561 | 18.9697 | 0.21057 | 0.041199 | 13.5773 | 121.3989 | -0.050354 | 121.2936 | 121.2387 | 121.2662 | -0.05951 | -121.376 | 121.3303 | 121.3715 | 121.2616 | 42.8375
2590.3281 | 121.5591 | -121.312 | 0.07782 | 0.044098 | 0.015855 | -0.034363 | 0.036694 | -0.014635 | -0.02989 | -0.022178 | 0.011658 | 0.020166 | 0.084056 | 0.062241 | -0.019222 | 0.0072034 | 0.00056183 | -0.004578 | -0.013733 | -0.009155 | 0.013733 | 0.19226 | 0.036621 | 0.050354 | -78.2822 | 0.022888 | -121.3577 | 0.064087 | -107.634 | -102.2003 | -117.8925 | 121.3028 | -0.091553 | -0.064087 | 121.5042 | 121.3623 | 121.3486 | 0.059509 | 0.045776 | -0.045776 | -0.054932 | -0.013733 | 13.678 | 3.4195 | 19.1116 | 3.4653 | 19.1574 | 0.20142 | 0.022888 | 13.7238 | 121.4218 | -0.004578 | 121.3806 | 121.2982 | 121.3348 | -0.086975 | -121.4355 | 121.3257 | 121.376 | 121.3074 | 43.0298
2592.1094 | 121.5775 | -121.2982 | 0.068665 | 0.01358 | 0.013078 | -0.035859 | 0.034772 | -0.019335 | -0.028608 | -0.02111 | 0.0055542 | 0.018457 | 0.08427 | 0.065659 | -0.019649 | 0.0048536 | 0.0029116 | -0.041199 | -0.013733 | -0.009155 | 0.009155 | 0.12817 | 0.032043 | 0.068665 | -78.1677 | -0.009155 | -121.344 | 0.068665 | -107.4326 | -101.9943 | -117.8238 | 121.2891 | -0.082398 | -0.05951 | 121.4264 | 121.3669 | 121.3303 | 0.07782 | 0.041198 | -0.045776 | -0.07782 | 0 | 13.8657 | 3.4744 | 19.3039 | 3.5202 | 19.3497 | 0.13733 | 0.01831 | 13.9114 | 121.4127 | -0.004578 | 121.3348 | 121.2845 | 121.2891 | -0.07782 | -121.4127 | 121.3074 | 121.3669 | 121.257 | 43.1305
2593.8125 | 121.5179 | -121.3394 | 0.086975 | 0.01358 | 0.012651 | -0.036286 | 0.034344 | -0.021471 | -0.030958 | -0.020256 | 0.0055542 | 0.02038 | 0.084056 | 0.05861 | -0.019863 | 0.0050672 | 0.0012028 | 0 | -0.036621 | -0.004578 | 0.009155 | 0.15106 | 0.068665 | 0.07782 | -78.0853 | 0.027466 | -121.3669 | 0.009155 | -107.3456 | -101.9302 | -117.865 | 121.3348 | -0.1236 | -0.07782 | 121.4905 | 121.4172 | 121.4081 | 0.082398 | 0.073243 | -0.027465 | -0.059509 | -0.07782 | 13.9938 | 3.4744 | 19.4092 | 3.5019 | 19.4366 | 0.15564 | 0.013733 | 14.0213 | 121.376 | -0.032043 | 121.3943 | 121.3028 | 121.3669 | -0.091553 | -121.4539 | 121.3486 | 121.3486 | 121.3394 | 43.2541
2595.5938 | 121.6415 | -121.3211 | 0.073242 | -0.0016786 | 0.014146 | -0.036927 | 0.033276 | -0.018053 | -0.029676 | -0.020042 | 0.0025024 | 0.023584 | 0.086193 | 0.059037 | -0.018367 | 0.0054944 | 0.0054752 | 0 | -0.027466 | 0 | 0.050354 | 0.21515 | 0.11444 | 0.10529 | -77.8976 | 0 | -121.3623 | 0.1236 | -107.103 | -101.6464 | -117.7551 | 121.3211 | -0.10071 | -0.022888 | 121.5363 | 121.4264 | 121.4355 | 0.10529 | 0.11444 | -0.041199 | -0.073242 | 0.050354 | 14.2181 | 3.566 | 19.6747 | 3.6072 | 19.7159 | 0.21515 | 0.050354 | 14.2593 | 121.4859 | -0.027466 | 121.3623 | 121.2936 | 121.3211 | -0.073242 | -121.4355 | 121.3715 | 121.4447 | 121.3211 | 43.4235
2597.3125 | 121.6278 | -121.3165 | 0.068665 | 0.0059509 | 0.013719 | -0.032654 | 0.036053 | -0.016771 | -0.029249 | -0.022605 | -0.00054937 | 0.022943 | 0.083629 | 0.064805 | -0.014308 | 0.0067762 | 0.0024844 | 0 | -0.018311 | 0.009155 | 0.032043 | 0.16022 | 0.041199 | 0.054932 | -77.8885 | 0 | -121.3669 | 0.10529 | -107.0572 | -101.5594 | -117.7231 | 121.3257 | -0.086976 | -0.036622 | 121.4767 | 121.3715 | 121.3577 | 0.045777 | 0.032044 | -0.050354 | -0.068665 | 0.036621 | 14.2593 | 3.5934 | 19.7571 | 3.6438 | 19.8074 | 0.15106 | 0.022888 | 14.3097 | 121.4722 | -0.027466 | 121.3669 | 121.2982 | 121.3165 | -0.05951 | -121.4355 | 121.3486 | 121.4218 | 121.3165 | 43.428
2599.0938 | 121.5042 | -121.3806 | 0.09613 | -0.0016786 | 0.014787 | -0.032441 | 0.037976 | -0.01784 | -0.031172 | -0.024101 | 0.0025024 | 0.024652 | 0.086406 | 0.061814 | -0.02264 | 0.0069898 | -0.00029257 | -0.082397 | 0.018311 | -0.032043 | -0.082397 | 0.036621 | -0.022888 | -0.027466 | -77.9572 | 0.064087 | -121.4218 | -0.045776 | -107.0343 | -101.4816 | -117.8238 | 121.3486 | -0.077819 | -0.17853 | 121.4172 | 121.3531 | 121.3577 | 0.004577 | 0.009155 | -0.041199 | -0.032043 | -0.14191 | 14.3463 | 3.5568 | 19.899 | 3.598 | 19.9402 | 0.068664 | -0.050354 | 14.3875 | 121.376 | 0.050354 | 121.4859 | 121.3989 | 121.4447 | -0.12817 | -121.5179 | 121.2982 | 121.3348 | 121.2982 | 43.4235
2600.8281 | 121.6644 | -121.3257 | 0.064087 | 0.0059509 | 0.010515 | -0.03415 | 0.033703 | -0.019976 | -0.031385 | -0.02111 | 0.0055542 | 0.022089 | 0.083843 | 0.069504 | -0.019008 | 0.0084852 | 0.0046206 | -0.004578 | -0.013733 | -0.004578 | 0.036621 | 0.20599 | 0.10071 | 0.11444 | -77.6138 | -0.018311 | -121.3852 | 0.11902 | -106.7368 | -101.1658 | -117.659 | 121.3211 | -0.07782 | -0.027466 | 121.5317 | 121.4401 | 121.4264 | 0.11902 | 0.10529 | -0.059509 | -0.082398 | 0.054932 | 14.5889 | 3.6667 | 20.1599 | 3.7262 | 20.2194 | 0.21057 | 0.041199 | 14.6484 | 121.5042 | -0.009155 | 121.3669 | 121.312 | 121.3074 | -0.068665 | -121.4493 | 121.3623 | 121.4447 | 121.3211 | 43.7119
2602.6094 | 121.6507 | -121.3623 | 0.07782 | 0.066986 | 0.016069 | -0.030732 | 0.038403 | -0.015703 | -0.029249 | -0.025383 | 0.020813 | 0.024866 | 0.085125 | 0.064805 | -0.01794 | 0.0099806 | 0.0024844 | 0.041199 | 0 | -0.004578 | 0.082397 | 0.21515 | 0.073242 | 0.10529 | -77.5085 | 0.018311 | -121.4081 | 0.10529 | -106.6406 | -101.088 | -117.6544 | 121.3577 | -0.07782 | 0.004577 | 121.5775 | 121.4676 | 121.4355 | 0.10986 | 0.07782 | -0.045776 | -0.059509 | 0.027466 | 14.7217 | 3.7079 | 20.2744 | 3.7537 | 20.3201 | 0.21973 | 0.086975 | 14.7675 | 121.5134 | 0.004578 | 121.4264 | 121.3623 | 121.3806 | -0.082398 | -121.4859 | 121.4447 | 121.4676 | 121.4035 | 43.8538
2604.4062 | 121.6232 | -121.3577 | 0.082397 | 0.036468 | 0.014787 | -0.030945 | 0.036908 | -0.013994 | -0.025404 | -0.022392 | 0.017761 | 0.023798 | 0.087902 | 0.064164 | -0.01559 | 0.0067762 | 0.0071842 | 0.022888 | -0.022888 | -0.004578 | 0.059509 | 0.20142 | 0.073242 | 0.082397 | -77.2934 | 0.013733 | -121.4447 | 0.073242 | -106.4941 | -100.8911 | -117.659 | 121.3531 | -0.10528 | -0.022888 | 121.5591 | 121.4401 | 121.431 | 0.086975 | 0.07782 | -0.086975 | -0.068664 | -0.009155 | 14.8636 | 3.6987 | 20.4666 | 3.7857 | 20.5536 | 0.20599 | 0.064087 | 14.9506 | 121.5179 | -0.01831 | 121.4584 | 121.3348 | 121.3715 | -0.086975 | -121.5271 | 121.4172 | 121.431 | 121.3806 | 44.0643
2606.1406 | 121.6232 | -121.3852 | 0.091553 | 0.028839 | 0.015428 | -0.033295 | 0.035626 | -0.017412 | -0.026045 | -0.023887 | 0.008606 | 0.022729 | 0.087688 | 0.065232 | -0.018581 | 0.0095532 | 0.007825 | -0.050354 | -0.013733 | -0.018311 | -0.004578 | 0.11902 | 0.032043 | 0.050354 | -77.449 | 0.027466 | -121.4218 | 0.050354 | -106.4484 | -100.7492 | -117.6315 | 121.3669 | -0.10529 | -0.096131 | 121.5042 | 121.4355 | 121.4172 | 0.068665 | 0.050354 | -0.036621 | -0.064087 | -0.041199 | 14.9368 | 3.7537 | 20.636 | 3.7903 | 20.6726 | 0.13733 | 0.013733 | 14.9734 | 121.4722 | 0.004578 | 121.4493 | 121.3715 | 121.4127 | -0.10986 | -121.5134 | 121.3806 | 121.4355 | 121.3348 | 43.9362
2607.9219 | 121.5775 | -121.4218 | 0.11444 | 0.0059509 | 0.013078 | -0.0318 | 0.034131 | -0.016558 | -0.030317 | -0.022605 | 0.0025024 | 0.024011 | 0.088115 | 0.059037 | -0.021144 | 0.005708 | 0.0069706 | -0.022888 | -0.009155 | -0.004578 | -0.013733 | 0.11902 | 0.032043 | 0.032043 | -77.2385 | 0.027466 | -121.4264 | -0.022888 | -106.3568 | -100.6302 | -117.659 | 121.4172 | -0.1236 | -0.12817 | 121.5408 | 121.4539 | 121.4539 | 0.036621 | 0.036621 | -0.004578 | -0.086975 | -0.13733 | 15.065 | 3.7628 | 20.7916 | 3.7674 | 20.7962 | 0.1236 | -0.009155 | 15.0696 | 121.4035 | -0.004577 | 121.4539 | 121.4127 | 121.4493 | -0.11902 | -121.5408 | 121.4081 | 121.3989 | 121.3989 | 44.1834
2609.7031 | 121.6003 | -121.3943 | 0.11444 | 0.028839 | 0.015214 | -0.032441 | 0.037549 | -0.015062 | -0.029249 | -0.023887 | 0.0055542 | 0.025507 | 0.088115 | 0.056473 | -0.017513 | 0.005708 | 0.0041934 | -0.009155 | -0.004578 | -0.013733 | -0.018311 | 0.10529 | 0 | 0.013733 | -77.2064 | 0.041199 | -121.463 | 0.013733 | -106.2607 | -100.4471 | -117.6132 | 121.3806 | -0.11902 | -0.13275 | 121.4996 | 121.4081 | 121.3943 | 0.027466 | 0.013733 | -0.068665 | -0.073242 | -0.10071 | 15.1337 | 3.7811 | 20.9473 | 3.8498 | 21.0159 | 0.11902 | -0.004578 | 15.2023 | 121.4767 | 0.009155 | 121.5042 | 121.3898 | 121.4355 | -0.12817 | -121.5775 | 121.376 | 121.4081 | 121.3852 | 44.1879
2611.4844 | 121.5683 | -121.3852 | 0.07782 | 0.02121 | 0.011796 | -0.035004 | 0.037121 | -0.015276 | -0.026899 | -0.02111 | 0.0055542 | 0.025934 | 0.090465 | 0.063737 | -0.015377 | 0.0097668 | 0.0046206 | -0.064087 | 0.013733 | -0.018311 | -0.064087 | 0.068665 | -0.041199 | -0.027466 | -76.9867 | 0.045776 | -121.4355 | 0.068665 | -106.1508 | -100.2045 | -117.5217 | 121.3669 | -0.064087 | -0.14191 | 121.4539 | 121.3577 | 121.344 | -0.009155 | -0.022888 | -0.050354 | -0.032044 | -0.009155 | 15.2344 | 3.8635 | 21.1807 | 3.9139 | 21.2311 | 0.086976 | -0.045776 | 15.2847 | 121.5042 | 0.032044 | 121.4813 | 121.3989 | 121.431 | -0.096131 | -121.5134 | 121.3211 | 121.4539 | 121.3211 | 44.3985
2613.2656 | 121.6873 | -121.3806 | 0.07782 | 0.01358 | 0.012437 | -0.032227 | 0.036267 | -0.01784 | -0.029249 | -0.023674 | 0.0025024 | 0.025507 | 0.087474 | 0.069077 | -0.017513 | 0.010408 | 0.0020572 | -0.036621 | 0.004578 | -0.022888 | 0.004578 | 0.13275 | 0.022888 | 0.036621 | -76.6663 | -0.004578 | -121.4218 | 0.09613 | -106.1188 | -99.9893 | -117.4484 | 121.3577 | -0.073242 | -0.073242 | 121.5134 | 121.4172 | 121.4035 | 0.059509 | 0.045776 | -0.041199 | -0.082398 | 0.01831 | 15.2618 | 3.9322 | 21.3913 | 3.9734 | 21.4325 | 0.15564 | 0.027466 | 15.303 | 121.5179 | 0.027466 | 121.4172 | 121.3852 | 121.376 | -0.10071 | -121.4996 | 121.3852 | 121.4767 | 121.344 | 44.7144
2615.0469 | 121.6232 | -121.431 | 0.10986 | 0.01358 | 0.012864 | -0.03415 | 0.036908 | -0.019335 | -0.02754 | -0.023033 | 0.011658 | 0.051782 | 0.089183 | 0.058182 | -0.019008 | 0.0082716 | 0.027692 | -0.022888 | 0.004578 | -0.018311 | -0.004578 | 0.1236 | 0.018311 | 0.036621 | -76.4603 | 0.018311 | -121.4676 | 0.032043 | -104.8737 | -99.852 | -100.3967 | 121.4127 | -0.10529 | -0.11444 | 121.5546 | 121.4676 | 121.4493 | 0.054932 | 0.036622 | -0.036621 | -0.091552 | -0.07782 | 16.5573 | 21.0342 | 21.579 | 21.0709 | 21.6156 | 0.14191 | 0.013733 | 16.5939 | 121.4996 | 0.022889 | 121.4859 | 121.4355 | 121.4493 | -0.12817 | -121.5775 | 121.4264 | 121.463 | 121.4081 | 44.9707
2616.7656 | 121.5683 | -121.3989 | 0.10529 | 0.0059509 | 0.013719 | -0.035004 | 0.034772 | -0.019762 | -0.027113 | -0.020897 | 0.0055542 | 0.53842 | 0.093883 | 0.057755 | -0.021358 | 0.0089124 | 0.50493 | -0.018311 | -0.036621 | 0.013733 | -0.004578 | 0.15106 | 0.068665 | 0.059509 | -75.1968 | -0.022888 | -121.3943 | -0.036621 | -98.7442 | -99.3988 | -43.6981 | 121.4127 | -0.14191 | -0.10986 | 121.55 | 121.4584 | 121.4676 | 0.045776 | 0.054932 | 0.004578 | -0.12817 | -0.14191 | 22.6547 | 77.7008 | 22.0001 | 77.6962 | 21.9955 | 0.13733 | -0.018311 | 22.6501 | 121.3577 | -0.050354 | 121.3715 | 121.3623 | 121.376 | -0.091553 | -121.4996 | 121.3943 | 121.3623 | 121.3806 | 46.2021
2618.5625 | 121.4859 | -121.3669 | 0.11902 | 0.01358 | 0.014573 | -0.033936 | 0.037121 | -0.016344 | -0.02989 | -0.021751 | -0.00054937 | 0.78729 | 0.097728 | 0.055619 | -0.020076 | 0.0086988 | 0.74611 | -0.068665 | 0.027466 | -0.027466 | -0.10986 | -0.004578 | -0.091553 | -0.050354 | -74.6613 | -0.009155 | -121.3623 | -0.059509 | -94.6426 | -98.7259 | -3.3737 | 121.3394 | -0.091553 | -0.22888 | 121.3623 | 121.3165 | 121.2753 | -0.022888 | -0.064087 | 0.004577 | -0.12817 | -0.17853 | 26.7242 | 117.9932 | 22.641 | 117.9886 | 22.6364 | 0.022888 | -0.082397 | 26.7197 | 121.3028 | 0.054932 | 121.3531 | 121.3943 | 121.3577 | -0.14649 | -121.4813 | 121.257 | 121.3074 | 121.2982 | 46.7056
2620.2812 | 121.4081 | -121.2433 | 0.21057 | 0.0059509 | 0.01436 | -0.0365 | 0.036694 | -0.01848 | -0.028395 | -0.021965 | 0.0025024 | 0.78707 | 0.096233 | 0.052628 | -0.022212 | 0.0078442 | 0.74782 | -0.082397 | 0.009155 | -0.041199 | -0.059509 | 0.07782 | -0.009155 | -0.009155 | -74.5651 | 0.07782 | -121.1975 | 0.004578 | -94.3039 | -98.291 | -2.4857 | 121.2021 | -0.20142 | -0.27008 | 121.3211 | 121.2341 | 121.2341 | 0.032044 | 0.032044 | 0.045776 | -0.13275 | -0.20599 | 26.9394 | 118.7576 | 22.9523 | 118.7119 | 22.9065 | 0.11902 | -0.01831 | 26.8936 | 121.2021 | 0.050354 | 121.2753 | 121.2524 | 121.3211 | -0.25177 | -121.4081 | 121.1838 | 121.2479 | 121.1609 | 46.6782
2622.0625 | 115.448 | -111.4197 | 4.1382 | 0.036468 | 0.01671 | -0.032013 | 0.03883 | -0.014849 | -0.02989 | -0.022605 | 0.020813 | 0.75012 | 0.092815 | 0.051133 | -0.016017 | 0.0067762 | 0.70509 | -0.027466 | 0.004578 | -0.032043 | -0.041199 | 0.11902 | 0.036621 | 0.032043 | -67.3645 | 4.1061 | -111.5433 | 3.8361 | -85.6064 | -89.5935 | 1.561 | 111.3876 | -4.1336 | -4.1794 | 111.5387 | 111.4517 | 111.4563 | 0.064086 | 0.068664 | -0.1236 | -0.032044 | -0.30212 | 25.8133 | 112.9807 | 21.8262 | 113.1042 | 21.9498 | 0.15106 | -0.009156 | 25.9369 | 115.3793 | 0.036621 | 115.6494 | 111.4243 | 115.5258 | -4.1702 | -115.6815 | 111.3785 | 115.2557 | 111.3922 | 44.0552
2623.8438 | 121.0281 | -120.7993 | 0.073242 | 0.0059509 | 0.013505 | -0.030304 | 0.034131 | -0.019976 | -0.032026 | -0.023246 | 0.0025024 | 0.77639 | 0.09431 | 0.056046 | -0.018581 | 0.0084852 | 0.73649 | -0.009155 | -0.032043 | 0.018311 | 0.041199 | 0.21515 | 0.11444 | 0.10071 | -73.732 | -0.064087 | -120.7489 | 0.027466 | -93.512 | -97.3251 | -1.6479 | 120.8176 | -0.10529 | -0.032043 | 121.0144 | 120.9 | 120.9137 | 0.082397 | 0.09613 | 0.050354 | -0.13733 | -0.045776 | 27.2873 | 119.1513 | 23.4741 | 119.101 | 23.4238 | 0.19684 | 0.022888 | 27.2369 | 120.7764 | -0.050354 | 120.6848 | 120.7672 | 120.7352 | -0.054931 | -120.8221 | 120.8405 | 120.8267 | 120.7901 | 47.0673
2625.6406 | 121.1838 | -120.8817 | 0.07782 | 0.01358 | 0.012651 | -0.033295 | 0.034344 | -0.022967 | -0.031172 | -0.022605 | 0.008606 | 0.77639 | 0.097515 | 0.053055 | -0.018154 | 0.0097668 | 0.73393 | -0.018311 | -0.045776 | 0.013733 | 0.032043 | 0.21973 | 0.10529 | 0.11444 | -73.6542 | -0.073242 | -120.8496 | 0.050354 | -93.4387 | -96.9818 | -1.2131 | 120.8954 | -0.1236 | -0.045777 | 121.1014 | 120.9961 | 120.9869 | 0.10071 | 0.091553 | 0.032044 | -0.15106 | -0.027466 | 27.4429 | 119.6686 | 23.8998 | 119.6365 | 23.8678 | 0.20599 | 0.01831 | 27.4109 | 120.9 | -0.059509 | 120.7764 | 120.8359 | 120.8084 | -0.064087 | -120.9274 | 120.9137 | 120.932 | 120.8633 | 47.2275
2627.3594 | 121.2341 | -120.9503 | 0.082397 | 0.0059509 | 0.011155 | -0.035431 | 0.033276 | -0.019121 | -0.029463 | -0.023674 | 0.0055542 | 0.77853 | 0.096019 | 0.054764 | -0.018581 | 0.010194 | 0.74055 | -0.009155 | -0.032043 | 0 | 0.022888 | 0.16937 | 0.082397 | 0.091553 | -73.6542 | -0.068665 | -120.9137 | 0.022888 | -93.3334 | -97.2244 | -0.23804 | 120.9503 | -0.11444 | -0.059509 | 121.1197 | 121.0419 | 121.0327 | 0.091553 | 0.082397 | 0.036621 | -0.15106 | -0.059509 | 27.6169 | 120.7123 | 23.7259 | 120.6757 | 23.6893 | 0.16937 | 0.022888 | 27.5803 | 120.9366 | -0.032043 | 120.845 | 120.9183 | 120.8817 | -0.082397 | -120.9961 | 120.9732 | 120.9732 | 120.9412 | 47.2961
2629.1406 | 121.2753 | -120.9457 | 0.073242 | 0.01358 | 0.015428 | -0.033295 | 0.035412 | -0.016558 | -0.027967 | -0.022178 | 0.0025024 | 0.56298 | 0.09666 | 0.27736 | -0.01559 | 0.010194 | 0.735 | 0.009155 | -0.027466 | 0.004578 | 0.027466 | 0.16479 | 0.050354 | 0.059509 | -73.7091 | -0.064087 | -120.9457 | 0.013733 | -93.2968 | -97.1695 | -0.14191 | 120.9503 | -0.10071 | -0.045776 | 121.1105 | 121.0052 | 120.9961 | 0.054931 | 0.045776 | 0 | -0.13733 | -0.059509 | 27.6489 | 120.8038 | 23.7762 | 120.8038 | 23.7762 | 0.16022 | 0.022888 | 27.6489 | 120.9595 | -0.032044 | 120.8817 | 120.9183 | 120.8817 | -0.068664 | -121.019 | 120.9732 | 120.9595 | 120.9549 | 47.2366
2630.8594 | 121.1929 | -121.0144 | 0.11444 | 0.01358 | 0.014573 | -0.032654 | 0.037121 | -0.014635 | -0.028181 | -0.023246 | 0.0025024 | 0.54141 | 0.097942 | 0.28847 | -0.01559 | 0.010621 | 0.73158 | -0.07782 | -0.004578 | -0.036621 | -0.09613 | 0.032043 | -0.054932 | -0.050354 | -73.7274 | -0.032043 | -121.0373 | -0.09613 | -93.3197 | -97.2427 | -0.2243 | 120.9778 | -0.11902 | -0.21057 | 121.0464 | 120.9641 | 120.9595 | -0.013733 | -0.018311 | -0.022888 | -0.14648 | -0.21057 | 27.6947 | 120.7901 | 23.7717 | 120.813 | 23.7946 | 0.068664 | -0.059509 | 27.7176 | 120.9412 | 0.032043 | 121.0052 | 121.0098 | 120.9824 | -0.15106 | -121.1517 | 120.9183 | 120.9183 | 120.9366 | 47.287
2632.6406 | 121.2845 | -121.0052 | 0.09613 | 0.059357 | 0.014573 | -0.033295 | 0.03883 | -0.012926 | -0.025404 | -0.020469 | 0.023865 | 0.5241 | 0.10008 | 0.30577 | -0.017299 | 0.0097668 | 0.73115 | 0.027466 | -0.004578 | -0.032043 | 0.068665 | 0.2243 | 0.073242 | 0.091553 | -73.5352 | -0.018311 | -121.0556 | -0.027466 | -93.187 | -96.9955 | -0.16022 | 120.9732 | -0.10071 | -0.027465 | 121.2296 | 121.0968 | 121.0785 | 0.1236 | 0.10529 | -0.050354 | -0.11444 | -0.1236 | 27.8183 | 120.845 | 24.0097 | 120.8954 | 24.0601 | 0.25635 | 0.10071 | 27.8687 | 121.0281 | 0.027465 | 121.0373 | 121.0007 | 120.9869 | -0.12817 | -121.1517 | 121.0739 | 120.9778 | 121.0327 | 47.4701
2634.4219 | 121.3028 | -121.0281 | 0.07782 | 0.082245 | 0.017778 | -0.02945 | 0.037335 | -0.020403 | -0.026899 | -0.019188 | 0.03302 | 0.51705 | 0.10286 | 0.31068 | -0.016231 | 0.0095532 | 0.72004 | 0.032043 | 0.009155 | -0.004578 | 0.073242 | 0.2243 | 0.091553 | 0.10529 | -73.4344 | -0.032043 | -121.0739 | 0 | -93.0862 | -96.9589 | -0.14191 | 121.0236 | -0.068665 | -0.004578 | 121.2524 | 121.1334 | 121.1197 | 0.10986 | 0.096131 | -0.045777 | -0.10986 | -0.07782 | 27.9419 | 120.8862 | 24.0692 | 120.932 | 24.115 | 0.22888 | 0.07782 | 27.9877 | 121.0739 | 0.013733 | 121.0419 | 121.0373 | 120.9961 | -0.082398 | -121.1517 | 121.1014 | 121.0281 | 121.0602 | 47.5937
2636.1719 | 121.3623 | -121.0602 | 0.082397 | 0.01358 | 0.015855 | -0.033509 | 0.037762 | -0.019335 | -0.028608 | -0.023674 | 0.042175 | 0.51278 | 0.10521 | 0.31346 | -0.016658 | 0.0097668 | 0.7194 | 0.018311 | -0.027466 | 0.004578 | 0.064087 | 0.24261 | 0.11444 | 0.13733 | -73.3063 | 0.004578 | -121.1014 | 0.022888 | -92.9718 | -96.3821 | -0.09613 | 121.0648 | -0.10986 | -0.01831 | 121.3028 | 121.1975 | 121.1746 | 0.13275 | 0.10986 | -0.041198 | -0.077819 | -0.059509 | 28.0884 | 120.9641 | 24.678 | 121.0052 | 24.7192 | 0.23804 | 0.059509 | 28.1296 | 121.1243 | -0.032044 | 121.106 | 121.0327 | 121.0648 | -0.077819 | -121.1838 | 121.1243 | 121.0831 | 121.0785 | 47.7539
2637.9531 | 121.3623 | -121.0602 | 0.082397 | 0.11276 | 0.016496 | -0.032227 | 0.036267 | -0.013781 | -0.026899 | -0.020042 | 0.03302 | 0.50787 | 0.10093 | 0.31047 | -0.016658 | 0.010621 | 0.71727 | 0.059509 | 0.013733 | -0.045776 | 0.10071 | 0.23804 | 0.091553 | 0.11444 | -73.2101 | -0.004578 | -121.0693 | 0.018311 | -92.8482 | -96.1349 | -0.11444 | 121.0144 | -0.068664 | 0.018311 | 121.2982 | 121.1746 | 121.1517 | 0.16022 | 0.13733 | -0.009155 | -0.086975 | -0.064086 | 28.212 | 120.9457 | 24.9252 | 120.9549 | 24.9344 | 0.28381 | 0.14648 | 28.2211 | 121.0876 | 0.059509 | 121.0648 | 121.0739 | 121.0556 | -0.12817 | -121.1517 | 121.1609 | 121.0785 | 121.1197 | 47.85
2639.7344 | 121.3806 | -121.1197 | 0.068665 | 0.0059509 | 0.012864 | -0.034577 | 0.036267 | -0.01848 | -0.028608 | -0.024528 | -0.00054937 | 0.50125 | 0.099437 | 0.31453 | -0.021358 | 0.01233 | 0.7147 | -0.032043 | -0.027466 | -0.004578 | 0.009155 | 0.14648 | 0.064087 | 0.073242 | -73.2422 | -0.041199 | -121.0785 | -0.004578 | -92.6971 | -96.2311 | -0.10986 | 121.1151 | -0.096131 | -0.05951 | 121.2662 | 121.1929 | 121.1838 | 0.07782 | 0.068665 | 0.041199 | -0.10986 | -0.073243 | 28.4225 | 121.0098 | 24.8886 | 120.9686 | 24.8474 | 0.15106 | 0.013733 | 28.3813 | 121.0739 | -0.022888 | 121.0373 | 121.0922 | 121.0785 | -0.073243 | -121.1472 | 121.1288 | 121.1151 | 121.0876 | 47.8775
2641.5156 | 121.1288 | -120.6665 | 0.49896 | 0.0059509 | 0.015641 | -0.03415 | 0.035626 | -0.01784 | -0.03224 | -0.022178 | 0.0055542 | 0.49676 | 0.097087 | 0.31197 | -0.02264 | 0.0099806 | 0.70573 | -0.050354 | -0.018311 | -0.013733 | -0.036621 | 0.082397 | 0 | 0.018311 | -72.8394 | 0.36621 | -120.5795 | 0.27924 | -92.308 | -95.5444 | 0.17853 | 120.6528 | -0.51727 | -0.53558 | 120.7489 | 120.6848 | 120.6665 | 0.032044 | 0.013733 | 0.086975 | -0.13275 | -0.21973 | 28.3585 | 120.845 | 25.1221 | 120.7581 | 25.0351 | 0.09613 | -0.022888 | 28.2715 | 120.8588 | -0.004578 | 120.9457 | 120.6482 | 121.0327 | -0.5127 | -121.0785 | 120.6299 | 120.9457 | 120.6162 | 47.8271
2643.3125 | 121.1746 | -120.8954 | 0.2655 | 0.02121 | 0.014146 | -0.032441 | 0.03648 | -0.019549 | -0.029463 | -0.022605 | 0.0025024 | 0.49612 | 0.096447 | 0.30022 | -0.019008 | 0.012544 | 0.70787 | -0.022888 | 0.009155 | -0.013733 | -0.036621 | 0.086975 | -0.032043 | -0.009155 | -72.345 | 0.15106 | -120.8862 | 0.068665 | -92.3767 | -93.8416 | -0.041199 | 120.8817 | -0.25635 | -0.30212 | 120.9824 | 120.8862 | 120.8633 | 0.004578 | -0.01831 | 0.009156 | -0.11444 | -0.19684 | 28.5187 | 120.8542 | 27.0538 | 120.845 | 27.0447 | 0.10071 | -0.022888 | 28.5095 | 120.9549 | 0.022888 | 121.0373 | 120.9045 | 121.0464 | -0.27924 | -121.1517 | 120.8588 | 120.9641 | 120.8725 | 48.5504
2645.0938 | 121.2753 | -120.7718 | 0.27924 | 0.01358 | 0.011796 | -0.036072 | 0.034344 | -0.018908 | -0.032026 | -0.024955 | 0.0025024 | 0.49099 | 0.099651 | 0.30663 | -0.019222 | 0.013826 | 0.7036 | 0 | -0.036621 | 0.027466 | 0.068665 | 0.25177 | 0.11902 | 0.09613 | -72.2488 | 0.16937 | -120.7672 | 0.23804 | -92.0242 | -94.5419 | 0.14191 | 120.7993 | -0.31586 | -0.21057 | 121.0236 | 120.8679 | 120.8908 | 0.068664 | 0.091553 | 0.004578 | -0.10986 | -0.041199 | 28.7476 | 120.9137 | 26.2299 | 120.9091 | 26.2253 | 0.2243 | 0.041199 | 28.743 | 121.0052 | -0.064087 | 120.9366 | 120.7352 | 120.9412 | -0.25177 | -121.0464 | 120.8405 | 121.0098 | 120.7718 | 48.5229
2646.875 | 121.0831 | -120.2545 | 0.68207 | 0.074615 | 0.016923 | -0.030945 | 0.037976 | -0.017412 | -0.028822 | -0.021324 | 0.029968 | 0.49056 | 0.10221 | 0.31111 | -0.02029 | 0.0089124 | 0.69612 | 0.004578 | 0.041199 | -0.041199 | -0.018311 | 0.12817 | 0.027466 | 0.045776 | -72.0886 | 0.57678 | -120.3094 | 0.5127 | -91.5894 | -94.5648 | 0.45319 | 120.2133 | -0.64087 | -0.70038 | 120.3827 | 120.3003 | 120.282 | 0.086975 | 0.068665 | -0.054931 | -0.10529 | -0.16937 | 28.6652 | 120.7077 | 25.6897 | 120.7626 | 25.7446 | 0.16937 | 0.022888 | 28.7201 | 120.8221 | 0.082398 | 120.8862 | 120.2957 | 120.8313 | -0.72327 | -120.9915 | 120.2362 | 120.7672 | 120.2591 | 48.1659
2648.6719 | 121.3211 | -121.0739 | 0.082397 | 0.01358 | 0.013719 | -0.032441 | 0.035626 | -0.023821 | -0.027967 | -0.022392 | 0.011658 | 0.48373 | 0.10221 | 0.31047 | -0.019649 | 0.014253 | 0.69954 | -0.045776 | -0.027466 | -0.022888 | 0.004578 | 0.16022 | 0.054932 | 0.082397 | -69.4611 | -0.07782 | -121.0693 | -0.027466 | -91.333 | -92.9626 | -0.10986 | 121.051 | -0.10986 | -0.077819 | 121.2341 | 121.1563 | 121.1288 | 0.10528 | 0.07782 | 0.004578 | -0.16022 | -0.10986 | 29.7409 | 120.9641 | 28.1113 | 120.9595 | 28.1067 | 0.1831 | 0.027466 | 29.7363 | 121.0419 | -0.004578 | 120.9915 | 121.0464 | 120.9961 | -0.10528 | -121.1517 | 121.0785 | 121.0464 | 121.0281 | 51.6129
2650.3906 | 121.2204 | -121.17 | 0.086975 | -0.0016786 | 0.015641 | -0.033082 | 0.039044 | -0.01784 | -0.029036 | -0.023033 | 0.0025024 | 0.48757 | 0.10264 | 0.30577 | -0.016017 | 0.013826 | 0.6974 | -0.054932 | 0.004578 | -0.027466 | -0.07782 | 0.041199 | -0.059509 | -0.041199 | -69.3466 | -0.032043 | -121.0922 | -0.1236 | -91.3193 | -92.5095 | -0.22888 | 121.1426 | -0.082397 | -0.16479 | 121.2112 | 121.1288 | 121.1105 | -0.013733 | -0.032043 | 0.07782 | -0.11902 | -0.21057 | 29.8508 | 120.9412 | 28.6606 | 120.8633 | 28.5828 | 0.068665 | -0.050354 | 29.7729 | 120.9686 | 0.032044 | 121.0602 | 121.1746 | 121.138 | -0.11444 | -121.1792 | 121.0922 | 121.0464 | 121.1151 | 51.8234
2652.1875 | 121.3303 | -121.1334 | 0.10071 | 0.051727 | 0.01436 | -0.031586 | 0.039898 | -0.019976 | -0.029036 | -0.021965 | 0.023865 | 0.49142 | 0.10221 | 0.3109 | -0.019435 | 0.023652 | 0.68886 | -0.027466 | 0.009155 | -0.045776 | -0.013733 | 0.11902 | 0.022888 | 0.022888 | -63.0753 | -0.009155 | -121.1243 | -0.036621 | -91.1087 | -91.1636 | -0.14648 | 121.0876 | -0.091553 | -0.11444 | 121.2524 | 121.1563 | 121.1563 | 0.068664 | 0.068664 | 0.009155 | -0.10986 | -0.13733 | 30.0247 | 120.9869 | 29.9698 | 120.9778 | 29.9606 | 0.16479 | 0.032043 | 30.0156 | 121.0876 | 0.054931 | 121.1151 | 121.1426 | 121.1243 | -0.14648 | -121.225 | 121.1197 | 121.0968 | 121.106 | 58.0582
2653.9844 | 121.3806 | -121.1105 | 0.050354 | 0.097504 | 0.01436 | -0.029877 | 0.036053 | -0.013994 | -0.026045 | -0.021537 | 0.03302 | 0.535 | 0.10948 | 0.35042 | -0.015163 | 0.090944 | 0.68544 | 0.054932 | 0.022888 | -0.041199 | 0.09613 | 0.23346 | 0.10529 | 0.09613 | -41.4001 | -0.041199 | -121.1105 | -0.009155 | -89.8041 | -0.14191 | -0.11902 | 121.0693 | -0.027466 | 0.045776 | 121.344 | 121.2067 | 121.2158 | 0.13733 | 0.14649 | 0 | -0.091553 | -0.059509 | 31.3065 | 120.9915 | 120.9686 | 120.9915 | 120.9686 | 0.27466 | 0.13733 | 31.3065 | 121.1014 | 0.064087 | 121.0693 | 121.1334 | 121.0693 | -0.091553 | -121.1609 | 121.2067 | 121.1014 | 121.1655 | 79.7104
2655.7031 | 121.3989 | -121.1151 | 0.073242 | 0.0059509 | 0.013719 | -0.036072 | 0.033063 | -0.021044 | -0.031172 | -0.023246 | 0.008606 | 0.56832 | 0.16523 | 0.36559 | -0.021144 | 0.089448 | 0.68351 | -0.013733 | -0.036621 | -0.013733 | 0.041199 | 0.1831 | 0.082397 | 0.073242 | -39.7568 | -0.050354 | -121.0876 | -0.041199 | -0.041199 | -0.13275 | -0.16022 | 121.1014 | -0.10986 | -0.032043 | 121.2982 | 121.1884 | 121.1975 | 0.086975 | 0.09613 | 0.027466 | -0.1236 | -0.11444 | 121.0739 | 120.9549 | 120.9824 | 120.9274 | 120.9549 | 0.19684 | 0.054932 | 121.0464 | 121.0464 | -0.022888 | 121.0373 | 121.0785 | 121.0648 | -0.086975 | -121.1609 | 121.1563 | 121.0739 | 121.1014 | 81.3583
2657.4844 | 121.3623 | -121.1563 | 0.068665 | -0.0016786 | 0.015001 | -0.035645 | 0.036267 | -0.019762 | -0.024549 | -0.023246 | 0.0055542 | 0.56683 | 0.16502 | 0.35939 | -0.014736 | 0.091798 | 0.67625 | -0.082397 | 0 | -0.032043 | -0.064087 | 0.059509 | -0.064087 | -0.018311 | -39.8758 | -0.059509 | -121.1288 | -0.086975 | -0.091553 | -0.19684 | -0.1831 | 121.1243 | -0.068665 | -0.13275 | 121.2158 | 121.138 | 121.0922 | 0.013732 | -0.032044 | 0.027466 | -0.12817 | -0.15564 | 121.0648 | 120.9732 | 120.9595 | 120.9457 | 120.932 | 0.091552 | -0.032044 | 121.0373 | 121.0419 | 0.032043 | 121.0693 | 121.1563 | 121.0968 | -0.10071 | -121.1975 | 121.0922 | 121.0693 | 121.0739 | 81.2805
2659.2656 | 121.4127 | -121.1426 | 0.054932 | 0.11276 | 0.016923 | -0.032013 | 0.038617 | -0.012713 | -0.028181 | -0.019188 | 0.036072 | 0.56683 | 0.16758 | 0.36025 | -0.017299 | 0.090516 | 0.67732 | 0.045776 | 0.004578 | -0.050354 | 0.091553 | 0.21973 | 0.10071 | 0.10071 | -40.0955 | -0.018311 | -121.1655 | -0.018311 | -0.018311 | -0.12817 | -0.12817 | 121.0922 | -0.050354 | 0.036621 | 121.3623 | 121.2433 | 121.2433 | 0.15106 | 0.15106 | -0.022888 | -0.073243 | -0.073243 | 121.1243 | 121.0144 | 121.0144 | 121.0373 | 121.0373 | 0.27008 | 0.14191 | 121.1472 | 121.1472 | 0.054932 | 121.1472 | 121.1472 | 121.1243 | -0.10529 | -121.2204 | 121.2341 | 121.1243 | 121.1884 | 81.0471
2661.0625 | 121.4264 | -121.1517 | 0.050354 | 0.01358 | 0.015001 | -0.033936 | 0.033917 | -0.016344 | -0.026045 | -0.022605 | 0.03302 | 0.56661 | 0.16972 | 0.3658 | -0.013668 | 0.093507 | 0.67689 | 0.022888 | -0.045776 | 0.009155 | 0.10071 | 0.21515 | 0.09613 | 0.12817 | -39.8758 | -0.009155 | -121.1929 | -0.009155 | -0.013733 | -0.1236 | -0.11902 | 121.1609 | -0.09613 | 0.050354 | 121.3669 | 121.2799 | 121.2479 | 0.11902 | 0.086975 | -0.041199 | -0.059509 | -0.059509 | 121.138 | 121.0327 | 121.0281 | 121.0739 | 121.0693 | 0.20599 | 0.091553 | 121.1792 | 121.1838 | -0.054931 | 121.1838 | 121.106 | 121.1426 | -0.041199 | -121.2433 | 121.2524 | 121.1426 | 121.1746 | 81.2759
2662.7812 | 121.4264 | -121.1746 | 0.050354 | -0.0016786 | 0.013292 | -0.035218 | 0.035199 | -0.020403 | -0.031599 | -0.023033 | 0.0025024 | -0.064429 | -0.0016064 | 0.035752 | -0.020717 | -0.010741 | -0.013751 | -0.013733 | -0.036621 | -0.009155 | 0.045776 | 0.21057 | 0.10529 | 0.09613 | -0.11902 | -0.17853 | -0.2655 | -0.10986 | 0.004578 | -0.082397 | 0.018311 | 121.1655 | -0.086975 | -0.004578 | 121.3852 | 121.2708 | 121.2799 | 0.10528 | 0.11444 | 120.9091 | -0.22888 | -0.16022 | 121.1792 | 121.1929 | 121.0922 | 0.28381 | 0.18311 | 0.21973 | 0.054931 | 0.27008 | 0.15564 | -0.027466 | 0.086975 | 121.138 | 120.9961 | -0.059509 | -0.31586 | 121.2204 | 121.0648 | 121.1609 | 121.0556
2664.5781 | 121.3898 | -121.3165 | 0.086975 | -0.0016786 | 0.013933 | -0.035645 | 0.035626 | -0.016771 | -0.030317 | -0.020469 | -0.00054937 | -0.062292 | 0.0020252 | 0.044938 | -0.019863 | -0.0092456 | -0.0099056 | -0.091553 | -0.009155 | -0.027466 | -0.091553 | 0.041199 | -0.041199 | -0.022888 | -0.16937 | -0.032043 | -0.21973 | -0.13275 | -0.050354 | -0.1236 | -0.009155 | 121.2891 | -0.09613 | -0.17853 | 121.3577 | 121.2936 | 121.2753 | 0.004578 | -0.013733 | 121.0968 | -0.11902 | -0.21973 | 121.2662 | 121.3074 | 121.1929 | 0.21057 | 0.096131 | 0.068665 | -0.064087 | 0.16937 | 0.086976 | 0.018311 | 0.18768 | 121.3074 | 121.2845 | -0.11444 | -0.3067 | 121.225 | 121.1838 | 121.225 | 121.1472
2666.2969 | 121.582 | -121.2799 | 0.073242 | 0.02121 | 0.012651 | -0.035004 | 0.033063 | -0.016131 | -0.027967 | -0.020897 | 0.0025024 | -0.062933 | 0.00031615 | 0.043229 | -0.020931 | -0.0098864 | -0.011828 | -0.013733 | -0.059509 | -0.004578 | 0.054932 | 0.22888 | 0.11902 | 0.11444 | 0.004578 | -0.073242 | -0.14648 | 0 | 0.13275 | 0.045776 | 0.11902 | 121.2753 | -0.13275 | -0.01831 | 121.5088 | 121.3943 | 121.3989 | 0.11902 | 0.1236 | 121.1334 | -0.14648 | -0.073242 | 121.4127 | 121.3989 | 121.3257 | 0.2655 | 0.19226 | 0.23346 | 0.05951 | 0.27924 | 0.14648 | -0.054931 | 0.073242 | 121.2204 | 121.2067 | -0.07782 | -0.21973 | 121.3348 | 121.2799 | 121.2662 | 121.2845
2668.1094 | 121.5088 | -121.3165 | 0.064087 | 0.01358 | 0.018205 | -0.034363 | 0.036694 | -0.017412 | -0.030958 | -0.022819 | 0.008606 | -0.061224 | -0.0013928 | 0.032334 | -0.019649 | -0.012023 | -0.013751 | -0.018311 | -0.004578 | -0.036621 | -0.018311 | 0.10071 | 0.018311 | 0.018311 | -0.045776 | -0.018311 | -0.15106 | -0.027466 | 0.041199 | -0.045776 | 0.086975 | 121.2799 | -0.068665 | -0.082398 | 121.4172 | 121.3348 | 121.3348 | 0.054932 | 0.054932 | 121.1655 | -0.082398 | -0.091553 | 121.3577 | 121.4035 | 121.2708 | 0.23804 | 0.10529 | 0.13733 | 0.01831 | 0.19226 | 0.1236 | 0.032043 | 0.13275 | 121.312 | 121.2982 | -0.10071 | -0.21515 | 121.2982 | 121.2891 | 121.2982 | 121.2708
2669.8281 | 121.5546 | -121.3394 | 0.059509 | 0.02121 | 0.015214 | -0.033936 | 0.037549 | -0.012285 | -0.027967 | -0.023674 | 0.0055542 | -0.061651 | 0.001598 | 0.040879 | -0.014949 | -0.009032 | -0.012896 | -0.009155 | -0.054932 | -0.004578 | 0.045776 | 0.19684 | 0.068665 | 0.07782 | 0.032043 | -0.050354 | -0.14191 | 0.022888 | 0.09613 | -0.004578 | 0.11902 | 121.3348 | -0.11444 | -0.013733 | 121.5363 | 121.4172 | 121.4081 | 0.082398 | 0.073243 | 121.1975 | -0.10986 | -0.036621 | 121.4355 | 121.4584 | 121.3348 | 0.26093 | 0.13733 | 0.20142 | 0.050354 | 0.23804 | 0.16479 | -0.050354 | 0.091553 | 121.2845 | 121.2891 | -0.064087 | -0.20142 | 121.3852 | 121.3623 | 121.3303 | 121.3715
2671.6094 | 121.5134 | -121.3211 | 0.09613 | 0.028839 | 0.01436 | -0.036286 | 0.03584 | -0.01549 | -0.027967 | -0.021751 | 0.014709 | -0.060797 | 0.001598 | 0.036393 | -0.017299 | -0.013091 | -0.010119 | -0.045776 | 0.009155 | -0.045776 | -0.054932 | 0.068665 | 0 | 0.009155 | -0.073242 | 0.013733 | -0.13275 | -0.036621 | 0.045776 | -0.050354 | 0.082397 | 121.2753 | -0.086975 | -0.15106 | 121.3898 | 121.3303 | 121.3211 | 0.054931 | 0.045776 | 121.1884 | -0.082397 | -0.13275 | 121.3669 | 121.4035 | 121.2708 | 0.21515 | 0.082397 | 0.11444 | -0.009156 | 0.17853 | 0.09613 | 0.054931 | 0.14648 | 121.3303 | 121.3348 | -0.14191 | -0.22888 | 121.2662 | 121.2845 | 121.2753 | 121.2479
2673.4062 | 121.4813 | -121.3806 | 0.091553 | 0.0059509 | 0.015428 | -0.032654 | 0.037762 | -0.021258 | -0.029036 | -0.023887 | 0.0055542 | -0.063147 | 0.0011708 | 0.037461 | -0.016017 | -0.0101 | -0.013965 | -0.045776 | -0.004578 | -0.027466 | -0.054932 | 0.068665 | -0.045776 | -0.041199 | -0.10071 | -0.013733 | -0.13733 | -0.068665 | 0 | -0.11444 | 0.054932 | 121.3531 | -0.096131 | -0.14649 | 121.4493 | 121.3394 | 121.3348 | -0.013733 | -0.01831 | 121.2433 | -0.10529 | -0.16022 | 121.3806 | 121.4355 | 121.2662 | 0.19226 | 0.022888 | 0.096131 | -0.027466 | 0.13733 | 0.068664 | 0.022888 | 0.1236 | 121.376 | 121.3669 | -0.11902 | -0.22888 | 121.3257 | 121.312 | 121.3348 | 121.2799
2675.1406 | 121.4813 | -121.3806 | 0.07782 | 0.01358 | 0.017778 | -0.034791 | 0.037549 | -0.018267 | -0.030745 | -0.023246 | 0.0025024 | -0.061224 | -0.00053825 | 0.033829 | -0.018367 | -0.0101 | -0.0099056 | -0.086975 | 0.009155 | -0.032043 | -0.10986 | 0.009155 | -0.086975 | -0.050354 | -0.13733 | 0 | -0.15564 | -0.07782 | -0.027466 | -0.12817 | 0.045776 | 121.3486 | -0.068665 | -0.18768 | 121.3898 | 121.3303 | 121.2936 | -0.018311 | -0.054932 | 121.225 | -0.07782 | -0.15564 | 121.3531 | 121.4264 | 121.2524 | 0.20142 | 0.027466 | 0.041198 | -0.07782 | 0.12817 | 0.07782 | 0.041198 | 0.15564 | 121.3898 | 121.3806 | -0.10986 | -0.23346 | 121.2708 | 121.3028 | 121.2936 | 121.2433
2676.9375 | 121.5363 | -121.4218 | 0.091553 | -0.0016786 | 0.014787 | -0.033295 | 0.034558 | -0.022967 | -0.02989 | -0.022819 | 0.011658 | -0.061438 | 0.00074335 | 0.041947 | -0.02029 | -0.010527 | -0.012896 | -0.10986 | 0.004578 | -0.045776 | -0.10529 | 0.045776 | -0.018311 | -0.018311 | -0.10529 | 0.041199 | -0.13275 | -0.073242 | 0.018311 | -0.054932 | 0.064087 | 121.376 | -0.086975 | -0.19684 | 121.4676 | 121.4035 | 121.4035 | 0.027465 | 0.027465 | 121.2891 | -0.050354 | -0.16479 | 121.4401 | 121.4859 | 121.3669 | 0.19684 | 0.077819 | 0.091552 | -0.05951 | 0.15106 | 0.059509 | 0.050354 | 0.17395 | 121.4264 | 121.463 | -0.13733 | -0.2243 | 121.3165 | 121.3486 | 121.312 | 121.3165
2678.7344 | 121.6507 | -121.344 | 0.07782 | 0.0059509 | 0.011796 | -0.032654 | 0.036694 | -0.016131 | -0.02754 | -0.025596 | 0.0025024 | -0.065497 | -0.0013928 | 0.039597 | -0.014949 | -0.006682 | -0.017169 | -0.064087 | -0.022888 | -0.027466 | -0.032043 | 0.11444 | -0.009155 | 0.013733 | -0.013733 | -0.027466 | -0.1236 | 0.050354 | 0.10529 | 0.027466 | 0.16022 | 121.3165 | -0.10071 | -0.10986 | 121.4584 | 121.3577 | 121.3348 | 0.041199 | 0.018311 | 121.2204 | -0.10529 | -0.027466 | 121.4493 | 121.5042 | 121.3715 | 0.28381 | 0.15106 | 0.14191 | -0.004577 | 0.22888 | 0.17395 | 0.004578 | 0.09613 | 121.3211 | 121.3165 | -0.10529 | -0.20142 | 121.312 | 121.3943 | 121.2799 | 121.3303
2680.5156 | 121.6919 | -121.4127 | 0.073242 | 0.0059509 | 0.013933 | -0.03415 | 0.036908 | -0.018053 | -0.028608 | -0.022605 | 0.014709 | -0.063574 | 0.00031615 | 0.040879 | -0.014736 | -0.0079638 | -0.015246 | 0.013733 | -0.018311 | 0 | 0.054932 | 0.19226 | 0.073242 | 0.082397 | 0.059509 | -0.027466 | -0.1236 | 0.068665 | 0.14191 | 0.054932 | 0.16479 | 121.4127 | -0.091553 | -0.01831 | 121.6049 | 121.4951 | 121.4859 | 0.082397 | 0.073242 | 121.2891 | -0.10071 | -0.004577 | 121.5546 | 121.5775 | 121.4676 | 0.28839 | 0.17853 | 0.19226 | 0.054932 | 0.2655 | 0.19226 | -0.018311 | 0.09613 | 121.3943 | 121.3852 | -0.073242 | -0.19684 | 121.4676 | 121.4813 | 121.4264 | 121.4722
2682.25 | 121.6599 | -121.431 | 0.036621 | 0.028839 | 0.013933 | -0.033082 | 0.03648 | -0.019335 | -0.02754 | -0.024101 | 0.008606 | -0.064002 | 0.00031615 | 0.03917 | -0.019222 | -0.0081774 | -0.016101 | -0.027466 | -0.032043 | -0.009155 | 0.004578 | 0.15106 | 0.022888 | 0.050354 | -0.009155 | -0.013733 | -0.1236 | 0.022888 | 0.09613 | 0.036621 | 0.13275 | 121.4218 | -0.068664 | -0.032043 | 121.582 | 121.4813 | 121.4539 | 0.059509 | 0.032043 | 121.3074 | -0.050354 | -0.013733 | 121.5271 | 121.5637 | 121.4676 | 0.25635 | 0.16022 | 0.16022 | 0.013733 | 0.21973 | 0.14648 | -0.022888 | 0.10986 | 121.3989 | 121.4172 | -0.045776 | -0.16022 | 121.4355 | 121.4539 | 121.4035 | 121.4218
2684.0469 | 121.7285 | -121.4035 | 0.041199 | 0.01358 | 0.014573 | -0.032654 | 0.037121 | -0.017412 | -0.029463 | -0.024955 | -0.00054937 | -0.064642 | -0.00096545 | 0.046006 | -0.01559 | -0.007323 | -0.0084104 | -0.018311 | -0.032043 | 0 | 0.022888 | 0.14648 | 0.041199 | 0.050354 | 0.027466 | -0.004578 | -0.091553 | 0.073242 | 0.14191 | 0.045776 | 0.17853 | 121.4035 | -0.073242 | -0.018311 | 121.55 | 121.4539 | 121.4447 | 0.050354 | 0.041199 | 121.3119 | -0.045777 | 0.032043 | 121.5454 | 121.582 | 121.4493 | 0.27008 | 0.13733 | 0.14648 | 0.022888 | 0.23346 | 0.16479 | -0.032043 | 0.086975 | 121.3715 | 121.3989 | -0.041199 | -0.13275 | 121.4264 | 121.4767 | 121.3852 | 121.431
2685.7656 | 121.6415 | -121.4767 | 0.086975 | 0.028839 | 0.014146 | -0.034791 | 0.036053 | -0.01549 | -0.025831 | -0.021324 | 0.008606 | -0.063361 | -0.00011105 | 0.032334 | -0.020931 | -0.010314 | -0.010333 | -0.036621 | 0.004578 | -0.050354 | -0.041199 | 0.07782 | 0.009155 | 0 | -0.036621 | 0.036621 | -0.10986 | 0 | 0.07782 | -0.004578 | 0.13733 | 121.4264 | -0.082397 | -0.12817 | 121.5546 | 121.4767 | 121.4859 | 0.050354 | 0.059509 | 121.3669 | -0.050354 | -0.086975 | 121.5546 | 121.6141 | 121.4722 | 0.24719 | 0.10529 | 0.12817 | 0.009155 | 0.18768 | 0.10986 | 0.054932 | 0.14648 | 121.4813 | 121.5134 | -0.13733 | -0.19684 | 121.4355 | 121.4767 | 121.4401 | 121.4401
2687.5469 | 121.7514 | -121.431 | 0.045776 | 0.01358 | 0.012651 | -0.03415 | 0.035199 | -0.013994 | -0.030745 | -0.024101 | 0.008606 | -0.064215 | -0.00075185 | 0.042161 | -0.016231 | -0.010314 | -0.014605 | -0.013733 | -0.041199 | 0.004578 | 0.036621 | 0.17395 | 0.041199 | 0.059509 | 0.050354 | -0.032043 | -0.09613 | 0.082397 | 0.13275 | 0.045776 | 0.17853 | 121.4355 | -0.086975 | -0.009155 | 121.6049 | 121.4905 | 121.4722 | 0.054931 | 0.036621 | 121.3348 | -0.077819 | 0.036621 | 121.5637 | 121.6095 | 121.4767 | 0.27466 | 0.14191 | 0.16937 | 0.032043 | 0.22888 | 0.17853 | -0.045777 | 0.064087 | 121.3898 | 121.3989 | -0.041198 | -0.14191 | 121.4676 | 121.5134 | 121.4172 | 121.4813
2689.3438 | 120.9869 | -120.9229 | 0.086975 | 0.01358 | 0.016282 | -0.035431 | 0.037121 | -0.014422 | -0.026899 | -0.023033 | 0.0025024 | -0.061651 | -0.00075185 | 0.035111 | -0.018581 | -0.0096728 | -0.013324 | -0.09613 | 0 | -0.027466 | -0.11444 | 0.009155 | -0.082397 | -0.054932 | -0.1236 | 0.027466 | -0.11902 | -0.068665 | 0 | -0.091553 | 0.086975 | 120.8954 | -0.086975 | -0.20142 | 120.932 | 120.8679 | 120.8405 | -0.027466 | -0.054931 | 120.8038 | -0.059509 | -0.15564 | 120.9229 | 121.0098 | 120.8313 | 0.20599 | 0.027466 | 0.036621 | -0.086975 | 0.11902 | 0.050354 | 0.027466 | 0.14649 | 120.9229 | 120.9503 | -0.11444 | -0.20599 | 120.8084 | 120.8542 | 120.8267 | 120.7993
2691.0781 | 121.3806 | -121.1151 | 0.068665 | 0.0059509 | 0.014146 | -0.034363 | 0.033276 | -0.016558 | -0.031172 | -0.023887 | 0.0025024 | -0.065283 | -0.00032465 | 0.047074 | -0.017726 | -0.009032 | -0.012256 | -0.050354 | -0.013733 | -0.004578 | -0.004578 | 0.15564 | 0.064087 | 0.068665 | 0.022888 | 0 | -0.086975 | 0.050354 | 0.16937 | 0.082397 | 0.17853 | 121.1105 | -0.082398 | -0.073243 | 121.2708 | 121.1838 | 121.1792 | 0.073243 | 0.068665 | 121.0281 | -0.068665 | -0.018311 | 121.2845 | 121.2936 | 121.1975 | 0.2655 | 0.16937 | 0.16022 | 0 | 0.25635 | 0.13733 | -0.009155 | 0.086975 | 121.1014 | 121.1151 | -0.073243 | -0.15564 | 121.1105 | 121.1655 | 121.0648 | 121.138
2692.8438 | 121.3303 | -121.2387 | 0.091553 | 0.02121 | 0.015214 | -0.033082 | 0.036267 | -0.019976 | -0.029676 | -0.022178 | 0.011658 | -0.062506 | 0.00010255 | 0.031266 | -0.021144 | -0.010955 | -0.010119 | -0.073242 | 0.036621 | -0.054932 | -0.073242 | 0.050354 | -0.013733 | 0.004578 | -0.10529 | 0.041199 | -0.1236 | -0.059509 | 0.041199 | -0.032043 | 0.086975 | 121.1838 | -0.054932 | -0.16479 | 121.2891 | 121.2433 | 121.225 | 0.05951 | 0.041199 | 121.1151 | -0.050354 | -0.15106 | 121.2799 | 121.3257 | 121.2067 | 0.21057 | 0.091553 | 0.10529 | -0.01831 | 0.16479 | 0.064087 | 0.091553 | 0.16479 | 121.2753 | 121.2799 | -0.14649 | -0.21515 | 121.1655 | 121.1792 | 121.1655 | 121.1334
2694.5781 | 121.4951 | -121.2067 | 0.041199 | 0.02121 | 0.015001 | -0.034577 | 0.033276 | -0.020617 | -0.029249 | -0.024955 | 0.0055542 | -0.061865 | 0.00031615 | 0.028061 | -0.021572 | -0.0081774 | -0.016101 | -0.032043 | -0.050354 | -0.009155 | 0.050354 | 0.20599 | 0.09613 | 0.086975 | 0.073242 | -0.009155 | -0.086975 | 0.073242 | 0.18768 | 0.10986 | 0.18768 | 121.1975 | -0.091553 | 0.009155 | 121.4127 | 121.2936 | 121.3028 | 0.09613 | 0.10528 | 121.1197 | -0.050354 | 0.032043 | 121.3943 | 121.3943 | 121.3165 | 0.27466 | 0.19684 | 0.21515 | 0.059509 | 0.27466 | 0.16022 | -0.041199 | 0.07782 | 121.1563 | 121.1975 | -0.050354 | -0.12817 | 121.257 | 121.2799 | 121.1746 | 121.2799
2696.3594 | 121.0602 | -120.932 | 0.073242 | 0.01358 | 0.011583 | -0.032868 | 0.035199 | -0.013781 | -0.02989 | -0.023033 | 0.0025024 | -0.064642 | 0.00031615 | 0.035538 | -0.018581 | -0.011595 | -0.010333 | -0.009155 | -0.032043 | 0.009155 | 0.041199 | 0.17395 | 0.07782 | 0.07782 | 0.032043 | -0.009155 | -0.082397 | 0.018311 | 0.15106 | 0.050354 | 0.14191 | 120.9412 | -0.10529 | -0.032043 | 121.106 | 121.0098 | 121.0098 | 0.068665 | 0.068665 | 120.8496 | -0.082397 | -0.054931 | 121.0831 | 121.0739 | 120.9824 | 0.2243 | 0.13275 | 0.16479 | 0.032044 | 0.23346 | 0.10071 | -0.041198 | 0.073242 | 120.9 | 120.9229 | -0.064087 | -0.15564 | 120.9732 | 120.9503 | 120.9229 | 120.9641
2698.0781 | 121.2021 | -121.1472 | 0.10071 | 0.0059509 | 0.014146 | -0.035431 | 0.035626 | -0.018267 | -0.030531 | -0.023887 | 0.008606 | -0.062933 | -0.0013928 | 0.030198 | -0.02264 | -0.010741 | -0.012469 | -0.09613 | 0 | -0.050354 | -0.086975 | 0.041199 | -0.027466 | -0.022888 | -0.09613 | 0.054932 | -0.1236 | -0.07782 | 0.045776 | -0.036621 | 0.073242 | 121.0968 | -0.10071 | -0.18768 | 121.1884 | 121.1243 | 121.1197 | 0.027466 | 0.022888 | 121.0236 | -0.045776 | -0.17853 | 121.1929 | 121.2204 | 121.1105 | 0.19684 | 0.086975 | 0.091553 | -0.036621 | 0.16937 | 0.045776 | 0.050354 | 0.17853 | 121.1472 | 121.2021 | -0.15106 | -0.2243 | 121.0602 | 121.0693 | 121.051 | 121.051
2699.8594 | 121.3028 | -121.1838 | 0.082397 | -0.0016786 | 0.015855 | -0.03415 | 0.03648 | -0.013781 | -0.02754 | -0.025383 | -0.00054937 | -0.063147 | -0.00053825 | 0.036393 | -0.018154 | -0.011168 | -0.013751 | -0.036621 | -0.022888 | -0.009155 | -0.041199 | 0.09613 | -0.027466 | -0.032043 | -0.045776 | 0.027466 | -0.10529 | -0.041199 | 0.036621 | -0.041199 | 0.086975 | 121.1746 | -0.10528 | -0.1236 | 121.2799 | 121.1517 | 121.1563 | -0.022888 | -0.018311 | 121.0785 | -0.054931 | -0.1236 | 121.2204 | 121.2708 | 121.1426 | 0.19226 | 0.064087 | 0.10528 | -0.032044 | 0.14191 | 0.064087 | -0.013733 | 0.13275 | 121.1609 | 121.2112 | -0.091552 | -0.18768 | 121.1426 | 121.1426 | 121.1472 | 121.138
2701.6562 | 121.4172 | -121.1792 | 0.050354 | 0.0059509 | 0.013292 | -0.036072 | 0.034558 | -0.016985 | -0.029463 | -0.021324 | 0.0055542 | -0.066138 | -0.0013928 | 0.039811 | -0.018794 | -0.010314 | -0.013537 | -0.032043 | -0.032043 | -0.013733 | 0.013733 | 0.16937 | 0.086975 | 0.07782 | 0.050354 | -0.027466 | -0.068665 | 0.054932 | 0.19684 | 0.09613 | 0.18768 | 121.1655 | -0.082397 | -0.036621 | 121.3486 | 121.257 | 121.2662 | 0.091553 | 0.10071 | 121.1105 | -0.07782 | 0.004578 | 121.376 | 121.3669 | 121.2753 | 0.25635 | 0.16479 | 0.18311 | 0.027466 | 0.2655 | 0.1236 | -0.01831 | 0.041199 | 121.1472 | 121.1517 | -0.064087 | -0.11902 | 121.1929 | 121.2341 | 121.1472 | 121.2296
2703.4375 | 120.9961 | -120.9 | 0.064087 | 0.028839 | 0.015641 | -0.033295 | 0.035412 | -0.017626 | -0.029036 | -0.024314 | 0.008606 | -0.062933 | 0.00074335 | 0.033829 | -0.016658 | -0.0092456 | -0.014819 | -0.07782 | -0.013733 | -0.041199 | -0.07782 | 0.041199 | -0.064087 | -0.045776 | -0.068665 | 0.032043 | -0.10986 | -0.027466 | 0.050354 | -0.045776 | 0.10071 | 120.8588 | -0.07782 | -0.14191 | 120.9412 | 120.8542 | 120.8359 | -0.004577 | -0.022888 | 120.7901 | -0.032044 | -0.091553 | 120.9503 | 121.0007 | 120.8542 | 0.21057 | 0.064087 | 0.082398 | -0.036621 | 0.16022 | 0.082397 | 0.027466 | 0.14191 | 120.8862 | 120.932 | -0.10529 | -0.17395 | 120.8221 | 120.8725 | 120.8221 | 120.8313
2705.2344 | 121.1929 | -120.9778 | 0.068665 | 0.01358 | 0.012437 | -0.033509 | 0.034772 | -0.019549 | -0.031813 | -0.022819 | 0.0025024 | -0.064642 | -0.0013928 | 0.039597 | -0.017513 | -0.0094592 | -0.01546 | -0.068665 | -0.032043 | -0.009155 | -0.027466 | 0.11902 | 0.027466 | 0.045776 | -0.027466 | -0.009155 | -0.091553 | 0.009155 | 0.1236 | 0.064087 | 0.15564 | 120.9686 | -0.10071 | -0.096131 | 121.0968 | 121.0236 | 121.0052 | 0.054931 | 0.036621 | 120.8862 | -0.07782 | -0.05951 | 121.1014 | 121.1334 | 121.0419 | 0.24719 | 0.15564 | 0.12817 | -0.018311 | 0.21515 | 0.10071 | -0.022888 | 0.082398 | 120.9457 | 120.9686 | -0.07782 | -0.16022 | 120.9503 | 120.9869 | 120.9091 | 120.9503
2707.0312 | 121.2067 | -121.0968 | 0.09613 | 0.028839 | 0.014573 | -0.037568 | 0.038403 | -0.01784 | -0.028822 | -0.021324 | 0.008606 | -0.061651 | -0.0013928 | 0.040024 | -0.020503 | -0.010527 | -0.012896 | -0.064087 | -0.004578 | -0.059509 | -0.068665 | 0.054932 | -0.032043 | -0.018311 | -0.09613 | 0.068665 | -0.11902 | -0.045776 | 0.059509 | -0.022888 | 0.10986 | 121.0373 | -0.10071 | -0.16479 | 121.1517 | 121.0785 | 121.0648 | 0.041198 | 0.027466 | 120.9778 | -0.027465 | -0.14191 | 121.1563 | 121.2067 | 121.0739 | 0.22888 | 0.096131 | 0.11444 | -0.009156 | 0.17853 | 0.073243 | 0.054931 | 0.18768 | 121.0922 | 121.1655 | -0.15564 | -0.21515 | 121.0281 | 121.051 | 121.0327 | 121.0007
2708.75 | 121.3394 | -121.0648 | 0.059509 | 0.01358 | 0.012864 | -0.036927 | 0.032849 | -0.016985 | -0.029676 | -0.020256 | 0.0025024 | -0.065924 | -0.00032465 | 0.03917 | -0.018154 | -0.010314 | -0.010974 | -0.041199 | -0.045776 | -0.004578 | -0.009155 | 0.11902 | 0.036621 | 0.045776 | 0.009155 | 0 | -0.091553 | 0.041199 | 0.16479 | 0.073242 | 0.17395 | 121.0602 | -0.10528 | -0.068664 | 121.1838 | 121.1105 | 121.1014 | 0.050354 | 0.041199 | 120.9732 | -0.059509 | -0.01831 | 121.2296 | 121.2387 | 121.138 | 0.2655 | 0.16479 | 0.1236 | -0.004577 | 0.25635 | 0.13275 | -0.041198 | 0.091553 | 121.019 | 121.0648 | -0.064087 | -0.15106 | 121.0556 | 121.106 | 121.0236 | 121.0739
2710.5312 | 121.4264 | -121.1014 | 0.041199 | 0.01358 | 0.013292 | -0.032654 | 0.035199 | -0.016985 | -0.028822 | -0.020469 | 0.011658 | -0.063361 | -0.00075185 | 0.043442 | -0.016017 | -0.0092456 | -0.010974 | 0.004578 | -0.045776 | 0.009155 | 0.032043 | 0.19226 | 0.050354 | 0.059509 | 0.041199 | 0.004578 | -0.09613 | 0.018311 | 0.10529 | 0.050354 | 0.15106 | 121.1105 | -0.086975 | -0.009156 | 121.2936 | 121.1609 | 121.1517 | 0.050354 | 0.041199 | 121.0052 | -0.036621 | -0.022888 | 121.2067 | 121.2524 | 121.1517 | 0.24719 | 0.14648 | 0.18311 | 0.022888 | 0.20142 | 0.11444 | -0.054931 | 0.10071 | 121.0556 | 121.106 | -0.032044 | -0.13733 | 121.1334 | 121.1197 | 121.106 | 121.1426
2712.25 | 120.726 | -120.4971 | 0.11902 | 0.01358 | 0.010942 | -0.035004 | 0.034985 | -0.019762 | -0.028181 | -0.020897 | 0.0025024 | -0.065283 | -0.0016064 | 0.036606 | -0.017726 | -0.011595 | -0.013537 | -0.041199 | -0.036621 | -0.013733 | 0 | 0.14648 | 0.045776 | 0.045776 | 0.013733 | -0.018311 | -0.086975 | 0.022888 | 0.14648 | 0.064087 | 0.17395 | 120.4834 | -0.15564 | -0.11902 | 120.6436 | 120.5429 | 120.5429 | 0.059509 | 0.059509 | 120.4102 | -0.13733 | -0.096131 | 120.6436 | 120.6711 | 120.5612 | 0.26092 | 0.15106 | 0.16022 | 0.013733 | 0.23346 | 0.10986 | -0.022888 | 0.068664 | 120.4605 | 120.4788 | -0.13275 | -0.20599 | 120.4971 | 120.52 | 120.4559 | 120.5109
2714.0312 | 120.9824 | -120.7718 | 0.082397 | 0.0059509 | 0.015214 | -0.033722 | 0.035199 | -0.023394 | -0.027754 | -0.023033 | 0.0055542 | -0.064215 | -0.0020336 | 0.036606 | -0.019435 | -0.010314 | -0.013324 | 0 | -0.041199 | 0 | 0.032043 | 0.17853 | 0.068665 | 0.073242 | 0.045776 | 0.018311 | -0.068665 | 0.041199 | 0.15106 | 0.064087 | 0.16022 | 120.7718 | -0.1236 | -0.050354 | 120.9503 | 120.845 | 120.8405 | 0.073242 | 0.068665 | 120.7031 | -0.064086 | -0.041198 | 120.9229 | 120.932 | 120.8359 | 0.22888 | 0.13275 | 0.17853 | 0.032043 | 0.21973 | 0.10986 | -0.041199 | 0.086976 | 120.7306 | 120.7901 | -0.082397 | -0.15106 | 120.8038 | 120.813 | 120.7718 | 120.8176
2715.8281 | 121.1105 | -120.6665 | 0.1831 | -0.0093076 | 0.01671 | -0.032868 | 0.03648 | -0.014635 | -0.029036 | -0.025169 | 0.0025024 | -0.061865 | -0.00032465 | 0.046433 | -0.012813 | -0.0094592 | -0.012256 | 0.004578 | -0.032043 | 0 | 0.032043 | 0.16479 | 0.032043 | 0.059509 | 0.036621 | -0.064087 | -0.11444 | 0.045776 | 0.1236 | 0.032043 | 0.16937 | 120.6665 | -0.21515 | -0.15106 | 120.8313 | 120.726 | 120.6985 | 0.059509 | 0.032043 | 120.5521 | -0.24719 | -0.13733 | 120.7901 | 120.8359 | 120.6985 | 0.28381 | 0.14648 | 0.16479 | 0.032043 | 0.23804 | 0.16022 | -0.032043 | 0.050354 | 120.6345 | 120.6024 | -0.1831 | -0.29755 | 120.6985 | 120.7123 | 120.6711 | 120.7031
2717.5938 | 121.1243 | -120.7306 | 0.15564 | 0.01358 | 0.014146 | -0.033295 | 0.037762 | -0.015062 | -0.02754 | -0.023887 | -0.00054937 | -0.062292 | -0.00053825 | 0.034257 | -0.015377 | -0.0079638 | -0.012683 | -0.059509 | -0.018311 | -0.018311 | -0.013733 | 0.1236 | 0 | 0.018311 | -0.013733 | -0.018311 | -0.12817 | 0.032043 | 0.10529 | 0.036621 | 0.16479 | 120.7123 | -0.17395 | -0.16937 | 120.8542 | 120.7489 | 120.7306 | 0.036622 | 0.018311 | 120.6024 | -0.17395 | -0.1236 | 120.8359 | 120.8954 | 120.7672 | 0.29297 | 0.1648 | 0.14191 | 0.004578 | 0.23346 | 0.16022 | 0 | 0.10986 | 120.7123 | 120.7123 | -0.17395 | -0.28381 | 120.7169 | 120.7626 | 120.6711 | 120.7169
2719.3125 | 121.1151 | -120.813 | 0.16022 | 0.02121 | 0.013719 | -0.032441 | 0.035199 | -0.016344 | -0.028181 | -0.021965 | 0.008606 | -0.065497 | -0.0013928 | 0.040238 | -0.018154 | -0.0101 | -0.016955 | -0.045776 | -0.036621 | -0.013733 | -0.022888 | 0.11444 | 0.018311 | 0.027466 | -0.027466 | -0.022888 | -0.10529 | -0.027466 | 0.068665 | -0.013733 | 0.10529 | 120.7993 | -0.19684 | -0.1831 | 120.9274 | 120.8405 | 120.8313 | 0.041199 | 0.032044 | 120.7077 | -0.1831 | -0.18768 | 120.8817 | 120.9183 | 120.7993 | 0.21057 | 0.091553 | 0.12817 | -0.009155 | 0.17395 | 0.07782 | -0.022888 | 0.082398 | 120.7764 | 120.7901 | -0.17395 | -0.2655 | 120.7901 | 120.7855 | 120.7672 | 120.7855
2721.0469 | 121.1792 | -120.9503 | 0.064087 | 0.02121 | 0.016069 | -0.031373 | 0.036694 | -0.017412 | -0.030531 | -0.023887 | 0.0055542 | -0.064429 | 0.0018116 | 0.036393 | -0.018794 | -0.009032 | -0.010333 | -0.045776 | -0.032043 | -0.013733 | 0 | 0.11902 | 0.018311 | 0.027466 | -0.045776 | -0.027466 | -0.11902 | -0.041199 | 0.07782 | 0 | 0.11444 | 120.9366 | -0.09613 | -0.064087 | 121.0693 | 120.9778 | 120.9686 | 0.041199 | 0.032044 | 120.8313 | -0.091553 | -0.10529 | 121.0281 | 121.0648 | 120.9503 | 0.23346 | 0.11902 | 0.13275 | 0.013733 | 0.19684 | 0.07782 | -0.01831 | 0.091553 | 120.9183 | 120.9229 | -0.07782 | -0.18311 | 120.9503 | 120.9091 | 120.9045 | 120.9045
2722.7656 | 121.2067 | -120.9641 | 0.086975 | 0.0059509 | 0.012437 | -0.033082 | 0.036053 | -0.018908 | -0.028395 | -0.026237 | 0.008606 | -0.063788 | -0.0024608 | 0.038743 | -0.018581 | -0.0088184 | -0.012896 | -0.041199 | -0.022888 | -0.013733 | -0.022888 | 0.10071 | 0.018311 | 0.027466 | -0.050354 | -0.041199 | -0.10986 | -0.036621 | 0.068665 | -0.013733 | 0.11902 | 120.9503 | -0.10986 | -0.10986 | 121.0648 | 120.9915 | 120.9824 | 0.041199 | 0.032044 | 120.8542 | -0.12817 | -0.1236 | 121.0327 | 121.0831 | 120.9503 | 0.22888 | 0.09613 | 0.11444 | -0.009155 | 0.17853 | 0.073242 | -0.009155 | 0.068664 | 120.9412 | 120.9229 | -0.10071 | -0.19684 | 120.9412 | 120.9274 | 120.9229 | 120.9137
2724.4688 | 121.1426 | -120.9457 | 0.11444 | 0.01358 | 0.01436 | -0.032868 | 0.035412 | -0.011217 | -0.026686 | -0.019615 | 0.014709 | -0.064429 | 0.0028798 | 0.04451 | -0.019008 | -0.006682 | -0.013537 | 0 | -0.045776 | 0.013733 | 0.068665 | 0.18768 | 0.073242 | 0.07782 | 0.050354 | -0.036621 | -0.12817 | 0.050354 | 0.13275 | 0.041199 | 0.16022 | 120.9595 | -0.16022 | -0.045776 | 121.1334 | 121.0236 | 121.019 | 0.064087 | 0.059509 | 120.8176 | -0.15106 | -0.064087 | 121.0785 | 121.106 | 120.9869 | 0.28839 | 0.16937 | 0.17395 | 0.054932 | 0.26093 | 0.17853 | -0.059509 | 0.091553 | 120.9 | 120.9091 | -0.10071 | -0.24262 | 121.0144 | 120.9961 | 120.9457 | 120.9961
2726.1719 | 121.2845 | -120.7993 | 0.22888 | -0.0093076 | 0.013078 | -0.035431 | 0.033917 | -0.019121 | -0.029249 | -0.023674 | 0.0055542 | -0.064002 | 0.00074335 | 0.037461 | -0.020503 | -0.010314 | -0.014392 | 0.004578 | -0.050354 | 0.009155 | 0.059509 | 0.20142 | 0.11444 | 0.091553 | 0.059509 | -0.032043 | -0.07782 | 0.045776 | 0.16022 | 0.07782 | 0.15106 | 120.8084 | -0.27924 | -0.16937 | 121.0007 | 120.8908 | 120.9137 | 0.082398 | 0.10529 | 120.7214 | -0.26093 | -0.18311 | 120.9595 | 120.9503 | 120.8771 | 0.22888 | 0.15564 | 0.19226 | 0.050354 | 0.23804 | 0.1236 | -0.059509 | 0.045777 | 120.7489 | 120.7672 | -0.21973 | -0.3067 | 120.8588 | 120.845 | 120.8038 | 120.8588
2727.875 | 121.0098 | -120.4697 | 0.48523 | 0.02121 | 0.015214 | -0.033936 | 0.036908 | -0.020189 | -0.030104 | -0.024742 | 0.0025024 | -0.061224 | -0.00053825 | 0.037247 | -0.017085 | -0.010314 | -0.016101 | -0.086975 | -0.018311 | -0.032043 | -0.073242 | 0.036621 | -0.073242 | -0.032043 | -0.13733 | -0.018311 | -0.14191 | -0.073242 | -0.004578 | -0.10071 | 0.045776 | 120.4376 | -0.50354 | -0.55847 | 120.5063 | 120.4376 | 120.3964 | 0 | -0.041199 | 120.3278 | -0.50354 | -0.55847 | 120.4651 | 120.5154 | 120.369 | 0.18768 | 0.041199 | 0.068664 | -0.041199 | 0.13733 | 0.068665 | 0.013732 | 0.1236 | 120.4514 | 120.4514 | -0.51727 | -0.62714 | 120.3964 | 120.3964 | 120.3827 | 120.3323
2729.6094 | 121.0556 | -120.3735 | 0.50812 | 0.02121 | 0.012651 | -0.034363 | 0.037335 | -0.015917 | -0.02989 | -0.02111 | 0.0025024 | -0.059729 | 0.00052975 | 0.04387 | -0.019008 | -0.0094592 | -0.012683 | -0.082397 | -0.004578 | -0.032043 | -0.07782 | 0.041199 | -0.073242 | -0.036621 | -0.13733 | -0.022888 | -0.13733 | -0.054932 | -0.009155 | -0.10529 | 0.045776 | 120.3415 | -0.5127 | -0.58594 | 120.4147 | 120.3369 | 120.3003 | -0.004578 | -0.041199 | 120.2362 | -0.53101 | -0.56305 | 120.3644 | 120.4193 | 120.2682 | 0.18311 | 0.032043 | 0.073242 | -0.045777 | 0.12817 | 0.082397 | 0.027465 | 0.11444 | 120.369 | 120.3506 | -0.54016 | -0.64545 | 120.2957 | 120.3186 | 120.2911 | 120.2362
2731.3438 | 121.2067 | -120.8954 | 0.17853 | 0.01358 | 0.014787 | -0.035431 | 0.03584 | -0.016558 | -0.029463 | -0.024528 | 0.008606 | -0.065497 | -0.00096545 | 0.040024 | -0.022212 | -0.0096728 | -0.016101 | -0.004578 | -0.027466 | -0.009155 | 0.004578 | 0.15106 | 0.064087 | 0.050354 | -0.022888 | -0.004578 | -0.09613 | -0.022888 | 0.07782 | -0.022888 | 0.091553 | 120.8862 | -0.20599 | -0.17395 | 121.0464 | 120.9457 | 120.9595 | 0.059509 | 0.073242 | 120.7993 | -0.18311 | -0.20142 | 120.9732 | 120.9869 | 120.8725 | 0.18768 | 0.073242 | 0.16022 | 0.013733 | 0.17395 | 0.073242 | -0.018311 | 0.091552 | 120.8679 | 120.8908 | -0.18768 | -0.27466 | 120.9 | 120.8725 | 120.8908 | 120.8725
2733.0625 | 121.312 | -121.0556 | 0.059509 | 0.02121 | 0.012864 | -0.035431 | 0.034131 | -0.01848 | -0.030958 | -0.020042 | 0.0025024 | -0.063147 | 0.00010255 | 0.037034 | -0.021358 | -0.012664 | -0.008624 | -0.032043 | -0.045776 | -0.004578 | 0.032043 | 0.20142 | 0.10071 | 0.09613 | 0.022888 | -0.018311 | -0.082397 | 0.045776 | 0.14648 | 0.064087 | 0.16022 | 121.051 | -0.10528 | -0.027466 | 121.257 | 121.1517 | 121.1563 | 0.10071 | 0.10529 | 120.9732 | -0.07782 | -0.013733 | 121.2021 | 121.2158 | 121.1197 | 0.24261 | 0.14648 | 0.20599 | 0.036621 | 0.22888 | 0.12817 | -0.041198 | 0.064086 | 121.0098 | 121.0373 | -0.064087 | -0.14191 | 121.0876 | 121.1014 | 121.0236 | 121.0785
2734.7812 | 121.3898 | -121.0831 | 0.059509 | 0.02121 | 0.013719 | -0.033295 | 0.034772 | -0.016558 | -0.026472 | -0.023887 | 0.0055542 | -0.064856 | 0.00010255 | 0.037675 | -0.018581 | -0.012023 | -0.011615 | -0.004578 | -0.059509 | -0.004578 | 0.064087 | 0.23346 | 0.11902 | 0.10529 | 0.054932 | -0.027466 | -0.086975 | 0.068665 | 0.1831 | 0.10529 | 0.16022 | 121.0785 | -0.11902 | 0.004578 | 121.3165 | 121.1884 | 121.2021 | 0.10986 | 0.1236 | 120.9961 | -0.086975 | 0.009156 | 121.2662 | 121.2433 | 121.1884 | 0.24719 | 0.19226 | 0.23804 | 0.068665 | 0.27008 | 0.15564 | -0.054931 | 0.059509 | 121.0236 | 121.0556 | -0.064087 | -0.14648 | 121.1472 | 121.1517 | 121.0785 | 121.138
2736.5156 | 121.344 | -121.106 | 0.068665 | 0.0059509 | 0.015214 | -0.034791 | 0.034344 | -0.01784 | -0.030531 | -0.024314 | 0.0025024 | -0.064002 | 0.00031615 | 0.038102 | -0.021999 | -0.011168 | -0.014605 | -0.004578 | -0.041199 | -0.013733 | 0.050354 | 0.17395 | 0.082397 | 0.07782 | 0.009155 | -0.022888 | -0.07782 | 0.009155 | 0.13275 | 0.050354 | 0.12817 | 121.0922 | -0.10986 | -0.018311 | 121.2799 | 121.1838 | 121.1884 | 0.091553 | 0.09613 | 121.0281 | -0.091553 | -0.05951 | 121.2387 | 121.2341 | 121.1563 | 0.20599 | 0.12817 | 0.18768 | 0.064087 | 0.21057 | 0.086975 | -0.027466 | 0.054932 | 121.0648 | 121.0831 | -0.082398 | -0.14649 | 121.1563 | 121.1151 | 121.1014 | 121.1151
2738.25 | 121.3623 | -121.1334 | 0.073242 | 0.02121 | 0.013505 | -0.034363 | 0.035626 | -0.016771 | -0.027327 | -0.02111 | 0.0055542 | -0.064642 | 0.00074335 | 0.040452 | -0.019008 | -0.011382 | -0.016314 | -0.064087 | -0.022888 | -0.022888 | -0.027466 | 0.10986 | 0.018311 | 0.027466 | -0.050354 | -0.004578 | -0.091553 | -0.018311 | 0.082397 | -0.004578 | 0.1236 | 121.1105 | -0.09613 | -0.10071 | 121.2433 | 121.1609 | 121.1517 | 0.050354 | 0.041199 | 121.0419 | -0.07782 | -0.091553 | 121.2158 | 121.257 | 121.1288 | 0.21515 | 0.086975 | 0.13275 | -0.004578 | 0.17395 | 0.073242 | 0 | 0.086975 | 121.1105 | 121.1288 | -0.09613 | -0.16479 | 121.106 | 121.1151 | 121.0693 | 121.0831
2740 | 121.2799 | -121.1792 | 0.09613 | 0.0059509 | 0.014146 | -0.033295 | 0.03883 | -0.017626 | -0.028181 | -0.019615 | 0.0025024 | -0.059943 | -0.0013928 | 0.04152 | -0.016658 | -0.0096728 | -0.015246 | -0.073242 | -0.013733 | -0.041199 | -0.086975 | 0.009155 | -0.082397 | -0.086975 | -0.16022 | 0.013733 | -0.13733 | -0.091553 | -0.027466 | -0.10071 | 0.059509 | 121.138 | -0.10986 | -0.1831 | 121.1884 | 121.0922 | 121.0968 | -0.045776 | -0.041198 | 121.0419 | -0.082397 | -0.18768 | 121.1517 | 121.2387 | 121.0785 | 0.19684 | 0.036621 | 0.050354 | -0.045776 | 0.10986 | 0.045776 | 0.027466 | 0.15106 | 121.1655 | 121.1929 | -0.13733 | -0.23346 | 121.0922 | 121.0876 | 121.106 | 121.019
2741.6875 | 121.3211 | -121.1746 | 0.09613 | -0.0016786 | 0.013933 | -0.035218 | 0.035412 | -0.021685 | -0.030104 | -0.024101 | 0.0055542 | -0.062506 | 0.00074335 | 0.033402 | -0.020076 | -0.011809 | -0.013324 | -0.082397 | -0.013733 | -0.036621 | -0.07782 | 0.050354 | -0.022888 | -0.022888 | -0.11444 | 0.027466 | -0.10986 | -0.07782 | 0.041199 | -0.054932 | 0.050354 | 121.138 | -0.10986 | -0.17395 | 121.225 | 121.1517 | 121.1517 | 0.013733 | 0.013733 | 121.0648 | -0.068664 | -0.17395 | 121.2158 | 121.225 | 121.1197 | 0.16022 | 0.054931 | 0.086975 | -0.041199 | 0.15106 | 0.032043 | 0.022888 | 0.13733 | 121.1609 | 121.2021 | -0.13275 | -0.20599 | 121.0968 | 121.0968 | 121.0922 | 121.0602
2743.3906 | 121.3165 | -121.2021 | 0.09613 | 0.01358 | 0.013719 | -0.035218 | 0.033917 | -0.018908 | -0.029036 | -0.019188 | 0.008606 | -0.06272 | -0.00053825 | 0.041306 | -0.020076 | -0.013304 | -0.015674 | -0.10986 | -0.013733 | -0.050354 | -0.07782 | 0.054932 | 0 | -0.004578 | -0.11444 | 0.022888 | -0.12817 | -0.068665 | 0.027466 | -0.045776 | 0.073242 | 121.1517 | -0.10986 | -0.17395 | 121.257 | 121.1975 | 121.2021 | 0.045776 | 0.050354 | 121.0739 | -0.073242 | -0.16479 | 121.2296 | 121.2753 | 121.1563 | 0.20142 | 0.082398 | 0.10529 | -0.027466 | 0.15564 | 0.059509 | 0.036621 | 0.15106 | 121.1884 | 121.225 | -0.14648 | -0.2243 | 121.1243 | 121.1334 | 121.0922 | 121.0876
2745.0938 | 121.3898 | -121.2021 | 0.10071 | 0.044098 | 0.014146 | -0.033722 | 0.037121 | -0.019762 | -0.031385 | -0.021965 | 0.008606 | -0.061438 | -0.00011105 | 0.031052 | -0.016872 | -0.0096728 | -0.015674 | -0.045776 | 0.018311 | -0.054932 | -0.041199 | 0.073242 | 0.022888 | 0.009155 | -0.07782 | 0.022888 | -0.13275 | -0.032043 | 0.064087 | -0.032043 | 0.091553 | 121.1472 | -0.082397 | -0.14191 | 121.2753 | 121.2112 | 121.225 | 0.064087 | 0.07782 | 121.0693 | -0.07782 | -0.13275 | 121.2662 | 121.2936 | 121.17 | 0.2243 | 0.10071 | 0.12817 | 0.013733 | 0.19684 | 0.10071 | 0.073243 | 0.15564 | 121.2204 | 121.225 | -0.15564 | -0.23346 | 121.1609 | 121.17 | 121.1563 | 121.1243
2746.8125 | 121.4172 | -121.2387 | 0.068665 | -0.0016786 | 0.015428 | -0.0318 | 0.037335 | -0.015276 | -0.02989 | -0.022605 | 0.008606 | -0.061224 | 0.00095715 | 0.037247 | -0.017513 | -0.010527 | -0.015033 | -0.032043 | -0.018311 | -0.027466 | -0.022888 | 0.11444 | 0.009155 | 0.013733 | -0.032043 | 0.022888 | -0.10986 | 0 | 0.07782 | -0.009155 | 0.11902 | 121.2112 | -0.086976 | -0.091553 | 121.3531 | 121.2524 | 121.2479 | 0.041199 | 0.036621 | 121.1288 | -0.045777 | -0.068665 | 121.3165 | 121.3577 | 121.2296 | 0.22888 | 0.10071 | 0.14191 | 0.004578 | 0.18768 | 0.10986 | 0.009155 | 0.13275 | 121.2204 | 121.2616 | -0.096131 | -0.17853 | 121.2158 | 121.2387 | 121.2067 | 121.2067
2748.5156 | 121.4127 | -121.257 | 0.073242 | 0.0059509 | 0.012651 | -0.033509 | 0.033703 | -0.021685 | -0.029249 | -0.022605 | 0.0055542 | -0.064215 | -0.00053825 | 0.040024 | -0.019222 | -0.0094592 | -0.014392 | -0.009155 | -0.050354 | 0.004578 | 0.004578 | 0.15564 | 0.068665 | 0.059509 | -0.022888 | -0.004578 | -0.091553 | -0.027466 | 0.068665 | 0 | 0.10071 | 121.2616 | -0.1236 | -0.068664 | 121.4127 | 121.3165 | 121.3257 | 0.054931 | 0.064087 | 121.1655 | -0.07782 | -0.10071 | 121.3257 | 121.3577 | 121.257 | 0.19226 | 0.091553 | 0.15106 | 0 | 0.16022 | 0.064087 | -0.054932 | 0.086975 | 121.2067 | 121.2524 | -0.068664 | -0.16479 | 121.2616 | 121.2296 | 121.2479 | 121.2341
2750.2344 | 121.4218 | -121.2296 | 0.073242 | 0.028839 | 0.01735 | -0.035004 | 0.036908 | -0.018053 | -0.028395 | -0.023887 | 0.008606 | -0.063147 | 0.001598 | 0.041947 | -0.018794 | -0.008391 | -0.013537 | -0.050354 | 0.004578 | -0.041199 | -0.054932 | 0.059509 | -0.004578 | -0.004578 | -0.064087 | 0.027466 | -0.1236 | -0.009155 | 0.073242 | -0.032043 | 0.091553 | 121.1884 | -0.068664 | -0.12817 | 121.2891 | 121.225 | 121.225 | 0.036621 | 0.036621 | 121.106 | -0.045776 | -0.082397 | 121.3028 | 121.3211 | 121.1975 | 0.21515 | 0.091553 | 0.10071 | -0.013733 | 0.19684 | 0.11444 | 0.045777 | 0.15106 | 121.2341 | 121.257 | -0.11444 | -0.19684 | 121.1746 | 121.2204 | 121.1792 | 121.1655
2751.9844 | 121.4859 | -121.2341 | 0.059509 | 0.01358 | 0.013933 | -0.035431 | 0.036908 | -0.019121 | -0.029463 | -0.021537 | 0.0055542 | -0.060156 | 0.00010255 | 0.038956 | -0.013027 | -0.0077502 | -0.012042 | -0.086975 | -0.013733 | -0.022888 | -0.064087 | 0.068665 | -0.059509 | -0.022888 | -0.073242 | -0.018311 | -0.1236 | 0.004578 | 0.068665 | -0.022888 | 0.1236 | 121.2112 | -0.073242 | -0.1236 | 121.3028 | 121.2112 | 121.1746 | 0 | -0.036621 | 121.1105 | -0.07782 | -0.054931 | 121.3028 | 121.3577 | 121.2112 | 0.24719 | 0.10071 | 0.091553 | -0.041199 | 0.19226 | 0.12817 | 0.009155 | 0.10528 | 121.2204 | 121.2158 | -0.082397 | -0.1831 | 121.17 | 121.2387 | 121.1472 | 121.1609
2753.6875 | 121.4539 | -121.2708 | 0.09613 | 0.01358 | 0.014787 | -0.035004 | 0.03584 | -0.022326 | -0.028181 | -0.022819 | 0.011658 | -0.061651 | -0.0033154 | 0.031266 | -0.016658 | -0.0101 | -0.012683 | -0.07782 | 0.018311 | -0.073242 | -0.07782 | 0.041199 | -0.013733 | -0.027466 | -0.1236 | 0.013733 | -0.13733 | -0.068665 | 0.032043 | -0.050354 | 0.073242 | 121.1975 | -0.077819 | -0.17395 | 121.312 | 121.2433 | 121.257 | 0.045776 | 0.059509 | 121.1334 | -0.082397 | -0.16479 | 121.3028 | 121.344 | 121.2204 | 0.21057 | 0.086975 | 0.11444 | -0.004578 | 0.16937 | 0.068664 | 0.091553 | 0.15106 | 121.2891 | 121.2845 | -0.16937 | -0.23346 | 121.1929 | 121.2021 | 121.1929 | 121.1472
2755.3906 | 121.4584 | -121.3028 | 0.086975 | 0.028839 | 0.012651 | -0.034577 | 0.036694 | -0.01784 | -0.032026 | -0.022392 | 0.008606 | -0.060797 | 0.00074335 | 0.035752 | -0.017726 | -0.011595 | -0.016955 | -0.068665 | 0.013733 | -0.045776 | -0.07782 | 0.059509 | 0 | -0.009155 | -0.086975 | 0.013733 | -0.11444 | -0.032043 | 0.054932 | -0.027466 | 0.086975 | 121.257 | -0.073242 | -0.16479 | 121.3623 | 121.2936 | 121.3028 | 0.036621 | 0.045776 | 121.1884 | -0.073242 | -0.11902 | 121.3577 | 121.3898 | 121.2753 | 0.20142 | 0.086975 | 0.10528 | -0.032044 | 0.16937 | 0.082398 | 0.059509 | 0.12817 | 121.3165 | 121.3165 | -0.13275 | -0.20142 | 121.225 | 121.2708 | 121.2341 | 121.2158
2757.125 | 121.4584 | -121.3211 | 0.086975 | -0.0016786 | 0.01436 | -0.036927 | 0.036267 | -0.021898 | -0.029036 | -0.021537 | -0.00054937 | -0.062933 | -0.00096545 | 0.038529 | -0.019863 | -0.012023 | -0.011615 | -0.086975 | -0.004578 | -0.032043 | -0.086975 | 0.07782 | -0.022888 | -0.027466 | -0.10986 | 0.009155 | -0.1236 | -0.059509 | 0.036621 | -0.054932 | 0.068665 | 121.2891 | -0.091553 | -0.17395 | 121.3989 | 121.2936 | 121.2982 | 0.004577 | 0.009155 | 121.1975 | -0.07782 | -0.14648 | 121.3577 | 121.3898 | 121.2662 | 0.19226 | 0.068664 | 0.10986 | -0.054932 | 0.16022 | 0.064087 | 0.027465 | 0.13275 | 121.3165 | 121.3303 | -0.11902 | -0.21057 | 121.2341 | 121.2616 | 121.2341 | 121.2112
2758.875 | 121.4401 | -121.3577 | 0.082397 | -0.0016786 | 0.01201 | -0.036286 | 0.036694 | -0.015703 | -0.031813 | -0.021324 | 0.011658 | -0.063361 | 0.00031615 | 0.035111 | -0.02029 | -0.011382 | -0.013537 | -0.10986 | -0.004578 | -0.050354 | -0.09613 | 0.045776 | -0.018311 | -0.018311 | -0.11444 | 0.036621 | -0.12817 | -0.082397 | 0.022888 | -0.064087 | 0.054932 | 121.3074 | -0.086975 | -0.17853 | 121.4035 | 121.3394 | 121.3394 | 0.032043 | 0.032043 | 121.2296 | -0.045776 | -0.16479 | 121.3806 | 121.4127 | 121.2936 | 0.18311 | 0.064087 | 0.09613 | -0.045776 | 0.15106 | 0.045777 | 0.045776 | 0.1648 | 121.3531 | 121.3943 | -0.13275 | -0.21057 | 121.2616 | 121.2753 | 121.2479 | 121.2433
2760.5781 | 121.5271 | -121.3394 | 0.064087 | 0.01358 | 0.014146 | -0.034791 | 0.036053 | -0.018908 | -0.026472 | -0.022178 | 0.017761 | -0.061224 | 0.00095715 | 0.038956 | -0.017726 | -0.0098864 | -0.0099056 | -0.032043 | -0.018311 | -0.036621 | -0.050354 | 0.1236 | 0.009155 | 0.004578 | -0.041199 | 0.018311 | -0.10986 | -0.004578 | 0.068665 | -0.027466 | 0.10986 | 121.3028 | -0.082398 | -0.11444 | 121.463 | 121.344 | 121.3486 | 0.041199 | 0.045776 | 121.2296 | -0.045776 | -0.068665 | 121.4081 | 121.4493 | 121.312 | 0.21973 | 0.082397 | 0.16022 | -0.013733 | 0.17853 | 0.10529 | 0.01831 | 0.12817 | 121.3211 | 121.3577 | -0.10071 | -0.17395 | 121.2891 | 121.3348 | 121.3074 | 121.2982
2762.2812 | 121.55 | -121.3394 | 0.068665 | 0.01358 | 0.014146 | -0.032441 | 0.037335 | -0.015917 | -0.02519 | -0.022178 | 0.008606 | -0.063788 | 0.00052975 | 0.035752 | -0.015804 | -0.009032 | -0.016314 | -0.091553 | -0.009155 | -0.041199 | -0.073242 | 0.036621 | -0.054932 | -0.041199 | -0.086975 | -0.004578 | -0.1236 | -0.018311 | 0.050354 | -0.027466 | 0.10529 | 121.2982 | -0.07782 | -0.14191 | 121.376 | 121.2982 | 121.2845 | 0 | -0.013733 | 121.2158 | -0.073243 | -0.086976 | 121.3898 | 121.4447 | 121.312 | 0.22888 | 0.09613 | 0.07782 | -0.032043 | 0.17395 | 0.10528 | 0.032044 | 0.11902 | 121.3303 | 121.3348 | -0.10986 | -0.19226 | 121.2662 | 121.3211 | 121.2479 | 121.2524
2764.0156 | 121.5729 | -121.3303 | 0.07782 | 0.01358 | 0.014787 | -0.033509 | 0.035412 | -0.01784 | -0.029036 | -0.024314 | 0.0025024 | -0.064642 | -0.00053825 | 0.046219 | -0.017726 | -0.0088184 | -0.013965 | -0.059509 | -0.032043 | -0.013733 | -0.032043 | 0.10986 | 0.032043 | 0.027466 | -0.045776 | -0.022888 | -0.10986 | -0.004578 | 0.09613 | -0.004578 | 0.11902 | 121.3165 | -0.10986 | -0.10986 | 121.4401 | 121.3577 | 121.3623 | 0.041199 | 0.045776 | 121.2204 | -0.10071 | -0.082398 | 121.4264 | 121.4493 | 121.3257 | 0.22888 | 0.10529 | 0.1236 | -0.01831 | 0.20599 | 0.10529 | -0.01831 | 0.086975 | 121.2982 | 121.3074 | -0.091553 | -0.18768 | 121.2982 | 121.3257 | 121.2708 | 121.2845
2765.75 | 121.6324 | -121.3486 | 0.045776 | 0.0059509 | 0.013078 | -0.032227 | 0.034985 | -0.015917 | -0.028822 | -0.022605 | 0.0025024 | -0.063574 | 0.00031615 | 0.03447 | -0.013668 | -0.007323 | -0.01076 | 0.004578 | -0.036621 | -0.013733 | 0.013733 | 0.16022 | 0.041199 | 0.054932 | 0.022888 | -0.036621 | -0.10529 | 0.068665 | 0.13733 | 0.045776 | 0.16937 | 121.3348 | -0.082397 | -0.032043 | 121.5088 | 121.4035 | 121.3898 | 0.068665 | 0.054932 | 121.2433 | -0.082397 | 0.022889 | 121.4859 | 121.5179 | 121.3943 | 0.27466 | 0.15106 | 0.17395 | 0.027466 | 0.24262 | 0.17395 | -0.022888 | 0.068665 | 121.312 | 121.312 | -0.059509 | -0.15106 | 121.3623 | 121.4172 | 121.3531 | 121.3715
2767.4531 | 121.5317 | -121.3898 | 0.073242 | 0.02121 | 0.015214 | -0.034577 | 0.037976 | -0.016985 | -0.029249 | -0.024528 | 0.008606 | -0.063574 | 0.001598 | 0.037888 | -0.017726 | -0.0071094 | -0.013324 | -0.082397 | 0.009155 | -0.032043 | -0.11444 | 0.009155 | -0.073242 | -0.045776 | -0.10986 | 0.004578 | -0.11444 | -0.054932 | 0.004578 | -0.086975 | 0.068665 | 121.3577 | -0.064087 | -0.18768 | 121.3989 | 121.344 | 121.3165 | -0.013733 | -0.041199 | 121.2753 | -0.068664 | -0.12817 | 121.3943 | 121.4584 | 121.3028 | 0.18311 | 0.027466 | 0.041198 | -0.082398 | 0.11902 | 0.059509 | 0.041198 | 0.11902 | 121.3989 | 121.3943 | -0.10529 | -0.18768 | 121.2753 | 121.3348 | 121.3074 | 121.2799
2769.1562 | 121.5546 | -121.3943 | 0.086975 | 0.01358 | 0.014787 | -0.034363 | 0.037335 | -0.015703 | -0.031385 | -0.024528 | 0.011658 | -0.061438 | -0.00182 | 0.03682 | -0.01794 | -0.0088184 | -0.011615 | -0.022888 | -0.004578 | -0.027466 | -0.004578 | 0.11444 | 0.013733 | 0.022888 | -0.027466 | 0.009155 | -0.10529 | -0.004578 | 0.059509 | -0.013733 | 0.10071 | 121.3669 | -0.091553 | -0.091553 | 121.5088 | 121.4172 | 121.4081 | 0.050354 | 0.041199 | 121.2891 | -0.07782 | -0.091553 | 121.4539 | 121.4951 | 121.3806 | 0.20599 | 0.091553 | 0.14191 | 0.022888 | 0.16479 | 0.10071 | 0.022888 | 0.11444 | 121.3898 | 121.4035 | -0.11444 | -0.19226 | 121.3898 | 121.3898 | 121.3715 | 121.3669
2770.9219 | 121.6232 | -121.3806 | 0.059509 | 0.028839 | 0.012864 | -0.033722 | 0.034985 | -0.016344 | -0.030104 | -0.02111 | 0.008606 | -0.063361 | 0.00010255 | 0.036179 | -0.018367 | -0.0077502 | -0.012256 | -0.041199 | -0.041199 | 0.009155 | -0.013733 | 0.13275 | 0.027466 | 0.041199 | -0.027466 | -0.013733 | -0.11444 | 0.009155 | 0.09613 | -0.004578 | 0.11444 | 121.3898 | -0.10071 | -0.073242 | 121.5134 | 121.4218 | 121.4081 | 0.032044 | 0.018311 | 121.2662 | -0.073242 | -0.050354 | 121.4767 | 121.4951 | 121.376 | 0.22888 | 0.10986 | 0.1236 | -0.022888 | 0.21057 | 0.1236 | -0.050354 | 0.10071 | 121.3394 | 121.3669 | -0.050354 | -0.17395 | 121.3669 | 121.3898 | 121.3394 | 121.3531
2772.6562 | 121.6278 | -121.3989 | 0.082397 | 0.028839 | 0.01201 | -0.036713 | 0.036267 | -0.016344 | -0.029036 | -0.022392 | 0.0025024 | -0.061865 | 0.00010255 | 0.037247 | -0.019649 | -0.0094592 | -0.016314 | -0.045776 | -0.027466 | -0.022888 | -0.022888 | 0.10529 | 0.032043 | 0.036621 | -0.050354 | -0.018311 | -0.09613 | -0.004578 | 0.073242 | 0.013733 | 0.14648 | 121.376 | -0.10986 | -0.10528 | 121.5042 | 121.4355 | 121.431 | 0.059509 | 0.054931 | 121.3028 | -0.10071 | -0.086975 | 121.4722 | 121.5454 | 121.4127 | 0.24261 | 0.10986 | 0.12817 | 0 | 0.16937 | 0.091552 | -0.004578 | 0.077819 | 121.3715 | 121.3806 | -0.10528 | -0.17853 | 121.376 | 121.3943 | 121.3531 | 121.3486
2774.3594 | 121.6782 | -121.4172 | 0.068665 | 0.01358 | 0.014146 | -0.033722 | 0.036053 | -0.020403 | -0.029036 | -0.023246 | 0.0025024 | -0.065497 | -0.00075185 | 0.038743 | -0.020076 | -0.0098864 | -0.011615 | -0.009155 | -0.036621 | -0.004578 | 0.059509 | 0.21515 | 0.09613 | 0.091553 | 0.068665 | -0.036621 | -0.091553 | 0.068665 | 0.17395 | 0.082397 | 0.16937 | 121.4127 | -0.10529 | -0.009156 | 121.6324 | 121.5088 | 121.5134 | 0.096131 | 0.10071 | 121.3257 | -0.10529 | 0 | 121.5912 | 121.5866 | 121.4996 | 0.26093 | 0.17395 | 0.21973 | 0.064087 | 0.2655 | 0.16022 | -0.032043 | 0.054932 | 121.3806 | 121.3806 | -0.073243 | -0.16022 | 121.4767 | 121.4859 | 121.4081 | 121.4859
2776.0781 | 121.6553 | -121.4264 | 0.073242 | 0.028839 | 0.015641 | -0.033295 | 0.034558 | -0.014422 | -0.031385 | -0.021751 | 0.0025024 | -0.064642 | -0.0020336 | 0.034684 | -0.01559 | -0.008391 | -0.011828 | -0.036621 | -0.032043 | 0.009155 | -0.013733 | 0.13275 | 0.032043 | 0.045776 | -0.027466 | -0.027466 | -0.10529 | -0.004578 | 0.068665 | 0.009155 | 0.11444 | 121.4355 | -0.10529 | -0.086975 | 121.5591 | 121.4722 | 121.4584 | 0.036621 | 0.022888 | 121.3211 | -0.10071 | -0.07782 | 121.4951 | 121.5408 | 121.4355 | 0.21973 | 0.11444 | 0.1236 | -0.022888 | 0.17395 | 0.10071 | -0.041198 | 0.07782 | 121.3943 | 121.3989 | -0.064087 | -0.17853 | 121.4127 | 121.4218 | 121.3898 | 121.3989
2777.7812 | 121.5683 | -121.4264 | 0.09613 | 0.0059509 | 0.016282 | -0.035859 | 0.037762 | -0.015917 | -0.02989 | -0.021751 | 0.008606 | -0.061865 | -0.00032465 | 0.031266 | -0.016872 | -0.0079638 | -0.011187 | -0.036621 | -0.018311 | -0.032043 | -0.036621 | 0.059509 | -0.041199 | -0.036621 | -0.082397 | 0 | -0.10986 | -0.059509 | 0.013733 | -0.082397 | 0.054932 | 121.3943 | -0.11444 | -0.13275 | 121.4859 | 121.3898 | 121.3852 | -0.004578 | -0.009156 | 121.3165 | -0.09613 | -0.15564 | 121.4401 | 121.4813 | 121.344 | 0.16479 | 0.027466 | 0.091552 | -0.004578 | 0.1236 | 0.050354 | 0.013732 | 0.10986 | 121.4081 | 121.4264 | -0.12817 | -0.20599 | 121.3898 | 121.3669 | 121.3898 | 121.344
2779.5 | 121.669 | -121.4081 | 0.064087 | 0.01358 | 0.012651 | -0.032654 | 0.037762 | -0.01549 | -0.028181 | -0.021965 | 0.014709 | -0.064429 | 0.0018116 | 0.039384 | -0.015804 | -0.0094592 | -0.015033 | -0.009155 | -0.036621 | 0 | 0.027466 | 0.1831 | 0.050354 | 0.054932 | 0.022888 | -0.018311 | -0.10071 | 0.022888 | 0.091553 | 0.018311 | 0.1236 | 121.4081 | -0.10071 | -0.036621 | 121.5912 | 121.463 | 121.4584 | 0.054932 | 0.050354 | 121.3074 | -0.082398 | -0.041199 | 121.4996 | 121.5317 | 121.4264 | 0.2243 | 0.11902 | 0.1831 | 0.027466 | 0.19226 | 0.1236 | -0.036621 | 0.082397 | 121.3715 | 121.3898 | -0.064087 | -0.1648 | 121.4355 | 121.431 | 121.3989 | 121.431
2781.2188 | 121.3211 | -121.0602 | 0.054932 | 0.01358 | 0.011796 | -0.036927 | 0.034131 | -0.019549 | -0.030745 | -0.019828 | 0.0055542 | -0.063574 | -0.0026744 | 0.044724 | -0.01794 | -0.0081774 | -0.013324 | -0.036621 | -0.045776 | -0.013733 | 0 | 0.15106 | 0.064087 | 0.059509 | 0.027466 | 0.009155 | -0.068665 | 0.064087 | 0.17853 | 0.10071 | 0.1831 | 121.0464 | -0.10071 | -0.054932 | 121.2112 | 121.1197 | 121.1243 | 0.073242 | 0.07782 | 120.9915 | -0.045777 | 0.009155 | 121.2387 | 121.2433 | 121.1609 | 0.25177 | 0.16937 | 0.16479 | 0.013733 | 0.24719 | 0.13275 | -0.032043 | 0.07782 | 121.0144 | 121.0693 | -0.068665 | -0.1236 | 121.0602 | 121.1243 | 121.0236 | 121.0876
2782.9844 | 121.4172 | -121.2112 | 0.068665 | 0.02121 | 0.015855 | -0.034791 | 0.036908 | -0.020189 | -0.027967 | -0.022392 | 0.0055542 | -0.062506 | -0.00032465 | 0.038102 | -0.018367 | -0.010955 | -0.011615 | -0.032043 | 0 | -0.018311 | -0.013733 | 0.10986 | 0.013733 | 0.018311 | -0.004578 | 0.036621 | -0.082397 | 0.022888 | 0.09613 | 0.009155 | 0.13275 | 121.1929 | -0.068665 | -0.082398 | 121.3211 | 121.2296 | 121.225 | 0.036622 | 0.032044 | 121.1288 | -0.032044 | -0.045777 | 121.3074 | 121.344 | 121.2204 | 0.21515 | 0.091552 | 0.12817 | 0.004578 | 0.17853 | 0.10528 | 0.018311 | 0.11902 | 121.2112 | 121.2479 | -0.086976 | -0.15106 | 121.1975 | 121.2341 | 121.1792 | 121.2067
2784.6875 | 121.4035 | -121.3165 | 0.07782 | 0.0059509 | 0.016496 | -0.033936 | 0.035626 | -0.016985 | -0.026899 | -0.019615 | 0.0055542 | -0.063147 | -0.00011105 | 0.036606 | -0.01794 | -0.010527 | -0.021014 | -0.045776 | -0.009155 | -0.032043 | -0.073242 | 0.050354 | -0.050354 | -0.054932 | -0.091553 | 0.032043 | -0.082397 | -0.022888 | 0.022888 | -0.064087 | 0.09613 | 121.2845 | -0.086975 | -0.15106 | 121.3669 | 121.2616 | 121.2662 | -0.022889 | -0.018311 | 121.2341 | -0.045777 | -0.10071 | 121.3394 | 121.4127 | 121.2524 | 0.17853 | 0.01831 | 0.082397 | -0.041199 | 0.10528 | 0.059509 | 0.022888 | 0.11444 | 121.3074 | 121.3486 | -0.10986 | -0.16022 | 121.2433 | 121.2936 | 121.2708 | 121.225
2786.3906 | 121.5866 | -121.2982 | 0.041199 | 0.01358 | 0.012224 | -0.033936 | 0.032635 | -0.01848 | -0.030317 | -0.022819 | 0.0055542 | -0.062933 | -0.00011105 | 0.042588 | -0.018154 | -0.0094592 | -0.01311 | -0.036621 | -0.036621 | 0.004578 | 0.009155 | 0.16479 | 0.073242 | 0.07782 | 0.054932 | -0.009155 | -0.050354 | 0.068665 | 0.19684 | 0.10529 | 0.21515 | 121.3028 | -0.07782 | -0.032044 | 121.463 | 121.376 | 121.3715 | 0.073242 | 0.068664 | 121.2479 | -0.050354 | 0.027466 | 121.4951 | 121.5134 | 121.4035 | 0.2655 | 0.15564 | 0.16022 | 0.004577 | 0.24719 | 0.11902 | -0.041199 | 0.041199 | 121.2616 | 121.2891 | -0.036621 | -0.091553 | 121.3074 | 121.3669 | 121.2616 | 121.3531
2788.1094 | 121.2982 | -121.0373 | 0.059509 | -0.0016786 | 0.011583 | -0.033722 | 0.033276 | -0.020189 | -0.030531 | -0.022392 | 0.0025024 | -0.064215 | -0.00075185 | 0.039597 | -0.019649 | -0.0094592 | -0.013751 | -0.004578 | -0.054932 | -0.004578 | 0.041199 | 0.19684 | 0.091553 | 0.086975 | 0.091553 | 0.004578 | -0.054932 | 0.082397 | 0.19684 | 0.1236 | 0.18768 | 121.0327 | -0.11444 | -0.01831 | 121.2341 | 121.1243 | 121.1288 | 0.091553 | 0.096131 | 120.9824 | -0.054931 | 0.022888 | 121.2341 | 121.225 | 121.1609 | 0.24261 | 0.17853 | 0.20142 | 0.045777 | 0.25177 | 0.13733 | -0.050354 | 0.05951 | 120.9824 | 121.0419 | -0.064087 | -0.11444 | 121.0785 | 121.1197 | 121.0327 | 121.1288
2789.8125 | 121.4127 | -121.17 | 0.054932 | 0.036468 | 0.014573 | -0.031159 | 0.035626 | -0.011217 | -0.028608 | -0.023887 | 0.014709 | -0.063147 | -0.00075185 | 0.040238 | -0.016658 | -0.0094592 | -0.014819 | -0.013733 | -0.032043 | 0 | 0.032043 | 0.1831 | 0.045776 | 0.073242 | 0.091553 | 0 | -0.068665 | 0.064087 | 0.14191 | 0.045776 | 0.15106 | 121.17 | -0.086975 | -0.022889 | 121.3531 | 121.2433 | 121.2158 | 0.073242 | 0.045776 | 121.1014 | -0.054932 | 0.009155 | 121.312 | 121.3211 | 121.2158 | 0.21973 | 0.11444 | 0.1831 | 0.032043 | 0.21057 | 0.13275 | -0.032043 | 0.068665 | 121.138 | 121.17 | -0.054932 | -0.1236 | 121.2021 | 121.2341 | 121.1563 | 121.2616
2791.5156 | 121.4035 | -121.2662 | 0.07782 | 0.044098 | 0.013719 | -0.035218 | 0.037549 | -0.018694 | -0.028608 | -0.020897 | 0.0055542 | -0.06037 | 0.00010255 | 0.032548 | -0.02029 | -0.012023 | -0.012469 | -0.059509 | 0.018311 | -0.054932 | -0.068665 | 0.054932 | -0.009155 | -0.022888 | -0.064087 | 0.073242 | -0.082397 | -0.009155 | 0.073242 | -0.004578 | 0.11444 | 121.2112 | -0.059509 | -0.14649 | 121.3211 | 121.2433 | 121.257 | 0.032044 | 0.045777 | 121.1838 | -0.004578 | -0.086975 | 121.3394 | 121.3806 | 121.2616 | 0.19684 | 0.077819 | 0.10986 | -0.013733 | 0.15564 | 0.073242 | 0.073243 | 0.15564 | 121.2845 | 121.3394 | -0.13275 | -0.16022 | 121.1975 | 121.257 | 121.2067 | 121.2021
2793.2188 | 121.4172 | -121.2845 | 0.10529 | 0.036468 | 0.014573 | -0.034791 | 0.034985 | -0.024462 | -0.02989 | -0.019615 | 0.011658 | -0.062079 | 0.001598 | 0.032334 | -0.021999 | -0.0096728 | -0.014178 | -0.073242 | 0.009155 | -0.064087 | -0.082397 | 0.045776 | -0.018311 | -0.013733 | -0.082397 | 0.07782 | -0.09613 | -0.036621 | 0.054932 | -0.022888 | 0.10529 | 121.2204 | -0.096131 | -0.18768 | 121.3303 | 121.2708 | 121.2662 | 0.050354 | 0.045776 | 121.1884 | -0.027466 | -0.14191 | 121.3394 | 121.3898 | 121.2616 | 0.20142 | 0.073242 | 0.10986 | -0.01831 | 0.15106 | 0.059509 | 0.073242 | 0.17395 | 121.2936 | 121.3623 | -0.16937 | -0.20142 | 121.2021 | 121.2479 | 121.2112 | 121.2021
2794.9844 | 121.55 | -121.2891 | 0.041199 | 0.02121 | 0.015428 | -0.033722 | 0.035412 | -0.021044 | -0.026899 | -0.02111 | 0.008606 | -0.062506 | -0.00011105 | 0.041947 | -0.014095 | -0.0079638 | -0.011187 | 0 | -0.059509 | -0.009155 | 0.036621 | 0.18768 | 0.073242 | 0.068665 | 0.068665 | 0.004578 | -0.07782 | 0.059509 | 0.14648 | 0.064087 | 0.16937 | 121.2799 | -0.10071 | -0.004578 | 121.4767 | 121.3577 | 121.3623 | 0.07782 | 0.082397 | 121.2112 | -0.036621 | 0.01831 | 121.4355 | 121.4584 | 121.3531 | 0.24719 | 0.14191 | 0.19684 | 0.045776 | 0.2243 | 0.13733 | -0.050354 | 0.082398 | 121.2296 | 121.2936 | -0.050354 | -0.11902 | 121.3257 | 121.3486 | 121.2891 | 121.3577
2796.7188 | 121.5637 | -121.3074 | 0.045776 | 0.044098 | 0.015428 | -0.0318 | 0.03883 | -0.018267 | -0.026472 | -0.023674 | 0.0055542 | -0.063788 | 0.00095715 | 0.039597 | -0.01559 | -0.008391 | -0.013537 | 0.004578 | -0.050354 | 0.018311 | 0.059509 | 0.19684 | 0.059509 | 0.068665 | 0.082397 | -0.004578 | -0.068665 | 0.068665 | 0.15106 | 0.07782 | 0.16937 | 121.3257 | -0.09613 | 0.013733 | 121.5042 | 121.376 | 121.3669 | 0.050354 | 0.041198 | 121.2387 | -0.050354 | 0.022889 | 121.4584 | 121.4767 | 121.3852 | 0.23804 | 0.14649 | 0.17853 | 0.041198 | 0.21973 | 0.13733 | -0.068665 | 0.064087 | 121.257 | 121.3028 | -0.027465 | -0.11444 | 121.3669 | 121.376 | 121.312 | 121.3898
2798.4375 | 121.5271 | -121.344 | 0.068665 | 0.01358 | 0.014787 | -0.03415 | 0.035626 | -0.014422 | -0.027327 | -0.021965 | -0.00054937 | -0.060797 | 0.001598 | 0.033616 | -0.016017 | -0.0075366 | -0.013324 | -0.09613 | -0.004578 | -0.036621 | -0.07782 | 0.045776 | -0.054932 | -0.032043 | -0.059509 | 0.032043 | -0.073242 | 0.009155 | 0.059509 | -0.027466 | 0.11444 | 121.3074 | -0.073243 | -0.14649 | 121.3898 | 121.312 | 121.2891 | 0.004578 | -0.018311 | 121.2708 | -0.036622 | -0.05951 | 121.4035 | 121.4584 | 121.3165 | 0.18768 | 0.045776 | 0.082397 | -0.041199 | 0.13275 | 0.082397 | 0.032043 | 0.10529 | 121.3394 | 121.376 | -0.10529 | -0.14191 | 121.2662 | 121.3531 | 121.2479 | 121.2845
2800.1406 | 121.5042 | -121.3531 | 0.073242 | 0.0059509 | 0.015214 | -0.032868 | 0.038617 | -0.01549 | -0.028608 | -0.020683 | 0.0025024 | -0.063788 | -0.00053825 | 0.036179 | -0.018367 | -0.010314 | -0.016101 | -0.086975 | -0.009155 | -0.022888 | -0.09613 | 0.032043 | -0.07782 | -0.050354 | -0.082397 | 0.045776 | -0.10071 | -0.041199 | 0.032043 | -0.059509 | 0.086975 | 121.3303 | -0.082397 | -0.16937 | 121.3852 | 121.3028 | 121.2753 | -0.027466 | -0.054932 | 121.2524 | -0.027466 | -0.11444 | 121.3852 | 121.4401 | 121.2936 | 0.18768 | 0.041199 | 0.054931 | -0.073242 | 0.13275 | 0.059509 | 0.013733 | 0.14648 | 121.344 | 121.3989 | -0.09613 | -0.17395 | 121.257 | 121.3119 | 121.2662 | 121.2708
2801.9062 | 121.5729 | -121.3577 | 0.045776 | 0.01358 | 0.013933 | -0.035431 | 0.037335 | -0.015276 | -0.029463 | -0.022605 | 0.0025024 | -0.063574 | -0.00096545 | 0.036393 | -0.015163 | -0.0081774 | -0.013537 | -0.073242 | 0.004578 | -0.041199 | -0.07782 | 0.050354 | -0.050354 | -0.022888 | -0.041199 | -0.009155 | -0.091553 | 0.013733 | 0.09613 | 0.004578 | 0.13275 | 121.3165 | -0.041198 | -0.1236 | 121.4081 | 121.3348 | 121.3074 | 0.018311 | -0.009155 | 121.2662 | -0.054931 | -0.032043 | 121.4539 | 121.4905 | 121.3623 | 0.2243 | 0.096131 | 0.091553 | -0.036621 | 0.18768 | 0.10529 | 0.045777 | 0.082398 | 121.3623 | 121.3486 | -0.086975 | -0.13733 | 121.2799 | 121.3715 | 121.2845 | 121.3165
2803.6094 | 121.5408 | -121.4172 | 0.073242 | -0.0016786 | 0.015428 | -0.033295 | 0.037976 | -0.015703 | -0.02989 | -0.022392 | 0.0025024 | -0.061224 | 0.00052975 | 0.033188 | -0.01794 | -0.0101 | -0.012256 | -0.086975 | 0.013733 | -0.018311 | -0.091553 | 0.009155 | -0.086975 | -0.059509 | -0.10986 | 0.041199 | -0.091553 | -0.032043 | 0.009155 | -0.059509 | 0.082397 | 121.3989 | -0.059509 | -0.16479 | 121.4264 | 121.3577 | 121.3303 | -0.041198 | -0.068664 | 121.3257 | -0.032043 | -0.10529 | 121.4264 | 121.4996 | 121.3577 | 0.17395 | 0.032044 | 0.027466 | -0.073242 | 0.10071 | 0.05951 | 0.032044 | 0.13275 | 121.431 | 121.4584 | -0.091553 | -0.16479 | 121.3257 | 121.3852 | 121.3303 | 121.3074
2805.3125 | 121.6553 | -121.3806 | 0.050354 | 0.0059509 | 0.012437 | -0.034577 | 0.035199 | -0.01549 | -0.02754 | -0.022819 | 0.0025024 | -0.064642 | 0.0013844 | 0.037888 | -0.019435 | -0.0086048 | -0.013324 | -0.050354 | -0.018311 | -0.004578 | -0.022888 | 0.11902 | 0.045776 | 0.041199 | 0.004578 | -0.009155 | -0.054932 | 0.050354 | 0.15564 | 0.073242 | 0.16937 | 121.376 | -0.068665 | -0.073242 | 121.4996 | 121.4218 | 121.4264 | 0.045777 | 0.050354 | 121.3257 | -0.059509 | 0 | 121.5363 | 121.55 | 121.4539 | 0.22431 | 0.12817 | 0.1236 | -0.01831 | 0.21057 | 0.10529 | -0.013733 | 0.045777 | 121.3623 | 121.3715 | -0.054932 | -0.10529 | 121.3577 | 121.431 | 121.3303 | 121.3852
2807.0156 | 120.7077 | -120.314 | 0.15564 | 0.01358 | 0.010728 | -0.035645 | 0.033063 | -0.018694 | -0.030104 | -0.024314 | 0.0025024 | -0.066351 | 0.00010255 | 0.046647 | -0.018581 | -0.008391 | -0.012896 | -0.004578 | -0.068665 | 0.004578 | 0.050354 | 0.24261 | 0.1236 | 0.11444 | 0.054932 | -0.041199 | -0.082397 | 0.036621 | 0.16022 | 0.09613 | 0.14191 | 120.3186 | -0.22431 | -0.10529 | 120.5566 | 120.4285 | 120.4376 | 0.10986 | 0.11902 | 120.2316 | -0.19684 | -0.11902 | 120.4742 | 120.4559 | 120.4102 | 0.2243 | 0.17853 | 0.23804 | 0.045776 | 0.24261 | 0.11902 | -0.073243 | 0.041198 | 120.2454 | 120.2728 | -0.15106 | -0.23804 | 120.3644 | 120.3506 | 120.3094 | 120.369
2808.7188 | 120.9457 | -120.6665 | 0.064087 | 0.028839 | 0.013719 | -0.036072 | 0.034558 | -0.016771 | -0.031172 | -0.023246 | 0.0025024 | -0.064429 | -0.00053825 | 0.040238 | -0.018794 | -0.008391 | -0.0092648 | -0.050354 | -0.027466 | -0.018311 | -0.009155 | 0.12817 | 0.050354 | 0.054932 | -0.064087 | -0.068665 | -0.13733 | 0 | 0.10986 | 0.022888 | 0.11444 | 120.6482 | -0.091553 | -0.073242 | 120.7947 | 120.7214 | 120.7169 | 0.073243 | 0.068665 | 120.5292 | -0.13275 | -0.064087 | 120.7764 | 120.7809 | 120.6894 | 0.25177 | 0.16022 | 0.14649 | 0.009156 | 0.24719 | 0.13733 | -0.009155 | 0.068664 | 120.639 | 120.5978 | -0.082398 | -0.20142 | 120.6573 | 120.6665 | 120.6162 | 120.6024
2810.4219 | 121.0602 | -120.7947 | 0.045776 | 0.028839 | 0.014573 | -0.033722 | 0.036908 | -0.011217 | -0.028181 | -0.02111 | 0.0055542 | -0.06272 | -0.00032465 | 0.039811 | -0.016872 | -0.0086048 | -0.015246 | 0.018311 | -0.032043 | 0 | 0.064087 | 0.19684 | 0.07782 | 0.07782 | 0.018311 | -0.059509 | -0.14648 | -0.009155 | 0.086975 | 0 | 0.10986 | 120.7947 | -0.077819 | 0.018311 | 120.9915 | 120.8725 | 120.8725 | 0.07782 | 0.07782 | 120.6482 | -0.10528 | -0.054931 | 120.8817 | 120.9045 | 120.7947 | 0.25635 | 0.14648 | 0.19684 | 0.064087 | 0.23346 | 0.13733 | -0.032043 | 0.086975 | 120.7626 | 120.7352 | -0.045776 | -0.19226 | 120.8588 | 120.7855 | 120.813 | 120.813
2812.1406 | 121.138 | -120.8588 | 0.050354 | 0.0059509 | 0.015001 | -0.032227 | 0.036908 | -0.014635 | -0.027327 | -0.022605 | 0.0055542 | -0.063147 | -0.00096545 | 0.042588 | -0.01559 | -0.010314 | -0.014605 | -0.004578 | -0.036621 | 0.009155 | 0.018311 | 0.15106 | 0.050354 | 0.045776 | 0.009155 | -0.064087 | -0.10986 | 0.036621 | 0.10529 | 0.013733 | 0.16479 | 120.8679 | -0.086975 | -0.032043 | 121.0098 | 120.9045 | 120.9091 | 0.036621 | 0.041199 | 120.7489 | -0.11444 | -0.013733 | 120.9641 | 121.0236 | 120.8725 | 0.27466 | 0.1236 | 0.14191 | 0.009156 | 0.21515 | 0.14648 | -0.045776 | 0.045776 | 120.8221 | 120.7947 | -0.041199 | -0.16022 | 120.8771 | 120.8954 | 120.8542 | 120.8679
2813.9062 | 121.1929 | -120.9045 | 0.050354 | 0.0059509 | 0.015855 | -0.032654 | 0.039685 | -0.011858 | -0.027327 | -0.020256 | 0.014709 | -0.062079 | 0.00010255 | 0.037888 | -0.016872 | -0.0071094 | -0.010974 | 0.013733 | -0.045776 | -0.004578 | 0.054932 | 0.17853 | 0.082397 | 0.073242 | 0.041199 | -0.032043 | -0.11444 | 0.050354 | 0.11902 | 0.022888 | 0.13275 | 120.9 | -0.09613 | 0.004578 | 121.0831 | 120.9778 | 120.9869 | 0.07782 | 0.086975 | 120.7901 | -0.082397 | 0 | 121.0236 | 121.0373 | 120.9274 | 0.24719 | 0.13733 | 0.18311 | 0.05951 | 0.23346 | 0.16479 | -0.041198 | 0.082398 | 120.8588 | 120.8725 | -0.054932 | -0.16479 | 120.9595 | 120.9549 | 120.9183 | 120.9457
2815.625 | 121.1884 | -120.9503 | 0.045776 | 0.036468 | 0.013078 | -0.034363 | 0.035412 | -0.014422 | -0.028608 | -0.021751 | 0.008606 | -0.06272 | 0.00010255 | 0.041306 | -0.016872 | -0.0094592 | -0.011828 | -0.018311 | -0.032043 | 0.009155 | 0.041199 | 0.19226 | 0.064087 | 0.064087 | 0.036621 | -0.032043 | -0.1236 | 0.013733 | 0.082397 | 0.009155 | 0.11902 | 120.9595 | -0.077819 | -0.004577 | 121.1426 | 121.0144 | 121.0144 | 0.054932 | 0.054932 | 120.8267 | -0.077819 | -0.032043 | 121.0327 | 121.0693 | 120.9595 | 0.24261 | 0.13275 | 0.18311 | 0.032044 | 0.20599 | 0.13733 | -0.041198 | 0.091553 | 120.9183 | 120.9183 | -0.036621 | -0.16937 | 120.9915 | 120.9641 | 120.932 | 120.9869
2817.3438 | 121.1517 | -121.0052 | 0.073242 | 0.028839 | 0.015641 | -0.034577 | 0.03648 | -0.015703 | -0.028395 | -0.021537 | 0.0055542 | -0.061651 | -0.00032465 | 0.035325 | -0.020503 | -0.010527 | -0.01076 | -0.036621 | -0.018311 | -0.022888 | -0.013733 | 0.09613 | -0.004578 | 0.018311 | -0.050354 | 0 | -0.11444 | -0.032043 | 0.036621 | -0.054932 | 0.068665 | 120.9824 | -0.091553 | -0.086975 | 121.1014 | 121.0236 | 121.0007 | 0.041199 | 0.01831 | 120.8908 | -0.073242 | -0.10529 | 121.0419 | 121.0739 | 120.9503 | 0.18311 | 0.059509 | 0.11902 | 0.009155 | 0.15106 | 0.082398 | 0.004577 | 0.11444 | 120.9869 | 121.0052 | -0.09613 | -0.18768 | 120.9915 | 120.9732 | 120.9686 | 120.9549
2819.0781 | 121.2524 | -121.019 | 0.050354 | 0.028839 | 0.016923 | -0.027955 | 0.03648 | -0.014849 | -0.028181 | -0.02346 | 0.0055542 | -0.062506 | 0.0020252 | 0.038956 | -0.017726 | -0.0088184 | -0.014178 | -0.004578 | -0.050354 | -0.009155 | 0.050354 | 0.20142 | 0.059509 | 0.082397 | 0.032043 | -0.027466 | -0.10529 | 0.018311 | 0.09613 | 0.013733 | 0.1236 | 121.0098 | -0.10071 | 0 | 121.2204 | 121.1014 | 121.0785 | 0.091552 | 0.068664 | 120.9137 | -0.07782 | -0.032043 | 121.1151 | 121.1426 | 121.0327 | 0.22888 | 0.11902 | 0.21057 | 0.059509 | 0.20142 | 0.1236 | -0.041199 | 0.07782 | 120.9686 | 120.9915 | -0.059509 | -0.15564 | 121.0693 | 121.0373 | 121.0144 | 121.051
2820.7812 | 121.2982 | -121.0098 | 0.032043 | 0.02121 | 0.014573 | -0.031159 | 0.034985 | -0.016131 | -0.026045 | -0.021751 | 0.008606 | -0.064215 | -0.00011105 | 0.042801 | -0.017513 | -0.0088184 | -0.012256 | 0.009155 | -0.032043 | -0.004578 | 0.059509 | 0.19226 | 0.082397 | 0.082397 | 0.032043 | -0.045776 | -0.1236 | 0.036621 | 0.11444 | 0.013733 | 0.1236 | 121.0052 | -0.064086 | 0.027466 | 121.2021 | 121.0922 | 121.0922 | 0.086975 | 0.086975 | 120.8862 | -0.077819 | 0.004578 | 121.1243 | 121.1334 | 121.0236 | 0.24719 | 0.13733 | 0.19684 | 0.064087 | 0.23804 | 0.16022 | -0.027465 | 0.07782 | 120.9778 | 120.9641 | -0.036621 | -0.15564 | 121.0693 | 121.0464 | 121.019 | 121.0419
2822.4844 | 121.3303 | -121.0327 | 0.054932 | -0.0016786 | 0.013078 | -0.035645 | 0.035199 | -0.020403 | -0.030531 | -0.023033 | -0.00054937 | -0.064002 | -0.00032465 | 0.035325 | -0.019649 | -0.011382 | -0.014392 | -0.004578 | -0.054932 | 0.013733 | 0.050354 | 0.2243 | 0.11902 | 0.10986 | 0.10071 | -0.004578 | -0.059509 | 0.068665 | 0.20142 | 0.091553 | 0.1831 | 121.0464 | -0.10986 | -0.004578 | 121.257 | 121.1426 | 121.1517 | 0.09613 | 0.10529 | 120.9732 | -0.05951 | 0.013733 | 121.2341 | 121.2158 | 121.1243 | 0.24261 | 0.15106 | 0.21057 | 0.036621 | 0.26093 | 0.12817 | -0.068665 | 0.054931 | 120.9778 | 121.0281 | -0.041199 | -0.11444 | 121.0831 | 121.1014 | 121.0281 | 121.1334
2824.1875 | 121.3165 | -121.0968 | 0.054932 | 0.028839 | 0.013505 | -0.032227 | 0.035199 | -0.017626 | -0.027967 | -0.023246 | 0.0055542 | -0.063574 | -0.00096545 | 0.038315 | -0.017085 | -0.0092456 | -0.012896 | -0.059509 | -0.036621 | -0.013733 | -0.013733 | 0.11902 | 0.022888 | 0.036621 | -0.032043 | 0.004578 | -0.09613 | 0.004578 | 0.07782 | 0.009155 | 0.13275 | 121.0831 | -0.091553 | -0.068665 | 121.2158 | 121.1334 | 121.1197 | 0.050354 | 0.036621 | 121.0007 | -0.050354 | -0.050354 | 121.1746 | 121.2296 | 121.106 | 0.22888 | 0.10528 | 0.13275 | 0 | 0.17395 | 0.10071 | -0.022888 | 0.10071 | 121.0602 | 121.1014 | -0.068665 | -0.15106 | 121.0831 | 121.1014 | 121.0373 | 121.0648
2825.9375 | 121.376 | -121.1014 | 0.054932 | 0.0059509 | 0.011155 | -0.033082 | 0.034985 | -0.020617 | -0.030531 | -0.024314 | 0.0025024 | -0.063147 | -0.0026744 | 0.03447 | -0.020076 | -0.010527 | -0.011401 | -0.036621 | -0.032043 | 0.009155 | 0.022888 | 0.16479 | 0.059509 | 0.082397 | 0.050354 | 0.004578 | -0.07782 | 0.059509 | 0.16022 | 0.086975 | 0.17395 | 121.1105 | -0.086975 | -0.032044 | 121.2662 | 121.1838 | 121.1609 | 0.073242 | 0.050354 | 121.0236 | -0.050354 | 0.004577 | 121.2616 | 121.2753 | 121.1884 | 0.25177 | 0.16479 | 0.15564 | 0.013733 | 0.23804 | 0.13733 | -0.041198 | 0.082398 | 121.0693 | 121.106 | -0.045777 | -0.13275 | 121.1243 | 121.1609 | 121.0648 | 121.1517
2827.6406 | 121.3852 | -121.1243 | 0.050354 | 0.036468 | 0.015641 | -0.032441 | 0.034131 | -0.015276 | -0.029036 | -0.025383 | 0.008606 | -0.062933 | 0.0011708 | 0.035966 | -0.019649 | -0.010314 | -0.011187 | 0.013733 | -0.036621 | 0.022888 | 0.050354 | 0.19684 | 0.064087 | 0.073242 | 0.07782 | 0 | -0.082397 | 0.068665 | 0.13275 | 0.041199 | 0.14648 | 121.1472 | -0.086975 | 0 | 121.3211 | 121.1975 | 121.1884 | 0.050354 | 0.041199 | 121.0419 | -0.050354 | 0.018311 | 121.257 | 121.2708 | 121.1655 | 0.22888 | 0.1236 | 0.17395 | 0.027466 | 0.21515 | 0.15106 | -0.059509 | 0.082397 | 121.0876 | 121.1243 | -0.027466 | -0.13275 | 121.1746 | 121.1929 | 121.138 | 121.2021
2829.3594 | 121.2845 | -121.2112 | 0.10529 | -0.0016786 | 0.012437 | -0.035431 | 0.038189 | -0.02083 | -0.029463 | -0.022392 | 0.011658 | -0.061865 | 0.0011708 | 0.036393 | -0.021572 | -0.010741 | -0.017383 | -0.086975 | -0.009155 | -0.045776 | -0.07782 | 0.054932 | -0.018311 | -0.013733 | -0.086975 | 0.041199 | -0.12817 | -0.064087 | 0.027466 | -0.054932 | 0.064087 | 121.1655 | -0.11444 | -0.18311 | 121.2662 | 121.1975 | 121.1929 | 0.032043 | 0.027465 | 121.0831 | -0.064087 | -0.16937 | 121.2387 | 121.2753 | 121.1563 | 0.19226 | 0.073242 | 0.10071 | -0.032044 | 0.15564 | 0.064087 | 0.036621 | 0.16937 | 121.2021 | 121.2524 | -0.15106 | -0.23346 | 121.1334 | 121.1472 | 121.1243 | 121.1243
2831.0625 | 121.4447 | -121.1792 | 0.054932 | 0.0059509 | 0.011796 | -0.036927 | 0.033703 | -0.016985 | -0.030745 | -0.024314 | 0.0025024 | -0.062506 | 0.00095715 | 0.041733 | -0.021358 | -0.0096728 | -0.013965 | -0.013733 | -0.032043 | 0 | 0.050354 | 0.20599 | 0.09613 | 0.09613 | 0.07782 | -0.009155 | -0.054932 | 0.07782 | 0.17853 | 0.09613 | 0.16479 | 121.1792 | -0.086975 | -0.004578 | 121.3852 | 121.2753 | 121.2753 | 0.09613 | 0.09613 | 121.1243 | -0.064087 | 0.022888 | 121.3577 | 121.344 | 121.2753 | 0.21973 | 0.15106 | 0.20599 | 0.050354 | 0.23346 | 0.13275 | -0.032043 | 0.045777 | 121.1472 | 121.17 | -0.054932 | -0.10986 | 121.2296 | 121.257 | 121.1655 | 121.257
2832.8125 | 121.463 | -121.1975 | 0.045776 | 0.01358 | 0.013505 | -0.034363 | 0.035626 | -0.019549 | -0.028822 | -0.023033 | -0.00054937 | -0.063574 | -0.00075185 | 0.04387 | -0.017085 | -0.012236 | -0.013751 | -0.041199 | -0.050354 | -0.009155 | -0.004578 | 0.13275 | 0.050354 | 0.050354 | 0.004578 | -0.013733 | -0.082397 | 0.036621 | 0.13733 | 0.068665 | 0.16022 | 121.1884 | -0.09613 | -0.050354 | 121.3303 | 121.2479 | 121.2479 | 0.059509 | 0.059509 | 121.1151 | -0.059509 | -0.009155 | 121.3348 | 121.3577 | 121.2662 | 0.24261 | 0.15106 | 0.14191 | 0.004577 | 0.21973 | 0.11902 | -0.041199 | 0.068664 | 121.1472 | 121.1838 | -0.054931 | -0.12817 | 121.1929 | 121.2341 | 121.1563 | 121.2021
2834.5156 | 121.4401 | -121.2021 | 0.073242 | 0.02121 | 0.012864 | -0.035645 | 0.034985 | -0.017412 | -0.027754 | -0.021751 | 0.0055542 | -0.065711 | 0.00010255 | 0.035966 | -0.016658 | -0.010527 | -0.010119 | -0.041199 | -0.032043 | -0.018311 | -0.018311 | 0.1236 | 0.022888 | 0.041199 | -0.032043 | -0.018311 | -0.086975 | -0.004578 | 0.09613 | 0.013733 | 0.11902 | 121.1838 | -0.10529 | -0.091553 | 121.3257 | 121.2433 | 121.225 | 0.05951 | 0.041199 | 121.1151 | -0.091553 | -0.07782 | 121.2982 | 121.3211 | 121.2158 | 0.20599 | 0.10071 | 0.14191 | 0 | 0.1831 | 0.082397 | -0.013732 | 0.068664 | 121.17 | 121.1838 | -0.091553 | -0.16022 | 121.1838 | 121.1975 | 121.1609 | 121.17
2836.2188 | 121.4996 | -121.225 | 0.054932 | 0.01358 | 0.010087 | -0.033722 | 0.035626 | -0.021471 | -0.02754 | -0.023246 | 0.0055542 | -0.063788 | 0.0011708 | 0.043229 | -0.020076 | -0.0096728 | -0.015887 | -0.041199 | -0.041199 | -0.013733 | -0.009155 | 0.13275 | 0.059509 | 0.059509 | 0.004578 | -0.004578 | -0.091553 | 0.050354 | 0.15564 | 0.073242 | 0.15564 | 121.2112 | -0.096131 | -0.064087 | 121.3577 | 121.2845 | 121.2845 | 0.073242 | 0.073242 | 121.1334 | -0.05951 | -0.004578 | 121.3806 | 121.3806 | 121.2982 | 0.24719 | 0.16479 | 0.14648 | 0.004578 | 0.24719 | 0.14191 | -0.027466 | 0.086975 | 121.1838 | 121.2204 | -0.068665 | -0.14649 | 121.2158 | 121.2753 | 121.1838 | 121.2296
2837.9844 | 121.4447 | -121.2662 | 0.059509 | 0.02121 | 0.012651 | -0.034363 | 0.038617 | -0.015917 | -0.027113 | -0.022178 | 0.008606 | -0.064002 | 0.00010255 | 0.034684 | -0.018581 | -0.010527 | -0.016742 | -0.054932 | -0.032043 | -0.018311 | -0.013733 | 0.11444 | 0.018311 | 0.036621 | -0.036621 | -0.013733 | -0.082397 | 0 | 0.09613 | -0.009155 | 0.1236 | 121.2479 | -0.091552 | -0.073242 | 121.3806 | 121.3028 | 121.2845 | 0.054932 | 0.036622 | 121.1838 | -0.073242 | -0.059509 | 121.3623 | 121.3898 | 121.257 | 0.20599 | 0.073242 | 0.13275 | 0.004578 | 0.17853 | 0.082397 | -0.013732 | 0.068664 | 121.2341 | 121.2524 | -0.07782 | -0.14191 | 121.2524 | 121.2662 | 121.2112 | 121.2296
2839.6875 | 120.5704 | -120.4559 | 0.082397 | 0.02121 | 0.015855 | -0.033509 | 0.038617 | -0.016131 | -0.027967 | -0.022392 | 0.0025024 | -0.061865 | 0.0011708 | 0.036606 | -0.018794 | -0.010314 | -0.012896 | -0.036621 | -0.009155 | -0.032043 | -0.036621 | 0.073242 | -0.045776 | -0.022888 | -0.068665 | 0.027466 | -0.09613 | -0.054932 | 0.018311 | -0.073242 | 0.068665 | 120.4239 | -0.091552 | -0.11902 | 120.5292 | 120.433 | 120.4102 | 0.009155 | -0.013733 | 120.3598 | -0.054931 | -0.13733 | 120.4742 | 120.5246 | 120.3827 | 0.16479 | 0.022888 | 0.10529 | -0.004578 | 0.11444 | 0.041198 | 0.022888 | 0.1236 | 120.4468 | 120.4834 | -0.11444 | -0.17853 | 120.4193 | 120.401 | 120.4193 | 120.3873
2841.4219 | 120.8221 | -120.6894 | 0.091553 | 0.028839 | 0.014146 | -0.034363 | 0.03584 | -0.01549 | -0.027967 | -0.020897 | 0.008606 | -0.060797 | -0.00011105 | 0.030411 | -0.021358 | -0.010741 | -0.011615 | -0.068665 | -0.004578 | -0.041199 | -0.059509 | 0.045776 | -0.009155 | -0.013733 | -0.082397 | 0.045776 | -0.11444 | -0.018311 | 0.068665 | -0.036621 | 0.10071 | 120.6482 | -0.096131 | -0.15106 | 120.7352 | 120.6757 | 120.6802 | 0.027466 | 0.032044 | 120.575 | -0.045777 | -0.10986 | 120.7581 | 120.7901 | 120.6528 | 0.21515 | 0.07782 | 0.086975 | -0.01831 | 0.18311 | 0.09613 | 0.036621 | 0.16022 | 120.6848 | 120.7352 | -0.13275 | -0.20599 | 120.6299 | 120.6711 | 120.6207 | 120.607
2843.1406 | 121.0007 | -120.726 | 0.054932 | 0.01358 | 0.015214 | -0.033295 | 0.034772 | -0.015917 | -0.02754 | -0.021965 | 0.0025024 | -0.063788 | -0.00053825 | 0.040238 | -0.015804 | -0.010314 | -0.012256 | -0.064087 | -0.022888 | -0.032043 | -0.045776 | 0.068665 | -0.041199 | -0.009155 | -0.036621 | -0.032043 | -0.09613 | 0.027466 | 0.09613 | 0.022888 | 0.15564 | 120.694 | -0.07782 | -0.10071 | 120.7947 | 120.7169 | 120.6848 | 0.022888 | -0.009156 | 120.6299 | -0.086975 | -0.027466 | 120.8221 | 120.8817 | 120.7489 | 0.25177 | 0.11902 | 0.10071 | -0.013733 | 0.19226 | 0.1236 | 0.009155 | 0.064087 | 120.7031 | 120.694 | -0.086975 | -0.15106 | 120.6802 | 120.7535 | 120.6619 | 120.6894
2844.9062 | 121.0785 | -120.7993 | 0.045776 | 0.0059509 | 0.013078 | -0.033722 | 0.034985 | -0.018694 | -0.027967 | -0.022819 | 0.0055542 | -0.065283 | 0.00031615 | 0.038102 | -0.01559 | -0.008391 | -0.012683 | -0.027466 | -0.041199 | 0.013733 | 0.018311 | 0.16937 | 0.082397 | 0.073242 | 0.036621 | -0.027466 | -0.082397 | 0.059509 | 0.16022 | 0.086975 | 0.16022 | 120.813 | -0.086975 | -0.027465 | 120.9686 | 120.8725 | 120.8817 | 0.059509 | 0.068664 | 120.7169 | -0.073242 | 0.013733 | 120.9595 | 120.9595 | 120.8862 | 0.24261 | 0.16937 | 0.15564 | 0.004578 | 0.24261 | 0.14191 | -0.054932 | 0.054931 | 120.7581 | 120.7718 | -0.032043 | -0.12817 | 120.8176 | 120.8588 | 120.7718 | 120.8359
2846.6094 | 121.0281 | -120.8771 | 0.068665 | 0.01358 | 0.016069 | -0.034363 | 0.03883 | -0.014208 | -0.027754 | -0.022392 | 0.0055542 | -0.061224 | 0.00095715 | 0.036179 | -0.017513 | -0.010314 | -0.011828 | -0.073242 | -0.004578 | -0.036621 | -0.09613 | 0.036621 | -0.064087 | -0.045776 | -0.091553 | -0.009155 | -0.11902 | -0.050354 | 0.022888 | -0.082397 | 0.054932 | 120.8405 | -0.073243 | -0.16479 | 120.9137 | 120.8313 | 120.813 | -0.009155 | -0.027466 | 120.7581 | -0.07782 | -0.11902 | 120.9 | 120.932 | 120.7947 | 0.17395 | 0.036622 | 0.073242 | -0.059509 | 0.14191 | 0.068665 | 0.032043 | 0.10986 | 120.8725 | 120.8679 | -0.10529 | -0.18768 | 120.7809 | 120.8267 | 120.8038 | 120.7855
2848.3594 | 121.1655 | -120.8862 | 0.064087 | 0.0059509 | 0.015214 | -0.035004 | 0.03648 | -0.014422 | -0.030531 | -0.020042 | 0.0055542 | -0.063361 | -0.00053825 | 0.039811 | -0.014308 | -0.0096728 | -0.014605 | 0.004578 | -0.041199 | -0.009155 | 0.036621 | 0.15564 | 0.045776 | 0.054932 | 0.022888 | -0.036621 | -0.07782 | 0.068665 | 0.12817 | 0.036621 | 0.16479 | 120.8771 | -0.10529 | -0.027466 | 121.0419 | 120.9412 | 120.932 | 0.064087 | 0.054931 | 120.8084 | -0.10071 | 0.004578 | 121.0144 | 121.051 | 120.9229 | 0.24261 | 0.11444 | 0.16479 | 0.045776 | 0.20599 | 0.14649 | -0.032044 | 0.041199 | 120.845 | 120.8496 | -0.073242 | -0.14191 | 120.9229 | 120.9549 | 120.8908 | 120.9091
2850.0781 | 121.1151 | -120.9366 | 0.07782 | 0.01358 | 0.013505 | -0.034577 | 0.037335 | -0.015062 | -0.029249 | -0.021965 | 0.0055542 | -0.062292 | 0.0011708 | 0.042161 | -0.016231 | -0.009032 | -0.017383 | -0.07782 | -0.009155 | -0.032043 | -0.068665 | 0.050354 | -0.064087 | -0.036621 | -0.091553 | -0.027466 | -0.11902 | -0.018311 | 0.041199 | -0.045776 | 0.07782 | 120.9045 | -0.086975 | -0.14649 | 120.9869 | 120.9 | 120.8725 | -0.004578 | -0.032044 | 120.8176 | -0.10529 | -0.096131 | 120.9778 | 121.0144 | 120.8908 | 0.19684 | 0.073243 | 0.082397 | -0.036622 | 0.16022 | 0.10071 | 0.022888 | 0.091553 | 120.9274 | 120.9091 | -0.10986 | -0.19684 | 120.8679 | 120.9183 | 120.8588 | 120.845
2851.7812 | 121.1655 | -120.9824 | 0.07782 | 0.028839 | 0.017137 | -0.032868 | 0.037762 | -0.017199 | -0.028181 | -0.023246 | 0.0055542 | -0.061438 | 0.00031615 | 0.030839 | -0.018367 | -0.0098864 | -0.013965 | -0.032043 | -0.013733 | -0.032043 | -0.036621 | 0.10529 | 0.013733 | 0.018311 | -0.059509 | -0.018311 | -0.13275 | -0.018311 | 0.073242 | -0.036621 | 0.082397 | 120.9503 | -0.091553 | -0.11444 | 121.0876 | 121.0007 | 120.9961 | 0.050354 | 0.045776 | 120.8496 | -0.096131 | -0.096131 | 121.0556 | 121.0648 | 120.9457 | 0.21515 | 0.09613 | 0.13733 | -0.004578 | 0.20599 | 0.11444 | 0.01831 | 0.11444 | 120.9686 | 120.9641 | -0.10986 | -0.21057 | 120.9457 | 120.9641 | 120.9503 | 120.9229
2853.4844 | 121.0693 | -120.9686 | 0.045776 | 0.0059509 | 0.015428 | -0.033509 | 0.036908 | -0.014208 | -0.027113 | -0.021751 | -0.00054937 | -0.062079 | -0.00096545 | 0.041306 | -0.016231 | -0.0077502 | -0.010974 | -0.068665 | 0.004578 | -0.027466 | -0.064087 | 0.059509 | -0.041199 | -0.022888 | -0.059509 | -0.022888 | -0.11444 | -0.009155 | 0.059509 | -0.018311 | 0.11444 | 120.9412 | -0.041198 | -0.10986 | 121.0281 | 120.9457 | 120.9274 | 0.004578 | -0.013733 | 120.8542 | -0.068664 | -0.054931 | 121.0281 | 121.0831 | 120.9503 | 0.22888 | 0.09613 | 0.086975 | -0.036621 | 0.17395 | 0.10529 | 0.032044 | 0.091553 | 120.9732 | 120.9457 | -0.073242 | -0.16022 | 120.9045 | 120.9595 | 120.9 | 120.9091
2855.1875 | 121.1929 | -121.019 | 0.082397 | 0.0059509 | 0.014146 | -0.035004 | 0.037335 | -0.01314 | -0.029463 | -0.021751 | 0.0055542 | -0.063574 | -0.00011105 | 0.037247 | -0.017726 | -0.0092456 | -0.012469 | -0.091553 | -0.009155 | -0.027466 | -0.091553 | 0.050354 | -0.054932 | -0.027466 | -0.091553 | -0.009155 | -0.10986 | -0.041199 | 0.027466 | -0.068665 | 0.086975 | 120.9915 | -0.091552 | -0.17395 | 121.0693 | 120.9915 | 120.9641 | 0 | -0.027466 | 120.9091 | -0.091552 | -0.1236 | 121.0464 | 121.106 | 120.9503 | 0.19684 | 0.041198 | 0.07782 | -0.064087 | 0.13733 | 0.068664 | 0.018311 | 0.10071 | 121.0098 | 121.0098 | -0.10986 | -0.19226 | 120.9274 | 120.9778 | 120.9274 | 120.9274
2856.9219 | 121.312 | -121.0144 | 0.045776 | 0.02121 | 0.013933 | -0.033509 | 0.036267 | -0.016771 | -0.026899 | -0.022819 | 0.0025024 | -0.064856 | -0.0024608 | 0.039811 | -0.017726 | -0.008391 | -0.016314 | 0.004578 | -0.041199 | 0 | 0.022888 | 0.16937 | 0.059509 | 0.059509 | 0.018311 | -0.064087 | -0.10986 | 0.045776 | 0.10529 | 0.036621 | 0.15106 | 121.0144 | -0.086975 | -0.022888 | 121.1838 | 121.0739 | 121.0739 | 0.059509 | 0.059509 | 120.9045 | -0.10986 | 0 | 121.1197 | 121.1655 | 121.051 | 0.26093 | 0.14648 | 0.16937 | 0.022888 | 0.21515 | 0.15564 | -0.041199 | 0.045776 | 120.9732 | 120.9503 | -0.045776 | -0.15564 | 121.0373 | 121.0602 | 121.019 | 121.0327
2858.625 | 120.3552 | -120.2225 | 0.059509 | 0.01358 | 0.014573 | -0.030945 | 0.034131 | -0.014635 | -0.028608 | -0.023246 | 0.008606 | -0.065283 | 0.00052975 | 0.038102 | -0.019649 | -0.0098864 | -0.014178 | -0.064087 | -0.032043 | -0.009155 | -0.018311 | 0.11444 | 0.018311 | 0.041199 | -0.10071 | -0.10529 | -0.15564 | -0.073242 | 0 | -0.059509 | 0.027466 | 120.2133 | -0.091552 | -0.07782 | 120.3369 | 120.2637 | 120.2408 | 0.050354 | 0.027466 | 120.0668 | -0.16479 | -0.13275 | 120.2225 | 120.2499 | 120.163 | 0.18311 | 0.096131 | 0.1236 | -0.009156 | 0.15564 | 0.082398 | -0.022888 | 0.050354 | 120.1904 | 120.1172 | -0.068664 | -0.21515 | 120.2042 | 120.1492 | 120.1584 | 120.1218
2860.3594 | 120.8176 | -120.7581 | 0.10986 | 0.028839 | 0.014146 | -0.035431 | 0.035199 | -0.019976 | -0.029036 | -0.022178 | 0.008606 | -0.062933 | -0.00032465 | 0.031052 | -0.019008 | -0.0094592 | -0.0099056 | -0.059509 | -0.004578 | -0.013733 | -0.07782 | 0.086975 | 0.013733 | -0.009155 | -0.16937 | -0.068665 | -0.18768 | -0.15564 | -0.045776 | -0.11902 | -0.022888 | 120.7443 | -0.11444 | -0.18768 | 120.845 | 120.7489 | 120.7718 | 0.004578 | 0.027466 | 120.5704 | -0.17853 | -0.2655 | 120.7123 | 120.7352 | 120.639 | 0.16479 | 0.068664 | 0.10071 | -0.064087 | 0.14191 | 0.032043 | 0.009155 | 0.11902 | 120.7535 | 120.6894 | -0.1236 | -0.29755 | 120.6802 | 120.6024 | 120.6985 | 120.5887
2862.0625 | 121.0236 | -120.7581 | 0.068665 | -0.0016786 | 0.013505 | -0.03415 | 0.033703 | -0.013994 | -0.030531 | -0.022392 | 0.008606 | -0.064002 | -0.0020336 | 0.041092 | -0.020076 | -0.0094592 | -0.012256 | -0.013733 | -0.041199 | -0.018311 | 0.032043 | 0.18768 | 0.09613 | 0.086975 | -0.054932 | -0.10071 | -0.15564 | -0.050354 | 0.073242 | -0.004578 | 0.059509 | 120.7397 | -0.10986 | -0.036622 | 120.9457 | 120.845 | 120.8542 | 0.10529 | 0.11444 | 120.6024 | -0.16937 | -0.11902 | 120.8313 | 120.8176 | 120.7535 | 0.21515 | 0.15106 | 0.20599 | 0.050354 | 0.22888 | 0.10529 | -0.022888 | 0.054932 | 120.7169 | 120.6573 | -0.086976 | -0.22431 | 120.7901 | 120.7077 | 120.7443 | 120.7031
2863.7656 | 121.0922 | -120.8221 | 0.068665 | 0.01358 | 0.013505 | -0.029664 | 0.034131 | -0.02318 | -0.025831 | -0.020469 | 0.017761 | -0.06272 | -0.00032465 | 0.04152 | -0.016231 | -0.0075366 | -0.015887 | 0.004578 | -0.050354 | 0.032043 | 0.064087 | 0.18768 | 0.064087 | 0.07782 | -0.032043 | -0.10071 | -0.19684 | -0.036621 | 0.064087 | -0.045776 | 0.064087 | 120.8542 | -0.11902 | -0.004578 | 121.0098 | 120.9 | 120.8862 | 0.045777 | 0.032044 | 120.6253 | -0.16937 | -0.10529 | 120.8862 | 120.8862 | 120.7764 | 0.26093 | 0.15106 | 0.15564 | 0.032044 | 0.26093 | 0.16022 | -0.082397 | 0.09613 | 120.7718 | 120.7214 | -0.036622 | -0.2655 | 120.8862 | 120.7855 | 120.8267 | 120.7901
2865.5 | 121.0648 | -120.8862 | 0.086975 | 0.036468 | 0.01436 | -0.032868 | 0.036908 | -0.017199 | -0.029036 | -0.023246 | 0.008606 | -0.061651 | -0.00075185 | 0.038743 | -0.019222 | -0.010955 | -0.012683 | -0.027466 | -0.022888 | -0.036621 | -0.041199 | 0.086975 | 0.018311 | 0 | -0.15564 | -0.068665 | -0.1831 | -0.11902 | -0.013733 | -0.12817 | 0.004578 | 120.8496 | -0.10986 | -0.12817 | 120.9732 | 120.8862 | 120.9045 | 0.036621 | 0.054932 | 120.7031 | -0.15564 | -0.20599 | 120.8725 | 120.8908 | 120.7581 | 0.18768 | 0.054931 | 0.1236 | -0.004578 | 0.16937 | 0.064086 | 0.013733 | 0.11444 | 120.8633 | 120.8176 | -0.1236 | -0.27008 | 120.845 | 120.7672 | 120.8588 | 120.7306
2867.2031 | 121.17 | -120.9137 | 0.059509 | 0.01358 | 0.014573 | -0.032654 | 0.033917 | -0.022539 | -0.029036 | -0.020469 | 0.0055542 | -0.065497 | -0.0011792 | 0.038102 | -0.019649 | -0.0092456 | -0.014605 | -0.018311 | -0.045776 | -0.004578 | 0.050354 | 0.20599 | 0.09613 | 0.09613 | -0.050354 | -0.1236 | -0.16479 | -0.045776 | 0.068665 | -0.004578 | 0.07782 | 120.9091 | -0.10528 | -0.009155 | 121.1197 | 121.0098 | 121.0098 | 0.10071 | 0.10071 | 120.7489 | -0.1831 | -0.10528 | 120.9824 | 120.9915 | 120.9091 | 0.24261 | 0.16022 | 0.21057 | 0.054932 | 0.23346 | 0.11902 | -0.041198 | 0.041199 | 120.8679 | 120.7901 | -0.064087 | -0.2243 | 120.9641 | 120.8679 | 120.8954 | 120.8633
2868.9062 | 121.2021 | -120.9183 | 0.054932 | 0.02121 | 0.012651 | -0.035645 | 0.035412 | -0.018694 | -0.029676 | -0.022605 | 0.0055542 | -0.06507 | -0.00011105 | 0.036606 | -0.018154 | -0.009032 | -0.009692 | -0.041199 | -0.045776 | 0 | 0.009155 | 0.19226 | 0.086975 | 0.09613 | -0.036621 | -0.12817 | -0.16479 | -0.036621 | 0.07782 | 0 | 0.091553 | 120.9183 | -0.10071 | -0.045777 | 121.1105 | 121.0144 | 121.0052 | 0.09613 | 0.086975 | 120.7535 | -0.18311 | -0.091553 | 120.9961 | 121.0098 | 120.9183 | 0.25635 | 0.16479 | 0.19226 | 0.009155 | 0.24261 | 0.12817 | -0.045776 | 0.036621 | 120.8725 | 120.7901 | -0.054932 | -0.21973 | 120.9274 | 120.8817 | 120.8771 | 120.8817
2870.625 | 121.1472 | -120.9915 | 0.082397 | 0.02121 | 0.015428 | -0.033722 | 0.03584 | -0.016985 | -0.028608 | -0.022819 | 0.0055542 | -0.061865 | -0.00011105 | 0.036179 | -0.019863 | -0.0094592 | -0.014178 | -0.073242 | 0.013733 | -0.073242 | -0.082397 | 0.036621 | -0.018311 | -0.022888 | -0.21057 | -0.082397 | -0.21515 | -0.14648 | -0.059509 | -0.13733 | -0.013733 | 120.9183 | -0.068664 | -0.16479 | 121.0281 | 120.9686 | 120.9732 | 0.050354 | 0.054931 | 120.7764 | -0.16479 | -0.22888 | 120.932 | 120.9778 | 120.8542 | 0.20142 | 0.07782 | 0.10986 | -0.009155 | 0.15564 | 0.068665 | 0.086975 | 0.13275 | 121.0052 | 120.9091 | -0.15564 | -0.29755 | 120.9091 | 120.845 | 120.9183 | 120.7809
2872.3438 | 119.1605 | -119.133 | 0.091553 | 0.0059509 | 0.016496 | -0.031373 | 0.036908 | -0.016985 | -0.028608 | -0.021324 | 0.0025024 | -0.061438 | 0.0013844 | 0.03682 | -0.016658 | -0.0101 | -0.014178 | -0.086975 | -0.009155 | -0.032043 | -0.10986 | 0.022888 | -0.073242 | -0.045776 | -0.17853 | -0.027466 | -0.15106 | -0.11444 | -0.050354 | -0.15106 | 0.013733 | 119.101 | -0.10071 | -0.20142 | 119.1559 | 119.0872 | 119.0598 | -0.013733 | -0.041199 | 118.9819 | -0.11902 | -0.20599 | 119.0826 | 119.1467 | 118.9819 | 0.16479 | 0 | 0.054931 | -0.07782 | 0.10071 | 0.036621 | 0.022888 | 0.1236 | 119.1238 | 119.1055 | -0.1236 | -0.24261 | 119.0231 | 119.0186 | 119.046 | 118.9545
2874.0625 | 119.5404 | -119.5312 | 0.09613 | 0.0059509 | 0.012437 | -0.034577 | 0.037976 | -0.016131 | -0.028395 | -0.024955 | 0.0055542 | -0.062506 | 0.00074335 | 0.03682 | -0.017299 | -0.0086048 | -0.0094784 | -0.10071 | -0.004578 | -0.032043 | -0.10529 | 0.013733 | -0.07782 | -0.064087 | -0.16937 | -0.004578 | -0.16022 | -0.11444 | -0.059509 | -0.1236 | 0.022888 | 119.4992 | -0.10071 | -0.20142 | 119.545 | 119.4672 | 119.4534 | -0.032044 | -0.045777 | 119.371 | -0.10071 | -0.21057 | 119.4717 | 119.5541 | 119.4077 | 0.1831 | 0.036621 | 0.045776 | -0.073243 | 0.10071 | 0.045776 | 0.027465 | 0.15564 | 119.5267 | 119.5267 | -0.12817 | -0.25635 | 119.426 | 119.4168 | 119.4305 | 119.3619
2875.7656 | 120.4697 | -120.3918 | 0.10986 | 0.036468 | 0.014146 | -0.035431 | 0.037121 | -0.014849 | -0.027967 | -0.022819 | 0.011658 | -0.06272 | 0.0011708 | 0.033829 | -0.021144 | -0.0098864 | -0.013324 | -0.064087 | 0.018311 | -0.064087 | -0.086975 | 0.041199 | -0.013733 | -0.022888 | -0.16479 | 0.009155 | -0.16937 | -0.11444 | 0 | -0.086975 | 0.036621 | 120.3278 | -0.091552 | -0.19684 | 120.433 | 120.369 | 120.3781 | 0.041199 | 0.050354 | 120.2225 | -0.10071 | -0.2243 | 120.3918 | 120.4285 | 120.3049 | 0.20599 | 0.082398 | 0.10529 | -0.022888 | 0.16937 | 0.054932 | 0.082398 | 0.17853 | 120.4102 | 120.401 | -0.17395 | -0.27924 | 120.3049 | 120.2774 | 120.3278 | 120.2271
2877.4844 | 120.639 | -120.4514 | 0.059509 | 0.028839 | 0.01201 | -0.031373 | 0.035412 | -0.015703 | -0.030317 | -0.022178 | 0.011658 | -0.064002 | 0.0020252 | 0.040665 | -0.015377 | -0.0088184 | -0.015033 | -0.045776 | -0.041199 | 0.013733 | -0.022888 | 0.12817 | 0.027466 | 0.041199 | -0.07782 | -0.050354 | -0.13733 | -0.045776 | 0.050354 | -0.041199 | 0.068665 | 120.4651 | -0.10071 | -0.082397 | 120.5795 | 120.4926 | 120.4788 | 0.027466 | 0.013733 | 120.314 | -0.10986 | -0.10528 | 120.5017 | 120.52 | 120.4102 | 0.20599 | 0.09613 | 0.11444 | -0.036621 | 0.18768 | 0.091553 | -0.054932 | 0.086975 | 120.4102 | 120.401 | -0.045776 | -0.19684 | 120.4285 | 120.4056 | 120.4056 | 120.3735
2879.2031 | 120.7947 | -120.52 | 0.064087 | 0.028839 | 0.011583 | -0.035004 | 0.033917 | -0.020189 | -0.029036 | -0.022178 | 0.0025024 | -0.064002 | 0.00010255 | 0.03682 | -0.018154 | -0.010527 | -0.013751 | -0.022888 | -0.050354 | 0 | 0.045776 | 0.22888 | 0.10529 | 0.10071 | 0.050354 | -0.082397 | -0.11902 | 0 | 0.12817 | 0.045776 | 0.1236 | 120.52 | -0.11444 | -0.018311 | 120.7489 | 120.6207 | 120.6253 | 0.10071 | 0.10529 | 120.401 | -0.14648 | -0.064087 | 120.6482 | 120.6436 | 120.5658 | 0.24261 | 0.16479 | 0.22888 | 0.045776 | 0.24719 | 0.11902 | -0.050354 | 0.036622 | 120.4697 | 120.4376 | -0.064087 | -0.18311 | 120.5658 | 120.52 | 120.4971 | 120.5704
2880.9062 | 120.813 | -120.5887 | 0.068665 | -0.0016786 | 0.013292 | -0.033082 | 0.034131 | -0.02318 | -0.029036 | -0.022605 | -0.00054937 | -0.066138 | -0.00032465 | 0.042801 | -0.016017 | -0.0094592 | -0.014605 | -0.050354 | -0.036621 | 0.009155 | -0.018311 | 0.10986 | 0.032043 | 0.054932 | -0.07782 | -0.068665 | -0.15564 | -0.045776 | 0.068665 | -0.018311 | 0.086975 | 120.5978 | -0.10529 | -0.086976 | 120.6985 | 120.6436 | 120.6207 | 0.045777 | 0.022888 | 120.433 | -0.13733 | -0.11444 | 120.6573 | 120.6757 | 120.5704 | 0.24261 | 0.13733 | 0.10071 | -0.027466 | 0.22431 | 0.10986 | -0.045776 | 0.086975 | 120.5521 | 120.52 | -0.05951 | -0.22431 | 120.5704 | 120.5429 | 120.5383 | 120.5109
2882.625 | 120.8359 | -120.5978 | 0.054932 | 0.028839 | 0.016069 | -0.033082 | 0.035626 | -0.016771 | -0.027967 | -0.023033 | 0.008606 | -0.063361 | 0.0024524 | 0.03447 | -0.015804 | -0.0079638 | -0.014392 | -0.004578 | -0.054932 | 0.009155 | 0.045776 | 0.19226 | 0.054932 | 0.07782 | -0.009155 | -0.068665 | -0.15564 | -0.009155 | 0.059509 | -0.018311 | 0.07782 | 120.607 | -0.10986 | -0.009156 | 120.7901 | 120.6757 | 120.6528 | 0.068665 | 0.045777 | 120.4422 | -0.1236 | -0.064087 | 120.6573 | 120.6757 | 120.5795 | 0.23346 | 0.13733 | 0.18311 | 0.036621 | 0.21515 | 0.14649 | -0.064087 | 0.086975 | 120.5429 | 120.5292 | -0.045777 | -0.21057 | 120.6436 | 120.5887 | 120.5933 | 120.5887
2884.3906 | 120.8221 | -120.7077 | 0.09613 | 0.028839 | 0.013719 | -0.035431 | 0.038189 | -0.016131 | -0.030104 | -0.021324 | 0.011658 | -0.062506 | -0.0024608 | 0.035752 | -0.020503 | -0.0096728 | -0.010547 | -0.082397 | 0.018311 | -0.054932 | -0.059509 | 0.041199 | -0.032043 | -0.013733 | -0.16479 | -0.004578 | -0.17853 | -0.14191 | -0.054932 | -0.11902 | 0 | 120.6528 | -0.077819 | -0.15564 | 120.7489 | 120.694 | 120.6757 | 0.041199 | 0.022889 | 120.5292 | -0.10071 | -0.23804 | 120.6528 | 120.7077 | 120.5887 | 0.17853 | 0.059509 | 0.096131 | -0.004577 | 0.1236 | 0.036621 | 0.073243 | 0.17395 | 120.726 | 120.7031 | -0.15106 | -0.27466 | 120.6482 | 120.5658 | 120.6253 | 120.5429
2886.0938 | 120.9503 | -120.6894 | 0.068665 | 0.0059509 | 0.014146 | -0.033722 | 0.032635 | -0.019121 | -0.029036 | -0.020683 | 0.0055542 | -0.064642 | -0.0011792 | 0.039597 | -0.020076 | -0.010527 | -0.016101 | -0.013733 | -0.050354 | 0 | 0.054932 | 0.1831 | 0.086975 | 0.082397 | -0.022888 | -0.07782 | -0.12817 | -0.013733 | 0.086975 | 0.013733 | 0.10071 | 120.6894 | -0.11902 | -0.013733 | 120.8725 | 120.7718 | 120.7764 | 0.082397 | 0.086975 | 120.5612 | -0.14649 | -0.082398 | 120.7764 | 120.7901 | 120.7031 | 0.22888 | 0.14191 | 0.1831 | 0.054932 | 0.21515 | 0.11444 | -0.050354 | 0.050354 | 120.639 | 120.6116 | -0.068665 | -0.19684 | 120.7443 | 120.6757 | 120.6757 | 120.6665
2887.8281 | 120.8679 | -120.7855 | 0.10529 | 0.01358 | 0.015428 | -0.035218 | 0.03648 | -0.016771 | -0.029036 | -0.022178 | 0.0055542 | -0.061865 | -0.00075185 | 0.035111 | -0.021572 | -0.010527 | -0.015674 | -0.091553 | -0.013733 | -0.036621 | -0.086975 | 0.041199 | -0.045776 | -0.018311 | -0.16022 | -0.041199 | -0.16022 | -0.13275 | -0.045776 | -0.11444 | 0.004578 | 120.7489 | -0.11902 | -0.19226 | 120.8267 | 120.7672 | 120.7397 | 0.01831 | -0.009155 | 120.6253 | -0.14649 | -0.23804 | 120.7397 | 120.7901 | 120.6711 | 0.16479 | 0.045776 | 0.07782 | -0.050354 | 0.11444 | 0.027466 | 0.022888 | 0.11902 | 120.7718 | 120.7443 | -0.14191 | -0.2655 | 120.6985 | 120.6528 | 120.694 | 120.6253
2889.5469 | 120.9183 | -120.7855 | 0.082397 | 0.028839 | 0.013719 | -0.033936 | 0.037335 | -0.021258 | -0.030745 | -0.024101 | 0.0055542 | -0.060797 | -0.00053825 | 0.031052 | -0.020503 | -0.0096728 | -0.015033 | -0.082397 | 0.022888 | -0.045776 | -0.07782 | 0.041199 | -0.027466 | -0.022888 | -0.17853 | -0.041199 | -0.1831 | -0.14648 | -0.036621 | -0.10986 | 0.018311 | 120.7397 | -0.059509 | -0.16022 | 120.8267 | 120.7626 | 120.7581 | 0.022888 | 0.01831 | 120.6024 | -0.1236 | -0.22888 | 120.7489 | 120.8038 | 120.6757 | 0.20142 | 0.073242 | 0.086975 | -0.032044 | 0.14648 | 0.036621 | 0.068664 | 0.14191 | 120.8084 | 120.7443 | -0.12817 | -0.2655 | 120.7077 | 120.639 | 120.7031 | 120.607
2891.25 | 120.9961 | -120.813 | 0.086975 | 0.028839 | 0.013719 | -0.036072 | 0.037335 | -0.018053 | -0.028822 | -0.020256 | 0.008606 | -0.062079 | -0.0011792 | 0.030839 | -0.01794 | -0.010741 | -0.018664 | -0.054932 | 0.004578 | -0.050354 | -0.050354 | 0.07782 | 0.013733 | 0 | -0.1236 | -0.036621 | -0.15564 | -0.082397 | 0.009155 | -0.073242 | 0.050354 | 120.7626 | -0.082397 | -0.13733 | 120.8908 | 120.813 | 120.8267 | 0.050354 | 0.064087 | 120.6573 | -0.1236 | -0.16937 | 120.8221 | 120.8633 | 120.7397 | 0.20599 | 0.082398 | 0.12817 | 0 | 0.16479 | 0.073243 | 0.054932 | 0.11902 | 120.8176 | 120.7764 | -0.13733 | -0.24261 | 120.7626 | 120.7306 | 120.7581 | 120.6894
2892.9531 | 121.0098 | -120.8542 | 0.068665 | 0.028839 | 0.013719 | -0.035004 | 0.037549 | -0.015276 | -0.030104 | -0.024101 | 0.0055542 | -0.060797 | -0.0024608 | 0.032334 | -0.018367 | -0.010527 | -0.017596 | -0.027466 | 0 | -0.045776 | -0.027466 | 0.091553 | -0.004578 | 0.018311 | -0.10071 | -0.050354 | -0.17853 | -0.073242 | 0.018311 | -0.068665 | 0.036621 | 120.8084 | -0.068665 | -0.096131 | 120.9457 | 120.8725 | 120.8496 | 0.064087 | 0.041198 | 120.6757 | -0.11902 | -0.14191 | 120.8725 | 120.8908 | 120.7855 | 0.21515 | 0.10986 | 0.13733 | 0.01831 | 0.19684 | 0.10529 | 0.045776 | 0.12817 | 120.8542 | 120.8038 | -0.11444 | -0.24719 | 120.8267 | 120.7809 | 120.8267 | 120.7535
2894.6719 | 121.0739 | -120.8588 | 0.07782 | 0.028839 | 0.012224 | -0.032441 | 0.035199 | -0.019335 | -0.027967 | -0.022605 | 0.008606 | -0.064429 | -0.00075185 | 0.041306 | -0.016658 | -0.0079638 | -0.01311 | -0.054932 | -0.027466 | -0.004578 | -0.018311 | 0.14191 | 0.018311 | 0.027466 | -0.09613 | -0.086975 | -0.15564 | -0.054932 | 0.027466 | -0.045776 | 0.041199 | 120.8542 | -0.10529 | -0.096131 | 121.0007 | 120.8862 | 120.8771 | 0.032044 | 0.022889 | 120.7031 | -0.16479 | -0.13275 | 120.8862 | 120.9 | 120.813 | 0.19684 | 0.10986 | 0.14649 | -0.013733 | 0.18311 | 0.10071 | -0.022888 | 0.068665 | 120.8313 | 120.7718 | -0.082398 | -0.23346 | 120.8405 | 120.8038 | 120.8038 | 120.7626
2896.375 | 121.138 | -120.8862 | 0.045776 | 0.01358 | 0.013719 | -0.030518 | 0.036053 | -0.015276 | -0.025618 | -0.020897 | 0.011658 | -0.066351 | -0.00075185 | 0.033188 | -0.01794 | -0.0092456 | -0.016742 | 0.018311 | -0.050354 | 0.004578 | 0.064087 | 0.19226 | 0.07782 | 0.091553 | -0.004578 | -0.07782 | -0.14648 | 0.004578 | 0.082397 | 0 | 0.091553 | 120.8908 | -0.09613 | 0.018311 | 121.0785 | 120.9778 | 120.9641 | 0.086975 | 0.073242 | 120.7397 | -0.1236 | -0.041198 | 120.9686 | 120.9778 | 120.8862 | 0.23804 | 0.14648 | 0.18768 | 0.059509 | 0.22888 | 0.15106 | -0.054932 | 0.068664 | 120.8359 | 120.8084 | -0.041198 | -0.19226 | 120.9503 | 120.8908 | 120.9045 | 120.8817
2898.0781 | 121.1014 | -120.8862 | 0.041199 | 0.01358 | 0.015855 | -0.032441 | 0.03648 | -0.018053 | -0.026045 | -0.019401 | 0.008606 | -0.06272 | -0.0016064 | 0.031907 | -0.017299 | -0.0101 | -0.012683 | -0.013733 | -0.022888 | -0.004578 | 0.022888 | 0.16937 | 0.054932 | 0.054932 | -0.11444 | -0.16022 | -0.21515 | -0.11902 | -0.032043 | -0.11444 | -0.004578 | 120.8817 | -0.064087 | -0.018311 | 121.0556 | 120.9412 | 120.9412 | 0.05951 | 0.05951 | 120.6711 | -0.20142 | -0.16022 | 120.8542 | 120.8817 | 120.7718 | 0.21057 | 0.10071 | 0.17395 | 0.027466 | 0.18311 | 0.09613 | -0.01831 | 0.054932 | 120.8633 | 120.726 | -0.045777 | -0.25635 | 120.9091 | 120.7672 | 120.8725 | 120.7718
2899.7812 | 120.6848 | -120.5704 | 0.07782 | 0.02121 | 0.015214 | -0.033936 | 0.037549 | -0.012926 | -0.028608 | -0.021751 | 0.0055542 | -0.060584 | -0.00011105 | 0.035538 | -0.018794 | -0.011168 | -0.012683 | -0.018311 | -0.018311 | -0.036621 | 0 | 0.10071 | -0.018311 | 0 | -0.16022 | -0.09613 | -0.21973 | -0.13733 | -0.073242 | -0.16937 | -0.022888 | 120.5338 | -0.096131 | -0.07782 | 120.6711 | 120.5704 | 120.5521 | 0.036621 | 0.01831 | 120.3506 | -0.17395 | -0.21515 | 120.4971 | 120.5475 | 120.401 | 0.19684 | 0.050354 | 0.13733 | 0.036621 | 0.14649 | 0.082398 | 0.01831 | 0.1236 | 120.5521 | 120.4742 | -0.11444 | -0.29755 | 120.5704 | 120.433 | 120.5521 | 120.4102
2901.5 | 120.4056 | -120.163 | 0.050354 | 0.02121 | 0.01671 | -0.033082 | 0.036053 | -0.017626 | -0.029676 | -0.020683 | 0.008606 | -0.064429 | -0.00053825 | 0.038315 | -0.019435 | -0.0088184 | -0.015033 | -0.041199 | -0.022888 | -0.004578 | -0.018311 | 0.11902 | 0.027466 | 0.050354 | -0.2243 | -0.20142 | -0.27008 | -0.19684 | -0.09613 | -0.1831 | -0.073242 | 120.1584 | -0.073242 | -0.068665 | 120.282 | 120.2133 | 120.1904 | 0.054932 | 0.032044 | 119.8929 | -0.25177 | -0.24719 | 120.0668 | 120.0897 | 119.9799 | 0.19684 | 0.086976 | 0.1236 | -0.013733 | 0.17395 | 0.073243 | -0.01831 | 0.068665 | 120.1401 | 119.9615 | -0.054932 | -0.32044 | 120.1447 | 119.9661 | 120.1218 | 119.9387
2903.2188 | 120.5704 | -120.3323 | 0.15564 | 0.01358 | 0.017564 | -0.033936 | 0.038189 | -0.016131 | -0.028395 | -0.021324 | -0.00054937 | -0.059302 | 0.00095715 | 0.044938 | -0.015377 | -0.0094592 | -0.012256 | -0.086975 | -0.004578 | -0.018311 | -0.086975 | 0.004578 | -0.091553 | -0.054932 | -0.3479 | -0.1831 | -0.31586 | -0.3067 | -0.24719 | -0.34332 | -0.19226 | 120.314 | -0.16022 | -0.24261 | 120.3369 | 120.2774 | 120.2408 | -0.036621 | -0.073242 | 120.0165 | -0.33874 | -0.46234 | 120.0851 | 120.1401 | 119.989 | 0.1236 | -0.027466 | 0.022889 | -0.068664 | 0.068665 | 0.009155 | 0.013733 | 0.13275 | 120.3278 | 120.1492 | -0.17395 | -0.4715 | 120.2454 | 120.0256 | 120.2454 | 119.9844
2904.9844 | 120.7764 | -120.488 | 0.073242 | 0.028839 | 0.013292 | -0.035645 | 0.034985 | -0.015276 | -0.028395 | -0.021537 | -0.00054937 | -0.062933 | 0.00074335 | 0.044083 | -0.016658 | -0.0098864 | -0.011828 | -0.050354 | -0.036621 | -0.013733 | -0.009155 | 0.13733 | 0.032043 | 0.054932 | -0.27466 | -0.27466 | -0.33417 | -0.23804 | -0.11902 | -0.19684 | -0.091553 | 120.4742 | -0.10986 | -0.082397 | 120.6253 | 120.5429 | 120.52 | 0.068665 | 0.045776 | 120.1538 | -0.3479 | -0.31128 | 120.369 | 120.3964 | 120.2911 | 0.24261 | 0.13733 | 0.15106 | 0.004578 | 0.21515 | 0.09613 | -0.022888 | 0.059509 | 120.4514 | 120.2133 | -0.086975 | -0.40741 | 120.4788 | 120.2499 | 120.4376 | 120.2133
2906.6875 | 119.3985 | -119.133 | 0.086975 | 0.028839 | 0.014573 | -0.0318 | 0.034985 | -0.014635 | -0.027967 | -0.019188 | 0.014709 | -0.062292 | -0.00032465 | 0.041092 | -0.017299 | -0.010955 | -0.01546 | 0.004578 | -0.041199 | 0.009155 | 0.064087 | 0.19684 | 0.059509 | 0.073242 | -0.086975 | -0.16479 | -0.20599 | -0.091553 | -0.009155 | -0.10071 | -0.004578 | 119.1422 | -0.12817 | -0.022888 | 119.3298 | 119.2062 | 119.1925 | 0.064087 | 0.050354 | 118.927 | -0.25177 | -0.17853 | 119.1238 | 119.1284 | 119.0323 | 0.20142 | 0.10529 | 0.18768 | 0.054932 | 0.19684 | 0.11444 | -0.050354 | 0.041199 | 119.0918 | 118.9682 | -0.07782 | -0.29297 | 119.1971 | 119.0414 | 119.1376 | 119.046
2908.4219 | 120.5933 | -120.3781 | 0.050354 | 0.01358 | 0.013933 | -0.031586 | 0.036053 | -0.017626 | -0.027113 | -0.022605 | 0.011658 | -0.062933 | 0.00095715 | 0.037888 | -0.016872 | -0.0101 | -0.0088376 | -0.018311 | -0.032043 | -0.009155 | 0.018311 | 0.16022 | 0.032043 | 0.045776 | -0.07782 | -0.13275 | -0.16479 | -0.07782 | 0 | -0.082397 | 0.032043 | 120.369 | -0.082397 | -0.032043 | 120.5383 | 120.4239 | 120.4102 | 0.054931 | 0.041198 | 120.2133 | -0.18311 | -0.12817 | 120.3781 | 120.4102 | 120.2957 | 0.19684 | 0.082398 | 0.16937 | 0.027466 | 0.16479 | 0.086975 | -0.022888 | 0.032044 | 120.3461 | 120.2454 | -0.059509 | -0.21515 | 120.3964 | 120.3003 | 120.3598 | 120.3003
2910.1562 | 120.6985 | -120.4559 | 0.068665 | 0.01358 | 0.01201 | -0.034791 | 0.033917 | -0.019976 | -0.029036 | -0.021537 | 0.0055542 | -0.062079 | 0.00074335 | 0.041733 | -0.021144 | -0.0101 | -0.010974 | -0.050354 | -0.041199 | 0 | -0.022888 | 0.11902 | 0.009155 | 0.027466 | -0.25177 | -0.21515 | -0.31128 | -0.2243 | -0.12817 | -0.20142 | -0.10071 | 120.4559 | -0.10986 | -0.091553 | 120.575 | 120.4834 | 120.4651 | 0.027466 | 0.009155 | 120.1447 | -0.28381 | -0.29297 | 120.3278 | 120.3552 | 120.2545 | 0.21057 | 0.10986 | 0.11902 | -0.022888 | 0.1831 | 0.086975 | -0.041199 | 0.09613 | 120.4147 | 120.2408 | -0.068665 | -0.37994 | 120.433 | 120.2316 | 120.4056 | 120.2042
2911.9219 | 120.2179 | -120.0714 | 0.09613 | 0.02121 | 0.012224 | -0.033722 | 0.037976 | -0.017199 | -0.029676 | -0.023246 | 0.008606 | -0.060156 | 0.00010255 | 0.040665 | -0.019863 | -0.011382 | -0.013324 | -0.068665 | 0 | -0.064087 | -0.059509 | 0.054932 | -0.022888 | -0.018311 | -0.16479 | -0.027466 | -0.18768 | -0.1236 | -0.018311 | -0.11444 | 0.018311 | 120.0073 | -0.09613 | -0.15564 | 120.1263 | 120.0531 | 120.0485 | 0.045776 | 0.041199 | 119.8837 | -0.1236 | -0.21973 | 120.0531 | 120.0897 | 119.957 | 0.20599 | 0.073242 | 0.11902 | 0.004578 | 0.16937 | 0.064087 | 0.064087 | 0.16022 | 120.0714 | 120.0439 | -0.16022 | -0.28381 | 120.0119 | 119.9478 | 120.0027 | 119.9066
2913.625 | 120.3552 | -120.2591 | 0.10071 | 0.01358 | 0.015428 | -0.035218 | 0.035412 | -0.016131 | -0.030104 | -0.023033 | 0.008606 | -0.060584 | -0.00053825 | 0.034897 | -0.018794 | -0.0092456 | -0.014605 | -0.086975 | 0.018311 | -0.041199 | -0.09613 | 0.045776 | -0.022888 | -0.013733 | -0.28839 | -0.15106 | -0.28381 | -0.24719 | -0.15106 | -0.23346 | -0.11444 | 120.2179 | -0.082397 | -0.19684 | 120.3049 | 120.2454 | 120.2362 | 0.027466 | 0.018311 | 119.9753 | -0.25177 | -0.3479 | 120.108 | 120.1447 | 120.0256 | 0.16937 | 0.050354 | 0.086975 | -0.054931 | 0.13275 | 0.036621 | 0.05951 | 0.13275 | 120.2774 | 120.108 | -0.14191 | -0.38452 | 120.163 | 120.0119 | 120.1721 | 119.9707
2915.3438 | 120.4559 | -120.2133 | 0.032043 | 0.01358 | 0.015001 | -0.033722 | 0.034772 | -0.014635 | -0.029676 | -0.02111 | 0.008606 | -0.063361 | 0.0013844 | 0.037461 | -0.017726 | -0.0092456 | -0.016955 | -0.022888 | -0.041199 | 0 | 0.018311 | 0.16479 | 0.041199 | 0.054932 | -0.054932 | -0.086975 | -0.13733 | 0.004578 | 0.054932 | -0.009155 | 0.10529 | 120.2133 | -0.073242 | -0.013732 | 120.3781 | 120.2682 | 120.2545 | 0.054932 | 0.041199 | 120.076 | -0.11902 | -0.027465 | 120.2682 | 120.3186 | 120.2042 | 0.24262 | 0.12817 | 0.16479 | 0.018311 | 0.19226 | 0.14191 | -0.041199 | 0.050354 | 120.1721 | 120.1263 | -0.032043 | -0.16937 | 120.2316 | 120.2179 | 120.1904 | 120.1584
2917.0469 | 120.4788 | -120.3461 | 0.059509 | 0.0059509 | 0.015214 | -0.033722 | 0.037335 | -0.016771 | -0.027113 | -0.020469 | 0.0055542 | -0.063574 | -0.00032465 | 0.044083 | -0.016658 | -0.0086048 | -0.01546 | -0.082397 | 0 | -0.032043 | -0.07782 | 0.041199 | -0.064087 | -0.045776 | -0.17853 | -0.082397 | -0.16937 | -0.13275 | -0.064087 | -0.16022 | -0.018311 | 120.314 | -0.059509 | -0.13733 | 120.3873 | 120.3003 | 120.282 | -0.013733 | -0.032044 | 120.1767 | -0.14191 | -0.19226 | 120.282 | 120.3278 | 120.1859 | 0.15106 | 0.009156 | 0.073242 | -0.045777 | 0.10529 | 0.036622 | 0.032043 | 0.086976 | 120.3461 | 120.2637 | -0.091552 | -0.22888 | 120.2682 | 120.2133 | 120.2637 | 120.1675
2918.75 | 120.6848 | -120.3644 | 0.045776 | 0.02121 | 0.012864 | -0.0365 | 0.036267 | -0.018694 | -0.028181 | -0.02111 | -0.00054937 | -0.064002 | 0.002666 | 0.034897 | -0.020503 | -0.0101 | -0.0099056 | -0.018311 | -0.041199 | 0 | 0.022888 | 0.19684 | 0.10986 | 0.10529 | 0.009155 | -0.09613 | -0.1236 | -0.004578 | 0.10529 | 0.032043 | 0.11444 | 120.3644 | -0.086975 | -0.022888 | 120.5612 | 120.4697 | 120.4742 | 0.10529 | 0.10986 | 120.2408 | -0.14191 | -0.050354 | 120.4697 | 120.4788 | 120.3964 | 0.23804 | 0.15564 | 0.19684 | 0.022888 | 0.22888 | 0.11902 | -0.041199 | 0.027466 | 120.3232 | 120.2682 | -0.045776 | -0.16937 | 120.3873 | 120.3598 | 120.3461 | 120.3735
2920.4531 | 120.726 | -120.4193 | 0.054932 | 0.01358 | 0.011369 | -0.035004 | 0.035412 | -0.021685 | -0.027327 | -0.023674 | 0.0025024 | -0.063788 | -0.00032465 | 0.044724 | -0.021999 | -0.010314 | -0.013751 | -0.041199 | -0.050354 | 0 | 0.018311 | 0.16479 | 0.082397 | 0.082397 | -0.041199 | -0.11444 | -0.15564 | -0.018311 | 0.09613 | -0.004578 | 0.09613 | 120.4193 | -0.10529 | -0.036621 | 120.5841 | 120.5017 | 120.5017 | 0.082397 | 0.082397 | 120.2637 | -0.16937 | -0.073243 | 120.5154 | 120.5154 | 120.4147 | 0.25177 | 0.15106 | 0.16479 | 0.018311 | 0.25177 | 0.13733 | -0.050354 | 0.041199 | 120.369 | 120.3049 | -0.054932 | -0.21057 | 120.4376 | 120.401 | 120.3781 | 120.3781
2922.1719 | 120.6802 | -120.4971 | 0.082397 | 0.01358 | 0.015001 | -0.032868 | 0.037762 | -0.014849 | -0.02754 | -0.022392 | 0.008606 | -0.060156 | 0.0030934 | 0.035966 | -0.018367 | -0.010527 | -0.014392 | -0.009155 | -0.027466 | -0.013733 | -0.013733 | 0.1236 | 0.013733 | 0.027466 | -0.068665 | -0.045776 | -0.12817 | -0.054932 | 0.027466 | -0.064087 | 0.064087 | 120.4834 | -0.10986 | -0.09613 | 120.6207 | 120.5246 | 120.5109 | 0.041199 | 0.027466 | 120.369 | -0.12817 | -0.13733 | 120.5246 | 120.5612 | 120.433 | 0.19226 | 0.064087 | 0.13733 | 0 | 0.15564 | 0.073242 | -0.013733 | 0.082398 | 120.4697 | 120.4514 | -0.09613 | -0.21057 | 120.4834 | 120.4422 | 120.488 | 120.4285
2923.9375 | 120.726 | -120.52 | 0.073242 | 0.01358 | 0.015855 | -0.033722 | 0.037335 | -0.016985 | -0.02754 | -0.021324 | 0.0055542 | -0.06507 | 0.00031615 | 0.039384 | -0.016017 | -0.011168 | -0.01546 | -0.07782 | 0 | -0.041199 | -0.07782 | 0.041199 | -0.064087 | -0.050354 | -0.13733 | -0.054932 | -0.13275 | -0.07782 | 0 | -0.091553 | 0.050354 | 120.4788 | -0.073242 | -0.15106 | 120.5612 | 120.4697 | 120.4559 | -0.009155 | -0.022888 | 120.3873 | -0.12817 | -0.15106 | 120.52 | 120.5704 | 120.4285 | 0.18311 | 0.041198 | 0.082398 | -0.036621 | 0.13275 | 0.054931 | 0.041199 | 0.077819 | 120.52 | 120.4651 | -0.11444 | -0.20599 | 120.4422 | 120.4422 | 120.4422 | 120.3827
2925.6562 | 120.1584 | -119.8929 | 0.041199 | 0.0059509 | 0.015001 | -0.032013 | 0.039685 | -0.016131 | -0.026899 | -0.023674 | 0.0055542 | -0.064429 | -0.00011105 | 0.041306 | -0.014736 | -0.0068958 | -0.012256 | -0.054932 | -0.027466 | -0.009155 | -0.013733 | 0.1236 | 0.013733 | 0.041199 | -0.022888 | -0.073242 | -0.10071 | 0.022888 | 0.07782 | 0.009155 | 0.12817 | 119.8837 | -0.068665 | -0.054932 | 120.0165 | 119.9341 | 119.9066 | 0.050354 | 0.022888 | 119.7922 | -0.11444 | -0.018311 | 119.9707 | 120.0211 | 119.902 | 0.22888 | 0.10986 | 0.13275 | -0.004578 | 0.17853 | 0.1236 | -0.018311 | 0.027466 | 119.8654 | 119.8196 | -0.050354 | -0.14191 | 119.8791 | 119.9158 | 119.838 | 119.87
2927.3906 | 120.4193 | -120.282 | 0.09613 | 0.0059509 | 0.014573 | -0.037354 | 0.03584 | -0.019976 | -0.029463 | -0.022178 | 0.0025024 | -0.063361 | 0.0024524 | 0.038529 | -0.024776 | -0.0101 | -0.013965 | -0.10529 | -0.009155 | -0.036621 | -0.086975 | 0.050354 | -0.032043 | -0.027466 | -0.15106 | -0.022888 | -0.14191 | -0.1236 | -0.009155 | -0.09613 | 0.013733 | 120.2454 | -0.10528 | -0.1831 | 120.3323 | 120.2545 | 120.2499 | 0.009155 | 0.004578 | 120.1401 | -0.11902 | -0.21973 | 120.2728 | 120.2957 | 120.1859 | 0.15564 | 0.045777 | 0.086975 | -0.050354 | 0.13275 | 0.018311 | 0.027466 | 0.11902 | 120.2728 | 120.2591 | -0.13275 | -0.23804 | 120.195 | 120.1584 | 120.1767 | 120.1309
2929.1094 | 120.4559 | -120.401 | 0.10529 | 0.01358 | 0.016496 | -0.032227 | 0.036053 | -0.016558 | -0.027327 | -0.023033 | 0.0055542 | -0.060797 | 0.00095715 | 0.027848 | -0.016017 | -0.0094592 | -0.015246 | -0.059509 | -0.022888 | -0.032043 | -0.07782 | 0.041199 | -0.054932 | -0.050354 | -0.15106 | -0.032043 | -0.14191 | -0.09613 | -0.050354 | -0.13733 | 0.018311 | 120.369 | -0.12817 | -0.18311 | 120.4422 | 120.3506 | 120.3461 | -0.018311 | -0.022889 | 120.2591 | -0.13733 | -0.20142 | 120.3506 | 120.4193 | 120.2637 | 0.16022 | 0.004578 | 0.073242 | -0.045777 | 0.091553 | 0.045777 | 0.009155 | 0.10986 | 120.3781 | 120.369 | -0.13733 | -0.24719 | 120.3232 | 120.3049 | 120.3415 | 120.2499
2930.8125 | 120.6528 | -120.4742 | 0.073242 | 0.02121 | 0.015428 | -0.033082 | 0.037335 | -0.011431 | -0.028608 | -0.020042 | 0.008606 | -0.064215 | -0.00096545 | 0.031907 | -0.019649 | -0.010741 | -0.013751 | -0.027466 | 0 | -0.036621 | -0.032043 | 0.11444 | 0 | 0 | -0.059509 | -0.027466 | -0.11902 | -0.036621 | 0.041199 | -0.041199 | 0.064087 | 120.4376 | -0.073242 | -0.10529 | 120.5887 | 120.4742 | 120.4742 | 0.036621 | 0.036621 | 120.3552 | -0.10071 | -0.10986 | 120.5154 | 120.5383 | 120.433 | 0.18311 | 0.07782 | 0.15106 | 0.004578 | 0.16022 | 0.082398 | 0.036621 | 0.091553 | 120.4742 | 120.4468 | -0.10986 | -0.19226 | 120.4422 | 120.4376 | 120.4468 | 120.4147
2932.5156 | 120.8176 | -120.1767 | 0.48523 | 0.0059509 | 0.014573 | -0.033082 | 0.033276 | -0.014635 | -0.030531 | -0.022605 | 0.0055542 | -0.064002 | -0.00032465 | 0.041306 | -0.021999 | -0.0101 | -0.014605 | -0.018311 | -0.054932 | 0.009155 | 0.027466 | 0.1831 | 0.07782 | 0.07782 | -0.29755 | -0.32044 | -0.3891 | -0.24261 | -0.091553 | -0.1831 | -0.09613 | 120.1859 | -0.54016 | -0.45776 | 120.3598 | 120.2545 | 120.2545 | 0.068665 | 0.068665 | 119.7876 | -0.80566 | -0.72784 | 120.0851 | 120.0806 | 119.9936 | 0.29297 | 0.20599 | 0.17395 | 0.018311 | 0.29755 | 0.14648 | -0.064087 | 0.068664 | 120.1218 | 119.8563 | -0.47607 | -0.87433 | 120.2042 | 119.9341 | 120.1584 | 119.8792
2934.2188 | 119.7372 | -8.6838 | 111.1084 | 0.02121 | 0.010942 | -0.036072 | 0.032849 | -0.018908 | -0.028608 | -0.024101 | 0.0025024 | -0.064002 | -0.0013928 | 0.037675 | -0.019435 | -0.011809 | -0.011615 | -0.041199 | -0.086975 | -0.045776 | 0.018311 | 0.17853 | 0.059509 | 0.054932 | 0.086975 | -0.004578 | -0.013733 | 0.10986 | 0.19226 | 0.11902 | 0.20599 | 8.638 | -111.1954 | -111.0901 | 8.8623 | 8.7387 | 8.7433 | 0.10071 | 0.10528 | 8.67 | -111.113 | -110.9985 | 8.876 | 8.8898 | 8.8028 | 0.21973 | 0.13275 | 0.2243 | 0.064087 | 0.20599 | 0.1236 | -0.041199 | 0.009155 | 8.5968 | 8.6792 | -111.1542 | -111.1221 | 8.7021 | 8.7936 | 8.6426 | 8.7708
2935.9844 | 120.2591 | -44.1422 | 75.7324 | -0.68832 | 0.022264 | -0.030091 | 0.035199 | -0.017412 | -0.026258 | -0.02346 | 0.008606 | -0.061438 | 0.0022388 | 0.03682 | -0.016231 | -0.0096728 | -0.011828 | -0.045776 | -0.059509 | -0.027466 | 0.004578 | 0.16479 | 0.027466 | 0.036621 | 0.013733 | -0.032043 | -0.07782 | 0.050354 | 0.11444 | 0.050354 | 0.12817 | 44.1147 | -75.7919 | -75.7278 | 44.3069 | 44.1788 | 44.1696 | 0.064087 | 0.054932 | 44.0643 | -75.7645 | -75.6821 | 44.2566 | 44.2703 | 44.1925 | 0.20599 | 0.12817 | 0.19226 | 0.032044 | 0.19226 | 0.12817 | -0.032043 | 0.045777 | 44.0826 | 44.1101 | -75.7599 | -75.8102 | 44.1467 | 44.1925 | 44.0964 | 44.1559
2937.6875 | 120.1675 | -76.5015 | 43.9407 | 0.02121 | 0.00026062 | -0.03949 | 0.034985 | -0.017199 | -0.027754 | -0.029441 | -0.263 | 0.037256 | 0.0097156 | 0.037461 | -0.028835 | -0.019072 | -0.01311 | -0.032043 | -0.045776 | -0.054932 | -0.022888 | 0.09613 | -0.004578 | 6.0196 | -0.022888 | -0.086975 | -0.1831 | -0.009155 | 0.07782 | -0.073242 | 0.068665 | 76.4465 | -43.9865 | -43.9636 | 76.5976 | 82.5211 | 76.4969 | 6.0745 | 0.050354 | 76.3184 | -44.0277 | -43.9499 | 76.5793 | 76.5701 | 76.4282 | 0.25177 | 0.10986 | 0.15106 | 0.032044 | 0.26092 | 0.17395 | 0.009156 | 0.09613 | 76.4557 | 76.4145 | -43.9957 | -44.1238 | 76.4786 | 76.4923 | 76.4694 | 76.4786
2939.4219 | 120.3598 | -119.9799 | 0.073242 | 0.028839 | 0.015214 | -0.032441 | 0.0052915 | 0.026808 | -0.045485 | 0.029091 | 0.048279 | 0.01568 | -0.013997 | 0.022507 | 0.023503 | 0.028566 | 0.019361 | -0.2655 | 0 | 0.16022 | 0.09613 | 0.09613 | 0.09613 | 0.091553 | -0.25177 | -0.16937 | -0.09613 | -0.091553 | 0.091553 | 0.10071 | 0.09613 | 120.1401 | -0.073242 | 0.022888 | 120.076 | 120.0714 | 120.076 | -0.068664 | -0.064087 | 119.8837 | -0.24261 | -0.16479 | 120.0714 | 120.076 | 120.0806 | 0.19226 | 0.19684 | -0.064087 | -0.064087 | 0.18768 | 0.004577 | -0.16022 | -0.073243 | 119.9799 | 119.8105 | 0.086975 | -0.16937 | 120.076 | 119.8883 | 119.7144 | 119.7281
2941.125 | 120.282 | -119.8791 | 0.1236 | 0.028839 | 0.016282 | -0.032013 | 0.021527 | -0.021898 | -0.030104 | -0.032005 | 0.048279 | -0.071051 | -0.0024608 | 0.022294 | 0.02393 | 0.026643 | 0.018933 | -0.041199 | 0.004578 | -0.032043 | -0.16479 | 0.086975 | 0.091553 | 0.091553 | -0.059509 | -0.27466 | -0.045776 | -0.013733 | -0.32501 | 0.091553 | 0.091553 | 119.8471 | -0.11902 | -0.28839 | 119.9661 | 119.9707 | 119.9707 | 0.1236 | 0.1236 | 119.8334 | -0.39825 | -0.13733 | 119.5541 | 119.9707 | 119.9707 | 0.13733 | 0.13733 | 0.11902 | -0.13275 | -0.27924 | 0.032043 | 0.036621 | -0.22888 | 119.8837 | 119.6045 | -0.15564 | -0.16937 | 119.7144 | 119.8654 | 119.838 | 119.8196
2942.8906 | 120.3873 | -120.1126 | 0.13275 | 0.051727 | 0.016282 | -0.035004 | 0.037335 | -0.018908 | -0.029036 | -0.021537 | -0.12262 | -0.069556 | -0.0033154 | 0.02977 | -0.023921 | -0.01245 | -0.017596 | -0.086975 | 0.018311 | -0.050354 | -0.2243 | -0.32501 | -0.37537 | -0.16479 | -0.12817 | -0.013733 | 0.086975 | -0.068665 | -0.10986 | -0.42572 | -0.17395 | 120.0623 | -0.11444 | -0.35706 | 119.7876 | 119.9478 | 119.7372 | -0.11444 | -0.32501 | 120.1996 | -0.14648 | -0.20142 | 120.0027 | 119.9387 | 119.6869 | -0.26092 | -0.5127 | -0.27466 | -0.17395 | -0.19684 | -0.15564 | 0.068665 | -0.10071 | 120.1309 | 120.0989 | -0.18311 | -0.045776 | 119.8883 | 120.0439 | 120.0256 | 119.9844
2944.5938 | 120.2225 | -119.9982 | 0.14648 | 0.0059509 | 0.012864 | -0.03415 | 0.036908 | -0.022326 | -0.029463 | -0.020683 | -0.14398 | -0.062079 | -0.0026744 | 0.044083 | -0.01794 | -0.010314 | -0.012683 | -0.068665 | -0.022888 | -0.009155 | -0.064087 | -0.064087 | -0.11902 | -0.27008 | -0.11444 | -0.018311 | 0.064087 | -0.086975 | -0.013733 | -0.17395 | -0.15106 | 119.989 | -0.16937 | -0.21057 | 119.9341 | 119.7281 | 119.8792 | -0.26093 | -0.10986 | 120.0623 | -0.16479 | -0.23346 | 119.9844 | 119.8471 | 119.8242 | -0.21515 | -0.23804 | -0.054932 | -0.054932 | -0.07782 | -0.15106 | -0.013733 | -0.082398 | 119.9753 | 119.9799 | -0.15564 | -0.082397 | 119.9341 | 119.9112 | 119.9295 | 119.8837
2946.3125 | 120.3964 | -120.1309 | 0.10529 | 0.02121 | 0.013719 | -0.033936 | 0.037549 | -0.014208 | -0.028608 | -0.020897 | -0.1684 | -0.061011 | 0.00031615 | 0.045151 | -0.015804 | -0.010314 | -0.014605 | -0.082397 | -0.004578 | -0.041199 | -0.086975 | -0.086975 | -0.18768 | -0.34332 | -0.091553 | -0.009155 | -0.10986 | -0.013733 | 0.013733 | -0.082397 | -0.032043 | 120.0897 | -0.10986 | -0.19226 | 120.0439 | 119.7876 | 119.9432 | -0.30212 | -0.14648 | 120.0211 | -0.11444 | -0.11902 | 120.1447 | 120.0989 | 120.0485 | 0.07782 | 0.027466 | -0.045776 | -0.045776 | 0.1236 | 0.09613 | 0.036621 | 0.10071 | 120.1263 | 120.1218 | -0.14649 | -0.21515 | 120.0439 | 120.1172 | 120.0485 | 120.0394
2948.0312 | 120.5017 | -119.9432 | 0.28839 | 0.02121 | 0.015001 | -0.032227 | 0.036267 | -0.016771 | -0.030317 | -0.020897 | -0.0066528 | -0.064429 | -0.00011105 | 0.037675 | -0.015377 | -0.0045458 | -0.013324 | -0.004578 | -0.045776 | 0.009155 | 0.041199 | 0.17395 | 0.064087 | -0.013733 | -0.004578 | -0.091553 | -0.1236 | 0.013733 | 0.059509 | 0 | 0.10529 | 119.9524 | -0.33417 | -0.24719 | 120.1172 | 119.9295 | 120.0073 | -0.022888 | 0.054932 | 119.8196 | -0.37994 | -0.27466 | 120.0027 | 120.0485 | 119.9432 | 0.22888 | 0.1236 | 0.16479 | 0.032044 | 0.1831 | 0.13733 | -0.054931 | 0.032043 | 119.8975 | 119.8517 | -0.27924 | -0.41199 | 119.9844 | 119.957 | 119.9387 | 119.9387
2949.75 | 120.314 | -119.5633 | 0.65918 | 0.01358 | 0.016282 | -0.035004 | 0.039685 | -0.013994 | -0.027113 | -0.023246 | -0.22943 | -0.075751 | -0.0031018 | 0.03447 | -0.016445 | -0.014159 | -0.017169 | -0.050354 | -0.009155 | -0.041199 | -0.045776 | -0.068665 | -0.24719 | -0.32959 | -0.10071 | -0.013733 | -0.12817 | -0.068665 | -0.013733 | -0.20142 | -0.28381 | 119.5221 | -0.66834 | -0.70496 | 119.4946 | 119.2337 | 119.3161 | -0.28839 | -0.20599 | 119.4351 | -0.67291 | -0.72784 | 119.5496 | 119.2795 | 119.3619 | -0.15564 | -0.073242 | -0.027466 | -0.004577 | 0.11444 | 0.059509 | 0.032044 | 0.11444 | 119.5541 | 119.5496 | -0.70038 | -0.78735 | 119.5175 | 119.4946 | 119.5129 | 119.4626
2951.5 | 120.3049 | -119.7968 | 0.032043 | 0.01358 | 0.014573 | -0.03415 | 0.03648 | -0.016344 | -0.029036 | -0.021324 | -0.061584 | -0.065283 | -0.0011792 | 0.043442 | -0.014308 | -0.007323 | -0.018237 | -0.004578 | -0.050354 | 0.018311 | 0.022888 | 0.16479 | 0.064087 | -0.027466 | 0.032043 | -0.050354 | -0.064087 | 0.073242 | 0.13733 | 0.027466 | 0.15564 | 119.8151 | -0.082397 | -0.009155 | 119.9615 | 119.7693 | 119.8608 | -0.045777 | 0.045776 | 119.7327 | -0.082397 | 0.041199 | 119.9341 | 119.9524 | 119.8242 | 0.21973 | 0.091553 | 0.14648 | 0.004577 | 0.20142 | 0.13733 | -0.068665 | 0.013733 | 119.7464 | 119.7464 | -0.013732 | -0.09613 | 119.8196 | 119.87 | 119.7922 | 119.8288
2953.25 | 120.4376 | -120.2179 | 0.10071 | 0.01358 | 0.013505 | -0.034577 | 0.036908 | -0.018053 | -0.029249 | -0.020683 | -0.11652 | -0.063147 | -0.0020336 | 0.040024 | -0.02029 | -0.010741 | -0.01076 | -0.091553 | 0.013733 | -0.050354 | -0.091553 | 0.036621 | -0.032043 | -0.17395 | -0.11444 | 0.018311 | -0.13733 | -0.064087 | -0.004578 | -0.091553 | -0.064087 | 120.1675 | -0.086975 | -0.19226 | 120.2545 | 120.0439 | 120.1859 | -0.1236 | 0.018311 | 120.0806 | -0.082397 | -0.1648 | 120.2133 | 120.1538 | 120.1263 | 0.073242 | 0.045776 | 0.086975 | -0.041199 | 0.13275 | 0.073242 | 0.064087 | 0.15564 | 120.2316 | 120.2362 | -0.15106 | -0.23804 | 120.1263 | 120.1538 | 120.1263 | 120.1035
2955.0312 | 120.4971 | -120.3461 | 0.09613 | 0.0059509 | 0.013292 | -0.033722 | 0.037762 | -0.015917 | -0.026899 | -0.019615 | -0.13483 | -0.067206 | -0.00075185 | 0.03682 | -0.015163 | -0.0079638 | -0.013537 | -0.07782 | -0.004578 | -0.032043 | -0.10529 | -0.018311 | -0.13733 | -0.29297 | -0.14191 | 0.004578 | -0.11444 | -0.050354 | -0.041199 | -0.11444 | -0.032043 | 120.314 | -0.10071 | -0.20142 | 120.3278 | 120.0531 | 120.2087 | -0.26093 | -0.10529 | 120.2316 | -0.091552 | -0.14648 | 120.3049 | 120.314 | 120.2316 | 0.082398 | 0 | 0.013732 | -0.073243 | 0.073242 | 0.064087 | 0.027465 | 0.11902 | 120.3415 | 120.3506 | -0.12817 | -0.21057 | 120.2408 | 120.2957 | 120.2682 | 120.2042
2956.7344 | 120.5292 | -120.3964 | 0.082397 | 0.01358 | 0.016923 | -0.032013 | 0.038189 | -0.01784 | -0.028822 | -0.019188 | -0.08905 | -0.062292 | -0.00011105 | 0.032975 | -0.016872 | -0.009032 | -0.011615 | -0.091553 | 0 | -0.045776 | -0.10986 | -0.004578 | -0.07782 | -0.22888 | -0.14648 | -0.004578 | -0.11902 | -0.073242 | -0.041199 | -0.11902 | 0.036621 | 120.3506 | -0.082397 | -0.19226 | 120.3918 | 120.1675 | 120.3186 | -0.18311 | -0.032044 | 120.2774 | -0.086975 | -0.15564 | 120.3552 | 120.433 | 120.2774 | 0.15564 | 0 | 0.041198 | -0.064087 | 0.07782 | 0.045777 | 0.045776 | 0.11444 | 120.3964 | 120.3918 | -0.12817 | -0.20142 | 120.2866 | 120.3232 | 120.3049 | 120.2499
2958.5 | 120.6665 | -120.314 | 0.12817 | 0.028839 | 0.014573 | -0.033295 | 0.035199 | -0.015703 | -0.029676 | -0.020897 | 0.0055542 | -0.066565 | -0.0016064 | 0.038956 | -0.018154 | -0.0098864 | -0.0094784 | -0.054932 | -0.059509 | -0.013733 | -0.013733 | 0.13275 | 0.045776 | 0.059509 | -0.018311 | -0.054932 | -0.09613 | 0.045776 | 0.12817 | 0.050354 | 0.14191 | 120.3003 | -0.18768 | -0.14191 | 120.4468 | 120.3735 | 120.3598 | 0.073242 | 0.059509 | 120.2179 | -0.18311 | -0.082398 | 120.4422 | 120.4559 | 120.3644 | 0.23804 | 0.14648 | 0.14648 | 0 | 0.2243 | 0.14191 | -0.045776 | 0.041198 | 120.2545 | 120.2591 | -0.14191 | -0.2243 | 120.3003 | 120.3598 | 120.2591 | 120.2957
2960.2188 | 120.7352 | -120.401 | 0.045776 | 0.02121 | 0.014146 | -0.033295 | 0.033276 | -0.017199 | -0.030745 | -0.023887 | 0.0055542 | -0.063574 | -0.0013928 | 0.037461 | -0.019863 | -0.009032 | -0.01076 | 0.013733 | -0.045776 | 0.004578 | 0.050354 | 0.21057 | 0.10529 | 0.10071 | 0.059509 | -0.041199 | -0.07782 | 0.041199 | 0.15106 | 0.073242 | 0.15106 | 120.4056 | -0.091552 | 0.004578 | 120.6116 | 120.5017 | 120.5063 | 0.09613 | 0.10071 | 120.3232 | -0.086975 | -0.004577 | 120.5521 | 120.5521 | 120.4742 | 0.22888 | 0.15106 | 0.20599 | 0.045776 | 0.22888 | 0.11902 | -0.050354 | 0.036621 | 120.3552 | 120.3598 | -0.041198 | -0.1236 | 120.4514 | 120.4422 | 120.4147 | 120.4605
2962.0156 | 120.6299 | -120.4742 | 0.09613 | 0.01358 | 0.014146 | -0.033082 | 0.039044 | -0.015917 | -0.028608 | -0.023674 | 0.008606 | -0.061438 | -0.0028882 | 0.041733 | -0.017513 | -0.0098864 | -0.01076 | -0.082397 | -0.004578 | -0.032043 | -0.11444 | 0.018311 | -0.068665 | -0.068665 | -0.11444 | -0.013733 | -0.1236 | -0.073242 | -0.027466 | -0.09613 | 0.050354 | 120.4422 | -0.10071 | -0.21057 | 120.4926 | 120.4056 | 120.4056 | -0.036622 | -0.036622 | 120.3506 | -0.10986 | -0.16937 | 120.4468 | 120.5246 | 120.3781 | 0.17395 | 0.027466 | 0.050354 | -0.082398 | 0.09613 | 0.050354 | 0.027465 | 0.10986 | 120.4697 | 120.4605 | -0.12817 | -0.21973 | 120.3598 | 120.401 | 120.3918 | 120.3598
2963.7188 | 115.361 | -12.8586 | 92.3538 | 0.12802 | -0.00038018 | -0.043763 | 0.032849 | -0.025316 | -0.036726 | -0.028587 | 0.048279 | -0.074255 | -0.011219 | 0.042374 | -0.01324 | -0.0088184 | -0.015887 | 0.10071 | -0.40283 | -0.09613 | 0.10529 | 0.091553 | 0.091553 | 0.091553 | -0.93384 | 0.10071 | -0.10071 | -0.3891 | -0.050354 | -0.19684 | 0.041199 | 12.7625 | -92.7567 | -92.2485 | 12.9501 | 12.9501 | 12.9501 | 0.18768 | 0.18768 | 12.7579 | -92.2531 | -92.7429 | 12.8082 | 12.8998 | 12.6617 | 0.14191 | -0.09613 | 0.18768 | 0.20142 | 0.050354 | -0.28839 | -0.3067 | 0.20142 | 12.4558 | 12.9593 | -92.45 | -92.4545 | 12.9639 | 12.4695 | 12.9593 | 11.9247
2965.4375 | 96.9452 | -0.10529 | 96.0434 | 0.028839 | 0.006883 | -0.052948 | 0.0048641 | 0.021894 | -0.036085 | -0.03051 | 0.057434 | 0.015893 | 0.012279 | 0.022721 | 0.023289 | 0.027711 | 0.019361 | -0.16479 | -0.32501 | -0.018311 | 0.091553 | 0.10071 | 0.10071 | 0.09613 | -0.13275 | 0.091553 | -0.10071 | 0.10071 | 0.09613 | 0.09613 | 0.09613 | 0.086975 | -96.3684 | -95.9518 | 0.20599 | 0.20142 | 0.20599 | 0.11444 | 0.11902 | 0.004578 | -95.9518 | -95.9427 | 0.20142 | 0.20142 | 0.20142 | 0.19684 | 0.19684 | 0.11902 | 0.10986 | 0.19684 | 0.20142 | -0.3067 | 0.19226 | -0.21973 | 0.19684 | -96.0617 | -96.1441 | 0.19684 | 0.20599 | -0.059509 | -0.027465
2967.1562 | 120.5704 | -2.861 | 116.8716 | -0.032196 | 0.015001 | -0.032013 | 0.037549 | -0.016131 | -0.02519 | -0.02346 | -0.12567 | -0.064856 | 0.0011708 | 0.039597 | -0.013881 | -0.0088184 | -0.01076 | -0.022888 | -0.07782 | 0.064087 | -0.004578 | 0.004578 | -0.1236 | -0.19684 | 0.064087 | -0.13275 | 0.2243 | 0.073242 | 0.082397 | -0.032043 | 0.086975 | 2.9251 | -116.9495 | -116.8762 | 2.8656 | 2.6642 | 2.7374 | -0.26093 | -0.18768 | 3.0853 | -117.0044 | -116.7984 | 2.9434 | 2.948 | 2.829 | -0.13733 | -0.25635 | -0.059509 | -0.068665 | -0.14191 | -0.15106 | -0.14191 | -0.35706 | 2.7832 | 2.7283 | -116.8076 | -116.6473 | 2.8564 | 2.9343 | 2.8381 | 2.9251
2968.9375 | 120.694 | -4.0604 | 116.1667 | 0.036468 | 0.014573 | -0.032441 | 0.037976 | -0.016558 | -0.028181 | -0.020897 | -0.076843 | -0.064429 | 0.00010255 | 0.036179 | -0.016231 | -0.008391 | -0.01311 | -0.054932 | -0.068665 | -0.027466 | -0.004578 | 0.12817 | -0.004578 | -0.10071 | 0.059509 | -0.022888 | 0.064087 | 0.045776 | 0.12817 | 0.032043 | 0.13275 | 4.0329 | -116.2354 | -116.1713 | 4.1885 | 3.9597 | 4.0558 | -0.073242 | 0.022888 | 4.1245 | -116.1896 | -116.1209 | 4.1885 | 4.1931 | 4.0924 | 0.068664 | -0.032044 | 0.15564 | 0.022888 | 0.064087 | -0.018311 | -0.041199 | -0.086975 | 3.9917 | 4.0375 | -116.1942 | -116.1026 | 4.0558 | 4.1061 | 4.0054 | 4.1199
2970.6875 | 115.9927 | -60.6995 | 54.8126 | 0.02121 | 0.020341 | -0.031159 | 0.020245 | -0.025744 | -0.030958 | -0.032859 | -0.073792 | -0.075324 | -0.0048108 | 0.03212 | -0.020503 | -0.013945 | -0.016314 | -0.09613 | -0.013733 | -0.059509 | -0.16479 | -0.28839 | -0.12817 | 0.086975 | -0.041199 | 0.027466 | 0.11444 | -0.045776 | -0.29297 | 0.091553 | 0.10071 | 60.64 | -54.8264 | -54.9774 | 60.4111 | 60.7864 | 60.5713 | 0.14648 | -0.068665 | 60.8139 | -54.7852 | -54.8584 | 60.4065 | 60.8002 | 60.791 | -0.013733 | -0.022888 | -0.22888 | -0.10529 | -0.40741 | -0.16022 | 0.045776 | -0.086975 | 60.6857 | 60.7269 | -54.8721 | -54.6982 | 60.5347 | 60.6537 | 60.6033 | 60.6583
2972.3906 | 120.5566 | -91.2415 | 25.3372 | 0.14328 | 0.00966 | -0.032013 | 0.0052915 | -0.026171 | 0.34758 | 0.094033 | 0.051331 | 0.014825 | 0.011852 | 0.022507 | 0.024785 | -0.0030506 | 0.019361 | -0.21515 | -0.10986 | 0.009155 | 0.3479 | 0.091553 | 0.09613 | 0.10071 | 0.10071 | 0.09613 | -0.086975 | -0.89722 | 0.09613 | 0.091553 | 0.09613 | 91.2506 | -25.4471 | -24.9893 | 91.333 | 91.3422 | 91.3376 | 0.091553 | 0.086975 | 91.1545 | -25.2411 | -26.2344 | 91.3376 | 91.3376 | 91.333 | 0.1831 | 0.17853 | 0.082398 | 0.33874 | 0.1831 | -0.81024 | -0.11902 | 0.1831 | 91.1316 | 91.3376 | -25.3281 | -25.4242 | 91.5894 | 90.3442 | 91.0263 | 91.3422
2974.0938 | 120.5017 | -14.9826 | 104.8782 | 0.036468 | 0.013933 | -0.031586 | 0.035626 | -0.016344 | -0.026899 | -0.020042 | -0.10431 | -0.063574 | 0.0013844 | 0.037247 | -0.016445 | -0.0079638 | -0.01311 | -0.054932 | -0.059509 | 0.07782 | -0.027466 | 0.050354 | -0.10071 | -0.15106 | 0.045776 | -0.16022 | 0.27466 | 0.027466 | 0.07782 | -0.009155 | 0.09613 | 15.0604 | -104.9377 | -104.9057 | 15.033 | 14.8315 | 14.8819 | -0.22888 | -0.17853 | 15.2573 | -105.0385 | -104.8508 | 15.0604 | 15.0787 | 14.9734 | -0.17853 | -0.28381 | -0.027466 | -0.10529 | -0.19684 | -0.24719 | -0.13733 | -0.43488 | 14.9231 | 14.8224 | -104.8004 | -104.6036 | 14.9551 | 15.0101 | 14.9277 | 15.0284
2975.7969 | 119.8975 | -12.4786 | 107.1625 | 0.02121 | 0.013078 | -0.037354 | 0.026867 | -0.022326 | -0.036299 | -0.023674 | 0.03302 | -0.072119 | -0.003529 | 0.040879 | -0.015163 | -0.0092456 | -0.01311 | -0.13275 | -0.045776 | -0.054932 | -0.27924 | -0.2243 | -0.22888 | 0.10986 | -0.068665 | -0.07782 | 0.2243 | -0.068665 | -0.30212 | -0.37079 | -0.16022 | 12.4237 | -107.2083 | -107.4417 | 12.2543 | 12.5885 | 12.2498 | 0.16479 | -0.17395 | 12.7029 | -107.2403 | -107.2311 | 12.1765 | 12.3184 | 12.1078 | -0.38452 | -0.59509 | -0.16937 | -0.2243 | -0.52643 | -0.29297 | 0.009156 | -0.30212 | 12.4329 | 12.4008 | -107.2174 | -106.9382 | 12.1994 | 12.41 | 12.3459 | 12.41
2977.5 | 92.6651 | -0.13275 | 94.693 | -0.17715 | 0.019273 | 0.066894 | 0.0048641 | 0.027021 | 0.034624 | 0.029091 | 0.054382 | 0.015893 | 0.012066 | 0.022294 | 0.02393 | 0.028566 | 0.019361 | 0.09613 | -0.041199 | 0.30212 | 0.09613 | 0.091553 | 0.09613 | 0.09613 | -0.064087 | 0.09613 | -0.10071 | 0.10071 | 0.09613 | 0.091553 | 0.10529 | 0.43488 | -94.7342 | -94.5969 | 0.2243 | 0.22888 | 0.22888 | -0.20599 | -0.20599 | 0.032043 | -94.5969 | -94.5923 | 0.22888 | 0.23804 | 0.2243 | 0.20599 | 0.19226 | -0.21057 | -0.20599 | 0.19684 | 0.20142 | -0.34332 | 0.19684 | 0.091552 | 0.22888 | -94.3909 | -94.7937 | 0.22888 | 0.23346 | 0.22888 | 0.068664
2979.2188 | 99.8062 | -2.6642 | 86.6455 | 0.044098 | 0.013078 | -0.037568 | 0.037762 | -0.030871 | -0.040358 | -0.032005 | 0.054382 | -0.066138 | -0.0088696 | 0.022507 | -0.034816 | -0.025481 | -0.021655 | 0.10529 | -0.23804 | 0.28381 | 0.09613 | 0.09613 | 0.10071 | 0.10986 | 0.091553 | 0.09613 | -0.10529 | 0.09613 | 0.09613 | 0.10071 | 0.10071 | 2.948 | -86.8835 | -86.5494 | 2.7603 | 2.774 | 2.7649 | -0.17395 | -0.1831 | 2.5589 | -86.5494 | -86.5494 | 2.7603 | 2.7649 | 2.7649 | 0.20599 | 0.20599 | -0.18768 | -0.18768 | 0.20142 | 0.20142 | -0.52185 | 0.20142 | 2.4261 | 2.7603 | -86.3617 | -86.7508 | 2.7603 | 2.7603 | 2.7695 | 2.7557
2980.9844 | 120.6528 | -3.9642 | 115.9103 | -0.41367 | 0.015855 | -0.0318 | 0.036694 | -0.016131 | -0.027754 | -0.021751 | -0.13483 | -0.064856 | 0.00052975 | 0.043229 | -0.01559 | -0.009032 | -0.013965 | -0.054932 | -0.073242 | 0.082397 | -0.050354 | -0.022888 | -0.14191 | -0.19226 | 0.07782 | -0.21973 | 0.29297 | 0.054932 | 0.050354 | -0.032043 | 0.07782 | 4.0466 | -115.9836 | -115.9607 | 3.9413 | 3.772 | 3.8223 | -0.27466 | -0.2243 | 4.2572 | -116.1301 | -115.8554 | 4.0146 | 4.0421 | 3.9322 | -0.21515 | -0.32501 | -0.10528 | -0.13275 | -0.24261 | -0.23804 | -0.15564 | -0.5127 | 3.891 | 3.7445 | -115.8279 | -115.6174 | 3.9139 | 4.0192 | 3.9093 | 4.0421
2982.6875 | 119.6548 | -106.5445 | 12.6892 | 0.02121 | 0.011369 | -0.028168 | 0.033276 | -0.018267 | -0.027754 | -0.021537 | -0.21417 | -0.06272 | -0.00011105 | 0.042588 | -0.014522 | -0.0075366 | -0.012896 | -0.091553 | -0.013733 | -0.013733 | -0.28839 | -0.21515 | -0.31586 | -0.13275 | -0.004578 | -0.33875 | 0.26093 | -0.027466 | -0.15106 | -0.25635 | -0.11444 | 106.5308 | -12.7029 | -12.9776 | 106.3293 | 106.4117 | 106.2286 | -0.11902 | -0.30212 | 106.8054 | -13.028 | -12.7167 | 106.3934 | 106.4301 | 106.2881 | -0.37537 | -0.51727 | -0.20142 | -0.27466 | -0.41199 | -0.28839 | 0 | -0.59967 | 106.5308 | 106.2057 | -12.7029 | -12.4283 | 106.2561 | 106.517 | 106.4529 | 106.5399
2984.4688 | 120.6253 | -106.4117 | 13.7238 | 0.028839 | 0.011796 | -0.030732 | 0.031781 | -0.017412 | -0.02989 | -0.02111 | -0.073792 | -0.066565 | -0.00182 | 0.041092 | -0.01559 | -0.0098864 | -0.010333 | -0.07782 | -0.013733 | -0.027466 | -0.3067 | -0.091553 | -0.15106 | 0.068665 | -0.068665 | -0.059509 | 0.21057 | 0 | -0.19226 | -0.3891 | -0.23804 | 106.3843 | -13.7375 | -14.0305 | 106.3202 | 106.4804 | 106.2607 | 0.096131 | -0.1236 | 106.6223 | -13.7833 | -13.7238 | 106.2195 | 106.1737 | 106.0226 | -0.44861 | -0.59967 | -0.064087 | -0.27924 | -0.40283 | -0.21057 | 0.013733 | -0.27008 | 106.398 | 106.3522 | -13.7512 | -13.5132 | 106.105 | 106.4117 | 106.3339 | 106.3431
2986.1719 | 120.5109 | -105.7663 | 14.1495 | 0.02121 | 0.015001 | -0.029664 | 0.029858 | -0.015276 | -0.027113 | -0.021324 | -0.19891 | -0.063147 | -0.00032465 | 0.039384 | -0.016231 | -0.006682 | -0.011401 | -0.25177 | -0.013733 | 0.082397 | -0.42572 | -0.032043 | -0.15564 | -0.064087 | -0.21057 | -0.33417 | 0.027466 | 0.041199 | -0.1831 | -0.32044 | -0.19684 | 105.8487 | -14.1632 | -14.5752 | 105.7343 | 105.7022 | 105.6107 | -0.14648 | -0.23804 | 105.7938 | -14.4836 | -14.1083 | 105.5832 | 105.5695 | 105.4459 | -0.2243 | -0.3479 | -0.11444 | -0.50812 | -0.21057 | 0.013733 | -0.09613 | -0.36163 | 105.7526 | 105.4321 | -14.0671 | -14.122 | 105.3406 | 105.8075 | 105.5145 | 105.5557
2987.9375 | 115.2969 | -47.9233 | 66.5451 | 0.02121 | 0.02205 | -0.02945 | 0.036908 | -0.016344 | -0.028608 | -0.020897 | -0.073792 | -0.065497 | 0.0011708 | 0.042374 | -0.018154 | -0.0079638 | -0.01076 | -0.073242 | -0.31586 | 0.25177 | -0.032043 | 0.032043 | -0.10986 | -0.15564 | 0.004578 | -0.32044 | 0.2655 | 0.027466 | 0.073242 | -0.009155 | 0.091553 | 48.175 | -66.861 | -66.5771 | 47.9553 | 47.7676 | 47.8134 | -0.40741 | -0.36163 | 48.1888 | -66.8655 | -66.5176 | 47.9965 | 48.0148 | 47.9141 | -0.17395 | -0.27466 | -0.21973 | -0.28381 | -0.19226 | -0.23804 | -0.56763 | -0.58594 | 47.6074 | 47.6028 | -66.2933 | -66.2796 | 47.8912 | 47.9507 | 47.85 | 47.9279
2989.6406 | 120.4102 | -0.38452 | 119.3115 | 0.044098 | 0.013933 | -0.032654 | 0.034772 | -0.019976 | -0.028181 | -0.023674 | -0.079895 | -0.064856 | -0.0011792 | 0.038102 | -0.015804 | -0.0086048 | -0.011615 | -0.10071 | -0.059509 | 0.041199 | -0.086975 | 0.022888 | -0.082397 | -0.13733 | -0.041199 | -0.16022 | 0.23346 | -0.004578 | 0.09613 | 0.013733 | 0.12817 | 0.42572 | -119.371 | -119.3985 | 0.40741 | 0.24719 | 0.30212 | -0.17853 | -0.1236 | 0.61798 | -119.4717 | -119.3161 | 0.48065 | 0.5127 | 0.39825 | -0.10528 | -0.21973 | -0.018311 | -0.12817 | -0.13733 | -0.23804 | -0.10071 | -0.39368 | 0.32501 | 0.2243 | -119.2703 | -119.0781 | 0.29755 | 0.37994 | 0.28381 | 0.34332
2991.3438 | 119.8196 | -0.737 | 118.309 | 0.044098 | 0.015214 | -0.0365 | 0.035626 | -0.014849 | -0.030317 | -0.022605 | -0.19281 | -0.063788 | -0.0016064 | 0.038956 | -0.02029 | -0.0086048 | -0.013324 | -0.064087 | -0.086975 | 0.25635 | -0.07782 | -0.10071 | -0.19226 | -0.27008 | -0.004578 | -0.3067 | 0.004578 | 0 | -0.07782 | -0.2243 | -0.16022 | 0.99335 | -118.396 | -118.3868 | 0.63629 | 0.46692 | 0.54474 | -0.52643 | -0.44861 | 0.74158 | -118.6157 | -118.309 | 0.65918 | 0.57678 | 0.5127 | -0.16479 | -0.22888 | -0.35706 | -0.33417 | -0.082398 | -0.004578 | -0.34332 | -0.31128 | 0.65002 | 0.4303 | -118.0527 | -118.3044 | 0.65918 | 0.737 | 0.67291 | 0.73242
2993.0781 | 120.4193 | -0.54932 | 119.3619 | 0.02121 | 0.013292 | -0.033082 | 0.036908 | -0.016131 | -0.027967 | -0.021965 | -0.23248 | -0.066351 | -0.0022472 | 0.046006 | -0.013027 | -0.0081774 | -0.013751 | -0.045776 | -0.07782 | -0.004578 | -0.022888 | -0.09613 | -0.21973 | -0.32501 | 0.059509 | -0.050354 | 0.17853 | 0.091553 | 0.11444 | -0.082397 | 0.022888 | 0.54474 | -119.4397 | -119.3848 | 0.45319 | 0.2243 | 0.32959 | -0.32043 | -0.21515 | 0.72784 | -119.4122 | -119.2703 | 0.66376 | 0.5722 | 0.46692 | -0.15564 | -0.26092 | -0.091552 | -0.01831 | -0.064087 | -0.086975 | -0.073242 | -0.22888 | 0.4715 | 0.49896 | -119.3665 | -119.1833 | 0.52643 | 0.64087 | 0.50354 | 0.60883
2994.7812 | 120.1584 | -1.2955 | 118.8538 | 0.15854 | 0.010728 | -0.051026 | 0.023449 | -0.029375 | -0.039717 | -0.032432 | 0.060486 | -0.078741 | -0.011647 | 0.044083 | -0.013881 | -0.0101 | -0.018023 | -0.46234 | -0.027466 | 0.20142 | -0.40741 | 0.09613 | 0.10071 | 0.10529 | -0.13733 | -0.29755 | 0.3067 | -0.11444 | -0.10986 | -0.21057 | -0.24261 | 1.4969 | -118.8812 | -119.2612 | 1.3916 | 1.4008 | 1.3962 | -0.09613 | -0.10071 | 1.6022 | -119.1513 | -118.9682 | 1.1856 | 1.0529 | 1.0849 | -0.54932 | -0.51727 | -0.10529 | -0.60883 | -0.41656 | -0.42114 | -0.22888 | -0.60425 | 1.268 | 0.99793 | -118.6523 | -118.5471 | 0.88806 | 1.181 | 0.83313 | 1.1581
2996.5156 | 120.3918 | -1.3824 | 119.0689 | 0.01358 | 0.013933 | -0.033082 | 0.031781 | -0.01848 | -0.02989 | -0.02111 | -0.040222 | -0.063574 | 0.00052975 | 0.022721 | -0.019649 | -0.010955 | -0.012683 | -0.16937 | -0.045776 | 0.22888 | -0.27466 | -0.35248 | -0.26093 | -0.12817 | -0.086975 | -0.21515 | -0.041199 | -0.050354 | -0.3067 | -0.10071 | -0.059509 | 1.6113 | -119.1147 | -119.3436 | 1.03 | 1.2543 | 1.1215 | -0.35706 | -0.48981 | 1.3412 | -119.2841 | -119.1193 | 1.0757 | 1.3229 | 1.2817 | -0.01831 | -0.059509 | -0.58136 | -0.50354 | -0.2655 | -0.009155 | -0.27466 | -0.17395 | 1.3367 | 1.1673 | -118.84 | -119.1101 | 1.1078 | 1.3321 | 1.2131 | 1.2955
2998.25 | 120.4468 | -0.58136 | 119.3298 | 0.028839 | 0.01436 | -0.033082 | 0.03349 | -0.016344 | -0.028181 | -0.022605 | -0.055481 | -0.066992 | -0.0039562 | 0.02913 | -0.016017 | -0.0077502 | -0.011401 | -0.12817 | -0.064087 | -0.07782 | -0.19684 | -0.35248 | -0.45319 | -0.13275 | -0.036621 | 0.009155 | 0.09613 | 0.027466 | -0.036621 | -0.31128 | -0.2243 | 0.50354 | -119.3939 | -119.5267 | 0.22888 | 0.44861 | 0.12817 | -0.054931 | -0.37537 | 0.67749 | -119.3207 | -119.3024 | 0.54474 | 0.35706 | 0.27008 | -0.32043 | -0.40741 | -0.27466 | -0.11902 | -0.13275 | -0.068664 | 0.013733 | -0.086975 | 0.51727 | 0.59052 | -119.4077 | -119.2337 | 0.38452 | 0.60883 | 0.45319 | 0.54474
3000 | 120.5841 | -0.74158 | 119.5358 | 0.02121 | 0.010942 | -0.034363 | 0.034772 | -0.021044 | -0.030745 | -0.019188 | -0.076843 | -0.065711 | 0.0011708 | 0.036393 | -0.018794 | -0.006682 | -0.01076 | -0.068665 | -0.082397 | -0.027466 | 0 | 0.16479 | 0.045776 | -0.013733 | 0.091553 | -0.018311 | -0.027466 | 0.07782 | 0.17853 | 0.10529 | 0.16022 | 0.71411 | -119.6182 | -119.5358 | 0.90637 | 0.72784 | 0.78735 | 0.013733 | 0.073242 | 0.71411 | -119.5541 | -119.458 | 0.92011 | 0.90179 | 0.84686 | 0.18768 | 0.13275 | 0.19226 | 0.027466 | 0.20599 | 0.10529 | -0.054931 | 0.009155 | 0.65918 | 0.72327 | -119.5633 | -119.5633 | 0.74158 | 0.8194 | 0.67291 | 0.83313
3001.7031 | 120.6116 | -0.82855 | 119.5587 | 0.02121 | 0.01671 | -0.032654 | 0.037549 | -0.015276 | -0.028608 | -0.021751 | -0.064636 | -0.065711 | 0.00052975 | 0.04451 | -0.017726 | -0.0081774 | -0.010119 | -0.050354 | -0.064087 | -0.036621 | -0.004578 | 0.14648 | 0.018311 | -0.07782 | 0.064087 | 0.013733 | -0.073242 | 0.073242 | 0.10986 | 0.041199 | 0.14648 | 0.79193 | -119.6228 | -119.5633 | 0.97504 | 0.75073 | 0.84686 | -0.041199 | 0.054932 | 0.75531 | -119.545 | -119.4855 | 0.93841 | 0.97504 | 0.86975 | 0.21973 | 0.11444 | 0.18311 | 0.032043 | 0.18311 | 0.14648 | -0.027466 | 0.086975 | 0.76446 | 0.84228 | -119.5953 | -119.632 | 0.82397 | 0.90179 | 0.7782 | 0.89264
3003.4062 | 119.6411 | -1.0757 | 119.0872 | 0.028839 | 0.013292 | -0.0318 | 0.038617 | -0.011431 | -0.027967 | -0.019615 | -0.085999 | -0.063361 | 0.00095715 | 0.048142 | -0.016658 | -0.0071094 | -0.016314 | -0.045776 | -0.073242 | -0.045776 | 0.018311 | 0.14648 | -0.013733 | -0.15106 | 0.082397 | -0.013733 | -0.050354 | 0.073242 | 0.15106 | 0.045776 | 0.09613 | 1.03 | -119.1605 | -119.0689 | 1.2222 | 0.92468 | 1.062 | -0.10529 | 0.032043 | 1.0254 | -119.101 | -119.014 | 1.2268 | 1.1719 | 1.1215 | 0.14648 | 0.09613 | 0.19226 | 0.064087 | 0.20142 | 0.1236 | -0.027466 | 0.036621 | 1.0025 | 1.062 | -119.133 | -119.1376 | 1.0941 | 1.149 | 1.03 | 1.1581
3005.1406 | 120.2087 | -1.1261 | 119.2017 | 0.028839 | 0.012651 | -0.032441 | 0.036908 | -0.016771 | -0.030104 | -0.024101 | -0.0066528 | -0.064215 | -0.0011792 | 0.041306 | -0.016872 | -0.0077502 | -0.0088376 | -0.10529 | -0.064087 | -0.045776 | -0.050354 | 0.073242 | -0.004578 | 0 | -0.004578 | 0 | -0.054932 | 0.027466 | 0.11902 | 0.054932 | 0.16022 | 1.0803 | -119.2657 | -119.252 | 1.1993 | 1.1261 | 1.1215 | 0.045776 | 0.041198 | 1.0712 | -119.2017 | -119.1742 | 1.2451 | 1.2863 | 1.181 | 0.21515 | 0.10986 | 0.11902 | -0.004578 | 0.17395 | 0.082398 | -0.018311 | 0.054932 | 1.062 | 1.1261 | -119.2474 | -119.2566 | 1.0757 | 1.1536 | 1.0208 | 1.1215
3006.8438 | 119.5679 | -102.4475 | 16.4429 | -0.68069 | -0.0037982 | -0.026032 | 0.036267 | -0.023821 | -0.02989 | -0.020042 | 0.0025024 | -0.063788 | -0.00075185 | 0.042801 | -0.017513 | -0.0092456 | -0.0045652 | -0.082397 | -0.027466 | -0.013733 | 0.009155 | 0.14648 | 0.068665 | 0.068665 | 0.036621 | -0.027466 | -0.086975 | 0.041199 | 0.17395 | 0.059509 | 0.14648 | 102.4338 | -16.4703 | -16.4337 | 102.594 | 102.5162 | 102.5162 | 0.082398 | 0.082398 | 102.3605 | -16.4703 | -16.4017 | 102.6215 | 102.594 | 102.507 | 0.23346 | 0.14648 | 0.16022 | 0.022888 | 0.26092 | 0.12817 | -0.013733 | 0.059509 | 102.42 | 102.42 | -16.4566 | -16.5298 | 102.4567 | 102.4887 | 102.3651 | 102.4841
3008.5469 | 120.4468 | -2.7191 | 117.5262 | 0.02121 | 0.012864 | -0.033722 | 0.036694 | -0.019549 | -0.031599 | -0.022819 | -0.055481 | -0.064215 | -0.0011792 | 0.043442 | -0.02029 | -0.008391 | -0.0081968 | -0.09613 | -0.086975 | -0.050354 | -0.045776 | 0.07782 | 0 | -0.068665 | 0.004578 | -0.004578 | 0.009155 | 0.032043 | 0.13275 | 0.068665 | 0.16479 | 2.6688 | -117.6132 | -117.572 | 2.7969 | 2.6505 | 2.7191 | -0.018311 | 0.050354 | 2.7283 | -117.5308 | -117.4942 | 2.8519 | 2.8839 | 2.7878 | 0.15564 | 0.05951 | 0.12817 | 0.004578 | 0.1236 | 0.022888 | -0.036621 | -0.013733 | 2.6321 | 2.7145 | -117.5766 | -117.5171 | 2.6733 | 2.7512 | 2.623 | 2.7237
3010.2812 | 88.4857 | -0.11902 | 86.2976 | 0.044098 | 0.012651 | -0.034577 | 0.037762 | -0.036638 | -0.031172 | -0.036277 | 0.054382 | 0.015039 | -0.014637 | 0.022507 | -0.031398 | -0.020781 | -0.022082 | -0.073242 | -0.032043 | 0.21057 | -0.15106 | 0.091553 | 0.10071 | 0.10071 | -0.050354 | -0.29755 | -0.10529 | -0.27466 | 0.086975 | 0.09613 | 0.09613 | 0.32959 | -86.3297 | -86.4487 | 0.21057 | 0.21973 | 0.21973 | -0.10986 | -0.10986 | 0.013733 | -86.5952 | -86.5723 | 0.20599 | 0.21515 | 0.21515 | 0.20142 | 0.20142 | -0.11902 | -0.36163 | 0.19226 | -0.16937 | -0.24261 | -0.19226 | 0.086976 | -0.17853 | -86.087 | -86.4029 | -0.032043 | -0.15564 | 0.045777 | 0.068665
3011.9844 | 111.7355 | -2.4765 | 89.6027 | 0.01358 | 0.010728 | -0.05423 | 0.0052915 | -0.02788 | -0.044416 | 0.028664 | 0.057434 | 0.015893 | -0.016774 | 0.021226 | 0.023076 | 0.028138 | 0.020002 | -0.082397 | -0.054932 | -0.022888 | -0.24261 | 0.091553 | 0.10071 | 0.091553 | -0.073242 | -0.14191 | 0.14191 | -0.37994 | 0.10071 | 0.09613 | 0.09613 | 2.4536 | -89.6576 | -89.8453 | 2.5681 | 2.5681 | 2.5772 | 0.11444 | 0.1236 | 2.6184 | -89.7446 | -89.9826 | 2.5772 | 2.5726 | 2.5726 | -0.045777 | -0.045777 | 0.11444 | -0.21973 | -0.041199 | -0.52185 | -0.032044 | -0.28381 | 2.4216 | 2.3346 | -89.6255 | -89.4608 | 2.2339 | 2.0966 | 2.3941 | 2.4033
3013.7031 | 120.3369 | -81.4133 | 40.3427 | 0.01358 | 0.012224 | -0.029023 | 0.03648 | -0.018267 | -0.030104 | -0.021324 | -0.076843 | -0.062506 | -0.0041698 | 0.041733 | -0.019222 | -0.0088184 | -0.012683 | -0.050354 | -0.064087 | 0.004578 | 0.045776 | 0.19226 | 0.018311 | -0.091553 | 0.050354 | -0.013733 | 0.059509 | 0.07782 | 0.17395 | 0.027466 | 0.059509 | 81.4178 | -40.4068 | -40.2969 | 81.6055 | 81.3217 | 81.4316 | -0.096131 | 0.013733 | 81.4728 | -40.3564 | -40.2649 | 81.5872 | 81.4728 | 81.4407 | 0 | -0.032043 | 0.18768 | 0.041198 | 0.11444 | 0.018311 | -0.068665 | -0.073242 | 81.3492 | 81.3995 | -40.3381 | -40.2832 | 81.459 | 81.4911 | 81.3629 | 81.4636
3015.4219 | 120.5612 | -108.6411 | 11.2793 | -0.68832 | 0.015214 | -0.027955 | 0.034344 | -0.019762 | -0.029676 | -0.024955 | -0.10431 | -0.063574 | -0.00032465 | 0.042588 | -0.016017 | -0.008391 | -0.011187 | -0.068665 | -0.036621 | 0.22888 | 0.018311 | 0.073242 | -0.036621 | -0.10986 | 0.059509 | -0.39368 | -0.11902 | 0.064087 | 0.073242 | -0.004578 | 0.068665 | 108.8699 | -11.3159 | -11.261 | 108.7143 | 108.5312 | 108.6044 | -0.33875 | -0.2655 | 108.522 | -11.673 | -11.2152 | 108.7143 | 108.7097 | 108.6365 | 0.18768 | 0.11444 | -0.15564 | -0.21057 | 0.19226 | 0.18311 | -0.2655 | -0.27466 | 108.6044 | 108.2474 | -11.0504 | -11.3983 | 108.6594 | 108.7051 | 108.5724 | 108.7006
3017.125 | 119.9432 | -0.14648 | 119.8883 | 0.02121 | 0.013933 | -0.034363 | 0.034131 | -0.015276 | -0.02754 | -0.021965 | -0.092102 | -0.064856 | -0.00053825 | 0.043229 | -0.016658 | -0.0086048 | -0.012042 | -0.082397 | -0.073242 | 0.086975 | -0.022888 | 0.091553 | -0.027466 | -0.086975 | 0.050354 | -0.18768 | 0.28381 | 0.054932 | 0.14648 | 0.054932 | 0.14191 | 0.23346 | -119.9615 | -119.9112 | 0.23804 | 0.059509 | 0.11902 | -0.17395 | -0.11444 | 0.4303 | -120.076 | -119.8334 | 0.29297 | 0.28839 | 0.20142 | -0.14191 | -0.22888 | 0.004578 | -0.10986 | -0.13733 | -0.22888 | -0.16022 | -0.4715 | 0.073242 | -0.041199 | -119.8013 | -119.6045 | 0.1236 | 0.20142 | 0.064087 | 0.19684
3018.875 | 119.9615 | -0.16479 | 119.4168 | 0.036468 | 0.015855 | -0.033936 | 0.034985 | -0.018908 | -0.029463 | -0.022392 | -0.061584 | -0.064429 | -0.00096545 | 0.041092 | -0.014095 | -0.0094592 | -0.010333 | -0.10529 | -0.068665 | -0.041199 | -0.068665 | 0.050354 | -0.041199 | -0.10529 | -0.022888 | 0 | 0.091553 | -0.004578 | 0.086975 | 0.009155 | 0.12817 | 0.1236 | -119.4855 | -119.4855 | 0.21515 | 0.059509 | 0.1236 | -0.064087 | 0 | 0.25635 | -119.4168 | -119.4214 | 0.25177 | 0.29297 | 0.17395 | 0.036621 | -0.082398 | 0.091553 | -0.027466 | -0.004578 | -0.096131 | -0.027466 | -0.091553 | 0.09613 | 0.16479 | -119.458 | -119.3253 | 0.09613 | 0.16022 | 0.059509 | 0.14191
3020.5938 | 119.8471 | -0.022888 | 116.1575 | 0.02121 | 0.016069 | -0.032013 | 0.036908 | -0.013353 | -0.031172 | -0.020042 | -0.22943 | -0.065497 | -0.0016064 | 0.036179 | -0.014308 | -0.0094592 | -0.016101 | -0.059509 | -0.068665 | -0.036621 | -0.004578 | -0.064087 | -0.25177 | -0.3479 | 0.059509 | -0.018311 | 0.050354 | 0.068665 | 0.064087 | -0.1236 | -0.022888 | -0.013733 | -116.2262 | -116.1621 | -0.041199 | -0.32501 | -0.22888 | -0.31128 | -0.21515 | 0.073242 | -116.1758 | -116.0889 | 0.086975 | 0 | -0.10071 | -0.073242 | -0.17395 | -0.027466 | 0.032043 | 0.013733 | 0.018311 | -0.032044 | -0.068665 | -0.045777 | 0.004577 | -116.1942 | -116.1072 | 0.01831 | 0.091553 | -0.036621 | 0.082397
3022.2969 | 120.4834 | -0.17395 | 119.7739 | 0.02121 | 0.01201 | -0.032441 | 0.03114 | -0.019549 | -0.03224 | -0.024742 | -0.079895 | -0.068915 | 0.00052975 | 0.044083 | -0.017085 | -0.0092456 | -0.012683 | -0.11444 | -0.041199 | -0.082397 | -0.11902 | -0.3067 | -0.43488 | -0.73242 | -0.059509 | 0.018311 | 0.018311 | 0 | -0.09613 | -0.3891 | -0.20599 | 0.091553 | -119.8151 | -119.8929 | -0.13275 | -0.55847 | -0.26093 | -0.65003 | -0.35248 | 0.19226 | -119.7556 | -119.7739 | 0.07782 | -0.032044 | -0.21515 | -0.22431 | -0.40741 | -0.2243 | -0.036622 | -0.11444 | -0.018311 | 0.041198 | 0 | 0.13275 | 0.19226 | -119.8563 | -119.7556 | 0.054931 | 0.17395 | 0.059509 | 0.11444
3024.0156 | 119.9844 | -0.15106 | 119.1879 | 0.036468 | 0.014787 | -0.033722 | 0.034344 | -0.018694 | -0.027967 | -0.018547 | -0.073792 | -0.065711 | -0.0011792 | 0.04387 | -0.020076 | -0.0094592 | -0.010547 | -0.10529 | -0.073242 | -0.059509 | -0.041199 | 0.07782 | -0.032043 | -0.091553 | 0.004578 | -0.022888 | 0.15106 | 0.054932 | 0.11902 | 0.073242 | 0.16022 | 0.091553 | -119.2612 | -119.2291 | 0.22888 | 0.059509 | 0.11902 | -0.032044 | 0.027466 | 0.30212 | -119.2108 | -119.133 | 0.27008 | 0.31128 | 0.2243 | 0.009155 | -0.07782 | 0.13733 | 0.01831 | -0.032043 | -0.09613 | -0.013733 | -0.17395 | 0.07782 | 0.12817 | -119.2474 | -119.0369 | 0.10986 | 0.20599 | 0.045776 | 0.15564
3025.7188 | 89.8773 | -46.376 | 72.3495 | -0.39078 | 0.013078 | -0.030945 | 0.023236 | -0.017199 | -0.032454 | -0.023246 | 0.048279 | -0.069769 | -0.0028882 | 0.035966 | -0.015377 | -0.0088184 | -0.016742 | -0.09613 | -0.032043 | 0.091553 | -0.24719 | -0.041199 | 0.045776 | 0.082397 | -0.054932 | -0.25635 | 0.14648 | 0.013733 | -0.20142 | -0.36163 | -0.12817 | 46.4676 | -72.3816 | -72.5967 | 46.3348 | 46.4584 | 46.4218 | -0.009156 | -0.045777 | 46.5225 | -72.6059 | -72.3358 | 46.1746 | 46.2479 | 46.0144 | -0.27466 | -0.50812 | -0.13275 | -0.33874 | -0.3479 | -0.13275 | -0.1236 | -0.40283 | 46.344 | 46.1197 | -72.258 | -72.2031 | 46.1288 | 46.3898 | 46.2799 | 46.3211
3027.4531 | 119.5038 | -3.6255 | 87.6709 | 0.036468 | 0.00068782 | -0.052308 | 0.0048641 | -0.024889 | -0.045485 | -0.031578 | 0.066589 | 0.016321 | 0.0062976 | 0.023148 | 0.017308 | -0.016509 | 0.019361 | 0.091553 | -0.3479 | -0.009155 | 0.09613 | 0.10986 | 0.10986 | 0.10986 | -0.14191 | 0.10529 | -0.10529 | 0.11444 | 0.10529 | 0.11444 | 0.11444 | 3.6163 | -88.0188 | -87.5748 | 3.7354 | 3.7354 | 3.7354 | 0.11902 | 0.11902 | 3.5202 | -87.5656 | -87.5565 | 3.7308 | 3.7399 | 3.7399 | 0.21973 | 0.21973 | 0.11902 | 0.10528 | 0.21057 | 0.21973 | -0.33874 | 0.21057 | 3.2776 | 3.7308 | -87.6801 | -87.7762 | 3.7216 | 3.7399 | 3.717 | 3.4836
3029.1719 | 111.3785 | -21.0571 | 97.8882 | 0.01358 | 0.015428 | -0.033509 | 0.031354 | -0.014849 | -0.027327 | -0.023887 | -0.064636 | -0.064002 | 0.00031615 | 0.042801 | -0.014308 | -0.007323 | -0.015033 | -0.27924 | -0.050354 | 0.14648 | -0.35706 | -0.18768 | -0.25177 | -0.059509 | -0.004578 | -0.32959 | 0.22888 | -0.09613 | -0.18768 | -0.27924 | -0.15106 | 21.2036 | -97.9385 | -98.2452 | 20.8694 | 20.9976 | 20.8054 | -0.20599 | -0.39825 | 21.286 | -98.2178 | -97.9843 | 20.8694 | 20.9061 | 20.7779 | -0.37994 | -0.50812 | -0.33417 | -0.50354 | -0.41656 | -0.32501 | -0.19684 | -0.55847 | 21.0068 | 20.7275 | -97.7417 | -97.6593 | 20.7001 | 20.961 | 20.7779 | 21.0526
3030.9375 | 120.3094 | -117.3615 | 2.623 | 0.01358 | 0.013719 | -0.033936 | 0.034985 | -0.017626 | -0.032026 | -0.021537 | -0.17145 | -0.064002 | -0.0011792 | 0.044297 | -0.021144 | -0.010955 | -0.01076 | -0.059509 | -0.027466 | 0.091553 | -0.09613 | -0.20599 | -0.31128 | -0.35248 | -0.068665 | -0.14648 | 0 | -0.036621 | -0.15564 | -0.37994 | -0.27924 | 117.453 | -2.6505 | -2.7191 | 117.1555 | 117.009 | 117.0502 | -0.44403 | -0.40283 | 117.3615 | -2.7695 | -2.6596 | 117.2058 | 117.0822 | 116.9815 | -0.27924 | -0.37994 | -0.29755 | -0.18768 | -0.15564 | -0.036621 | -0.11902 | -0.14648 | 117.334 | 117.215 | -2.5314 | -2.623 | 117.2653 | 117.3248 | 117.3019 | 117.2928
3032.6406 | 118.634 | -6.8024 | 95.3384 | 0.15854 | 0.0064558 | -0.047608 | 0.024945 | -0.03023 | -0.038435 | -0.031364 | 0.060486 | -0.077673 | -0.011647 | 0.040238 | -0.018154 | -0.011595 | -0.018023 | -0.50812 | -0.041199 | 0.27008 | 0.091553 | 0.09613 | 0.10071 | 0.10529 | -0.33875 | -0.16022 | -0.086975 | -0.027466 | -0.32959 | -0.17395 | -0.27466 | 7.0724 | -95.3796 | -95.2469 | 6.8985 | 6.9077 | 6.9031 | -0.1648 | -0.16937 | 6.7154 | -95.4987 | -95.3659 | 6.4728 | 6.5277 | 6.6284 | -0.18768 | -0.086975 | -0.17395 | -0.17853 | -0.24261 | 0.059509 | -0.31128 | -0.073242 | 6.7612 | 6.6422 | -95.0684 | -95.4254 | 6.8939 | 6.7749 | 6.2943 | 6.4636
3034.3594 | 94.6335 | -0.32959 | 85.5606 | 0.036468 | 0.01201 | -0.040131 | 0.031994 | -0.037706 | -0.035871 | -0.041404 | 0.057434 | 0.015893 | -0.011006 | 0.022507 | -0.026699 | -0.012236 | 0.01872 | -0.44861 | -0.022888 | 0.2243 | 0.086975 | 0.10071 | 0.10071 | 0.09613 | -0.21973 | -0.036621 | -0.09613 | -0.1236 | 0.10071 | 0.09613 | 0.10071 | 0.55389 | -85.5835 | -85.4736 | 0.4303 | 0.42572 | 0.4303 | -0.12817 | -0.1236 | 0.23346 | -85.5972 | -85.6842 | 0.4303 | 0.4303 | 0.42572 | 0.19684 | 0.19226 | -0.1236 | -0.13733 | 0.19684 | -0.027466 | -0.24719 | 0.059509 | 0.3067 | 0.29297 | -85.3363 | -85.6567 | 0.41656 | 0.20599 | -0.11902 | 0.10986
3036.0781 | 120.0989 | -7.4249 | 111.9141 | 0.036468 | 0.013292 | -0.032441 | 0.034558 | -0.017412 | -0.026472 | -0.019188 | -0.092102 | -0.064856 | -0.00075185 | 0.041092 | -0.018367 | -0.0086048 | -0.009692 | -0.09613 | -0.07782 | 0.16479 | -0.041199 | 0.022888 | -0.09613 | -0.13733 | -0.022888 | -0.21057 | 0.27008 | 0.004578 | 0.086975 | -0.009155 | 0.10986 | 7.5897 | -111.9919 | -111.9553 | 7.4478 | 7.2876 | 7.3288 | -0.30212 | -0.26092 | 7.695 | -112.1246 | -111.9095 | 7.5119 | 7.5348 | 7.4158 | -0.16022 | -0.27924 | -0.14191 | -0.20599 | -0.18311 | -0.2655 | -0.24261 | -0.48065 | 7.3471 | 7.2144 | -111.7493 | -111.644 | 7.3837 | 7.4295 | 7.3288 | 7.402
3037.7812 | 120.5933 | -6.752 | 112.9074 | 0.02121 | 0.013292 | -0.030518 | 0.026013 | -0.018908 | -0.034162 | -0.024742 | 0.054382 | -0.071265 | -0.0022472 | 0.039597 | -0.014522 | -0.008391 | -0.013324 | -0.16937 | -0.032043 | -0.022888 | -0.3479 | -0.068665 | -0.21057 | 0.07782 | -0.086975 | -0.14191 | 0.27008 | -0.004578 | -0.20599 | -0.3891 | -0.13275 | 6.7291 | -112.9395 | -113.2553 | 6.6833 | 6.8298 | 6.5414 | 0.10071 | -0.18768 | 7.0221 | -113.0493 | -112.912 | 6.546 | 6.6193 | 6.3629 | -0.40283 | -0.65918 | -0.045777 | -0.32501 | -0.47608 | -0.27466 | -0.009155 | -0.41199 | 6.72 | 6.6101 | -112.9303 | -112.6373 | 6.4041 | 6.7474 | 6.5826 | 6.665
3039.5 | 119.5862 | -35.0601 | 84.3658 | 0.051727 | 0.01671 | -0.032868 | 0.028149 | -0.016558 | -0.028608 | -0.022819 | -0.01886 | -0.071692 | 0.0013844 | 0.022507 | -0.021144 | -0.011382 | -0.010974 | -0.11902 | -0.027466 | 0.018311 | -0.24719 | -0.25177 | -0.10071 | 0.09613 | -0.10071 | -0.07782 | 0.24261 | -0.050354 | -0.24719 | -0.10529 | 0.091553 | 35.0784 | -84.3933 | -84.613 | 34.8083 | 35.1562 | 34.9594 | 0.077819 | -0.11902 | 35.3027 | -84.4437 | -84.4162 | 34.8129 | 35.1517 | 34.9548 | -0.15106 | -0.3479 | -0.27008 | -0.2655 | -0.48981 | -0.29297 | -0.045777 | -0.32044 | 35.0327 | 34.9823 | -84.3475 | -84.1232 | 34.8129 | 35.0098 | 34.9411 | 34.9594
3041.2344 | 120.2774 | -20.1828 | 99.8016 | 0.01358 | 0.013292 | -0.033936 | 0.035199 | -0.02083 | -0.030958 | -0.023887 | -0.064636 | -0.066565 | -0.00096545 | 0.042374 | -0.017299 | -0.0094592 | -0.010119 | -0.059509 | -0.082397 | -0.022888 | -0.018311 | 0.14648 | 0.054932 | -0.027466 | 0.059509 | -0.022888 | -0.032043 | 0.073242 | 0.16022 | 0.10986 | 0.16479 | 20.1599 | -99.884 | -99.8199 | 20.3293 | 20.1553 | 20.2377 | -0.004578 | 0.07782 | 20.1508 | -99.8245 | -99.7284 | 20.343 | 20.3476 | 20.2927 | 0.19684 | 0.14191 | 0.16937 | 0.004577 | 0.19226 | 0.10529 | -0.059509 | 0.009155 | 20.1004 | 20.1599 | -99.8245 | -99.8337 | 20.1645 | 20.256 | 20.1233 | 20.2423
3042.9844 | 120.3506 | -39.6194 | 80.3696 | 0.036468 | 0.015214 | -0.032654 | 0.037335 | -0.019976 | -0.028181 | -0.023033 | -0.040222 | -0.063574 | 0.00010255 | 0.046006 | -0.015377 | -0.0088184 | -0.016101 | -0.050354 | -0.064087 | -0.013733 | -0.018311 | 0.14191 | 0.018311 | -0.054932 | 0.022888 | 0 | -0.068665 | 0.041199 | 0.082397 | 0.041199 | 0.14191 | 39.6057 | -80.4337 | -80.3879 | 39.7614 | 39.5645 | 39.6378 | -0.041199 | 0.032044 | 39.5508 | -80.3696 | -80.3284 | 39.7018 | 39.7614 | 39.6606 | 0.21057 | 0.10986 | 0.15564 | -0.004578 | 0.15106 | 0.10986 | -0.050354 | 0.068665 | 39.5554 | 39.6194 | -80.3833 | -80.4382 | 39.6011 | 39.6606 | 39.5691 | 39.6423
3044.6875 | 115.0726 | -24.4492 | 95.7916 | 0.02121 | 0.014573 | -0.032868 | 0.036908 | -0.016131 | -0.029249 | -0.020256 | -0.17755 | -0.064215 | -0.00182 | 0.039811 | -0.020503 | -0.0098864 | -0.012256 | -0.10529 | -0.032043 | -0.059509 | -0.10071 | 0.004578 | -0.1831 | -0.33875 | -0.07782 | 0.022888 | -0.091553 | -0.068665 | 0.013733 | -0.13275 | -0.23804 | 24.3896 | -95.8237 | -95.8923 | 24.4537 | 24.1104 | 24.2661 | -0.27924 | -0.1236 | 24.3576 | -95.7687 | -95.8603 | 24.4629 | 24.2111 | 24.3164 | -0.14648 | -0.041198 | 0.064087 | -0.041199 | 0.10529 | 0.022888 | 0.027466 | 0.11444 | 24.4171 | 24.472 | -95.8511 | -95.8832 | 24.3484 | 24.3805 | 24.3439 | 24.3713
3046.4062 | 105.8441 | -22.9477 | 97.1512 | 0.01358 | 0.015428 | -0.0318 | 0.027936 | -0.018908 | -0.036085 | -0.039482 | 0.054382 | 0.01568 | -0.0056652 | 0.038315 | -0.021358 | -0.026976 | -0.018237 | -0.064087 | -0.041199 | -0.050354 | -0.082397 | -0.16022 | -0.37537 | 0.09613 | -0.036621 | 0.022888 | -0.086975 | -0.013733 | 0.018311 | -0.33875 | 0.10071 | 22.8973 | -97.1924 | -97.2336 | 22.7875 | 23.0438 | 22.5723 | 0.14648 | -0.32501 | 22.8607 | -97.1283 | -97.1649 | 22.966 | 23.0484 | 22.6089 | 0.18768 | -0.25177 | -0.10986 | -0.032043 | 0.10529 | 0.073242 | 0.009155 | 0.10986 | 22.9065 | 22.9706 | -97.2015 | -97.2382 | 22.8653 | 22.934 | 22.8836 | 22.9111
3048.1094 | 120.1996 | -6.4178 | 113.1088 | 0.01358 | 0.015214 | -0.039063 | 0.034344 | -0.029375 | -0.034803 | -0.036918 | 0.051331 | 0.015466 | -0.006947 | 0.035325 | -0.032894 | -0.026976 | -0.019946 | -0.082397 | -0.041199 | -0.086975 | -0.086975 | -0.12817 | -0.4303 | 0.086975 | -0.091553 | 0.018311 | -0.064087 | -0.041199 | 0.018311 | -0.27924 | 0.004578 | 6.3309 | -113.15 | -113.1958 | 6.2897 | 6.5048 | 5.9875 | 0.17395 | -0.34332 | 6.3538 | -113.0905 | -113.15 | 6.4362 | 6.4224 | 6.1386 | 0.068665 | -0.21515 | -0.041199 | 0 | 0.082398 | 0.022888 | 0.045776 | 0.082398 | 6.3766 | 6.4362 | -113.1958 | -113.1729 | 6.3309 | 6.3766 | 6.3354 | 6.3263
3049.875 | 120.5063 | -5.983 | 114.1205 | 0.01358 | 0.010942 | -0.03415 | 0.036053 | -0.018267 | -0.029676 | -0.023033 | -0.028015 | -0.064642 | -0.0016064 | 0.03917 | -0.019863 | -0.0075366 | -0.016101 | -0.059509 | -0.091553 | -0.027466 | 0.018311 | 0.16937 | 0.064087 | 0.013733 | 0.050354 | -0.013733 | -0.050354 | 0.064087 | 0.15564 | 0.07782 | 0.16479 | 5.9555 | -114.212 | -114.1022 | 6.1523 | 5.9967 | 6.0471 | 0.041199 | 0.091553 | 5.9326 | -114.1342 | -114.0564 | 6.1386 | 6.1478 | 6.0608 | 0.21515 | 0.12817 | 0.19684 | 0.045777 | 0.20599 | 0.11444 | -0.064087 | 0.036621 | 5.8914 | 5.9692 | -114.1479 | -114.1708 | 6.0013 | 6.0471 | 5.9235 | 6.0333
3051.5781 | 119.9799 | -6.4407 | 113.9053 | 0.02121 | 0.015855 | -0.034577 | 0.037549 | -0.01848 | -0.027967 | -0.023033 | -0.1806 | -0.06742 | -0.00032465 | 0.02913 | -0.029476 | -0.021849 | -0.0208 | -0.07782 | -0.041199 | -0.064087 | -0.059509 | 0.036621 | -0.22888 | -0.22888 | 0 | 0.027466 | -0.064087 | 0.009155 | 0.086975 | -0.09613 | -0.23346 | 6.3766 | -113.9465 | -113.9648 | 6.4774 | 6.2119 | 6.2119 | -0.16479 | -0.16479 | 6.3766 | -113.8779 | -113.8962 | 6.5277 | 6.2073 | 6.3446 | -0.16937 | -0.032043 | 0.10071 | 0.004578 | 0.15106 | 0.073242 | 0.022888 | 0.091553 | 6.3995 | 6.4682 | -113.9694 | -113.9694 | 6.3812 | 6.4499 | 6.3629 | 6.4407
3053.2969 | 120.5933 | -4.7012 | 115.2054 | 0.01358 | 0.013505 | -0.031373 | 0.036053 | -0.018053 | -0.027754 | -0.020897 | -0.00054937 | -0.06507 | 0.001598 | 0.046647 | -0.014736 | -0.0068958 | -0.011401 | -0.032043 | -0.09613 | -0.022888 | 0.009155 | 0.13275 | 0.013733 | 0 | 0.082397 | -0.013733 | -0.059509 | 0.068665 | 0.15106 | 0.073242 | 0.1831 | 4.6783 | -115.3015 | -115.1962 | 4.834 | 4.7012 | 4.715 | 0.022888 | 0.036621 | 4.6417 | -115.2191 | -115.1367 | 4.8523 | 4.8843 | 4.7745 | 0.24261 | 0.13275 | 0.15564 | 0.032043 | 0.21057 | 0.12817 | -0.073242 | 0.045776 | 4.6051 | 4.6875 | -115.2283 | -115.2649 | 4.7104 | 4.7699 | 4.6692 | 4.7836
3055.0156 | 120.6253 | -38.7589 | 81.3812 | 0.0059509 | 0.016282 | -0.031586 | 0.036053 | -0.019121 | -0.028181 | -0.023033 | 0.0055542 | -0.06507 | 0.0048024 | 0.041733 | -0.017299 | -0.009032 | -0.011828 | -0.068665 | -0.082397 | -0.041199 | 0.027466 | 0.17395 | 0.07782 | 0.054932 | 0.059509 | -0.009155 | -0.032043 | 0.073242 | 0.1831 | 0.10529 | 0.17395 | 38.7177 | -81.4636 | -81.3538 | 38.9328 | 38.8138 | 38.8367 | 0.096131 | 0.11902 | 38.7268 | -81.3904 | -81.308 | 38.942 | 38.9328 | 38.8641 | 0.20599 | 0.13733 | 0.21515 | 0.068665 | 0.21515 | 0.10529 | -0.041198 | 0.022888 | 38.6765 | 38.7497 | -81.4224 | -81.4133 | 38.7863 | 38.8321 | 38.6902 | 38.8184
3056.7344 | 120.5978 | -3.4607 | 117.009 | 0.01358 | 0.013719 | -0.034791 | 0.039044 | -0.014849 | -0.030104 | -0.021324 | -0.12872 | -0.06272 | -0.0011792 | 0.034684 | -0.016231 | -0.009032 | -0.012896 | -0.12817 | -0.054932 | -0.068665 | -0.11902 | 0 | -0.091553 | -0.23804 | -0.082397 | 0 | -0.07782 | -0.022888 | 0.032043 | -0.068665 | 0.082397 | 3.392 | -117.0639 | -117.128 | 3.4607 | 3.2227 | 3.3691 | -0.16937 | -0.022888 | 3.3829 | -117.009 | -117.0319 | 3.4927 | 3.5431 | 3.392 | 0.16022 | 0.009155 | 0.068665 | -0.050354 | 0.10986 | 0.054932 | 0.013733 | 0.07782 | 3.4058 | 3.4607 | -117.0776 | -117.0868 | 3.3417 | 3.4378 | 3.3325 | 3.3783
3058.4844 | 120.0623 | -119.6457 | 0.064087 | 0.01358 | 0.012437 | -0.032013 | 0.037549 | -0.016344 | -0.029036 | -0.020469 | 0.023865 | -0.063788 | -0.00032465 | 0.039597 | -0.014522 | -0.007323 | -0.016101 | -0.013733 | -0.050354 | -0.018311 | 0.07782 | 0.19684 | 0.059509 | 0.082397 | 0.11902 | 0.027466 | -0.022888 | 0.10071 | 0.1831 | 0.10071 | 0.20142 | 119.6274 | -0.11444 | 0.013733 | 119.8425 | 119.7281 | 119.7052 | 0.10071 | 0.07782 | 119.6228 | -0.036621 | 0.036621 | 119.8288 | 119.8471 | 119.7464 | 0.2243 | 0.1236 | 0.21515 | 0.096131 | 0.20599 | 0.1236 | -0.032043 | 0.050354 | 119.5953 | 119.6732 | -0.082398 | -0.086975 | 119.7235 | 119.7464 | 119.632 | 119.7647
3060.1875 | 120.4422 | -120.0531 | 0.064087 | 0.01358 | 0.016069 | -0.032013 | 0.036053 | -0.015062 | -0.027327 | -0.021537 | 0.023865 | -0.064642 | -0.0026744 | 0.039384 | -0.016231 | -0.0077502 | -0.015033 | 0.022888 | -0.036621 | 0.004578 | 0.054932 | 0.19226 | 0.064087 | 0.082397 | 0.10986 | 0.032043 | -0.018311 | 0.11444 | 0.1831 | 0.09613 | 0.21515 | 120.0577 | -0.10071 | -0.009155 | 120.2454 | 120.1355 | 120.1172 | 0.077819 | 0.059509 | 120.0348 | -0.032044 | 0.050354 | 120.2362 | 120.2682 | 120.1492 | 0.23346 | 0.11444 | 0.18768 | 0.050354 | 0.20142 | 0.13275 | -0.041199 | 0.050354 | 120.0165 | 120.0851 | -0.059509 | -0.082398 | 120.108 | 120.1675 | 120.076 | 120.163
3061.9375 | 120.5246 | -120.2042 | 0.10071 | 0.02121 | 0.014573 | -0.033509 | 0.03584 | -0.014635 | -0.029036 | -0.023246 | 0.008606 | -0.062933 | -0.00096545 | 0.037034 | -0.018367 | -0.0086048 | -0.014392 | -0.054932 | -0.050354 | 0.009155 | -0.018311 | 0.10986 | 0.022888 | 0.045776 | 0.036621 | 0.032043 | -0.027466 | 0.068665 | 0.14191 | 0.068665 | 0.17853 | 120.2133 | -0.15106 | -0.11902 | 120.314 | 120.2499 | 120.2271 | 0.036621 | 0.013733 | 120.1767 | -0.068665 | -0.032043 | 120.3461 | 120.3827 | 120.2728 | 0.20599 | 0.096131 | 0.10071 | -0.027466 | 0.16937 | 0.096131 | -0.059509 | 0.059509 | 120.1538 | 120.2362 | -0.091553 | -0.12817 | 120.1859 | 120.2728 | 120.1492 | 120.2408
3063.6875 | 120.4193 | -120.195 | 0.21515 | 0.01358 | 0.014573 | -0.033936 | 0.03584 | -0.019762 | -0.031172 | -0.024314 | 0.008606 | -0.062292 | -0.0024608 | 0.038529 | -0.021785 | -0.012236 | -0.01311 | -0.036621 | -0.027466 | -0.009155 | -0.054932 | 0.07782 | 0.004578 | 0 | -0.022888 | 0.050354 | -0.032043 | -0.013733 | 0.059509 | -0.018311 | 0.086975 | 120.1859 | -0.24261 | -0.27008 | 120.2728 | 120.195 | 120.1996 | 0.009155 | 0.013733 | 120.163 | -0.16479 | -0.22888 | 120.2545 | 120.282 | 120.1767 | 0.11902 | 0.013732 | 0.086975 | -0.045777 | 0.091552 | 0.01831 | -0.018311 | 0.082397 | 120.1675 | 120.2454 | -0.2243 | -0.24719 | 120.1401 | 120.1813 | 120.1584 | 120.1721
3065.4062 | 119.9158 | -119.4122 | 0.10529 | 0.01358 | 0.014787 | -0.032441 | 0.036267 | -0.017412 | -0.027967 | -0.021965 | 0.0025024 | -0.065711 | -0.0037426 | 0.034043 | -0.018367 | -0.010955 | -0.011828 | -0.022888 | -0.054932 | 0.009155 | 0.054932 | 0.21057 | 0.09613 | 0.086975 | 0.09613 | 0.027466 | -0.018311 | 0.10986 | 0.19226 | 0.10529 | 0.20142 | 119.4214 | -0.16022 | -0.050354 | 119.6228 | 119.4992 | 119.5084 | 0.07782 | 0.086975 | 119.3939 | -0.07782 | 0.004577 | 119.6045 | 119.6136 | 119.5175 | 0.21973 | 0.1236 | 0.20142 | 0.045777 | 0.21057 | 0.12817 | -0.064087 | 0.045777 | 119.3573 | 119.4397 | -0.096131 | -0.1236 | 119.4672 | 119.5221 | 119.3893 | 119.5084
3067.1094 | 120.0714 | -119.6503 | 0.20142 | 0.0059509 | 0.013292 | -0.031373 | 0.035626 | -0.012713 | -0.030317 | -0.022178 | 0.008606 | -0.065924 | -0.00182 | 0.047074 | -0.019222 | -0.0092456 | -0.015887 | -0.013733 | -0.045776 | 0.004578 | 0.045776 | 0.18768 | 0.091553 | 0.091553 | 0.07782 | 0.018311 | -0.004578 | 0.086975 | 0.17853 | 0.10986 | 0.17853 | 119.6548 | -0.24719 | -0.15564 | 119.838 | 119.7418 | 119.7418 | 0.086975 | 0.086975 | 119.6457 | -0.18311 | -0.11444 | 119.8288 | 119.8288 | 119.7601 | 0.18311 | 0.11444 | 0.1831 | 0.041198 | 0.18311 | 0.091553 | -0.050354 | 0.022889 | 119.6045 | 119.6686 | -0.19684 | -0.20599 | 119.696 | 119.7372 | 119.6365 | 119.7281
3068.875 | 119.8975 | -119.4901 | 0.068665 | 0.036468 | 0.016496 | -0.034363 | 0.038403 | -0.012713 | -0.02754 | -0.020683 | 0.020813 | -0.064215 | -0.0022472 | 0.037675 | -0.01324 | -0.0079638 | -0.015674 | 0.009155 | -0.050354 | 0 | 0.045776 | 0.18768 | 0.050354 | 0.07782 | 0.11444 | 0.013733 | -0.004578 | 0.10986 | 0.16937 | 0.07782 | 0.20142 | 119.4901 | -0.11902 | -0.022889 | 119.6777 | 119.5679 | 119.5404 | 0.07782 | 0.050354 | 119.4855 | -0.054932 | 0.041198 | 119.6594 | 119.6915 | 119.5679 | 0.20599 | 0.082398 | 0.18768 | 0.045776 | 0.17395 | 0.11444 | -0.050354 | 0.018311 | 119.4397 | 119.5038 | -0.068665 | -0.073243 | 119.5358 | 119.5999 | 119.4992 | 119.6045
3070.5781 | 120.2911 | -119.9341 | 0.091553 | 0.01358 | 0.013292 | -0.034577 | 0.034985 | -0.019121 | -0.027754 | -0.021537 | 0.008606 | -0.063147 | -0.0028882 | 0.039597 | -0.01794 | -0.0098864 | -0.014392 | 0 | -0.036621 | 0.009155 | 0.050354 | 0.19684 | 0.09613 | 0.082397 | 0.091553 | 0.018311 | -0.009155 | 0.11444 | 0.1831 | 0.10529 | 0.18768 | 119.9432 | -0.12817 | -0.041199 | 120.1309 | 120.0165 | 120.0302 | 0.073242 | 0.086975 | 119.9249 | -0.073242 | 0.022888 | 120.1172 | 120.1218 | 120.0394 | 0.19684 | 0.11444 | 0.18768 | 0.041199 | 0.19226 | 0.1236 | -0.045776 | 0.027466 | 119.8975 | 119.9524 | -0.082398 | -0.10071 | 119.9844 | 120.0485 | 119.9341 | 120.0256
3072.2812 | 120.2866 | -120.0485 | 0.15106 | 0.02121 | 0.016069 | -0.033082 | 0.040326 | -0.019549 | -0.026045 | -0.024314 | 0.011658 | -0.062506 | -0.0024608 | 0.035111 | -0.020076 | -0.011809 | -0.018237 | -0.068665 | 0.013733 | -0.041199 | -0.07782 | 0.036621 | -0.022888 | -0.022888 | -0.068665 | 0.050354 | -0.068665 | -0.004578 | 0.050354 | -0.027466 | 0.09613 | 120.0073 | -0.13733 | -0.22888 | 120.0851 | 120.0256 | 120.0256 | 0.018311 | 0.018311 | 119.9799 | -0.10071 | -0.15564 | 120.0989 | 120.1447 | 120.0211 | 0.16479 | 0.041199 | 0.07782 | -0.036621 | 0.11902 | 0.064087 | 0.054932 | 0.11902 | 120.0623 | 120.0989 | -0.19226 | -0.21973 | 119.9707 | 120.0439 | 119.9799 | 119.9799
3074 | 120.3781 | -120.0668 | 0.059509 | 0.02121 | 0.013505 | -0.035431 | 0.037335 | -0.016558 | -0.028822 | -0.026023 | 0.0055542 | -0.062079 | -0.0020336 | 0.037034 | -0.014522 | -0.0075366 | -0.01546 | -0.064087 | -0.022888 | -0.022888 | -0.027466 | 0.09613 | -0.013733 | 0.009155 | 0.032043 | 0.036621 | -0.018311 | 0.10986 | 0.16022 | 0.064087 | 0.21057 | 120.0439 | -0.082397 | -0.086975 | 120.163 | 120.076 | 120.0531 | 0.032043 | 0.009155 | 120.0485 | -0.022888 | 0.050354 | 120.2271 | 120.2774 | 120.1309 | 0.22888 | 0.082398 | 0.11902 | -0.004578 | 0.17853 | 0.12817 | 0 | 0.054932 | 120.0439 | 120.1035 | -0.082397 | -0.07782 | 120.0394 | 120.1767 | 120.0027 | 120.0989
3075.7344 | 120.4285 | -119.8837 | 0.27924 | 0.0059509 | 0.015001 | -0.0318 | 0.035626 | -0.01314 | -0.028608 | -0.022178 | 0.008606 | -0.064002 | -0.0041698 | 0.040452 | -0.012386 | -0.0086048 | -0.0094784 | 0 | -0.041199 | 0 | 0.032043 | 0.16022 | 0.041199 | 0.050354 | 0.09613 | 0.022888 | -0.013733 | 0.13275 | 0.18768 | 0.091553 | 0.21057 | 119.8837 | -0.32043 | -0.24719 | 120.0439 | 119.9341 | 119.9249 | 0.050354 | 0.041199 | 119.87 | -0.25635 | -0.14648 | 120.0714 | 120.0943 | 119.9753 | 0.2243 | 0.10529 | 0.16022 | 0.032043 | 0.20142 | 0.14648 | -0.041199 | 0.036621 | 119.8425 | 119.9066 | -0.27924 | -0.29297 | 119.9158 | 120.0165 | 119.8837 | 119.9799
3077.6562 | 119.165 | -118.6615 | 0.19684 | 0.028839 | 0.019273 | -0.0318 | 0.039258 | -0.012499 | -0.027967 | -0.021324 | 0.014709 | -0.063574 | -0.0016064 | 0.039384 | -0.014949 | -0.0092456 | -0.016314 | 0.013733 | -0.050354 | 0 | 0.054932 | 0.18768 | 0.064087 | 0.064087 | 0.10529 | 0.041199 | -0.032043 | 0.11902 | 0.17395 | 0.07782 | 0.18768 | 118.6615 | -0.24719 | -0.14191 | 118.8492 | 118.7256 | 118.7256 | 0.064087 | 0.064087 | 118.6295 | -0.15564 | -0.077819 | 118.8354 | 118.8492 | 118.7393 | 0.21973 | 0.10986 | 0.18768 | 0.054932 | 0.20599 | 0.15106 | -0.050354 | 0.073242 | 118.6111 | 118.7027 | -0.19684 | -0.22888 | 118.7164 | 118.7805 | 118.6752 | 118.7668
3079.5 | 120.3415 | -120.0943 | 0.091553 | 0.044098 | 0.013505 | -0.032654 | 0.037549 | -0.018053 | -0.028608 | -0.020042 | 0.014709 | -0.061651 | -0.0013928 | 0.042374 | -0.020931 | -0.010955 | -0.013537 | -0.036621 | 0.013733 | -0.059509 | -0.045776 | 0.050354 | -0.009155 | -0.013733 | -0.022888 | 0.059509 | -0.045776 | 0.027466 | 0.082397 | 0.009155 | 0.13733 | 120.0348 | -0.07782 | -0.13733 | 120.1447 | 120.0806 | 120.0851 | 0.045776 | 0.050354 | 120.0485 | -0.032044 | -0.064087 | 120.1767 | 120.2316 | 120.1035 | 0.18311 | 0.054931 | 0.10986 | 0.013733 | 0.12817 | 0.073242 | 0.073242 | 0.10528 | 120.108 | 120.1538 | -0.15106 | -0.13733 | 120.0485 | 120.1218 | 120.0577 | 120.0714
3081.2344 | 120.488 | -120.1538 | 0.07782 | 0.02121 | 0.015001 | -0.031586 | 0.037549 | -0.013781 | -0.027327 | -0.022605 | 0.011658 | -0.063574 | -0.00182 | 0.041306 | -0.014522 | -0.0077502 | -0.012469 | 0 | -0.041199 | 0.004578 | 0.050354 | 0.16937 | 0.054932 | 0.054932 | 0.091553 | 0.013733 | -0.018311 | 0.11902 | 0.17853 | 0.10071 | 0.20142 | 120.1584 | -0.11902 | -0.027466 | 120.3232 | 120.2087 | 120.2087 | 0.050354 | 0.050354 | 120.1355 | -0.064087 | 0.041199 | 120.3323 | 120.3552 | 120.2545 | 0.21973 | 0.11902 | 0.16479 | 0.045776 | 0.19684 | 0.13733 | -0.045777 | 0.032044 | 120.1126 | 120.1675 | -0.073242 | -0.096131 | 120.2042 | 120.2728 | 120.1538 | 120.2454
3083.0156 | 120.5109 | -120.2179 | 0.091553 | 0.02121 | 0.012437 | -0.034577 | 0.037121 | -0.013781 | -0.027754 | -0.022178 | 0.011658 | -0.064856 | -0.0028882 | 0.042374 | -0.019008 | -0.0088184 | -0.010333 | -0.041199 | -0.022888 | -0.009155 | 0 | 0.11444 | 0.013733 | 0.050354 | 0.022888 | 0.036621 | -0.027466 | 0.054932 | 0.13733 | 0.041199 | 0.15106 | 120.2087 | -0.11444 | -0.091553 | 120.3323 | 120.2682 | 120.2316 | 0.059509 | 0.022888 | 120.1904 | -0.054932 | -0.036621 | 120.3552 | 120.369 | 120.2591 | 0.17853 | 0.068665 | 0.1236 | 0.009155 | 0.16479 | 0.082398 | -0.013733 | 0.064087 | 120.195 | 120.2545 | -0.10071 | -0.11902 | 120.2179 | 120.2728 | 120.1767 | 120.2408
3084.8125 | 120.4376 | -120.2957 | 0.10529 | 0.036468 | 0.015428 | -0.033295 | 0.036908 | -0.011644 | -0.029676 | -0.020042 | 0.014709 | -0.060156 | -0.0026744 | 0.027634 | -0.016445 | -0.010741 | -0.015033 | -0.032043 | -0.009155 | -0.032043 | -0.036621 | 0.09613 | 0.009155 | 0.013733 | 0.013733 | 0.064087 | -0.036621 | 0.041199 | 0.10071 | 0.013733 | 0.14648 | 120.2637 | -0.11444 | -0.14191 | 120.3918 | 120.3094 | 120.3049 | 0.045776 | 0.041198 | 120.2591 | -0.041199 | -0.064087 | 120.3964 | 120.4422 | 120.3094 | 0.18311 | 0.050354 | 0.12817 | -0.004578 | 0.13733 | 0.07782 | 0.022888 | 0.10071 | 120.2866 | 120.3598 | -0.13733 | -0.14191 | 120.2591 | 120.3369 | 120.2637 | 120.3094
3086.625 | 120.5475 | -120.3186 | 0.07782 | 0.01358 | 0.013078 | -0.033509 | 0.038189 | -0.013567 | -0.027754 | -0.024314 | 0.0055542 | -0.064642 | 0.0013844 | 0.044938 | -0.015804 | -0.0064684 | -0.010974 | -0.082397 | -0.013733 | -0.032043 | -0.054932 | 0.068665 | -0.054932 | -0.032043 | -0.013733 | 0.032043 | -0.027466 | 0.059509 | 0.11902 | 0.032043 | 0.15564 | 120.2866 | -0.091553 | -0.13275 | 120.3873 | 120.2866 | 120.2637 | 0 | -0.022889 | 120.2911 | -0.045777 | -0.018311 | 120.4376 | 120.4742 | 120.3506 | 0.18311 | 0.059509 | 0.10071 | -0.022889 | 0.14649 | 0.086975 | 0.01831 | 0.059509 | 120.3049 | 120.3506 | -0.10986 | -0.10529 | 120.2637 | 120.3781 | 120.2362 | 120.3049
3088.3438 | 120.6299 | -120.3278 | 0.050354 | 0.01358 | 0.017137 | -0.032227 | 0.03584 | -0.013353 | -0.02754 | -0.02346 | 0.008606 | -0.063361 | -0.0022472 | 0.041306 | -0.014736 | -0.0064684 | -0.016314 | 0.009155 | -0.054932 | 0.018311 | 0.050354 | 0.16479 | 0.045776 | 0.045776 | 0.10529 | 0.036621 | -0.022888 | 0.11902 | 0.19226 | 0.10071 | 0.20599 | 120.3461 | -0.10529 | 0 | 120.4926 | 120.3735 | 120.3735 | 0.027465 | 0.027465 | 120.3049 | -0.013733 | 0.068665 | 120.52 | 120.5338 | 120.4285 | 0.22888 | 0.1236 | 0.14648 | 0.032043 | 0.21515 | 0.14191 | -0.073243 | 0.059509 | 120.2728 | 120.3644 | -0.032043 | -0.073242 | 120.3781 | 120.4468 | 120.3369 | 120.433
3090.125 | 120.5841 | -120.3918 | 0.09613 | 0.036468 | 0.013719 | -0.032868 | 0.036694 | -0.013353 | -0.029249 | -0.021537 | 0.008606 | -0.060797 | -0.00011105 | 0.037034 | -0.017726 | -0.010741 | -0.010333 | -0.022888 | -0.009155 | -0.036621 | -0.022888 | 0.1236 | 0.013733 | 0.022888 | 0.036621 | 0.045776 | -0.045776 | 0.050354 | 0.1236 | 0.022888 | 0.14648 | 120.3552 | -0.10528 | -0.11902 | 120.5154 | 120.4147 | 120.4056 | 0.059509 | 0.050354 | 120.3461 | -0.050354 | -0.045776 | 120.5154 | 120.5383 | 120.4147 | 0.19226 | 0.068664 | 0.16022 | 0.013733 | 0.16937 | 0.09613 | 0.027466 | 0.091552 | 120.3827 | 120.4376 | -0.13275 | -0.14191 | 120.369 | 120.4422 | 120.369 | 120.4285
3091.9062 | 120.6162 | -120.433 | 0.068665 | 0.01358 | 0.012864 | -0.035431 | 0.033917 | -0.01549 | -0.029676 | -0.02581 | 0.011658 | -0.063574 | -0.00075185 | 0.037034 | -0.020717 | -0.009032 | -0.014819 | -0.022888 | -0.050354 | -0.009155 | 0.018311 | 0.16937 | 0.07782 | 0.064087 | 0.050354 | 0.041199 | -0.027466 | 0.036621 | 0.13733 | 0.068665 | 0.15106 | 120.4239 | -0.11902 | -0.050354 | 120.6024 | 120.4971 | 120.5109 | 0.073242 | 0.086975 | 120.4056 | -0.027466 | -0.032044 | 120.5704 | 120.5841 | 120.5017 | 0.17853 | 0.096131 | 0.17853 | 0.027466 | 0.16479 | 0.064087 | -0.041199 | 0.068665 | 120.3827 | 120.4742 | -0.07782 | -0.096131 | 120.4514 | 120.4697 | 120.4102 | 120.4834
3093.6406 | 120.5841 | -120.4422 | 0.07782 | 0.01358 | 0.015001 | -0.032227 | 0.036053 | -0.014422 | -0.030104 | -0.024742 | 0.0055542 | -0.062933 | 0.0013844 | 0.040665 | -0.017726 | -0.0098864 | -0.012896 | -0.068665 | -0.004578 | -0.032043 | -0.09613 | 0.027466 | -0.086975 | -0.050354 | -0.054932 | 0.068665 | -0.054932 | 0 | 0.054932 | -0.032043 | 0.11444 | 120.4102 | -0.082398 | -0.17395 | 120.4697 | 120.3918 | 120.3552 | -0.018311 | -0.054932 | 120.3873 | -0.009155 | -0.07782 | 120.4971 | 120.5566 | 120.4102 | 0.16937 | 0.022889 | 0.059509 | -0.064087 | 0.10986 | 0.054932 | 0.027465 | 0.1236 | 120.4376 | 120.5109 | -0.10986 | -0.13275 | 120.3461 | 120.4422 | 120.3735 | 120.3873
3095.3906 | 120.6024 | -120.488 | 0.10529 | 0.02121 | 0.015001 | -0.035645 | 0.039044 | -0.01549 | -0.027327 | -0.021537 | 0.008606 | -0.062292 | 0.0018116 | 0.03682 | -0.017299 | -0.010314 | -0.0088376 | -0.07782 | -0.013733 | -0.027466 | -0.10986 | -0.009155 | -0.10071 | -0.068665 | -0.10986 | 0.036621 | -0.054932 | -0.022888 | 0.036621 | -0.059509 | 0.09613 | 120.4605 | -0.11902 | -0.21515 | 120.4788 | 120.4193 | 120.3873 | -0.041199 | -0.073242 | 120.433 | -0.068665 | -0.12817 | 120.5246 | 120.5841 | 120.4285 | 0.15106 | -0.004577 | 0.018311 | -0.082397 | 0.091553 | 0.032044 | 0.013733 | 0.091553 | 120.4742 | 120.5246 | -0.13275 | -0.16022 | 120.3781 | 120.4651 | 120.4102 | 120.3781
3097.1875 | 120.6162 | -120.5154 | 0.10986 | 0.01358 | 0.01436 | -0.035645 | 0.036053 | -0.013567 | -0.028181 | -0.02111 | 0.008606 | -0.062292 | -0.0013928 | 0.035325 | -0.02029 | -0.011382 | -0.01546 | -0.041199 | -0.022888 | -0.018311 | -0.045776 | 0.10071 | 0.022888 | 0.013733 | -0.027466 | 0.045776 | -0.036621 | -0.009155 | 0.068665 | 0.004578 | 0.10529 | 120.4971 | -0.13275 | -0.15564 | 120.6161 | 120.5292 | 120.5383 | 0.032044 | 0.041199 | 120.4788 | -0.064087 | -0.11902 | 120.5841 | 120.6207 | 120.52 | 0.14191 | 0.041199 | 0.11902 | -0.027465 | 0.10529 | 0.027466 | -0.004577 | 0.082397 | 120.4926 | 120.5612 | -0.12817 | -0.14648 | 120.4697 | 120.5063 | 120.4742 | 120.488
3098.9688 | 120.7535 | -120.4834 | 0.082397 | 0.028839 | 0.012437 | -0.032868 | 0.03584 | -0.014849 | -0.025618 | -0.023246 | 0.008606 | -0.064856 | -0.00182 | 0.046219 | -0.018154 | -0.0086048 | -0.011615 | -0.050354 | -0.032043 | -0.004578 | -0.013733 | 0.14191 | 0.045776 | 0.064087 | 0.045776 | 0.027466 | -0.013733 | 0.07782 | 0.1831 | 0.11902 | 0.20599 | 120.4788 | -0.11444 | -0.09613 | 120.6253 | 120.5475 | 120.5292 | 0.068665 | 0.050354 | 120.4697 | -0.054931 | -0.004577 | 120.6665 | 120.6894 | 120.6024 | 0.21973 | 0.13275 | 0.14649 | -0.009155 | 0.19684 | 0.091553 | -0.027465 | 0.041199 | 120.4514 | 120.5109 | -0.086975 | -0.09613 | 120.4697 | 120.5612 | 120.433 | 120.5292
3100.7031 | 120.7993 | -120.5109 | 0.073242 | 0.01358 | 0.01436 | -0.032441 | 0.035199 | -0.019976 | -0.029676 | -0.025596 | 0.0025024 | -0.06507 | 0.00031615 | 0.033616 | -0.019008 | -0.0101 | -0.013324 | -0.009155 | -0.068665 | 0.004578 | 0.050354 | 0.21973 | 0.10986 | 0.086975 | 0.10071 | 0.004578 | -0.009155 | 0.082397 | 0.2243 | 0.13275 | 0.20142 | 120.5154 | -0.14191 | -0.022888 | 120.7306 | 120.5978 | 120.6207 | 0.082397 | 0.10529 | 120.5017 | -0.068664 | 0.009155 | 120.7352 | 120.7123 | 120.6436 | 0.21057 | 0.14191 | 0.21515 | 0.045776 | 0.23346 | 0.091552 | -0.073243 | 0.013733 | 120.4422 | 120.5154 | -0.068664 | -0.082397 | 120.5612 | 120.5933 | 120.5017 | 120.6116
3102.5156 | 120.8084 | -120.5063 | 0.064087 | 0.0059509 | 0.013078 | -0.033722 | 0.036908 | -0.015062 | -0.028822 | -0.019828 | 0.0055542 | -0.064002 | -0.0013928 | 0.040879 | -0.018794 | -0.009032 | -0.012042 | -0.022888 | -0.050354 | -0.013733 | 0.050354 | 0.1831 | 0.091553 | 0.09613 | 0.10986 | 0.013733 | -0.013733 | 0.10529 | 0.2243 | 0.14191 | 0.2243 | 120.4926 | -0.11444 | -0.013733 | 120.6894 | 120.6024 | 120.5978 | 0.10986 | 0.10529 | 120.4926 | -0.050354 | 0.041199 | 120.7306 | 120.7306 | 120.6482 | 0.23804 | 0.15564 | 0.19684 | 0.064087 | 0.23804 | 0.11902 | -0.036621 | 0.027466 | 120.4559 | 120.52 | -0.07782 | -0.07782 | 120.5566 | 120.6116 | 120.4834 | 120.6162
3104.25 | 120.7214 | -120.575 | 0.10529 | 0.036468 | 0.014787 | -0.035431 | 0.037335 | -0.022967 | -0.030104 | -0.017906 | 0.014709 | -0.062079 | 0.002666 | 0.033616 | -0.019008 | -0.010955 | -0.013324 | -0.073242 | 0.009155 | -0.045776 | -0.07782 | 0.050354 | -0.036621 | -0.013733 | -0.059509 | 0.073242 | -0.064087 | -0.022888 | 0.059509 | -0.027466 | 0.11902 | 120.5292 | -0.096131 | -0.18311 | 120.6253 | 120.5612 | 120.5383 | 0.032043 | 0.009155 | 120.5109 | -0.032044 | -0.12817 | 120.6345 | 120.694 | 120.5475 | 0.18311 | 0.036621 | 0.09613 | -0.032044 | 0.1236 | 0.041199 | 0.054931 | 0.13733 | 120.5841 | 120.6482 | -0.15106 | -0.16937 | 120.4971 | 120.5521 | 120.5017 | 120.5154
3105.9688 | 120.7031 | -120.5933 | 0.09613 | 0.028839 | 0.013292 | -0.033295 | 0.037549 | -0.018908 | -0.029036 | -0.024528 | 0.008606 | -0.064429 | -0.0013928 | 0.034684 | -0.016872 | -0.010527 | -0.015033 | -0.068665 | -0.013733 | -0.032043 | -0.073242 | 0.018311 | -0.073242 | -0.064087 | -0.09613 | 0.068665 | -0.041199 | -0.036621 | 0.041199 | -0.050354 | 0.091553 | 120.5612 | -0.10986 | -0.16937 | 120.6116 | 120.5292 | 120.52 | -0.032044 | -0.041199 | 120.5521 | -0.027465 | -0.13275 | 120.6345 | 120.6848 | 120.5429 | 0.13275 | -0.009155 | 0.050354 | -0.041199 | 0.082398 | 0.004578 | 0.01831 | 0.10986 | 120.5795 | 120.6619 | -0.12817 | -0.13733 | 120.52 | 120.5566 | 120.5246 | 120.4971
3107.75 | 120.8633 | -120.5658 | 0.07782 | 0.036468 | 0.015855 | -0.031159 | 0.03584 | -0.017412 | -0.027113 | -0.022605 | 0.014709 | -0.062506 | -0.00011105 | 0.038743 | -0.014522 | -0.0086048 | -0.011187 | 0.013733 | -0.045776 | 0.013733 | 0.041199 | 0.19684 | 0.064087 | 0.073242 | 0.10529 | 0.027466 | -0.022888 | 0.091553 | 0.17853 | 0.09613 | 0.1831 | 120.5795 | -0.1236 | -0.036621 | 120.7626 | 120.639 | 120.6299 | 0.059509 | 0.050354 | 120.5429 | -0.050354 | 0.013733 | 120.7443 | 120.7489 | 120.6619 | 0.20599 | 0.11902 | 0.18311 | 0.027466 | 0.20142 | 0.11444 | -0.059509 | 0.050354 | 120.52 | 120.5933 | -0.064087 | -0.10071 | 120.607 | 120.6573 | 120.5795 | 120.6711
3109.5469 | 120.8084 | -120.6436 | 0.082397 | 0.036468 | 0.016923 | -0.035218 | 0.037121 | -0.019549 | -0.02989 | -0.018547 | 0.014709 | -0.063788 | -0.00032465 | 0.037675 | -0.019649 | -0.011595 | -0.012469 | -0.054932 | -0.004578 | -0.045776 | -0.068665 | 0.059509 | -0.004578 | -0.004578 | -0.054932 | 0.064087 | -0.064087 | -0.004578 | 0.086975 | 0.004578 | 0.14648 | 120.5978 | -0.086975 | -0.15106 | 120.7031 | 120.639 | 120.639 | 0.041198 | 0.041198 | 120.5795 | -0.01831 | -0.086975 | 120.7306 | 120.7901 | 120.6482 | 0.21057 | 0.068665 | 0.10528 | -0.022889 | 0.15106 | 0.059509 | 0.041198 | 0.12817 | 120.639 | 120.7077 | -0.12817 | -0.14648 | 120.575 | 120.639 | 120.5887 | 120.5887
3111.2812 | 115.5579 | -77.8152 | 37.587 | 0.036468 | 0.012864 | -0.036713 | 0.036267 | -0.01549 | -0.028822 | -0.022178 | 0.011658 | -0.063574 | -0.00075185 | 0.039597 | -0.015163 | -0.011595 | -0.011615 | -0.064087 | -0.022888 | -0.041199 | -0.064087 | 0.059509 | -0.054932 | -0.036621 | -0.036621 | -0.018311 | -0.082397 | 0.022888 | 0.091553 | 0.013733 | 0.13733 | 77.774 | -37.6099 | -37.6511 | 77.8748 | 77.7786 | 77.7603 | 0.004578 | -0.013733 | 77.7328 | -37.6053 | -37.5641 | 77.9068 | 77.9526 | 77.829 | 0.21973 | 0.09613 | 0.10071 | -0.022888 | 0.17395 | 0.10528 | 0.018311 | 0.064086 | 77.7924 | 77.7969 | -37.6282 | -37.6694 | 77.7512 | 77.8381 | 77.7512 | 77.7786
3113.0781 | 120.6299 | -120.2728 | 0.082397 | 0.01358 | 0.013933 | -0.032441 | 0.03648 | -0.01848 | -0.02989 | -0.019401 | 0.008606 | -0.06272 | -0.00075185 | 0.034897 | -0.019649 | -0.010527 | -0.01076 | -0.013733 | -0.059509 | 0.009155 | 0.050354 | 0.17395 | 0.086975 | 0.073242 | 0.073242 | 0.022888 | -0.022888 | 0.07782 | 0.16937 | 0.091553 | 0.17395 | 120.282 | -0.14191 | -0.032043 | 120.4468 | 120.3461 | 120.3598 | 0.064087 | 0.07782 | 120.2499 | -0.059509 | -0.004577 | 120.4422 | 120.4468 | 120.3644 | 0.19684 | 0.11444 | 0.16479 | 0.041199 | 0.19226 | 0.10071 | -0.068664 | 0.045776 | 120.2133 | 120.2957 | -0.073242 | -0.10528 | 120.3232 | 120.3506 | 120.2591 | 120.3461
3114.8125 | 120.726 | -120.4056 | 0.073242 | 0.028839 | 0.012651 | -0.033722 | 0.035626 | -0.016558 | -0.026899 | -0.022392 | 0.011658 | -0.06272 | -0.00096545 | 0.042374 | -0.015804 | -0.0094592 | -0.01311 | -0.004578 | -0.041199 | 0 | 0.041199 | 0.1831 | 0.045776 | 0.068665 | 0.082397 | 0.032043 | -0.041199 | 0.068665 | 0.13275 | 0.059509 | 0.16479 | 120.4056 | -0.11444 | -0.032043 | 120.5887 | 120.4742 | 120.4514 | 0.068665 | 0.045776 | 120.3644 | -0.041199 | -0.004577 | 120.5383 | 120.5704 | 120.4651 | 0.20599 | 0.10071 | 0.1831 | 0.041199 | 0.17395 | 0.10986 | -0.041199 | 0.073242 | 120.3644 | 120.4376 | -0.073242 | -0.11444 | 120.4468 | 120.4742 | 120.401 | 120.488
3116.5938 | 120.7626 | -120.488 | 0.041199 | 0.028839 | 0.01671 | -0.033936 | 0.037335 | -0.019121 | -0.026045 | -0.021324 | 0.017761 | -0.06272 | 0.001598 | 0.037461 | -0.016872 | -0.0101 | -0.013751 | -0.018311 | -0.036621 | -0.004578 | 0.027466 | 0.1831 | 0.050354 | 0.07782 | 0.07782 | 0.022888 | -0.032043 | 0.073242 | 0.13733 | 0.07782 | 0.16479 | 120.4834 | -0.07782 | -0.013733 | 120.6711 | 120.5658 | 120.5383 | 0.082398 | 0.054932 | 120.4559 | -0.018311 | 0.032043 | 120.6253 | 120.6528 | 120.5658 | 0.19684 | 0.10986 | 0.18768 | 0.032044 | 0.16937 | 0.10529 | -0.032043 | 0.054931 | 120.4514 | 120.5109 | -0.045777 | -0.073242 | 120.5154 | 120.5612 | 120.4697 | 120.5658
3118.3906 | 120.7993 | -120.5566 | 0.082397 | 0.0059509 | 0.015641 | -0.034577 | 0.034985 | -0.014849 | -0.028822 | -0.023887 | 0.008606 | -0.06272 | -0.0022472 | 0.033188 | -0.018367 | -0.0088184 | -0.013965 | -0.009155 | -0.054932 | 0.004578 | 0.036621 | 0.1831 | 0.073242 | 0.064087 | 0.064087 | 0.027466 | -0.018311 | 0.064087 | 0.15564 | 0.073242 | 0.16479 | 120.5612 | -0.13733 | -0.045776 | 120.7397 | 120.6207 | 120.6299 | 0.059509 | 0.068664 | 120.5383 | -0.054931 | -0.01831 | 120.7123 | 120.7214 | 120.6299 | 0.18311 | 0.091553 | 0.17853 | 0.032043 | 0.17395 | 0.082398 | -0.05951 | 0.045777 | 120.5017 | 120.5841 | -0.077819 | -0.10071 | 120.5933 | 120.6207 | 120.5475 | 120.6207
3120.1875 | 120.8771 | -120.5612 | 0.059509 | 0.01358 | 0.013292 | -0.033082 | 0.036908 | -0.016344 | -0.030104 | -0.026451 | 0.0025024 | -0.063574 | -0.0013928 | 0.034897 | -0.014736 | -0.0096728 | -0.012042 | 0.013733 | -0.054932 | -0.009155 | 0.041199 | 0.16937 | 0.064087 | 0.050354 | 0.09613 | 0.027466 | -0.032043 | 0.1236 | 0.19226 | 0.086975 | 0.21515 | 120.5521 | -0.11444 | -0.01831 | 120.7306 | 120.6116 | 120.6253 | 0.059509 | 0.073242 | 120.5292 | -0.032043 | 0.064087 | 120.7535 | 120.7764 | 120.6482 | 0.24719 | 0.11902 | 0.17853 | 0.050354 | 0.2243 | 0.15564 | -0.045777 | 0.059509 | 120.5063 | 120.5887 | -0.068664 | -0.091552 | 120.6024 | 120.6848 | 120.575 | 120.6573
3121.9062 | 120.7718 | -120.6116 | 0.11902 | 0.028839 | 0.013078 | -0.035218 | 0.037121 | -0.016985 | -0.026258 | -0.023033 | 0.014709 | -0.062933 | -0.00011105 | 0.040452 | -0.020076 | -0.009032 | -0.011828 | -0.082397 | 0.013733 | -0.073242 | -0.068665 | 0.045776 | -0.036621 | -0.018311 | -0.073242 | 0.064087 | -0.064087 | -0.013733 | 0.064087 | -0.009155 | 0.10529 | 120.5383 | -0.10529 | -0.18768 | 120.6573 | 120.5933 | 120.575 | 0.054931 | 0.036621 | 120.5475 | -0.054932 | -0.13275 | 120.6757 | 120.7169 | 120.6024 | 0.16937 | 0.054932 | 0.11902 | 0.004577 | 0.12817 | 0.050354 | 0.086975 | 0.12817 | 120.6253 | 120.6757 | -0.19226 | -0.18311 | 120.5429 | 120.5978 | 120.5292 | 120.5383
3123.6875 | 120.7901 | -120.6665 | 0.11902 | 0.01358 | 0.013933 | -0.036072 | 0.037335 | -0.014208 | -0.030958 | -0.022819 | 0.0025024 | -0.063147 | 0.00010255 | 0.038743 | -0.021358 | -0.0098864 | -0.010974 | -0.10529 | -0.018311 | -0.036621 | -0.09613 | 0.045776 | -0.018311 | -0.032043 | -0.064087 | 0.059509 | -0.059509 | -0.032043 | 0.059509 | -0.022888 | 0.091553 | 120.6299 | -0.13733 | -0.21515 | 120.7123 | 120.6345 | 120.6482 | 0.004578 | 0.01831 | 120.607 | -0.05951 | -0.15106 | 120.726 | 120.7581 | 120.6436 | 0.15106 | 0.036621 | 0.082397 | -0.059509 | 0.11902 | 0.027466 | 0.01831 | 0.11902 | 120.6482 | 120.726 | -0.15564 | -0.17853 | 120.5704 | 120.6345 | 120.5612 | 120.6024
3125.4688 | 120.2087 | -119.9615 | 0.068665 | 0.0059509 | 0.014787 | -0.033509 | 0.035412 | -0.017412 | -0.02754 | -0.022392 | 0.0055542 | -0.062933 | -0.0011792 | 0.035752 | -0.019008 | -0.012236 | -0.015674 | -0.032043 | -0.054932 | -0.009155 | -0.004578 | 0.13733 | 0.041199 | 0.022888 | 0 | 0.036621 | -0.041199 | -0.004578 | 0.10071 | 0.032043 | 0.1236 | 119.9524 | -0.1236 | -0.073243 | 120.0989 | 119.9844 | 120.0027 | 0.032043 | 0.050354 | 119.9203 | -0.032044 | -0.073243 | 120.0623 | 120.0851 | 119.9936 | 0.16479 | 0.073242 | 0.14648 | 0.004577 | 0.14191 | 0.036621 | -0.045777 | 0.07782 | 119.9066 | 119.9982 | -0.07782 | -0.10986 | 119.957 | 119.957 | 119.9295 | 119.9615
3127.2656 | 120.575 | -120.3232 | 0.091553 | 0.02121 | 0.015855 | -0.036072 | 0.038189 | -0.017199 | -0.029036 | -0.022819 | 0.008606 | -0.063147 | 0.00010255 | 0.045365 | -0.01324 | -0.0094592 | -0.01546 | -0.018311 | 0.004578 | -0.032043 | -0.018311 | 0.12817 | 0.013733 | 0.004578 | 0.032043 | 0.041199 | -0.027466 | 0.036621 | 0.086975 | 0 | 0.11902 | 120.2911 | -0.086975 | -0.10986 | 120.4514 | 120.3278 | 120.3369 | 0.036621 | 0.045776 | 120.2957 | -0.050354 | -0.054932 | 120.4102 | 120.4422 | 120.3232 | 0.14649 | 0.027466 | 0.16022 | 0.013732 | 0.11444 | 0.064087 | 0.036621 | 0.068665 | 120.3278 | 120.3644 | -0.1236 | -0.11902 | 120.3049 | 120.3598 | 120.3049 | 120.3552
3129.0469 | 120.6757 | -120.4422 | 0.082397 | 0.02121 | 0.014787 | -0.03415 | 0.037549 | -0.017199 | -0.02989 | -0.020469 | 0.017761 | -0.06272 | -0.00053825 | 0.041092 | -0.017726 | -0.0086048 | -0.018023 | -0.036621 | 0 | -0.027466 | -0.022888 | 0.11902 | 0 | -0.004578 | 0.018311 | 0.059509 | -0.045776 | 0.050354 | 0.1236 | 0.022888 | 0.13733 | 120.4147 | -0.082397 | -0.10528 | 120.5612 | 120.4376 | 120.4422 | 0.022888 | 0.027466 | 120.3964 | -0.022888 | -0.032043 | 120.5658 | 120.5795 | 120.4651 | 0.18311 | 0.068664 | 0.14649 | 0.004578 | 0.16937 | 0.09613 | 0.027466 | 0.10528 | 120.4422 | 120.5017 | -0.10986 | -0.12817 | 120.4193 | 120.4926 | 120.4056 | 120.4605
3130.7812 | 120.7993 | -120.488 | 0.054932 | 0.01358 | 0.016069 | -0.033509 | 0.036053 | -0.014422 | -0.028822 | -0.021537 | 0.011658 | -0.061438 | -0.00075185 | 0.044083 | -0.013668 | -0.0077502 | -0.016314 | -0.004578 | -0.068665 | 0.004578 | 0.041199 | 0.19226 | 0.050354 | 0.064087 | 0.086975 | 0.027466 | -0.022888 | 0.11444 | 0.18768 | 0.10071 | 0.21057 | 120.4926 | -0.1236 | -0.013733 | 120.6802 | 120.5521 | 120.5383 | 0.059509 | 0.045776 | 120.4651 | -0.027466 | 0.059509 | 120.6757 | 120.6985 | 120.5887 | 0.23346 | 0.1236 | 0.18768 | 0.036621 | 0.21057 | 0.13733 | -0.073243 | 0.050354 | 120.4193 | 120.5154 | -0.050354 | -0.07782 | 120.5292 | 120.6024 | 120.4834 | 120.575
3132.5781 | 120.7489 | -120.5658 | 0.059509 | 0.01358 | 0.015641 | -0.032654 | 0.037976 | -0.01848 | -0.031172 | -0.021965 | 0.0055542 | -0.063361 | 0.0024524 | 0.038102 | -0.018367 | -0.0075366 | -0.012256 | -0.086975 | -0.018311 | -0.036621 | -0.07782 | 0.041199 | -0.068665 | -0.050354 | -0.027466 | 0.045776 | -0.041199 | 0.022888 | 0.09613 | -0.009155 | 0.13733 | 120.5292 | -0.07782 | -0.13733 | 120.607 | 120.5154 | 120.4971 | -0.013733 | -0.032044 | 120.5246 | -0.013733 | -0.036621 | 120.6619 | 120.7031 | 120.5566 | 0.17853 | 0.032044 | 0.07782 | -0.041199 | 0.13733 | 0.064087 | 0.01831 | 0.086975 | 120.5475 | 120.6116 | -0.09613 | -0.10071 | 120.488 | 120.5887 | 120.4788 | 120.5383
3134.375 | 120.8359 | -120.5658 | 0.059509 | 0.0059509 | 0.014787 | -0.033295 | 0.034131 | -0.018694 | -0.030104 | -0.020042 | 0.0055542 | -0.064642 | -0.00053825 | 0.044083 | -0.02029 | -0.0088184 | -0.011828 | -0.064087 | -0.027466 | -0.009155 | -0.004578 | 0.13275 | 0.050354 | 0.054932 | 0.045776 | 0.018311 | -0.022888 | 0.07782 | 0.17395 | 0.10529 | 0.18768 | 120.5566 | -0.086975 | -0.064087 | 120.6985 | 120.6207 | 120.6162 | 0.064087 | 0.059509 | 120.5429 | -0.041198 | 0.018311 | 120.7397 | 120.7535 | 120.6711 | 0.21057 | 0.12817 | 0.14191 | 0.004577 | 0.19684 | 0.10071 | -0.018311 | 0.041199 | 120.5383 | 120.5841 | -0.068664 | -0.082397 | 120.5612 | 120.6436 | 120.5017 | 120.6116
3136.1719 | 120.8221 | -120.5704 | 0.13733 | 0.0059509 | 0.012864 | -0.033509 | 0.03648 | -0.011858 | -0.02989 | -0.021965 | 0.0055542 | -0.062292 | -0.0011792 | 0.036179 | -0.021144 | -0.0096728 | -0.011615 | -0.004578 | -0.064087 | -0.004578 | 0.027466 | 0.16479 | 0.068665 | 0.059509 | 0.050354 | 0.032043 | -0.013733 | 0.027466 | 0.15106 | 0.054932 | 0.15106 | 120.5658 | -0.20142 | -0.10986 | 120.7352 | 120.6299 | 120.639 | 0.064087 | 0.073243 | 120.5566 | -0.10529 | -0.10986 | 120.7214 | 120.7214 | 120.6253 | 0.16479 | 0.068665 | 0.16937 | 0.032044 | 0.16479 | 0.041199 | -0.059509 | 0.045776 | 120.5063 | 120.6024 | -0.14191 | -0.15106 | 120.5978 | 120.5978 | 120.5658 | 120.6207
3137.875 | 120.7672 | -120.6528 | 0.082397 | 0.028839 | 0.016496 | -0.032227 | 0.037121 | -0.018053 | -0.029036 | -0.02346 | 0.0025024 | -0.06272 | 0.00031615 | 0.040024 | -0.016872 | -0.011382 | -0.013324 | -0.082397 | -0.004578 | -0.041199 | -0.10071 | 0.004578 | -0.086975 | -0.07782 | -0.10986 | 0.064087 | -0.068665 | -0.022888 | 0.027466 | -0.045776 | 0.09613 | 120.6116 | -0.086975 | -0.18311 | 120.6573 | 120.575 | 120.5658 | -0.036621 | -0.045776 | 120.5841 | -0.01831 | -0.10528 | 120.6802 | 120.7489 | 120.607 | 0.16479 | 0.022889 | 0.045777 | -0.059509 | 0.096131 | 0.045777 | 0.036621 | 0.13275 | 120.6482 | 120.7169 | -0.1236 | -0.15106 | 120.5521 | 120.6299 | 120.5704 | 120.5429
3139.6562 | 120.7993 | -120.5658 | 0.16022 | 0.01358 | 0.017778 | -0.03415 | 0.038189 | -0.01549 | -0.031385 | -0.022392 | 0.0025024 | -0.060156 | -0.0022472 | 0.032548 | -0.019649 | -0.010314 | -0.012256 | -0.054932 | -0.027466 | -0.004578 | -0.082397 | 0.050354 | -0.068665 | -0.059509 | -0.059509 | 0.050354 | -0.032043 | -0.013733 | 0.041199 | -0.054932 | 0.086975 | 120.5612 | -0.18768 | -0.24261 | 120.6162 | 120.5063 | 120.4971 | -0.054931 | -0.064087 | 120.5338 | -0.10986 | -0.17395 | 120.607 | 120.6528 | 120.5109 | 0.11902 | -0.022889 | 0.054932 | -0.077819 | 0.073242 | 0.01831 | -0.022888 | 0.082397 | 120.5383 | 120.6162 | -0.16479 | -0.19226 | 120.4834 | 120.5521 | 120.5109 | 120.5063
3141.4531 | 120.8862 | -120.6573 | 0.11902 | 0.036468 | 0.013719 | -0.033722 | 0.03648 | -0.018908 | -0.030745 | -0.02111 | 0.011658 | -0.061011 | -0.00053825 | 0.036179 | -0.018581 | -0.0096728 | -0.014819 | -0.064087 | 0.013733 | -0.045776 | -0.07782 | 0.032043 | -0.013733 | -0.018311 | -0.050354 | 0.068665 | -0.045776 | -0.022888 | 0.07782 | 0.004578 | 0.11902 | 120.6116 | -0.10529 | -0.19684 | 120.6894 | 120.639 | 120.6436 | 0.027465 | 0.032043 | 120.6116 | -0.050354 | -0.14191 | 120.7352 | 120.7764 | 120.6619 | 0.16479 | 0.050354 | 0.077819 | -0.032044 | 0.1236 | 0.022888 | 0.059509 | 0.11444 | 120.6711 | 120.726 | -0.16479 | -0.16479 | 120.5795 | 120.6345 | 120.5933 | 120.607
3143.2344 | 120.845 | -120.7169 | 0.10986 | 0.0059509 | 0.015641 | -0.033722 | 0.036053 | -0.012713 | -0.029249 | -0.023674 | 0.0055542 | -0.061865 | -0.0020336 | 0.03447 | -0.021572 | -0.011382 | -0.01311 | -0.059509 | -0.027466 | -0.022888 | -0.073242 | 0.064087 | 0.009155 | 0.004578 | -0.054932 | 0.050354 | -0.036621 | -0.027466 | 0.068665 | 0 | 0.091553 | 120.694 | -0.13733 | -0.18311 | 120.7809 | 120.7214 | 120.726 | 0.027466 | 0.032043 | 120.6802 | -0.059509 | -0.13733 | 120.7855 | 120.8084 | 120.7169 | 0.12817 | 0.036621 | 0.086975 | -0.050354 | 0.10529 | 0.009155 | -0.004578 | 0.086975 | 120.6894 | 120.7672 | -0.13275 | -0.14648 | 120.6436 | 120.6894 | 120.6573 | 120.6619
3145.0156 | 120.6116 | -120.2774 | 0.050354 | 0.0059509 | 0.013292 | -0.034363 | 0.036267 | -0.021258 | -0.028608 | -0.022819 | 0.011658 | -0.064002 | -0.0011792 | 0.042801 | -0.015804 | -0.0088184 | -0.011615 | -0.045776 | -0.027466 | 0.004578 | 0 | 0.15564 | 0.073242 | 0.073242 | 0.050354 | 0.022888 | -0.036621 | 0.091553 | 0.1831 | 0.13275 | 0.20142 | 120.282 | -0.07782 | -0.050354 | 120.433 | 120.3506 | 120.3506 | 0.068664 | 0.068664 | 120.2408 | -0.027466 | 0.041199 | 120.4605 | 120.4788 | 120.4102 | 0.23804 | 0.16937 | 0.15106 | -0.004578 | 0.21973 | 0.12817 | -0.032044 | 0.059509 | 120.2499 | 120.3003 | -0.045776 | -0.086975 | 120.2774 | 120.369 | 120.2316 | 120.3278
3146.8125 | 120.8084 | -120.5566 | 0.064087 | 0.01358 | 0.013505 | -0.032654 | 0.034985 | -0.018267 | -0.029249 | -0.022605 | 0.008606 | -0.062506 | -0.0039562 | 0.041306 | -0.017085 | -0.0101 | -0.011828 | -0.059509 | -0.041199 | -0.009155 | -0.013733 | 0.11444 | 0.009155 | 0.036621 | 0.004578 | 0.027466 | -0.041199 | 0.045776 | 0.14191 | 0.036621 | 0.15564 | 120.5475 | -0.10529 | -0.07782 | 120.6711 | 120.5933 | 120.5658 | 0.045776 | 0.01831 | 120.5154 | -0.036621 | -0.018311 | 120.6985 | 120.7123 | 120.5933 | 0.19684 | 0.07782 | 0.1236 | -0.004578 | 0.18311 | 0.086975 | -0.032044 | 0.068665 | 120.5154 | 120.5841 | -0.073242 | -0.10529 | 120.5429 | 120.6024 | 120.4971 | 120.5612
3148.5469 | 120.7993 | -120.6573 | 0.082397 | 0.0059509 | 0.013719 | -0.03415 | 0.035626 | -0.016344 | -0.028608 | -0.018974 | 0.0025024 | -0.063147 | -0.0022472 | 0.038956 | -0.021572 | -0.011168 | -0.0092648 | -0.022888 | -0.027466 | -0.018311 | -0.022888 | 0.11444 | 0.032043 | 0.022888 | -0.036621 | 0.045776 | -0.041199 | -0.004578 | 0.073242 | 0.013733 | 0.086975 | 120.639 | -0.10986 | -0.10528 | 120.7718 | 120.6802 | 120.6894 | 0.041199 | 0.050354 | 120.6161 | -0.036621 | -0.086975 | 120.7306 | 120.7443 | 120.6711 | 0.12817 | 0.054932 | 0.13275 | -0.004577 | 0.11444 | 0.036621 | -0.009155 | 0.086975 | 120.6299 | 120.7031 | -0.10071 | -0.1236 | 120.6345 | 120.6528 | 120.6345 | 120.6207
3150.3438 | 120.8633 | -120.6757 | 0.10071 | 0.036468 | 0.013719 | -0.034363 | 0.037121 | -0.016985 | -0.030104 | -0.021751 | 0.011658 | -0.060156 | -0.004597 | 0.02678 | -0.01794 | -0.012023 | -0.01076 | -0.064087 | -0.013733 | -0.032043 | -0.054932 | 0.059509 | 0.009155 | 0.004578 | -0.054932 | 0.073242 | -0.050354 | 0.013733 | 0.10071 | 0.004578 | 0.13275 | 120.6436 | -0.11444 | -0.15564 | 120.7352 | 120.6802 | 120.6848 | 0.036621 | 0.041198 | 120.6253 | -0.027466 | -0.086975 | 120.7764 | 120.8084 | 120.6802 | 0.18311 | 0.054932 | 0.091552 | -0.022889 | 0.15106 | 0.064087 | 0.01831 | 0.1236 | 120.6619 | 120.7489 | -0.13275 | -0.15106 | 120.6207 | 120.6894 | 120.6116 | 120.6207
3152.125 | 120.8588 | -120.7169 | 0.10529 | 0.01358 | 0.015214 | -0.033509 | 0.038403 | -0.012926 | -0.027113 | -0.020256 | 0.0025024 | -0.06037 | 0.00095715 | 0.035111 | -0.016658 | -0.009032 | -0.011401 | -0.068665 | -0.022888 | -0.027466 | -0.10071 | 0.004578 | -0.07782 | -0.059509 | -0.059509 | 0.064087 | -0.045776 | -0.004578 | 0.036621 | -0.041199 | 0.10986 | 120.6894 | -0.12817 | -0.20599 | 120.7214 | 120.6573 | 120.639 | -0.032043 | -0.050354 | 120.6711 | -0.041199 | -0.10986 | 120.7535 | 120.8267 | 120.6757 | 0.15564 | 0.004577 | 0.032044 | -0.073242 | 0.082397 | 0.041198 | 0.004578 | 0.10986 | 120.694 | 120.7809 | -0.13275 | -0.15106 | 120.6162 | 120.7123 | 120.6482 | 120.6573
3153.8438 | 120.8633 | -120.7077 | 0.086975 | 0.0059509 | 0.014573 | -0.034363 | 0.036694 | -0.017626 | -0.030317 | -0.020683 | 0.0055542 | -0.061865 | -0.0020336 | 0.039384 | -0.016017 | -0.0096728 | -0.012469 | -0.064087 | -0.018311 | -0.022888 | -0.10529 | 0.018311 | -0.07782 | -0.050354 | -0.082397 | 0.050354 | -0.059509 | 0 | 0.054932 | -0.054932 | 0.12817 | 120.6848 | -0.10529 | -0.19226 | 120.726 | 120.6573 | 120.6299 | -0.027466 | -0.054932 | 120.6482 | -0.036621 | -0.086975 | 120.7626 | 120.8359 | 120.6528 | 0.18768 | 0.004577 | 0.041199 | -0.082398 | 0.11444 | 0.059509 | 0.004577 | 0.10986 | 120.6894 | 120.7581 | -0.10986 | -0.14648 | 120.6024 | 120.7077 | 120.6436 | 120.6253
3155.625 | 121.0098 | -120.7535 | 0.064087 | 0.01358 | 0.013292 | -0.03415 | 0.035412 | -0.018053 | -0.026899 | -0.024314 | 0.008606 | -0.06507 | -0.00182 | 0.040879 | -0.019649 | -0.0094592 | -0.014392 | -0.045776 | -0.041199 | 0 | 0 | 0.13733 | 0.050354 | 0.064087 | 0.032043 | 0.022888 | -0.022888 | 0.073242 | 0.17395 | 0.11444 | 0.20142 | 120.7535 | -0.10529 | -0.064087 | 120.8908 | 120.8176 | 120.8038 | 0.064087 | 0.050354 | 120.7306 | -0.041199 | 0.009155 | 120.9274 | 120.9549 | 120.8679 | 0.2243 | 0.13733 | 0.13733 | 0 | 0.19684 | 0.09613 | -0.041199 | 0.045776 | 120.7123 | 120.7764 | -0.064087 | -0.086975 | 120.7535 | 120.8267 | 120.7077 | 120.7855
3157.4375 | 120.9183 | -120.7764 | 0.091553 | 0.01358 | 0.015428 | -0.032868 | 0.038189 | -0.016344 | -0.028181 | -0.021537 | 0.0055542 | -0.06272 | 0.00031615 | 0.042374 | -0.017726 | -0.009032 | -0.010333 | -0.073242 | -0.013733 | -0.045776 | -0.10986 | 0.009155 | -0.082397 | -0.059509 | -0.059509 | 0.045776 | -0.041199 | -0.009155 | 0.045776 | -0.045776 | 0.11444 | 120.7306 | -0.10529 | -0.20142 | 120.7855 | 120.7169 | 120.694 | -0.013733 | -0.036621 | 120.7352 | -0.045777 | -0.10071 | 120.8221 | 120.8908 | 120.7306 | 0.15564 | -0.004577 | 0.054931 | -0.064087 | 0.086975 | 0.032044 | 0.032043 | 0.086975 | 120.7626 | 120.8221 | -0.13733 | -0.13275 | 120.6665 | 120.7672 | 120.7031 | 120.7169
3159.1719 | 120.9183 | -120.6207 | 0.27466 | 0.0059509 | 0.014573 | -0.033936 | 0.037335 | -0.018053 | -0.029036 | -0.020897 | 0.0025024 | -0.062079 | -0.00011105 | 0.041092 | -0.018794 | -0.0086048 | -0.010333 | -0.091553 | 0 | -0.036621 | -0.10529 | 0.027466 | -0.059509 | -0.059509 | -0.054932 | 0.054932 | -0.045776 | -0.004578 | 0.054932 | -0.022888 | 0.1236 | 120.5841 | -0.27466 | -0.37994 | 120.6482 | 120.5612 | 120.5612 | -0.022888 | -0.022888 | 120.575 | -0.21973 | -0.27924 | 120.6757 | 120.7443 | 120.5978 | 0.16937 | 0.022888 | 0.064087 | -0.068665 | 0.10071 | 0.041198 | 0.036621 | 0.10071 | 120.6207 | 120.6757 | -0.31128 | -0.32043 | 120.5154 | 120.6162 | 120.5292 | 120.5658
3160.9531 | 121.138 | -120.7581 | 0.064087 | 0.01358 | 0.01201 | -0.035004 | 0.033276 | -0.01784 | -0.02989 | -0.021537 | 0.0055542 | -0.063788 | -0.00032465 | 0.03682 | -0.018581 | -0.010527 | -0.014392 | -0.018311 | -0.041199 | -0.013733 | 0.041199 | 0.20599 | 0.091553 | 0.10986 | 0.11902 | 0.013733 | -0.022888 | 0.11444 | 0.21973 | 0.12817 | 0.20599 | 120.7443 | -0.10529 | -0.022888 | 120.9641 | 120.8679 | 120.8496 | 0.1236 | 0.10529 | 120.7352 | -0.050354 | 0.050354 | 120.9778 | 120.9641 | 120.8862 | 0.22888 | 0.15106 | 0.21973 | 0.054932 | 0.24261 | 0.13733 | -0.027466 | 0.036621 | 120.7169 | 120.7718 | -0.07782 | -0.086975 | 120.7993 | 120.8725 | 120.7397 | 120.8771
3162.6875 | 120.9229 | -120.6619 | 0.21515 | 0.01358 | 0.015641 | -0.032654 | 0.036267 | -0.016131 | -0.02989 | -0.022178 | 0.008606 | -0.062292 | 0.00074335 | 0.03682 | -0.019649 | -0.0098864 | -0.015033 | -0.013733 | -0.022888 | -0.036621 | -0.036621 | 0.10071 | 0 | 0.009155 | 0.032043 | 0.054932 | -0.032043 | 0.022888 | 0.12817 | 0.022888 | 0.14191 | 120.6253 | -0.23804 | -0.25177 | 120.7626 | 120.6711 | 120.6619 | 0.045776 | 0.036621 | 120.6299 | -0.16022 | -0.19226 | 120.7901 | 120.8038 | 120.6848 | 0.17395 | 0.054931 | 0.13733 | 0 | 0.16022 | 0.054931 | 0.013733 | 0.086975 | 120.639 | 120.7169 | -0.25177 | -0.24719 | 120.6253 | 120.6848 | 120.6482 | 120.694
3164.4844 | 121.0648 | -120.7031 | 0.073242 | 0.036468 | 0.012437 | -0.033722 | 0.037335 | -0.01314 | -0.029676 | -0.019188 | 0.008606 | -0.064002 | -0.0026744 | 0.033188 | -0.01794 | -0.0098864 | -0.015033 | -0.027466 | -0.027466 | 0.018311 | -0.009155 | 0.12817 | 0.013733 | 0.022888 | 0.027466 | 0.022888 | -0.018311 | 0.041199 | 0.13733 | 0.050354 | 0.16479 | 120.7214 | -0.10071 | -0.082397 | 120.8313 | 120.726 | 120.7169 | 0.004577 | -0.004578 | 120.6848 | -0.050354 | -0.032043 | 120.8405 | 120.8679 | 120.7535 | 0.18311 | 0.068665 | 0.10986 | -0.027466 | 0.15564 | 0.05951 | -0.045777 | 0.041199 | 120.6757 | 120.726 | -0.054931 | -0.091553 | 120.694 | 120.7443 | 120.6757 | 120.7306
3166.2188 | 121.0144 | -120.8542 | 0.10529 | 0.02121 | 0.017778 | -0.035218 | 0.035412 | -0.020189 | -0.029036 | -0.022605 | 0.0055542 | -0.061224 | -0.00096545 | 0.037247 | -0.020931 | -0.012236 | -0.013965 | -0.09613 | -0.018311 | -0.036621 | -0.086975 | 0.036621 | -0.032043 | -0.004578 | -0.068665 | 0.045776 | -0.036621 | -0.045776 | 0.059509 | -0.022888 | 0.09613 | 120.8176 | -0.1236 | -0.19226 | 120.8908 | 120.8496 | 120.8221 | 0.032043 | 0.004578 | 120.8176 | -0.05951 | -0.15106 | 120.9137 | 120.9503 | 120.8313 | 0.13275 | 0.013733 | 0.073242 | -0.050354 | 0.09613 | -0.009155 | 0.01831 | 0.082397 | 120.8359 | 120.9 | -0.14191 | -0.14191 | 120.7672 | 120.8084 | 120.7581 | 120.7855
3168.0156 | 120.8725 | -120.0211 | 0.073242 | 0.01358 | 0.012224 | -0.035218 | 0.034985 | -0.021258 | -0.029036 | -0.022605 | 0.011658 | -0.045416 | -0.0041698 | 0.038956 | -0.014949 | 0.020234 | -0.0094784 | -0.041199 | -0.022888 | 0.80109 | -0.018311 | 0.11444 | 0.036621 | 0.009155 | 0.004578 | 0.018311 | 1.2543 | 0.059509 | 0.16022 | 0.073242 | 0.16937 | 120.8221 | -0.09613 | -0.091553 | 120.1355 | 120.0302 | 120.0577 | -0.79193 | -0.76446 | 121.2753 | -0.054931 | -0.013733 | 120.1813 | 120.1904 | 120.0943 | -1.0849 | -1.181 | -0.68664 | -0.8194 | -1.0941 | -1.1948 | -0.82397 | -1.236 | 119.9982 | 120.0394 | 0.72784 | 1.181 | 120.0027 | 120.0806 | 119.9799 | 120.0256
3169.7344 | 121.0281 | -120.6894 | 0.054932 | 0.0059509 | 0.012224 | -0.033509 | 0.03584 | -0.016558 | -0.030104 | -0.023246 | 0.011658 | -0.063574 | -0.003529 | 0.040452 | -0.01794 | -0.010955 | -0.008624 | -0.009155 | -0.068665 | 0.022888 | 0.045776 | 0.20599 | 0.10071 | 0.10529 | 0.10071 | 0.022888 | -0.013733 | 0.10986 | 0.21973 | 0.14191 | 0.21515 | 120.7123 | -0.1236 | -0.009156 | 120.8954 | 120.7947 | 120.7901 | 0.082398 | 0.07782 | 120.6757 | -0.032044 | 0.054931 | 120.9091 | 120.9045 | 120.8313 | 0.22888 | 0.15564 | 0.18311 | 0.022888 | 0.23346 | 0.1236 | -0.091553 | 0.036621 | 120.6207 | 120.7123 | -0.032044 | -0.068665 | 120.7352 | 120.7993 | 120.6802 | 120.7901
3171.5312 | 121.0281 | -120.7764 | 0.059509 | 0.036468 | 0.015214 | -0.033509 | 0.038189 | -0.01848 | -0.029036 | -0.019615 | 0.008606 | -0.062079 | -0.00053825 | 0.042374 | -0.014522 | -0.0101 | -0.010119 | 0.004578 | -0.045776 | 0.009155 | 0.059509 | 0.1831 | 0.068665 | 0.068665 | 0.10986 | 0.022888 | -0.022888 | 0.10071 | 0.16479 | 0.082397 | 0.19684 | 120.7855 | -0.10528 | 0 | 120.9595 | 120.845 | 120.845 | 0.05951 | 0.05951 | 120.7535 | -0.036621 | 0.041199 | 120.9412 | 120.9732 | 120.8588 | 0.21973 | 0.10528 | 0.17395 | 0.050354 | 0.18768 | 0.1236 | -0.054931 | 0.045776 | 120.7306 | 120.7993 | -0.050354 | -0.082397 | 120.8359 | 120.8771 | 120.7809 | 120.8862
3173.3281 | 121.0236 | -120.7947 | 0.082397 | 0.02121 | 0.012864 | -0.033082 | 0.032849 | -0.012713 | -0.031813 | -0.021965 | 0.008606 | -0.064215 | -0.00182 | 0.037675 | -0.018367 | -0.010314 | -0.011615 | -0.054932 | -0.050354 | -0.004578 | -0.027466 | 0.10986 | 0.013733 | 0.018311 | 0 | 0.009155 | -0.004578 | 0.045776 | 0.14191 | 0.059509 | 0.16937 | 120.7901 | -0.13275 | -0.10986 | 120.9045 | 120.813 | 120.8084 | 0.022889 | 0.018311 | 120.7901 | -0.073242 | -0.036621 | 120.9366 | 120.9641 | 120.8542 | 0.17395 | 0.064087 | 0.11444 | -0.022888 | 0.14649 | 0.050354 | -0.045776 | 0.013733 | 120.7443 | 120.8038 | -0.086975 | -0.086975 | 120.7672 | 120.8405 | 120.7397 | 120.7947
3175.125 | 121.1151 | -120.7855 | 0.064087 | 0.01358 | 0.013078 | -0.033509 | 0.035626 | -0.01848 | -0.028822 | -0.02346 | 0.0025024 | -0.063574 | -0.004597 | 0.036606 | -0.018154 | -0.009032 | -0.014392 | 0 | -0.054932 | 0.018311 | 0.064087 | 0.21973 | 0.11444 | 0.11444 | 0.10529 | 0.013733 | 0.004578 | 0.086975 | 0.21515 | 0.13275 | 0.19684 | 120.8038 | -0.11902 | 0 | 121.0052 | 120.9 | 120.9 | 0.09613 | 0.09613 | 120.7901 | -0.050354 | 0.022888 | 121.0007 | 120.9824 | 120.9183 | 0.19226 | 0.12817 | 0.20142 | 0.045776 | 0.21057 | 0.082397 | -0.073243 | 0.009155 | 120.7306 | 120.7993 | -0.045776 | -0.059509 | 120.8496 | 120.8725 | 120.7855 | 120.8908
3176.9531 | 121.1426 | -120.8405 | 0.068665 | 0.01358 | 0.015428 | -0.034363 | 0.035626 | -0.018267 | -0.025618 | -0.020897 | 0.011658 | -0.062292 | -0.0011792 | 0.039811 | -0.014736 | -0.010741 | -0.011615 | 0.022888 | -0.054932 | 0.004578 | 0.068665 | 0.1831 | 0.059509 | 0.07782 | 0.10986 | 0.009155 | -0.013733 | 0.10071 | 0.1831 | 0.10986 | 0.20599 | 120.845 | -0.1236 | 0 | 121.0236 | 120.9183 | 120.9 | 0.073242 | 0.054931 | 120.8267 | -0.05951 | 0.032043 | 121.0236 | 121.0464 | 120.9503 | 0.21973 | 0.1236 | 0.17853 | 0.064087 | 0.19684 | 0.11444 | -0.05951 | 0.022888 | 120.7855 | 120.8496 | -0.064087 | -0.082398 | 120.9091 | 120.9412 | 120.8633 | 120.9503
3178.6875 | 121.0739 | -120.8817 | 0.064087 | 0.036468 | 0.013933 | -0.032654 | 0.03648 | -0.014422 | -0.028822 | -0.020683 | 0.008606 | -0.065924 | -0.0011792 | 0.039811 | -0.016872 | -0.009032 | -0.01546 | -0.041199 | -0.041199 | 0.009155 | 0 | 0.11902 | 0.018311 | 0.036621 | 0.018311 | 0.041199 | -0.018311 | 0.050354 | 0.1236 | 0.045776 | 0.15564 | 120.8908 | -0.10529 | -0.064087 | 121.0007 | 120.9183 | 120.9 | 0.027466 | 0.009156 | 120.8633 | -0.022888 | -0.013733 | 121.0052 | 121.0373 | 120.9274 | 0.17395 | 0.064087 | 0.10986 | -0.009155 | 0.14191 | 0.068665 | -0.050354 | 0.05951 | 120.8405 | 120.9229 | -0.054932 | -0.082398 | 120.8817 | 120.932 | 120.8405 | 120.9
3180.4219 | 121.138 | -120.8633 | 0.073242 | 0.0059509 | 0.013505 | -0.033509 | 0.037121 | -0.014422 | -0.029249 | -0.025596 | 0.0055542 | -0.062079 | -0.00011105 | 0.040452 | -0.018581 | -0.0101 | -0.013324 | -0.041199 | -0.022888 | -0.009155 | -0.013733 | 0.09613 | 0.022888 | 0.027466 | 0.013733 | 0.022888 | -0.041199 | 0.050354 | 0.14191 | 0.050354 | 0.16937 | 120.8542 | -0.09613 | -0.086975 | 120.9595 | 120.8908 | 120.8862 | 0.036621 | 0.032043 | 120.8221 | -0.050354 | -0.022888 | 121.0052 | 121.0327 | 120.9137 | 0.21057 | 0.091553 | 0.10528 | -0.004578 | 0.18311 | 0.091553 | -0.013733 | 0.064087 | 120.8405 | 120.8862 | -0.082397 | -0.11444 | 120.8496 | 120.9137 | 120.8221 | 120.8771
3182.1562 | 121.1884 | -120.8908 | 0.082397 | 0.01358 | 0.013719 | -0.032868 | 0.03648 | -0.018267 | -0.028822 | -0.022392 | 0.0055542 | -0.062933 | -0.00075185 | 0.042588 | -0.018581 | -0.010314 | -0.011187 | 0 | -0.045776 | 0.004578 | 0.068665 | 0.2243 | 0.1236 | 0.09613 | 0.10529 | 0.009155 | -0.022888 | 0.091553 | 0.21973 | 0.14648 | 0.20142 | 120.8954 | -0.12817 | -0.013732 | 121.1151 | 120.9869 | 121.0144 | 0.091552 | 0.11902 | 120.8679 | -0.073242 | 0.009156 | 121.1105 | 121.0922 | 121.0373 | 0.2243 | 0.16937 | 0.21973 | 0.064087 | 0.24261 | 0.11444 | -0.050354 | 0.032043 | 120.845 | 120.9 | -0.077819 | -0.10528 | 120.9595 | 120.9824 | 120.8908 | 120.9961
3183.9531 | 121.2387 | -120.8908 | 0.059509 | 0.01358 | 0.013078 | -0.03415 | 0.034985 | -0.019549 | -0.027754 | -0.023246 | 0.0055542 | -0.063574 | -0.0011792 | 0.045579 | -0.016872 | -0.011809 | -0.016528 | -0.018311 | -0.045776 | -0.009155 | 0.050354 | 0.1831 | 0.082397 | 0.091553 | 0.10529 | 0.018311 | -0.009155 | 0.10071 | 0.20142 | 0.14191 | 0.21515 | 120.8817 | -0.10528 | -0.009155 | 121.0739 | 120.9824 | 120.9732 | 0.10071 | 0.091552 | 120.8817 | -0.041198 | 0.041199 | 121.0922 | 121.106 | 121.0327 | 0.2243 | 0.15106 | 0.19226 | 0.059509 | 0.21057 | 0.10986 | -0.036621 | 0.027466 | 120.845 | 120.9091 | -0.068664 | -0.068664 | 120.9412 | 120.9915 | 120.8725 | 120.9961
3185.6719 | 121.1563 | -120.9091 | 0.054932 | 0.028839 | 0.012437 | -0.032654 | 0.03648 | -0.016558 | -0.030317 | -0.024314 | 0.011658 | -0.062506 | 0.0013844 | 0.040024 | -0.016658 | -0.0092456 | -0.014819 | -0.045776 | -0.045776 | 0.004578 | -0.018311 | 0.10986 | 0.018311 | 0.032043 | 0.013733 | 0.032043 | -0.036621 | 0.032043 | 0.12817 | 0.045776 | 0.15564 | 120.9137 | -0.10071 | -0.073243 | 121.019 | 120.9412 | 120.9274 | 0.027465 | 0.013733 | 120.8725 | -0.022889 | -0.022889 | 121.0373 | 121.0648 | 120.9549 | 0.19226 | 0.082397 | 0.10529 | -0.022889 | 0.1648 | 0.068664 | -0.050354 | 0.068664 | 120.8633 | 120.9412 | -0.050354 | -0.091553 | 120.8908 | 120.9412 | 120.8633 | 120.9229
3187.4531 | 121.2296 | -120.8954 | 0.054932 | 0.01358 | 0.013933 | -0.033082 | 0.036694 | -0.016131 | -0.027327 | -0.020683 | 0.0025024 | -0.062933 | -0.0013928 | 0.042801 | -0.013881 | -0.010741 | -0.015033 | -0.004578 | -0.041199 | 0 | 0.041199 | 0.16022 | 0.054932 | 0.045776 | 0.086975 | 0.013733 | -0.018311 | 0.10986 | 0.17395 | 0.082397 | 0.21515 | 120.8954 | -0.096131 | -0.013733 | 121.0556 | 120.9412 | 120.9503 | 0.045776 | 0.054932 | 120.8771 | -0.041199 | 0.054931 | 121.0693 | 121.1105 | 120.9778 | 0.23346 | 0.10071 | 0.16022 | 0.041199 | 0.19226 | 0.12817 | -0.041199 | 0.032044 | 120.8542 | 120.9091 | -0.054932 | -0.073243 | 120.9366 | 121.0052 | 120.8908 | 120.9824
3189.1562 | 121.2524 | -120.9366 | 0.050354 | 0.02121 | 0.013292 | -0.031159 | 0.03648 | -0.0099357 | -0.030531 | -0.018974 | 0.011658 | -0.06272 | 0.001598 | 0.038956 | -0.015804 | -0.0096728 | -0.01076 | -0.009155 | -0.036621 | -0.009155 | 0.041199 | 0.19684 | 0.068665 | 0.068665 | 0.091553 | 0.022888 | -0.027466 | 0.082397 | 0.15106 | 0.086975 | 0.17853 | 120.9274 | -0.086975 | -0.009155 | 121.1334 | 121.0052 | 121.0052 | 0.07782 | 0.07782 | 120.9091 | -0.027466 | 0.032043 | 121.0876 | 121.1151 | 121.0236 | 0.20599 | 0.11444 | 0.20599 | 0.050354 | 0.17853 | 0.10986 | -0.027466 | 0.050354 | 120.9 | 120.9595 | -0.059509 | -0.07782 | 120.9778 | 121.019 | 120.9274 | 121.0281
3190.875 | 121.0922 | -120.9915 | 0.07782 | 0.0059509 | 0.015428 | -0.033722 | 0.038403 | -0.016344 | -0.028181 | -0.022392 | 0.0055542 | -0.060797 | -0.0013928 | 0.034043 | -0.017299 | -0.0092456 | -0.016101 | -0.059509 | 0.009155 | -0.018311 | -0.073242 | 0.032043 | -0.073242 | -0.059509 | -0.10071 | 0.064087 | -0.036621 | -0.036621 | 0.036621 | -0.059509 | 0.10071 | 120.9732 | -0.068665 | -0.15106 | 121.0236 | 120.932 | 120.9183 | -0.041198 | -0.054931 | 120.9549 | -0.013733 | -0.11444 | 121.0281 | 121.0922 | 120.932 | 0.13733 | -0.022888 | 0.050354 | -0.054931 | 0.073242 | 0 | 0.027466 | 0.10071 | 121.0007 | 121.0556 | -0.096131 | -0.11444 | 120.9183 | 120.9549 | 120.932 | 120.8908
3192.5938 | 121.1746 | -121.0052 | 0.10986 | 0.028839 | 0.015641 | -0.032868 | 0.035199 | -0.019976 | -0.028395 | -0.020683 | 0.014709 | -0.060797 | 0.00010255 | 0.029343 | -0.019863 | -0.011595 | -0.01546 | -0.07782 | 0.018311 | -0.041199 | -0.073242 | 0.036621 | -0.027466 | -0.013733 | -0.068665 | 0.054932 | -0.064087 | -0.032043 | 0.064087 | -0.041199 | 0.10529 | 120.9641 | -0.091552 | -0.18311 | 121.0419 | 120.9915 | 120.9778 | 0.027466 | 0.013733 | 120.9412 | -0.054931 | -0.14191 | 121.0693 | 121.1105 | 120.9641 | 0.16937 | 0.022888 | 0.07782 | -0.032043 | 0.12817 | 0.032044 | 0.05951 | 0.11902 | 121.0236 | 121.0602 | -0.15106 | -0.17395 | 120.932 | 120.9732 | 120.9274 | 120.9366
3194.3281 | 121.2662 | -120.9686 | 0.086975 | 0.02121 | 0.011796 | -0.032013 | 0.03584 | -0.013353 | -0.02754 | -0.020683 | 0.0055542 | -0.064856 | 0.0011708 | 0.037675 | -0.018794 | -0.0094592 | -0.012896 | -0.054932 | -0.032043 | -0.018311 | -0.022888 | 0.11902 | 0.004578 | 0.036621 | 0 | 0.018311 | -0.027466 | 0.041199 | 0.15106 | 0.068665 | 0.16937 | 120.9503 | -0.11902 | -0.10986 | 121.0876 | 121.0052 | 120.9732 | 0.054932 | 0.022889 | 120.9412 | -0.068664 | -0.045776 | 121.1197 | 121.138 | 121.0373 | 0.19684 | 0.096131 | 0.13733 | -0.004577 | 0.17853 | 0.068665 | -0.013732 | 0.045777 | 120.9366 | 120.9869 | -0.10529 | -0.11444 | 120.9457 | 121.0098 | 120.9137 | 120.9686
3196.0469 | 121.1792 | -120.9732 | 0.13733 | 0.01358 | 0.016282 | -0.032013 | 0.039471 | -0.01314 | -0.029036 | -0.023246 | 0.008606 | -0.061651 | -0.0016064 | 0.034257 | -0.017726 | -0.011809 | -0.013324 | -0.018311 | -0.009155 | 0.004578 | -0.004578 | 0.11902 | 0.018311 | 0.009155 | 0.032043 | 0.045776 | -0.022888 | 0.036621 | 0.10986 | 0.027466 | 0.13733 | 120.9778 | -0.14648 | -0.14191 | 121.0922 | 120.9824 | 120.9915 | 0.004577 | 0.013733 | 120.9503 | -0.091553 | -0.10071 | 121.0831 | 121.1105 | 121.0007 | 0.16022 | 0.050354 | 0.11444 | -0.009156 | 0.13275 | 0.059509 | -0.013733 | 0.068664 | 120.9641 | 121.019 | -0.13275 | -0.16022 | 120.9686 | 121.0098 | 120.9549 | 121.0052
3197.75 | 121.225 | -121.0236 | 0.073242 | 0.01358 | 0.015641 | -0.032654 | 0.03584 | -0.014208 | -0.029676 | -0.017906 | 0.0055542 | -0.062079 | 0.0018116 | 0.039811 | -0.017726 | -0.010741 | -0.014178 | -0.032043 | 0.009155 | -0.018311 | -0.036621 | 0.09613 | -0.013733 | -0.018311 | -0.018311 | 0.054932 | -0.041199 | 0.004578 | 0.086975 | -0.022888 | 0.11444 | 121.0052 | -0.064087 | -0.10986 | 121.1197 | 121.0052 | 121.0098 | 0 | 0.004578 | 120.9824 | -0.01831 | -0.068664 | 121.1105 | 121.138 | 121.0007 | 0.15564 | 0.018311 | 0.11444 | -0.01831 | 0.12817 | 0.045777 | 0.027466 | 0.096131 | 121.0327 | 121.0785 | -0.091553 | -0.11444 | 120.9869 | 121.0281 | 120.9915 | 121.0052
3199.4688 | 121.225 | -121.0098 | 0.059509 | 0.02121 | 0.012437 | -0.032868 | 0.034985 | -0.017626 | -0.02754 | -0.021537 | 0.008606 | -0.066138 | -0.00011105 | 0.049424 | -0.01794 | -0.0094592 | -0.009692 | -0.064087 | -0.027466 | 0.009155 | 0.004578 | 0.13733 | 0.022888 | 0.032043 | -0.009155 | 0.027466 | -0.022888 | 0.032043 | 0.13733 | 0.050354 | 0.14648 | 121.019 | -0.086975 | -0.054931 | 121.1472 | 121.0419 | 121.0327 | 0.022888 | 0.013733 | 120.9869 | -0.032043 | -0.027466 | 121.1472 | 121.1563 | 121.0602 | 0.16937 | 0.073242 | 0.12817 | -0.004577 | 0.16022 | 0.054931 | -0.036621 | 0.050354 | 120.9824 | 121.0373 | -0.050354 | -0.082397 | 121.0144 | 121.0419 | 120.9457 | 121.0007
3201.2031 | 121.1975 | -121.051 | 0.091553 | -0.0016786 | 0.013719 | -0.034577 | 0.037762 | -0.016344 | -0.027754 | -0.022819 | 0.0055542 | -0.061865 | 0.00031615 | 0.038743 | -0.017513 | -0.0098864 | -0.011828 | -0.086975 | -0.009155 | -0.059509 | -0.091553 | 0.009155 | -0.068665 | -0.050354 | -0.054932 | 0.054932 | -0.050354 | -0.013733 | 0.036621 | -0.041199 | 0.10529 | 120.9915 | -0.10071 | -0.18311 | 121.0602 | 121.0007 | 120.9824 | 0.009155 | -0.009156 | 121.0007 | -0.036621 | -0.10529 | 121.0876 | 121.1563 | 121.0098 | 0.15564 | 0.009155 | 0.068664 | -0.032044 | 0.086975 | 0.036621 | 0.050354 | 0.10529 | 121.0419 | 121.106 | -0.15106 | -0.14191 | 120.9595 | 121.0373 | 120.9641 | 120.9961
3202.9688 | 121.2433 | -121.0602 | 0.064087 | 0.01358 | 0.013719 | -0.033722 | 0.034344 | -0.016131 | -0.028395 | -0.021537 | 0.008606 | -0.064429 | 0.0018116 | 0.038743 | -0.021999 | -0.0101 | -0.01311 | -0.013733 | -0.041199 | -0.004578 | 0.018311 | 0.17853 | 0.082397 | 0.064087 | 0.036621 | 0.036621 | -0.032043 | 0.032043 | 0.14191 | 0.050354 | 0.13275 | 121.0556 | -0.10529 | -0.045776 | 121.2387 | 121.1243 | 121.1426 | 0.068665 | 0.086975 | 121.0281 | -0.027466 | -0.032044 | 121.2021 | 121.1929 | 121.1105 | 0.16479 | 0.082397 | 0.18311 | 0.022889 | 0.17395 | 0.064086 | -0.036621 | 0.068664 | 121.019 | 121.0968 | -0.068665 | -0.09613 | 121.0785 | 121.0922 | 121.0464 | 121.0968
3204.6875 | 121.3165 | -120.9824 | 0.059509 | 0.01358 | 0.011369 | -0.034791 | 0.033703 | -0.01314 | -0.028822 | -0.020683 | -0.00054937 | -0.066565 | -0.0016064 | 0.050278 | -0.019435 | -0.010527 | -0.014605 | -0.013733 | -0.059509 | 0 | 0.045776 | 0.23346 | 0.1236 | 0.10071 | 0.12817 | 0.018311 | -0.009155 | 0.10071 | 0.21057 | 0.12817 | 0.19684 | 120.9824 | -0.11902 | -0.013733 | 121.2158 | 121.0831 | 121.106 | 0.10071 | 0.1236 | 120.9732 | -0.041198 | 0.041199 | 121.1929 | 121.1792 | 121.1105 | 0.20599 | 0.13733 | 0.23346 | 0.045776 | 0.21973 | 0.10986 | -0.059509 | 0.027466 | 120.9229 | 121.0007 | -0.059509 | -0.068664 | 121.0281 | 121.0831 | 120.9686 | 121.1105
3206.4062 | 121.3806 | -120.9961 | 0.086975 | 0.02121 | 0.014787 | -0.032868 | 0.035412 | -0.013781 | -0.030745 | -0.020897 | 0.0055542 | -0.063361 | -0.0022472 | 0.035325 | -0.019222 | -0.010741 | -0.014392 | 0 | -0.041199 | 0.009155 | 0.054932 | 0.22888 | 0.11902 | 0.10071 | 0.10529 | 0.009155 | -0.027466 | 0.09613 | 0.2243 | 0.13275 | 0.19684 | 121.0052 | -0.12817 | -0.032043 | 121.225 | 121.0968 | 121.1151 | 0.091553 | 0.10986 | 120.9686 | -0.07782 | 0.009155 | 121.2204 | 121.1929 | 121.1288 | 0.2243 | 0.16022 | 0.21973 | 0.045777 | 0.25177 | 0.1236 | -0.050354 | 0.036621 | 120.9549 | 121.0052 | -0.07782 | -0.11444 | 121.051 | 121.0922 | 120.9961 | 121.1014
3208.125 | 121.4035 | -121.0373 | 0.07782 | 0.01358 | 0.013933 | -0.035431 | 0.03349 | -0.017199 | -0.028181 | -0.022178 | 0.0055542 | -0.063147 | -0.00011105 | 0.038315 | -0.021358 | -0.012236 | -0.016528 | 0.009155 | -0.059509 | 0.009155 | 0.041199 | 0.2243 | 0.10529 | 0.10071 | 0.10529 | 0.018311 | -0.009155 | 0.091553 | 0.21057 | 0.13733 | 0.21057 | 121.0464 | -0.13733 | -0.036621 | 121.2616 | 121.138 | 121.1426 | 0.091553 | 0.096131 | 121.0281 | -0.059509 | 0.013733 | 121.2479 | 121.2479 | 121.1746 | 0.21973 | 0.14648 | 0.21515 | 0.032044 | 0.21973 | 0.10071 | -0.068664 | 0.027466 | 120.9778 | 121.0556 | -0.068665 | -0.086975 | 121.0785 | 121.1288 | 121.0464 | 121.1426
3209.8906 | 121.3211 | -121.0419 | 0.068665 | 0.01358 | 0.015214 | -0.031373 | 0.034131 | -0.018694 | -0.027113 | -0.023674 | 0.0055542 | -0.064642 | -0.0011792 | 0.036179 | -0.016658 | -0.0098864 | -0.012896 | -0.045776 | -0.027466 | 0.009155 | -0.004578 | 0.1236 | 0.050354 | 0.036621 | 0.036621 | 0.009155 | -0.022888 | 0.064087 | 0.16479 | 0.10986 | 0.17395 | 121.051 | -0.096131 | -0.073243 | 121.1655 | 121.0785 | 121.0922 | 0.027466 | 0.041199 | 121.019 | -0.05951 | -0.004578 | 121.2067 | 121.2158 | 121.1517 | 0.19684 | 0.13275 | 0.11444 | -0.013733 | 0.18768 | 0.086975 | -0.036621 | 0.032043 | 121.0144 | 121.051 | -0.05951 | -0.091553 | 121.0373 | 121.106 | 120.9961 | 121.0785
3211.6094 | 121.2616 | -121.0968 | 0.086975 | 0.051727 | 0.016069 | -0.035431 | 0.036694 | -0.014849 | -0.028395 | -0.020897 | 0.017761 | -0.06037 | 0.00010255 | 0.035111 | -0.020503 | -0.012664 | -0.01781 | -0.073242 | 0.018311 | -0.054932 | -0.07782 | 0.045776 | -0.009155 | -0.009155 | -0.07782 | 0.059509 | -0.059509 | -0.027466 | 0.050354 | -0.032043 | 0.10529 | 121.0419 | -0.068664 | -0.16479 | 121.1426 | 121.0876 | 121.0876 | 0.045777 | 0.045777 | 121.0373 | -0.027466 | -0.11444 | 121.1472 | 121.2021 | 121.0648 | 0.16479 | 0.027466 | 0.10071 | -0.022888 | 0.10986 | 0.032043 | 0.073243 | 0.11902 | 121.1151 | 121.1563 | -0.14191 | -0.14648 | 121.019 | 121.0693 | 121.0236 | 121.019
3213.3125 | 121.2799 | -121.138 | 0.10071 | 0.036468 | 0.013719 | -0.032227 | 0.03648 | -0.022112 | -0.028822 | -0.021751 | 0.008606 | -0.061438 | -0.0011792 | 0.03212 | -0.016231 | -0.0096728 | -0.015033 | -0.027466 | -0.022888 | -0.032043 | -0.018311 | 0.11444 | -0.013733 | 0.004578 | -0.013733 | 0.050354 | -0.032043 | 0.027466 | 0.086975 | 0.004578 | 0.12817 | 121.106 | -0.1236 | -0.11902 | 121.2524 | 121.1426 | 121.1243 | 0.036621 | 0.01831 | 121.106 | -0.050354 | -0.073242 | 121.225 | 121.2662 | 121.1426 | 0.16022 | 0.036621 | 0.14648 | 0.013732 | 0.11902 | 0.059509 | 0.009155 | 0.082397 | 121.1151 | 121.1884 | -0.13275 | -0.13275 | 121.1197 | 121.1655 | 121.1105 | 121.1243
3215.0312 | 121.2433 | -121.0922 | 0.12817 | 0.028839 | 0.015641 | -0.032654 | 0.03883 | -0.017626 | -0.029036 | -0.019615 | 0.011658 | -0.062506 | 0.00010255 | 0.034897 | -0.016872 | -0.011382 | -0.014605 | -0.022888 | -0.013733 | -0.041199 | -0.018311 | 0.10071 | 0.018311 | 0.009155 | 0.009155 | 0.041199 | -0.041199 | 0.032043 | 0.1236 | 0.036621 | 0.12817 | 121.051 | -0.14191 | -0.14649 | 121.1929 | 121.1014 | 121.1105 | 0.050354 | 0.05951 | 121.051 | -0.086975 | -0.096131 | 121.2158 | 121.2204 | 121.1288 | 0.16937 | 0.07782 | 0.14191 | 0.022888 | 0.16479 | 0.073242 | 0.027466 | 0.082398 | 121.0785 | 121.1334 | -0.16937 | -0.16937 | 121.0739 | 121.1243 | 121.0693 | 121.1014
3216.7344 | 121.3211 | -121.0327 | 0.10986 | 0.01358 | 0.013078 | -0.032868 | 0.035412 | -0.014635 | -0.027327 | -0.024314 | 0.0055542 | -0.065711 | -0.00032465 | 0.043656 | -0.018794 | -0.009032 | -0.010974 | -0.045776 | -0.050354 | -0.009155 | -0.009155 | 0.11444 | 0.027466 | 0.022888 | -0.022888 | 0.013733 | -0.032043 | 0.036621 | 0.14648 | 0.045776 | 0.15106 | 121.0236 | -0.16022 | -0.11902 | 121.1472 | 121.0556 | 121.0602 | 0.032043 | 0.036621 | 121.0007 | -0.09613 | -0.073242 | 121.1792 | 121.1838 | 121.0785 | 0.18311 | 0.077819 | 0.1236 | 0 | 0.17853 | 0.068664 | -0.041199 | 0.045776 | 120.9824 | 121.0464 | -0.11902 | -0.14191 | 121.0236 | 121.0693 | 120.9869 | 121.0098
3218.5 | 120.3323 | -8.6517 | 112.0651 | 0.044098 | 0.013292 | -0.035004 | 0.037335 | -0.018267 | -0.031813 | -0.023246 | 0.017761 | -0.061224 | -0.00096545 | 0.039384 | -0.018367 | -0.011595 | -0.013965 | -0.091553 | -0.041199 | -0.07782 | -0.10071 | 0.013733 | -0.041199 | -0.036621 | -0.082397 | 0.004578 | -0.10986 | -0.022888 | 0.041199 | -0.041199 | 0.086975 | 8.5739 | -112.1063 | -112.1658 | 8.6655 | 8.6151 | 8.6105 | 0.041199 | 0.036621 | 8.5419 | -112.0605 | -112.088 | 8.6929 | 8.7387 | 8.6105 | 0.19684 | 0.068664 | 0.091553 | -0.022888 | 0.15106 | 0.086975 | 0.036621 | 0.11444 | 8.6105 | 8.6563 | -112.1429 | -112.175 | 8.551 | 8.6288 | 8.5602 | 8.5693
3220.2031 | 120.3873 | -9.2148 | 111.1816 | 0.01358 | 0.015428 | -0.033509 | 0.037762 | -0.018267 | -0.028181 | -0.024528 | 0.011658 | -0.061011 | -0.00011105 | 0.040238 | -0.017299 | -0.014159 | -0.015246 | -0.059509 | -0.050354 | -0.07782 | -0.068665 | 0.086975 | -0.032043 | -0.013733 | -0.022888 | 0.009155 | -0.09613 | 0.009155 | 0.082397 | -0.004578 | 0.10529 | 9.137 | -111.232 | -111.2503 | 9.3018 | 9.2011 | 9.1827 | 0.064087 | 0.045777 | 9.1187 | -111.1725 | -111.1725 | 9.2972 | 9.3201 | 9.2102 | 0.20142 | 0.091552 | 0.16479 | 0.009155 | 0.17853 | 0.10528 | 0.027466 | 0.10528 | 9.1644 | 9.2239 | -111.2595 | -111.2778 | 9.1461 | 9.2239 | 9.1553 | 9.1919
3221.9062 | 121.2433 | -6.2164 | 114.8392 | 0.02121 | 0.015855 | -0.033722 | 0.03648 | -0.015062 | -0.027967 | -0.022178 | 0.0055542 | -0.063147 | 0.00031615 | 0.040024 | -0.014522 | -0.0092456 | -0.012256 | -0.091553 | -0.059509 | -0.041199 | -0.073242 | 0.073242 | -0.032043 | -0.036621 | -0.013733 | -0.018311 | -0.050354 | 0.050354 | 0.13733 | 0.045776 | 0.15106 | 6.1752 | -114.8987 | -114.9124 | 6.2897 | 6.1798 | 6.1844 | 0.004578 | 0.009156 | 6.1661 | -114.8575 | -114.7888 | 6.3538 | 6.3675 | 6.2622 | 0.20142 | 0.09613 | 0.11444 | -0.032043 | 0.18768 | 0.10071 | -0.01831 | 0.032043 | 6.1569 | 6.1981 | -114.8804 | -114.8895 | 6.1432 | 6.2668 | 6.1249 | 6.2027
3223.6094 | 121.2479 | -4.7012 | 116.423 | 0.02121 | 0.012437 | -0.034577 | 0.035412 | -0.01848 | -0.028395 | -0.021751 | 0.008606 | -0.064642 | 0.0013844 | 0.036606 | -0.020717 | -0.010955 | -0.011828 | -0.045776 | -0.09613 | -0.032043 | 0.004578 | 0.15564 | 0.050354 | 0.036621 | 0.009155 | -0.027466 | -0.068665 | 0.027466 | 0.16022 | 0.068665 | 0.13275 | 4.6692 | -116.5192 | -116.4185 | 4.8569 | 4.7379 | 4.7516 | 0.068664 | 0.082397 | 4.6326 | -116.4505 | -116.3956 | 4.8615 | 4.834 | 4.7699 | 0.20142 | 0.13733 | 0.18768 | 0.036621 | 0.22888 | 0.096131 | -0.064087 | 0.041199 | 4.6051 | 4.6738 | -116.4551 | -116.4917 | 4.7058 | 4.7287 | 4.6555 | 4.7104
3225.3906 | 121.1609 | -5.9143 | 114.592 | 0.028839 | 0.015001 | -0.033722 | 0.034558 | -0.01784 | -0.029249 | -0.021751 | 0.011658 | -0.064215 | 0.00095715 | 0.032761 | -0.020717 | -0.012877 | -0.012256 | -0.11444 | -0.045776 | -0.086975 | -0.10529 | 0.027466 | -0.064087 | -0.054932 | -0.10071 | 0.045776 | -0.10071 | -0.073242 | 0.027466 | -0.054932 | 0.054932 | 5.8273 | -114.6378 | -114.6973 | 5.9418 | 5.8594 | 5.8502 | 0.032043 | 0.022888 | 5.8136 | -114.5462 | -114.6652 | 5.9418 | 5.9692 | 5.8594 | 0.15564 | 0.045776 | 0.11444 | -0.018311 | 0.12817 | 0.027466 | 0.041199 | 0.14648 | 5.8685 | 5.9601 | -114.679 | -114.6927 | 5.809 | 5.8411 | 5.7999 | 5.8136
3227.1094 | 121.2021 | -3.3142 | 117.7368 | 0.044098 | 0.015855 | -0.034577 | 0.035199 | -0.015062 | -0.027113 | -0.022605 | 0.014709 | -0.061438 | -0.00011105 | 0.041306 | -0.01794 | -0.012236 | -0.013537 | -0.11444 | -0.018311 | -0.09613 | -0.10071 | 0.013733 | -0.050354 | -0.050354 | -0.11902 | 0.036621 | -0.10071 | -0.064087 | 0.045776 | -0.036621 | 0.059509 | 3.2181 | -117.7551 | -117.8375 | 3.3279 | 3.2639 | 3.2639 | 0.045776 | 0.045776 | 3.2135 | -117.7002 | -117.8009 | 3.36 | 3.3737 | 3.2776 | 0.16022 | 0.064087 | 0.10986 | -0.004578 | 0.14648 | 0.036621 | 0.077819 | 0.13733 | 3.2959 | 3.3508 | -117.8329 | -117.8375 | 3.2135 | 3.2501 | 3.1998 | 3.1952
3228.8438 | 121.2112 | -3.1174 | 118.1259 | 0.01358 | 0.017564 | -0.032013 | 0.037335 | -0.016131 | -0.029249 | -0.026023 | 0.0025024 | -0.061011 | -0.0011792 | 0.037247 | -0.014949 | -0.011382 | -0.014392 | -0.10529 | -0.041199 | -0.054932 | -0.11902 | -0.009155 | -0.10529 | -0.091553 | -0.13733 | 0.022888 | -0.09613 | -0.064087 | -0.004578 | -0.09613 | 0.068665 | 3.0624 | -118.1671 | -118.2449 | 3.1082 | 3.0258 | 3.0121 | -0.036621 | -0.050354 | 3.0212 | -118.103 | -118.19 | 3.1128 | 3.186 | 3.0212 | 0.16479 | 0 | 0.045777 | -0.064087 | 0.091552 | 0.032043 | 0.013733 | 0.11902 | 3.0762 | 3.1403 | -118.1808 | -118.222 | 2.9984 | 3.0533 | 3.0121 | 2.98
3230.5625 | 121.3303 | -3.7765 | 117.5079 | 0.028839 | 0.013933 | -0.033295 | 0.03584 | -0.01784 | -0.028608 | -0.02346 | 0.0055542 | -0.063361 | -0.00011105 | 0.039384 | -0.017299 | -0.0086048 | -0.0071286 | -0.10529 | -0.07782 | -0.045776 | -0.059509 | 0.082397 | 0.009155 | -0.004578 | -0.050354 | -0.018311 | -0.07782 | -0.004578 | 0.086975 | 0.004578 | 0.1236 | 3.7308 | -117.5858 | -117.5674 | 3.8589 | 3.772 | 3.7857 | 0.041198 | 0.054931 | 3.6987 | -117.5262 | -117.5125 | 3.8635 | 3.9001 | 3.7811 | 0.20142 | 0.082398 | 0.12817 | -0.013733 | 0.16479 | 0.073242 | -0.032044 | 0.059509 | 3.6987 | 3.7582 | -117.5537 | -117.5858 | 3.717 | 3.772 | 3.6713 | 3.7262
3232.2812 | 121.3028 | -9.1782 | 111.9232 | 0.02121 | 0.016069 | -0.032868 | 0.035626 | -0.013353 | -0.029036 | -0.022178 | 0.011658 | -0.063361 | 0.001598 | 0.04152 | -0.016445 | -0.0092456 | -0.011828 | -0.073242 | -0.091553 | -0.041199 | -0.041199 | 0.086975 | -0.022888 | 0 | -0.027466 | -0.027466 | -0.068665 | -0.004578 | 0.10071 | 0.013733 | 0.1236 | 9.137 | -112.0148 | -111.9644 | 9.2651 | 9.1782 | 9.1553 | 0.041199 | 0.018311 | 9.1095 | -111.9507 | -111.9278 | 9.2789 | 9.3018 | 9.1919 | 0.19226 | 0.082398 | 0.12817 | 0 | 0.16937 | 0.064087 | -0.050354 | 0.041199 | 9.0866 | 9.1507 | -111.9644 | -111.9919 | 9.137 | 9.1736 | 9.1049 | 9.1507
3234.0156 | 121.1517 | -5.0629 | 115.6494 | 0.044098 | 0.015214 | -0.032654 | 0.037549 | -0.014208 | -0.027113 | -0.023033 | 0.008606 | -0.064215 | -0.0011792 | 0.040238 | -0.014308 | -0.0081774 | -0.012896 | -0.036621 | -0.07782 | -0.041199 | 0.009155 | 0.15106 | 0.004578 | 0.032043 | 0.032043 | -0.004578 | -0.045776 | 0.018311 | 0.10986 | 0.041199 | 0.14191 | 5.0217 | -115.7272 | -115.6403 | 5.2139 | 5.0949 | 5.0674 | 0.073242 | 0.045777 | 5.0171 | -115.654 | -115.6311 | 5.1727 | 5.2048 | 5.1041 | 0.18768 | 0.086975 | 0.19226 | 0.050354 | 0.15564 | 0.064087 | -0.036621 | 0.041198 | 4.985 | 5.0583 | -115.6906 | -115.6952 | 5.072 | 5.0812 | 5.0262 | 5.0949
3235.7344 | 121.3303 | -4.3488 | 116.89 | 0.028839 | 0.015428 | -0.032868 | 0.036053 | -0.013781 | -0.025618 | -0.021751 | 0.008606 | -0.061651 | -0.00011105 | 0.042161 | -0.011959 | -0.0075366 | -0.015674 | -0.073242 | -0.073242 | -0.045776 | -0.018311 | 0.091553 | -0.013733 | 0.009155 | 0.022888 | -0.018311 | -0.054932 | 0.059509 | 0.14191 | 0.045776 | 0.1831 | 4.303 | -116.9632 | -116.9083 | 4.4403 | 4.3579 | 4.335 | 0.054931 | 0.032043 | 4.2938 | -116.9083 | -116.8304 | 4.4907 | 4.5319 | 4.3945 | 0.23804 | 0.10071 | 0.13733 | 0.027465 | 0.19684 | 0.11444 | -0.027466 | 0.036621 | 4.2755 | 4.3304 | -116.9357 | -116.9449 | 4.3304 | 4.4083 | 4.2755 | 4.3716
3237.4531 | 121.376 | -4.9942 | 115.535 | -0.15427 | 0.012651 | -0.033936 | 0.036053 | -0.012926 | -0.028181 | -0.022178 | 0.008606 | -0.061865 | -0.00075185 | 0.036179 | -0.01559 | -0.0071094 | -0.016314 | -0.018311 | -0.086975 | -0.045776 | 0.013733 | 0.13275 | 0.009155 | 0.018311 | 0.059509 | -0.013733 | 0.16479 | 0.073242 | 0.15106 | 0.064087 | 0.17853 | 4.9484 | -115.6219 | -115.5212 | 5.127 | 5.0125 | 5.0034 | 0.064087 | 0.054931 | 5.159 | -115.5487 | -115.4617 | 5.1453 | 5.1727 | 5.0583 | 0.013733 | -0.10071 | 0.17853 | 0.059509 | -0.013733 | -0.091553 | -0.041199 | -0.17853 | 4.9072 | 4.9805 | -115.5807 | -115.3702 | 5.0079 | 5.0674 | 4.9759 | 5.0537
3239.1875 | 121.4539 | -113.4567 | 7.4615 | 0.02121 | 0.01201 | -0.030091 | 0.033703 | -0.019121 | -0.028608 | -0.022819 | 0.011658 | -0.063147 | 0.0024524 | 0.046433 | -0.017513 | -0.010955 | -0.0099056 | -0.091553 | -0.050354 | 0.054932 | -0.004578 | 0.12817 | 0.054932 | 0.054932 | 0.013733 | -0.14648 | 0.27008 | 0.054932 | 0.16479 | 0.082397 | 0.19226 | 113.5117 | -7.5119 | -7.4661 | 113.5849 | 113.5117 | 113.5117 | 0 | 0 | 113.7268 | -7.608 | -7.4066 | 113.6215 | 113.649 | 113.5391 | -0.07782 | -0.18768 | 0.073242 | -0.05951 | -0.10529 | -0.21515 | -0.10529 | -0.41657 | 113.4064 | 113.3102 | -7.4066 | -7.1915 | 113.4521 | 113.5117 | 113.3652 | 113.4705
3240.9688 | 121.4584 | -120.9732 | 0.16479 | 0.036468 | 0.013078 | -0.030304 | 0.036694 | -0.020617 | -0.030317 | -0.020897 | 0.014709 | -0.065283 | 0.00010255 | 0.044724 | -0.018154 | -0.0088184 | -0.010119 | -0.041199 | -0.022888 | 0.018311 | 0.013733 | 0.15564 | 0.041199 | 0.059509 | 0.027466 | 0.004578 | 0.086975 | 0.073242 | 0.12817 | 0.068665 | 0.16022 | 120.9915 | -0.18768 | -0.15106 | 121.1288 | 121.0327 | 121.0144 | 0.041198 | 0.022888 | 121.0602 | -0.16022 | -0.091553 | 121.1014 | 121.1334 | 121.0419 | 0.073242 | -0.01831 | 0.13733 | -0.004578 | 0.041199 | -0.013733 | -0.041199 | -0.082397 | 120.9503 | 120.9778 | -0.14648 | -0.07782 | 120.9869 | 121.0464 | 120.932 | 121.0007
3242.6875 | 121.4447 | -120.8496 | 0.30212 | 0.036468 | 0.013078 | -0.031586 | 0.036908 | -0.015062 | -0.029676 | -0.02111 | 0.008606 | -0.063361 | -0.0013928 | 0.046433 | -0.01559 | -0.0077502 | -0.011828 | -0.027466 | -0.036621 | 0.004578 | 0.032043 | 0.17853 | 0.07782 | 0.064087 | 0.073242 | 0.013733 | -0.027466 | 0.064087 | 0.13275 | 0.073242 | 0.17853 | 120.8542 | -0.33875 | -0.27008 | 121.0281 | 120.9137 | 120.9274 | 0.059509 | 0.073242 | 120.8221 | -0.28839 | -0.23804 | 120.9824 | 121.0281 | 120.9229 | 0.20599 | 0.10071 | 0.17395 | 0.027465 | 0.16022 | 0.091553 | -0.041199 | 0.041199 | 120.813 | 120.8633 | -0.29755 | -0.32959 | 120.8817 | 120.9137 | 120.8221 | 120.9229
3244.4688 | 121.4035 | -120.5704 | 0.6546 | 0.02121 | 0.014573 | -0.031586 | 0.027508 | 0.028089 | -0.029676 | -0.031578 | 0.0055542 | -0.0781 | 0.00031615 | 0.027421 | -0.028835 | -0.021208 | -0.016101 | -0.018311 | -0.009155 | -0.022888 | -0.009155 | 0.10071 | 0.013733 | 0.009155 | 0.036621 | 0.032043 | -0.032043 | 0.054932 | 0.059509 | -0.3479 | -0.036621 | 120.5475 | -0.66376 | -0.66376 | 120.6711 | 120.5795 | 120.5841 | 0.032043 | 0.036621 | 120.5383 | -0.62256 | -0.59967 | 120.6299 | 120.5338 | 120.2225 | -0.004578 | -0.31586 | 0.1236 | 0.013733 | 0.091552 | 0.086975 | 0.013733 | 0.064086 | 120.5612 | 120.6024 | -0.67749 | -0.68665 | 120.5612 | 120.6253 | 120.5521 | 120.607
3246.1719 | 121.344 | -120.8176 | 0.41199 | 0.028839 | 0.015214 | -0.034577 | 0.036267 | -0.021471 | -0.027113 | -0.024528 | 0.011658 | -0.072333 | -0.0020336 | 0.030839 | -0.025844 | -0.021636 | -0.020587 | -0.032043 | -0.004578 | -0.045776 | -0.013733 | 0.10529 | 0.013733 | 0.004578 | -0.009155 | 0.054932 | -0.027466 | 0.045776 | 0.073242 | -0.25635 | -0.21973 | 120.7718 | -0.41657 | -0.42572 | 120.9229 | 120.8221 | 120.8313 | 0.050354 | 0.059509 | 120.7901 | -0.35706 | -0.36621 | 120.8908 | 120.5978 | 120.5612 | -0.19226 | -0.22888 | 0.15106 | 0.032043 | 0.10071 | 0.073242 | 0.041198 | 0.082398 | 120.813 | 120.8725 | -0.45776 | -0.43945 | 120.8038 | 120.8633 | 120.7855 | 120.8084
3247.9375 | 121.4401 | -120.8771 | 0.36621 | 0.02121 | 0.013292 | -0.032013 | 0.034131 | -0.016344 | -0.029463 | -0.022392 | 0.011658 | -0.064429 | -0.003529 | 0.039597 | -0.01794 | -0.010741 | -0.013537 | 0 | -0.050354 | -0.009155 | 0.059509 | 0.19226 | 0.091553 | 0.091553 | 0.082397 | 0.018311 | -0.022888 | 0.091553 | 0.17853 | 0.09613 | 0.17853 | 120.8679 | -0.41657 | -0.3067 | 121.0693 | 120.9686 | 120.9686 | 0.10071 | 0.10071 | 120.8542 | -0.3479 | -0.27466 | 121.0556 | 121.0556 | 120.9732 | 0.20142 | 0.11902 | 0.20142 | 0.068664 | 0.20142 | 0.11444 | -0.041199 | 0.041199 | 120.8267 | 120.8954 | -0.37537 | -0.3891 | 120.9366 | 120.9686 | 120.8771 | 120.9595
3249.6406 | 121.3394 | -120.8221 | 0.44861 | 0.01358 | 0.016282 | -0.034363 | 0.037549 | -0.017199 | -0.029463 | -0.021324 | 0.014709 | -0.064215 | 0.00031615 | 0.038743 | -0.014095 | -0.009032 | -0.012896 | -0.082397 | 0.018311 | -0.027466 | -0.10986 | -0.022888 | -0.068665 | -0.07782 | -0.073242 | 0.054932 | -0.041199 | -0.013733 | 0.018311 | -0.059509 | -0.045776 | 120.7947 | -0.4303 | -0.55847 | 120.7993 | 120.7443 | 120.7535 | -0.050354 | -0.041199 | 120.7809 | -0.39368 | -0.46234 | 120.8405 | 120.7764 | 120.7626 | -0.004577 | -0.01831 | 0.004578 | -0.082397 | 0.05951 | 0.027466 | 0.045777 | 0.096131 | 120.8405 | 120.8771 | -0.47607 | -0.48981 | 120.7123 | 120.8084 | 120.7397 | 120.7489
3251.3438 | 121.4539 | -120.9595 | 0.27008 | 0.02121 | 0.015641 | -0.033082 | 0.035199 | -0.015062 | -0.027327 | -0.021965 | 0.008606 | -0.064002 | -0.00182 | 0.042801 | -0.016231 | -0.0068958 | -0.012469 | -0.050354 | -0.032043 | -0.018311 | 0.009155 | 0.13733 | 0.022888 | 0.045776 | 0.068665 | 0.027466 | 0.009155 | 0.10986 | 0.16479 | 0.064087 | 0.20142 | 120.9412 | -0.30212 | -0.26093 | 121.0968 | 121.0052 | 120.9824 | 0.064087 | 0.041199 | 120.9686 | -0.24262 | -0.16022 | 121.1243 | 121.1609 | 121.0236 | 0.19226 | 0.054932 | 0.15564 | 0.027466 | 0.15564 | 0.10071 | -0.013732 | 0.018311 | 120.9274 | 120.9869 | -0.28839 | -0.26093 | 120.9686 | 121.0693 | 120.9091 | 121.0281
3253.0781 | 121.4722 | -120.9366 | 0.32959 | 0.01358 | 0.014573 | -0.0318 | 0.034772 | -0.01549 | -0.028822 | -0.02581 | 0.008606 | -0.063574 | -0.00011105 | 0.044724 | -0.016872 | -0.0092456 | -0.012256 | -0.036621 | -0.036621 | 0.009155 | 0.009155 | 0.15106 | 0.064087 | 0.082397 | 0.054932 | 0.018311 | -0.036621 | 0.09613 | 0.1831 | 0.10071 | 0.19684 | 120.9457 | -0.36621 | -0.32043 | 121.0876 | 121.019 | 121.0007 | 0.073242 | 0.054932 | 120.9 | -0.31128 | -0.23346 | 121.1197 | 121.1334 | 121.0373 | 0.23346 | 0.13733 | 0.14191 | 0 | 0.21973 | 0.13275 | -0.045776 | 0.054932 | 120.9 | 120.9549 | -0.32043 | -0.36621 | 120.9457 | 121.0327 | 120.9 | 120.9915
3254.7969 | 121.4355 | -120.8542 | 0.36621 | 0.02121 | 0.014573 | -0.032441 | 0.036908 | -0.015917 | -0.031813 | -0.020897 | 0.0055542 | -0.064215 | -0.00032465 | 0.033616 | -0.017513 | -0.0075366 | -0.012469 | -0.013733 | -0.059509 | 0.018311 | 0.054932 | 0.19684 | 0.11444 | 0.091553 | 0.086975 | 0.032043 | -0.009155 | 0.086975 | 0.19226 | 0.10529 | 0.19226 | 120.8725 | -0.42572 | -0.31128 | 121.051 | 120.9457 | 120.9686 | 0.073242 | 0.09613 | 120.845 | -0.33417 | -0.27924 | 121.0464 | 121.0464 | 120.9595 | 0.20142 | 0.11444 | 0.17853 | 0.036621 | 0.20142 | 0.09613 | -0.07782 | 0.041198 | 120.7947 | 120.8862 | -0.3479 | -0.37537 | 120.9091 | 120.9412 | 120.8405 | 120.9412
3256.5156 | 121.4859 | -120.9503 | 0.32044 | 0.02121 | 0.015001 | -0.033936 | 0.034985 | -0.020403 | -0.029463 | -0.02111 | 0.008606 | -0.06272 | -0.0022472 | 0.046219 | -0.018367 | -0.0092456 | -0.016742 | -0.009155 | -0.045776 | 0.009155 | 0.045776 | 0.17395 | 0.07782 | 0.086975 | 0.064087 | 0.018311 | -0.022888 | 0.064087 | 0.1831 | 0.082397 | 0.17395 | 120.9595 | -0.36621 | -0.27466 | 121.1243 | 121.0373 | 121.0281 | 0.07782 | 0.068665 | 120.9274 | -0.30212 | -0.25635 | 121.1334 | 121.1243 | 121.0327 | 0.19684 | 0.10528 | 0.16479 | 0.036621 | 0.20599 | 0.086975 | -0.054931 | 0.041199 | 120.9045 | 120.9686 | -0.31128 | -0.34332 | 120.9961 | 121.0144 | 120.9412 | 121.0144
3258.2188 | 121.312 | -119.3939 | 1.918 | 0.036468 | 0.015428 | -0.033936 | 0.037762 | -0.015062 | -0.032026 | -0.024101 | 0.014709 | -0.062292 | -0.0022472 | 0.034684 | -0.020076 | -0.010741 | -0.01076 | -0.064087 | 0 | -0.064087 | -0.07782 | 0.041199 | -0.018311 | -0.009155 | -0.07782 | 0.064087 | -0.07782 | -0.041199 | 0.041199 | -0.036621 | 0.09613 | 119.3298 | -1.918 | -1.9958 | 119.4351 | 119.3848 | 119.3756 | 0.054932 | 0.045776 | 119.3161 | -1.8539 | -1.9592 | 119.4351 | 119.4901 | 119.3573 | 0.17395 | 0.041199 | 0.10529 | -0.013733 | 0.11902 | 0.036621 | 0.064087 | 0.14191 | 119.3939 | 119.458 | -1.9821 | -1.9958 | 119.3161 | 119.3527 | 119.3298 | 119.3161
3260 | 121.4355 | -121.138 | 0.2243 | 0.02121 | 0.015428 | -0.033295 | 0.038189 | -0.019335 | -0.028181 | -0.02111 | 0.020813 | -0.063788 | -0.00075185 | 0.033829 | -0.018581 | -0.009032 | -0.012256 | -0.064087 | -0.004578 | -0.045776 | -0.059509 | 0.059509 | -0.004578 | 0.004578 | -0.045776 | 0.059509 | -0.064087 | 0.004578 | 0.073242 | -0.009155 | 0.11444 | 121.0922 | -0.22888 | -0.28381 | 121.1975 | 121.1426 | 121.1334 | 0.050354 | 0.041198 | 121.0739 | -0.16479 | -0.21973 | 121.2112 | 121.2524 | 121.1288 | 0.17853 | 0.054932 | 0.10528 | -0.013733 | 0.13733 | 0.068665 | 0.041198 | 0.1236 | 121.1334 | 121.1975 | -0.27008 | -0.28839 | 121.0785 | 121.1426 | 121.0739 | 121.0922
3261.7031 | 121.4218 | -119.7464 | 1.6113 | 0.0059509 | 0.013505 | -0.032654 | 0.036694 | -0.019549 | -0.029676 | -0.022819 | 0.008606 | -0.064429 | -0.00053825 | 0.034257 | -0.017085 | -0.0092456 | -0.01546 | -0.013733 | -0.050354 | 0.004578 | 0.022888 | 0.16479 | 0.07782 | 0.054932 | 0.022888 | 0.027466 | -0.032043 | 0.009155 | 0.1236 | 0.036621 | 0.11902 | 119.751 | -1.6617 | -1.5884 | 119.9112 | 119.8013 | 119.8242 | 0.050354 | 0.073242 | 119.7144 | -1.5839 | -1.6022 | 119.87 | 119.8654 | 119.783 | 0.15106 | 0.068664 | 0.16022 | 0.01831 | 0.15564 | 0.041198 | -0.054932 | 0.059509 | 119.696 | 119.7739 | -1.6068 | -1.6434 | 119.7693 | 119.7556 | 119.7327 | 119.7693
3263.4688 | 121.1563 | -117.2699 | 4.0833 | 0.0059509 | 0.015855 | -0.035004 | 0.037335 | -0.018694 | -0.028822 | -0.020683 | 0.017761 | -0.062506 | -0.00032465 | 0.033616 | -0.019222 | -0.012664 | -0.012256 | -0.10071 | 0.004578 | -0.054932 | -0.07782 | 0.059509 | -0.013733 | -0.018311 | -0.073242 | 0.082397 | -0.059509 | -0.041199 | 0.054932 | -0.022888 | 0.07782 | 117.215 | -4.0787 | -4.1611 | 117.3294 | 117.2516 | 117.2562 | 0.036621 | 0.041199 | 117.2104 | -4.0009 | -4.1245 | 117.3248 | 117.3477 | 117.247 | 0.13733 | 0.036621 | 0.11444 | -0.022888 | 0.11444 | 0.01831 | 0.05951 | 0.14191 | 117.2745 | 117.3523 | -4.1382 | -4.1428 | 117.1921 | 117.2287 | 117.1692 | 117.1967
3265.1875 | 121.4539 | -119.9066 | 1.4053 | 0.028839 | 0.015001 | -0.032654 | 0.036053 | -0.015276 | -0.028822 | -0.02111 | 0.011658 | -0.06272 | -0.0028882 | 0.033402 | -0.01559 | -0.011168 | -0.012896 | -0.041199 | 0 | -0.045776 | -0.032043 | 0.073242 | 0.013733 | 0.009155 | 0.009155 | 0.054932 | -0.041199 | 0.013733 | 0.10986 | 0 | 0.13733 | 119.8608 | -1.4053 | -1.4374 | 119.9799 | 119.9158 | 119.9203 | 0.054931 | 0.059509 | 119.8654 | -1.3504 | -1.3916 | 120.0165 | 120.0439 | 119.9066 | 0.17853 | 0.041199 | 0.11902 | 0.013733 | 0.15106 | 0.054932 | 0.045776 | 0.096131 | 119.9066 | 119.9615 | -1.4511 | -1.4465 | 119.8746 | 119.9203 | 119.8654 | 119.9158
3266.9531 | 121.3303 | -118.7805 | 2.4857 | 0.01358 | 0.012864 | -0.033082 | 0.031994 | -0.020189 | -0.029676 | -0.022605 | 0.008606 | -0.063147 | 0.0018116 | 0.035966 | -0.019435 | -0.011382 | -0.010974 | -0.073242 | -0.013733 | -0.013733 | -0.073242 | 0.032043 | -0.018311 | -0.027466 | -0.073242 | 0.045776 | -0.054932 | -0.059509 | 0.045776 | -0.018311 | 0.068665 | 118.7668 | -2.4994 | -2.5589 | 118.8126 | 118.7531 | 118.7622 | -0.013733 | -0.004578 | 118.7256 | -2.4399 | -2.5452 | 118.8263 | 118.8492 | 118.7622 | 0.1236 | 0.036621 | 0.045776 | -0.059509 | 0.10071 | -0.004577 | 0 | 0.10071 | 118.7668 | 118.8263 | -2.4994 | -2.5406 | 118.7073 | 118.721 | 118.7073 | 118.7073
3268.6719 | 121.4859 | -121.0693 | 0.26093 | 0.036468 | 0.014573 | -0.032227 | 0.036053 | -0.019976 | -0.028181 | -0.021324 | 0.008606 | -0.061011 | -0.00075185 | 0.030839 | -0.014949 | -0.0094592 | -0.013324 | -0.032043 | 0.004578 | -0.032043 | -0.027466 | 0.10986 | 0.013733 | 0.009155 | 0.009155 | 0.036621 | -0.050354 | 0.032043 | 0.10071 | 0.013733 | 0.14191 | 121.0373 | -0.25635 | -0.28839 | 121.1792 | 121.0785 | 121.0831 | 0.041198 | 0.045776 | 121.019 | -0.2243 | -0.22888 | 121.17 | 121.2112 | 121.0831 | 0.19226 | 0.064087 | 0.14191 | 0.004577 | 0.15106 | 0.082397 | 0.036621 | 0.086975 | 121.0739 | 121.106 | -0.29297 | -0.31128 | 121.0419 | 121.1014 | 121.0373 | 121.0785
3270.3906 | 120.163 | -119.8929 | 0.10071 | 0.01358 | 0.014146 | -0.028168 | 0.03648 | -0.016131 | -0.03224 | -0.021537 | -0.0066528 | -0.073614 | -0.0024608 | 0.035325 | -0.017513 | 0.027284 | -0.032122 | -0.073242 | -0.013733 | -0.027466 | -0.041199 | 0.073242 | -0.050354 | -0.032043 | -0.032043 | 0.041199 | -0.027466 | -0.004578 | 0.064087 | -0.045776 | 0.091553 | 119.8654 | -0.11444 | -0.14191 | 119.9661 | 119.8608 | 119.8425 | -0.004577 | -0.022888 | 119.8654 | -0.059509 | -0.10529 | 119.957 | 119.9844 | 119.8471 | 0.11902 | -0.01831 | 0.10071 | -0.013733 | 0.091553 | 0.022888 | 0.013733 | 0.068665 | 119.8791 | 119.9341 | -0.12817 | -0.12817 | 119.8517 | 119.8883 | 119.8196 | 119.8608
3272.1094 | 120.0256 | -120.6345 | 0.10071 | 0.01358 | 0.011583 | -0.030091 | 0.039044 | -0.01549 | -0.030317 | -0.021751 | 0.011658 | -0.063147 | -0.0041698 | 0.045365 | -0.016017 | -0.0088184 | -0.009692 | -0.10071 | -0.013733 | -0.018311 | -0.082397 | 0.050354 | -0.059509 | -0.032043 | -0.036621 | 0.045776 | -0.036621 | 0.032043 | 0.09613 | 0.013733 | 0.14648 | 120.6161 | -0.11444 | -0.18311 | 120.6848 | 120.6024 | 120.575 | -0.013732 | -0.041198 | 120.5978 | -0.054932 | -0.068665 | 120.7306 | 120.7809 | 120.6482 | 0.18311 | 0.050354 | 0.068665 | -0.064086 | 0.13275 | 0.068664 | 0.004578 | 0.082397 | 120.6207 | 120.6802 | -0.11902 | -0.13733 | 120.5521 | 120.6665 | 120.5338 | 120.5978
3273.875 | 120.7947 | -120.3598 | 0.32501 | 0.0059509 | 0.013505 | -0.033509 | 0.035626 | -0.015276 | -0.031599 | -0.019188 | 0.011658 | -0.061011 | -0.0026744 | 0.035111 | -0.020931 | -0.0098864 | -0.007983 | -0.086975 | -0.013733 | -0.027466 | -0.086975 | 0.064087 | -0.018311 | -0.022888 | -0.082397 | 0.036621 | 0.23346 | -0.027466 | 0.050354 | -0.027466 | 0.064087 | 120.3323 | -0.33875 | -0.41199 | 120.4239 | 120.3369 | 120.3415 | 0.004578 | 0.009155 | 120.5933 | -0.28839 | -0.35248 | 120.4102 | 120.4239 | 120.3323 | -0.16937 | -0.26093 | 0.091553 | -0.059509 | -0.1831 | -0.26093 | 0.013733 | -0.19684 | 120.3461 | 120.3964 | -0.35248 | -0.091553 | 120.2728 | 120.3323 | 120.2728 | 120.2774
3275.5781 | 121.0327 | -120.6802 | 0.10986 | 0.02121 | 0.014146 | -0.032441 | 0.037121 | -0.019549 | -0.031172 | -0.022178 | 0.0055542 | -0.065497 | -0.0022472 | 0.045579 | -0.016231 | -0.010741 | -0.01546 | -0.068665 | -0.022888 | -0.009155 | -0.018311 | 0.10986 | 0.041199 | 0.054932 | 0.027466 | 0.018311 | -0.022888 | 0.07782 | 0.15564 | 0.073242 | 0.17853 | 120.6711 | -0.13275 | -0.12817 | 120.7901 | 120.7352 | 120.7214 | 0.064087 | 0.050354 | 120.6573 | -0.091552 | -0.032043 | 120.8359 | 120.8588 | 120.7535 | 0.20142 | 0.09613 | 0.11902 | -0.009156 | 0.17853 | 0.10071 | -0.013733 | 0.041199 | 120.6573 | 120.6985 | -0.11902 | -0.13275 | 120.6619 | 120.7581 | 120.6116 | 120.7077
3277.2969 | 121.0373 | -120.7947 | 0.091553 | 0.044098 | 0.01436 | -0.032227 | 0.03883 | -0.01848 | -0.030104 | -0.020897 | 0.011658 | -0.066138 | -0.003529 | 0.037247 | -0.023494 | -0.019286 | -0.02016 | -0.045776 | -0.009155 | -0.027466 | -0.045776 | 0.07782 | 0.004578 | -0.009155 | 0.004578 | 0.059509 | -0.059509 | 0.027466 | 0.091553 | 0.013733 | 0.09613 | 120.7672 | -0.10071 | -0.13733 | 120.8725 | 120.7855 | 120.7993 | 0.018311 | 0.032044 | 120.7352 | -0.032044 | -0.064087 | 120.8862 | 120.8908 | 120.8084 | 0.15564 | 0.073242 | 0.10529 | -0.01831 | 0.15106 | 0.086975 | 0.018311 | 0.11902 | 120.7855 | 120.8542 | -0.11902 | -0.15106 | 120.7489 | 120.8221 | 120.7489 | 120.7993
3279 | 121.0693 | -120.6207 | 0.23804 | 0.036468 | 0.015428 | -0.032227 | 0.037335 | -0.018908 | -0.028608 | -0.019615 | 0.014709 | -0.064002 | -0.0031018 | 0.038743 | -0.015163 | -0.0098864 | -0.014178 | 0.013733 | -0.050354 | 0.009155 | 0.050354 | 0.17395 | 0.064087 | 0.059509 | 0.10986 | 0.013733 | -0.013733 | 0.10986 | 0.16479 | 0.068665 | 0.19684 | 120.6299 | -0.28839 | -0.18768 | 120.7947 | 120.6802 | 120.6848 | 0.050354 | 0.054932 | 120.607 | -0.2243 | -0.12817 | 120.7855 | 120.8176 | 120.6894 | 0.21057 | 0.082398 | 0.16479 | 0.041199 | 0.17853 | 0.1236 | -0.059509 | 0.027466 | 120.5704 | 120.6345 | -0.22888 | -0.25177 | 120.6711 | 120.7306 | 120.6345 | 120.7306
3280.7188 | 121.1746 | -120.8176 | 0.054932 | 0.02121 | 0.016282 | -0.033936 | 0.037549 | -0.020189 | -0.030958 | -0.022605 | 0.011658 | -0.061651 | -0.0033154 | 0.037247 | -0.013027 | -0.006682 | -0.013324 | 0 | -0.059509 | 0.018311 | 0.045776 | 0.16479 | 0.036621 | 0.054932 | 0.091553 | 0.009155 | 0 | 0.10071 | 0.17853 | 0.086975 | 0.20599 | 120.8359 | -0.11444 | -0.009156 | 120.9824 | 120.8725 | 120.8542 | 0.036621 | 0.01831 | 120.8176 | -0.045777 | 0.045776 | 120.9961 | 121.0236 | 120.9045 | 0.20599 | 0.086975 | 0.14648 | 0.027465 | 0.17853 | 0.10071 | -0.07782 | 0.009155 | 120.7581 | 120.8267 | -0.036621 | -0.054932 | 120.8633 | 120.9183 | 120.8176 | 120.9091
3282.4531 | 121.0785 | -120.9183 | 0.09613 | 0.0059509 | 0.015214 | -0.03415 | 0.037976 | -0.016131 | -0.029676 | -0.020469 | 0.008606 | -0.06272 | -0.0022472 | 0.031907 | -0.016872 | -0.0094592 | -0.01546 | -0.086975 | -0.022888 | -0.032043 | -0.091553 | 0.018311 | -0.07782 | -0.041199 | -0.068665 | 0.045776 | -0.036621 | 0 | 0.036621 | -0.041199 | 0.10529 | 120.8862 | -0.11902 | -0.18768 | 120.9366 | 120.8771 | 120.8405 | -0.009156 | -0.045777 | 120.8817 | -0.050354 | -0.09613 | 120.9549 | 121.0236 | 120.8771 | 0.14191 | -0.004578 | 0.050354 | -0.05951 | 0.073242 | 0.036621 | 0.009155 | 0.082397 | 120.8954 | 120.9641 | -0.12817 | -0.13275 | 120.8267 | 120.9183 | 120.8313 | 120.8496
3284.1562 | 121.2204 | -120.6894 | 0.24261 | 0.02121 | 0.01436 | -0.034363 | 0.037762 | -0.01314 | -0.027967 | -0.02111 | 0.014709 | -0.064002 | -0.0011792 | 0.040238 | -0.016017 | -0.007323 | -0.011187 | 0.009155 | -0.050354 | 0.013733 | 0.059509 | 0.19226 | 0.059509 | 0.07782 | 0.11444 | 0.022888 | -0.027466 | 0.10986 | 0.16479 | 0.091553 | 0.20599 | 120.7031 | -0.29297 | -0.18311 | 120.8817 | 120.7672 | 120.7489 | 0.064087 | 0.045776 | 120.6619 | -0.21973 | -0.13275 | 120.8542 | 120.8954 | 120.7809 | 0.23346 | 0.11902 | 0.17853 | 0.045776 | 0.19226 | 0.13733 | -0.064087 | 0.050354 | 120.639 | 120.7123 | -0.22888 | -0.27008 | 120.7489 | 120.7993 | 120.6985 | 120.8038
3285.9062 | 121.2845 | -120.9229 | 0.054932 | 0.02121 | 0.011796 | -0.034363 | 0.036908 | -0.016771 | -0.028181 | -0.025169 | 0.0055542 | -0.064429 | -0.0020336 | 0.040452 | -0.018581 | -0.0092456 | -0.0092648 | -0.013733 | -0.054932 | 0 | 0.045776 | 0.20599 | 0.09613 | 0.086975 | 0.13275 | 0.018311 | -0.022888 | 0.11444 | 0.20142 | 0.12817 | 0.21973 | 120.9229 | -0.10986 | -0.009156 | 121.1288 | 121.0098 | 121.019 | 0.086975 | 0.09613 | 120.9 | -0.036621 | 0.059509 | 121.1243 | 121.1426 | 121.051 | 0.24261 | 0.15106 | 0.20599 | 0.045776 | 0.2243 | 0.13733 | -0.054932 | 0.041199 | 120.8679 | 120.9412 | -0.054932 | -0.07782 | 120.9686 | 121.0373 | 120.9091 | 121.0556
3287.625 | 121.1746 | -121.0007 | 0.068665 | 0.036468 | 0.015428 | -0.033722 | 0.039044 | -0.012285 | -0.025618 | -0.024101 | 0.011658 | -0.061865 | -0.0011792 | 0.035111 | -0.017085 | -0.0101 | -0.014605 | -0.036621 | -0.018311 | -0.032043 | -0.009155 | 0.11902 | 0.009155 | 0.004578 | 0.027466 | 0.059509 | -0.027466 | 0.022888 | 0.086975 | -0.004578 | 0.1236 | 120.9686 | -0.086976 | -0.07782 | 121.1197 | 121.0052 | 121.0098 | 0.036621 | 0.041198 | 120.9732 | -0.009156 | -0.045777 | 121.0876 | 121.1243 | 120.9961 | 0.15106 | 0.022888 | 0.15106 | 0.022888 | 0.11444 | 0.050354 | 0.013732 | 0.086975 | 120.9824 | 121.0602 | -0.10071 | -0.096131 | 120.9915 | 121.0236 | 120.9641 | 121.0281
3289.4062 | 121.1746 | -121.019 | 0.10071 | 0.0059509 | 0.014787 | -0.0365 | 0.03648 | -0.014635 | -0.027754 | -0.020469 | 0.020813 | -0.062079 | -0.00011105 | 0.044083 | -0.021358 | -0.011382 | -0.011187 | -0.10071 | 0.013733 | -0.054932 | -0.073242 | 0.041199 | -0.013733 | -0.004578 | -0.068665 | 0.073242 | -0.07782 | -0.041199 | 0.054932 | -0.027466 | 0.09613 | 120.9641 | -0.086975 | -0.17395 | 121.0602 | 121.0144 | 121.0052 | 0.050354 | 0.041199 | 120.9412 | -0.027466 | -0.14191 | 121.0739 | 121.1151 | 120.9915 | 0.17395 | 0.050354 | 0.096131 | -0.01831 | 0.13275 | 0.036621 | 0.068665 | 0.15106 | 121.0327 | 121.0922 | -0.15564 | -0.17853 | 120.9457 | 120.9778 | 120.9183 | 120.9503
3291.125 | 121.2296 | -121.0327 | 0.09613 | 0.036468 | 0.01735 | -0.033936 | 0.037762 | -0.016771 | -0.029249 | -0.020469 | 0.014709 | -0.060797 | -0.00096545 | 0.029343 | -0.014736 | -0.010527 | -0.014605 | -0.027466 | 0 | -0.032043 | -0.032043 | 0.09613 | 0.004578 | 0.004578 | 0.004578 | 0.041199 | -0.054932 | 0.022888 | 0.10529 | 0.013733 | 0.13275 | 121.0007 | -0.09613 | -0.12817 | 121.1288 | 121.0373 | 121.0373 | 0.036621 | 0.036621 | 120.9778 | -0.054931 | -0.073242 | 121.138 | 121.1655 | 121.0464 | 0.18768 | 0.068665 | 0.12817 | 0 | 0.16022 | 0.07782 | 0.032043 | 0.096131 | 121.0327 | 121.0739 | -0.12817 | -0.15106 | 121.0007 | 121.0556 | 121.0052 | 121.0373
3292.8438 | 121.3028 | -121.0556 | 0.068665 | 0.0059509 | 0.014573 | -0.033936 | 0.035626 | -0.016771 | -0.028181 | -0.020469 | 0.014709 | -0.064215 | -0.0020336 | 0.039597 | -0.016872 | -0.0092456 | -0.013324 | -0.050354 | -0.045776 | 0.004578 | -0.022888 | 0.10986 | 0.018311 | 0.022888 | 0 | 0.013733 | -0.032043 | 0.032043 | 0.13733 | 0.064087 | 0.16937 | 121.0602 | -0.11444 | -0.091553 | 121.1655 | 121.0785 | 121.0739 | 0.01831 | 0.013733 | 121.0236 | -0.054932 | -0.036622 | 121.1929 | 121.225 | 121.1197 | 0.20142 | 0.09613 | 0.10529 | -0.027466 | 0.16937 | 0.064086 | -0.050354 | 0.045776 | 121.0098 | 121.0693 | -0.064087 | -0.10071 | 121.0327 | 121.0876 | 121.0052 | 121.0556
3294.5469 | 121.2753 | -121.0556 | 0.086975 | 0.036468 | 0.014146 | -0.0318 | 0.033276 | -0.015703 | -0.028395 | -0.019615 | 0.008606 | -0.06272 | -0.00053825 | 0.031479 | -0.016445 | -0.011595 | -0.015674 | -0.032043 | -0.009155 | -0.036621 | -0.022888 | 0.10529 | 0.013733 | 0.013733 | 0.018311 | 0.064087 | -0.027466 | 0.022888 | 0.10986 | 0.009155 | 0.14191 | 121.019 | -0.09613 | -0.10986 | 121.1609 | 121.0693 | 121.0693 | 0.050354 | 0.050354 | 121.0281 | -0.022888 | -0.064087 | 121.1655 | 121.1975 | 121.0648 | 0.16937 | 0.036621 | 0.14191 | 0.013733 | 0.13733 | 0.050354 | 0.027466 | 0.091553 | 121.0464 | 121.1197 | -0.1236 | -0.11444 | 121.0327 | 121.0785 | 121.0236 | 121.0739
3296.2812 | 121.2479 | -121.0602 | 0.07782 | 0.028839 | 0.013078 | -0.032227 | 0.038189 | -0.016771 | -0.02989 | -0.02111 | 0.008606 | -0.060797 | -0.0016064 | 0.035325 | -0.01559 | -0.0086048 | -0.01076 | -0.032043 | -0.018311 | -0.027466 | -0.027466 | 0.11902 | 0.004578 | 0.018311 | 0.009155 | 0.036621 | -0.036621 | 0.032043 | 0.082397 | -0.009155 | 0.12817 | 121.0327 | -0.096131 | -0.10529 | 121.1792 | 121.0785 | 121.0648 | 0.045777 | 0.032044 | 121.0236 | -0.041199 | -0.045777 | 121.1426 | 121.1884 | 121.051 | 0.1648 | 0.027466 | 0.14649 | 0 | 0.11902 | 0.068664 | 0.009155 | 0.073242 | 121.0419 | 121.0968 | -0.10529 | -0.11444 | 121.0327 | 121.0922 | 121.0281 | 121.0693
3297.9844 | 121.3669 | -121.0648 | 0.059509 | 0.01358 | 0.015855 | -0.032868 | 0.03883 | -0.014422 | -0.027754 | -0.02111 | 0.0055542 | -0.06272 | 0.0018116 | 0.042161 | -0.013881 | -0.010314 | -0.015033 | -0.036621 | -0.045776 | -0.009155 | 0.013733 | 0.15106 | 0.036621 | 0.054932 | 0.07782 | 0.004578 | 0.004578 | 0.091553 | 0.16479 | 0.091553 | 0.21515 | 121.0556 | -0.10528 | -0.045776 | 121.2158 | 121.1197 | 121.1014 | 0.064087 | 0.045776 | 121.0693 | -0.054931 | 0.032044 | 121.2296 | 121.2799 | 121.1563 | 0.21057 | 0.086975 | 0.16022 | 0.022888 | 0.16022 | 0.086975 | -0.036621 | 0 | 121.019 | 121.0693 | -0.068664 | -0.054931 | 121.0785 | 121.1563 | 121.0281 | 121.1426
3299.7031 | 121.3531 | -121.0831 | 0.064087 | 0.02121 | 0.014573 | -0.033082 | 0.037335 | -0.015276 | -0.02754 | -0.023033 | 0.014709 | -0.063788 | 0.00031615 | 0.043442 | -0.013881 | -0.0077502 | -0.010547 | -0.004578 | -0.059509 | 0.004578 | 0.041199 | 0.17395 | 0.064087 | 0.073242 | 0.10529 | 0.032043 | -0.022888 | 0.10529 | 0.17395 | 0.082397 | 0.20599 | 121.0876 | -0.1236 | -0.022888 | 121.257 | 121.1563 | 121.1472 | 0.068664 | 0.059509 | 121.0602 | -0.032044 | 0.041199 | 121.257 | 121.2891 | 121.1655 | 0.22888 | 0.10528 | 0.16937 | 0.036621 | 0.19684 | 0.12817 | -0.064087 | 0.054931 | 121.0236 | 121.1151 | -0.059509 | -0.086975 | 121.1243 | 121.1884 | 121.0785 | 121.1884
3301.4688 | 121.3806 | -121.0968 | 0.07782 | 0.01358 | 0.013292 | -0.035859 | 0.03648 | -0.016131 | -0.030531 | -0.020897 | 0.011658 | -0.066565 | 0.00031615 | 0.031479 | -0.021572 | -0.008391 | -0.012042 | -0.064087 | -0.032043 | 0.009155 | -0.013733 | 0.13275 | 0.050354 | 0.041199 | 0.032043 | 0.009155 | -0.027466 | 0.054932 | 0.16022 | 0.086975 | 0.1831 | 121.106 | -0.10986 | -0.091553 | 121.2296 | 121.138 | 121.1472 | 0.032044 | 0.041199 | 121.0693 | -0.068665 | -0.022888 | 121.257 | 121.2799 | 121.1838 | 0.21057 | 0.11444 | 0.1236 | -0.022888 | 0.18768 | 0.082398 | -0.041198 | 0.036621 | 121.0648 | 121.106 | -0.068665 | -0.10529 | 121.0831 | 121.1517 | 121.0327 | 121.1288
3303.1875 | 121.4218 | -121.0968 | 0.054932 | 0.0059509 | 0.011155 | -0.032227 | 0.034344 | -0.017412 | -0.026686 | -0.024314 | 0.008606 | -0.065711 | -0.00096545 | 0.040879 | -0.019008 | -0.0096728 | -0.015246 | 0 | -0.050354 | 0.009155 | 0.036621 | 0.21057 | 0.10986 | 0.086975 | 0.10529 | 0.013733 | -0.018311 | 0.086975 | 0.20142 | 0.1236 | 0.18768 | 121.106 | -0.10529 | -0.018311 | 121.3074 | 121.1838 | 121.2067 | 0.07782 | 0.10071 | 121.0785 | -0.041199 | 0.032043 | 121.2982 | 121.2845 | 121.2204 | 0.20599 | 0.14191 | 0.20142 | 0.027466 | 0.21973 | 0.10529 | -0.059509 | 0.032044 | 121.0464 | 121.1105 | -0.045777 | -0.073243 | 121.1334 | 121.1838 | 121.0968 | 121.2021
3304.9531 | 121.3623 | -121.1563 | 0.10071 | 0.02121 | 0.015001 | -0.032441 | 0.036053 | -0.015062 | -0.02754 | -0.023674 | 0.008606 | -0.062506 | -0.00075185 | 0.026352 | -0.016445 | -0.0094592 | -0.012256 | -0.07782 | 0 | -0.032043 | -0.082397 | 0.036621 | -0.059509 | -0.032043 | -0.045776 | 0.045776 | -0.045776 | 0.013733 | 0.082397 | -0.009155 | 0.11902 | 121.1243 | -0.10071 | -0.18311 | 121.1929 | 121.1243 | 121.0968 | 0 | -0.027466 | 121.1105 | -0.054932 | -0.086975 | 121.2387 | 121.2753 | 121.1472 | 0.16479 | 0.036621 | 0.068664 | -0.050354 | 0.12817 | 0.059509 | 0.032043 | 0.091552 | 121.1563 | 121.2021 | -0.13275 | -0.14648 | 121.0739 | 121.17 | 121.0785 | 121.1105
3306.6562 | 121.4172 | -121.1426 | 0.082397 | 0.01358 | 0.01436 | -0.033082 | 0.038617 | -0.016344 | -0.028608 | -0.022819 | 0.0055542 | -0.064215 | 0.0011708 | 0.041306 | -0.015804 | -0.010955 | -0.01546 | -0.059509 | -0.022888 | -0.009155 | -0.027466 | 0.091553 | 0 | 0.009155 | 0.045776 | 0.027466 | -0.041199 | 0.073242 | 0.14648 | 0.068665 | 0.17853 | 121.1334 | -0.10528 | -0.10986 | 121.2341 | 121.1517 | 121.1426 | 0.01831 | 0.009155 | 121.1014 | -0.054931 | -0.009155 | 121.2891 | 121.3211 | 121.2112 | 0.21973 | 0.10986 | 0.10071 | -0.018311 | 0.18768 | 0.11444 | -0.013733 | 0.068665 | 121.1197 | 121.17 | -0.091552 | -0.1236 | 121.1151 | 121.2158 | 121.0831 | 121.1884
3308.3594 | 121.3531 | -121.1838 | 0.054932 | 0.028839 | 0.015214 | -0.032441 | 0.037762 | -0.017412 | -0.026045 | -0.022819 | 0.014709 | -0.061224 | -0.00096545 | 0.046006 | -0.01794 | -0.0075366 | -0.010974 | -0.013733 | -0.027466 | -0.009155 | 0.045776 | 0.16479 | 0.041199 | 0.045776 | 0.059509 | 0.013733 | -0.027466 | 0.050354 | 0.13275 | 0.059509 | 0.16022 | 121.1746 | -0.082398 | -0.009156 | 121.3486 | 121.2296 | 121.225 | 0.054931 | 0.050354 | 121.1563 | -0.041199 | -0.004578 | 121.3165 | 121.344 | 121.2433 | 0.18768 | 0.086975 | 0.17395 | 0.054931 | 0.16022 | 0.07782 | -0.018311 | 0.041199 | 121.1563 | 121.1975 | -0.064087 | -0.082398 | 121.2296 | 121.2341 | 121.17 | 121.2433
3310.0938 | 121.2982 | -121.2021 | 0.12817 | 0.01358 | 0.015855 | -0.03415 | 0.036267 | -0.014422 | -0.027967 | -0.021965 | 0.008606 | -0.061865 | 0.00031615 | 0.03447 | -0.021999 | -0.010741 | -0.017169 | -0.073242 | -0.009155 | -0.022888 | -0.073242 | 0.064087 | -0.036621 | -0.022888 | -0.064087 | 0.041199 | -0.054932 | -0.059509 | 0.050354 | -0.022888 | 0.073242 | 121.1792 | -0.13733 | -0.20142 | 121.2662 | 121.1792 | 121.1655 | 0 | -0.013733 | 121.1472 | -0.086975 | -0.18768 | 121.2524 | 121.2753 | 121.1792 | 0.12817 | 0.032044 | 0.086975 | -0.050354 | 0.10529 | -0.004577 | 0.013733 | 0.096131 | 121.1929 | 121.2433 | -0.15106 | -0.18311 | 121.1288 | 121.1426 | 121.1288 | 121.138
3311.7969 | 121.4264 | -121.1517 | 0.11444 | 0.02121 | 0.017137 | -0.033722 | 0.035626 | -0.018053 | -0.030104 | -0.019615 | 0.011658 | -0.064429 | -0.0028882 | 0.038102 | -0.018581 | -0.011595 | -0.011187 | -0.009155 | -0.068665 | 0.004578 | 0.045776 | 0.16937 | 0.086975 | 0.07782 | 0.050354 | 0.027466 | -0.018311 | 0.041199 | 0.14648 | 0.082397 | 0.16022 | 121.1563 | -0.18311 | -0.068665 | 121.3211 | 121.2296 | 121.2387 | 0.073242 | 0.082397 | 121.1334 | -0.086975 | -0.073242 | 121.2982 | 121.3119 | 121.2341 | 0.17853 | 0.10071 | 0.16479 | 0.041198 | 0.16479 | 0.05951 | -0.073243 | 0.045777 | 121.0831 | 121.1792 | -0.10986 | -0.13275 | 121.1975 | 121.1929 | 121.1426 | 121.2021
3313.5 | 121.4172 | -121.1838 | 0.09613 | 0.044098 | 0.015428 | -0.035004 | 0.039471 | -0.015276 | -0.029463 | -0.022605 | 0.011658 | -0.062933 | -0.00011105 | 0.029984 | -0.017085 | -0.012023 | -0.013965 | -0.054932 | 0 | -0.041199 | -0.032043 | 0.086975 | 0.009155 | 0 | 0 | 0.054932 | -0.050354 | 0.013733 | 0.10986 | 0.013733 | 0.12817 | 121.1426 | -0.09613 | -0.12817 | 121.2708 | 121.1838 | 121.1929 | 0.041199 | 0.050354 | 121.1334 | -0.041198 | -0.082397 | 121.2936 | 121.312 | 121.1975 | 0.17853 | 0.064087 | 0.12817 | 0.009156 | 0.16022 | 0.064087 | 0.041199 | 0.10529 | 121.1838 | 121.2387 | -0.13733 | -0.14648 | 121.1517 | 121.1975 | 121.1288 | 121.1838
3315.2188 | 121.3898 | -121.2112 | 0.10986 | 0.036468 | 0.013719 | -0.034363 | 0.037335 | -0.014422 | -0.027754 | -0.021324 | 0.014709 | -0.060584 | -0.00075185 | 0.031266 | -0.016872 | -0.0094592 | -0.012256 | -0.07782 | 0.018311 | -0.036621 | -0.073242 | 0.041199 | -0.013733 | -0.013733 | -0.082397 | 0.054932 | -0.068665 | -0.027466 | 0.068665 | -0.018311 | 0.10071 | 121.1746 | -0.091552 | -0.18311 | 121.2524 | 121.1975 | 121.1975 | 0.022888 | 0.022888 | 121.1426 | -0.054931 | -0.13733 | 121.2799 | 121.312 | 121.1929 | 0.16937 | 0.050354 | 0.07782 | -0.036621 | 0.13733 | 0.041199 | 0.054932 | 0.1236 | 121.2296 | 121.2662 | -0.14648 | -0.17853 | 121.138 | 121.1838 | 121.1334 | 121.1288
3316.9844 | 115.3519 | -72.7341 | 42.6773 | 0.01358 | 0.014573 | -0.033722 | 0.035412 | -0.017199 | -0.028395 | -0.020897 | 0.008606 | -0.064002 | 0.00031615 | 0.038315 | -0.016017 | -0.0092456 | -0.01076 | -0.027466 | -0.050354 | -0.013733 | 0.004578 | 0.1236 | 0.027466 | 0.036621 | 0.036621 | -0.013733 | -0.027466 | 0.045776 | 0.13275 | 0.045776 | 0.16937 | 72.7203 | -42.7277 | -42.6727 | 72.8577 | 72.7707 | 72.7615 | 0.050354 | 0.041199 | 72.7066 | -42.691 | -42.6315 | 72.8668 | 72.9034 | 72.7798 | 0.19684 | 0.073242 | 0.13733 | 0.018311 | 0.16022 | 0.073242 | -0.036621 | 0.013733 | 72.6837 | 72.7203 | -42.691 | -42.7048 | 72.7386 | 72.7798 | 72.7066 | 72.7707
3318.7031 | 120.7855 | -120.2545 | 0.068665 | 0.02121 | 0.012437 | -0.030518 | 0.034131 | -0.016985 | -0.029036 | -0.021537 | -0.003601 | -0.064215 | 0.0013844 | 0.03682 | -0.01794 | -0.011382 | -0.016528 | -0.059509 | -0.050354 | 0.18768 | 0.018311 | 0.12817 | 0.041199 | -0.022888 | 0.036621 | -0.26093 | 0.24719 | 0.045776 | 0.16937 | 0.07782 | 0.15106 | 120.4422 | -0.11902 | -0.050354 | 120.3827 | 120.2316 | 120.2957 | -0.21057 | -0.14648 | 120.5017 | -0.32959 | -0.022889 | 120.4239 | 120.4056 | 120.3323 | -0.09613 | -0.16937 | -0.059509 | -0.16937 | -0.077819 | -0.20142 | -0.23804 | -0.50812 | 120.2042 | 119.9936 | 0.11902 | 0.17853 | 120.2728 | 120.3003 | 120.195 | 120.2911
3320.4688 | 120.5109 | -119.87 | 0.17395 | 0.02121 | 0.013719 | -0.030091 | 0.037121 | -0.01848 | -0.028822 | -0.02111 | -0.11346 | -0.062292 | 0.0013844 | 0.040024 | -0.014949 | -0.0086048 | -0.015033 | -0.004578 | -0.059509 | 0.045776 | 0.059509 | 0.041199 | -0.11444 | -0.19684 | 0.09613 | -0.13275 | 0.27008 | 0.086975 | 0.11902 | -0.036621 | 0.082397 | 119.9158 | -0.23346 | -0.11444 | 119.9112 | 119.6732 | 119.7556 | -0.24261 | -0.16022 | 120.1401 | -0.3067 | -0.086975 | 119.989 | 119.9524 | 119.8334 | -0.18768 | -0.3067 | -0.004577 | 0.013733 | -0.15106 | -0.18311 | -0.10528 | -0.40283 | 119.8105 | 119.7372 | -0.12817 | 0.096131 | 119.9295 | 119.957 | 119.8654 | 119.9661
3322.1875 | 120.7672 | -120.4376 | 0.07782 | 0.01358 | 0.013292 | -0.029877 | 0.03648 | -0.015276 | -0.029249 | -0.020469 | -0.024963 | -0.065283 | 0.00010255 | 0.047501 | -0.018794 | -0.0086048 | -0.013965 | -0.045776 | -0.036621 | -0.004578 | -0.009155 | 0.1236 | 0.018311 | -0.041199 | 0.009155 | 0.013733 | 0.027466 | 0.050354 | 0.10071 | 0.050354 | 0.15564 | 120.433 | -0.11444 | -0.086975 | 120.5612 | 120.3964 | 120.4559 | -0.036621 | 0.022889 | 120.4651 | -0.064087 | -0.027466 | 120.5383 | 120.5933 | 120.488 | 0.12817 | 0.022888 | 0.12817 | -0.004577 | 0.073242 | 0.022888 | -0.032043 | -0.013733 | 120.401 | 120.4514 | -0.082398 | -0.050354 | 120.4285 | 120.488 | 120.3918 | 120.4468
3323.9531 | 120.8359 | -120.0806 | 0.36621 | 0.02121 | 0.013292 | -0.032441 | 0.037121 | -0.01784 | -0.030745 | -0.022392 | -0.18671 | -0.083441 | -0.00075185 | 0.062241 | -0.015804 | -0.0077502 | -0.013751 | -0.041199 | -0.013733 | -0.022888 | -0.013733 | 0.004578 | -0.20142 | -0.32044 | -0.58136 | -0.6134 | -0.6546 | -0.51727 | -0.44403 | -0.65002 | -0.62714 | 120.0577 | -0.37994 | -0.37994 | 120.0851 | 119.7601 | 119.8792 | -0.29755 | -0.17853 | 119.426 | -0.97961 | -0.88348 | 119.6365 | 119.4534 | 119.4305 | 0.027466 | 0.004578 | 0.027466 | 0.009155 | 0.21057 | 0.13733 | 0.009155 | 0.041199 | 120.0668 | 119.4672 | -0.3891 | -1.0208 | 120.0668 | 119.5633 | 120.0394 | 119.4992
3325.6562 | 120.5063 | -118.7714 | 1.561 | 0.02121 | 0.01436 | -0.033509 | 0.037549 | -0.014635 | -0.02989 | -0.024528 | -0.21112 | -0.35218 | 0.00031615 | 0.33077 | -0.018154 | -0.0092456 | -0.015033 | -0.082397 | -0.027466 | -0.022888 | -0.050354 | -0.018311 | -0.23804 | -0.37994 | -2.4582 | -2.4857 | -2.4582 | -2.4536 | -2.3117 | -2.5909 | -2.4582 | 118.7485 | -1.5884 | -1.6113 | 118.7531 | 118.3914 | 118.5333 | -0.35706 | -0.21515 | 116.3132 | -4.0466 | -4.0146 | 116.4597 | 116.3132 | 116.1804 | 0 | -0.13275 | 0.004577 | -0.027466 | 0.14648 | 0.004578 | -0.004578 | -0.027466 | 118.7439 | 116.2857 | -1.5839 | -4.0192 | 118.721 | 116.3177 | 118.689 | 116.3132
3327.3906 | 120.9045 | -120.5109 | 0.1236 | 0.01358 | 0.013292 | -0.033509 | 0.035626 | -0.01848 | -0.029676 | -0.021324 | 0.0055542 | -0.069128 | -0.00182 | 0.053483 | -0.018367 | -0.0092456 | -0.013324 | -0.045776 | -0.054932 | 0.009155 | -0.004578 | 0.12817 | 0.050354 | 0.064087 | -0.059509 | -0.086975 | -0.10071 | 0.013733 | 0.091553 | 0.022888 | 0.1236 | 120.52 | -0.17853 | -0.12817 | 120.639 | 120.575 | 120.5612 | 0.054932 | 0.041199 | 120.4102 | -0.21057 | -0.10986 | 120.6024 | 120.6345 | 120.5338 | 0.2243 | 0.1236 | 0.11902 | -0.013733 | 0.19226 | 0.11444 | -0.064087 | 0.013733 | 120.4559 | 120.4239 | -0.11444 | -0.2243 | 120.5063 | 120.5246 | 120.4651 | 120.4514
3329.0938 | 120.8908 | -120.6345 | 0.07782 | 0.02121 | 0.013078 | -0.033509 | 0.036694 | -0.017626 | -0.031813 | -0.022605 | 0.0055542 | -0.064856 | -0.0043834 | 0.03682 | -0.02029 | -0.010955 | -0.012042 | -0.004578 | -0.036621 | -0.004578 | 0.054932 | 0.20142 | 0.09613 | 0.091553 | 0.1236 | 0.013733 | -0.013733 | 0.091553 | 0.19684 | 0.11444 | 0.17853 | 120.6299 | -0.11444 | -0.022888 | 120.8359 | 120.726 | 120.7306 | 0.096131 | 0.10071 | 120.6207 | -0.064087 | 0.013733 | 120.8313 | 120.813 | 120.7489 | 0.19226 | 0.12817 | 0.20599 | 0.05951 | 0.21057 | 0.10529 | -0.032043 | 0.027466 | 120.5978 | 120.6482 | -0.082398 | -0.091553 | 120.6894 | 120.726 | 120.6299 | 120.7581
3330.8125 | 120.607 | -120.1035 | 0.39368 | 0.044098 | 0.015855 | -0.033509 | 0.035412 | -0.021471 | -0.030104 | -0.021751 | -0.034119 | -0.078528 | -0.0020336 | 0.030625 | -0.019008 | -0.010314 | -0.011187 | -0.050354 | 0.013733 | -0.018311 | -0.036621 | 0.022888 | -0.2655 | -0.064087 | -0.009155 | 0.027466 | -0.059509 | 0.013733 | 0.068665 | -0.15564 | 0.045776 | 120.0851 | -0.37994 | -0.4303 | 120.1263 | 120.0394 | 119.838 | -0.045776 | -0.24719 | 120.0439 | -0.36621 | -0.37994 | 120.1721 | 120.1492 | 119.9478 | 0.10528 | -0.096131 | 0.041199 | -0.01831 | 0.12817 | 0.073242 | 0.032044 | 0.086975 | 120.1172 | 120.1309 | -0.41199 | -0.45319 | 120.0668 | 120.1172 | 120.0531 | 120.0943
3332.5469 | 120.607 | -120.1859 | 0.37537 | 0.02121 | 0.014146 | -0.031373 | 0.03883 | -0.01549 | -0.029036 | -0.020042 | 0.017761 | -0.090704 | -0.0033154 | 0.065873 | -0.016017 | -0.010955 | -0.013324 | -0.045776 | -0.027466 | 0 | 0.004578 | 0.10986 | 0.027466 | 0.036621 | -0.45319 | -0.48523 | -0.54474 | -0.44403 | -0.36621 | -0.45319 | -0.34332 | 120.1859 | -0.40283 | -0.37079 | 120.2957 | 120.2225 | 120.2133 | 0.036621 | 0.027466 | 119.6411 | -0.86059 | -0.8194 | 119.8196 | 119.8425 | 119.7327 | 0.20142 | 0.091553 | 0.10986 | 0.004578 | 0.17853 | 0.10071 | -0.027466 | 0.05951 | 120.1584 | 119.7006 | -0.37537 | -0.9201 | 120.1904 | 119.7418 | 120.1401 | 119.7327
3334.25 | 120.7855 | -120.6116 | 0.1236 | 0.036468 | 0.015214 | -0.034363 | 0.038189 | -0.01848 | -0.029463 | -0.023246 | -0.076843 | -0.06272 | -0.00096545 | 0.039811 | -0.020717 | -0.012023 | -0.0094784 | -0.082397 | -0.004578 | -0.032043 | -0.082397 | 0.041199 | -0.022888 | -0.16022 | -0.068665 | 0.050354 | -0.059509 | -0.045776 | 0.054932 | -0.045776 | -0.013733 | 120.5795 | -0.12817 | -0.20599 | 120.6528 | 120.4514 | 120.5887 | -0.12817 | 0.009155 | 120.5521 | -0.073242 | -0.16937 | 120.6665 | 120.5978 | 120.5658 | 0.045776 | 0.013733 | 0.073242 | -0.050354 | 0.11444 | 0.013733 | 0.027465 | 0.10986 | 120.607 | 120.6619 | -0.15564 | -0.1831 | 120.5292 | 120.5658 | 120.5292 | 120.5429
3335.9844 | 120.7901 | -120.1172 | 0.4303 | 0.01358 | 0.015428 | -0.032868 | 0.038403 | -0.018908 | -0.028608 | -0.023246 | -0.20197 | -0.068915 | -0.0031018 | 0.034043 | -0.027553 | -0.012664 | -0.013751 | -0.004578 | -0.022888 | -0.032043 | -0.004578 | 0.10986 | -0.068665 | -0.36163 | 0.036621 | 0.050354 | -0.059509 | 0.036621 | 0.091553 | -0.013733 | -0.13733 | 120.0851 | -0.45319 | -0.43488 | 120.2271 | 119.7556 | 120.0485 | -0.32959 | -0.036622 | 120.0577 | -0.37994 | -0.39368 | 120.2087 | 119.9799 | 120.1035 | -0.07782 | 0.045776 | 0.14191 | 0.027465 | 0.15106 | 0.09613 | 0.009155 | 0.10986 | 120.0943 | 120.1675 | -0.46234 | -0.48981 | 120.1126 | 120.1538 | 120.1126 | 120.1538
3337.6875 | 120.6619 | -119.9661 | 0.67749 | 0.02121 | 0.015428 | -0.034363 | 0.03883 | -0.017199 | -0.028181 | -0.020683 | -0.1745 | -0.069556 | -0.00096545 | 0.033402 | -0.016017 | -0.010955 | -0.012896 | -0.054932 | 0 | -0.027466 | -0.07782 | 0.022888 | -0.10071 | -0.32959 | -0.1831 | -0.041199 | -0.13733 | -0.10071 | -0.073242 | -0.15106 | -0.11444 | 119.9387 | -0.67749 | -0.75531 | 119.989 | 119.6365 | 119.8654 | -0.30212 | -0.073242 | 119.8288 | -0.71869 | -0.7782 | 119.8929 | 119.8517 | 119.8151 | 0.022888 | -0.013733 | 0.050354 | -0.050354 | 0.064087 | 0.036621 | 0.027466 | 0.09613 | 119.9661 | 119.9249 | -0.70496 | -0.81482 | 119.8883 | 119.8654 | 119.9112 | 119.783
3339.4375 | 120.9503 | -120.5841 | 0.068665 | 0.0059509 | 0.012224 | -0.034363 | 0.033063 | -0.012713 | -0.029676 | -0.021965 | 0.008606 | -0.063788 | -0.0026744 | 0.037461 | -0.016872 | -0.0079638 | -0.013751 | -0.009155 | -0.050354 | 0.004578 | 0.041199 | 0.21515 | 0.10071 | 0.10071 | 0.12817 | 0 | -0.009155 | 0.11902 | 0.21057 | 0.11902 | 0.19226 | 120.5887 | -0.11902 | -0.027466 | 120.7993 | 120.6848 | 120.6848 | 0.09613 | 0.09613 | 120.575 | -0.068665 | 0.050354 | 120.7947 | 120.7764 | 120.7031 | 0.20142 | 0.12817 | 0.21057 | 0.036621 | 0.21973 | 0.12817 | -0.054932 | 0.009155 | 120.5338 | 120.5841 | -0.064087 | -0.07782 | 120.6253 | 120.7031 | 120.575 | 120.7123
3341.1562 | 120.845 | -120.4742 | 0.27466 | 0.044098 | 0.014573 | -0.033936 | 0.037549 | -0.017412 | -0.02989 | -0.019188 | -0.049377 | -0.064642 | -0.00053825 | 0.039597 | -0.017299 | -0.0094592 | -0.0092648 | -0.064087 | 0 | -0.041199 | -0.054932 | 0.050354 | 0 | -0.082397 | -0.054932 | 0.050354 | -0.050354 | 0.009155 | 0.082397 | -0.004578 | 0.11444 | 120.433 | -0.27466 | -0.32959 | 120.5246 | 120.3918 | 120.4742 | -0.041198 | 0.041199 | 120.4239 | -0.2243 | -0.2655 | 120.5566 | 120.5887 | 120.4697 | 0.16479 | 0.045776 | 0.091553 | -0.013733 | 0.13275 | 0.059509 | 0.041199 | 0.10071 | 120.4742 | 120.5246 | -0.31586 | -0.32501 | 120.4193 | 120.4834 | 120.4102 | 120.4193
3342.9219 | 120.9869 | -120.7169 | 0.059509 | 0.028839 | 0.011369 | -0.034363 | 0.037121 | -0.016344 | -0.027113 | -0.023887 | 0.008606 | -0.064002 | 0.00031615 | 0.042374 | -0.016445 | -0.010314 | -0.011828 | -0.045776 | -0.032043 | -0.009155 | -0.022888 | 0.10529 | 0.022888 | 0.027466 | -0.009155 | 0.036621 | -0.036621 | 0.041199 | 0.12817 | 0.027466 | 0.14191 | 120.7077 | -0.091552 | -0.082397 | 120.8221 | 120.7443 | 120.7397 | 0.036621 | 0.032043 | 120.6802 | -0.022888 | -0.01831 | 120.845 | 120.8588 | 120.7443 | 0.17853 | 0.064087 | 0.11444 | -0.013733 | 0.1648 | 0.07782 | -0.022888 | 0.073242 | 120.6848 | 120.7535 | -0.068664 | -0.09613 | 120.694 | 120.7581 | 120.6711 | 120.7077
3344.6406 | 120.9137 | -120.7672 | 0.068665 | 0.01358 | 0.015428 | -0.034363 | 0.037121 | -0.016131 | -0.028822 | -0.025596 | 0.014709 | -0.064215 | -0.0024608 | 0.036179 | -0.017085 | -0.0088184 | -0.013965 | -0.009155 | -0.041199 | -0.004578 | 0.064087 | 0.21057 | 0.09613 | 0.10071 | 0.10071 | 0.018311 | -0.004578 | 0.082397 | 0.1831 | 0.10529 | 0.16937 | 120.7626 | -0.10986 | -0.004578 | 120.9778 | 120.8679 | 120.8633 | 0.10529 | 0.10071 | 120.7626 | -0.050354 | 0.013732 | 120.9503 | 120.9366 | 120.8725 | 0.17395 | 0.10986 | 0.21515 | 0.068665 | 0.18768 | 0.086975 | -0.036621 | 0.022889 | 120.726 | 120.7855 | -0.073243 | -0.073243 | 120.8313 | 120.8496 | 120.7581 | 120.8679
3346.3594 | 120.8954 | -120.0485 | 0.65918 | 0.01358 | 0.015001 | -0.03415 | 0.037762 | -0.022539 | -0.027113 | -0.026237 | 0.008606 | -0.064215 | -0.0024608 | 0.038743 | -0.021999 | -0.011809 | -0.013324 | 0.009155 | -0.064087 | 0.009155 | 0.041199 | 0.16937 | 0.091553 | 0.073242 | 0.050354 | 0.027466 | -0.032043 | 0.032043 | 0.13275 | 0.054932 | 0.14648 | 120.0577 | -0.72327 | -0.61798 | 120.2179 | 120.1218 | 120.1401 | 0.064087 | 0.082398 | 120.0165 | -0.63171 | -0.62714 | 120.1813 | 120.195 | 120.1035 | 0.17853 | 0.086975 | 0.16022 | 0.032044 | 0.16479 | 0.064086 | -0.073242 | 0.059509 | 119.9844 | 120.076 | -0.65002 | -0.69122 | 120.0897 | 120.0806 | 120.0577 | 120.0989
3348.0938 | 120.7535 | -120.7764 | 0.073242 | 0.01358 | 0.014146 | -0.034577 | 0.036267 | -0.015703 | -0.028822 | -0.021965 | 0.011658 | -0.066351 | -0.0048108 | 0.047715 | -0.017513 | -0.010314 | -0.014392 | 0 | -0.045776 | 0.022888 | 0.054932 | 0.20599 | 0.10986 | 0.10071 | 0.10071 | 0.022888 | -0.013733 | 0.09613 | 0.19684 | 0.09613 | 0.19226 | 120.7993 | -0.11902 | -0.01831 | 120.9824 | 120.8771 | 120.8862 | 0.07782 | 0.086975 | 120.7626 | -0.050354 | 0.022888 | 120.9732 | 120.9686 | 120.8725 | 0.20599 | 0.10986 | 0.18311 | 0.032044 | 0.21057 | 0.10986 | -0.068664 | 0.036621 | 120.7306 | 120.7993 | -0.050354 | -0.086975 | 120.8313 | 120.8725 | 120.7764 | 120.8771
3349.8125 | 116.2628 | -82.8964 | 33.0368 | 0.02121 | 0.013719 | -0.03415 | 0.035199 | -0.018267 | -0.02989 | -0.020683 | 0.008606 | -0.056525 | -0.0020336 | 0.037247 | -0.018154 | -0.0096728 | -0.012469 | -0.013733 | -0.068665 | -0.009155 | 0.054932 | 0.1831 | 0.073242 | 0.07782 | -0.30212 | -0.37537 | -0.43488 | -0.30212 | -0.17395 | -0.26093 | -0.1831 | 82.8873 | -33.1055 | -32.9819 | 83.0795 | 82.9742 | 82.9697 | 0.086975 | 0.082397 | 82.4615 | -33.4122 | -33.3389 | 82.7225 | 82.7133 | 82.6355 | 0.25177 | 0.17395 | 0.19226 | 0.064087 | 0.26093 | 0.13275 | -0.05951 | 0.059509 | 82.8278 | 82.5211 | -33.046 | -33.4717 | 82.9514 | 82.5943 | 82.8827 | 82.5943
3351.5312 | 120.6848 | -120.1492 | 0.24261 | 0.01358 | 0.015641 | -0.033509 | 0.039044 | -0.013353 | -0.027754 | -0.022178 | 0.0055542 | -0.060584 | -0.00032465 | 0.02913 | -0.014308 | -0.0088184 | -0.008624 | -0.073242 | -0.009155 | -0.018311 | -0.091553 | 0.009155 | -0.086975 | -0.059509 | -0.086975 | 0.036621 | -0.036621 | -0.018311 | 0.009155 | -0.059509 | 0.068665 | 120.1309 | -0.25177 | -0.33417 | 120.1584 | 120.0897 | 120.0623 | -0.041198 | -0.068664 | 120.1126 | -0.20599 | -0.26093 | 120.1584 | 120.2179 | 120.0897 | 0.10529 | -0.022888 | 0.027466 | -0.073242 | 0.045776 | 0.01831 | 0.009156 | 0.073242 | 120.1401 | 120.1859 | -0.26093 | -0.27924 | 120.0577 | 120.1309 | 120.076 | 120.0623
3353.25 | 120.163 | -119.8654 | 0.10529 | 0.01358 | 0.014787 | -0.031159 | 0.039898 | -0.013567 | -0.027327 | -0.023246 | 0.008606 | -0.060156 | -0.00096545 | 0.035966 | -0.015377 | -0.010527 | -0.013324 | -0.082397 | -0.004578 | -0.036621 | -0.09613 | 0.022888 | -0.07782 | -0.032043 | -0.050354 | 0.032043 | -0.041199 | 0.013733 | 0.045776 | -0.036621 | 0.091553 | 119.8288 | -0.10986 | -0.20142 | 119.8883 | 119.8334 | 119.7876 | 0.004578 | -0.041199 | 119.8242 | -0.073243 | -0.091553 | 119.9112 | 119.957 | 119.8288 | 0.13275 | 0.004578 | 0.059509 | -0.059509 | 0.086975 | 0.054932 | 0.032043 | 0.073242 | 119.8608 | 119.8975 | -0.14191 | -0.14649 | 119.7693 | 119.8791 | 119.783 | 119.8151
3355 | 120.5566 | -120.1721 | 0.086975 | 0.02121 | 0.013505 | -0.034363 | 0.036908 | -0.017412 | -0.028608 | -0.022819 | 0.011658 | -0.061651 | -0.0016064 | 0.039811 | -0.019435 | -0.008391 | -0.015887 | -0.004578 | -0.059509 | 0.004578 | 0.064087 | 0.21973 | 0.11444 | 0.1236 | 0.1236 | 0.004578 | -0.013733 | 0.091553 | 0.19684 | 0.13275 | 0.18768 | 120.1767 | -0.14648 | -0.022888 | 120.3918 | 120.2957 | 120.2866 | 0.11902 | 0.10986 | 120.1584 | -0.082397 | 0.004578 | 120.369 | 120.3598 | 120.3049 | 0.20142 | 0.14648 | 0.21515 | 0.059509 | 0.21057 | 0.10529 | -0.064087 | 0.018311 | 120.1126 | 120.1767 | -0.082397 | -0.10071 | 120.2362 | 120.2637 | 120.1675 | 120.2957
3356.7031 | 120.639 | -120.4422 | 0.07782 | 0.01358 | 0.014787 | -0.033509 | 0.036694 | -0.015062 | -0.031172 | -0.019401 | 0.008606 | -0.060156 | 0.0013844 | 0.030411 | -0.020503 | -0.010955 | -0.015887 | -0.07782 | -0.022888 | -0.018311 | -0.064087 | 0.068665 | -0.027466 | -0.013733 | -0.064087 | 0.036621 | -0.041199 | -0.022888 | 0.036621 | -0.018311 | 0.073242 | 120.4239 | -0.10071 | -0.14191 | 120.5109 | 120.4285 | 120.4147 | 0.004578 | -0.009155 | 120.401 | -0.041199 | -0.10071 | 120.4788 | 120.5154 | 120.4239 | 0.11444 | 0.022888 | 0.086976 | -0.045776 | 0.07782 | 0.018311 | -0.004577 | 0.07782 | 120.4193 | 120.4788 | -0.096131 | -0.11902 | 120.3781 | 120.4193 | 120.3644 | 120.3781
3358.4062 | 120.6665 | -120.4605 | 0.068665 | 0.036468 | 0.015428 | -0.032654 | 0.035412 | -0.018267 | -0.028181 | -0.022819 | 0.008606 | -0.059729 | -0.00075185 | 0.034897 | -0.019222 | -0.0098864 | -0.013324 | -0.036621 | -0.009155 | -0.027466 | -0.032043 | 0.09613 | 0.013733 | 0.013733 | 0.004578 | 0.027466 | -0.036621 | 0.022888 | 0.091553 | 0.013733 | 0.12817 | 120.433 | -0.07782 | -0.10071 | 120.5566 | 120.4742 | 120.4742 | 0.041199 | 0.041199 | 120.4239 | -0.041199 | -0.045777 | 120.5521 | 120.5887 | 120.4742 | 0.1648 | 0.050354 | 0.1236 | -0.004577 | 0.12817 | 0.059509 | 0.018311 | 0.064087 | 120.4514 | 120.488 | -0.096131 | -0.10529 | 120.4285 | 120.4834 | 120.4239 | 120.4651
3360.125 | 120.7626 | -120.5017 | 0.073242 | 0.01358 | 0.014146 | -0.032227 | 0.037121 | -0.021471 | -0.030104 | -0.022605 | 0.008606 | -0.062079 | -0.0013928 | 0.043015 | -0.017513 | -0.0098864 | -0.01311 | -0.050354 | -0.027466 | -0.013733 | -0.022888 | 0.11902 | 0.045776 | 0.045776 | -0.004578 | 0.018311 | -0.041199 | 0.068665 | 0.15564 | 0.068665 | 0.14648 | 120.488 | -0.10071 | -0.09613 | 120.6207 | 120.5475 | 120.5475 | 0.059509 | 0.059509 | 120.4605 | -0.054931 | -0.004577 | 120.6573 | 120.6482 | 120.5704 | 0.18768 | 0.10986 | 0.13275 | -0.009155 | 0.19684 | 0.10986 | -0.013733 | 0.05951 | 120.4742 | 120.52 | -0.086975 | -0.11444 | 120.4788 | 120.5704 | 120.4514 | 120.4971
3361.8281 | 120.7901 | -120.5292 | 0.086975 | 0.0059509 | 0.013933 | -0.033295 | 0.034772 | -0.01784 | -0.02754 | -0.021751 | 0.0055542 | -0.062933 | -0.0022472 | 0.035325 | -0.018154 | -0.0094592 | -0.012256 | -0.054932 | -0.036621 | 0.009155 | -0.018311 | 0.10986 | 0.009155 | 0.027466 | 0.009155 | 0.009155 | -0.036621 | 0.045776 | 0.11444 | 0.045776 | 0.14648 | 120.5383 | -0.1236 | -0.10529 | 120.639 | 120.5566 | 120.5383 | 0.018311 | 0 | 120.4926 | -0.07782 | -0.041199 | 120.6436 | 120.6757 | 120.575 | 0.18311 | 0.082397 | 0.10071 | -0.027466 | 0.15106 | 0.082397 | -0.045776 | 0.045776 | 120.4926 | 120.5383 | -0.07782 | -0.1236 | 120.5109 | 120.575 | 120.4742 | 120.5383
3363.5469 | 120.7123 | -120.2866 | 0.33417 | 0.036468 | 0.017564 | -0.033082 | 0.037121 | -0.01314 | -0.026045 | -0.024314 | 0.0055542 | -0.059088 | 0.00074335 | 0.033616 | -0.017513 | -0.011595 | -0.012683 | -0.013733 | -0.018311 | -0.022888 | -0.022888 | 0.091553 | -0.009155 | 0 | 0.018311 | 0.032043 | -0.027466 | 0.018311 | 0.10071 | -0.013733 | 0.10071 | 120.2637 | -0.35248 | -0.35706 | 120.3781 | 120.2866 | 120.2774 | 0.022888 | 0.013733 | 120.2591 | -0.30212 | -0.31586 | 120.3873 | 120.3873 | 120.2728 | 0.12817 | 0.013733 | 0.11444 | 0 | 0.12817 | 0.045777 | 0.004577 | 0.059509 | 120.2682 | 120.3186 | -0.35706 | -0.36163 | 120.2637 | 120.3049 | 120.2728 | 120.3049
3365.2812 | 119.7784 | -119.2474 | 0.21515 | 0.0059509 | 0.013505 | -0.030732 | 0.035412 | -0.01848 | -0.028395 | -0.023033 | 0.008606 | -0.060797 | 0.00074335 | 0.035752 | -0.017299 | -0.0094592 | -0.010119 | -0.064087 | -0.027466 | -0.004578 | -0.022888 | 0.10071 | 0.022888 | 0.022888 | -0.045776 | -0.018311 | -0.091553 | 0.009155 | 0.07782 | 0.013733 | 0.10529 | 119.2429 | -0.24261 | -0.23804 | 119.3481 | 119.2703 | 119.2703 | 0.027466 | 0.027466 | 119.1559 | -0.23346 | -0.20599 | 119.3253 | 119.3527 | 119.2612 | 0.19684 | 0.10529 | 0.10529 | -0.01831 | 0.16937 | 0.10071 | -0.022888 | 0.073242 | 119.22 | 119.2291 | -0.21973 | -0.3067 | 119.2245 | 119.2566 | 119.1834 | 119.2017
3366.9844 | 120.1492 | -119.8151 | 0.18768 | 0.0059509 | 0.013078 | -0.031159 | 0.036908 | -0.017626 | -0.030745 | -0.021965 | 0.011658 | -0.062506 | -0.0013928 | 0.038102 | -0.019435 | -0.0096728 | -0.013751 | -0.022888 | -0.059509 | -0.004578 | 0.050354 | 0.17853 | 0.091553 | 0.082397 | 0.054932 | 0.009155 | -0.004578 | 0.064087 | 0.15106 | 0.073242 | 0.16479 | 119.8105 | -0.24719 | -0.13733 | 119.9936 | 119.8975 | 119.9066 | 0.086975 | 0.096131 | 119.8105 | -0.17853 | -0.1236 | 119.9661 | 119.9799 | 119.8883 | 0.16937 | 0.07782 | 0.18311 | 0.054932 | 0.15564 | 0.068665 | -0.054931 | 0.013733 | 119.7556 | 119.8242 | -0.19226 | -0.19226 | 119.8654 | 119.8791 | 119.7922 | 119.87
3368.7188 | 120.2362 | -120.0073 | 0.14191 | 0.01358 | 0.014146 | -0.0318 | 0.037976 | -0.014635 | -0.027754 | -0.022178 | 0.014709 | -0.061224 | -0.0016064 | 0.023362 | -0.016658 | -0.0086048 | -0.016528 | -0.009155 | -0.018311 | -0.018311 | -0.013733 | 0.10071 | 0.004578 | 0.022888 | 0.013733 | 0.027466 | -0.032043 | 0.032043 | 0.086975 | 0.009155 | 0.1236 | 119.989 | -0.16022 | -0.15564 | 120.108 | 120.0302 | 120.0119 | 0.041199 | 0.022889 | 119.9753 | -0.11444 | -0.10986 | 120.0943 | 120.1309 | 120.0165 | 0.15564 | 0.041198 | 0.11902 | 0.004578 | 0.11902 | 0.064086 | 0 | 0.059509 | 119.989 | 120.0348 | -0.16022 | -0.17395 | 119.9936 | 120.0394 | 119.9982 | 120.0211
3370.4531 | 120.2499 | -119.9295 | 0.27008 | 0.028839 | 0.017137 | -0.0318 | 0.038403 | -0.018267 | -0.029676 | -0.021537 | 0.011658 | -0.057379 | -0.0043834 | 0.034897 | -0.018367 | -0.010955 | -0.011401 | -0.032043 | -0.009155 | -0.032043 | -0.032043 | 0.09613 | -0.004578 | -0.009155 | -0.004578 | 0.041199 | -0.036621 | 0.022888 | 0.07782 | -0.018311 | 0.10071 | 119.8975 | -0.27924 | -0.30212 | 120.0256 | 119.9203 | 119.9249 | 0.022888 | 0.027465 | 119.8929 | -0.22888 | -0.24719 | 120.0073 | 120.0302 | 119.9112 | 0.13733 | 0.01831 | 0.12817 | 0 | 0.11444 | 0.059509 | 0.022888 | 0.07782 | 119.9203 | 119.9707 | -0.30212 | -0.3067 | 119.8975 | 119.9524 | 119.8975 | 119.9249
3372.1719 | 120.1584 | -119.5358 | 0.45319 | 0.02121 | 0.014787 | -0.029236 | 0.037762 | -0.013994 | -0.027967 | -0.024314 | 0.011658 | -0.06037 | -0.00182 | 0.031479 | -0.016872 | -0.010955 | -0.012896 | -0.032043 | -0.032043 | -0.032043 | -0.022888 | 0.10986 | -0.004578 | -0.013733 | 0 | 0.036621 | -0.032043 | 0.032043 | 0.086975 | -0.004578 | 0.1236 | 119.5038 | -0.48523 | -0.47607 | 119.6457 | 119.5221 | 119.5312 | 0.01831 | 0.027465 | 119.5038 | -0.41656 | -0.42114 | 119.6228 | 119.6594 | 119.5312 | 0.15564 | 0.027465 | 0.14191 | 0.009155 | 0.11902 | 0.064086 | 0 | 0.068664 | 119.5038 | 119.5724 | -0.48523 | -0.48523 | 119.5129 | 119.5679 | 119.5038 | 119.5358
3373.875 | 120.3506 | -119.8929 | 0.32501 | 0.02121 | 0.015641 | -0.032654 | 0.037976 | -0.015062 | -0.029249 | -0.021324 | 0.011658 | -0.058661 | -0.0013928 | 0.02678 | -0.018581 | -0.011809 | -0.015674 | -0.032043 | -0.013733 | -0.018311 | -0.004578 | 0.11902 | 0.018311 | -0.004578 | 0.013733 | 0.036621 | -0.032043 | 0.036621 | 0.11444 | 0.009155 | 0.1236 | 119.8746 | -0.33875 | -0.32959 | 120.0119 | 119.8883 | 119.9112 | 0.013733 | 0.036622 | 119.8608 | -0.28839 | -0.28839 | 120.0073 | 120.0165 | 119.902 | 0.15564 | 0.041198 | 0.13733 | 0.013733 | 0.14648 | 0.068664 | 0.004578 | 0.068664 | 119.8791 | 119.9295 | -0.34332 | -0.35706 | 119.8883 | 119.9295 | 119.8608 | 119.9066
3375.6094 | 120.488 | -120.1859 | 0.068665 | 0.01358 | 0.013505 | -0.032868 | 0.035626 | -0.019976 | -0.028608 | -0.022392 | 0.011658 | -0.061224 | -0.0011792 | 0.036179 | -0.017085 | -0.010527 | -0.012896 | -0.050354 | -0.050354 | -0.013733 | -0.022888 | 0.11902 | 0.013733 | 0.027466 | -0.009155 | 0.027466 | -0.027466 | 0.032043 | 0.11444 | 0.041199 | 0.15106 | 120.1721 | -0.11902 | -0.091553 | 120.3049 | 120.2133 | 120.1996 | 0.041199 | 0.027466 | 120.1584 | -0.041199 | -0.036622 | 120.3003 | 120.3369 | 120.2271 | 0.17853 | 0.068665 | 0.13275 | -0.009155 | 0.14191 | 0.059509 | -0.036621 | 0.054932 | 120.1355 | 120.2133 | -0.082398 | -0.096131 | 120.163 | 120.2179 | 120.1355 | 120.1767
3377.3281 | 120.3918 | -120.0531 | 0.28839 | 0.01358 | 0.016496 | -0.035859 | 0.037335 | -0.013781 | -0.029036 | -0.020256 | 0.0055542 | -0.061011 | -0.00096545 | 0.036606 | -0.018154 | -0.010314 | -0.012683 | -0.073242 | -0.009155 | -0.018311 | -0.073242 | 0.059509 | -0.027466 | -0.009155 | -0.07782 | 0.064087 | -0.041199 | -0.018311 | 0.064087 | -0.013733 | 0.064087 | 120.0348 | -0.29755 | -0.36163 | 120.1126 | 120.0439 | 120.0256 | 0.009156 | -0.009155 | 120.0119 | -0.2243 | -0.3067 | 120.1172 | 120.1172 | 120.0394 | 0.10529 | 0.027466 | 0.07782 | -0.054931 | 0.10529 | 0.022888 | 0.009156 | 0.10529 | 120.0439 | 120.1172 | -0.3067 | -0.32959 | 119.9799 | 120.0348 | 119.9799 | 119.9753
3379.0469 | 120.5933 | -120.3186 | 0.050354 | 0.01358 | 0.013078 | -0.033509 | 0.034985 | -0.012499 | -0.029463 | -0.02111 | 0.0055542 | -0.062933 | -0.0026744 | 0.035111 | -0.016445 | -0.0094592 | -0.014392 | -0.054932 | -0.045776 | -0.004578 | 0 | 0.13733 | 0.045776 | 0.050354 | 0.032043 | 0.022888 | -0.013733 | 0.07782 | 0.16022 | 0.09613 | 0.19226 | 120.314 | -0.09613 | -0.050354 | 120.4559 | 120.369 | 120.3644 | 0.054932 | 0.050354 | 120.3049 | -0.027466 | 0.027466 | 120.4788 | 120.5109 | 120.4147 | 0.20599 | 0.10986 | 0.14191 | 0.004578 | 0.17395 | 0.091553 | -0.041198 | 0.036621 | 120.2728 | 120.3415 | -0.054932 | -0.064087 | 120.3186 | 120.3964 | 120.2637 | 120.3506
3380.75 | 120.5246 | -120.1355 | 0.068665 | 0.01358 | 0.013292 | -0.033509 | 0.036908 | -0.016985 | -0.030104 | -0.022819 | 0.014709 | -0.06272 | -0.0011792 | 0.036393 | -0.017085 | -0.010527 | -0.012896 | -0.022888 | -0.059509 | 0.013733 | 0.041199 | 0.21515 | 0.10071 | 0.09613 | 0.10986 | 0.004578 | -0.004578 | 0.10529 | 0.19684 | 0.12817 | 0.20599 | 120.1492 | -0.12817 | -0.027466 | 120.3506 | 120.2316 | 120.2362 | 0.082397 | 0.086975 | 120.1309 | -0.064087 | 0.036621 | 120.3323 | 120.3415 | 120.2637 | 0.21057 | 0.13275 | 0.20142 | 0.027466 | 0.20142 | 0.10986 | -0.073242 | 0.009156 | 120.076 | 120.1401 | -0.054932 | -0.073243 | 120.1767 | 120.2408 | 120.1126 | 120.2454
3382.4531 | 120.5383 | -120.3964 | 0.09613 | 0.01358 | 0.013933 | -0.035431 | 0.037335 | -0.022326 | -0.029249 | -0.021324 | 0.0055542 | -0.060584 | -0.00182 | 0.025925 | -0.020503 | -0.011809 | -0.012896 | -0.07782 | -0.018311 | -0.032043 | -0.068665 | 0.050354 | -0.018311 | -0.032043 | -0.050354 | 0.027466 | -0.032043 | -0.032043 | 0.054932 | -0.018311 | 0.068665 | 120.3644 | -0.11444 | -0.16479 | 120.4468 | 120.3644 | 120.3781 | 0 | 0.013732 | 120.3644 | -0.068664 | -0.12817 | 120.4514 | 120.4651 | 120.3781 | 0.10071 | 0.013732 | 0.082397 | -0.036622 | 0.086975 | 0 | 0.013732 | 0.059509 | 120.3781 | 120.4239 | -0.12817 | -0.12817 | 120.3278 | 120.3644 | 120.3186 | 120.3461
3384.1719 | 120.6573 | -120.369 | 0.054932 | 0.044098 | 0.012437 | -0.032227 | 0.034985 | -0.016771 | -0.026899 | -0.022819 | 0.014709 | -0.059943 | -0.0016064 | 0.035538 | -0.016231 | -0.0079638 | -0.014178 | -0.022888 | -0.054932 | 0.013733 | 0.054932 | 0.1831 | 0.050354 | 0.050354 | 0.086975 | 0.009155 | -0.041199 | 0.09613 | 0.14648 | 0.07782 | 0.16937 | 120.3827 | -0.10986 | 0 | 120.5521 | 120.4193 | 120.4193 | 0.036621 | 0.036621 | 120.3278 | -0.045777 | 0.041198 | 120.5154 | 120.5383 | 120.4468 | 0.21057 | 0.11902 | 0.16937 | 0.041199 | 0.18768 | 0.13733 | -0.068665 | 0.050354 | 120.314 | 120.3781 | -0.041199 | -0.096131 | 120.4239 | 120.4651 | 120.3461 | 120.4559
3385.8906 | 120.6345 | -120.4193 | 0.07782 | 0.028839 | 0.013292 | -0.033295 | 0.036267 | -0.019549 | -0.029463 | -0.021965 | 0.008606 | -0.058447 | -0.00053825 | 0.028702 | -0.01794 | -0.010314 | -0.013324 | -0.022888 | -0.018311 | -0.032043 | -0.022888 | 0.10529 | 0.009155 | 0.009155 | 0.018311 | 0.022888 | -0.041199 | 0.054932 | 0.11444 | 0.004578 | 0.13275 | 120.3873 | -0.096131 | -0.10071 | 120.5246 | 120.4285 | 120.4285 | 0.041198 | 0.041198 | 120.3781 | -0.054932 | -0.022888 | 120.5338 | 120.5521 | 120.4239 | 0.17395 | 0.045777 | 0.13733 | 0.009155 | 0.15564 | 0.096131 | 0.013732 | 0.064087 | 120.401 | 120.4422 | -0.10986 | -0.11902 | 120.3964 | 120.4742 | 120.3964 | 120.4376
3387.625 | 120.6436 | -120.4468 | 0.07782 | 0.01358 | 0.014573 | -0.032868 | 0.037335 | -0.021044 | -0.027327 | -0.022178 | 0.014709 | -0.059729 | -0.00053825 | 0.038529 | -0.015377 | -0.0081774 | -0.012469 | -0.086975 | -0.009155 | -0.032043 | -0.082397 | 0.022888 | -0.086975 | -0.036621 | -0.068665 | 0.041199 | -0.045776 | 0.009155 | 0.059509 | -0.036621 | 0.11444 | 120.4147 | -0.086975 | -0.16022 | 120.4697 | 120.4102 | 120.3598 | -0.004578 | -0.054932 | 120.401 | -0.036621 | -0.068665 | 120.5063 | 120.5612 | 120.4102 | 0.16022 | 0.009155 | 0.054931 | -0.050354 | 0.10528 | 0.054931 | 0.022888 | 0.086975 | 120.4376 | 120.488 | -0.10986 | -0.1236 | 120.3644 | 120.4559 | 120.3598 | 120.3781
3389.3906 | 120.5292 | -119.8196 | 0.5127 | 0.01358 | 0.016282 | -0.033295 | 0.035626 | -0.018053 | -0.030745 | -0.022819 | 0.008606 | -0.062506 | -0.0033154 | 0.033402 | -0.014949 | -0.0098864 | -0.015033 | -0.07782 | -0.004578 | -0.027466 | -0.027466 | 0.10071 | -0.027466 | -0.022888 | 0.004578 | 0.004578 | -0.022888 | 0.068665 | 0.13733 | 0.064087 | 0.17853 | 119.7922 | -0.51727 | -0.54016 | 119.9203 | 119.7968 | 119.7922 | 0.004578 | 0 | 119.7968 | -0.50812 | -0.44403 | 119.957 | 119.9982 | 119.8837 | 0.20142 | 0.086975 | 0.12817 | 0 | 0.16022 | 0.091553 | 0.022888 | 0.027466 | 119.8151 | 119.8242 | -0.54016 | -0.53558 | 119.7922 | 119.8883 | 119.7418 | 119.8242
3391.1094 | 120.5109 | -119.5312 | 0.85144 | 0.01358 | 0.01436 | -0.034363 | 0.037121 | -0.016344 | -0.027967 | -0.02346 | 0.0055542 | -0.060584 | -0.0022472 | 0.043442 | -0.017513 | -0.007323 | -0.0084104 | -0.059509 | -0.013733 | -0.022888 | -0.054932 | 0.054932 | -0.054932 | -0.041199 | -0.004578 | 0.022888 | -0.022888 | 0.054932 | 0.10529 | 0.018311 | 0.15106 | 119.5084 | -0.86517 | -0.90637 | 119.5862 | 119.4901 | 119.4763 | -0.018311 | -0.032044 | 119.5084 | -0.82855 | -0.79651 | 119.6365 | 119.6823 | 119.5496 | 0.17395 | 0.041199 | 0.07782 | -0.032044 | 0.12817 | 0.07782 | 0.009155 | 0.045776 | 119.5175 | 119.5541 | -0.87433 | -0.87433 | 119.4763 | 119.5862 | 119.4717 | 119.5267
3392.8281 | 120.7581 | -120.433 | 0.091553 | 0.02121 | 0.015214 | -0.033722 | 0.034985 | -0.016985 | -0.028395 | -0.021537 | 0.008606 | -0.061224 | 0.00031615 | 0.039597 | -0.018154 | -0.0092456 | -0.010547 | -0.050354 | -0.036621 | -0.013733 | -0.009155 | 0.12817 | 0.036621 | 0.041199 | 0.018311 | 0.022888 | -0.032043 | 0.027466 | 0.10986 | 0.068665 | 0.15564 | 120.4193 | -0.12817 | -0.10071 | 120.5612 | 120.4742 | 120.4697 | 0.054932 | 0.050354 | 120.401 | -0.068665 | -0.064087 | 120.5429 | 120.5887 | 120.5017 | 0.18768 | 0.10071 | 0.14191 | 0.004578 | 0.14191 | 0.059509 | -0.022888 | 0.054931 | 120.3964 | 120.4559 | -0.10529 | -0.1236 | 120.4239 | 120.4605 | 120.3827 | 120.4514
3394.5469 | 120.5383 | -119.4168 | 0.88806 | 0.028839 | 0.015001 | -0.032868 | 0.037335 | -0.015703 | -0.02754 | -0.024101 | 0.011658 | -0.061011 | -0.0033154 | 0.034684 | -0.01559 | -0.0088184 | -0.015887 | -0.064087 | -0.032043 | -0.036621 | -0.009155 | 0.091553 | -0.018311 | 0.013733 | 0.032043 | 0.013733 | -0.018311 | 0.086975 | 0.14648 | 0.07782 | 0.21057 | 119.3802 | -0.92011 | -0.89722 | 119.5084 | 119.4305 | 119.3985 | 0.050354 | 0.01831 | 119.3985 | -0.87433 | -0.80109 | 119.5633 | 119.6274 | 119.4946 | 0.22888 | 0.096131 | 0.12817 | 0.027466 | 0.16479 | 0.10529 | 0.004578 | 0.032044 | 119.3848 | 119.4305 | -0.92468 | -0.90637 | 119.4077 | 119.5038 | 119.3527 | 119.4489
3396.3125 | 120.7031 | -120.4056 | 0.082397 | 0.02121 | 0.012864 | -0.03415 | 0.036908 | -0.01314 | -0.029249 | -0.020042 | 0.0055542 | -0.060584 | 0.00031615 | 0.041092 | -0.017085 | -0.0101 | -0.013751 | -0.068665 | -0.009155 | -0.032043 | -0.041199 | 0.064087 | -0.027466 | -0.018311 | 0.013733 | 0.041199 | -0.013733 | 0.068665 | 0.11902 | 0.036621 | 0.16022 | 120.3735 | -0.091552 | -0.1236 | 120.4697 | 120.3873 | 120.3781 | 0.013732 | 0.004577 | 120.3918 | -0.041198 | -0.013732 | 120.5246 | 120.5658 | 120.4422 | 0.17395 | 0.050354 | 0.09613 | -0.009156 | 0.13275 | 0.082398 | 0.022888 | 0.054932 | 120.3964 | 120.4468 | -0.11444 | -0.09613 | 120.3644 | 120.4742 | 120.3369 | 120.4193
3398.0938 | 120.5521 | -119.8837 | 0.70953 | 0.01358 | 0.015428 | -0.032868 | 0.036908 | -0.019762 | -0.029036 | -0.018547 | 0.017761 | -0.06037 | 0.00095715 | 0.037034 | -0.020503 | -0.0096728 | -0.012896 | -0.11444 | 0 | -0.022888 | -0.086975 | 0.068665 | -0.013733 | -0.004578 | -0.07782 | 0.068665 | -0.073242 | -0.041199 | 0.050354 | -0.032043 | 0.086975 | 119.8608 | -0.70953 | -0.79651 | 119.9524 | 119.8792 | 119.87 | 0.01831 | 0.009155 | 119.8105 | -0.64087 | -0.75073 | 119.9341 | 119.9707 | 119.8517 | 0.16022 | 0.041199 | 0.091553 | -0.064087 | 0.1236 | 0.032043 | 0.022888 | 0.14191 | 119.8837 | 119.9524 | -0.73242 | -0.78278 | 119.7968 | 119.8425 | 119.7693 | 119.8059
3399.8438 | 120.8267 | -120.4788 | 0.10529 | 0.0059509 | 0.012651 | -0.033295 | 0.03349 | -0.016131 | -0.029249 | -0.024955 | 0.011658 | -0.063574 | -0.0013928 | 0.030839 | -0.019008 | -0.0101 | -0.012042 | -0.018311 | -0.059509 | 0.004578 | 0.068665 | 0.20599 | 0.10071 | 0.091553 | 0.064087 | 0.022888 | -0.004578 | 0.091553 | 0.18768 | 0.1236 | 0.19684 | 120.4834 | -0.16479 | -0.036621 | 120.6848 | 120.5704 | 120.5795 | 0.086975 | 0.09613 | 120.4742 | -0.082398 | -0.013733 | 120.6665 | 120.6757 | 120.6024 | 0.20142 | 0.12817 | 0.20142 | 0.064087 | 0.19226 | 0.096131 | -0.064087 | 0.027466 | 120.4193 | 120.5017 | -0.10071 | -0.10986 | 120.5475 | 120.5704 | 120.4605 | 120.5429
3401.6406 | 120.7718 | -120.5566 | 0.082397 | 0.02121 | 0.014787 | -0.032654 | 0.038617 | -0.015703 | -0.030104 | -0.020469 | 0.014709 | -0.059088 | 0.00031615 | 0.027848 | -0.016872 | -0.0096728 | -0.013324 | -0.013733 | -0.018311 | -0.009155 | -0.022888 | 0.10529 | 0.013733 | 0.004578 | 0.018311 | 0.050354 | -0.032043 | 0.018311 | 0.10529 | 0.022888 | 0.14648 | 120.5475 | -0.10071 | -0.10528 | 120.6619 | 120.5612 | 120.5704 | 0.013733 | 0.022888 | 120.5246 | -0.032043 | -0.064086 | 120.6619 | 120.7031 | 120.5795 | 0.17853 | 0.054931 | 0.11444 | -0.013733 | 0.13733 | 0.050354 | -0.009156 | 0.082397 | 120.5383 | 120.607 | -0.091552 | -0.11444 | 120.5338 | 120.575 | 120.5429 | 120.575
3403.4375 | 120.7947 | -120.6207 | 0.091553 | 0.028839 | 0.015001 | -0.033082 | 0.036267 | -0.016344 | -0.031172 | -0.024314 | 0.0055542 | -0.061224 | 0.0020252 | 0.032761 | -0.019863 | -0.011382 | -0.015033 | 0.004578 | -0.054932 | 0.018311 | 0.018311 | 0.15106 | 0.068665 | 0.059509 | 0.027466 | 0.032043 | -0.022888 | 0.013733 | 0.10529 | 0.032043 | 0.13733 | 120.639 | -0.14649 | -0.073242 | 120.7718 | 120.6802 | 120.6894 | 0.041198 | 0.050354 | 120.5978 | -0.05951 | -0.07782 | 120.726 | 120.7581 | 120.6528 | 0.16022 | 0.054931 | 0.13275 | 0 | 0.12817 | 0.036621 | -0.073243 | 0.054931 | 120.5658 | 120.6528 | -0.073242 | -0.11444 | 120.639 | 120.6345 | 120.6253 | 120.6482
3405.1875 | 120.7764 | -120.6619 | 0.086975 | 0.02121 | 0.013933 | -0.035218 | 0.035412 | -0.014422 | -0.030531 | -0.024101 | 0.011658 | -0.059302 | 0.0011708 | 0.028489 | -0.018794 | -0.012023 | -0.0099056 | -0.10529 | -0.004578 | -0.045776 | -0.068665 | 0.045776 | -0.013733 | -0.027466 | -0.059509 | 0.073242 | -0.068665 | -0.041199 | 0.036621 | -0.032043 | 0.10071 | 120.6161 | -0.091553 | -0.15564 | 120.7077 | 120.6345 | 120.6482 | 0.01831 | 0.032043 | 120.5933 | -0.013733 | -0.12817 | 120.6985 | 120.7626 | 120.6299 | 0.16937 | 0.036622 | 0.091552 | -0.022889 | 0.10529 | 0.027466 | 0.041198 | 0.14191 | 120.6573 | 120.7352 | -0.13275 | -0.15564 | 120.5933 | 120.6207 | 120.5566 | 120.6024
3406.9844 | 120.7535 | -120.3506 | 0.32501 | 0.028839 | 0.016282 | -0.034363 | 0.036267 | -0.017626 | -0.031385 | -0.021324 | 0.011658 | -0.057806 | -0.00011105 | 0.02913 | -0.018154 | -0.011382 | -0.012469 | -0.059509 | 0.013733 | -0.045776 | -0.091553 | 0.036621 | -0.013733 | -0.013733 | -0.068665 | 0.054932 | -0.073242 | -0.027466 | 0.054932 | -0.027466 | 0.10071 | 120.3049 | -0.31128 | -0.41657 | 120.3873 | 120.3369 | 120.3369 | 0.032043 | 0.032043 | 120.2774 | -0.27008 | -0.35248 | 120.4056 | 120.4514 | 120.3232 | 0.17395 | 0.045776 | 0.082397 | -0.045777 | 0.12817 | 0.045776 | 0.059509 | 0.12817 | 120.3644 | 120.4056 | -0.37079 | -0.39825 | 120.2591 | 120.3232 | 120.2911 | 120.282
3408.7812 | 120.9595 | -120.6116 | 0.082397 | 0.01358 | 0.013933 | -0.034577 | 0.032849 | -0.017412 | -0.028608 | -0.020683 | 0.0055542 | -0.062079 | -0.00096545 | 0.037888 | -0.017726 | -0.0098864 | -0.015246 | 0.009155 | -0.059509 | 0.013733 | 0.064087 | 0.21515 | 0.11444 | 0.082397 | 0.10071 | -0.004578 | -0.041199 | 0.10071 | 0.20599 | 0.13275 | 0.19684 | 120.6253 | -0.14191 | -0.01831 | 120.8267 | 120.694 | 120.726 | 0.068664 | 0.10071 | 120.5704 | -0.086975 | 0.018311 | 120.8176 | 120.8084 | 120.7443 | 0.23804 | 0.17395 | 0.20142 | 0.050354 | 0.24719 | 0.14191 | -0.073242 | 0.036621 | 120.5521 | 120.607 | -0.068664 | -0.1236 | 120.6757 | 120.7123 | 120.6207 | 120.7123
3410.5781 | 120.8588 | -120.6573 | 0.10986 | 0.01358 | 0.016496 | -0.031373 | 0.037335 | -0.011004 | -0.02989 | -0.023246 | 0.011658 | -0.057593 | -0.00182 | 0.032548 | -0.01559 | -0.0081774 | -0.014392 | -0.07782 | -0.018311 | -0.018311 | -0.091553 | 0.009155 | -0.082397 | -0.050354 | -0.086975 | 0.050354 | -0.050354 | -0.018311 | 0.013733 | -0.059509 | 0.091553 | 120.639 | -0.12817 | -0.20142 | 120.6665 | 120.607 | 120.575 | -0.032043 | -0.064086 | 120.607 | -0.059509 | -0.12817 | 120.6711 | 120.7489 | 120.5978 | 0.14191 | -0.009155 | 0.027466 | -0.073242 | 0.064087 | 0.032043 | 0 | 0.10071 | 120.639 | 120.7077 | -0.12817 | -0.16022 | 120.5658 | 120.639 | 120.5795 | 120.5704
3412.3125 | 120.9457 | -120.5612 | 0.14191 | 0.01358 | 0.013078 | -0.031373 | 0.036267 | -0.017412 | -0.027327 | -0.021537 | 0.008606 | -0.062506 | 0.00031615 | 0.038102 | -0.01324 | -0.0088184 | -0.013324 | -0.027466 | -0.041199 | 0.004578 | 0.022888 | 0.14648 | 0.054932 | 0.054932 | 0.073242 | 0.018311 | -0.013733 | 0.10986 | 0.16479 | 0.082397 | 0.20142 | 120.5658 | -0.18311 | -0.11902 | 120.7077 | 120.6161 | 120.6161 | 0.050354 | 0.050354 | 120.5475 | -0.1236 | -0.032044 | 120.726 | 120.7626 | 120.6436 | 0.21515 | 0.09613 | 0.14191 | 0.01831 | 0.17853 | 0.1236 | -0.045777 | 0.032044 | 120.52 | 120.5795 | -0.13733 | -0.15564 | 120.5841 | 120.6711 | 120.5338 | 120.6345
3414.0938 | 120.8633 | -120.7031 | 0.09613 | 0.028839 | 0.014146 | -0.033295 | 0.036694 | -0.012713 | -0.027754 | -0.021537 | 0.011658 | -0.060156 | -0.00053825 | 0.031907 | -0.017299 | -0.011168 | -0.015674 | -0.022888 | -0.013733 | -0.036621 | 0 | 0.10986 | 0.027466 | 0.032043 | 0.013733 | 0.036621 | -0.041199 | 0.045776 | 0.10986 | 0.018311 | 0.13275 | 120.6665 | -0.10986 | -0.09613 | 120.813 | 120.7352 | 120.7306 | 0.068664 | 0.064087 | 120.6619 | -0.059509 | -0.050354 | 120.813 | 120.8359 | 120.7214 | 0.17395 | 0.05951 | 0.14648 | 0.036621 | 0.15106 | 0.086975 | 0.022888 | 0.07782 | 120.6894 | 120.7397 | -0.13275 | -0.13733 | 120.7031 | 120.7489 | 120.6802 | 120.7169
3415.8125 | 120.8405 | -120.7031 | 0.11902 | 0.0059509 | 0.014573 | -0.032654 | 0.037121 | -0.01848 | -0.028822 | -0.020897 | 0.0055542 | -0.059088 | 0.00095715 | 0.033616 | -0.017726 | -0.0094592 | -0.013965 | -0.086975 | -0.018311 | -0.022888 | -0.10071 | 0.022888 | -0.068665 | -0.050354 | -0.073242 | 0.041199 | -0.032043 | -0.022888 | 0.027466 | -0.050354 | 0.11444 | 120.6802 | -0.13733 | -0.21973 | 120.726 | 120.6528 | 120.6345 | -0.027466 | -0.045777 | 120.6711 | -0.07782 | -0.14191 | 120.7306 | 120.8176 | 120.6528 | 0.14648 | -0.018311 | 0.045776 | -0.07782 | 0.059509 | 0.009155 | 0.004577 | 0.073242 | 120.6848 | 120.7443 | -0.14191 | -0.15106 | 120.6024 | 120.6802 | 120.6162 | 120.6299
3417.625 | 120.9137 | -120.7581 | 0.10529 | 0.0059509 | 0.014573 | -0.035004 | 0.036053 | -0.016558 | -0.030104 | -0.022605 | 0.008606 | -0.061438 | 0.00010255 | 0.02913 | -0.019008 | -0.010955 | -0.013324 | -0.022888 | -0.013733 | -0.009155 | -0.036621 | 0.07782 | -0.027466 | -0.018311 | -0.009155 | 0.050354 | -0.032043 | 0 | 0.050354 | -0.032043 | 0.091553 | 120.7489 | -0.11902 | -0.14191 | 120.8359 | 120.7397 | 120.7306 | -0.009156 | -0.018311 | 120.726 | -0.054932 | -0.10529 | 120.8084 | 120.8496 | 120.726 | 0.1236 | 0 | 0.086975 | -0.027466 | 0.082397 | 0.032043 | -0.004578 | 0.082397 | 120.7443 | 120.8084 | -0.11444 | -0.13733 | 120.7214 | 120.7581 | 120.7352 | 120.7489
3419.4219 | 121.0007 | -120.7626 | 0.054932 | 0.02121 | 0.014787 | -0.033082 | 0.036053 | -0.016558 | -0.029676 | -0.024101 | 0.011658 | -0.062292 | -0.00032465 | 0.038956 | -0.017085 | -0.0101 | -0.015887 | -0.045776 | -0.027466 | -0.004578 | -0.018311 | 0.12817 | 0.018311 | 0.022888 | -0.009155 | 0.013733 | -0.027466 | 0.036621 | 0.11902 | 0.059509 | 0.15564 | 120.7581 | -0.082398 | -0.073243 | 120.8908 | 120.7855 | 120.7809 | 0.027466 | 0.022889 | 120.7352 | -0.041199 | -0.018311 | 120.8817 | 120.9183 | 120.8221 | 0.18311 | 0.086975 | 0.13275 | -0.013733 | 0.14649 | 0.064087 | -0.022888 | 0.041199 | 120.7352 | 120.7764 | -0.05951 | -0.082398 | 120.7443 | 120.7993 | 120.7169 | 120.7535
3421.2188 | 119.8471 | -77.3666 | 42.3614 | 0.036468 | 0.015428 | -0.032868 | 0.037335 | -0.012072 | -0.028181 | -0.022819 | 0.011658 | -0.058875 | -0.00011105 | 0.030411 | -0.016445 | -0.010741 | -0.013324 | -0.086975 | -0.022888 | -0.045776 | -0.11444 | 0 | -0.091553 | -0.068665 | -0.091553 | 0.032043 | -0.050354 | -0.045776 | 0.022888 | -0.07782 | 0.073242 | 77.3209 | -42.3843 | -42.4759 | 77.3666 | 77.298 | 77.2751 | -0.022889 | -0.045777 | 77.3163 | -42.3294 | -42.4072 | 77.3895 | 77.4399 | 77.2888 | 0.1236 | -0.027466 | 0.045776 | -0.068665 | 0.073242 | 0.004578 | 0.022888 | 0.082397 | 77.3438 | 77.3987 | -42.4072 | -42.4118 | 77.2522 | 77.3209 | 77.2797 | 77.2751
3422.9375 | 120.7169 | -118.2266 | 2.0462 | 0.028839 | 0.015001 | -0.030945 | 0.034558 | -0.016985 | -0.025831 | -0.021324 | 0.011658 | -0.061438 | -0.00075185 | 0.040665 | -0.015377 | -0.0098864 | -0.012683 | -0.027466 | -0.050354 | 0.013733 | 0.064087 | 0.1831 | 0.059509 | 0.068665 | 0.07782 | 0.032043 | -0.018311 | 0.10529 | 0.13733 | 0.073242 | 0.16937 | 118.2404 | -2.0966 | -1.9821 | 118.4097 | 118.2953 | 118.2861 | 0.054932 | 0.045776 | 118.2083 | -2.0142 | -1.9409 | 118.364 | 118.396 | 118.2999 | 0.18768 | 0.091553 | 0.16937 | 0.050354 | 0.15564 | 0.1236 | -0.064087 | 0.050354 | 118.1763 | 118.2587 | -2.0325 | -2.0645 | 118.2907 | 118.3319 | 118.1992 | 118.3044
3424.7188 | 121.7606 | -67.5339 | 50.6516 | 0.02121 | 0.013719 | -0.032868 | 0.038403 | -0.014635 | -0.029036 | -0.018547 | 0.008606 | -0.05802 | -0.0026744 | 0.034043 | -0.019008 | -0.0086048 | -0.016314 | -0.064087 | -0.036621 | -0.013733 | -0.041199 | 0.091553 | -0.027466 | -0.022888 | -0.036621 | 0.018311 | -0.041199 | 0.013733 | 0.036621 | -0.050354 | 0.46234 | 67.5201 | -50.6882 | -50.6927 | 67.6254 | 67.511 | 67.5064 | -0.009155 | -0.013733 | 67.4927 | -50.6332 | -50.6378 | 67.5705 | 67.9962 | 67.4835 | 0.50354 | -0.009155 | 0.10529 | -0.027466 | 0.07782 | 0.054932 | -0.022888 | 0.05951 | 67.4973 | 67.5522 | -50.6653 | -50.6927 | 67.4927 | 67.5476 | 67.4698 | 67.4973
3426.4375 | 120.8588 | -119.3985 | 1.0941 | 0.02121 | 0.01436 | -0.028168 | 0.03584 | -0.015062 | -0.030104 | -0.021324 | 0.017761 | -0.061011 | -0.0020336 | 0.037461 | -0.017299 | -0.008391 | -0.01546 | -0.022888 | -0.036621 | 0.022888 | 0.050354 | 0.1831 | 0.050354 | 0.068665 | 0.10071 | 0 | -0.013733 | 0.10071 | 0.14191 | 0.068665 | 0.16479 | 119.4214 | -1.1307 | -1.0437 | 119.5816 | 119.4672 | 119.4489 | 0.045777 | 0.027466 | 119.3848 | -1.0941 | -0.99335 | 119.5404 | 119.5633 | 119.4672 | 0.17853 | 0.082398 | 0.16022 | 0.027466 | 0.15564 | 0.11444 | -0.059509 | 0.013733 | 119.3619 | 119.3985 | -1.0712 | -1.1078 | 119.4489 | 119.4992 | 119.3756 | 119.4992
3428.2188 | 120.8771 | -114.6652 | 4.3625 | 0.01358 | 0.01436 | -0.032227 | 0.035412 | -0.014635 | -0.031172 | -0.021965 | 0.011658 | -0.062292 | 0.00031615 | 0.033402 | -0.017299 | -0.0094592 | -0.013537 | -0.054932 | -0.050354 | 0.013733 | -0.009155 | 0.10986 | 0.004578 | 0.041199 | -0.004578 | 0 | -0.022888 | 0.064087 | 0.10529 | 0.045776 | 0.15564 | 114.679 | -4.4128 | -4.3716 | 114.7751 | 114.7064 | 114.6698 | 0.027466 | -0.009155 | 114.6423 | -4.3625 | -4.2984 | 114.7705 | 114.8209 | 114.711 | 0.17853 | 0.068664 | 0.09613 | -0.022888 | 0.12817 | 0.086975 | -0.064087 | 0.022888 | 114.6149 | 114.6652 | -4.3488 | -4.3854 | 114.6561 | 114.7293 | 114.6103 | 114.6606
3430.0156 | 120.8313 | -119.8929 | 0.84228 | 0.01358 | 0.01735 | -0.032868 | 0.038189 | -0.016985 | -0.029036 | -0.022178 | 0.011658 | -0.05802 | 0.00010255 | 0.031907 | -0.017085 | -0.0096728 | -0.013537 | -0.059509 | -0.009155 | -0.018311 | -0.07782 | 0.050354 | -0.045776 | -0.045776 | -0.054932 | 0.050354 | -0.032043 | 0.004578 | 0 | -0.050354 | 0.082397 | 119.8746 | -0.85144 | -0.9201 | 119.9432 | 119.8471 | 119.8471 | -0.027465 | -0.027465 | 119.8608 | -0.79193 | -0.83771 | 119.8929 | 119.9753 | 119.8425 | 0.11444 | -0.018311 | 0.068665 | -0.059509 | 0.032043 | 0.036621 | 0.009156 | 0.082397 | 119.8837 | 119.9432 | -0.8606 | -0.87433 | 119.8151 | 119.8975 | 119.8334 | 119.838
3431.7344 | 120.9457 | -119.8425 | 0.85144 | 0.036468 | 0.015641 | -0.032654 | 0.037121 | -0.018908 | -0.028822 | -0.021965 | 0.014709 | -0.060797 | -0.00075185 | 0.037034 | -0.016445 | -0.009032 | -0.013324 | 0.013733 | -0.036621 | 0.013733 | 0.054932 | 0.20599 | 0.064087 | 0.068665 | 0.09613 | 0.018311 | -0.009155 | 0.11902 | 0.16022 | 0.068665 | 0.1831 | 119.8563 | -0.88806 | -0.79651 | 120.0485 | 119.9112 | 119.9066 | 0.054932 | 0.050354 | 119.8334 | -0.83313 | -0.73242 | 120.0027 | 120.0256 | 119.9112 | 0.19226 | 0.07782 | 0.19226 | 0.041199 | 0.16937 | 0.12817 | -0.050354 | 0.027466 | 119.8059 | 119.8608 | -0.83771 | -0.86059 | 119.8975 | 119.9615 | 119.8563 | 119.9387
3433.5156 | 120.8817 | -120.0073 | 0.81482 | 0.028839 | 0.01436 | -0.035645 | 0.037549 | -0.012713 | -0.028822 | -0.020042 | 0.008606 | -0.059943 | 0.00074335 | 0.021012 | -0.018154 | -0.009032 | -0.012683 | -0.086975 | 0.013733 | -0.045776 | -0.07782 | 0.045776 | -0.022888 | -0.013733 | -0.07782 | 0.07782 | -0.059509 | -0.009155 | 0.059509 | -0.027466 | 0.091553 | 119.9615 | -0.80109 | -0.89264 | 120.0531 | 119.9936 | 119.9844 | 0.032043 | 0.022888 | 119.9478 | -0.737 | -0.82397 | 120.0668 | 120.0989 | 119.9799 | 0.15106 | 0.032043 | 0.091552 | -0.032044 | 0.11902 | 0.050354 | 0.059509 | 0.13733 | 120.0211 | 120.0851 | -0.86059 | -0.87433 | 119.9295 | 119.9982 | 119.9203 | 119.9295
3435.3125 | 120.9961 | -120.1035 | 0.63629 | 0.01358 | 0.012437 | -0.035004 | 0.034985 | -0.013781 | -0.028395 | -0.024314 | 0.008606 | -0.06272 | -0.0031018 | 0.038956 | -0.018794 | -0.0092456 | -0.0099056 | -0.027466 | -0.059509 | 0.013733 | 0.045776 | 0.18768 | 0.091553 | 0.10529 | 0.09613 | 0.013733 | -0.013733 | 0.10986 | 0.21057 | 0.1236 | 0.19684 | 120.1172 | -0.6958 | -0.59052 | 120.2911 | 120.2087 | 120.195 | 0.091553 | 0.07782 | 120.0897 | -0.62256 | -0.52643 | 120.314 | 120.3003 | 120.2271 | 0.21057 | 0.13733 | 0.17395 | 0.032043 | 0.2243 | 0.1236 | -0.073242 | 0.027466 | 120.0439 | 120.1172 | -0.62256 | -0.65002 | 120.1492 | 120.2133 | 120.076 | 120.1996
3437.0469 | 121.051 | -120.1401 | 0.61798 | 0.028839 | 0.01436 | -0.0318 | 0.034344 | -0.015062 | -0.026258 | -0.020897 | 0.014709 | -0.059515 | -0.0022472 | 0.033616 | -0.01324 | -0.0092456 | -0.012683 | 0.013733 | -0.050354 | 0.036621 | 0.050354 | 0.17853 | 0.054932 | 0.073242 | 0.11444 | 0.004578 | -0.004578 | 0.12817 | 0.18768 | 0.091553 | 0.20142 | 120.1767 | -0.66834 | -0.56763 | 120.3186 | 120.2133 | 120.195 | 0.036621 | 0.018311 | 120.1355 | -0.6134 | -0.48981 | 120.3278 | 120.3415 | 120.2316 | 0.20599 | 0.096131 | 0.14191 | 0.013733 | 0.19226 | 0.13275 | -0.086975 | 0.009156 | 120.0897 | 120.1447 | -0.58136 | -0.62256 | 120.1904 | 120.2682 | 120.1538 | 120.2545
3438.8281 | 121.0556 | -119.4946 | 1.2817 | 0.01358 | 0.012437 | -0.03415 | 0.03648 | -0.014208 | -0.029249 | -0.021324 | 0.0055542 | -0.063788 | -0.0016064 | 0.03447 | -0.020076 | -0.0079638 | -0.012469 | -0.013733 | -0.059509 | 0.004578 | 0.045776 | 0.21057 | 0.10529 | 0.07782 | 0.086975 | 0.018311 | -0.009155 | 0.10529 | 0.19684 | 0.09613 | 0.1831 | 119.4992 | -1.3412 | -1.236 | 119.7052 | 119.5724 | 119.5999 | 0.073242 | 0.10071 | 119.4855 | -1.2634 | -1.1765 | 119.6915 | 119.6777 | 119.5908 | 0.19226 | 0.10528 | 0.20599 | 0.041198 | 0.20599 | 0.11444 | -0.064087 | 0.027466 | 119.4351 | 119.5129 | -1.2772 | -1.2909 | 119.5404 | 119.5999 | 119.4809 | 119.5816
3440.5469 | 120.9961 | -120.3598 | 0.50812 | 0.028839 | 0.015641 | -0.035004 | 0.039044 | -0.015917 | -0.026686 | -0.020683 | 0.008606 | -0.059302 | 0.00074335 | 0.030625 | -0.018154 | -0.010955 | -0.014178 | -0.027466 | -0.009155 | -0.013733 | -0.009155 | 0.1236 | 0.013733 | 0 | 0 | 0.022888 | -0.032043 | 0.050354 | 0.10071 | 0.018311 | 0.14648 | 120.3461 | -0.51727 | -0.51727 | 120.4834 | 120.3598 | 120.3735 | 0.013733 | 0.027466 | 120.3278 | -0.48523 | -0.45776 | 120.4605 | 120.5063 | 120.3781 | 0.17853 | 0.050354 | 0.13733 | 0.004578 | 0.13275 | 0.082397 | 0.004578 | 0.054931 | 120.3506 | 120.3827 | -0.52185 | -0.54016 | 120.3506 | 120.4102 | 120.3323 | 120.3598
3442.2812 | 120.9549 | -119.0598 | 1.7212 | 0.0059509 | 0.01671 | -0.033509 | 0.034558 | -0.017199 | -0.028822 | -0.02111 | 0.008606 | -0.06272 | -0.00096545 | 0.037461 | -0.019435 | -0.0098864 | -0.013324 | -0.018311 | -0.054932 | -0.004578 | 0.013733 | 0.16022 | 0.082397 | 0.054932 | 0.018311 | 0.036621 | -0.022888 | 0.027466 | 0.10529 | 0.032043 | 0.11902 | 119.0552 | -1.7761 | -1.7075 | 119.22 | 119.1147 | 119.1422 | 0.05951 | 0.086975 | 119.0369 | -1.6846 | -1.6937 | 119.165 | 119.1788 | 119.0918 | 0.14191 | 0.054931 | 0.16479 | 0.018311 | 0.12817 | 0.050354 | -0.050354 | 0.059509 | 119.0048 | 119.0964 | -1.7258 | -1.7441 | 119.0735 | 119.0872 | 119.0414 | 119.0781
3444.0625 | 120.9824 | -120.4651 | 0.44861 | 0.02121 | 0.015428 | -0.032013 | 0.03584 | -0.014635 | -0.029463 | -0.022392 | 0.014709 | -0.06037 | -0.00011105 | 0.029557 | -0.020076 | -0.012664 | -0.013751 | -0.073242 | 0.009155 | -0.045776 | -0.082397 | 0.022888 | -0.013733 | -0.022888 | -0.082397 | 0.050354 | -0.054932 | -0.032043 | 0.059509 | -0.009155 | 0.091553 | 120.4193 | -0.43945 | -0.531 | 120.488 | 120.4422 | 120.4514 | 0.022888 | 0.032043 | 120.4102 | -0.39825 | -0.48065 | 120.5246 | 120.5566 | 120.4559 | 0.14649 | 0.045777 | 0.068664 | -0.036621 | 0.11444 | 0.022889 | 0.054931 | 0.10529 | 120.4742 | 120.5154 | -0.49438 | -0.50354 | 120.3827 | 120.433 | 120.3918 | 120.3827
3445.8438 | 120.9366 | -118.5196 | 2.4124 | 0.02121 | 0.015001 | -0.033722 | 0.039898 | -0.017412 | -0.028395 | -0.021965 | 0.008606 | -0.059515 | -0.00075185 | 0.033188 | -0.016658 | -0.007323 | -0.012256 | -0.068665 | 0 | -0.032043 | -0.11444 | 0.004578 | -0.073242 | -0.054932 | -0.086975 | 0.041199 | -0.059509 | -0.013733 | 0.032043 | -0.059509 | 0.10071 | 118.4875 | -2.4124 | -2.5269 | 118.5242 | 118.4647 | 118.4464 | -0.022889 | -0.041199 | 118.4601 | -2.3712 | -2.4261 | 118.5516 | 118.6203 | 118.4601 | 0.16022 | 0 | 0.036621 | -0.082398 | 0.091552 | 0.045776 | 0.032043 | 0.10071 | 118.5196 | 118.5608 | -2.4445 | -2.4719 | 118.4052 | 118.5059 | 118.4509 | 118.4326
3447.5938 | 121.1014 | -119.8654 | 1.0666 | 0.0059509 | 0.013078 | -0.035004 | 0.035626 | -0.014849 | -0.029463 | -0.021324 | 0.008606 | -0.06037 | -0.00075185 | 0.039597 | -0.017726 | -0.0092456 | -0.012896 | -0.004578 | -0.054932 | 0.013733 | 0.036621 | 0.17395 | 0.082397 | 0.064087 | 0.064087 | 0.022888 | -0.022888 | 0.045776 | 0.14648 | 0.059509 | 0.15564 | 119.8791 | -1.1215 | -1.03 | 120.0394 | 119.9295 | 119.9478 | 0.050354 | 0.068664 | 119.8425 | -1.0437 | -1.0208 | 120.0119 | 120.0211 | 119.9249 | 0.17853 | 0.082397 | 0.16022 | 0.022888 | 0.16937 | 0.068664 | -0.068665 | 0.045776 | 119.8105 | 119.8883 | -1.0529 | -1.0895 | 119.902 | 119.9112 | 119.8608 | 119.9295
3449.375 | 121.1197 | -120.3049 | 0.60883 | 0.01358 | 0.012651 | -0.033509 | 0.035412 | -0.017626 | -0.027967 | -0.022605 | 0.0055542 | -0.062506 | -0.00011105 | 0.035538 | -0.016658 | -0.010741 | -0.013965 | -0.045776 | -0.045776 | -0.009155 | 0.004578 | 0.13275 | 0.050354 | 0.059509 | 0.022888 | 0.027466 | -0.018311 | 0.073242 | 0.16022 | 0.10071 | 0.19226 | 120.2957 | -0.6546 | -0.60425 | 120.4376 | 120.3644 | 120.3552 | 0.068664 | 0.059509 | 120.2866 | -0.58136 | -0.53558 | 120.4651 | 120.4971 | 120.4056 | 0.21057 | 0.11902 | 0.14191 | 0.013733 | 0.17853 | 0.091553 | -0.036621 | 0.045777 | 120.2591 | 120.3323 | -0.61798 | -0.62714 | 120.3094 | 120.3781 | 120.2591 | 120.3278
3451.1719 | 121.0648 | -120.1172 | 0.82398 | 0.02121 | 0.013719 | -0.03415 | 0.035199 | -0.018053 | -0.029249 | -0.02346 | 0.0055542 | -0.061865 | -0.0031018 | 0.034257 | -0.022426 | -0.010527 | -0.013751 | -0.022888 | -0.050354 | -0.009155 | -0.022888 | 0.10529 | 0.022888 | 0.032043 | -0.032043 | 0.027466 | -0.041199 | -0.013733 | 0.086975 | -0.004578 | 0.086975 | 120.108 | -0.87433 | -0.84686 | 120.2225 | 120.1492 | 120.1401 | 0.041198 | 0.032043 | 120.076 | -0.79651 | -0.83771 | 120.2042 | 120.2042 | 120.1126 | 0.12817 | 0.036621 | 0.11444 | -0.013733 | 0.12817 | 0.027466 | -0.041199 | 0.068665 | 120.0668 | 120.1447 | -0.83313 | -0.86517 | 120.0943 | 120.1035 | 120.0943 | 120.0851
3452.9062 | 121.0876 | -120.0302 | 0.94299 | 0.028839 | 0.013292 | -0.034791 | 0.038617 | -0.013781 | -0.029463 | -0.020256 | 0.014709 | -0.061438 | -0.0026744 | 0.029557 | -0.016017 | -0.011595 | -0.017169 | -0.022888 | -0.027466 | -0.022888 | -0.004578 | 0.10529 | -0.004578 | 0 | 0.004578 | 0.050354 | -0.041199 | 0.041199 | 0.09613 | 0.018311 | 0.13275 | 120.0073 | -0.97046 | -0.94757 | 120.1355 | 120.0302 | 120.0256 | 0.022888 | 0.01831 | 119.989 | -0.89264 | -0.90179 | 120.1263 | 120.163 | 120.0485 | 0.17395 | 0.05951 | 0.12817 | 0.01831 | 0.13733 | 0.082398 | -0.004578 | 0.091553 | 120.0027 | 120.0806 | -0.96588 | -0.98419 | 120.0256 | 120.0714 | 120.0073 | 120.0348
3454.7031 | 121.1884 | -120.0394 | 0.90637 | 0.02121 | 0.013292 | -0.034577 | 0.036694 | -0.015917 | -0.028608 | -0.023033 | 0.0055542 | -0.061865 | -0.0013928 | 0.039384 | -0.019008 | -0.0101 | -0.016314 | 0 | -0.064087 | 0.009155 | 0.050354 | 0.19684 | 0.10071 | 0.091553 | 0.082397 | 0.009155 | -0.004578 | 0.091553 | 0.19684 | 0.10071 | 0.17853 | 120.0485 | -0.97046 | -0.85602 | 120.2362 | 120.1309 | 120.1401 | 0.082398 | 0.091553 | 120.0348 | -0.89722 | -0.81482 | 120.2362 | 120.2179 | 120.1401 | 0.18311 | 0.10529 | 0.18768 | 0.041199 | 0.20142 | 0.096131 | -0.073242 | 0.013733 | 119.9753 | 120.0485 | -0.89722 | -0.91095 | 120.0897 | 120.1309 | 120.0394 | 120.1218
3456.4375 | 121.17 | -120.4605 | 0.41657 | 0.036468 | 0.014787 | -0.033722 | 0.03584 | -0.014849 | -0.02754 | -0.024101 | 0.008606 | -0.061011 | 0.001598 | 0.041947 | -0.017085 | -0.0086048 | -0.013751 | 0.009155 | -0.045776 | 0.009155 | 0.050354 | 0.19226 | 0.059509 | 0.064087 | 0.10071 | 0.032043 | -0.013733 | 0.091553 | 0.14648 | 0.064087 | 0.16479 | 120.4697 | -0.46234 | -0.36621 | 120.6528 | 120.5246 | 120.52 | 0.054932 | 0.050354 | 120.4468 | -0.38452 | -0.32501 | 120.607 | 120.6253 | 120.5246 | 0.17853 | 0.07782 | 0.18311 | 0.041199 | 0.16022 | 0.10529 | -0.054931 | 0.045776 | 120.4147 | 120.4926 | -0.40741 | -0.4303 | 120.5109 | 120.5521 | 120.4697 | 120.5612
3458.25 | 121.0693 | -120.5429 | 0.47607 | 0.028839 | 0.015641 | -0.031159 | 0.039044 | -0.013567 | -0.028181 | -0.022605 | 0.0055542 | -0.059729 | -0.00075185 | 0.033616 | -0.019649 | -0.0098864 | -0.0092648 | -0.091553 | -0.009155 | -0.022888 | -0.07782 | 0.013733 | -0.07782 | -0.059509 | -0.091553 | 0.045776 | -0.041199 | -0.013733 | 0.004578 | -0.064087 | 0.086975 | 120.52 | -0.48523 | -0.55389 | 120.5566 | 120.4834 | 120.4651 | -0.036621 | -0.054932 | 120.5017 | -0.4303 | -0.48981 | 120.5475 | 120.6299 | 120.4788 | 0.12817 | -0.022888 | 0.036621 | -0.054932 | 0.045777 | 0.027466 | 0.013733 | 0.086975 | 120.5338 | 120.5887 | -0.49896 | -0.51727 | 120.4651 | 120.5292 | 120.4514 | 120.4514
3460.0469 | 121.0602 | -120.6024 | 0.43488 | 0.028839 | 0.014787 | -0.032868 | 0.037762 | -0.015917 | -0.025831 | -0.02111 | 0.0055542 | -0.058875 | 0.0022388 | 0.035325 | -0.017085 | -0.0092456 | -0.013537 | -0.082397 | 0.004578 | -0.022888 | -0.086975 | 0.004578 | -0.07782 | -0.045776 | -0.068665 | 0.054932 | -0.045776 | -0.009155 | 0.036621 | -0.059509 | 0.07782 | 120.5795 | -0.4303 | -0.52185 | 120.607 | 120.5566 | 120.5246 | -0.022888 | -0.054932 | 120.5566 | -0.37994 | -0.44403 | 120.639 | 120.6802 | 120.5429 | 0.1236 | -0.013733 | 0.027466 | -0.064087 | 0.082397 | 0.036621 | 0.027466 | 0.10071 | 120.607 | 120.6573 | -0.45776 | -0.48065 | 120.5154 | 120.5933 | 120.52 | 120.5338
3461.7812 | 121.1838 | -120.52 | 0.45776 | 0.02121 | 0.012651 | -0.031586 | 0.036267 | -0.019976 | -0.028608 | -0.022605 | 0.0055542 | -0.063574 | -0.00011105 | 0.028061 | -0.017513 | -0.010527 | -0.0049924 | -0.054932 | -0.032043 | 0 | -0.013733 | 0.1236 | 0.018311 | 0.045776 | 0.022888 | 0 | -0.018311 | 0.073242 | 0.14191 | 0.07782 | 0.16937 | 120.52 | -0.48981 | -0.4715 | 120.6436 | 120.5658 | 120.5383 | 0.045776 | 0.018311 | 120.5017 | -0.45776 | -0.38452 | 120.6619 | 120.6894 | 120.5978 | 0.18768 | 0.096131 | 0.1236 | -0.013733 | 0.16022 | 0.091553 | -0.032043 | 0.018311 | 120.488 | 120.52 | -0.45776 | -0.47608 | 120.5063 | 120.5933 | 120.4651 | 120.5429
3463.5625 | 121.1105 | -120.4971 | 0.50812 | 0.02121 | 0.015001 | -0.033722 | 0.037762 | -0.014849 | -0.029249 | -0.020469 | 0.008606 | -0.060797 | -0.00182 | 0.035111 | -0.017726 | -0.0101 | -0.014178 | -0.068665 | 0.004578 | -0.041199 | -0.082397 | 0.032043 | -0.068665 | -0.059509 | -0.068665 | 0.045776 | -0.041199 | 0 | 0.041199 | -0.032043 | 0.10529 | 120.4559 | -0.50354 | -0.59051 | 120.5292 | 120.4376 | 120.4285 | -0.01831 | -0.027466 | 120.4559 | -0.46234 | -0.50812 | 120.5383 | 120.6024 | 120.4651 | 0.14649 | 0.009156 | 0.073242 | -0.041198 | 0.082398 | 0.041199 | 0.045777 | 0.086975 | 120.5017 | 120.5429 | -0.54932 | -0.54932 | 120.4147 | 120.4971 | 120.4285 | 120.4285
3465.375 | 121.1746 | -120.5566 | 0.52185 | 0.051727 | 0.015428 | -0.033509 | 0.037762 | -0.014635 | -0.028395 | -0.023033 | 0.008606 | -0.060797 | 0.00010255 | 0.031479 | -0.020931 | -0.0096728 | -0.013751 | -0.059509 | -0.004578 | -0.064087 | -0.064087 | 0.036621 | -0.022888 | -0.018311 | -0.073242 | 0.059509 | -0.045776 | -0.027466 | 0.068665 | -0.009155 | 0.10529 | 120.4926 | -0.52643 | -0.58594 | 120.5933 | 120.5383 | 120.5338 | 0.045776 | 0.041199 | 120.5109 | -0.46234 | -0.54932 | 120.6253 | 120.6619 | 120.5475 | 0.15106 | 0.036621 | 0.10071 | 0 | 0.11444 | 0.01831 | 0.059509 | 0.10528 | 120.5521 | 120.6162 | -0.58594 | -0.56763 | 120.4926 | 120.5292 | 120.4971 | 120.4834
3467.125 | 121.1746 | -120.4834 | 0.55847 | 0.036468 | 0.013078 | -0.033295 | 0.034772 | -0.019335 | -0.03224 | -0.022819 | 0.011658 | -0.061865 | 0.00010255 | 0.038743 | -0.019008 | -0.0101 | -0.010333 | -0.068665 | -0.032043 | -0.004578 | -0.022888 | 0.11902 | 0.013733 | 0.022888 | -0.022888 | 0.018311 | -0.018311 | 0.045776 | 0.13275 | 0.045776 | 0.14191 | 120.4788 | -0.59052 | -0.58136 | 120.6024 | 120.5063 | 120.4971 | 0.027466 | 0.018311 | 120.4651 | -0.54016 | -0.5127 | 120.6161 | 120.6253 | 120.5292 | 0.16022 | 0.064087 | 0.1236 | -0.01831 | 0.15106 | 0.064087 | -0.027465 | 0.036622 | 120.4514 | 120.5017 | -0.56305 | -0.57678 | 120.4605 | 120.5292 | 120.4147 | 120.4605
3468.9062 | 121.2021 | -120.5795 | 0.46234 | 0.0059509 | 0.01671 | -0.034791 | 0.037549 | -0.016771 | -0.029463 | -0.023033 | 0.011658 | -0.059515 | 0.0020252 | 0.026993 | -0.022426 | -0.012236 | -0.0094784 | -0.10071 | 0.004578 | -0.064087 | -0.059509 | 0.050354 | -0.027466 | -0.013733 | -0.068665 | 0.068665 | -0.064087 | -0.041199 | 0.032043 | -0.018311 | 0.082397 | 120.5154 | -0.45776 | -0.52185 | 120.6299 | 120.5658 | 120.5521 | 0.050354 | 0.036621 | 120.5154 | -0.39368 | -0.50354 | 120.6116 | 120.6619 | 120.5612 | 0.14648 | 0.045776 | 0.11444 | 0.004578 | 0.09613 | 0.022888 | 0.068665 | 0.13275 | 120.5841 | 120.6482 | -0.52643 | -0.52643 | 120.52 | 120.5383 | 120.4788 | 120.5109
3470.6875 | 121.1014 | -120.0806 | 0.86517 | 0.02121 | 0.016282 | -0.0318 | 0.036267 | -0.013567 | -0.02989 | -0.02111 | 0.008606 | -0.059729 | 0.0020252 | 0.037461 | -0.014949 | -0.0092456 | -0.012256 | -0.082397 | -0.009155 | -0.027466 | -0.09613 | 0.009155 | -0.086975 | -0.054932 | -0.10071 | 0.050354 | -0.050354 | -0.009155 | 0.032043 | -0.050354 | 0.086975 | 120.0531 | -0.87433 | -0.9613 | 120.0897 | 120.0256 | 119.9936 | -0.027466 | -0.059509 | 120.0302 | -0.81482 | -0.87433 | 120.1126 | 120.1675 | 120.0302 | 0.13733 | 0 | 0.036621 | -0.068664 | 0.082397 | 0.041199 | 0.018311 | 0.10071 | 120.0714 | 120.1309 | -0.89264 | -0.91553 | 119.9844 | 120.0714 | 119.9982 | 119.9799
3472.4844 | 121.2158 | -120.4376 | 0.72327 | 0.01358 | 0.013078 | -0.03415 | 0.033276 | -0.017412 | -0.030104 | -0.020256 | 0.0055542 | -0.061651 | -0.0020336 | 0.031052 | -0.019863 | -0.011382 | -0.015246 | -0.045776 | -0.022888 | 0 | -0.027466 | 0.10986 | 0.004578 | 0.013733 | -0.054932 | 0.036621 | -0.018311 | -0.013733 | 0.064087 | -0.013733 | 0.091553 | 120.4376 | -0.74616 | -0.75073 | 120.5475 | 120.4514 | 120.4422 | 0.013733 | 0.004578 | 120.4193 | -0.68665 | -0.737 | 120.5017 | 120.5292 | 120.4239 | 0.10986 | 0.004578 | 0.10986 | -0.027466 | 0.082398 | 0.004578 | -0.022888 | 0.054932 | 120.4147 | 120.4742 | -0.72327 | -0.74158 | 120.4102 | 120.4239 | 120.3918 | 120.3827
3474.2188 | 121.3394 | -120.5017 | 0.57678 | -0.0016786 | 0.013719 | -0.032441 | 0.03584 | -0.019762 | -0.030745 | -0.023887 | 0.0055542 | -0.062292 | -0.0011792 | 0.034043 | -0.018581 | -0.011168 | -0.013537 | -0.004578 | -0.054932 | 0.009155 | 0.068665 | 0.23804 | 0.10071 | 0.091553 | 0.09613 | -0.004578 | -0.018311 | 0.10986 | 0.19684 | 0.12817 | 0.19226 | 120.5109 | -0.63171 | -0.50812 | 120.7397 | 120.5933 | 120.6024 | 0.082398 | 0.091553 | 120.4834 | -0.58136 | -0.46692 | 120.6985 | 120.694 | 120.6299 | 0.21057 | 0.14649 | 0.22888 | 0.05951 | 0.21515 | 0.12817 | -0.064087 | 0.013733 | 120.4468 | 120.4971 | -0.56763 | -0.59509 | 120.5704 | 120.6116 | 120.4971 | 120.5978
3476.0156 | 121.1975 | -120.6482 | 0.47607 | 0.02121 | 0.01436 | -0.033082 | 0.038189 | -0.012713 | -0.028608 | -0.020469 | 0.011658 | -0.058447 | -0.00182 | 0.031266 | -0.020503 | -0.011382 | -0.012042 | -0.032043 | -0.004578 | -0.036621 | -0.018311 | 0.10071 | 0.009155 | 0.018311 | -0.004578 | 0.032043 | -0.027466 | 0.041199 | 0.091553 | 0.013733 | 0.12817 | 120.6116 | -0.48065 | -0.49439 | 120.7489 | 120.6665 | 120.6573 | 0.054932 | 0.045776 | 120.6207 | -0.44403 | -0.43488 | 120.7397 | 120.7764 | 120.6619 | 0.15564 | 0.041199 | 0.13733 | 0.01831 | 0.11902 | 0.068665 | 0.032043 | 0.059509 | 120.6436 | 120.6802 | -0.5127 | -0.50354 | 120.6299 | 120.6894 | 120.6162 | 120.6436
3477.75 | 119.632 | -9.8923 | 109.5886 | 0.044098 | 0.013078 | -0.034791 | 0.03648 | -0.015062 | -0.028822 | -0.020469 | 0.008606 | -0.06272 | 0.00074335 | 0.037034 | -0.017299 | -0.0101 | -0.012683 | -0.054932 | -0.091553 | -0.036621 | -0.050354 | 0.09613 | -0.013733 | -0.004578 | -0.032043 | -0.036621 | -0.054932 | 0.022888 | 0.082397 | 0.004578 | 0.11902 | 9.8557 | -109.6802 | -109.639 | 9.9884 | 9.8877 | 9.8785 | 0.032043 | 0.022888 | 9.8373 | -109.6252 | -109.5657 | 9.9747 | 10.0113 | 9.8969 | 0.17395 | 0.05951 | 0.13275 | -0.013733 | 0.13733 | 0.07782 | -0.054932 | 0.018311 | 9.8007 | 9.8557 | -109.6252 | -109.6436 | 9.8419 | 9.9152 | 9.8373 | 9.8602
3479.5312 | 120.6619 | -13.9389 | 106.7459 | -0.40604 | 0.015214 | -0.0318 | 0.035199 | -0.017412 | -0.026899 | -0.022178 | 0.011658 | -0.061224 | 0.0018116 | 0.04152 | -0.016658 | -0.011168 | -0.013965 | -0.036621 | -0.086975 | 0.10071 | 0.004578 | 0.15564 | 0.027466 | 0.032043 | 0.054932 | -0.1831 | 0.30212 | 0.054932 | 0.10071 | 0.032043 | 0.14191 | 14.0396 | -106.8329 | -106.7413 | 14.0945 | 13.9709 | 13.9664 | -0.068665 | -0.073242 | 14.241 | -106.929 | -106.691 | 14.0396 | 14.0808 | 13.9709 | -0.16022 | -0.27008 | 0.054932 | -0.09613 | -0.20142 | -0.24719 | -0.18768 | -0.48523 | 13.8519 | 13.7558 | -106.6452 | -106.4438 | 13.9435 | 13.9938 | 13.9023 | 13.9938
3481.2656 | 108.6502 | -54.6753 | 66.0233 | 0.02121 | 0.019914 | -0.031159 | 0.030926 | -0.025957 | -0.044203 | -0.034355 | -0.085999 | -0.055456 | 0.012279 | 0.022721 | -0.027126 | -0.016082 | 0.018933 | -0.082397 | -0.004578 | 0.29297 | -0.073242 | -0.10071 | -0.24719 | -0.3479 | -0.1236 | -0.041199 | -0.091553 | -0.068665 | 0.022888 | -0.22888 | -0.091553 | 54.9683 | -66.0278 | -66.0965 | 54.5746 | 54.3274 | 54.4281 | -0.64087 | -0.54016 | 54.5837 | -66.0645 | -66.0919 | 54.6982 | 54.5837 | 54.4464 | 0 | -0.13733 | -0.39368 | -0.36621 | 0.11444 | 0.022888 | -0.29755 | 0.050354 | 54.6707 | 54.6341 | -65.7303 | -66.1148 | 54.6021 | 54.6066 | 54.5929 | 54.5517
3483.0625 | 121.3486 | -117.6041 | 3.392 | 0.01358 | 0.019914 | -0.030732 | 0.033063 | -0.021258 | -0.027967 | -0.02346 | -0.15009 | -0.062292 | 0.00010255 | 0.036606 | -0.019435 | -0.011595 | -0.012042 | -0.045776 | -0.068665 | 0.35248 | -0.022888 | -0.018311 | -0.12817 | -0.1831 | -0.059509 | -0.20599 | 0.004578 | 0.041199 | -0.004578 | -0.10529 | -0.022888 | 117.9565 | -3.4607 | -3.4149 | 117.5858 | 117.421 | 117.4759 | -0.53558 | -0.48065 | 117.6086 | -3.598 | -3.3508 | 117.5995 | 117.5812 | 117.4988 | -0.027466 | -0.10986 | -0.37079 | -0.37537 | -0.009156 | 0.036621 | -0.42114 | -0.21057 | 117.5354 | 117.3981 | -3.0396 | -3.3875 | 117.5812 | 117.6453 | 117.5583 | 117.5446
3484.8594 | 121.2753 | -118.8309 | 2.0416 | 0.028839 | 0.010728 | -0.032013 | 0.03349 | -0.016344 | -0.027754 | -0.018547 | -0.043274 | -0.062933 | 0.00010255 | 0.037675 | -0.017085 | -0.010527 | -0.012683 | -0.07782 | -0.032043 | 0.050354 | -0.027466 | 0.07782 | -0.027466 | -0.082397 | -0.013733 | -0.15564 | 0.25635 | 0.018311 | 0.11902 | 0.036621 | 0.13733 | 118.8812 | -2.0737 | -2.0691 | 118.9087 | 118.7485 | 118.8034 | -0.13275 | -0.07782 | 119.0872 | -2.1973 | -2.0233 | 118.9499 | 118.9682 | 118.8675 | -0.11902 | -0.21973 | 0.027466 | -0.07782 | -0.13733 | -0.23804 | -0.082397 | -0.41199 | 118.7988 | 118.6752 | -1.9913 | -1.7853 | 118.8034 | 118.8492 | 118.7531 | 118.8171
3486.6562 | 121.2158 | -119.1605 | 1.8082 | 0.02121 | 0.015855 | -0.049958 | 0.033276 | 0.026594 | -0.042921 | 0.028664 | 0.051331 | 0.01568 | -0.016133 | 0.029984 | 0.023076 | 0.027284 | -0.016314 | -0.21057 | -0.032043 | -0.009155 | -0.21973 | 0.10071 | 0.091553 | 0.091553 | -0.050354 | -0.14191 | 0.050354 | 0 | -0.032043 | 0.091553 | 0.09613 | 119.1513 | -1.8402 | -2.0279 | 119.2612 | 119.252 | 119.252 | 0.10071 | 0.10071 | 119.2108 | -1.9501 | -1.8082 | 119.1284 | 119.2566 | 119.252 | 0.045776 | 0.041199 | 0.10986 | -0.21057 | -0.082397 | -0.050354 | -0.022888 | -0.19226 | 119.1284 | 119.0186 | -1.8173 | -1.7578 | 118.9407 | 119.1605 | 118.9499 | 119.1101
3488.3906 | 121.3165 | -120.3827 | 0.54016 | 0.02121 | 0.013719 | -0.02945 | 0.035626 | -0.014849 | -0.028181 | -0.020042 | -0.058533 | -0.061011 | -0.00011105 | 0.034897 | -0.018794 | -0.010955 | -0.012042 | -0.041199 | -0.041199 | -0.018311 | 0.013733 | 0.09613 | -0.059509 | -0.11444 | 0.050354 | -0.064087 | 0.27008 | 0.068665 | 0.11444 | 0.041199 | 0.1236 | 120.3644 | -0.58136 | -0.52643 | 120.4788 | 120.2682 | 120.3232 | -0.09613 | -0.041198 | 120.6528 | -0.60425 | -0.4715 | 120.4971 | 120.5063 | 120.4239 | -0.14649 | -0.22888 | 0.11444 | 0.032044 | -0.15564 | -0.20142 | -0.022888 | -0.33417 | 120.3415 | 120.3186 | -0.55847 | -0.27008 | 120.3964 | 120.4514 | 120.3415 | 120.433
3490.1875 | 121.3486 | -120.0806 | 0.91095 | 0.01358 | 0.013078 | -0.033509 | 0.037762 | -0.02083 | -0.031172 | -0.021751 | -0.073792 | -0.063788 | -0.0043834 | 0.040238 | -0.018367 | -0.0081774 | -0.011615 | 0.004578 | -0.050354 | 0 | 0.050354 | 0.19226 | 0.032043 | -0.059509 | 0.09613 | 0.013733 | 0.059509 | 0.10986 | 0.1831 | 0.086975 | 0.09613 | 120.0806 | -0.9613 | -0.8606 | 120.2728 | 120.0211 | 120.1126 | -0.059509 | 0.032043 | 120.1401 | -0.89722 | -0.80109 | 120.2637 | 120.1767 | 120.1675 | 0.036621 | 0.027466 | 0.19226 | 0.050354 | 0.1236 | 0.050354 | -0.050354 | -0.045776 | 120.0302 | 120.0943 | -0.91095 | -0.85144 | 120.1309 | 120.1904 | 120.0851 | 120.1767
3491.9688 | 121.3348 | -103.7521 | 17.0929 | 0.02121 | 0.013078 | -0.032013 | 0.037549 | -0.018694 | -0.030317 | -0.020042 | -0.082947 | -0.060156 | 0.00074335 | 0.033829 | -0.017085 | -0.010955 | -0.016314 | -0.041199 | -0.045776 | -0.004578 | 0.032043 | 0.15106 | 0.013733 | -0.041199 | 0.10529 | -0.004578 | 0.17395 | 0.1236 | 0.16937 | 0.11444 | 0.16022 | 103.7476 | -17.1387 | -17.0609 | 103.9032 | 103.7109 | 103.7659 | -0.036621 | 0.018311 | 103.9261 | -17.0975 | -16.9693 | 103.9215 | 103.9124 | 103.8666 | -0.013733 | -0.059509 | 0.15564 | 0.036621 | -0.004577 | -0.050354 | -0.041198 | -0.17853 | 103.7064 | 103.7476 | -17.0975 | -16.9189 | 103.7842 | 103.8757 | 103.7109 | 103.8574
3493.75 | 121.4447 | -119.9295 | 1.0345 | 0.01358 | 0.012437 | -0.030091 | 0.038189 | -0.01549 | -0.028608 | -0.021324 | -0.22943 | -0.062933 | -0.0024608 | 0.037247 | -0.014949 | -0.0092456 | -0.0088376 | -0.013733 | -0.045776 | 0.009155 | 0.036621 | -0.050354 | -0.26093 | -0.30212 | 0.086975 | 0.004578 | 0.13275 | 0.14191 | 0.13275 | -0.018311 | 0.036621 | 119.9387 | -1.0803 | -0.99792 | 119.8791 | 119.6274 | 119.6686 | -0.31128 | -0.27008 | 120.0623 | -1.03 | -0.89264 | 120.0623 | 119.9661 | 119.9112 | -0.09613 | -0.15106 | -0.059509 | 0.027466 | 0 | 0.009156 | -0.054931 | -0.12817 | 119.8837 | 119.9341 | -1.0254 | -0.90179 | 119.9661 | 120.0714 | 119.9158 | 120.0165
3495.4688 | 121.3943 | -119.5633 | 1.5289 | 0.02121 | 0.013078 | -0.033082 | 0.037121 | -0.018053 | -0.02989 | -0.020897 | -0.034119 | -0.064642 | -0.0033154 | 0.039811 | -0.016445 | -0.0101 | -0.012256 | -0.059509 | -0.036621 | 0 | -0.027466 | 0.10071 | 0 | -0.064087 | 0.004578 | 0.022888 | -0.022888 | 0.073242 | 0.086975 | 0.027466 | 0.16022 | 119.5633 | -1.5656 | -1.5564 | 119.664 | 119.4992 | 119.5633 | -0.064087 | 0 | 119.5404 | -1.506 | -1.4557 | 119.6503 | 119.7235 | 119.5908 | 0.1831 | 0.050354 | 0.10071 | -0.027466 | 0.10986 | 0.09613 | -0.036621 | 0.045776 | 119.5267 | 119.5862 | -1.5289 | -1.5518 | 119.5358 | 119.6365 | 119.5038 | 119.5679
3497.25 | 121.344 | -119.6182 | 1.4648 | 0.02121 | 0.01436 | -0.032868 | 0.035626 | -0.014849 | -0.031172 | -0.021965 | -0.10736 | -0.068488 | -0.0020336 | 0.033188 | -0.014308 | -0.010955 | -0.010547 | -0.073242 | 0.009155 | -0.036621 | -0.10071 | -0.21973 | -0.27466 | 0.09613 | -0.059509 | 0.045776 | -0.045776 | 0.022888 | 0.009155 | -0.15564 | -0.25177 | 119.5816 | -1.4557 | -1.5656 | 119.3985 | 119.7144 | 119.3436 | 0.13275 | -0.23804 | 119.5724 | -1.4191 | -1.442 | 119.6274 | 119.3665 | 119.4626 | -0.20599 | -0.10986 | -0.18311 | -0.064087 | 0.054931 | 0.068664 | 0.045776 | 0.091552 | 119.6274 | 119.664 | -1.5015 | -1.5106 | 119.5175 | 119.6411 | 119.545 | 119.5587
3499.0312 | 120.2042 | -120.0073 | 0.13733 | 0.02121 | 0.010301 | -0.030304 | 0.03114 | -0.02083 | -0.026472 | -0.020897 | -0.15619 | -0.061438 | -0.0011792 | 0.022507 | -0.023281 | -0.011168 | -0.010974 | -0.12817 | -0.009155 | 0.33417 | -0.36621 | -0.09613 | -0.082397 | -0.21973 | -0.068665 | -0.31128 | -0.091553 | -0.018311 | -0.10071 | -0.14191 | 0.054932 | 120.3415 | -0.14648 | -0.50354 | 119.9112 | 119.7876 | 119.9249 | -0.55389 | -0.41656 | 119.9158 | -0.44861 | -0.15564 | 119.9066 | 120.0623 | 119.8654 | 0.14649 | -0.050354 | -0.4303 | -0.70038 | -0.009155 | 0.073242 | -0.34332 | -0.21973 | 119.9982 | 119.696 | 0.19684 | -0.22888 | 119.6411 | 119.989 | 119.8791 | 119.9387
3500.8281 | 120.9824 | -120.6573 | 0.059509 | 0.028839 | 0.012651 | -0.031373 | 0.038617 | -0.011858 | -0.027967 | -0.020042 | -0.092102 | -0.062506 | -0.0028882 | 0.041733 | -0.016658 | -0.0098864 | -0.01076 | -0.009155 | -0.041199 | 0.018311 | 0.022888 | 0.073242 | -0.073242 | -0.13733 | 0.09613 | -0.013733 | 0.22888 | 0.10071 | 0.16022 | 0.032043 | 0.11444 | 120.6757 | -0.10071 | -0.036621 | 120.7306 | 120.52 | 120.5841 | -0.15564 | -0.091553 | 120.8862 | -0.073242 | 0.041199 | 120.8176 | 120.7718 | 120.6894 | -0.11444 | -0.19684 | 0.054931 | 0.004577 | -0.068665 | -0.12817 | -0.05951 | -0.24261 | 120.6161 | 120.6436 | -0.041198 | 0.16937 | 120.6802 | 120.7581 | 120.6482 | 120.7535
3502.6406 | 121.0968 | -120.7489 | 0.059509 | 0.02121 | 0.01436 | -0.033082 | 0.035626 | -0.017412 | -0.028395 | -0.021324 | -0.082947 | -0.061865 | -0.0024608 | 0.036179 | -0.018367 | -0.011168 | -0.01546 | -0.013733 | -0.045776 | 0.013733 | 0.050354 | 0.16937 | 0.045776 | -0.064087 | 0.10071 | 0.004578 | 0.059509 | 0.10529 | 0.1831 | 0.09613 | 0.11444 | 120.7626 | -0.10528 | -0.009155 | 120.9183 | 120.6848 | 120.7947 | -0.07782 | 0.032043 | 120.8084 | -0.054931 | 0.045777 | 120.932 | 120.8633 | 120.845 | 0.054932 | 0.036621 | 0.15564 | 0.036621 | 0.1236 | 0.045777 | -0.059509 | -0.054931 | 120.7031 | 120.7535 | -0.045776 | 0 | 120.7993 | 120.8542 | 120.7352 | 120.8496
3504.4219 | 121.051 | -120.8542 | 0.086975 | 0.02121 | 0.013719 | -0.033722 | 0.034985 | -0.01784 | -0.029676 | -0.022819 | -0.14093 | -0.061438 | 0.00010255 | 0.041733 | -0.018367 | -0.008391 | -0.011828 | -0.009155 | -0.050354 | 0.018311 | 0.018311 | 0.10071 | -0.068665 | -0.17853 | 0.018311 | 0.027466 | -0.013733 | 0.022888 | 0.10071 | -0.068665 | -0.10071 | 120.8725 | -0.13733 | -0.068664 | 120.9549 | 120.6757 | 120.7855 | -0.19684 | -0.086976 | 120.8405 | -0.059509 | -0.064087 | 120.9549 | 120.7535 | 120.7855 | -0.086975 | -0.054932 | 0.082397 | 0 | 0.11444 | 0.036621 | -0.068665 | 0.041199 | 120.8038 | 120.8817 | -0.068664 | -0.10071 | 120.8725 | 120.8771 | 120.845 | 120.8725
3506.1562 | 121.1884 | -120.8359 | 0.07782 | 0.02121 | 0.016496 | -0.033082 | 0.03883 | -0.016131 | -0.030958 | -0.022819 | -0.14398 | -0.062506 | -0.0037426 | 0.039811 | -0.011531 | -0.012236 | -0.014819 | 0 | -0.054932 | 0 | 0.036621 | 0.15106 | -0.07782 | -0.20599 | 0.086975 | 0.013733 | 0.013733 | 0.1236 | 0.16022 | 0.082397 | 0.10986 | 120.8359 | -0.13275 | -0.041199 | 120.9869 | 120.6299 | 120.7581 | -0.20599 | -0.07782 | 120.8496 | -0.064087 | 0.045776 | 120.9961 | 120.9457 | 120.9183 | 0.09613 | 0.068664 | 0.15106 | 0.036621 | 0.14648 | 0.10986 | -0.054932 | 0 | 120.7809 | 120.8496 | -0.07782 | -0.064087 | 120.8725 | 120.9595 | 120.8359 | 120.9229
3507.9531 | 120.8633 | -120.9091 | 0.1236 | 0.01358 | 0.014146 | -0.031159 | 0.038617 | -0.025316 | -0.028395 | -0.02581 | 0.036072 | -0.068915 | -0.00075185 | 0.02977 | -0.01324 | -0.010955 | -0.011615 | -0.064087 | -0.022888 | -0.036621 | -0.091553 | -0.20142 | -0.35706 | 0.091553 | -0.091553 | 0.059509 | -0.022888 | -0.045776 | 0.009155 | -0.32044 | 0.009155 | 120.8725 | -0.14648 | -0.21515 | 120.7077 | 121.0007 | 120.5521 | 0.12817 | -0.32043 | 120.8862 | -0.064087 | -0.16937 | 120.9183 | 120.9183 | 120.5887 | 0.032043 | -0.29755 | -0.1648 | -0.054932 | 0.032043 | -0.022888 | 0.013733 | 0.082397 | 120.8862 | 120.9686 | -0.16022 | -0.14648 | 120.8176 | 120.8633 | 120.845 | 120.8176
3509.7344 | 121.2341 | -120.8954 | 0.073242 | 0.02121 | 0.012651 | -0.033082 | 0.037335 | -0.016131 | -0.028608 | -0.020683 | -0.13483 | -0.06272 | -0.0031018 | 0.040238 | -0.01324 | -0.0077502 | -0.018878 | -0.018311 | -0.022888 | -0.013733 | 0.022888 | 0.14648 | -0.009155 | -0.15564 | 0.064087 | -0.004578 | 0 | 0.10529 | 0.16479 | 0.073242 | 0.16479 | 120.8817 | -0.09613 | -0.050354 | 121.0419 | 120.7397 | 120.8862 | -0.14191 | 0.004578 | 120.8954 | -0.07782 | 0.032044 | 121.0602 | 121.0602 | 120.9686 | 0.16479 | 0.073242 | 0.16022 | 0.036621 | 0.16479 | 0.10529 | -0.009155 | -0.004578 | 120.8725 | 120.8908 | -0.086975 | -0.073242 | 120.9183 | 121.0007 | 120.8771 | 120.9595
3511.4531 | 121.2296 | -120.9091 | 0.064087 | 0.036468 | 0.014787 | -0.029877 | 0.039044 | -0.013781 | -0.025831 | -0.02111 | -0.0097046 | -0.061011 | -0.0024608 | 0.044938 | -0.015377 | -0.0086048 | -0.012469 | 0.032043 | -0.045776 | -0.009155 | 0.064087 | 0.18768 | 0.059509 | 0.027466 | 0.091553 | -0.004578 | 0 | 0.091553 | 0.17395 | 0.09613 | 0.19684 | 120.9 | -0.10986 | 0 | 121.0968 | 120.9366 | 120.9686 | 0.036621 | 0.068664 | 120.9091 | -0.068665 | 0.027466 | 121.0831 | 121.106 | 121.0052 | 0.19684 | 0.09613 | 0.19684 | 0.073242 | 0.17395 | 0.091553 | -0.036621 | -0.004578 | 120.8633 | 120.9045 | -0.073242 | -0.064087 | 120.9732 | 121.0007 | 120.9412 | 121.0007
3513.25 | 121.2524 | -120.9595 | 0.059509 | 0.02121 | 0.01201 | -0.031586 | 0.037762 | -0.015276 | -0.028822 | -0.018974 | -0.073792 | -0.06037 | 0.0022388 | 0.034257 | -0.014736 | -0.0081774 | -0.013537 | -0.054932 | -0.036621 | 0 | -0.013733 | 0.10986 | 0.013733 | -0.11902 | 0.054932 | -0.004578 | -0.013733 | 0.091553 | 0.15106 | 0.073242 | 0.17853 | 120.9595 | -0.09613 | -0.073242 | 121.0693 | 120.8405 | 120.9732 | -0.11902 | 0.013733 | 120.9457 | -0.064087 | 0.032044 | 121.1105 | 121.138 | 121.0327 | 0.19226 | 0.086975 | 0.10986 | -0.013733 | 0.16479 | 0.10529 | -0.036621 | 0.009155 | 120.9229 | 120.9549 | -0.059509 | -0.073242 | 120.9457 | 121.051 | 120.9045 | 121.0144
3515.0469 | 121.2387 | -120.9778 | 0.054932 | 0.036468 | 0.016069 | -0.032654 | 0.036908 | -0.0099357 | -0.027967 | -0.021751 | 0.014709 | -0.061651 | -0.0031018 | 0.031479 | -0.017726 | -0.010741 | -0.011401 | -0.032043 | -0.041199 | -0.013733 | 0.022888 | 0.15564 | 0.036621 | 0.041199 | 0.059509 | 0.013733 | -0.018311 | 0.059509 | 0.11902 | 0.045776 | 0.16022 | 120.9641 | -0.096131 | -0.032044 | 121.1334 | 121.019 | 121.0144 | 0.054932 | 0.050354 | 120.9595 | -0.041199 | 0.004577 | 121.0968 | 121.138 | 121.0236 | 0.17853 | 0.064087 | 0.16937 | 0.036621 | 0.13733 | 0.07782 | -0.027466 | 0.032044 | 120.9366 | 120.9915 | -0.068665 | -0.073243 | 121.0007 | 121.0373 | 120.9457 | 121.0373
3516.7656 | 121.2845 | -121.0007 | 0.054932 | 0.036468 | 0.015428 | -0.030945 | 0.037335 | -0.016131 | -0.029463 | -0.021751 | 0.014709 | -0.061438 | -0.00053825 | 0.039597 | -0.015804 | -0.0086048 | -0.0092648 | 0.018311 | -0.045776 | 0.009155 | 0.050354 | 0.19684 | 0.068665 | 0.068665 | 0.11444 | 0.009155 | -0.009155 | 0.09613 | 0.17853 | 0.091553 | 0.20142 | 121.0098 | -0.10071 | -0.004578 | 121.1975 | 121.0693 | 121.0693 | 0.05951 | 0.05951 | 120.9915 | -0.045777 | 0.041198 | 121.1792 | 121.2021 | 121.0922 | 0.21057 | 0.10071 | 0.18768 | 0.041199 | 0.18768 | 0.10528 | -0.054931 | 0.01831 | 120.9549 | 121.0098 | -0.045777 | -0.064087 | 121.051 | 121.0968 | 121.019 | 121.1151
3518.5625 | 121.2616 | -121.0236 | 0.082397 | 0.02121 | 0.011369 | -0.032868 | 0.034985 | -0.01784 | -0.029463 | -0.022392 | 0.011658 | -0.060584 | -0.0011792 | 0.042161 | -0.018794 | -0.0092456 | -0.013751 | -0.045776 | -0.045776 | -0.009155 | -0.004578 | 0.12817 | 0.022888 | 0.050354 | 0.027466 | 0.027466 | -0.036621 | 0.032043 | 0.11444 | 0.054932 | 0.16022 | 121.0144 | -0.12817 | -0.086975 | 121.1517 | 121.0739 | 121.0464 | 0.059509 | 0.032043 | 120.9869 | -0.054931 | -0.050354 | 121.138 | 121.1838 | 121.0785 | 0.19684 | 0.091553 | 0.13733 | 0.004577 | 0.15106 | 0.068664 | -0.036621 | 0.064087 | 120.9778 | 121.051 | -0.091552 | -0.11902 | 121.019 | 121.0556 | 120.9778 | 121.051
3520.3125 | 121.2753 | -121.0373 | 0.073242 | 0.036468 | 0.014787 | -0.03415 | 0.036908 | -0.01784 | -0.028181 | -0.02111 | 0.014709 | -0.06272 | -0.00096545 | 0.042801 | -0.016872 | -0.0071094 | -0.015246 | -0.004578 | -0.045776 | 0 | 0.027466 | 0.16479 | 0.032043 | 0.045776 | 0.050354 | 0.013733 | -0.013733 | 0.050354 | 0.12817 | 0.036621 | 0.16022 | 121.0373 | -0.11902 | -0.045776 | 121.2021 | 121.0831 | 121.0693 | 0.045776 | 0.032043 | 121.0236 | -0.059509 | -0.022888 | 121.1655 | 121.1975 | 121.0739 | 0.17395 | 0.050354 | 0.16479 | 0.027466 | 0.14191 | 0.064087 | -0.045776 | 0.027466 | 120.9915 | 121.051 | -0.073242 | -0.086975 | 121.0648 | 121.0876 | 121.0327 | 121.0876
3522.0469 | 120.9549 | -121.019 | 0.10529 | 0.02121 | 0.014146 | -0.033295 | 0.03584 | -0.015917 | -0.030745 | -0.021965 | 0.017761 | -0.061865 | 0.00095715 | 0.035752 | -0.021144 | -0.010955 | -0.011401 | -0.09613 | 0.004578 | -0.050354 | -0.07782 | 0.050354 | -0.013733 | -0.018311 | -0.073242 | 0.054932 | -0.054932 | -0.054932 | 0.050354 | -0.018311 | 0.086975 | 120.9686 | -0.10071 | -0.18311 | 121.0693 | 121.0007 | 121.0052 | 0.032043 | 0.036621 | 120.9641 | -0.050354 | -0.16022 | 121.0693 | 121.106 | 121.0007 | 0.14191 | 0.036621 | 0.10071 | -0.027466 | 0.10529 | 0 | 0.054932 | 0.10986 | 121.0236 | 121.0739 | -0.15564 | -0.16022 | 120.9412 | 120.9641 | 120.9229 | 120.9457
3523.8281 | 121.3348 | -121.0831 | 0.059509 | 0.028839 | 0.011369 | -0.032868 | 0.034344 | -0.015703 | -0.028822 | -0.022605 | 0.011658 | -0.062079 | 0.00052975 | 0.034684 | -0.019008 | -0.011382 | -0.014605 | -0.064087 | -0.027466 | 0 | -0.009155 | 0.14648 | 0.045776 | 0.050354 | 0.041199 | 0.013733 | -0.009155 | 0.068665 | 0.17395 | 0.09613 | 0.1831 | 121.0831 | -0.086975 | -0.068664 | 121.2296 | 121.1334 | 121.1288 | 0.050354 | 0.045776 | 121.0739 | -0.045776 | 0.009156 | 121.257 | 121.2662 | 121.1792 | 0.19226 | 0.10528 | 0.14648 | -0.009155 | 0.1831 | 0.07782 | -0.027466 | 0.022888 | 121.0556 | 121.0968 | -0.059509 | -0.068664 | 121.0739 | 121.1517 | 121.019 | 121.1243
3525.625 | 120.8267 | -120.5978 | 0.082397 | 0.02121 | 0.018846 | -0.033722 | 0.039471 | -0.01314 | -0.027754 | -0.020042 | 0.008606 | -0.066351 | -0.00096545 | 0.032761 | -0.016231 | -0.012236 | -0.013537 | -0.013733 | -0.013733 | -0.022888 | -0.018311 | 0.10529 | 0.009155 | 0 | 0.018311 | 0.050354 | -0.022888 | 0.018311 | 0.10529 | 0.004578 | 0.13275 | 120.575 | -0.09613 | -0.10071 | 120.7031 | 120.5978 | 120.607 | 0.022888 | 0.032043 | 120.575 | -0.032043 | -0.064086 | 120.7031 | 120.7306 | 120.6024 | 0.15564 | 0.027466 | 0.12817 | 0.004577 | 0.12817 | 0.041199 | 0.009155 | 0.073242 | 120.5841 | 120.6482 | -0.10528 | -0.10528 | 120.5795 | 120.6161 | 120.5841 | 120.6161
3527.4531 | 121.2891 | -121.1105 | 0.10071 | 0.02121 | 0.013292 | -0.033082 | 0.034985 | -0.019121 | -0.026686 | -0.019615 | 0.008606 | -0.062506 | -0.0020336 | 0.031052 | -0.018367 | -0.013304 | -0.011187 | -0.013733 | -0.036621 | 0 | 0.032043 | 0.16022 | 0.068665 | 0.054932 | 0.022888 | 0.032043 | -0.027466 | 0.004578 | 0.11902 | 0.032043 | 0.13733 | 121.1105 | -0.13733 | -0.068665 | 121.2708 | 121.1655 | 121.1792 | 0.054932 | 0.068665 | 121.0831 | -0.068665 | -0.09613 | 121.2296 | 121.2479 | 121.1426 | 0.16479 | 0.059509 | 0.16022 | 0.032043 | 0.14649 | 0.032044 | -0.036621 | 0.059509 | 121.0739 | 121.1426 | -0.10071 | -0.12817 | 121.1426 | 121.1151 | 121.0968 | 121.1334
3529.2344 | 121.2067 | -121.0922 | 0.10986 | 0.0059509 | 0.013292 | -0.033509 | 0.036908 | -0.011004 | -0.029036 | -0.022819 | 0.008606 | -0.061011 | -0.00075185 | 0.029984 | -0.019008 | -0.011595 | -0.013965 | -0.09613 | -0.013733 | -0.032043 | -0.082397 | 0.041199 | -0.036621 | -0.018311 | -0.068665 | 0.059509 | -0.059509 | -0.054932 | 0.041199 | -0.032043 | 0.086975 | 121.0602 | -0.1236 | -0.19226 | 121.1334 | 121.0739 | 121.0556 | 0.013732 | -0.004578 | 121.0327 | -0.050354 | -0.16479 | 121.1334 | 121.1792 | 121.0602 | 0.14648 | 0.027466 | 0.073242 | -0.050354 | 0.10071 | 0.004577 | 0.01831 | 0.11902 | 121.0785 | 121.1517 | -0.14191 | -0.16937 | 121.0098 | 121.0373 | 120.9961 | 121.0236
3530.9844 | 121.3715 | -121.0876 | 0.07782 | 0.01358 | 0.01436 | -0.033722 | 0.034558 | -0.022112 | -0.031599 | -0.024314 | 0.008606 | -0.063574 | -0.0016064 | 0.041306 | -0.018367 | -0.011168 | -0.01546 | -0.009155 | -0.050354 | -0.004578 | 0.068665 | 0.20142 | 0.091553 | 0.082397 | 0.082397 | 0.004578 | 0 | 0.07782 | 0.19684 | 0.10529 | 0.1831 | 121.0831 | -0.12817 | -0.009155 | 121.2891 | 121.17 | 121.1792 | 0.086975 | 0.096131 | 121.0876 | -0.073242 | 0 | 121.2845 | 121.2708 | 121.1929 | 0.1831 | 0.10529 | 0.20599 | 0.073243 | 0.19684 | 0.07782 | -0.045776 | 0.004578 | 121.0373 | 121.0922 | -0.082398 | -0.07782 | 121.1563 | 121.1655 | 121.0785 | 121.17
3532.7812 | 121.4172 | -121.0602 | 0.068665 | 0.01358 | 0.015214 | -0.033722 | 0.037976 | -0.013781 | -0.028181 | -0.024314 | 0.011658 | -0.059943 | 0.00010255 | 0.040024 | -0.013668 | -0.010955 | -0.010119 | -0.036621 | -0.045776 | 0.013733 | 0.013733 | 0.13275 | 0.022888 | 0.045776 | 0.073242 | 0.004578 | -0.009155 | 0.09613 | 0.17395 | 0.068665 | 0.20599 | 121.0739 | -0.11444 | -0.054932 | 121.1929 | 121.106 | 121.0831 | 0.032043 | 0.009155 | 121.051 | -0.064087 | 0.027465 | 121.2341 | 121.2662 | 121.1288 | 0.21515 | 0.07782 | 0.11902 | 0 | 0.1831 | 0.10528 | -0.059509 | 0.013733 | 121.0144 | 121.0648 | -0.054932 | -0.07782 | 121.0739 | 121.1563 | 121.0236 | 121.1334
3534.5781 | 121.4127 | -121.1334 | 0.082397 | 0.02121 | 0.013933 | -0.034577 | 0.035626 | -0.017626 | -0.029249 | -0.024314 | 0.008606 | -0.063788 | -0.00096545 | 0.034897 | -0.01559 | -0.008391 | -0.011401 | -0.036621 | -0.054932 | 0.004578 | 0.004578 | 0.14191 | 0.054932 | 0.045776 | 0.045776 | 0.018311 | -0.013733 | 0.068665 | 0.17853 | 0.10071 | 0.19226 | 121.138 | -0.13733 | -0.077819 | 121.2753 | 121.1792 | 121.1884 | 0.041198 | 0.050354 | 121.1197 | -0.064086 | -0.013732 | 121.312 | 121.3257 | 121.2341 | 0.20599 | 0.11444 | 0.13733 | 0 | 0.19226 | 0.082398 | -0.05951 | 0.032044 | 121.0785 | 121.1517 | -0.077819 | -0.09613 | 121.138 | 121.2021 | 121.0968 | 121.1792
3536.3594 | 121.4264 | -121.1243 | 0.064087 | 0.028839 | 0.013078 | -0.034363 | 0.034985 | -0.012285 | -0.029036 | -0.021537 | 0.0055542 | -0.062506 | -0.0011792 | 0.039384 | -0.018794 | -0.009032 | -0.012683 | -0.054932 | -0.059509 | 0.004578 | -0.013733 | 0.11902 | 0.041199 | 0.041199 | 0.027466 | 0.018311 | 0.009155 | 0.054932 | 0.14648 | 0.082397 | 0.17395 | 121.1288 | -0.1236 | -0.07782 | 121.2433 | 121.1655 | 121.1655 | 0.036621 | 0.036621 | 121.1334 | -0.045776 | -0.009155 | 121.2708 | 121.2982 | 121.2067 | 0.16479 | 0.073242 | 0.11444 | -0.018311 | 0.13733 | 0.045777 | -0.064087 | 0.009156 | 121.0648 | 121.1426 | -0.059509 | -0.054932 | 121.1105 | 121.1792 | 121.0693 | 121.1517
3538.0938 | 116.2445 | -77.2659 | 38.7039 | 0.02121 | 0.013078 | -0.036286 | 0.033063 | -0.018908 | -0.028395 | -0.024742 | 0.008606 | -0.06272 | -0.0016064 | 0.035752 | -0.017085 | -0.0088184 | -0.012256 | -0.059509 | -0.045776 | -0.027466 | -0.032043 | 0.10986 | 0.009155 | 0.022888 | -0.022888 | 0.004578 | -0.022888 | 0.022888 | 0.1236 | 0.054932 | 0.15564 | 77.2385 | -38.7497 | -38.736 | 77.3758 | 77.2888 | 77.2751 | 0.050354 | 0.036621 | 77.243 | -38.6993 | -38.681 | 77.3895 | 77.4216 | 77.3209 | 0.17853 | 0.07782 | 0.13733 | -0.004577 | 0.14648 | 0.045776 | -0.01831 | 0.027466 | 77.2202 | 77.2705 | -38.7314 | -38.7268 | 77.2339 | 77.2888 | 77.2064 | 77.243
3539.875 | 121.1014 | -5.3329 | 114.6698 | 0.02121 | 0.01436 | -0.036713 | 0.034985 | -0.016344 | -0.031172 | -0.023033 | 0.011658 | -0.062506 | -0.00011105 | 0.03447 | -0.019649 | -0.010741 | -0.014819 | -0.036621 | -0.10071 | -0.036621 | -0.009155 | 0.11902 | 0.036621 | 0.022888 | 0 | -0.013733 | 0.09613 | -0.013733 | 0.07782 | -0.004578 | 0.091553 | 5.2963 | -114.7705 | -114.679 | 5.452 | 5.3558 | 5.3696 | 0.059509 | 0.073242 | 5.4291 | -114.6835 | -114.6835 | 5.4108 | 5.4245 | 5.3284 | -0.004577 | -0.10071 | 0.15564 | 0.027466 | -0.01831 | -0.10986 | -0.064087 | -0.10986 | 5.2322 | 5.3192 | -114.7064 | -114.5737 | 5.3238 | 5.3192 | 5.2963 | 5.3329
3541.6094 | 121.0831 | -3.9597 | 116.3361 | 0.01358 | 0.012437 | -0.034363 | 0.032849 | -0.020189 | -0.029676 | -0.023887 | -0.08905 | -0.062506 | -0.00053825 | 0.040452 | -0.01794 | -0.0101 | -0.011615 | -0.054932 | -0.086975 | 0.22888 | 0.022888 | 0.17853 | 0.073242 | -0.068665 | 0.059509 | -0.21515 | 0.31586 | 0.068665 | 0.16937 | 0.082397 | 0.054932 | 4.1885 | -116.423 | -116.3132 | 4.1382 | 3.891 | 4.0329 | -0.29755 | -0.15564 | 4.2755 | -116.5512 | -116.2674 | 4.129 | 4.0146 | 4.0421 | -0.26093 | -0.23346 | -0.050354 | -0.20599 | -0.14648 | -0.24719 | -0.31586 | -0.53101 | 3.8727 | 3.7445 | -116.1072 | -116.0202 | 3.9825 | 4.0283 | 3.9047 | 4.0192
3543.4062 | 121.1792 | -4.0009 | 108.2565 | 0.02121 | 0.015855 | -0.032441 | 0.02879 | -0.015276 | -0.031385 | -0.019401 | -0.12872 | -0.064002 | 0.0020252 | 0.022507 | -0.019008 | -0.011809 | -0.014605 | -0.14191 | -0.050354 | 0.24261 | -0.11444 | 0 | -0.086975 | -0.41199 | -0.1236 | -0.15106 | -0.018311 | -0.050354 | 0.009155 | -0.25635 | -0.004578 | 4.2435 | -108.3069 | -108.371 | 4.0009 | 3.5889 | 3.9139 | -0.6546 | -0.32959 | 3.9825 | -108.4076 | -108.3069 | 4.01 | 3.9963 | 3.7445 | 0.013733 | -0.23804 | -0.24261 | -0.35706 | 0.027466 | -0.032043 | -0.29297 | -0.13275 | 3.9505 | 3.8498 | -108.0139 | -108.2748 | 3.8864 | 3.9505 | 3.8589 | 3.8773
3545.2031 | 120.8862 | -2.9755 | 111.3693 | 0.02121 | 0.014787 | -0.037568 | 0.033917 | 0.026594 | -0.034376 | -0.027092 | -0.085999 | 0.015893 | -0.017842 | 0.029984 | 0.023503 | 0.028138 | 0.020856 | -0.073242 | -0.036621 | -0.059509 | -0.054932 | 0.082397 | -0.16479 | -0.1831 | -0.009155 | -0.09613 | 0.30212 | -0.086975 | -0.022888 | -0.35706 | 0.09613 | 2.916 | -111.4059 | -111.4243 | 3.0579 | 2.7924 | 2.8107 | -0.1236 | -0.10529 | 3.2776 | -111.4655 | -111.4563 | 2.9526 | 3.0716 | 2.6184 | -0.20599 | -0.65918 | 0.14191 | 0.004577 | -0.32501 | -0.3891 | 0.022888 | -0.39825 | 2.9388 | 2.8793 | -111.4288 | -111.0672 | 2.9205 | 2.8885 | 2.9022 | 2.9663
3546.9219 | 121.3211 | -3.7674 | 116.8304 | 0.028839 | 0.017564 | -0.033082 | 0.035626 | -0.018694 | -0.028822 | -0.02346 | 0.0055542 | -0.061438 | 0.0024524 | 0.036179 | -0.015377 | -0.010527 | -0.011401 | -0.050354 | -0.073242 | -0.027466 | 0.018311 | 0.16022 | 0.022888 | 0.013733 | 0.059509 | -0.027466 | -0.054932 | 0.050354 | 0.13733 | 0.054932 | 0.15106 | 3.7399 | -116.9037 | -116.8121 | 3.9276 | 3.7811 | 3.7903 | 0.041199 | 0.050354 | 3.7125 | -116.8579 | -116.7801 | 3.9047 | 3.9185 | 3.8223 | 0.20599 | 0.10986 | 0.18768 | 0.045777 | 0.19226 | 0.10529 | -0.045776 | 0.027466 | 3.6942 | 3.7399 | -116.8579 | -116.8854 | 3.7857 | 3.8177 | 3.717 | 3.8269
3548.7188 | 121.2341 | -4.129 | 117.0731 | 0.01358 | 0.013719 | -0.0318 | 0.035199 | -0.027666 | -0.030745 | -0.024101 | -0.15009 | -0.069342 | 0.00031615 | 0.031052 | -0.017513 | -0.010314 | -0.011828 | -0.10986 | -0.050354 | -0.073242 | -0.13275 | -0.032043 | -0.11444 | -0.3067 | -0.1236 | 0 | -0.091553 | -0.068665 | -0.013733 | -0.13275 | -0.17395 | 4.0558 | -117.1234 | -117.2058 | 4.097 | 3.8223 | 4.0146 | -0.23346 | -0.041199 | 4.0375 | -117.0731 | -117.1417 | 4.1153 | 3.9551 | 3.9963 | -0.082397 | -0.041198 | 0.041199 | -0.059509 | 0.07782 | 0.022888 | 0.022888 | 0.091553 | 4.0787 | 4.129 | -117.1463 | -117.1646 | 3.9963 | 4.0604 | 4.0192 | 4.0054
3550.5156 | 102.5116 | -45.6619 | 75.4623 | 0.13565 | 0.006242 | -0.031373 | 0.037762 | 0.027021 | -0.043135 | 0.028878 | 0.054382 | 0.015893 | 0.012066 | 0.022507 | 0.023717 | 0.028779 | 0.019574 | -0.09613 | -0.059509 | -0.036621 | -0.027466 | 0.059509 | -0.18768 | 0.059509 | 0.009155 | -0.15564 | -0.10071 | -0.15106 | -0.14648 | -0.14648 | 0.091553 | 45.6253 | -75.5219 | -75.4898 | 45.7214 | 45.7214 | 45.4742 | 0.09613 | -0.15106 | 45.5612 | -75.618 | -75.6134 | 45.5154 | 45.7535 | 45.5154 | 0.19226 | -0.045776 | 0.09613 | 0.009155 | -0.045776 | -0.050354 | -0.022888 | -0.054932 | 45.6024 | 45.5063 | -75.499 | -75.563 | 45.6345 | 45.5109 | 45.5658 | 45.6711
3552.25 | 120.9595 | -115.7822 | 4.7424 | 0.028839 | 0.010301 | -0.028809 | 0.035412 | -0.016344 | -0.02754 | -0.021324 | -0.058533 | -0.061224 | -0.00096545 | 0.041947 | -0.016231 | -0.0101 | -0.011615 | -0.086975 | -0.041199 | 0.032043 | -0.032043 | 0.068665 | -0.041199 | -0.09613 | -0.009155 | -0.18768 | 0.27008 | 0.027466 | 0.11902 | 0.022888 | 0.14191 | 115.8142 | -4.7836 | -4.7745 | 115.8508 | 115.686 | 115.741 | -0.12817 | -0.073242 | 116.0522 | -4.9301 | -4.715 | 115.9012 | 115.9241 | 115.8051 | -0.12817 | -0.24719 | 0.036622 | -0.064086 | -0.15106 | -0.24262 | -0.073242 | -0.45776 | 115.741 | 115.5945 | -4.7104 | -4.4724 | 115.7501 | 115.8096 | 115.6952 | 115.773
3554.0469 | 121.2708 | -113.5941 | 7.251 | 0.0059509 | 0.012651 | -0.033509 | 0.033917 | -0.016344 | -0.028608 | -0.023674 | -0.076843 | -0.062079 | -0.00032465 | 0.041092 | -0.017726 | -0.0098864 | -0.012469 | -0.041199 | -0.064087 | 0.013733 | 0.041199 | 0.17853 | 0.050354 | -0.013733 | 0.086975 | -0.009155 | 0.21515 | 0.091553 | 0.19684 | 0.10986 | 0.16937 | 113.6078 | -7.3151 | -7.2098 | 113.7726 | 113.5803 | 113.6444 | -0.027466 | 0.036621 | 113.8092 | -7.2601 | -7.1594 | 113.7909 | 113.7634 | 113.7039 | -0.045776 | -0.10529 | 0.16479 | 0.027466 | -0.018311 | -0.1236 | -0.07782 | -0.2243 | 113.53 | 113.5849 | -7.2372 | -7.0358 | 113.6353 | 113.6856 | 113.5529 | 113.681
3555.7656 | 121.3028 | -97.4167 | 23.2681 | 0.02121 | 0.01201 | -0.028809 | 0.037762 | -0.016344 | -0.028395 | -0.020897 | -0.076843 | -0.060156 | 0.0020252 | 0.048569 | -0.015804 | -0.0086048 | -0.011828 | -0.041199 | -0.059509 | 0.041199 | -0.004578 | 0.032043 | -0.10529 | -0.15106 | 0.082397 | -0.18768 | 0.34332 | 0.082397 | 0.1236 | 0.018311 | 0.11902 | 97.4579 | -23.3276 | -23.2727 | 97.4487 | 97.2656 | 97.3114 | -0.19226 | -0.14649 | 97.76 | -23.4558 | -23.1857 | 97.5403 | 97.5357 | 97.435 | -0.2243 | -0.32501 | -0.009156 | -0.045777 | -0.21973 | -0.26093 | -0.10071 | -0.53101 | 97.3572 | 97.229 | -23.2269 | -22.9248 | 97.4121 | 97.4991 | 97.3755 | 97.4991
3557.5469 | 120.5429 | -115.3839 | 4.9072 | 0.02121 | 0.016282 | -0.030304 | 0.0042233 | 0.026594 | -0.081373 | 0.02845 | 0.057434 | 0.016107 | 0.0080066 | 0.027421 | -0.032894 | -0.026335 | -0.019305 | -0.27466 | -0.004578 | 0.12817 | 0.091553 | 0.086975 | 0.091553 | 0.10071 | -0.35706 | 0.086975 | -0.091553 | -0.16479 | 0.086975 | 0.09613 | 0.10071 | 115.5121 | -4.9118 | -4.8157 | 115.4709 | 115.4846 | 115.4755 | -0.027466 | -0.036621 | 115.2924 | -4.8203 | -5.072 | 115.4709 | 115.4846 | 115.48 | 0.19226 | 0.18768 | -0.041199 | -0.036621 | 0.17853 | -0.073242 | -0.13275 | 0.17853 | 115.3793 | 115.4709 | -4.7791 | -4.9988 | 115.4755 | 115.2191 | 115.1093 | 115.0269
3559.3438 | 120.9229 | -115.3976 | 5.2551 | 0.02121 | 0.013078 | -0.032227 | 0.034344 | -0.0024587 | -0.031172 | -0.037132 | 0.051331 | 0.016107 | -0.00075185 | 0.022294 | 0.023076 | 0.028138 | 0.019147 | -0.064087 | -0.032043 | -0.027466 | 0.086975 | 0.091553 | 0.086975 | 0.09613 | 0.009155 | -0.26093 | -0.086975 | 0.045776 | 0.086975 | 0.086975 | 0.09613 | 115.3702 | -5.2872 | -5.1682 | 115.4892 | 115.4938 | 115.4846 | 0.1236 | 0.11444 | 115.3107 | -5.5161 | -5.2094 | 115.4846 | 115.4938 | 115.4846 | 0.1831 | 0.17395 | 0.11902 | 0.11444 | 0.17395 | 0.13275 | -0.004577 | -0.17395 | 115.3656 | 115.1367 | -5.2826 | -5.3421 | 115.4846 | 115.4434 | 115.3336 | 115.4068
3561.125 | 121.0098 | -114.2807 | 6.2942 | 0.01358 | 0.011796 | -0.03415 | 0.035626 | -0.012926 | -0.030531 | -0.021537 | -0.11652 | -0.063147 | -0.0033154 | 0.040238 | -0.020717 | -0.0088184 | -0.014605 | -0.036621 | -0.064087 | 0.009155 | 0.036621 | 0.064087 | -0.054932 | -0.13275 | 0.073242 | -0.054932 | 0.33875 | 0.082397 | 0.15106 | -0.009155 | 0.041199 | 114.2899 | -6.3583 | -6.2576 | 114.3448 | 114.1479 | 114.2258 | -0.14191 | -0.064087 | 114.6194 | -6.3492 | -6.2119 | 114.4318 | 114.3219 | 114.2715 | -0.29755 | -0.3479 | 0.054932 | 0.027466 | -0.18768 | -0.25635 | -0.073242 | -0.39368 | 114.2166 | 114.2258 | -6.2851 | -5.9555 | 114.3173 | 114.3631 | 114.2441 | 114.3539
3562.9062 | 120.9366 | -116.2903 | 4.5044 | 0.01358 | 0.01436 | -0.034577 | 0.03584 | -0.018053 | -0.030958 | -0.022178 | -0.23248 | -0.061011 | -0.0028882 | 0.035966 | -0.021572 | -0.010527 | -0.013324 | -0.082397 | -0.036621 | -0.009155 | -0.082397 | -0.17853 | -0.35706 | -0.35248 | -0.068665 | 0.059509 | 0.1236 | -0.013733 | 0.032043 | -0.28839 | -0.27924 | 116.2811 | -4.541 | -4.5868 | 116.1118 | 115.9378 | 115.9332 | -0.34332 | -0.3479 | 116.4139 | -4.4449 | -4.5181 | 116.3223 | 116.011 | 116.0019 | -0.40283 | -0.41199 | -0.16937 | -0.073242 | -0.091553 | -0.13733 | -0.027466 | -0.064087 | 116.2537 | 116.3498 | -4.5135 | -4.3808 | 116.2079 | 116.2766 | 116.2079 | 116.2216
3564.6406 | 121.019 | -118.4967 | 2.3666 | 0.01358 | 0.013505 | -0.033082 | 0.029004 | -0.029589 | -0.030745 | -0.027305 | 0.051331 | -0.070837 | -0.0016064 | 0.035538 | -0.023067 | -0.018645 | -0.020587 | -0.07782 | -0.018311 | -0.022888 | -0.21973 | -0.16022 | 0.09613 | 0.091553 | -0.086975 | 0.027466 | -0.036621 | -0.004578 | 0.004578 | -0.43945 | 0.09613 | 118.4738 | -2.3849 | -2.5864 | 118.3365 | 118.5883 | 118.5928 | 0.11444 | 0.11902 | 118.4601 | -2.3392 | -2.3712 | 118.5013 | 118.5928 | 118.0573 | 0.13275 | -0.40283 | -0.13733 | -0.19684 | 0.041199 | 0.032043 | 0.004577 | 0.064087 | 118.4784 | 118.5242 | -2.3895 | -2.4033 | 118.277 | 118.4921 | 118.4189 | 118.4097
3566.4531 | 121.1105 | -117.3889 | 3.3188 | 0.02121 | 0.012651 | -0.0318 | 0.037335 | -0.013353 | -0.025404 | -0.022819 | -0.073792 | -0.063574 | -0.0016064 | 0.037034 | -0.016231 | -0.0088184 | -0.012256 | -0.050354 | -0.041199 | 0.004578 | -0.004578 | 0.14191 | -0.009155 | -0.082397 | 0.041199 | 0.013733 | -0.022888 | 0.064087 | 0.086975 | 0.045776 | 0.14648 | 117.3935 | -3.36 | -3.3234 | 117.5308 | 117.3065 | 117.3798 | -0.086975 | -0.013733 | 117.366 | -3.3051 | -3.2547 | 117.4759 | 117.5354 | 117.4347 | 0.16937 | 0.068664 | 0.13733 | -0.009156 | 0.10986 | 0.086975 | -0.045777 | 0.036621 | 117.3477 | 117.4026 | -3.3142 | -3.3417 | 117.3843 | 117.453 | 117.3386 | 117.4301
3568.25 | 121.1288 | -114.7751 | 6.0379 | 0.028839 | 0.014146 | -0.031373 | 0.037762 | -0.016558 | -0.027967 | -0.021965 | -0.043274 | -0.064429 | -0.00182 | 0.039384 | -0.017085 | -0.008391 | -0.010333 | -0.059509 | -0.036621 | -0.004578 | -0.009155 | 0.13275 | 0.032043 | -0.041199 | 0.032043 | -0.013733 | -0.004578 | 0.073242 | 0.091553 | 0.045776 | 0.13733 | 114.7705 | -6.0745 | -6.0471 | 114.9078 | 114.7339 | 114.8071 | -0.036621 | 0.036621 | 114.7705 | -6.0516 | -5.9647 | 114.8666 | 114.9124 | 114.8209 | 0.14191 | 0.050354 | 0.13733 | -0.004577 | 0.096131 | 0.07782 | -0.032043 | -0.009155 | 114.7385 | 114.7614 | -6.0425 | -6.0425 | 114.7659 | 114.8483 | 114.7156 | 114.8071
3570.0469 | 120.9961 | -114.4226 | 6.3538 | 0.036468 | 0.015855 | -0.030518 | 0.034772 | -0.024035 | -0.028395 | -0.02346 | 0.045227 | 0.015039 | -0.0024608 | 0.040238 | -0.02563 | -0.020995 | -0.016101 | -0.041199 | -0.036621 | -0.036621 | -0.041199 | -0.13733 | -0.068665 | 0.091553 | 0 | 0.032043 | -0.036621 | 0.050354 | 0.07782 | -0.16022 | 0.10071 | 114.386 | -6.3904 | -6.395 | 114.2853 | 114.5142 | 114.3539 | 0.12817 | -0.032044 | 114.386 | -6.3217 | -6.3034 | 114.5004 | 114.5233 | 114.2624 | 0.13733 | -0.1236 | -0.10071 | -0.004578 | 0.11444 | 0.086975 | 0 | 0.068664 | 114.386 | 114.4547 | -6.3904 | -6.3904 | 114.3814 | 114.473 | 114.3814 | 114.4226
3571.8281 | 121.0052 | -116.5878 | 4.3121 | 0.02121 | 0.013933 | -0.0318 | 0.036908 | -0.015917 | -0.030531 | -0.021324 | -0.18365 | -0.060797 | -0.0011792 | 0.032975 | -0.019863 | -0.011382 | -0.012469 | -0.10986 | -0.009155 | -0.041199 | -0.07782 | 0.036621 | -0.19684 | -0.37537 | -0.068665 | 0.045776 | -0.064087 | -0.022888 | 0.032043 | -0.050354 | -0.16937 | 116.5466 | -4.3213 | -4.39 | 116.6245 | 116.2125 | 116.391 | -0.33417 | -0.15564 | 116.5237 | -4.2664 | -4.335 | 116.6199 | 116.4185 | 116.5375 | -0.10529 | 0.013733 | 0.07782 | -0.036621 | 0.09613 | 0.041199 | 0.032044 | 0.10986 | 116.5787 | 116.6336 | -4.3533 | -4.3762 | 116.51 | 116.5649 | 116.478 | 116.5192
3573.625 | 121.0281 | -117.6682 | 3.2593 | 0.028839 | 0.014573 | -0.031373 | 0.039685 | -0.012285 | -0.030317 | -0.02346 | -0.034119 | -0.078314 | -0.00096545 | 0.035325 | -0.015377 | -0.010741 | -0.014178 | -0.064087 | 0 | -0.032043 | -0.10071 | -0.068665 | -0.36163 | -0.15106 | -0.086975 | 0.036621 | -0.050354 | -0.022888 | 0 | -0.09613 | -0.12817 | 117.6361 | -3.2593 | -3.36 | 117.5995 | 117.5171 | 117.3065 | -0.11902 | -0.32959 | 117.6178 | -3.2227 | -3.2822 | 117.6682 | 117.54 | 117.572 | -0.07782 | -0.045776 | -0.036622 | -0.068665 | 0.050354 | 0.027466 | 0.032043 | 0.086975 | 117.6682 | 117.7048 | -3.2913 | -3.3096 | 117.5674 | 117.6453 | 117.6041 | 117.5812
3575.375 | 121.0602 | -116.6519 | 4.2892 | 0.01358 | 0.016282 | -0.031586 | 0.037335 | -0.014849 | -0.029249 | -0.019828 | -0.12262 | -0.068701 | -0.0020336 | 0.038956 | -0.017299 | -0.011168 | -0.013537 | -0.050354 | 0.009155 | -0.054932 | -0.064087 | 0.054932 | -0.17853 | -0.3067 | -0.068665 | 0.041199 | -0.054932 | 0.022888 | 0.068665 | -0.022888 | -0.068665 | 116.597 | -4.2801 | -4.3533 | 116.7068 | 116.3452 | 116.4734 | -0.25177 | -0.1236 | 116.597 | -4.248 | -4.2664 | 116.7206 | 116.5833 | 116.629 | -0.013733 | 0.032044 | 0.10986 | -0.009155 | 0.1236 | 0.07782 | 0.064087 | 0.096131 | 116.6611 | 116.6931 | -4.3442 | -4.3442 | 116.5878 | 116.6748 | 116.6016 | 116.5833
3577.1719 | 121.1334 | -117.7231 | 3.1357 | 0.02121 | 0.013933 | -0.03415 | 0.036267 | -0.019121 | -0.029463 | -0.024314 | 0.008606 | -0.062506 | -0.00182 | 0.03917 | -0.016231 | -0.0071094 | -0.011187 | -0.050354 | -0.036621 | 0 | -0.013733 | 0.11444 | 0.045776 | 0.045776 | 0.022888 | 0.004578 | -0.032043 | 0.064087 | 0.14648 | 0.073242 | 0.16479 | 117.7231 | -3.1723 | -3.1494 | 117.8375 | 117.7689 | 117.7689 | 0.045776 | 0.045776 | 117.691 | -3.1311 | -3.0716 | 117.8696 | 117.8879 | 117.7963 | 0.19684 | 0.10529 | 0.11444 | -0.013733 | 0.17853 | 0.09613 | -0.036621 | 0.036621 | 117.6865 | 117.7277 | -3.1357 | -3.1677 | 117.7094 | 117.7872 | 117.6727 | 117.746
3578.9062 | 121.1014 | -115.416 | 5.4474 | 0.02121 | 0.015855 | -0.033722 | 0.037549 | -0.015062 | -0.029249 | -0.021965 | 0.008606 | -0.06272 | -0.0026744 | 0.038529 | -0.017726 | -0.010955 | -0.011615 | -0.041199 | -0.041199 | -0.022888 | 0 | 0.11444 | 0.027466 | 0.036621 | 0.018311 | 0.013733 | -0.027466 | 0.068665 | 0.13733 | 0.059509 | 0.15564 | 115.3931 | -5.4886 | -5.4474 | 115.5304 | 115.4526 | 115.4434 | 0.059509 | 0.050354 | 115.3885 | -5.4337 | -5.3787 | 115.5533 | 115.5716 | 115.4755 | 0.18311 | 0.086975 | 0.13733 | 0.022888 | 0.16479 | 0.096131 | -0.018311 | 0.041199 | 115.3748 | 115.4297 | -5.4703 | -5.4749 | 115.416 | 115.4846 | 115.3748 | 115.4343
3580.7031 | 121.1243 | -117.9108 | 2.9617 | 0.036468 | 0.011583 | -0.031373 | 0.035412 | -0.014208 | -0.028395 | -0.020469 | 0.017761 | -0.062506 | -0.00011105 | 0.038315 | -0.016658 | -0.0092456 | -0.015246 | -0.018311 | -0.045776 | 0.009155 | 0.018311 | 0.15564 | 0.032043 | 0.068665 | 0.050354 | 0.009155 | -0.022888 | 0.059509 | 0.11444 | 0.036621 | 0.14191 | 117.9199 | -3.0075 | -2.9434 | 118.0664 | 117.9794 | 117.9428 | 0.05951 | 0.022888 | 117.8879 | -2.9526 | -2.9022 | 118.0252 | 118.0527 | 117.9474 | 0.16479 | 0.059509 | 0.14649 | 0.009156 | 0.13733 | 0.082397 | -0.054931 | 0.032043 | 117.865 | 117.9199 | -2.9526 | -2.9846 | 117.9291 | 117.9703 | 117.8925 | 117.9611
3582.5156 | 121.2799 | -116.4368 | 4.4312 | 0.036468 | 0.01436 | -0.0318 | 0.037335 | -0.015917 | -0.027754 | -0.022605 | 0.011658 | -0.061651 | -0.00053825 | 0.04451 | -0.014522 | -0.0096728 | -0.014178 | -0.041199 | -0.064087 | 0.004578 | 0.009155 | 0.13275 | 0.018311 | 0.032043 | 0.018311 | 0.004578 | -0.041199 | 0.041199 | 0.11444 | 0.032043 | 0.14191 | 116.4413 | -4.4952 | -4.422 | 116.5695 | 116.4688 | 116.4551 | 0.027465 | 0.013733 | 116.3956 | -4.4266 | -4.39 | 116.5512 | 116.5787 | 116.4688 | 0.18311 | 0.073242 | 0.12817 | 0.004577 | 0.15564 | 0.082398 | -0.068665 | 0.045777 | 116.3727 | 116.4413 | -4.4266 | -4.4724 | 116.4459 | 116.478 | 116.3956 | 116.4551
3584.2656 | 121.3486 | -120.1675 | 0.80109 | 0.01358 | 0.014787 | -0.034577 | 0.03648 | 0.00031832 | -0.029249 | -0.02346 | 0.011658 | -0.062506 | -0.00075185 | 0.032548 | -0.019863 | -0.012236 | -0.01076 | 0.009155 | -0.059509 | 0 | 0.054932 | 0.20142 | 0.09613 | 0.09613 | 0.10529 | 0.004578 | -0.009155 | 0.11902 | 0.19226 | 0.11444 | 0.1831 | 120.1675 | -0.86059 | -0.74615 | 120.369 | 120.2637 | 120.2637 | 0.09613 | 0.09613 | 120.1584 | -0.79651 | -0.68207 | 120.3598 | 120.3506 | 120.282 | 0.19226 | 0.1236 | 0.20142 | 0.054932 | 0.20142 | 0.12817 | -0.059509 | 0.013733 | 120.108 | 120.1721 | -0.80109 | -0.81024 | 120.2225 | 120.2866 | 120.1767 | 120.2728
3586.0625 | 121.1838 | -120.1355 | 0.96588 | 0.02121 | 0.015001 | -0.031586 | 0.034985 | -0.016131 | -0.031172 | -0.023246 | 0.011658 | -0.061438 | -0.0020336 | 0.034684 | -0.021999 | -0.011382 | -0.014819 | -0.041199 | -0.032043 | 0 | -0.013733 | 0.10071 | -0.009155 | 0.009155 | -0.036621 | 0.041199 | -0.036621 | -0.009155 | 0.045776 | -0.009155 | 0.073242 | 120.1355 | -0.99792 | -0.97961 | 120.2362 | 120.1447 | 120.1263 | 0.009155 | -0.009155 | 120.0989 | -0.92468 | -0.97504 | 120.1813 | 120.2087 | 120.1263 | 0.10986 | 0.027466 | 0.10071 | -0.013733 | 0.082397 | 0.027466 | -0.032043 | 0.07782 | 120.1035 | 120.1767 | -0.96588 | -1.0025 | 120.1218 | 120.1263 | 120.0943 | 120.0989
3587.7812 | 121.3257 | -120.3094 | 0.7782 | 0.0059509 | 0.014787 | -0.033722 | 0.034772 | -0.016558 | -0.029463 | -0.021324 | 0.014709 | -0.062292 | -0.00182 | 0.032975 | -0.019222 | -0.0101 | -0.011828 | 0.004578 | -0.054932 | 0.009155 | 0.064087 | 0.20599 | 0.10986 | 0.086975 | 0.09613 | 0.009155 | -0.009155 | 0.09613 | 0.19226 | 0.10986 | 0.19684 | 120.3186 | -0.83313 | -0.71411 | 120.5154 | 120.3964 | 120.4193 | 0.07782 | 0.10071 | 120.3003 | -0.76904 | -0.68207 | 120.5017 | 120.5063 | 120.4193 | 0.20599 | 0.11902 | 0.19684 | 0.054932 | 0.20142 | 0.10528 | -0.064087 | 0.01831 | 120.2545 | 120.3186 | -0.76904 | -0.78735 | 120.3735 | 120.4056 | 120.314 | 120.4056
3589.5938 | 121.2433 | -119.4489 | 1.6663 | 0.028839 | 0.016282 | -0.033082 | 0.037549 | -0.016344 | -0.029249 | -0.020897 | 0.0055542 | -0.059729 | -0.00053825 | 0.031052 | -0.017513 | -0.0101 | -0.012469 | -0.064087 | -0.009155 | -0.050354 | -0.068665 | 0.054932 | -0.013733 | -0.022888 | -0.064087 | 0.059509 | -0.054932 | 0.004578 | 0.068665 | -0.022888 | 0.11444 | 119.3985 | -1.6754 | -1.7349 | 119.5038 | 119.426 | 119.4351 | 0.027466 | 0.036621 | 119.3939 | -1.6068 | -1.6617 | 119.5175 | 119.5633 | 119.426 | 0.16937 | 0.032044 | 0.10529 | -0.018311 | 0.1236 | 0.05951 | 0.041199 | 0.11444 | 119.4397 | 119.5084 | -1.7166 | -1.7212 | 119.3802 | 119.4534 | 119.3848 | 119.3848
3591.3438 | 121.3486 | -120.5887 | 0.52185 | 0.02121 | 0.015214 | -0.034791 | 0.035412 | -0.017412 | -0.029463 | -0.021324 | 0.008606 | -0.061865 | -0.0016064 | 0.030625 | -0.018154 | -0.010527 | -0.010119 | -0.027466 | -0.045776 | 0.004578 | 0.032043 | 0.16022 | 0.082397 | 0.082397 | 0.091553 | 0.004578 | -0.004578 | 0.10071 | 0.19684 | 0.11902 | 0.19684 | 120.5933 | -0.56763 | -0.48981 | 120.7489 | 120.6711 | 120.6711 | 0.077819 | 0.077819 | 120.5841 | -0.51727 | -0.42114 | 120.7855 | 120.7855 | 120.7077 | 0.20142 | 0.1236 | 0.15564 | 0.027465 | 0.20142 | 0.10529 | -0.050354 | 0.009156 | 120.5429 | 120.5933 | -0.51727 | -0.52643 | 120.6207 | 120.6894 | 120.5612 | 120.6802
3593.1406 | 121.2982 | -120.2179 | 0.86975 | 0.028839 | 0.014573 | -0.032227 | 0.037976 | -0.015062 | -0.028822 | -0.022392 | 0.011658 | -0.061224 | -0.0037426 | 0.035538 | -0.016445 | -0.0092456 | -0.013751 | -0.022888 | -0.036621 | 0.027466 | 0.041199 | 0.18768 | 0.059509 | 0.064087 | 0.086975 | 0.013733 | -0.009155 | 0.082397 | 0.14648 | 0.059509 | 0.16022 | 120.2454 | -0.90637 | -0.82855 | 120.4056 | 120.282 | 120.2774 | 0.036621 | 0.032043 | 120.2087 | -0.85602 | -0.78735 | 120.3644 | 120.3781 | 120.2774 | 0.16937 | 0.068664 | 0.16022 | 0.013733 | 0.15564 | 0.091552 | -0.064087 | 0.022888 | 120.1813 | 120.2316 | -0.84229 | -0.87891 | 120.2591 | 120.3003 | 120.195 | 120.3049
3594.9531 | 121.2524 | -120.7489 | 0.40283 | 0.028839 | 0.017564 | -0.032654 | 0.038189 | -0.012499 | -0.027967 | -0.02111 | 0.011658 | -0.061011 | 0.00052975 | 0.030411 | -0.017513 | -0.012236 | -0.013751 | -0.032043 | -0.022888 | -0.032043 | -0.032043 | 0.07782 | 0.027466 | 0 | 0.013733 | 0.045776 | -0.032043 | 0.036621 | 0.10529 | 0.009155 | 0.14191 | 120.7169 | -0.42572 | -0.43488 | 120.8267 | 120.7489 | 120.7764 | 0.032043 | 0.059509 | 120.7169 | -0.35706 | -0.36621 | 120.8542 | 120.8908 | 120.7581 | 0.17395 | 0.041198 | 0.10986 | 0 | 0.13733 | 0.068664 | 0.009155 | 0.077819 | 120.726 | 120.7947 | -0.43488 | -0.43488 | 120.7169 | 120.7855 | 120.7169 | 120.7626
3596.7344 | 121.3394 | -120.7443 | 0.4303 | 0.0059509 | 0.013505 | -0.033082 | 0.034131 | -0.011858 | -0.027754 | -0.020897 | 0.011658 | -0.061011 | 0.00074335 | 0.03917 | -0.016445 | -0.0079638 | -0.013965 | -0.054932 | -0.027466 | -0.004578 | -0.018311 | 0.11444 | 0.013733 | 0.032043 | 0.009155 | 0.013733 | -0.022888 | 0.041199 | 0.13275 | 0.045776 | 0.15564 | 120.7397 | -0.45776 | -0.44861 | 120.8588 | 120.7764 | 120.7581 | 0.036621 | 0.018311 | 120.7214 | -0.41657 | -0.3891 | 120.8771 | 120.9 | 120.7901 | 0.17853 | 0.068664 | 0.11902 | -0.013733 | 0.15564 | 0.064087 | -0.022888 | 0.036621 | 120.7169 | 120.7581 | -0.43488 | -0.45319 | 120.726 | 120.7855 | 120.6894 | 120.7535
3598.4688 | 121.3806 | -120.6848 | 0.47607 | 0.01358 | 0.012864 | -0.035218 | 0.035412 | -0.015062 | -0.029463 | -0.02111 | 0.008606 | -0.061438 | -0.0016064 | 0.039811 | -0.017085 | -0.0094592 | -0.013965 | -0.045776 | -0.032043 | -0.009155 | 0 | 0.12817 | 0.045776 | 0.054932 | 0.050354 | 0.018311 | -0.018311 | 0.064087 | 0.16937 | 0.10529 | 0.17395 | 120.6757 | -0.50812 | -0.47607 | 120.813 | 120.7397 | 120.7306 | 0.064087 | 0.054931 | 120.6665 | -0.45776 | -0.41199 | 120.8542 | 120.8588 | 120.7901 | 0.19226 | 0.1236 | 0.13733 | 0.009155 | 0.18768 | 0.082398 | -0.022888 | 0.036622 | 120.6528 | 120.7031 | -0.48523 | -0.49439 | 120.6848 | 120.7489 | 120.639 | 120.7352
3600.2656 | 121.2982 | -118.0847 | 3.1082 | -0.0016786 | 0.01436 | -0.030518 | 0.037335 | -0.01549 | -0.028822 | -0.022178 | 0.008606 | -0.062079 | -0.0020336 | 0.036393 | -0.016445 | -0.0098864 | -0.011828 | -0.050354 | -0.036621 | -0.018311 | -0.022888 | 0.10529 | 0.013733 | 0.032043 | 0.004578 | 0.022888 | -0.022888 | 0.041199 | 0.1236 | 0.045776 | 0.15106 | 118.0664 | -3.1448 | -3.1311 | 118.19 | 118.1168 | 118.0984 | 0.050354 | 0.032044 | 118.0618 | -3.0853 | -3.067 | 118.2083 | 118.2358 | 118.1305 | 0.17395 | 0.068664 | 0.1236 | -0.004577 | 0.14648 | 0.064087 | -0.01831 | 0.045776 | 118.0481 | 118.1076 | -3.1265 | -3.1311 | 118.0618 | 118.1259 | 118.0344 | 118.0893
3602.0625 | 121.3852 | -120.7809 | 0.37994 | 0.01358 | 0.013719 | -0.033509 | 0.03584 | -0.013994 | -0.029676 | -0.020897 | 0.008606 | -0.061651 | -0.0016064 | 0.035111 | -0.01794 | -0.010741 | -0.0099056 | -0.009155 | -0.059509 | 0 | 0.064087 | 0.20142 | 0.091553 | 0.086975 | 0.10071 | 0.022888 | -0.009155 | 0.09613 | 0.19684 | 0.10529 | 0.17853 | 120.7809 | -0.43945 | -0.31586 | 120.9824 | 120.8679 | 120.8725 | 0.086975 | 0.091553 | 120.7718 | -0.35706 | -0.28381 | 120.9778 | 120.9595 | 120.8862 | 0.18768 | 0.11444 | 0.20142 | 0.064087 | 0.20599 | 0.10528 | -0.059509 | 0.032043 | 120.7214 | 120.8038 | -0.37994 | -0.3891 | 120.845 | 120.8771 | 120.7718 | 120.8817
3603.7812 | 121.3943 | -120.7352 | 0.39368 | 0.036468 | 0.016069 | -0.032227 | 0.037976 | -0.016985 | -0.027754 | -0.023033 | 0.014709 | -0.059302 | -0.00032465 | 0.035538 | -0.01559 | -0.0096728 | -0.012896 | 0.013733 | -0.054932 | 0.018311 | 0.073242 | 0.1831 | 0.064087 | 0.054932 | 0.11444 | 0.009155 | -0.032043 | 0.11444 | 0.17395 | 0.091553 | 0.17853 | 120.7535 | -0.44861 | -0.32044 | 120.9183 | 120.7901 | 120.7993 | 0.036621 | 0.045776 | 120.7031 | -0.38452 | -0.27924 | 120.9091 | 120.9137 | 120.8267 | 0.21057 | 0.1236 | 0.16479 | 0.054931 | 0.20599 | 0.14648 | -0.073243 | 0.041198 | 120.6802 | 120.7443 | -0.37537 | -0.42572 | 120.8084 | 120.8496 | 120.7489 | 120.8496
3605.5781 | 119.87 | -116.629 | 2.8839 | 0.02121 | 0.018419 | -0.028382 | 0.036694 | -0.014849 | -0.025404 | -0.020469 | 0.017761 | -0.061865 | -0.0011792 | 0.027634 | -0.016658 | -0.010955 | -0.012896 | -0.041199 | -0.050354 | 0 | 0.018311 | 0.14191 | 0.027466 | 0.032043 | 0.041199 | 0.013733 | -0.013733 | 0.045776 | 0.1236 | 0.050354 | 0.14191 | 116.629 | -2.9343 | -2.8656 | 116.7709 | 116.6611 | 116.6565 | 0.032043 | 0.027466 | 116.6153 | -2.8702 | -2.8381 | 116.7526 | 116.7709 | 116.6794 | 0.15564 | 0.064087 | 0.14191 | 0.018311 | 0.13733 | 0.059509 | -0.050354 | 0.027466 | 116.5787 | 116.6428 | -2.8839 | -2.8976 | 116.6473 | 116.6748 | 116.5878 | 116.6702
3607.3906 | 120.8496 | -119.3527 | 1.2222 | 0.02121 | 0.015001 | -0.031373 | 0.037121 | -0.0090811 | -0.030104 | -0.02111 | 0.008606 | -0.069342 | 0.00031615 | 0.033829 | -0.01559 | -0.010314 | -0.016528 | -0.045776 | -0.032043 | -0.036621 | -0.018311 | 0.09613 | -0.032043 | -0.018311 | -0.004578 | 0.041199 | -0.022888 | 0.032043 | 0.045776 | -0.027466 | 0.10529 | 119.3161 | -1.2543 | -1.2405 | 119.4489 | 119.3344 | 119.3207 | 0.01831 | 0.004578 | 119.3298 | -1.181 | -1.1902 | 119.3985 | 119.458 | 119.3253 | 0.12817 | -0.004578 | 0.13275 | 0.01831 | 0.068664 | 0.054931 | 0.004578 | 0.064087 | 119.3207 | 119.3939 | -1.2589 | -1.2451 | 119.3344 | 119.3848 | 119.3069 | 119.3481
3609.1719 | 121.0327 | -119.7144 | 0.96588 | 0.02121 | 0.013719 | -0.035218 | 0.036694 | -0.022112 | -0.029036 | -0.02111 | 0.008606 | -0.060584 | -0.0024608 | 0.035966 | -0.019435 | -0.0101 | -0.014605 | -0.013733 | -0.045776 | 0.009155 | 0.064087 | 0.19226 | 0.086975 | 0.07782 | 0.068665 | 0.027466 | -0.009155 | 0.10529 | 0.1831 | 0.10071 | 0.17853 | 119.7235 | -1.0117 | -0.90179 | 119.9066 | 119.7922 | 119.8013 | 0.068665 | 0.07782 | 119.7052 | -0.93841 | -0.86059 | 119.8975 | 119.8929 | 119.8151 | 0.18768 | 0.10986 | 0.18311 | 0.054932 | 0.19226 | 0.11444 | -0.054931 | 0.036621 | 119.6686 | 119.7418 | -0.95673 | -0.97504 | 119.7784 | 119.8196 | 119.7006 | 119.783
3610.9688 | 120.9686 | -120.195 | 0.6546 | 0.01358 | 0.015001 | -0.032868 | 0.037549 | -0.015917 | -0.029676 | -0.019188 | 0.0055542 | -0.059515 | -0.00182 | 0.032975 | -0.01559 | -0.011168 | -0.013965 | -0.073242 | -0.009155 | -0.018311 | -0.09613 | 0.013733 | -0.073242 | -0.064087 | -0.064087 | 0.045776 | -0.050354 | 0.004578 | 0.022888 | -0.041199 | 0.086975 | 120.1767 | -0.66376 | -0.75073 | 120.2087 | 120.1309 | 120.1218 | -0.045776 | -0.054931 | 120.1447 | -0.60883 | -0.65002 | 120.2179 | 120.282 | 120.1538 | 0.13733 | 0.009155 | 0.032044 | -0.077819 | 0.073242 | 0.054932 | 0.009156 | 0.09613 | 120.1859 | 120.2408 | -0.67291 | -0.70496 | 120.0989 | 120.1996 | 120.1218 | 120.1309
3612.75 | 121.019 | -120.314 | 0.5722 | 0.02121 | 0.015001 | -0.032013 | 0.039258 | -0.014422 | -0.028395 | -0.02111 | 0.0055542 | -0.058875 | -0.00096545 | 0.028275 | -0.014308 | -0.010741 | -0.013751 | -0.10071 | -0.022888 | -0.022888 | -0.091553 | 0.013733 | -0.064087 | -0.054932 | -0.073242 | 0.036621 | -0.036621 | -0.004578 | 0.036621 | -0.045776 | 0.09613 | 120.2911 | -0.59509 | -0.66376 | 120.3278 | 120.2591 | 120.2499 | -0.032044 | -0.041199 | 120.2774 | -0.53558 | -0.57678 | 120.3506 | 120.4102 | 120.2682 | 0.13275 | -0.009155 | 0.036621 | -0.068665 | 0.073242 | 0.032043 | 0 | 0.073242 | 120.2911 | 120.3506 | -0.59509 | -0.60883 | 120.2225 | 120.3094 | 120.2133 | 120.2408
3614.5469 | 121.0556 | -120.488 | 0.46234 | 0.028839 | 0.016496 | -0.033082 | 0.039044 | -0.012926 | -0.02989 | -0.021965 | 0.008606 | -0.060797 | 0.00010255 | 0.038956 | -0.015163 | -0.0101 | -0.014819 | -0.086975 | -0.022888 | -0.036621 | -0.082397 | 0.027466 | -0.068665 | -0.041199 | -0.054932 | 0.041199 | -0.027466 | 0.013733 | 0.050354 | -0.027466 | 0.10986 | 120.4514 | -0.48523 | -0.54474 | 120.5154 | 120.4468 | 120.4193 | -0.004578 | -0.032044 | 120.4605 | -0.42114 | -0.44861 | 120.5383 | 120.5978 | 120.4605 | 0.13733 | 0 | 0.064087 | -0.045776 | 0.07782 | 0.041199 | 0.013733 | 0.068665 | 120.4651 | 120.5292 | -0.49896 | -0.48981 | 120.4056 | 120.5017 | 120.401 | 120.433
3616.2812 | 121.1609 | -120.4147 | 0.49439 | 0.02121 | 0.015428 | -0.032441 | 0.034131 | -0.014208 | -0.028822 | -0.021965 | 0.011658 | -0.06272 | -0.0011792 | 0.040879 | -0.015377 | -0.0071094 | -0.0092648 | 0.004578 | -0.064087 | 0.032043 | 0.041199 | 0.20599 | 0.054932 | 0.086975 | 0.10071 | 0.009155 | -0.018311 | 0.1236 | 0.19226 | 0.082397 | 0.20142 | 120.4468 | -0.55847 | -0.45319 | 120.6207 | 120.5017 | 120.4697 | 0.054932 | 0.022889 | 120.3964 | -0.48523 | -0.37079 | 120.607 | 120.6161 | 120.4971 | 0.21973 | 0.10071 | 0.17395 | 0.009156 | 0.21057 | 0.14191 | -0.09613 | 0.027466 | 120.3506 | 120.4239 | -0.46234 | -0.5127 | 120.4559 | 120.5383 | 120.4193 | 120.5154
3618.0781 | 121.1792 | -120.4926 | 0.43945 | 0.028839 | 0.014787 | -0.032227 | 0.037762 | -0.012285 | -0.028608 | -0.019188 | 0.017761 | -0.062079 | -0.0016064 | 0.038529 | -0.014095 | -0.0081774 | -0.012256 | 0.013733 | -0.045776 | -0.004578 | 0.068665 | 0.19226 | 0.050354 | 0.07782 | 0.11444 | 0.004578 | 0 | 0.11902 | 0.1831 | 0.091553 | 0.16937 | 120.488 | -0.48523 | -0.37079 | 120.6848 | 120.5704 | 120.5429 | 0.082398 | 0.054932 | 120.4926 | -0.43487 | -0.32043 | 120.6757 | 120.6619 | 120.5841 | 0.16937 | 0.091553 | 0.19684 | 0.073243 | 0.1831 | 0.11902 | -0.041198 | 0.004578 | 120.4468 | 120.4971 | -0.44403 | -0.43945 | 120.5612 | 120.6116 | 120.5063 | 120.607
3619.875 | 121.1609 | -120.5246 | 0.43945 | 0.036468 | 0.015001 | -0.032868 | 0.036908 | -0.014635 | -0.027327 | -0.021324 | 0.011658 | -0.063574 | -0.0020336 | 0.040024 | -0.018581 | -0.0094592 | -0.012256 | -0.064087 | -0.054932 | 0.013733 | -0.013733 | 0.11902 | 0.013733 | 0.036621 | 0.009155 | 0.027466 | -0.032043 | 0.032043 | 0.1236 | 0.032043 | 0.15564 | 120.5383 | -0.49438 | -0.45319 | 120.6436 | 120.5612 | 120.5383 | 0.022888 | 0 | 120.4926 | -0.41199 | -0.40741 | 120.6482 | 120.6802 | 120.5566 | 0.18768 | 0.064086 | 0.10529 | -0.027466 | 0.15564 | 0.064086 | -0.068665 | 0.059509 | 120.4697 | 120.5521 | -0.42572 | -0.4715 | 120.5109 | 120.5566 | 120.4605 | 120.5338
3621.6562 | 121.2021 | -120.5246 | 0.45319 | 0.028839 | 0.01671 | -0.031159 | 0.035412 | -0.016344 | -0.024763 | -0.020042 | 0.011658 | -0.06037 | -0.0011792 | 0.043442 | -0.016445 | -0.0096728 | -0.016528 | 0.018311 | -0.064087 | 0.013733 | 0.064087 | 0.1831 | 0.068665 | 0.059509 | 0.10986 | 0.018311 | -0.018311 | 0.10529 | 0.17395 | 0.091553 | 0.1831 | 120.5383 | -0.51727 | -0.3891 | 120.7077 | 120.5841 | 120.5933 | 0.045776 | 0.054932 | 120.5063 | -0.43487 | -0.3479 | 120.6985 | 120.7077 | 120.6162 | 0.20142 | 0.10986 | 0.16937 | 0.050354 | 0.19226 | 0.1236 | -0.07782 | 0.036622 | 120.4605 | 120.5429 | -0.43945 | -0.4715 | 120.5887 | 120.6299 | 120.5429 | 120.6345
3623.4531 | 121.1746 | -120.7397 | 0.29297 | 0.02121 | 0.013719 | -0.031586 | 0.037121 | -0.013567 | -0.02989 | -0.021324 | 0.008606 | -0.061438 | -0.00182 | 0.042801 | -0.020076 | -0.012236 | -0.011828 | -0.059509 | -0.032043 | -0.009155 | -0.018311 | 0.11444 | 0.022888 | 0.022888 | 0.004578 | 0.013733 | -0.022888 | 0.032043 | 0.11902 | 0.045776 | 0.14191 | 120.7306 | -0.32501 | -0.31128 | 120.8542 | 120.7626 | 120.7626 | 0.032043 | 0.032043 | 120.7169 | -0.27924 | -0.26093 | 120.8588 | 120.8817 | 120.7855 | 0.16479 | 0.068664 | 0.1236 | -0.009156 | 0.14191 | 0.054931 | -0.022888 | 0.036621 | 120.7077 | 120.7535 | -0.30212 | -0.31586 | 120.7214 | 120.7718 | 120.6802 | 120.7443
3625.1875 | 121.1792 | -120.7535 | 0.3067 | 0.01358 | 0.015855 | -0.031586 | 0.038189 | -0.016985 | -0.030958 | -0.021537 | 0.0055542 | -0.059729 | -0.00053825 | 0.038102 | -0.014095 | -0.0098864 | -0.011828 | -0.068665 | -0.032043 | -0.032043 | -0.064087 | 0.050354 | -0.064087 | -0.022888 | -0.018311 | 0.032043 | -0.036621 | 0.041199 | 0.10071 | 0.018311 | 0.15106 | 120.7214 | -0.33874 | -0.37079 | 120.8038 | 120.7306 | 120.6894 | 0.009155 | -0.032044 | 120.7169 | -0.27466 | -0.2655 | 120.8542 | 120.9045 | 120.7718 | 0.18768 | 0.054932 | 0.082397 | -0.032044 | 0.13733 | 0.07782 | 0 | 0.068664 | 120.7214 | 120.7855 | -0.33874 | -0.34332 | 120.6894 | 120.7947 | 120.6848 | 120.7352
3626.9688 | 121.1792 | -120.6253 | 0.44403 | 0.0059509 | 0.013078 | -0.032441 | 0.037335 | -0.01549 | -0.030104 | -0.019828 | 0.0055542 | -0.059515 | -0.0011792 | 0.036393 | -0.015163 | -0.0094592 | -0.01546 | -0.082397 | -0.013733 | -0.027466 | -0.082397 | 0.045776 | -0.064087 | -0.041199 | -0.027466 | 0.032043 | -0.036621 | 0.018311 | 0.07782 | 0.013733 | 0.13275 | 120.5978 | -0.45776 | -0.52643 | 120.6711 | 120.5841 | 120.5612 | -0.013733 | -0.036621 | 120.5887 | -0.41199 | -0.42572 | 120.7031 | 120.7581 | 120.639 | 0.16937 | 0.050354 | 0.073242 | -0.054931 | 0.11444 | 0.054932 | 0.013733 | 0.068664 | 120.6116 | 120.6573 | -0.4715 | -0.48065 | 120.5429 | 120.6436 | 120.5429 | 120.5978
3628.75 | 121.2982 | -120.7077 | 0.34332 | 0.0059509 | 0.014787 | -0.030945 | 0.037335 | -0.016131 | -0.030104 | -0.020897 | 0.017761 | -0.061865 | -0.00096545 | 0.035752 | -0.01559 | -0.0092456 | -0.012256 | 0.009155 | -0.050354 | 0.004578 | 0.059509 | 0.20142 | 0.054932 | 0.082397 | 0.10986 | 0.004578 | -0.009155 | 0.086975 | 0.1831 | 0.091553 | 0.18768 | 120.7123 | -0.39368 | -0.28381 | 120.9091 | 120.7901 | 120.7626 | 0.077819 | 0.050354 | 120.6985 | -0.33874 | -0.25635 | 120.8908 | 120.8954 | 120.7993 | 0.19684 | 0.10071 | 0.19684 | 0.054931 | 0.19226 | 0.09613 | -0.054932 | 0.013733 | 120.6573 | 120.7123 | -0.33874 | -0.35248 | 120.7672 | 120.7947 | 120.7169 | 120.8176
3630.4844 | 121.2662 | -120.7306 | 0.39368 | 0.02121 | 0.013719 | -0.033936 | 0.037121 | -0.01549 | -0.030745 | -0.022392 | 0.0025024 | -0.061438 | -0.0020336 | 0.03682 | -0.018154 | -0.010741 | -0.013751 | -0.073242 | -0.018311 | -0.027466 | -0.068665 | 0.045776 | -0.059509 | -0.027466 | -0.027466 | 0.045776 | -0.022888 | 0.032043 | 0.07782 | 0.018311 | 0.15106 | 120.7031 | -0.41199 | -0.46234 | 120.7764 | 120.7031 | 120.6711 | 0 | -0.032043 | 120.7077 | -0.3479 | -0.36163 | 120.8084 | 120.8817 | 120.7489 | 0.17395 | 0.041199 | 0.073242 | -0.041199 | 0.10071 | 0.054931 | 0.009155 | 0.068664 | 120.7123 | 120.7764 | -0.42114 | -0.41657 | 120.6619 | 120.7626 | 120.6573 | 120.7031
3632.2812 | 121.2936 | -120.7947 | 0.29755 | 0.01358 | 0.01201 | -0.031373 | 0.035199 | -0.018908 | -0.03224 | -0.021751 | 0.014709 | -0.061651 | 0.00031615 | 0.035325 | -0.016231 | -0.010314 | -0.015887 | 0.009155 | -0.054932 | 0.018311 | 0.041199 | 0.17395 | 0.059509 | 0.073242 | 0.10071 | 0.022888 | -0.009155 | 0.091553 | 0.17853 | 0.091553 | 0.21057 | 120.813 | -0.35248 | -0.25635 | 120.9686 | 120.8679 | 120.8542 | 0.054931 | 0.041198 | 120.7855 | -0.27466 | -0.20599 | 120.9732 | 121.0052 | 120.8862 | 0.21973 | 0.10071 | 0.15564 | 0.022888 | 0.18768 | 0.10071 | -0.073243 | 0.032043 | 120.7397 | 120.8176 | -0.27923 | -0.3067 | 120.8359 | 120.8862 | 120.8038 | 120.8954
3634.0781 | 121.3165 | -120.6757 | 0.40741 | 0.01358 | 0.012864 | -0.033295 | 0.034772 | -0.013994 | -0.028608 | -0.023887 | -0.003601 | -0.062079 | -0.0026744 | 0.035111 | -0.018367 | -0.011595 | -0.012896 | 0 | -0.07782 | 0.013733 | 0.064087 | 0.19684 | 0.10071 | 0.091553 | 0.086975 | 0.004578 | -0.013733 | 0.082397 | 0.19226 | 0.11444 | 0.19226 | 120.6894 | -0.48523 | -0.34332 | 120.8725 | 120.7672 | 120.7764 | 0.07782 | 0.086975 | 120.6619 | -0.40283 | -0.32501 | 120.8679 | 120.8679 | 120.7901 | 0.20599 | 0.12817 | 0.18311 | 0.050354 | 0.20599 | 0.09613 | -0.091553 | 0.018311 | 120.5978 | 120.6802 | -0.39368 | -0.42114 | 120.7397 | 120.7581 | 120.6757 | 120.7626
3635.7969 | 121.3806 | -120.8313 | 0.49896 | 0.044098 | 0.01436 | -0.034577 | 0.038403 | -0.01549 | -0.031813 | -0.023246 | 0.011658 | -0.057806 | 0.00095715 | 0.028702 | -0.021785 | -0.011168 | -0.0081968 | -0.07782 | 0.004578 | -0.050354 | -0.068665 | 0.045776 | -0.013733 | -0.018311 | -0.073242 | 0.073242 | -0.059509 | -0.050354 | 0.064087 | -0.032043 | 0.091553 | 120.7809 | -0.49438 | -0.56763 | 120.8771 | 120.813 | 120.8176 | 0.032043 | 0.036621 | 120.7718 | -0.42572 | -0.54932 | 120.8954 | 120.9229 | 120.7993 | 0.15106 | 0.027466 | 0.09613 | -0.018311 | 0.1236 | 0.009155 | 0.054932 | 0.13275 | 120.8359 | 120.9045 | -0.54932 | -0.55847 | 120.7626 | 120.7809 | 120.7535 | 120.7581
3637.5938 | 121.2296 | -121.0007 | 0.17395 | 0.02121 | 0.014146 | -0.0318 | 0.038617 | -0.012926 | -0.028181 | -0.024528 | 0.008606 | -0.058875 | 0.00010255 | 0.032334 | -0.018154 | -0.011382 | -0.011187 | -0.041199 | -0.027466 | -0.018311 | -0.050354 | 0.082397 | -0.045776 | -0.018311 | -0.041199 | 0.036621 | -0.022888 | -0.009155 | 0.032043 | -0.032043 | 0.10071 | 120.9824 | -0.20142 | -0.2243 | 121.0831 | 120.9824 | 120.9549 | 0 | -0.027465 | 120.9778 | -0.13733 | -0.1831 | 121.0327 | 121.1014 | 120.9686 | 0.1236 | -0.009155 | 0.10071 | -0.032043 | 0.054931 | 0.013733 | -0.009155 | 0.059509 | 120.9732 | 121.0373 | -0.19226 | -0.19684 | 120.9503 | 120.9915 | 120.9595 | 120.9595
3639.3281 | 121.3028 | -120.9641 | 0.13733 | 0.036468 | 0.013719 | -0.033082 | 0.037549 | -0.014635 | -0.029036 | -0.021965 | 0.011658 | -0.060584 | 0.00031615 | 0.038956 | -0.017513 | -0.010527 | -0.015887 | -0.009155 | -0.045776 | 0.018311 | 0.032043 | 0.18768 | 0.054932 | 0.068665 | 0.091553 | 0.018311 | -0.022888 | 0.054932 | 0.14648 | 0.064087 | 0.1831 | 120.9824 | -0.18311 | -0.10529 | 121.1517 | 121.0327 | 121.019 | 0.050354 | 0.036621 | 120.9412 | -0.11902 | -0.082397 | 121.1105 | 121.1472 | 121.0281 | 0.20599 | 0.086975 | 0.16937 | 0.013732 | 0.16937 | 0.07782 | -0.064087 | 0.041199 | 120.9183 | 120.9824 | -0.11902 | -0.16022 | 120.9961 | 121.019 | 120.9549 | 121.0556
3641.125 | 121.2799 | -120.7214 | 0.46692 | 0.01358 | 0.01735 | -0.033295 | 0.037335 | -0.010363 | -0.028395 | -0.022819 | 0.008606 | -0.060156 | 0.0011708 | 0.030411 | -0.016658 | -0.011382 | -0.010119 | -0.054932 | -0.004578 | -0.022888 | -0.091553 | 0 | -0.086975 | -0.059509 | -0.11902 | 0.050354 | -0.045776 | -0.018311 | 0.022888 | -0.059509 | 0.09613 | 120.6985 | -0.4715 | -0.55847 | 120.7214 | 120.6619 | 120.6345 | -0.036621 | -0.064087 | 120.6757 | -0.41656 | -0.48523 | 120.7443 | 120.8176 | 120.6619 | 0.14191 | -0.013733 | 0.022888 | -0.068665 | 0.068664 | 0.027465 | 0.01831 | 0.09613 | 120.7169 | 120.7718 | -0.48981 | -0.5127 | 120.6299 | 120.7031 | 120.6665 | 120.6024
3642.8438 | 120.5383 | -15.303 | 98.7579 | 0.13565 | -0.0025164 | -0.041413 | 0.022595 | -0.022112 | -0.033949 | -0.026023 | -0.064636 | -0.063361 | -0.0048108 | 0.040238 | -0.014949 | -0.0101 | -0.010119 | -0.11902 | -0.050354 | 0.24261 | -0.10529 | 0.013733 | -0.086975 | -0.09613 | -0.082397 | -0.36163 | -0.013733 | -0.004578 | 0.032043 | -0.050354 | 0.10071 | 15.5457 | -98.8083 | -98.8632 | 15.3168 | 15.2069 | 15.2161 | -0.33874 | -0.32959 | 15.2893 | -99.1196 | -98.7625 | 15.3351 | 15.4037 | 15.2527 | 0.11444 | -0.036621 | -0.22888 | -0.3479 | 0.045776 | 0.009155 | -0.29297 | -0.3479 | 15.2527 | 14.9414 | -98.5153 | -98.7717 | 15.1978 | 15.2985 | 15.184 | 15.2206
3644.6406 | 121.1746 | -95.723 | 24.9023 | 0.02121 | 0.01201 | -0.031373 | 0.032422 | -0.016771 | -0.02754 | -0.021965 | -0.034119 | -0.063361 | -0.0016064 | 0.039811 | -0.018367 | -0.010314 | -0.012256 | -0.09613 | -0.036621 | 0.10529 | -0.018311 | 0.059509 | -0.064087 | -0.086975 | -0.009155 | -0.22888 | 0.27924 | 0.013733 | 0.10071 | 0.022888 | 0.12817 | 95.8282 | -24.939 | -24.9207 | 95.7825 | 95.636 | 95.6589 | -0.19226 | -0.16937 | 96.0022 | -25.1312 | -24.8886 | 95.8237 | 95.8511 | 95.7458 | -0.15106 | -0.25635 | -0.045777 | -0.1236 | -0.17853 | -0.2655 | -0.14191 | -0.50812 | 95.6863 | 95.4941 | -24.7971 | -24.6231 | 95.7047 | 95.7367 | 95.6268 | 95.7138
3646.3906 | 121.2616 | -95.8008 | 24.9527 | 0.044098 | 0.012651 | -0.03415 | 0.036908 | -0.018694 | -0.026686 | -0.021751 | -0.03717 | -0.06272 | -0.00096545 | 0.036606 | -0.018794 | -0.010527 | -0.015033 | -0.068665 | -0.054932 | -0.022888 | -0.032043 | 0.10529 | -0.013733 | -0.059509 | -0.009155 | 0.018311 | 0.09613 | 0.022888 | 0.086975 | 0.032043 | 0.13733 | 95.7779 | -25.0076 | -24.9847 | 95.9061 | 95.7413 | 95.787 | -0.036621 | 0.009155 | 95.8969 | -24.9344 | -24.9298 | 95.8878 | 95.9381 | 95.8328 | 0.041199 | -0.064087 | 0.12817 | -0.009155 | -0.009155 | -0.073242 | -0.032044 | -0.077819 | 95.7458 | 95.8191 | -24.9756 | -24.8566 | 95.7687 | 95.8237 | 95.7321 | 95.7916
3648.1875 | 121.2296 | -95.8786 | 25.0122 | 0.028839 | 0.015214 | -0.033509 | 0.030926 | -0.021685 | -0.031172 | -0.039695 | 0.054382 | 0.015893 | -0.009724 | 0.024644 | -0.027767 | -0.029326 | -0.02315 | -0.045776 | -0.018311 | -0.036621 | -0.17853 | -0.054932 | 0.086975 | 0.09613 | 0.009155 | 0.009155 | 0.24719 | 0.032043 | -0.13275 | 0.086975 | 0.091553 | 95.842 | -25.0305 | -25.1907 | 95.8237 | 95.9747 | 95.9656 | 0.13275 | 0.1236 | 96.1258 | -25.0031 | -24.9802 | 95.7459 | 95.9702 | 95.9656 | -0.15564 | -0.16022 | -0.018311 | -0.14191 | -0.37994 | -0.21515 | 0.01831 | -0.23804 | 95.8603 | 95.8878 | -25.0488 | -24.765 | 95.7001 | 95.9106 | 95.8328 | 95.8878
3649.9062 | 121.1838 | -95.9747 | 25.0214 | 0.02121 | 0.015214 | -0.032227 | 0.022809 | 0.026594 | -0.032667 | -0.034355 | 0.051331 | 0.016107 | -0.006306 | 0.025284 | -0.029689 | -0.028044 | -0.024218 | -0.059509 | -0.018311 | -0.032043 | -0.2243 | -0.032043 | 0.07782 | 0.091553 | -0.045776 | 0.041199 | 0.082397 | -0.009155 | -0.036621 | -0.2243 | 0.091553 | 95.9427 | -25.0397 | -25.2457 | 95.9427 | 96.0663 | 96.0526 | 0.1236 | 0.10986 | 96.0571 | -24.9802 | -25.0305 | 95.9381 | 96.0663 | 95.7504 | 0.009156 | -0.3067 | 0 | -0.19226 | -0.11902 | -0.091552 | 0.013732 | -0.041198 | 95.9564 | 96.0159 | -25.0534 | -24.939 | 95.7504 | 95.9656 | 95.9152 | 95.929
3651.6875 | 121.17 | -95.929 | 25.1129 | 0.02121 | 0.016069 | -0.033082 | 0.03349 | -0.021685 | -0.029249 | -0.029441 | 0.045227 | -0.074469 | -0.0022472 | 0.031693 | -0.017513 | -0.015227 | -0.017169 | -0.09613 | -0.027466 | -0.032043 | -0.17853 | -0.33417 | -0.24261 | 0.086975 | -0.11444 | 0.032043 | -0.059509 | -0.009155 | 0.004578 | -0.31586 | -0.032043 | 95.8969 | -25.1404 | -25.2914 | 95.5948 | 96.0159 | 95.6863 | 0.11902 | -0.21057 | 95.8694 | -25.0809 | -25.1221 | 95.9335 | 95.8969 | 95.6131 | 0.027466 | -0.25635 | -0.30212 | -0.14648 | 0.064087 | 0.050354 | 0.004577 | 0.091552 | 95.9015 | 95.961 | -25.145 | -25.1724 | 95.7504 | 95.9198 | 95.8328 | 95.8145
3653.4844 | 121.3028 | -96.4188 | 24.5728 | 0.028839 | 0.011583 | -0.031586 | 0.036267 | -0.018267 | -0.029463 | -0.019401 | -0.003601 | -0.062933 | 0.00010255 | 0.032761 | -0.018154 | -0.011595 | -0.012256 | -0.07782 | -0.054932 | -0.009155 | -0.027466 | 0.13275 | 0.032043 | 0.032043 | 0.009155 | 0.004578 | -0.018311 | 0.068665 | 0.13275 | 0.07782 | 0.16937 | 96.4096 | -24.6277 | -24.6002 | 96.5515 | 96.4508 | 96.4508 | 0.041198 | 0.041198 | 96.4005 | -24.5682 | -24.5041 | 96.5515 | 96.5881 | 96.4966 | 0.18768 | 0.096131 | 0.14191 | -0.018311 | 0.15106 | 0.086976 | -0.045777 | 0.022889 | 96.3638 | 96.4233 | -24.5819 | -24.5911 | 96.3913 | 96.4874 | 96.3409 | 96.4279
3655.2656 | 121.2341 | -96.9818 | 24.1104 | 0.02121 | 0.012224 | -0.031586 | 0.036053 | -0.013994 | -0.030104 | -0.021965 | -0.098206 | -0.059729 | -0.00075185 | 0.035111 | -0.019008 | -0.013304 | -0.013965 | -0.045776 | -0.050354 | -0.032043 | -0.068665 | 0.086975 | -0.054932 | -0.17853 | -0.045776 | 0.027466 | -0.045776 | -0.036621 | 0.045776 | -0.027466 | -0.004578 | 96.9498 | -24.1608 | -24.1791 | 97.0688 | 96.8033 | 96.9269 | -0.14648 | -0.022889 | 96.936 | -24.0829 | -24.147 | 97.0276 | 96.9772 | 96.9543 | 0.041198 | 0.01831 | 0.11902 | -0.036622 | 0.091552 | 0.009155 | -0.018311 | 0.073242 | 96.9315 | 97.0093 | -24.1425 | -24.1562 | 96.9131 | 96.9452 | 96.936 | 96.936
3657 | 121.3486 | -21.7575 | 99.1882 | -0.49759 | 0.014146 | -0.032441 | 0.037762 | -0.013994 | -0.026686 | -0.020683 | -0.12262 | -0.061224 | -0.00011105 | 0.040024 | -0.014949 | -0.0094592 | -0.012042 | -0.018311 | -0.07782 | -0.027466 | 0.022888 | 0.15106 | -0.041199 | -0.20142 | 0.07782 | -0.022888 | -0.027466 | 0.07782 | 0.14191 | 0.050354 | 0.10529 | 21.73 | -99.2661 | -99.1653 | 21.9086 | 21.5561 | 21.7163 | -0.17395 | -0.013733 | 21.73 | -99.2111 | -99.1104 | 21.8994 | 21.8628 | 21.8079 | 0.13275 | 0.07782 | 0.17853 | 0.050354 | 0.16937 | 0.10529 | -0.050354 | 0.004578 | 21.6797 | 21.7346 | -99.2157 | -99.2157 | 21.7804 | 21.8353 | 21.7392 | 21.8353
3658.7812 | 121.2616 | -3.804 | 117.1326 | 0.01358 | 0.01436 | -0.032227 | 0.038189 | -0.016344 | -0.030745 | -0.018119 | -0.1684 | -0.062079 | -0.00053825 | 0.039597 | -0.021358 | -0.0092456 | -0.011401 | -0.036621 | -0.082397 | -0.041199 | 0.013733 | 0.15106 | -0.032043 | -0.21973 | 0.036621 | -0.032043 | 0.022888 | 0.032043 | 0.1236 | 0.041199 | -0.022888 | 3.7628 | -117.215 | -117.1188 | 3.9551 | 3.5843 | 3.772 | -0.17853 | 0.009156 | 3.8269 | -117.1646 | -117.1005 | 3.9276 | 3.7811 | 3.8452 | -0.045776 | 0.018311 | 0.19226 | 0.054932 | 0.10071 | 0.009155 | -0.041198 | -0.054931 | 3.7216 | 3.772 | -117.1738 | -117.1097 | 3.8177 | 3.8361 | 3.7674 | 3.8406
3660.5781 | 121.2845 | -4.7562 | 116.0843 | 0.02121 | 0.010728 | -0.053162 | 0.021527 | -0.027666 | -0.045271 | 0.028878 | 0.054382 | 0.015893 | -0.017414 | 0.028061 | -0.018794 | -0.019499 | -0.029773 | -0.068665 | -0.068665 | -0.064087 | -0.082397 | -0.23804 | -0.19684 | 0.091553 | -0.064087 | 0.004578 | -0.027466 | -0.041199 | 0.004578 | -0.28839 | 0.10071 | 4.6921 | -116.153 | -116.1667 | 4.5181 | 4.8477 | 4.5593 | 0.15564 | -0.13275 | 4.7287 | -116.0797 | -116.1255 | 4.7607 | 4.8569 | 4.4678 | 0.12817 | -0.26093 | -0.17395 | -0.01831 | 0.032044 | -0.013733 | -0.004578 | 0.032044 | 4.6875 | 4.7607 | -116.1484 | -116.1118 | 4.6738 | 4.715 | 4.6875 | 4.6921
3662.3125 | 121.2296 | -5.7037 | 115.0314 | 0.02121 | 0.015641 | -0.037568 | 0.035199 | -0.018053 | -0.034162 | -0.038627 | 0.048279 | -0.075324 | -0.010792 | 0.030625 | -0.019863 | -0.018218 | -0.022082 | -0.13275 | -0.050354 | -0.054932 | -0.14648 | -0.16479 | -0.48981 | 0.082397 | -0.15106 | 0.027466 | -0.091553 | -0.059509 | -0.013733 | -0.17395 | -0.33417 | 5.6488 | -115.0818 | -115.1779 | 5.5389 | 5.7861 | 5.2139 | 0.13733 | -0.43488 | 5.6122 | -115.004 | -115.0909 | 5.69 | 5.3696 | 5.5298 | -0.24261 | -0.082397 | -0.10986 | -0.091552 | 0.07782 | 0.032044 | 0.004578 | 0.11902 | 5.6534 | 5.7312 | -115.0864 | -115.123 | 5.5573 | 5.6442 | 5.571 | 5.5527
3664.1094 | 121.2708 | -4.1748 | 117.1371 | 0.036468 | 0.01436 | -0.031159 | 0.03648 | -0.017199 | -0.028181 | -0.021751 | -0.024963 | -0.061011 | 0.00074335 | 0.036393 | -0.016017 | -0.008391 | -0.0084104 | -0.086975 | -0.082397 | -0.050354 | -0.032043 | 0.10071 | -0.013733 | -0.027466 | -0.036621 | -0.027466 | -0.045776 | 0.013733 | 0.09613 | 0.013733 | 0.11444 | 4.1245 | -117.2195 | -117.1692 | 4.2755 | 4.1473 | 4.1611 | 0.022888 | 0.036621 | 4.129 | -117.1646 | -117.1234 | 4.2709 | 4.2892 | 4.1885 | 0.16022 | 0.059509 | 0.15106 | 0.018311 | 0.14191 | 0.059509 | -0.032043 | 0.01831 | 4.0924 | 4.1473 | -117.1875 | -117.1829 | 4.1428 | 4.1885 | 4.0878 | 4.1382
3665.9062 | 121.431 | -4.8203 | 116.7206 | 0.01358 | 0.014573 | -0.033082 | 0.034772 | -0.017199 | -0.029463 | -0.023033 | -0.00054937 | -0.061651 | -0.0026744 | 0.040024 | -0.019008 | -0.011382 | -0.011401 | -0.064087 | -0.086975 | -0.036621 | 0.013733 | 0.15564 | 0.054932 | 0.045776 | 0.082397 | -0.032043 | -0.059509 | 0.068665 | 0.17395 | 0.10071 | 0.16022 | 4.7836 | -116.8076 | -116.7068 | 4.9759 | 4.866 | 4.8752 | 0.082397 | 0.091553 | 4.7607 | -116.7526 | -116.6519 | 4.9942 | 4.9805 | 4.921 | 0.21973 | 0.16022 | 0.19226 | 0.050354 | 0.23346 | 0.12817 | -0.050354 | 0.027466 | 4.7333 | 4.7882 | -116.7572 | -116.7801 | 4.834 | 4.8889 | 4.7562 | 4.9026
3667.6875 | 121.3989 | -112.9028 | 8.1894 | 0.02121 | 0.015214 | -0.035218 | 0.034558 | -0.015703 | -0.030958 | -0.020256 | -0.0097046 | -0.059729 | -0.0031018 | 0.040452 | -0.021785 | -0.012236 | -0.012042 | -0.091553 | -0.036621 | -0.009155 | -0.068665 | 0.050354 | -0.022888 | -0.15106 | -0.073242 | 0.050354 | -0.041199 | -0.018311 | 0.032043 | -0.041199 | 0.059509 | 112.8937 | -8.226 | -8.2581 | 112.9532 | 112.7518 | 112.8799 | -0.14191 | -0.013733 | 112.8616 | -8.139 | -8.2077 | 112.9349 | 112.9623 | 112.8616 | 0.10071 | 0 | 0.059509 | -0.05951 | 0.073242 | 0.022888 | -0.027466 | 0.091553 | 112.8662 | 112.9532 | -8.1985 | -8.2306 | 112.8342 | 112.8845 | 112.8113 | 112.8296
3669.4844 | 121.5088 | -114.2212 | 6.839 | 0.01358 | 0.015001 | -0.030732 | 0.037762 | -0.013781 | -0.028822 | -0.023674 | -0.0066528 | -0.062292 | -0.0026744 | 0.037675 | -0.014736 | -0.0088184 | -0.012683 | 0.013733 | -0.064087 | 0.009155 | 0.045776 | 0.16937 | 0.064087 | 0.022888 | 0.082397 | 0 | -0.013733 | 0.1236 | 0.16022 | 0.091553 | 0.20142 | 114.2303 | -6.9031 | -6.7932 | 114.3906 | 114.2441 | 114.2853 | 0.013733 | 0.054932 | 114.2075 | -6.839 | -6.7154 | 114.3814 | 114.4226 | 114.3127 | 0.21515 | 0.10529 | 0.16022 | 0.036621 | 0.17395 | 0.13733 | -0.073242 | 0.013733 | 114.1571 | 114.2212 | -6.8298 | -6.8527 | 114.267 | 114.3448 | 114.2349 | 114.3036
3671.2656 | 121.4951 | -114.5599 | 6.6055 | 0.044098 | 0.016069 | -0.032654 | 0.036694 | -0.013353 | -0.030531 | -0.020897 | 0.017761 | -0.062292 | -0.00075185 | 0.038956 | -0.015377 | -0.008391 | -0.01311 | 0.009155 | -0.027466 | 0.018311 | 0.068665 | 0.19684 | 0.064087 | 0.073242 | 0.11902 | 0.013733 | -0.018311 | 0.11902 | 0.14191 | 0.07782 | 0.17853 | 114.5782 | -6.633 | -6.5369 | 114.7568 | 114.6332 | 114.624 | 0.054931 | 0.045776 | 114.5416 | -6.5918 | -6.4865 | 114.7018 | 114.7385 | 114.6378 | 0.19684 | 0.096131 | 0.17853 | 0.050354 | 0.16022 | 0.13733 | -0.045777 | 0.032044 | 114.5325 | 114.5737 | -6.5872 | -6.6238 | 114.6286 | 114.679 | 114.5691 | 114.679
3673 | 121.4951 | -114.8163 | 6.3675 | 0.028839 | 0.014573 | -0.0318 | 0.03883 | -0.014849 | -0.030958 | -0.020897 | 0.008606 | -0.061651 | 0.00095715 | 0.039597 | -0.01324 | -0.0081774 | -0.014392 | -0.004578 | -0.050354 | 0.004578 | 0.036621 | 0.14648 | 0.059509 | 0.045776 | 0.082397 | 0.004578 | -0.004578 | 0.12817 | 0.15564 | 0.073242 | 0.20142 | 114.8209 | -6.4178 | -6.3309 | 114.9628 | 114.8621 | 114.8758 | 0.041198 | 0.054931 | 114.8117 | -6.3629 | -6.2393 | 114.9719 | 115.0177 | 114.8895 | 0.20599 | 0.07782 | 0.14191 | 0.032043 | 0.16022 | 0.13275 | -0.054932 | 0.009156 | 114.7659 | 114.8209 | -6.3629 | -6.3721 | 114.8529 | 114.9445 | 114.8117 | 114.8987
3674.7812 | 121.4081 | -116.0522 | 5.2231 | 0.0059509 | 0.011583 | -0.033722 | 0.036267 | -0.015703 | -0.031385 | -0.024314 | 0.008606 | -0.060797 | -0.0016064 | 0.038529 | -0.022212 | -0.0101 | -0.013965 | -0.027466 | -0.050354 | 0.004578 | -0.022888 | 0.11902 | 0.032043 | 0.022888 | -0.022888 | 0.032043 | -0.032043 | -0.013733 | 0.064087 | -0.004578 | 0.091553 | 116.0568 | -5.2734 | -5.246 | 116.1713 | 116.0751 | 116.0843 | 0.01831 | 0.027465 | 116.0202 | -5.191 | -5.2368 | 116.1163 | 116.1438 | 116.0477 | 0.1236 | 0.027465 | 0.11444 | -0.027466 | 0.09613 | 0.01831 | -0.054932 | 0.064086 | 116.0019 | 116.0843 | -5.2185 | -5.2551 | 116.0294 | 116.0385 | 116.0248 | 116.0294
3676.5938 | 121.4218 | -116.0019 | 5.3238 | 0.02121 | 0.013933 | -0.033295 | 0.038617 | -0.014849 | -0.029249 | -0.02111 | -0.012756 | -0.060584 | -0.00096545 | 0.035752 | -0.019435 | -0.0101 | -0.015246 | -0.068665 | 0.004578 | -0.041199 | -0.086975 | 0.027466 | -0.032043 | -0.068665 | -0.050354 | 0.059509 | -0.064087 | 0 | 0.064087 | -0.013733 | 0.09613 | 115.9607 | -5.3192 | -5.4108 | 116.0294 | 115.9332 | 115.9698 | -0.027466 | 0.009156 | 115.9378 | -5.2643 | -5.3238 | 116.066 | 116.098 | 115.9882 | 0.16022 | 0.050354 | 0.068665 | -0.045776 | 0.12817 | 0.064087 | 0.045777 | 0.1236 | 116.0065 | 116.0614 | -5.365 | -5.3879 | 115.9149 | 116.0019 | 115.9332 | 115.9515
3678.3281 | 121.3806 | -115.5533 | 5.7724 | 0.02121 | 0.013505 | -0.034791 | 0.036694 | -0.016344 | -0.031172 | -0.021537 | 0.008606 | -0.062292 | -0.00011105 | 0.040024 | -0.021572 | -0.013091 | -0.011187 | -0.082397 | -0.004578 | -0.036621 | -0.082397 | 0.050354 | -0.032043 | -0.027466 | -0.068665 | 0.045776 | -0.013733 | -0.027466 | 0.045776 | -0.027466 | 0.073242 | 115.5167 | -5.777 | -5.8548 | 115.6036 | 115.5258 | 115.5212 | 0.009155 | 0.004578 | 115.5396 | -5.7266 | -5.7999 | 115.5991 | 115.6265 | 115.5258 | 0.086975 | -0.013733 | 0.086975 | -0.045776 | 0.059509 | -0.013733 | 0.032043 | 0.059509 | 115.5487 | 115.5991 | -5.809 | -5.7861 | 115.4709 | 115.5258 | 115.4709 | 115.4846
3680.1094 | 121.3852 | -116.4825 | 4.8111 | 0.036468 | 0.014146 | -0.035004 | 0.038403 | -0.016985 | -0.02989 | -0.020469 | 0.011658 | -0.061438 | -0.00032465 | 0.039597 | -0.018154 | -0.0098864 | -0.013537 | -0.068665 | -0.004578 | -0.045776 | -0.082397 | 0.036621 | -0.027466 | -0.032043 | -0.082397 | 0.064087 | -0.064087 | -0.027466 | 0.054932 | -0.041199 | 0.09613 | 116.4368 | -4.8157 | -4.8935 | 116.5192 | 116.4505 | 116.4551 | 0.013733 | 0.01831 | 116.4185 | -4.747 | -4.8386 | 116.5375 | 116.5787 | 116.4413 | 0.16022 | 0.022888 | 0.082397 | -0.036621 | 0.11902 | 0.036621 | 0.041198 | 0.12817 | 116.478 | 116.5466 | -4.8569 | -4.8752 | 116.4001 | 116.4551 | 116.4139 | 116.4001
3681.9062 | 121.3852 | -117.3615 | 3.9734 | 0.01358 | 0.015428 | -0.031586 | 0.037335 | -0.013567 | -0.026686 | -0.019188 | 0.0055542 | -0.059943 | -0.00032465 | 0.037247 | -0.014736 | -0.011382 | -0.013537 | -0.059509 | -0.004578 | -0.018311 | -0.082397 | 0.027466 | -0.082397 | -0.050354 | -0.091553 | 0.054932 | -0.041199 | -0.032043 | 0.022888 | -0.068665 | 0.07782 | 117.3431 | -3.978 | -4.0558 | 117.3889 | 117.3111 | 117.2791 | -0.032043 | -0.064086 | 117.3203 | -3.9185 | -4.0054 | 117.3843 | 117.4393 | 117.2928 | 0.11902 | -0.027466 | 0.045777 | -0.064086 | 0.064087 | 0.009156 | 0.013733 | 0.096131 | 117.3569 | 117.4164 | -3.9917 | -4.0146 | 117.2791 | 117.3294 | 117.3019 | 117.2699
3683.7031 | 121.4035 | -117.6178 | 3.7354 | 0.01358 | 0.015001 | -0.03415 | 0.035199 | -0.014849 | -0.028608 | -0.020469 | 0.008606 | -0.061651 | -0.00075185 | 0.030411 | -0.020503 | -0.011168 | -0.014392 | -0.022888 | -0.050354 | -0.009155 | -0.004578 | 0.14191 | 0.059509 | 0.059509 | 0.009155 | 0.027466 | -0.018311 | 0.004578 | 0.09613 | 0.022888 | 0.10529 | 117.6086 | -3.7857 | -3.7399 | 117.7597 | 117.6773 | 117.6773 | 0.068664 | 0.068664 | 117.5995 | -3.7079 | -3.7308 | 117.7139 | 117.7231 | 117.6407 | 0.1236 | 0.041199 | 0.15106 | 0.004577 | 0.11444 | 0.022889 | -0.041199 | 0.045777 | 117.5674 | 117.6453 | -3.7445 | -3.7537 | 117.6132 | 117.6224 | 117.5949 | 117.627
3685.5 | 121.5363 | -118.1168 | 3.1265 | 0.0059509 | 0.015214 | -0.035004 | 0.034131 | -0.013567 | -0.026899 | -0.024742 | 0.0055542 | -0.065497 | -0.0020336 | 0.042161 | -0.017726 | -0.011595 | -0.01311 | -0.013733 | -0.050354 | 0.027466 | 0.068665 | 0.21973 | 0.11444 | 0.11444 | 0.09613 | 0 | 0.013733 | 0.10986 | 0.20599 | 0.10986 | 0.17853 | 118.1442 | -3.1769 | -3.0579 | 118.3365 | 118.2312 | 118.2312 | 0.086975 | 0.086975 | 118.1305 | -3.1265 | -3.0167 | 118.3228 | 118.2953 | 118.2266 | 0.16479 | 0.09613 | 0.19226 | 0.041199 | 0.19226 | 0.09613 | -0.07782 | -0.013733 | 118.0664 | 118.1168 | -3.0991 | -3.1128 | 118.1854 | 118.2266 | 118.103 | 118.2129
3687.2344 | 121.4493 | -118.3548 | 3.0075 | 0.01358 | 0.013719 | -0.033722 | 0.037762 | -0.015703 | -0.029249 | -0.02346 | 0.0055542 | -0.059088 | -0.00032465 | 0.033829 | -0.016445 | -0.0094592 | -0.011828 | -0.082397 | -0.022888 | -0.018311 | -0.091553 | 0.032043 | -0.068665 | -0.041199 | -0.050354 | 0.064087 | -0.041199 | 0.009155 | 0.050354 | -0.041199 | 0.10071 | 118.3365 | -3.0304 | -3.0991 | 118.3868 | 118.3136 | 118.2861 | -0.022888 | -0.050354 | 118.3136 | -2.9434 | -2.9984 | 118.4052 | 118.4555 | 118.3136 | 0.14191 | 0 | 0.050354 | -0.073242 | 0.091553 | 0.050354 | -0.004577 | 0.10529 | 118.3319 | 118.4189 | -3.0258 | -3.0487 | 118.2632 | 118.364 | 118.2724 | 118.3044
3689.0312 | 121.4127 | -118.4463 | 2.9114 | 0.01358 | 0.013505 | -0.032227 | 0.040112 | -0.011858 | -0.029676 | -0.021324 | 0.008606 | -0.060584 | -0.0013928 | 0.03447 | -0.016445 | -0.0092456 | -0.014605 | -0.068665 | -0.018311 | -0.032043 | -0.09613 | -0.004578 | -0.091553 | -0.050354 | -0.07782 | 0.054932 | -0.041199 | -0.022888 | 0.018311 | -0.059509 | 0.086975 | 118.4143 | -2.9297 | -3.0075 | 118.4418 | 118.396 | 118.3548 | -0.018311 | -0.05951 | 118.4052 | -2.8564 | -2.9343 | 118.4647 | 118.5333 | 118.3868 | 0.12817 | -0.01831 | 0.027465 | -0.064087 | 0.05951 | 0.018311 | 0.013732 | 0.096131 | 118.428 | 118.5013 | -2.9434 | -2.9526 | 118.3502 | 118.4235 | 118.3777 | 118.3685
3690.8281 | 121.4905 | -118.5837 | 2.6962 | 0.036468 | 0.01436 | -0.033936 | 0.036053 | -0.013781 | -0.028181 | -0.022605 | 0.011658 | -0.063574 | -0.0013928 | 0.041306 | -0.016231 | -0.0092456 | -0.012896 | -0.045776 | -0.041199 | 0.004578 | -0.009155 | 0.11444 | 0.013733 | 0.041199 | 0.009155 | 0.032043 | -0.013733 | 0.045776 | 0.11902 | 0.050354 | 0.14191 | 118.5883 | -2.7374 | -2.7054 | 118.6981 | 118.6249 | 118.5974 | 0.036621 | 0.009155 | 118.5699 | -2.6642 | -2.6505 | 118.7027 | 118.7256 | 118.634 | 0.15564 | 0.064087 | 0.10986 | -0.013733 | 0.13275 | 0.059509 | -0.045777 | 0.045776 | 118.5425 | 118.6157 | -2.6917 | -2.71 | 118.5745 | 118.6295 | 118.5379 | 118.5928
3692.625 | 121.4996 | -118.634 | 2.6733 | 0.02121 | 0.013719 | -0.032013 | 0.03648 | -0.016985 | -0.028822 | -0.022178 | 0.008606 | -0.063788 | -0.00032465 | 0.03682 | -0.016231 | -0.0101 | -0.013751 | -0.054932 | -0.041199 | 0.013733 | 0 | 0.11444 | 0.018311 | 0.018311 | 0.009155 | 0.027466 | -0.027466 | 0.027466 | 0.11444 | 0.032043 | 0.13275 | 118.6478 | -2.7145 | -2.6733 | 118.7485 | 118.6523 | 118.6523 | 0.004578 | 0.004578 | 118.6066 | -2.6459 | -2.6459 | 118.7485 | 118.7668 | 118.6661 | 0.16022 | 0.059509 | 0.10071 | -0.013733 | 0.14191 | 0.054932 | -0.054932 | 0.054932 | 118.5928 | 118.6615 | -2.6596 | -2.7008 | 118.634 | 118.6615 | 118.5791 | 118.6432
3694.3594 | 121.4722 | -118.6935 | 2.6642 | 0.02121 | 0.015855 | -0.034363 | 0.038617 | -0.01314 | -0.028181 | -0.02111 | 0.008606 | -0.058661 | -0.0016064 | 0.033616 | -0.018367 | -0.010955 | -0.013537 | -0.036621 | -0.009155 | -0.050354 | -0.022888 | 0.091553 | 0.009155 | 0.013733 | 0.004578 | 0.045776 | -0.036621 | 0.032043 | 0.10529 | 0.009155 | 0.13275 | 118.6432 | -2.6733 | -2.6871 | 118.7851 | 118.7073 | 118.7027 | 0.064087 | 0.059509 | 118.6569 | -2.6184 | -2.6321 | 118.7988 | 118.8263 | 118.7027 | 0.16937 | 0.045776 | 0.14191 | 0.027466 | 0.14191 | 0.068664 | 0.041199 | 0.082397 | 118.6844 | 118.7393 | -2.7145 | -2.7008 | 118.6707 | 118.7256 | 118.6569 | 118.6981
3696.1562 | 121.55 | -118.7164 | 2.5955 | 0.028839 | 0.015214 | -0.033082 | 0.035412 | -0.013994 | -0.028608 | -0.022392 | 0.008606 | -0.058875 | 0.0020252 | 0.043656 | -0.016231 | -0.0094592 | -0.014605 | -0.054932 | -0.032043 | -0.009155 | -0.036621 | 0.10071 | -0.004578 | 0.013733 | 0.036621 | 0.013733 | -0.022888 | 0.073242 | 0.15106 | 0.073242 | 0.19226 | 118.7073 | -2.6276 | -2.6321 | 118.8171 | 118.7302 | 118.7119 | 0.022888 | 0.004577 | 118.6935 | -2.5818 | -2.5223 | 118.8675 | 118.9087 | 118.7897 | 0.21515 | 0.09613 | 0.10986 | -0.027466 | 0.17395 | 0.09613 | -0.022888 | 0.036621 | 118.6844 | 118.7302 | -2.6047 | -2.6184 | 118.6798 | 118.7897 | 118.6615 | 118.7531
3697.9375 | 121.4401 | -119.0323 | 2.3712 | 0.0059509 | 0.01436 | -0.033509 | 0.03648 | -0.012926 | -0.030531 | -0.019828 | 0.0055542 | -0.058447 | -0.0026744 | 0.028702 | -0.019435 | -0.010527 | -0.009692 | -0.09613 | -0.022888 | -0.032043 | -0.082397 | 0.004578 | -0.086975 | -0.059509 | -0.09613 | 0.036621 | -0.041199 | -0.032043 | 0.004578 | -0.064087 | 0.091553 | 119.0002 | -2.3941 | -2.4536 | 119.0369 | 118.9728 | 118.9453 | -0.027466 | -0.054932 | 118.9911 | -2.3346 | -2.4033 | 119.0369 | 119.1238 | 118.9682 | 0.13275 | -0.022888 | 0.036621 | -0.050354 | 0.045777 | 0.009156 | 0.009155 | 0.07782 | 119.0094 | 119.0689 | -2.4033 | -2.4124 | 118.9499 | 119.0002 | 118.9362 | 118.9362
3699.7188 | 121.4447 | -119.0231 | 2.3987 | 0.02121 | 0.015001 | -0.033295 | 0.037335 | -0.01549 | -0.028822 | -0.020469 | 0.0055542 | -0.059515 | -0.0028882 | 0.030198 | -0.016445 | -0.011382 | -0.015674 | -0.10529 | -0.032043 | -0.032043 | -0.10071 | 0.009155 | -0.07782 | -0.068665 | -0.073242 | 0.041199 | -0.032043 | -0.027466 | 0.027466 | -0.050354 | 0.086975 | 118.9911 | -2.4307 | -2.4994 | 119.0323 | 118.9545 | 118.9453 | -0.036622 | -0.045777 | 118.9911 | -2.3575 | -2.4261 | 119.0506 | 119.1101 | 118.9728 | 0.11902 | -0.018311 | 0.041198 | -0.068665 | 0.059509 | 0.004577 | 0 | 0.073242 | 118.9911 | 119.0643 | -2.4307 | -2.4307 | 118.9224 | 118.9957 | 118.9178 | 118.9499
3701.5312 | 121.4996 | -119.0002 | 2.3758 | 0.02121 | 0.015001 | -0.032013 | 0.035626 | -0.012072 | -0.028822 | -0.022178 | 0.014709 | -0.059943 | 0.00095715 | 0.034257 | -0.018581 | -0.012023 | -0.011401 | -0.027466 | -0.018311 | -0.036621 | -0.032043 | 0.09613 | 0.022888 | 0.013733 | 0.013733 | 0.032043 | -0.018311 | 0.022888 | 0.10986 | 0.018311 | 0.14191 | 118.9636 | -2.3941 | -2.4078 | 119.0964 | 119.014 | 119.0231 | 0.050354 | 0.059509 | 118.9819 | -2.3438 | -2.3529 | 119.1101 | 119.1422 | 119.0186 | 0.16022 | 0.036622 | 0.13275 | 0.004578 | 0.12817 | 0.041199 | 0.01831 | 0.050354 | 118.9819 | 119.0323 | -2.4124 | -2.3941 | 118.9682 | 119.0231 | 118.9728 | 119.014
3703.2656 | 121.4996 | -119.0323 | 2.3529 | 0.036468 | 0.015428 | -0.033295 | 0.036053 | -0.011644 | -0.028608 | -0.021324 | 0.011658 | -0.060584 | -0.0011792 | 0.032334 | -0.017299 | -0.010314 | -0.012469 | -0.041199 | -0.027466 | -0.004578 | -0.018311 | 0.11444 | 0.013733 | 0.022888 | 0.013733 | 0.036621 | -0.027466 | 0.022888 | 0.10529 | 0.032043 | 0.14191 | 119.0277 | -2.3804 | -2.3712 | 119.1467 | 119.0552 | 119.046 | 0.027466 | 0.018311 | 119.0048 | -2.3163 | -2.33 | 119.1376 | 119.1742 | 119.0643 | 0.16937 | 0.059509 | 0.11902 | -0.013733 | 0.13275 | 0.050354 | -0.022888 | 0.064087 | 119.0048 | 119.0689 | -2.3575 | -2.3804 | 119.014 | 119.0552 | 118.9911 | 119.046
3705.0625 | 121.4905 | -119.0872 | 2.3254 | 0.01358 | 0.013719 | -0.03415 | 0.033703 | -0.016771 | -0.028822 | -0.024101 | 0.011658 | -0.062079 | 0.001598 | 0.02913 | -0.021572 | -0.0101 | -0.010333 | -0.09613 | -0.009155 | -0.036621 | -0.07782 | 0.045776 | -0.022888 | -0.013733 | -0.059509 | 0.054932 | -0.050354 | -0.045776 | 0.032043 | -0.022888 | 0.086975 | 119.0506 | -2.3346 | -2.4033 | 119.133 | 119.0735 | 119.0643 | 0.022888 | 0.013733 | 119.0369 | -2.2705 | -2.3712 | 119.1193 | 119.1742 | 119.0643 | 0.13733 | 0.027466 | 0.082397 | -0.041199 | 0.082397 | 0.004578 | 0.027466 | 0.10529 | 119.0781 | 119.1422 | -2.3621 | -2.3758 | 119.0094 | 119.0414 | 118.9911 | 119.0277
3706.8594 | 121.5454 | -119.101 | 2.3071 | 0.02121 | 0.015641 | -0.033509 | 0.037549 | -0.011004 | -0.02989 | -0.020469 | 0.011658 | -0.059088 | -0.00075185 | 0.032548 | -0.017085 | -0.01245 | -0.015033 | -0.050354 | -0.036621 | -0.022888 | -0.018311 | 0.10986 | 0 | 0.013733 | 0.004578 | 0.036621 | -0.027466 | 0.022888 | 0.11444 | 0.036621 | 0.15106 | 119.0781 | -2.3438 | -2.3254 | 119.2108 | 119.1147 | 119.101 | 0.036621 | 0.022888 | 119.0735 | -2.2705 | -2.2842 | 119.2154 | 119.252 | 119.1376 | 0.17853 | 0.064087 | 0.13275 | 0.004577 | 0.14191 | 0.050354 | -0.013733 | 0.064087 | 119.0643 | 119.1376 | -2.33 | -2.3346 | 119.0826 | 119.1238 | 119.0506 | 119.1055
3708.6562 | 121.5408 | -119.1284 | 2.2705 | 0.02121 | 0.012224 | -0.031586 | 0.036267 | -0.017199 | -0.028395 | -0.024528 | 0.0055542 | -0.06037 | -0.0031018 | 0.037675 | -0.016231 | -0.011809 | -0.011401 | -0.082397 | -0.013733 | -0.032043 | -0.09613 | 0.041199 | -0.059509 | -0.036621 | -0.032043 | 0.009155 | -0.045776 | 0.018311 | 0.091553 | 0.004578 | 0.15106 | 119.0964 | -2.2842 | -2.3666 | 119.1696 | 119.0918 | 119.0689 | -0.004578 | -0.027466 | 119.0826 | -2.2614 | -2.2522 | 119.22 | 119.2795 | 119.133 | 0.19684 | 0.050354 | 0.073242 | -0.064087 | 0.13733 | 0.064087 | 0.01831 | 0.054931 | 119.1147 | 119.1376 | -2.3026 | -2.3163 | 119.0323 | 119.1467 | 119.046 | 119.0964
3710.3906 | 121.6324 | -119.1788 | 2.2247 | 0.01358 | 0.011796 | -0.035431 | 0.034558 | -0.016985 | -0.031172 | -0.021324 | 0.0025024 | -0.062933 | -0.0013928 | 0.036606 | -0.01794 | -0.010955 | -0.010547 | -0.036621 | -0.045776 | -0.004578 | 0.022888 | 0.17395 | 0.07782 | 0.082397 | 0.082397 | 0.022888 | -0.018311 | 0.091553 | 0.20142 | 0.11902 | 0.21057 | 119.1742 | -2.2705 | -2.2018 | 119.3527 | 119.2612 | 119.2566 | 0.086975 | 0.082398 | 119.1605 | -2.2018 | -2.1332 | 119.3802 | 119.3893 | 119.2978 | 0.22888 | 0.13733 | 0.17853 | 0.027466 | 0.21973 | 0.10986 | -0.041198 | 0.041199 | 119.133 | 119.2017 | -2.2293 | -2.243 | 119.2017 | 119.2703 | 119.1422 | 119.2612
3712.1875 | 121.4722 | -119.2383 | 2.2247 | 0.0059509 | 0.016282 | -0.032868 | 0.037121 | -0.017199 | -0.030531 | -0.020683 | 0.0055542 | -0.059729 | -0.0011792 | 0.029557 | -0.018581 | -0.010527 | -0.009692 | -0.07782 | -0.009155 | -0.013733 | -0.09613 | -0.009155 | -0.073242 | -0.073242 | -0.10071 | 0.054932 | -0.036621 | -0.041199 | 0.013733 | -0.059509 | 0.091553 | 119.2245 | -2.2339 | -2.3209 | 119.2291 | 119.165 | 119.165 | -0.059509 | -0.059509 | 119.2017 | -2.1698 | -2.2659 | 119.252 | 119.3298 | 119.1788 | 0.12817 | -0.022888 | 0.004578 | -0.082397 | 0.050354 | -0.004578 | 0.004578 | 0.091553 | 119.2291 | 119.2932 | -2.2385 | -2.2614 | 119.1422 | 119.1971 | 119.1605 | 119.1376
3713.9688 | 121.637 | -119.2062 | 2.1606 | 0.01358 | 0.013719 | -0.033509 | 0.033917 | -0.011431 | -0.028608 | -0.019615 | 0.0055542 | -0.061011 | -0.0026744 | 0.037461 | -0.01559 | -0.0101 | -0.013965 | -0.009155 | -0.054932 | 0.018311 | 0.036621 | 0.16937 | 0.045776 | 0.050354 | 0.073242 | 0.004578 | -0.009155 | 0.11444 | 0.17395 | 0.091553 | 0.20599 | 119.2245 | -2.2156 | -2.124 | 119.3756 | 119.2566 | 119.252 | 0.032043 | 0.027465 | 119.1971 | -2.1561 | -2.0462 | 119.3802 | 119.4122 | 119.2978 | 0.21515 | 0.10071 | 0.15106 | 0.01831 | 0.1831 | 0.1236 | -0.073243 | 0.013733 | 119.1513 | 119.2108 | -2.1423 | -2.1698 | 119.2429 | 119.3207 | 119.1971 | 119.2795
3715.75 | 121.5958 | -119.2703 | 2.1652 | 0.028839 | 0.014573 | -0.033295 | 0.035626 | -0.017412 | -0.030104 | -0.024101 | 0.0055542 | -0.061224 | -0.00075185 | 0.028916 | -0.019649 | -0.0079638 | -0.013324 | -0.054932 | -0.054932 | -0.013733 | -0.009155 | 0.11444 | 0.022888 | 0.036621 | 0.013733 | 0.009155 | -0.027466 | 0.036621 | 0.11902 | 0.059509 | 0.14191 | 119.2566 | -2.2202 | -2.1744 | 119.3848 | 119.3069 | 119.2932 | 0.050354 | 0.036621 | 119.2429 | -2.1561 | -2.1286 | 119.3893 | 119.4122 | 119.3298 | 0.16937 | 0.086975 | 0.12817 | 0.004578 | 0.14649 | 0.064087 | -0.041199 | 0.036621 | 119.2154 | 119.2795 | -2.179 | -2.1927 | 119.2612 | 119.3069 | 119.2154 | 119.2841
3717.5625 | 121.669 | -119.3939 | 2.0462 | 0.0059509 | 0.010087 | -0.034791 | 0.034344 | -0.01784 | -0.028822 | -0.024101 | 0.0055542 | -0.06272 | 0.00031615 | 0.038315 | -0.020931 | -0.011809 | -0.01076 | -0.027466 | -0.050354 | 0.013733 | 0.041199 | 0.20142 | 0.086975 | 0.09613 | 0.12817 | -0.004578 | -0.004578 | 0.10071 | 0.20599 | 0.14648 | 0.18768 | 119.4077 | -2.0966 | -2.005 | 119.5953 | 119.4901 | 119.4809 | 0.082397 | 0.073242 | 119.3893 | -2.0508 | -1.9455 | 119.5999 | 119.5816 | 119.5404 | 0.19226 | 0.15106 | 0.18768 | 0.027466 | 0.21057 | 0.10529 | -0.064087 | 0 | 119.3436 | 119.3893 | -2.0325 | -2.0508 | 119.4351 | 119.4946 | 119.3665 | 119.5221
3719.2969 | 121.6141 | -119.4168 | 2.0142 | 0.044098 | 0.015001 | -0.030732 | 0.037335 | -0.01314 | -0.028395 | -0.020683 | 0.014709 | -0.062506 | -0.0016064 | 0.037461 | -0.018367 | -0.010314 | -0.0077694 | -0.022888 | -0.045776 | 0.009155 | 0.009155 | 0.13733 | 0.041199 | 0.036621 | 0.059509 | 0.018311 | -0.009155 | 0.054932 | 0.11902 | 0.054932 | 0.15106 | 119.426 | -2.0599 | -2.005 | 119.5541 | 119.4534 | 119.458 | 0.027466 | 0.032044 | 119.4077 | -1.9958 | -1.9592 | 119.5358 | 119.5679 | 119.4717 | 0.16022 | 0.064087 | 0.12817 | 0 | 0.12817 | 0.064087 | -0.054931 | 0.027466 | 119.371 | 119.4351 | -2.005 | -2.0233 | 119.426 | 119.4717 | 119.3939 | 119.4763
3721.0781 | 121.6644 | -119.4992 | 1.9089 | 0.01358 | 0.013292 | -0.033082 | 0.038617 | -0.012285 | -0.024977 | -0.020897 | 0.0055542 | -0.06037 | -0.0011792 | 0.035538 | -0.014522 | -0.010955 | -0.01311 | 0.009155 | -0.041199 | 0.018311 | 0.050354 | 0.16022 | 0.050354 | 0.068665 | 0.10529 | 0.009155 | 0.013733 | 0.09613 | 0.16022 | 0.091553 | 0.21057 | 119.5175 | -1.9501 | -1.8585 | 119.6594 | 119.5679 | 119.5496 | 0.050354 | 0.032043 | 119.5129 | -1.8997 | -1.8127 | 119.6594 | 119.7098 | 119.5908 | 0.19684 | 0.07782 | 0.14191 | 0.032043 | 0.14648 | 0.082397 | -0.05951 | -0.004578 | 119.458 | 119.5084 | -1.8906 | -1.8951 | 119.5496 | 119.5953 | 119.5084 | 119.6045
3722.7969 | 121.637 | -119.6411 | 1.8082 | 0.028839 | 0.015428 | -0.031586 | 0.038403 | -0.014635 | -0.028181 | -0.020683 | 0.011658 | -0.060156 | -0.00075185 | 0.037034 | -0.019222 | -0.0088184 | -0.015246 | -0.018311 | -0.045776 | 0.009155 | 0.045776 | 0.17853 | 0.032043 | 0.068665 | 0.07782 | 0.018311 | 0 | 0.059509 | 0.13733 | 0.050354 | 0.14648 | 119.6503 | -1.8539 | -1.7624 | 119.8196 | 119.7098 | 119.6732 | 0.05951 | 0.022888 | 119.6411 | -1.7899 | -1.7487 | 119.7784 | 119.7876 | 119.6915 | 0.14648 | 0.050354 | 0.16937 | 0.036621 | 0.13733 | 0.059509 | -0.054931 | 0.018311 | 119.5953 | 119.6594 | -1.799 | -1.8082 | 119.6869 | 119.7006 | 119.6228 | 119.7189
3724.5938 | 121.55 | -119.7372 | 1.7807 | 0.028839 | 0.017137 | -0.033295 | 0.038189 | -0.013353 | -0.029676 | -0.022605 | 0.011658 | -0.061011 | 0.00052975 | 0.034043 | -0.016445 | -0.012236 | -0.012896 | -0.032043 | -0.018311 | -0.032043 | -0.059509 | 0.050354 | -0.050354 | -0.050354 | -0.050354 | 0.041199 | -0.022888 | -0.036621 | 0.036621 | -0.050354 | 0.082397 | 119.7052 | -1.799 | -1.8402 | 119.7876 | 119.6869 | 119.6869 | -0.018311 | -0.018311 | 119.7144 | -1.7395 | -1.8173 | 119.7739 | 119.8196 | 119.6869 | 0.10528 | -0.027466 | 0.082397 | -0.027466 | 0.059509 | -0.013733 | 0.013732 | 0.064087 | 119.7189 | 119.7784 | -1.8127 | -1.8036 | 119.6777 | 119.7006 | 119.7052 | 119.6869
3726.3281 | 121.6095 | -119.8425 | 1.6434 | 0.01358 | 0.014146 | -0.030304 | 0.037121 | -0.012499 | -0.028822 | -0.020897 | 0.014709 | -0.059943 | -0.0013928 | 0.03917 | -0.016231 | -0.010527 | -0.015674 | -0.032043 | -0.013733 | 0 | -0.009155 | 0.10071 | 0.004578 | 0.018311 | 0.013733 | 0.027466 | -0.027466 | 0.013733 | 0.082397 | 0 | 0.12817 | 119.8425 | -1.6571 | -1.6525 | 119.9432 | 119.8608 | 119.8471 | 0.018311 | 0.004578 | 119.8151 | -1.6159 | -1.6296 | 119.9249 | 119.9707 | 119.8425 | 0.15564 | 0.027466 | 0.10071 | -0.009155 | 0.10986 | 0.041199 | -0.013733 | 0.054932 | 119.8288 | 119.87 | -1.6434 | -1.6708 | 119.8334 | 119.8563 | 119.8105 | 119.8563
3728.1094 | 121.5591 | -119.9524 | 1.5747 | 0.01358 | 0.015428 | -0.032013 | 0.037121 | -0.016131 | -0.029463 | -0.023246 | 0.0025024 | -0.061865 | -0.00075185 | 0.027207 | -0.01794 | -0.011168 | -0.013324 | -0.086975 | -0.027466 | -0.032043 | -0.10529 | -0.009155 | -0.073242 | -0.059509 | -0.082397 | 0.041199 | -0.045776 | -0.036621 | 0.022888 | -0.068665 | 0.091553 | 119.9203 | -1.6022 | -1.68 | 119.9432 | 119.8929 | 119.8792 | -0.027466 | -0.041199 | 119.9066 | -1.5335 | -1.6113 | 119.9753 | 120.0439 | 119.8837 | 0.13733 | -0.022889 | 0.022888 | -0.073243 | 0.068664 | 0.009155 | 0.004577 | 0.086975 | 119.9249 | 119.9936 | -1.6068 | -1.6205 | 119.8471 | 119.9158 | 119.8654 | 119.87
3729.8906 | 121.6187 | -120.0302 | 1.506 | 0.02121 | 0.013505 | -0.0318 | 0.036908 | -0.01549 | -0.02989 | -0.023246 | 0.011658 | -0.059515 | 0.00074335 | 0.034257 | -0.01794 | -0.0101 | -0.013537 | -0.032043 | -0.036621 | -0.036621 | -0.027466 | 0.11902 | 0.009155 | 0.018311 | 0.009155 | 0.064087 | -0.032043 | 0.027466 | 0.10529 | 0.032043 | 0.13733 | 119.9936 | -1.5427 | -1.5335 | 120.1492 | 120.0485 | 120.0394 | 0.054932 | 0.045776 | 119.9982 | -1.442 | -1.4786 | 120.1355 | 120.1675 | 120.0623 | 0.16937 | 0.064086 | 0.15564 | 0.009155 | 0.13733 | 0.059509 | 0 | 0.09613 | 119.9936 | 120.0943 | -1.5427 | -1.5381 | 120.0027 | 120.0577 | 119.9982 | 120.0394
3731.7031 | 121.6873 | -120.1309 | 1.3458 | 0.028839 | 0.01436 | -0.032227 | 0.034985 | -0.016558 | -0.027967 | -0.021324 | 0.008606 | -0.063147 | -0.00053825 | 0.043015 | -0.017513 | -0.010527 | -0.013537 | -0.022888 | -0.041199 | 0.009155 | 0.027466 | 0.17853 | 0.027466 | 0.050354 | 0.059509 | 0.009155 | -0.018311 | 0.041199 | 0.1236 | 0.050354 | 0.17395 | 120.1401 | -1.387 | -1.3184 | 120.3094 | 120.1813 | 120.1584 | 0.041199 | 0.018311 | 120.1126 | -1.3367 | -1.3046 | 120.2545 | 120.3049 | 120.1813 | 0.19226 | 0.068665 | 0.16937 | 0.018311 | 0.14191 | 0.05951 | -0.050354 | 0.027466 | 120.0897 | 120.1401 | -1.3367 | -1.3641 | 120.1584 | 120.1721 | 120.108 | 120.1904
3733.5 | 121.6324 | -120.2866 | 1.2497 | 0.02121 | 0.013292 | -0.030945 | 0.037335 | -0.015703 | -0.026899 | -0.022605 | 0.008606 | -0.060584 | -0.00011105 | 0.037247 | -0.018367 | -0.011168 | -0.012256 | -0.054932 | -0.004578 | -0.032043 | -0.036621 | 0.07782 | 0.004578 | 0.004578 | -0.004578 | 0.054932 | -0.054932 | 0.004578 | 0.10529 | 0.009155 | 0.12817 | 120.2545 | -1.2543 | -1.2863 | 120.3644 | 120.2911 | 120.2911 | 0.036621 | 0.036621 | 120.2316 | -1.1948 | -1.2451 | 120.3918 | 120.4147 | 120.2957 | 0.18311 | 0.064087 | 0.10986 | -0.004578 | 0.16022 | 0.05951 | 0.027465 | 0.10986 | 120.282 | 120.3415 | -1.2817 | -1.3046 | 120.2499 | 120.2911 | 120.2316 | 120.282
3735.2344 | 121.7422 | -120.3552 | 1.1215 | 0.01358 | 0.011583 | -0.03415 | 0.033917 | -0.018694 | -0.028181 | -0.020469 | 0.008606 | -0.064856 | -0.00053825 | 0.031479 | -0.018367 | -0.0101 | -0.0099056 | -0.036621 | -0.054932 | 0 | 0.018311 | 0.18768 | 0.086975 | 0.082397 | 0.068665 | 0.009155 | -0.013733 | 0.082397 | 0.19226 | 0.1236 | 0.19684 | 120.3552 | -1.1765 | -1.1032 | 120.5429 | 120.4376 | 120.4422 | 0.082397 | 0.086975 | 120.3415 | -1.1124 | -1.0391 | 120.5475 | 120.5521 | 120.4788 | 0.21057 | 0.13733 | 0.18768 | 0.018311 | 0.20599 | 0.09613 | -0.054932 | 0.022888 | 120.3003 | 120.3644 | -1.1215 | -1.1353 | 120.3735 | 120.4376 | 120.3186 | 120.4239
3737.0469 | 121.7285 | -120.4742 | 1.062 | 0.02121 | 0.016069 | -0.035645 | 0.03584 | -0.015062 | -0.029036 | -0.020897 | 0.0055542 | -0.062292 | -0.0020336 | 0.031052 | -0.018367 | -0.011595 | -0.016314 | 0 | -0.054932 | 0.027466 | 0.068665 | 0.22888 | 0.11902 | 0.10529 | 0.07782 | 0 | -0.004578 | 0.086975 | 0.21057 | 0.1236 | 0.1831 | 120.5017 | -1.1169 | -0.99335 | 120.7031 | 120.5795 | 120.5933 | 0.07782 | 0.091553 | 120.4697 | -1.062 | -0.97504 | 120.6848 | 120.6573 | 120.5978 | 0.18768 | 0.12817 | 0.20142 | 0.041199 | 0.21515 | 0.091553 | -0.082398 | 0.004578 | 120.4193 | 120.4742 | -1.0345 | -1.0666 | 120.5429 | 120.5612 | 120.4742 | 120.5521
3738.8438 | 121.7331 | -120.4376 | 1.0529 | -0.0016786 | 0.015641 | -0.030732 | 0.038189 | -0.015276 | -0.028608 | -0.023246 | 0.011658 | -0.062079 | 0.00031615 | 0.041733 | -0.013454 | -0.0092456 | -0.016528 | 0.013733 | -0.073242 | 0.022888 | 0.036621 | 0.17853 | 0.064087 | 0.054932 | 0.10071 | 0.022888 | -0.004578 | 0.10529 | 0.16937 | 0.09613 | 0.20599 | 120.4605 | -1.1261 | -1.0162 | 120.6162 | 120.4926 | 120.5017 | 0.032044 | 0.041199 | 120.433 | -1.03 | -0.94757 | 120.607 | 120.6436 | 120.5338 | 0.21057 | 0.10071 | 0.15564 | 0.013733 | 0.17395 | 0.10986 | -0.09613 | 0.027466 | 120.3644 | 120.4605 | -1.03 | -1.0574 | 120.4742 | 120.5429 | 120.4514 | 120.5383
3740.6406 | 121.6553 | -120.5063 | 1.0483 | 0.036468 | 0.015001 | -0.033722 | 0.037335 | -0.011004 | -0.030531 | -0.023674 | 0.011658 | -0.059302 | -0.00096545 | 0.033188 | -0.020931 | -0.010955 | -0.013324 | -0.068665 | -0.009155 | -0.022888 | -0.068665 | 0.032043 | -0.022888 | -0.022888 | -0.086975 | 0.068665 | -0.050354 | -0.036621 | 0.064087 | -0.022888 | 0.091553 | 120.4834 | -1.0574 | -1.1169 | 120.5383 | 120.4834 | 120.4834 | 0 | 0 | 120.4559 | -0.97961 | -1.0849 | 120.5704 | 120.5978 | 120.4834 | 0.14191 | 0.027466 | 0.054931 | -0.045777 | 0.11444 | 0.013733 | 0.013733 | 0.11902 | 120.4971 | 120.575 | -1.0712 | -1.0986 | 120.4376 | 120.4697 | 120.4376 | 120.4193
3742.3906 | 121.6187 | -120.3094 | 1.2405 | 0.01358 | 0.014573 | -0.032013 | 0.03584 | -0.017626 | -0.028608 | -0.020256 | 0.008606 | -0.061011 | -0.00011105 | 0.038102 | -0.016017 | -0.011809 | -0.01546 | -0.036621 | -0.018311 | -0.009155 | -0.032043 | 0.082397 | -0.018311 | -0.013733 | -0.022888 | 0.032043 | -0.018311 | -0.004578 | 0.050354 | -0.027466 | 0.10071 | 120.3003 | -1.2589 | -1.2726 | 120.3918 | 120.2957 | 120.2911 | -0.004578 | -0.009156 | 120.2911 | -1.2085 | -1.2451 | 120.3598 | 120.4102 | 120.282 | 0.11902 | -0.009155 | 0.091552 | -0.022888 | 0.068665 | 0.013733 | -0.009156 | 0.050354 | 120.2911 | 120.3415 | -1.2497 | -1.2589 | 120.2774 | 120.3049 | 120.2728 | 120.2866
3744.1875 | 121.6141 | -120.2545 | 1.3367 | 0.02121 | 0.016069 | -0.029877 | 0.037549 | -0.014208 | -0.02754 | -0.021751 | 0.008606 | -0.06037 | -0.00011105 | 0.035325 | -0.018581 | -0.010955 | -0.016955 | -0.082397 | -0.013733 | -0.032043 | -0.091553 | 0.022888 | -0.086975 | -0.059509 | -0.086975 | 0.041199 | -0.050354 | -0.027466 | 0.018311 | -0.064087 | 0.086975 | 120.2225 | -1.3504 | -1.4282 | 120.2774 | 120.195 | 120.1675 | -0.027466 | -0.054932 | 120.2042 | -1.2955 | -1.3641 | 120.2728 | 120.3415 | 120.1904 | 0.13733 | -0.013733 | 0.054931 | -0.05951 | 0.068665 | 0.022888 | 0.01831 | 0.091553 | 120.2408 | 120.2957 | -1.3687 | -1.387 | 120.163 | 120.2271 | 120.1721 | 120.1675
3745.9844 | 121.7148 | -120.2454 | 1.3412 | 0.028839 | 0.014573 | -0.031159 | 0.036694 | -0.01314 | -0.02989 | -0.021751 | 0.008606 | -0.063574 | 0.0018116 | 0.032975 | -0.017085 | -0.010527 | -0.010333 | -0.041199 | -0.036621 | 0 | 0 | 0.14191 | 0.022888 | 0.027466 | 0.041199 | 0.013733 | -0.032043 | 0.027466 | 0.13275 | 0.054932 | 0.15106 | 120.2454 | -1.3779 | -1.3412 | 120.3873 | 120.2728 | 120.2682 | 0.027466 | 0.022888 | 120.2133 | -1.3275 | -1.3138 | 120.3781 | 120.3964 | 120.3003 | 0.18311 | 0.086975 | 0.14191 | 0 | 0.16479 | 0.059509 | -0.036621 | 0.045776 | 120.2087 | 120.2591 | -1.3412 | -1.3733 | 120.2454 | 120.2728 | 120.2042 | 120.2866
3747.7656 | 121.6644 | -120.1447 | 1.4557 | 0.02121 | 0.014787 | -0.033082 | 0.037976 | -0.016985 | -0.028822 | -0.021751 | 0.0055542 | -0.059302 | 0.0013844 | 0.029343 | -0.020503 | -0.012236 | -0.011401 | -0.018311 | -0.022888 | -0.022888 | -0.013733 | 0.1236 | 0.009155 | 0.018311 | 0.013733 | 0.027466 | -0.022888 | 0.027466 | 0.10529 | 0.022888 | 0.12817 | 120.1218 | -1.4786 | -1.4694 | 120.2682 | 120.163 | 120.1538 | 0.041199 | 0.032043 | 120.1218 | -1.4282 | -1.4282 | 120.2499 | 120.2728 | 120.1675 | 0.15106 | 0.045776 | 0.14648 | 0.009155 | 0.12817 | 0.050354 | 0 | 0.050354 | 120.1218 | 120.1721 | -1.4786 | -1.4786 | 120.1309 | 120.1721 | 120.1263 | 120.1584
3749.5625 | 121.6873 | -120.0577 | 1.4877 | 0.02121 | 0.015214 | -0.034577 | 0.037976 | -0.013353 | -0.028395 | -0.021751 | 0.008606 | -0.061438 | 0.00074335 | 0.042374 | -0.016872 | -0.0088184 | -0.015033 | -0.086975 | -0.032043 | -0.036621 | -0.091553 | 0.036621 | -0.068665 | -0.041199 | -0.054932 | 0.032043 | -0.045776 | 0 | 0.059509 | -0.018311 | 0.11444 | 120.0211 | -1.5198 | -1.5793 | 120.0943 | 120.0165 | 119.989 | -0.004578 | -0.032044 | 120.0119 | -1.4557 | -1.4877 | 120.1172 | 120.1721 | 120.0394 | 0.16022 | 0.027465 | 0.073242 | -0.054932 | 0.10528 | 0.045776 | 0.004578 | 0.077819 | 120.0256 | 120.0897 | -1.5244 | -1.5335 | 119.9661 | 120.0577 | 119.9707 | 120.0027
3751.3438 | 121.6553 | -119.9478 | 1.6388 | 0.01358 | 0.01671 | -0.032654 | 0.038189 | -0.014208 | -0.028822 | -0.020256 | 0.0055542 | -0.059088 | 0.00095715 | 0.033829 | -0.017513 | -0.0101 | -0.013537 | -0.045776 | -0.027466 | 0 | -0.050354 | 0.068665 | -0.041199 | -0.036621 | -0.045776 | 0.041199 | -0.027466 | -0.018311 | 0.059509 | -0.032043 | 0.086975 | 119.9478 | -1.6663 | -1.6891 | 120.0165 | 119.9112 | 119.9066 | -0.036621 | -0.041199 | 119.9203 | -1.5976 | -1.6571 | 120.0073 | 120.0348 | 119.9158 | 0.11444 | -0.004577 | 0.068665 | -0.050354 | 0.086975 | 0.009155 | -0.027466 | 0.068665 | 119.9203 | 119.989 | -1.6388 | -1.6663 | 119.8975 | 119.9295 | 119.902 | 119.902
3753.0781 | 121.7148 | -120.0531 | 1.5381 | 0.02121 | 0.016496 | -0.034577 | 0.038403 | -0.011431 | -0.030958 | -0.021965 | 0.008606 | -0.059943 | -0.00075185 | 0.034684 | -0.019008 | -0.010314 | -0.013324 | -0.041199 | -0.018311 | -0.027466 | -0.027466 | 0.11902 | 0.013733 | 0.004578 | -0.009155 | 0.027466 | -0.027466 | 0.036621 | 0.11444 | 0.027466 | 0.14191 | 120.0256 | -1.5564 | -1.5656 | 120.1721 | 120.0577 | 120.0668 | 0.032044 | 0.041199 | 120.0256 | -1.5106 | -1.5015 | 120.1675 | 120.195 | 120.0806 | 0.16937 | 0.054932 | 0.14649 | 0 | 0.14191 | 0.064087 | 0.009155 | 0.054932 | 120.0348 | 120.0806 | -1.5656 | -1.5656 | 120.0256 | 120.0897 | 120.0119 | 120.0439
3754.8438 | 121.7697 | -120.0623 | 1.4969 | 0.0059509 | 0.013078 | -0.032441 | 0.035199 | -0.014849 | -0.026899 | -0.023033 | 0.011658 | -0.061651 | -0.00032465 | 0.033829 | -0.016231 | -0.010527 | -0.012042 | -0.036621 | -0.050354 | 0.022888 | 0.004578 | 0.14191 | 0.041199 | 0.050354 | 0.050354 | 0.013733 | 0.013733 | 0.09613 | 0.1831 | 0.086975 | 0.20599 | 120.0851 | -1.5472 | -1.4923 | 120.2042 | 120.1126 | 120.1035 | 0.027466 | 0.018311 | 120.076 | -1.4832 | -1.4008 | 120.2454 | 120.2683 | 120.1492 | 0.19226 | 0.073242 | 0.11902 | -0.01831 | 0.16937 | 0.082397 | -0.073242 | 0 | 120.0119 | 120.076 | -1.474 | -1.4832 | 120.0668 | 120.1584 | 120.0256 | 120.1126
3756.6562 | 121.7926 | -120.1126 | 1.4465 | 0.01358 | 0.012437 | -0.032227 | 0.035412 | -0.01848 | -0.02754 | -0.020897 | 0.008606 | -0.062506 | -0.00011105 | 0.038529 | -0.019008 | -0.011595 | -0.011615 | -0.009155 | -0.054932 | 0.009155 | 0.054932 | 0.2243 | 0.10529 | 0.11444 | 0.1236 | 0.013733 | -0.009155 | 0.082397 | 0.19226 | 0.11444 | 0.19684 | 120.1218 | -1.5015 | -1.3916 | 120.3369 | 120.2271 | 120.2179 | 0.10529 | 0.096131 | 120.1035 | -1.4328 | -1.3641 | 120.3049 | 120.3094 | 120.2271 | 0.20599 | 0.1236 | 0.21515 | 0.045777 | 0.20142 | 0.091552 | -0.064087 | 0.022888 | 120.0577 | 120.1263 | -1.4374 | -1.4557 | 120.1675 | 120.195 | 120.1035 | 120.2362
3758.4531 | 121.8018 | -120.1401 | 1.4008 | 0.01358 | 0.014787 | -0.033509 | 0.036694 | -0.015276 | -0.026258 | -0.022819 | 0.008606 | -0.058661 | 0.00010255 | 0.034043 | -0.015163 | -0.0096728 | -0.011187 | -0.036621 | -0.045776 | -0.013733 | 0 | 0.15106 | 0.036621 | 0.041199 | 0.050354 | 0.004578 | -0.013733 | 0.091553 | 0.15564 | 0.082397 | 0.20599 | 120.1263 | -1.4465 | -1.4008 | 120.2911 | 120.1813 | 120.1767 | 0.054932 | 0.050354 | 120.1263 | -1.3962 | -1.3092 | 120.2957 | 120.3461 | 120.2225 | 0.21973 | 0.09613 | 0.16479 | 0.013733 | 0.16937 | 0.10529 | -0.032043 | 0.018311 | 120.0943 | 120.1447 | -1.4145 | -1.4145 | 120.1401 | 120.2316 | 120.1035 | 120.1904
3760.2031 | 121.669 | -120.2316 | 1.3916 | 0.0059509 | 0.016496 | -0.034577 | 0.035412 | -0.015917 | -0.026899 | -0.023674 | 0.011658 | -0.059515 | -0.00096545 | 0.036179 | -0.020931 | -0.012023 | -0.011401 | -0.09613 | 0.004578 | -0.054932 | -0.07782 | 0.045776 | -0.018311 | -0.009155 | -0.068665 | 0.054932 | -0.045776 | -0.050354 | 0.050354 | -0.009155 | 0.082397 | 120.1767 | -1.387 | -1.4694 | 120.2774 | 120.2225 | 120.2133 | 0.045777 | 0.036621 | 120.1859 | -1.3367 | -1.442 | 120.282 | 120.314 | 120.2225 | 0.12817 | 0.036621 | 0.10071 | -0.022888 | 0.09613 | -0.004578 | 0.05951 | 0.10071 | 120.2362 | 120.2866 | -1.4465 | -1.4374 | 120.1538 | 120.1813 | 120.1355 | 120.163
3762 | 121.7285 | -120.2957 | 1.3412 | 0.028839 | 0.015855 | -0.034577 | 0.03648 | -0.014422 | -0.02754 | -0.021537 | 0.011658 | -0.059729 | 0.0013844 | 0.02977 | -0.020076 | -0.0148 | -0.012896 | -0.086975 | -0.013733 | -0.036621 | -0.068665 | 0.041199 | -0.018311 | -0.022888 | -0.073242 | 0.045776 | -0.041199 | -0.036621 | 0.068665 | -0.018311 | 0.11444 | 120.2591 | -1.355 | -1.4099 | 120.3369 | 120.2728 | 120.2774 | 0.013733 | 0.01831 | 120.2545 | -1.2955 | -1.3779 | 120.3644 | 120.4102 | 120.2774 | 0.15564 | 0.022888 | 0.07782 | -0.032044 | 0.10986 | 0.004578 | 0.022888 | 0.086975 | 120.282 | 120.3415 | -1.3779 | -1.3824 | 120.2271 | 120.2591 | 120.2087 | 120.2225
3763.7812 | 121.8063 | -120.3049 | 1.2543 | 0.028839 | 0.015641 | -0.0318 | 0.035412 | -0.013994 | -0.027327 | -0.021751 | 0.014709 | -0.062506 | -0.00096545 | 0.033616 | -0.014736 | -0.0092456 | -0.01311 | 0.004578 | -0.041199 | 0.018311 | 0.050354 | 0.19684 | 0.045776 | 0.068665 | 0.11444 | 0.009155 | -0.004578 | 0.07782 | 0.16937 | 0.091553 | 0.19226 | 120.3232 | -1.2955 | -1.2039 | 120.5017 | 120.3735 | 120.3506 | 0.050354 | 0.027465 | 120.3003 | -1.2451 | -1.1765 | 120.4742 | 120.4971 | 120.3964 | 0.19684 | 0.096131 | 0.17853 | 0.032043 | 0.17395 | 0.082398 | -0.05951 | 0.013733 | 120.2637 | 120.314 | -1.236 | -1.2589 | 120.3552 | 120.3827 | 120.3094 | 120.4193
3765.5156 | 121.7468 | -120.3506 | 1.2726 | 0.028839 | 0.016923 | -0.032868 | 0.037549 | -0.013353 | -0.027967 | -0.021751 | 0.011658 | -0.059088 | 0.0018116 | 0.031693 | -0.017513 | -0.010527 | -0.016742 | -0.064087 | 0.004578 | -0.041199 | -0.054932 | 0.064087 | -0.004578 | 0 | -0.018311 | 0.068665 | -0.032043 | 0.009155 | 0.09613 | 0 | 0.13275 | 120.3094 | -1.268 | -1.3275 | 120.4147 | 120.3506 | 120.3461 | 0.041199 | 0.036621 | 120.3186 | -1.2039 | -1.2634 | 120.4468 | 120.4834 | 120.3506 | 0.16479 | 0.032043 | 0.10529 | -0.013733 | 0.12817 | 0.041198 | 0.045777 | 0.10071 | 120.3552 | 120.4193 | -1.3138 | -1.3046 | 120.2957 | 120.3598 | 120.2866 | 120.3323
3768.625 | 121.8201 | -120.3827 | 1.2131 | 0.02121 | 0.014573 | -0.033082 | 0.035199 | -0.01784 | -0.027967 | -0.022605 | 0.011658 | -0.062292 | 0.0011708 | 0.03917 | -0.016872 | -0.0092456 | -0.014178 | -0.045776 | -0.059509 | 0.004578 | -0.013733 | 0.13275 | 0.050354 | 0.050354 | 0.018311 | -0.004578 | -0.018311 | 0.050354 | 0.16937 | 0.086975 | 0.17395 | 120.3873 | -1.2726 | -1.2268 | 120.5154 | 120.433 | 120.433 | 0.045776 | 0.045776 | 120.3644 | -1.2177 | -1.1627 | 120.5521 | 120.5566 | 120.4697 | 0.19226 | 0.10529 | 0.12817 | -0.018311 | 0.18768 | 0.068665 | -0.064087 | 0.013733 | 120.3232 | 120.3781 | -1.2085 | -1.2314 | 120.369 | 120.433 | 120.3369 | 120.401
3772.7188 | 121.6873 | -118.7576 | 2.8976 | 0.01358 | 0.01436 | -0.033295 | 0.037762 | -0.014635 | -0.029676 | -0.02111 | 0.0055542 | -0.058661 | -0.00053825 | 0.031052 | -0.01559 | -0.012236 | -0.013751 | -0.036621 | -0.032043 | -0.018311 | -0.032043 | 0.073242 | -0.041199 | -0.036621 | -0.059509 | 0.027466 | -0.059509 | -0.036621 | 0.027466 | -0.059509 | 0.082397 | 118.7393 | -2.9297 | -2.9297 | 118.8309 | 118.721 | 118.7164 | -0.01831 | -0.022888 | 118.6981 | -2.8702 | -2.9343 | 118.7851 | 118.84 | 118.6981 | 0.14191 | 0 | 0.091553 | -0.013732 | 0.086975 | 0.022888 | -0.013732 | 0.086975 | 118.7256 | 118.7851 | -2.916 | -2.9572 | 118.7256 | 118.721 | 118.721 | 118.6981
3778.875 | 121.8155 | -118.1305 | 3.4058 | 0.01358 | 0.015855 | -0.032441 | 0.03648 | -0.017199 | -0.028395 | -0.022819 | 0.0055542 | -0.061224 | -0.0011792 | 0.035538 | -0.017085 | -0.011595 | -0.017383 | -0.064087 | -0.045776 | 0.009155 | -0.004578 | 0.12817 | 0.050354 | 0.045776 | -0.013733 | -0.018311 | -0.045776 | 0.022888 | 0.13275 | 0.073242 | 0.15564 | 118.1396 | -3.4515 | -3.4103 | 118.2587 | 118.1763 | 118.1808 | 0.036621 | 0.041199 | 118.0847 | -3.4241 | -3.3829 | 118.2632 | 118.2861 | 118.2037 | 0.20142 | 0.11902 | 0.11902 | -0.013733 | 0.17853 | 0.068664 | -0.054931 | 0.027465 | 118.0847 | 118.1122 | -3.3966 | -3.4515 | 118.1259 | 118.1534 | 118.0664 | 118.1168
3780.8281 | 121.6782 | -118.6066 | 3.0533 | 0.0059509 | 0.01735 | -0.032654 | 0.037976 | -0.011431 | -0.029036 | -0.021324 | 0.008606 | -0.059943 | -0.00053825 | 0.035538 | -0.016872 | -0.011595 | -0.017383 | -0.059509 | -0.032043 | -0.027466 | -0.068665 | 0.045776 | -0.050354 | -0.054932 | -0.050354 | 0.059509 | -0.032043 | -0.022888 | 0.032043 | -0.054932 | 0.07782 | 118.5791 | -3.0853 | -3.1219 | 118.6523 | 118.5516 | 118.5562 | -0.027466 | -0.022888 | 118.5745 | -2.9938 | -3.0762 | 118.6386 | 118.6844 | 118.5516 | 0.10986 | -0.022889 | 0.073242 | -0.041199 | 0.064086 | 0.009155 | -0.004577 | 0.091552 | 118.5745 | 118.6661 | -3.0808 | -3.0853 | 118.5379 | 118.5837 | 118.5471 | 118.5562
3782.6562 | 121.6873 | -119.2474 | 2.3529 | 0.01358 | 0.01436 | -0.030732 | 0.038403 | -0.010363 | -0.026258 | -0.022178 | 0.0055542 | -0.059088 | 0.00052975 | 0.035325 | -0.018154 | -0.011595 | -0.013324 | -0.09613 | -0.004578 | -0.013733 | -0.10071 | 0.004578 | -0.082397 | -0.059509 | -0.07782 | 0.045776 | -0.041199 | -0.032043 | 0.032043 | -0.054932 | 0.10071 | 119.2337 | -2.3575 | -2.4536 | 119.252 | 119.1879 | 119.165 | -0.045776 | -0.068664 | 119.2062 | -2.3071 | -2.3849 | 119.2795 | 119.3481 | 119.1925 | 0.14191 | -0.013733 | 0.018311 | -0.086975 | 0.073242 | 0.009156 | 0.009155 | 0.086975 | 119.2429 | 119.2932 | -2.3666 | -2.3941 | 119.1467 | 119.2154 | 119.1513 | 119.1696
3784.4531 | 121.7651 | -118.7256 | 2.8061 | 0.02121 | 0.013505 | -0.032654 | 0.033276 | -0.018694 | -0.030531 | -0.025596 | 0.008606 | -0.061651 | -0.0028882 | 0.04387 | -0.019649 | -0.012664 | -0.014392 | -0.009155 | -0.050354 | 0.022888 | 0.064087 | 0.22888 | 0.09613 | 0.091553 | 0.091553 | -0.009155 | -0.004578 | 0.07782 | 0.19226 | 0.12817 | 0.18768 | 118.7485 | -2.8564 | -2.742 | 118.9545 | 118.8171 | 118.8217 | 0.068665 | 0.073242 | 118.721 | -2.8152 | -2.7283 | 118.9178 | 118.9133 | 118.8538 | 0.19226 | 0.13275 | 0.20599 | 0.041199 | 0.19684 | 0.082398 | -0.073242 | -0.004577 | 118.6752 | 118.7164 | -2.7832 | -2.8107 | 118.7897 | 118.8034 | 118.7164 | 118.8171
3786.1875 | 121.6507 | -119.8883 | 1.7715 | 0.01358 | 0.016923 | -0.032441 | 0.035412 | -0.013353 | -0.026686 | -0.020469 | 0.0055542 | -0.059088 | -0.00096545 | 0.032334 | -0.019008 | -0.012236 | -0.013965 | -0.032043 | -0.013733 | -0.009155 | -0.027466 | 0.11444 | 0.013733 | -0.004578 | 0.004578 | 0.022888 | -0.027466 | 0 | 0.10071 | -0.004578 | 0.13275 | 119.8792 | -1.7853 | -1.799 | 120.0027 | 119.8837 | 119.902 | 0.004577 | 0.022888 | 119.8608 | -1.7487 | -1.7715 | 119.989 | 120.0211 | 119.8837 | 0.16022 | 0.022888 | 0.1236 | -0.018311 | 0.12817 | 0.027466 | -0.004578 | 0.050354 | 119.8746 | 119.9112 | -1.7807 | -1.799 | 119.8608 | 119.8883 | 119.8563 | 119.8929
3787.9688 | 121.7377 | -120.282 | 1.3596 | 0.028839 | 0.01436 | -0.033082 | 0.034985 | -0.0099357 | -0.02989 | -0.021965 | 0.0055542 | -0.058447 | -0.00053825 | 0.032975 | -0.017726 | -0.012023 | -0.015246 | -0.073242 | -0.013733 | -0.032043 | -0.059509 | 0.054932 | -0.004578 | -0.013733 | -0.068665 | 0.059509 | -0.045776 | 0 | 0.091553 | 0.004578 | 0.12817 | 120.2499 | -1.3733 | -1.4191 | 120.3369 | 120.2682 | 120.2774 | 0.01831 | 0.027465 | 120.2362 | -1.3 | -1.3596 | 120.3735 | 120.4102 | 120.2866 | 0.17395 | 0.050354 | 0.086975 | -0.027466 | 0.13733 | 0.045776 | 0.01831 | 0.10528 | 120.2682 | 120.3415 | -1.3916 | -1.4053 | 120.2225 | 120.282 | 120.2087 | 120.2133
3789.7656 | 121.8475 | -120.6757 | 0.93842 | 0.01358 | 0.013078 | -0.033722 | 0.034344 | -0.017626 | -0.031172 | -0.023033 | 0.0055542 | -0.063574 | -0.0013928 | 0.038102 | -0.018581 | -0.011382 | -0.016314 | -0.054932 | -0.054932 | 0.004578 | 0.027466 | 0.16937 | 0.068665 | 0.091553 | 0.059509 | 0.009155 | 0 | 0.073242 | 0.1831 | 0.11902 | 0.19226 | 120.6802 | -0.99335 | -0.91095 | 120.845 | 120.7672 | 120.7443 | 0.086975 | 0.064087 | 120.6757 | -0.92926 | -0.86517 | 120.8588 | 120.8679 | 120.7947 | 0.19226 | 0.11902 | 0.16479 | 0.022888 | 0.1831 | 0.073242 | -0.05951 | 0.009155 | 120.6207 | 120.6848 | -0.93384 | -0.93842 | 120.7031 | 120.7489 | 120.6207 | 120.7352
3791.5 | 121.7834 | -120.3964 | 1.2451 | 0.02121 | 0.013505 | -0.033082 | 0.038189 | -0.015062 | -0.029676 | -0.024528 | 0.0055542 | -0.059515 | 0.0011708 | 0.02678 | -0.016445 | -0.010527 | -0.012683 | -0.082397 | -0.018311 | -0.022888 | -0.09613 | 0.041199 | -0.054932 | -0.036621 | -0.041199 | 0.036621 | -0.036621 | 0.018311 | 0.086975 | -0.009155 | 0.13733 | 120.3735 | -1.2634 | -1.3412 | 120.4376 | 120.3598 | 120.3415 | -0.013733 | -0.032044 | 120.3598 | -1.2085 | -1.2268 | 120.4834 | 120.5338 | 120.3873 | 0.17395 | 0.027466 | 0.064087 | -0.073242 | 0.1236 | 0.054932 | 0.004577 | 0.073242 | 120.3781 | 120.433 | -1.268 | -1.2817 | 120.3003 | 120.4147 | 120.314 | 120.3552
3793.2344 | 121.7331 | -119.4443 | 2.2018 | 0.02121 | 0.017564 | -0.034577 | 0.03584 | -0.017626 | -0.029463 | -0.022178 | 0.014709 | -0.05802 | 0.0022388 | 0.029343 | -0.01794 | -0.012236 | -0.013965 | -0.073242 | -0.004578 | -0.045776 | -0.068665 | 0.041199 | -0.018311 | -0.009155 | -0.059509 | 0.050354 | -0.059509 | -0.027466 | 0.068665 | -0.009155 | 0.10986 | 119.3985 | -2.2064 | -2.2705 | 119.4855 | 119.4351 | 119.426 | 0.036621 | 0.027465 | 119.3848 | -2.1515 | -2.2293 | 119.5129 | 119.5541 | 119.4351 | 0.16937 | 0.050354 | 0.086975 | -0.022889 | 0.12817 | 0.032043 | 0.041198 | 0.10986 | 119.4397 | 119.4946 | -2.2476 | -2.2614 | 119.3756 | 119.4168 | 119.371 | 119.3848
3794.9688 | 121.8063 | -118.9224 | 2.6276 | 0.0059509 | 0.013933 | -0.033082 | 0.034985 | -0.013567 | -0.028395 | -0.022605 | 0.0055542 | -0.061011 | -0.00032465 | 0.03682 | -0.016445 | -0.010955 | -0.012896 | -0.027466 | -0.064087 | -0.009155 | 0.032043 | 0.15564 | 0.041199 | 0.054932 | 0.054932 | -0.004578 | 0.004578 | 0.09613 | 0.16937 | 0.09613 | 0.20142 | 118.9133 | -2.6917 | -2.5955 | 119.0781 | 118.9774 | 118.9636 | 0.064087 | 0.050354 | 118.927 | -2.6321 | -2.5314 | 119.0918 | 119.1238 | 119.0186 | 0.19684 | 0.091552 | 0.16479 | 0.041198 | 0.16479 | 0.091552 | -0.054932 | -0.009156 | 118.8583 | 118.9178 | -2.6367 | -2.623 | 118.9545 | 119.0186 | 118.895 | 118.9774
3796.75 | 121.6278 | -118.5471 | 3.0762 | 0.02121 | 0.015428 | -0.033722 | 0.039471 | -0.013994 | -0.02989 | -0.025383 | 0.0055542 | -0.061011 | -0.0016064 | 0.033188 | -0.017726 | -0.008391 | -0.014605 | -0.073242 | -0.027466 | -0.036621 | -0.086975 | 0.004578 | -0.07782 | -0.068665 | -0.10986 | 0.045776 | -0.041199 | -0.064087 | 0.009155 | -0.07782 | 0.073242 | 118.5104 | -3.1036 | -3.1631 | 118.5516 | 118.4784 | 118.4692 | -0.032044 | -0.041199 | 118.5059 | -3.0304 | -3.1403 | 118.5562 | 118.6203 | 118.4692 | 0.11444 | -0.036621 | 0.041199 | -0.050354 | 0.050354 | -0.022888 | 0.009155 | 0.086975 | 118.5196 | 118.5928 | -3.1128 | -3.1174 | 118.4601 | 118.483 | 118.4738 | 118.4372
3798.4844 | 121.6873 | -117.4988 | 4.0146 | 0.01358 | 0.013292 | -0.033082 | 0.033703 | -0.016985 | -0.025618 | -0.021965 | 0.0025024 | -0.064002 | 0.00052975 | 0.037247 | -0.018154 | -0.010527 | -0.012042 | -0.022888 | -0.041199 | 0.013733 | 0.050354 | 0.1831 | 0.086975 | 0.073242 | 0.041199 | 0.009155 | -0.018311 | 0.032043 | 0.16479 | 0.086975 | 0.16022 | 117.5125 | -4.0558 | -3.9642 | 117.6819 | 117.572 | 117.5858 | 0.059509 | 0.073242 | 117.4805 | -4.0054 | -3.9825 | 117.6636 | 117.659 | 117.5858 | 0.17853 | 0.10529 | 0.16937 | 0.036621 | 0.18311 | 0.050354 | -0.054932 | 0.027466 | 117.4576 | 117.5079 | -4.0009 | -4.0329 | 117.5491 | 117.5308 | 117.4759 | 117.54
3800.2344 | 121.8338 | -118.7119 | 2.861 | 0.02121 | 0.013719 | -0.032441 | 0.031781 | -0.016558 | -0.027967 | -0.023887 | 0.0055542 | -0.062079 | -0.0011792 | 0.030625 | -0.018154 | -0.010527 | -0.012896 | -0.036621 | -0.054932 | 0.004578 | 0.004578 | 0.15106 | 0.07782 | 0.086975 | 0.032043 | 0 | -0.013733 | 0.07782 | 0.17395 | 0.10529 | 0.18768 | 118.7164 | -2.916 | -2.8564 | 118.8629 | 118.7988 | 118.7897 | 0.082397 | 0.073242 | 118.6981 | -2.861 | -2.7832 | 118.8858 | 118.8995 | 118.8171 | 0.20142 | 0.11902 | 0.14648 | 0 | 0.18768 | 0.091553 | -0.05951 | 0.013733 | 118.6569 | 118.7119 | -2.8564 | -2.8748 | 118.7164 | 118.7897 | 118.6752 | 118.7439
3801.9688 | 121.6782 | -119.3481 | 2.1744 | 0.01358 | 0.013505 | -0.033295 | 0.036267 | -0.019335 | -0.029463 | -0.022605 | 0.0055542 | -0.06037 | 0.00052975 | 0.031479 | -0.020717 | -0.01245 | -0.013965 | -0.027466 | -0.054932 | 0.004578 | -0.004578 | 0.12817 | 0.045776 | 0.027466 | -0.009155 | 0.036621 | -0.022888 | -0.004578 | 0.073242 | 0 | 0.09613 | 119.3527 | -2.2293 | -2.179 | 119.4763 | 119.3756 | 119.3939 | 0.022888 | 0.041198 | 119.3253 | -2.1378 | -2.179 | 119.4214 | 119.4443 | 119.3481 | 0.11902 | 0.022888 | 0.1236 | -0.009156 | 0.09613 | 0.01831 | -0.05951 | 0.059509 | 119.2932 | 119.3848 | -2.1698 | -2.1973 | 119.3436 | 119.3436 | 119.3207 | 119.339
3803.7656 | 121.8063 | -118.9224 | 2.5406 | 0.028839 | 0.015855 | -0.033082 | 0.037549 | -0.014422 | -0.025404 | -0.020256 | 0.014709 | -0.060156 | 0.00031615 | 0.037247 | -0.013881 | -0.011595 | -0.015033 | -0.013733 | -0.050354 | 0.027466 | 0.064087 | 0.20142 | 0.059509 | 0.082397 | 0.082397 | 0.004578 | 0 | 0.091553 | 0.14648 | 0.086975 | 0.19226 | 118.9499 | -2.5909 | -2.4765 | 119.1238 | 119.0048 | 118.9819 | 0.054931 | 0.032043 | 118.9224 | -2.536 | -2.449 | 119.0689 | 119.1147 | 119.0094 | 0.19226 | 0.086975 | 0.17395 | 0.036621 | 0.14648 | 0.091553 | -0.07782 | 0.004578 | 118.8721 | 118.927 | -2.5131 | -2.5406 | 118.9865 | 119.014 | 118.9087 | 119.0048
3805.5625 | 121.7606 | -121.312 | 0.3891 | 0.036468 | 0.013505 | -0.033936 | 0.036267 | -0.015062 | -0.028181 | -0.018974 | 0.017761 | -0.059302 | -0.0022472 | 0.030198 | -0.018367 | -0.01245 | -0.017383 | -0.086975 | 0.013733 | -0.050354 | -0.073242 | 0.036621 | -0.018311 | -0.013733 | -0.068665 | 0.041199 | -0.059509 | -0.018311 | 0.041199 | -0.032043 | 0.09613 | 121.2616 | -0.37537 | -0.46234 | 121.3486 | 121.2982 | 121.2936 | 0.036621 | 0.032043 | 121.2524 | -0.3479 | -0.40741 | 121.3531 | 121.4081 | 121.2799 | 0.15564 | 0.027466 | 0.086975 | -0.022888 | 0.10071 | 0.041198 | 0.064087 | 0.10071 | 121.3257 | 121.3531 | -0.43945 | -0.44861 | 121.2387 | 121.2936 | 121.225 | 121.2433
3807.3594 | 121.8018 | -121.2891 | 0.3891 | 0.02121 | 0.015001 | -0.033509 | 0.036267 | -0.013994 | -0.028822 | -0.020897 | 0.011658 | -0.059088 | 0.0011708 | 0.033829 | -0.017726 | -0.012664 | -0.016742 | -0.027466 | -0.018311 | -0.022888 | -0.009155 | 0.09613 | 0.018311 | 0.013733 | 0.022888 | 0.045776 | -0.022888 | 0.045776 | 0.10986 | 0.032043 | 0.12817 | 121.2662 | -0.40741 | -0.39825 | 121.3852 | 121.3028 | 121.3074 | 0.036621 | 0.041199 | 121.2662 | -0.34332 | -0.34332 | 121.3989 | 121.4172 | 121.3211 | 0.15106 | 0.054931 | 0.11902 | 0.013733 | 0.13275 | 0.068664 | 0.004577 | 0.068664 | 121.2708 | 121.3348 | -0.41199 | -0.41199 | 121.2799 | 121.3348 | 121.2616 | 121.3119
3809.1719 | 121.8109 | -121.2936 | 0.39368 | 0.036468 | 0.015001 | -0.032654 | 0.035412 | -0.014635 | -0.027113 | -0.018333 | 0.008606 | -0.062506 | 0.00095715 | 0.027634 | -0.020717 | -0.012023 | -0.013537 | -0.036621 | -0.009155 | -0.041199 | -0.027466 | 0.086975 | 0.004578 | -0.004578 | -0.013733 | 0.027466 | -0.032043 | 0.032043 | 0.086975 | 0.018311 | 0.13733 | 121.2524 | -0.40283 | -0.42114 | 121.3806 | 121.2891 | 121.2982 | 0.036621 | 0.045777 | 121.2616 | -0.36621 | -0.36163 | 121.3806 | 121.431 | 121.312 | 0.16937 | 0.050354 | 0.12817 | 0.013733 | 0.11902 | 0.064086 | 0.032044 | 0.059509 | 121.2845 | 121.3211 | -0.43488 | -0.42572 | 121.2662 | 121.3257 | 121.257 | 121.2799
3810.9688 | 121.8796 | -121.2753 | 0.3479 | 0.028839 | 0.012437 | -0.029664 | 0.034985 | -0.017412 | -0.027754 | -0.019615 | 0.017761 | -0.062292 | 0.00074335 | 0.031479 | -0.017085 | -0.0092456 | -0.015033 | 0.004578 | -0.059509 | 0.013733 | 0.050354 | 0.19684 | 0.073242 | 0.064087 | 0.10071 | 0 | 0.009155 | 0.10071 | 0.16937 | 0.082397 | 0.18768 | 121.2891 | -0.40741 | -0.29755 | 121.4722 | 121.3394 | 121.3486 | 0.050354 | 0.059509 | 121.2845 | -0.3479 | -0.24719 | 121.4447 | 121.463 | 121.3577 | 0.17853 | 0.073242 | 0.18311 | 0.036621 | 0.16022 | 0.091553 | -0.073242 | -0.009155 | 121.2158 | 121.2753 | -0.33417 | -0.33874 | 121.3257 | 121.376 | 121.2799 | 121.376
3812.75 | 121.8887 | -121.2753 | 0.37079 | 0.028839 | 0.014787 | -0.032868 | 0.037549 | -0.012926 | -0.026686 | -0.020042 | 0.0055542 | -0.061865 | 0.00031615 | 0.032334 | -0.015377 | -0.008391 | -0.012042 | -0.054932 | -0.022888 | 0 | -0.009155 | 0.10071 | -0.013733 | 0.004578 | 0.032043 | 0.018311 | -0.018311 | 0.086975 | 0.14648 | 0.064087 | 0.19226 | 121.2753 | -0.39368 | -0.37994 | 121.376 | 121.2799 | 121.2616 | 0.004578 | -0.013733 | 121.257 | -0.35248 | -0.28381 | 121.4218 | 121.4676 | 121.3394 | 0.21057 | 0.082398 | 0.10071 | -0.009155 | 0.16479 | 0.10529 | -0.022888 | 0.036622 | 121.2524 | 121.2936 | -0.37079 | -0.3891 | 121.2662 | 121.3623 | 121.2204 | 121.3074
3814.5469 | 121.8613 | -121.2845 | 0.40741 | 0.02121 | 0.014146 | -0.033722 | 0.037335 | -0.018694 | -0.028181 | -0.021324 | 0.008606 | -0.062506 | -0.0011792 | 0.039384 | -0.016231 | -0.010527 | -0.014605 | -0.054932 | -0.059509 | 0.013733 | -0.018311 | 0.11444 | 0.013733 | 0.027466 | 0.022888 | 0.018311 | -0.022888 | 0.045776 | 0.12817 | 0.036621 | 0.14191 | 121.2982 | -0.46692 | -0.42572 | 121.3989 | 121.312 | 121.2982 | 0.013733 | 0 | 121.2616 | -0.3891 | -0.36163 | 121.4127 | 121.4264 | 121.3211 | 0.16479 | 0.059509 | 0.10071 | -0.032044 | 0.15106 | 0.068664 | -0.073242 | 0.041199 | 121.225 | 121.3028 | -0.39368 | -0.4303 | 121.2662 | 121.3303 | 121.2296 | 121.3074
3816.2812 | 121.9208 | -121.2936 | 0.37994 | 0.01358 | 0.014573 | -0.033722 | 0.034344 | -0.020617 | -0.027967 | -0.023033 | 0.008606 | -0.062079 | 0.00052975 | 0.033188 | -0.020503 | -0.011595 | -0.015246 | -0.032043 | -0.041199 | 0.004578 | 0.022888 | 0.19226 | 0.082397 | 0.10071 | 0.09613 | -0.004578 | -0.004578 | 0.10986 | 0.20142 | 0.11902 | 0.20599 | 121.2982 | -0.42114 | -0.35706 | 121.4859 | 121.3943 | 121.376 | 0.09613 | 0.077819 | 121.2891 | -0.38452 | -0.27008 | 121.4951 | 121.4996 | 121.4127 | 0.21057 | 0.1236 | 0.18768 | 0.01831 | 0.20599 | 0.11444 | -0.045777 | 0 | 121.2524 | 121.2891 | -0.37537 | -0.38452 | 121.3165 | 121.4035 | 121.2616 | 121.3898
3818.0156 | 121.875 | -121.2982 | 0.41657 | 0.028839 | 0.014787 | -0.033295 | 0.036053 | -0.016771 | -0.026899 | -0.020897 | 0.011658 | -0.060584 | -0.0026744 | 0.034897 | -0.016872 | -0.011382 | -0.012683 | -0.07782 | -0.041199 | 0 | -0.013733 | 0.11444 | 0.032043 | 0.041199 | -0.018311 | 0.009155 | -0.022888 | 0.032043 | 0.12817 | 0.032043 | 0.14648 | 121.2982 | -0.45776 | -0.4303 | 121.4127 | 121.3394 | 121.3303 | 0.041199 | 0.032043 | 121.2753 | -0.40741 | -0.38452 | 121.4264 | 121.4447 | 121.3303 | 0.16937 | 0.054931 | 0.11444 | -0.013733 | 0.15106 | 0.054931 | -0.041199 | 0.032043 | 121.257 | 121.3074 | -0.41657 | -0.43945 | 121.2845 | 121.3303 | 121.2204 | 121.2799
3819.75 | 121.9025 | -121.2708 | 0.40283 | 0.02121 | 0.014146 | -0.032227 | 0.036908 | -0.01314 | -0.02754 | -0.021751 | 0.011658 | -0.061011 | 0.00074335 | 0.041947 | -0.016231 | -0.009032 | -0.011828 | 0.004578 | -0.032043 | 0.013733 | 0.054932 | 0.18768 | 0.059509 | 0.068665 | 0.09613 | 0.013733 | -0.022888 | 0.082397 | 0.17853 | 0.086975 | 0.17853 | 121.2845 | -0.43488 | -0.3479 | 121.4584 | 121.3394 | 121.3303 | 0.054932 | 0.045776 | 121.2479 | -0.3891 | -0.32044 | 121.4493 | 121.4493 | 121.3577 | 0.20142 | 0.10986 | 0.17395 | 0.041199 | 0.20142 | 0.10528 | -0.045776 | 0.036621 | 121.2387 | 121.2845 | -0.3891 | -0.42572 | 121.3257 | 121.3531 | 121.2753 | 121.3669
3821.4844 | 121.7102 | -118.1259 | 3.5431 | 0.0059509 | 0.016282 | -0.033082 | 0.037335 | -0.015917 | -0.028181 | -0.022605 | 0.0025024 | -0.058875 | 0.00031615 | 0.031052 | -0.019649 | -0.010314 | -0.013751 | -0.054932 | -0.045776 | -0.018311 | -0.059509 | 0.041199 | -0.050354 | -0.041199 | -0.054932 | 0.059509 | -0.036621 | -0.018311 | 0.036621 | -0.045776 | 0.073242 | 118.1076 | -3.5889 | -3.6026 | 118.1671 | 118.0847 | 118.0756 | -0.022888 | -0.032043 | 118.0893 | -3.4836 | -3.5614 | 118.1625 | 118.1992 | 118.0801 | 0.10986 | -0.009155 | 0.05951 | -0.041198 | 0.073242 | 0.01831 | -0.027465 | 0.09613 | 118.0801 | 118.1854 | -3.5614 | -3.5797 | 118.0664 | 118.1076 | 118.071 | 118.071
3823.2812 | 121.788 | -118.0573 | 3.598 | 0.01358 | 0.013505 | -0.033295 | 0.034985 | -0.016558 | -0.029463 | -0.021537 | 0.0055542 | -0.062079 | -0.00075185 | 0.040024 | -0.018581 | -0.012023 | -0.013324 | -0.027466 | -0.054932 | 0 | 0.032043 | 0.15564 | 0.064087 | 0.054932 | 0.004578 | 0.041199 | 0 | 0.004578 | 0.13733 | 0.041199 | 0.12817 | 118.0573 | -3.653 | -3.566 | 118.2129 | 118.1122 | 118.1213 | 0.054932 | 0.064087 | 118.0573 | -3.5568 | -3.5934 | 118.1946 | 118.1854 | 118.0984 | 0.12817 | 0.041199 | 0.15564 | 0.032043 | 0.13733 | 0.004578 | -0.054932 | 0.041199 | 118.0023 | 118.0984 | -3.598 | -3.598 | 118.0893 | 118.0618 | 118.0298 | 118.0618
3825 | 121.7926 | -121.3989 | 0.28839 | 0.02121 | 0.015641 | -0.0318 | 0.037549 | -0.012926 | -0.028608 | -0.023033 | 0.008606 | -0.06037 | 0.00031615 | 0.025925 | -0.017726 | -0.01245 | -0.015033 | -0.032043 | -0.018311 | -0.027466 | -0.018311 | 0.10986 | 0.009155 | 0.009155 | 0.004578 | 0.032043 | -0.018311 | 0.009155 | 0.086975 | 0 | 0.10529 | 121.3715 | -0.3067 | -0.3067 | 121.5088 | 121.4081 | 121.4081 | 0.036621 | 0.036621 | 121.3806 | -0.25635 | -0.27924 | 121.4859 | 121.5042 | 121.3989 | 0.1236 | 0.018311 | 0.13733 | 0.009155 | 0.10529 | 0.027466 | 0.009155 | 0.050354 | 121.3806 | 121.431 | -0.31586 | -0.3067 | 121.3806 | 121.4081 | 121.3669 | 121.4035
3826.7812 | 121.7834 | -121.4401 | 0.31128 | 0.01358 | 0.015214 | -0.033295 | 0.036908 | -0.011217 | -0.026899 | -0.02346 | 0.008606 | -0.059943 | -0.00075185 | 0.02208 | -0.018581 | -0.01245 | -0.012896 | -0.059509 | -0.022888 | -0.018311 | -0.073242 | 0.054932 | -0.068665 | -0.045776 | -0.07782 | 0.036621 | -0.022888 | -0.027466 | 0.041199 | -0.059509 | 0.082397 | 121.4218 | -0.33417 | -0.38452 | 121.4951 | 121.3943 | 121.3715 | -0.027465 | -0.050354 | 121.4172 | -0.27466 | -0.33874 | 121.4813 | 121.5225 | 121.3806 | 0.10528 | -0.036621 | 0.073243 | -0.054931 | 0.064087 | -0.004578 | -0.004577 | 0.059509 | 121.4172 | 121.4767 | -0.32959 | -0.33417 | 121.3669 | 121.4127 | 121.3806 | 121.3623
3828.5781 | 121.8842 | -121.4035 | 0.25635 | 0.028839 | 0.015641 | -0.031586 | 0.033703 | -0.011644 | -0.02519 | -0.021751 | 0.011658 | -0.06272 | 0.00052975 | 0.038102 | -0.016445 | -0.0098864 | -0.010119 | -0.009155 | -0.054932 | 0.022888 | 0.050354 | 0.20599 | 0.059509 | 0.073242 | 0.091553 | 0 | 0 | 0.082397 | 0.16479 | 0.082397 | 0.1831 | 121.4264 | -0.31128 | -0.20599 | 121.6095 | 121.4767 | 121.463 | 0.050354 | 0.036621 | 121.4035 | -0.25635 | -0.17395 | 121.5683 | 121.5866 | 121.4859 | 0.1831 | 0.082397 | 0.18311 | 0.027466 | 0.16479 | 0.082397 | -0.07782 | 0 | 121.3486 | 121.4035 | -0.23346 | -0.25635 | 121.4539 | 121.4859 | 121.3943 | 121.4951
3830.375 | 121.843 | -121.4584 | 0.31128 | 0.028839 | 0.016496 | -0.031373 | 0.037335 | -0.016558 | -0.029463 | -0.02346 | 0.008606 | -0.058661 | 0.0013844 | 0.028061 | -0.020931 | -0.011595 | -0.013751 | -0.068665 | -0.004578 | -0.032043 | -0.064087 | 0.054932 | -0.022888 | -0.013733 | -0.068665 | 0.064087 | -0.045776 | -0.022888 | 0.07782 | -0.018311 | 0.10986 | 121.4264 | -0.31586 | -0.37537 | 121.5134 | 121.4447 | 121.4355 | 0.01831 | 0.009155 | 121.4127 | -0.24719 | -0.33417 | 121.5363 | 121.5683 | 121.4401 | 0.15564 | 0.027465 | 0.086975 | -0.032044 | 0.1236 | 0.022888 | 0.027465 | 0.10986 | 121.4539 | 121.5225 | -0.34332 | -0.35705 | 121.3943 | 121.4355 | 121.3898 | 121.3898
3832.1094 | 121.9391 | -121.4355 | 0.2655 | 0.02121 | 0.017778 | -0.033295 | 0.034772 | -0.015276 | -0.026045 | -0.022392 | 0.008606 | -0.060584 | -0.00182 | 0.034043 | -0.014949 | -0.010741 | -0.013751 | -0.013733 | -0.041199 | 0.004578 | 0.027466 | 0.16479 | 0.036621 | 0.054932 | 0.07782 | 0.013733 | -0.018311 | 0.10986 | 0.17395 | 0.091553 | 0.19684 | 121.4401 | -0.3067 | -0.23804 | 121.6003 | 121.4905 | 121.4722 | 0.050354 | 0.032043 | 121.4172 | -0.25177 | -0.15564 | 121.6095 | 121.6324 | 121.5271 | 0.21515 | 0.10986 | 0.16022 | 0.022888 | 0.19226 | 0.12817 | -0.045777 | 0.032044 | 121.3943 | 121.4493 | -0.26092 | -0.28381 | 121.463 | 121.5454 | 121.4218 | 121.5134
3833.8906 | 121.9528 | -121.4447 | 0.25635 | 0.02121 | 0.015001 | -0.034363 | 0.034772 | -0.018908 | -0.027327 | -0.023246 | 0.008606 | -0.061651 | 0.00031615 | 0.038743 | -0.018367 | -0.010741 | -0.013324 | -0.041199 | -0.045776 | 0 | 0.027466 | 0.18768 | 0.082397 | 0.091553 | 0.091553 | 0.013733 | -0.018311 | 0.09613 | 0.21057 | 0.13275 | 0.20142 | 121.4447 | -0.30212 | -0.22888 | 121.6324 | 121.5363 | 121.5271 | 0.091553 | 0.082397 | 121.4264 | -0.24262 | -0.16022 | 121.6553 | 121.6461 | 121.5775 | 0.21973 | 0.15106 | 0.18768 | 0.027466 | 0.22888 | 0.11444 | -0.045776 | 0.032044 | 121.3989 | 121.4584 | -0.25635 | -0.27466 | 121.4722 | 121.5408 | 121.4035 | 121.5363
3835.6406 | 121.9528 | -121.4493 | 0.25635 | 0.01358 | 0.013292 | -0.032441 | 0.03584 | -0.017412 | -0.028822 | -0.022392 | 0.0055542 | -0.061438 | 0.00031615 | 0.036179 | -0.015377 | -0.011168 | -0.014392 | 0.009155 | -0.054932 | 0.041199 | 0.054932 | 0.16022 | 0.045776 | 0.054932 | 0.10071 | 0.013733 | -0.004578 | 0.10986 | 0.16479 | 0.068665 | 0.19684 | 121.4905 | -0.31128 | -0.20142 | 121.6095 | 121.5042 | 121.4951 | 0.013733 | 0.004577 | 121.4447 | -0.24262 | -0.14649 | 121.6141 | 121.6461 | 121.5179 | 0.20142 | 0.073243 | 0.11902 | 0.013733 | 0.16937 | 0.11444 | -0.096131 | 0.018311 | 121.3943 | 121.463 | -0.21515 | -0.26093 | 121.5042 | 121.5591 | 121.4584 | 121.55
3837.4375 | 121.8887 | -121.4859 | 0.28839 | 0.0059509 | 0.013505 | -0.031586 | 0.037335 | -0.017199 | -0.028181 | -0.021751 | 0.011658 | -0.060584 | -0.0013928 | 0.03447 | -0.018581 | -0.011809 | -0.014605 | -0.041199 | -0.022888 | -0.022888 | -0.013733 | 0.1236 | 0.009155 | 0.013733 | 0.013733 | 0.045776 | -0.027466 | 0.027466 | 0.09613 | 0.027466 | 0.16022 | 121.463 | -0.31128 | -0.30212 | 121.6095 | 121.4996 | 121.4951 | 0.036621 | 0.032043 | 121.4584 | -0.24262 | -0.26093 | 121.582 | 121.6461 | 121.5134 | 0.18768 | 0.054932 | 0.14648 | 0.009155 | 0.1236 | 0.054932 | 0 | 0.073242 | 121.463 | 121.5317 | -0.31128 | -0.31586 | 121.4722 | 121.5134 | 121.4447 | 121.4996
3839.2344 | 121.9116 | -121.4722 | 0.25635 | 0.02121 | 0.014146 | -0.031586 | 0.035199 | -0.013353 | -0.029463 | -0.024101 | 0.011658 | -0.06037 | 0.0030934 | 0.034684 | -0.017726 | -0.010527 | -0.012469 | -0.036621 | -0.059509 | 0.009155 | 0.009155 | 0.16479 | 0.032043 | 0.050354 | 0.041199 | 0.022888 | -0.018311 | 0.045776 | 0.12817 | 0.054932 | 0.14648 | 121.4813 | -0.31586 | -0.24719 | 121.637 | 121.5225 | 121.5042 | 0.041199 | 0.022888 | 121.4539 | -0.23346 | -0.21057 | 121.6003 | 121.6187 | 121.5271 | 0.16479 | 0.073243 | 0.15564 | 0 | 0.14649 | 0.064087 | -0.068664 | 0.041199 | 121.4127 | 121.4951 | -0.24719 | -0.27466 | 121.4813 | 121.5179 | 121.4355 | 121.5134
3841.0312 | 121.9437 | -121.4401 | 0.28381 | 0.01358 | 0.013933 | -0.032013 | 0.03349 | -0.014208 | -0.028181 | -0.021965 | 0.0055542 | -0.06272 | -0.0013928 | 0.037675 | -0.019649 | -0.011595 | -0.014178 | -0.013733 | -0.050354 | 0.018311 | 0.068665 | 0.21515 | 0.10529 | 0.086975 | 0.091553 | 0.013733 | 0 | 0.073242 | 0.20142 | 0.11902 | 0.19226 | 121.4584 | -0.33417 | -0.21515 | 121.6553 | 121.5271 | 121.5454 | 0.068664 | 0.086975 | 121.4401 | -0.27008 | -0.21057 | 121.6415 | 121.6324 | 121.5591 | 0.19226 | 0.11902 | 0.19684 | 0.050354 | 0.20142 | 0.073242 | -0.068665 | 0.013733 | 121.3898 | 121.4539 | -0.2655 | -0.28381 | 121.5088 | 121.5134 | 121.4264 | 121.5317
3842.8125 | 121.9574 | -121.4035 | 0.31128 | 0.0059509 | 0.014573 | -0.031159 | 0.035199 | -0.013994 | -0.029676 | -0.020897 | 0.0055542 | -0.061438 | 0.00074335 | 0.042161 | -0.014949 | -0.009032 | -0.01546 | -0.004578 | -0.064087 | 0.018311 | 0.050354 | 0.1831 | 0.059509 | 0.059509 | 0.082397 | 0.013733 | -0.009155 | 0.11902 | 0.17395 | 0.091553 | 0.20599 | 121.4218 | -0.37537 | -0.26092 | 121.5866 | 121.463 | 121.463 | 0.041198 | 0.041198 | 121.3943 | -0.29755 | -0.19226 | 121.5775 | 121.6095 | 121.4951 | 0.21515 | 0.10071 | 0.16479 | 0.032043 | 0.1831 | 0.12817 | -0.082398 | 0.022888 | 121.3394 | 121.4172 | -0.29297 | -0.32043 | 121.4539 | 121.5225 | 121.3989 | 121.4859
3844.5469 | 121.9299 | -121.4127 | 0.32501 | 0.02121 | 0.012864 | -0.032013 | 0.034772 | -0.015917 | -0.027754 | -0.022605 | 0.008606 | -0.060797 | -0.0011792 | 0.040024 | -0.01559 | -0.0101 | -0.011187 | -0.004578 | -0.059509 | 0.004578 | 0.059509 | 0.19684 | 0.068665 | 0.064087 | 0.091553 | 0.009155 | 0 | 0.09613 | 0.15564 | 0.086975 | 0.1831 | 121.4172 | -0.38452 | -0.2655 | 121.6095 | 121.4767 | 121.4813 | 0.059509 | 0.064087 | 121.4127 | -0.31586 | -0.22888 | 121.5683 | 121.5958 | 121.4996 | 0.1831 | 0.086975 | 0.19226 | 0.054931 | 0.15564 | 0.09613 | -0.064087 | 0.009155 | 121.3531 | 121.4218 | -0.32043 | -0.32501 | 121.4722 | 121.5088 | 121.4081 | 121.5042
3846.3438 | 121.8521 | -121.4447 | 0.37994 | 0.02121 | 0.015214 | -0.033295 | 0.036267 | -0.012499 | -0.028822 | -0.021965 | 0.0055542 | -0.058875 | 0.0022388 | 0.03682 | -0.020076 | -0.010314 | -0.015246 | -0.091553 | -0.018311 | -0.036621 | -0.086975 | 0 | -0.07782 | -0.045776 | -0.086975 | 0.041199 | -0.032043 | -0.032043 | 0.018311 | -0.059509 | 0.082397 | 121.4081 | -0.39826 | -0.46692 | 121.4447 | 121.3989 | 121.3669 | -0.009155 | -0.041199 | 121.4127 | -0.33875 | -0.41199 | 121.463 | 121.5271 | 121.3852 | 0.11444 | -0.027466 | 0.036621 | -0.050354 | 0.050354 | 0 | 0.01831 | 0.073242 | 121.4264 | 121.4859 | -0.41657 | -0.41199 | 121.3577 | 121.4127 | 121.3531 | 121.3577
3848.1406 | 121.9803 | -121.3989 | 0.33417 | 0.01358 | 0.013292 | -0.031586 | 0.032849 | -0.017199 | -0.030958 | -0.021965 | -0.00054937 | -0.061224 | -0.00053825 | 0.038956 | -0.020503 | -0.013091 | -0.011615 | -0.027466 | -0.059509 | 0 | 0.036621 | 0.1831 | 0.086975 | 0.073242 | 0.07782 | 0.018311 | 0.004578 | 0.09613 | 0.19684 | 0.11902 | 0.21057 | 121.3989 | -0.39368 | -0.29755 | 121.582 | 121.4722 | 121.4859 | 0.073242 | 0.086975 | 121.4035 | -0.31586 | -0.23804 | 121.5958 | 121.6095 | 121.5179 | 0.20599 | 0.11444 | 0.1831 | 0.036621 | 0.19226 | 0.091552 | -0.059509 | 0.013733 | 121.3394 | 121.4172 | -0.33417 | -0.32959 | 121.4355 | 121.4951 | 121.3715 | 121.4767
3849.9375 | 121.9528 | -121.4218 | 0.35706 | 0.028839 | 0.015001 | -0.031586 | 0.037549 | -0.013781 | -0.029036 | -0.025596 | 0.011658 | -0.061438 | 0.00031615 | 0.036179 | -0.017513 | -0.012236 | -0.014392 | -0.036621 | -0.045776 | -0.004578 | 0.013733 | 0.15564 | 0.032043 | 0.041199 | 0.032043 | 0.009155 | -0.004578 | 0.036621 | 0.10986 | 0.050354 | 0.15106 | 121.4172 | -0.40283 | -0.34332 | 121.5775 | 121.463 | 121.4539 | 0.045777 | 0.036621 | 121.4172 | -0.3479 | -0.32043 | 121.5317 | 121.5729 | 121.4722 | 0.15564 | 0.054932 | 0.16022 | 0.018311 | 0.11444 | 0.041199 | -0.041198 | 0.013733 | 121.376 | 121.431 | -0.36163 | -0.36163 | 121.4355 | 121.4584 | 121.3852 | 121.4539
3851.6719 | 121.8613 | -121.4493 | 0.40741 | 0.01358 | 0.013933 | -0.035218 | 0.034344 | -0.019549 | -0.02989 | -0.02346 | 0.011658 | -0.059729 | 0.00010255 | 0.03212 | -0.020931 | -0.010741 | -0.01076 | -0.10529 | -0.032043 | -0.027466 | -0.082397 | 0.068665 | -0.018311 | -0.018311 | -0.082397 | 0.054932 | -0.032043 | -0.045776 | 0.027466 | -0.036621 | 0.086975 | 121.4218 | -0.43945 | -0.48981 | 121.5179 | 121.431 | 121.431 | 0.009155 | 0.009155 | 121.4172 | -0.35248 | -0.45319 | 121.4767 | 121.5363 | 121.4127 | 0.11902 | -0.004578 | 0.096131 | -0.054931 | 0.059509 | -0.013733 | -0.004577 | 0.086975 | 121.4172 | 121.5042 | -0.43488 | -0.43945 | 121.3669 | 121.4035 | 121.344 | 121.3669
3853.4688 | 121.9757 | -121.3943 | 0.37079 | 0.01358 | 0.011369 | -0.031586 | 0.03648 | -0.015062 | -0.029463 | -0.024101 | 0.008606 | -0.061865 | 0.0011708 | 0.030411 | -0.020931 | -0.011595 | -0.014392 | -0.050354 | -0.050354 | 0.004578 | 0 | 0.14648 | 0.045776 | 0.054932 | 0.018311 | -0.004578 | -0.004578 | 0.059509 | 0.16479 | 0.10071 | 0.17853 | 121.3989 | -0.42114 | -0.37079 | 121.5408 | 121.4493 | 121.4401 | 0.050354 | 0.041198 | 121.3898 | -0.37537 | -0.31128 | 121.5591 | 121.5729 | 121.4951 | 0.18311 | 0.10529 | 0.14191 | -0.004578 | 0.16937 | 0.064087 | -0.054932 | 0 | 121.344 | 121.3898 | -0.36621 | -0.37537 | 121.3943 | 121.4539 | 121.344 | 121.4127
3855.2031 | 121.8613 | -121.4355 | 0.3891 | 0.0059509 | 0.016496 | -0.032441 | 0.036694 | -0.0099357 | -0.029676 | -0.021537 | 0.008606 | -0.060156 | 0.0013844 | 0.03447 | -0.016231 | -0.010314 | -0.012683 | -0.068665 | -0.022888 | -0.032043 | -0.082397 | 0.032043 | -0.068665 | -0.050354 | -0.10071 | 0.027466 | -0.036621 | -0.050354 | 0.013733 | -0.059509 | 0.082397 | 121.4035 | -0.41199 | -0.4715 | 121.4676 | 121.3852 | 121.3669 | -0.018311 | -0.036622 | 121.3989 | -0.36163 | -0.43945 | 121.4493 | 121.5179 | 121.376 | 0.11902 | -0.022888 | 0.064086 | -0.050354 | 0.050354 | -0.013733 | 0.009155 | 0.064087 | 121.4127 | 121.463 | -0.42114 | -0.42572 | 121.3531 | 121.3852 | 121.3669 | 121.3348
3857 | 121.9208 | -121.4447 | 0.3891 | 0.02121 | 0.015641 | -0.033509 | 0.03584 | -0.01314 | -0.029249 | -0.024101 | 0.011658 | -0.060584 | 0.00010255 | 0.039597 | -0.019008 | -0.011595 | -0.016101 | -0.045776 | -0.022888 | -0.027466 | -0.013733 | 0.086975 | 0.004578 | 0.009155 | 0 | 0.045776 | -0.036621 | 0.009155 | 0.10071 | 0.018311 | 0.13733 | 121.4172 | -0.41199 | -0.40283 | 121.5317 | 121.4539 | 121.4493 | 0.036621 | 0.032044 | 121.4081 | -0.34332 | -0.37994 | 121.5454 | 121.582 | 121.463 | 0.17395 | 0.054932 | 0.11444 | 0.013733 | 0.13733 | 0.045776 | 0.004578 | 0.082397 | 121.4218 | 121.4905 | -0.41656 | -0.42572 | 121.431 | 121.4539 | 121.3989 | 121.4447
3858.7969 | 121.9345 | -121.4447 | 0.37079 | 0.02121 | 0.013933 | -0.0318 | 0.03349 | -0.017412 | -0.027754 | -0.019615 | -0.00054937 | -0.061438 | 0.0011708 | 0.032975 | -0.019435 | -0.011809 | -0.013965 | -0.018311 | -0.064087 | 0.022888 | 0.009155 | 0.17395 | 0.054932 | 0.068665 | 0.013733 | 0.022888 | -0.013733 | 0.022888 | 0.13275 | 0.045776 | 0.13275 | 121.4676 | -0.43488 | -0.36163 | 121.6187 | 121.5134 | 121.4996 | 0.045777 | 0.032044 | 121.431 | -0.3479 | -0.3479 | 121.5775 | 121.5775 | 121.4905 | 0.14648 | 0.059509 | 0.15106 | -0.013733 | 0.14648 | 0.036621 | -0.086975 | 0.036621 | 121.3806 | 121.4676 | -0.3479 | -0.38452 | 121.4539 | 121.4676 | 121.4264 | 121.4584
3860.5625 | 121.9574 | -121.4401 | 0.39825 | 0.02121 | 0.013078 | -0.033295 | 0.035412 | -0.018908 | -0.027754 | -0.021324 | 0.011658 | -0.059729 | 0.00010255 | 0.026993 | -0.016872 | -0.010741 | -0.013537 | -0.064087 | -0.054932 | -0.004578 | -0.013733 | 0.11902 | 0.018311 | 0.022888 | -0.018311 | 0.009155 | -0.032043 | 0.032043 | 0.11902 | 0.050354 | 0.14191 | 121.4355 | -0.45319 | -0.41199 | 121.5591 | 121.463 | 121.4584 | 0.027466 | 0.022889 | 121.4081 | -0.3891 | -0.36621 | 121.5591 | 121.582 | 121.4905 | 0.17395 | 0.082397 | 0.1236 | -0.009155 | 0.15106 | 0.064086 | -0.050354 | 0.041198 | 121.3852 | 121.4493 | -0.40283 | -0.4303 | 121.4264 | 121.4722 | 121.376 | 121.4218
3862.3594 | 121.9208 | -121.4218 | 0.39825 | 0.028839 | 0.015214 | -0.034577 | 0.03648 | -0.017199 | -0.030745 | -0.022178 | 0.008606 | -0.059302 | -0.0011792 | 0.039597 | -0.019649 | -0.011168 | -0.015887 | -0.073242 | -0.018311 | -0.036621 | -0.073242 | 0.059509 | 0.004578 | -0.022888 | -0.059509 | 0.050354 | -0.054932 | 0 | 0.091553 | 0.009155 | 0.11902 | 121.3852 | -0.41657 | -0.4715 | 121.4813 | 121.3989 | 121.4264 | 0.013733 | 0.041199 | 121.3669 | -0.3479 | -0.39825 | 121.5134 | 121.5408 | 121.431 | 0.17395 | 0.064087 | 0.09613 | -0.036621 | 0.14649 | 0.054932 | 0.01831 | 0.10529 | 121.4035 | 121.4722 | -0.43488 | -0.45319 | 121.3486 | 121.4218 | 121.3486 | 121.3623
3864.0781 | 121.9986 | -121.4081 | 0.38452 | 0.02121 | 0.013933 | -0.032868 | 0.037762 | -0.015917 | -0.026686 | -0.020042 | 0.011658 | -0.059088 | -0.00011105 | 0.041306 | -0.014095 | -0.0092456 | -0.014605 | -0.009155 | -0.064087 | 0.032043 | 0.032043 | 0.19684 | 0.059509 | 0.068665 | 0.10529 | 0.018311 | -0.013733 | 0.091553 | 0.16479 | 0.082397 | 0.18768 | 121.4401 | -0.44861 | -0.35248 | 121.6049 | 121.4767 | 121.4676 | 0.036622 | 0.027466 | 121.3943 | -0.36621 | -0.29297 | 121.5729 | 121.5958 | 121.4905 | 0.20142 | 0.09613 | 0.1648 | 0 | 0.17853 | 0.10529 | -0.09613 | 0.032044 | 121.344 | 121.4264 | -0.35248 | -0.39825 | 121.4401 | 121.4996 | 121.3989 | 121.5134
3865.8594 | 121.9345 | -121.4539 | 0.40283 | 0.028839 | 0.013719 | -0.034363 | 0.03648 | -0.01848 | -0.029249 | -0.02346 | 0.011658 | -0.05802 | 0.0035206 | 0.031479 | -0.018794 | -0.012664 | -0.016955 | -0.07782 | -0.018311 | -0.027466 | -0.07782 | 0.054932 | -0.009155 | -0.013733 | -0.064087 | 0.041199 | -0.050354 | -0.004578 | 0.082397 | -0.018311 | 0.10529 | 121.4264 | -0.42114 | -0.48065 | 121.5088 | 121.4401 | 121.4447 | 0.013733 | 0.018311 | 121.4035 | -0.36163 | -0.40741 | 121.5363 | 121.5591 | 121.4355 | 0.15564 | 0.032043 | 0.082398 | -0.050354 | 0.13275 | 0.045776 | 0.009155 | 0.091553 | 121.4355 | 121.4951 | -0.4303 | -0.45319 | 121.376 | 121.4493 | 121.376 | 121.3898
3867.6562 | 121.9894 | -121.431 | 0.37994 | 0.036468 | 0.013078 | -0.030945 | 0.036053 | -0.017199 | -0.028822 | -0.021965 | 0.011658 | -0.06272 | -0.00053825 | 0.040024 | -0.016017 | -0.011595 | -0.012042 | -0.018311 | -0.050354 | 0.022888 | 0.041199 | 0.1831 | 0.064087 | 0.068665 | 0.073242 | 0.009155 | -0.013733 | 0.068665 | 0.13733 | 0.064087 | 0.17853 | 121.4539 | -0.4303 | -0.33875 | 121.6141 | 121.4996 | 121.4951 | 0.045777 | 0.041199 | 121.4172 | -0.37079 | -0.31128 | 121.5683 | 121.6095 | 121.4951 | 0.19226 | 0.07782 | 0.16022 | 0.018311 | 0.15106 | 0.082398 | -0.073242 | 0.022888 | 121.3806 | 121.4401 | -0.35706 | -0.39368 | 121.4722 | 121.4996 | 121.4127 | 121.5042
3869.3906 | 121.9574 | -121.4264 | 0.39825 | 0.028839 | 0.014573 | -0.033082 | 0.037335 | -0.017626 | -0.028395 | -0.022392 | 0.008606 | -0.059515 | 0.00074335 | 0.023148 | -0.016017 | -0.011168 | -0.014392 | -0.009155 | -0.027466 | -0.022888 | -0.004578 | 0.10986 | 0.018311 | 0 | 0 | 0.045776 | -0.022888 | 0.018311 | 0.11444 | 0.004578 | 0.15106 | 121.4035 | -0.42572 | -0.40283 | 121.5363 | 121.4264 | 121.4447 | 0.022888 | 0.041199 | 121.4035 | -0.35248 | -0.37994 | 121.5408 | 121.5775 | 121.431 | 0.17395 | 0.027466 | 0.13275 | 0.01831 | 0.13733 | 0.041199 | -0.004578 | 0.068664 | 121.3989 | 121.4722 | -0.42114 | -0.42114 | 121.4218 | 121.4447 | 121.4172 | 121.4264
3871.1875 | 121.9666 | -121.431 | 0.36621 | 0.01358 | 0.01436 | -0.031373 | 0.037976 | -0.015062 | -0.027113 | -0.021537 | 0.0055542 | -0.059943 | -0.00011105 | 0.037675 | -0.014522 | -0.0098864 | -0.014819 | -0.073242 | 0 | -0.018311 | -0.059509 | 0.045776 | -0.054932 | -0.027466 | -0.018311 | 0.036621 | -0.018311 | 0.036621 | 0.10529 | 0.009155 | 0.14648 | 121.4127 | -0.36621 | -0.42572 | 121.4767 | 121.4035 | 121.376 | -0.009155 | -0.036621 | 121.4127 | -0.32959 | -0.32959 | 121.5363 | 121.5775 | 121.4401 | 0.16479 | 0.027466 | 0.064087 | -0.041198 | 0.1236 | 0.054932 | 0.018311 | 0.054932 | 121.431 | 121.4676 | -0.38452 | -0.38452 | 121.3715 | 121.4676 | 121.3577 | 121.4127
3872.9844 | 122.0306 | -121.4127 | 0.37079 | 0.028839 | 0.016282 | -0.032441 | 0.036694 | -0.016558 | -0.028395 | -0.022819 | 0.011658 | -0.060797 | -0.0011792 | 0.035538 | -0.015377 | -0.009032 | -0.01546 | -0.013733 | -0.059509 | 0.009155 | 0.059509 | 0.19684 | 0.068665 | 0.068665 | 0.091553 | 0.004578 | 0.009155 | 0.082397 | 0.16937 | 0.091553 | 0.19226 | 121.4218 | -0.4303 | -0.31128 | 121.6095 | 121.4813 | 121.4813 | 0.05951 | 0.05951 | 121.4218 | -0.36621 | -0.28839 | 121.582 | 121.6049 | 121.5042 | 0.18311 | 0.082398 | 0.18768 | 0.050354 | 0.16022 | 0.073242 | -0.068664 | -0.004577 | 121.3531 | 121.4172 | -0.36163 | -0.36163 | 121.4722 | 121.4951 | 121.3989 | 121.5042
3874.7031 | 122.0535 | -121.431 | 0.36163 | -0.0016786 | 0.012651 | -0.035004 | 0.035626 | -0.015917 | -0.029463 | -0.02111 | 0.008606 | -0.061865 | -0.00032465 | 0.03682 | -0.018154 | -0.010314 | -0.011828 | -0.009155 | -0.068665 | 0.018311 | 0.050354 | 0.23346 | 0.10986 | 0.091553 | 0.09613 | 0.013733 | -0.004578 | 0.10071 | 0.21057 | 0.11902 | 0.18768 | 121.4493 | -0.4303 | -0.31128 | 121.6644 | 121.5225 | 121.5408 | 0.073242 | 0.091552 | 121.4264 | -0.3479 | -0.26092 | 121.6415 | 121.6187 | 121.55 | 0.19226 | 0.1236 | 0.21515 | 0.032043 | 0.21515 | 0.10529 | -0.086976 | 0.018311 | 121.3623 | 121.4447 | -0.34332 | -0.36621 | 121.4813 | 121.5317 | 121.4218 | 121.5271
3876.5 | 121.9208 | -121.4813 | 0.39368 | 0.02121 | 0.015428 | -0.032654 | 0.037762 | -0.012285 | -0.02754 | -0.024955 | 0.0025024 | -0.060584 | 0.00095715 | 0.02913 | -0.01559 | -0.010741 | -0.011828 | -0.073242 | 0 | -0.032043 | -0.086975 | 0.009155 | -0.086975 | -0.064087 | -0.07782 | 0.050354 | -0.027466 | -0.032043 | 0.022888 | -0.050354 | 0.10071 | 121.4493 | -0.39368 | -0.48065 | 121.4905 | 121.4172 | 121.3943 | -0.032044 | -0.054932 | 121.4539 | -0.34332 | -0.42572 | 121.5042 | 121.582 | 121.431 | 0.12817 | -0.022888 | 0.041198 | -0.054932 | 0.050354 | -0.004577 | 0.032043 | 0.07782 | 121.4813 | 121.5317 | -0.42572 | -0.42114 | 121.3943 | 121.4493 | 121.4081 | 121.4035
3878.2969 | 122.0352 | -121.4172 | 0.37537 | 0.028839 | 0.012651 | -0.030732 | 0.036053 | -0.011217 | -0.027754 | -0.020469 | 0.008606 | -0.061438 | 0.00010255 | 0.036393 | -0.016445 | -0.0094592 | -0.01311 | 0.009155 | -0.064087 | 0.004578 | 0.054932 | 0.19226 | 0.059509 | 0.07782 | 0.091553 | 0.009155 | -0.018311 | 0.10071 | 0.17395 | 0.091553 | 0.19684 | 121.4218 | -0.43945 | -0.32043 | 121.6095 | 121.4951 | 121.4767 | 0.073242 | 0.054931 | 121.3989 | -0.36621 | -0.27466 | 121.5912 | 121.6141 | 121.5088 | 0.21515 | 0.10986 | 0.18768 | 0.050354 | 0.19226 | 0.11902 | -0.068665 | 0.027466 | 121.3531 | 121.4264 | -0.37079 | -0.39368 | 121.4722 | 121.5179 | 121.4264 | 121.5088
3880.0156 | 122.0444 | -121.4355 | 0.3891 | 0.01358 | 0.013292 | -0.0318 | 0.037335 | -0.013567 | -0.026472 | -0.024742 | 0.0055542 | -0.062506 | 0.00010255 | 0.033829 | -0.017513 | -0.011168 | -0.013537 | -0.041199 | -0.027466 | -0.004578 | 0.004578 | 0.1236 | 0.018311 | 0.032043 | 0.036621 | 0.013733 | -0.018311 | 0.09613 | 0.16479 | 0.068665 | 0.17853 | 121.431 | -0.41656 | -0.38452 | 121.5591 | 121.4676 | 121.4539 | 0.036621 | 0.022889 | 121.4172 | -0.37537 | -0.29297 | 121.6003 | 121.6141 | 121.5042 | 0.19684 | 0.086976 | 0.12817 | 0.009156 | 0.18311 | 0.11444 | -0.022888 | 0.032044 | 121.4081 | 121.4493 | -0.39368 | -0.40741 | 121.4401 | 121.5317 | 121.3943 | 121.4722
3881.7969 | 121.9299 | -121.4584 | 0.41199 | 0.02121 | 0.013933 | -0.0318 | 0.036267 | -0.018908 | -0.030531 | -0.022819 | 0.0025024 | -0.059729 | -0.00032465 | 0.041092 | -0.018154 | -0.011382 | -0.012469 | -0.10071 | -0.004578 | -0.027466 | -0.10529 | -0.004578 | -0.082397 | -0.07782 | -0.10071 | 0.036621 | -0.045776 | -0.045776 | 0.032043 | -0.059509 | 0.09613 | 121.431 | -0.41657 | -0.51727 | 121.4539 | 121.3806 | 121.376 | -0.050354 | -0.054931 | 121.4127 | -0.37537 | -0.45776 | 121.4905 | 121.5546 | 121.3989 | 0.14191 | -0.013733 | 0.022888 | -0.07782 | 0.077819 | 0 | 0.022888 | 0.082397 | 121.4539 | 121.4951 | -0.43945 | -0.45776 | 121.3531 | 121.4127 | 121.3577 | 121.3577
3883.5938 | 121.8567 | -119.6182 | 2.2202 | 0.01358 | 0.016282 | -0.033082 | 0.036267 | -0.01314 | -0.026686 | -0.025169 | 0.0055542 | -0.059943 | 0.0022388 | 0.035325 | -0.018367 | -0.010527 | -0.012683 | -0.082397 | -0.036621 | -0.032043 | -0.086975 | 0.022888 | -0.091553 | -0.050354 | -0.086975 | 0.036621 | -0.032043 | -0.036621 | 0.018311 | -0.054932 | 0.091553 | 119.5862 | -2.2568 | -2.3071 | 119.6411 | 119.5679 | 119.5267 | -0.018311 | -0.05951 | 119.5862 | -2.1835 | -2.2568 | 119.6365 | 119.7098 | 119.5633 | 0.1236 | -0.022889 | 0.054931 | -0.054932 | 0.050354 | -0.004578 | -0.004578 | 0.068664 | 119.5816 | 119.6548 | -2.2522 | -2.2522 | 119.5312 | 119.5816 | 119.5358 | 119.5312
3885.4062 | 121.9894 | -116.2079 | 5.5527 | 0.01358 | 0.013505 | -0.032654 | 0.034344 | -0.019762 | -0.027754 | -0.021751 | 0.0025024 | -0.061865 | 0.00010255 | 0.029984 | -0.022853 | -0.012023 | -0.01076 | -0.10529 | 0 | -0.018311 | -0.082397 | 0.041199 | -0.032043 | -0.018311 | -0.086975 | 0.054932 | -0.073242 | -0.027466 | 0.032043 | -0.032043 | 0.07782 | 116.1896 | -5.5527 | -5.6351 | 116.2491 | 116.1896 | 116.1758 | 0 | -0.013732 | 116.1346 | -5.4977 | -5.5801 | 116.2399 | 116.2857 | 116.1758 | 0.15106 | 0.041199 | 0.05951 | -0.064086 | 0.10529 | 0.045776 | 0.018311 | 0.12817 | 116.2079 | 116.2628 | -5.571 | -5.6259 | 116.1255 | 116.1804 | 116.1026 | 116.1209
3887.1406 | 122.0261 | -116.2811 | 5.5115 | 0.01358 | 0.015428 | -0.033936 | 0.03584 | -0.012926 | -0.026686 | -0.020683 | 0.0055542 | -0.062079 | 0.00074335 | 0.037034 | -0.017513 | -0.011595 | -0.01311 | -0.032043 | -0.013733 | -0.009155 | -0.032043 | 0.07782 | 0.013733 | 0 | -0.009155 | 0.009155 | -0.036621 | 0.022888 | 0.10071 | 0.018311 | 0.1236 | 116.272 | -5.5252 | -5.5435 | 116.3589 | 116.2811 | 116.2949 | 0.009155 | 0.022888 | 116.2445 | -5.5023 | -5.4886 | 116.3818 | 116.4047 | 116.2994 | 0.16022 | 0.054932 | 0.086975 | -0.022888 | 0.13733 | 0.059509 | -0.004578 | 0.045776 | 116.2674 | 116.2903 | -5.5206 | -5.5481 | 116.2491 | 116.304 | 116.2491 | 116.272
3888.9219 | 122.0078 | -118.4463 | 3.3966 | 0.0059509 | 0.013505 | -0.033509 | 0.03584 | -0.011217 | -0.028395 | -0.022819 | 0.0025024 | -0.059515 | 0.001598 | 0.032761 | -0.021999 | -0.01245 | -0.012042 | -0.10071 | -0.018311 | -0.022888 | -0.082397 | 0.054932 | -0.009155 | -0.018311 | -0.073242 | 0.045776 | -0.045776 | -0.027466 | 0.041199 | -0.032043 | 0.073242 | 118.4235 | -3.4149 | -3.479 | 118.5013 | 118.428 | 118.4372 | 0.004577 | 0.013733 | 118.4006 | -3.3508 | -3.4241 | 118.4875 | 118.5196 | 118.4143 | 0.11902 | 0.013733 | 0.07782 | -0.059509 | 0.086975 | 0.01831 | 0.004577 | 0.091552 | 118.428 | 118.4921 | -3.4195 | -3.4424 | 118.364 | 118.4189 | 118.3456 | 118.3731
3890.7188 | 121.9574 | -118.5928 | 3.2867 | 0.0059509 | 0.015214 | -0.032868 | 0.036908 | -0.01314 | -0.029036 | -0.022178 | 0.0025024 | -0.060797 | 0.00010255 | 0.030839 | -0.018794 | -0.010527 | -0.012256 | -0.064087 | -0.041199 | -0.018311 | -0.082397 | 0.022888 | -0.068665 | -0.054932 | -0.10071 | 0.032043 | -0.036621 | -0.009155 | 0.018311 | -0.068665 | 0.07782 | 118.5745 | -3.3279 | -3.3691 | 118.6157 | 118.5379 | 118.5242 | -0.036621 | -0.050354 | 118.5562 | -3.2547 | -3.2959 | 118.6111 | 118.6707 | 118.5242 | 0.11444 | -0.032044 | 0.041199 | -0.064086 | 0.054932 | 0.027466 | -0.022888 | 0.068664 | 118.5516 | 118.6249 | -3.3051 | -3.3234 | 118.5104 | 118.5837 | 118.5287 | 118.4921
3892.5156 | 122.0993 | -119.5679 | 2.2385 | 0.028839 | 0.013505 | -0.030732 | 0.03648 | -0.01314 | -0.029036 | -0.024528 | 0.011658 | -0.061651 | -0.00011105 | 0.035111 | -0.014522 | -0.0081774 | -0.012683 | -0.004578 | -0.064087 | 0.018311 | 0.041199 | 0.19684 | 0.068665 | 0.073242 | 0.10986 | -0.004578 | -0.004578 | 0.11444 | 0.17853 | 0.073242 | 0.18768 | 119.5862 | -2.3026 | -2.1973 | 119.7647 | 119.6411 | 119.6365 | 0.054931 | 0.050354 | 119.5633 | -2.243 | -2.124 | 119.7464 | 119.7556 | 119.6411 | 0.19226 | 0.07782 | 0.17853 | 0.022888 | 0.18311 | 0.11902 | -0.082398 | 0 | 119.5038 | 119.5633 | -2.2202 | -2.243 | 119.6091 | 119.6823 | 119.5633 | 119.6777
3894.2344 | 122.1313 | -119.5541 | 2.2751 | 0.0059509 | 0.01436 | -0.033295 | 0.035412 | -0.0077993 | -0.029036 | -0.022178 | 0.008606 | -0.061651 | 0.0011708 | 0.036606 | -0.016445 | -0.008391 | -0.012256 | 0.013733 | -0.068665 | 0.027466 | 0.050354 | 0.19226 | 0.050354 | 0.073242 | 0.10986 | 0.009155 | -0.004578 | 0.11444 | 0.1831 | 0.086975 | 0.20142 | 119.5816 | -2.3438 | -2.2247 | 119.7464 | 119.6274 | 119.6045 | 0.045776 | 0.022888 | 119.5496 | -2.2659 | -2.1606 | 119.7372 | 119.7556 | 119.6411 | 0.20599 | 0.091553 | 0.16479 | 0.022888 | 0.18768 | 0.11902 | -0.096131 | 0.013733 | 119.4855 | 119.5633 | -2.2476 | -2.2797 | 119.6045 | 119.6686 | 119.5679 | 119.664
3896.0312 | 122.081 | -119.664 | 2.1606 | 0.036468 | 0.01436 | -0.030518 | 0.036694 | -0.013781 | -0.027327 | -0.020897 | 0.014709 | -0.061438 | 0.0013844 | 0.038529 | -0.01559 | -0.010741 | -0.015033 | 0.009155 | -0.068665 | 0.027466 | 0.059509 | 0.20599 | 0.082397 | 0.086975 | 0.11444 | 0.004578 | -0.004578 | 0.11902 | 0.15106 | 0.086975 | 0.21057 | 119.6915 | -2.2293 | -2.1011 | 119.87 | 119.751 | 119.7464 | 0.059509 | 0.054931 | 119.6594 | -2.1561 | -2.0416 | 119.8151 | 119.8746 | 119.751 | 0.21515 | 0.091553 | 0.17853 | 0.032043 | 0.15564 | 0.1236 | -0.096131 | 0.009156 | 119.5953 | 119.6686 | -2.1332 | -2.1652 | 119.7235 | 119.783 | 119.6732 | 119.7784
3897.7656 | 122.0352 | -119.7784 | 2.1057 | 0.028839 | 0.014573 | -0.034577 | 0.039044 | -0.014635 | -0.026899 | -0.020683 | 0.0055542 | -0.058234 | -0.0013928 | 0.027848 | -0.019008 | -0.011809 | -0.013324 | -0.027466 | -0.032043 | -0.018311 | -0.022888 | 0.11444 | 0.004578 | 0.013733 | 0.013733 | 0.032043 | -0.027466 | 0.050354 | 0.10986 | 0.018311 | 0.13275 | 119.7601 | -2.1378 | -2.1286 | 119.8929 | 119.7922 | 119.783 | 0.032044 | 0.022889 | 119.751 | -2.0737 | -2.0554 | 119.8883 | 119.9112 | 119.7968 | 0.16022 | 0.045777 | 0.13275 | -0.004577 | 0.13733 | 0.07782 | -0.013732 | 0.059509 | 119.7464 | 119.8105 | -2.124 | -2.1332 | 119.7556 | 119.8288 | 119.751 | 119.7922
3899.5625 | 122.0718 | -119.7006 | 2.179 | 0.01358 | 0.012224 | -0.033295 | 0.03584 | -0.018267 | -0.027754 | -0.025596 | 0.0055542 | -0.061651 | -0.0024608 | 0.038529 | -0.020503 | -0.011382 | -0.012042 | -0.059509 | -0.050354 | -0.013733 | -0.013733 | 0.11444 | 0.027466 | 0.050354 | 0 | 0.018311 | -0.027466 | 0.059509 | 0.13275 | 0.064087 | 0.16022 | 119.6869 | -2.2293 | -2.1927 | 119.8151 | 119.751 | 119.7281 | 0.064087 | 0.041199 | 119.6732 | -2.1606 | -2.1194 | 119.8334 | 119.8608 | 119.7647 | 0.18768 | 0.091553 | 0.12817 | 0 | 0.16022 | 0.086975 | -0.036621 | 0.045777 | 119.6503 | 119.7189 | -2.1927 | -2.2064 | 119.6869 | 119.7601 | 119.6411 | 119.7006
3901.3438 | 122.0764 | -119.6686 | 2.211 | 0.01358 | 0.013933 | -0.035218 | 0.032635 | -0.017199 | -0.029463 | -0.020683 | 0.0055542 | -0.061651 | -0.00075185 | 0.024644 | -0.018367 | -0.0101 | -0.016955 | -0.022888 | -0.059509 | 0.018311 | 0.050354 | 0.18768 | 0.09613 | 0.073242 | 0.064087 | 0.013733 | -0.004578 | 0.068665 | 0.16937 | 0.082397 | 0.16479 | 119.6869 | -2.2705 | -2.1606 | 119.8563 | 119.7418 | 119.7647 | 0.054931 | 0.077819 | 119.664 | -2.1973 | -2.1423 | 119.838 | 119.8334 | 119.751 | 0.16937 | 0.086975 | 0.16937 | 0.032043 | 0.17395 | 0.073243 | -0.07782 | 0.018311 | 119.6091 | 119.6823 | -2.1927 | -2.2156 | 119.7189 | 119.7372 | 119.6457 | 119.7327
3903.0781 | 121.9803 | -119.8288 | 2.1149 | 0.02121 | 0.014787 | -0.0318 | 0.037976 | -0.01079 | -0.030104 | -0.021751 | 0.0055542 | -0.060156 | 0.00095715 | 0.02913 | -0.016445 | -0.011382 | -0.016314 | -0.059509 | -0.050354 | -0.027466 | -0.073242 | 0.045776 | -0.054932 | -0.045776 | -0.054932 | 0.050354 | -0.036621 | 0 | 0.027466 | -0.064087 | 0.082397 | 119.8013 | -2.1652 | -2.1881 | 119.8746 | 119.783 | 119.7739 | -0.01831 | -0.027466 | 119.7922 | -2.0645 | -2.1149 | 119.8563 | 119.9112 | 119.7647 | 0.11902 | -0.027466 | 0.073242 | -0.045776 | 0.064087 | 0.036621 | -0.022888 | 0.086975 | 119.7784 | 119.8791 | -2.1423 | -2.1515 | 119.7556 | 119.8288 | 119.7693 | 119.7739
3904.8594 | 122.0673 | -119.6732 | 2.2568 | 0.0059509 | 0.013719 | -0.032654 | 0.033917 | -0.01549 | -0.029676 | -0.025169 | 0.008606 | -0.061011 | 0.0011708 | 0.037034 | -0.018581 | -0.011595 | -0.017383 | -0.054932 | -0.045776 | 0.009155 | -0.027466 | 0.11444 | 0.022888 | 0.032043 | 0 | 0 | -0.018311 | 0.027466 | 0.11444 | 0.041199 | 0.15106 | 119.6823 | -2.3026 | -2.2842 | 119.7876 | 119.7052 | 119.696 | 0.022888 | 0.013733 | 119.6548 | -2.2568 | -2.2293 | 119.7876 | 119.8242 | 119.7144 | 0.16937 | 0.05951 | 0.10529 | -0.036621 | 0.13275 | 0.045777 | -0.054931 | 0.018311 | 119.6274 | 119.6732 | -2.2476 | -2.2751 | 119.6457 | 119.7006 | 119.6182 | 119.6732
3906.6562 | 122.0581 | -119.5999 | 2.2751 | 0.01358 | 0.015214 | -0.034363 | 0.039471 | -0.015917 | -0.02754 | -0.023246 | 0.0055542 | -0.062079 | 0.0011708 | 0.030839 | -0.013027 | -0.0101 | -0.010547 | -0.068665 | -0.032043 | -0.018311 | -0.073242 | 0.045776 | -0.064087 | -0.041199 | -0.032043 | 0.022888 | -0.013733 | 0.045776 | 0.082397 | 0.004578 | 0.14648 | 119.5816 | -2.3071 | -2.3483 | 119.6457 | 119.5587 | 119.5358 | -0.022888 | -0.045776 | 119.5862 | -2.2522 | -2.2293 | 119.6823 | 119.7464 | 119.6045 | 0.16022 | 0.018311 | 0.064087 | -0.054931 | 0.09613 | 0.059509 | -0.013732 | 0.036621 | 119.5679 | 119.6228 | -2.2934 | -2.2888 | 119.5267 | 119.6457 | 119.5312 | 119.5679
3908.3906 | 122.1497 | -119.8883 | 1.9638 | 0.0059509 | 0.014787 | -0.033722 | 0.034772 | -0.012713 | -0.028822 | -0.021965 | 0.0055542 | -0.062292 | 0.00074335 | 0.035325 | -0.018581 | -0.011382 | -0.016742 | -0.022888 | -0.054932 | 0.013733 | 0.045776 | 0.20142 | 0.091553 | 0.10071 | 0.10986 | 0 | 0 | 0.10529 | 0.20599 | 0.13733 | 0.19684 | 119.902 | -2.0187 | -1.918 | 120.0897 | 119.989 | 119.9799 | 0.086975 | 0.07782 | 119.8883 | -1.9638 | -1.8585 | 120.0943 | 120.0851 | 120.0256 | 0.19684 | 0.13733 | 0.18768 | 0.032043 | 0.20599 | 0.10529 | -0.068665 | 0 | 119.8334 | 119.8883 | -1.9501 | -1.9638 | 119.9341 | 119.9936 | 119.8654 | 119.9982
3910.1719 | 122.1268 | -120.0027 | 1.8448 | 0.02121 | 0.014787 | -0.032013 | 0.03584 | -0.017626 | -0.029036 | -0.024101 | 0.011658 | -0.059515 | -0.0011792 | 0.035966 | -0.016231 | -0.011595 | -0.014819 | 0.009155 | -0.059509 | 0.027466 | 0.041199 | 0.17395 | 0.054932 | 0.068665 | 0.086975 | 0.013733 | -0.004578 | 0.10529 | 0.17853 | 0.086975 | 0.20142 | 120.0302 | -1.9043 | -1.8036 | 120.1767 | 120.0714 | 120.0577 | 0.041199 | 0.027466 | 119.9982 | -1.8311 | -1.7395 | 120.1813 | 120.2042 | 120.0897 | 0.20599 | 0.091553 | 0.14648 | 0.013733 | 0.18311 | 0.10986 | -0.086975 | 0.018311 | 119.9432 | 120.0165 | -1.8173 | -1.8494 | 120.0439 | 120.108 | 120.0119 | 120.0897
3911.8906 | 122.1359 | -120.1126 | 1.767 | 0.0059509 | 0.015641 | -0.033082 | 0.034772 | -0.011858 | -0.028395 | -0.022819 | 0.014709 | -0.059302 | -0.00032465 | 0.03682 | -0.014522 | -0.011595 | -0.012896 | 0.009155 | -0.045776 | 0.013733 | 0.064087 | 0.17853 | 0.045776 | 0.07782 | 0.09613 | 0.018311 | -0.004578 | 0.11902 | 0.16022 | 0.09613 | 0.19684 | 120.1263 | -1.8127 | -1.7029 | 120.2911 | 120.1904 | 120.1584 | 0.064087 | 0.032043 | 120.108 | -1.7487 | -1.6479 | 120.2728 | 120.3094 | 120.2087 | 0.20142 | 0.10071 | 0.16479 | 0.050354 | 0.16479 | 0.1236 | -0.059509 | 0.022889 | 120.0668 | 120.1309 | -1.7532 | -1.7715 | 120.1767 | 120.2316 | 120.1218 | 120.2087
3913.6875 | 122.113 | -120.0989 | 1.7715 | 0.044098 | 0.015001 | -0.032227 | 0.036908 | -0.014208 | -0.028181 | -0.021751 | 0.011658 | -0.060156 | 0.00074335 | 0.037675 | -0.014949 | -0.011168 | -0.011828 | -0.018311 | -0.054932 | 0 | 0.059509 | 0.19684 | 0.068665 | 0.082397 | 0.086975 | 0.004578 | -0.009155 | 0.09613 | 0.16479 | 0.082397 | 0.19226 | 120.0989 | -1.8265 | -1.712 | 120.2957 | 120.1813 | 120.1675 | 0.082397 | 0.068665 | 120.0897 | -1.767 | -1.6754 | 120.2637 | 120.2911 | 120.1813 | 0.20142 | 0.091552 | 0.19684 | 0.059509 | 0.17395 | 0.10528 | -0.054932 | 0.013733 | 120.0439 | 120.1035 | -1.7715 | -1.7807 | 120.1584 | 120.195 | 120.0806 | 120.1859
3915.4844 | 122.1039 | -120.0394 | 1.8631 | 0.028839 | 0.013933 | -0.032868 | 0.03349 | -0.018908 | -0.026258 | -0.020469 | 0.008606 | -0.064002 | 0.00052975 | 0.031479 | -0.018581 | -0.012023 | -0.010119 | -0.054932 | -0.064087 | 0 | -0.013733 | 0.11902 | 0.032043 | 0.054932 | 0.018311 | 0.018311 | -0.004578 | 0.059509 | 0.15106 | 0.073242 | 0.17395 | 120.0394 | -1.9272 | -1.8768 | 120.1584 | 120.0943 | 120.0714 | 0.054932 | 0.032043 | 120.0348 | -1.8448 | -1.8036 | 120.1904 | 120.2133 | 120.1126 | 0.17853 | 0.07782 | 0.11902 | -0.013733 | 0.15564 | 0.064087 | -0.064087 | 0.022889 | 119.9753 | 120.0577 | -1.8631 | -1.8677 | 120.0256 | 120.0989 | 119.9844 | 120.0577
3917.2969 | 121.9803 | -120.0989 | 1.8951 | 0.01358 | 0.012224 | -0.033295 | 0.037549 | -0.017626 | -0.032667 | -0.022178 | 0.011658 | -0.058661 | 0.0018116 | 0.02977 | -0.022426 | -0.0148 | -0.012683 | -0.09613 | -0.036621 | -0.041199 | -0.091553 | 0.041199 | -0.032043 | -0.032043 | -0.054932 | 0.041199 | -0.059509 | -0.045776 | 0.045776 | -0.036621 | 0.07782 | 120.0577 | -1.9318 | -1.9867 | 120.1401 | 120.0668 | 120.0668 | 0.009156 | 0.009156 | 120.0394 | -1.8539 | -1.9409 | 120.1447 | 120.1767 | 120.0623 | 0.13733 | 0.022888 | 0.082398 | -0.050354 | 0.10528 | 0.013733 | 0.004578 | 0.10071 | 120.0623 | 120.1401 | -1.9363 | -1.9547 | 120.0073 | 120.0531 | 120.0027 | 120.0439
3919.0156 | 122.0444 | -120.1401 | 1.8539 | 0.028839 | 0.015001 | -0.033936 | 0.037335 | -0.017626 | -0.029676 | -0.022392 | 0.014709 | -0.059515 | -0.00011105 | 0.032548 | -0.018367 | -0.010955 | -0.014819 | -0.073242 | 0 | -0.050354 | -0.064087 | 0.032043 | -0.032043 | -0.022888 | -0.064087 | 0.054932 | -0.050354 | -0.018311 | 0.073242 | -0.009155 | 0.10071 | 120.0897 | -1.8539 | -1.918 | 120.1721 | 120.1172 | 120.108 | 0.027466 | 0.018311 | 120.0897 | -1.799 | -1.8723 | 120.2133 | 120.2408 | 120.1309 | 0.15106 | 0.041199 | 0.082397 | -0.013733 | 0.1236 | 0.032043 | 0.050354 | 0.10529 | 120.1401 | 120.195 | -1.9043 | -1.9043 | 120.076 | 120.1218 | 120.0668 | 120.076
3920.7969 | 122.0535 | -119.957 | 2.0004 | 0.01358 | 0.014787 | -0.033509 | 0.034558 | -0.013353 | -0.029249 | -0.022178 | 0.0025024 | -0.06272 | -0.0016064 | 0.037888 | -0.020076 | -0.013091 | -0.014392 | -0.018311 | -0.054932 | -0.009155 | 0.004578 | 0.14648 | 0.064087 | 0.059509 | 0.027466 | 0.032043 | -0.009155 | 0.009155 | 0.10071 | 0.022888 | 0.12817 | 119.9478 | -2.0554 | -1.9958 | 120.1035 | 120.0165 | 120.0211 | 0.068664 | 0.073242 | 119.9478 | -1.9684 | -1.9913 | 120.0577 | 120.0851 | 119.9799 | 0.13733 | 0.032043 | 0.15564 | 0.013733 | 0.10986 | 0.01831 | -0.045777 | 0.041198 | 119.902 | 119.989 | -2.0096 | -2.0096 | 119.9615 | 119.9661 | 119.9387 | 119.9844
3922.5469 | 122.0856 | -119.7739 | 2.1378 | 0.01358 | 0.012224 | -0.032654 | 0.03648 | -0.014849 | -0.028395 | -0.021965 | 0.0025024 | -0.062292 | 0.00010255 | 0.036606 | -0.013454 | -0.0081774 | -0.018664 | -0.045776 | -0.054932 | 0.004578 | 0.018311 | 0.12817 | 0.018311 | 0.022888 | 0.050354 | 0 | 0.004578 | 0.082397 | 0.16479 | 0.07782 | 0.19684 | 119.7784 | -2.1927 | -2.1194 | 119.902 | 119.7968 | 119.7922 | 0.01831 | 0.013733 | 119.7784 | -2.1378 | -2.0554 | 119.9387 | 119.9707 | 119.8517 | 0.19226 | 0.073242 | 0.1236 | 0.013733 | 0.16022 | 0.077819 | -0.05951 | -0.004578 | 119.7189 | 119.7739 | -2.1332 | -2.1332 | 119.7922 | 119.8563 | 119.7281 | 119.8242
3924.3438 | 122.1359 | -119.9799 | 1.9043 | 0.01358 | 0.012864 | -0.033936 | 0.034344 | -0.014208 | -0.029676 | -0.020897 | 0.0055542 | -0.061011 | -0.00032465 | 0.035538 | -0.020076 | -0.010314 | -0.015033 | -0.027466 | -0.059509 | 0.018311 | 0.032043 | 0.19684 | 0.091553 | 0.09613 | 0.09613 | 0 | -0.009155 | 0.091553 | 0.20142 | 0.13275 | 0.20142 | 119.9982 | -1.9638 | -1.8723 | 120.1767 | 120.076 | 120.0714 | 0.077819 | 0.073242 | 119.9707 | -1.9043 | -1.8127 | 120.1813 | 120.1813 | 120.1126 | 0.21057 | 0.14191 | 0.17853 | 0.013732 | 0.21057 | 0.10071 | -0.07782 | 0.009155 | 119.9203 | 119.9799 | -1.886 | -1.9135 | 120.0119 | 120.0714 | 119.9524 | 120.076
3926.0625 | 122.0764 | -119.8746 | 2.0554 | 0.0059509 | 0.01436 | -0.033082 | 0.033917 | -0.015276 | -0.029463 | -0.023246 | 0.0055542 | -0.063574 | -0.00182 | 0.038315 | -0.019863 | -0.012664 | -0.014392 | -0.013733 | -0.045776 | 0.018311 | 0.022888 | 0.16937 | 0.086975 | 0.073242 | 0.045776 | -0.004578 | -0.022888 | 0.032043 | 0.14648 | 0.054932 | 0.14648 | 119.8929 | -2.1011 | -2.0325 | 120.0439 | 119.9478 | 119.9615 | 0.054931 | 0.068664 | 119.8517 | -2.0599 | -2.0233 | 120.0211 | 120.0211 | 119.9295 | 0.16937 | 0.07782 | 0.15106 | 0.004577 | 0.16937 | 0.054931 | -0.064087 | 0.01831 | 119.8288 | 119.87 | -2.037 | -2.0782 | 119.8975 | 119.9066 | 119.8608 | 119.9203
3927.8438 | 122.3648 | -119.6136 | 2.3163 | 0.028839 | 0.015641 | -0.032441 | 0.036053 | -0.01848 | -0.027327 | -0.023246 | 0.014709 | -0.060584 | 0.0028798 | 0.034684 | -0.014522 | -0.010955 | -0.011187 | 0.009155 | -0.059509 | 0.032043 | 0.041199 | 0.1831 | 0.050354 | 0.073242 | 0.082397 | 0.018311 | 0.004578 | 0.082397 | 0.16479 | 0.073242 | 0.17853 | 119.6457 | -2.3758 | -2.2751 | 119.7968 | 119.6869 | 119.664 | 0.041199 | 0.018311 | 119.6182 | -2.298 | -2.2339 | 119.7784 | 119.7922 | 119.6869 | 0.17395 | 0.068664 | 0.15106 | 0.009156 | 0.16022 | 0.077819 | -0.091552 | 0.013733 | 119.5541 | 119.632 | -2.2842 | -2.3117 | 119.6548 | 119.696 | 119.6228 | 119.696
3929.5625 | 121.962 | -119.9661 | 2.0233 | 0.0059509 | 0.012437 | -0.034363 | 0.037549 | -0.018053 | -0.02989 | -0.022605 | 0.0055542 | -0.060797 | 0.00095715 | 0.035325 | -0.021144 | -0.012023 | -0.012683 | -0.091553 | -0.004578 | -0.018311 | -0.068665 | 0.045776 | -0.032043 | -0.022888 | -0.07782 | 0.041199 | -0.027466 | -0.045776 | 0.050354 | -0.022888 | 0.091553 | 119.9478 | -2.0279 | -2.092 | 120.0119 | 119.9432 | 119.9341 | -0.004577 | -0.013732 | 119.9387 | -1.9821 | -2.0691 | 120.0165 | 120.0577 | 119.9432 | 0.11902 | 0.004578 | 0.064087 | -0.050354 | 0.07782 | -0.01831 | 0.013733 | 0.068665 | 119.9615 | 120.0073 | -2.0416 | -2.0508 | 119.8975 | 119.9203 | 119.8746 | 119.8883
3931.3594 | 122.1725 | -119.5908 | 2.3346 | 0.01358 | 0.012864 | -0.032654 | 0.035199 | -0.01848 | -0.030958 | -0.021537 | 0.0055542 | -0.062079 | -0.0011792 | 0.037247 | -0.016445 | -0.011382 | -0.011615 | -0.054932 | -0.050354 | 0.004578 | -0.009155 | 0.14191 | 0.041199 | 0.041199 | 0.027466 | 0.004578 | -0.018311 | 0.064087 | 0.16022 | 0.091553 | 0.1831 | 119.5953 | -2.3849 | -2.3438 | 119.7327 | 119.632 | 119.632 | 0.036621 | 0.036621 | 119.5724 | -2.33 | -2.2705 | 119.751 | 119.7739 | 119.6823 | 0.20142 | 0.10986 | 0.13733 | -0.013733 | 0.17853 | 0.082398 | -0.054932 | 0.022889 | 119.5404 | 119.5953 | -2.33 | -2.3529 | 119.5816 | 119.6548 | 119.5358 | 119.6182
3933.0781 | 122.0078 | -114.3677 | 7.489 | 0.02121 | 0.015855 | -0.03415 | 0.037121 | -0.01549 | -0.030317 | -0.022178 | 0.008606 | -0.058447 | -0.00011105 | 0.036393 | -0.017085 | -0.011168 | -0.01311 | -0.018311 | -0.041199 | 0.032043 | -0.013733 | 0.086975 | -0.018311 | -0.009155 | 0 | 0.041199 | 0.022888 | 0.013733 | 0.068665 | -0.022888 | 0.11444 | 114.3997 | -7.5302 | -7.5027 | 114.4547 | 114.3585 | 114.3494 | -0.041198 | -0.050354 | 114.3906 | -7.4478 | -7.4753 | 114.4363 | 114.4821 | 114.3448 | 0.091553 | -0.045776 | 0.054932 | -0.045776 | 0.045777 | -0.009155 | -0.073242 | 0.018311 | 114.3265 | 114.4089 | -7.457 | -7.4661 | 114.3539 | 114.3814 | 114.3494 | 114.3677
3934.8594 | 121.5729 | -13.4445 | 108.3252 | 0.01358 | 0.016923 | -0.035645 | 0.035626 | -0.017626 | -0.026045 | -0.02111 | 0.075745 | -0.060584 | 0.0013844 | 0.035111 | -0.015377 | -0.010955 | -0.014605 | -0.064087 | -0.07782 | -0.036621 | -0.022888 | 0.09613 | -0.022888 | 2.4124 | 0.027466 | -0.018311 | -0.041199 | 0.059509 | 0.11902 | 0.036621 | 0.17395 | 13.4079 | -108.403 | -108.3481 | 13.5406 | 15.8569 | 13.4216 | 2.449 | 0.013733 | 13.4033 | -108.3435 | -108.2657 | 13.5635 | 13.6185 | 13.4811 | 0.21515 | 0.07782 | 0.13275 | 0.013733 | 0.16022 | 0.10071 | -0.041199 | 0.022888 | 13.3667 | 13.4262 | -108.3618 | -108.3664 | 13.4216 | 13.504 | 13.3804 | 13.472
3936.6562 | 121.9849 | -84.2056 | 37.3627 | 0.02121 | 0.015214 | -0.032868 | 0.036694 | -0.016344 | -0.030104 | -0.025383 | 0.0025024 | -0.059729 | -0.0011792 | 0.033188 | -0.017085 | -0.011809 | -0.015246 | -0.068665 | -0.045776 | -0.018311 | -0.073242 | 0.050354 | -0.064087 | -0.068665 | -0.064087 | 0.036621 | -0.004578 | -0.032043 | 0.032043 | -0.073242 | 0.064087 | 84.1873 | -37.4084 | -37.4359 | 84.256 | 84.137 | 84.1415 | -0.050354 | -0.045776 | 84.201 | -37.3261 | -37.3947 | 84.2377 | 84.2697 | 84.1324 | 0.068665 | -0.068664 | 0.068665 | -0.054931 | 0.036621 | -0.027465 | -0.027465 | 0.041199 | 84.1599 | 84.2422 | -37.381 | -37.3672 | 84.1324 | 84.1736 | 84.137 | 84.1415
3938.4375 | 121.7331 | -5.4108 | 116.5192 | 0.01358 | 0.015214 | -0.032868 | 0.036908 | -0.016771 | -0.027327 | -0.017906 | 0.008606 | -0.059515 | 0.00095715 | 0.032761 | -0.014949 | -0.010527 | -0.012683 | -0.10529 | -0.073242 | -0.054932 | -0.10529 | 0.013733 | -0.10071 | -0.082397 | -0.07782 | 0 | -0.07782 | -0.013733 | 0.036621 | -0.064087 | 0.073242 | 5.3558 | -116.5924 | -116.6245 | 5.4245 | 5.3284 | 5.3101 | -0.027465 | -0.045776 | 5.3329 | -116.5192 | -116.5329 | 5.4474 | 5.484 | 5.3467 | 0.15106 | 0.013733 | 0.068665 | -0.050354 | 0.11444 | 0.064087 | -0.01831 | 0.07782 | 5.3375 | 5.4108 | -116.5741 | -116.597 | 5.3055 | 5.397 | 5.3055 | 5.3329
3940.2344 | 122.0352 | -4.6005 | 117.3248 | 0.036468 | 0.013078 | -0.033722 | 0.03648 | -0.012926 | -0.027327 | -0.022178 | 0.011658 | -0.062292 | -0.00011105 | 0.032975 | -0.018794 | -0.010527 | -0.014819 | -0.10529 | -0.10986 | -0.050354 | -0.059509 | 0.07782 | -0.013733 | -0.004578 | -0.054932 | -0.022888 | -0.050354 | -0.004578 | 0.09613 | 0 | 0.11902 | 4.5502 | -117.4347 | -117.3843 | 4.6783 | 4.5959 | 4.5868 | 0.045776 | 0.036621 | 4.5502 | -117.3477 | -117.3294 | 4.6967 | 4.7195 | 4.6005 | 0.16937 | 0.050354 | 0.12817 | -0.009155 | 0.14648 | 0.045776 | -0.059509 | 0.027466 | 4.4907 | 4.5776 | -117.3752 | -117.3752 | 4.541 | 4.5959 | 4.4952 | 4.5456
3941.9688 | 121.9528 | -4.3442 | 117.691 | 0.044098 | 0.01436 | -0.033509 | 0.036694 | -0.018908 | -0.030317 | -0.022178 | 0.020813 | -0.059515 | 0.0011708 | 0.033829 | -0.020717 | -0.010314 | -0.015674 | -0.11444 | -0.041199 | -0.073242 | -0.10071 | 0.004578 | -0.064087 | -0.041199 | -0.10529 | 0.018311 | -0.07782 | -0.068665 | 0.018311 | -0.068665 | 0.050354 | 4.2709 | -117.7322 | -117.7917 | 4.3488 | 4.303 | 4.2801 | 0.032043 | 0.009155 | 4.2664 | -117.6727 | -117.7597 | 4.3625 | 4.3945 | 4.2755 | 0.12817 | 0.009155 | 0.07782 | -0.027466 | 0.096131 | 0.009155 | 0.032043 | 0.096131 | 4.303 | 4.3625 | -117.7643 | -117.7689 | 4.2435 | 4.2755 | 4.2297 | 4.2389
3943.75 | 121.9528 | -4.1656 | 117.865 | 0.02121 | 0.012864 | -0.035004 | 0.036053 | -0.015276 | -0.030104 | -0.02346 | 0.0055542 | -0.058234 | 0.00074335 | 0.033829 | -0.021572 | -0.012023 | -0.014178 | -0.13275 | -0.059509 | -0.050354 | -0.11444 | 0 | -0.068665 | -0.054932 | -0.11902 | -0.009155 | -0.086975 | -0.09613 | 0.022888 | -0.050354 | 0.036621 | 4.1153 | -117.9245 | -117.9794 | 4.1656 | 4.1107 | 4.097 | -0.004578 | -0.018311 | 4.0787 | -117.8741 | -117.9611 | 4.1885 | 4.2023 | 4.1153 | 0.1236 | 0.036621 | 0.050354 | -0.064087 | 0.10986 | -0.009155 | -0.009155 | 0.07782 | 4.1061 | 4.1565 | -117.9153 | -117.952 | 4.0512 | 4.0695 | 4.0329 | 4.0466
3945.5625 | 122.0306 | -3.9322 | 118.1168 | 0.02121 | 0.015428 | -0.032227 | 0.037121 | -0.012499 | -0.030104 | -0.021537 | 0.014709 | -0.058234 | 0.00052975 | 0.029984 | -0.018581 | -0.012664 | -0.013324 | -0.09613 | -0.059509 | -0.068665 | -0.09613 | 0.027466 | -0.054932 | -0.054932 | -0.073242 | 0 | -0.068665 | -0.045776 | 0.064087 | -0.027466 | 0.086975 | 3.8635 | -118.1763 | -118.2129 | 3.9597 | 3.8773 | 3.8773 | 0.013733 | 0.013733 | 3.8635 | -118.1168 | -118.1625 | 3.9963 | 4.0192 | 3.9047 | 0.15564 | 0.041199 | 0.096131 | -0.027465 | 0.13275 | 0.022889 | 0.009156 | 0.068665 | 3.8727 | 3.9322 | -118.1854 | -118.1854 | 3.8361 | 3.8864 | 3.8361 | 3.8589
3947.375 | 121.9803 | -3.7857 | 118.2587 | 0.028839 | 0.015214 | -0.029877 | 0.037335 | -0.011858 | -0.027754 | -0.019188 | 0.0055542 | -0.059729 | 0.00031615 | 0.033402 | -0.019222 | -0.0098864 | -0.014178 | -0.13275 | -0.068665 | -0.064087 | -0.12817 | -0.022888 | -0.12817 | -0.1236 | -0.15564 | 0.004578 | -0.082397 | -0.082397 | 0.004578 | -0.082397 | 0.068665 | 3.7216 | -118.3273 | -118.3868 | 3.7628 | 3.6621 | 3.6575 | -0.059509 | -0.064087 | 3.7033 | -118.2541 | -118.3411 | 3.7903 | 3.8544 | 3.7033 | 0.15106 | 0 | 0.041199 | -0.064087 | 0.086975 | 0 | -0.004578 | 0.086975 | 3.717 | 3.7903 | -118.3228 | -118.3411 | 3.6575 | 3.7033 | 3.653 | 3.6301
3949.1562 | 122.0123 | -3.7308 | 118.3136 | 0.02121 | 0.014787 | -0.033082 | 0.03648 | -0.011858 | -0.028822 | -0.019828 | 0.008606 | -0.06037 | 0.0013844 | 0.027421 | -0.016445 | -0.011382 | -0.012256 | -0.082397 | -0.082397 | -0.054932 | -0.050354 | 0.059509 | -0.027466 | -0.022888 | -0.022888 | 0 | -0.07782 | -0.004578 | 0.07782 | -0.004578 | 0.10529 | 3.6758 | -118.396 | -118.364 | 3.7903 | 3.7079 | 3.7033 | 0.032044 | 0.027466 | 3.653 | -118.3136 | -118.3182 | 3.8086 | 3.8361 | 3.7262 | 0.18311 | 0.073242 | 0.11444 | 0.004578 | 0.15564 | 0.073242 | -0.027465 | 0.07782 | 3.6484 | 3.7308 | -118.3685 | -118.3914 | 3.6804 | 3.7262 | 3.6484 | 3.7079
3950.875 | 122.0078 | -3.6896 | 118.3319 | 0.02121 | 0.014146 | -0.033936 | 0.03648 | -0.014422 | -0.025618 | -0.018119 | 0.008606 | -0.059515 | 0.0011708 | 0.031479 | -0.015163 | -0.008391 | -0.014605 | -0.11902 | -0.068665 | -0.059509 | -0.13275 | -0.022888 | -0.11444 | -0.10071 | -0.13733 | 0 | -0.07782 | -0.073242 | 0.004578 | -0.07782 | 0.054932 | 3.6301 | -118.4006 | -118.4647 | 3.6667 | 3.5889 | 3.5751 | -0.041199 | -0.054932 | 3.6118 | -118.3319 | -118.4052 | 3.6942 | 3.7445 | 3.6118 | 0.13275 | 0 | 0.036621 | -0.073242 | 0.082398 | 0.004578 | -0.009156 | 0.07782 | 3.6209 | 3.6896 | -118.3914 | -118.4097 | 3.5568 | 3.6163 | 3.5706 | 3.5522
3952.6719 | 122.049 | -3.6255 | 118.4052 | 0.044098 | 0.015428 | -0.032013 | 0.036053 | -0.01314 | -0.028395 | -0.021324 | 0.017761 | -0.058875 | 0.0024524 | 0.025071 | -0.018794 | -0.0098864 | -0.015887 | -0.1236 | -0.059509 | -0.086975 | -0.10986 | 0.009155 | -0.045776 | -0.045776 | -0.11444 | -0.018311 | -0.086975 | -0.050354 | 0.050354 | -0.050354 | 0.082397 | 3.5385 | -118.4647 | -118.515 | 3.6346 | 3.5797 | 3.5797 | 0.041199 | 0.041199 | 3.5385 | -118.4235 | -118.4555 | 3.6758 | 3.7079 | 3.5751 | 0.16937 | 0.036621 | 0.09613 | -0.022888 | 0.13733 | 0.036621 | 0.027466 | 0.068664 | 3.566 | 3.6072 | -118.4921 | -118.4921 | 3.5156 | 3.5751 | 3.5019 | 3.511
3954.4688 | 122.1268 | -3.4836 | 118.4555 | 0.01358 | 0.012437 | -0.032868 | 0.034558 | -0.015276 | -0.027967 | -0.023887 | 0.011658 | -0.061438 | -0.00075185 | 0.041092 | -0.016231 | -0.010314 | -0.013751 | -0.027466 | -0.09613 | -0.018311 | 0.004578 | 0.16937 | 0.027466 | 0.041199 | 0.059509 | -0.036621 | -0.027466 | 0.059509 | 0.14648 | 0.064087 | 0.16937 | 3.4653 | -118.5516 | -118.4509 | 3.653 | 3.5248 | 3.511 | 0.05951 | 0.045777 | 3.4561 | -118.4921 | -118.396 | 3.6301 | 3.653 | 3.5477 | 0.19684 | 0.091553 | 0.18768 | 0.022889 | 0.17395 | 0.086975 | -0.077819 | -0.009155 | 3.3875 | 3.447 | -118.4738 | -118.483 | 3.4882 | 3.5431 | 3.4561 | 3.5431
3956.2031 | 121.9894 | -41.803 | 79.8843 | 0.0059509 | 0.010087 | -0.032654 | 0.036908 | -0.019121 | -0.029249 | -0.021537 | 0.0055542 | -0.063361 | 0.00074335 | 0.031693 | -0.020717 | -0.011595 | -0.010974 | -0.068665 | -0.068665 | -0.013733 | -0.045776 | 0.11444 | 0.022888 | 0.013733 | -0.050354 | 0.013733 | -0.041199 | -0.045776 | 0.054932 | -0.009155 | 0.082397 | 41.7892 | -79.953 | -79.9301 | 41.9174 | 41.8167 | 41.8259 | 0.027466 | 0.036621 | 41.7618 | -79.8706 | -79.9301 | 41.8579 | 41.8854 | 41.7938 | 0.1236 | 0.032044 | 0.12817 | -0.032043 | 0.096131 | -0.004577 | -0.054932 | 0.054932 | 41.7343 | 41.8167 | -79.8981 | -79.9255 | 41.7572 | 41.7572 | 41.7343 | 41.7526
3958 | 121.8292 | -5.0583 | 117.0181 | 0.01358 | 0.015001 | -0.030304 | 0.03648 | -0.011644 | -0.028822 | -0.021965 | 0.0055542 | -0.059729 | -0.00096545 | 0.032334 | -0.016445 | -0.012236 | -0.014819 | -0.1236 | -0.054932 | -0.059509 | -0.13275 | -0.036621 | -0.1236 | -0.091553 | -0.13275 | -0.009155 | -0.068665 | -0.07782 | -0.013733 | -0.10071 | 0.045776 | 4.9988 | -117.0731 | -117.1509 | 5.0217 | 4.9667 | 4.9347 | -0.032044 | -0.064087 | 4.9896 | -117.0273 | -117.0959 | 5.0446 | 5.1041 | 4.9576 | 0.11444 | -0.032043 | 0.022888 | -0.073242 | 0.054932 | -0.009155 | 0.004577 | 0.05951 | 5.0034 | 5.0491 | -117.0776 | -117.0868 | 4.9255 | 4.9805 | 4.9347 | 4.9255
3959.7969 | 122.0078 | -4.7333 | 117.3203 | 0.0059509 | 0.01436 | -0.036072 | 0.034558 | -0.016771 | -0.030104 | -0.019828 | 0.0055542 | -0.060797 | 0.00052975 | 0.034257 | -0.021785 | -0.011809 | -0.013324 | -0.073242 | -0.086975 | -0.032043 | -0.064087 | 0.073242 | -0.009155 | -0.018311 | -0.086975 | -0.013733 | -0.064087 | -0.068665 | 0.050354 | -0.050354 | 0.064087 | 4.7012 | -117.4072 | -117.3843 | 4.8065 | 4.715 | 4.7241 | 0.013732 | 0.022888 | 4.6692 | -117.334 | -117.3889 | 4.7836 | 4.7974 | 4.6829 | 0.12817 | 0.013733 | 0.10529 | -0.032044 | 0.11444 | -0.004578 | -0.054932 | 0.050354 | 4.6463 | 4.7195 | -117.3523 | -117.3843 | 4.6692 | 4.6646 | 4.66 | 4.6463
3961.5469 | 122.0169 | -4.9576 | 117.1051 | 0.02121 | 0.013719 | -0.033936 | 0.034985 | -0.013353 | -0.029463 | -0.024314 | 0.0025024 | -0.059729 | -0.00011105 | 0.038956 | -0.020503 | -0.013091 | -0.011401 | -0.1236 | -0.068665 | -0.064087 | -0.11444 | 0.018311 | -0.054932 | -0.059509 | -0.10986 | 0.018311 | -0.082397 | -0.091553 | 0.027466 | -0.054932 | 0.050354 | 4.8935 | -117.1738 | -117.2195 | 4.9759 | 4.8981 | 4.9026 | 0.004578 | 0.009155 | 4.8752 | -117.0868 | -117.1967 | 4.985 | 5.0079 | 4.9026 | 0.13275 | 0.027465 | 0.082398 | -0.050354 | 0.10986 | -0.009156 | -0.004578 | 0.10071 | 4.8889 | 4.9759 | -117.1692 | -117.1875 | 4.8431 | 4.866 | 4.834 | 4.8477
3963.3594 | 122.1634 | -5.0034 | 116.9128 | 0.01358 | 0.012437 | -0.034363 | 0.034558 | -0.017626 | -0.031599 | -0.025596 | 0.0055542 | -0.061651 | -0.0026744 | 0.034043 | -0.017513 | -0.014586 | -0.011615 | -0.059509 | -0.10071 | -0.027466 | 0 | 0.17853 | 0.073242 | 0.068665 | 0.059509 | -0.013733 | -0.027466 | 0.064087 | 0.1831 | 0.10986 | 0.17395 | 4.9759 | -117.0135 | -116.9128 | 5.1819 | 5.072 | 5.0766 | 0.096131 | 0.10071 | 4.9759 | -116.9266 | -116.8488 | 5.1865 | 5.1773 | 5.1132 | 0.20142 | 0.13733 | 0.20599 | 0.027466 | 0.21057 | 0.091553 | -0.073242 | 0.013733 | 4.9026 | 4.9896 | -116.9403 | -116.9403 | 5.0034 | 5.0674 | 4.9438 | 5.0629
3965.1562 | 122.0032 | -4.4312 | 117.6224 | 0.01358 | 0.013719 | -0.032868 | 0.036267 | -0.016344 | -0.028822 | -0.019828 | 0.0055542 | -0.059088 | 0.00010255 | 0.031479 | -0.01559 | -0.0098864 | -0.014392 | -0.11444 | -0.064087 | -0.059509 | -0.1236 | -0.022888 | -0.10529 | -0.11444 | -0.16022 | 0.018311 | -0.073242 | -0.086975 | -0.018311 | -0.10986 | 0.068665 | 4.3716 | -117.6865 | -117.746 | 4.4083 | 4.3167 | 4.3259 | -0.054932 | -0.045777 | 4.3579 | -117.6041 | -117.7094 | 4.4128 | 4.4998 | 4.3213 | 0.14191 | -0.036621 | 0.036621 | -0.064087 | 0.054931 | -0.013733 | -0.004578 | 0.091553 | 4.3671 | 4.4495 | -117.6819 | -117.6956 | 4.3076 | 4.3442 | 4.3167 | 4.2709
3966.9531 | 122.0718 | -4.3625 | 117.7094 | 0.028839 | 0.014573 | -0.032013 | 0.036908 | -0.015062 | -0.028608 | -0.021324 | 0.011658 | -0.06037 | 0.0020252 | 0.039384 | -0.015804 | -0.0096728 | -0.014605 | -0.10529 | -0.054932 | -0.073242 | -0.10529 | 0.027466 | -0.045776 | -0.032043 | -0.07782 | 0.013733 | -0.07782 | -0.045776 | 0.059509 | -0.027466 | 0.10529 | 4.2892 | -117.7643 | -117.8146 | 4.39 | 4.3304 | 4.3167 | 0.041199 | 0.027466 | 4.2847 | -117.6956 | -117.7551 | 4.422 | 4.4678 | 4.335 | 0.18311 | 0.050354 | 0.10071 | -0.032044 | 0.13733 | 0.032044 | 0.01831 | 0.091553 | 4.3076 | 4.3762 | -117.7826 | -117.7872 | 4.2572 | 4.3167 | 4.2572 | 4.2847
3968.6719 | 122.0352 | -4.248 | 117.8101 | 0.02121 | 0.015641 | -0.031586 | 0.038617 | -0.015703 | -0.02754 | -0.021751 | 0.0055542 | -0.058661 | 0.0020252 | 0.03447 | -0.015377 | -0.010955 | -0.011828 | -0.11902 | -0.050354 | -0.064087 | -0.13275 | -0.027466 | -0.1236 | -0.086975 | -0.13275 | 0.004578 | -0.082397 | -0.068665 | -0.013733 | -0.091553 | 0.064087 | 4.184 | -117.8604 | -117.9428 | 4.2206 | 4.1611 | 4.1245 | -0.022888 | -0.059509 | 4.1656 | -117.8055 | -117.8787 | 4.2343 | 4.3121 | 4.1565 | 0.14648 | -0.009156 | 0.036621 | -0.068664 | 0.068664 | 0.013732 | 0.013733 | 0.086975 | 4.1977 | 4.2526 | -117.8741 | -117.8925 | 4.1153 | 4.1794 | 4.129 | 4.1153
3970.4688 | 122.1771 | -4.2572 | 117.746 | 0.02121 | 0.013078 | -0.031586 | 0.034131 | -0.017199 | -0.028181 | -0.022605 | 0.0025024 | -0.062292 | 0.00074335 | 0.037461 | -0.016872 | -0.011809 | -0.013751 | -0.068665 | -0.10529 | -0.027466 | 0.004578 | 0.15106 | 0.068665 | 0.059509 | 0.064087 | -0.018311 | -0.036621 | 0.050354 | 0.17853 | 0.091553 | 0.16479 | 4.2297 | -117.8513 | -117.7414 | 4.4083 | 4.3167 | 4.3259 | 0.086975 | 0.096131 | 4.2206 | -117.7643 | -117.6956 | 4.4357 | 4.422 | 4.3488 | 0.20142 | 0.12817 | 0.17853 | 0.032044 | 0.21515 | 0.086975 | -0.07782 | 0.01831 | 4.1519 | 4.2389 | -117.7734 | -117.7826 | 4.2618 | 4.3076 | 4.1885 | 4.3213
3972.2656 | 122.0535 | -4.0192 | 118.0847 | 0.02121 | 0.016069 | -0.033936 | 0.037121 | -0.016771 | -0.02754 | -0.021751 | 0.008606 | -0.060156 | 0.0011708 | 0.034043 | -0.016231 | -0.010314 | -0.014605 | -0.1236 | -0.050354 | -0.073242 | -0.14191 | -0.009155 | -0.10986 | -0.10071 | -0.10986 | 0.004578 | -0.086975 | -0.059509 | 0.013733 | -0.068665 | 0.064087 | 3.9459 | -118.1351 | -118.2266 | 4.01 | 3.9185 | 3.9093 | -0.027466 | -0.036621 | 3.9322 | -118.0801 | -118.1442 | 4.0329 | 4.0833 | 3.9505 | 0.15106 | 0.01831 | 0.064087 | -0.068665 | 0.10071 | 0.027466 | 0.022888 | 0.091553 | 3.9688 | 4.0237 | -118.158 | -118.1717 | 3.8773 | 3.9597 | 3.8956 | 3.9093
3974 | 122.1817 | -4.0649 | 117.8787 | 0.01358 | 0.013719 | -0.030304 | 0.037335 | -0.018908 | -0.028608 | -0.021965 | 0.0055542 | -0.062506 | 0.00074335 | 0.03447 | -0.015804 | -0.0071094 | -0.015033 | -0.050354 | -0.086975 | -0.036621 | -0.013733 | 0.11902 | 0.004578 | 0.004578 | 0.013733 | -0.022888 | -0.050354 | 0.054932 | 0.14191 | 0.059509 | 0.19226 | 4.0283 | -117.9657 | -117.8925 | 4.184 | 4.0695 | 4.0695 | 0.041199 | 0.041199 | 4.0146 | -117.9016 | -117.8238 | 4.2068 | 4.2572 | 4.1245 | 0.24261 | 0.10986 | 0.15564 | 0.022888 | 0.19226 | 0.10529 | -0.050354 | 0.027466 | 3.978 | 4.0421 | -117.9153 | -117.9291 | 4.0512 | 4.1199 | 4.0146 | 4.0787
3975.7969 | 122.0627 | -4.1245 | 117.952 | 0.028839 | 0.013719 | -0.03415 | 0.03648 | -0.0099357 | -0.028395 | -0.022178 | 0.008606 | -0.060584 | 0.00074335 | 0.035752 | -0.018581 | -0.01245 | -0.013965 | -0.073242 | -0.068665 | -0.036621 | -0.082397 | 0.054932 | -0.050354 | -0.050354 | -0.059509 | 0 | -0.068665 | -0.068665 | 0.018311 | -0.064087 | 0.07782 | 4.0878 | -118.0206 | -118.0344 | 4.1794 | 4.0741 | 4.0741 | -0.013733 | -0.013733 | 4.0558 | -117.952 | -118.0206 | 4.1428 | 4.2023 | 4.0604 | 0.14649 | 0.004578 | 0.091553 | -0.045776 | 0.086976 | 0 | -0.032044 | 0.068665 | 4.0558 | 4.1245 | -117.9886 | -118.0206 | 4.0421 | 4.0558 | 4.0512 | 4.0649
3977.6094 | 122.0627 | -4.0558 | 118.0115 | 0.02121 | 0.01436 | -0.032013 | 0.036908 | -0.01079 | -0.028181 | -0.02111 | 0.0055542 | -0.059088 | 0.0028798 | 0.033402 | -0.017513 | -0.011595 | -0.012042 | -0.068665 | -0.068665 | -0.059509 | -0.082397 | 0.050354 | -0.054932 | -0.059509 | -0.073242 | -0.013733 | -0.064087 | -0.064087 | 0.032043 | -0.068665 | 0.073242 | 3.9963 | -118.0801 | -118.0939 | 4.1061 | 3.9963 | 4.0009 | 0 | 0.004577 | 3.9917 | -118.0252 | -118.0756 | 4.0878 | 4.129 | 3.9871 | 0.13733 | -0.004578 | 0.10986 | -0.022888 | 0.09613 | 0 | -0.009156 | 0.050354 | 3.9871 | 4.0421 | -118.071 | -118.0756 | 3.9734 | 3.9917 | 3.9871 | 3.9825
3979.4062 | 122.0215 | -4.0466 | 118.0252 | 0.01358 | 0.016496 | -0.031159 | 0.037549 | -0.016131 | -0.030104 | -0.019615 | 0.008606 | -0.058875 | 0.00095715 | 0.027634 | -0.019222 | -0.009032 | -0.014392 | -0.1236 | -0.059509 | -0.059509 | -0.1236 | -0.022888 | -0.10986 | -0.10529 | -0.15564 | -0.013733 | -0.068665 | -0.09613 | -0.032043 | -0.10986 | 0.041199 | 3.9871 | -118.0847 | -118.1488 | 4.0237 | 3.9413 | 3.9368 | -0.045777 | -0.050354 | 3.978 | -118.0389 | -118.1213 | 4.0146 | 4.0878 | 3.9368 | 0.10986 | -0.041198 | 0.036621 | -0.064087 | 0.036622 | -0.027465 | 0 | 0.054932 | 3.9871 | 4.0329 | -118.0847 | -118.0939 | 3.923 | 3.9505 | 3.923 | 3.891
3981.125 | 122.168 | -4.01 | 118.0161 | 0.02121 | 0.014787 | -0.031373 | 0.037976 | -0.014208 | -0.028822 | -0.021324 | 0.0055542 | -0.058875 | 0.001598 | 0.031052 | -0.019649 | -0.0086048 | -0.011828 | -0.10986 | -0.064087 | -0.045776 | -0.068665 | 0.059509 | -0.054932 | -0.032043 | -0.013733 | -0.022888 | -0.050354 | 0.018311 | 0.10529 | 0.022888 | 0.14648 | 3.9642 | -118.0801 | -118.0847 | 4.0695 | 3.978 | 3.9551 | 0.013733 | -0.009156 | 3.9597 | -118.0389 | -117.9977 | 4.1153 | 4.1565 | 4.0329 | 0.19684 | 0.073242 | 0.10528 | -0.022889 | 0.15564 | 0.068665 | -0.018311 | 0.027466 | 3.9459 | 3.9871 | -118.0618 | -118.0664 | 3.9413 | 4.0283 | 3.9001 | 3.9963
3982.9219 | 122.1085 | -3.9322 | 118.1168 | 0.028839 | 0.014146 | -0.034577 | 0.036267 | -0.012499 | -0.028822 | -0.02111 | 0.008606 | -0.060797 | -0.00011105 | 0.028275 | -0.01794 | -0.011382 | -0.014392 | -0.068665 | -0.054932 | -0.086975 | -0.064087 | 0.059509 | -0.041199 | -0.027466 | -0.041199 | 0.013733 | -0.073242 | -0.022888 | 0.082397 | -0.018311 | 0.091553 | 3.8452 | -118.1717 | -118.1808 | 3.9917 | 3.9047 | 3.891 | 0.059509 | 0.045776 | 3.8589 | -118.103 | -118.1396 | 4.0146 | 4.0237 | 3.9139 | 0.16479 | 0.054931 | 0.14648 | 0.022888 | 0.15564 | 0.050354 | 0.032043 | 0.086975 | 3.8773 | 3.9459 | -118.2037 | -118.19 | 3.8681 | 3.9093 | 3.8635 | 3.891
3984.6875 | 122.1863 | -3.8269 | 118.1808 | 0.028839 | 0.015001 | -0.032441 | 0.036908 | -0.014208 | -0.029676 | -0.025596 | 0.0025024 | -0.060156 | 0.0013844 | 0.037247 | -0.01559 | -0.0096728 | -0.011187 | -0.059509 | -0.10529 | -0.022888 | -0.013733 | 0.1236 | 0.013733 | 0.009155 | 0.036621 | -0.032043 | -0.041199 | 0.050354 | 0.14191 | 0.054932 | 0.17395 | 3.804 | -118.2861 | -118.1946 | 3.9505 | 3.8361 | 3.8406 | 0.032043 | 0.036621 | 3.7857 | -118.2129 | -118.1305 | 3.9688 | 4.0009 | 3.8818 | 0.21515 | 0.096131 | 0.14648 | 0.009155 | 0.18311 | 0.091553 | -0.082398 | 0.009156 | 3.7216 | 3.7949 | -118.2037 | -118.222 | 3.8132 | 3.8773 | 3.7674 | 3.8635
3986.5 | 122.0718 | -3.9917 | 118.071 | 0.01358 | 0.012864 | -0.035218 | 0.035199 | -0.015917 | -0.027113 | -0.02111 | 0.0025024 | -0.059729 | 0.00052975 | 0.036606 | -0.020931 | -0.012023 | -0.0092648 | -0.10986 | -0.07782 | -0.050354 | -0.10071 | 0.027466 | -0.064087 | -0.045776 | -0.091553 | 0.004578 | -0.059509 | -0.09613 | 0.009155 | -0.054932 | 0.041199 | 3.9413 | -118.1488 | -118.1717 | 4.0192 | 3.9459 | 3.9276 | 0.004578 | -0.013733 | 3.9322 | -118.0664 | -118.1671 | 4.0009 | 4.0329 | 3.9368 | 0.10071 | 0.004577 | 0.07782 | -0.050354 | 0.068664 | -0.036621 | -0.027466 | 0.064087 | 3.9139 | 3.9963 | -118.1213 | -118.1305 | 3.891 | 3.8956 | 3.8818 | 3.9001
3988.2188 | 122.1588 | -3.9047 | 118.103 | 0.01358 | 0.01201 | -0.033295 | 0.033063 | -0.016985 | -0.026899 | -0.022178 | 0.008606 | -0.063788 | -0.00096545 | 0.036179 | -0.016231 | -0.01245 | -0.011401 | -0.09613 | -0.10071 | -0.045776 | -0.064087 | 0.064087 | -0.022888 | 0 | -0.050354 | -0.018311 | -0.045776 | -0.013733 | 0.059509 | -0.004578 | 0.10986 | 3.8589 | -118.2037 | -118.1671 | 3.9688 | 3.9047 | 3.8818 | 0.045776 | 0.022888 | 3.8589 | -118.1213 | -118.1168 | 3.9642 | 4.0146 | 3.9001 | 0.15564 | 0.041198 | 0.10986 | -0.018311 | 0.10528 | 0.032043 | -0.054932 | 0.027465 | 3.804 | 3.8864 | -118.1488 | -118.1488 | 3.8406 | 3.891 | 3.8086 | 3.8544
3990 | 122.081 | -4.1702 | 117.9337 | -0.0016786 | 0.014146 | -0.035218 | 0.035199 | -0.014635 | -0.029463 | -0.02346 | 0.0055542 | -0.059302 | 0.00095715 | 0.03212 | -0.024349 | -0.013091 | -0.015246 | -0.1236 | -0.064087 | -0.068665 | -0.11902 | 0 | -0.07782 | -0.059509 | -0.091553 | 0 | -0.091553 | -0.10071 | 0.009155 | -0.073242 | 0.050354 | 4.1016 | -117.9977 | -118.0527 | 4.1702 | 4.1107 | 4.0924 | 0.009156 | -0.009155 | 4.0787 | -117.9337 | -118.0344 | 4.1794 | 4.2206 | 4.097 | 0.14191 | 0.018311 | 0.068665 | -0.050354 | 0.10071 | -0.009155 | 0.004578 | 0.091553 | 4.1061 | 4.1702 | -118.0023 | -118.0252 | 4.0512 | 4.0695 | 4.0466 | 4.0787
3991.7031 | 122.0627 | -4.1611 | 117.9108 | 0.0059509 | 0.016282 | -0.034577 | 0.038189 | -0.013353 | -0.029676 | -0.018974 | 0.008606 | -0.05802 | 0.00010255 | 0.035752 | -0.016445 | -0.011595 | -0.016314 | -0.082397 | -0.059509 | -0.059509 | -0.086975 | 0.018311 | -0.068665 | -0.064087 | -0.086975 | 0 | -0.073242 | -0.054932 | -0.009155 | -0.091553 | 0.054932 | 4.1016 | -117.9703 | -117.9977 | 4.1794 | 4.097 | 4.0924 | -0.004578 | -0.009156 | 4.0878 | -117.9108 | -117.9657 | 4.1519 | 4.216 | 4.0695 | 0.12817 | -0.018311 | 0.07782 | -0.027466 | 0.064087 | 0.01831 | 0 | 0.073242 | 4.1016 | 4.1611 | -117.9703 | -117.984 | 4.0741 | 4.1061 | 4.0787 | 4.0741
3993.4688 | 122.081 | -4.216 | 117.9245 | 0.028839 | 0.01436 | -0.033936 | 0.033063 | -0.013781 | -0.030531 | -0.021965 | 0.011658 | -0.060584 | 0.00095715 | 0.027421 | -0.019863 | -0.012877 | -0.010547 | -0.1236 | -0.045776 | -0.082397 | -0.12817 | -0.004578 | -0.064087 | -0.064087 | -0.10986 | 0.004578 | -0.09613 | -0.082397 | 0.018311 | -0.068665 | 0.064087 | 4.1336 | -117.9703 | -118.0527 | 4.2114 | 4.1519 | 4.1519 | 0.01831 | 0.01831 | 4.1199 | -117.9199 | -118.0069 | 4.2343 | 4.2801 | 4.1473 | 0.16022 | 0.027465 | 0.077819 | -0.045777 | 0.11444 | 0.013733 | 0.036621 | 0.10071 | 4.1702 | 4.2206 | -118.0069 | -118.0206 | 4.0878 | 4.1336 | 4.0924 | 4.1061
3995.1719 | 122.1451 | -4.1611 | 117.9062 | 0.01358 | 0.01436 | -0.035004 | 0.035199 | -0.014635 | -0.028822 | -0.024528 | 0.008606 | -0.062292 | -0.00096545 | 0.040879 | -0.017726 | -0.010527 | -0.013965 | -0.082397 | -0.09613 | -0.041199 | -0.059509 | 0.086975 | -0.004578 | -0.004578 | -0.041199 | -0.027466 | -0.064087 | 0 | 0.073242 | 0 | 0.10986 | 4.1199 | -118.0023 | -117.9657 | 4.248 | 4.1565 | 4.1565 | 0.036621 | 0.036621 | 4.097 | -117.9337 | -117.9062 | 4.2343 | 4.2709 | 4.1611 | 0.17395 | 0.064087 | 0.12817 | -0.01831 | 0.13733 | 0.064087 | -0.054931 | 0.036621 | 4.0649 | 4.1336 | -117.9474 | -117.9703 | 4.1016 | 4.1611 | 4.0787 | 4.1199
3996.9531 | 122.168 | -4.0237 | 117.9749 | 0.036468 | 0.01436 | -0.032868 | 0.036694 | -0.019121 | -0.028395 | -0.023887 | 0.008606 | -0.061438 | -0.00075185 | 0.03682 | -0.019222 | -0.010527 | -0.012896 | -0.054932 | -0.07782 | -0.022888 | -0.004578 | 0.14191 | 0.004578 | 0.027466 | 0.018311 | -0.022888 | -0.054932 | 0.009155 | 0.091553 | 0.036621 | 0.11444 | 4.0009 | -118.0527 | -117.9794 | 4.1656 | 4.0512 | 4.0283 | 0.050354 | 0.027466 | 3.9688 | -117.9977 | -117.9657 | 4.1153 | 4.1382 | 4.0604 | 0.16937 | 0.091553 | 0.16479 | 0.01831 | 0.14649 | 0.064087 | -0.054932 | 0.032044 | 3.9459 | 4.0009 | -117.9977 | -118.0298 | 4.0192 | 4.0329 | 3.9688 | 4.0421
3998.6719 | 122.168 | -4.1931 | 117.8192 | 0.036468 | 0.013933 | -0.033295 | 0.03584 | -0.014849 | -0.029036 | -0.023674 | 0.008606 | -0.062292 | 0.00052975 | 0.038956 | -0.017726 | -0.010314 | -0.013537 | -0.059509 | -0.10071 | -0.022888 | -0.041199 | 0.10529 | -0.009155 | 0.013733 | -0.009155 | -0.032043 | -0.059509 | 0.004578 | 0.086975 | 0.004578 | 0.11902 | 4.1702 | -117.9199 | -117.8604 | 4.2984 | 4.2068 | 4.184 | 0.036621 | 0.013733 | 4.1336 | -117.8513 | -117.8146 | 4.2801 | 4.3121 | 4.1977 | 0.17853 | 0.064087 | 0.12817 | -0.018311 | 0.14648 | 0.064087 | -0.07782 | 0.027466 | 4.0924 | 4.1611 | -117.8421 | -117.8787 | 4.1519 | 4.1977 | 4.1336 | 4.184
4000.3906 | 122.1039 | -4.1199 | 117.9749 | 0.02121 | 0.012437 | -0.031586 | 0.034344 | -0.014422 | -0.029036 | -0.02111 | 0.0055542 | -0.058875 | 0.00095715 | 0.032975 | -0.02029 | -0.013091 | -0.013537 | -0.064087 | -0.086975 | -0.032043 | -0.050354 | 0.082397 | 0.004578 | 0.009155 | -0.045776 | -0.013733 | -0.064087 | -0.073242 | 0.050354 | -0.050354 | 0.059509 | 4.0878 | -118.0618 | -118.0252 | 4.2023 | 4.129 | 4.1245 | 0.041198 | 0.036621 | 4.0558 | -117.9886 | -118.0481 | 4.1702 | 4.1794 | 4.0695 | 0.1236 | 0.013733 | 0.11444 | -0.018311 | 0.11444 | -0.009155 | -0.054932 | 0.050354 | 4.0329 | 4.1061 | -118.0069 | -118.0389 | 4.0695 | 4.0466 | 4.0558 | 4.0741
4002.1562 | 122.0856 | -4.0512 | 118.0801 | 0.0059509 | 0.013292 | -0.033295 | 0.037335 | -0.014849 | -0.030958 | -0.02346 | 0.011658 | -0.057806 | 0.00052975 | 0.03447 | -0.020503 | -0.015441 | -0.013751 | -0.1236 | -0.054932 | -0.064087 | -0.10986 | 0.004578 | -0.054932 | -0.045776 | -0.11444 | 0.018311 | -0.09613 | -0.10071 | 0.009155 | -0.064087 | 0.036621 | 3.9871 | -118.1351 | -118.19 | 4.0558 | 4.0054 | 3.9963 | 0.018311 | 0.009155 | 3.9551 | -118.0618 | -118.1808 | 4.0604 | 4.0878 | 3.9871 | 0.13275 | 0.032043 | 0.068665 | -0.045776 | 0.10528 | -0.004578 | 0.009155 | 0.11444 | 3.9963 | 4.0695 | -118.1442 | -118.1763 | 3.9413 | 3.9505 | 3.9276 | 3.9368
4004.0156 | 122.0627 | -5.983 | 116.1209 | 0.01358 | 0.0026104 | -0.034577 | 0.038403 | -0.01314 | -0.030104 | -0.021965 | 0.0055542 | -0.060584 | 0.0020252 | 0.034043 | -0.016872 | -0.011595 | -0.014178 | -0.068665 | -0.068665 | -0.064087 | -0.10071 | 0.013733 | -0.07782 | -0.064087 | -0.10071 | -0.004578 | -0.068665 | -0.054932 | -0.013733 | -0.091553 | 0.050354 | 5.9189 | -116.1896 | -116.2216 | 5.9967 | 5.9189 | 5.9052 | 0 | -0.013733 | 5.9143 | -116.1255 | -116.1758 | 5.9692 | 6.0333 | 5.8914 | 0.11902 | -0.022888 | 0.07782 | -0.036621 | 0.054932 | 0.013733 | -0.004578 | 0.064087 | 5.9143 | 5.9784 | -116.185 | -116.1896 | 5.8823 | 5.928 | 5.9143 | 5.8823
4005.7188 | 122.1405 | -6.6925 | 115.3473 | 0.028839 | 0.014146 | -0.033295 | 0.034772 | -0.011644 | -0.026686 | -0.022392 | 0.011658 | -0.060797 | 0.0011708 | 0.036179 | -0.01559 | -0.012664 | -0.016955 | -0.022888 | -0.10529 | -0.027466 | 0.018311 | 0.14648 | 0.032043 | 0.027466 | 0.064087 | -0.018311 | -0.045776 | 0.064087 | 0.12817 | 0.041199 | 0.15106 | 6.665 | -115.4526 | -115.329 | 6.839 | 6.72 | 6.7245 | 0.054932 | 0.059509 | 6.6467 | -115.3656 | -115.2832 | 6.8207 | 6.8436 | 6.7337 | 0.19684 | 0.086975 | 0.17395 | 0.045777 | 0.17395 | 0.10986 | -0.07782 | 0.027465 | 6.5872 | 6.6742 | -115.3748 | -115.3931 | 6.7108 | 6.7566 | 6.6696 | 6.7566
4007.4219 | 122.1222 | -5.7449 | 116.2903 | 0.02121 | 0.014146 | -0.032227 | 0.034985 | -0.015703 | -0.024336 | -0.025596 | 0.017761 | -0.061651 | 0.00095715 | 0.035752 | -0.016872 | -0.011809 | -0.015887 | -0.07782 | -0.082397 | -0.045776 | -0.041199 | 0.064087 | -0.009155 | -0.004578 | -0.027466 | -0.022888 | -0.059509 | -0.018311 | 0.07782 | 0.004578 | 0.10529 | 5.6992 | -116.3727 | -116.3315 | 5.809 | 5.7404 | 5.7358 | 0.041198 | 0.036621 | 5.6854 | -116.3132 | -116.3086 | 5.8228 | 5.8502 | 5.7495 | 0.16479 | 0.064087 | 0.10986 | 0.004577 | 0.13733 | 0.041198 | -0.036621 | 0.036621 | 5.6625 | 5.722 | -116.3361 | -116.3498 | 5.7037 | 5.7266 | 5.6671 | 5.7175
4009.1406 | 121.3943 | -4.248 | 117.8833 | 0.02121 | 0.015428 | -0.032654 | 0.036694 | -0.016131 | -0.029036 | -0.022178 | 0.011658 | -0.058234 | 0.0020252 | 0.032334 | -0.019435 | -0.010741 | -0.014605 | -0.10071 | -0.064087 | -0.054932 | -0.10071 | -0.009155 | -0.10986 | -0.10071 | -0.13733 | 0.009155 | -0.07782 | -0.09613 | -0.004578 | -0.11444 | 0.036621 | 4.1931 | -117.9474 | -117.984 | 4.2389 | 4.1473 | 4.1382 | -0.045776 | -0.054931 | 4.1702 | -117.8741 | -117.9794 | 4.2435 | 4.2847 | 4.1336 | 0.11444 | -0.036621 | 0.045777 | -0.045776 | 0.073242 | -0.01831 | -0.009155 | 0.086975 | 4.184 | 4.2572 | -117.9382 | -117.9611 | 4.1473 | 4.1519 | 4.1473 | 4.1107
4010.8594 | 121.7056 | -5.0583 | 117.0639 | 0.01358 | 0.011583 | -0.033082 | 0.034772 | -0.013994 | -0.028395 | -0.023246 | 0.0055542 | -0.059729 | 0.0020252 | 0.025498 | -0.02029 | -0.011168 | -0.012256 | -0.059509 | -0.09613 | -0.050354 | -0.027466 | 0.10071 | 0.018311 | -0.004578 | -0.050354 | -0.009155 | -0.068665 | -0.068665 | 0.064087 | -0.036621 | 0.059509 | 5.0079 | -117.16 | -117.0914 | 5.159 | 5.0537 | 5.0766 | 0.045776 | 0.068665 | 4.9896 | -117.0731 | -117.1326 | 5.1224 | 5.1178 | 5.0217 | 0.12817 | 0.032044 | 0.15106 | 0.022888 | 0.13275 | 0 | -0.045776 | 0.05951 | 4.9622 | 5.0491 | -117.1143 | -117.1326 | 5.0308 | 4.9896 | 4.9988 | 5.0079
4012.5781 | 121.5775 | -6.514 | 115.6265 | -0.0016786 | 0.020128 | -0.032013 | 0.037762 | -0.014422 | -0.028395 | -0.02581 | 0.0055542 | -0.059729 | 0.00074335 | 0.032334 | -0.015804 | -0.011382 | -0.013324 | -0.1236 | -0.050354 | -0.045776 | -0.13733 | -0.045776 | -0.1236 | -0.10529 | -0.15564 | 0.018311 | -0.068665 | -0.086975 | -0.004578 | -0.09613 | 0.064087 | 6.4682 | -115.6769 | -115.7639 | 6.4682 | 6.4087 | 6.3904 | -0.05951 | -0.07782 | 6.4453 | -115.6082 | -115.7135 | 6.5094 | 6.5781 | 6.4178 | 0.13275 | -0.027465 | 0 | -0.091553 | 0.064087 | -0.01831 | -0.004578 | 0.086976 | 6.4636 | 6.5323 | -115.6723 | -115.6952 | 6.3766 | 6.427 | 6.3904 | 6.3583
4014.2969 | 122.1451 | -4.2297 | 117.8421 | 0.036468 | 0.014146 | -0.033295 | 0.033703 | -0.0088675 | -0.029036 | -0.02346 | 0.014709 | -0.060156 | 0.0020252 | 0.035538 | -0.01794 | -0.011809 | -0.010547 | -0.068665 | -0.091553 | -0.027466 | -0.027466 | 0.09613 | -0.004578 | -0.004578 | -0.018311 | -0.036621 | -0.059509 | -0.018311 | 0.086975 | 0.018311 | 0.11444 | 4.2023 | -117.9337 | -117.8696 | 4.3259 | 4.2252 | 4.2252 | 0.022888 | 0.022888 | 4.1702 | -117.8787 | -117.8604 | 4.3167 | 4.3442 | 4.248 | 0.17395 | 0.07782 | 0.1236 | 0 | 0.14648 | 0.041198 | -0.064087 | 0.022888 | 4.1382 | 4.1931 | -117.8696 | -117.9016 | 4.2023 | 4.2114 | 4.1611 | 4.2114
4016.0156 | 122.0764 | -4.7562 | 117.3706 | 0.036468 | 0.013933 | -0.032441 | 0.035199 | -0.015276 | -0.029036 | -0.021751 | 0.014709 | -0.059088 | 0.0022388 | 0.037034 | -0.021358 | -0.012877 | -0.012256 | -0.11444 | -0.036621 | -0.086975 | -0.10529 | 0.018311 | -0.045776 | -0.050354 | -0.10986 | 0.032043 | -0.086975 | -0.091553 | 0.013733 | -0.064087 | 0.050354 | 4.6692 | -117.4072 | -117.4759 | 4.7745 | 4.7058 | 4.7104 | 0.036621 | 0.041199 | 4.6692 | -117.3386 | -117.4622 | 4.7699 | 4.8065 | 4.6921 | 0.13733 | 0.022888 | 0.10529 | -0.018311 | 0.10071 | -0.004578 | 0.050354 | 0.11902 | 4.7195 | 4.7882 | -117.4576 | -117.4576 | 4.6509 | 4.6646 | 4.6417 | 4.6463
4017.7188 | 122.1817 | -4.8294 | 117.1509 | 0.02121 | 0.013078 | -0.034577 | 0.034985 | -0.01549 | -0.027754 | -0.020256 | 0.0055542 | -0.062506 | -0.00053825 | 0.040879 | -0.016658 | -0.0098864 | -0.01311 | -0.086975 | -0.10071 | -0.036621 | -0.032043 | 0.10986 | 0.022888 | 0.032043 | -0.004578 | -0.041199 | -0.059509 | 0.022888 | 0.15564 | 0.073242 | 0.15564 | 4.7928 | -117.2516 | -117.1829 | 4.9393 | 4.8614 | 4.8523 | 0.068664 | 0.059509 | 4.7699 | -117.1921 | -117.128 | 4.985 | 4.985 | 4.9026 | 0.21515 | 0.13275 | 0.14648 | 0.004578 | 0.21515 | 0.082397 | -0.064087 | 0.01831 | 4.7287 | 4.7882 | -117.1875 | -117.2104 | 4.7974 | 4.8523 | 4.7424 | 4.8248
4019.4844 | 121.7789 | -4.303 | 117.5446 | 0.02121 | 0.010942 | -0.0318 | 0.038189 | -0.013567 | -0.026686 | -0.022178 | 0.0055542 | -0.058661 | -0.00096545 | 0.028916 | -0.018367 | -0.012664 | -0.013751 | -0.086975 | -0.073242 | -0.059509 | -0.09613 | -0.013733 | -0.091553 | -0.091553 | -0.12817 | 0 | -0.064087 | -0.07782 | 0 | -0.11444 | 0.036621 | 4.2435 | -117.6178 | -117.6407 | 4.2892 | 4.2114 | 4.2114 | -0.032044 | -0.032044 | 4.2389 | -117.5446 | -117.6224 | 4.303 | 4.3396 | 4.1885 | 0.10071 | -0.050354 | 0.045776 | -0.036621 | 0.064087 | -0.013733 | -0.013733 | 0.064087 | 4.2297 | 4.303 | -117.6041 | -117.6086 | 4.2068 | 4.2252 | 4.216 | 4.1748
4021.1875 | 122.0993 | -4.628 | 117.54 | 0.02121 | 0.014787 | -0.033509 | 0.037549 | -0.0084403 | -0.028608 | -0.021965 | 0.008606 | -0.058234 | 0.00010255 | 0.033188 | -0.019649 | -0.011809 | -0.015246 | -0.073242 | -0.054932 | -0.064087 | -0.068665 | 0.054932 | -0.050354 | -0.041199 | -0.054932 | 0.004578 | -0.054932 | -0.059509 | 0.032043 | -0.068665 | 0.073242 | 4.5639 | -117.5949 | -117.6086 | 4.6829 | 4.5868 | 4.5776 | 0.022888 | 0.013733 | 4.5731 | -117.5354 | -117.5995 | 4.66 | 4.7012 | 4.5593 | 0.12817 | -0.013733 | 0.11902 | -0.004578 | 0.086975 | -0.004577 | 0.009155 | 0.05951 | 4.5731 | 4.6326 | -117.6041 | -117.5949 | 4.5593 | 4.5685 | 4.5547 | 4.5731
4022.9688 | 121.701 | -3.0167 | 119.1696 | 0.0059509 | 0.016282 | -0.033722 | 0.035412 | -0.016558 | -0.029036 | -0.024101 | 0.014709 | -0.059088 | 0.00074335 | 0.036179 | -0.021358 | -0.011595 | -0.012683 | -0.16479 | -0.045776 | -0.082397 | -0.11902 | 0.022888 | -0.036621 | -0.059509 | -0.10986 | 0.013733 | -0.09613 | -0.086975 | 0.004578 | -0.064087 | 0.045776 | 2.9343 | -119.2154 | -119.2886 | 3.0396 | 2.9572 | 2.98 | 0.022888 | 0.045776 | 2.9205 | -119.1559 | -119.2566 | 3.0212 | 3.0624 | 2.9526 | 0.14191 | 0.032043 | 0.10528 | -0.036622 | 0.10071 | 0.009155 | 0.036621 | 0.10986 | 2.9709 | 3.0304 | -119.252 | -119.2657 | 2.8976 | 2.9297 | 2.8519 | 2.9068
4024.6875 | 122.1268 | -4.9026 | 117.1967 | 0.01358 | 0.013078 | -0.033936 | 0.036053 | -0.016131 | -0.030958 | -0.025596 | 0.011658 | -0.058447 | 0.0035206 | 0.028702 | -0.021144 | -0.012877 | -0.01311 | -0.13275 | -0.064087 | -0.10071 | -0.11902 | 0.022888 | -0.059509 | -0.045776 | -0.11902 | 0.013733 | -0.07782 | -0.07782 | 0.004578 | -0.054932 | 0.064087 | 4.8019 | -117.2607 | -117.3157 | 4.9255 | 4.8569 | 4.8431 | 0.054932 | 0.041199 | 4.8248 | -117.1829 | -117.2745 | 4.9072 | 4.9667 | 4.8477 | 0.14191 | 0.022888 | 0.1236 | -0.018311 | 0.082398 | 0 | 0.036621 | 0.091553 | 4.8386 | 4.9164 | -117.2974 | -117.2745 | 4.7836 | 4.8248 | 4.7699 | 4.7836
4026.4531 | 122.168 | -4.0237 | 118.0573 | 0.036468 | 0.013292 | -0.030304 | 0.037549 | -0.01314 | -0.029036 | -0.020897 | 0.0025024 | -0.060156 | 0.00095715 | 0.035752 | -0.016231 | -0.011809 | -0.012683 | -0.064087 | -0.10986 | -0.036621 | -0.018311 | 0.13733 | -0.004578 | 0.013733 | -0.004578 | -0.027466 | -0.054932 | 0.022888 | 0.086975 | 0.013733 | 0.1236 | 3.9871 | -118.1671 | -118.0756 | 4.1611 | 4.0375 | 4.0192 | 0.050354 | 0.032043 | 3.9688 | -118.0847 | -118.0344 | 4.1107 | 4.1473 | 4.0375 | 0.17853 | 0.068665 | 0.17395 | 0.01831 | 0.14191 | 0.07782 | -0.073242 | 0.027466 | 3.9139 | 3.9963 | -118.0939 | -118.1122 | 4.0054 | 4.0466 | 3.9597 | 4.0192
4028.1562 | 122.287 | -3.7308 | 118.309 | 0.02121 | 0.013505 | -0.033722 | 0.037121 | -0.013567 | -0.030531 | -0.021751 | 0.0055542 | -0.059515 | -0.00182 | 0.03917 | -0.015804 | -0.009032 | -0.011615 | -0.059509 | -0.10529 | -0.022888 | -0.004578 | 0.15106 | 0.068665 | 0.054932 | 0.050354 | -0.041199 | -0.050354 | 0.041199 | 0.15564 | 0.10986 | 0.17853 | 3.7079 | -118.4143 | -118.3136 | 3.8818 | 3.7857 | 3.7994 | 0.07782 | 0.091553 | 3.6804 | -118.3502 | -118.2678 | 3.8864 | 3.9093 | 3.8406 | 0.22888 | 0.16022 | 0.17395 | 0.01831 | 0.20599 | 0.091553 | -0.082398 | 0.009155 | 3.6255 | 3.6896 | -118.3319 | -118.3594 | 3.7262 | 3.772 | 3.6713 | 3.7811
4029.875 | 121.3165 | -120.9869 | 0.10986 | 0.01358 | 0.012651 | -0.027741 | 0.03648 | -0.014635 | -0.028608 | -0.021965 | 0.0055542 | -0.059515 | -0.0026744 | 0.031907 | -0.017085 | -0.0096728 | -0.012042 | -0.086975 | -0.045776 | 0.004578 | -0.022888 | 0.10529 | 0.041199 | 0.032043 | -0.009155 | 0 | -0.004578 | 0.041199 | 0.10529 | 0.036621 | 0.15106 | 120.9915 | -0.15564 | -0.13275 | 121.0922 | 121.019 | 121.0281 | 0.027465 | 0.036621 | 120.9824 | -0.10986 | -0.068664 | 121.0922 | 121.138 | 121.0236 | 0.15564 | 0.041199 | 0.10071 | -0.027466 | 0.10986 | 0.045777 | -0.050354 | 0.004578 | 120.9412 | 120.9869 | -0.10529 | -0.11444 | 120.9641 | 121.0281 | 120.9 | 120.9778
4031.5781 | 121.3303 | -120.1904 | 1.1261 | 0.028839 | 0.011369 | -0.03415 | 0.039044 | -0.011858 | -0.030745 | -0.01876 | 0.017761 | -0.059515 | -0.0016064 | 0.037034 | -0.02029 | -0.011595 | -0.011828 | -0.086975 | 0.009155 | -0.036621 | -0.059509 | 0.045776 | -0.027466 | -0.018311 | -0.07782 | 0.036621 | -0.045776 | -0.027466 | 0.059509 | -0.013733 | 0.11902 | 120.1538 | -1.1169 | -1.1856 | 120.2362 | 120.1721 | 120.163 | 0.01831 | 0.009155 | 120.1447 | -1.0895 | -1.1536 | 120.2499 | 120.3094 | 120.1767 | 0.16479 | 0.032043 | 0.082397 | -0.022888 | 0.10528 | 0.01831 | 0.045776 | 0.082397 | 120.1996 | 120.2271 | -1.1627 | -1.1719 | 120.1309 | 120.163 | 120.1035 | 120.1126
4033.2969 | 121.3852 | -6.3995 | 114.2578 | 0.059357 | 0.01671 | -0.029236 | 0.036053 | -0.018053 | -0.027327 | -0.019828 | 0.014709 | -0.060584 | 0.00095715 | 0.033616 | -0.017085 | -0.010314 | -0.012469 | -0.022888 | -0.086975 | -0.027466 | 0.013733 | 0.15564 | 0.036621 | 0.018311 | 0.068665 | -0.022888 | 0.1831 | 0.064087 | 0.11902 | 0.045776 | 0.15106 | 6.3721 | -114.3448 | -114.2441 | 6.5552 | 6.4178 | 6.4362 | 0.045777 | 0.064087 | 6.5826 | -114.2807 | -114.1937 | 6.5186 | 6.5506 | 6.4453 | -0.032043 | -0.13733 | 0.18311 | 0.041199 | -0.064086 | -0.11902 | -0.059509 | -0.20599 | 6.3126 | 6.3766 | -114.2853 | -114.0747 | 6.4133 | 6.4636 | 6.3766 | 6.4682
4035.0156 | 121.2479 | -8.6517 | 105.8533 | 0.02121 | 0.015428 | -0.033295 | 0.023877 | -0.020403 | -0.029249 | -0.036491 | 0.008606 | -0.060797 | 0.0013844 | 0.036606 | -0.01559 | -0.0101 | -0.018664 | -0.11444 | -0.07782 | -0.082397 | -0.1236 | -0.032043 | -0.11902 | -0.082397 | -0.13275 | 0.018311 | 0.10986 | -0.059509 | -0.027466 | -0.10071 | 0.068665 | 8.5693 | -105.9311 | -105.9769 | 8.6197 | 8.5693 | 8.5327 | 0 | -0.036622 | 8.7616 | -105.835 | -105.9128 | 8.6243 | 8.7204 | 8.551 | -0.041198 | -0.21057 | 0.050354 | -0.041199 | -0.13733 | -0.16937 | 0.004577 | -0.091552 | 8.5739 | 8.67 | -105.9357 | -105.7434 | 8.5281 | 8.5922 | 8.5373 | 8.519
4036.7656 | 121.1151 | -8.8852 | 112.1613 | 0.02121 | 0.013933 | -0.035004 | 0.036053 | -0.01549 | -0.029036 | -0.022178 | 0.008606 | -0.060156 | -0.00053825 | 0.041092 | -0.017726 | -0.0096728 | -0.010547 | -0.050354 | -0.10529 | -0.027466 | 0.022888 | 0.16937 | 0.064087 | 0.050354 | 0.050354 | -0.036621 | -0.036621 | 0.050354 | 0.15564 | 0.086975 | 0.14648 | 8.8577 | -112.2665 | -112.1384 | 9.0546 | 8.9355 | 8.9493 | 0.07782 | 0.091553 | 8.8486 | -112.1979 | -112.1109 | 9.0408 | 9.0317 | 8.9722 | 0.18311 | 0.1236 | 0.19684 | 0.050354 | 0.19226 | 0.086975 | -0.07782 | 0 | 8.7799 | 8.8486 | -112.1887 | -112.1979 | 8.9081 | 8.9355 | 8.8348 | 8.9355
4038.4844 | 121.3486 | -6.5277 | 114.473 | 0.02121 | 0.013078 | -0.032654 | 0.036694 | -0.016558 | -0.030745 | -0.01876 | 0.008606 | -0.060156 | 0.001598 | 0.034684 | -0.019222 | -0.01245 | -0.011401 | -0.045776 | -0.086975 | -0.027466 | 0.022888 | 0.14648 | 0.068665 | 0.041199 | 0.041199 | -0.041199 | -0.050354 | 0.045776 | 0.15564 | 0.054932 | 0.14648 | 6.5002 | -114.5599 | -114.4501 | 6.6742 | 6.5689 | 6.5964 | 0.068665 | 0.096131 | 6.4774 | -114.5142 | -114.4272 | 6.6833 | 6.6742 | 6.5826 | 0.19684 | 0.10529 | 0.17395 | 0.050354 | 0.20599 | 0.09613 | -0.059509 | 0.009155 | 6.4407 | 6.4865 | -114.5004 | -114.5233 | 6.5506 | 6.5735 | 6.4819 | 6.5689
4040.2031 | 121.7514 | -107.9269 | 13.3255 | 0.01358 | 0.013719 | -0.031373 | 0.03584 | -0.018267 | -0.029463 | -0.020469 | 0.008606 | -0.061438 | -0.00053825 | 0.031907 | -0.017299 | -0.011382 | -0.014819 | -0.013733 | -0.068665 | 0 | 0.041199 | 0.16937 | 0.09613 | 0.073242 | 0.073242 | 0 | -0.022888 | 0.050354 | 0.15564 | 0.082397 | 0.15106 | 107.9269 | -13.3942 | -13.2843 | 108.0963 | 108.0002 | 108.0231 | 0.073242 | 0.09613 | 107.9041 | -13.3255 | -13.2751 | 108.0826 | 108.078 | 108.0093 | 0.17395 | 0.10528 | 0.16937 | 0.041199 | 0.17853 | 0.073242 | -0.068665 | 0.022888 | 107.8583 | 107.9269 | -13.3255 | -13.3484 | 107.9681 | 107.9773 | 107.9132 | 108.0002
4041.9688 | 121.3394 | -42.3431 | 78.9917 | 0.036468 | 0.01436 | -0.032227 | 0.03584 | -0.016558 | -0.030958 | -0.019615 | 0.014709 | -0.059943 | -0.00075185 | 0.037675 | -0.015377 | -0.010955 | -0.012896 | -0.022888 | -0.086975 | -0.018311 | 0.032043 | 0.16022 | 0.032043 | 0.045776 | 0.068665 | -0.032043 | -0.018311 | 0.059509 | 0.14648 | 0.064087 | 0.15564 | 42.3248 | -79.0787 | -78.9597 | 42.5034 | 42.3889 | 42.3752 | 0.064087 | 0.050354 | 42.3248 | -79.0237 | -78.9322 | 42.4896 | 42.4988 | 42.4072 | 0.17395 | 0.082398 | 0.17853 | 0.050354 | 0.16479 | 0.07782 | -0.068664 | -0.013732 | 42.2562 | 42.3111 | -79.01 | -79.01 | 42.3752 | 42.4026 | 42.3203 | 42.4118
4043.7188 | 121.3943 | -22.0184 | 99.4583 | 0.028839 | 0.013933 | -0.034363 | 0.039044 | -0.012072 | -0.030958 | -0.022605 | 0.011658 | -0.062933 | -0.00032465 | 0.044297 | -0.019008 | -0.0096728 | -0.01076 | -0.082397 | -0.091553 | -0.022888 | -0.045776 | 0.07782 | -0.009155 | 0.013733 | -0.032043 | -0.013733 | -0.054932 | -0.004578 | 0.082397 | -0.004578 | 0.1236 | 21.9955 | -99.5499 | -99.5041 | 22.0963 | 22.0322 | 22.0093 | 0.036621 | 0.013733 | 21.9635 | -99.472 | -99.4629 | 22.1008 | 22.142 | 22.0139 | 0.17853 | 0.050354 | 0.10071 | -0.022888 | 0.13733 | 0.050354 | -0.068665 | 0.041199 | 21.9269 | 22.0047 | -99.4812 | -99.5132 | 21.9727 | 22.0139 | 21.936 | 21.9864
4045.4375 | 121.1655 | -13.9755 | 107.1716 | 0.01358 | 0.012437 | -0.032868 | 0.036694 | -0.013994 | -0.030104 | -0.021537 | 0.008606 | -0.061438 | -0.00053825 | 0.03447 | -0.019649 | -0.012877 | -0.011615 | -0.045776 | -0.091553 | -0.022888 | 0.018311 | 0.17395 | 0.059509 | 0.059509 | 0.050354 | -0.018311 | -0.036621 | 0.045776 | 0.16479 | 0.073242 | 0.13733 | 13.9526 | -107.2632 | -107.1533 | 14.1495 | 14.035 | 14.035 | 0.082397 | 0.082397 | 13.9389 | -107.1899 | -107.1259 | 14.1403 | 14.1129 | 14.0488 | 0.17395 | 0.10986 | 0.19684 | 0.041199 | 0.20142 | 0.082397 | -0.068665 | 0.01831 | 13.884 | 13.9572 | -107.1945 | -107.2083 | 13.9938 | 14.0213 | 13.9297 | 14.0259
4047.1562 | 120.8908 | -7.8369 | 113.0173 | 0.028839 | 0.016069 | -0.034791 | 0.037976 | -0.015062 | -0.029036 | -0.020897 | 0.020813 | -0.058447 | 0.0024524 | 0.032334 | -0.022426 | -0.012664 | -0.011615 | -0.13733 | -0.045776 | -0.064087 | -0.1236 | 0.018311 | -0.059509 | -0.041199 | -0.10071 | 0.013733 | -0.09613 | -0.10071 | 0.013733 | -0.073242 | 0.041199 | 7.7728 | -113.063 | -113.1409 | 7.8552 | 7.7957 | 7.7774 | 0.022888 | 0.004578 | 7.7408 | -113.0035 | -113.118 | 7.8506 | 7.8781 | 7.7637 | 0.13733 | 0.022888 | 0.082398 | -0.059509 | 0.10986 | -0.004578 | 0.018311 | 0.10986 | 7.7911 | 7.8506 | -113.0814 | -113.1134 | 7.7133 | 7.7362 | 7.6996 | 7.7362
4048.9219 | 98.8861 | -8.0933 | 113.5437 | -0.039826 | 0.0047468 | -0.036072 | 0.027936 | -0.023607 | -0.028181 | -0.028801 | 0.008606 | -0.07041 | -0.0078014 | 0.026352 | -0.029048 | -0.029753 | -0.015674 | -0.054932 | -0.068665 | -0.064087 | -0.041199 | 0.068665 | -0.022888 | -0.050354 | -0.036621 | 0.004578 | -0.064087 | -0.009155 | 0.073242 | -0.022888 | 0.082397 | 8.0292 | -113.6124 | -113.5849 | 8.1619 | 8.0429 | 8.0704 | 0.013733 | 0.041199 | 8.0292 | -113.5391 | -113.5529 | 8.1665 | 8.1757 | 8.0704 | 0.14648 | 0.041199 | 0.13275 | 0.022888 | 0.13733 | 0.054932 | -0.004578 | 0.068665 | 8.0246 | 8.0978 | -113.6078 | -113.6078 | 8.0521 | 8.0841 | 8.0383 | 8.0566
4050.6406 | 100.0397 | -21.1533 | 74.5056 | 0.14328 | 0.019273 | 0.067535 | 0.021527 | 0.026167 | 0.033983 | 0.029305 | 0.011658 | -0.071692 | -0.015919 | 0.027634 | 0.024357 | 0.028352 | -0.02315 | -0.068665 | -0.064087 | -0.054932 | -0.064087 | 0.041199 | -0.068665 | -0.068665 | -0.07782 | 0.004578 | -0.004578 | -0.11902 | 0.004578 | -0.091553 | -0.027466 | 21.0983 | -74.5697 | -74.5697 | 21.1945 | 21.0846 | 21.0846 | -0.013733 | -0.013733 | 21.1487 | -74.501 | -74.6246 | 21.1578 | 21.1258 | 21.0617 | -0.022888 | -0.086975 | 0.096131 | -0.009155 | 0.009156 | -0.11444 | -0.009155 | 0.009156 | 21.0892 | 21.1578 | -74.5605 | -74.5102 | 21.0892 | 21.0342 | 21.0846 | 21.0754
4052.3594 | 121.1014 | -16.8961 | 103.8483 | 0.0059509 | 0.013933 | -0.0318 | 0.037976 | -0.013781 | -0.029463 | -0.023033 | 0.0055542 | -0.061651 | -0.00096545 | 0.038529 | -0.019649 | -0.010955 | -0.013324 | -0.041199 | -0.082397 | -0.027466 | 0.027466 | 0.17395 | 0.068665 | 0.050354 | 0.054932 | -0.032043 | -0.027466 | 0.036621 | 0.16022 | 0.09613 | 0.16022 | 16.8686 | -103.9307 | -103.8208 | 17.07 | 16.9464 | 16.9647 | 0.07782 | 0.096131 | 16.8686 | -103.8803 | -103.8116 | 17.0563 | 17.0563 | 16.9922 | 0.18768 | 0.1236 | 0.20142 | 0.054932 | 0.18768 | 0.064087 | -0.054931 | -0.004577 | 16.8137 | 16.864 | -103.8757 | -103.8757 | 16.9235 | 16.9327 | 16.8549 | 16.951
4054.0781 | 111.3235 | -15.9668 | 100.5066 | 0.02121 | 0.006883 | -0.052735 | 0.025372 | -0.026171 | -0.041639 | -0.032219 | 0.008606 | -0.068701 | -0.0092968 | 0.037034 | -0.01794 | -0.016722 | -0.019732 | -0.11902 | -0.050354 | -0.073242 | -0.10986 | -0.027466 | -0.10529 | -0.07782 | -0.11902 | -0.004578 | 0.004578 | -0.10529 | -0.018311 | -0.091553 | 0.027466 | 15.8936 | -100.5569 | -100.6165 | 15.9393 | 15.889 | 15.8615 | -0.004578 | -0.032044 | 15.9714 | -100.5112 | -100.6119 | 15.9485 | 15.9943 | 15.8752 | 0.022888 | -0.096131 | 0.045776 | -0.036621 | -0.022889 | -0.10986 | 0.022888 | -0.009156 | 15.9164 | 15.9622 | -100.5798 | -100.502 | 15.8569 | 15.8615 | 15.8478 | 15.8478
4055.7812 | 121.0098 | -14.1357 | 106.3477 | 0.028839 | 0.014573 | -0.030091 | 0.037976 | -0.015917 | -0.028181 | -0.020683 | 0.008606 | -0.060156 | -0.00075185 | 0.038102 | -0.015377 | -0.0092456 | -0.013324 | -0.050354 | -0.091553 | -0.022888 | -0.013733 | 0.13275 | 0.009155 | 0.018311 | 0.032043 | -0.018311 | -0.018311 | 0.068665 | 0.14191 | 0.068665 | 0.1831 | 14.1129 | -106.4392 | -106.3614 | 14.2685 | 14.1541 | 14.1449 | 0.041199 | 0.032043 | 14.1174 | -106.366 | -106.279 | 14.2776 | 14.3188 | 14.2044 | 0.20142 | 0.086976 | 0.15564 | 0.009155 | 0.16022 | 0.086976 | -0.068665 | 0 | 14.0442 | 14.1174 | -106.3705 | -106.366 | 14.122 | 14.2044 | 14.0854 | 14.1678
4057.4844 | 121.907 | -87.6801 | 33.7234 | 0.036468 | 0.010942 | -0.026886 | 0.036908 | -0.017199 | -0.030317 | -0.019401 | 0.014709 | -0.060584 | -0.00075185 | 0.044297 | -0.017085 | -0.0098864 | -0.014178 | -0.045776 | -0.054932 | -0.009155 | 0.041199 | 0.16937 | 0.050354 | 0.059509 | 0.07782 | -0.004578 | -0.027466 | 0.086975 | 0.15564 | 0.082397 | 0.17853 | 87.6709 | -33.7784 | -33.6823 | 87.8494 | 87.7396 | 87.7304 | 0.068664 | 0.059509 | 87.6526 | -33.728 | -33.6365 | 87.8357 | 87.8586 | 87.7625 | 0.20599 | 0.10986 | 0.17853 | 0.050354 | 0.18311 | 0.11444 | -0.045777 | 0.022888 | 87.6251 | 87.6755 | -33.7326 | -33.7509 | 87.7213 | 87.767 | 87.6343 | 87.7579
4059.1875 | 121.8338 | -59.9808 | 61.4731 | 0.01358 | 0.011583 | -0.030732 | 0.034131 | -0.014208 | -0.031172 | -0.018974 | 0.011658 | -0.060797 | -0.00182 | 0.039811 | -0.016872 | -0.010527 | -0.010547 | -0.064087 | -0.059509 | -0.013733 | 0.004578 | 0.15106 | 0.068665 | 0.073242 | 0.050354 | 0 | 0.009155 | 0.068665 | 0.17853 | 0.10986 | 0.1831 | 59.967 | -61.5326 | -61.4685 | 60.1318 | 60.054 | 60.0494 | 0.086975 | 0.082398 | 59.9899 | -61.4731 | -61.4044 | 60.1593 | 60.1639 | 60.0906 | 0.17395 | 0.10071 | 0.16479 | 0.018311 | 0.16937 | 0.05951 | -0.045776 | -0.009155 | 59.9213 | 59.9808 | -61.4868 | -61.4639 | 59.9854 | 60.0494 | 59.9167 | 60.0311
4060.8906 | 112.6923 | -9.343 | 86.2152 | 0.036468 | 0.014787 | -0.03415 | 0.037335 | 0.02638 | -0.032881 | -0.04055 | -0.18365 | 0.016321 | -0.0022472 | 0.022721 | 0.023289 | 0.028566 | 0.019788 | -0.073242 | -0.059509 | -0.045776 | -0.059509 | -0.032043 | -0.13275 | -0.20142 | -0.018311 | -0.32959 | -0.09613 | -0.004578 | -0.24261 | 0.09613 | 0.09613 | 9.2972 | -86.2747 | -86.2747 | 9.3109 | 9.1415 | 9.2102 | -0.15564 | -0.086975 | 9.2468 | -86.5448 | -86.2198 | 9.1003 | 9.4391 | 9.4391 | 0.19226 | 0.19226 | 0.013733 | -0.013733 | -0.14649 | 0.091552 | -0.013733 | -0.23346 | 9.2834 | 9.0134 | -86.261 | -86.3113 | 9.2834 | 9.3384 | 9.2697 | 9.3246
4062.625 | 121.8292 | -9.2239 | 111.5524 | 0.028839 | 0.014146 | -0.030518 | 0.03648 | -0.013567 | -0.028395 | -0.022392 | 0.014709 | -0.060797 | -0.00032465 | 0.034897 | -0.015163 | -0.0092456 | -0.013537 | -0.032043 | -0.11444 | -0.009155 | 0.013733 | 0.15106 | 0.027466 | 0.032043 | 0.073242 | -0.027466 | 0.004578 | 0.059509 | 0.13733 | 0.050354 | 0.091553 | 9.2148 | -111.6669 | -111.5387 | 9.375 | 9.256 | 9.2514 | 0.041198 | 0.036621 | 9.2285 | -111.5799 | -111.4929 | 9.3613 | 9.3155 | 9.2743 | 0.086975 | 0.045776 | 0.16022 | 0.022888 | 0.13275 | 0.054931 | -0.10529 | -0.032044 | 9.1095 | 9.1965 | -111.5616 | -111.5479 | 9.2377 | 9.2834 | 9.1919 | 9.2972
4064.3281 | 121.431 | -11.5997 | 109.845 | 0.036468 | 0.016282 | -0.033082 | 0.034558 | -0.012926 | -0.029249 | -0.021751 | 0.011658 | -0.06272 | 0.00031615 | 0.040452 | -0.018581 | -0.010314 | -0.015033 | -0.082397 | -0.091553 | -0.045776 | -0.050354 | 0.091553 | 0.004578 | 0 | -0.027466 | -0.027466 | -0.054932 | -0.004578 | 0.07782 | 0.009155 | 0.1236 | 11.554 | -109.9365 | -109.8953 | 11.6913 | 11.5997 | 11.6043 | 0.045776 | 0.050354 | 11.5448 | -109.8724 | -109.8495 | 11.6776 | 11.7233 | 11.6089 | 0.17853 | 0.064087 | 0.13733 | -0.004578 | 0.13275 | 0.050354 | -0.045777 | 0.027466 | 11.5082 | 11.5723 | -109.8907 | -109.8999 | 11.5494 | 11.5952 | 11.5173 | 11.5723
4066.0469 | 121.3577 | -10.0113 | 110.9253 | 0.02121 | 0.010515 | -0.0318 | 0.035626 | -0.016558 | -0.026899 | -0.020897 | 0.008606 | -0.062933 | -0.00096545 | 0.035111 | -0.017299 | -0.010955 | -0.01311 | -0.07782 | -0.07782 | -0.032043 | -0.036621 | 0.091553 | 0.009155 | 0.013733 | -0.009155 | -0.027466 | 0.086975 | 0.027466 | 0.1236 | 0.054932 | 0.11902 | 9.9792 | -111.0031 | -110.9619 | 10.1028 | 10.025 | 10.0204 | 0.045776 | 0.041198 | 10.0983 | -110.9528 | -110.8978 | 10.1349 | 10.1303 | 10.0662 | 0.032044 | -0.032043 | 0.1236 | -0.004578 | 0.036621 | -0.059509 | -0.045777 | -0.11444 | 9.9335 | 9.9838 | -110.9573 | -110.8383 | 9.9747 | 10.0388 | 9.9335 | 10.0021
4067.75 | 121.8613 | -8.8806 | 111.9736 | 0.02121 | 0.015001 | -0.032868 | 0.034344 | -0.017412 | -0.028395 | -0.02111 | -0.012756 | -0.059943 | -0.00096545 | 0.041306 | -0.017513 | -0.011809 | -0.013751 | -0.091553 | -0.07782 | -0.036621 | -0.050354 | 0.086975 | 0.004578 | 0.004578 | -0.018311 | -0.059509 | 0.16937 | 0.009155 | 0.12817 | 0.050354 | 0.13733 | 8.844 | -112.0514 | -112.0239 | 8.9676 | 8.8852 | 8.8852 | 0.041199 | 0.041199 | 9.05 | -112.0331 | -111.9644 | 9.0088 | 9.0179 | 8.931 | -0.032044 | -0.11902 | 0.1236 | -0.013733 | -0.041199 | -0.16022 | -0.041199 | -0.22888 | 8.8028 | 8.8211 | -112.0102 | -111.8042 | 8.8303 | 8.8898 | 8.7891 | 8.8623
4069.4531 | 121.0556 | -10.5377 | 111.1496 | 0.01358 | 0.013933 | -0.033295 | 0.035199 | -0.01784 | -0.029463 | -0.024528 | -0.076843 | -0.06272 | -0.00182 | 0.032548 | -0.02029 | -0.010741 | -0.011401 | -0.054932 | -0.10071 | -0.027466 | 0.032043 | 0.16479 | 0.068665 | -0.022888 | 0.054932 | -0.018311 | 0.25177 | 0.045776 | 0.15564 | -0.022888 | 0.022888 | 10.5103 | -111.2503 | -111.1176 | 10.7025 | 10.5148 | 10.6064 | 0.004578 | 0.096131 | 10.7895 | -111.1679 | -111.1038 | 10.6934 | 10.5606 | 10.5148 | -0.22888 | -0.27466 | 0.19226 | 0.059509 | -0.09613 | -0.20599 | -0.073242 | -0.27008 | 10.437 | 10.5194 | -111.1771 | -110.8978 | 10.5698 | 10.5835 | 10.4828 | 10.5927
4071.1562 | 101.3535 | -9.407 | 92.157 | -0.0093076 | 0.013505 | -0.034577 | 0.028149 | -0.017199 | -0.030745 | -0.020469 | -0.12262 | -0.066779 | 0.00010255 | 0.032761 | -0.020076 | -0.011382 | -0.012683 | -0.13275 | -0.045776 | 0.018311 | -0.11444 | -0.041199 | -0.24261 | -0.42572 | -0.11902 | 0.013733 | 0.23346 | -0.064087 | -0.16479 | -0.13275 | 0.082397 | 9.4254 | -92.2028 | -92.2714 | 9.3658 | 8.9813 | 9.1644 | -0.44403 | -0.26093 | 9.6405 | -92.1432 | -92.2211 | 9.2422 | 9.4894 | 9.2743 | -0.15106 | -0.36621 | -0.05951 | -0.13275 | -0.39825 | -0.29755 | -0.064087 | -0.21973 | 9.3613 | 9.4208 | -92.1387 | -91.9235 | 9.2926 | 9.343 | 9.2743 | 9.288
4072.8906 | 121.4264 | -10.2219 | 110.8704 | 0.01358 | 0.013933 | -0.032013 | 0.034558 | -0.016558 | -0.029036 | -0.02346 | -0.01886 | -0.061011 | -0.0013928 | 0.037034 | -0.019863 | -0.0098864 | -0.0094784 | -0.086975 | -0.091553 | -0.050354 | -0.054932 | 0.07782 | 0 | 0.004578 | -0.004578 | -0.032043 | 0 | 0.004578 | 0.11444 | 0.050354 | 0.13733 | 10.1715 | -110.9619 | -110.9253 | 10.2997 | 10.2264 | 10.2219 | 0.054932 | 0.050354 | 10.2219 | -110.9024 | -110.8658 | 10.3363 | 10.3592 | 10.2722 | 0.13733 | 0.050354 | 0.12817 | -0.004578 | 0.11444 | 0.004578 | -0.041199 | -0.032043 | 10.1303 | 10.1898 | -110.9207 | -110.8704 | 10.1669 | 10.2264 | 10.1349 | 10.2173
4074.6562 | 121.4813 | -9.9426 | 111.0489 | 0.036468 | 0.014787 | -0.031373 | 0.034985 | -0.013994 | -0.028181 | -0.024528 | -0.021912 | -0.062933 | -0.00032465 | 0.042801 | -0.017085 | -0.010955 | -0.014178 | -0.086975 | -0.09613 | -0.032043 | -0.027466 | 0.10071 | 0 | -0.004578 | -0.013733 | -0.036621 | -0.045776 | 0 | 0.086975 | 0.009155 | 0.10071 | 9.9106 | -111.145 | -111.0764 | 10.0433 | 9.938 | 9.9426 | 0.027465 | 0.032043 | 9.8969 | -111.0855 | -111.0489 | 10.0296 | 10.0433 | 9.9518 | 0.14648 | 0.054931 | 0.13275 | 0.004577 | 0.13275 | 0.045776 | -0.064087 | 0.009155 | 9.8465 | 9.906 | -111.0809 | -111.0947 | 9.9152 | 9.9426 | 9.8557 | 9.9289
4076.375 | 121.257 | -10.6339 | 110.5362 | 0.044098 | 0.015001 | -0.0318 | 0.034558 | -0.011004 | -0.028395 | -0.02111 | -0.052429 | -0.060797 | -0.00053825 | 0.048356 | -0.016872 | -0.0088184 | -0.009692 | -0.032043 | -0.082397 | -0.022888 | 0.009155 | 0.14648 | 0.027466 | -0.041199 | 0.068665 | -0.013733 | -0.022888 | 0.045776 | 0.11902 | 0.027466 | 0.091553 | 10.611 | -110.6186 | -110.527 | 10.7803 | 10.5927 | 10.6613 | -0.018311 | 0.050354 | 10.611 | -110.5499 | -110.4904 | 10.7529 | 10.7254 | 10.6613 | 0.11444 | 0.050354 | 0.16937 | 0.032043 | 0.14191 | 0.068664 | -0.059509 | 0.009155 | 10.5515 | 10.6201 | -110.5591 | -110.5591 | 10.643 | 10.6796 | 10.6018 | 10.7025
4078.0781 | 121.4401 | -10.2219 | 111.3052 | 0.028839 | 0.01201 | -0.03415 | 0.035412 | -0.01549 | -0.032026 | -0.01876 | 0.0055542 | -0.06272 | -0.00096545 | 0.035752 | -0.015163 | -0.0092456 | -0.014819 | -0.086975 | -0.082397 | -0.041199 | -0.022888 | 0.10071 | 0.018311 | 0.018311 | 0.009155 | -0.027466 | -0.032043 | 0.032043 | 0.13733 | 0.050354 | 0.16479 | 10.1807 | -111.3876 | -111.3281 | 10.3226 | 10.2402 | 10.2402 | 0.05951 | 0.05951 | 10.1898 | -111.3327 | -111.2732 | 10.3592 | 10.3867 | 10.2722 | 0.19684 | 0.082397 | 0.14191 | 0.018311 | 0.16937 | 0.064086 | -0.041198 | 0.004577 | 10.1395 | 10.1944 | -111.3464 | -111.3373 | 10.199 | 10.2539 | 10.1349 | 10.231
4079.7812 | 121.4264 | -9.9884 | 111.5433 | 0.02121 | 0.015001 | -0.0318 | 0.036694 | -0.013994 | -0.026472 | -0.022178 | 0.0055542 | -0.062292 | -0.00032465 | 0.035752 | -0.016872 | -0.010955 | -0.015674 | -0.059509 | -0.082397 | -0.041199 | -0.022888 | 0.11444 | -0.009155 | 0.009155 | 0.004578 | -0.018311 | -0.041199 | 0.013733 | 0.068665 | 0.004578 | 0.10986 | 9.9472 | -111.6257 | -111.5662 | 10.1028 | 9.9976 | 9.9792 | 0.050354 | 0.032044 | 9.9472 | -111.5616 | -111.5295 | 10.0571 | 10.0983 | 9.993 | 0.15106 | 0.045777 | 0.15564 | 0.018311 | 0.10986 | 0.054932 | -0.041198 | 0.022888 | 9.906 | 9.9701 | -111.5845 | -111.5845 | 9.9655 | 10.0021 | 9.9289 | 9.993
4081.4844 | 121.1792 | -7.7408 | 112.9532 | 0.028839 | 0.013933 | -0.034363 | 0.037762 | -0.012926 | -0.029676 | -0.024101 | -0.064636 | -0.06037 | -0.00075185 | 0.02913 | -0.013881 | -0.010527 | -0.014178 | -0.018311 | -0.11902 | -0.013733 | 0.018311 | 0.1236 | -0.004578 | -0.07782 | 0.073242 | -0.041199 | -0.054932 | 0.064087 | 0.13733 | 0.045776 | 0.050354 | 7.7271 | -113.0722 | -112.9349 | 7.8644 | 7.663 | 7.7362 | -0.064087 | 0.009155 | 7.6859 | -112.9944 | -112.8891 | 7.8781 | 7.7911 | 7.7866 | 0.10529 | 0.10071 | 0.13733 | 0.032044 | 0.19226 | 0.11902 | -0.10529 | 0.013733 | 7.6218 | 7.6996 | -112.9669 | -113.0081 | 7.7591 | 7.8049 | 7.7225 | 7.814
4083.2031 | 121.1746 | -7.7591 | 113.2233 | 0.02121 | 0.013719 | -0.032013 | 0.03648 | -0.014422 | -0.027113 | -0.021537 | -0.003601 | -0.059729 | -0.00075185 | 0.03917 | -0.014522 | -0.0092456 | -0.014605 | -0.027466 | -0.11444 | -0.027466 | 0.032043 | 0.15106 | 0.022888 | -0.022888 | 0.068665 | -0.027466 | -0.059509 | 0.059509 | 0.13275 | 0.050354 | 0.091553 | 7.7316 | -113.3377 | -113.1912 | 7.9102 | 7.7362 | 7.782 | 0.004578 | 0.050354 | 7.6996 | -113.2507 | -113.1638 | 7.8918 | 7.8506 | 7.8094 | 0.15106 | 0.10986 | 0.17853 | 0.059509 | 0.19226 | 0.11902 | -0.086975 | 0.032043 | 7.6447 | 7.7316 | -113.2507 | -113.2828 | 7.7911 | 7.8186 | 7.7316 | 7.8278
4084.9688 | 104.4525 | -7.6813 | 113.0676 | 0.036468 | 0.012864 | -0.033295 | 0.038403 | -0.015276 | -0.029249 | -0.023674 | -0.11041 | -0.063574 | -0.0013928 | 0.03447 | -0.020931 | -0.013518 | -0.010547 | -0.10986 | -0.041199 | -0.073242 | -0.11902 | 0 | -0.068665 | -0.23346 | -0.11444 | 0.036621 | -0.07782 | -0.07782 | 0.004578 | -0.23804 | -0.13733 | 7.608 | -113.1088 | -113.1866 | 7.6813 | 7.4478 | 7.6126 | -0.16022 | 0.004577 | 7.6035 | -113.031 | -113.1454 | 7.6859 | 7.5439 | 7.4432 | -0.059509 | -0.16022 | 0.073242 | -0.045777 | 0.082398 | 0 | 0.032043 | 0.11444 | 7.6401 | 7.7179 | -113.1409 | -113.1454 | 7.5623 | 7.6035 | 7.5714 | 7.5668
4086.6719 | 92.1661 | -8.194 | 86.3892 | 0.028839 | 0.013292 | -0.032441 | 0.035626 | -0.018267 | -0.029036 | -0.030937 | -0.16229 | -0.077673 | -0.0031018 | 0.031693 | -0.018367 | -0.011168 | -0.01546 | -0.068665 | -0.045776 | -0.059509 | -0.059509 | 0.050354 | -0.045776 | -0.27924 | -0.032043 | 0 | -0.07782 | -0.027466 | 0.064087 | -0.26093 | -0.38452 | 8.1345 | -86.4349 | -86.4487 | 8.2443 | 7.9147 | 8.1482 | -0.21973 | 0.013733 | 8.1162 | -86.3892 | -86.4166 | 8.2581 | 7.8094 | 7.933 | -0.3067 | -0.18311 | 0.10986 | 0 | 0.14191 | 0.050354 | 0.013733 | 0.07782 | 8.1482 | 8.194 | -86.4487 | -86.467 | 8.1345 | 8.1665 | 8.1253 | 8.1619
4088.4062 | 103.5507 | -7.9147 | 97.0413 | 0.01358 | 0.016496 | -0.031586 | 0.039685 | -0.015062 | -0.029463 | -0.027305 | -0.11041 | -0.069342 | -0.00182 | 0.036179 | -0.018367 | -0.013518 | -0.018023 | -0.11444 | -0.045776 | -0.068665 | -0.13275 | -0.036621 | -0.12817 | -0.28381 | -0.13733 | 0.018311 | -0.07782 | -0.09613 | -0.045776 | -0.22888 | -0.32959 | 7.8461 | -97.0871 | -97.1741 | 7.8781 | 7.6309 | 7.7866 | -0.21515 | -0.059509 | 7.8369 | -97.023 | -97.1375 | 7.869 | 7.5851 | 7.6859 | -0.25177 | -0.15106 | 0.032044 | -0.064086 | 0.032044 | -0.01831 | 0.022889 | 0.096131 | 7.869 | 7.933 | -97.11 | -97.1191 | 7.782 | 7.8186 | 7.8003 | 7.7774
4090.1094 | 110.8475 | -7.9834 | 113.5345 | 0.01358 | 0.015641 | -0.030518 | 0.036908 | -0.012926 | -0.029036 | -0.019828 | -0.046326 | -0.060156 | -0.00011105 | 0.03682 | -0.018154 | -0.01245 | -0.012896 | -0.10529 | -0.054932 | -0.059509 | -0.11902 | -0.022888 | -0.12817 | -0.17853 | -0.12817 | 0.009155 | -0.086975 | -0.068665 | -0.022888 | -0.12817 | -0.14191 | 7.9239 | -113.5895 | -113.6536 | 7.9605 | 7.8049 | 7.8552 | -0.11902 | -0.068665 | 7.8964 | -113.5254 | -113.6032 | 7.9605 | 7.8415 | 7.8552 | -0.054932 | -0.041199 | 0.036621 | -0.05951 | 0.064087 | 0.01831 | 0.004577 | 0.09613 | 7.9285 | 7.9926 | -113.5941 | -113.6215 | 7.8644 | 7.9147 | 7.8781 | 7.8552
4091.8438 | 121.4996 | -8.5464 | 112.5458 | 0.036468 | 0.013933 | -0.032441 | 0.038403 | -0.013994 | -0.028395 | -0.022178 | 0.011658 | -0.06272 | -0.0020336 | 0.036179 | -0.01794 | -0.0098864 | -0.012896 | -0.09613 | -0.10071 | -0.041199 | -0.045776 | 0.091553 | -0.004578 | 0.009155 | -0.009155 | -0.036621 | -0.054932 | 0.032043 | 0.10529 | 0.054932 | 0.14648 | 8.5052 | -112.6465 | -112.5916 | 8.638 | 8.5556 | 8.5419 | 0.050354 | 0.036621 | 8.4915 | -112.5824 | -112.5137 | 8.6517 | 8.6929 | 8.6014 | 0.20142 | 0.10986 | 0.13275 | -0.004577 | 0.16022 | 0.086975 | -0.059509 | 0.018311 | 8.4457 | 8.5098 | -112.587 | -112.6007 | 8.5007 | 8.5785 | 8.4503 | 8.5373
4093.5625 | 104.6265 | -8.844 | 94.1071 | 0.044098 | 0.014787 | -0.033509 | 0.037121 | -0.014635 | -0.030317 | -0.021324 | -0.076843 | -0.064002 | -0.0013928 | 0.029984 | -0.020717 | -0.01245 | -0.014392 | -0.10986 | -0.032043 | -0.082397 | -0.10986 | 0.004578 | -0.054932 | -0.16022 | -0.11902 | 0.022888 | -0.10071 | -0.082397 | 0 | -0.15564 | -0.31586 | 8.7616 | -94.1391 | -94.2169 | 8.8486 | 8.6838 | 8.7891 | -0.07782 | 0.027465 | 8.7433 | -94.0842 | -94.1895 | 8.844 | 8.5281 | 8.6884 | -0.21515 | -0.054932 | 0.086975 | -0.027466 | 0.10071 | 0.018311 | 0.050354 | 0.1236 | 8.812 | 8.8669 | -94.1895 | -94.2078 | 8.7341 | 8.7616 | 8.7341 | 8.725
4095.2969 | 121.5454 | -8.7433 | 112.3032 | 0.028839 | 0.014146 | -0.034791 | 0.034985 | -0.014208 | -0.029249 | -0.022392 | 0.008606 | -0.062506 | -0.00096545 | 0.03917 | -0.017085 | -0.011168 | -0.010547 | -0.073242 | -0.086975 | -0.036621 | -0.009155 | 0.13733 | 0.045776 | 0.050354 | 0.054932 | -0.032043 | -0.054932 | 0.059509 | 0.15106 | 0.09613 | 0.16022 | 8.7067 | -112.3901 | -112.3123 | 8.8806 | 8.7936 | 8.7891 | 0.086975 | 0.082397 | 8.6884 | -112.3352 | -112.2437 | 8.8943 | 8.9035 | 8.8394 | 0.21515 | 0.15106 | 0.17395 | 0.027466 | 0.20599 | 0.11444 | -0.050354 | 0.022889 | 8.6563 | 8.7112 | -112.3398 | -112.3581 | 8.7341 | 8.8028 | 8.67 | 8.7982
4097.0312 | 121.5454 | -8.8028 | 112.6648 | 0.02121 | 0.012651 | -0.033082 | 0.035626 | -0.011858 | -0.029249 | -0.020897 | 0.011658 | -0.060584 | 0.00074335 | 0.039811 | -0.017513 | -0.010314 | -0.014605 | -0.045776 | -0.10071 | -0.036621 | 0.013733 | 0.1831 | 0.073242 | 0.068665 | 0.09613 | -0.036621 | -0.022888 | 0.045776 | 0.14648 | 0.07782 | 0.15564 | 8.7662 | -112.7655 | -112.6511 | 8.9859 | 8.8715 | 8.876 | 0.10529 | 0.10986 | 8.7799 | -112.7014 | -112.619 | 8.9493 | 8.9584 | 8.8806 | 0.17853 | 0.10071 | 0.21973 | 0.050354 | 0.16937 | 0.068664 | -0.064087 | -0.013733 | 8.7021 | 8.7662 | -112.7014 | -112.6877 | 8.8165 | 8.8486 | 8.757 | 8.8989
4098.7344 | 121.2387 | -15.4175 | 101.8982 | 0.01358 | 0.014146 | -0.03415 | 0.036053 | -0.01549 | -0.030745 | -0.02346 | 0.008606 | -0.060584 | -0.0028882 | 0.037461 | -0.017726 | -0.010955 | -0.015674 | -0.045776 | -0.10071 | -0.009155 | 0.013733 | 0.16479 | 0.082397 | 0.050354 | 0.068665 | -0.041199 | -0.036621 | 0.064087 | 0.12817 | 0.073242 | 0.1236 | 15.4083 | -101.9989 | -101.8845 | 15.5823 | 15.4678 | 15.4999 | 0.059509 | 0.091552 | 15.3809 | -101.9394 | -101.8341 | 15.5457 | 15.5411 | 15.4907 | 0.16022 | 0.10986 | 0.17395 | 0.022888 | 0.1648 | 0.10071 | -0.091553 | -0.004578 | 15.3168 | 15.3763 | -101.9073 | -101.9348 | 15.4312 | 15.4816 | 15.3717 | 15.4861
4100.4688 | 121.9482 | -8.9081 | 111.8134 | 0.01358 | 0.013505 | -0.030945 | 0.039258 | -0.013567 | -0.031813 | -0.020897 | -0.076843 | -0.059729 | -0.00032465 | 0.035752 | -0.016017 | -0.0096728 | -0.017383 | -0.10529 | -0.068665 | -0.073242 | -0.091553 | 0.022888 | -0.086975 | -0.11902 | -0.045776 | -0.004578 | -0.050354 | 0.018311 | 0.059509 | 0 | -0.022888 | 8.8348 | -111.882 | -111.9049 | 8.931 | 8.7891 | 8.8211 | -0.045777 | -0.013733 | 8.8577 | -111.8179 | -111.795 | 8.9676 | 8.8852 | 8.9081 | 0.027466 | 0.050354 | 0.09613 | -0.018311 | 0.10986 | 0.068665 | 0.004577 | 0.045776 | 8.8394 | 8.9035 | -111.8866 | -111.8637 | 8.8165 | 8.9264 | 8.8028 | 8.8623
4102.1719 | 121.9803 | -95.018 | 26.3809 | 0.028839 | 0.017564 | -0.029877 | 0.038617 | -0.012499 | -0.029036 | -0.022819 | 0.017761 | -0.061651 | -0.0024608 | 0.031479 | -0.014095 | -0.0096728 | -0.010547 | -0.004578 | -0.050354 | -0.009155 | 0.059509 | 0.1831 | 0.054932 | 0.045776 | 0.086975 | -0.022888 | -0.027466 | 0.07782 | 0.16022 | 0.059509 | 0.16937 | 95.0088 | -26.4313 | -26.3214 | 95.2011 | 95.0638 | 95.0729 | 0.054931 | 0.064087 | 94.9905 | -26.4038 | -26.3031 | 95.1782 | 95.1874 | 95.0775 | 0.19684 | 0.086975 | 0.19226 | 0.068664 | 0.18768 | 0.10529 | -0.041199 | 0.004578 | 94.9677 | 94.9951 | -26.3901 | -26.4084 | 95.0775 | 95.0958 | 95.0134 | 95.105
4103.9375 | 121.5454 | -9.3109 | 112.4359 | 0.01358 | 0.012224 | -0.032441 | 0.037549 | -0.011644 | -0.030531 | -0.019188 | 0.011658 | -0.063574 | -0.00011105 | 0.030839 | -0.018794 | -0.011595 | -0.012683 | -0.09613 | -0.082397 | -0.041199 | -0.050354 | 0.086975 | -0.009155 | -0.004578 | -0.027466 | -0.013733 | -0.064087 | 0.009155 | 0.09613 | 0.032043 | 0.1236 | 9.2697 | -112.5183 | -112.4863 | 9.3979 | 9.3063 | 9.3018 | 0.036621 | 0.032044 | 9.2468 | -112.4496 | -112.4268 | 9.407 | 9.4345 | 9.343 | 0.18768 | 0.09613 | 0.12817 | -0.009155 | 0.16022 | 0.073242 | -0.041198 | 0.050354 | 9.2285 | 9.2972 | -112.4771 | -112.5 | 9.2606 | 9.3201 | 9.2148 | 9.2834
4105.6562 | 121.9299 | -8.5648 | 112.5137 | 0.02121 | 0.014573 | -0.035218 | 0.034344 | -0.016131 | -0.029036 | -0.021965 | -0.034119 | -0.064856 | -0.00053825 | 0.033402 | -0.022853 | -0.01245 | -0.014605 | -0.041199 | -0.086975 | -0.018311 | 0.022888 | 0.15106 | 0.050354 | 0.036621 | 0.009155 | -0.027466 | 0.009155 | 0.013733 | 0.11902 | 0.068665 | -0.013733 | 8.5464 | -112.6007 | -112.4908 | 8.7158 | 8.6014 | 8.6151 | 0.054932 | 0.068665 | 8.5739 | -112.5412 | -112.5 | 8.6838 | 8.551 | 8.6334 | -0.022888 | 0.05951 | 0.16937 | 0.041199 | 0.10986 | 0.004578 | -0.068664 | -0.036621 | 8.4778 | 8.5373 | -112.532 | -112.5046 | 8.5876 | 8.5785 | 8.5236 | 8.5739
4107.375 | 108.2108 | -9.2011 | 102.5253 | 0.01358 | 0.014787 | -0.033082 | 0.034558 | -0.013781 | -0.029676 | -0.025169 | -0.1806 | -0.063361 | 0.00052975 | 0.018876 | -0.020503 | -0.010955 | -0.010974 | -0.14648 | -0.050354 | -0.064087 | -0.11902 | 0.013733 | -0.050354 | -0.25635 | -0.10529 | 0.036621 | 0.013733 | -0.086975 | 0.013733 | -0.1831 | -0.091553 | 9.137 | -102.5757 | -102.6443 | 9.2148 | 8.9447 | 9.1507 | -0.19226 | 0.013733 | 9.2148 | -102.4887 | -102.6123 | 9.2148 | 9.1095 | 9.0179 | -0.10529 | -0.19684 | 0.07782 | -0.054932 | 0 | -0.10071 | 0.013733 | 0.022888 | 9.1507 | 9.2377 | -102.5894 | -102.5116 | 9.082 | 9.1141 | 9.0546 | 9.0958
4109.125 | 121.1792 | -8.3817 | 113.4338 | 0.01358 | 0.013505 | -0.033295 | 0.036694 | -0.016131 | -0.029249 | -0.018119 | 0.0055542 | -0.063361 | -0.0024608 | 0.034684 | -0.019863 | -0.012023 | -0.0094784 | -0.050354 | -0.09613 | -0.032043 | 0.018311 | 0.16022 | 0.068665 | 0.050354 | 0.041199 | -0.032043 | -0.036621 | 0.045776 | 0.16479 | 0.064087 | 0.10529 | 8.3496 | -113.53 | -113.4155 | 8.5419 | 8.432 | 8.4503 | 0.082397 | 0.10071 | 8.345 | -113.4659 | -113.3881 | 8.5464 | 8.4869 | 8.4457 | 0.14191 | 0.10071 | 0.19226 | 0.050354 | 0.20142 | 0.082397 | -0.064087 | 0.004578 | 8.2855 | 8.3496 | -113.4659 | -113.4705 | 8.4 | 8.4274 | 8.3313 | 8.4229
4110.8438 | 100.8774 | -14.1769 | 92.8757 | 0.01358 | 0.015001 | -0.032654 | 0.023236 | -0.020617 | -0.029036 | -0.026878 | -0.22943 | -0.07511 | -0.0048108 | 0.019089 | -0.029903 | -0.025695 | -0.02315 | -0.086975 | -0.068665 | -0.082397 | -0.082397 | 0.018311 | -0.050354 | -0.32501 | -0.09613 | 0.013733 | -0.032043 | -0.032043 | 0.054932 | -0.23346 | 0.022888 | 14.0945 | -92.9443 | -92.9581 | 14.1953 | 13.8519 | 14.1266 | -0.24262 | 0.032043 | 14.1449 | -92.8619 | -92.9077 | 14.2319 | 14.1998 | 13.9435 | 0.054931 | -0.20142 | 0.10071 | 0 | 0.086975 | 0 | 0.013732 | 0.045776 | 14.1083 | 14.1907 | -92.9581 | -92.9077 | 14.0945 | 14.1449 | 14.09 | 14.0808
4112.5781 | 121.2341 | -8.2535 | 113.0264 | 0.01358 | 0.012437 | -0.030945 | 0.034131 | -0.015276 | -0.027754 | -0.022178 | 0.0055542 | -0.062506 | -0.00182 | 0.033829 | -0.018154 | -0.01245 | -0.012256 | -0.054932 | -0.091553 | -0.050354 | 0.013733 | 0.17395 | 0.050354 | 0.050354 | 0.050354 | -0.022888 | -0.050354 | 0.050354 | 0.15106 | 0.07782 | 0.13733 | 8.2031 | -113.118 | -113.0127 | 8.4274 | 8.3038 | 8.3038 | 0.10071 | 0.10071 | 8.2031 | -113.0493 | -112.9761 | 8.4045 | 8.3908 | 8.3313 | 0.18768 | 0.12817 | 0.2243 | 0.064087 | 0.20142 | 0.10071 | -0.041199 | 0.027466 | 8.1619 | 8.2306 | -113.0768 | -113.0768 | 8.2672 | 8.3038 | 8.1985 | 8.3038
4114.3125 | 115.0177 | -8.0887 | 104.4754 | 0.028839 | 0.013933 | -0.033509 | 0.037549 | -0.014849 | -0.029249 | -0.020042 | -0.015808 | -0.062079 | 0.0013844 | 0.030625 | -0.019863 | -0.010527 | -0.011615 | -0.1236 | -0.059509 | -0.059509 | -0.11902 | 0.009155 | -0.07782 | -0.082397 | -0.09613 | 0.013733 | -0.09613 | -0.086975 | 0.009155 | -0.064087 | -0.15564 | 8.0292 | -104.5349 | -104.5944 | 8.0978 | 8.0063 | 8.0109 | -0.022888 | -0.018311 | 7.9926 | -104.4617 | -104.5624 | 8.0978 | 7.933 | 8.0246 | -0.05951 | 0.032043 | 0.068664 | -0.05951 | 0.10528 | 0.009155 | 0 | 0.10986 | 8.0292 | 8.1024 | -104.5349 | -104.5715 | 7.9697 | 8.0017 | 7.9651 | 7.9926
4116.0469 | 121.4905 | -7.7316 | 113.4476 | 0.028839 | 0.014146 | -0.033082 | 0.036267 | -0.016344 | -0.031385 | -0.019828 | 0.008606 | -0.061651 | -0.0016064 | 0.03212 | -0.021358 | -0.014373 | -0.011187 | -0.073242 | -0.10071 | -0.032043 | -0.054932 | 0.07782 | -0.009155 | -0.004578 | -0.054932 | -0.013733 | -0.068665 | -0.07782 | 0.036621 | -0.050354 | 0.009155 | 7.6996 | -113.5483 | -113.5025 | 7.8094 | 7.727 | 7.7225 | 0.027465 | 0.022888 | 7.663 | -113.4613 | -113.5254 | 7.7682 | 7.7408 | 7.6813 | 0.07782 | 0.018311 | 0.10986 | -0.022889 | 0.10529 | -0.009155 | -0.068665 | 0.054932 | 7.6309 | 7.7179 | -113.4796 | -113.5162 | 7.6767 | 7.6538 | 7.6584 | 7.6767
4117.75 | 121.6827 | -7.5302 | 111.7264 | 0.044098 | 0.012437 | -0.033722 | 0.03883 | -0.016344 | -0.031172 | -0.018974 | -0.003601 | -0.060584 | 0.00031615 | 0.02977 | -0.02029 | -0.013091 | -0.010547 | -0.10986 | -0.032043 | -0.10071 | -0.1236 | 0.004578 | -0.068665 | -0.086975 | -0.11902 | 0.022888 | -0.091553 | -0.07782 | 0.004578 | -0.073242 | -0.13275 | 7.4295 | -111.7584 | -111.85 | 7.5348 | 7.4432 | 7.4615 | 0.013733 | 0.032043 | 7.4387 | -111.7035 | -111.8042 | 7.5348 | 7.3975 | 7.457 | -0.041198 | 0.018311 | 0.10529 | -0.022888 | 0.096131 | 0.013733 | 0.068665 | 0.11444 | 7.4982 | 7.5531 | -111.8271 | -111.8179 | 7.4066 | 7.4524 | 7.4203 | 7.4112
4119.4844 | 121.8613 | -7.5577 | 113.6581 | 0.028839 | 0.015641 | -0.033082 | 0.037762 | -0.01549 | -0.030317 | -0.022392 | -0.00054937 | -0.064429 | 0.00010255 | 0.027421 | -0.015804 | -0.0101 | -0.011828 | -0.10529 | -0.068665 | -0.07782 | -0.11444 | -0.041199 | -0.1236 | -0.10071 | -0.10986 | 0.018311 | -0.068665 | -0.073242 | 0.004578 | -0.082397 | -0.036621 | 7.4799 | -113.7268 | -113.7726 | 7.5165 | 7.457 | 7.4341 | -0.022888 | -0.045776 | 7.489 | -113.6398 | -113.7314 | 7.5623 | 7.5211 | 7.4753 | 0.032044 | -0.013732 | 0.036621 | -0.036621 | 0.073243 | -0.004577 | 0.009155 | 0.086976 | 7.489 | 7.576 | -113.736 | -113.7268 | 7.4432 | 7.4844 | 7.4524 | 7.4478
4121.2188 | 121.2067 | -119.2429 | 1.6022 | 0.044098 | 0.019914 | -0.0318 | 0.021527 | -0.023607 | -0.030531 | -0.024101 | -0.034119 | -0.07746 | -0.0011792 | 0.022507 | -0.031825 | -0.019927 | -0.031695 | -0.07782 | 0 | 0.10986 | -0.082397 | -0.022888 | -0.21057 | -0.10071 | -0.068665 | -0.31128 | -0.091553 | -0.23804 | -0.26093 | 0.086975 | 0.086975 | 119.3527 | -1.6022 | -1.6846 | 119.22 | 119.1422 | 119.0323 | -0.21057 | -0.32043 | 119.1513 | -1.9135 | -1.8402 | 118.9819 | 119.3298 | 119.3298 | 0.17853 | 0.17853 | -0.13275 | -0.19226 | -0.16937 | -0.14648 | -0.10986 | -0.21973 | 119.2429 | 118.9316 | -1.4923 | -1.6937 | 119.1605 | 119.0048 | 119.165 | 119.1742
4123 | 121.5637 | -120.0119 | 1.3596 | 0.0059509 | 0.014787 | -0.0318 | 0.034772 | -0.01784 | -0.030317 | -0.020683 | -0.22943 | -0.06272 | 0.00074335 | 0.025712 | -0.019435 | -0.013091 | -0.012256 | -0.10529 | -0.022888 | -0.036621 | -0.09613 | 0.045776 | -0.091553 | -0.37079 | -0.09613 | 0.022888 | 0.31128 | -0.009155 | -0.10071 | -0.3479 | -0.050354 | 119.9753 | -1.3824 | -1.4557 | 120.0577 | 119.6411 | 119.9203 | -0.33417 | -0.054932 | 120.3232 | -1.3367 | -1.3687 | 119.9112 | 119.9615 | 119.664 | -0.36163 | -0.65918 | 0.082397 | -0.059509 | -0.41199 | -0.32043 | 0.013733 | -0.28839 | 119.989 | 120.0348 | -1.3962 | -1.0483 | 119.9158 | 120.0027 | 119.9066 | 119.9158
4124.7031 | 121.6095 | -120.163 | 1.3046 | 0.0059509 | 0.015214 | -0.032868 | 0.023236 | -0.030871 | -0.027113 | -0.029655 | -0.034119 | 0.015039 | -0.0043834 | 0.015671 | 0.023289 | 0.028352 | 0.019147 | -0.050354 | -0.032043 | -0.009155 | -0.050354 | 0 | -0.24719 | -0.12817 | -0.022888 | 0.032043 | 0.14648 | 0.018311 | -0.12817 | -0.14191 | 0.091553 | 120.1538 | -1.3367 | -1.355 | 120.163 | 120.0348 | 119.9158 | -0.11902 | -0.23804 | 120.3094 | -1.2726 | -1.2863 | 120.0348 | 120.2545 | 120.0211 | -0.054931 | -0.28839 | 0.009155 | -0.041199 | -0.27466 | -0.12817 | -0.022888 | -0.11444 | 120.1309 | 120.195 | -1.3138 | -1.1581 | 120.1126 | 120.1813 | 120.1126 | 120.1401
4126.4688 | 121.756 | -120.6573 | 0.82398 | 0.02121 | 0.012224 | -0.032868 | 0.036267 | -0.014208 | -0.028181 | -0.019615 | 0.011658 | -0.062292 | -0.0037426 | 0.035325 | -0.017085 | -0.0101 | -0.0094784 | -0.059509 | -0.054932 | 0 | -0.004578 | 0.15106 | 0.059509 | 0.07782 | 0.050354 | -0.004578 | -0.032043 | 0.091553 | 0.15564 | 0.10529 | 0.19684 | 120.6573 | -0.87891 | -0.82855 | 120.8084 | 120.7352 | 120.7169 | 0.07782 | 0.059509 | 120.6253 | -0.82855 | -0.73242 | 120.813 | 120.8542 | 120.7626 | 0.22888 | 0.13733 | 0.15106 | -0.004578 | 0.18768 | 0.1236 | -0.054932 | 0.027465 | 120.6024 | 120.6528 | -0.82398 | -0.85602 | 120.6528 | 120.7489 | 120.5978 | 120.7077
4128.1719 | 121.7926 | -120.7169 | 0.80566 | 0.01358 | 0.012864 | -0.033295 | 0.036694 | -0.01549 | -0.031599 | -0.021324 | 0.0055542 | -0.062292 | -0.0022472 | 0.039811 | -0.018367 | -0.0101 | -0.013537 | -0.054932 | -0.054932 | 0.022888 | -0.004578 | 0.14191 | 0.041199 | 0.068665 | 0.050354 | -0.013733 | -0.013733 | 0.086975 | 0.14191 | 0.09613 | 0.19226 | 120.7397 | -0.8606 | -0.81024 | 120.8588 | 120.7855 | 120.7581 | 0.045777 | 0.018311 | 120.7031 | -0.8194 | -0.71869 | 120.8588 | 120.9091 | 120.813 | 0.20599 | 0.10986 | 0.11902 | -0.027466 | 0.15564 | 0.10071 | -0.07782 | 0 | 120.6619 | 120.7031 | -0.78278 | -0.8194 | 120.7123 | 120.8038 | 120.6619 | 120.7672
4129.9375 | 121.6232 | -120.9824 | 0.6546 | 0.01358 | 0.014573 | -0.033295 | 0.036267 | -0.016344 | -0.031813 | -0.023033 | -0.00054937 | -0.059943 | -0.0028882 | 0.033188 | -0.020931 | -0.011595 | -0.012469 | -0.036621 | -0.036621 | -0.032043 | -0.059509 | 0.073242 | 0 | -0.018311 | -0.050354 | 0.022888 | -0.004578 | -0.022888 | 0.041199 | -0.013733 | -0.054932 | 120.9503 | -0.69122 | -0.71411 | 121.0556 | 120.9641 | 120.9824 | 0.013732 | 0.032043 | 120.9778 | -0.63171 | -0.67749 | 121.0236 | 120.9274 | 120.9686 | -0.050354 | -0.009155 | 0.10529 | -0.027466 | 0.045777 | -0.01831 | -0.004578 | 0.027466 | 120.9457 | 121.0052 | -0.68665 | -0.65918 | 120.9229 | 120.9595 | 120.9457 | 120.932
4131.6406 | 121.7239 | -120.9503 | 0.62714 | 0.02121 | 0.016923 | -0.0318 | 0.036908 | -0.012499 | -0.028608 | -0.018119 | -0.098206 | -0.071905 | -0.0028882 | 0.029557 | -0.022853 | -0.015441 | -0.016314 | -0.045776 | -0.027466 | -0.032043 | -0.041199 | 0.073242 | 0.004578 | -0.18768 | -0.004578 | 0.054932 | -0.027466 | 0.027466 | 0.09613 | -0.054932 | -0.24261 | 120.9183 | -0.6546 | -0.66834 | 121.0236 | 120.7626 | 120.9549 | -0.15564 | 0.036621 | 120.9229 | -0.5722 | -0.59967 | 121.0464 | 120.7077 | 120.8954 | -0.21515 | -0.027466 | 0.10529 | -0.009156 | 0.1236 | 0.054932 | 0.004577 | 0.082398 | 120.9229 | 121.0052 | -0.65918 | -0.6546 | 120.9091 | 120.9778 | 120.9045 | 120.9457
4133.375 | 121.7834 | -120.9686 | 0.59509 | 0.01358 | 0.013292 | -0.032013 | 0.03883 | -0.012072 | -0.028181 | -0.021965 | 0.0055542 | -0.061011 | -0.0013928 | 0.036179 | -0.015377 | -0.0088184 | -0.014178 | -0.064087 | -0.036621 | 0 | -0.045776 | 0.073242 | -0.027466 | 0 | 0.013733 | 0.018311 | -0.018311 | 0.086975 | 0.12817 | 0.045776 | 0.18768 | 120.9686 | -0.63171 | -0.64087 | 121.0419 | 120.9686 | 120.9412 | 0 | -0.027466 | 120.9503 | -0.57678 | -0.50812 | 121.0968 | 121.1563 | 121.0144 | 0.20599 | 0.064087 | 0.073242 | -0.045776 | 0.14649 | 0.10529 | -0.036621 | 0.036622 | 120.932 | 120.9869 | -0.59509 | -0.6134 | 120.9229 | 121.0556 | 120.9045 | 120.9824
4135.1094 | 121.7377 | -120.9045 | 0.72784 | 0.028839 | 0.015001 | -0.032654 | 0.036908 | -0.012713 | -0.026686 | -0.024101 | -0.064636 | -0.067847 | -0.00096545 | 0.034043 | -0.016658 | -0.014159 | -0.012683 | -0.027466 | -0.032043 | -0.022888 | -0.032043 | 0.09613 | 0 | -0.10529 | 0.018311 | 0.032043 | -0.018311 | 0.041199 | 0.10529 | 0.018311 | -0.10529 | 120.8817 | -0.75989 | -0.75989 | 121.0007 | 120.7993 | 120.9045 | -0.082398 | 0.022888 | 120.8862 | -0.6958 | -0.68665 | 121.0098 | 120.7993 | 120.9229 | -0.086975 | 0.036622 | 0.11902 | -0.009155 | 0.1236 | 0.05951 | -0.009155 | 0.050354 | 120.8725 | 120.9366 | -0.75073 | -0.74616 | 120.8725 | 120.9457 | 120.8771 | 120.9229
4136.8125 | 121.6736 | -121.0236 | 0.63171 | 0.02121 | 0.017564 | -0.030732 | 0.039258 | -0.012072 | -0.029036 | -0.023674 | -0.0097046 | -0.058875 | -0.00075185 | 0.039384 | -0.017513 | -0.012023 | -0.013965 | -0.091553 | -0.032043 | -0.013733 | -0.082397 | 0.004578 | -0.082397 | -0.082397 | -0.091553 | 0.050354 | -0.041199 | -0.027466 | 0.013733 | -0.086975 | 0.050354 | 121.0098 | -0.66376 | -0.71411 | 121.0281 | 120.9412 | 120.9412 | -0.068664 | -0.068664 | 120.9824 | -0.58136 | -0.65918 | 121.0373 | 121.0739 | 120.9366 | 0.091553 | -0.045776 | 0.018311 | -0.068664 | 0.054932 | 0.013733 | -0.01831 | 0.091553 | 120.9915 | 121.0739 | -0.64545 | -0.67291 | 120.9412 | 120.9961 | 120.932 | 120.932
4138.5938 | 121.8109 | -120.9549 | 0.62256 | 0.028839 | 0.014573 | -0.033295 | 0.037335 | -0.013353 | -0.029676 | -0.023033 | 0.014709 | -0.062292 | 0.00031615 | 0.031693 | -0.016872 | -0.0094592 | -0.01311 | -0.022888 | -0.068665 | 0.009155 | 0.027466 | 0.16937 | 0.032043 | 0.059509 | 0.059509 | 0.009155 | -0.018311 | 0.059509 | 0.12817 | 0.054932 | 0.15564 | 120.9641 | -0.69122 | -0.59509 | 121.1243 | 121.0144 | 120.9869 | 0.050354 | 0.022888 | 120.9366 | -0.6134 | -0.56305 | 121.0831 | 121.1105 | 121.0098 | 0.17395 | 0.073243 | 0.16022 | 0.018311 | 0.14649 | 0.07782 | -0.07782 | 0.027466 | 120.8862 | 120.9641 | -0.6134 | -0.64087 | 120.9824 | 121.0144 | 120.932 | 121.0144
4140.3281 | 121.8201 | -120.8542 | 0.737 | 0.0059509 | 0.013292 | -0.031586 | 0.038189 | -0.013353 | -0.028181 | -0.022605 | 0.0055542 | -0.060156 | -0.00053825 | 0.040452 | -0.015163 | -0.0094592 | -0.010119 | -0.064087 | -0.041199 | -0.009155 | -0.032043 | 0.082397 | -0.013733 | -0.004578 | 0.027466 | 0.013733 | 0.004578 | 0.073242 | 0.13733 | 0.064087 | 0.1831 | 120.845 | -0.7782 | -0.76904 | 120.9366 | 120.8496 | 120.8405 | 0.004577 | -0.004578 | 120.8588 | -0.72327 | -0.66376 | 120.9915 | 121.0373 | 120.9183 | 0.17853 | 0.059509 | 0.091552 | -0.022888 | 0.13275 | 0.068664 | -0.032044 | 0.009155 | 120.813 | 120.8679 | -0.74616 | -0.73242 | 120.8221 | 120.9274 | 120.7901 | 120.8817
4142.0625 | 121.7972 | -120.3278 | 1.2451 | 0.02121 | 0.012224 | -0.030732 | 0.037121 | -0.012499 | -0.029676 | -0.020897 | 0.008606 | -0.061651 | -0.0054516 | 0.034684 | -0.016017 | -0.0094592 | -0.010547 | -0.027466 | -0.054932 | -0.013733 | 0.004578 | 0.14191 | 0.027466 | 0.045776 | 0.068665 | 0.013733 | 0 | 0.10071 | 0.16479 | 0.059509 | 0.19684 | 120.314 | -1.3 | -1.2405 | 120.4697 | 120.3735 | 120.3552 | 0.059509 | 0.041199 | 120.3278 | -1.2314 | -1.1444 | 120.4926 | 120.5246 | 120.3873 | 0.19684 | 0.059509 | 0.15564 | 0.018311 | 0.16479 | 0.10071 | -0.041199 | 0.013733 | 120.2728 | 120.3415 | -1.2589 | -1.2451 | 120.3323 | 120.4285 | 120.3003 | 120.3964
4143.7812 | 121.9574 | -120.9183 | 0.68207 | 0.0059509 | 0.010728 | -0.037354 | 0.034985 | -0.018694 | -0.032026 | -0.023033 | 0.008606 | -0.061865 | -0.00182 | 0.035538 | -0.021144 | -0.011595 | -0.013537 | 0 | -0.064087 | 0 | 0.036621 | 0.20599 | 0.086975 | 0.082397 | 0.10529 | -0.004578 | -0.004578 | 0.091553 | 0.1831 | 0.13275 | 0.18768 | 120.9183 | -0.74616 | -0.64545 | 121.1243 | 121.0007 | 121.0052 | 0.082397 | 0.086975 | 120.9137 | -0.68665 | -0.59052 | 121.1014 | 121.106 | 121.051 | 0.19226 | 0.13733 | 0.20599 | 0.036621 | 0.18768 | 0.096131 | -0.064087 | 0 | 120.8542 | 120.9137 | -0.68207 | -0.68665 | 120.9549 | 121.0098 | 120.9183 | 121.0236
4145.5 | 117.1097 | -67.6254 | 48.0927 | 0.028839 | 0.01201 | -0.034363 | 0.034344 | -0.014635 | -0.030958 | -0.022819 | 0.011658 | -0.061865 | -0.0011792 | 0.036179 | -0.019008 | -0.010955 | -0.013537 | 0 | -0.064087 | -0.009155 | 0.027466 | 0.19226 | 0.07782 | 0.068665 | 0.091553 | -0.032043 | -0.013733 | 0.064087 | 0.19226 | 0.10529 | 0.16479 | 67.6163 | -48.1567 | -48.0652 | 67.8177 | 67.6941 | 67.7032 | 0.07782 | 0.086975 | 67.6117 | -48.1247 | -48.0286 | 67.8177 | 67.7902 | 67.7307 | 0.17853 | 0.11902 | 0.20142 | 0.036621 | 0.20599 | 0.07782 | -0.054932 | -0.01831 | 67.5613 | 67.5934 | -48.1018 | -48.1064 | 67.6529 | 67.6895 | 67.6254 | 67.717
4147.2031 | 116.2445 | -66.0278 | 51.1459 | 0.13565 | 0.00966 | -0.0318 | 0.038403 | -0.025744 | -0.029036 | -0.027305 | 0.048279 | -0.065283 | -0.0099376 | 0.02208 | -0.034603 | -0.021849 | -0.025927 | -0.10071 | -0.036621 | 0.16937 | -0.082397 | 0.004578 | -0.27924 | 0.09613 | -0.082397 | -0.032043 | -0.091553 | -0.009155 | 0.018311 | -0.37537 | 0.086975 | 66.1972 | -51.1826 | -51.2283 | 66.0324 | 66.124 | 65.7486 | -0.073243 | -0.44861 | 65.9363 | -51.178 | -51.1551 | 66.0461 | 66.1148 | 65.6525 | 0.17853 | -0.28381 | -0.16479 | -0.25177 | 0.10986 | 0.082398 | -0.20599 | 0.05951 | 65.9912 | 65.9958 | -50.9766 | -51.2375 | 65.9454 | 66.0187 | 65.9271 | 65.9454
4148.9375 | 120.9183 | -98.1445 | 22.3755 | 0.0059509 | 0.018205 | -0.029236 | 0.033276 | -0.012072 | -0.026472 | -0.020256 | -0.22943 | -0.060584 | 0.0037342 | 0.035752 | -0.015377 | -0.011168 | -0.0090512 | -0.16022 | -0.041199 | 0.18768 | -0.27008 | -0.21973 | -0.32044 | -0.20142 | -0.082397 | -0.33875 | 0.16937 | 0 | -0.082397 | -0.18768 | -0.073242 | 98.3322 | -22.4167 | -22.6456 | 97.9248 | 97.9431 | 97.8241 | -0.3891 | -0.50812 | 98.3139 | -22.7142 | -22.3755 | 98.0621 | 98.0713 | 97.9568 | -0.24261 | -0.35706 | -0.40741 | -0.45776 | -0.25177 | -0.16937 | -0.22888 | -0.50812 | 98.1033 | 97.8058 | -22.1878 | -22.2061 | 97.8744 | 98.1445 | 97.9843 | 98.0621
4150.7188 | 121.1243 | -119.7052 | 1.0025 | 0.01358 | 0.015214 | -0.030091 | 0.0044369 | 0.026808 | 0.033983 | 0.029091 | 0.054382 | 0.015893 | 0.011852 | 0.022294 | 0.023503 | 0.028138 | 0.019574 | 0.086975 | -0.045776 | 0.31128 | 0.091553 | 0.10071 | 0.09613 | 0.086975 | 0.091553 | 0.09613 | -0.091553 | -0.32501 | 0.09613 | 0.09613 | 0.091553 | 120.0165 | -1.0483 | -0.91095 | 119.8059 | 119.7922 | 119.8013 | -0.2243 | -0.21515 | 119.6136 | -0.90637 | -1.3275 | 119.8013 | 119.7968 | 119.8013 | 0.18311 | 0.18768 | -0.21057 | -0.21973 | 0.18768 | -0.23346 | -0.35705 | 0.18768 | 119.6594 | 119.8013 | -0.69122 | -1.0941 | 119.7968 | 119.3802 | 119.7922 | 119.7968
4152.4844 | 120.4788 | -105.2719 | 14.0762 | -0.0016786 | 0.014787 | 0.17435 | 0.032208 | -0.018908 | -0.029463 | -0.021965 | -0.23859 | -0.06272 | 0.046672 | 0.037461 | -0.018794 | -0.0098864 | -0.01076 | -0.10529 | -0.064087 | 0.16022 | -0.14648 | -0.17395 | -0.29297 | -0.17853 | 0 | 0.20142 | -0.091553 | 0.073242 | -0.082397 | -0.27008 | -0.18768 | 105.4321 | -14.1403 | -14.2227 | 105.098 | 105.0934 | 104.9789 | -0.33874 | -0.45319 | 105.1804 | -13.8748 | -14.003 | 105.1895 | 105.0842 | 105.0018 | -0.09613 | -0.17853 | -0.33417 | -0.3067 | 0.009156 | 0.16479 | -0.2243 | 0.29297 | 105.2078 | 105.4733 | -13.916 | -14.1678 | 105.1254 | 105.3452 | 105.1666 | 105.2719
4154.2188 | 120.6802 | -119.2703 | 0.91095 | 0.01358 | 0.011369 | -0.033082 | 0.036908 | -0.013781 | -0.029676 | -0.019615 | -0.13483 | -0.064642 | -0.004597 | 0.03682 | -0.019649 | -0.012236 | -0.016528 | -0.050354 | -0.064087 | 0.036621 | 0 | 0.004578 | -0.10986 | -0.18768 | 0.059509 | -0.16937 | 0.31128 | 0.07782 | 0.086975 | -0.054932 | 0.004578 | 119.3069 | -0.97504 | -0.91095 | 119.2749 | 119.0826 | 119.1605 | -0.2243 | -0.14648 | 119.5816 | -1.0803 | -0.83313 | 119.3573 | 119.2749 | 119.2154 | -0.3067 | -0.36621 | -0.032043 | -0.036621 | -0.2243 | -0.23346 | -0.10071 | -0.48065 | 119.2062 | 119.101 | -0.87433 | -0.59967 | 119.2703 | 119.3481 | 119.22 | 119.3298
4155.9844 | 120.2316 | -46.55 | 72.8027 | 0.0059509 | 0.015641 | -0.032441 | 0.035626 | -0.016771 | -0.030317 | -0.021965 | -0.092102 | -0.06037 | -0.0020336 | 0.033402 | -0.017513 | -0.012664 | -0.014605 | -0.10071 | -0.091553 | -0.027466 | -0.036621 | 0.064087 | -0.041199 | -0.073242 | 0.018311 | -0.086975 | 0.22888 | 0.054932 | 0.12817 | 0.059509 | 0.14191 | 46.5225 | -72.8943 | -72.8394 | 46.6141 | 46.4767 | 46.5088 | -0.045776 | -0.013733 | 46.7789 | -72.8897 | -72.7478 | 46.6782 | 46.6919 | 46.6095 | -0.086975 | -0.16937 | 0.091553 | -0.009155 | -0.10071 | -0.17395 | -0.064087 | -0.31586 | 46.4584 | 46.463 | -72.8302 | -72.5739 | 46.5134 | 46.6049 | 46.4493 | 46.5683
4157.6875 | 120.5063 | -119.3893 | 0.59509 | 0.02121 | 0.012864 | -0.031586 | 0.03584 | -0.01079 | -0.027327 | -0.021324 | -0.21112 | -0.062506 | -0.0026744 | 0.040452 | -0.014949 | -0.010527 | -0.012683 | -0.032043 | -0.068665 | 0.013733 | -0.045776 | -0.13733 | -0.27466 | -0.31128 | 0.082397 | -0.032043 | 0.27008 | 0.1236 | 0.09613 | -0.09613 | 0.018311 | 119.4031 | -0.66376 | -0.64087 | 119.252 | 119.0781 | 119.1147 | -0.32501 | -0.28839 | 119.6594 | -0.62714 | -0.4715 | 119.4855 | 119.4077 | 119.2932 | -0.25177 | -0.36621 | -0.15106 | -0.059509 | -0.17395 | -0.14649 | -0.082398 | -0.30212 | 119.3207 | 119.3573 | -0.58136 | -0.32501 | 119.3436 | 119.5129 | 119.3573 | 119.4717
4159.4062 | 120.6711 | -119.3802 | 0.82398 | 0.036468 | 0.011796 | -0.028595 | 0.034131 | -0.014208 | -0.029249 | -0.021751 | -0.07074 | -0.059943 | -0.0016064 | 0.037034 | -0.018581 | -0.011382 | -0.011401 | -0.041199 | -0.050354 | 0.009155 | 0.004578 | 0.064087 | -0.073242 | -0.12817 | 0.054932 | -0.004578 | 0.23804 | 0.036621 | 0.11444 | 0.013733 | 0.10986 | 119.3893 | -0.87433 | -0.8194 | 119.4443 | 119.252 | 119.3069 | -0.13733 | -0.082397 | 119.6182 | -0.82855 | -0.78735 | 119.4946 | 119.4901 | 119.3939 | -0.12817 | -0.2243 | 0.054932 | -0.004577 | -0.1236 | -0.20142 | -0.059509 | -0.24261 | 119.3298 | 119.3756 | -0.81482 | -0.58594 | 119.3848 | 119.4168 | 119.339 | 119.4351
4161.1406 | 120.7718 | -120.0485 | 0.5127 | 0.02121 | 0.015214 | -0.030945 | 0.029431 | -0.027453 | -0.02989 | -0.037773 | 0.048279 | -0.068488 | -0.00053825 | 0.031052 | -0.028621 | -0.029326 | -0.025287 | -0.09613 | -0.018311 | -0.018311 | 0.086975 | 0.09613 | 0.091553 | 0.09613 | -0.11444 | -0.12817 | 0.054932 | 0 | -0.21515 | 0.086975 | 0.086975 | 120.0302 | -0.53101 | -0.42572 | 120.1447 | 120.1447 | 120.1401 | 0.11444 | 0.10986 | 120.1035 | -0.64087 | -0.5127 | 119.8334 | 120.1355 | 120.1355 | 0.032043 | 0.032043 | 0.11444 | 0.10529 | -0.27008 | -0.054932 | 0 | -0.18311 | 120.0302 | 119.9203 | -0.53101 | -0.45776 | 120.1355 | 120.0485 | 119.9524 | 119.9341
4162.9531 | 116.8396 | -70.6467 | 45.7718 | 0.13565 | 0.0083784 | -0.032868 | 0.025586 | -0.018267 | -0.030104 | -0.018119 | 0.045227 | -0.06742 | -0.00032465 | 0.03682 | -0.016231 | -0.0101 | -0.013537 | -0.1236 | -0.041199 | 0.004578 | -0.20142 | 0.091553 | 0.07782 | 0.091553 | -0.050354 | -0.14648 | 0.28839 | 0.022888 | -0.20599 | -0.32959 | -0.07782 | 70.6512 | -45.813 | -45.9732 | 70.7382 | 70.7382 | 70.7245 | 0.086975 | 0.073242 | 70.9351 | -45.9183 | -45.7489 | 70.4407 | 70.5688 | 70.3171 | -0.36621 | -0.61798 | 0.086975 | -0.20599 | -0.49439 | -0.2655 | -0.045777 | -0.43488 | 70.6055 | 70.5002 | -45.7672 | -45.4834 | 70.4453 | 70.6696 | 70.5231 | 70.5963
4164.6875 | 119.8242 | -96.4188 | 22.9431 | 0.16617 | 0.014573 | -0.035859 | 0.0052915 | 0.026808 | -0.039076 | 0.02845 | 0.057434 | 0.01568 | -0.0016064 | 0.028061 | -0.033748 | -0.020781 | 0.013379 | -0.20599 | -0.018311 | 0.11444 | 0.09613 | 0.086975 | 0.10071 | 0.09613 | -0.2243 | -0.027466 | -0.09613 | -0.25635 | 0.091553 | 0.091553 | 0.09613 | 96.5332 | -22.9614 | -22.847 | 96.5057 | 96.5149 | 96.5195 | -0.018311 | -0.013733 | 96.3226 | -22.9706 | -23.1995 | 96.5103 | 96.5149 | 96.5103 | 0.19226 | 0.18768 | -0.027466 | -0.018311 | 0.18768 | -0.16022 | -0.13275 | 0.068664 | 96.4005 | 96.3913 | -22.8287 | -23.0392 | 96.5149 | 96.1624 | 96.2128 | 96.1945
4166.4219 | 120.7214 | -119.87 | 0.56305 | 0.028839 | 0.014573 | -0.033082 | 0.029004 | -0.018053 | -0.031385 | -0.020256 | 0.045227 | -0.073614 | -0.00032465 | 0.02208 | -0.027553 | -0.021208 | -0.026996 | -0.10071 | -0.013733 | -0.036621 | -0.25177 | 0.086975 | 0.09613 | 0.09613 | -0.064087 | -0.16022 | 0.027466 | 0 | -0.28381 | 0.091553 | 0.09613 | 119.8334 | -0.57678 | -0.81482 | 119.957 | 119.9661 | 119.9661 | 0.13275 | 0.13275 | 119.8975 | -0.72327 | -0.56305 | 119.5862 | 119.9661 | 119.9615 | 0.068664 | 0.064087 | 0.1236 | -0.21515 | -0.31128 | -0.027466 | 0.022888 | -0.18768 | 119.8563 | 119.7098 | -0.59967 | -0.53558 | 119.6182 | 119.87 | 119.7693 | 119.8059
4168.1562 | 120.7672 | -120.0577 | 0.54932 | 0.01358 | 0.015001 | -0.031159 | 0.034985 | -0.015703 | -0.028822 | -0.020683 | 0.048279 | -0.070624 | -0.0039562 | 0.029343 | -0.01559 | -0.011595 | -0.015887 | -0.10071 | -0.022888 | -0.036621 | -0.39368 | -0.059509 | -0.32501 | 0.09613 | -0.073242 | 0.045776 | 0.15106 | 0.009155 | -0.054932 | -0.42114 | 0.018311 | 120.0211 | -0.5722 | -0.94299 | 119.9982 | 120.1538 | 119.7327 | 0.13275 | -0.28839 | 120.2087 | -0.50354 | -0.54016 | 120.0027 | 120.076 | 119.6365 | -0.13275 | -0.5722 | -0.022888 | -0.35706 | -0.20599 | -0.14191 | 0.013733 | -0.10529 | 120.0348 | 120.1035 | -0.58594 | -0.39825 | 119.664 | 120.0668 | 119.957 | 119.9844
4169.9219 | 120.1218 | -119.1101 | 0.60883 | 0.02121 | 0.0092328 | -0.027314 | 0.034985 | -0.011858 | -0.028822 | -0.020256 | -0.067688 | -0.063788 | -0.0016064 | 0.038315 | -0.017726 | -0.010314 | -0.013324 | -0.086975 | -0.059509 | 0.022888 | -0.022888 | 0.045776 | -0.064087 | -0.10986 | 0.009155 | 0 | 0.21515 | 0.054932 | 0.086975 | 0.041199 | 0.12817 | 119.133 | -0.66834 | -0.63171 | 119.1559 | 119.0002 | 119.046 | -0.13275 | -0.086975 | 119.3253 | -0.60883 | -0.55389 | 119.1971 | 119.2383 | 119.1513 | -0.086975 | -0.17395 | 0.022888 | -0.045776 | -0.12817 | -0.16022 | -0.082397 | -0.21515 | 119.0506 | 119.1101 | -0.58594 | -0.39368 | 119.0872 | 119.165 | 119.0231 | 119.1193
4171.625 | 120.2866 | -117.9474 | 1.8356 | 0.02121 | 0.010301 | -0.030518 | 0.034558 | -0.01314 | -0.031385 | -0.021965 | -0.076843 | -0.061011 | -0.00182 | 0.034043 | -0.016445 | -0.011168 | -0.011615 | -0.059509 | -0.059509 | 0.013733 | 0.018311 | 0.11444 | -0.004578 | -0.059509 | 0.09613 | -0.09613 | 0.32044 | 0.09613 | 0.1831 | 0.086975 | 0.15564 | 117.9611 | -1.8951 | -1.8173 | 118.0618 | 117.8879 | 117.9428 | -0.073242 | -0.018311 | 118.2678 | -1.9318 | -1.7395 | 118.1305 | 118.103 | 118.0344 | -0.1648 | -0.23346 | 0.10071 | 0.004578 | -0.13733 | -0.22431 | -0.073242 | -0.41657 | 117.8879 | 117.8513 | -1.8219 | -1.5152 | 117.9657 | 118.0435 | 117.8879 | 118.0435
4173.3438 | 120.6436 | -115.8646 | 4.4312 | 0.0059509 | 0.012224 | -0.033509 | 0.036267 | -0.013567 | -0.030317 | -0.021537 | -0.24164 | -0.060797 | -0.00053825 | 0.034897 | -0.021572 | -0.010314 | -0.0081968 | -0.041199 | -0.032043 | 0.11902 | -0.10071 | -0.16479 | -0.3067 | -0.34332 | -0.045776 | -0.10986 | 0.07782 | 0.004578 | -0.041199 | -0.31586 | -0.2655 | 115.9836 | -4.4632 | -4.5319 | 115.6998 | 115.5212 | 115.5579 | -0.46234 | -0.42572 | 115.9424 | -4.541 | -4.4266 | 115.8234 | 115.5991 | 115.5487 | -0.34332 | -0.39368 | -0.28381 | -0.21973 | -0.11902 | -0.073242 | -0.15106 | -0.18768 | 115.8325 | 115.7547 | -4.3121 | -4.3533 | 115.7639 | 115.8691 | 115.8234 | 115.8188
4175.0625 | 120.7626 | -116.3361 | 4.0924 | 0.01358 | 0.015428 | -0.032868 | 0.031354 | -0.016131 | -0.028608 | -0.024742 | -0.043274 | -0.064215 | 0.00010255 | 0.038315 | -0.016231 | -0.011809 | -0.012683 | -0.09613 | -0.036621 | -0.022888 | -0.20599 | -0.2655 | -0.13275 | 0.10071 | -0.054932 | 0.018311 | 0.091553 | 0.045776 | 0.036621 | -0.3067 | -0.23346 | 116.3132 | -4.129 | -4.2984 | 116.0706 | 116.4368 | 116.2033 | 0.1236 | -0.10986 | 116.4276 | -4.0741 | -4.0466 | 116.3727 | 116.1026 | 116.0294 | -0.32501 | -0.39825 | -0.24261 | -0.18311 | -0.054932 | -0.045777 | -0.013733 | -0.073242 | 116.2994 | 116.3544 | -4.1153 | -4.0009 | 116.1301 | 116.3818 | 116.2399 | 116.2811
4176.7812 | 120.8542 | -118.0664 | 2.4353 | 0.028839 | 0.013505 | -0.030945 | 0.038617 | -0.017412 | -0.029463 | -0.020256 | -0.095154 | -0.061011 | -0.0013928 | 0.036393 | -0.017513 | -0.012023 | -0.013965 | -0.004578 | -0.050354 | -0.004578 | 0.036621 | 0.16479 | -0.013733 | -0.11444 | 0.091553 | 0.009155 | -0.004578 | 0.10986 | 0.13733 | 0.082397 | 0.15564 | 118.0618 | -2.4857 | -2.3987 | 118.2312 | 117.952 | 118.0527 | -0.10986 | -0.009155 | 118.0618 | -2.4261 | -2.3254 | 118.2037 | 118.222 | 118.1488 | 0.16022 | 0.086975 | 0.16937 | 0.041199 | 0.14191 | 0.11444 | -0.045776 | 0.013733 | 118.0161 | 118.0756 | -2.4399 | -2.4399 | 118.103 | 118.1763 | 118.0618 | 118.158
4178.5 | 120.8954 | -118.0481 | 2.4353 | 0.036468 | 0.013078 | -0.031373 | 0.037762 | -0.012713 | -0.029463 | -0.023887 | -0.07074 | -0.061438 | -0.0022472 | 0.038956 | -0.016445 | -0.0081774 | -0.010974 | -0.013733 | -0.059509 | 0.004578 | 0.032043 | 0.17853 | -0.036621 | -0.10529 | 0.07782 | 0 | -0.004578 | 0.10529 | 0.11444 | 0.045776 | 0.13275 | 118.0527 | -2.4948 | -2.4033 | 118.2266 | 117.9428 | 118.0115 | -0.10986 | -0.041199 | 118.0435 | -2.4353 | -2.33 | 118.1625 | 118.1808 | 118.0939 | 0.13733 | 0.050354 | 0.17395 | 0.027465 | 0.11902 | 0.10986 | -0.064087 | 0.004578 | 117.9886 | 118.0481 | -2.4307 | -2.4399 | 118.0801 | 118.1534 | 118.0344 | 118.1259
4180.2188 | 120.9915 | -118.3502 | 2.2156 | 0.01358 | 0.015214 | -0.030304 | 0.038189 | -0.013353 | -0.029249 | -0.019828 | -0.15924 | -0.063361 | -0.0028882 | 0.032761 | -0.016231 | -0.012236 | -0.0071286 | 0.004578 | -0.064087 | 0.009155 | 0.032043 | 0.1236 | -0.10071 | -0.24261 | 0.073242 | 0.013733 | -0.013733 | 0.14648 | 0.14191 | 0.068665 | 0.11444 | 118.3594 | -2.2797 | -2.1835 | 118.4738 | 118.1076 | 118.2495 | -0.25177 | -0.10986 | 118.3365 | -2.2018 | -2.0691 | 118.4921 | 118.4647 | 118.4189 | 0.12817 | 0.082398 | 0.11444 | 0.022888 | 0.15564 | 0.16022 | -0.073242 | 0.027466 | 118.2861 | 118.364 | -2.2064 | -2.2293 | 118.3823 | 118.4967 | 118.3548 | 118.4235
4181.9844 | 120.8817 | -118.5699 | 2.092 | 0.02121 | 0.015428 | -0.035218 | 0.037335 | -0.012926 | -0.028181 | -0.021537 | -0.18671 | -0.06272 | -0.0033154 | 0.034043 | -0.016658 | -0.0088184 | -0.011401 | -0.091553 | -0.032043 | -0.027466 | -0.086975 | -0.050354 | -0.36163 | -0.16022 | -0.050354 | 0.036621 | -0.045776 | 0.059509 | 0.041199 | -0.018311 | -0.054932 | 118.5425 | -2.124 | -2.179 | 118.5196 | 118.4097 | 118.2083 | -0.13275 | -0.33417 | 118.5242 | -2.0554 | -2.0325 | 118.6111 | 118.515 | 118.5516 | -0.009156 | 0.027465 | -0.022888 | -0.059509 | 0.086975 | 0.10528 | -0.004577 | 0.082397 | 118.5379 | 118.6066 | -2.1194 | -2.1378 | 118.483 | 118.6295 | 118.4784 | 118.5196
4183.6875 | 120.9091 | -118.959 | 1.7349 | 0.028839 | 0.015001 | -0.034363 | 0.038189 | -0.011644 | -0.030317 | -0.022819 | 0.051331 | -0.079382 | -0.0013928 | 0.036393 | -0.019008 | -0.012236 | -0.014605 | -0.059509 | -0.009155 | -0.027466 | -0.064087 | -0.07782 | -0.37537 | 0.10071 | -0.059509 | 0.054932 | -0.050354 | 0.022888 | 0.064087 | -0.022888 | -0.24261 | 118.9316 | -1.7441 | -1.799 | 118.8812 | 119.0598 | 118.5837 | 0.12817 | -0.3479 | 118.9087 | -1.68 | -1.712 | 119.0231 | 118.7164 | 118.9362 | -0.19226 | 0.027466 | -0.050354 | -0.036621 | 0.11444 | 0.073242 | 0.018311 | 0.10529 | 118.9499 | 119.014 | -1.7624 | -1.7853 | 118.895 | 118.9819 | 118.8995 | 118.8995
4185.4531 | 120.9137 | -118.5104 | 2.1423 | 0.02121 | 0.016496 | -0.031159 | 0.03883 | -0.017412 | -0.027967 | -0.019828 | -0.058533 | -0.072974 | -0.00096545 | 0.033829 | -0.018367 | -0.011382 | -0.011828 | -0.091553 | -0.041199 | -0.036621 | -0.10986 | -0.10986 | -0.4303 | 0.091553 | -0.09613 | 0.032043 | -0.032043 | 0 | -0.009155 | -0.07782 | -0.11902 | 118.4738 | -2.1835 | -2.2522 | 118.4006 | 118.602 | 118.0801 | 0.12817 | -0.39368 | 118.4784 | -2.1103 | -2.1423 | 118.5013 | 118.3914 | 118.4326 | -0.086976 | -0.045777 | -0.073242 | -0.073242 | 0.022888 | 0.032043 | -0.004578 | 0.064086 | 118.4692 | 118.5425 | -2.179 | -2.1744 | 118.4006 | 118.5104 | 118.4189 | 118.4143
4187.2344 | 120.9961 | -119.4077 | 1.3458 | 0.01358 | 0.012651 | -0.033082 | 0.037121 | -0.011431 | -0.029463 | -0.022178 | -0.14703 | -0.063147 | -0.00011105 | 0.030625 | -0.019863 | -0.013091 | -0.01311 | -0.032043 | -0.054932 | 0.004578 | -0.036621 | 0.10529 | -0.036621 | -0.21515 | -0.032043 | 0.032043 | -0.018311 | 0.013733 | 0.064087 | -0.027466 | 0.059509 | 119.4122 | -1.4008 | -1.3824 | 119.5129 | 119.1925 | 119.371 | -0.21973 | -0.041199 | 119.3893 | -1.3138 | -1.3321 | 119.4717 | 119.4672 | 119.3802 | 0.07782 | -0.009155 | 0.10071 | -0.041199 | 0.082398 | 0.032044 | -0.05951 | 0.050354 | 119.3527 | 119.4397 | -1.3412 | -1.3641 | 119.371 | 119.4214 | 119.3756 | 119.3756
4188.9688 | 120.7809 | -118.4189 | 2.0966 | 0.02121 | 0.011583 | -0.0271 | 0.037549 | -0.016771 | -0.02754 | -0.018547 | -0.061584 | -0.061438 | -0.00096545 | 0.038102 | -0.017085 | -0.0092456 | -0.010119 | -0.050354 | -0.045776 | 0 | 0.045776 | 0.15106 | -0.07782 | -0.11444 | 0.068665 | -0.022888 | 0.2243 | 0.10071 | 0.11902 | 0.032043 | 0.15106 | 118.4189 | -2.1423 | -2.0508 | 118.5699 | 118.3044 | 118.3411 | -0.11444 | -0.07782 | 118.6432 | -2.1194 | -1.9958 | 118.5379 | 118.5699 | 118.4509 | -0.073242 | -0.19226 | 0.15106 | 0.045776 | -0.10529 | -0.1236 | -0.045776 | -0.24719 | 118.3731 | 118.396 | -2.0966 | -1.8723 | 118.4647 | 118.5196 | 118.3685 | 118.4875
4190.75 | 120.8405 | -117.778 | 2.9709 | 0.01358 | 0.013505 | -0.032013 | 0.037549 | -0.018694 | -0.030104 | -0.019188 | -0.12262 | -0.060156 | -0.00075185 | 0.02208 | -0.020503 | -0.011168 | -0.012896 | -0.11444 | -0.032043 | -0.022888 | -0.10071 | -0.29297 | -0.19684 | -0.091553 | -0.082397 | 0.009155 | 0.19684 | 0.009155 | 0.041199 | -0.050354 | -0.19684 | 117.7551 | -3.0029 | -3.0716 | 117.485 | 117.6865 | 117.5812 | -0.068665 | -0.17395 | 117.9749 | -2.9617 | -2.9617 | 117.8192 | 117.5812 | 117.7277 | -0.39368 | -0.24719 | -0.27008 | -0.07782 | -0.15564 | -0.18768 | -0.009155 | -0.18768 | 117.746 | 117.7872 | -2.9938 | -2.774 | 117.6773 | 117.7872 | 117.6636 | 117.6956
4192.4844 | 120.9366 | -118.8858 | 1.7578 | 0.028839 | 0.014573 | -0.032654 | 0.033703 | -0.013994 | -0.031813 | -0.022392 | 0.048279 | -0.070624 | -0.0016064 | 0.031052 | -0.023067 | -0.01715 | -0.026996 | -0.07782 | -0.004578 | -0.036621 | -0.07782 | -0.31586 | 0.082397 | 0.091553 | -0.068665 | 0.050354 | 0.18768 | 0.018311 | 0.059509 | -0.059509 | 0.032043 | 118.8492 | -1.7624 | -1.8356 | 118.5699 | 118.9774 | 118.9682 | 0.12817 | 0.11902 | 119.0735 | -1.7075 | -1.7395 | 118.9453 | 118.9178 | 118.8263 | -0.15564 | -0.24719 | -0.27924 | -0.041199 | -0.12817 | -0.16937 | 0.032043 | -0.13733 | 118.8812 | 118.9362 | -1.7944 | -1.5701 | 118.808 | 118.9041 | 118.808 | 118.8171
4194.25 | 120.9549 | -119.1101 | 1.6067 | 0.036468 | 0.016069 | -0.033509 | 0.034131 | -0.015703 | -0.032667 | -0.022392 | 0.054382 | -0.071478 | -0.0031018 | 0.013535 | -0.037593 | -0.021849 | 0.013806 | -0.073242 | -0.018311 | -0.032043 | -0.064087 | -0.19226 | 0.082397 | 0.091553 | -0.018311 | 0.032043 | 0.086975 | 0.07782 | 0.07782 | -0.032043 | 0.032043 | 119.0781 | -1.6251 | -1.6708 | 118.9178 | 119.2017 | 119.1925 | 0.1236 | 0.11444 | 119.1971 | -1.5747 | -1.5289 | 119.1879 | 119.1422 | 119.0781 | -0.054932 | -0.11902 | -0.16022 | -0.032044 | -0.009155 | -0.009155 | 0.013732 | -0.054932 | 119.0918 | 119.1422 | -1.6388 | -1.5198 | 119.046 | 119.1879 | 119.0369 | 119.0918
4196.0156 | 120.9595 | -114.7156 | 3.8315 | -0.4213 | 0.011369 | -0.031586 | 0.036908 | -0.015062 | -0.046553 | -0.022819 | 0.051331 | -0.068701 | -0.0022472 | 0.034257 | -0.017085 | 0.18793 | 0.032605 | -0.1236 | -0.045776 | -0.027466 | -0.12817 | -0.2655 | 0.091553 | 0.086975 | -0.09613 | 0.022888 | -2.1469 | 0.045776 | 0.24261 | -0.036621 | -0.21057 | 114.6881 | -3.8773 | -3.9597 | 114.4501 | 114.8026 | 114.8071 | 0.11444 | 0.11902 | 112.5687 | -3.8086 | -3.7857 | 114.9582 | 114.505 | 114.679 | 1.9363 | 2.1103 | -0.23804 | -0.10071 | 2.3895 | 2.1927 | -0.01831 | 2.1698 | 114.6698 | 114.7385 | -3.8589 | -5.9784 | 114.5874 | 114.7614 | 114.592 | 114.6194
4197.7188 | 121.0373 | -119.2932 | 1.4191 | 0.028839 | 0.016069 | -0.033722 | 0.037335 | -0.022112 | -0.029463 | -0.019828 | 0.051331 | 0.01568 | -0.0048108 | 0.016312 | 0.022648 | -0.013091 | -0.01546 | -0.045776 | -0.013733 | -0.027466 | -0.09613 | 0.022888 | 0.086975 | 0.086975 | 0.013733 | 0.036621 | 0.11444 | 0.054932 | 0.059509 | -0.009155 | 0.050354 | 119.2657 | -1.4328 | -1.5152 | 119.3161 | 119.3802 | 119.3802 | 0.11444 | 0.11444 | 119.4077 | -1.3824 | -1.3641 | 119.3527 | 119.3436 | 119.2841 | -0.064087 | -0.1236 | 0.050354 | -0.068664 | -0.054932 | -0.059509 | 0.013733 | -0.07782 | 119.2795 | 119.3298 | -1.4465 | -1.3046 | 119.1971 | 119.3481 | 119.2474 | 119.3069
4199.4844 | 121.0831 | -117.6132 | 3.1036 | 0.01358 | 0.014146 | -0.033936 | 0.037549 | -0.01079 | -0.030531 | -0.017479 | -0.22638 | -0.062292 | -0.0060924 | 0.035538 | -0.015377 | -0.012664 | -0.014819 | -0.013733 | -0.064087 | -0.004578 | 0.018311 | 0.10529 | -0.18768 | -0.32044 | 0.073242 | 0.004578 | 0.004578 | 0.13733 | 0.14648 | 0.064087 | 0.19684 | 117.6086 | -3.1677 | -3.0853 | 117.7185 | 117.2928 | 117.4255 | -0.31586 | -0.1831 | 117.6178 | -3.0991 | -2.9663 | 117.7597 | 117.8101 | 117.6773 | 0.19226 | 0.059509 | 0.10986 | 0.022889 | 0.14191 | 0.13275 | -0.059509 | 0 | 117.5491 | 117.6178 | -3.1082 | -3.0991 | 117.6315 | 117.7505 | 117.5995 | 117.6865
4201.2031 | 121.0831 | -119.4077 | 1.3687 | 0.02121 | 0.012651 | -0.032013 | 0.037121 | -0.0092947 | -0.028181 | -0.020897 | -0.098206 | -0.063574 | -0.00075185 | 0.041092 | -0.015377 | -0.011595 | -0.012469 | -0.018311 | -0.082397 | -0.004578 | 0.036621 | 0.16479 | -0.013733 | -0.15106 | 0.10986 | -0.004578 | -0.009155 | 0.13275 | 0.16937 | 0.082397 | 0.17853 | 119.4031 | -1.4511 | -1.3321 | 119.5724 | 119.2566 | 119.3939 | -0.14648 | -0.009155 | 119.3985 | -1.3733 | -1.236 | 119.577 | 119.5862 | 119.4901 | 0.18768 | 0.091552 | 0.16937 | 0.041199 | 0.17853 | 0.14191 | -0.077819 | 0.004577 | 119.3253 | 119.4031 | -1.3733 | -1.3779 | 119.4443 | 119.5404 | 119.3893 | 119.5175
4203 | 120.9732 | -119.2383 | 1.6113 | 0.01358 | 0.015428 | -0.032013 | 0.035626 | -0.012285 | -0.02989 | -0.020042 | -0.55292 | -0.075324 | -0.00096545 | 0.026566 | -0.016231 | -0.010955 | -0.013965 | -0.068665 | -0.022888 | -0.032043 | -0.10529 | -0.11444 | -0.44403 | 0.086975 | -0.12817 | 0.041199 | -0.032043 | -0.013733 | 0.027466 | -0.073242 | 0.050354 | 119.2062 | -1.6342 | -1.7166 | 119.1238 | 119.3253 | 118.7943 | 0.11902 | -0.41199 | 119.2062 | -1.5701 | -1.6251 | 119.2657 | 119.2886 | 119.165 | 0.082397 | -0.041199 | -0.082398 | -0.073243 | 0.059509 | 0.01831 | 0.009155 | 0.073242 | 119.2154 | 119.2795 | -1.6434 | -1.6434 | 119.133 | 119.2245 | 119.1696 | 119.1101
4204.75 | 121.0693 | -119.8013 | 1.062 | 0.036468 | 0.013505 | -0.0318 | 0.036694 | -0.015917 | -0.027113 | -0.021324 | -0.003601 | -0.062292 | -0.00096545 | 0.033829 | -0.018154 | -0.012236 | -0.012683 | -0.045776 | -0.054932 | -0.004578 | -0.032043 | 0.10529 | 0.018311 | 0.013733 | 0.013733 | 0.009155 | -0.013733 | 0.064087 | 0.11444 | 0.027466 | 0.13733 | 119.7968 | -1.1169 | -1.0941 | 119.9066 | 119.8151 | 119.8196 | 0.018311 | 0.022889 | 119.7876 | -1.0529 | -0.99792 | 119.9158 | 119.9387 | 119.8288 | 0.15106 | 0.041199 | 0.10986 | -0.027465 | 0.12817 | 0.07782 | -0.050354 | 0.022888 | 119.7464 | 119.8105 | -1.0666 | -1.0757 | 119.7693 | 119.8654 | 119.7556 | 119.8151
4206.5 | 120.9686 | -119.902 | 1.0117 | 0.028839 | 0.014146 | -0.032441 | 0.038189 | -0.015917 | -0.028181 | -0.020683 | -0.049377 | -0.071905 | -0.0020336 | 0.021653 | -0.019222 | -0.010955 | -0.015887 | -0.036621 | -0.018311 | -0.004578 | -0.045776 | 0.054932 | -0.29755 | -0.15106 | -0.022888 | 0.027466 | -0.032043 | 0 | 0.045776 | -0.054932 | 0.086975 | 119.8975 | -1.03 | -1.0574 | 119.957 | 119.751 | 119.6045 | -0.14648 | -0.29297 | 119.87 | -0.98419 | -1.0117 | 119.9478 | 119.989 | 119.8471 | 0.11902 | -0.022889 | 0.05951 | -0.041198 | 0.077819 | 0.032043 | -0.013733 | 0.059509 | 119.8837 | 119.9295 | -1.0162 | -1.0437 | 119.8563 | 119.902 | 119.8654 | 119.8792
4208.2656 | 121.0144 | -119.0323 | 1.9363 | 0.044098 | 0.013933 | -0.032868 | 0.036694 | -0.012072 | -0.030104 | -0.019828 | -0.20197 | -0.059515 | -0.00182 | 0.027421 | -0.020931 | -0.010527 | -0.0092648 | -0.07782 | -0.004578 | -0.050354 | -0.091553 | 0.032043 | -0.07782 | -0.31586 | -0.068665 | 0.059509 | -0.041199 | -0.004578 | 0.045776 | -0.032043 | 0.07782 | 118.9819 | -1.9409 | -2.0279 | 119.0643 | 118.7164 | 118.9545 | -0.2655 | -0.027466 | 118.9911 | -1.8768 | -1.9409 | 119.0781 | 119.1101 | 119.0002 | 0.11902 | 0.009156 | 0.082397 | -0.041199 | 0.086975 | 0.036621 | 0.045776 | 0.10071 | 119.0277 | 119.0918 | -1.9867 | -1.9775 | 118.9407 | 119.0277 | 118.9545 | 118.9636
4210.0156 | 121.0098 | -119.7235 | 1.2634 | 0.01358 | 0.013719 | -0.033722 | 0.037549 | -0.016131 | -0.032026 | -0.020256 | -0.11957 | -0.059729 | -0.0016064 | 0.032975 | -0.021785 | -0.011809 | -0.012042 | -0.10071 | -0.018311 | -0.041199 | -0.09613 | 0.032043 | -0.022888 | -0.1831 | -0.073242 | 0.050354 | -0.036621 | -0.027466 | 0.036621 | -0.045776 | 0.068665 | 119.6823 | -1.2817 | -1.3596 | 119.7556 | 119.5404 | 119.7006 | -0.14191 | 0.018311 | 119.6869 | -1.2131 | -1.2909 | 119.7601 | 119.7922 | 119.6777 | 0.10529 | -0.009155 | 0.073242 | -0.054931 | 0.073242 | 0.009155 | 0.022888 | 0.086975 | 119.7052 | 119.7739 | -1.3046 | -1.3 | 119.6274 | 119.696 | 119.6228 | 119.6503
4211.7656 | 121.1243 | -119.7739 | 1.1536 | 0.02121 | 0.015214 | -0.032868 | 0.035199 | -0.014849 | -0.028395 | -0.023246 | 0.008606 | -0.062933 | -0.003529 | 0.036606 | -0.019008 | -0.011809 | -0.012896 | -0.050354 | -0.041199 | 0 | -0.013733 | 0.11444 | 0.036621 | 0.068665 | 0.032043 | 0 | -0.018311 | 0.073242 | 0.16937 | 0.091553 | 0.16937 | 119.7739 | -1.1948 | -1.1673 | 119.8883 | 119.8425 | 119.8105 | 0.068665 | 0.036621 | 119.7556 | -1.1536 | -1.0803 | 119.9432 | 119.9432 | 119.8654 | 0.18768 | 0.10986 | 0.11444 | -0.013733 | 0.18768 | 0.091553 | -0.041199 | 0.018311 | 119.7327 | 119.7739 | -1.1536 | -1.1719 | 119.7601 | 119.8471 | 119.7235 | 119.8059
4213.4844 | 121.0419 | -119.902 | 1.0162 | 0.02121 | 0.017564 | -0.0318 | 0.037549 | -0.013994 | -0.02754 | -0.02111 | -0.14398 | -0.068915 | -0.0033154 | 0.029343 | -0.017726 | -0.010314 | -0.016742 | -0.032043 | -0.041199 | -0.018311 | -0.036621 | 0.09613 | 0.004578 | -0.27008 | 0 | 0.027466 | -0.041199 | 0.013733 | 0.086975 | -0.018311 | 0.11902 | 119.8837 | -1.0574 | -1.0529 | 119.9982 | 119.632 | 119.9066 | -0.25177 | 0.022889 | 119.8608 | -0.98877 | -1.0025 | 119.989 | 120.0211 | 119.8837 | 0.16022 | 0.022888 | 0.11444 | -0.01831 | 0.12817 | 0.054932 | -0.022888 | 0.068665 | 119.8608 | 119.9295 | -1.0345 | -1.0574 | 119.8654 | 119.9158 | 119.87 | 119.902
4215.2344 | 121.0922 | -120.1218 | 0.82398 | 0.02121 | 0.012864 | -0.032868 | 0.037762 | -0.014635 | -0.030104 | -0.021537 | 0.011658 | -0.061651 | -0.00182 | 0.037034 | -0.017085 | -0.012236 | -0.0099056 | -0.050354 | -0.068665 | 0 | -0.036621 | 0.10529 | 0.013733 | 0.022888 | 0.009155 | -0.004578 | -0.032043 | 0.032043 | 0.13275 | 0.027466 | 0.13733 | 120.1218 | -0.89264 | -0.8606 | 120.2271 | 120.1447 | 120.1355 | 0.022888 | 0.013733 | 120.0897 | -0.82855 | -0.79193 | 120.2545 | 120.2591 | 120.1492 | 0.16937 | 0.059509 | 0.10529 | -0.036621 | 0.16479 | 0.064086 | -0.068665 | 0.027465 | 120.0531 | 120.1172 | -0.82398 | -0.85602 | 120.0851 | 120.1538 | 120.0714 | 120.1309
4217 | 121.1517 | -119.8929 | 1.0574 | 0.01358 | 0.013505 | -0.0318 | 0.036694 | -0.011217 | -0.028608 | -0.021751 | 0.011658 | -0.060797 | -0.0022472 | 0.035325 | -0.015163 | -0.011809 | -0.011615 | -0.050354 | -0.054932 | 0 | -0.022888 | 0.1236 | 0.009155 | 0.022888 | 0.050354 | 0.004578 | 0 | 0.10529 | 0.16479 | 0.082397 | 0.19684 | 119.8929 | -1.1124 | -1.0803 | 120.0165 | 119.9158 | 119.902 | 0.022888 | 0.009155 | 119.8929 | -1.0529 | -0.95215 | 120.0577 | 120.0897 | 119.9753 | 0.19684 | 0.082397 | 0.1236 | -0.022888 | 0.16479 | 0.10529 | -0.054932 | 0.004578 | 119.838 | 119.8975 | -1.0574 | -1.0574 | 119.87 | 119.9982 | 119.8425 | 119.9432
4218.7812 | 121.1288 | -120.3644 | 0.61798 | 0.036468 | 0.015428 | -0.032013 | 0.037335 | -0.014635 | -0.029249 | -0.020042 | -0.028015 | -0.060584 | -0.00096545 | 0.029984 | -0.016445 | -0.010955 | -0.013965 | -0.022888 | -0.022888 | -0.013733 | -0.018311 | 0.086975 | 0 | -0.050354 | 0.022888 | 0.032043 | -0.027466 | 0.032043 | 0.11444 | 0.022888 | 0.12817 | 120.3506 | -0.64087 | -0.63629 | 120.4514 | 120.314 | 120.3644 | -0.036621 | 0.013733 | 120.3369 | -0.58594 | -0.58594 | 120.4788 | 120.4926 | 120.3873 | 0.15564 | 0.050354 | 0.10071 | -0.004578 | 0.14191 | 0.059509 | -0.009155 | 0.059509 | 120.3415 | 120.3964 | -0.63171 | -0.64545 | 120.3461 | 120.3964 | 120.3415 | 120.3873
4220.5625 | 121.051 | -120.4742 | 0.57678 | 0.02121 | 0.015428 | -0.035645 | 0.037762 | -0.013567 | -0.029036 | -0.024528 | 0.0055542 | -0.063147 | -0.0020336 | 0.031693 | -0.021785 | -0.012236 | -0.0094784 | -0.091553 | -0.018311 | -0.032043 | -0.09613 | 0.045776 | -0.041199 | -0.032043 | -0.064087 | 0.050354 | -0.041199 | -0.036621 | 0.050354 | -0.027466 | 0.073242 | 120.4422 | -0.59509 | -0.67291 | 120.52 | 120.4422 | 120.433 | 0 | -0.009156 | 120.433 | -0.52643 | -0.6134 | 120.5246 | 120.5475 | 120.4468 | 0.11444 | 0.013733 | 0.077819 | -0.064087 | 0.091553 | 0.004578 | 0.013732 | 0.091553 | 120.4559 | 120.5246 | -0.60883 | -0.61798 | 120.3781 | 120.4376 | 120.3827 | 120.4102
4222.3438 | 121.2524 | -120.1675 | 0.72784 | 0.02121 | 0.015001 | -0.033936 | 0.034344 | -0.012072 | -0.027754 | -0.021751 | 0.011658 | -0.06272 | -0.0037426 | 0.040238 | -0.017726 | -0.011595 | -0.012896 | -0.032043 | -0.059509 | 0.009155 | 0.032043 | 0.16937 | 0.07782 | 0.086975 | 0.09613 | -0.009155 | -0.013733 | 0.091553 | 0.19684 | 0.1236 | 0.19226 | 120.1767 | -0.78735 | -0.6958 | 120.3369 | 120.2545 | 120.2454 | 0.07782 | 0.068665 | 120.1538 | -0.737 | -0.63629 | 120.3644 | 120.3598 | 120.2911 | 0.20599 | 0.13733 | 0.16022 | 0.022888 | 0.21057 | 0.10529 | -0.068664 | 0.004578 | 120.108 | 120.1584 | -0.71869 | -0.74158 | 120.1996 | 120.2591 | 120.1355 | 120.2637
4224.125 | 121.1243 | -120.3918 | 0.66834 | 0.036468 | 0.014573 | -0.032654 | 0.035626 | -0.016558 | -0.028608 | -0.023246 | 0.011658 | -0.061011 | 0.00010255 | 0.036179 | -0.02029 | -0.013518 | -0.013965 | -0.073242 | -0.013733 | -0.036621 | -0.091553 | 0.045776 | -0.027466 | -0.032043 | -0.07782 | 0.07782 | -0.050354 | -0.032043 | 0.045776 | -0.027466 | 0.082397 | 120.3552 | -0.68207 | -0.75989 | 120.4376 | 120.3598 | 120.3644 | 0.004578 | 0.009155 | 120.3415 | -0.59052 | -0.70038 | 120.4376 | 120.4742 | 120.3644 | 0.13275 | 0.022888 | 0.082397 | -0.054932 | 0.09613 | 0.018311 | 0.022888 | 0.12817 | 120.3781 | 120.4697 | -0.70496 | -0.71869 | 120.3003 | 120.3598 | 120.3186 | 120.314
4225.8594 | 121.2112 | -120.2911 | 0.70496 | -0.0016786 | 0.013078 | -0.031586 | 0.037762 | -0.015276 | -0.028608 | -0.021965 | 0.014709 | -0.062079 | -0.0013928 | 0.031907 | -0.013668 | -0.011595 | -0.012042 | 0.004578 | -0.054932 | 0.013733 | 0.041199 | 0.16937 | 0.050354 | 0.050354 | 0.09613 | 0.027466 | -0.018311 | 0.11444 | 0.16937 | 0.082397 | 0.19684 | 120.3049 | -0.75989 | -0.66376 | 120.4605 | 120.3415 | 120.3415 | 0.036621 | 0.036621 | 120.2728 | -0.67749 | -0.59052 | 120.4605 | 120.488 | 120.3735 | 0.21515 | 0.10071 | 0.15564 | 0.027466 | 0.18768 | 0.13275 | -0.068665 | 0.045777 | 120.2362 | 120.3186 | -0.69122 | -0.72327 | 120.3323 | 120.4056 | 120.2957 | 120.3873
4227.625 | 121.2616 | -119.2383 | 1.6617 | 0.02121 | 0.015855 | -0.028809 | 0.035412 | -0.01079 | -0.028822 | -0.02346 | 0.014709 | -0.061011 | -0.00182 | 0.032334 | -0.015377 | -0.012023 | -0.013537 | -0.050354 | -0.054932 | -0.004578 | 0.013733 | 0.13733 | 0.027466 | 0.036621 | 0.054932 | 0.004578 | -0.022888 | 0.050354 | 0.11444 | 0.036621 | 0.15106 | 119.2337 | -1.7166 | -1.6479 | 119.3756 | 119.2749 | 119.2657 | 0.041199 | 0.032044 | 119.2154 | -1.6571 | -1.6113 | 119.3527 | 119.3893 | 119.2749 | 0.17395 | 0.059509 | 0.14191 | 0.018311 | 0.13733 | 0.073242 | -0.050354 | 0.027466 | 119.1833 | 119.2429 | -1.6663 | -1.6846 | 119.252 | 119.2886 | 119.1879 | 119.2932
4229.3906 | 121.1563 | -119.2062 | 1.8951 | 0.02121 | 0.015641 | -0.032227 | 0.03883 | -0.013994 | -0.030958 | -0.020683 | 0.011658 | -0.059515 | -0.00075185 | 0.037461 | -0.016445 | -0.0098864 | -0.010119 | -0.041199 | -0.032043 | -0.027466 | -0.018311 | 0.10986 | 0.013733 | 0.009155 | 0.027466 | 0.027466 | -0.022888 | 0.045776 | 0.082397 | 0 | 0.1236 | 119.1788 | -1.9272 | -1.9135 | 119.3161 | 119.2154 | 119.22 | 0.036621 | 0.041199 | 119.1834 | -1.8677 | -1.8494 | 119.2886 | 119.3298 | 119.2062 | 0.14648 | 0.022888 | 0.13733 | 0.009155 | 0.10528 | 0.068664 | -0.004577 | 0.050354 | 119.1742 | 119.2337 | -1.9226 | -1.918 | 119.1879 | 119.252 | 119.165 | 119.2337
4231.125 | 120.0485 | -74.9222 | 44.8105 | 0.0059509 | 0.013933 | -0.030945 | 0.039258 | -0.011858 | -0.030317 | -0.020683 | -0.061584 | -0.060156 | -0.00053825 | 0.035752 | 0.26233 | -0.0043322 | -0.013537 | -0.10529 | -0.041199 | -0.013733 | -0.07782 | 0.082397 | -0.027466 | -0.10071 | -0.013733 | 0.009155 | 0.14648 | 0.091553 | 0.13733 | 0.041199 | 0.1831 | 74.9084 | -44.8517 | -44.8883 | 75.0046 | 74.8215 | 74.8947 | -0.086975 | -0.013733 | 75.0687 | -44.8013 | -44.7189 | 75.0595 | 75.1053 | 74.9634 | 0.036621 | -0.10529 | 0.09613 | -0.064087 | -0.009155 | -0.054931 | -0.027466 | -0.13733 | 74.881 | 74.9313 | -44.8242 | -44.664 | 74.8444 | 75.0137 | 74.8169 | 74.9084
4232.875 | 104.7043 | -5.4291 | 90.8478 | 0.12039 | 0.0077374 | -0.029236 | 0.036694 | -0.016558 | -0.029249 | -0.021324 | -0.22638 | -0.060584 | 0.002666 | 0.041092 | -0.019863 | -0.01245 | -0.012042 | -0.10529 | -0.091553 | 0.23346 | -0.16937 | -0.19226 | -0.31586 | -0.33417 | -0.082397 | -0.10986 | -0.086975 | -0.004578 | -0.11902 | -0.21515 | -0.1236 | 5.6625 | -90.9393 | -91.0172 | 5.2368 | 5.0949 | 5.1132 | -0.56763 | -0.54932 | 5.3421 | -90.9576 | -90.8524 | 5.3101 | 5.3055 | 5.2139 | -0.036621 | -0.12817 | -0.42572 | -0.40283 | -0.032044 | 0.082397 | -0.32501 | -0.022888 | 5.3375 | 5.3192 | -90.6143 | -90.9348 | 5.2597 | 5.4245 | 5.3238 | 5.3467
4234.625 | 120.2682 | -96.0938 | 23.8586 | 0.0059509 | 0.014573 | -0.026886 | 0.033276 | -0.013353 | -0.030531 | -0.023887 | -0.23553 | -0.061865 | -0.0033154 | 0.038529 | -0.020931 | -0.01245 | -0.011615 | -0.10986 | -0.054932 | 0.32501 | -0.27008 | -0.29297 | -0.3479 | -0.29755 | -0.25177 | -0.70496 | -0.09613 | -0.25635 | -0.29755 | -0.32959 | -0.21973 | 96.4188 | -23.9136 | -24.1287 | 95.8008 | 95.7962 | 95.7459 | -0.62256 | -0.67291 | 95.9976 | -24.5636 | -24.115 | 95.7962 | 95.874 | 95.7642 | -0.1236 | -0.23346 | -0.61798 | -0.59509 | -0.20142 | -0.16022 | -0.37994 | -0.60883 | 96.0388 | 95.3888 | -23.5336 | -23.9548 | 95.8237 | 95.8374 | 95.9839 | 95.842
4236.375 | 120.4285 | -95.9244 | 24.1699 | 0.02121 | 0.012437 | -0.028595 | 0.037976 | -0.019549 | -0.033094 | -0.030296 | 0.051331 | -0.069769 | -0.011006 | 0.035752 | -0.019649 | -0.016082 | -0.026355 | -0.37994 | -0.022888 | 0.17395 | 0.091553 | 0.09613 | 0.09613 | 0.10529 | -0.22888 | 0.082397 | -0.091553 | 0.10071 | 0.086975 | 0.086975 | 0.09613 | 96.0983 | -24.1928 | -24.0784 | 96.0205 | 96.0297 | 96.0205 | -0.068664 | -0.07782 | 95.8328 | -24.0875 | -24.0692 | 96.0114 | 96.0205 | 96.0114 | 0.18768 | 0.17853 | -0.07782 | -0.082397 | 0.17853 | 0.19226 | -0.19684 | 0.17395 | 95.9015 | 96.0068 | -23.996 | -24.2615 | 96.0159 | 96.0251 | 95.5444 | 95.6955
4238.1406 | 120.2911 | -95.842 | 23.9273 | -0.53574 | 0.013505 | -0.030945 | 0.022168 | -0.015917 | -0.035658 | -0.024955 | 0.042175 | -0.068701 | -0.004597 | 0.025498 | -0.018367 | -0.010527 | -0.014605 | -0.2655 | -0.036621 | 0.21515 | -0.17853 | 0.10071 | 0.10071 | 0.086975 | -0.36163 | -0.041199 | 0.13275 | -0.3067 | -0.11444 | -0.20599 | -0.082397 | 96.0571 | -23.9639 | -24.1058 | 95.9427 | 95.929 | 95.9427 | -0.12817 | -0.11444 | 95.9747 | -23.9685 | -24.234 | 95.7275 | 95.7596 | 95.636 | -0.21515 | -0.33875 | -0.11444 | -0.39368 | -0.24719 | -0.43945 | -0.25177 | -0.17395 | 95.8054 | 95.8008 | -23.7122 | -23.7946 | 95.6635 | 95.5353 | 95.5765 | 95.4803
4239.8594 | 117.2104 | -68.2709 | 45.7306 | 0.02121 | 0.00966 | -0.030945 | 0.012982 | -0.022753 | -0.035658 | -0.021751 | 0.051331 | -0.069556 | -0.0048108 | 0.022507 | -0.032894 | 0.12918 | -0.019091 | -0.31128 | -0.004578 | 0.20599 | -0.25635 | 0.10986 | 0.07782 | 0.086975 | 3.6804 | 0.086975 | -0.091553 | -0.10071 | 0.091553 | 0.086975 | 0.10071 | 68.4769 | -45.7352 | -45.9869 | 68.3807 | 68.3578 | 68.3487 | -0.11902 | -0.12817 | 68.1793 | -45.6436 | -45.8313 | 68.3624 | 68.3716 | 68.3578 | 0.19226 | 0.17853 | -0.096131 | -0.46234 | 0.18311 | -0.009155 | -0.21057 | 0.17853 | 68.2663 | 68.3578 | -45.5246 | -45.8221 | 68.0145 | 68.1702 | 67.9596 | 71.9513
4241.6094 | 104.3701 | -63.5742 | 55.5267 | 0.01358 | 0.013933 | -0.029877 | 0.033917 | -0.015276 | -0.026258 | -0.023033 | -0.22333 | -0.060797 | 0.00074335 | 0.03212 | -0.014095 | -0.009032 | -0.012469 | -0.25177 | -0.064087 | 0.1236 | -0.26093 | -0.22888 | -0.33875 | -0.27008 | -0.018311 | -0.37994 | 0.2243 | 0.082397 | -0.068665 | -0.1831 | -0.059509 | 63.6978 | -55.5908 | -55.7877 | 63.3453 | 63.3041 | 63.2355 | -0.39368 | -0.46234 | 63.7985 | -55.9067 | -55.4443 | 63.5056 | 63.5147 | 63.3911 | -0.28381 | -0.40741 | -0.35248 | -0.38452 | -0.29297 | -0.14191 | -0.18768 | -0.60425 | 63.5101 | 63.1943 | -55.4031 | -55.3024 | 63.3133 | 63.6566 | 63.3224 | 63.5559
4243.3281 | 120.2774 | -105.0751 | 16.8091 | 0.01358 | 0.013719 | -0.0271 | 0.0040097 | 0.02638 | -0.043135 | 0.030587 | 0.057434 | 0.015893 | 0.011211 | 0.022507 | 0.02393 | 0.028138 | 0.019361 | -0.45319 | -0.022888 | 0.13275 | 0.086975 | 0.091553 | 0.091553 | 0.091553 | -0.1236 | 0.086975 | -0.086975 | 0.09613 | 0.091553 | 0.09613 | 0.091553 | 105.2078 | -16.832 | -16.7221 | 105.1666 | 105.1666 | 105.1666 | -0.041198 | -0.041198 | 104.9881 | -16.7221 | -16.713 | 105.1666 | 105.1666 | 105.1712 | 0.17853 | 0.1831 | -0.041198 | -0.045776 | 0.17853 | 0.1831 | -0.15564 | 0.17395 | 105.0522 | 105.162 | -16.6763 | -16.8961 | 105.162 | 105.1712 | 104.6219 | 104.9515
4245.0625 | 120.5612 | -25.3738 | 89.1769 | 0.14328 | 0.019914 | 0.067535 | 0.0046505 | 0.027021 | 0.034411 | 0.029305 | 0.057434 | 0.016107 | 0.012066 | 0.022507 | 0.02393 | 0.028566 | 0.019788 | 0.10071 | -0.082397 | 0.12817 | 0.10529 | 0.09613 | 0.09613 | 0.09613 | 0.10071 | 0.10071 | -0.09613 | 0.10071 | 0.10529 | 0.10529 | 0.09613 | 25.502 | -89.2593 | -89.0717 | 25.47 | 25.47 | 25.47 | -0.032044 | -0.032044 | 25.2777 | -89.0762 | -89.0762 | 25.4791 | 25.47 | 25.4791 | 0.19226 | 0.20142 | -0.032044 | -0.022888 | 0.20142 | 0.19684 | -0.21057 | 0.19684 | 25.2914 | 25.4745 | -89.0488 | -89.2731 | 25.4791 | 25.4745 | 25.4745 | 25.4745
4246.7812 | 89.5615 | -0.10986 | 82.8415 | 0.13565 | 0.019273 | 0.067535 | 0.0050779 | 0.027662 | 0.034624 | 0.029305 | 0.063538 | 0.016321 | 0.012279 | 0.022935 | 0.024144 | 0.028779 | 0.019574 | 0.10071 | -0.10986 | -0.009155 | 0.10071 | 0.10071 | 0.10071 | 0.10529 | 0.10529 | 0.10529 | -0.09613 | 0.10071 | 0.10529 | 0.10071 | 0.10529 | 0.10071 | -82.9514 | -82.7408 | 0.21057 | 0.21515 | 0.21057 | 0.11444 | 0.10986 | 0.013733 | -82.7362 | -82.7408 | 0.21515 | 0.21515 | 0.21057 | 0.20142 | 0.19684 | 0.10986 | 0.10986 | 0.20142 | 0.19684 | -0.10071 | 0.20142 | 0 | 0.21515 | -82.8506 | -82.9376 | 0.21057 | 0.21057 | 0.21057 | 0.21515
4248.5 | 110.6461 | -7.8461 | 88.2385 | -0.15427 | 0.0094464 | 0.066894 | 0.0046505 | 0.027235 | 0.034411 | 0.029091 | 0.054382 | 0.016107 | 0.011852 | 0.021226 | -0.029476 | -0.015654 | 0.019574 | 0.09613 | -0.054932 | 0.17395 | 0.09613 | 0.09613 | 0.09613 | 0.086975 | -0.46234 | 0.10529 | -0.091553 | 0.082397 | 0.091553 | 0.10071 | 0.10071 | 8.02 | -88.2935 | -88.1424 | 7.9422 | 7.933 | 7.9422 | -0.086975 | -0.07782 | 7.7545 | -88.1332 | -88.1561 | 7.9376 | 7.9468 | 7.9468 | 0.19226 | 0.19226 | -0.07782 | -0.07782 | 0.18311 | 0.17395 | -0.22888 | 0.19684 | 7.7911 | 7.9514 | -88.0646 | -88.3301 | 7.9422 | 7.9285 | 7.9422 | 7.3837
4250.3281 | 120.1767 | -10.5835 | 109.4421 | 0.028839 | 0.012224 | -0.031373 | 0.033703 | -0.014422 | -0.027327 | -0.02111 | -0.082947 | -0.061011 | 0.00010255 | 0.034897 | -0.018794 | -0.011595 | -0.010119 | -0.11444 | -0.07782 | 0.045776 | -0.064087 | 0.054932 | -0.054932 | -0.09613 | -0.036621 | -0.13275 | 0.2243 | 0.018311 | 0.10529 | 0.032043 | 0.12817 | 10.6293 | -109.52 | -109.5062 | 10.6384 | 10.4874 | 10.5286 | -0.14191 | -0.10071 | 10.8078 | -109.5749 | -109.4238 | 10.6888 | 10.7117 | 10.6155 | -0.09613 | -0.19226 | 0.009156 | -0.10986 | -0.11902 | -0.20599 | -0.1236 | -0.35706 | 10.5057 | 10.4507 | -109.3964 | -109.2178 | 10.5194 | 10.6018 | 10.4691 | 10.5469
4252.1094 | 119.8837 | -117.1555 | 2.211 | 0.01358 | 0.016282 | -0.031373 | 0.034985 | -0.013567 | -0.029463 | -0.020042 | -0.067688 | -0.061865 | -0.0022472 | 0.035966 | -0.019435 | -0.010741 | -0.014819 | -0.054932 | -0.073242 | 0.09613 | 0.041199 | 0.14191 | 0.009155 | -0.050354 | 0.086975 | -0.13733 | 0.35248 | 0.068665 | 0.14191 | 0.041199 | 0.09613 | 117.2516 | -2.2842 | -2.1698 | 117.2974 | 117.1051 | 117.1646 | -0.14648 | -0.086975 | 117.5079 | -2.3483 | -2.1423 | 117.2974 | 117.2516 | 117.1967 | -0.25635 | -0.31128 | 0.045777 | -0.054931 | -0.21057 | -0.28381 | -0.16937 | -0.48981 | 117.0822 | 117.0181 | -2.1149 | -1.8585 | 117.1967 | 117.2241 | 117.1005 | 117.2424
4253.8906 | 120.2637 | -119.0277 | 0.78278 | 0.01358 | 0.006883 | -0.033722 | 0.033917 | -0.016558 | -0.030104 | -0.021751 | -0.049377 | -0.061865 | -0.0016064 | 0.041733 | -0.021144 | -0.011595 | -0.011187 | -0.10071 | -0.041199 | -0.018311 | -0.018311 | 0.082397 | -0.027466 | -0.036621 | 0.009155 | -0.082397 | 0.24261 | 0.045776 | 0.15564 | 0.082397 | 0.16937 | 119.0094 | -0.82398 | -0.80109 | 119.1101 | 118.9911 | 119.0002 | -0.01831 | -0.009155 | 119.2703 | -0.86517 | -0.737 | 119.1834 | 119.1971 | 119.1101 | -0.073242 | -0.16022 | 0.10071 | 0 | -0.086975 | -0.19684 | -0.022888 | -0.32501 | 118.9865 | 118.9453 | -0.80109 | -0.54016 | 119.0094 | 119.0735 | 118.927 | 119.0369
4255.6094 | 120.6665 | -119.6091 | 0.70953 | 0.02121 | 0.013292 | -0.030732 | 0.020672 | -0.021044 | -0.030958 | -0.022819 | 0.051331 | 0.015039 | -0.0028882 | 0.02208 | -0.038448 | -0.029753 | -0.021869 | -0.082397 | -0.032043 | -0.036621 | -0.45319 | 0.082397 | 0.091553 | 0.09613 | -0.064087 | -0.14648 | 0.032043 | 0.022888 | 0.018311 | 0.086975 | 0.09613 | 119.5724 | -0.74158 | -1.1627 | 119.6915 | 119.7052 | 119.7006 | 0.13275 | 0.12817 | 119.6411 | -0.85602 | -0.68665 | 119.6274 | 119.7052 | 119.696 | 0.064087 | 0.054932 | 0.11902 | -0.41656 | -0.013732 | -0.009155 | 0.004578 | -0.17853 | 119.577 | 119.4626 | -0.74616 | -0.67749 | 119.1559 | 119.632 | 119.5267 | 119.545
4257.3906 | 120.488 | -119.5908 | 0.66376 | 0.028839 | 0.012437 | -0.0318 | 0.036908 | -0.014208 | -0.028181 | -0.01876 | -0.058533 | -0.060584 | 0.00031615 | 0.035325 | -0.017085 | -0.0096728 | -0.011187 | -0.064087 | -0.045776 | 0.013733 | -0.022888 | 0.059509 | -0.045776 | -0.09613 | -0.004578 | 0.009155 | 0.1831 | 0.041199 | 0.10529 | 0.041199 | 0.12817 | 119.6045 | -0.70953 | -0.68665 | 119.6503 | 119.4946 | 119.545 | -0.10986 | -0.059509 | 119.7739 | -0.6546 | -0.62256 | 119.696 | 119.7189 | 119.632 | -0.054931 | -0.14191 | 0.045776 | -0.036621 | -0.077819 | -0.14191 | -0.059509 | -0.17395 | 119.545 | 119.5999 | -0.65002 | -0.48065 | 119.5679 | 119.632 | 119.5267 | 119.5862
4259.1406 | 119.8105 | -119.101 | 0.32044 | -0.54337 | 0.0094464 | -0.029664 | 0.021313 | -0.020403 | -0.040358 | -0.027732 | 0.060486 | -0.072546 | -0.010579 | 0.03682 | -0.016231 | -0.01245 | -0.01076 | -0.16479 | -0.022888 | 0.11902 | 0.10071 | 0.091553 | 0.091553 | 0.10071 | -0.25635 | -0.032043 | -0.10529 | -0.059509 | -0.1236 | -0.19226 | 0 | 119.22 | -0.34332 | -0.21973 | 119.1925 | 119.2017 | 119.1925 | -0.018311 | -0.027466 | 118.9957 | -0.35248 | -0.37994 | 118.9774 | 119.101 | 118.9087 | 0.10529 | -0.086975 | -0.027466 | -0.018311 | -0.01831 | 0.045777 | -0.14191 | 0.073243 | 119.0781 | 119.0689 | -0.20142 | -0.42572 | 119.2017 | 119.0414 | 118.9362 | 118.8446
4260.8438 | 120.4971 | -119.7418 | 0.37994 | 0.01358 | 0.01436 | -0.033082 | 0.033917 | -0.014635 | -0.029676 | -0.021537 | -0.12567 | -0.062292 | -0.00182 | 0.034257 | -0.020076 | -0.0098864 | -0.010547 | -0.045776 | -0.050354 | 0.09613 | 0.045776 | 0.068665 | -0.054932 | -0.12817 | 0.068665 | -0.16937 | 0.35248 | 0.091553 | 0.11902 | -0.009155 | 0.054932 | 119.838 | -0.4303 | -0.33417 | 119.8105 | 119.6136 | 119.6869 | -0.2243 | -0.15106 | 120.0943 | -0.54932 | -0.28839 | 119.8608 | 119.7968 | 119.7327 | -0.29755 | -0.36163 | -0.027465 | -0.050354 | -0.23346 | -0.26093 | -0.14648 | -0.52185 | 119.6915 | 119.5724 | -0.28381 | -0.027466 | 119.7876 | 119.8334 | 119.696 | 119.8105
4262.5625 | 120.5338 | -120.0119 | 0.33417 | 0.0059509 | 0.013292 | -0.032227 | 0.033063 | -0.015276 | -0.030317 | -0.022392 | -0.21112 | -0.061011 | -0.0016064 | 0.033188 | -0.021358 | -0.012023 | -0.015033 | -0.022888 | -0.064087 | 0.041199 | 0 | -0.013733 | -0.16937 | -0.27466 | 0 | -0.018311 | 0.31586 | 0.013733 | 0.041199 | -0.20599 | -0.16479 | 120.0531 | -0.39825 | -0.33417 | 119.9982 | 119.7372 | 119.8425 | -0.31586 | -0.21057 | 120.3278 | -0.35248 | -0.32043 | 120.0531 | 119.8471 | 119.8059 | -0.48065 | -0.52185 | -0.054932 | -0.041199 | -0.27466 | -0.30212 | -0.10529 | -0.33417 | 119.9478 | 119.9936 | -0.29297 | -0.01831 | 120.0119 | 120.0256 | 119.989 | 120.0119
4264.2969 | 120.639 | -120.108 | 0.27466 | 0.02121 | 0.013505 | -0.034791 | 0.035199 | -0.01549 | -0.029249 | -0.023033 | -0.043274 | -0.063361 | -0.0024608 | 0.040665 | -0.01794 | -0.0098864 | -0.010974 | -0.059509 | -0.054932 | -0.004578 | -0.022888 | 0.12817 | 0.018311 | -0.022888 | 0.018311 | 0.004578 | -0.032043 | 0.054932 | 0.14191 | 0.064087 | 0.15564 | 120.1035 | -0.32959 | -0.29755 | 120.2362 | 120.0851 | 120.1263 | -0.01831 | 0.022889 | 120.076 | -0.27008 | -0.21973 | 120.2499 | 120.2637 | 120.1721 | 0.18768 | 0.09613 | 0.13275 | -0.01831 | 0.17395 | 0.086975 | -0.050354 | 0.036621 | 120.0531 | 120.1126 | -0.27924 | -0.3067 | 120.0851 | 120.163 | 120.0485 | 120.1263
4266 | 120.6345 | -120.1904 | 0.29755 | 0.02121 | 0.01671 | -0.032227 | 0.024304 | -0.01314 | -0.028181 | -0.035423 | 0.051331 | 0.016107 | -0.0056652 | 0.01503 | 0.024998 | -0.01715 | -0.029559 | -0.032043 | -0.041199 | -0.022888 | -0.064087 | -0.13275 | 0.082397 | 0.10071 | 0.022888 | 0.022888 | 0.032043 | 0.022888 | -0.041199 | 0.041199 | 0.091553 | 120.1675 | -0.33874 | -0.36163 | 120.0577 | 120.2911 | 120.2728 | 0.1236 | 0.10528 | 120.2225 | -0.27466 | -0.27466 | 120.1492 | 120.282 | 120.2316 | 0.05951 | 0.009156 | -0.10986 | -0.041199 | -0.073242 | -0.009155 | -0.018311 | -0.009155 | 120.1492 | 120.2133 | -0.32043 | -0.2655 | 120.1263 | 120.2133 | 120.1584 | 120.2133
4267.7656 | 120.6116 | -120.3049 | 0.31586 | 0.01358 | 0.013505 | -0.033082 | 0.037762 | -0.015703 | -0.032881 | -0.022819 | -0.03717 | -0.061438 | -0.0024608 | 0.021012 | -0.019863 | -0.011809 | -0.012042 | -0.10986 | -0.027466 | -0.032043 | -0.10529 | -0.068665 | -0.28839 | -0.2655 | -0.073242 | 0.064087 | -0.054932 | -0.041199 | 0.036621 | -0.22888 | -0.23346 | 120.2728 | -0.34332 | -0.42114 | 120.2362 | 120.0394 | 120.0165 | -0.23346 | -0.25635 | 120.2499 | -0.25177 | -0.35706 | 120.3415 | 120.0714 | 120.076 | -0.17853 | -0.17395 | -0.036622 | -0.073243 | 0.091553 | 0.013733 | 0.004577 | 0.11902 | 120.2774 | 120.369 | -0.3479 | -0.37079 | 120.1996 | 120.2637 | 120.195 | 120.2316
4269.4844 | 120.6757 | -120.1996 | 0.33875 | 0.036468 | 0.015214 | -0.033722 | 0.037335 | -0.015062 | -0.030317 | -0.02346 | 0.014709 | -0.073828 | -0.00182 | 0.027421 | -0.024776 | -0.0148 | -0.015246 | -0.068665 | -0.013733 | -0.050354 | -0.07782 | -0.10071 | -0.37994 | -0.18768 | -0.064087 | 0.050354 | -0.045776 | -0.018311 | 0.050354 | -0.25635 | 0.059509 | 120.1492 | -0.35248 | -0.41657 | 120.0989 | 120.0119 | 119.8196 | -0.13733 | -0.32959 | 120.1538 | -0.28839 | -0.35706 | 120.2499 | 120.2591 | 119.9432 | 0.10528 | -0.21057 | -0.050354 | -0.027466 | 0.09613 | 0.027465 | 0.036621 | 0.09613 | 120.1859 | 120.2499 | -0.3891 | -0.38452 | 120.1218 | 120.1813 | 120.1309 | 120.1355
4271.2031 | 120.6573 | -120.2499 | 0.35248 | 0.02121 | 0.016069 | -0.033082 | 0.036908 | -0.021044 | -0.028181 | -0.021751 | 0.060486 | -0.072333 | 0.00031615 | 0.029557 | -0.019649 | -0.01715 | -0.01781 | -0.091553 | -0.027466 | -0.041199 | -0.09613 | -0.1236 | -0.45319 | 0.10986 | -0.11444 | 0.045776 | -0.036621 | -0.022888 | 0.009155 | -0.18768 | -0.2655 | 120.2087 | -0.37994 | -0.44861 | 120.1263 | 120.3598 | 119.7968 | 0.15106 | -0.41199 | 120.2133 | -0.3067 | -0.37537 | 120.2591 | 119.9844 | 120.0623 | -0.22888 | -0.15106 | -0.082397 | -0.054931 | 0.045776 | 0.013733 | 0.013733 | 0.082397 | 120.2225 | 120.2957 | -0.39368 | -0.3891 | 120.1538 | 120.2271 | 120.1584 | 120.1355
4272.9219 | 120.7214 | -120.1904 | 0.42572 | 0.01358 | 0.012651 | -0.0318 | 0.040326 | -0.0090811 | -0.030531 | -0.020897 | -0.21722 | -0.06507 | 0.00031615 | 0.035752 | -0.017085 | -0.0098864 | -0.01311 | -0.082397 | -0.018311 | -0.022888 | -0.10986 | -0.009155 | -0.24719 | -0.39825 | -0.082397 | 0.022888 | -0.032043 | -0.004578 | 0.027466 | -0.073242 | -0.091553 | 120.1675 | -0.44403 | -0.53558 | 120.1813 | 119.7922 | 119.9432 | -0.37537 | -0.2243 | 120.1584 | -0.40283 | -0.4303 | 120.2179 | 120.0989 | 120.1172 | -0.05951 | -0.041199 | 0.013733 | -0.086975 | 0.059509 | 0.027465 | 0.004577 | 0.054931 | 120.1721 | 120.2133 | -0.44861 | -0.45776 | 120.0806 | 120.1859 | 120.108 | 120.108
4274.6406 | 120.7031 | -120.3003 | 0.35248 | 0.01358 | 0.015428 | -0.032441 | 0.034772 | -0.014635 | -0.029463 | -0.023674 | -0.058533 | -0.059943 | -0.00032465 | 0.032548 | -0.024135 | -0.025481 | -0.026782 | -0.032043 | -0.045776 | -0.009155 | -0.022888 | 0.027466 | -0.29297 | -0.15106 | 0.009155 | 0.036621 | -0.013733 | 0.027466 | 0.09613 | -0.10071 | -0.23804 | 120.2911 | -0.39825 | -0.37537 | 120.3278 | 120.1492 | 120.0073 | -0.14191 | -0.28381 | 120.2866 | -0.31586 | -0.32501 | 120.3964 | 120.0623 | 120.1996 | -0.2243 | -0.086975 | 0.036621 | -0.013733 | 0.10986 | 0.041199 | -0.036621 | 0.050354 | 120.2545 | 120.3369 | -0.36163 | -0.36621 | 120.2774 | 120.3278 | 120.2682 | 120.3094
4276.4219 | 120.7947 | -120.2866 | 0.36163 | 0.02121 | 0.014787 | -0.033082 | 0.036267 | -0.010149 | -0.030745 | -0.021751 | -0.098206 | -0.074469 | 0.00052975 | 0.02913 | -0.019649 | -0.021636 | -0.021228 | -0.018311 | -0.032043 | -0.032043 | -0.027466 | 0.068665 | -0.20142 | -0.18768 | 0.027466 | 0.032043 | -0.022888 | 0.022888 | 0.10529 | -0.036621 | -0.17395 | 120.2545 | -0.39368 | -0.3891 | 120.3552 | 120.0989 | 120.0851 | -0.15564 | -0.16937 | 120.2637 | -0.32959 | -0.33874 | 120.3918 | 120.1126 | 120.2499 | -0.15106 | -0.013733 | 0.10071 | 0.004577 | 0.12817 | 0.045776 | 0 | 0.054931 | 120.2545 | 120.3186 | -0.39368 | -0.38452 | 120.2591 | 120.3094 | 120.2682 | 120.314
4278.1562 | 120.7535 | -120.4285 | 0.29755 | 0.01358 | 0.013078 | -0.034363 | 0.034985 | -0.012285 | -0.030531 | -0.020897 | -0.061584 | -0.061011 | -0.0011792 | 0.03212 | -0.020931 | -0.012023 | -0.013537 | -0.054932 | -0.041199 | -0.009155 | -0.064087 | 0.064087 | -0.004578 | -0.10071 | -0.054932 | 0.041199 | -0.022888 | -0.041199 | 0.064087 | -0.022888 | 0.07782 | 120.4193 | -0.33874 | -0.36163 | 120.4926 | 120.3278 | 120.4239 | -0.091553 | 0.004577 | 120.4056 | -0.25635 | -0.33874 | 120.4926 | 120.5063 | 120.4056 | 0.10071 | 0 | 0.073242 | -0.054932 | 0.086975 | -0.018311 | -0.032044 | 0.064087 | 120.3873 | 120.4697 | -0.3067 | -0.32043 | 120.3644 | 120.3873 | 120.3735 | 120.3735
4279.875 | 120.8359 | -120.3735 | 0.30212 | 0.0059509 | 0.01436 | -0.032441 | 0.034985 | -0.016771 | -0.030958 | -0.024101 | -0.10126 | -0.062079 | -0.00011105 | 0.028702 | -0.022212 | -0.011595 | -0.010333 | -0.064087 | -0.022888 | -0.004578 | -0.073242 | 0.064087 | -0.018311 | -0.11444 | -0.059509 | 0.032043 | -0.036621 | -0.036621 | 0.041199 | -0.036621 | 0.068665 | 120.369 | -0.32501 | -0.37537 | 120.4376 | 120.2591 | 120.3552 | -0.10986 | -0.013733 | 120.3369 | -0.27008 | -0.33875 | 120.4147 | 120.4422 | 120.3369 | 0.10529 | 0 | 0.068665 | -0.068664 | 0.07782 | 0 | -0.01831 | 0.068664 | 120.3506 | 120.4056 | -0.3067 | -0.33875 | 120.3003 | 120.3369 | 120.3094 | 120.314
4281.6406 | 120.8633 | -120.3232 | 0.36621 | 0.0059509 | 0.015428 | -0.033722 | 0.035199 | -0.013994 | -0.029036 | -0.023246 | -0.003601 | -0.059943 | -0.0028882 | 0.032548 | -0.017085 | -0.010741 | -0.015887 | -0.018311 | -0.059509 | 0.013733 | 0.027466 | 0.16937 | 0.07782 | 0.064087 | 0.022888 | 0.018311 | -0.018311 | 0.022888 | 0.13275 | 0.045776 | 0.14648 | 120.3369 | -0.42572 | -0.33875 | 120.4926 | 120.3873 | 120.401 | 0.050354 | 0.064087 | 120.3049 | -0.3479 | -0.34332 | 120.4559 | 120.4697 | 120.369 | 0.16479 | 0.064087 | 0.15564 | 0.013733 | 0.15106 | 0.041199 | -0.073242 | 0.036622 | 120.2637 | 120.3415 | -0.35248 | -0.38452 | 120.3506 | 120.3461 | 120.3049 | 120.3461
4283.3906 | 120.9091 | -120.4285 | 0.2655 | 0.036468 | 0.012651 | -0.032654 | 0.034772 | -0.011644 | -0.030317 | -0.020897 | 0.011658 | -0.062079 | -0.0037426 | 0.036606 | -0.016017 | -0.011168 | -0.011401 | -0.050354 | -0.059509 | 0.004578 | -0.013733 | 0.1236 | 0.032043 | 0.050354 | -0.004578 | 0.004578 | 0 | 0.059509 | 0.14191 | 0.07782 | 0.16479 | 120.433 | -0.32501 | -0.27924 | 120.5521 | 120.4788 | 120.4605 | 0.045776 | 0.027465 | 120.4285 | -0.26092 | -0.20599 | 120.5704 | 120.5933 | 120.5063 | 0.16479 | 0.07782 | 0.11902 | -0.018311 | 0.14191 | 0.059509 | -0.064087 | 0.004578 | 120.369 | 120.433 | -0.26092 | -0.2655 | 120.4147 | 120.488 | 120.3781 | 120.4239
4285.125 | 120.845 | -120.5017 | 0.29297 | 0.028839 | 0.014146 | -0.032013 | 0.039685 | -0.013781 | -0.029676 | -0.022178 | -0.073792 | -0.06806 | -0.00032465 | 0.031052 | -0.015377 | -0.011595 | -0.014819 | -0.086975 | -0.022888 | -0.022888 | -0.12817 | -0.027466 | -0.10071 | -0.23346 | -0.086975 | 0.045776 | -0.041199 | -0.022888 | 0.018311 | -0.068665 | 0.07782 | 120.4788 | -0.31586 | -0.42114 | 120.4742 | 120.2683 | 120.401 | -0.21057 | -0.07782 | 120.4605 | -0.24719 | -0.31586 | 120.52 | 120.5795 | 120.433 | 0.11902 | -0.027466 | -0.004578 | -0.10529 | 0.05951 | 0.018311 | 0 | 0.086975 | 120.4788 | 120.5475 | -0.31586 | -0.33417 | 120.3735 | 120.4788 | 120.4147 | 120.4147
4286.875 | 120.9503 | -120.4559 | 0.27924 | 0.01358 | 0.013719 | -0.034791 | 0.037121 | -0.01314 | -0.030317 | -0.02111 | 0.011658 | -0.062292 | -0.0028882 | 0.032334 | -0.017085 | -0.008391 | -0.011401 | -0.045776 | -0.045776 | -0.004578 | -0.013733 | 0.12817 | 0.027466 | 0.032043 | 0.018311 | 0.009155 | -0.009155 | 0.064087 | 0.14191 | 0.086975 | 0.16937 | 120.4514 | -0.32501 | -0.29297 | 120.5841 | 120.488 | 120.4834 | 0.036621 | 0.032044 | 120.4468 | -0.27008 | -0.21515 | 120.5978 | 120.6253 | 120.5429 | 0.17853 | 0.09613 | 0.13275 | -0.009155 | 0.15106 | 0.073242 | -0.041198 | 0.01831 | 120.4102 | 120.4651 | -0.28381 | -0.28839 | 120.4422 | 120.52 | 120.4102 | 120.4742
4288.6406 | 120.9091 | -120.4971 | 0.28839 | 0.028839 | 0.012651 | -0.035004 | 0.034985 | -0.01549 | -0.028395 | -0.019615 | 0.008606 | -0.062506 | -0.0024608 | 0.033616 | -0.016445 | -0.0098864 | -0.01546 | -0.059509 | -0.064087 | 0 | -0.009155 | 0.11902 | 0.022888 | 0.027466 | 0.004578 | 0.013733 | -0.018311 | 0.036621 | 0.1236 | 0.027466 | 0.14648 | 120.4971 | -0.35248 | -0.29755 | 120.6161 | 120.5246 | 120.52 | 0.027466 | 0.022888 | 120.4788 | -0.27466 | -0.25177 | 120.6207 | 120.6436 | 120.5246 | 0.16479 | 0.045777 | 0.11902 | -0.009155 | 0.14191 | 0.054932 | -0.064087 | 0.032044 | 120.433 | 120.5109 | -0.28839 | -0.3067 | 120.488 | 120.5338 | 120.4376 | 120.5017
4290.3594 | 121.0602 | -120.3644 | 0.40283 | 0.02121 | 0.012651 | -0.033082 | 0.038403 | -0.015062 | -0.02989 | -0.021751 | 0.008606 | -0.061651 | -0.0016064 | 0.036606 | -0.017513 | -0.0096728 | -0.012256 | -0.054932 | -0.045776 | -0.004578 | -0.009155 | 0.12817 | 0.022888 | 0.050354 | 0.041199 | 0.013733 | -0.018311 | 0.068665 | 0.16479 | 0.10529 | 0.17395 | 120.3598 | -0.44861 | -0.41199 | 120.4926 | 120.4147 | 120.3873 | 0.054932 | 0.027466 | 120.3461 | -0.3891 | -0.33417 | 120.5292 | 120.5383 | 120.4697 | 0.19226 | 0.1236 | 0.13275 | -0.004577 | 0.18311 | 0.086976 | -0.041198 | 0.032044 | 120.3186 | 120.3781 | -0.40741 | -0.42114 | 120.3552 | 120.433 | 120.3094 | 120.4056
4292.0938 | 120.9412 | -120.5109 | 0.28839 | 0.02121 | 0.014787 | -0.035004 | 0.038189 | -0.011217 | -0.027327 | -0.021537 | 0.014709 | -0.057166 | -0.00053825 | 0.040452 | -0.018794 | -0.012664 | -0.011828 | -0.073242 | -0.009155 | -0.045776 | -0.073242 | 0.036621 | -0.036621 | -0.036621 | -0.064087 | 0.064087 | -0.054932 | -0.022888 | 0.054932 | -0.032043 | 0.09613 | 120.4651 | -0.29755 | -0.36163 | 120.5475 | 120.4742 | 120.4742 | 0.009155 | 0.009155 | 120.4559 | -0.2243 | -0.31128 | 120.5658 | 120.607 | 120.4788 | 0.15106 | 0.022889 | 0.082397 | -0.027466 | 0.10986 | 0.032044 | 0.036621 | 0.11902 | 120.5017 | 120.575 | -0.33417 | -0.34332 | 120.4376 | 120.488 | 120.4376 | 120.4468
4293.8125 | 120.9274 | -120.5521 | 0.27008 | 0.01358 | 0.013292 | -0.033936 | 0.034985 | -0.013994 | -0.02754 | -0.020897 | 0.008606 | -0.061438 | -0.00011105 | 0.035538 | -0.019435 | -0.01245 | -0.013324 | -0.013733 | -0.059509 | -0.004578 | 0 | 0.11902 | 0.045776 | 0.054932 | 0.013733 | 0.018311 | -0.022888 | 0 | 0.09613 | 0.013733 | 0.11444 | 120.5475 | -0.32959 | -0.27008 | 120.6711 | 120.607 | 120.5978 | 0.05951 | 0.050354 | 120.5292 | -0.25177 | -0.27008 | 120.6482 | 120.6665 | 120.5658 | 0.13733 | 0.036621 | 0.1236 | 0.004578 | 0.11902 | 0.022888 | -0.054931 | 0.041199 | 120.4926 | 120.5704 | -0.27466 | -0.29297 | 120.5521 | 120.5521 | 120.5383 | 120.5658
4295.5469 | 120.8588 | -118.8629 | 1.6617 | 0.02121 | 0.011155 | -0.033509 | 0.034772 | -0.015703 | -0.030958 | -0.020897 | 0.017761 | -0.062079 | -0.003529 | 0.035752 | -0.020076 | -0.010527 | -0.012256 | -0.022888 | -0.068665 | 0.013733 | 0.041199 | 0.18768 | 0.086975 | 0.086975 | 0.068665 | 0.018311 | -0.013733 | 0.064087 | 0.16022 | 0.082397 | 0.16937 | 118.8766 | -1.7303 | -1.6205 | 119.0506 | 118.9499 | 118.9499 | 0.073242 | 0.073242 | 118.8492 | -1.6434 | -1.5976 | 119.0231 | 119.0323 | 118.9453 | 0.18311 | 0.09613 | 0.17395 | 0.027466 | 0.17395 | 0.07782 | -0.082398 | 0.032044 | 118.7943 | 118.8812 | -1.6479 | -1.6754 | 118.9041 | 118.927 | 118.84 | 118.9316
4297.2812 | 120.2591 | -94.3405 | 25.3738 | -0.0016786 | 0.015855 | -0.032441 | 0.032422 | -0.016985 | -0.029249 | -0.020897 | -0.16229 | -0.062292 | -0.00182 | 0.039384 | -0.02029 | -0.011382 | -0.013537 | -0.045776 | -0.064087 | 0.33875 | -0.09613 | -0.07782 | -0.19684 | -0.26093 | -0.091553 | -0.11444 | -0.086975 | -0.054932 | -0.13275 | -0.2243 | -0.13733 | 94.6793 | -25.4379 | -25.47 | 94.2627 | 94.0796 | 94.1437 | -0.59967 | -0.53558 | 94.2535 | -25.4883 | -25.4288 | 94.2078 | 94.2032 | 94.1162 | -0.050354 | -0.13733 | -0.41657 | -0.43488 | -0.045776 | 0.032043 | -0.40283 | -0.027466 | 94.2764 | 94.2261 | -25.0351 | -25.4608 | 94.2444 | 94.2856 | 94.2947 | 94.249
4299 | 120.7626 | -113.887 | 6.3583 | 0.02121 | 0.011369 | -0.033936 | 0.034558 | -0.01784 | -0.029463 | -0.023674 | -0.043274 | -0.062933 | -0.00096545 | 0.039384 | -0.02029 | -0.011168 | -0.016101 | -0.050354 | -0.050354 | 0.018311 | 0.022888 | 0.13733 | 0.032043 | -0.022888 | 0.086975 | -0.10529 | 0.3067 | 0.07782 | 0.1831 | 0.10986 | 0.16937 | 113.9053 | -6.4087 | -6.3354 | 114.0244 | 113.8641 | 113.9191 | -0.041199 | 0.013732 | 114.1937 | -6.4636 | -6.2805 | 114.0701 | 114.0564 | 113.9969 | -0.13733 | -0.19684 | 0.11902 | 0.004577 | -0.1236 | -0.22888 | -0.068665 | -0.41199 | 113.8367 | 113.7817 | -6.34 | -6.0516 | 113.9099 | 113.9648 | 113.8367 | 113.974
4300.7188 | 120.8038 | -109.8633 | 10.4965 | 0.028839 | 0.013933 | -0.030945 | 0.03349 | -0.012499 | -0.027327 | -0.016838 | -0.031067 | -0.062933 | -0.0024608 | 0.040024 | -0.016872 | -0.0098864 | -0.011615 | -0.082397 | -0.054932 | 0 | -0.050354 | 0.068665 | -0.032043 | -0.068665 | -0.004578 | 0.004578 | 0.20142 | 0.045776 | 0.082397 | 0.032043 | 0.14191 | 109.8633 | -10.5515 | -10.5469 | 109.9319 | 109.7946 | 109.8312 | -0.068665 | -0.032043 | 110.0647 | -10.4919 | -10.4507 | 109.9457 | 110.0052 | 109.8953 | -0.059509 | -0.16937 | 0.068665 | -0.050354 | -0.11902 | -0.15564 | -0.054932 | -0.19684 | 109.8083 | 109.8679 | -10.4965 | -10.2951 | 109.8129 | 109.9091 | 109.7809 | 109.8587
4302.4531 | 116.7709 | -93.2281 | 23.5336 | 0.02121 | 0.010087 | -0.030304 | 0.036267 | -0.012926 | -0.031172 | -0.021751 | -0.061584 | -0.060797 | 0.0018116 | 0.038529 | -0.018367 | -0.010527 | -0.0099056 | -0.10529 | -0.050354 | 0.059509 | -0.054932 | 0.045776 | -0.068665 | -0.09613 | -0.018311 | -0.10986 | 0.25177 | 0.041199 | 0.086975 | 0.036621 | 0.14191 | 93.2877 | -23.584 | -23.5886 | 93.2739 | 93.132 | 93.1595 | -0.15564 | -0.12817 | 93.4799 | -23.6435 | -23.4924 | 93.3151 | 93.3701 | 93.2648 | -0.10986 | -0.21515 | -0.013733 | -0.11444 | -0.16479 | -0.21057 | -0.10986 | -0.36163 | 93.1778 | 93.1183 | -23.4741 | -23.2819 | 93.1732 | 93.2693 | 93.1229 | 93.2098
4304.1875 | 120.4788 | -94.6609 | 25.1541 | -0.055084 | 0.011796 | -0.032227 | 0.035199 | -0.013994 | -0.026472 | -0.022605 | -0.14093 | -0.062079 | 0.0030934 | 0.035752 | -0.015377 | -0.010527 | -0.010333 | -0.036621 | -0.064087 | 0.19684 | -0.07782 | -0.07782 | -0.20142 | -0.24261 | 0.09613 | -0.24719 | 0.35248 | 0.10529 | 0.10986 | -0.036621 | 0.054932 | 94.8578 | -25.2182 | -25.2319 | 94.5831 | 94.4183 | 94.4595 | -0.43945 | -0.39825 | 95.0134 | -25.4013 | -25.0488 | 94.7708 | 94.7159 | 94.6243 | -0.29755 | -0.3891 | -0.27466 | -0.27466 | -0.24262 | -0.24719 | -0.26093 | -0.59967 | 94.5969 | 94.4138 | -24.9573 | -24.8016 | 94.5831 | 94.7662 | 94.6243 | 94.7571
4305.9062 | 120.6162 | -94.4824 | 25.7767 | 0.02121 | 0.016282 | -0.040131 | 0.0044369 | 0.026808 | 0.028643 | 0.028878 | 0.048279 | 0.015893 | -0.0088696 | 0.028275 | -0.04037 | 0.027925 | 0.019361 | -0.28839 | -0.036621 | 0.21057 | 0.086975 | 0.10071 | 0.09613 | 0.091553 | -0.19684 | -0.041199 | -0.082397 | -0.013733 | -0.27008 | 0.091553 | 0.09613 | 94.693 | -25.8133 | -25.6897 | 94.5831 | 94.574 | 94.5786 | -0.11902 | -0.11444 | 94.4 | -25.8179 | -25.7904 | 94.2123 | 94.5786 | 94.574 | 0.17853 | 0.17395 | -0.10986 | -0.1236 | -0.18768 | 0.068664 | -0.24719 | 0.041198 | 94.4458 | 94.4412 | -25.5661 | -25.8591 | 94.5694 | 94.4687 | 94.194 | 94.2856
4307.6406 | 120.8038 | -111.763 | 8.4961 | 0.02121 | 0.012437 | -0.027955 | 0.035626 | -0.016985 | -0.027327 | -0.021751 | -0.043274 | -0.061224 | -0.003529 | 0.038315 | -0.01794 | -0.009032 | -0.011187 | -0.036621 | -0.059509 | 0.13275 | -0.004578 | 0.045776 | -0.09613 | -0.14191 | 0.082397 | -0.27008 | 0.35706 | 0.086975 | 0.11902 | 0.009155 | 0.11444 | 111.8958 | -8.5556 | -8.5007 | 111.8088 | 111.6211 | 111.6669 | -0.27466 | -0.22888 | 112.1201 | -8.7662 | -8.4091 | 111.882 | 111.8774 | 111.7722 | -0.24261 | -0.3479 | -0.086975 | -0.13733 | -0.23804 | -0.27008 | -0.19226 | -0.62714 | 111.7035 | 111.4929 | -8.3633 | -8.139 | 111.7584 | 111.85 | 111.7264 | 111.8454
4309.3906 | 120.8588 | -111.8454 | 8.551 | 0.01358 | 0.015001 | -0.030518 | 0.035199 | -0.019121 | -0.030745 | -0.022178 | -0.03717 | -0.063147 | -0.00053825 | 0.03917 | -0.019222 | -0.011595 | -0.011615 | -0.054932 | -0.064087 | 0.004578 | 0.004578 | 0.15564 | 0.045776 | -0.009155 | 0.054932 | -0.013733 | 0.11902 | 0.09613 | 0.16479 | 0.11444 | 0.18768 | 111.85 | -8.6151 | -8.5464 | 112.001 | 111.8362 | 111.8912 | -0.013733 | 0.041198 | 111.9644 | -8.5648 | -8.4549 | 112.0102 | 112.0331 | 111.9598 | 0.068664 | -0.004578 | 0.15106 | 0 | 0.045776 | -0.022889 | -0.068665 | -0.13275 | 111.7813 | 111.8317 | -8.5464 | -8.432 | 111.85 | 111.9415 | 111.7905 | 111.9003
4311.125 | 120.932 | -112.9257 | 7.4524 | 0.02121 | 0.013078 | -0.030732 | 0.035626 | -0.014208 | -0.030317 | -0.022605 | -0.10736 | -0.062933 | -0.00096545 | 0.036393 | -0.017513 | -0.010314 | -0.013324 | -0.009155 | -0.045776 | -0.004578 | 0.050354 | 0.20599 | 0.022888 | -0.059509 | 0.10986 | -0.013733 | 0.16022 | 0.09613 | 0.1831 | 0.068665 | 0.10529 | 112.9211 | -7.4982 | -7.402 | 113.1317 | 112.8662 | 112.9486 | -0.054931 | 0.027466 | 113.0859 | -7.4661 | -7.3563 | 113.1088 | 113.031 | 112.9944 | -0.054931 | -0.091552 | 0.21057 | 0.054932 | 0.022888 | -0.064087 | -0.041198 | -0.17395 | 112.8799 | 112.912 | -7.457 | -7.2922 | 112.9761 | 113.0219 | 112.9166 | 113.0356
4312.8594 | 120.9274 | -113.7634 | 6.7062 | 0.01358 | 0.012864 | -0.033936 | 0.03883 | -0.012713 | -0.031172 | -0.022605 | -0.12567 | -0.059515 | 0.00052975 | 0.035325 | -0.014095 | -0.011382 | -0.010547 | 0 | -0.059509 | 0.018311 | 0.050354 | 0.13733 | -0.10986 | -0.18768 | 0.091553 | 0.009155 | -0.004578 | 0.12817 | 0.15106 | 0.086975 | 0.09613 | 113.7817 | -6.7657 | -6.6559 | 113.9008 | 113.5757 | 113.6536 | -0.20599 | -0.12817 | 113.7589 | -6.6971 | -6.5781 | 113.9145 | 113.8596 | 113.8504 | 0.10071 | 0.091553 | 0.11902 | 0.032043 | 0.15564 | 0.13275 | -0.07782 | 0.013733 | 113.7039 | 113.7726 | -6.6879 | -6.7108 | 113.8138 | 113.8916 | 113.7634 | 113.855
4314.625 | 120.9778 | -114.2395 | 6.2622 | 0.01358 | 0.012651 | -0.034577 | 0.035199 | -0.014849 | -0.029463 | -0.020256 | -0.10431 | -0.062079 | -0.00075185 | 0.03212 | -0.018581 | -0.010527 | -0.012256 | -0.018311 | -0.054932 | 0 | 0.050354 | 0.20142 | 0.022888 | -0.073242 | 0.10071 | 0.004578 | 0.009155 | 0.10986 | 0.16479 | 0.11444 | 0.09613 | 114.2395 | -6.3171 | -6.2119 | 114.4409 | 114.1663 | 114.2624 | -0.073242 | 0.022888 | 114.2487 | -6.2576 | -6.1523 | 114.4043 | 114.3356 | 114.3539 | 0.086975 | 0.10529 | 0.20142 | 0.050354 | 0.15564 | 0.10071 | -0.054932 | -0.004577 | 114.1846 | 114.2441 | -6.2622 | -6.2531 | 114.2899 | 114.3494 | 114.2212 | 114.3402
4316.3594 | 120.4056 | -117.4301 | 2.623 | 0.036468 | 0.015001 | -0.030304 | 0.035199 | -0.011431 | -0.029036 | -0.020469 | -0.095154 | -0.059729 | 0.0011708 | 0.032975 | -0.015804 | -0.010314 | -0.012896 | -0.004578 | -0.045776 | 0 | 0.050354 | 0.1831 | 0.004578 | -0.12817 | 0.09613 | 0.018311 | -0.009155 | 0.11444 | 0.14191 | 0.064087 | 0.16022 | 117.4301 | -2.6688 | -2.5726 | 117.6132 | 117.3019 | 117.4347 | -0.12817 | 0.004578 | 117.421 | -2.6047 | -2.5085 | 117.572 | 117.5903 | 117.4942 | 0.16937 | 0.073242 | 0.1831 | 0.050354 | 0.15106 | 0.1236 | -0.045776 | 0.027466 | 117.3843 | 117.4484 | -2.623 | -2.6321 | 117.4805 | 117.5446 | 117.4255 | 117.5262
4318.0938 | 120.9641 | -116.2903 | 4.2526 | 0.028839 | 0.012651 | -0.032013 | 0.035626 | -0.01549 | -0.032454 | -0.020897 | -0.040222 | -0.061224 | 0.00052975 | 0.035752 | -0.017513 | -0.0101 | -0.011828 | -0.073242 | -0.036621 | -0.004578 | -0.022888 | 0.11444 | 0.022888 | -0.041199 | 0.009155 | 0.004578 | 0 | 0.07782 | 0.11444 | 0.064087 | 0.15564 | 116.2857 | -4.2892 | -4.2755 | 116.4047 | 116.2491 | 116.3132 | -0.036621 | 0.027466 | 116.2903 | -4.248 | -4.1748 | 116.4047 | 116.4459 | 116.3544 | 0.15564 | 0.064087 | 0.11902 | -0.01831 | 0.11444 | 0.07782 | -0.032043 | 0.004578 | 116.2537 | 116.2949 | -4.2572 | -4.2526 | 116.2674 | 116.3681 | 116.217 | 116.2994
4319.8125 | 120.726 | -118.895 | 1.5793 | 0.02121 | 0.013719 | -0.033082 | 0.023449 | -0.020189 | -0.030317 | -0.032219 | 0.051331 | 0.016535 | -0.003529 | 0.02977 | -0.019649 | -0.020354 | -0.020587 | -0.10071 | -0.009155 | -0.022888 | -0.10986 | -0.31586 | 0.086975 | 0.09613 | -0.091553 | 0.022888 | 0.15564 | 0.018311 | -0.009155 | -0.21515 | 0.022888 | 118.8721 | -1.5884 | -1.6891 | 118.5791 | 118.9911 | 118.9819 | 0.11902 | 0.10986 | 119.0506 | -1.5564 | -1.561 | 118.8858 | 118.9178 | 118.6798 | -0.13275 | -0.37079 | -0.29297 | -0.086975 | -0.16479 | -0.13733 | 0.013733 | -0.13275 | 118.8858 | 118.9178 | -1.6022 | -1.4236 | 118.7851 | 118.9133 | 118.7943 | 118.8034
4321.5312 | 120.6802 | -117.865 | 2.5955 | 0.01358 | 0.015855 | -0.033295 | 0.027295 | -0.025744 | -0.030958 | -0.029441 | 0.045227 | -0.076819 | -0.0016064 | 0.037034 | -0.016445 | -0.015227 | -0.02016 | -0.09613 | -0.027466 | -0.027466 | -0.09613 | -0.3479 | 0.082397 | 0.091553 | -0.07782 | 0.041199 | 0.25177 | 0 | 0 | -0.16937 | 0.013733 | 117.8375 | -2.623 | -2.6917 | 117.5171 | 117.9565 | 117.9474 | 0.11902 | 0.10986 | 118.1168 | -2.5543 | -2.5955 | 117.865 | 117.8787 | 117.6956 | -0.23804 | -0.42114 | -0.32043 | -0.068664 | -0.25177 | -0.25177 | 0 | -0.21057 | 117.8375 | 117.9062 | -2.623 | -2.3438 | 117.7689 | 117.865 | 117.7689 | 117.7872
4323.25 | 120.7855 | -119.0277 | 1.4511 | 0.036468 | 0.013933 | -0.032227 | 0.038189 | -0.013353 | -0.028608 | -0.020469 | -0.064636 | -0.06272 | -0.0031018 | 0.045792 | -0.016658 | -0.010741 | -0.0090512 | -0.050354 | -0.045776 | 0.009155 | -0.018311 | 0.16022 | -0.018311 | -0.09613 | 0.027466 | 0 | -0.009155 | 0.07782 | 0.09613 | 0.041199 | 0.15106 | 119.0369 | -1.4969 | -1.4694 | 119.1879 | 118.9316 | 119.0094 | -0.10528 | -0.027466 | 119.0186 | -1.4511 | -1.3733 | 119.1238 | 119.1788 | 119.0689 | 0.16022 | 0.050354 | 0.15106 | -0.027466 | 0.10528 | 0.086975 | -0.054931 | 0.009155 | 118.9819 | 119.0277 | -1.442 | -1.4603 | 119.0094 | 119.1055 | 118.9774 | 119.0552
4325 | 120.8679 | -114.9811 | 5.5893 | 0.028839 | 0.015641 | -0.032654 | 0.030285 | -0.017199 | -0.029036 | -0.029441 | 0.048279 | 0.015253 | 0.00074335 | 0.013321 | 0.024785 | 0.028138 | 0.019147 | -0.027466 | -0.036621 | -0.027466 | -0.027466 | -0.25177 | 0.09613 | 0.09613 | 0.018311 | 0.018311 | 0.13275 | 0.064087 | 0.091553 | -0.11444 | 0.091553 | 114.9536 | -5.6259 | -5.6168 | 114.7293 | 115.0772 | 115.0772 | 0.1236 | 0.1236 | 115.1138 | -5.571 | -5.5252 | 115.0726 | 115.0726 | 114.8666 | -0.041198 | -0.24719 | -0.2243 | 0 | -0.041198 | -0.068664 | -0.009155 | -0.11444 | 114.9445 | 114.9994 | -5.6168 | -5.4565 | 114.9536 | 115.0452 | 114.9536 | 114.9994
4326.7344 | 120.0027 | -118.4509 | 1.3046 | 0.0059509 | 0.011796 | -0.031586 | 0.036053 | -0.013567 | -0.030958 | -0.020042 | -0.23248 | -0.061651 | -0.0020336 | 0.032548 | -0.019222 | -0.011595 | -0.012256 | -0.086975 | -0.018311 | -0.018311 | -0.086975 | -0.13275 | -0.37994 | -0.23804 | -0.082397 | 0.045776 | 0.31586 | -0.009155 | 0.041199 | -0.050354 | -0.27924 | 118.4326 | -1.3229 | -1.3916 | 118.3182 | 118.2129 | 118.071 | -0.21973 | -0.36163 | 118.7668 | -1.2589 | -1.3138 | 118.4921 | 118.1717 | 118.4006 | -0.59509 | -0.36621 | -0.11444 | -0.068664 | -0.27466 | -0.32501 | 0 | -0.27008 | 118.4326 | 118.4967 | -1.3229 | -0.98877 | 118.364 | 118.4418 | 118.364 | 118.3685
4328.4531 | 120.0119 | -112.2437 | 7.1823 | 0.01358 | 0.010942 | -0.030091 | 0.035626 | -0.013994 | -0.029463 | -0.020042 | -0.073792 | -0.060584 | -0.00032465 | 0.034257 | -0.019863 | -0.012877 | -0.011615 | -0.032043 | -0.073242 | 0.027466 | 0.041199 | 0.13733 | -0.009155 | -0.059509 | 0.091553 | -0.073242 | 0.3067 | 0.10071 | 0.16479 | 0.091553 | 0.10529 | 112.2711 | -7.2556 | -7.1411 | 112.381 | 112.1841 | 112.2345 | -0.086975 | -0.036621 | 112.5504 | -7.2556 | -7.0816 | 112.4084 | 112.3489 | 112.3352 | -0.20142 | -0.21515 | 0.10986 | 0.013733 | -0.14191 | -0.20599 | -0.10071 | -0.37994 | 112.1704 | 112.1704 | -7.1548 | -6.8756 | 112.2849 | 112.3444 | 112.2116 | 112.3352
4330.1875 | 119.7464 | -114.1434 | 5.3192 | 0.0059509 | 0.018846 | -0.026032 | 0.0044369 | 0.026808 | -0.048902 | 0.028878 | 0.054382 | 0.015893 | 0.011425 | 0.022507 | 0.023289 | 0.027711 | 0.019574 | -0.064087 | -0.018311 | 0.15106 | 0.086975 | 0.09613 | 0.10071 | 0.091553 | -0.38452 | 0.086975 | -0.091553 | 0.013733 | 0.091553 | 0.09613 | 0.086975 | 114.2944 | -5.3375 | -5.2322 | 114.2395 | 114.2349 | 114.2441 | -0.059509 | -0.050354 | 114.0518 | -5.2322 | -5.3055 | 114.2349 | 114.2303 | 114.2395 | 0.17853 | 0.18768 | -0.054932 | -0.064087 | 0.18311 | 0.10529 | -0.16937 | 0.17853 | 114.1251 | 114.2303 | -5.1682 | -5.4108 | 114.2303 | 114.1571 | 114.0793 | 113.7589
4331.9688 | 118.3594 | -65.7669 | 49.8688 | 0.01358 | 0.013292 | -0.027314 | 0.059338 | 0.026594 | -0.03224 | 0.029732 | 0.33209 | -0.06272 | -0.00032465 | 0.039811 | -0.01559 | -0.011382 | -0.010974 | -0.059509 | -0.073242 | 0.07782 | -0.19684 | -0.13275 | -0.045776 | -0.27924 | 0.064087 | -0.33417 | 0.28839 | 0.10529 | 0.068665 | -0.10529 | -0.004578 | 65.8447 | -49.942 | -50.0656 | 65.6342 | 65.4877 | 65.7211 | -0.35706 | -0.1236 | 66.0553 | -50.2029 | -49.7635 | 65.8356 | 65.7623 | 65.6616 | -0.29297 | -0.39368 | -0.21057 | -0.27466 | -0.21973 | -0.18311 | -0.15106 | -0.62256 | 65.6937 | 65.4327 | -49.791 | -49.5804 | 65.5701 | 65.8722 | 65.7074 | 65.831
4333.6875 | 118.2953 | -116.8625 | 2.4536 | 0.01358 | 0.015641 | -0.030732 | 0.035412 | -0.011004 | -0.028395 | -0.021965 | -0.049377 | -0.062292 | 0.0011708 | 0.040665 | -0.018794 | -0.0096728 | -0.010333 | -0.059509 | -0.045776 | -0.009155 | -0.027466 | 0.064087 | -0.041199 | -0.09613 | -0.009155 | -0.059509 | 0.24719 | 0.041199 | 0.086975 | 0.050354 | 0.13275 | 116.8533 | -2.4994 | -2.4811 | 116.9266 | 116.7664 | 116.8213 | -0.086975 | -0.032044 | 117.1097 | -2.5131 | -2.4124 | 116.9495 | 116.9952 | 116.9128 | -0.11444 | -0.19684 | 0.073242 | -0.018311 | -0.16022 | -0.20599 | -0.036621 | -0.3067 | 116.8167 | 116.803 | -2.4628 | -2.2064 | 116.835 | 116.9037 | 116.803 | 116.8533
4335.4688 | 119.989 | -117.8833 | 1.7212 | 0.0059509 | 0.015641 | -0.032441 | 0.0044369 | 0.027021 | -0.036299 | 0.02845 | 0.048279 | 0.015466 | -0.017414 | 0.022294 | 0.023289 | 0.028138 | 0.019361 | -0.054932 | -0.032043 | 0.2243 | 0.091553 | 0.086975 | 0.091553 | 0.091553 | -0.09613 | -0.050354 | -0.091553 | 0.004578 | 0.082397 | 0.091553 | 0.09613 | 118.1076 | -1.7532 | -1.6296 | 117.9703 | 117.9749 | 117.9749 | -0.13275 | -0.13275 | 117.7917 | -1.7715 | -1.7166 | 117.9657 | 117.9794 | 117.9749 | 0.18768 | 0.18311 | -0.13733 | -0.13275 | 0.17395 | 0.096131 | -0.25635 | 0.041199 | 117.8513 | 117.8329 | -1.4969 | -1.8127 | 117.9749 | 117.8879 | 117.8284 | 117.7872
4337.1875 | 116.4688 | -86.5997 | 29.393 | 0.13565 | 0.012864 | -0.033509 | 0.0042233 | -0.021044 | -0.035871 | -0.034996 | 0.054382 | 0.01568 | -0.016774 | 0.022294 | 0.022862 | 0.027711 | 0.018933 | -0.07782 | -0.036621 | 0.23804 | 0.091553 | 0.091553 | 0.09613 | 0.09613 | -0.15106 | 0.10071 | -0.086975 | 0.027466 | 0.086975 | 0.091553 | 0.091553 | 86.8378 | -29.4296 | -29.3015 | 86.6913 | 86.6959 | 86.6959 | -0.14191 | -0.14191 | 86.5128 | -29.2923 | -29.3655 | 86.6867 | 86.6913 | 86.6913 | 0.17853 | 0.17853 | -0.14648 | -0.14648 | 0.17395 | 0.11444 | -0.27466 | 0.18768 | 86.5631 | 86.7004 | -29.155 | -29.48 | 86.6913 | 86.6272 | 86.5219 | 86.4487
4338.9688 | 119.6182 | -118.8171 | 0.60883 | 0.0059509 | 0.021409 | -0.02945 | 0.021313 | -0.022753 | -0.04228 | -0.030723 | -0.073792 | -0.073828 | -0.0095104 | 0.033188 | -0.016658 | -0.010527 | -0.015674 | -0.31586 | -0.018311 | 0.20599 | 0.09613 | 0.086975 | 0.086975 | 0.091553 | -0.15106 | 0.082397 | -0.091553 | -0.25635 | -0.032043 | -0.21973 | 0.064087 | 119.0231 | -0.62714 | -0.5127 | 118.9041 | 118.9087 | 118.9041 | -0.11444 | -0.11902 | 118.7256 | -0.52643 | -0.86517 | 118.7851 | 118.8812 | 118.5974 | 0.15564 | -0.12817 | -0.11902 | -0.10986 | 0.05951 | -0.1648 | -0.22431 | 0.17395 | 118.7988 | 118.8995 | -0.40283 | -0.70038 | 118.9133 | 118.5608 | 118.5013 | 118.6661
4340.7031 | 120.1218 | -119.577 | 0.21515 | 0.02121 | 0.010515 | -0.034363 | 0.03349 | -0.014635 | -0.028608 | -0.021965 | -0.061584 | -0.063147 | 0.00095715 | 0.044083 | -0.018367 | -0.010314 | -0.012256 | -0.054932 | -0.054932 | 0.050354 | -0.022888 | 0.10071 | -0.004578 | -0.036621 | 0.032043 | -0.082397 | 0.24719 | 0.059509 | 0.16479 | 0.082397 | 0.16479 | 119.6274 | -0.27008 | -0.23804 | 119.6777 | 119.5404 | 119.5724 | -0.086975 | -0.054932 | 119.8242 | -0.29755 | -0.15564 | 119.7418 | 119.7418 | 119.6594 | -0.082397 | -0.16479 | 0.050354 | -0.073242 | -0.082397 | -0.18768 | -0.10529 | -0.32959 | 119.5221 | 119.4946 | -0.16479 | 0.032043 | 119.5541 | 119.6365 | 119.5221 | 119.6091
4342.4531 | 120.2408 | -119.696 | 0.21515 | 0.02121 | 0.013505 | -0.032654 | 0.035412 | -0.0095083 | -0.027967 | -0.020469 | -0.079895 | -0.062292 | -0.0013928 | 0.040238 | -0.016658 | -0.010527 | -0.006915 | -0.054932 | -0.059509 | 0.013733 | -0.018311 | 0.059509 | -0.054932 | -0.086975 | 0.009155 | -0.009155 | 0.21057 | 0.032043 | 0.10986 | 0.032043 | 0.12817 | 119.7098 | -0.27466 | -0.23346 | 119.7556 | 119.6091 | 119.6411 | -0.10071 | -0.068665 | 119.9066 | -0.2243 | -0.18311 | 119.8059 | 119.8242 | 119.7281 | -0.082397 | -0.17853 | 0.045776 | -0.032044 | -0.10071 | -0.17853 | -0.073242 | -0.21973 | 119.6365 | 119.6869 | -0.20142 | -0.004578 | 119.6777 | 119.7281 | 119.6411 | 119.7052
4344.3438 | 120.3873 | -119.8471 | 0.21973 | 0.01358 | 0.013505 | -0.032654 | 0.034344 | -0.011004 | -0.029676 | -0.020897 | -0.095154 | -0.064642 | -0.0022472 | 0.037461 | -0.019435 | -0.0098864 | -0.010333 | -0.022888 | -0.064087 | 0.004578 | 0.064087 | 0.2243 | 0.036621 | -0.064087 | 0.10071 | -0.004578 | 0.10071 | 0.091553 | 0.16937 | 0.091553 | 0.11902 | 119.8517 | -0.28381 | -0.15564 | 120.0714 | 119.783 | 119.8837 | -0.068665 | 0.032043 | 119.9478 | -0.22431 | -0.12817 | 120.0165 | 119.9661 | 119.9387 | 0.018311 | -0.009155 | 0.21973 | 0.059509 | 0.068665 | -0.009155 | -0.068665 | -0.10529 | 119.783 | 119.8425 | -0.21515 | -0.11902 | 119.9112 | 119.9387 | 119.8242 | 119.9478
4346.1562 | 119.989 | -119.4534 | 0.25177 | 0.044098 | 0.016923 | -0.029664 | 0.022381 | -0.028521 | -0.026899 | -0.034996 | 0.057434 | 0.015466 | -0.0065196 | 0.021866 | -0.028194 | -0.018431 | -0.017169 | -0.064087 | -0.022888 | -0.036621 | -0.21973 | 0.086975 | 0.091553 | 0.091553 | -0.022888 | -0.073242 | 0.022888 | 0.027466 | -0.21057 | 0.091553 | 0.091553 | 119.4168 | -0.27466 | -0.4715 | 119.5404 | 119.545 | 119.545 | 0.12817 | 0.12817 | 119.4763 | -0.32501 | -0.2243 | 119.2429 | 119.545 | 119.545 | 0.068665 | 0.068665 | 0.1236 | -0.18311 | -0.23346 | 0.004578 | 0.013733 | -0.09613 | 119.4305 | 119.3802 | -0.28839 | -0.22888 | 119.2337 | 119.4809 | 119.3893 | 119.4305
4347.9688 | 120.3644 | -119.8151 | 0.1831 | 0.0059509 | 0.014787 | -0.031159 | 0.035199 | -0.0030997 | -0.030317 | -0.019188 | -0.20197 | -0.061438 | -0.00075185 | 0.038102 | -0.015804 | -0.0094592 | -0.016314 | 0.004578 | -0.068665 | 0.022888 | 0.032043 | 0.018311 | -0.20142 | -0.30212 | 0.073242 | -0.013733 | 0.022888 | 0.11444 | 0.16022 | 0.013733 | 0.059509 | 119.838 | -0.25177 | -0.15106 | 119.8334 | 119.5129 | 119.6136 | -0.32501 | -0.2243 | 119.838 | -0.19684 | -0.068664 | 119.9753 | 119.8746 | 119.8288 | 0.036621 | -0.009155 | -0.004577 | 0.009155 | 0.13733 | 0.091553 | -0.091553 | -0.036621 | 119.7464 | 119.8013 | -0.16022 | -0.16022 | 119.8471 | 119.9295 | 119.8196 | 119.8883
4349.7812 | 120.4468 | -119.8746 | 0.20599 | 0.02121 | 0.013719 | -0.033295 | 0.039258 | -0.0075857 | -0.029676 | -0.02111 | -0.22333 | -0.063147 | -0.0013928 | 0.040665 | -0.012386 | -0.011168 | -0.011828 | -0.013733 | -0.073242 | 0 | 0.013733 | 0.068665 | -0.19226 | -0.3067 | 0.073242 | -0.004578 | 0 | 0.12817 | 0.14191 | 0.054932 | 0.059509 | 119.8746 | -0.27924 | -0.19226 | 119.9432 | 119.5679 | 119.6823 | -0.3067 | -0.19226 | 119.8746 | -0.21057 | -0.07782 | 120.0165 | 119.9341 | 119.9295 | 0.059509 | 0.054932 | 0.068665 | 0.013733 | 0.14191 | 0.12817 | -0.073242 | -0.004578 | 119.8013 | 119.87 | -0.20599 | -0.20599 | 119.8883 | 120.0027 | 119.8608 | 119.9478
4351.6094 | 120.3735 | -119.9936 | 0.31586 | 0.028839 | 0.015428 | -0.033295 | 0.039044 | -0.011004 | -0.030104 | -0.022178 | 0.054382 | -0.07276 | -0.00182 | 0.023362 | -0.02264 | -0.0101 | -0.012042 | -0.07782 | -0.032043 | -0.027466 | -0.073242 | -0.19684 | -0.16022 | 0.082397 | -0.059509 | 0.032043 | -0.050354 | -0.004578 | 0.032043 | -0.27008 | -0.054932 | 119.9661 | -0.3479 | -0.3891 | 119.7968 | 120.076 | 119.8334 | 0.10986 | -0.13275 | 119.9432 | -0.28381 | -0.32044 | 120.0256 | 119.9387 | 119.7235 | -0.004578 | -0.21973 | -0.16937 | -0.045776 | 0.082397 | 0.045776 | -0.004577 | 0.082397 | 119.9615 | 120.0256 | -0.34332 | -0.36621 | 119.9203 | 119.989 | 119.9158 | 119.9341
4353.4219 | 120.3918 | -119.9753 | 0.37079 | 0.02121 | 0.015641 | -0.029664 | 0.036908 | -0.0097219 | -0.028181 | -0.026023 | 0.051331 | 0.011194 | -0.00075185 | 0.033402 | -0.017513 | -0.016936 | -0.021014 | -0.045776 | -0.018311 | -0.022888 | -0.07782 | -0.21973 | -0.15106 | 0.086975 | -0.068665 | 0.036621 | -0.013733 | -0.018311 | 0.004578 | -0.25177 | 0.004578 | 119.9524 | -0.3891 | -0.44861 | 119.7556 | 120.0623 | 119.8242 | 0.10986 | -0.12817 | 119.9615 | -0.33417 | -0.3891 | 119.9799 | 119.9799 | 119.7235 | 0.018311 | -0.23804 | -0.19684 | -0.054932 | 0.018311 | -0.004578 | 0.004577 | 0.050354 | 119.957 | 120.0119 | -0.39368 | -0.38452 | 119.8975 | 119.957 | 119.9295 | 119.9066
4355.1562 | 120.4834 | -120.0897 | 0.25177 | 0.02121 | 0.014787 | -0.030304 | 0.037976 | -0.011004 | -0.029036 | -0.020469 | -0.01886 | -0.063147 | -0.0016064 | 0.038743 | -0.016658 | -0.0092456 | -0.014178 | -0.059509 | -0.054932 | 0 | -0.022888 | 0.11444 | 0.022888 | -0.004578 | 0.027466 | 0.022888 | -0.009155 | 0.050354 | 0.1236 | 0.041199 | 0.13733 | 120.0897 | -0.3067 | -0.27466 | 120.2042 | 120.0851 | 120.1126 | -0.004578 | 0.022888 | 120.0806 | -0.22888 | -0.20142 | 120.2133 | 120.2271 | 120.1309 | 0.14648 | 0.050354 | 0.11444 | -0.022888 | 0.13275 | 0.059509 | -0.054932 | 0.032043 | 120.0348 | 120.1126 | -0.25177 | -0.26093 | 120.0668 | 120.1401 | 120.0302 | 120.1172
4356.9531 | 120.5521 | -120.0623 | 0.26093 | 0.02121 | 0.014146 | -0.032868 | 0.035626 | -0.012072 | -0.028181 | -0.022819 | -0.021912 | -0.063147 | -0.00182 | 0.037034 | -0.019435 | -0.011382 | -0.011828 | -0.018311 | -0.068665 | 0.004578 | 0.050354 | 0.19684 | 0.091553 | 0.054932 | 0.10071 | -0.004578 | 0.004578 | 0.091553 | 0.19226 | 0.11902 | 0.17853 | 120.0668 | -0.32959 | -0.21057 | 120.2591 | 120.1172 | 120.1538 | 0.050354 | 0.086975 | 120.0668 | -0.2655 | -0.16937 | 120.2545 | 120.2408 | 120.1813 | 0.17395 | 0.11444 | 0.19226 | 0.045776 | 0.18768 | 0.086975 | -0.073243 | -0.009156 | 119.9936 | 120.0577 | -0.25635 | -0.25635 | 120.1126 | 120.1538 | 120.0439 | 120.163
4358.75 | 120.2682 | -119.783 | 0.24261 | 0.028839 | 0.01436 | -0.031586 | 0.036694 | -0.011858 | -0.030104 | -0.022392 | 0.054382 | 0.015253 | -0.00096545 | 0.026352 | -0.032466 | -0.026549 | -0.027636 | -0.050354 | -0.027466 | -0.022888 | -0.027466 | -0.041199 | -0.15106 | 0.091553 | -0.004578 | 0.027466 | -0.027466 | 0.022888 | 0.073242 | -0.1236 | 0.041199 | 119.7601 | -0.27008 | -0.27008 | 119.7418 | 119.8746 | 119.632 | 0.11444 | -0.12817 | 119.7556 | -0.21515 | -0.21973 | 119.8563 | 119.8242 | 119.6594 | 0.068665 | -0.09613 | -0.018311 | -0.004578 | 0.10071 | 0.050354 | -0.004578 | 0.054932 | 119.7556 | 119.8105 | -0.2655 | -0.27008 | 119.7556 | 119.8059 | 119.7327 | 119.7784
4360.5781 | 120.4376 | -120.0668 | 0.27466 | 0.01358 | 0.01671 | -0.033082 | 0.036694 | -0.0056631 | -0.02989 | -0.022178 | -0.19586 | -0.061651 | -0.0020336 | 0.034043 | -0.019649 | -0.01245 | -0.014178 | -0.086975 | -0.036621 | -0.032043 | -0.086975 | 0.050354 | -0.07782 | -0.3067 | -0.054932 | 0.054932 | -0.032043 | -0.032043 | 0.054932 | -0.032043 | -0.022888 | 120.0348 | -0.31128 | -0.36163 | 120.1172 | 119.7601 | 119.989 | -0.27466 | -0.045777 | 120.0348 | -0.21973 | -0.3067 | 120.1218 | 120.0439 | 120.0348 | 0.009155 | 0 | 0.082397 | -0.054932 | 0.086975 | 0 | -0.004578 | 0.086975 | 120.0302 | 120.1218 | -0.3067 | -0.3067 | 119.9799 | 120.0348 | 119.9799 | 120.0119
4362.375 | 120.575 | -120.1218 | 0.23804 | 0.01358 | 0.01201 | -0.032013 | 0.034344 | -0.010149 | -0.030104 | -0.023246 | 0.011658 | -0.062933 | -0.0028882 | 0.03917 | -0.015377 | -0.012236 | -0.014819 | -0.059509 | -0.059509 | 0.004578 | -0.022888 | 0.10986 | 0.027466 | 0.032043 | -0.004578 | 0.013733 | -0.009155 | 0.068665 | 0.1236 | 0.068665 | 0.16022 | 120.1263 | -0.29755 | -0.26093 | 120.2316 | 120.1538 | 120.1492 | 0.027465 | 0.022888 | 120.1126 | -0.2243 | -0.16937 | 120.2454 | 120.282 | 120.1904 | 0.16937 | 0.07782 | 0.10529 | -0.027466 | 0.13275 | 0.07782 | -0.064087 | 0.022888 | 120.0623 | 120.1355 | -0.23346 | -0.24719 | 120.0989 | 120.1904 | 120.0623 | 120.1172
4364.1719 | 120.4926 | -120.2042 | 0.27466 | 0.02121 | 0.013505 | -0.033722 | 0.038617 | -0.0090811 | -0.029036 | -0.021537 | -0.22638 | -0.069769 | -0.00182 | 0.039384 | -0.016658 | -0.010955 | -0.007983 | -0.07782 | -0.013733 | -0.022888 | -0.10986 | -0.004578 | -0.1831 | -0.41657 | -0.091553 | 0.054932 | -0.045776 | -0.022888 | -0.004578 | -0.064087 | -0.004578 | 120.1813 | -0.28839 | -0.38452 | 120.1996 | 119.7876 | 120.0211 | -0.39368 | -0.16022 | 120.1584 | -0.21973 | -0.29755 | 120.1996 | 120.1996 | 120.1401 | 0.041198 | -0.018311 | 0.01831 | -0.086975 | 0.041198 | 0.022888 | 0.009155 | 0.10071 | 120.1904 | 120.2591 | -0.29755 | -0.32043 | 120.0943 | 120.1813 | 120.1263 | 120.1126
4365.9219 | 120.5658 | -120.1904 | 0.24261 | 0.028839 | 0.015001 | -0.033509 | 0.038189 | -0.0077993 | -0.029249 | -0.02346 | -0.21722 | -0.071478 | -0.0028882 | 0.029984 | -0.01559 | -0.013945 | -0.012042 | -0.036621 | -0.027466 | -0.032043 | -0.013733 | 0.10529 | -0.09613 | -0.32501 | 0.032043 | 0.045776 | -0.013733 | 0.045776 | 0.10071 | 0.004578 | -0.009155 | 120.1584 | -0.27008 | -0.25635 | 120.2957 | 119.8654 | 120.0943 | -0.29297 | -0.064087 | 120.1767 | -0.19684 | -0.19684 | 120.2911 | 120.1813 | 120.195 | 0.004578 | 0.018311 | 0.13733 | 0.01831 | 0.11444 | 0.059509 | 0.004577 | 0.059509 | 120.163 | 120.2362 | -0.27466 | -0.25635 | 120.1767 | 120.2362 | 120.1538 | 120.2225
4367.7188 | 120.5933 | -120.2179 | 0.27008 | 0.028839 | 0.013933 | -0.032441 | 0.035199 | -0.0063041 | -0.030958 | -0.021965 | -0.21722 | -0.064642 | -0.00096545 | 0.040238 | -0.018581 | -0.010741 | -0.0077694 | -0.036621 | -0.027466 | -0.022888 | -0.032043 | 0.10071 | -0.041199 | -0.31586 | 0.009155 | 0.036621 | -0.032043 | 0.050354 | 0.10071 | 0.013733 | 0.064087 | 120.195 | -0.29755 | -0.30212 | 120.3186 | 119.902 | 120.1767 | -0.29297 | -0.018311 | 120.1859 | -0.23346 | -0.21973 | 120.3186 | 120.282 | 120.2316 | 0.09613 | 0.045776 | 0.1236 | -0.009155 | 0.13275 | 0.082397 | -0.004578 | 0.068664 | 120.1904 | 120.2545 | -0.29297 | -0.30212 | 120.1859 | 120.2682 | 120.1813 | 120.2271
4369.5156 | 120.5429 | -120.2591 | 0.28839 | 0.02121 | 0.015214 | -0.033509 | 0.037121 | -0.012285 | -0.030745 | -0.022819 | -0.061584 | -0.060797 | -0.00075185 | 0.035966 | -0.020717 | -0.011809 | -0.011401 | -0.10986 | -0.027466 | -0.041199 | -0.10071 | 0.036621 | -0.009155 | -0.091553 | -0.073242 | 0.041199 | -0.073242 | -0.045776 | 0.041199 | -0.041199 | 0.07782 | 120.2179 | -0.31586 | -0.3891 | 120.2957 | 120.1675 | 120.2499 | -0.050354 | 0.032044 | 120.1859 | -0.24719 | -0.33417 | 120.3003 | 120.3369 | 120.2179 | 0.15106 | 0.032043 | 0.07782 | -0.059509 | 0.11444 | 0.027466 | 0.013733 | 0.11444 | 120.2316 | 120.3003 | -0.32959 | -0.36163 | 120.1584 | 120.2133 | 120.1492 | 120.1859
4371.2656 | 120.5704 | -120.3094 | 0.25635 | 0.02121 | 0.014573 | -0.034577 | 0.037549 | -0.0067313 | -0.02754 | -0.020469 | -0.07074 | -0.060584 | -0.0024608 | 0.036606 | -0.014522 | -0.01245 | -0.013965 | -0.073242 | -0.018311 | -0.022888 | -0.10986 | 0.004578 | -0.09613 | -0.18768 | -0.07782 | 0.054932 | -0.045776 | -0.032043 | 0.022888 | -0.07782 | 0.086975 | 120.2866 | -0.27466 | -0.36621 | 120.314 | 120.1218 | 120.2133 | -0.16479 | -0.073242 | 120.2637 | -0.20142 | -0.28839 | 120.3323 | 120.3964 | 120.2316 | 0.13275 | -0.032044 | 0.027466 | -0.086975 | 0.068664 | 0.013733 | 0.004577 | 0.10071 | 120.2911 | 120.3644 | -0.27924 | -0.30212 | 120.1996 | 120.2774 | 120.2362 | 120.2316
4373.0625 | 120.6436 | -120.2866 | 0.26093 | 0.044098 | 0.01436 | -0.033082 | 0.037549 | -0.0065177 | -0.030104 | -0.020683 | -0.082947 | -0.059943 | -0.0022472 | 0.02443 | -0.017513 | -0.0101 | -0.013537 | -0.036621 | -0.032043 | -0.022888 | -0.041199 | 0.086975 | 0 | -0.11444 | 0.004578 | 0.041199 | -0.027466 | 0.013733 | 0.10986 | 0.018311 | 0.10986 | 120.2637 | -0.29297 | -0.30212 | 120.3735 | 120.1721 | 120.2866 | -0.091553 | 0.022888 | 120.2591 | -0.21973 | -0.24719 | 120.3964 | 120.3964 | 120.3049 | 0.13733 | 0.045777 | 0.10986 | -0.018311 | 0.13733 | 0.041199 | -0.009155 | 0.068665 | 120.2545 | 120.3278 | -0.28381 | -0.28839 | 120.2454 | 120.3003 | 120.2499 | 120.2911
4374.7969 | 120.607 | -120.3232 | 0.2655 | 0.02121 | 0.014146 | -0.033936 | 0.036053 | -0.0092947 | -0.029036 | -0.022392 | 0.011658 | -0.061438 | -0.00032465 | 0.026566 | -0.021358 | -0.013091 | -0.013965 | -0.064087 | -0.032043 | -0.032043 | -0.082397 | 0.045776 | -0.032043 | -0.045776 | -0.07782 | 0.050354 | -0.036621 | -0.045776 | 0.050354 | -0.022888 | 0.07782 | 120.2911 | -0.29755 | -0.3479 | 120.369 | 120.2774 | 120.2911 | -0.013733 | 0 | 120.2866 | -0.21515 | -0.31128 | 120.3735 | 120.401 | 120.3003 | 0.11444 | 0.013733 | 0.077819 | -0.050354 | 0.086975 | -0.009155 | 0 | 0.086975 | 120.2911 | 120.3735 | -0.29755 | -0.30212 | 120.2408 | 120.2774 | 120.2591 | 120.2454
4376.5938 | 120.7489 | -120.3369 | 0.25177 | 0.028839 | 0.013933 | -0.032227 | 0.034558 | -0.0080129 | -0.028181 | -0.021537 | 0.0025024 | -0.064429 | -0.0011792 | 0.035752 | -0.015804 | -0.010955 | -0.010333 | -0.064087 | -0.059509 | -0.013733 | -0.032043 | 0.10529 | 0.027466 | 0.036621 | 0.004578 | 0.022888 | -0.013733 | 0.036621 | 0.14648 | 0.07782 | 0.16022 | 120.3232 | -0.31128 | -0.28381 | 120.4422 | 120.3735 | 120.3644 | 0.050354 | 0.041199 | 120.3232 | -0.22888 | -0.21515 | 120.4834 | 120.4971 | 120.4147 | 0.17395 | 0.091553 | 0.11902 | -0.01831 | 0.16022 | 0.050354 | -0.045776 | 0.036621 | 120.2774 | 120.3598 | -0.2655 | -0.2655 | 120.3049 | 120.3735 | 120.2728 | 120.3415
4378.3906 | 120.6573 | -120.3781 | 0.27008 | 0.01358 | 0.015641 | -0.032441 | 0.035199 | -0.0080129 | -0.030317 | -0.023246 | 0.0055542 | -0.061438 | -0.00053825 | 0.030411 | -0.019222 | -0.013304 | -0.015246 | -0.10071 | -0.036621 | -0.009155 | -0.082397 | 0.041199 | -0.022888 | -0.041199 | -0.073242 | 0.045776 | -0.032043 | -0.064087 | 0.045776 | -0.032043 | 0.068665 | 120.369 | -0.3067 | -0.35248 | 120.4193 | 120.3369 | 120.3552 | -0.032044 | -0.013733 | 120.3461 | -0.22431 | -0.33417 | 120.4239 | 120.4468 | 120.3461 | 0.10071 | 0 | 0.050354 | -0.073242 | 0.077819 | -0.032044 | -0.027466 | 0.077819 | 120.3415 | 120.4239 | -0.27924 | -0.30212 | 120.2957 | 120.314 | 120.2774 | 120.3049
4380.2188 | 120.7169 | -120.3644 | 0.23804 | 0.02121 | 0.01436 | -0.033082 | 0.037549 | -0.0092947 | -0.02754 | -0.023033 | 0.008606 | -0.059515 | -0.00032465 | 0.030625 | -0.012813 | -0.011595 | -0.013324 | -0.073242 | -0.027466 | -0.027466 | -0.091553 | 0.032043 | -0.082397 | -0.045776 | -0.045776 | 0.027466 | -0.041199 | 0.009155 | 0.059509 | -0.013733 | 0.13275 | 120.3369 | -0.2655 | -0.32959 | 120.3964 | 120.3186 | 120.282 | -0.01831 | -0.054931 | 120.3232 | -0.21057 | -0.22888 | 120.4239 | 120.4971 | 120.3506 | 0.17395 | 0.027466 | 0.059509 | -0.064087 | 0.10071 | 0.050354 | 0 | 0.068665 | 120.3369 | 120.3918 | -0.2655 | -0.27924 | 120.2728 | 120.3735 | 120.2911 | 120.3186

## Thermal Data
Fire Time | B Position - Tray - Middle | B Position - Conduit - 3' | B Position - Conduit - Middle | B Position - Conduit - 7' | D Position - 3' | D Position - Middle | D Position - 7'
-0.9646 | 6.7734 | 6.6106 | 6.7024 | 6.6163 | 6.6406 | 6.8873 | 6.9225
0.0354 | 6.7705 | 6.6132 | 6.7065 | 6.617 | 6.6387 | 6.8852 | 6.9306
1.0354 | 6.776 | 6.6125 | 6.7187 | 6.6172 | 6.6379 | 6.8832 | 6.9253
2.0354 | 6.7807 | 6.6153 | 6.7122 | 6.6164 | 6.6441 | 6.9001 | 6.9315
3.0354 | 6.7901 | 6.6149 | 6.7146 | 6.6242 | 6.6506 | 6.8945 | 6.9297
4.0354 | 6.7955 | 6.6141 | 6.7155 | 6.6214 | 6.6617 | 6.9011 | 6.9327
5.0354 | 6.7789 | 6.6175 | 6.7159 | 6.6151 | 6.6592 | 6.906 | 6.9225
6.0354 | 6.7853 | 6.6194 | 6.7137 | 6.6278 | 6.6616 | 6.9052 | 6.9407
7.0354 | 6.8108 | 6.6234 | 6.7179 | 6.6353 | 6.6622 | 6.9248 | 6.9446
8.0354 | 7.0075 | 6.6307 | 6.928 | 6.668 | 6.6896 | 7.2115 | 6.9584
9.0354 | 7.329 | 6.6411 | 7.1972 | 6.8052 | 6.8573 | 7.6941 | 7.5834
10.0354 | 8.0886 | 6.892 | 7.2569 | 6.8966 | 7.7673 | 8.5786 | 8.7952
11.0354 | 10.1484 | 6.8515 | 7.5328 | 6.9671 | 8.6993 | 10.3667 | 10.4745
12.0354 | 12.2551 | 6.8238 | 7.4262 | 7.1107 | 10.7566 | 13.223 | 12.185
13.0354 | 14.4135 | 6.8062 | 7.6616 | 7.3149 | 13.0535 | 16.4711 | 13.8645
14.0354 | 17.2405 | 6.8714 | 7.9566 | 7.5401 | 15.6463 | 20.9416 | 17.2234
15.0354 | 20.7646 | 6.9193 | 8.1931 | 7.6368 | 17.6273 | 25.7265 | 19.5288
16.0354 | 25.5875 | 6.9491 | 8.1911 | 7.7444 | 20.8978 | 30.6265 | 21.9667
17.0354 | 28.5832 | 7.0523 | 8.3494 | 7.74 | 23.7355 | 34.3161 | 23.7792
18.0354 | 33.6705 | 7.094 | 8.6253 | 7.967 | 26.3768 | 37.9511 | 27.2212
19.0354 | 37.3049 | 7.1538 | 8.8749 | 8.0491 | 29.9889 | 43.0952 | 31.0688
20.0354 | 40.5163 | 7.3008 | 9.1489 | 8.589 | 33.3845 | 49.7825 | 34.1204
21.0354 | 42.7969 | 7.2911 | 9.2259 | 8.4896 | 37.6394 | 55.2711 | 37.6197
22.0354 | 45.1197 | 7.5154 | 10.1147 | 8.5551 | 39.668 | 56.6639 | 40.8542
23.0354 | 49.0544 | 7.4145 | 10.4701 | 8.8179 | 41.6608 | 59.7382 | 43.7539
24.0354 | 52.941 | 7.5714 | 10.4166 | 8.7574 | 45.1685 | 66.1676 | 48.6474
25.0354 | 55.7159 | 7.5919 | 10.5123 | 9.0086 | 48.8339 | 68.6845 | 53.0789
26.0354 | 57.9326 | 7.7776 | 10.6032 | 9.0587 | 52.4955 | 72.3989 | 56.1847
27.0354 | 59.8348 | 7.8462 | 11.2183 | 9.0069 | 55.6501 | 76.4267 | 59.3524
28.0354 | 62.5858 | 7.8494 | 11.0847 | 9.2534 | 57.132 | 80.9033 | 61.4627
29.0354 | 65.0332 | 7.9377 | 11.5388 | 9.4792 | 59.1813 | 84.1895 | 63.7638
30.0354 | 67.9443 | 8.0546 | 11.7526 | 9.7219 | 61.8994 | 87.3122 | 66.494
31.0354 | 70.2127 | 8.0804 | 12.059 | 9.7773 | 64.1896 | 89.3774 | 69.5733
32.0354 | 71.5543 | 8.2228 | 12.1895 | 9.9393 | 66.8049 | 91.7391 | 72.1596
33.0354 | 74.4736 | 8.3108 | 12.6182 | 10.0075 | 68.5093 | 94.4608 | 74.8498
34.0354 | 77.1899 | 8.4782 | 13.0681 | 10.3965 | 69.0819 | 97.8568 | 78.5564
35.0354 | 79.9674 | 8.5596 | 13.0252 | 10.1837 | 71.5216 | 101.7058 | 81.6432
36.0354 | 81.8209 | 8.8212 | 13.3025 | 10.5409 | 72.786 | 104.8127 | 83.9866
37.0354 | 84.2056 | 8.8071 | 13.4677 | 10.6292 | 74.15 | 108.1631 | 86.6115
38.0354 | 86.6215 | 9.0518 | 13.6223 | 10.5425 | 75.5625 | 115.0107 | 90.5184
39.0354 | 88.6851 | 9.1525 | 14.0642 | 10.7497 | 76.937 | 119.5597 | 92.835
40.0354 | 91.1794 | 9.156 | 14.1041 | 10.8538 | 77.9703 | 124.2813 | 95.6698
41.0354 | 91.9549 | 9.2348 | 14.0196 | 10.8874 | 79.204 | 127.241 | 98.3208
42.0354 | 92.7585 | 9.2377 | 14.2973 | 10.943 | 79.9542 | 129.7016 | 99.2463
43.0354 | 92.7789 | 9.2933 | 14.5305 | 11.1111 | 81.0335 | 132.1673 | 99.8557
44.0354 | 93.3356 | 9.473 | 14.6432 | 11.2599 | 82.5745 | 135.0679 | 101.0471
45.0354 | 94.6667 | 9.5044 | 15.0357 | 11.4604 | 83.5097 | 137.4888 | 102.1073
46.0354 | 96.4374 | 9.5951 | 15.171 | 11.4942 | 83.8989 | 139.1049 | 103.529
47.0354 | 97.7139 | 9.9003 | 15.3009 | 11.522 | 85.675 | 140.6698 | 105.9531
48.0354 | 98.6874 | 10.116 | 15.8749 | 11.6786 | 87.2573 | 142.1176 | 106.8191
49.0354 | 100.2736 | 10.2263 | 16.0343 | 12.3632 | 88.2669 | 143.2206 | 107.5446
50.0354 | 103.2493 | 10.1314 | 16.0759 | 12.2371 | 90.0882 | 145.5203 | 108.2561
51.0354 | 104.918 | 10.0892 | 16.6625 | 12.4002 | 92.3929 | 147.2506 | 109.0673
52.0354 | 106.5822 | 10.2687 | 16.7268 | 12.5745 | 94.984 | 148.4193 | 110.7018
53.0354 | 109.4081 | 10.3751 | 17.2088 | 12.835 | 96.7564 | 149.2397 | 111.8971
54.0354 | 111.3457 | 10.5073 | 17.3533 | 12.8977 | 99.1983 | 150.1836 | 113.2497
55.0354 | 112.6403 | 10.5495 | 17.254 | 12.877 | 103.0808 | 152.3962 | 114.1984
56.0354 | 114.3119 | 10.5454 | 17.4218 | 13.34 | 103.91 | 153.281 | 114.7736
57.0354 | 115.9559 | 11.0245 | 17.8999 | 13.4284 | 106.1408 | 154.5556 | 115.5808
58.0354 | 117.2895 | 11.0467 | 17.9912 | 13.711 | 107.9727 | 155.0706 | 116.2853
59.0354 | 117.9481 | 11.166 | 18.0394 | 13.7598 | 109.8962 | 155.1095 | 117.1107
60.0354 | 118.0875 | 11.242 | 18.2654 | 13.9974 | 111.6456 | 155.6642 | 117.7899
61.0354 | 119.4958 | 11.2918 | 18.5713 | 14.1961 | 112.773 | 155.3412 | 118.7349
62.0354 | 120.2122 | 11.3095 | 18.8349 | 14.6099 | 113.8198 | 155.1456 | 119.352
63.0354 | 121.2887 | 11.4695 | 19.0653 | 15.0434 | 116.1148 | 156.0492 | 120.0664
64.0354 | 121.3671 | 11.6181 | 19.3839 | 15.2478 | 116.923 | 156.3055 | 120.3129
65.0354 | 122.2595 | 11.8677 | 19.8527 | 15.4297 | 118.7625 | 156.4227 | 121.564
66.0354 | 121.5709 | 11.9132 | 20.5351 | 15.6749 | 118.8118 | 155.1654 | 121.5178
67.0354 | 122.3243 | 12.077 | 21.254 | 15.7896 | 118.1134 | 154.031 | 121.4551
68.0354 | 121.5343 | 11.9144 | 21.2596 | 15.868 | 118.2802 | 153.0397 | 121.3322
69.0354 | 122.3719 | 11.9957 | 23.2236 | 15.8772 | 118.0166 | 152.8527 | 121.8865
70.0354 | 122.4425 | 11.9034 | 22.3662 | 16.2096 | 118.6526 | 152.5555 | 122.5459
71.0354 | 122.8717 | 11.9934 | 22.5935 | 16.3251 | 118.8767 | 151.508 | 122.2704
72.0354 | 124.2104 | 12.1847 | 23.5572 | 16.5421 | 119.959 | 151.7918 | 122.9499
73.0354 | 125.0872 | 12.5014 | 24.6362 | 16.7772 | 120.7999 | 152.5694 | 123.8428
74.0354 | 125.4959 | 12.4608 | 24.8452 | 16.9798 | 121.7127 | 151.7278 | 123.9243
75.0354 | 125.2955 | 12.4444 | 24.8618 | 17.1483 | 121.5756 | 152.0565 | 124.6186
76.0354 | 125.2278 | 12.6165 | 26.7895 | 17.3372 | 121.6919 | 150.8031 | 124.8104
77.0354 | 126.025 | 12.5048 | 26.3722 | 17.5334 | 121.0974 | 150.4274 | 125.0473
78.0354 | 126.4602 | 12.6477 | 26.7024 | 17.6716 | 121.8482 | 149.7226 | 125.1214
79.0354 | 126.5932 | 12.8929 | 27.0705 | 17.951 | 121.7992 | 149.6002 | 125.6948
80.0354 | 126.8967 | 13.2715 | 28.0184 | 17.929 | 121.4769 | 148.5581 | 125.669
81.0354 | 127.1173 | 13.6128 | 29.0428 | 18.1419 | 121.7229 | 148.3424 | 125.7402
82.0354 | 127.4914 | 13.6895 | 29.3088 | 18.2226 | 122.2324 | 148.1598 | 126.4242
83.0354 | 127.7114 | 13.6929 | 29.9378 | 18.4314 | 121.5856 | 147.3278 | 126.2036
84.0354 | 128.5854 | 13.8429 | 30.1854 | 18.5873 | 121.1197 | 146.3124 | 125.8741
85.0354 | 128.3453 | 14.041 | 31.4962 | 18.8062 | 121.0334 | 146.2005 | 126.2947
86.0354 | 127.7018 | 14.0344 | 31.8261 | 19.0427 | 121.0986 | 145.0417 | 126.1607
87.0354 | 127.6376 | 14.095 | 32.7002 | 18.9591 | 120.5365 | 144.5322 | 126.266
88.0354 | 127.5525 | 14.1499 | 33.022 | 19.158 | 120.4979 | 143.9743 | 125.9722
89.0354 | 128.2823 | 14.4249 | 32.9403 | 19.1903 | 120.2015 | 142.8059 | 125.5985
90.0354 | 128.1746 | 14.494 | 33.0635 | 19.3478 | 119.7275 | 142.8005 | 125.8265
91.0354 | 128.4146 | 14.729 | 34.3698 | 19.5454 | 119.1505 | 142.3252 | 125.8776
92.0354 | 128.133 | 14.8386 | 34.6163 | 19.8137 | 119.1358 | 141.6487 | 125.9798
93.0354 | 128.4526 | 14.8636 | 35.1937 | 20.0805 | 118.9928 | 140.8524 | 125.9574
94.0354 | 128.6716 | 15.336 | 35.2514 | 20.0522 | 119.3597 | 140.9177 | 126.6253
95.0354 | 129.4647 | 15.4841 | 36.3374 | 20.1974 | 120.3073 | 141.7089 | 127.9551
96.0354 | 130.8156 | 15.5897 | 36.6534 | 20.7095 | 121.3989 | 142.2943 | 128.8064
97.0354 | 131.7787 | 15.6075 | 37.5292 | 20.6155 | 121.6569 | 142.6566 | 129.3784
98.0354 | 131.9391 | 15.3257 | 38.9587 | 20.645 | 121.3906 | 142.1619 | 129.4735
99.0354 | 132.3881 | 15.4746 | 38.1271 | 20.7815 | 121.2136 | 141.5926 | 129.5976
100.0354 | 132.5319 | 15.6821 | 39.1491 | 20.9152 | 121.1587 | 141.6146 | 130.5706
101.0354 | 132.5168 | 15.7077 | 39.7072 | 21.0621 | 121.3776 | 141.7564 | 131.1033
102.0354 | 132.9534 | 16.0642 | 39.8761 | 21.1541 | 122.6043 | 143.1658 | 132.0495
103.0354 | 133.5924 | 16.0864 | 42.1231 | 21.5154 | 123.244 | 144.0078 | 133.1281
104.0354 | 133.0255 | 16.2353 | 42.6789 | 21.7912 | 123.4901 | 144.5693 | 134.3391
105.0354 | 134.6953 | 16.4293 | 42.1027 | 21.9496 | 124.6001 | 145.4526 | 134.9397
106.0354 | 135.3356 | 16.8433 | 43.1948 | 22.0176 | 125.374 | 146.4598 | 135.9752
107.0354 | 136.0847 | 16.8898 | 43.7472 | 22.1571 | 125.9384 | 148.0295 | 136.9262
108.0354 | 136.9107 | 16.7739 | 43.7358 | 22.279 | 126.6679 | 149.2235 | 138.378
109.0354 | 137.3476 | 16.939 | 44.7698 | 22.1165 | 126.7537 | 150.0611 | 139.6296
110.0354 | 137.0366 | 17.0885 | 44.8753 | 22.2934 | 126.4464 | 150.307 | 140.0874
111.0354 | 136.957 | 17.2894 | 45.5161 | 22.6115 | 127.4611 | 151.1274 | 140.9334
112.0354 | 137.0814 | 17.3335 | 46.0047 | 22.7027 | 127.7731 | 151.6648 | 142.1332
113.0354 | 137.5971 | 17.5286 | 46.1392 | 22.7961 | 128.3702 | 152.5512 | 143.8544
114.0354 | 138.1856 | 17.7279 | 47.8128 | 23.1071 | 130.3483 | 154.7512 | 145.2339
115.0354 | 138.953 | 17.9564 | 47.4536 | 23.2324 | 131.3761 | 155.6034 | 146.1584
116.0354 | 139.1293 | 17.8052 | 48.2069 | 23.2489 | 132.3285 | 156.8147 | 147.1132
117.0354 | 140.2405 | 17.7902 | 48.3266 | 23.7377 | 133.0043 | 157.2093 | 148.1837
118.0354 | 141.5838 | 17.8389 | 48.9895 | 23.7859 | 134.8416 | 157.5577 | 149.1548
119.0354 | 141.6456 | 18.1234 | 50.079 | 23.8529 | 136.8956 | 159.6625 | 150.9335
120.0354 | 142.512 | 18.1018 | 49.9805 | 23.9054 | 138.34 | 161.9577 | 153.6491
121.0354 | 143.4841 | 18.2549 | 50.2764 | 23.8755 | 139.7477 | 163.314 | 155.9977
122.0354 | 144.35 | 18.4509 | 51.4138 | 24.1631 | 140.1515 | 165.1343 | 157.6187
123.0354 | 146.0058 | 18.6684 | 52.0135 | 24.3657 | 140.6838 | 166.3326 | 158.6602
124.0354 | 148.3684 | 18.7555 | 53.197 | 24.5157 | 140.7592 | 168.1703 | 160.9483
125.0354 | 150.3369 | 18.9256 | 53.4033 | 24.9167 | 141.1284 | 169.4103 | 161.6821
126.0354 | 151.1865 | 19.067 | 53.5231 | 25.2671 | 140.7707 | 170.184 | 162.2349
127.0354 | 150.9043 | 19.1047 | 53.9902 | 25.37 | 142.5953 | 170.8134 | 162.168
128.0354 | 151.1593 | 19.4731 | 54.2247 | 25.5187 | 141.9947 | 170.0774 | 161.9378
129.0354 | 151.3744 | 19.4233 | 54.442 | 25.4678 | 143.2442 | 171.2145 | 163.0423
130.0354 | 152.3614 | 19.5155 | 54.7209 | 25.4713 | 143.3987 | 173.5689 | 163.9196
131.0354 | 152.8367 | 19.6098 | 55.0805 | 25.6828 | 144.4052 | 174.525 | 164.0421
132.0354 | 154.0151 | 19.6516 | 56.2904 | 26.0914 | 145.1447 | 175.6234 | 165.4852
133.0354 | 153.9634 | 19.6985 | 56.0645 | 26.305 | 146.2599 | 177.4566 | 167.2562
134.0354 | 154.3374 | 20.0596 | 56.5523 | 26.3896 | 146.4459 | 177.5959 | 167.9878
135.0354 | 154.2308 | 20.2535 | 57.9726 | 26.4169 | 146.4309 | 177.7202 | 168.4335
136.0354 | 153.3901 | 20.3267 | 58.9341 | 26.733 | 145.4599 | 175.8987 | 168.1782
137.0354 | 151.8027 | 20.4365 | 59.7024 | 26.9115 | 144.1124 | 175.1189 | 167.1453
138.0354 | 151.5362 | 20.492 | 59.563 | 26.9726 | 144.7489 | 175.3204 | 168.073
139.0354 | 151.9509 | 20.5978 | 59.5595 | 27.1424 | 145.4561 | 177.9898 | 169.6111
140.0354 | 152.1692 | 20.933 | 60.4614 | 27.3678 | 146.208 | 178.6218 | 169.2084
141.0354 | 152.5187 | 21.004 | 60.7276 | 27.6044 | 147.256 | 179.5595 | 169.6753
142.0354 | 153.2248 | 21.1282 | 61.3578 | 27.6209 | 147.7632 | 180.2167 | 169.92
143.0354 | 152.7185 | 21.1163 | 61.4455 | 27.6731 | 147.7082 | 181.1713 | 171.5309
144.0354 | 152.562 | 21.3613 | 62.5118 | 27.9083 | 147.1667 | 182.2883 | 172.9241
145.0354 | 153.0074 | 21.5668 | 62.7833 | 27.9708 | 147.7442 | 184.1316 | 174.6967
146.0354 | 153.1102 | 21.6757 | 63.2387 | 28.1717 | 148.1677 | 185.246 | 175.7451
147.0354 | 153.5617 | 21.7283 | 64.0233 | 28.4527 | 148.9586 | 184.3199 | 175.8264
148.0354 | 153.611 | 21.7734 | 64.3257 | 28.5944 | 147.6743 | 183.6959 | 175.273
149.0354 | 152.8661 | 22.0475 | 65.7403 | 28.6832 | 148.3936 | 183.3361 | 174.1013
150.0354 | 152.4414 | 22.5846 | 66.646 | 28.9513 | 148.6178 | 182.3068 | 173.2482
151.0354 | 152.1324 | 22.4884 | 66.3982 | 29.3581 | 148.0704 | 181.368 | 171.8656
152.0354 | 152.2222 | 22.5196 | 66.7826 | 29.6134 | 147.7076 | 180.5677 | 171.0848
153.0354 | 152.0067 | 22.6377 | 67.1231 | 29.4559 | 147.568 | 180.741 | 170.2975
154.0354 | 151.0222 | 22.7503 | 67.8653 | 29.5702 | 149.1838 | 180.9584 | 170.2062
155.0354 | 150.9752 | 22.7719 | 68.1788 | 29.6508 | 150.3254 | 181.6668 | 170.7433
156.0354 | 151.1529 | 23.1018 | 68.8884 | 29.7404 | 151.2087 | 181.8096 | 170.7144
157.0354 | 150.0594 | 23.5897 | 68.7303 | 29.8099 | 150.5062 | 181.0779 | 170.6637
158.0354 | 149.8785 | 23.5766 | 69.2646 | 29.9877 | 150.0638 | 180.584 | 171.3723
159.0354 | 149.6418 | 23.6312 | 69.7948 | 30.2414 | 149.1538 | 179.5617 | 171.7342
160.0354 | 150.0195 | 23.9712 | 70.9121 | 30.3939 | 148.7632 | 180.1021 | 171.9968
161.0354 | 150.3218 | 24.3145 | 71.9162 | 30.6337 | 147.7114 | 180.7389 | 172.1669
162.0354 | 149.9934 | 24.5067 | 71.9912 | 30.8707 | 146.9688 | 180.7956 | 172.187
163.0354 | 150.9 | 24.416 | 74.3328 | 31.0714 | 146.8617 | 180.5175 | 171.869
164.0354 | 150.8482 | 24.5317 | 74.2839 | 31.1848 | 147.4479 | 180.6759 | 171.6257
165.0354 | 150.9028 | 24.6993 | 73.8411 | 31.3122 | 147.9612 | 180.7256 | 172.1033
166.0354 | 150.4698 | 24.8597 | 74.1083 | 31.4167 | 148.3741 | 181.0608 | 172.7418
167.0354 | 150.2661 | 24.8945 | 74.9266 | 31.5363 | 148.2329 | 180.4741 | 172.5025
168.0354 | 150.0426 | 25.4061 | 76.3467 | 31.8142 | 148.6334 | 182.0649 | 173.178
169.0354 | 150.0853 | 25.4472 | 76.3846 | 31.9724 | 148.2656 | 181.1758 | 172.3715
170.0354 | 149.8879 | 25.7509 | 76.8017 | 32.1347 | 147.4242 | 180.731 | 172.893
171.0354 | 150.2713 | 25.8805 | 77.0038 | 32.4994 | 147.7251 | 179.9355 | 172.5287
172.0354 | 150.5817 | 25.8011 | 79.0234 | 32.5054 | 147.702 | 179.4745 | 172.0017
173.0354 | 150.7014 | 25.9094 | 79.5961 | 32.607 | 147.2906 | 179.41 | 172.0873
174.0354 | 150.7183 | 26.2467 | 80.3204 | 32.7457 | 147.1801 | 178.1071 | 171.7067
175.0354 | 151.4262 | 26.5113 | 80.6312 | 32.8456 | 147.1949 | 178.1801 | 172.3837
176.0354 | 151.6138 | 26.4266 | 80.4998 | 32.8765 | 147.9436 | 178.5538 | 172.9522
177.0354 | 151.4855 | 26.9697 | 80.3563 | 33.0254 | 147.9001 | 178.4911 | 172.809
178.0354 | 151.4828 | 26.9659 | 82.0799 | 33.0625 | 147.7023 | 179.5492 | 172.9308
179.0354 | 151.7318 | 26.8751 | 83.0233 | 33.2286 | 147.7173 | 179.324 | 173.7214
180.0354 | 151.6482 | 27.0385 | 82.7293 | 33.3865 | 148.4509 | 180.8268 | 174.8089
181.0354 | 151.6935 | 27.1687 | 83.2201 | 33.3807 | 148.4173 | 180.0956 | 175.2919
182.0354 | 151.9266 | 27.3665 | 84.2347 | 33.5162 | 148.0889 | 180.5984 | 176.0135
183.0354 | 152.0191 | 27.4653 | 84.2856 | 33.6337 | 148.5507 | 181.1499 | 176.6512
184.0354 | 153.0268 | 27.6384 | 85.5315 | 33.9694 | 149.1011 | 180.623 | 177.5645
185.0354 | 153.4589 | 27.8983 | 86.682 | 34.0191 | 148.5028 | 179.8312 | 177.2432
186.0354 | 153.7193 | 28.1607 | 86.5351 | 34.2468 | 148.3925 | 179.7369 | 177.3417
187.0354 | 153.8216 | 28.3776 | 86.2701 | 34.2754 | 148.6122 | 179.2724 | 176.8806
188.0354 | 153.3694 | 28.4073 | 87.5901 | 34.4739 | 149.3615 | 179.0178 | 176.3571
189.0354 | 153.1687 | 28.4779 | 87.3541 | 34.5113 | 149.2885 | 179.0161 | 176.4286
190.0354 | 153.5319 | 28.5957 | 88.0212 | 34.624 | 149.9471 | 180.2343 | 176.5375
191.0354 | 153.1306 | 28.5955 | 89.823 | 34.853 | 149.6117 | 181.4184 | 178.4429
192.0354 | 153.4193 | 28.7817 | 89.5874 | 34.9376 | 149.4117 | 179.9228 | 177.147
193.0354 | 153.184 | 28.9547 | 89.2595 | 35.0417 | 148.7137 | 179.4137 | 176.726
194.0354 | 152.5264 | 29.0701 | 91.9378 | 35.2827 | 149.7542 | 179.673 | 176.7867
195.0354 | 152.1526 | 29.3565 | 92.1762 | 35.4028 | 149.4974 | 178.6923 | 176.4206
196.0354 | 152.0147 | 29.2494 | 92.8804 | 35.5149 | 149.3494 | 178.423 | 176.2627
197.0354 | 152.2934 | 29.2896 | 93.1724 | 35.615 | 150.455 | 178.5345 | 176.2443
198.0354 | 152.8083 | 29.44 | 93.9825 | 35.7913 | 151.0169 | 178.8094 | 176.1673
199.0354 | 153.4277 | 29.8277 | 94.3362 | 35.973 | 150.7553 | 179.2901 | 175.8514
200.0354 | 154.1579 | 30.0587 | 95.0036 | 35.9664 | 151.9015 | 179.348 | 176.5497
201.0354 | 154.3447 | 30.1371 | 94.3944 | 36.0794 | 151.435 | 179.5827 | 175.8545
202.0354 | 154.252 | 30.2401 | 95.2611 | 36.3164 | 152.289 | 180.0971 | 177.0776
203.0354 | 154.0478 | 30.4643 | 96.6686 | 36.4049 | 153.4834 | 179.7227 | 177.8448
204.0354 | 154.2875 | 30.7671 | 97.4292 | 36.6998 | 153.6061 | 179.7973 | 178.1331
205.0354 | 154.1721 | 30.5922 | 98.1099 | 36.793 | 152.3516 | 177.9739 | 177.2675
206.0354 | 153.7408 | 30.7272 | 98.6718 | 36.9051 | 151.5161 | 177.8137 | 177.1763
207.0354 | 154.0455 | 30.8927 | 99.3595 | 37.0903 | 152.2213 | 177.6873 | 177.1261
208.0354 | 153.5062 | 31.0835 | 99.6596 | 37.1983 | 152.2344 | 176.9046 | 176.0263
209.0354 | 153.5481 | 31.3679 | 99.6577 | 37.2207 | 151.9362 | 176.6401 | 175.1707
210.0354 | 153.4909 | 31.3871 | 100.4033 | 37.4276 | 151.9618 | 176.73 | 175.1124
211.0354 | 153.1359 | 31.4476 | 101.5141 | 37.4904 | 152.3939 | 176.8816 | 175.6226
212.0354 | 153.7068 | 31.612 | 102.8803 | 37.8005 | 153.7778 | 177.621 | 176.1757
213.0354 | 154.6536 | 31.5939 | 102.6062 | 38.3973 | 154.8256 | 177.8279 | 176.707
214.0354 | 154.2519 | 31.8124 | 104.3248 | 38.0587 | 154.5764 | 177.2572 | 176.0882
215.0354 | 154.1807 | 32.0916 | 104.9047 | 38.2757 | 154.4035 | 177.6854 | 176.1562
216.0354 | 154.4373 | 32.1903 | 104.6367 | 38.317 | 154.7132 | 177.824 | 176.5151
217.0354 | 154.9797 | 32.4268 | 105.2658 | 38.4777 | 156.0709 | 178.835 | 177.6184
218.0354 | 155.3171 | 32.5346 | 105.7656 | 38.6242 | 156.8658 | 180.2224 | 178.3372
219.0354 | 155.659 | 32.5443 | 107.4873 | 38.8249 | 157.2629 | 180.3915 | 178.8971
220.0354 | 156.2857 | 32.686 | 107.8321 | 38.9903 | 155.9247 | 180.7706 | 178.9486
221.0354 | 156.3783 | 32.7137 | 108.2598 | 39.1116 | 156.1331 | 179.9573 | 179.2762
222.0354 | 156.494 | 32.7604 | 109.7413 | 39.1187 | 156.6581 | 180.6566 | 179.5691
223.0354 | 156.6034 | 32.9095 | 110.3561 | 39.3255 | 156.4778 | 181.6169 | 180.0264
224.0354 | 156.3334 | 33.149 | 110.2448 | 39.4623 | 156.5841 | 181.9643 | 180.0405
225.0354 | 156.6599 | 33.3269 | 111.0686 | 39.5371 | 156.6267 | 180.6508 | 178.8367
226.0354 | 155.779 | 33.5089 | 111.1819 | 39.5972 | 156.5931 | 180.42 | 178.1919
227.0354 | 156.4672 | 33.5494 | 111.1983 | 39.7675 | 158.3498 | 181.0118 | 178.8652
228.0354 | 157.0612 | 33.8684 | 111.9043 | 39.8874 | 159.1784 | 182.0571 | 178.6733
229.0354 | 157.8798 | 33.858 | 112.4158 | 40.047 | 161.1986 | 182.951 | 180.1533
230.0354 | 158.9599 | 33.8834 | 113.6021 | 40.4583 | 161.0116 | 183.2999 | 179.9066
231.0354 | 160.0426 | 34.0382 | 114.4578 | 40.4456 | 160.8297 | 182.9128 | 180.345
232.0354 | 161.0248 | 34.3306 | 115.1163 | 40.5287 | 161.6795 | 183.751 | 180.9648
233.0354 | 161.0669 | 34.4403 | 115.4892 | 40.66 | 161.0426 | 183.5296 | 181.14
234.0354 | 161.2443 | 34.6164 | 115.4074 | 40.8215 | 160.3133 | 183.6619 | 180.6331
235.0354 | 161.2909 | 34.5682 | 116.9096 | 40.9476 | 160.4709 | 183.9351 | 180.8927
236.0354 | 161.9515 | 34.7189 | 118.695 | 41.1267 | 160.521 | 183.9551 | 180.6701
237.0354 | 162.6952 | 35.0202 | 118.266 | 41.3223 | 160.8499 | 184.0123 | 180.5834
238.0354 | 162.4755 | 35.1237 | 119.3864 | 41.5319 | 160.7991 | 183.9038 | 181.6991
239.0354 | 161.8343 | 35.5537 | 119.8044 | 41.6704 | 159.6189 | 184.2171 | 180.925
240.0354 | 161.3829 | 35.5707 | 120.5953 | 41.8428 | 160.4193 | 184.4751 | 181.1734
241.0354 | 161.3284 | 35.72 | 119.7149 | 41.9973 | 160.9236 | 185.0237 | 181.9314
242.0354 | 160.5583 | 35.6956 | 119.9223 | 42.1209 | 161.8229 | 185.1109 | 182.6701
243.0354 | 160.8916 | 35.7615 | 120.3198 | 42.51 | 162.6029 | 185.5333 | 182.246
244.0354 | 161.3026 | 35.7529 | 121.8437 | 42.6824 | 163.555 | 185.9125 | 182.6759
245.0354 | 161.6973 | 35.8527 | 123.159 | 42.8371 | 165.4331 | 187.4437 | 183.3995
246.0354 | 160.835 | 35.9773 | 123.1456 | 42.7325 | 164.3764 | 186.4938 | 183.0887
247.0354 | 161.2685 | 36.1068 | 123.9101 | 42.9017 | 164.8947 | 186.5087 | 183.35
248.0354 | 161.274 | 36.1201 | 124.8258 | 43.0977 | 164.8412 | 187.3429 | 183.5391
249.0354 | 161.3113 | 36.3387 | 125.4032 | 43.4453 | 165.058 | 187.5845 | 183.0689
250.0354 | 160.9992 | 36.571 | 125.8447 | 43.5653 | 165.7491 | 187.6756 | 183.8387
251.0354 | 160.6418 | 36.7758 | 125.5915 | 43.6923 | 165.5536 | 186.6008 | 184.03
252.0354 | 161.1683 | 36.8143 | 126.6903 | 43.7867 | 164.8457 | 187.2913 | 184.8065
253.0354 | 162.2511 | 36.9512 | 128.1634 | 43.9872 | 164.4735 | 187.9388 | 185.4044
254.0354 | 161.9453 | 36.9328 | 128.0961 | 43.985 | 163.2326 | 187.5576 | 185.0763
255.0354 | 161.5526 | 37.1905 | 129.4526 | 44.224 | 162.9356 | 187.6909 | 184.5855
256.0354 | 162.2816 | 37.3884 | 129.1927 | 44.6002 | 164.6966 | 189.1432 | 185.5754
257.0354 | 161.8594 | 37.5202 | 131.0591 | 44.5614 | 165.3317 | 188.7785 | 186.1756
258.0354 | 162.1903 | 37.545 | 131.7789 | 44.8671 | 164.5963 | 189.1491 | 186.442
259.0354 | 163.1696 | 37.7415 | 132.9053 | 45.0091 | 163.636 | 189.7703 | 187.6959
260.0354 | 163.6561 | 37.7835 | 131.7986 | 45.0163 | 163.2825 | 190.731 | 187.4861
261.0354 | 163.931 | 37.8643 | 133.7756 | 45.4233 | 162.5636 | 190.4627 | 186.7909
262.0354 | 163.4857 | 38.1804 | 132.9348 | 45.4823 | 162.3911 | 189.6224 | 186.7161
263.0354 | 162.9622 | 38.7192 | 133.0692 | 45.7356 | 161.8353 | 188.3238 | 185.6415
264.0354 | 162.8852 | 38.5662 | 134.5563 | 45.8107 | 162.5228 | 188.6936 | 186.2614
265.0354 | 163.6962 | 38.4584 | 135.5313 | 45.9619 | 163.7512 | 189.9454 | 187.7127
266.0354 | 163.9416 | 38.5427 | 135.8659 | 46.1227 | 164.3471 | 190.7233 | 187.1872
267.0354 | 165.213 | 38.6651 | 136.7533 | 46.2907 | 164.4456 | 191.9308 | 187.3963
268.0354 | 165.7094 | 38.6666 | 138.1551 | 46.5029 | 165.8023 | 192.3567 | 188.3498
269.0354 | 165.8157 | 38.8353 | 138.1055 | 46.5966 | 164.6409 | 191.9804 | 188.3535
270.0354 | 165.1819 | 38.9558 | 138.3968 | 46.7027 | 165.2922 | 191.1746 | 187.9336
271.0354 | 164.7118 | 39.1648 | 138.647 | 46.8331 | 164.6663 | 190.836 | 187.2489
272.0354 | 163.6395 | 39.4308 | 139.5736 | 46.9483 | 163.4228 | 189.7085 | 186.1582
273.0354 | 163.231 | 39.7596 | 140.2578 | 47.2007 | 162.7537 | 189.3791 | 185.3687
274.0354 | 162.6337 | 39.9925 | 140.2885 | 47.3343 | 163.0372 | 188.9228 | 184.5052
275.0354 | 161.8747 | 40.1216 | 140.4462 | 47.3734 | 162.5218 | 188.005 | 183.9321
276.0354 | 161.7796 | 40.2621 | 141.2174 | 47.5396 | 163.2003 | 189.2542 | 183.5828
277.0354 | 162.1743 | 40.2107 | 142.615 | 47.6553 | 162.654 | 188.8652 | 183.2674
278.0354 | 162.1832 | 40.3207 | 142.8535 | 47.9883 | 161.8174 | 187.3372 | 182.5613
279.0354 | 162.6598 | 40.4333 | 142.8107 | 48.1235 | 162.0746 | 187.5979 | 182.8896
280.0354 | 163.5608 | 40.6183 | 144.1556 | 48.3324 | 162.4805 | 189.1299 | 183.4673
281.0354 | 163.9445 | 40.746 | 145.5285 | 48.5521 | 162.3571 | 188.5689 | 184.3254
282.0354 | 164.6087 | 40.7835 | 146.3017 | 48.8432 | 161.4942 | 188.6558 | 183.9726
283.0354 | 165.3659 | 40.7102 | 145.4922 | 48.8847 | 162.7858 | 189.4903 | 184.6214
284.0354 | 165.7386 | 40.6845 | 146.0916 | 49.0075 | 162.1571 | 188.2876 | 184.991
285.0354 | 165.4072 | 40.8058 | 147.8897 | 49.0989 | 162.17 | 188.5374 | 185.4903
286.0354 | 165.3974 | 41.1497 | 149.5971 | 49.2952 | 161.8146 | 187.482 | 186.2105
287.0354 | 164.7653 | 41.2587 | 149.3306 | 49.4822 | 161.1093 | 186.9408 | 186.4085
288.0354 | 164.4419 | 41.4502 | 149.7432 | 49.664 | 160.5989 | 186.535 | 186.32
289.0354 | 164.0444 | 41.682 | 149.4191 | 49.9858 | 160.3689 | 186.0938 | 186.517
290.0354 | 163.7367 | 41.6741 | 150.3188 | 49.9076 | 161.925 | 188.4745 | 188.0874
291.0354 | 163.5148 | 41.6759 | 150.0127 | 50.1489 | 163.4738 | 189.5094 | 188.6429
292.0354 | 163.0906 | 41.863 | 150.4523 | 50.1768 | 163.8879 | 189.7013 | 188.9872
293.0354 | 162.9834 | 42.1336 | 151.5639 | 50.7039 | 164.2294 | 188.611 | 188.9871
294.0354 | 162.6166 | 42.4687 | 152.2282 | 50.7761 | 163.058 | 187.871 | 189.2514
295.0354 | 163.1079 | 42.6177 | 152.1964 | 50.8193 | 162.9365 | 187.6905 | 189.2213
296.0354 | 163.1939 | 42.7056 | 153.368 | 50.974 | 162.7354 | 187.9783 | 189.0494
297.0354 | 163.7854 | 42.8632 | 154.5424 | 51.1889 | 161.9611 | 187.8857 | 188.5547
298.0354 | 163.6857 | 43.0885 | 155.1058 | 51.3924 | 161.8899 | 188.0676 | 189.3007
299.0354 | 163.5489 | 43.1322 | 156.0438 | 51.5878 | 161.554 | 187.146 | 189.048
300.0354 | 165.1537 | 43.2027 | 157.3753 | 52.0345 | 160.6572 | 185.4494 | 188.7893
301.0354 | 164.8443 | 43.3105 | 158.738 | 51.9791 | 160.36 | 186.3014 | 188.9736
302.0354 | 164.1712 | 43.5111 | 157.7959 | 52.07 | 160.6603 | 186.4331 | 189.6575
303.0354 | 164.0366 | 44.009 | 157.1891 | 52.285 | 160.445 | 185.6586 | 189.0946
304.0354 | 163.4614 | 44.1651 | 157.8413 | 52.4913 | 160.449 | 185.2058 | 188.9597
305.0354 | 163.1898 | 44.0785 | 158.2914 | 52.6516 | 159.8314 | 184.0685 | 188.4861
306.0354 | 161.9596 | 44.2383 | 158.5645 | 52.8015 | 159.2149 | 184.1345 | 188.2454
307.0354 | 161.7533 | 44.6104 | 160.8288 | 52.8462 | 159.3561 | 184.1181 | 189.1388
308.0354 | 162.2915 | 44.5823 | 161.2294 | 53.13 | 159.5099 | 184.3502 | 188.75
309.0354 | 162.2514 | 44.7543 | 162.6805 | 53.2613 | 159.0496 | 184.8237 | 188.7541
310.0354 | 162.5583 | 44.8861 | 161.6747 | 53.3313 | 158.8589 | 185.6308 | 189.0286
311.0354 | 161.9857 | 45.0278 | 163.1485 | 53.3998 | 158.6118 | 184.4245 | 188.799
312.0354 | 161.8034 | 45.1575 | 163.9036 | 53.5316 | 157.6943 | 184.1176 | 188.6208
313.0354 | 161.4339 | 45.3628 | 163.8161 | 53.9816 | 157.0416 | 183.8067 | 188.1416
314.0354 | 161.791 | 45.6368 | 164.8996 | 53.902 | 157.1381 | 183.6152 | 188.1191
315.0354 | 161.4425 | 45.6361 | 164.7537 | 54.2253 | 157.2326 | 183.2558 | 188.2498
316.0354 | 160.5418 | 45.9086 | 164.4132 | 54.2748 | 156.7942 | 183.3603 | 187.9653
317.0354 | 160.9222 | 46.1884 | 165.7446 | 54.5553 | 156.3918 | 182.7541 | 187.2724
318.0354 | 161.2181 | 46.5215 | 166.1235 | 54.6917 | 156.4176 | 182.2177 | 188.0219
319.0354 | 160.7368 | 46.4922 | 167.3763 | 54.8288 | 156.3748 | 182.371 | 187.9625
320.0354 | 160.2419 | 46.5189 | 168.8763 | 54.8759 | 155.8253 | 182.398 | 187.7923
321.0354 | 159.9219 | 46.6958 | 169.0478 | 55.033 | 155.2747 | 183.3997 | 188.0058
322.0354 | 160.583 | 46.7396 | 171.2228 | 55.1937 | 154.8715 | 182.7596 | 188.0025
323.0354 | 162.2261 | 46.7426 | 170.9144 | 55.3847 | 154.8704 | 182.2618 | 187.4646
324.0354 | 162.1182 | 46.9053 | 171.4178 | 55.2958 | 154.6206 | 183.5865 | 187.3937
325.0354 | 161.9982 | 47.0055 | 171.8327 | 55.4978 | 155.273 | 182.6963 | 187.0612
326.0354 | 161.6481 | 47.5232 | 171.6763 | 55.6104 | 155.2119 | 183.1286 | 187.0406
327.0354 | 161.0854 | 47.6217 | 173.8092 | 55.7536 | 155.3416 | 182.5751 | 186.2672
328.0354 | 160.7741 | 47.7995 | 174.2789 | 55.7817 | 155.2649 | 182.5297 | 185.8695
329.0354 | 161.6382 | 47.7397 | 174.255 | 55.9669 | 154.7005 | 182.3088 | 185.7597
330.0354 | 161.3127 | 47.8048 | 173.6125 | 56.1992 | 154.748 | 181.7586 | 184.7944
331.0354 | 160.3414 | 47.7805 | 174.0716 | 56.2069 | 155.114 | 181.0595 | 184.1132
332.0354 | 160.4868 | 47.9725 | 174.3427 | 56.5394 | 155.6884 | 181.9697 | 183.8701
333.0354 | 160.7786 | 48.3986 | 174.4322 | 56.6476 | 156.365 | 181.9536 | 184.0803
334.0354 | 161.063 | 48.5967 | 174.8153 | 56.7966 | 156.681 | 183.728 | 184.4526
335.0354 | 161.4582 | 48.6226 | 176.0759 | 56.794 | 157.4408 | 184.9493 | 184.4963
336.0354 | 161.358 | 48.7345 | 176.0578 | 56.948 | 157.8608 | 185.9048 | 184.4779
337.0354 | 162.828 | 48.677 | 176.7548 | 57.2311 | 159.9269 | 187.7109 | 184.4982
338.0354 | 163.2891 | 48.7187 | 176.3067 | 57.3845 | 162.2393 | 189.7468 | 186.2411
339.0354 | 163.2927 | 48.8997 | 177.2803 | 57.4345 | 164.9634 | 190.8446 | 187.7956
340.0354 | 163.9498 | 49.0177 | 178.4868 | 57.8107 | 164.8574 | 192.1209 | 188.0949
341.0354 | 165.0037 | 49.5016 | 178.196 | 58.1657 | 164.9358 | 191.6837 | 188.3817
342.0354 | 166.4089 | 49.6229 | 179.0835 | 58.0669 | 165.6994 | 191.8483 | 188.2675
343.0354 | 166.6322 | 49.7948 | 181.0006 | 58.1235 | 165.7668 | 191.4346 | 188.2002
344.0354 | 167.3607 | 49.8748 | 182.6109 | 58.306 | 165.2641 | 190.6656 | 187.7083
345.0354 | 167.5365 | 49.9216 | 182.3213 | 58.5371 | 165.8995 | 191.1287 | 188.1053
346.0354 | 167.4095 | 50.0123 | 183.1316 | 58.6212 | 166.2562 | 191.33 | 188.256
347.0354 | 167.3812 | 50.2005 | 183.7094 | 58.852 | 166.5667 | 192.4554 | 189.3752
348.0354 | 167.5948 | 50.3407 | 184.2759 | 58.9711 | 166.8178 | 193.0134 | 189.8958
349.0354 | 168.8603 | 50.3106 | 185.929 | 59.167 | 166.4357 | 193.6056 | 190.0974
350.0354 | 168.567 | 50.4663 | 185.4827 | 59.2289 | 165.3149 | 192.7572 | 189.5452
351.0354 | 169.4047 | 50.5177 | 186.1784 | 59.7294 | 165.2841 | 192.7972 | 189.5462
352.0354 | 169.5432 | 50.6477 | 187.8917 | 59.9681 | 166.9141 | 193.4906 | 191.1215
353.0354 | 170.0032 | 50.877 | 188.163 | 60.0009 | 166.508 | 193.6354 | 191.886
354.0354 | 170.3666 | 51.0681 | 189.035 | 59.9973 | 166.5705 | 193.4667 | 191.9075
355.0354 | 170.1477 | 51.4649 | 190.5454 | 60.0992 | 167.1965 | 194.6328 | 192.1586
356.0354 | 170.3028 | 51.8294 | 190.2029 | 60.6197 | 166.5412 | 194.4427 | 192.4055
357.0354 | 170.9442 | 51.8378 | 191.3398 | 60.6795 | 167.7071 | 195.6712 | 192.6428
358.0354 | 171.4609 | 51.8549 | 192.5724 | 60.8218 | 167.5928 | 196.9044 | 193.2073
359.0354 | 171.03 | 52.0414 | 191.8462 | 60.8479 | 168.313 | 198.7623 | 193.7939
360.0354 | 171.1147 | 52.0667 | 192.4557 | 61.0778 | 170.8372 | 200.2734 | 195.0183
361.0354 | 172.4126 | 52.2433 | 192.9689 | 61.2853 | 172.3067 | 200.8358 | 196.2397
362.0354 | 173.2409 | 52.3511 | 193.5595 | 61.3457 | 173.0881 | 200.3449 | 195.6346
363.0354 | 172.9656 | 52.7393 | 193.7467 | 61.5149 | 172.2375 | 199.041 | 194.8759
364.0354 | 172.842 | 52.9858 | 194.2497 | 62.1439 | 171.2595 | 198.4972 | 194.1171
365.0354 | 172.3939 | 53.0472 | 194.7388 | 61.9514 | 170.6023 | 196.9674 | 193.2506
366.0354 | 171.533 | 53.0653 | 194.7704 | 62.1387 | 169.7693 | 195.8487 | 192.0078
367.0354 | 170.976 | 52.9898 | 195.6975 | 62.2694 | 168.9771 | 195.283 | 191.4594
368.0354 | 170.5377 | 52.9771 | 195.9165 | 62.2972 | 168.995 | 194.6704 | 191.4305
369.0354 | 170.5443 | 53.4872 | 196.1807 | 62.5144 | 168.5226 | 193.4826 | 190.8823
370.0354 | 171.0267 | 53.7879 | 197.5921 | 62.7605 | 168.2289 | 193.1387 | 190.4503
371.0354 | 170.0701 | 53.8523 | 197.6722 | 62.9451 | 167.8429 | 192.2951 | 189.6244
372.0354 | 170.6563 | 53.6742 | 197.8477 | 63.279 | 167.0053 | 190.9091 | 188.5626
373.0354 | 170.7946 | 54.0863 | 197.6873 | 63.368 | 166.574 | 190.7988 | 187.8299
374.0354 | 171.1113 | 54.2029 | 198.6704 | 63.5069 | 166.0657 | 190.0095 | 187.097
375.0354 | 171.3283 | 54.1777 | 199.8784 | 63.9725 | 166.8746 | 190.0498 | 186.927
376.0354 | 171.4194 | 54.4303 | 199.3964 | 64.3766 | 167.3701 | 189.6657 | 186.384
377.0354 | 172.0323 | 54.4577 | 199.3357 | 64.4628 | 168.416 | 188.9166 | 186.0923
378.0354 | 171.6878 | 54.5866 | 200.2378 | 64.4271 | 169.2067 | 189.1811 | 185.7457
379.0354 | 170.8784 | 54.5287 | 200.9037 | 64.5111 | 169.4801 | 189.691 | 186.1852
380.0354 | 171.2309 | 54.8973 | 201.4856 | 64.7832 | 169.9004 | 190.2277 | 186.5404
381.0354 | 171.8445 | 55.1554 | 203.9613 | 64.9926 | 170.0225 | 191.136 | 186.8598
382.0354 | 171.5724 | 54.9906 | 203.3524 | 65.0627 | 170.7622 | 191.8458 | 187.6203
383.0354 | 171.2277 | 55.27 | 202.761 | 65.1003 | 171.5952 | 192.3628 | 188.9816
384.0354 | 171.7024 | 55.4452 | 203.5879 | 65.4149 | 175.174 | 193.7436 | 189.3271
385.0354 | 171.884 | 55.3355 | 203.8002 | 65.6239 | 178.7123 | 195.2653 | 190.1511
386.0354 | 171.9935 | 55.4065 | 203.6592 | 65.745 | 180.6983 | 197.9424 | 192.3213
387.0354 | 171.6531 | 55.3422 | 203.8054 | 65.7791 | 180.5465 | 199.3532 | 193.991
388.0354 | 171.5612 | 55.3168 | 204.2263 | 65.9867 | 179.4453 | 199.6339 | 194.9908
389.0354 | 171.7219 | 55.5147 | 205.2006 | 66.2282 | 180.6021 | 199.9812 | 195.0309
390.0354 | 172.9672 | 55.7778 | 205.556 | 66.5444 | 181.2725 | 200.8631 | 195.9901
391.0354 | 173.6877 | 55.7142 | 206.0508 | 67.2808 | 183.0282 | 200.9669 | 196.2844
392.0354 | 173.2359 | 55.7996 | 207.4242 | 67.0583 | 184.2597 | 200.5896 | 195.9708
393.0354 | 173.7573 | 55.9138 | 208.2874 | 67.0603 | 184.5414 | 200.2085 | 195.9194
394.0354 | 174.1508 | 56.0405 | 207.1693 | 67.2281 | 184.3687 | 199.9605 | 196.4481
395.0354 | 174.6686 | 56.1213 | 207.6653 | 67.3372 | 184.7378 | 198.965 | 195.8297
396.0354 | 174.9128 | 56.0653 | 208.0343 | 67.6054 | 185.4254 | 198.8634 | 195.3595
397.0354 | 175.1023 | 56.1526 | 208.1754 | 67.6033 | 186.6275 | 200.0636 | 196.157
398.0354 | 174.7624 | 56.3263 | 208.0054 | 67.7358 | 185.7952 | 200.6903 | 196.8774
399.0354 | 174.8931 | 56.5319 | 208.3624 | 68.1083 | 187.8906 | 201.3385 | 195.8516
400.0354 | 174.2757 | 56.5756 | 208.0297 | 68.1365 | 188.803 | 201.4789 | 196.2105
401.0354 | 174.2308 | 56.5993 | 208.4561 | 68.3527 | 188.4541 | 201.0992 | 195.1456
402.0354 | 174.1923 | 56.5846 | 208.434 | 68.6236 | 187.5799 | 200.9674 | 194.5774
403.0354 | 174.4081 | 56.791 | 208.4872 | 68.8157 | 187.6258 | 201.5472 | 193.6723
404.0354 | 176.0759 | 57.0031 | 209.0383 | 68.9919 | 187.8597 | 201.0313 | 192.5162
405.0354 | 176.9808 | 57.0656 | 210.4787 | 69.176 | 187.6814 | 201.6986 | 192.7136
406.0354 | 176.9583 | 57.1161 | 210.7841 | 69.4667 | 189.1924 | 203.6387 | 195.6443
407.0354 | 177.4277 | 57.2139 | 210.844 | 69.7324 | 189.8948 | 204.8961 | 196.7703
408.0354 | 178.981 | 57.3762 | 210.7194 | 69.6559 | 191.2407 | 205.9334 | 197.6751
409.0354 | 180.0458 | 57.6747 | 210.4806 | 69.7942 | 191.3467 | 207.5264 | 198.6108
410.0354 | 181.3653 | 57.6789 | 211.0227 | 70.2198 | 191.6332 | 207.74 | 198.4082
411.0354 | 182.6318 | 57.6621 | 211.0259 | 70.339 | 192.6821 | 209.0507 | 198.7883
412.0354 | 184.3705 | 57.8678 | 211.4005 | 70.7575 | 193.1793 | 209.5907 | 199.5077
413.0354 | 186.4154 | 57.9987 | 211.3634 | 71.3523 | 193.5784 | 210.5738 | 199.1339
414.0354 | 187.288 | 57.9997 | 213.0264 | 71.3826 | 195.0074 | 211.4637 | 199.0126
415.0354 | 187.4305 | 58.0654 | 212.3375 | 71.4913 | 194.8804 | 212.578 | 198.1947
416.0354 | 186.7826 | 58.5072 | 212.2544 | 72.0376 | 195.9759 | 213.5847 | 198.6766
417.0354 | 186.3483 | 58.5974 | 213.2709 | 71.9815 | 196.0593 | 213.2685 | 198.909
418.0354 | 187.0469 | 58.8703 | 213.4902 | 72.2535 | 196.2549 | 212.7553 | 198.8933
419.0354 | 188.8088 | 58.9948 | 214.2383 | 72.4163 | 195.7623 | 211.8262 | 198.2131
420.0354 | 188.6295 | 59.1625 | 215.4301 | 72.5141 | 194.3622 | 210.9544 | 197.52
421.0354 | 188.5745 | 59.3822 | 215.4265 | 72.6337 | 193.2618 | 209.6418 | 196.7206
422.0354 | 189.0522 | 59.3152 | 217.024 | 73.0824 | 192.6644 | 209.6844 | 197.0675
423.0354 | 190.1621 | 59.3942 | 217.5861 | 73.3147 | 192.1983 | 210.5911 | 198.0886
424.0354 | 190.6301 | 59.5688 | 216.595 | 74.7518 | 193.1216 | 211.2271 | 197.6771
425.0198 | 192.5026 | 59.8276 | 218.4134 | 74.2193 | 192.3688 | 210.7074 | 197.11
426.0198 | 192.5028 | 60.2069 | 217.856 | 74.0016 | 192.2497 | 210.6655 | 197.3694
427.0198 | 191.832 | 60.3207 | 217.1378 | 74.5488 | 191.595 | 209.7147 | 197.63
428.0354 | 190.2756 | 60.5825 | 217.603 | 74.4544 | 190.1829 | 208.1723 | 196.9665
429.0354 | 190.1353 | 60.761 | 218.136 | 74.9676 | 189.338 | 206.9855 | 196.2054
430.0354 | 190.2125 | 60.8686 | 219.1005 | 75.4609 | 188.001 | 207.4109 | 195.897
431.0354 | 191.2396 | 60.9678 | 220.3421 | 75.327 | 188.7248 | 206.9762 | 195.1594
432.0354 | 190.4125 | 61.1088 | 220.9013 | 75.5724 | 188.7178 | 206.891 | 195.5345
433.0354 | 190.5849 | 61.4903 | 220.6259 | 75.6296 | 188.2536 | 206.8919 | 195.7493
434.0354 | 190.4612 | 61.7157 | 220.2189 | 75.803 | 190.4288 | 208.0434 | 197.3416
435.0354 | 189.9172 | 61.6168 | 221.0641 | 75.8837 | 191.0744 | 208.6011 | 197.7256
436.0354 | 190.2627 | 61.4162 | 221.7108 | 76.1257 | 191.1352 | 209.2406 | 198.4563
437.0354 | 190.4145 | 61.5755 | 222.0063 | 76.2315 | 192.0296 | 210.2031 | 200.1037
438.0198 | 190.0839 | 61.7529 | 222.0095 | 76.5027 | 193.426 | 211.9916 | 201.2552
439.0198 | 188.8795 | 61.6929 | 223.3066 | 76.7819 | 193.6115 | 213.2486 | 203.2828
440.0198 | 188.6283 | 61.7081 | 223.3975 | 77.1083 | 194.1347 | 212.3276 | 202.7315
441.0198 | 190.1727 | 61.6959 | 223.3143 | 77.1015 | 195.1603 | 212.4073 | 202.1822
442.0198 | 190.4914 | 61.7232 | 223.7431 | 77.3679 | 195.5672 | 212.7404 | 201.8176
443.0198 | 190.434 | 61.885 | 224.993 | 77.5595 | 195.135 | 211.3419 | 201.5285
444.0198 | 192.3063 | 62.1434 | 226.031 | 77.8114 | 194.466 | 211.331 | 201.7017
445.0354 | 192.465 | 62.225 | 226.1892 | 78.1239 | 194.0348 | 211.938 | 201.8634
446.0354 | 192.4823 | 62.4795 | 225.6901 | 78.14 | 193.9755 | 212.3168 | 202.1294
447.0354 | 193.1246 | 62.6692 | 225.9438 | 78.7176 | 194.558 | 212.2888 | 202.5487
448.0354 | 193.0504 | 62.8975 | 225.5455 | 78.774 | 194.0014 | 212.4939 | 202.2877
449.0354 | 194.8236 | 62.9925 | 226.3575 | 79.1853 | 194.3589 | 214.1595 | 202.7816
450.0354 | 195.3131 | 63.0294 | 226.3088 | 79.5152 | 194.9467 | 215.2102 | 203.3819
451.0354 | 195.7922 | 62.8166 | 227.0378 | 79.622 | 196.5675 | 216.819 | 203.9629
452.0354 | 195.7662 | 62.9881 | 227.2763 | 79.8863 | 198.3674 | 217.7144 | 204.8824
453.0354 | 196.9441 | 62.938 | 228.3475 | 80.1098 | 199.0895 | 217.9595 | 204.314
454.0354 | 196.3983 | 62.9072 | 228.1501 | 80.2762 | 199.1824 | 218.2188 | 204.8576
455.0354 | 196.0571 | 63.1501 | 228.6056 | 80.9815 | 199.8656 | 219.6418 | 205.9847
456.0354 | 195.7288 | 63.5837 | 228.3062 | 81.3843 | 199.691 | 219.1368 | 206.1132
457.0354 | 196.8234 | 63.6569 | 228.512 | 81.8461 | 199.4943 | 218.7046 | 206.3289
458.0354 | 197.6903 | 63.6261 | 228.3381 | 82.2825 | 199.7939 | 218.804 | 206.6949
459.0354 | 198.2422 | 63.9797 | 228.6427 | 82.3557 | 198.9572 | 218.1794 | 205.6765
460.0354 | 198.7606 | 63.9664 | 228.5666 | 82.8814 | 198.9577 | 217.4086 | 205.269
461.0354 | 200.1286 | 64.3369 | 229.1622 | 83.5661 | 198.844 | 215.4273 | 204.2649
462.0354 | 199.9143 | 64.717 | 229.2236 | 83.1957 | 197.9796 | 214.2779 | 203.2846
463.0354 | 199.2009 | 64.756 | 230.1212 | 83.3781 | 196.8273 | 213.272 | 202.3572
464.0354 | 199.1986 | 64.702 | 230.4772 | 83.8841 | 196.3135 | 212.5457 | 201.5698
465.0354 | 198.9078 | 64.7062 | 230.8221 | 83.8722 | 196.2354 | 212.2344 | 200.7597
466.0354 | 199.2444 | 64.817 | 230.8783 | 85.1328 | 195.8221 | 212.2841 | 200.4738
467.0354 | 200.5707 | 64.9565 | 231.2531 | 85.549 | 195.0152 | 213.0005 | 200.068
468.0354 | 202.6241 | 65.1634 | 231.5974 | 84.7913 | 195.6014 | 211.9412 | 199.4639
469.0354 | 203.1115 | 65.2705 | 233.0237 | 84.917 | 197.0863 | 213.0157 | 199.2988
470.0354 | 204.1934 | 65.4176 | 232.9517 | 85.4315 | 199.9233 | 215.4465 | 201.0702
471.0354 | 204.133 | 65.69 | 232.8652 | 85.9471 | 201.6332 | 216.4893 | 202.3097
472.0354 | 205.7772 | 65.7277 | 234.4967 | 85.8721 | 203.5744 | 218.0252 | 203.5591
473.0354 | 206.6887 | 65.5997 | 233.3869 | 86.1005 | 205.3548 | 219.6867 | 205.5017
474.0354 | 206.3332 | 65.8318 | 232.9542 | 86.279 | 205.7814 | 221.2274 | 206.83
475.0354 | 205.6165 | 65.745 | 233.3881 | 86.4807 | 206.3437 | 221.4005 | 207.3556
476.0354 | 204.8586 | 65.8167 | 235.0501 | 86.7673 | 208.0201 | 223.2121 | 207.6024
477.0354 | 205.3155 | 65.9044 | 236.0109 | 86.8493 | 209.5959 | 224.3492 | 208.8519
478.0354 | 206.4954 | 66.1918 | 236.7802 | 87.1425 | 208.9608 | 225.0843 | 209.7455
479.0354 | 206.8172 | 66.2171 | 237.999 | 87.4645 | 208.7796 | 225.5764 | 211.322
480.0354 | 206.3422 | 66.4924 | 237.1387 | 87.915 | 208.6104 | 225.8161 | 211.4274
481.0354 | 207.4385 | 66.4245 | 237.3441 | 88.3463 | 211.1875 | 225.6221 | 211.3035
482.0354 | 208.5329 | 66.7054 | 237.7999 | 88.7787 | 211.7293 | 225.1844 | 210.4858
483.0354 | 209.157 | 66.7064 | 238.5267 | 88.5386 | 210.0882 | 224.0881 | 209.4692
484.0354 | 209.1383 | 66.9372 | 239.1703 | 88.7461 | 209.6189 | 224.2857 | 209.518
485.0354 | 208.5112 | 67.0565 | 238.6983 | 88.8849 | 209.9762 | 224.6078 | 210.4177
486.0354 | 208.1614 | 67.0558 | 238.4288 | 88.9898 | 211.3156 | 226.3315 | 212.4685
487.0354 | 208.6387 | 67.0782 | 239.3471 | 89.182 | 211.2101 | 227.4878 | 213.3667
488.0354 | 208.8681 | 67.097 | 239.6761 | 89.4921 | 211.3397 | 228.558 | 215.4867
489.0354 | 208.8874 | 67.327 | 241.8107 | 89.8945 | 210.8819 | 228.8394 | 216.3809
490.0354 | 209.6433 | 67.5814 | 241.0326 | 90.1911 | 209.2036 | 227.808 | 216.6219
491.0354 | 210.4253 | 67.5686 | 240.2773 | 90.5236 | 208.7832 | 227.7318 | 215.8307
492.0354 | 210.7734 | 67.6194 | 240.2963 | 90.8623 | 210.3756 | 229.36 | 216.1733
493.0354 | 210.4957 | 67.6523 | 240.5093 | 90.7859 | 211.1047 | 231.4829 | 216.3599
494.0354 | 209.712 | 67.7141 | 240.9184 | 90.8458 | 211.7207 | 232.774 | 216.9311
495.0354 | 208.3017 | 67.8372 | 241.1304 | 90.9781 | 212.8609 | 233.9266 | 217.4717
496.0354 | 207.2702 | 67.8988 | 241.1247 | 91.453 | 212.5323 | 234.2793 | 216.7815
497.0354 | 207.713 | 68.0892 | 241.6908 | 91.6059 | 212.3419 | 234.1249 | 216.2752
498.0354 | 208.705 | 68.1934 | 241.9327 | 91.9275 | 212.6202 | 236.0487 | 216.5397
499.0354 | 209.9807 | 68.4447 | 242.2988 | 92.1135 | 213.9755 | 237.9308 | 217.5916
500.0354 | 211.0738 | 68.6064 | 242.4316 | 92.4666 | 214.6461 | 238.2532 | 218.4566
501.0354 | 211.4521 | 68.6712 | 243.1506 | 92.6668 | 215.7193 | 239.5324 | 220.3579
502.0354 | 211.2869 | 68.7877 | 243.676 | 93.0614 | 215.4094 | 238.3534 | 220.9781
503.0354 | 210.8154 | 68.9617 | 244.2358 | 93.1608 | 215.0638 | 237.579 | 220.7653
504.0354 | 209.4449 | 69.0573 | 244.695 | 93.2668 | 215.631 | 238.1091 | 221.3282
505.051 | 208.9491 | 68.9713 | 244.3973 | 93.3852 | 217.0722 | 239.2632 | 222.7166
506.0354 | 209.4191 | 69.3415 | 244.3341 | 93.5419 | 218.9172 | 239.6752 | 222.5765
507.0354 | 208.8032 | 69.4909 | 244.5454 | 93.8661 | 220.7726 | 241.6067 | 223.2893
508.0354 | 209.2872 | 69.6823 | 245.8625 | 94.0276 | 220.3271 | 241.6267 | 223.4336
509.0354 | 209.1921 | 69.7599 | 245.681 | 94.2592 | 220.9569 | 242.1128 | 224.2889
510.0354 | 209.758 | 69.7938 | 245.7959 | 94.5506 | 223.0919 | 242.3844 | 224.5247
511.0354 | 209.8528 | 69.9099 | 246.0281 | 94.6591 | 226.5017 | 244.0331 | 225.9462
512.0354 | 209.7225 | 70.0346 | 245.6936 | 94.7857 | 226.8636 | 245.6396 | 225.5749
513.0354 | 209.3693 | 70.2469 | 246.1162 | 95.1819 | 226.9954 | 245.8709 | 224.9832
514.0354 | 210.076 | 70.4139 | 246.4103 | 95.7665 | 228.577 | 247.4122 | 226.344
515.0354 | 210.3783 | 70.5863 | 246.0467 | 96.0069 | 228.4604 | 247.923 | 227.4389
516.0354 | 210.6543 | 70.6984 | 246.3608 | 96.0772 | 230.0471 | 248.2171 | 227.7759
517.0354 | 210.5575 | 70.7211 | 246.1949 | 96.3025 | 228.8278 | 247.7254 | 226.6005
518.0354 | 211.3294 | 70.9712 | 246.1252 | 96.6075 | 228.685 | 248.7137 | 225.9089
519.0354 | 211.627 | 71.0936 | 246.1506 | 96.7557 | 227.9766 | 247.8659 | 225.2859
520.0354 | 211.8779 | 71.0689 | 246.1894 | 97.5442 | 228.6858 | 248.2445 | 225.4119
521.0354 | 212.0737 | 71.0081 | 246.4735 | 97.4344 | 228.5423 | 248.87 | 224.4245
522.0354 | 212.2964 | 71.161 | 247.4362 | 97.6246 | 228.283 | 248.8628 | 224.924
523.0354 | 213.0544 | 71.4661 | 247.1545 | 97.9409 | 228.1941 | 248.8744 | 225.7206
524.0354 | 213.0184 | 71.392 | 247.1973 | 98.2587 | 228.9104 | 248.7407 | 225.2908
525.0354 | 212.815 | 71.3451 | 246.8764 | 98.1046 | 228.1583 | 249.0601 | 225.3156
526.0354 | 212.8582 | 71.5609 | 247.2058 | 98.3599 | 227.3886 | 248.5461 | 224.3392
527.0354 | 211.9679 | 71.8039 | 247.5663 | 98.9226 | 227.9312 | 249.2086 | 224.5826
528.0354 | 212.5784 | 71.8362 | 248.0415 | 99.7145 | 229.9236 | 249.1053 | 225.3278
529.0354 | 213.4856 | 72.0092 | 247.9157 | 99.6207 | 230.1061 | 247.3995 | 224.2812
530.0354 | 214.9243 | 72.1623 | 248.047 | 99.7792 | 232.2972 | 247.8211 | 224.4779
531.0354 | 215.2087 | 72.0642 | 248.0599 | 99.9547 | 233.0453 | 248.4987 | 224.5648
532.0354 | 215.0722 | 72.1027 | 247.9785 | 100.0348 | 233.5714 | 248.9831 | 225.1744
533.0354 | 215.8693 | 72.305 | 248.2067 | 100.3342 | 233.821 | 248.7461 | 225.1065
534.0354 | 216.3594 | 72.4982 | 248.1288 | 100.5352 | 233.8447 | 249.7396 | 225.4964
535.0354 | 216.0456 | 72.5238 | 248.6409 | 100.8701 | 233.1744 | 248.486 | 224.4074
536.0354 | 216.3445 | 72.5375 | 248.8707 | 101.1715 | 234.2647 | 248.854 | 224.5038
537.0354 | 216.0914 | 72.6001 | 249.1101 | 101.5395 | 233.9253 | 249.1637 | 225.3479
538.0354 | 216.1435 | 72.6784 | 249.1625 | 101.644 | 233.4963 | 250.9448 | 225.7397
539.0354 | 215.5366 | 72.9669 | 249.1902 | 102.2964 | 232.953 | 251.9111 | 226.0175
540.0354 | 215.1116 | 73.0803 | 249.1867 | 102.6406 | 233.4243 | 253.4292 | 226.7756
541.0354 | 216.4838 | 73.198 | 248.9386 | 103.3223 | 234.413 | 253.73 | 226.3674
542.0354 | 217.1762 | 73.4935 | 248.9747 | 103.1979 | 234.5141 | 254.3262 | 227.3712
543.0354 | 218.4378 | 73.5701 | 249.3006 | 104.1063 | 235.2419 | 255.4735 | 227.0934
544.0354 | 220.405 | 73.6755 | 250.096 | 104.8396 | 234.354 | 255.7551 | 228.5136
545.0354 | 222.2885 | 73.8619 | 249.8184 | 104.9449 | 234.4431 | 256.4512 | 228.8103
546.0354 | 222.615 | 74.1128 | 250.0377 | 104.7074 | 234.3308 | 256.4795 | 228.6355
547.0354 | 223.1298 | 74.1551 | 249.9583 | 105.7075 | 233.7955 | 257.5423 | 229.8251
548.0354 | 224.0366 | 74.2867 | 250.4516 | 106.4146 | 235.7529 | 257.8508 | 229.7989
549.0354 | 224.8285 | 74.5231 | 250.3137 | 106.9574 | 236.0423 | 259.1617 | 230.5274
550.0354 | 225.4479 | 74.7628 | 250.4047 | 107.2082 | 235.944 | 259.2819 | 231.0472
551.0354 | 226.306 | 74.8208 | 250.1097 | 106.9519 | 236.2949 | 260.0254 | 230.3206
552.0354 | 226.5632 | 74.9546 | 250.4171 | 106.9372 | 238.3009 | 262.23 | 232.3263
553.0354 | 228.3425 | 75.166 | 252.0271 | 107.1655 | 237.4592 | 263.1478 | 233.6012
554.0354 | 227.2118 | 75.1782 | 252.1058 | 107.5458 | 237.2523 | 263.8861 | 235.0091
555.0354 | 227.6532 | 75.1492 | 251.6916 | 107.8171 | 236.6423 | 264.1882 | 235.6505
556.0354 | 227.8386 | 75.4206 | 252.1726 | 108.1928 | 238.0456 | 264.5607 | 237.4929
557.0354 | 229.0538 | 75.2876 | 252.1533 | 108.6137 | 240.1486 | 265.9641 | 239.6694
558.0354 | 229.6576 | 75.3659 | 253.2445 | 108.9047 | 239.3681 | 264.665 | 239.3138
559.0354 | 231.1494 | 75.5165 | 253.1501 | 109.2678 | 239.6729 | 264.0773 | 239.422
560.0354 | 232.1802 | 75.8291 | 252.9877 | 109.259 | 238.8363 | 263.4836 | 238.6393
561.0354 | 231.3186 | 75.8308 | 252.9326 | 109.5857 | 238.8183 | 264.2257 | 239.8979
562.0354 | 231.4624 | 75.775 | 253.1379 | 109.9096 | 238.5795 | 264.6215 | 240.4223
563.0354 | 230.8659 | 75.8446 | 252.6879 | 110.5115 | 240.2653 | 265.3094 | 241.0599
564.0354 | 231.8818 | 75.9695 | 253.3376 | 110.8423 | 239.8491 | 265.7217 | 242.097
565.0354 | 232.1591 | 76.0941 | 254.0454 | 111.6276 | 239.99 | 266.9753 | 242.8794
566.0354 | 231.9109 | 76.3889 | 253.3482 | 112.1345 | 240.7033 | 266.4737 | 243.1882
567.0354 | 232.9946 | 76.6185 | 253.8802 | 111.874 | 241.0542 | 266.0469 | 243.6414
568.0354 | 233.3411 | 76.6112 | 254.1717 | 112.3187 | 240.5223 | 265.954 | 243.0911
569.0354 | 234.3261 | 76.9222 | 254.0869 | 112.6335 | 241.0753 | 264.5954 | 242.7741
570.0354 | 234.232 | 76.9942 | 254.522 | 113.3151 | 240.4801 | 265.5211 | 243.6709
571.0354 | 236.1783 | 77.1834 | 254.9138 | 113.3987 | 240.6364 | 264.8854 | 243.6143
572.0354 | 236.1899 | 77.2614 | 254.7388 | 113.8369 | 240.8387 | 264.733 | 243.7225
573.0354 | 236.8614 | 77.4821 | 255.2104 | 114.4285 | 239.9469 | 265.1158 | 243.7395
574.0354 | 237.4323 | 77.4181 | 254.8577 | 114.5608 | 239.5232 | 264.3093 | 242.3309
575.0354 | 236.4346 | 77.7551 | 255.0436 | 115.8842 | 239.3719 | 263.0401 | 240.9831
576.0354 | 236.3481 | 77.9817 | 255.145 | 116.7731 | 240.0946 | 262.5833 | 240.9033
577.0354 | 235.5378 | 78.0818 | 254.5402 | 117.0256 | 240.8377 | 261.6993 | 239.331
578.0354 | 233.672 | 77.9135 | 254.7345 | 117.2309 | 240.3058 | 261.5476 | 237.7717
579.0354 | 233.2683 | 78.0996 | 254.9651 | 116.8002 | 241.7143 | 261.3341 | 238.5029
580.0354 | 232.345 | 78.364 | 255.3048 | 117.6899 | 240.5869 | 260.5225 | 238.0548
581.0354 | 231.7759 | 78.4272 | 255.3583 | 117.958 | 240.4491 | 259.2885 | 237.2063
582.0354 | 231.1471 | 78.2491 | 255.0964 | 118.3583 | 240.2464 | 258.4912 | 236.6539
583.0354 | 231.9122 | 78.4028 | 255.5159 | 118.4615 | 239.9537 | 258.1295 | 236.1105
584.0354 | 232.4407 | 78.4123 | 255.4737 | 118.5898 | 240.0475 | 259.0467 | 236.1917
585.0354 | 232.0669 | 78.3785 | 255.883 | 118.8941 | 240.1282 | 259.7483 | 235.7868
586.0354 | 232.4234 | 78.5032 | 255.8657 | 119.0804 | 239.3193 | 259.738 | 235.7172
587.0354 | 231.7591 | 78.6353 | 256.051 | 119.5383 | 239.3363 | 260.7673 | 236.0056
588.0354 | 230.5649 | 78.837 | 256.0252 | 119.8199 | 239.2137 | 260.9376 | 235.7313
589.0354 | 231.0609 | 79.1122 | 255.9367 | 120.1345 | 239.9599 | 261.4449 | 235.2199
590.0354 | 231.0505 | 79.1433 | 256.0751 | 120.8732 | 239.4908 | 260.8079 | 234.1061
591.0354 | 231.0103 | 79.122 | 256.6338 | 121.3458 | 240.634 | 261.3651 | 233.2568
592.0354 | 230.9192 | 79.3538 | 256.4017 | 121.5392 | 240.8934 | 262.8479 | 234.9458
593.0354 | 230.3796 | 79.4984 | 256.093 | 121.5168 | 240.6138 | 262.157 | 234.5559
594.0354 | 229.7916 | 79.5637 | 256.1136 | 121.9147 | 240.5093 | 261.2255 | 234.1029
595.0354 | 228.833 | 79.6745 | 256.0495 | 122.547 | 240.3775 | 260.1784 | 232.8682
596.0354 | 228.3028 | 79.9441 | 256.103 | 123.6573 | 239.5022 | 259.4101 | 232.2981
597.0354 | 229.1082 | 79.8922 | 256.8596 | 123.5075 | 240.4599 | 258.857 | 230.7671
598.0354 | 230.9119 | 80.0533 | 257.2835 | 123.7455 | 241.9708 | 259.7305 | 230.7186
599.0354 | 231.988 | 80.2431 | 257.2403 | 124.248 | 243.1726 | 260.8443 | 231.272
600.0354 | 231.6831 | 80.3981 | 257.0154 | 125.6672 | 242.9068 | 260.2658 | 231.1149
601.0354 | 231.3881 | 80.4911 | 256.83 | 125.579 | 244.3847 | 262.5984 | 232.182
602.0354 | 230.7183 | 80.5275 | 257.0506 | 125.6292 | 245.3271 | 262.3621 | 232.9404
603.0354 | 230.063 | 80.4149 | 257.0819 | 126.0455 | 243.8792 | 261.8782 | 233.6604
604.0354 | 229.7174 | 80.5602 | 257.023 | 127.8173 | 244.064 | 261.4256 | 233.1931
605.0354 | 229.2426 | 80.8418 | 257.1791 | 127.7183 | 244.4089 | 261.6781 | 234.2987
606.0354 | 230.1169 | 81.0156 | 257.3178 | 128.2777 | 244.0414 | 260.7145 | 233.1888
607.0354 | 229.7743 | 81.1335 | 257.215 | 129.3306 | 244.3138 | 259.9816 | 231.7341
608.0354 | 229.1069 | 81.3445 | 257.3485 | 128.5938 | 244.3396 | 260.1298 | 232.9457
609.0354 | 229.1846 | 81.3838 | 257.2447 | 129.4327 | 243.3832 | 260.4701 | 233.5318
610.0354 | 228.6602 | 81.4154 | 257.1525 | 130.5462 | 243.9158 | 261.4933 | 234.8233
611.0354 | 227.8598 | 81.7448 | 257.3867 | 130.2025 | 246.1541 | 262.2965 | 235.8452
612.0354 | 227.0862 | 81.784 | 257.4758 | 130.7344 | 245.3193 | 262.0302 | 236.955
613.0354 | 227.0232 | 81.8568 | 257.8609 | 131.4451 | 245.3051 | 262.7428 | 235.9159
614.0354 | 226.8711 | 81.917 | 257.707 | 131.7318 | 246.9504 | 263.472 | 237.1901
615.0354 | 227.2725 | 81.9096 | 257.7832 | 132.2661 | 247.2286 | 263.2896 | 237.3775
616.0354 | 226.8166 | 82.0779 | 257.6258 | 132.2209 | 245.3505 | 263.2102 | 236.6052
617.0354 | 226.7648 | 81.952 | 257.8932 | 132.5912 | 245.4685 | 262.2148 | 236.0813
618.0354 | 226.1442 | 82.1619 | 257.5264 | 133.4567 | 245.5538 | 261.8006 | 235.1537
619.0354 | 225.4384 | 82.3158 | 257.6884 | 133.7137 | 245.6563 | 260.3426 | 233.9908
620.0354 | 225.9218 | 82.3693 | 258.1537 | 133.8963 | 246.908 | 260.1888 | 233.4283
621.0354 | 227.3939 | 82.4434 | 258.1695 | 133.948 | 248.3406 | 261.133 | 233.6524
622.0354 | 227.6463 | 82.7292 | 258.2503 | 134.3926 | 250.1418 | 262.0416 | 234.3016
623.0354 | 227.1742 | 82.8787 | 258.1837 | 135.1177 | 251.5739 | 262.5975 | 236.1627
624.0354 | 226.7131 | 83.0144 | 258.0607 | 135.4956 | 252.9165 | 263.023 | 236.0376
625.0354 | 226.3333 | 82.9804 | 258.2612 | 135.7212 | 253.9998 | 263.7265 | 236.4744
626.0354 | 226.1118 | 82.9 | 258.0982 | 136.3337 | 252.2151 | 263.2907 | 235.7347
627.0354 | 225.9115 | 82.9295 | 258.2243 | 136.429 | 253.5848 | 263.1042 | 235.9652
628.0354 | 226.2294 | 83.05 | 258.3742 | 137.0065 | 253.499 | 263.274 | 235.2908
629.0354 | 227.0622 | 83.2801 | 259.0775 | 137.1681 | 253.2333 | 264.3028 | 236.6409
630.0354 | 227.2938 | 83.2456 | 258.8976 | 137.7909 | 252.6612 | 264.393 | 236.7713
631.0354 | 228.5507 | 83.6064 | 259.4213 | 139.0621 | 252.2406 | 264.3254 | 236.5581
632.0354 | 229.1406 | 83.8861 | 259.0632 | 138.8865 | 251.7531 | 264.9857 | 236.2331
633.0354 | 229.3945 | 83.8409 | 259.0102 | 139.8836 | 250.3881 | 265.6707 | 235.8002
634.0354 | 229.1606 | 83.8407 | 259.0826 | 139.57 | 249.6896 | 265.4707 | 234.8714
635.0354 | 228.5392 | 84.1277 | 259.0767 | 140.0043 | 251.6681 | 266.7019 | 236.5455
636.0354 | 227.7054 | 84.224 | 258.9102 | 139.7672 | 252.2172 | 266.7081 | 237.1517
637.0354 | 226.8884 | 84.2781 | 259.0721 | 140.1936 | 250.6293 | 265.4113 | 236.6371
638.0354 | 225.7631 | 84.5436 | 258.9316 | 140.7323 | 249.7965 | 264.4981 | 235.5153
639.0354 | 225.7903 | 84.486 | 259.118 | 141.5939 | 249.17 | 263.192 | 234.797
640.0354 | 225.45 | 84.3871 | 259.0379 | 141.6251 | 249.0002 | 262.6432 | 234.7325
641.0354 | 226.0425 | 84.4653 | 259.6578 | 141.7126 | 249.6726 | 263.6868 | 235.5245
642.0354 | 226.8804 | 84.5102 | 259.8148 | 142.15 | 248.3338 | 263.5007 | 235.3097
643.0354 | 228.7014 | 84.7708 | 260.3762 | 142.5751 | 249.7567 | 264.401 | 235.321
644.0354 | 229.5195 | 84.7208 | 260.6624 | 142.8399 | 250.5759 | 266.2345 | 235.805
645.0354 | 228.6553 | 84.7024 | 260.4371 | 143.1616 | 250.9442 | 266.9881 | 235.947
646.0354 | 228.7995 | 85.1187 | 260.3778 | 144.6167 | 251.062 | 266.8858 | 237.7527
647.0354 | 228.6736 | 85.1606 | 259.9388 | 145.1544 | 250.0497 | 266.9398 | 237.8655
648.0354 | 227.8304 | 85.2695 | 260.0926 | 145.3284 | 251.082 | 267.664 | 238.8567
649.0354 | 228.1163 | 85.5846 | 260.6854 | 144.8998 | 250.3086 | 267.1059 | 239.458
650.0354 | 228.2787 | 85.6024 | 261.4439 | 145.3357 | 249.5621 | 266.771 | 239.4982
651.0354 | 229.217 | 85.5271 | 260.7742 | 146.1954 | 250.4723 | 267.6492 | 240.7268
652.0354 | 229.5605 | 85.7132 | 260.6567 | 146.3306 | 252.5623 | 269.3316 | 241.8959
653.0354 | 229.7016 | 85.7892 | 260.8105 | 146.8499 | 252.244 | 269.3342 | 242.3329
654.0354 | 229.2264 | 86.0933 | 261.1493 | 147.5529 | 251.8191 | 268.4501 | 241.5708
655.0354 | 228.6096 | 86.312 | 261.1923 | 147.9281 | 251.1258 | 267.7885 | 241.4832
656.0354 | 228.2991 | 86.506 | 261.3053 | 148.6054 | 250.3036 | 267.1631 | 241.3172
657.0354 | 227.9988 | 86.2984 | 261.0412 | 148.2643 | 251.3381 | 268.3789 | 241.0282
658.0354 | 227.8236 | 86.2042 | 261.1676 | 148.8557 | 251.1948 | 268.7417 | 241.2366
659.0354 | 227.6549 | 86.2151 | 260.8703 | 148.8711 | 250.6314 | 269.1918 | 240.6347
660.0354 | 227.829 | 86.1652 | 261.1212 | 149.4739 | 250.4276 | 268.3611 | 239.9192
661.0354 | 227.9088 | 86.5526 | 261.1819 | 149.4496 | 251.4765 | 267.6815 | 240.4748
662.0354 | 227.4762 | 86.5982 | 261.2799 | 149.9707 | 252.7272 | 268.3809 | 241.6078
663.0354 | 227.101 | 86.7349 | 261.3719 | 150.3178 | 251.4822 | 267.9573 | 242.3749
664.0354 | 226.9646 | 87.0598 | 261.4223 | 150.658 | 251.8036 | 267.5442 | 241.7107
665.0354 | 227.5112 | 87.087 | 261.7034 | 151.1247 | 250.1022 | 266.9966 | 241.32
666.0354 | 227.503 | 87.1176 | 261.9851 | 151.6778 | 249.2987 | 266.058 | 240.2019
667.0354 | 227.6291 | 87.2121 | 261.5954 | 151.5965 | 248.3114 | 265.1153 | 239.8453
668.0354 | 227.1399 | 87.4045 | 261.6428 | 151.9581 | 247.1126 | 264.9507 | 238.7458
669.0354 | 227.3174 | 87.4104 | 261.4666 | 152.3979 | 247.4647 | 264.1894 | 238.3116
670.0354 | 226.7074 | 87.4467 | 261.7951 | 153.2315 | 247.5376 | 263.8172 | 237.1629
671.0354 | 226.5461 | 87.6678 | 261.6169 | 153.5473 | 247.1457 | 263.1918 | 237.3596
672.0354 | 226.966 | 87.5617 | 261.961 | 153.6819 | 245.9848 | 260.9219 | 236.0783
673.0354 | 227.4326 | 87.5577 | 262.3039 | 153.5928 | 245.0041 | 260.5026 | 235.7725
674.0354 | 227.0898 | 87.5966 | 261.7424 | 153.7383 | 243.7367 | 260.5686 | 235.2723
675.0354 | 226.5013 | 87.6407 | 261.6048 | 154.3134 | 243.3414 | 260.2647 | 235.0406
676.0354 | 225.945 | 87.7881 | 262.067 | 154.6873 | 243.0793 | 259.7438 | 234.6324
677.0354 | 226.685 | 87.8376 | 263.1256 | 154.7804 | 244.4199 | 259.9621 | 234.9565
678.0354 | 226.6267 | 88.1302 | 262.7023 | 155.1557 | 246.0208 | 260.6568 | 235.2064
679.0354 | 227.1964 | 88.091 | 262.316 | 155.8448 | 247.024 | 261.6655 | 236.3315
680.0354 | 227.3948 | 88.3252 | 262.5903 | 156.0023 | 246.4786 | 261.3681 | 235.2402
681.0354 | 228.252 | 88.3079 | 262.5439 | 156.2901 | 246.5382 | 260.6684 | 234.875
682.0354 | 227.9675 | 88.3377 | 262.4797 | 156.3325 | 247.3148 | 260.9598 | 234.1983
683.0354 | 228.0468 | 88.8049 | 262.2163 | 157.0447 | 247.9135 | 260.9187 | 233.2245
684.0354 | 227.5367 | 88.9202 | 262.5311 | 157.3106 | 248.126 | 261.0444 | 232.7307
685.0354 | 227.2532 | 89.0707 | 262.4292 | 157.3819 | 248.2663 | 260.7407 | 232.6108
686.0354 | 226.5402 | 89.2826 | 262.5786 | 157.8202 | 247.8457 | 260.2402 | 231.9725
687.0354 | 226.3668 | 89.4733 | 262.7002 | 158.2429 | 247.5339 | 259.8995 | 232.0743
688.0354 | 225.6587 | 89.5427 | 262.6284 | 158.5543 | 247.9764 | 259.6566 | 231.5079
689.0354 | 224.7247 | 89.5515 | 262.5366 | 158.8437 | 247.4889 | 259.3917 | 230.9337
690.0354 | 224.1035 | 89.7524 | 262.6136 | 159.5987 | 247.4807 | 259.6943 | 230.3502
691.0354 | 224.3516 | 89.5315 | 262.8351 | 159.6363 | 246.8429 | 259.5239 | 230.193
692.0354 | 224.4793 | 89.8009 | 262.632 | 160.0821 | 246.5738 | 258.8696 | 229.8417
693.0354 | 224.372 | 89.8124 | 262.4149 | 160.1528 | 246.7974 | 258.9421 | 229.5477
694.0354 | 224.0675 | 90.0133 | 262.6721 | 160.4569 | 246.667 | 258.4079 | 228.7979
695.0354 | 224.0668 | 90.0623 | 262.8251 | 161.1448 | 246.1394 | 258.5571 | 228.863
696.0354 | 224.718 | 90.2798 | 263.4832 | 160.7202 | 246.1018 | 257.5571 | 228.183
697.0354 | 224.5769 | 90.3697 | 263.2813 | 161.1534 | 245.5619 | 258.578 | 228.613
698.0354 | 225.654 | 90.4691 | 263.188 | 161.8978 | 245.0755 | 259.2277 | 229.0338
699.0354 | 226.2918 | 90.4652 | 263.4864 | 161.9693 | 245.3832 | 260.6382 | 229.4287
700.0354 | 227.2124 | 90.4129 | 263.4494 | 162.056 | 246.0325 | 262.1204 | 230.0266
701.0354 | 226.989 | 90.7161 | 263.558 | 162.3077 | 248.5839 | 262.4188 | 231.9094
702.0354 | 227.64 | 90.9224 | 264.1412 | 162.8079 | 249.8579 | 262.8234 | 233.4679
703.0354 | 228.1746 | 90.8846 | 263.7278 | 163.6861 | 249.7221 | 263.1451 | 233.775
704.0354 | 228.5362 | 91.0088 | 264.0666 | 163.8174 | 249.0603 | 263.9959 | 233.551
705.0354 | 227.7386 | 91.1161 | 264.4822 | 164.4147 | 248.9245 | 263.9693 | 233.5078
706.0354 | 227.775 | 91.1002 | 264.1929 | 164.7468 | 250.1116 | 265.2674 | 234.6997
707.0354 | 227.8712 | 91.4365 | 265.2336 | 164.6155 | 251.6097 | 266.1101 | 235.9293
708.0354 | 227.9833 | 91.6479 | 264.9429 | 164.7354 | 251.6403 | 266.5902 | 236.7816
709.0354 | 228.8309 | 91.7008 | 265.0005 | 165.4365 | 251.2518 | 267.0235 | 238.3035
710.0354 | 230.8978 | 91.6918 | 265.0748 | 166.085 | 251.6759 | 265.8052 | 237.7441
711.0354 | 231.8747 | 91.7957 | 264.609 | 165.8487 | 251.9711 | 265.3703 | 238.1099
712.0354 | 231.9487 | 91.9527 | 264.3492 | 166.9567 | 253.1806 | 265.3571 | 238.4642
713.0354 | 231.3777 | 92.0868 | 264.7436 | 166.7284 | 253.4001 | 265.2027 | 238.7947
714.0354 | 230.6617 | 92.1722 | 264.2769 | 167.0267 | 251.9978 | 264.6369 | 238.5
715.0354 | 229.9224 | 92.1693 | 264.4045 | 167.4245 | 250.8101 | 263.8846 | 237.1824
716.0354 | 230.1993 | 92.0215 | 264.6439 | 167.4533 | 250.0766 | 263.1146 | 235.9313
717.0354 | 229.534 | 92.3503 | 264.609 | 167.6826 | 250.5627 | 263.2614 | 236.0547
718.0354 | 229.4023 | 92.4209 | 264.7257 | 168.2709 | 249.727 | 262.6067 | 236.6434
719.0354 | 229.4839 | 92.5819 | 264.7638 | 168.648 | 250.0054 | 262.3057 | 235.6909
720.0354 | 228.7442 | 92.6788 | 265.2788 | 169.4835 | 249.3142 | 262.6407 | 236.6752
721.0354 | 228.9782 | 92.8691 | 265.4288 | 169.7576 | 250.0595 | 261.856 | 236.0909
722.0354 | 229.8243 | 92.8064 | 265.2516 | 170.7162 | 250.3429 | 262.5571 | 236.8735
723.0354 | 229.7176 | 92.8675 | 265.0789 | 170.8848 | 250.1014 | 263.6716 | 236.157
724.0354 | 229.6578 | 93.0139 | 266.4925 | 171.2164 | 249.6852 | 263.5661 | 236.8478
725.0354 | 229.2883 | 93.0499 | 265.4636 | 171.1903 | 250.3479 | 264.8432 | 236.4691
726.0354 | 229.91 | 93.2066 | 265.5378 | 171.5072 | 250.193 | 264.4068 | 235.8785
727.0354 | 230.6347 | 93.1851 | 265.69 | 171.7384 | 249.6133 | 264.6452 | 235.1012
728.0354 | 230.2875 | 93.1748 | 265.8695 | 172.3344 | 250.6471 | 264.4306 | 236.8977
729.0354 | 229.5869 | 93.1897 | 265.3187 | 172.5655 | 252.2287 | 265.7243 | 238.3701
730.0354 | 228.6767 | 93.2662 | 265.2224 | 173.6878 | 252.3701 | 264.6144 | 237.7307
731.0354 | 228.1633 | 93.4367 | 265.1726 | 174.0438 | 251.8096 | 263.4151 | 236.6234
732.0354 | 228.0704 | 93.7487 | 265.63 | 173.8328 | 250.9169 | 262.6553 | 235.3632
733.0354 | 228.6566 | 93.6906 | 265.5703 | 174.0827 | 250.6728 | 263.001 | 235.7076
734.0354 | 229.5924 | 93.6327 | 266.0022 | 174.6038 | 250.1634 | 262.8062 | 235.6296
735.0354 | 229.3634 | 93.9845 | 266.0273 | 174.581 | 251.5809 | 263.3826 | 237.0301
736.0354 | 230.2574 | 93.9663 | 265.9185 | 174.7942 | 253.2078 | 265.936 | 239.321
737.0354 | 230.0539 | 94.2231 | 266.1573 | 175.0396 | 252.3758 | 266.6933 | 240.7792
738.0354 | 229.417 | 94.4224 | 266.015 | 175.3464 | 252.151 | 265.9529 | 240.7458
739.0354 | 229.0876 | 94.4071 | 266.1649 | 175.5825 | 251.5562 | 264.9317 | 240.562
740.0354 | 228.6898 | 94.3613 | 266.2384 | 176.0461 | 251.2966 | 264.4349 | 239.5274
741.0354 | 228.8029 | 94.5265 | 265.9103 | 177.0163 | 251.6216 | 264.1231 | 238.3078
742.0354 | 229.0521 | 94.5329 | 265.8916 | 177.0707 | 252.1276 | 264.3497 | 238.2731
743.0354 | 228.8806 | 94.7098 | 266.3562 | 177.881 | 252.5321 | 263.8699 | 237.6081
744.0354 | 229.2576 | 94.7524 | 266.1019 | 177.7264 | 252.6939 | 263.8786 | 237.1974
745.0354 | 228.9834 | 94.9262 | 265.8978 | 177.5678 | 252.2729 | 263.7768 | 237.0405
746.0354 | 229.1774 | 95.0087 | 265.8804 | 178.1119 | 251.5625 | 263.3228 | 236.0337
747.0354 | 228.8846 | 94.9187 | 265.8578 | 178.0297 | 251.521 | 262.3754 | 234.9676
748.0354 | 228.5371 | 95.0839 | 266.2267 | 178.5703 | 250.9808 | 261.2913 | 233.9784
749.0354 | 229.5978 | 95.37 | 266.4372 | 178.9395 | 251.8621 | 261.6576 | 233.6211
750.0354 | 229.9081 | 95.302 | 266.8806 | 179.2167 | 251.7992 | 263.1656 | 234.7877
751.0354 | 230.6474 | 95.2281 | 267.4243 | 179.1246 | 252.1717 | 265.4154 | 237.2098
752.0354 | 231.4226 | 95.5074 | 267.9594 | 179.4383 | 251.6676 | 266.8322 | 239.4865
753.0354 | 231.7873 | 95.5972 | 267.5487 | 180.0508 | 250.6834 | 268.6319 | 241.4231
754.0354 | 231.4289 | 95.5148 | 267.1213 | 180.7526 | 250.8958 | 269.3334 | 242.0551
755.0354 | 230.7786 | 95.593 | 267.3824 | 180.5718 | 251.0025 | 269.7332 | 242.2851
756.0354 | 230.6391 | 95.7478 | 267.3435 | 181.0623 | 250.9474 | 269.1019 | 243.0781
757.0354 | 230.8058 | 95.842 | 267.7027 | 181.4414 | 251.8185 | 269.6046 | 243.4829
758.0354 | 231.1549 | 95.9977 | 267.3294 | 181.997 | 250.8594 | 267.8459 | 242.7001
759.0354 | 230.699 | 96.2634 | 267.7805 | 181.5893 | 250.0977 | 266.7486 | 241.6674
760.0354 | 231.9251 | 96.2533 | 268.1145 | 182.0656 | 248.6716 | 265.7295 | 240.4838
761.0354 | 232.8705 | 96.323 | 269.6409 | 182.1402 | 248.687 | 264.2419 | 239.9856
762.0354 | 233.9807 | 96.4369 | 269.456 | 182.3111 | 248.4829 | 263.7055 | 238.9884
763.0354 | 233.9389 | 96.8526 | 269.4104 | 183.8659 | 247.1911 | 262.2213 | 237.8951
764.0354 | 233.7325 | 97.0642 | 269.3131 | 183.3762 | 247.3488 | 261.5884 | 236.6902
765.0354 | 234.1442 | 97.1475 | 269.5319 | 183.5147 | 246.5012 | 261.3433 | 235.5888
766.0354 | 235.2568 | 97.2605 | 269.0531 | 183.8777 | 247.3186 | 262.0071 | 234.9959
767.0354 | 234.4056 | 97.3405 | 269.0141 | 184.5693 | 245.914 | 260.3332 | 234.0933
768.0354 | 233.7767 | 97.2702 | 269.269 | 184.8288 | 246.723 | 259.154 | 233.086
769.0354 | 234.7096 | 97.4799 | 269.6875 | 184.8272 | 247.7881 | 257.7986 | 232.0318
770.0354 | 235.6459 | 97.6492 | 270.3062 | 185.7404 | 247.4546 | 257.3788 | 230.9381
771.0354 | 236.7132 | 97.8144 | 269.9156 | 185.7166 | 248.6085 | 258.216 | 230.8464
772.0354 | 236.8611 | 97.9383 | 270.2998 | 185.7214 | 248.3231 | 258.5603 | 231.3509
773.0354 | 237.1136 | 98.0853 | 270.1785 | 186.0337 | 248.889 | 259.1518 | 231.2684
774.0354 | 236.512 | 98.0634 | 270.4375 | 186.087 | 250.3528 | 259.4061 | 231.8293
775.0354 | 236.8767 | 98.0696 | 271.1037 | 186.8056 | 250.2993 | 258.0939 | 231.6874
776.0354 | 237.141 | 98.1348 | 270.6457 | 187.7457 | 250.5457 | 257.802 | 231.8171
777.0354 | 237.7489 | 98.4083 | 271.1113 | 187.7966 | 251.0813 | 258.6505 | 231.3991
778.0354 | 236.6549 | 98.5324 | 270.8539 | 187.9022 | 250.3721 | 257.1518 | 231.2113
779.0354 | 236.0163 | 98.5609 | 271.3348 | 188.3358 | 250.0388 | 256.8426 | 231.4286
780.0354 | 236.1095 | 98.6717 | 271.6067 | 188.5216 | 249.4802 | 256.4081 | 231.0027
781.0354 | 235.9795 | 98.7674 | 272.0793 | 188.4891 | 249.1117 | 255.3168 | 230.4292
782.0354 | 236.3001 | 98.6784 | 272.1047 | 188.5168 | 249.1052 | 255.3799 | 230.6007
783.0354 | 235.8629 | 98.8885 | 271.9816 | 188.4919 | 248.7025 | 256.6081 | 231.4507
784.0354 | 235.1612 | 98.7967 | 271.713 | 188.7818 | 248.1821 | 258.0263 | 232.6277
785.0354 | 234.9081 | 98.7405 | 271.3786 | 189.0574 | 248.2075 | 259.0395 | 232.928
786.0354 | 235.0439 | 98.8223 | 271.8357 | 189.4293 | 248.1391 | 259.2776 | 232.4225
787.0354 | 234.4862 | 98.867 | 272.1239 | 189.6336 | 248.4258 | 260.5052 | 233.4185
788.0354 | 233.8588 | 99.1491 | 271.7696 | 190.1253 | 248.174 | 259.6371 | 233.8283
789.0354 | 233.6904 | 99.2092 | 271.9547 | 190.6707 | 248.3921 | 259.9914 | 234.5723
790.0354 | 232.9875 | 99.2302 | 271.8179 | 191.2265 | 247.2957 | 259.6055 | 235.7723
791.0354 | 232.1475 | 99.4022 | 272.1568 | 191.4716 | 247.9296 | 261.2417 | 236.5713
792.0354 | 232.231 | 99.603 | 272.2595 | 191.9975 | 247.7823 | 261.7873 | 237.4895
793.0354 | 232.2672 | 99.5791 | 272.1509 | 191.5591 | 248.6912 | 262.2517 | 237.4173
794.0354 | 232.0287 | 99.881 | 272.3895 | 191.9286 | 247.8259 | 262.2746 | 237.3881
795.0354 | 232.7946 | 99.6767 | 272.5319 | 191.9231 | 247.5695 | 262.668 | 237.1353
796.0354 | 233.3249 | 99.6519 | 272.3708 | 192.4832 | 247.5666 | 263.1618 | 237.2693
797.0354 | 233.063 | 99.9837 | 272.1477 | 192.5337 | 248.6227 | 261.6742 | 236.9153
798.0354 | 232.5481 | 100.1718 | 272.6529 | 192.985 | 248.1002 | 261.7045 | 236.7518
799.0354 | 232.8105 | 100.2212 | 272.94 | 192.9996 | 249.7366 | 262.1662 | 236.6129
800.0354 | 231.946 | 100.1332 | 272.7015 | 193.1348 | 249.9393 | 261.7982 | 237.1528
801.0354 | 232.4476 | 100.1938 | 272.8249 | 193.3212 | 249.9803 | 262.7435 | 237.009
802.0354 | 232.5833 | 100.1364 | 272.5224 | 193.5052 | 249.5322 | 262.7033 | 237.1252
803.0354 | 232.6519 | 100.3219 | 272.5422 | 194.0887 | 249.4309 | 262.8389 | 237.5138
804.0354 | 232.0739 | 100.4278 | 272.886 | 194.3155 | 249.2419 | 262.5522 | 236.8902
805.0354 | 231.9582 | 100.731 | 272.9908 | 194.7027 | 250.1324 | 262.9599 | 237.0765
806.0354 | 231.7015 | 100.8797 | 273.4352 | 194.5178 | 249.3901 | 262.842 | 237.2252
807.0354 | 231.5266 | 100.7474 | 273.5767 | 194.5177 | 249.7774 | 263.2963 | 239.0952
808.0354 | 232.0212 | 100.7835 | 273.9213 | 194.6966 | 250.7903 | 264.6606 | 239.7259
809.0354 | 232.1485 | 100.8599 | 273.5612 | 195.0008 | 249.6656 | 265.1252 | 241.0074
810.0354 | 233.0715 | 101.0709 | 273.5661 | 195.8174 | 249.8978 | 265.9187 | 240.815
811.0354 | 232.9751 | 101.1549 | 273.7817 | 195.5298 | 251.0909 | 265.5447 | 240.957
812.0354 | 232.8225 | 101.3468 | 274.1006 | 195.834 | 251.0489 | 265.0238 | 241.2201
813.0354 | 233.6884 | 101.4893 | 273.635 | 195.8557 | 249.7662 | 265.636 | 241.1545
814.0354 | 233.3761 | 101.6128 | 273.6741 | 196.0501 | 249.4128 | 265.086 | 240.6112
815.0354 | 233.2866 | 101.6691 | 273.6257 | 196.3573 | 248.9711 | 264.681 | 239.7103
816.0354 | 232.6143 | 101.7515 | 273.5403 | 196.4423 | 248.6636 | 263.7555 | 238.5714
817.0354 | 232.0377 | 102.0062 | 273.7595 | 196.8844 | 248.364 | 263.533 | 238.2804
818.0354 | 232.5023 | 101.9398 | 274.5937 | 198.3167 | 249.8027 | 264.0567 | 238.0363
819.0354 | 232.4517 | 102.1157 | 275.023 | 198.9803 | 249.5816 | 263.8954 | 239.1227
820.0354 | 232.9 | 102.2138 | 274.8136 | 198.2611 | 249.7145 | 263.928 | 238.5878
821.0354 | 232.5274 | 102.2102 | 274.548 | 198.1784 | 249.383 | 264.5954 | 240.1493
822.0354 | 231.7181 | 102.1371 | 274.571 | 199.2683 | 251.2766 | 265.0103 | 241.0107
823.0354 | 231.5262 | 102.2275 | 274.3549 | 199.5254 | 252.8731 | 264.183 | 240.4016
824.0354 | 230.8251 | 102.1798 | 274.3589 | 199.7639 | 253.1197 | 263.4279 | 240.7812
825.0354 | 230.1825 | 102.2529 | 274.7078 | 200.2233 | 253.5438 | 263.653 | 239.5939
826.0354 | 230.4181 | 102.5825 | 274.4513 | 200.4491 | 255.0923 | 264.0419 | 239.9127
827.0354 | 229.9634 | 102.6841 | 274.8045 | 201.1027 | 256.7535 | 264.4911 | 241.0098
828.0354 | 229.554 | 102.9514 | 274.6407 | 201.2918 | 256.9773 | 264.1497 | 241.8754
829.0354 | 229.7224 | 103.0251 | 274.538 | 201.4566 | 256.1085 | 263.2957 | 241.5539
830.0354 | 229.3486 | 103.0526 | 274.9502 | 201.398 | 256.2119 | 263.114 | 241.4224
831.0354 | 230.029 | 103.0463 | 274.944 | 201.5298 | 254.8591 | 263.0618 | 241.6793
832.0354 | 230.0927 | 103.193 | 275.1407 | 201.779 | 254.4116 | 262.5845 | 240.8727
833.0354 | 230.5766 | 103.2127 | 274.9669 | 201.8906 | 253.7609 | 261.5417 | 240.135
834.0354 | 230.5344 | 103.4672 | 274.8665 | 202.0038 | 253.3012 | 261.4972 | 239.1295
835.0354 | 229.545 | 103.6555 | 274.9116 | 202.0608 | 251.8519 | 260.3436 | 238.0153
836.0354 | 229.2214 | 103.7009 | 274.8978 | 202.2902 | 250.8608 | 259.0634 | 237.4343
837.0354 | 228.6152 | 103.7685 | 274.6796 | 202.3043 | 250.1756 | 258.4542 | 236.3446
838.0354 | 227.9488 | 103.7794 | 274.8917 | 202.6089 | 249.679 | 258.1971 | 235.8818
839.0354 | 227.1009 | 103.836 | 274.7905 | 203.2566 | 250.3871 | 259.0012 | 236.1403
840.0354 | 226.5242 | 103.9387 | 275.1708 | 203.4948 | 249.579 | 257.9721 | 235.1078
841.0354 | 226.792 | 103.7811 | 274.9595 | 203.4049 | 249.0298 | 256.996 | 234.1919
842.0354 | 227.0464 | 103.7983 | 275.6356 | 203.9802 | 248.8294 | 256.9164 | 233.0322
843.0354 | 227.0506 | 103.9047 | 275.2587 | 204.0873 | 249.3137 | 257.7857 | 234.0309
844.0354 | 227.6841 | 104.0676 | 275.4842 | 205.2509 | 248.7462 | 257.6841 | 234.5807
845.0354 | 227.8052 | 104.1649 | 275.6712 | 205.5654 | 249.8812 | 257.7365 | 233.8435
846.0354 | 228.4327 | 104.4441 | 275.5176 | 205.6088 | 249.1894 | 257.3757 | 233.4095
847.0354 | 227.647 | 104.2847 | 275.3102 | 206.0439 | 249.2917 | 257.8704 | 232.7787
848.0354 | 227.7451 | 104.1905 | 275.3096 | 205.8057 | 248.658 | 259.0578 | 234.0967
849.0354 | 227.4485 | 104.6055 | 275.2828 | 205.8397 | 248.1891 | 258.618 | 233.4704
850.0354 | 227.4944 | 104.5316 | 275.1731 | 206.1992 | 247.6193 | 259.7961 | 233.218
851.0354 | 227.4007 | 104.3922 | 275.5467 | 206.2511 | 247.7012 | 259.8826 | 233.6192
852.0354 | 228.002 | 104.5651 | 275.6578 | 206.3581 | 247.8101 | 259.8917 | 233.5756
853.0354 | 228.8054 | 104.8186 | 275.7018 | 206.7322 | 247.7218 | 260.221 | 233.8529
854.0354 | 228.7494 | 104.7403 | 275.3923 | 207.0423 | 247.8014 | 261.1059 | 233.6206
855.0354 | 229.8033 | 104.9785 | 276.247 | 207.5979 | 247.5785 | 261.4387 | 233.8847
856.0354 | 229.7385 | 105.1278 | 276.5347 | 207.5904 | 248.904 | 261.7704 | 234.6303
857.0354 | 229.9467 | 105.3765 | 276.1476 | 208.1516 | 250.2388 | 261.9401 | 234.6898
858.0354 | 229.179 | 105.5297 | 275.9169 | 208.2831 | 251.2397 | 261.2421 | 234.4455
859.0354 | 229.372 | 105.4486 | 276.0204 | 209.3726 | 251.1317 | 261.0992 | 235.4019
860.0354 | 229.5035 | 105.6169 | 275.9744 | 209.7275 | 250.62 | 259.9562 | 234.7482
861.0354 | 229.618 | 105.7476 | 276.3314 | 209.2398 | 250.5683 | 259.799 | 234.0228
862.0354 | 229.1627 | 105.6502 | 276.3984 | 209.2479 | 250.2748 | 259.6237 | 233.9465
863.0354 | 229.0377 | 105.9429 | 276.4769 | 209.7072 | 249.2661 | 259.1777 | 234.004
864.0354 | 230.1634 | 105.9969 | 276.3903 | 210.4837 | 249.3844 | 259.4697 | 234.5166
865.0354 | 230.9577 | 106.1377 | 277.6805 | 209.9095 | 249.3991 | 259.4171 | 234.7783
866.0354 | 232.6569 | 106.2791 | 279.2822 | 210.049 | 249.5653 | 260.3242 | 235.2198
867.0354 | 234.4841 | 106.5348 | 279.1465 | 210.0841 | 248.4026 | 259.6414 | 234.5359
868.0354 | 235.119 | 106.7449 | 279.8088 | 210.4706 | 247.5419 | 259.5529 | 234.5978
869.0354 | 234.4473 | 106.7629 | 280.5646 | 210.5507 | 247.3965 | 259.5636 | 234.7844
870.0354 | 235.2255 | 106.9339 | 279.9071 | 211.1549 | 247.6096 | 260.7542 | 235.5535
871.0354 | 235.2322 | 106.9461 | 280.6427 | 211.5826 | 247.9162 | 261.3294 | 235.2525
872.0354 | 235.8099 | 106.8247 | 279.1703 | 211.921 | 249.0857 | 262.3142 | 236.0192
873.0354 | 235.4645 | 106.9774 | 278.8881 | 211.7602 | 249.0221 | 261.8105 | 236.152
874.0354 | 234.5672 | 107.0437 | 278.9773 | 211.7869 | 250.0937 | 262.7919 | 236.8167
875.0354 | 234.2933 | 107.2977 | 278.6473 | 211.8065 | 249.7366 | 262.6942 | 236.6194
876.0354 | 233.2584 | 107.3492 | 278.8367 | 212.6128 | 248.8858 | 261.7267 | 235.8696
877.0354 | 232.8306 | 107.1976 | 279.0858 | 212.2677 | 249.3752 | 261.0679 | 235.8364
878.0354 | 232.9589 | 107.1721 | 279.4892 | 212.8292 | 248.0313 | 260.5895 | 236.4532
879.0354 | 233.2727 | 107.4167 | 279.3628 | 213.097 | 247.8281 | 260.2891 | 236.851
880.0354 | 233.1813 | 107.5083 | 280.2835 | 212.9873 | 247.2996 | 260.0671 | 237.4244
881.0354 | 232.7862 | 107.4194 | 280.0568 | 212.9742 | 248.222 | 260.2898 | 237.8157
882.0354 | 232.325 | 107.5651 | 280.9245 | 213.1005 | 247.276 | 260.7137 | 238.9369
883.0354 | 231.3097 | 107.8568 | 280.5566 | 213.6082 | 247.1865 | 261.0037 | 238.9058
884.0354 | 230.3641 | 107.9731 | 280.6942 | 213.7583 | 246.6952 | 260.4377 | 238.755
885.0354 | 230.6788 | 108.1716 | 281.5607 | 213.777 | 245.7584 | 260.7437 | 238.8065
886.0354 | 231.522 | 108.0602 | 281.8257 | 213.9184 | 245.6215 | 260.054 | 238.8574
887.0354 | 230.9835 | 108.0945 | 281.4487 | 214.1003 | 245.2851 | 259.7542 | 238.5166
888.0354 | 231.6909 | 108.2522 | 281.2354 | 214.6792 | 244.3366 | 259.1279 | 238.485
889.0354 | 231.8795 | 108.2011 | 282.0259 | 215.0496 | 243.6011 | 259.2759 | 238.1626
890.0354 | 231.35 | 108.3907 | 282.5009 | 215.2759 | 244.2523 | 259.1913 | 236.9777
891.0354 | 233.0933 | 108.3715 | 282.7639 | 214.8088 | 244.2633 | 258.5488 | 235.5499
892.0354 | 233.3151 | 108.407 | 283.3205 | 214.8133 | 243.4986 | 258.8333 | 235.6672
893.0354 | 234.1159 | 108.6054 | 284.2546 | 215.2238 | 243.2926 | 257.8256 | 235.7533
894.0354 | 234.7887 | 108.674 | 283.7247 | 215.4481 | 242.6997 | 257.1956 | 235.488
895.0354 | 234.7403 | 108.9074 | 283.7506 | 215.7297 | 242.7991 | 256.7471 | 234.7163
896.0354 | 234.2856 | 109.0681 | 283.4794 | 215.9107 | 241.966 | 255.5884 | 234.5536
897.0354 | 233.731 | 109.2555 | 283.6736 | 216.3139 | 241.6761 | 254.7688 | 234.9243
898.0354 | 233.2134 | 109.4013 | 283.7083 | 216.5027 | 241.8226 | 254.8371 | 236.3486
899.0354 | 232.496 | 109.3135 | 283.8358 | 216.4011 | 240.3661 | 255.3997 | 237.1807
900.0354 | 232.7943 | 109.2111 | 284.3642 | 216.964 | 240.2684 | 256.969 | 239.289
901.0354 | 232.8174 | 109.525 | 284.1329 | 217.1763 | 240.9491 | 257.704 | 238.9496
902.0354 | 233.1723 | 109.4753 | 284.2096 | 217.2059 | 241.6292 | 257.952 | 238.5367
903.0354 | 233.6358 | 109.4007 | 284.0988 | 217.5304 | 242.2816 | 258.2961 | 238.5709
904.0354 | 233.5828 | 109.468 | 284.3352 | 217.2597 | 241.8688 | 259.9364 | 240.4431
905.0354 | 234.1852 | 109.5389 | 284.3685 | 217.5989 | 243.1455 | 260.9636 | 240.192
906.0354 | 234.1168 | 109.9437 | 284.4305 | 218.2328 | 243.3791 | 261.8933 | 240.8836
907.0354 | 235.2572 | 110.0242 | 284.7868 | 218.4133 | 244.453 | 262.9685 | 240.5929
908.0354 | 236.3069 | 110.1642 | 284.661 | 219.161 | 245.745 | 264.9626 | 242.8123
909.0354 | 237.3585 | 110.31 | 285.2865 | 219.2243 | 248.7262 | 267.1838 | 244.7108
910.0354 | 237.6502 | 110.4093 | 285.6039 | 219.1988 | 251.802 | 267.6697 | 245.8993
911.0354 | 238.4601 | 110.5819 | 285.5302 | 219.4173 | 253.9432 | 267.9764 | 246.8484
912.0354 | 239.0367 | 110.4411 | 286.5275 | 219.9655 | 255.2461 | 268.367 | 247.1912
913.0354 | 240.8355 | 110.6421 | 286.4461 | 219.7094 | 257.6089 | 269.8033 | 248.8509
914.0354 | 241.7611 | 110.7601 | 286.6251 | 220.0835 | 259.3198 | 270.245 | 248.972
915.0354 | 243.7575 | 110.8119 | 286.7268 | 220.4193 | 260.2405 | 271.8351 | 250.1624
916.0354 | 244.5565 | 111.0392 | 287.1687 | 220.2835 | 262.2142 | 273.1371 | 251.1392
917.0354 | 244.9157 | 110.949 | 287.0369 | 221.535 | 263.1488 | 273.9347 | 251.5289
918.0354 | 245.1893 | 110.9683 | 286.9023 | 221.198 | 264.4641 | 274.8757 | 252.0307
919.0354 | 245.8427 | 111.0184 | 287.0443 | 221.1467 | 264.0842 | 275.4826 | 253.2125
920.0354 | 246.404 | 111.0907 | 287.9052 | 221.2947 | 264.2035 | 276.7419 | 253.248
921.0354 | 247.8398 | 111.0666 | 287.9567 | 222.0524 | 263.8723 | 279.0534 | 254.4506
922.0354 | 248.8904 | 111.3209 | 288.1246 | 222.7795 | 264.927 | 279.954 | 255.3296
923.0354 | 249.3147 | 111.4568 | 287.7195 | 222.6939 | 266.4054 | 281.3408 | 255.1487
924.0354 | 249.3032 | 111.3642 | 288.0495 | 222.6555 | 267.1983 | 280.8857 | 254.6659
925.0354 | 249.6635 | 111.3752 | 287.7563 | 223.2815 | 267.6989 | 281.2088 | 253.7813
926.0354 | 249.9136 | 111.6629 | 288.6427 | 222.9 | 268.3965 | 281.2563 | 254.0752
927.0354 | 250.1458 | 111.74 | 288.8362 | 223.132 | 268.6313 | 281.5447 | 254.5006
928.0354 | 250.9243 | 111.9463 | 289.4441 | 223.6163 | 268.2583 | 282.5494 | 255.0601
929.0354 | 251.9862 | 111.9987 | 289.3631 | 224.4789 | 270.5318 | 284.1956 | 257.8103
930.0354 | 252.5183 | 112.2507 | 289.2967 | 224.7515 | 271.729 | 285.0592 | 257.8572
931.0354 | 253.6714 | 112.2102 | 290.3838 | 224.673 | 272.266 | 285.6277 | 259.5289
932.0354 | 255.979 | 112.437 | 292.9131 | 224.8164 | 271.2413 | 286.6032 | 259.6454
933.0354 | 257.8807 | 112.323 | 292.6869 | 224.712 | 271.5626 | 287.9284 | 260.4307
934.0354 | 258.3686 | 112.3604 | 292.177 | 225.069 | 271.7975 | 287.376 | 260.5745
935.0354 | 258.7496 | 112.6117 | 291.4551 | 225.3435 | 271.4429 | 287.1128 | 260.6774
936.0354 | 258.9687 | 112.6778 | 291.3575 | 226.5946 | 271.8968 | 286.8767 | 260.7455
937.0354 | 258.8932 | 113.1067 | 291.4214 | 227.309 | 275.7612 | 288.8994 | 262.1105
938.0354 | 258.6659 | 113.2462 | 291.7103 | 226.6099 | 277.9934 | 290.9237 | 263.6722
939.0354 | 258.6083 | 113.3896 | 291.9193 | 226.5804 | 277.2387 | 291.5205 | 265.0219
940.0354 | 259.7186 | 113.2409 | 292.0048 | 227.1439 | 277.7334 | 292.0077 | 265.7727
941.0354 | 258.9288 | 113.3711 | 292.2373 | 227.225 | 277.7254 | 292.7962 | 265.8743
942.0354 | 259.1075 | 113.5899 | 292.1172 | 227.3564 | 277.3298 | 292.6213 | 266.2139
943.0354 | 258.9441 | 113.6137 | 292.6473 | 227.8148 | 277.0179 | 292.4616 | 265.897
944.0354 | 259.1082 | 113.8022 | 293.3113 | 227.7101 | 276.3123 | 293.8292 | 267.1703
945.0354 | 259.9287 | 113.9891 | 293.3782 | 228.5253 | 274.9884 | 294.7373 | 267.3673
946.0354 | 259.5242 | 114.0597 | 292.8569 | 229.4552 | 277.3069 | 295.6932 | 266.9531
947.0354 | 259.6207 | 114.2075 | 292.9175 | 229.8787 | 277.3393 | 294.9164 | 265.4392
948.0354 | 259.0227 | 114.2923 | 293.1772 | 229.7747 | 277.0511 | 293.5502 | 264.6332
949.0354 | 258.6315 | 114.304 | 293.6475 | 229.605 | 276.8491 | 293.4798 | 263.4106
950.0354 | 259.0074 | 114.5873 | 293.9277 | 230.1507 | 277.5642 | 294.1459 | 263.1711
951.0354 | 259.1921 | 114.8662 | 293.9945 | 231.2826 | 277.7125 | 295.2017 | 263.0519
952.0354 | 259.2878 | 115.0066 | 294.182 | 231.7305 | 278.0878 | 294.4086 | 262.7845
953.0354 | 260.0362 | 115.0121 | 294.1676 | 232.5023 | 278.5672 | 293.3637 | 262.7838
954.0354 | 259.3273 | 115.1278 | 294.1564 | 232.2664 | 278.255 | 293.8288 | 262.2539
955.0354 | 258.7732 | 115.2209 | 294.4142 | 232.3093 | 278.0063 | 292.7927 | 262.8328
956.0354 | 257.959 | 114.9992 | 294.4452 | 232.2201 | 278.9173 | 292.2143 | 262.3673
957.0354 | 257.4665 | 115.3156 | 294.173 | 232.2049 | 280.873 | 292.7524 | 263.248
958.0354 | 256.304 | 115.5593 | 294.4508 | 232.4405 | 279.6072 | 291.8271 | 261.8987
959.0354 | 255.8988 | 115.6903 | 294.4258 | 232.6154 | 278.8539 | 291.7666 | 261.6716
960.0354 | 255.6535 | 115.8772 | 294.6333 | 232.9024 | 278.1761 | 291.5284 | 261.3413
961.0354 | 255.3282 | 115.9015 | 294.7276 | 233.6433 | 277.3387 | 291.4514 | 260.8703
962.0354 | 255.633 | 115.8121 | 294.7806 | 234.2356 | 277.6951 | 291.0134 | 259.5748
963.0354 | 255.1838 | 115.6705 | 294.908 | 234.5348 | 277.08 | 290.4948 | 259.3042
964.0354 | 255.4829 | 115.7701 | 295.6652 | 234.5271 | 279.4108 | 291.5311 | 259.8316
965.0354 | 255.0136 | 116.1991 | 295.7956 | 235.1747 | 280.5347 | 292.8215 | 260.3928
966.0354 | 254.4342 | 116.2994 | 295.3513 | 235.8663 | 280.9188 | 293.2917 | 260.6671
967.0354 | 253.899 | 116.2052 | 295.2053 | 236.1131 | 281.4775 | 293.9394 | 261.4931
968.0354 | 253.0327 | 116.1524 | 295.4388 | 236.7523 | 282.1288 | 293.8857 | 260.6258
969.0354 | 252.8355 | 116.074 | 295.6254 | 236.9943 | 282.2954 | 293.4165 | 260.9572
970.0198 | 253.6401 | 116.1635 | 296.0336 | 237.2252 | 281.6586 | 292.9462 | 260.4394
971.0354 | 253.9587 | 116.6118 | 296.3875 | 237.827 | 282.9965 | 293.5568 | 261.6046
972.0354 | 255.4717 | 116.5437 | 296.1235 | 237.8879 | 283.7751 | 295.291 | 263.6599
973.0354 | 255.9969 | 116.6994 | 296.0742 | 239.1567 | 285.0521 | 297.0688 | 265.6342
974.0354 | 255.7641 | 117.0115 | 296.2789 | 239.2678 | 285.1024 | 297.2807 | 265.6942
975.0354 | 256.564 | 117.1917 | 296.9894 | 239.771 | 285.6617 | 297.2904 | 267.6205
976.0354 | 256.5932 | 117.271 | 296.857 | 240.0016 | 284.094 | 296.5589 | 266.784
977.0354 | 257.6423 | 117.3939 | 296.9364 | 240.5269 | 285.2415 | 297.0871 | 267.1098
978.0354 | 258.1241 | 117.5647 | 297.7049 | 241.6776 | 286.9939 | 297.6331 | 268.3592
979.0354 | 258.3375 | 117.6711 | 297.216 | 241.6226 | 287.456 | 296.9586 | 267.0535
980.0354 | 260.8306 | 117.8621 | 298.0028 | 242.5639 | 288.1693 | 297.042 | 266.749
981.0354 | 261.0303 | 117.8658 | 297.7761 | 242.4434 | 287.8483 | 295.7059 | 265.0982
982.0354 | 262.2071 | 117.9666 | 298.0862 | 242.3797 | 287.1617 | 296.8459 | 264.2259
983.0354 | 262.8548 | 117.9841 | 298.8078 | 242.9667 | 287.4324 | 298.1265 | 264.2211
984.0354 | 263.8683 | 118.2856 | 301.0404 | 242.9368 | 289.0884 | 299.6903 | 264.7091
985.0354 | 265.0351 | 118.5286 | 302.3458 | 243.4151 | 289.1126 | 299.5793 | 266.0257
986.0354 | 267.1515 | 118.4591 | 301.8421 | 243.3701 | 289.6979 | 300.385 | 265.699
987.0354 | 267.8732 | 118.6453 | 300.5614 | 244.1735 | 289.9507 | 301.8879 | 266.5612
988.0354 | 269.3731 | 118.7576 | 300.7745 | 244.4815 | 289.7328 | 303.0619 | 266.7779
989.0354 | 270.5044 | 118.6342 | 300.5729 | 244.5105 | 290.1565 | 303.0215 | 267.1731
990.0354 | 270.8802 | 118.7299 | 300.2687 | 244.8131 | 291.181 | 303.6247 | 267.4976
991.0354 | 270.7627 | 118.7962 | 300.6003 | 245.6931 | 292.1873 | 303.4376 | 266.903
992.0354 | 270.5904 | 118.9219 | 301.7974 | 245.6812 | 293.2566 | 305.221 | 269.5781
993.0354 | 271.0694 | 118.9251 | 301.6971 | 246.0276 | 291.958 | 305.8688 | 269.8688
994.0354 | 271.2486 | 119.2565 | 302.4722 | 246.5063 | 291.7787 | 306.1 | 270.3457
995.0354 | 271.4033 | 119.3415 | 302.0117 | 246.6812 | 291.1724 | 306.6222 | 270.3468
996.0354 | 271.3421 | 119.2669 | 301.6886 | 247.0785 | 290.7356 | 306.8847 | 270.155
997.0354 | 271.5484 | 119.5617 | 302.1594 | 247.2451 | 290.1715 | 307.1293 | 270.2883
998.0354 | 271.9174 | 119.848 | 302.2654 | 248.4695 | 290.154 | 307.0541 | 271.657
999.0354 | 271.9361 | 119.84 | 302.1217 | 249.848 | 291.1888 | 308.0117 | 272.1655
1000.0354 | 272.1829 | 119.8934 | 302.7892 | 249.6728 | 291.9602 | 307.2851 | 272.0171
1001.0354 | 271.4892 | 119.7636 | 302.7913 | 249.4785 | 290.7685 | 306.8472 | 271.3505
1002.0354 | 271.1785 | 119.8208 | 303.2291 | 250.1656 | 291.7087 | 306.7976 | 272.0974
1003.0354 | 271.4581 | 120.2123 | 302.7959 | 250.5784 | 293.1201 | 307.2289 | 272.998
1004.0354 | 271.6793 | 120.3596 | 303.7956 | 250.1529 | 293.4934 | 307.3122 | 273.1389
1005.0354 | 271.8557 | 120.3979 | 304.2654 | 250.8012 | 294.4406 | 309.0257 | 275.6505
1006.0354 | 271.6237 | 120.6133 | 303.6657 | 251.8403 | 294.1177 | 309.1443 | 274.6776
1007.0354 | 271.8117 | 120.5964 | 304.1657 | 251.8676 | 296.6047 | 311.4623 | 277.0207
1008.0354 | 271.9645 | 120.837 | 304.2807 | 252.5153 | 297.362 | 310.7733 | 277.4119
1009.0354 | 271.9108 | 120.8451 | 304.3583 | 253.4654 | 298.6038 | 310.5747 | 277.9933
1010.0354 | 271.1202 | 120.9285 | 304.0609 | 254.1224 | 298.8611 | 310.5823 | 277.69
1011.0354 | 269.7598 | 121.0214 | 304.414 | 253.9515 | 298.7235 | 309.4117 | 277.6286
1012.0198 | 268.9043 | 121.0121 | 304.4625 | 254.2563 | 297.2761 | 308.5167 | 276.8385
1013.0354 | 268.338 | 121.2853 | 304.2464 | 254.8435 | 297.1067 | 309.1256 | 277.6101
1014.0354 | 268.2609 | 121.3007 | 304.4195 | 254.8368 | 296.2975 | 308.9412 | 276.7436
1015.0354 | 267.8561 | 121.4267 | 304.9329 | 254.5693 | 296.4032 | 308.9454 | 277.1677
1016.0354 | 268.0773 | 121.4645 | 305.0727 | 255.8436 | 295.7026 | 308.124 | 277.1079
1017.0354 | 269.3714 | 121.4106 | 305.469 | 256.4416 | 295.4191 | 306.9733 | 276.5142
1018.0354 | 268.493 | 121.7694 | 305.1835 | 256.2562 | 296.3715 | 305.9097 | 276.1184
1019.0354 | 267.7899 | 121.9371 | 304.8731 | 256.6374 | 296.904 | 305.8529 | 276.1085
1020.0354 | 266.8005 | 121.8923 | 305.5616 | 257.4691 | 297.3593 | 304.3216 | 274.5212
1021.0354 | 266.3375 | 121.9102 | 305.4097 | 258.0503 | 297.5189 | 304.4723 | 275.6394
1022.0354 | 265.8735 | 122.1127 | 305.5722 | 257.9588 | 298.4482 | 304.997 | 275.7182
1023.0354 | 265.1706 | 122.2737 | 306.1856 | 258.3821 | 297.5839 | 306.1637 | 274.8438
1024.0354 | 265.6762 | 122.0963 | 306.74 | 258.3772 | 297.6999 | 306.2044 | 274.7733
1025.0354 | 265.914 | 122.1328 | 306.0893 | 258.6276 | 297.2022 | 306.28 | 273.7652
1026.0354 | 265.6787 | 122.195 | 306.7365 | 259.6889 | 297.0773 | 307.0199 | 274.377
1027.0354 | 267.0352 | 122.5738 | 306.6627 | 260.0532 | 297.1635 | 307.2907 | 274.9478
1028.0354 | 266.7693 | 122.6102 | 306.3367 | 260.0338 | 296.2349 | 306.6438 | 274.1582
1029.0354 | 266.5825 | 122.8757 | 306.4227 | 261.5272 | 296.5139 | 306.5667 | 273.392
1030.0354 | 266.4704 | 122.9326 | 306.1667 | 262.5923 | 296.3556 | 305.2442 | 272.0365
1031.0354 | 265.4926 | 123.0998 | 306.5964 | 263.8874 | 296.8403 | 304.977 | 271.3998
1032.0354 | 264.5028 | 123.323 | 306.4728 | 263.5785 | 296.3035 | 303.5491 | 270.6983
1033.0354 | 263.6354 | 123.5374 | 306.3099 | 262.8975 | 295.8316 | 303.6384 | 271.5084
1034.0354 | 264.5874 | 123.6363 | 307.0746 | 264.1371 | 295.6959 | 304.1681 | 270.1693
1035.0354 | 265.9277 | 123.642 | 307.0444 | 264.1646 | 298.8857 | 305.7572 | 271.6189
1036.0354 | 265.791 | 123.8895 | 307.2032 | 264.4195 | 297.8193 | 307.6879 | 272.447
1037.0354 | 267.2888 | 123.7545 | 308.5318 | 265.6478 | 299.203 | 308.4759 | 273.8259
1038.0354 | 268.8178 | 123.9459 | 309.8294 | 265.7838 | 298.7393 | 307.4786 | 273.4232
1039.0354 | 269.9418 | 123.9427 | 309.6066 | 265.2579 | 298.129 | 308.366 | 273.4171
1040.0354 | 272.1105 | 123.9472 | 309.555 | 265.5812 | 299.2227 | 309.9048 | 275.5947
1041.0354 | 272.9936 | 124.2413 | 309.1078 | 265.9563 | 299.1499 | 309.4242 | 275.8684
1042.0354 | 273.892 | 124.121 | 309.3955 | 266.3494 | 298.6409 | 310.0776 | 276.9652
1043.0354 | 274.776 | 124.3655 | 309.5322 | 266.5392 | 299.5685 | 310.4426 | 277.0266
1044.0354 | 275.3747 | 124.4551 | 310.2676 | 266.9821 | 299.5297 | 312.5374 | 277.8147
1045.0354 | 276.187 | 124.5233 | 310.6897 | 267.4613 | 299.916 | 311.9914 | 277.6962
1046.0354 | 275.9846 | 124.9494 | 309.5409 | 267.8931 | 300.2771 | 312.3965 | 277.4441
1047.0354 | 276.0817 | 125.0802 | 309.5611 | 267.9658 | 299.8987 | 311.4602 | 276.6758
1048.0354 | 275.5277 | 125.2411 | 309.9256 | 268.4078 | 300.4512 | 311.6868 | 276.7421
1049.0354 | 275.1671 | 125.2406 | 310.4908 | 268.6149 | 300.8549 | 311.7181 | 276.4241
1050.0354 | 275.3707 | 125.362 | 310.52 | 269.3082 | 299.7704 | 311.445 | 276.8585
1051.0354 | 275.8482 | 125.4861 | 310.4018 | 269.4782 | 299.716 | 311.5619 | 277.0949
1052.0354 | 275.2423 | 125.6379 | 310.2452 | 270.33 | 299.9745 | 311.2924 | 276.9959
1053.0354 | 274.4095 | 125.7803 | 310.6592 | 270.3829 | 299.8635 | 310.4802 | 276.8207
1054.0354 | 273.965 | 125.8216 | 311.2069 | 270.9 | 298.7733 | 310.3427 | 276.9248
1055.0354 | 274.2468 | 125.9554 | 311.0627 | 271.1049 | 298.9902 | 310.5338 | 277.56
1056.0354 | 274.9839 | 125.9728 | 311.1865 | 271.2542 | 298.3093 | 310.2982 | 277.7437
1057.0354 | 276.427 | 126.1034 | 311.9269 | 271.1547 | 297.881 | 310.3371 | 278.6479
1058.0354 | 277.1587 | 126.2129 | 311.5362 | 272.0952 | 297.8782 | 311.0831 | 279.2987
1059.0354 | 277.5881 | 126.2713 | 312.0149 | 272.304 | 298.3876 | 312.282 | 279.5109
1060.0354 | 278.2046 | 126.5331 | 311.5328 | 272.648 | 298.8224 | 311.582 | 279.0807
1061.0354 | 278.2393 | 126.5703 | 311.9536 | 272.878 | 299.0949 | 310.8952 | 278.5111
1062.0354 | 278.0274 | 126.7939 | 311.7591 | 273.6896 | 300.0757 | 311.4422 | 278.123
1063.0354 | 277.7734 | 127.0007 | 311.7534 | 273.5319 | 299.2489 | 311.986 | 277.8292
1064.0354 | 277.7394 | 127.1509 | 311.6715 | 273.8725 | 298.991 | 312.6692 | 277.8726
1065.0354 | 276.5987 | 127.0424 | 311.8039 | 274.9184 | 299.1521 | 312.9706 | 277.4861
1066.0354 | 276.244 | 127.2775 | 312.1629 | 275.0854 | 299.6961 | 311.8625 | 276.2968
1067.0354 | 276.0267 | 127.4433 | 312.5083 | 275.2244 | 299.2561 | 310.9821 | 275.8039
1068.0354 | 276.3478 | 127.5643 | 312.5121 | 276.0064 | 299.9444 | 311.0277 | 276.0736
1069.0354 | 275.3421 | 127.6952 | 312.3173 | 277.0418 | 300.1861 | 310.7435 | 275.4728
1070.0354 | 274.5466 | 127.5617 | 312.1976 | 277.8402 | 301.4419 | 310.7295 | 275.926
1071.0354 | 275.1075 | 127.7475 | 312.855 | 277.7202 | 302.5361 | 310.5414 | 275.2763
1072.0354 | 274.6491 | 127.6595 | 313.8052 | 278.1469 | 302.2593 | 309.7919 | 275.5262
1073.0354 | 274.9196 | 127.8491 | 314.1066 | 277.4674 | 301.5918 | 311.8447 | 276.7244
1074.0354 | 275.7353 | 127.7815 | 313.8432 | 278.8224 | 302.319 | 314.5494 | 278.3023
1075.0354 | 276.1445 | 128.1321 | 314.2478 | 278.9382 | 304.5422 | 316.7136 | 280.7911
1076.0354 | 277.7638 | 128.2378 | 314.4611 | 279.2722 | 305.2433 | 317.961 | 282.5104
1077.0354 | 278.8983 | 128.2258 | 314.5713 | 279.8853 | 305.3429 | 318.1593 | 282.4518
1078.0354 | 279.6844 | 128.2028 | 315.2041 | 280.4197 | 308.2476 | 318.0017 | 282.3694
1079.0354 | 280.0626 | 128.485 | 314.8922 | 281.0968 | 310.181 | 320.3106 | 284.2565
1080.0354 | 281.6389 | 128.6101 | 314.5543 | 281.6889 | 310.6841 | 319.7883 | 284.8038
1081.0354 | 282.3085 | 128.5301 | 314.4578 | 282.2884 | 311.5246 | 319.6614 | 284.8543
1082.0354 | 283.1495 | 128.5405 | 314.5472 | 282.4882 | 312.081 | 319.2588 | 283.9069
1083.0354 | 283.7591 | 128.9754 | 314.5751 | 282.864 | 311.8868 | 318.1462 | 283.4112
1084.0354 | 283.7613 | 129.0203 | 315.1016 | 283.5206 | 311.555 | 317.4984 | 282.6225
1085.0354 | 284.7551 | 129.0577 | 315.2969 | 283.5154 | 310.8706 | 317.0698 | 283.1153
1086.0354 | 285.787 | 129.2864 | 314.9895 | 284.0146 | 310.8101 | 317.6586 | 282.5811
1087.0354 | 286.2981 | 129.3734 | 315.2304 | 284.8912 | 311.2209 | 317.4589 | 281.7013
1088.0354 | 286.3191 | 129.4986 | 315.6441 | 285.5359 | 311.95 | 317.7413 | 280.7672
1089.0354 | 285.4992 | 129.7484 | 315.6089 | 285.2081 | 312.1876 | 318.2015 | 280.3593
1090.0354 | 285.5385 | 129.9219 | 315.6018 | 285.656 | 311.3074 | 317.456 | 280.0962
1091.0354 | 285.113 | 129.9843 | 316.442 | 286.1987 | 311.9063 | 317.5918 | 279.7766
1092.0354 | 284.6603 | 130.2016 | 315.8747 | 287.4218 | 311.6387 | 319.174 | 281.0802
1093.0354 | 284.3751 | 130.2836 | 316.0062 | 287.542 | 311.4498 | 318.7888 | 280.3292
1094.0354 | 283.8849 | 130.2697 | 316.0909 | 287.8208 | 311.2063 | 317.9094 | 281.0511
1095.0354 | 283.6837 | 130.394 | 316.0043 | 287.9129 | 310.7523 | 316.9534 | 279.6857
1096.0354 | 283.0513 | 130.5382 | 315.9843 | 288.3377 | 309.5506 | 316.1229 | 279.0817
1097.0354 | 282.6478 | 130.79 | 316.5393 | 288.4082 | 309.3798 | 315.7223 | 278.6633
1098.0354 | 283.2195 | 130.9386 | 317.2888 | 288.7384 | 308.1174 | 315.9492 | 278.8417
1099.0354 | 284.1792 | 131.0351 | 318.4089 | 289.3773 | 308.1202 | 315.7692 | 279.4608
1100.0354 | 284.6799 | 130.8727 | 317.5019 | 289.3308 | 308.0383 | 316.5027 | 280.8988
1101.0354 | 285.2543 | 130.8685 | 317.9057 | 289.7298 | 307.0358 | 316.5946 | 280.8832
1102.0354 | 285.7976 | 130.998 | 318.2223 | 290.3156 | 307.2334 | 317.244 | 281.1401
1103.0354 | 286.4774 | 131.1295 | 318.7151 | 290.7983 | 307.7573 | 317.873 | 282.1725
1104.0354 | 285.9845 | 131.396 | 318.1717 | 291.5896 | 308.0018 | 318.4376 | 283.5186
1105.0354 | 286.4226 | 131.5491 | 318.7508 | 291.401 | 308.3948 | 318.1136 | 282.887
1106.0354 | 286.8773 | 131.6705 | 318.1981 | 292.8224 | 308.4415 | 319.0493 | 282.4907
1107.0354 | 286.7468 | 131.7076 | 318.4512 | 292.847 | 308.184 | 319.041 | 282.8097
1108.0354 | 286.3218 | 131.8525 | 318.9908 | 292.9313 | 308.9416 | 318.5301 | 283.3644
1109.0354 | 287.043 | 132.1197 | 318.6189 | 293.5633 | 309.6874 | 319.2898 | 285.1463
1110.0354 | 286.4516 | 131.9288 | 319.1651 | 293.8805 | 308.461 | 319.4676 | 285.9607
1111.0354 | 286.9267 | 132.2206 | 319.0351 | 294.476 | 308.2529 | 319.7951 | 286.0854
1112.0354 | 286.7852 | 132.3575 | 318.9044 | 294.7247 | 307.2452 | 320.7757 | 287.0294
1113.0354 | 287.5395 | 132.2654 | 319.5882 | 294.7478 | 306.8441 | 320.3178 | 286.8283
1114.0354 | 287.2512 | 132.2433 | 320.0379 | 294.9542 | 306.3391 | 320.6578 | 287.204
1115.0354 | 286.1582 | 132.3007 | 320.1785 | 295.7744 | 306.3321 | 320.7865 | 288.4652
1116.0354 | 285.796 | 132.537 | 320.1394 | 296.1669 | 306.6399 | 320.8191 | 289.1036
1117.0354 | 286.3382 | 132.7145 | 320.9499 | 297.0926 | 306.7961 | 321.3099 | 290.4607
1118.0354 | 286.4279 | 132.7002 | 321.0767 | 296.9538 | 307.0778 | 320.6774 | 290.7017
1119.0354 | 287.1908 | 132.8432 | 321.1974 | 296.9691 | 306.322 | 322.4269 | 292.4101
1120.0354 | 288.729 | 132.8796 | 321.0977 | 297.2326 | 306.4491 | 323.1373 | 293.1649
1121.0354 | 289.5229 | 133.0039 | 321.4952 | 298.0681 | 305.8983 | 324.9969 | 293.6141
1122.0354 | 290.1273 | 133.0392 | 321.6888 | 297.8442 | 306.351 | 325.7798 | 293.6578
1123.0354 | 290.2585 | 133.3647 | 321.8385 | 298.0573 | 307.7755 | 326.0667 | 293.7909
1124.0354 | 291.2084 | 133.407 | 321.9458 | 298.3755 | 309.1757 | 327.0019 | 295.2475
1125.0354 | 293.6256 | 133.4789 | 322.1493 | 298.9826 | 308.5298 | 327.8125 | 296.3136
1126.0354 | 293.801 | 133.5936 | 322.5674 | 298.7525 | 308.6005 | 328.3786 | 296.4371
1127.0354 | 294.1952 | 133.7063 | 323.7421 | 299.5113 | 308.3025 | 329.0268 | 297.9633
1128.0354 | 295.1005 | 133.856 | 324.2745 | 299.6295 | 309.2635 | 328.9215 | 299.2385
1129.0354 | 295.751 | 133.9059 | 324.1726 | 299.9961 | 311.1286 | 330.1728 | 300.4115
1130.0354 | 297.822 | 133.9624 | 324.161 | 300.0484 | 311.6098 | 331.9864 | 302.9369
1131.0354 | 298.333 | 134.045 | 325.53 | 300.4157 | 311.8539 | 332.1295 | 304.2131
1132.0354 | 299.2493 | 134.3604 | 326.3921 | 300.6528 | 311.4951 | 332.9304 | 304.8971
1133.0354 | 299.7508 | 134.4424 | 327.6422 | 301.0026 | 311.1425 | 332.7289 | 305.8278
1134.0354 | 301.1479 | 134.723 | 328.1645 | 301.5076 | 311.4016 | 333.2008 | 306.1944
1135.0354 | 302.5275 | 134.9276 | 328.0926 | 301.718 | 311.1868 | 333.0793 | 305.5188
1136.0354 | 304.3343 | 135.1819 | 328.0435 | 302.4484 | 311.8237 | 333.5846 | 306.3106
1137.0354 | 305.0303 | 135.4355 | 327.699 | 302.3126 | 311.3344 | 333.7391 | 305.8603
1138.0354 | 305.5768 | 135.4904 | 329.3705 | 302.504 | 310.4274 | 332.8538 | 304.2763
1139.0354 | 306.2272 | 135.5779 | 329.6833 | 302.8536 | 311.1046 | 333.1807 | 304.6608
1140.0354 | 306.6229 | 135.8444 | 330.8824 | 303.1754 | 311.8123 | 334.1954 | 303.9137
1141.0354 | 308.4812 | 136.0109 | 331.556 | 303.6408 | 312.0843 | 336.5913 | 304.825
1142.0354 | 310.4795 | 135.9816 | 331.0674 | 303.3658 | 312.5311 | 337.775 | 306.2674
1143.0354 | 309.9965 | 136.0364 | 331.3981 | 303.9594 | 311.34 | 337.7241 | 306.5096
1144.0354 | 309.9546 | 136.2545 | 331.1979 | 305.0026 | 310.0823 | 336.6952 | 304.8855
1145.0354 | 310.1375 | 136.5907 | 331.6781 | 305.2534 | 310.3997 | 336.4934 | 304.1287
1146.0354 | 311.1302 | 136.6047 | 332.3264 | 306.4708 | 310.846 | 335.1247 | 302.4583
1147.0354 | 312.3144 | 136.7683 | 334.2337 | 306.2264 | 310.8155 | 334.5127 | 300.8962
1148.0354 | 313.0715 | 136.8158 | 334.9198 | 306.1531 | 311.4129 | 333.9815 | 299.8141
1149.0354 | 314.0507 | 137.1528 | 334.6486 | 306.0894 | 312.678 | 335.1003 | 299.3482
1150.0354 | 313.8331 | 137.1707 | 335.622 | 305.973 | 312.6233 | 336.3573 | 300.2883
1151.0354 | 315.1518 | 137.2279 | 337.7688 | 307.0722 | 312.9534 | 338.6975 | 302.4595
1152.0354 | 318.2174 | 137.3761 | 337.9694 | 307.0839 | 313.9548 | 340.7281 | 303.3125
1153.0354 | 318.7009 | 137.5809 | 337.3401 | 307.1423 | 315.51 | 341.6581 | 303.8951
1154.0354 | 319.9352 | 137.7413 | 337.8818 | 307.8794 | 315.361 | 342.7307 | 303.7212
1155.0354 | 320.4197 | 137.8364 | 338.0231 | 307.9404 | 316.9687 | 342.7004 | 304.417
1156.0354 | 322.9047 | 137.9546 | 339.3358 | 308.0905 | 317.1582 | 343.8986 | 304.3008
1157.0354 | 324.4185 | 138.1473 | 339.4391 | 308.102 | 318.8574 | 345.1574 | 305.4249
1158.0354 | 324.6065 | 138.2169 | 339.1791 | 308.2045 | 318.5848 | 346.4647 | 306.1053
1159.0354 | 326.5265 | 138.4476 | 339.6861 | 308.3874 | 320.8917 | 348.9097 | 307.8464
1160.0354 | 327.5611 | 138.4484 | 340.2434 | 308.9838 | 323.5149 | 352.3875 | 310.4545
1161.0354 | 328.1842 | 138.4157 | 341.1152 | 309.4056 | 326.2443 | 354.0824 | 311.5992
1162.0354 | 328.7622 | 138.6719 | 341.3676 | 309.8511 | 326.7134 | 355.8603 | 313.6771
1163.0354 | 329.0487 | 138.903 | 341.6585 | 310.6044 | 327.1766 | 358.208 | 317.2405
1164.0354 | 330.2371 | 138.985 | 341.9684 | 310.3314 | 329.1565 | 358.6219 | 318.4018
1165.0354 | 332.7173 | 139.1545 | 342.5142 | 310.6408 | 329.572 | 358.3516 | 318.195
1166.0354 | 334.3005 | 139.4066 | 344.2009 | 310.6941 | 330.4866 | 360.3204 | 320.3051
1167.0354 | 336.892 | 139.395 | 346.3269 | 311.1656 | 332.345 | 361.5226 | 321.3105
1168.0354 | 337.9434 | 139.3344 | 347.2157 | 311.4081 | 332.4315 | 362.1975 | 321.9406
1169.0354 | 339.3154 | 139.4258 | 346.2896 | 311.5989 | 331.4502 | 361.0719 | 322.6514
1170.0354 | 337.95 | 139.707 | 346.0552 | 312.2336 | 330.9909 | 360.6806 | 322.8199
1171.0354 | 339.4427 | 140.0278 | 345.5086 | 312.1122 | 332.8234 | 361.7109 | 323.9976
1172.0354 | 340.3246 | 139.9964 | 346.8216 | 312.6382 | 332.3273 | 362.2449 | 323.1109
1173.0354 | 342.856 | 140.2368 | 347.2816 | 314.2195 | 333.9291 | 364.025 | 324.3174
1174.0354 | 344.4537 | 140.4187 | 347.0292 | 315.7334 | 333.7207 | 362.819 | 323.0962
1175.0354 | 344.0868 | 140.5857 | 349.0602 | 314.4573 | 333.6135 | 361.9995 | 322.3818
1176.0354 | 347.6413 | 140.6819 | 349.5749 | 314.6548 | 333.5548 | 361.9952 | 321.4178
1177.0354 | 351.521 | 140.8867 | 349.671 | 316.3598 | 334.1285 | 362.5282 | 321.1912
1178.0354 | 352.9315 | 140.9829 | 349.1738 | 316.4307 | 334.7434 | 361.7666 | 319.9619
1179.0354 | 356.1511 | 141.0431 | 349.6542 | 316.1566 | 334.4985 | 360.3589 | 318.9979
1180.0354 | 355.6246 | 141.295 | 351.6245 | 316.1648 | 334.4024 | 361.3626 | 318.6296
1181.0354 | 354.9861 | 141.1579 | 351.4647 | 316.7684 | 336.0167 | 362.6743 | 320.2447
1182.0354 | 356.4809 | 141.32 | 353.6422 | 316.6772 | 336.0735 | 361.4792 | 319.5605
1183.0354 | 358.5831 | 141.6644 | 355.3023 | 317.5122 | 336.0593 | 363.9376 | 319.7657
1184.0354 | 358.8817 | 141.9098 | 355.3314 | 318.7845 | 336.6952 | 365.7615 | 320.7847
1185.0354 | 360.9875 | 142.0764 | 356.8641 | 318.6128 | 336.2243 | 366.3506 | 321.2068
1186.0354 | 363.7831 | 142.2723 | 358.5862 | 318.5378 | 336.8389 | 367.0403 | 321.7462
1187.0354 | 364.1722 | 142.312 | 358.2142 | 318.846 | 336.7234 | 367.7085 | 323.0901
1188.0354 | 364.5854 | 142.3345 | 358.0249 | 319.2171 | 336.8643 | 367.4532 | 322.6913
1189.0354 | 365.9599 | 142.3372 | 357.673 | 319.4876 | 338.5991 | 369.1633 | 324.4581
1190.0354 | 367.8753 | 142.6028 | 358.0129 | 319.9633 | 339.3137 | 370.3729 | 325.7314
1191.0354 | 367.6983 | 142.6095 | 358.3957 | 320.2673 | 339.6266 | 372.2975 | 325.2751
1192.0354 | 367.5689 | 142.636 | 359.0485 | 320.2321 | 340.3242 | 372.5863 | 325.0855
1193.0354 | 367.8182 | 142.8175 | 360.6151 | 320.3506 | 340.2227 | 373.9566 | 326.5028
1194.0354 | 369.1198 | 143.042 | 360.7502 | 320.8676 | 342.1199 | 373.8575 | 327.6566
1195.0354 | 368.5927 | 143.2449 | 360.9737 | 320.9813 | 341.7617 | 373.1841 | 326.7628
1196.0354 | 367.8324 | 143.4694 | 361.8024 | 321.076 | 342.8621 | 373.5442 | 328.5413
1197.0354 | 369.8386 | 143.4461 | 362.8542 | 321.3736 | 345.3822 | 373.2002 | 329.2178
1198.0354 | 374.0605 | 143.5825 | 364.1912 | 321.9022 | 346.8458 | 376.539 | 330.2885
1199.0354 | 375.3456 | 143.639 | 364.1501 | 322.7395 | 347.3017 | 377.1931 | 332.6344
1200.0354 | 381.5474 | 143.9303 | 364.8391 | 323.3892 | 346.2345 | 377.2735 | 332.889
1201.0354 | 381.4859 | 144.2761 | 364.2353 | 323.3976 | 345.4562 | 377.7833 | 333.3077
1202.0354 | 383.2972 | 144.3806 | 365.3944 | 323.6797 | 345.3078 | 377.1728 | 333.0159
1203.0354 | 389.547 | 144.7805 | 366.2021 | 324.1834 | 346.024 | 377.9187 | 333.9005
1204.0354 | 394.7414 | 144.9228 | 368.1297 | 324.7052 | 346.9845 | 379.9744 | 335.4449
1205.0354 | 397.4974 | 145.0298 | 369.2086 | 324.7143 | 346.6546 | 380.9173 | 334.1705
1206.0354 | 399.7701 | 145.1702 | 369.602 | 325.1958 | 346.8326 | 382.1886 | 334.4969
1207.0354 | 399.2316 | 145.3003 | 369.029 | 325.5624 | 348.0436 | 382.363 | 334.8147
1208.0354 | 398.0465 | 145.3065 | 370.1745 | 325.992 | 350.1708 | 383.1735 | 336.8367
1209.0354 | 402.2565 | 145.3498 | 369.4694 | 325.7449 | 351.9109 | 384.0315 | 338.5055
1210.0354 | 402.5024 | 145.4096 | 369.7399 | 326.3612 | 352.4034 | 384.8067 | 337.2338
1211.0354 | 403.8406 | 145.5532 | 372.1434 | 326.823 | 354.2527 | 386.1106 | 338.3795
1212.0354 | 409.0516 | 145.7168 | 373.3458 | 327.4565 | 355.21 | 386.8055 | 339.0038
1213.0354 | 411.3797 | 145.8788 | 374.6659 | 327.332 | 354.0849 | 386.8607 | 338.1304
1214.0354 | 411.1627 | 145.9546 | 373.7995 | 328.2243 | 353.5546 | 387.4963 | 340.044
1215.0354 | 410.4419 | 146.0926 | 373.6897 | 328.6243 | 353.7349 | 388.1748 | 340.8857
1216.0354 | 408.962 | 146.2019 | 374.2712 | 328.3894 | 354.6892 | 390.7276 | 340.7011
1217.0354 | 408.4371 | 146.4956 | 375.4072 | 328.6813 | 357.1741 | 391.1272 | 341.748
1218.0354 | 416.1294 | 146.6782 | 375.9552 | 329.0139 | 358.804 | 391.4915 | 342.2267
1219.0354 | 420.3391 | 146.6915 | 376.2814 | 329.2904 | 359.8224 | 392.706 | 344.5455
1220.0354 | 420.3184 | 146.7766 | 376.1303 | 330.4231 | 359.6992 | 394.962 | 345.2703
1221.0354 | 420.8104 | 146.8829 | 376.3163 | 330.7133 | 361.0846 | 395.5925 | 345.4024
1222.0354 | 425.0342 | 146.9803 | 376.5768 | 331.2579 | 361.3967 | 396.6876 | 344.6569
1223.0354 | 426.4506 | 147.1149 | 377.1296 | 331.9614 | 362.4799 | 395.533 | 343.9466
1224.0354 | 436.3999 | 147.2166 | 377.7531 | 331.4312 | 362.9946 | 396.3963 | 342.868
1225.0354 | 438.4571 | 147.2998 | 378.2166 | 331.4054 | 364.1284 | 399.6576 | 343.0598
1226.0354 | 445.3664 | 147.4808 | 378.7675 | 331.7917 | 364.2287 | 402.3756 | 344.2401
1227.0354 | 456.6029 | 147.8113 | 379.718 | 332.4967 | 364.5073 | 404.3274 | 344.2521
1228.0354 | 453.4369 | 147.9991 | 380.3148 | 333.0007 | 364.2424 | 405.0486 | 344.8062
1229.0354 | 453.8502 | 148.2039 | 380.9988 | 333.6224 | 367.1705 | 406.5375 | 345.8611
1230.0354 | 459.2371 | 148.5044 | 381.3036 | 334.0081 | 369.1713 | 406.8699 | 346.427
1231.0354 | 454.7899 | 148.7346 | 381.0788 | 334.81 | 370.7022 | 407.1506 | 346.5988
1232.0354 | 452.4741 | 148.8551 | 381.307 | 334.9143 | 372.9133 | 409.2343 | 345.9613
1233.0354 | 449.7746 | 149.1047 | 381.3542 | 336.3654 | 373.8363 | 410.6062 | 346.9393
1234.0354 | 467.2531 | 149.2675 | 381.9833 | 335.9708 | 374.5247 | 409.9822 | 347.431
1235.0354 | 466.3253 | 149.4617 | 382.3279 | 336.3446 | 374.4617 | 410.0519 | 347.6419
1236.0354 | 470.6484 | 149.4719 | 382.8008 | 336.5416 | 376.0451 | 409.9884 | 348.4994
1237.0354 | 469.8704 | 149.4304 | 382.9162 | 337.5672 | 375.1344 | 410.5409 | 348.0521
1238.0354 | 466.4278 | 149.6348 | 383.0562 | 338.0517 | 375.2531 | 410.3791 | 347.811
1239.0354 | 476.1458 | 149.7856 | 383.2041 | 338.3591 | 374.7972 | 409.6263 | 346.649
1240.0354 | 476.5595 | 150.0395 | 384.3077 | 338.8835 | 375.4299 | 409.9752 | 346.4516
1241.0354 | 493.5531 | 150.0055 | 384.5621 | 338.9878 | 375.196 | 409.9996 | 347.1736
1242.0354 | 488.4283 | 150.1451 | 385.7119 | 338.9327 | 374.7596 | 410.3321 | 348.0521
1243.0354 | 507.0421 | 150.3977 | 385.7699 | 339.9184 | 375.4641 | 410.9346 | 348.6548
1244.0354 | 520.208 | 150.3729 | 385.7373 | 341.3009 | 376.1427 | 412.0856 | 349.8839
1245.0354 | 528.8278 | 150.4724 | 385.5205 | 341.4183 | 376.2247 | 411.6328 | 349.7577
1246.0354 | 546.8916 | 150.6556 | 385.8892 | 342.4519 | 375.9862 | 409.8993 | 348.8291
1247.0354 | 547.7395 | 150.8267 | 386.2651 | 342.7745 | 376.9042 | 410.324 | 348.8685
1248.0354 | 562.9662 | 150.9115 | 387.0684 | 343.0934 | 376.7458 | 410.3872 | 348.6181
1249.0354 | 579.6504 | 151.0613 | 388.4905 | 342.7317 | 376.7016 | 411.2846 | 349.0951
1250.0354 | 590.4047 | 151.3939 | 390.6393 | 343.1819 | 377.3847 | 412.3249 | 350.5287
1251.0354 | 583.8155 | 151.5359 | 390.7787 | 343.5954 | 378.2502 | 413.8543 | 353.4297
1252.0354 | 595.1695 | 151.7496 | 390.461 | 343.9791 | 379.4589 | 414.6647 | 355.3099
1253.0354 | 607.2474 | 151.745 | 392.1229 | 344.4564 | 380.6865 | 416.0175 | 356.834
1254.0354 | 626.9186 | 152.0091 | 393.3564 | 344.7994 | 381.8397 | 417.5903 | 357.8065
1255.0354 | 655.229 | 152.276 | 393.288 | 345.4751 | 382.2747 | 418.0901 | 359.0204
1256.0354 | 670.6556 | 152.2265 | 392.9757 | 345.3911 | 381.3042 | 420.8906 | 361.1588
1257.0354 | 655.0271 | 152.3053 | 393.5039 | 345.9321 | 380.9767 | 421.6848 | 361.9856
1258.0354 | 671.9063 | 152.4746 | 393.6995 | 346.4838 | 383.6683 | 422.386 | 363.0814
1259.0354 | 671.1804 | 152.6338 | 393.8306 | 346.8857 | 383.682 | 423.5363 | 363.4266
1260.0354 | 682.2522 | 152.9549 | 394.4478 | 347.005 | 383.8816 | 423.9946 | 362.642
1261.0354 | 661.6716 | 153.1475 | 394.4562 | 347.5334 | 383.5972 | 423.9676 | 362.2794
1262.0354 | 645.4172 | 153.1194 | 395.8023 | 348.0679 | 384.4023 | 425.699 | 363.1752
1263.0354 | 653.1224 | 153.3612 | 397.6639 | 348.3346 | 386.2807 | 427.0138 | 364.6509
1264.0354 | 646.4928 | 153.4861 | 397.6783 | 348.4188 | 385.4844 | 425.5239 | 366.0099
1265.0354 | 630.3244 | 153.7113 | 397.1843 | 348.8011 | 384.0547 | 425.0285 | 365.798
1266.0354 | 638.9981 | 153.9385 | 396.8129 | 349.7583 | 385.322 | 425.6381 | 367.1511
1267.0354 | 661.161 | 154.0851 | 397.7246 | 349.694 | 385.7339 | 428.2863 | 367.9258
1268.0354 | 666.7388 | 154.2409 | 398.8387 | 349.8803 | 385.6861 | 429.2337 | 368.8561
1269.0354 | 645.7498 | 154.3937 | 398.7326 | 350.7243 | 386.9444 | 429.0742 | 370.5229
1270.0354 | 621.2515 | 154.7122 | 399.0765 | 351.6237 | 388.5873 | 427.7617 | 370.6373
1271.0354 | 600.8712 | 154.8387 | 399.3936 | 351.8535 | 389.287 | 427.5803 | 370.0736
1272.0354 | 584.8668 | 154.9416 | 400.0049 | 352.5633 | 391.1601 | 428.7022 | 369.8835
1273.0354 | 590.2059 | 155.1447 | 400.2002 | 352.537 | 392.1379 | 428.9848 | 370.8614
1274.0354 | 588.0475 | 155.3312 | 400.8223 | 353.2157 | 393.4572 | 428.8772 | 371.4267
1275.0354 | 577.1731 | 155.3931 | 401.3721 | 353.1966 | 392.5657 | 427.6249 | 371.4711
1276.0354 | 587.172 | 155.6192 | 402.3477 | 353.9476 | 391.8254 | 426.5826 | 370.7534
1277.0354 | 583.3872 | 155.9073 | 401.5698 | 354.7169 | 391.1454 | 427.4042 | 370.6703
1278.0354 | 591.5625 | 156.0932 | 402.8632 | 355.1139 | 391.3532 | 427.8426 | 370.0886
1279.0354 | 602.8408 | 156.2543 | 404.2045 | 354.9459 | 391.8582 | 425.5741 | 368.4448
1280.0354 | 615.4367 | 156.4202 | 403.3752 | 355.4923 | 390.5695 | 424.3395 | 368.4057
1281.0354 | 616.2204 | 156.5509 | 403.3656 | 356.7593 | 390.9438 | 424.6351 | 367.7254
1282.0354 | 607.8349 | 156.7296 | 403.3122 | 357.5443 | 390.0415 | 423.3406 | 366.9099
1283.0354 | 594.6106 | 156.8116 | 403.9292 | 357.1671 | 391.0892 | 422.9604 | 365.6844
1284.0354 | 585.1203 | 156.9411 | 404.0613 | 357.4456 | 390.0132 | 421.0593 | 363.578
1285.0354 | 573.3291 | 157.0397 | 403.9234 | 357.9098 | 392.0183 | 422.4857 | 362.6858
1286.0354 | 577.2638 | 157.2012 | 404.5849 | 358.3107 | 392.9322 | 422.3534 | 362.3172
1287.0354 | 591.0049 | 157.4525 | 405.0382 | 358.52 | 393.836 | 421.9303 | 361.1709
1288.0354 | 587.3963 | 157.6043 | 406.5871 | 359.006 | 394.2788 | 422.2763 | 361.9494
1289.0354 | 585.2694 | 157.7083 | 406.026 | 360.0707 | 394.5753 | 420.5948 | 362.4118
1290.0354 | 585.7946 | 157.7762 | 406.1618 | 362.4187 | 394.2737 | 418.6202 | 361.0738
1291.0354 | 588.7874 | 157.8755 | 405.9481 | 362.9496 | 392.9514 | 417.805 | 359.4053
1292.0354 | 565.472 | 158.0539 | 405.8637 | 362.5987 | 391.848 | 416.189 | 358.5613
1293.0354 | 568.305 | 158.3069 | 406.8671 | 362.7232 | 392.625 | 415.5054 | 358.4426
1294.0354 | 562.8496 | 158.5413 | 407.081 | 363.1334 | 393.8951 | 415.5755 | 359.1127
1295.0354 | 561.4482 | 158.6893 | 408.4706 | 363.4453 | 393.6606 | 415.4403 | 359.7763
1296.0354 | 555.4908 | 158.5344 | 407.9174 | 363.5454 | 392.7778 | 413.9032 | 358.3474
1297.0354 | 557.169 | 158.8063 | 408.1332 | 365.0004 | 392.8443 | 414.311 | 359.2904
1298.0354 | 560.4267 | 158.9958 | 407.8744 | 365.7731 | 393.5974 | 413.3654 | 358.9643
1299.0354 | 554.7241 | 159.2196 | 408.4338 | 366.8424 | 394.3282 | 413.4505 | 358.6075
1300.0354 | 568.0711 | 159.1327 | 408.7752 | 366.6616 | 395.4127 | 413.005 | 357.3936
1301.0354 | 563.1643 | 159.3737 | 409.2588 | 366.6584 | 395.2782 | 413.7613 | 357.9895
1302.0354 | 549.3554 | 159.4567 | 409.1157 | 366.7757 | 395.224 | 414.1186 | 358.8712
1303.0354 | 543.0416 | 159.479 | 409.3892 | 367.8986 | 396.2301 | 413.4613 | 358.9553
1304.0354 | 544.3634 | 159.7798 | 410.3607 | 368.1297 | 398.1629 | 415.002 | 359.333
1305.0354 | 555.794 | 159.8135 | 410.8803 | 368.8014 | 397.3735 | 414.5554 | 359.5273
1306.0354 | 564.7078 | 159.8609 | 410.833 | 369.0613 | 396.9431 | 416.271 | 360.158
1307.0354 | 563.5538 | 160.1017 | 411.8845 | 369.3742 | 395.7353 | 416.8029 | 360.7704
1308.0354 | 555.2557 | 160.1878 | 411.5944 | 370.04 | 394.3866 | 417.6677 | 361.1371
1309.0354 | 559.7249 | 160.3358 | 411.4002 | 370.5339 | 395.0729 | 419.0674 | 362.7442
1310.0354 | 553.0335 | 160.4183 | 412.1637 | 370.6064 | 395.4584 | 417.6719 | 363.1034
1311.0354 | 567.1381 | 160.6169 | 412.0059 | 371.3694 | 395.5909 | 417.717 | 362.9253
1312.0354 | 567.2123 | 160.643 | 412.2861 | 372.364 | 394.758 | 418.2031 | 362.6181
1313.0354 | 571.4797 | 160.7669 | 412.7928 | 371.9237 | 394.6545 | 419.5062 | 363.2107
1314.0354 | 580.5136 | 161.1703 | 413.0292 | 372.1183 | 393.8043 | 421.5008 | 363.975
1315.0354 | 573.7562 | 161.3041 | 412.7868 | 372.9029 | 392.7887 | 423.2637 | 363.4143
1316.0354 | 573.1893 | 161.3988 | 413.9068 | 373.1616 | 392.4952 | 424.2327 | 364.944
1317.0354 | 559.6864 | 161.5328 | 413.4867 | 374.6292 | 392.0171 | 424.6381 | 364.8044
1318.0354 | 558.6818 | 161.8527 | 413.7311 | 375.3739 | 391.9883 | 425.4954 | 363.5853
1319.0354 | 545.4648 | 162.0085 | 413.7318 | 374.9533 | 392.8703 | 423.4652 | 362.2389
1320.0354 | 539.8342 | 162.0367 | 413.8219 | 375.585 | 392.403 | 422.1915 | 361.1492
1321.0354 | 542.1666 | 162.0291 | 414.3985 | 376.5251 | 392.457 | 422.2285 | 361.3756
1322.0354 | 537.9279 | 162.0699 | 414.2543 | 375.9674 | 393.1369 | 420.699 | 360.896
1323.0354 | 522.3136 | 162.1764 | 415.333 | 376.4712 | 394.2803 | 420.6588 | 361.999
1324.0354 | 526.4043 | 162.3547 | 415.9772 | 377.15 | 394.0281 | 419.7771 | 362.4908
1325.0354 | 523.1283 | 162.7 | 415.7098 | 377.6772 | 394.5094 | 419.5645 | 362.762
1326.0354 | 515.4442 | 162.8889 | 415.3763 | 378.4186 | 393.7956 | 419.1578 | 362.2412
1327.0354 | 500.0019 | 163.1915 | 415.888 | 378.7185 | 393.7869 | 418.559 | 362.2818
1328.0354 | 500.4293 | 163.0909 | 415.9797 | 379.0094 | 394.2665 | 418.9002 | 363.1827
1329.0354 | 499.5664 | 163.0756 | 416.4513 | 379.1924 | 396.0449 | 419.8265 | 363.4382
1330.0354 | 501.6465 | 163.1363 | 416.3448 | 379.7607 | 394.9373 | 420.9362 | 363.24
1331.0354 | 506.1624 | 163.2351 | 416.5035 | 380.0296 | 395.1096 | 420.8682 | 363.1489
1332.0354 | 524.4279 | 163.5346 | 417.8755 | 380.8819 | 396.3539 | 421.1243 | 363.4569
1333.0354 | 523.7422 | 163.7349 | 418.8613 | 381.5241 | 395.3641 | 420.7764 | 362.2654
1334.0354 | 535.2337 | 163.98 | 419.1804 | 381.8604 | 395.464 | 420.4405 | 363.438
1335.0354 | 527.6838 | 164.2395 | 420.0202 | 381.7828 | 394.3609 | 420.1033 | 364.3064
1336.0354 | 518.1228 | 164.2814 | 419.8832 | 382.0738 | 393.2986 | 419.1292 | 364.7518
1337.0354 | 506.6756 | 164.3792 | 421.0362 | 382.6236 | 393.2258 | 419.2027 | 365.0682
1338.0354 | 496.3442 | 164.7332 | 422.0239 | 382.9662 | 392.7123 | 418.3466 | 363.95
1339.0354 | 486.5273 | 164.9825 | 421.6042 | 383.6098 | 393.6766 | 418.6327 | 363.7181
1340.0354 | 479.5807 | 165.1914 | 423.6608 | 383.5992 | 393.6491 | 419.3888 | 364.6525
1341.0354 | 471.7253 | 165.2181 | 423.1842 | 384.1134 | 393.3966 | 418.6574 | 364.3476
1342.0354 | 466.2055 | 165.1545 | 422.3694 | 384.5934 | 393.877 | 418.516 | 364.6026
1343.0354 | 460.3517 | 165.374 | 423.7003 | 384.9109 | 393.5132 | 418.3628 | 363.7385
1344.0354 | 454.3027 | 165.5774 | 423.6463 | 385.2673 | 395.1916 | 417.5733 | 364.1917
1345.0354 | 449.2142 | 165.7722 | 424.1838 | 386.0556 | 394.3929 | 416.4179 | 363.956
1346.0354 | 443.1783 | 166.0956 | 425.4364 | 385.8034 | 394.7265 | 415.8053 | 363.793
1347.0354 | 437.5518 | 165.9625 | 424.7228 | 386.3883 | 393.3656 | 415.3791 | 363.2287
1348.0354 | 435.6789 | 166.1327 | 424.54 | 386.7296 | 393.5607 | 416.6856 | 363.1319
1349.0354 | 433.5947 | 166.3502 | 424.892 | 387.2184 | 392.5967 | 417.0434 | 363.0951
1350.0354 | 430.513 | 166.4184 | 425.8058 | 387.0704 | 392.7418 | 417.3336 | 363.4102
1351.0354 | 428.9863 | 166.5571 | 426.5493 | 387.7102 | 392.1695 | 416.4886 | 363.3187
1352.0354 | 427.3486 | 166.7427 | 426.0626 | 388.25 | 393.5202 | 419.0929 | 364.5657
1353.0354 | 425.3062 | 166.9865 | 425.8514 | 388.4525 | 393.9101 | 419.8206 | 363.9271
1354.0354 | 424.99 | 167.0107 | 426.9201 | 389.1174 | 394.1576 | 420.1123 | 363.0555
1355.0354 | 422.6755 | 167.0053 | 427.1281 | 389.4359 | 393.7946 | 420.6725 | 363.1513
1356.0354 | 423.0778 | 167.2345 | 427.8548 | 389.3751 | 393.2615 | 420.7118 | 363.0039
1357.0354 | 422.1416 | 167.4267 | 427.6904 | 389.821 | 392.7461 | 420.1601 | 364.1121
1358.0354 | 418.7464 | 167.5752 | 427.8669 | 390.5349 | 392.1401 | 418.9957 | 364.6678
1359.0354 | 416.4974 | 167.8005 | 428.4173 | 391.2254 | 391.4807 | 417.6954 | 364.2396
1360.0354 | 415.9364 | 167.9956 | 429.3305 | 391.3358 | 391.9044 | 416.9893 | 363.947
1361.0354 | 414.4069 | 168.1934 | 429.6066 | 391.5869 | 391.3741 | 416.2799 | 364.1518
1362.0354 | 412.6805 | 168.3214 | 429.709 | 392.0068 | 390.7813 | 415.8458 | 364.1394
1363.0354 | 412.5764 | 168.4288 | 430.2629 | 392.1406 | 390.3178 | 415.0618 | 363.387
1364.0354 | 410.6193 | 168.6208 | 430.0288 | 392.217 | 390.5394 | 415.5078 | 363.7752
1365.0354 | 409.2949 | 168.8595 | 430.8321 | 392.7071 | 390.2023 | 414.9754 | 364.2366
1366.0354 | 409.1927 | 168.9469 | 432.1855 | 392.8431 | 391.67 | 415.1407 | 365.3634
1367.0354 | 411.0512 | 168.9837 | 431.9475 | 393.2715 | 390.7082 | 415.612 | 365.0048
1368.0354 | 410.5372 | 169.236 | 431.9897 | 393.9631 | 391.1697 | 415.9145 | 365.6916
1369.0354 | 408.4566 | 169.1539 | 432.2754 | 394.5193 | 392.12 | 415.5291 | 366.4019
1370.0354 | 408.5382 | 169.3695 | 433.0407 | 394.3082 | 392.3145 | 416.3227 | 366.6891
1371.0354 | 408.3801 | 169.4935 | 434.9803 | 394.7184 | 391.301 | 416.4107 | 366.7023
1372.0354 | 407.923 | 169.5745 | 434.5047 | 395.2481 | 391.8093 | 416.1205 | 366.9616
1373.0354 | 408.5945 | 169.7533 | 433.999 | 396.0728 | 392.171 | 416.3172 | 367.6489
1374.0354 | 407.949 | 169.8078 | 435.9895 | 396.5259 | 391.7346 | 415.5495 | 366.6242
1375.0354 | 407.8898 | 170.0231 | 435.8939 | 396.377 | 391.9899 | 414.0981 | 365.2231
1376.0354 | 407.921 | 170.2279 | 435.9353 | 396.2236 | 392.4111 | 414.8363 | 365.4106
1377.0354 | 409.7658 | 170.3615 | 435.6773 | 396.359 | 393.1619 | 415.8076 | 366.9201
1378.0354 | 409.354 | 170.528 | 436.6977 | 396.8588 | 393.2357 | 418.4486 | 367.1813
1379.0354 | 409.9774 | 170.9257 | 437.2818 | 397.3339 | 393.3643 | 418.0819 | 368.237
1380.0354 | 409.6059 | 171.8383 | 438.4039 | 397.4362 | 392.8043 | 416.2934 | 365.4569
1381.0354 | 409.8716 | 171.266 | 438.4861 | 398.1014 | 392.5895 | 415.5866 | 366.0649
1382.0354 | 411.0158 | 171.8072 | 438.5786 | 398.1989 | 392.5075 | 415.8487 | 366.51
1383.0354 | 410.5835 | 171.2981 | 438.3596 | 398.2261 | 392.0005 | 416.443 | 368.0993
1384.0354 | 408.8513 | 171.3241 | 438.0347 | 398.7391 | 391.3412 | 418.0509 | 368.3559
1385.0354 | 407.1125 | 171.5782 | 438.2129 | 398.7975 | 391.1673 | 419.2638 | 367.6269
1386.0354 | 408.0817 | 171.8227 | 438.5546 | 399.3989 | 391.2113 | 419.3591 | 366.3804
1387.0354 | 407.613 | 172.0035 | 438.6711 | 400.1372 | 391.3456 | 419.1615 | 367.1481
1388.0354 | 406.0105 | 172.1413 | 439.4148 | 400.0653 | 390.483 | 418.2276 | 367.3649
1389.0354 | 405.0735 | 172.241 | 440.03 | 400.194 | 390.248 | 417.3095 | 366.5244
1390.0354 | 403.6366 | 172.8452 | 439.8759 | 400.5127 | 391.2355 | 416.549 | 366.5871
1391.0354 | 403.032 | 172.768 | 440.4558 | 401.4921 | 390.5252 | 415.8871 | 365.0696
1392.0354 | 402.4951 | 172.5712 | 441.7218 | 400.9722 | 390.6907 | 416.2285 | 363.9496
1393.0354 | 401.3247 | 172.6991 | 442.4491 | 400.9638 | 391.35 | 416.1496 | 364.104
1394.0354 | 400.9546 | 172.914 | 442.5219 | 401.4359 | 391.738 | 416.4165 | 364.902
1395.0354 | 400.6581 | 172.9031 | 441.9591 | 402.1055 | 391.5913 | 416.0647 | 365.4109
1396.0354 | 400.6611 | 173.0329 | 442.7508 | 401.8229 | 391.6473 | 416.2988 | 366.4007
1397.0354 | 402.1657 | 173.1205 | 443.8638 | 402.1457 | 390.1614 | 416.8722 | 367.2128
1398.0354 | 402.4356 | 173.1924 | 444.0616 | 402.531 | 388.6577 | 416.295 | 367.779
1399.0354 | 402.0306 | 173.2358 | 443.8806 | 402.8819 | 387.7451 | 414.8083 | 367.7132
1400.0354 | 401.3024 | 173.6836 | 445.0475 | 403.0587 | 387.3256 | 414.479 | 367.232
1401.0354 | 400.5706 | 173.7385 | 445.7692 | 402.8948 | 387.0018 | 413.5986 | 367.2067
1402.0354 | 399.8509 | 174.0335 | 445.7146 | 403.022 | 387.2782 | 412.936 | 367.0527
1403.0354 | 399.0896 | 174.0898 | 445.7982 | 404.0808 | 386.1438 | 411.472 | 366.367
1404.0354 | 399.8473 | 174.1923 | 445.8503 | 403.8695 | 385.6135 | 410.9445 | 366.2262
1405.0354 | 399.8746 | 174.2633 | 446.3712 | 404.2566 | 385.6008 | 410.5423 | 365.4494
1406.0354 | 401.2313 | 174.3666 | 446.5071 | 404.0445 | 386.4133 | 410.8242 | 366.141
1407.0354 | 400.1008 | 174.4251 | 446.4391 | 404.4303 | 385.3851 | 410.949 | 366.4222
1408.0354 | 398.4377 | 174.5272 | 447.0464 | 404.4977 | 384.9885 | 412.3873 | 366.2701
1409.0354 | 396.5583 | 174.6825 | 446.9573 | 404.5027 | 384.1801 | 412.335 | 365.6538
1410.0354 | 394.7779 | 174.8572 | 446.914 | 404.7079 | 383.4633 | 411.2173 | 364.7642
1411.0354 | 392.7169 | 175.1357 | 447.263 | 405.7532 | 383.2144 | 409.8476 | 362.8574
1412.0354 | 391.3811 | 175.2638 | 449.7129 | 405.3255 | 382.6696 | 409.1644 | 362.5536
1413.0354 | 391.3871 | 175.3235 | 449.1374 | 405.3787 | 382.8294 | 408.9919 | 362.8779
1414.0354 | 392.103 | 175.4935 | 449.502 | 405.4762 | 381.8998 | 409.2437 | 363.1435
1415.0354 | 391.5907 | 175.8976 | 449.4232 | 405.6201 | 381.3135 | 409.4543 | 363.1435
1416.0354 | 392.8785 | 176.1273 | 449.0487 | 405.6865 | 381.5347 | 410.9737 | 363.034
1417.0354 | 393.1844 | 176.2098 | 449.6097 | 405.8955 | 380.6361 | 412.1206 | 363.5099
1418.0354 | 391.9202 | 176.4055 | 450.4345 | 406.1205 | 380.3514 | 412.6056 | 363.625
1419.0354 | 391.0634 | 176.3487 | 450.1691 | 406.2033 | 379.8483 | 412.4489 | 363.2803
1420.0354 | 391.7806 | 176.5335 | 449.952 | 406.1194 | 379.1497 | 411.3672 | 361.833
1421.0354 | 390.2009 | 176.7327 | 449.9589 | 406.9495 | 379.5102 | 411.7688 | 360.5931
1422.0354 | 389.4811 | 176.9337 | 450.4245 | 406.5977 | 380.2829 | 412.7554 | 360.5946
1423.0354 | 388.5619 | 177.0473 | 450.6502 | 406.5691 | 379.7378 | 412.0197 | 359.8212
1424.0354 | 386.4075 | 177.3499 | 451.6577 | 407.0286 | 379.7451 | 411.4874 | 359.4372
1425.0354 | 386.5998 | 177.5323 | 451.3166 | 407.1814 | 378.7975 | 411.2079 | 359.5237
1426.0354 | 385.3401 | 177.2833 | 452.0485 | 407.6184 | 378.1467 | 411.4203 | 359.5158
1427.0354 | 383.9741 | 177.3032 | 451.5677 | 407.2882 | 378.4686 | 410.6006 | 359.5852
1428.0354 | 383.4355 | 177.51 | 452.1604 | 407.3049 | 377.9645 | 409.8686 | 359.8388
1429.0354 | 383.9195 | 177.5737 | 452.3817 | 407.4462 | 377.824 | 408.5225 | 358.9774
1430.0354 | 383.715 | 177.838 | 453.3232 | 407.6435 | 378.99 | 408.2801 | 359.2108
1431.0354 | 383.5075 | 177.8592 | 452.9901 | 408.3875 | 378.8166 | 406.9619 | 359.6911
1432.0354 | 382.3027 | 177.8724 | 452.0569 | 407.9289 | 378.9461 | 405.8854 | 359.2649
1433.0354 | 381.2794 | 178.1785 | 451.9922 | 408.6764 | 377.7954 | 404.5927 | 357.536
1434.0354 | 380.6047 | 178.326 | 452.3235 | 408.1962 | 377.0885 | 403.3599 | 356.7864
1435.0354 | 378.5524 | 178.35 | 451.9361 | 409.0177 | 376.4949 | 401.8736 | 355.8851
1436.0354 | 377.5039 | 178.7013 | 452.1118 | 408.9972 | 375.6462 | 400.7207 | 354.552
1437.0354 | 375.69 | 178.8508 | 451.845 | 409.0037 | 376.9661 | 399.383 | 353.8142
1438.0354 | 374.4624 | 179.0048 | 451.8475 | 410.2487 | 377.4907 | 397.9377 | 351.9275
1439.0354 | 373.0009 | 179.0359 | 452.4179 | 409.7145 | 376.9277 | 397.8716 | 350.7629
1440.0354 | 372.0005 | 179.0594 | 453.3312 | 410.1426 | 377.4555 | 397.8527 | 350.1057
1441.0354 | 371.7759 | 179.1682 | 453.721 | 410.6388 | 379.0386 | 398.4107 | 351.1237
1442.0354 | 371.7388 | 179.2506 | 453.2467 | 411.2054 | 379.393 | 398.9613 | 351.4993
1443.0354 | 370.9894 | 179.4656 | 453.101 | 412.0403 | 380.5794 | 399.0658 | 352.8086
1444.0354 | 370.153 | 179.7501 | 453.0116 | 411.3157 | 379.6288 | 398.7114 | 353.013
1445.0354 | 369.9361 | 179.7451 | 453.2273 | 410.9789 | 378.9533 | 398.1141 | 352.9614
1446.0354 | 370.6974 | 180.0276 | 453.5198 | 411.3364 | 379.0439 | 397.5474 | 352.3133
1447.0354 | 370.6723 | 179.9773 | 452.8915 | 412.2979 | 379.4942 | 397.4276 | 352.5914
1448.0354 | 370.864 | 180.1228 | 452.601 | 412.4321 | 380.4146 | 397.6504 | 351.9202
1449.0354 | 371.076 | 180.3468 | 452.8002 | 412.3433 | 380.6329 | 395.9451 | 350.7422
1450.0354 | 370.9972 | 180.4886 | 453.0585 | 412.8001 | 381.1928 | 395.0476 | 349.7379
1451.0354 | 369.9672 | 180.5547 | 452.6385 | 412.8419 | 380.8492 | 395.09 | 349.0464
1452.0354 | 369.5838 | 180.8208 | 453.6637 | 414.2216 | 380.8045 | 394.5004 | 348.2147
1453.0354 | 368.0015 | 180.8606 | 453.8139 | 413.4973 | 382.0675 | 394.7287 | 347.9873
1454.0354 | 368.8973 | 180.9089 | 454.5645 | 413.3943 | 383.3113 | 395.1538 | 348.7976
1455.0354 | 369.9117 | 180.966 | 454.0264 | 413.4415 | 382.6692 | 396.2541 | 349.954
1456.0354 | 369.6211 | 181.0673 | 453.9244 | 413.8166 | 381.6285 | 396.3292 | 349.1959
1457.0354 | 369.4769 | 181.1765 | 453.6352 | 413.7805 | 381.0261 | 395.7332 | 348.6097
1458.0354 | 370.0927 | 181.3835 | 455.0646 | 414.3644 | 380.977 | 395.0545 | 348.2335
1459.0354 | 371.0491 | 181.7208 | 456.6635 | 414.0549 | 380.6223 | 396.0019 | 349.2238
1460.0354 | 372.7943 | 181.7926 | 456.738 | 414.2171 | 381.9458 | 398.065 | 351.3993
1461.0354 | 374.3854 | 181.9486 | 456.0431 | 414.5337 | 381.2883 | 399.8945 | 354.0407
1462.0354 | 376.8034 | 182.0786 | 457.1251 | 414.733 | 381.9078 | 401.1016 | 355.9064
1463.0354 | 377.7994 | 182.2448 | 456.8078 | 414.8324 | 381.8013 | 401.6122 | 356.7573
1464.0354 | 378.8736 | 182.2736 | 456.6342 | 415.0724 | 382.2416 | 402.7051 | 357.3445
1465.0354 | 379.8823 | 182.4062 | 457.0393 | 415.195 | 383.2523 | 403.0568 | 358.5863
1466.0354 | 381.8255 | 182.4949 | 457.681 | 415.6567 | 382.9789 | 403.2304 | 359.1264
1467.0354 | 382.2089 | 182.6735 | 457.9004 | 415.9579 | 383.1849 | 403.3476 | 358.9285
1468.0354 | 383.5947 | 182.8797 | 458.7276 | 416.705 | 383.1561 | 403.6659 | 358.7266
1469.0354 | 384.9565 | 183.027 | 459.7981 | 416.1958 | 383.1837 | 403.7535 | 358.6372
1470.0354 | 386.4791 | 183.0259 | 459.9536 | 416.1765 | 383.6737 | 404.2368 | 359.5675
1471.0354 | 387.9947 | 183.1274 | 460.5015 | 416.6862 | 383.8069 | 403.5465 | 358.8366
1472.0354 | 389.9227 | 183.364 | 461.5225 | 416.6279 | 383.1575 | 403.6892 | 358.8667
1473.0354 | 391.2299 | 183.7357 | 460.3186 | 416.4861 | 383.9412 | 404.5851 | 359.8738
1474.0354 | 391.8825 | 183.6399 | 459.9053 | 416.8162 | 385.5246 | 405.8107 | 360.548
1475.0354 | 393.1117 | 183.7068 | 460.1527 | 416.9362 | 384.7284 | 407.0538 | 361.2395
1476.0354 | 393.3076 | 183.8563 | 460.2285 | 417.4908 | 385.4403 | 407.6075 | 361.2232
1477.0354 | 393.9531 | 184.059 | 460.7774 | 417.8961 | 387.6443 | 407.7308 | 361.5144
1478.0354 | 393.9628 | 184.1043 | 460.0709 | 417.733 | 387.7891 | 408.1371 | 360.9596
1479.0354 | 393.4629 | 184.5149 | 460.476 | 417.612 | 388.2966 | 408.7733 | 361.532
1480.0354 | 394.4165 | 184.2626 | 461.1334 | 417.9353 | 387.3238 | 410.3246 | 361.5973
1481.0354 | 393.6214 | 184.4099 | 460.7525 | 417.7958 | 387.0104 | 410.3821 | 360.8236
1482.0354 | 393.3937 | 184.8132 | 460.6091 | 418.7124 | 387.0919 | 410.1906 | 360.0279
1483.0354 | 394.4257 | 184.8563 | 462.8332 | 418.3702 | 387.2733 | 409.3322 | 359.2375
1484.0354 | 393.7265 | 184.999 | 463.8835 | 418.3952 | 386.7966 | 408.9779 | 359.8723
1485.0354 | 395.2027 | 185.0333 | 463.7761 | 418.5648 | 386.574 | 408.4469 | 360.79
1486.0354 | 394.7548 | 185.27 | 462.6452 | 419.2085 | 385.6773 | 408.2943 | 361.6267
1487.0354 | 395.1166 | 185.2951 | 462.2493 | 419.1768 | 384.6686 | 408.0065 | 361.1534
1488.0354 | 394.4813 | 185.3686 | 462.2015 | 419.3765 | 384.75 | 408.3149 | 360.1039
1489.0354 | 391.819 | 185.4587 | 462.4052 | 419.4901 | 384.787 | 407.3599 | 359.326
1490.0354 | 391.6836 | 185.6452 | 463.7824 | 419.9415 | 384.8647 | 407.1672 | 359.7241
1491.0354 | 391.5484 | 185.6777 | 462.7735 | 419.741 | 384.8039 | 407.5881 | 359.7809
1492.0354 | 390.6376 | 185.8341 | 462.3172 | 420.1232 | 384.2865 | 408.2697 | 359.8865
1493.0354 | 390.955 | 186.025 | 462.3982 | 419.9377 | 384.5132 | 408.1375 | 359.1245
1494.0354 | 390.2928 | 186.1624 | 462.7861 | 420.3086 | 385.887 | 407.2901 | 358.0178
1495.0354 | 389.6027 | 186.3623 | 462.4766 | 420.7013 | 386.2255 | 406.8404 | 357.9099
1496.0354 | 388.9301 | 186.5684 | 462.3138 | 421.4298 | 385.9158 | 405.5287 | 357.816
1497.0354 | 387.9288 | 186.5441 | 462.6557 | 421.4007 | 385.6385 | 404.0428 | 357.1739
1498.0354 | 387.2836 | 186.5108 | 462.9168 | 421.9333 | 385.3703 | 403.3699 | 356.6517
1499.0354 | 387.2 | 186.7585 | 462.9256 | 422.6681 | 385.4826 | 404.3076 | 357.3816
1500.0354 | 385.5702 | 186.7605 | 464.0116 | 423.3729 | 385.1974 | 403.2022 | 357.8073
1501.0354 | 384.5318 | 186.9677 | 463.6601 | 422.4608 | 384.6402 | 403.014 | 356.411
1502.0354 | 383.6683 | 186.9603 | 463.9127 | 422.0996 | 384.6699 | 402.8769 | 356.202
1503.0354 | 383.6646 | 187.0309 | 463.766 | 422.6036 | 384.3888 | 402.4085 | 356.0664
1504.0354 | 382.8433 | 187.2412 | 463.9684 | 423.227 | 383.869 | 402.3121 | 356.2541
1505.0354 | 383.0877 | 187.3584 | 464.2691 | 423.4614 | 383.9888 | 402.1182 | 356.3105
1506.0354 | 383.6558 | 187.4548 | 464.3273 | 423.107 | 383.8714 | 402.5728 | 356.3166
1507.0354 | 382.5615 | 187.5211 | 464.9468 | 423.1522 | 383.6776 | 402.827 | 356.7933
1508.0354 | 381.9691 | 187.6032 | 464.2433 | 423.2831 | 383.5945 | 402.4478 | 356.8963
1509.0354 | 380.4341 | 187.7814 | 465.0142 | 423.3913 | 383.2703 | 401.6399 | 356.5476
1510.0354 | 380.9825 | 187.967 | 466.2045 | 423.65 | 382.9912 | 402.3928 | 357.1317
1511.0354 | 381.9714 | 188.0333 | 465.4052 | 423.8994 | 382.3812 | 402.1341 | 357.3995
1512.0354 | 382.7438 | 188.1692 | 464.9584 | 424.3704 | 382.1245 | 402.631 | 357.963
1513.0354 | 382.2524 | 188.4026 | 465.1972 | 424.5259 | 381.4936 | 401.7916 | 357.0635
1514.0354 | 382.5783 | 188.4894 | 465.5042 | 424.9241 | 381.2522 | 401.7416 | 357.4616
1515.0354 | 381.6843 | 188.479 | 464.8231 | 424.6521 | 381.2644 | 401.2857 | 357.364
1516.0354 | 381.0879 | 188.5632 | 464.6491 | 424.9168 | 381.1116 | 402.0517 | 356.4491
1517.0354 | 379.6383 | 188.6145 | 464.5746 | 424.9758 | 381.803 | 402.5409 | 356.732
1518.0354 | 378.4768 | 188.9024 | 464.2267 | 425.3293 | 381.3951 | 400.7985 | 355.6139
1519.0354 | 377.0906 | 189.165 | 464.1538 | 426.2223 | 380.7986 | 398.0863 | 353.5679
1520.0354 | 375.9179 | 189.2344 | 464.2804 | 425.8286 | 380.5573 | 396.2442 | 352.6085
1521.0354 | 375.0542 | 189.2835 | 465.5991 | 425.4941 | 380.8131 | 396.168 | 352.3384
1522.0354 | 373.6183 | 189.2944 | 465.1487 | 425.9097 | 380.8603 | 396.586 | 353.2906
1523.0354 | 372.336 | 189.3985 | 466.1889 | 425.8076 | 380.1256 | 396.3514 | 353.7096
1524.0354 | 372.4005 | 189.5029 | 465.987 | 425.8054 | 380.3779 | 396.4274 | 353.8216
1525.0354 | 371.164 | 189.572 | 465.2148 | 426.2419 | 380.8104 | 396.3012 | 354.3645
1526.0354 | 372.0187 | 189.9751 | 465.2379 | 426.4035 | 381.5797 | 396.1711 | 354.3149
1527.0354 | 373.0883 | 190.1196 | 465.8809 | 426.9526 | 381.0792 | 396.1589 | 353.5583
1528.0354 | 373.5749 | 190.1002 | 465.4615 | 426.9615 | 380.8299 | 396.7465 | 353.9676
1529.0354 | 374.1707 | 190.3612 | 465.1286 | 426.776 | 380.7746 | 396.87 | 353.2227
1530.0354 | 375.2474 | 190.5689 | 465.1868 | 426.6435 | 381.3608 | 398.0975 | 353.0845
1531.0354 | 375.8032 | 190.5015 | 465.4547 | 427.7476 | 381.3799 | 398.3097 | 353.5019
1532.0354 | 374.7558 | 190.6111 | 465.0335 | 429.0853 | 381.088 | 397.1498 | 353.5657
1533.0354 | 374.7255 | 190.6883 | 464.5883 | 428.1905 | 380.8283 | 396.9127 | 353.4084
1534.0354 | 374.172 | 190.846 | 465.0383 | 427.9519 | 380.7629 | 397.4673 | 352.8978
1535.0354 | 373.2078 | 190.9506 | 465.5788 | 427.8653 | 380.6427 | 396.741 | 352.6109
1536.0354 | 373.4041 | 191.1503 | 465.4972 | 427.7584 | 380.2315 | 397.1312 | 352.8505
1537.0354 | 373.8553 | 191.1888 | 465.8575 | 428.2624 | 380.1278 | 396.5828 | 353.3482
1538.0354 | 377.5455 | 191.314 | 466.5404 | 428.4954 | 379.6287 | 396.2473 | 353.4539
1539.0354 | 379.4241 | 191.562 | 466.7246 | 428.4093 | 379.2767 | 397.1654 | 354.6253
1540.0354 | 380.8416 | 191.6899 | 466.5588 | 428.3918 | 379.0866 | 396.7663 | 354.6194
1541.0354 | 382.1608 | 191.7161 | 466.7753 | 428.5663 | 379.0015 | 396.5489 | 355.7222
1542.0354 | 383.7761 | 191.8159 | 466.6231 | 429.1832 | 378.5009 | 396.9447 | 355.866
1543.0354 | 384.2037 | 191.9461 | 467.8226 | 429.7769 | 378.6944 | 397.0579 | 356.1013
1544.0354 | 384.8542 | 192.0169 | 468.5433 | 429.1389 | 378.799 | 398.145 | 355.4896
1545.0354 | 386.5968 | 192.1949 | 468.9709 | 429.0973 | 378.2977 | 398.9641 | 355.6727
1546.0354 | 388.3804 | 192.3152 | 467.437 | 429.0139 | 378.3871 | 398.9733 | 356.2519
1547.0354 | 389.6549 | 192.5344 | 469.3061 | 429.7157 | 378.0822 | 398.0985 | 355.5891
1548.0354 | 391.0409 | 192.4907 | 469.405 | 429.7043 | 378.9173 | 398.942 | 356.7022
1549.0354 | 392.5264 | 192.589 | 469.5735 | 429.8204 | 379.1187 | 398.4484 | 356.4304
1550.0354 | 393.0268 | 192.8045 | 469.0257 | 429.9793 | 379.8687 | 398.0505 | 355.6343
1551.0354 | 393.62 | 193.066 | 468.913 | 429.6774 | 380.8108 | 398.0403 | 356.0557
1552.0354 | 394.1712 | 193.0408 | 469.4882 | 430.3228 | 380.8947 | 399.014 | 357.4389
1553.0354 | 393.5944 | 193.0469 | 468.6609 | 429.9158 | 380.6548 | 398.8368 | 358.0714
1554.0354 | 392.4967 | 193.2067 | 468.3757 | 430.0843 | 380.1096 | 398.3717 | 357.3688
1555.0354 | 391.8402 | 193.2607 | 468.9588 | 430.4374 | 379.7196 | 397.1752 | 356.2752
1556.0354 | 392.5915 | 193.5476 | 469.7223 | 430.0989 | 379.7571 | 396.9264 | 356.1391
1557.0354 | 394.5451 | 193.6448 | 469.3887 | 430.0822 | 378.9629 | 397.8554 | 356.4888
1558.0354 | 396.5852 | 193.6675 | 469.3095 | 430.5137 | 378.7168 | 398.9387 | 356.7739
1559.0354 | 399.7556 | 193.7113 | 469.2844 | 430.0238 | 379.0013 | 400.7895 | 356.2198
1560.0354 | 398.6323 | 193.7124 | 470.2874 | 429.9902 | 378.9647 | 402.899 | 356.6966
1561.0354 | 400.2832 | 194.101 | 472.0032 | 430.3353 | 378.9691 | 403.617 | 357.4154
1562.0354 | 401.3384 | 194.239 | 471.9288 | 431.0616 | 378.6242 | 403.3096 | 357.6394
1563.0354 | 399.9776 | 194.3105 | 472.2181 | 431.0821 | 378.3253 | 402.7688 | 357.3882
1564.0354 | 402.0579 | 194.5701 | 471.9229 | 430.8901 | 377.7296 | 402.2358 | 356.7885
1565.0354 | 402.8942 | 194.7536 | 472.0941 | 430.8333 | 377.4672 | 401.8253 | 357.2618
1566.0354 | 402.9271 | 194.7814 | 471.5168 | 430.8269 | 377.2628 | 401.2114 | 357.7517
1567.0354 | 404.2074 | 194.7327 | 471.0205 | 431.3998 | 377.3435 | 402.656 | 358.3562
1568.0354 | 408.1116 | 194.9038 | 470.6024 | 431.0476 | 378.7556 | 403.0123 | 358.3567
1569.0354 | 413.2463 | 195.0753 | 470.6522 | 432.1777 | 381.1233 | 403.608 | 358.2864
1570.0354 | 430.5992 | 195.0683 | 471.3987 | 432.5596 | 381.6771 | 403.5542 | 357.3378
1571.0354 | 429.234 | 195.3055 | 471.3025 | 432.1651 | 382.4916 | 404.0994 | 356.809
1572.0354 | 427.5391 | 195.4937 | 470.9598 | 431.971 | 383.0843 | 404.2356 | 356.2335
1573.0354 | 431.0582 | 195.6382 | 470.7222 | 431.82 | 383.1246 | 403.6965 | 355.6776
1574.0354 | 434.3293 | 195.705 | 471.1451 | 432.702 | 383.5554 | 402.999 | 355.8553
1575.0354 | 432.6716 | 195.6899 | 472.0876 | 432.3342 | 384.5483 | 403.4462 | 355.6111
1576.0354 | 430.9108 | 195.7104 | 471.8693 | 431.9265 | 383.7846 | 403.0388 | 355.3623
1577.0354 | 431.1111 | 195.9302 | 471.3283 | 432.7731 | 382.9429 | 403.805 | 355.5314
1578.0354 | 429.0068 | 196.1708 | 472.6968 | 432.2321 | 383.4251 | 403.1331 | 354.6661
1579.0354 | 428.8853 | 196.4466 | 472.0351 | 432.0835 | 383.0462 | 403.1117 | 354.6287
1580.0354 | 428.0983 | 196.6257 | 471.9593 | 432.5669 | 381.8732 | 403.3634 | 355.2749
1581.0354 | 429.4499 | 196.6658 | 473.4054 | 432.8444 | 380.8045 | 403.7677 | 355.2819
1582.0354 | 428.6227 | 196.7067 | 473.7126 | 432.8177 | 380.5946 | 403.5081 | 356.4544
1583.0354 | 427.2262 | 196.8277 | 473.9408 | 433.0967 | 381.0531 | 403.1316 | 356.1852
1584.0354 | 426.2354 | 196.8519 | 473.4563 | 433.2635 | 381.0955 | 403.206 | 357.0449
1585.0354 | 425.8728 | 196.9984 | 472.4755 | 432.9273 | 380.7295 | 403.9669 | 356.7723
1586.0354 | 424.1334 | 197.2072 | 472.9184 | 433.3082 | 380.6759 | 405.4539 | 356.4937
1587.0354 | 422.051 | 197.3014 | 472.7788 | 433.5139 | 381.3573 | 406.9305 | 356.4879
1588.0354 | 425.1421 | 197.2778 | 473.3259 | 434.0648 | 382.3568 | 407.1515 | 355.7862
1589.0354 | 425.8129 | 197.3113 | 472.6431 | 434.2576 | 383.7541 | 407.7541 | 356.3039
1590.0354 | 430.8704 | 197.4267 | 474.3802 | 434.2688 | 383.7084 | 407.8674 | 357.2939
1591.0354 | 437.3549 | 197.6081 | 474.5729 | 435.1472 | 383.7807 | 408.5341 | 358.023
1592.0354 | 440.3099 | 197.7895 | 473.6721 | 434.3057 | 383.6296 | 408.6663 | 358.1552
1593.0354 | 443.8078 | 197.8775 | 474.1176 | 434.817 | 384.6325 | 409.0238 | 357.816
1594.0354 | 445.3626 | 198.1866 | 475.3912 | 434.831 | 383.9168 | 409.3775 | 357.5971
1595.0354 | 446.249 | 198.0948 | 474.6483 | 434.6739 | 383.4822 | 408.6338 | 357.4104
1596.0354 | 445.0682 | 198.1903 | 476.0315 | 434.8278 | 384.3193 | 408.9615 | 357.6614
1597.0354 | 451.9275 | 198.3208 | 475.9447 | 434.9365 | 384.5259 | 409.2342 | 358.9248
1598.0354 | 454.6982 | 198.6011 | 476.1154 | 435.0299 | 384.716 | 409.6714 | 360.2728
1599.0354 | 455.6984 | 198.5744 | 475.1235 | 435.23 | 385.1589 | 410.2904 | 361.5
1600.0354 | 459.2832 | 198.8214 | 475.5517 | 435.538 | 385.9315 | 412.4974 | 362.3818
1601.0354 | 461.9859 | 199.047 | 476.4193 | 435.4428 | 386.419 | 412.7104 | 363.1576
1602.0354 | 466.5995 | 198.9648 | 476.1915 | 435.5051 | 385.7032 | 411.9477 | 362.3413
1603.0354 | 469.8208 | 199.166 | 476.5336 | 435.4095 | 385.4318 | 412.5142 | 362.9216
1604.0354 | 468.599 | 199.37 | 477.6267 | 435.7449 | 385.3218 | 413.4084 | 364.1553
1605.0354 | 467.2814 | 199.4231 | 477.5449 | 435.6699 | 385.8835 | 414.1571 | 365.1189
1606.0354 | 465.1639 | 199.5749 | 477.381 | 435.5804 | 385.705 | 414.2966 | 365.4317
1607.0354 | 463.0874 | 199.6742 | 477.114 | 435.377 | 385.4273 | 415.0557 | 365.5896
1608.0354 | 468.7999 | 199.8598 | 476.9732 | 435.8727 | 385.4684 | 415.884 | 365.2788
1609.0354 | 467.9719 | 199.8974 | 476.5775 | 436.3052 | 385.4292 | 416.6004 | 363.9272
1610.0354 | 480.0058 | 199.8585 | 477.5762 | 437.5439 | 386.3037 | 416.9766 | 363.7895
1611.0354 | 480.4838 | 200.0144 | 477.0779 | 437.2899 | 386.9314 | 417.2787 | 364.1291
1612.0354 | 489.0835 | 200.1622 | 476.8414 | 437.3962 | 387.7514 | 417.5769 | 365.524
1613.0354 | 502.371 | 200.4114 | 476.5562 | 436.5436 | 388.1394 | 417.9205 | 366.6003
1614.0354 | 508.7026 | 200.5305 | 476.9511 | 436.7139 | 388.0235 | 419.0549 | 367.2998
1615.0354 | 508.0934 | 200.6596 | 476.9077 | 437.2552 | 387.8993 | 419.4565 | 367.1578
1616.0354 | 508.0675 | 200.6962 | 477.0364 | 438.0969 | 388.0267 | 418.828 | 366.912
1617.0354 | 510.9483 | 200.8605 | 476.7221 | 438.068 | 389.0152 | 417.9842 | 366.985
1618.0354 | 522.0472 | 201.0168 | 476.7391 | 437.2205 | 389.0242 | 418.3354 | 366.6963
1619.0354 | 518.9699 | 201.2968 | 477.8432 | 437.2163 | 389.5606 | 417.8193 | 366.5511
1620.0354 | 515.1837 | 201.2318 | 477.6195 | 437.151 | 389.1179 | 418.7426 | 367.2742
1621.0354 | 518.8771 | 201.3094 | 477.7343 | 437.6504 | 388.5163 | 420.9391 | 367.076
1622.0354 | 512.0546 | 201.4217 | 478.0223 | 437.3573 | 388.4346 | 422.1015 | 368.0195
1623.0354 | 510.7344 | 201.4289 | 477.4591 | 437.7204 | 388.2799 | 421.1771 | 367.9856
1624.0354 | 524.9142 | 201.569 | 478.0892 | 437.6352 | 388.0701 | 421.2861 | 367.6109
1625.0354 | 525.724 | 201.6859 | 478.4946 | 437.6096 | 387.7426 | 422.0259 | 368.0223
1626.0354 | 531.0708 | 201.896 | 478.3763 | 437.9254 | 386.3132 | 422.1606 | 367.4256
1627.0354 | 526.0601 | 201.9275 | 479.5501 | 438.3357 | 385.6869 | 422.521 | 367.7613
1628.0354 | 526.997 | 202.0329 | 479.3006 | 438.3263 | 385.8904 | 423.4283 | 368.1802
1629.0354 | 530.304 | 202.1384 | 479.5523 | 438.1909 | 385.7151 | 424.2629 | 368.2216
1630.0354 | 527.4886 | 202.2211 | 479.272 | 438.6196 | 386.5168 | 424.2197 | 368.6151
1631.0354 | 520.2234 | 202.2514 | 479.2978 | 438.6994 | 386.6528 | 424.6946 | 368.7969
1632.0354 | 521.3597 | 202.4386 | 479.6812 | 438.7728 | 387.5574 | 423.9582 | 367.9981
1633.0354 | 516.7683 | 202.6279 | 479.5644 | 438.9606 | 387.7798 | 423.402 | 368.5179
1634.0354 | 529.7409 | 202.7266 | 478.2989 | 439.0453 | 387.5023 | 423.7322 | 368.9132
1635.0354 | 539.9238 | 202.8047 | 478.2477 | 439.6243 | 387.5663 | 424.63 | 368.569
1636.0354 | 553.0269 | 202.8386 | 479.2658 | 439.2773 | 388.5427 | 423.5046 | 368.5741
1637.0354 | 560.5819 | 203.0357 | 479.8397 | 439.6995 | 388.7899 | 423.2112 | 368.1178
1638.0354 | 572.2828 | 203.1258 | 479.5107 | 439.1097 | 388.4667 | 422.1947 | 367.8551
1639.0354 | 563.6667 | 203.2538 | 480.4038 | 438.9569 | 387.6027 | 425.0933 | 369.1103
1640.0354 | 567.7036 | 203.6011 | 481.0277 | 438.9067 | 387.0407 | 426.5719 | 370.3435
1641.0354 | 565.3226 | 203.7063 | 480.489 | 439.4753 | 387.2463 | 426.9427 | 371.7105
1642.0354 | 558.3574 | 203.6746 | 479.8456 | 439.2784 | 387.046 | 426.9385 | 371.5085
1643.0354 | 549.206 | 203.7107 | 479.7887 | 439.3956 | 386.7706 | 427.7613 | 370.7697
1644.0354 | 552.682 | 203.9354 | 481.1291 | 439.274 | 387.3245 | 428.4662 | 369.5482
1645.0354 | 549.0742 | 204.0828 | 480.6084 | 439.6297 | 387.6078 | 428.3918 | 369.9556
1646.0354 | 539.6568 | 204.1255 | 480.197 | 439.5498 | 387.6115 | 429.9145 | 370.0905
1647.0354 | 534.9927 | 204.274 | 480.6364 | 439.7252 | 387.3744 | 428.9388 | 369.8999
1648.0354 | 529.9089 | 204.3957 | 480.4766 | 439.6831 | 387.4017 | 427.9405 | 369.3065
1649.0354 | 545.1674 | 204.5248 | 481.5767 | 439.5253 | 387.0576 | 428.8456 | 369.2131
1650.0354 | 537.0067 | 204.5831 | 481.4628 | 439.7049 | 386.9035 | 429.6422 | 369.1945
1651.0354 | 547.9874 | 204.7258 | 482.1027 | 440.4045 | 386.3322 | 430.1843 | 369.1401
1652.0354 | 563.064 | 204.833 | 482.7741 | 440.0515 | 385.6514 | 429.9039 | 370.0421
1653.0354 | 574.6912 | 205.1175 | 483.9187 | 439.8288 | 385.1017 | 429.6092 | 369.9119
1654.0354 | 565.0313 | 205.2944 | 483.958 | 439.7407 | 384.2544 | 428.3557 | 370.2793
1655.0354 | 557.3572 | 205.4442 | 483.4765 | 439.7449 | 384.3647 | 428.8654 | 372.1107
1656.0354 | 548.1546 | 205.4896 | 483.2819 | 439.9262 | 383.9887 | 427.9249 | 371.8655
1657.0354 | 538.8977 | 205.46 | 483.2547 | 440.5275 | 383.5884 | 426.8786 | 371.6701
1658.0354 | 534.41 | 205.4592 | 483.1129 | 440.4839 | 383.2895 | 426.1503 | 371.3655
1659.0354 | 536.4825 | 205.6078 | 483.0801 | 440.6187 | 383.8957 | 426.0557 | 371.7358
1660.0354 | 548.8364 | 205.757 | 482.9014 | 440.2489 | 384.4334 | 426.0577 | 371.6438
1661.0354 | 540.7094 | 205.9409 | 483.3739 | 439.9541 | 385.0967 | 426.2153 | 371.0572
1662.0354 | 550.9336 | 206.1167 | 483.5346 | 440.0296 | 384.5322 | 425.9888 | 371.5769
1663.0354 | 566.6676 | 206.4036 | 483.2158 | 440.6994 | 384.0673 | 426.073 | 370.9479
1664.0354 | 551.6858 | 206.3471 | 483.5955 | 440.6977 | 383.7307 | 425.167 | 370.2724
1665.0354 | 543.9062 | 206.3835 | 483.0209 | 440.7848 | 383.8373 | 423.5214 | 369.4658
1666.0354 | 536.7948 | 206.3939 | 482.6428 | 440.632 | 384.1362 | 422.0472 | 368.6701
1667.0354 | 524.6441 | 206.458 | 483.5661 | 441.3148 | 384.6387 | 420.1468 | 367.1561
1668.0354 | 516.2489 | 206.5904 | 483.9217 | 440.6338 | 385.3325 | 419.2832 | 366.0854
1669.0354 | 508.1324 | 206.8775 | 484.1062 | 441.0585 | 386.055 | 420.3759 | 367.4586
1670.0354 | 501.2426 | 206.9038 | 484.8157 | 440.6773 | 386.9833 | 420.1327 | 368.0001
1671.0354 | 516.949 | 206.9713 | 484.3458 | 440.634 | 386.3376 | 419.9174 | 367.7727
1672.0354 | 503.8883 | 207.2602 | 484.2568 | 440.9377 | 387.0971 | 420.4546 | 367.6652
1673.0354 | 494.2412 | 207.4523 | 485.6339 | 440.7183 | 387.1781 | 420.0842 | 368.393
1674.0354 | 491.351 | 207.4233 | 485.293 | 441.02 | 387.2782 | 420.235 | 368.616
1675.0354 | 485.1318 | 207.5393 | 485.1563 | 440.7369 | 387.0979 | 419.435 | 369.3968
1676.0354 | 479.5551 | 207.5888 | 484.8359 | 441.1969 | 387.2491 | 418.884 | 369.5452
1677.0354 | 477.7569 | 207.6378 | 484.8098 | 441.491 | 386.9163 | 417.6247 | 369.4335
1678.0354 | 471.2333 | 207.8663 | 484.2427 | 441.3108 | 387.5439 | 418.8611 | 370.2047
1679.0354 | 467.6854 | 207.9683 | 484.6592 | 441.3518 | 387.1339 | 418.9007 | 369.3112
1680.0354 | 463.6564 | 207.9591 | 484.9359 | 441.5018 | 387.8248 | 419.4495 | 370.1489
1681.0354 | 464.8862 | 207.9139 | 484.2553 | 440.8912 | 387.8583 | 419.641 | 369.4502
1682.0354 | 461.8957 | 207.9968 | 484.2863 | 441.1387 | 387.7173 | 421.1641 | 369.0764
1683.0354 | 461.4322 | 208.1606 | 485.2491 | 441.9086 | 387.5505 | 420.4439 | 368.1799
1684.0354 | 467.1442 | 208.2737 | 484.4927 | 441.8929 | 387.9409 | 421.6268 | 368.7291
1685.0354 | 469.6454 | 208.3991 | 484.468 | 442.5043 | 387.9622 | 422.5936 | 368.6242
1686.0354 | 466.339 | 208.4311 | 484.1803 | 442.3926 | 387.9678 | 420.8725 | 367.9576
1687.0354 | 460.8478 | 208.5299 | 484.3194 | 442.1568 | 388.0723 | 419.8936 | 367.3761
1688.0354 | 456.8434 | 208.6594 | 485.0386 | 441.8976 | 387.8839 | 418.7764 | 367.4018
1689.0354 | 453.9541 | 208.7738 | 485.4174 | 442.0114 | 387.8089 | 417.5219 | 367.3781
1690.0354 | 450.57 | 208.9164 | 484.4573 | 442.3013 | 388.1692 | 417.4703 | 368.1137
1691.0354 | 449.3403 | 208.9801 | 484.6966 | 442.5661 | 387.5462 | 415.8507 | 368.0598
1692.0354 | 445.5716 | 208.9974 | 484.4085 | 442.5151 | 386.9192 | 415.0784 | 367.8873
1693.0354 | 441.5004 | 209.0361 | 484.1081 | 442.5669 | 387.1446 | 415.9192 | 366.4717
1694.0354 | 441.8191 | 209.2755 | 484.7609 | 442.802 | 386.5031 | 414.053 | 365.2855
1695.0354 | 439.6239 | 209.4882 | 485.6078 | 443.1187 | 386.6846 | 414.0277 | 365.7136
1696.0354 | 437.4924 | 209.4526 | 484.8262 | 443.1993 | 386.9116 | 413.3941 | 365.2976
1697.0354 | 435.2441 | 209.4751 | 485.995 | 442.7817 | 387.2311 | 412.5932 | 365.2505
1698.0354 | 433.4981 | 209.7083 | 486.0665 | 443.0059 | 387.712 | 412.1858 | 365.2539
1699.0354 | 431.7926 | 209.8652 | 485.2597 | 443.2597 | 387.2481 | 412.5299 | 365.7756
1700.0354 | 431.3392 | 209.8776 | 485.3283 | 443.1923 | 386.9288 | 412.4343 | 365.6197
1701.0354 | 430.2625 | 210.0863 | 486.54 | 443.2629 | 386.8606 | 412.1553 | 365.1452
1702.0354 | 429.1493 | 210.238 | 486.5528 | 443.1559 | 386.1828 | 411.6968 | 365.2158
1703.0354 | 429.7317 | 210.3748 | 486.2033 | 443.3596 | 385.8102 | 412.1653 | 365.3843
1704.0354 | 429.169 | 210.3875 | 486.7784 | 443.5213 | 386.0799 | 413.0097 | 366.1951
1705.0354 | 428.2503 | 210.4674 | 486.1449 | 444.0978 | 386.4149 | 412.2473 | 366.3959
1706.0354 | 427.2559 | 210.5502 | 486.8354 | 443.6888 | 386.4026 | 413.3268 | 366.9488
1707.0354 | 426.3021 | 210.7066 | 487.5618 | 443.6737 | 386.288 | 413.043 | 366.981
1708.0354 | 425.8869 | 210.7332 | 486.7184 | 443.5148 | 386.2137 | 413.2231 | 367.5102
1709.0354 | 426.4847 | 210.8318 | 487.3895 | 444.1883 | 385.9521 | 413.5591 | 366.9195
1710.0354 | 425.6222 | 211.014 | 486.4451 | 444.4527 | 385.596 | 412.8452 | 367.0607
1711.0354 | 426.7717 | 211.1445 | 489.0979 | 444.1211 | 385.6159 | 412.1473 | 367.3263
1712.0354 | 428.5864 | 211.4024 | 488.8421 | 444.0784 | 385.9394 | 413.5539 | 368.2765
1713.0354 | 428.084 | 211.5473 | 488.374 | 444.36 | 385.7079 | 413.3489 | 368.3141
1714.0354 | 428.4258 | 211.5833 | 488.7308 | 444.5978 | 385.4931 | 412.2469 | 367.4203
1715.0354 | 430.4723 | 211.6469 | 488.1521 | 446.1669 | 386.425 | 412.0993 | 367.508
1716.0354 | 433.2402 | 211.8459 | 488.1926 | 445.157 | 387.1573 | 412.0361 | 366.9349
1717.0354 | 433.4728 | 211.8601 | 488.4587 | 445.1449 | 387.3358 | 412.1068 | 366.3908
1718.0354 | 431.0378 | 211.8251 | 488.7691 | 446.0452 | 388.4465 | 413.4037 | 367.5326
1719.0354 | 431.282 | 211.9953 | 488.3563 | 446.1181 | 388.9782 | 413.3011 | 368.3263
1720.0354 | 434.2779 | 212.1483 | 488.6619 | 445.6914 | 389.0527 | 412.6678 | 367.5074
1721.0354 | 436.3991 | 212.2643 | 489.5305 | 445.8111 | 389.2181 | 413.3365 | 367.4267
1722.0354 | 436.4326 | 212.5237 | 490.1799 | 446.6711 | 389.2326 | 414.9661 | 368.3547
1723.0354 | 435.6274 | 212.7829 | 490.6957 | 446.6868 | 389.6584 | 416.3326 | 368.9783
1724.0354 | 438.9846 | 212.7886 | 491.105 | 446.7976 | 390.0116 | 416.7092 | 368.2837
1725.0354 | 441.9178 | 212.8919 | 490.673 | 446.5175 | 390.0275 | 417.9535 | 368.4236
1726.0354 | 440.791 | 212.9567 | 490.8703 | 446.5599 | 390.3521 | 417.5048 | 368.8507
1727.0354 | 440.0795 | 213.0656 | 490.6057 | 446.6978 | 390.2566 | 417.4011 | 368.7924
1728.0354 | 439.979 | 213.2148 | 490.9659 | 446.582 | 390.0997 | 417.5045 | 369.1058
1729.0354 | 439.254 | 213.2849 | 490.9341 | 446.974 | 390.285 | 418.5451 | 369.0341
1730.0354 | 441.5676 | 213.4609 | 492.6012 | 447.3839 | 390.7272 | 418.9763 | 369.552
1731.0354 | 441.6273 | 213.7483 | 492.3015 | 447.2776 | 391.672 | 419.3357 | 370.3044
1732.0354 | 442.6043 | 213.7275 | 491.8467 | 447.6163 | 392.1091 | 419.4098 | 370.6763
1733.0354 | 448.0883 | 213.8273 | 492.018 | 447.2226 | 392.3669 | 419.8399 | 370.8691
1734.0354 | 449.6653 | 213.9142 | 491.5972 | 447.4699 | 392.4145 | 420.7419 | 371.3928
1735.0354 | 454.3409 | 213.99 | 491.9153 | 447.3625 | 393.0631 | 421.4499 | 371.6741
1736.0354 | 458.4557 | 214.1798 | 492.5392 | 447.3109 | 394.0545 | 423.6071 | 372.5882
1737.0354 | 461.894 | 214.2118 | 493.2202 | 447.6123 | 394.2604 | 425.9275 | 373.8809
1738.0354 | 461.9279 | 214.3192 | 492.3628 | 447.4438 | 394.3865 | 427.5152 | 374.8807
1739.0354 | 482.1864 | 214.3592 | 492.1987 | 447.3147 | 394.5494 | 430.9946 | 376.6123
1740.0354 | 484.511 | 214.6006 | 493.433 | 448.2817 | 394.7947 | 434.5619 | 378.2684
1741.0354 | 484.1324 | 214.7927 | 493.9449 | 449.0428 | 395.0213 | 434.6233 | 378.5758
1742.0354 | 487.7948 | 214.9028 | 493.3635 | 448.9642 | 395.5751 | 435.1325 | 378.0227
1743.0354 | 493.8125 | 215.1428 | 493.2931 | 448.5846 | 396.1196 | 434.6072 | 377.6058
1744.0354 | 490.806 | 215.2305 | 492.8791 | 448.7947 | 396.2189 | 433.774 | 377.4802
1745.0354 | 490.433 | 215.17 | 492.8176 | 448.098 | 396.6824 | 434.6393 | 377.7195
1746.0354 | 488.2533 | 215.4072 | 494.0571 | 448.1857 | 397.9041 | 435.4449 | 377.5935
1747.0354 | 483.9546 | 215.5565 | 493.8799 | 448.6267 | 398.0266 | 436.5056 | 377.4503
1748.0354 | 481.7021 | 215.6271 | 494.4625 | 449.6686 | 398.5306 | 436.1313 | 377.5388
1749.0354 | 478.7751 | 215.7053 | 495.0957 | 449.8345 | 399.0689 | 436.1038 | 377.9449
1750.0354 | 478.8038 | 215.8763 | 495.2022 | 449.9466 | 399.8567 | 434.9028 | 377.6939
1751.0354 | 478.283 | 216.09 | 495.4588 | 449.831 | 399.9803 | 434.6396 | 377.4351
1752.0354 | 476.1076 | 216.2034 | 495.8469 | 449.7276 | 400.0338 | 432.9853 | 377.7871
1753.0354 | 475.1711 | 216.274 | 495.74 | 450.1198 | 399.8942 | 431.0523 | 377.5103
1754.0354 | 479.9208 | 216.4677 | 495.9879 | 450.8225 | 400.2984 | 430.638 | 376.9111
1755.0354 | 485.0756 | 216.6768 | 496.2958 | 450.6646 | 400.469 | 430.8461 | 375.798
1756.0354 | 491.1818 | 217.0066 | 498.7771 | 450.5456 | 400.6987 | 430.1781 | 375.1976
1757.0354 | 490.0043 | 217.1326 | 497.3772 | 449.9756 | 400.1415 | 427.5925 | 373.8424
1758.0354 | 486.5561 | 216.9953 | 496.8553 | 450.2462 | 399.9836 | 427.6154 | 374.5764
1759.0354 | 485.4135 | 217.0956 | 496.194 | 450.5485 | 399.8478 | 428.8986 | 374.4974
1760.0354 | 484.7779 | 217.1683 | 496.0237 | 450.8038 | 400.1502 | 432.1617 | 376.0541
1761.0354 | 482.1438 | 217.2377 | 496.7235 | 450.7403 | 400.1948 | 432.8532 | 376.1059
1762.0354 | 480.7353 | 217.4701 | 496.7979 | 450.9482 | 399.9092 | 432.0238 | 376.3131
1763.0354 | 478.6558 | 217.5684 | 496.6432 | 450.5925 | 400.3885 | 433.0817 | 376.9422
1764.0354 | 477.9692 | 217.6134 | 496.2932 | 451.0016 | 401.3582 | 434.2026 | 377.0743
1765.0354 | 477.7513 | 217.7601 | 496.4896 | 451.2017 | 402.1386 | 434.0966 | 377.0348
1766.0354 | 478.0433 | 217.7851 | 496.5482 | 451.4677 | 402.6634 | 433.1662 | 376.3357
1767.0354 | 475.7091 | 217.8817 | 496.7243 | 451.4531 | 403.4629 | 433.9278 | 376.5577
1768.0354 | 472.1607 | 218.0235 | 496.7053 | 451.3332 | 403.8244 | 433.023 | 376.4798
1769.0354 | 472.7962 | 218.2034 | 496.4471 | 451.4948 | 403.0703 | 430.3364 | 375.1154
1770.0354 | 473.799 | 218.3493 | 498.6276 | 452.2231 | 402.6819 | 430.1923 | 375.0439
1771.0354 | 475.3933 | 218.5649 | 500.2259 | 452.2452 | 403.0299 | 431.5018 | 375.6034
1772.0354 | 474.9033 | 218.5964 | 498.0345 | 451.5619 | 403.8622 | 431.9407 | 375.5317
1773.0354 | 473.5248 | 218.9214 | 500.0131 | 452.2614 | 403.3947 | 431.4568 | 375.4656
1774.0354 | 473.9558 | 219.195 | 499.3595 | 452.2821 | 402.8685 | 431.838 | 376.5365
1775.0354 | 472.1028 | 219.1577 | 498.8454 | 452.6545 | 402.5059 | 430.5226 | 376.6274
1776.0354 | 475.23 | 219.2102 | 498.8756 | 452.2819 | 402.7354 | 430.9604 | 376.9871
1777.0354 | 476.6213 | 219.2289 | 498.3093 | 452.2015 | 403.4738 | 433.7046 | 377.4032
1778.0354 | 486.1237 | 219.2702 | 499.6655 | 452.6487 | 404.1622 | 438.1999 | 379.4326
1779.0354 | 484.9967 | 219.6212 | 500.8186 | 452.8453 | 404.9958 | 438.9913 | 380.5664
1780.0354 | 483.8824 | 219.8031 | 502.0376 | 452.9653 | 405.3301 | 439.6336 | 381.9206
1781.0354 | 484.0463 | 220.1278 | 502.8275 | 453.0072 | 405.1007 | 439.426 | 383.1338
1782.0354 | 484.7073 | 220.3029 | 502.4362 | 453.303 | 404.4132 | 438.8124 | 383.7925
1783.0354 | 485.0044 | 220.3623 | 501.9133 | 454.0633 | 404.6772 | 440.0794 | 384.7218
1784.0354 | 486.6838 | 220.4403 | 502.0172 | 454.076 | 405.1658 | 440.1773 | 385.4315
1785.0354 | 487.8845 | 220.4318 | 502.2322 | 453.829 | 405.4772 | 439.7372 | 385.2881
1786.0354 | 490.737 | 220.7711 | 501.4427 | 454.0272 | 405.8242 | 441.0146 | 386.0052
1787.0354 | 493.1776 | 220.7206 | 501.0488 | 453.399 | 406.5346 | 442.2098 | 386.192
1788.0354 | 503.8034 | 220.7556 | 501.009 | 453.0643 | 407.7513 | 450.2046 | 389.0177
1789.0354 | 506.9906 | 220.8712 | 501.0322 | 453.5261 | 409.0286 | 454.7626 | 390.5601
1790.0354 | 507.6785 | 220.9683 | 501.6053 | 453.9888 | 410.1369 | 458.0665 | 390.0609
1791.0354 | 506.3531 | 221.0568 | 501.0704 | 454.652 | 410.8195 | 459.6484 | 390.0892
1792.0354 | 506.5495 | 221.2225 | 501.0361 | 455.0697 | 411.6609 | 459.9942 | 389.8405
1793.0354 | 510.5271 | 221.4488 | 501.3577 | 455.1128 | 412.5927 | 460.1856 | 390.8
1794.0354 | 510.991 | 221.7019 | 503.1846 | 455.2458 | 413.2208 | 457.9058 | 390.6125
1795.0354 | 508.3141 | 221.782 | 503.3426 | 455.6844 | 413.7324 | 456.5068 | 390.1739
1796.0354 | 503.7828 | 221.9023 | 502.877 | 455.819 | 413.7818 | 454.4706 | 390.0011
1797.0354 | 500.8893 | 222.1063 | 504.1759 | 455.5134 | 413.696 | 452.6305 | 389.4317
1798.0354 | 499.8666 | 222.3279 | 503.5038 | 455.1841 | 413.3865 | 452.0828 | 389.6559
1799.0354 | 497.8249 | 222.4248 | 503.5607 | 455.3024 | 413.2814 | 451.9828 | 390.1547
1800.0354 | 495.3641 | 222.4536 | 502.8762 | 456.1487 | 412.7229 | 450.7219 | 389.9337
1801.0354 | 506.7067 | 222.7122 | 503.6422 | 456.2162 | 412.5572 | 449.2214 | 389.9115
1802.0354 | 506.5876 | 222.6783 | 504.1945 | 456.7381 | 412.6871 | 448.3161 | 390.0247
1803.0354 | 506.4661 | 222.9532 | 504.7398 | 456.5714 | 412.4063 | 446.9391 | 388.665
1804.0354 | 504.3068 | 223.1276 | 504.6761 | 456.3347 | 412.3815 | 445.9721 | 388.1331
1805.0354 | 508.1026 | 223.3013 | 505.1126 | 456.6762 | 412.1979 | 445.6 | 388.9592
1806.0354 | 507.1704 | 223.3886 | 506.8083 | 456.7863 | 412.4744 | 446.6796 | 390.3258
1807.0354 | 507.2531 | 223.5388 | 507.2604 | 457.0119 | 412.2755 | 445.9777 | 390.0616
1808.0354 | 506.6023 | 223.7931 | 507.147 | 457.0727 | 412.0465 | 445.1469 | 389.6969
1809.0354 | 508.7172 | 224.0928 | 507.9123 | 457.1269 | 411.3563 | 444.6738 | 389.7859
1810.0354 | 507.9027 | 224.3078 | 508.9584 | 458.3372 | 410.6279 | 444.4947 | 390.9198
1811.0354 | 507.9209 | 224.4718 | 511.2588 | 457.9258 | 410.156 | 444.9596 | 392.5053
1812.0354 | 507.9729 | 224.5203 | 511.1084 | 457.8169 | 409.6839 | 444.6542 | 391.9259
1813.0354 | 506.8464 | 224.6522 | 509.1689 | 458.2051 | 409.5646 | 443.4163 | 391.3146
1814.0354 | 503.7484 | 224.8519 | 508.2618 | 458.7184 | 409.2987 | 442.943 | 390.6125
1815.0354 | 506.8148 | 224.9027 | 507.9383 | 458.3854 | 409.368 | 442.4451 | 389.5684
1816.0354 | 510.4162 | 224.9802 | 508.801 | 457.9636 | 410.2945 | 445.538 | 390.3922
1817.0354 | 508.8133 | 225.0336 | 509.0857 | 457.8925 | 411.245 | 448.2041 | 390.982
1818.0354 | 509.1458 | 225.1123 | 508.5388 | 458.001 | 412.0402 | 452.1489 | 392.3517
1819.0354 | 510.9411 | 225.1188 | 508.2705 | 458.7347 | 413.1654 | 456.7286 | 392.8451
1820.0354 | 508.7202 | 225.4892 | 508.2838 | 458.5217 | 414.66 | 458.7535 | 392.8579
1821.0354 | 507.6422 | 225.677 | 508.2871 | 458.8758 | 416.2138 | 458.9848 | 393.0931
1822.0354 | 507.9628 | 225.7075 | 508.2299 | 459.3787 | 417.3009 | 458.0741 | 392.1592
1823.0354 | 504.1092 | 225.7927 | 508.1625 | 459.318 | 418.827 | 457.8604 | 392.4614
1824.0354 | 503.5594 | 226.1255 | 509.0246 | 458.5209 | 419.2568 | 457.0267 | 391.9063
1825.0354 | 502.0285 | 226.1178 | 509.2834 | 458.9276 | 419.7548 | 457.9447 | 392.0979
1826.0354 | 502.9699 | 226.2581 | 509.1563 | 459.3882 | 419.3253 | 456.7704 | 391.9959
1827.0354 | 515.5624 | 226.4152 | 510.0255 | 459.5269 | 420.467 | 459.6104 | 392.8788
1828.0354 | 524.7264 | 226.5081 | 510.1296 | 459.6494 | 420.8143 | 460.8485 | 395.0869
1829.0354 | 523.8464 | 226.718 | 511.0095 | 459.6385 | 420.913 | 461.391 | 396.059
1830.0354 | 522.5674 | 226.8982 | 512.3423 | 459.8991 | 421.1592 | 460.8591 | 396.8452
1831.0354 | 521.096 | 227.1313 | 511.5205 | 460.0117 | 420.7669 | 460.731 | 397.1683
1832.0354 | 516.2743 | 227.0627 | 510.2225 | 459.9918 | 420.9805 | 460.5308 | 397.7321
1833.0354 | 516.7508 | 227.2345 | 511.2474 | 460.1802 | 420.6751 | 459.654 | 397.6991
1834.0354 | 513.7692 | 227.3873 | 511.3153 | 460.6555 | 420.621 | 459.0539 | 397.8358
1835.0354 | 509.6216 | 227.6282 | 510.7765 | 460.6388 | 420.0914 | 458.4241 | 398.2654
1836.0354 | 505.5992 | 227.6175 | 510.4165 | 461.1389 | 419.7385 | 456.8419 | 397.7103
1837.0354 | 503.7699 | 227.7178 | 511.3551 | 461.7011 | 420.0682 | 455.9011 | 397.007
1838.0354 | 502.2668 | 228.022 | 513.1624 | 461.0702 | 419.9235 | 456.0704 | 397.6563
1839.0354 | 500.249 | 228.1759 | 512.5121 | 461.843 | 420.2303 | 456.1062 | 398.1239
1840.0354 | 498.7788 | 228.2962 | 510.9949 | 461.3444 | 420.6088 | 457.3253 | 397.4628
1841.0354 | 495.4087 | 228.376 | 511.2775 | 460.9553 | 420.9082 | 458.7593 | 397.9287
1842.0354 | 494.4152 | 228.5846 | 510.6271 | 461.6532 | 420.9331 | 457.8659 | 396.759
1843.0354 | 492.8815 | 228.859 | 511.9109 | 461.5054 | 420.7838 | 456.4703 | 395.6407
1844.0354 | 490.0485 | 228.7918 | 511.0929 | 461.2334 | 420.3046 | 457.493 | 395.5957
1845.0354 | 485.1165 | 228.7255 | 510.7983 | 461.3908 | 420.1709 | 456.7476 | 395.4265
1846.0354 | 481.2686 | 228.8394 | 510.9018 | 461.4814 | 419.5383 | 454.671 | 393.8302
1847.0354 | 478.4632 | 228.8203 | 510.8052 | 461.4242 | 419.2271 | 452.7193 | 392.5538
1848.0354 | 484.613 | 229.0579 | 511.0922 | 461.8763 | 419.5463 | 452.3937 | 392.1729
1849.0354 | 481.8455 | 229.0896 | 510.8241 | 461.9156 | 420.7189 | 451.6774 | 392.1793
1850.0354 | 480.428 | 229.3465 | 510.7791 | 462.2209 | 420.8142 | 451.1647 | 391.5995
1851.0354 | 478.2768 | 229.4193 | 511.3119 | 462.003 | 420.7203 | 452.1271 | 390.8904
1852.0354 | 474.2036 | 229.4978 | 510.9501 | 461.5997 | 420.6329 | 452.3225 | 391.2709
1853.0354 | 472.3524 | 229.6097 | 510.5744 | 461.5569 | 419.8465 | 451.967 | 391.4644
1854.0354 | 468.6766 | 229.6727 | 510.0669 | 461.7669 | 419.5095 | 451.6073 | 390.4452
1855.0354 | 464.1626 | 229.8384 | 509.8232 | 461.775 | 418.8463 | 450.8896 | 389.2738
1856.0354 | 462.1738 | 230.0227 | 509.5292 | 461.8662 | 418.5648 | 449.5152 | 388.464
1857.0354 | 462.9115 | 230.2009 | 509.4603 | 462.1623 | 418.8379 | 450.4686 | 388.4764
1858.0354 | 461.6982 | 230.3595 | 509.2749 | 462.9552 | 420.9705 | 452.1899 | 388.3182
1859.0354 | 459.8558 | 230.4093 | 509.4553 | 462.938 | 422.5449 | 452.0889 | 387.6018
1860.0354 | 459.837 | 230.476 | 509.3222 | 463.6077 | 422.6003 | 450.5382 | 387.0244
1861.0354 | 456.5626 | 230.5758 | 508.963 | 462.6992 | 423.0378 | 449.3554 | 386.1538
1862.0198 | 454.7918 | 230.6262 | 508.691 | 462.944 | 423.7583 | 447.9606 | 385.6002
1863.0354 | 453.6163 | 230.6922 | 508.5666 | 462.8861 | 424.327 | 445.9122 | 384.5354
1864.0354 | 452.728 | 230.7555 | 508.5217 | 463.5096 | 424.1199 | 444.7481 | 383.8605
1865.0354 | 453.0891 | 231.0634 | 508.2633 | 463.9225 | 424.0118 | 443.7191 | 383.7957
1866.0354 | 459.0142 | 231.1722 | 508.1118 | 464.3162 | 424.0738 | 442.9248 | 383.702
1867.0354 | 456.8758 | 231.0997 | 507.7492 | 464.2412 | 425.1227 | 443.2341 | 383.8117
1868.0354 | 454.3261 | 231.275 | 507.5837 | 464.7957 | 425.3173 | 441.8835 | 383.4841
1869.0354 | 451.6652 | 231.4151 | 507.3261 | 464.8061 | 425.3768 | 440.5762 | 382.3302
1870.0354 | 448.411 | 231.4161 | 507.1797 | 464.0459 | 424.8965 | 438.4519 | 381.5173
1871.0354 | 445.725 | 231.5775 | 507.4284 | 464.2621 | 424.374 | 437.612 | 381.1597
1872.0354 | 442.1604 | 231.6923 | 508.3006 | 464.7682 | 423.4554 | 436.9132 | 380.927
1873.0354 | 439.7163 | 231.7955 | 508.2613 | 464.4877 | 422.8022 | 436.7452 | 381.2274
1874.0354 | 437.8778 | 231.9713 | 506.9026 | 464.7601 | 422.4234 | 436.0201 | 380.6747
1875.0354 | 435.9139 | 232.0151 | 506.8009 | 464.6621 | 421.7502 | 434.1831 | 379.5565
1876.0354 | 435.08 | 232.2175 | 507.0357 | 464.2951 | 421.0975 | 432.5569 | 378.7685
1877.0354 | 435.2387 | 232.2567 | 507.1494 | 464.1368 | 421.0151 | 432.3704 | 378.3559
1878.0354 | 433.5783 | 232.3494 | 506.656 | 464.8873 | 420.7176 | 432.9875 | 378.0248
1879.0354 | 432.7375 | 232.4372 | 506.1919 | 465.5489 | 420.8242 | 433.4386 | 378.2984
1880.0354 | 432.4007 | 232.5117 | 506.1365 | 466.2949 | 420.6417 | 432.4595 | 377.8527
1881.0354 | 431.8082 | 232.6123 | 505.8616 | 466.2198 | 421.1546 | 432.0603 | 377.4456
1882.0354 | 431.006 | 232.6715 | 506.9577 | 465.4944 | 421.5325 | 431.7712 | 377.2219
1883.0354 | 431.3637 | 232.9208 | 506.4437 | 465.6012 | 421.1263 | 431.7139 | 377.5159
1884.0354 | 432.6093 | 232.9544 | 506.3603 | 465.5711 | 420.945 | 432.0262 | 378.5146
1885.0354 | 433.8658 | 233.0667 | 506.4793 | 465.9447 | 420.8189 | 433.0311 | 378.5607
1886.0354 | 433.883 | 233.2336 | 507.8787 | 465.9064 | 420.033 | 434.1464 | 379.7341
1887.0354 | 433.6208 | 233.5062 | 508.0262 | 465.9173 | 419.7917 | 434.4357 | 380.9633
1888.0354 | 435.4569 | 233.5665 | 506.7699 | 466.1781 | 419.6356 | 434.5465 | 381.6106
1889.0354 | 437.186 | 233.7767 | 510.2113 | 466.1798 | 420.3474 | 435.4537 | 382.9801
1890.0354 | 440.7082 | 233.7566 | 509.615 | 466.3647 | 420.3408 | 437.194 | 383.4831
1891.0354 | 442.3507 | 233.734 | 508.0975 | 466.4122 | 420.2954 | 438.6255 | 384.5499
1892.0354 | 442.1772 | 234.0694 | 509.3603 | 466.6937 | 419.8047 | 438.3102 | 385.4495
1893.0354 | 442.3733 | 234.3035 | 509.0551 | 466.6263 | 419.1651 | 439.0095 | 385.3567
1894.0354 | 444.9985 | 234.5016 | 507.8996 | 466.5048 | 419.6963 | 441.6258 | 386.6601
1895.0354 | 454.7411 | 234.5232 | 507.9921 | 467.0786 | 420.2085 | 445.4193 | 388.1433
1896.0354 | 453.7607 | 234.5532 | 507.9401 | 466.7338 | 420.7946 | 445.8038 | 389.2138
1897.0354 | 452.5891 | 234.5201 | 508.2888 | 467.1929 | 420.9308 | 445.1739 | 389.113
1898.0354 | 455.634 | 234.8958 | 508.7177 | 466.9775 | 421.0793 | 448.1801 | 390.3678
1899.0354 | 455.8821 | 234.7939 | 508.0634 | 467.7853 | 421.078 | 450.989 | 391.5766
1900.0354 | 455.9214 | 234.8482 | 508.043 | 468.0651 | 421.3279 | 449.8783 | 391.4454
1901.0354 | 456.9007 | 234.9239 | 508.1739 | 468.2608 | 422.1398 | 449.2647 | 391.3274
1902.0354 | 457.9285 | 235.0562 | 508.2833 | 467.9729 | 422.4218 | 449.0396 | 391.0625
1903.0354 | 458.9053 | 235.1999 | 508.7562 | 467.6255 | 422.8123 | 448.985 | 392.0692
1904.0354 | 457.9214 | 235.2802 | 508.9285 | 467.5136 | 423.1268 | 449.0862 | 393.0203
1905.0354 | 457.2454 | 235.4281 | 509.7144 | 467.761 | 423.1911 | 449.738 | 394.1602
1906.0354 | 457.8692 | 235.4495 | 508.8641 | 467.5954 | 423.0563 | 450.2699 | 395.5287
1907.0354 | 459.8713 | 235.6161 | 509.7141 | 467.9394 | 423.0085 | 451.5938 | 397.023
1908.0354 | 460.6542 | 235.7892 | 509.1417 | 468.2765 | 423.0124 | 455.8809 | 397.3616
1909.0354 | 458.6748 | 235.8684 | 508.6845 | 468.7704 | 423.279 | 455.021 | 397.3918
1910.0354 | 458.9572 | 236.045 | 509.2543 | 469.6303 | 423.5422 | 453.7383 | 396.7484
1911.0354 | 459.8156 | 236.2287 | 509.9892 | 468.7772 | 423.4017 | 452.5295 | 395.2474
1912.0354 | 459.9759 | 236.3157 | 509.2755 | 468.9896 | 423.782 | 452.067 | 394.7349
1913.0354 | 459.1024 | 236.4531 | 509.3274 | 469.1563 | 423.8744 | 451.0134 | 394.138
1914.0354 | 456.6725 | 236.5602 | 509.7102 | 469.0571 | 423.6749 | 450.3066 | 393.5777
1915.0354 | 456.1584 | 236.6425 | 509.0631 | 469.3293 | 423.4815 | 450.1702 | 394.0623
1916.0354 | 455.3535 | 236.8612 | 509.397 | 469.1432 | 423.419 | 450.0683 | 394.0271
1917.0354 | 455.4625 | 237.0228 | 509.7971 | 469.465 | 423.9882 | 449.7175 | 394.5762
1918.0354 | 455.2187 | 236.9933 | 509.1184 | 469.957 | 423.7679 | 448.5294 | 393.927
1919.0354 | 452.666 | 237.1351 | 509.4933 | 470.4118 | 423.3354 | 447.769 | 393.3098
1920.0354 | 452.4229 | 237.1735 | 509.3245 | 469.7718 | 423.8003 | 448.7624 | 394.1993
1921.0354 | 452.0654 | 237.4457 | 510.2632 | 469.8552 | 423.3769 | 449.626 | 394.6854
1922.0354 | 450.3329 | 237.587 | 509.5046 | 470.7338 | 424.2991 | 450.4169 | 396.7193
1923.0354 | 449.5478 | 237.6005 | 509.0689 | 470.3667 | 424.5237 | 449.5945 | 397.0595
1924.0354 | 452.0393 | 237.7302 | 508.8537 | 471.015 | 424.5014 | 450.1256 | 397.3975
1925.0354 | 451.2558 | 237.8987 | 509.7373 | 470.7918 | 425.5488 | 448.8555 | 397.8027
1926.0354 | 452.059 | 238.0844 | 509.3077 | 470.3653 | 425.2068 | 447.3788 | 396.3632
1927.0354 | 451.2164 | 238.1364 | 508.6371 | 470.4144 | 425.8317 | 448.4225 | 395.4287
1928.0354 | 450.4278 | 238.2967 | 509.168 | 470.5916 | 425.4169 | 448.591 | 395.0141
1929.0354 | 450.5842 | 238.2547 | 509.3007 | 470.3635 | 425.2855 | 448.5764 | 394.7872
1930.0354 | 451.1025 | 238.202 | 508.5872 | 470.3923 | 424.7401 | 448.7921 | 394.5849
1931.0354 | 450.254 | 238.2701 | 509.0794 | 470.544 | 424.1136 | 447.8362 | 394.5491
1932.0354 | 448.9455 | 238.5959 | 509.8374 | 470.8731 | 423.6169 | 447.4001 | 394.5201
1933.0354 | 445.7471 | 238.7577 | 509.1265 | 471.5929 | 423.7991 | 446.4825 | 394.9798
1934.0354 | 447.8018 | 238.8721 | 509.4041 | 471.9074 | 423.2199 | 444.9299 | 393.6205
1935.0354 | 448.6841 | 238.8767 | 509.4114 | 470.9681 | 423.1966 | 444.812 | 393.9816
1936.0354 | 448.8423 | 239.0413 | 509.7541 | 471.4474 | 423.7689 | 445.4523 | 394.3578
1937.0354 | 446.0838 | 239.2003 | 509.7791 | 471.972 | 423.8003 | 445.0837 | 394.6189
1938.0354 | 445.0818 | 239.3791 | 508.7793 | 471.6804 | 423.4837 | 444.1353 | 394.4953
1939.0354 | 443.2866 | 239.3301 | 509.6341 | 471.2275 | 424.0477 | 443.8897 | 394.638
1940.0354 | 443.663 | 239.3189 | 509.5084 | 471.2516 | 423.5137 | 442.719 | 394.1344
1941.0354 | 444.5277 | 239.4631 | 510.3829 | 471.2232 | 422.5865 | 442.5625 | 393.8349
1942.0354 | 444.6811 | 239.5832 | 509.7221 | 472.0126 | 422.3181 | 441.7547 | 394.0383
1943.0354 | 445.632 | 239.6057 | 511.1954 | 471.8775 | 422.379 | 440.9163 | 394.4792
1944.0354 | 447.3316 | 239.7206 | 511.937 | 471.7886 | 421.8648 | 441.4986 | 394.9095
1945.0354 | 447.3798 | 240.0393 | 511.5807 | 471.4789 | 421.8925 | 441.8227 | 395.8777
1946.0354 | 447.722 | 240.0882 | 510.9016 | 471.6024 | 421.1906 | 441.134 | 395.9525
1947.0354 | 449.1827 | 240.1677 | 510.5601 | 471.5213 | 420.2638 | 441.116 | 395.9029
1948.0354 | 448.8363 | 240.2269 | 509.6775 | 471.5929 | 420.3373 | 442.5568 | 395.8019
1949.0354 | 446.3661 | 240.3469 | 509.8879 | 471.892 | 420.5603 | 441.7917 | 394.7172
1950.0354 | 445.7935 | 240.4903 | 510.0337 | 471.4961 | 422.5785 | 442.4293 | 393.9498
1951.0354 | 444.1052 | 240.4262 | 509.5583 | 471.7184 | 422.5181 | 442.7176 | 393.5536
1952.0354 | 443.5406 | 240.5363 | 509.4185 | 471.68 | 423.2589 | 442.591 | 392.6398
1953.0354 | 443.4679 | 240.6411 | 509.7311 | 471.5963 | 423.4959 | 443.3366 | 391.9531
1954.0354 | 442.0913 | 240.6766 | 510.5147 | 472.0492 | 424.3814 | 443.7763 | 391.6454
1955.0354 | 441.5542 | 240.8025 | 509.9563 | 471.6486 | 424.6105 | 444.9171 | 391.6351
1956.0354 | 442.0709 | 241.0685 | 509.4291 | 471.4457 | 424.8586 | 446.7688 | 392.5174
1957.0354 | 444.5508 | 241.3129 | 510.3145 | 471.9244 | 425.1447 | 447.912 | 392.5638
1958.0354 | 446.3626 | 241.4033 | 512.799 | 472.4213 | 426.4705 | 449.5309 | 393.5722
1959.0354 | 448.3259 | 241.4873 | 513.3441 | 472.5692 | 425.8545 | 448.9797 | 393.5168
1960.0354 | 448.626 | 241.5018 | 511.3815 | 472.332 | 425.6582 | 447.8739 | 393.516
1961.0354 | 449.0536 | 241.721 | 511.3314 | 472.6968 | 425.3523 | 445.5889 | 392.3842
1962.0354 | 450.871 | 241.8271 | 513.0719 | 472.9574 | 425.157 | 444.5055 | 392.2129
1963.0354 | 455.5325 | 241.9841 | 513.5352 | 472.8705 | 426.6434 | 445.7688 | 392.0326
1964.0354 | 459.2782 | 242.0498 | 512.4497 | 473.634 | 427.4717 | 447.0235 | 392.1078
1965.0354 | 459.6051 | 242.3936 | 512.3514 | 472.7319 | 427.0516 | 445.0204 | 391.314
1966.0354 | 460.2273 | 242.421 | 513.6307 | 472.8557 | 426.4524 | 444.5466 | 390.7199
1967.0354 | 461.8997 | 242.8054 | 514.7692 | 472.8487 | 426.836 | 445.2997 | 392.588
1968.0354 | 463.2123 | 242.6965 | 514.4949 | 473.0549 | 426.3838 | 445.1108 | 393.0451
1969.0354 | 463.534 | 242.8283 | 513.9909 | 472.9844 | 426.3357 | 444.8036 | 393.5991
1970.0354 | 464.376 | 242.9664 | 515.306 | 473.0321 | 426.033 | 445.0563 | 393.902
1971.0354 | 466.3997 | 243.0164 | 514.8052 | 472.7025 | 425.7577 | 445.8807 | 395.2478
1972.0354 | 468.1471 | 243.0901 | 514.6014 | 472.9726 | 426.316 | 446.2585 | 396.1008
1973.0354 | 469.0142 | 243.0742 | 513.9567 | 472.9908 | 426.5768 | 446.8499 | 396.9158
1974.0354 | 469.097 | 243.0588 | 514.1978 | 472.9698 | 426.0345 | 447.0841 | 396.5801
1975.0354 | 469.0308 | 243.2487 | 514.411 | 473.4437 | 427.2122 | 447.2877 | 397.0214
1976.0354 | 469.4127 | 243.3837 | 514.5287 | 474.1589 | 428.1941 | 446.9052 | 397.219
1977.0354 | 468.4085 | 243.5098 | 515.2319 | 474.3193 | 428.0632 | 446.6399 | 397.0945
1978.0354 | 468.8048 | 243.5217 | 515.6581 | 474.186 | 427.9959 | 446.7441 | 396.9118
1979.0354 | 468.8645 | 243.7453 | 516.8631 | 474.0769 | 427.4596 | 446.2457 | 396.7575
1980.0354 | 468.8687 | 243.8589 | 515.9894 | 473.6839 | 427.3191 | 446.0404 | 396.2853
1981.0354 | 468.8966 | 243.8732 | 515.4373 | 473.9132 | 427.8204 | 445.8211 | 396.893
1982.0354 | 471.0004 | 244.0174 | 515.38 | 473.9979 | 427.5094 | 448.5705 | 398.0372
1983.0354 | 472.5129 | 244.185 | 515.3784 | 474.3199 | 427.2714 | 450.8795 | 398.8743
1984.0354 | 471.191 | 244.2519 | 514.9794 | 474.2544 | 427.2686 | 450.4573 | 398.4269
1985.0354 | 470.8694 | 244.456 | 514.9375 | 474.6748 | 428.2502 | 450.7772 | 398.6296
1986.0354 | 475.3393 | 244.382 | 514.8872 | 474.1205 | 429.457 | 449.1804 | 397.2522
1987.0354 | 473.295 | 244.4553 | 515.3223 | 475.0004 | 431.9111 | 449.6154 | 396.8305
1988.0354 | 472.1599 | 244.5833 | 515.616 | 474.9187 | 432.8936 | 449.2052 | 396.329
1989.0354 | 471.2203 | 244.6246 | 515.5144 | 474.9578 | 433.2629 | 448.4472 | 395.4006
1990.0354 | 470.2112 | 244.8012 | 515.3988 | 475.0287 | 433.3099 | 448.1684 | 395.4766
1991.0354 | 471.3676 | 244.9025 | 515.9923 | 475.3151 | 432.969 | 447.5786 | 395.1647
1992.0354 | 471.4106 | 245.0058 | 516.1106 | 475.0345 | 432.8425 | 448.5842 | 396.4781
1993.0354 | 469.8298 | 245.1505 | 515.8973 | 475.158 | 432.6046 | 448.3247 | 396.8796
1994.0354 | 469.5905 | 245.2656 | 515.8717 | 474.9951 | 432.9793 | 449.3616 | 397.2783
1995.0354 | 470.5824 | 245.3897 | 516.5821 | 475.2386 | 432.3203 | 450.115 | 397.5717
1996.0354 | 472.831 | 245.4519 | 516.957 | 475.761 | 432.8111 | 450.3692 | 398.3365
1997.0354 | 473.0165 | 245.4837 | 516.4427 | 475.4633 | 433.1068 | 449.3142 | 398.8055
1998.0354 | 474.0278 | 245.7746 | 517.8513 | 475.7873 | 432.5684 | 448.8997 | 399.1038
1999.0354 | 475.05 | 245.9087 | 517.4804 | 476.021 | 432.4467 | 448.2588 | 398.828
2000.0354 | 478.0295 | 246.1168 | 518.668 | 476.2493 | 431.7505 | 449.1755 | 399.491
2001.0354 | 480.6768 | 246.3543 | 520.3478 | 476.1003 | 432.139 | 451.9952 | 401.4019
2002.0354 | 479.4528 | 246.4105 | 518.72 | 476.1607 | 431.8884 | 453.4276 | 402.2029
2003.0354 | 477.0766 | 246.5743 | 517.5763 | 476.3569 | 432.3112 | 453.1113 | 401.8202
2004.0354 | 477.162 | 246.5967 | 517.7511 | 476.6383 | 433.5293 | 451.8654 | 400.7958
2005.0354 | 479.7509 | 246.6832 | 518.4526 | 478.2957 | 433.2012 | 451.6222 | 400.9337
2006.0354 | 479.2279 | 246.7497 | 518.5837 | 477.9298 | 432.9405 | 450.0911 | 400.7358
2007.0354 | 481.1771 | 246.8652 | 518.6751 | 477.0156 | 432.8344 | 449.3352 | 400.2833
2008.0354 | 480.334 | 246.9992 | 518.4901 | 476.9836 | 432.7581 | 450.4638 | 400.5091
2009.0354 | 479.1242 | 247.1357 | 518.1162 | 476.9817 | 432.8688 | 453.1696 | 401.5631
2010.0354 | 476.5843 | 247.3397 | 518.2223 | 477.4461 | 433.3208 | 455.0036 | 402.1423
2011.0354 | 474.8033 | 247.4227 | 518.3702 | 477.4146 | 434.0298 | 454.5197 | 401.7962
2012.0354 | 474.3858 | 247.4639 | 518.2039 | 477.7812 | 434.4509 | 455.0213 | 402.4834
2013.0354 | 472.6957 | 247.4669 | 517.6825 | 477.0373 | 435.0021 | 456.5676 | 402.2489
2014.0354 | 478.84 | 247.5046 | 517.5693 | 476.9121 | 436.5424 | 457.1046 | 401.3961
2015.0354 | 478.4886 | 247.6039 | 518.0353 | 478.0073 | 439.0659 | 458.5848 | 401.5222
2016.0354 | 476.8497 | 247.7973 | 518.0945 | 477.6449 | 439.9328 | 457.8909 | 401.1601
2017.0354 | 475.4456 | 247.9384 | 518.766 | 477.5486 | 440.3766 | 458.9733 | 401.4645
2018.0354 | 475.2073 | 247.9964 | 518.1522 | 477.8061 | 442.3152 | 462.333 | 401.5995
2019.0354 | 474.0024 | 248.1413 | 517.8479 | 478.3292 | 442.9461 | 463.2729 | 402.3578
2020.0354 | 472.1286 | 248.2664 | 519.0771 | 478.0371 | 444.0973 | 462.4083 | 402.6824
2021.0354 | 473.4722 | 248.4362 | 520.0718 | 478.2031 | 442.7938 | 461.8555 | 402.8324
2022.0354 | 472.383 | 248.4839 | 518.6418 | 478.4034 | 441.8313 | 461.9317 | 403.2898
2023.0354 | 473.4281 | 248.503 | 518.8849 | 478.4942 | 442.0022 | 461.6728 | 404.226
2024.0354 | 474.0529 | 248.6055 | 518.686 | 478.4324 | 441.8365 | 460.477 | 403.8864
2025.0354 | 473.307 | 248.688 | 518.5499 | 478.8874 | 441.4763 | 459.6702 | 403.4733
2026.0354 | 472.9974 | 248.8716 | 519.7301 | 479.293 | 441.7235 | 458.6876 | 403.2851
2027.0354 | 471.9885 | 248.9474 | 518.9159 | 478.8734 | 441.7341 | 457.6584 | 403.6803
2028.0354 | 475.5164 | 248.9789 | 519.2114 | 480.0777 | 441.7243 | 456.8143 | 404.8023
2029.0354 | 478.5425 | 249.1334 | 519.4637 | 480.346 | 442.4452 | 457.7158 | 405.1556
2030.0354 | 477.7227 | 249.2222 | 519.2587 | 480.0631 | 442.5977 | 457.3573 | 404.6255
2031.0354 | 478.6981 | 249.349 | 518.9805 | 479.8825 | 442.9629 | 457.0446 | 404.6017
2032.0354 | 481.5559 | 249.3853 | 518.407 | 479.8326 | 444.0884 | 463.3283 | 405.6437
2033.0354 | 483.834 | 249.489 | 518.8929 | 480.1639 | 444.6902 | 467.819 | 406.3181
2034.0354 | 483.5858 | 249.7204 | 520.3322 | 480.2319 | 445.2835 | 467.2444 | 406.3411
2035.0354 | 482.2727 | 249.7901 | 519.3223 | 480.2039 | 445.3941 | 465.9186 | 405.8594
2036.0354 | 480.427 | 249.7012 | 519.3617 | 480.5837 | 444.7025 | 465.4023 | 406.0635
2037.0354 | 478.804 | 249.9258 | 518.9799 | 481.1412 | 444.2234 | 463.6971 | 404.7868
2038.0354 | 479.3587 | 250.1492 | 518.4404 | 481.8837 | 444.1293 | 461.6254 | 403.4174
2039.0354 | 480.3812 | 250.2649 | 518.682 | 481.0292 | 444.1449 | 462.8968 | 403.517
2040.0354 | 481.6727 | 250.3144 | 518.5435 | 481.1067 | 445.9966 | 465.5413 | 404.2224
2041.0354 | 481.8364 | 250.3574 | 518.4218 | 481.142 | 447.6974 | 469.357 | 404.9251
2042.0354 | 479.8846 | 250.4195 | 518.4006 | 480.9015 | 447.4522 | 469.3891 | 403.8689
2043.0354 | 479.4949 | 250.5417 | 518.7524 | 480.9483 | 446.893 | 468.0341 | 403.3028
2044.0354 | 480.3126 | 250.6439 | 519.0311 | 481.6309 | 446.3414 | 466.7181 | 403.0384
2045.0354 | 480.1485 | 250.8088 | 519.1054 | 482.3747 | 445.8121 | 465.5738 | 402.7573
2046.0354 | 481.2665 | 251.091 | 519.3037 | 481.7925 | 446.0996 | 464.7298 | 403.0165
2047.0354 | 483.8705 | 251.2208 | 520.0301 | 481.342 | 445.9249 | 465.0168 | 403.5042
2048.0354 | 484.7038 | 251.3557 | 520.577 | 482.4928 | 445.7422 | 465.0931 | 404.5963
2049.0354 | 484.1387 | 251.2999 | 520.2421 | 482.1948 | 445.422 | 464.3045 | 404.3194
2050.0354 | 486.0696 | 251.4467 | 520.1119 | 481.9353 | 445.6978 | 463.6119 | 404.7761
2051.0354 | 484.9153 | 251.3913 | 518.977 | 482.4896 | 445.158 | 463.4072 | 404.5304
2052.0354 | 483.2111 | 251.5827 | 518.884 | 482.3347 | 446.2525 | 463.9591 | 404.724
2053.0354 | 483.5879 | 251.5946 | 520.2165 | 482.1698 | 446.1335 | 462.9647 | 404.682
2054.0354 | 483.9048 | 251.8177 | 519.9214 | 482.6254 | 446.7055 | 464.5267 | 405.2933
2055.0354 | 483.9376 | 251.8953 | 519.9256 | 483.2003 | 446.7455 | 465.3097 | 405.3863
2056.0354 | 483.638 | 252.0746 | 519.3804 | 483.226 | 445.8812 | 465.221 | 405.8749
2057.0354 | 486.4744 | 252.0751 | 519.6512 | 483.0331 | 445.9954 | 465.6786 | 406.57
2058.0354 | 490.7383 | 252.052 | 519.0776 | 482.8104 | 446.6745 | 470.9155 | 408.6083
2059.0354 | 495.4019 | 252.2697 | 518.9634 | 483.0924 | 448.9171 | 476.7478 | 410.3888
2060.0354 | 499.9775 | 252.5734 | 519.9682 | 483.5586 | 451.7079 | 481.2613 | 412.6098
2061.0354 | 498.5322 | 252.5628 | 518.9258 | 483.4582 | 453.2878 | 481.4132 | 412.6931
2062.0354 | 498.737 | 252.7701 | 518.9762 | 483.4795 | 453.2914 | 480.1137 | 412.3995
2063.0354 | 500.2129 | 252.9134 | 519.9999 | 484.12 | 454.7267 | 480.4132 | 411.654
2064.0354 | 501.3727 | 252.8649 | 520.3701 | 484.8031 | 454.0116 | 479.4126 | 411.1261
2065.0354 | 501.7815 | 252.9016 | 519.7196 | 483.6026 | 453.6697 | 477.8749 | 409.3294
2066.0354 | 502.1836 | 252.9076 | 519.7703 | 483.6568 | 453.5652 | 477.5413 | 409.5851
2067.0354 | 500.7231 | 253.0769 | 519.1585 | 483.5497 | 452.9482 | 478.1527 | 409.5207
2068.0354 | 497.872 | 253.2002 | 519.3591 | 483.7132 | 451.9254 | 476.6733 | 409.5114
2069.0354 | 497.6566 | 253.4335 | 519.4356 | 483.4191 | 451.895 | 476.1399 | 409.5801
2070.051 | 498.6442 | 253.5405 | 519.7493 | 483.4623 | 454.165 | 480.3202 | 410.0652
2071.0354 | 502.8626 | 253.642 | 519.4816 | 483.7771 | 457.6633 | 485.7536 | 411.8577
2072.0354 | 502.459 | 253.7978 | 520.2047 | 483.7067 | 459.088 | 492.4214 | 414.0191
2073.0354 | 500.1368 | 253.9033 | 519.7257 | 483.4854 | 459.9607 | 498.6543 | 415.861
2074.0354 | 499.9431 | 253.9636 | 519.0052 | 483.7862 | 458.6587 | 499.5594 | 414.9934
2075.0354 | 498.0716 | 253.9763 | 518.5663 | 483.7623 | 459.4659 | 502.0672 | 414.1146
2076.0354 | 495.6178 | 254.0172 | 519.9463 | 483.7925 | 462.5004 | 504.6012 | 414.7123
2077.0354 | 493.2495 | 254.0847 | 520.4562 | 483.5577 | 463.3666 | 504.6184 | 416.1571
2078.0354 | 494.4433 | 254.1783 | 519.2541 | 483.7131 | 462.9915 | 503.3271 | 416.408
2079.0354 | 494.6961 | 254.6056 | 519.2285 | 483.667 | 464.521 | 505.4105 | 417.0558
2080.0354 | 492.2007 | 254.7058 | 519.6994 | 483.3483 | 464.5475 | 504.0476 | 416.4161
2081.0354 | 492.9075 | 254.9161 | 519.4697 | 483.7049 | 463.1199 | 502.4343 | 416.7137
2082.0354 | 494.3767 | 255.0142 | 520.3422 | 483.2073 | 463.8796 | 512.9676 | 418.7786
2083.0354 | 495.1115 | 255.0074 | 521.5989 | 483.6277 | 465.0419 | 517.0151 | 421.2795
2084.0354 | 496.4608 | 255.1871 | 521.1919 | 483.7356 | 465.4669 | 517.2303 | 421.916
2085.0354 | 496.0495 | 255.2826 | 520.5593 | 483.7159 | 464.3348 | 517.3953 | 422.0951
2086.0354 | 498.4281 | 255.6317 | 520.9246 | 483.0819 | 463.5168 | 519.9138 | 422.5244
2087.0354 | 499.9116 | 255.7148 | 521.2785 | 483.6347 | 463.2259 | 521.6964 | 423.587
2088.0354 | 499.9274 | 255.6885 | 520.9807 | 483.495 | 461.5721 | 521.7981 | 423.8782
2089.0354 | 499.4585 | 255.6537 | 520.398 | 483.2985 | 460.7903 | 519.5358 | 423.9317
2090.0354 | 504.9382 | 255.7734 | 520.5122 | 483.2722 | 461.1785 | 525.9129 | 425.4913
2091.0354 | 508.1757 | 256.1379 | 521.2556 | 483.3854 | 462.9147 | 532.2573 | 428.1647
2092.0354 | 510.2888 | 256.3069 | 521.1404 | 483.8321 | 463.6307 | 531.8993 | 427.9133
2093.0354 | 512.7059 | 256.3133 | 521.5815 | 483.4571 | 464.5875 | 534.1522 | 428.5784
2094.0354 | 514.5029 | 256.4229 | 521.4282 | 483.9598 | 465.5109 | 534.4957 | 429.3433
2095.0354 | 515.1866 | 256.6654 | 521.7008 | 484.1777 | 468.7001 | 536.9435 | 428.9151
2096.0354 | 517.0177 | 256.8388 | 522.5593 | 483.6632 | 468.2906 | 552.8695 | 427.7715
2097.0354 | 524.1644 | 256.9393 | 523.2103 | 483.5332 | 469.2235 | 564.7416 | 427.9764
2098.0354 | 528.6653 | 257.1272 | 524.7779 | 483.8561 | 469.4726 | 566.4947 | 431.9749
2099.0354 | 531.038 | 257.5182 | 525.6873 | 483.7218 | 469.9137 | 561.5097 | 433.895
2100.0354 | 532.5537 | 257.6059 | 525.6341 | 483.7416 | 469.1797 | 556.0243 | 435.3924
2101.0354 | 534.2992 | 257.8258 | 526.1025 | 483.9586 | 468.8085 | 552.7873 | 437.1792
2102.0354 | 536.203 | 257.959 | 526.1439 | 484.5854 | 469.356 | 546.4471 | 437.5154
2103.0354 | 535.3784 | 258.0693 | 526.3699 | 484.3461 | 468.7911 | 543.1158 | 437.9394
2104.0354 | 534.7741 | 258.1153 | 526.3251 | 484.4948 | 468.2789 | 538.7295 | 438.1764
2105.0354 | 534.0478 | 258.1875 | 525.7235 | 484.086 | 469.2433 | 536.0068 | 437.5247
2106.0354 | 533.1448 | 258.3824 | 526.0545 | 483.6915 | 468.4652 | 530.3762 | 435.8403
2107.0354 | 531.7458 | 258.459 | 526.3009 | 484.05 | 470.8763 | 530.9893 | 436.7469
2108.0354 | 530.476 | 258.5948 | 526.1599 | 483.983 | 471.5688 | 530.2406 | 437.905
2109.0354 | 530.3358 | 258.4705 | 526.3153 | 484.235 | 471.1441 | 528.9058 | 437.7488
2110.0354 | 528.5913 | 258.6553 | 526.8859 | 484.0768 | 470.8373 | 531.022 | 438.1068
2111.0354 | 527.8328 | 259.0433 | 526.8541 | 484.0651 | 471.1555 | 526.7578 | 437.9285
2112.0354 | 526.3489 | 259.1599 | 526.0327 | 483.7577 | 470.5519 | 524.5142 | 437.7362
2113.0354 | 523.1687 | 259.3367 | 526.0855 | 483.7239 | 469.5792 | 525.0354 | 436.7221
2114.0354 | 522.5726 | 259.3555 | 526.7537 | 484.0811 | 469.6186 | 523.1705 | 436.7847
2115.0354 | 521.0348 | 259.4509 | 527.6317 | 484.2045 | 469.8561 | 518.098 | 435.3383
2116.0354 | 523.1297 | 259.6199 | 528.1813 | 483.7952 | 468.9592 | 514.87 | 434.9969
2117.0354 | 525.5232 | 259.8153 | 528.4837 | 483.6998 | 467.4084 | 512.0063 | 435.0774
2118.0354 | 533.222 | 260.2877 | 529.0098 | 484.073 | 467.7556 | 516.0948 | 438.0371
2119.0354 | 533.7119 | 260.1581 | 528.7942 | 484.0084 | 467.6807 | 514.396 | 439.4631
2120.0354 | 532.884 | 260.3583 | 528.6571 | 483.5504 | 467.8845 | 512.3163 | 440.2325
2121.0354 | 531.778 | 260.2488 | 528.6567 | 483.67 | 468.6898 | 513.3097 | 440.5633
2122.0354 | 531.7107 | 260.2717 | 528.4281 | 483.6672 | 469.4775 | 515.5826 | 441.0569
2123.0354 | 532.4752 | 260.3448 | 529.2853 | 483.2989 | 470.105 | 518.5913 | 440.8098
2124.0354 | 533.268 | 260.2497 | 528.7702 | 483.7692 | 469.9627 | 521.3983 | 441.3047
2125.0354 | 534.9096 | 260.5335 | 528.6631 | 483.3068 | 469.6661 | 519.5555 | 439.6883
2126.0354 | 533.8278 | 260.6472 | 528.7947 | 483.2824 | 470.4516 | 519.7413 | 439.8166
2127.0354 | 533.3018 | 260.7568 | 528.284 | 482.6859 | 469.214 | 517.0259 | 438.784
2128.0354 | 534.8954 | 260.7601 | 528.2027 | 483.0466 | 469.2569 | 520.7761 | 438.0544
2129.0354 | 538.7098 | 260.8333 | 527.9919 | 482.8822 | 472.0048 | 527.9508 | 438.9106
2130.0354 | 544.6008 | 260.9835 | 528.2238 | 482.8767 | 472.5593 | 530.3065 | 439.0197
2131.0354 | 549.6532 | 261.1214 | 528.6108 | 482.8506 | 473.4548 | 534.2038 | 439.5032
2132.0354 | 556.2825 | 261.4133 | 528.6965 | 483.1545 | 474.7317 | 536.2131 | 441.3992
2133.0354 | 560.9888 | 261.5038 | 528.4793 | 483.4132 | 475.102 | 535.934 | 444.3196
2134.0354 | 565.4343 | 261.5929 | 528.6425 | 483.1661 | 476.0781 | 536.0226 | 445.0286
2135.0354 | 567.7319 | 261.6891 | 528.2584 | 482.9013 | 476.6232 | 537.5483 | 446.5709
2136.0354 | 571.6383 | 261.7244 | 528.1018 | 482.8601 | 476.7833 | 537.5182 | 446.8728
2137.0354 | 575.042 | 261.9069 | 528.6469 | 482.8657 | 476.8695 | 539.347 | 447.6559
2138.0354 | 577.6367 | 262.011 | 528.5176 | 482.7401 | 477.2142 | 541.8212 | 449.4304
2139.0354 | 582.3138 | 262.1894 | 528.4071 | 483.3965 | 479.351 | 542.9718 | 449.8915
2140.0354 | 583.9481 | 262.2787 | 528.2984 | 482.6169 | 481.5173 | 543.0181 | 450.2323
2141.0354 | 583.9949 | 262.325 | 528.195 | 482.8038 | 483.5598 | 544.5761 | 450.8308
2142.0354 | 583.7658 | 262.489 | 528.3264 | 482.5385 | 485.1563 | 549.003 | 452.8151
2143.0354 | 582.893 | 262.6414 | 528.1377 | 482.146 | 486.361 | 547.6497 | 453.539
2144.0354 | 582.7206 | 262.716 | 527.5854 | 482.6643 | 487.183 | 549.9243 | 452.2914
2145.0354 | 583.6854 | 262.8476 | 527.7392 | 482.3105 | 488.9156 | 549.399 | 453.5358
2146.0354 | 584.3039 | 262.972 | 527.7734 | 482.4272 | 489.0153 | 550.875 | 452.8741
2147.0354 | 585.4714 | 263.1388 | 528.0388 | 482.4955 | 490.4334 | 550.988 | 454.0291
2148.0354 | 585.6788 | 263.2084 | 528.0813 | 482.7049 | 491.7969 | 548.5257 | 453.0601
2149.0354 | 587.5035 | 263.3031 | 527.2374 | 482.1355 | 493.8254 | 547.1705 | 452.4811
2150.0354 | 591.5095 | 263.4062 | 527.0454 | 482.0086 | 497.4519 | 545.7178 | 451.4561
2151.0354 | 595.2886 | 263.571 | 527.6788 | 482.1739 | 498.9101 | 546.079 | 450.4122
2152.0354 | 593.8622 | 263.6922 | 527.9771 | 482.6073 | 499.7211 | 542.3657 | 450.8763
2153.0354 | 591.782 | 263.7714 | 527.6468 | 482.9902 | 500.0202 | 539.2136 | 450.5466
2154.0354 | 590.3999 | 263.8407 | 527.4543 | 483.1866 | 498.9834 | 540.2526 | 449.1372
2155.0354 | 588.1605 | 264.0244 | 528.0861 | 483.0614 | 499.2852 | 538.9259 | 447.26
2156.0354 | 584.4057 | 264.1883 | 527.4082 | 483.2379 | 500.0156 | 536.0534 | 448.5485
2157.0354 | 583.551 | 264.2881 | 527.824 | 484.0234 | 498.9499 | 536.6286 | 447.7981
2158.0354 | 583.2679 | 264.4689 | 527.4521 | 483.2886 | 499.7725 | 540.577 | 448.2159
2159.0354 | 583.7266 | 264.692 | 527.7114 | 483.8088 | 502.6943 | 568.5244 | 449.3886
2160.0354 | 584.658 | 265.0126 | 528.8252 | 483.8451 | 503.1425 | 575.7268 | 449.9371
2161.0354 | 586.7661 | 265.05 | 528.9414 | 483.3659 | 503.7145 | 585.8448 | 450.3178
2162.0354 | 586.7156 | 265.1813 | 528.1446 | 483.3984 | 503.5197 | 581.2748 | 449.9452
2163.0354 | 586.2131 | 265.6383 | 528.465 | 483.6752 | 503.332 | 575.7026 | 450.4532
2164.0354 | 586.3737 | 265.8085 | 530.0861 | 483.6906 | 502.7525 | 571.5696 | 452.1398
2165.0354 | 583.9519 | 265.6564 | 528.8438 | 483.5733 | 501.519 | 564.6969 | 453.0538
2166.0354 | 580.4595 | 265.6337 | 528.7301 | 483.7441 | 500.5303 | 559.323 | 453.0368
2167.0354 | 578.2328 | 265.9008 | 529.0625 | 483.8817 | 499.5328 | 553.5615 | 452.9587
2168.0354 | 574.5219 | 266.0646 | 529.1917 | 483.4907 | 497.9332 | 548.8926 | 451.894
2169.0354 | 571.2933 | 266.0745 | 529.616 | 483.6053 | 496.8449 | 543.73 | 452.365
2170.0354 | 569.1256 | 266.1438 | 529.5004 | 484.0783 | 495.4484 | 538.8896 | 452.2858
2171.0354 | 567.6187 | 266.2477 | 529.327 | 483.7857 | 494.245 | 532.9359 | 452.1344
2172.0354 | 564.4483 | 266.5235 | 530.6101 | 483.4451 | 493.0404 | 528.1997 | 451.2655
2173.0354 | 562.149 | 266.545 | 531.6664 | 483.6308 | 492.0137 | 525.5372 | 449.9979
2174.0354 | 564.2399 | 266.6693 | 531.9359 | 483.7885 | 491.7539 | 523.29 | 450.1894
2175.0354 | 564.7743 | 266.7842 | 532.6161 | 483.869 | 491.4764 | 523.2267 | 450.6238
2176.0354 | 564.148 | 266.9397 | 531.9212 | 483.803 | 491.2367 | 522.2189 | 451.5299
2177.0354 | 564.8445 | 267.2182 | 530.8601 | 483.4578 | 491.155 | 521.6066 | 450.0151
2178.0354 | 568.7317 | 267.2918 | 531.2583 | 483.3652 | 491.3842 | 528.0165 | 451.7269
2179.0354 | 570.7464 | 267.5087 | 531.2784 | 483.3831 | 492.5504 | 528.7161 | 454.5725
2180.0354 | 572.9893 | 267.5228 | 530.8237 | 483.8193 | 492.4085 | 525.8526 | 454.911
2181.0354 | 577.4531 | 267.5213 | 532.0996 | 483.4603 | 493.4002 | 527.3125 | 455.0128
2182.0354 | 576.8945 | 267.5642 | 531.3293 | 483.9436 | 493.3851 | 525.5525 | 453.5954
2183.0354 | 576.4068 | 267.7263 | 532.1806 | 483.9792 | 492.9857 | 522.4954 | 453.0315
2184.0354 | 576.1555 | 267.791 | 531.5139 | 483.7884 | 492.7031 | 520.3116 | 452.0473
2185.0354 | 575.1983 | 267.9186 | 531.4817 | 484.065 | 492.1191 | 518.7279 | 452.05
2186.0354 | 574.4679 | 268.3102 | 533.862 | 484.0443 | 492.0561 | 520.3757 | 452.507
2187.0354 | 573.0222 | 268.5748 | 534.0456 | 484.091 | 491.845 | 519.818 | 453.755
2188.0354 | 571.5027 | 268.4458 | 532.7701 | 483.6037 | 490.6065 | 517.5083 | 451.3575
2189.0354 | 570.5434 | 268.4955 | 532.4213 | 483.9051 | 490.5921 | 518.3992 | 450.0808
2190.0354 | 571.4848 | 268.6156 | 531.8493 | 485.3893 | 490.433 | 521.2637 | 450.7144
2191.0354 | 578.0239 | 268.701 | 531.9313 | 485.1952 | 491.6433 | 522.9525 | 451.2843
2192.0354 | 581.5877 | 268.8762 | 532.2041 | 484.4155 | 491.9936 | 524.0346 | 453.0062
2193.0354 | 584.5464 | 269.0114 | 532.1746 | 484.0524 | 491.986 | 525.9569 | 455.1751
2194.0354 | 585.6009 | 269.1705 | 531.7455 | 484.4365 | 491.5282 | 526.6058 | 455.7006
2195.0354 | 585.3618 | 269.3501 | 532.579 | 483.9711 | 491.3998 | 528.6375 | 457.4961
2196.0354 | 585.8707 | 269.3597 | 531.8226 | 483.9378 | 490.9145 | 525.136 | 457.5903
2197.0354 | 590.1367 | 269.4823 | 531.537 | 483.7331 | 492.2363 | 530.902 | 458.1657
2198.0354 | 592.3868 | 269.6581 | 531.8703 | 483.9102 | 493.3074 | 533.227 | 458.9592
2199.0354 | 596.1312 | 269.7349 | 532.0076 | 483.8429 | 494.307 | 535.0619 | 459.114
2200.0354 | 599.4017 | 269.9691 | 532.1365 | 483.6228 | 495.8106 | 538.0034 | 460.957
2201.0354 | 599.0544 | 270.06 | 531.9879 | 483.6026 | 496.0001 | 541.414 | 462.5678
2202.0354 | 595.596 | 270.0035 | 531.5588 | 483.5799 | 496.0379 | 540.1399 | 462.2336
2203.0354 | 599.6582 | 270.0794 | 531.9985 | 483.8168 | 497.1223 | 541.639 | 461.975
2204.0354 | 600.8374 | 270.3163 | 531.776 | 483.7261 | 498.1562 | 543.9156 | 463.5304
2205.0354 | 605.5407 | 270.4063 | 532.1165 | 483.6151 | 499.5178 | 547.2437 | 464.5941
2206.0354 | 605.6581 | 270.8979 | 532.4478 | 483.529 | 500.322 | 551.6521 | 464.5217
2207.0354 | 604.2796 | 270.9415 | 531.8762 | 483.7193 | 500.6502 | 552.2507 | 465.1832
2208.0354 | 604.8987 | 271.0047 | 531.6953 | 483.6869 | 502.2434 | 553.3547 | 467.3929
2209.0354 | 610.1648 | 271.0326 | 531.3459 | 483.7458 | 504.1373 | 554.8503 | 466.8984
2210.0354 | 613.0192 | 271.1013 | 531.2286 | 483.5549 | 506.2456 | 552.3032 | 466.9246
2211.0354 | 617.4049 | 271.2601 | 530.9954 | 483.3763 | 508.3435 | 552.2617 | 466.4535
2212.0354 | 620.809 | 271.4533 | 530.8294 | 483.0922 | 510.4632 | 553.2436 | 466.8964
2213.0354 | 622.3942 | 271.4903 | 530.7376 | 483.2036 | 512.0801 | 554.3819 | 466.4152
2214.0354 | 626.6107 | 271.6637 | 530.6596 | 483.0708 | 513.984 | 554.2869 | 465.3676
2215.0354 | 631.7534 | 271.888 | 530.4696 | 483.1992 | 516.74 | 555.1401 | 465.7542
2216.0354 | 631.7713 | 272.1173 | 530.5526 | 482.9442 | 517.2572 | 556.1461 | 464.9413
2217.0354 | 629.8576 | 272.1628 | 530.545 | 483.1193 | 518.1129 | 554.0358 | 465.5926
2218.0354 | 630.3101 | 272.3067 | 529.8776 | 483.1802 | 519.861 | 552.9873 | 464.3107
2219.0354 | 631.5241 | 272.4446 | 530.4461 | 483.272 | 522.5018 | 553.1502 | 462.8818
2220.0354 | 629.4238 | 272.4749 | 529.9623 | 483.6621 | 523.7231 | 553.3018 | 463.18
2221.0354 | 627.4223 | 272.5347 | 529.8462 | 483.0901 | 525.0724 | 554.4583 | 463.5081
2222.0354 | 629.9264 | 272.7716 | 529.6806 | 482.6953 | 526.9306 | 552.4002 | 463.9418
2223.0354 | 631.2819 | 272.9012 | 529.3251 | 483.186 | 528.3123 | 552.5078 | 465.2967
2224.0354 | 634.2311 | 273.03 | 529.464 | 483.0714 | 529.3209 | 550.5115 | 465.0357
2225.0354 | 639.4639 | 273.0657 | 529.5671 | 483.3831 | 531.7331 | 550.1663 | 465.4916
2226.0354 | 638.1881 | 273.3238 | 529.632 | 483.0214 | 533.5064 | 551.1257 | 466.0464
2227.0354 | 634.662 | 273.3202 | 529.6157 | 483.088 | 533.5034 | 550.5334 | 467.0825
2228.0354 | 631.2999 | 273.4158 | 529.6132 | 483.1068 | 534.921 | 553.4107 | 468.8257
2229.0354 | 626.7446 | 273.7888 | 529.4597 | 482.7798 | 536.0284 | 554.0045 | 468.8339
2230.0354 | 623.1904 | 273.8908 | 528.9521 | 483.049 | 536.852 | 549.4769 | 466.9115
2231.0354 | 625.188 | 273.9371 | 528.6991 | 482.8588 | 538.7685 | 550.4786 | 465.1989
2232.0354 | 625.2476 | 274.0053 | 528.5209 | 482.7416 | 542.5571 | 554.1802 | 467.4782
2233.0354 | 624.1019 | 274.522 | 528.6494 | 482.7645 | 544.4488 | 555.455 | 467.8509
2234.0354 | 625.8761 | 274.5688 | 528.9102 | 482.7826 | 547.143 | 556.0507 | 469.3749
2235.0354 | 621.0525 | 274.5962 | 528.7419 | 482.2848 | 547.7237 | 553.3005 | 470.4601
2236.0354 | 616.8638 | 274.6784 | 530.4658 | 482.4857 | 547.2487 | 553.3979 | 469.5321
2237.0354 | 612.7246 | 274.832 | 529.1012 | 482.5779 | 548.4969 | 552.2652 | 470.6107
2238.0354 | 609.1119 | 275.1509 | 528.8308 | 482.6137 | 549.5433 | 563.433 | 474.018
2239.0354 | 606.0094 | 275.3161 | 528.7494 | 482.6127 | 551.6028 | 565.6665 | 477.3585
2240.0354 | 602.3055 | 275.3941 | 528.363 | 482.3625 | 551.9345 | 563.0124 | 476.9336
2241.0354 | 599.8725 | 275.5113 | 528.4202 | 483.8704 | 552.9308 | 557.6601 | 475.7135
2242.0354 | 599.5654 | 275.6009 | 528.9504 | 483.5765 | 556.4845 | 554.3332 | 477.3777
2243.0354 | 597.8043 | 275.6251 | 529.4259 | 482.9647 | 558.1661 | 554.27 | 478.3328
2244.0354 | 595.1017 | 275.9691 | 529.9749 | 482.5847 | 558.1517 | 550.5795 | 481.6538
2245.0354 | 591.6509 | 276.3164 | 528.7231 | 482.2728 | 558.548 | 549.2898 | 488.3192
2246.0354 | 591.2204 | 276.3941 | 528.6424 | 482.6005 | 558.9872 | 555.3234 | 497.6632
2247.0354 | 589.2658 | 276.421 | 528.7448 | 483.4642 | 561.1384 | 554.3756 | 504.5947
2248.0354 | 587.0107 | 276.4559 | 528.4218 | 483.8873 | 564.4587 | 548.7757 | 506.824
2249.0354 | 586.9886 | 276.5311 | 528.1734 | 483.4443 | 565.3954 | 551.5312 | 507.538
2250.0354 | 589.8832 | 276.7296 | 528.4212 | 483.0318 | 567.8147 | 549.8517 | 506.7364
2251.0354 | 593.6411 | 276.9766 | 528.2294 | 483.1439 | 568.3608 | 551.2969 | 503.233
2252.0354 | 594.5787 | 277.1157 | 528.9236 | 483.6962 | 567.8852 | 552.0469 | 500.474
2253.0354 | 597.7028 | 277.3566 | 529.8351 | 483.744 | 568.5405 | 553.2801 | 498.424
2254.0354 | 598.6341 | 277.5551 | 530.2159 | 483.5228 | 568.8453 | 558.4205 | 496.723
2255.0354 | 602.3415 | 277.9826 | 530.6825 | 483.0966 | 569.027 | 558.6056 | 494.3517
2256.0354 | 606.5821 | 278.1605 | 531.6133 | 483.3026 | 568.3193 | 560.2077 | 496.8113
2257.0354 | 608.9403 | 278.4028 | 533.6982 | 483.3203 | 565.771 | 560.0042 | 496.0771
2258.0354 | 609.8056 | 278.6553 | 533.9759 | 483.5397 | 563.7194 | 560.6362 | 496.3546
2259.0354 | 609.481 | 278.9272 | 533.5315 | 483.5052 | 563.25 | 559.7801 | 496.0465
2260.0354 | 608.0129 | 279.0839 | 532.8937 | 483.2748 | 561.8209 | 556.4052 | 495.9532
2261.0354 | 604.9993 | 278.9435 | 531.8104 | 483.1096 | 562.0186 | 552.7365 | 494.1691
2262.0354 | 603.6296 | 278.9295 | 531.5167 | 483.0343 | 562.0898 | 550.93 | 491.6621
2263.0354 | 602.625 | 278.866 | 531.7989 | 483.7669 | 562.3925 | 551.7693 | 491.3348
2264.0354 | 602.0797 | 278.9754 | 531.3156 | 483.7156 | 561.8942 | 549.5848 | 489.138
2265.0354 | 608.6503 | 279.22 | 531.8207 | 483.3514 | 564.7733 | 545.7203 | 488.9913
2266.0354 | 610.3167 | 279.2137 | 532.181 | 483.6528 | 566.2358 | 543.3092 | 488.4803
2267.0354 | 610.8504 | 279.4217 | 532.0435 | 483.5394 | 565.9984 | 546.0409 | 489.2765
2268.0354 | 608.3463 | 279.5992 | 532.0626 | 483.0067 | 564.2906 | 549.3974 | 491.2246
2269.0354 | 605.1538 | 279.6171 | 531.562 | 483.3636 | 562.6775 | 548.9502 | 490.3362
2270.0354 | 602.5303 | 279.708 | 531.6953 | 483.1081 | 562.0482 | 549.6981 | 489.7334
2271.0354 | 607.6157 | 279.8656 | 531.8055 | 483.1311 | 562.4691 | 555.0948 | 489.7997
2272.0354 | 608.6743 | 280.168 | 532.8182 | 483.5381 | 562.5893 | 555.3252 | 491.2155
2273.0354 | 607.1529 | 280.51 | 534.0777 | 483.1994 | 561.8934 | 554.9048 | 489.8863
2274.0354 | 609.8296 | 280.6357 | 535.0011 | 483.2188 | 561.6785 | 555.2589 | 491.1331
2275.0354 | 614.6053 | 280.8621 | 533.9335 | 483.6615 | 561.864 | 554.2257 | 492.8515
2276.0354 | 615.7712 | 280.7666 | 532.7432 | 483.3625 | 561.2253 | 553.2006 | 492.6797
2277.0354 | 618.0489 | 280.8843 | 533.013 | 483.2871 | 559.8771 | 556.3231 | 491.4763
2278.0354 | 621.9516 | 280.9426 | 532.7562 | 483.5564 | 560.6552 | 567.5007 | 494.3699
2279.0354 | 624.3524 | 281.0975 | 532.4949 | 483.9658 | 561.9907 | 571.7945 | 498.3479
2280.0354 | 627.318 | 281.3441 | 533.2461 | 483.6001 | 562.3155 | 571.2767 | 499.6957
2281.0354 | 630.7986 | 281.3958 | 533.2052 | 483.1484 | 562.0501 | 570.0977 | 503.6913
2282.0354 | 631.2228 | 281.6407 | 533.6459 | 483.194 | 562.633 | 572.0501 | 508.5619
2283.0354 | 632.1759 | 281.8888 | 534.0322 | 483.2128 | 560.8248 | 575.8719 | 508.4135
2284.0354 | 629.7609 | 281.9487 | 533.2676 | 483.2287 | 557.4011 | 576.7898 | 508.1723
2285.0354 | 628.3138 | 282.067 | 533.2981 | 483.301 | 558.7799 | 576.84 | 507.5944
2286.0354 | 626.1914 | 282.2461 | 532.8854 | 483.9608 | 558.6783 | 571.8358 | 505.1598
2287.0354 | 627.7511 | 282.2422 | 533.0455 | 483.6406 | 558.1006 | 570.3109 | 502.6159
2288.0354 | 631.5361 | 282.4055 | 532.891 | 484.3989 | 556.8671 | 571.0838 | 502.2496
2289.0354 | 633.3874 | 283.4097 | 532.8278 | 484.7375 | 556.7641 | 567.1931 | 499.7509
2290.0354 | 636.7596 | 286.0966 | 533.8094 | 484.9787 | 557.9339 | 567.2179 | 499.3724
2291.0354 | 635.9779 | 283.0002 | 533.1585 | 484.4156 | 555.4918 | 563.94 | 498.9843
2292.0354 | 635.1936 | 283.157 | 535.2044 | 483.9059 | 554.7496 | 566.9772 | 499.3442
2293.0354 | 636.8226 | 283.4413 | 535.1606 | 484.2123 | 552.1823 | 572.0471 | 499.2623
2294.0354 | 634.9591 | 283.5343 | 534.2597 | 484.7015 | 550.1056 | 566.9414 | 500.2989
2295.0354 | 636.4192 | 283.5914 | 534.1237 | 484.3254 | 548.5908 | 567.6488 | 499.2015
2296.0354 | 637.7457 | 283.75 | 534.141 | 484.5743 | 548.2829 | 569.2567 | 499.6284
2297.0354 | 639.9413 | 284.215 | 534.1704 | 485.2074 | 548.9433 | 571.9037 | 501.6113
2298.0354 | 641.5965 | 284.1705 | 533.8705 | 485.3384 | 549.8215 | 571.876 | 503.206
2299.0354 | 642.5868 | 284.2612 | 533.6664 | 484.5835 | 549.6493 | 575.4839 | 505.1023
2300.0354 | 641.6631 | 284.6507 | 534.5078 | 484.4526 | 548.197 | 574.6284 | 505.7567
2301.0354 | 644.4008 | 285.0618 | 537.3425 | 484.678 | 546.1476 | 576.816 | 508.0183
2302.0354 | 644.8113 | 285.1407 | 536.1535 | 485.0686 | 546.0117 | 578.5367 | 508.9807
2303.0354 | 641.9697 | 285.2593 | 536.8132 | 484.9437 | 546.5329 | 575.5036 | 508.8128
2304.0354 | 640.1592 | 285.3581 | 536.8189 | 484.8567 | 548.9142 | 572.0465 | 507.9503
2305.0354 | 637.7638 | 285.8674 | 536.3299 | 484.9935 | 550.9256 | 569.9112 | 508.3161
2306.0354 | 634.7094 | 286.2662 | 536.433 | 484.6559 | 550.6112 | 568.7057 | 506.8976
2307.0354 | 631.7226 | 285.9479 | 535.7746 | 484.4858 | 549.3269 | 565.1914 | 506.3401
2308.0354 | 631.9775 | 285.9413 | 536.676 | 484.5238 | 549.4093 | 565.5013 | 503.2581
2309.0354 | 632.6828 | 286.0996 | 536.0071 | 485.2199 | 550.4976 | 567.4599 | 505.1272
2310.0354 | 634.8584 | 286.2382 | 535.6117 | 484.6416 | 551.3564 | 568.1541 | 508.32
2311.0354 | 634.6859 | 286.9973 | 535.8171 | 485.3434 | 552.3477 | 566.7578 | 507.7149
2312.0354 | 635.6488 | 286.4673 | 536.9453 | 484.8109 | 553.2535 | 567.171 | 510.0675
2313.0354 | 632.7831 | 286.5515 | 536.6574 | 485.0605 | 552.987 | 563.7331 | 509.4487
2314.0354 | 630.2735 | 287.2982 | 537.7446 | 484.9153 | 551.7335 | 559.2228 | 508.4835
2315.0354 | 631.5178 | 287.2596 | 537.1382 | 484.6922 | 551.3528 | 562.499 | 509.4145
2316.0354 | 639.0289 | 287.5626 | 537.5085 | 484.6054 | 551.0019 | 563.7924 | 511.1966
2317.0354 | 642.0227 | 287.5053 | 536.9256 | 484.5286 | 550.8216 | 566.4584 | 513.0812
2318.0354 | 642.1309 | 287.5652 | 537.082 | 485.0874 | 550.8891 | 566.6223 | 510.0545
2319.0354 | 642.03 | 287.8755 | 537.1832 | 484.7001 | 552.115 | 567.0647 | 513.6878
2320.0354 | 643.8267 | 288.0338 | 537.0559 | 484.2969 | 553.2227 | 568.5165 | 514.3361
2321.0354 | 644.0701 | 288.4158 | 537.0505 | 484.3689 | 551.6331 | 567.2212 | 513.1911
2322.0354 | 642.8162 | 288.6278 | 536.9548 | 484.3855 | 551.7727 | 566.0833 | 512.9184
2323.0354 | 644.6899 | 288.6952 | 537.1854 | 484.2697 | 550.1929 | 571.6697 | 515.3602
2324.0354 | 646.5714 | 288.7166 | 537.1496 | 484.2501 | 548.9652 | 576.2248 | 515.2746
2325.0354 | 648.641 | 288.6526 | 536.4934 | 484.3934 | 546.487 | 576.2433 | 516.8624
2326.0354 | 651.882 | 288.7462 | 536.3962 | 483.9725 | 545.8264 | 573.6565 | 515.1222
2327.0354 | 652.2933 | 288.9071 | 537.0921 | 484.0609 | 546.6717 | 574.6158 | 514.5068
2328.0354 | 650.0404 | 289.015 | 536.8195 | 484.0672 | 547.4509 | 571.9753 | 514.0071
2329.0354 | 647.4918 | 289.0935 | 536.7815 | 484.066 | 549.5612 | 576.5764 | 514.5677
2330.0354 | 644.4818 | 289.8118 | 537.4857 | 484.3722 | 550.4434 | 573.274 | 514.2645
2331.0354 | 642.1798 | 289.7086 | 536.8236 | 484.0881 | 553.3016 | 570.8176 | 514.57
2332.0354 | 643.4781 | 289.6862 | 536.3547 | 484.3636 | 554.4391 | 575.3933 | 511.4046
2333.0354 | 647.614 | 289.7838 | 536.7935 | 484.2853 | 554.463 | 577.0388 | 516.6638
2334.0354 | 648.8851 | 289.843 | 536.3322 | 484.002 | 555.5094 | 574.5621 | 515.2137
2335.0354 | 651.5259 | 290.0214 | 536.4544 | 484.5193 | 553.8921 | 567.1431 | 512.8545
2336.0354 | 655.507 | 290.2233 | 536.7966 | 484.6548 | 553.2133 | 570.7556 | 512.937
2337.0354 | 655.8532 | 290.5375 | 537.1318 | 486.4438 | 554.8219 | 568.5899 | 512.325
2338.0354 | 652.995 | 290.8012 | 537.4146 | 484.8563 | 557.0255 | 566.6972 | 508.558
2339.0354 | 651.7211 | 291.1098 | 538.3246 | 484.6866 | 556.402 | 565.6318 | 509.4973
2340.0354 | 648.563 | 291.0921 | 536.9514 | 484.3469 | 557.6654 | 567.5324 | 510.5705
2341.0354 | 649.7226 | 291.2007 | 536.6586 | 484.6017 | 561.0185 | 573.0231 | 511.6113
2342.0354 | 651.5415 | 291.4262 | 536.6641 | 484.3837 | 561.4969 | 571.8957 | 512.6184
2343.0354 | 652.0708 | 291.4375 | 536.6889 | 484.5242 | 560.4311 | 570.6262 | 514.7435
2344.0354 | 649.6916 | 291.6031 | 536.6332 | 485.0102 | 561.301 | 570.379 | 515.1475
2345.0354 | 648.2999 | 292.6908 | 536.7964 | 484.8422 | 562.319 | 568.2479 | 514.4849
2346.0354 | 647.4524 | 293.9609 | 537.1503 | 484.9703 | 562.6561 | 565.6676 | 512.7249
2347.0354 | 646.1725 | 296.2907 | 538.0414 | 485.2634 | 564.6542 | 564.8582 | 510.3228
2348.0354 | 647.5224 | 297.6139 | 537.8819 | 485.4339 | 565.6756 | 564.6572 | 509.8261
2349.0354 | 645.392 | 292.3003 | 535.9271 | 484.6092 | 563.5962 | 563.8481 | 514.2822
2350.0354 | 648.1084 | 293.0928 | 536.2531 | 485.1476 | 564.0674 | 562.7919 | 512.8718
2351.0354 | 649.4306 | 292.5616 | 535.8524 | 484.9081 | 564.917 | 563.1435 | 513.0286
2352.0354 | 650.3782 | 292.8391 | 537.6707 | 484.8142 | 564.5702 | 564.5373 | 513.7958
2353.0354 | 648.9691 | 293.0006 | 537.4498 | 484.5622 | 565.6475 | 566.8488 | 515.0284
2354.0354 | 649.0365 | 293.0176 | 537.2658 | 484.5881 | 564.9508 | 565.9369 | 517.9033
2355.0354 | 647.5071 | 293.1696 | 536.9244 | 484.6721 | 565.1989 | 565.7373 | 518.7822
2356.0354 | 645.1492 | 293.179 | 536.7686 | 484.756 | 566.8194 | 561.664 | 516.7091
2357.0354 | 648.0406 | 293.3137 | 537.4322 | 484.5053 | 568.6051 | 561.5385 | 517.8544
2358.0354 | 650.1862 | 293.5038 | 536.5181 | 484.7222 | 568.9543 | 560.142 | 518.241
2359.0354 | 653.6761 | 293.7291 | 536.4815 | 484.2906 | 567.9649 | 562.1555 | 518.8115
2360.0354 | 655.2441 | 293.9247 | 536.535 | 484.532 | 567.7584 | 564.832 | 519.0143
2361.0354 | 657.6379 | 293.975 | 536.4649 | 484.1802 | 565.7886 | 566.9277 | 518.7118
2362.0354 | 659.0324 | 294.0906 | 536.1851 | 484.5052 | 563.6089 | 567.895 | 519.6952
2363.0354 | 662.9127 | 294.346 | 535.7059 | 484.3117 | 562.0349 | 569.1911 | 516.625
2364.0354 | 663.3421 | 294.4937 | 535.8845 | 484.2074 | 560.56 | 569.0076 | 517.8072
2365.0354 | 658.5105 | 294.7123 | 536.9919 | 484.4279 | 558.8425 | 566.6727 | 516.18
2366.0354 | 653.1527 | 294.9548 | 538.5065 | 484.4404 | 559.3357 | 562.4952 | 514.1894
2367.0354 | 651.7935 | 295.0803 | 538.0274 | 484.1235 | 559.224 | 559.3947 | 512.1281
2368.0354 | 647.4538 | 295.3679 | 537.3699 | 484.0839 | 559.9001 | 559.4154 | 511.4929
2369.0354 | 643.4585 | 295.3036 | 536.6305 | 484.5495 | 560.0638 | 557.5402 | 509.0645
2370.0354 | 648.6372 | 295.27 | 536.5296 | 484.9912 | 562.0242 | 561.0516 | 512.3573
2371.0354 | 650.9918 | 295.4866 | 536.5143 | 484.2436 | 562.3978 | 560.2714 | 512.0088
2372.0354 | 653.1388 | 295.7627 | 536.4075 | 483.8196 | 560.6034 | 566.2851 | 513.8509
2373.0354 | 655.882 | 295.7386 | 536.5271 | 483.7764 | 560.6086 | 568.2704 | 513.7272
2374.0354 | 655.7026 | 295.82 | 536.9763 | 484.0815 | 557.336 | 569.448 | 511.9976
2375.0354 | 653.2815 | 295.9573 | 536.7505 | 484.4358 | 557.9844 | 567.7071 | 512.1782
2376.0823 | 651.7308 | 296.0405 | 537.3405 | 484.1478 | 557.8259 | 563.9486 | 509.4733
2377.0354 | 649.9451 | 296.1698 | 537.1286 | 484.0105 | 557.6752 | 562.3711 | 508.5685
2378.0354 | 651.899 | 296.4205 | 537.1054 | 483.8714 | 558.8416 | 564.5439 | 508.9654
2379.0354 | 651.4013 | 296.5213 | 537.3747 | 484.7199 | 559.524 | 563.7794 | 508.3496
2380.0354 | 649.6073 | 296.639 | 536.3506 | 484.4564 | 559.0506 | 561.4889 | 505.498
2381.0354 | 653.3344 | 296.7623 | 538.2395 | 484.7059 | 560.3449 | 560.3218 | 503.669
2382.0354 | 654.3856 | 297.0738 | 538.1957 | 484.5448 | 560.5502 | 558.3336 | 507.8299
2383.0354 | 658.5625 | 297.294 | 537.4618 | 484.5859 | 562.4449 | 556.2209 | 507.4648
2384.0354 | 661.8545 | 297.4691 | 538.1481 | 484.2257 | 563.99 | 558.2462 | 508.5068
2385.0354 | 660.662 | 297.8332 | 537.8605 | 484.5679 | 564.0767 | 558.7743 | 508.8082
2386.0354 | 658.1823 | 297.9536 | 537.753 | 484.814 | 563.8717 | 556.7865 | 509.8349
2387.0354 | 655.0807 | 297.962 | 537.3349 | 485.2088 | 562.0342 | 557.5323 | 509.3136
2388.0354 | 653.1371 | 298.3829 | 538.4382 | 484.643 | 560.8468 | 557.4105 | 512.402
2389.0354 | 653.5756 | 298.5991 | 537.7959 | 484.3196 | 560.0119 | 557.4472 | 513.4866
2390.0354 | 653.4239 | 298.591 | 537.4885 | 483.9172 | 557.9224 | 561.4382 | 516.8688
2391.0354 | 655.7806 | 298.6564 | 537.8537 | 484.1771 | 556.2429 | 562.8643 | 516.8774
2392.0354 | 656.7811 | 298.8717 | 537.8095 | 484.25 | 554.7586 | 564.1788 | 516.2826
2393.0354 | 653.5018 | 298.7776 | 537.7364 | 484.3521 | 553.8713 | 561.8637 | 514.8168
2394.0354 | 655.5973 | 298.8931 | 537.7727 | 484.0577 | 553.7013 | 562.9072 | 514.6967
2395.0354 | 655.8984 | 299.1389 | 538.2413 | 483.7628 | 553.9955 | 566.9623 | 516.8648
2396.0354 | 652.2895 | 299.4328 | 538.2195 | 484.445 | 554.5047 | 566.4086 | 516.6317
2397.0354 | 653.365 | 299.3268 | 539.1429 | 484.4237 | 555.0391 | 567.8667 | 515.8192
2398.0354 | 652.7761 | 299.5006 | 538.8448 | 484.4856 | 553.9817 | 566.0119 | 516.8676
2399.0354 | 649.8669 | 299.5629 | 537.7542 | 484.8865 | 555.2637 | 565.3212 | 516.7977
2400.0354 | 651.0568 | 299.6369 | 537.826 | 484.5512 | 557.5198 | 566.5278 | 515.8596
2401.0354 | 650.913 | 299.7349 | 538.0562 | 483.7893 | 558.7661 | 564.2326 | 516.8814
2402.0354 | 652.6827 | 300.0579 | 538.0836 | 484.5145 | 558.1507 | 564.6 | 518.9287
2403.0354 | 656.3029 | 300.2215 | 538.0472 | 483.9861 | 557.1247 | 564.6283 | 519.0801
2404.0354 | 657.7215 | 300.3698 | 537.9574 | 483.9932 | 556.2253 | 567.4104 | 520.3595
2405.0354 | 658.1234 | 300.422 | 538.8021 | 483.6537 | 556.3454 | 569.2526 | 519.0055
2406.0354 | 661.085 | 300.5202 | 537.8467 | 484.1317 | 555.6709 | 573.81 | 519.1572
2407.0354 | 664.966 | 300.9123 | 538.2829 | 483.7669 | 554.4182 | 577.016 | 520.8631
2408.0354 | 663.0046 | 301.2051 | 538.7352 | 483.6696 | 554.6435 | 578.14 | 522.4067
2409.0354 | 662.6503 | 301.1321 | 538.102 | 483.8373 | 552.5192 | 576.5855 | 519.698
2410.0354 | 663.0671 | 301.3475 | 538.23 | 483.9524 | 552.6546 | 573.6416 | 520.8843
2411.0354 | 665.4346 | 301.1661 | 538.0686 | 483.9919 | 553.6986 | 571.8173 | 519.5149
2412.0354 | 666.0301 | 301.3309 | 539.6291 | 484.0101 | 554.3492 | 570.8768 | 521.701
2413.0354 | 662.3983 | 301.4253 | 540.3186 | 484.6578 | 554.3516 | 568.8093 | 520.1941
2414.0354 | 658.233 | 301.6682 | 540.8118 | 483.9122 | 553.5724 | 566.2897 | 520.2596
2415.0354 | 656.0349 | 301.7585 | 540.2274 | 483.8276 | 553.4641 | 563.7597 | 518.272
2416.0354 | 654.6812 | 301.8891 | 540.3009 | 483.6053 | 552.7365 | 564.9373 | 519.5112
2417.0354 | 656.2116 | 302.2511 | 542.393 | 483.9915 | 551.9628 | 562.7057 | 519.457
2418.0354 | 656.6222 | 302.24 | 542.2981 | 483.8107 | 551.4411 | 558.4335 | 517.6785
2419.0354 | 658.3288 | 302.3374 | 541.8908 | 483.7137 | 549.8099 | 557.7246 | 521.1895
2420.0354 | 659.16 | 302.6329 | 541.6305 | 483.8759 | 549.0297 | 558.227 | 522.5391
2421.0354 | 660.2248 | 302.8042 | 542.3271 | 484.0708 | 549.8983 | 558.2853 | 523.2487
2422.0354 | 659.9475 | 303.0416 | 542.9189 | 483.8352 | 550.2143 | 559.3041 | 521.1203
2423.0354 | 659.1328 | 303.4546 | 543.7315 | 484.0069 | 549.5141 | 557.1819 | 520.0609
2424.0354 | 659.1145 | 303.6029 | 543.7456 | 483.5259 | 549.5532 | 557.9353 | 520.0855
2425.0354 | 659.5382 | 303.6711 | 544.2624 | 483.5816 | 547.8531 | 558.0442 | 522.9966
2426.0354 | 659.6273 | 303.9443 | 543.798 | 483.4991 | 547.1691 | 557.8583 | 523.9291
2427.0354 | 658.8128 | 304.5486 | 545.9698 | 483.5275 | 548.0913 | 557.0286 | 522.7184
2428.0354 | 658.2423 | 304.8502 | 547.8998 | 483.7598 | 548.5512 | 560.2306 | 524.3772
2429.0354 | 657.3069 | 304.6719 | 546.7284 | 483.4886 | 547.4075 | 561.6851 | 524.7361
2430.0354 | 657.2951 | 304.7117 | 547.8897 | 483.6361 | 548.0112 | 559.6795 | 524.6949
2431.0354 | 656.6432 | 305.204 | 547.8796 | 483.6338 | 549.5679 | 559.0899 | 525.0493
2432.0354 | 655.3989 | 305.7554 | 547.4702 | 483.7304 | 551.5728 | 559.0653 | 524.9056
2433.0354 | 651.0955 | 305.718 | 547.5819 | 483.2681 | 551.5422 | 558.6168 | 525.2494
2434.0354 | 647.1943 | 305.5979 | 547.634 | 483.7705 | 550.6699 | 557.1933 | 524.8758
2435.0354 | 644.4029 | 305.5364 | 547.6488 | 483.4501 | 550.0911 | 555.5226 | 523.5742
2436.0354 | 642.7206 | 305.795 | 549.1468 | 483.219 | 549.6843 | 555.5347 | 522.7487
2437.0354 | 642.1813 | 306.4331 | 549.8193 | 483.165 | 548.3912 | 556.6001 | 525.033
2438.0354 | 644.9962 | 306.9704 | 550.3768 | 483.4749 | 546.8084 | 557.216 | 526.2327
2439.0354 | 649.1354 | 306.6032 | 551.1681 | 483.0525 | 546.5266 | 554.8503 | 526.6113
2440.0354 | 648.0426 | 306.8708 | 550.9837 | 483.6863 | 545.2684 | 551.1089 | 523.7991
2441.0354 | 646.928 | 307.1409 | 551.7337 | 483.0915 | 544.7447 | 550.0195 | 522.6333
2442.0354 | 646.0899 | 307.4805 | 552.2466 | 483.5192 | 544.6065 | 548.177 | 521.4263
2443.0354 | 647.2699 | 307.9934 | 550.8872 | 483.1078 | 544.2191 | 548.8265 | 521.4189
2444.0354 | 646.5117 | 308.1695 | 550.5502 | 483.3885 | 544.9676 | 549.6581 | 522.8397
2445.0354 | 646.8552 | 308.0401 | 551.2401 | 483.2285 | 544.012 | 549.4323 | 520.3416
2446.0354 | 646.788 | 308.3742 | 552.5051 | 482.8572 | 543.8078 | 550.3389 | 521.6027
2447.0354 | 651.5158 | 309.5113 | 553.2433 | 482.7147 | 542.8549 | 548.6861 | 521.9427
2448.0354 | 652.8347 | 309.0278 | 552.8404 | 482.7183 | 541.4533 | 550.3826 | 523.2406
2449.0354 | 651.2516 | 308.5957 | 552.9222 | 482.5281 | 540.4004 | 550.3823 | 525.9095
2450.0354 | 653.1713 | 308.7176 | 552.1883 | 482.2866 | 540.0587 | 553.1422 | 527.3013
2451.0354 | 655.9453 | 308.9727 | 552.6592 | 482.2624 | 540.307 | 556.3299 | 528.5938
2452.0354 | 656.7341 | 309.2508 | 553.3648 | 482.2278 | 539.3625 | 558.9282 | 528.6435
2453.0354 | 657.2989 | 309.2329 | 552.6962 | 482.1287 | 539.3579 | 562.8616 | 529.4861
2454.0354 | 658.9882 | 309.0711 | 552.4916 | 482.0595 | 539.59 | 566.81 | 531.147
2455.0354 | 660.4132 | 309.1595 | 552.7071 | 481.9118 | 540.7289 | 569.7475 | 532.0993
2456.0354 | 662.6282 | 309.4199 | 552.9767 | 482.6238 | 540.6701 | 573.6161 | 530.9047
2457.0354 | 663.1236 | 309.5806 | 552.7576 | 482.3101 | 541.0235 | 571.346 | 530.7213
2458.0354 | 661.6997 | 309.7711 | 553.3756 | 482.0616 | 541.3527 | 570.9969 | 531.7417
2459.0354 | 660.7831 | 309.8611 | 553.0891 | 481.7544 | 542.1191 | 571.8599 | 532.7226
2460.0354 | 661.6421 | 310.0218 | 553.1202 | 481.5808 | 542.2099 | 574.4389 | 531.652
2461.0354 | 663.4967 | 310.2241 | 552.892 | 481.6592 | 542.9293 | 578.9087 | 533.3097
2462.0354 | 664.2014 | 310.3267 | 552.5473 | 481.8532 | 543.2105 | 574.9733 | 533.4872
2463.0354 | 662.6599 | 310.3768 | 552.8047 | 482.1572 | 543.3258 | 571.0625 | 532.4691
2464.0354 | 662.6756 | 310.7522 | 553.1956 | 481.9209 | 543.9701 | 566.8297 | 531.092
2465.0354 | 662.8182 | 310.5278 | 553.0993 | 481.4007 | 545.2832 | 570.6538 | 532.1452
2466.0354 | 664.5151 | 310.6773 | 552.7326 | 481.3822 | 545.7515 | 572.1591 | 533.9321
2467.0354 | 667.2822 | 310.7914 | 552.7553 | 481.5389 | 546.0373 | 573.7208 | 533.1767
2468.0354 | 667.5637 | 310.8639 | 552.6636 | 482.175 | 547.7193 | 572.6227 | 531.1929
2469.0354 | 666.5975 | 311.0471 | 552.614 | 481.7187 | 550.4488 | 570.922 | 530.0737
2470.0354 | 665.9795 | 311.3182 | 553.0046 | 481.6034 | 551.1923 | 569.1303 | 530.2799
2471.0354 | 664.7805 | 311.4796 | 553.3082 | 481.5724 | 551.5157 | 569.3208 | 532.2683
2472.0354 | 664.4811 | 311.7529 | 553.291 | 481.6088 | 551.8182 | 567.4011 | 533.6551
2473.0354 | 662.8814 | 311.9377 | 552.9766 | 481.6807 | 553.2488 | 567.028 | 532.8712
2474.0354 | 661.0789 | 312.031 | 553.8563 | 481.5864 | 554.7506 | 569.0764 | 534.308
2475.0354 | 654.9185 | 312.2088 | 554.2014 | 481.3446 | 555.1536 | 568.5574 | 533.9941
2476.0354 | 653.8719 | 312.2787 | 553.9183 | 481.3478 | 554.1223 | 568.4383 | 533.1925
2477.0354 | 656.3745 | 312.313 | 553.3943 | 481.2626 | 556.1795 | 572.9562 | 535.6979
2478.0354 | 656.7669 | 312.5182 | 553.7511 | 481.22 | 557.9892 | 571.3826 | 536.3509
2479.0354 | 657.3811 | 312.7213 | 555.1712 | 481.2483 | 559.242 | 571.7467 | 536.9838
2480.0354 | 655.6776 | 313.0358 | 555.1089 | 481.1952 | 562.0464 | 569.1859 | 536.3331
2481.0354 | 653.9831 | 313.028 | 555.159 | 480.9849 | 563.7696 | 567.5548 | 535.6354
2482.0354 | 655.5945 | 312.9897 | 554.7919 | 481.2892 | 568.3695 | 565.5001 | 535.5096
2483.0354 | 656.452 | 313.3987 | 555.6375 | 481.4048 | 568.6433 | 565.9664 | 536.991
2484.0354 | 654.7111 | 313.5079 | 556.8042 | 481.2756 | 568.4158 | 565.6034 | 539.2317
2485.0354 | 655.3642 | 313.8049 | 556.075 | 481.7967 | 567.0857 | 563.2699 | 539.1987
2486.0354 | 656.4176 | 313.965 | 556.3331 | 481.4949 | 568.31 | 565.0424 | 540.0865
2487.0354 | 657.0157 | 314.2589 | 556.8872 | 481.3179 | 570.2162 | 565.7889 | 540.8499
2488.0354 | 661.0095 | 314.4958 | 558.0708 | 481.414 | 574.7328 | 568.536 | 543.3031
2489.0354 | 662.609 | 314.6588 | 557.913 | 481.4319 | 576.4526 | 569.4815 | 543.2213
2490.0354 | 661.7161 | 314.5534 | 559.096 | 481.4229 | 580.7932 | 567.3843 | 546.1863
2491.0354 | 661.1571 | 315.5141 | 559.7338 | 481.2438 | 584.6964 | 569.6609 | 551.8695
2492.0354 | 661.046 | 315.5552 | 559.9087 | 481.5638 | 587.3578 | 568.6674 | 553.0251
2493.0354 | 659.3129 | 315.3835 | 559.8723 | 481.7937 | 591.8977 | 568.3972 | 554.4608
2494.0354 | 656.3971 | 315.2926 | 558.3927 | 481.2364 | 596.0211 | 566.4991 | 553.8951
2495.0354 | 660.4949 | 315.3081 | 558.6993 | 481.4709 | 596.2454 | 568.9437 | 553.1791
2496.0354 | 659.0358 | 315.3498 | 559.3091 | 481.2257 | 595.2571 | 572.8455 | 553.8466
2497.0354 | 655.1131 | 315.8423 | 559.1511 | 481.2151 | 596.4068 | 571.8369 | 552.5123
2498.0354 | 657.1308 | 316.2431 | 559.1455 | 481.2423 | 597.1976 | 574.3032 | 550.45
2499.0354 | 656.4816 | 316.4873 | 559.8788 | 481.8424 | 597.8641 | 571.9818 | 551.0607
2500.0354 | 654.9871 | 316.4978 | 560.3732 | 481.389 | 597.1979 | 569.2178 | 548.3118
2501.0354 | 654.6651 | 317.4315 | 560.6811 | 481.185 | 597.3683 | 567.1096 | 548.0342
2502.0354 | 657.1319 | 317.4279 | 560.9737 | 481.5161 | 596.4982 | 569.6121 | 548.9193
2503.0354 | 658.8692 | 317.5581 | 561.7747 | 481.402 | 596.7981 | 570.8074 | 549.5178
2504.0354 | 660.613 | 317.8331 | 562.5971 | 481.3473 | 597.967 | 572.0383 | 549.1992
2505.0354 | 662.4993 | 317.7973 | 563.1629 | 481.4696 | 597.6599 | 575.8304 | 546.7397
2506.0354 | 662.6506 | 318.0638 | 562.9683 | 481.3471 | 598.3927 | 579.7763 | 549.7023
2507.0354 | 663.4708 | 318.0224 | 564.2948 | 481.2631 | 600.6132 | 582.1181 | 548.2645
2508.0354 | 659.7572 | 318.1136 | 564.8089 | 481.3342 | 597.706 | 579.7368 | 547.3704
2509.0354 | 660.3851 | 318.2071 | 564.7253 | 481.8413 | 598.2794 | 577.4402 | 546.9803
2510.0354 | 659.9048 | 318.3389 | 564.1654 | 481.7221 | 600.1198 | 574.8322 | 548.4044
2511.0354 | 660.0848 | 318.5219 | 564.3884 | 481.3348 | 600.7829 | 578.2226 | 550.2055
2512.0354 | 657.2319 | 318.6931 | 564.5809 | 481.4008 | 599.7488 | 577.6609 | 549.8722
2513.0354 | 657.0916 | 319.173 | 565.9504 | 481.5582 | 601.0112 | 577.1214 | 549.34
2514.0354 | 654.8714 | 319.1804 | 566.5911 | 481.4047 | 599.5441 | 574.5449 | 548.8611
2515.0354 | 652.0513 | 319.2103 | 566.3719 | 481.7494 | 599.8277 | 572.331 | 547.484
2516.0354 | 653.9556 | 319.4438 | 566.2889 | 481.4027 | 598.7273 | 570.4479 | 546.3955
2517.0354 | 654.4065 | 319.6527 | 566.8278 | 481.6931 | 597.3176 | 570.2248 | 545.8911
2518.0354 | 652.987 | 320.0266 | 566.9507 | 481.9086 | 595.6262 | 567.5394 | 543.4202
2519.0354 | 652.9085 | 320.1119 | 566.6989 | 482.2348 | 593.404 | 566.7648 | 552.62
2520.0354 | 650.4259 | 320.1094 | 566.6658 | 481.9154 | 592.6366 | 566.2625 | 551.5191
2521.0354 | 646.6876 | 320.1581 | 566.4624 | 481.9645 | 592.8201 | 568.166 | 550.9338
2522.0354 | 646.878 | 320.2499 | 566.1586 | 483.0002 | 593.5824 | 567.5417 | 550.1755
2523.0354 | 644.8243 | 320.1703 | 566.2347 | 482.7116 | 592.446 | 565.7929 | 548.1477
2524.0354 | 643.095 | 320.5267 | 567.716 | 482.9926 | 593.1312 | 562.8072 | 547.4591
2525.0354 | 643.7598 | 320.5254 | 568.4428 | 483.1459 | 590.4859 | 562.8894 | 548.4408
2526.0354 | 642.5967 | 320.7457 | 567.9888 | 483.2016 | 587.7271 | 560.4148 | 549.1709
2527.0354 | 642.4979 | 320.8449 | 567.9048 | 483.2314 | 585.1234 | 558.4074 | 551.6525
2528.0354 | 641.7119 | 320.8693 | 567.9128 | 482.6645 | 583.1939 | 557.7663 | 552.0419
2529.0354 | 640.4407 | 321.532 | 569.4777 | 482.541 | 581.266 | 560.0373 | 551.9382
2530.0354 | 640.5413 | 321.6726 | 569.1547 | 482.5739 | 581.5141 | 562.8881 | 551.8826
2531.0354 | 641.0945 | 321.4288 | 569.1579 | 482.7184 | 580.383 | 562.9307 | 549.1792
2532.0354 | 644.5118 | 321.4234 | 568.3036 | 482.7441 | 580.1355 | 564.3036 | 549.0909
2533.0354 | 646.8595 | 321.4282 | 568.7979 | 482.7601 | 577.1809 | 565.6254 | 549.5274
2534.0354 | 647.9297 | 321.8323 | 569.5068 | 482.6426 | 574.8934 | 566.9475 | 550.06
2535.0354 | 647.3068 | 321.9873 | 570.008 | 483.2425 | 573.0648 | 567.4411 | 549.8861
2536.0354 | 648.0175 | 322.8525 | 571.2821 | 483.4933 | 572.7069 | 564.8648 | 549.3441
2537.0354 | 647.2675 | 322.9566 | 572.1288 | 483.0635 | 573.4754 | 562.6083 | 547.2401
2538.0354 | 650.1289 | 322.824 | 571.6479 | 483.0699 | 572.5182 | 566.1993 | 546.8889
2539.0354 | 649.1294 | 322.916 | 571.4056 | 483.067 | 571.6679 | 565.9954 | 546.1356
2540.0354 | 646.422 | 323.0574 | 570.9118 | 482.7568 | 571.6692 | 564.0375 | 544.064
2541.0354 | 646.2377 | 322.9227 | 570.7794 | 483.0444 | 570.4398 | 565.7868 | 542.9076
2542.0354 | 648.1204 | 323.2369 | 570.8247 | 483.0337 | 568.7802 | 565.3821 | 543.5628
2543.0354 | 649.3919 | 323.31 | 573.0567 | 484.0407 | 569.6071 | 565.0576 | 543.4789
2544.0354 | 648.3904 | 323.3675 | 572.4043 | 483.7398 | 569.0176 | 560.5036 | 541.9306
2545.0354 | 647.2221 | 324.0274 | 571.2353 | 484.2756 | 572.0217 | 559.8032 | 541.7569
2546.0354 | 644.0535 | 323.954 | 572.5902 | 483.4462 | 572.6825 | 560.114 | 542.197
2547.0354 | 637.9657 | 323.8703 | 572.4002 | 483.1645 | 571.2377 | 561.3268 | 539.8382
2548.0354 | 638.1238 | 324.0904 | 572.3914 | 483.2075 | 577.5519 | 558.8599 | 539.2548
2549.0354 | 641.4122 | 323.9548 | 572.0872 | 483.069 | 576.4753 | 563.1402 | 541.4666
2550.0354 | 642.863 | 324.2029 | 572.7611 | 483.24 | 571.7748 | 563.2758 | 541.0055
2551.0354 | 643.6903 | 324.4059 | 572.624 | 483.2471 | 569.0694 | 560.8189 | 538.8241
2552.0354 | 645.3171 | 324.391 | 571.6463 | 483.2216 | 566.4256 | 561.5386 | 536.6968
2553.0354 | 648.7191 | 324.5574 | 571.1488 | 483.1327 | 567.3562 | 561.5948 | 536.7881
2554.0354 | 649.8613 | 324.5297 | 571.3106 | 483.3184 | 567.2842 | 560.2993 | 536.1174
2555.0354 | 652.4271 | 324.5279 | 571.7321 | 483.1794 | 568.5102 | 558.6186 | 534.1505
2556.0354 | 651.5305 | 324.7621 | 571.9921 | 483.1486 | 568.6618 | 561.7132 | 534.7746
2557.0354 | 652.094 | 325.1915 | 571.9557 | 483.1146 | 568.8897 | 565.4418 | 538.0899
2558.0354 | 651.2222 | 325.4023 | 572.0207 | 483.1047 | 565.8273 | 573.1131 | 540.8255
2559.0354 | 652.1535 | 325.7098 | 572.5125 | 483.2883 | 562.3473 | 573.9468 | 540.9952
2560.0354 | 655.5849 | 325.6978 | 572.1876 | 483.0516 | 563.2753 | 573.1135 | 545.399
2561.0354 | 657.0605 | 325.7507 | 572.1111 | 483.4583 | 562.5335 | 571.993 | 544.0693
2562.0354 | 658.4568 | 325.7531 | 572.9195 | 483.6999 | 561.4203 | 568.1294 | 543.774
2563.0354 | 657.948 | 325.7805 | 574.0964 | 483.4981 | 560.7079 | 568.2575 | 541.7266
2564.0354 | 656.9666 | 326.2935 | 575.5268 | 483.1924 | 559.6236 | 567.2946 | 542.1604
2565.0354 | 662.1625 | 326.5218 | 576.4164 | 483.2555 | 559.3832 | 568.6658 | 543.7103
2566.0354 | 664.318 | 326.8839 | 576.1883 | 483.4554 | 559.0958 | 569.2891 | 545.4482
2567.0354 | 666.5024 | 326.8461 | 576.8247 | 483.4526 | 558.5588 | 568.8235 | 547.3491
2568.0354 | 665.3682 | 326.7877 | 576.472 | 483.4112 | 558.1702 | 566.1347 | 548.0083
2569.0354 | 661.3675 | 326.8498 | 575.9388 | 483.204 | 556.3685 | 563.0288 | 545.2745
2570.0354 | 658.8199 | 327.0285 | 575.7164 | 483.0218 | 555.8814 | 561.4065 | 543.0661
2571.0354 | 657.8644 | 327.1643 | 576.6521 | 483.3145 | 553.522 | 561.8724 | 543.4262
2572.0354 | 656.8596 | 327.0496 | 577.2399 | 483.1594 | 552.0588 | 561.4314 | 543.6823
2573.0354 | 655.6128 | 327.0567 | 576.5563 | 482.9186 | 551.0027 | 562.0197 | 546.1953
2574.0354 | 655.1956 | 327.1494 | 576.0159 | 483.025 | 549.6081 | 561.2328 | 546.6714
2575.0354 | 651.2998 | 327.304 | 577.4866 | 482.983 | 550.4072 | 560.3097 | 546.3554
2576.0354 | 647.8359 | 327.7579 | 579.0449 | 483.2006 | 549.3542 | 559.6214 | 547.0948
2577.0354 | 647.2519 | 328.4646 | 579.7311 | 483.2116 | 551.9384 | 559.8896 | 546.3769
2578.0354 | 649.7576 | 328.2024 | 578.6883 | 482.7836 | 554.2432 | 559.4209 | 547.1293
2579.0354 | 652.6642 | 328.515 | 577.8841 | 482.8677 | 555.6981 | 559.3682 | 545.5609
2580.0354 | 653.3853 | 328.4694 | 577.2985 | 483.2857 | 560.5063 | 560.6799 | 544.2944
2581.0354 | 655.4756 | 328.3251 | 576.9889 | 483.294 | 562.0552 | 560.4113 | 543.7829
2582.0354 | 653.7169 | 328.539 | 577.289 | 483.3307 | 563.0761 | 559.2751 | 542.3099
2583.0354 | 654.8775 | 328.6749 | 577.0112 | 483.2672 | 564.3123 | 556.9955 | 541.0427
2584.0354 | 656.9031 | 328.7773 | 577.0241 | 484.1926 | 564.4617 | 556.0106 | 539.5346
2585.0354 | 654.4295 | 328.992 | 577.3265 | 483.4105 | 563.2723 | 553.9477 | 538.1788
2586.0354 | 651.5039 | 329.0798 | 577.7909 | 483.5033 | 560.9953 | 551.4814 | 537.0999
2587.0354 | 646.629 | 329.2448 | 577.5954 | 483.1129 | 558.1007 | 552.0633 | 537.4719
2588.0354 | 643.7574 | 329.748 | 577.5187 | 483.1104 | 556.0631 | 551.853 | 537.6054
2589.0354 | 644.1429 | 329.7439 | 577.636 | 482.8567 | 554.444 | 553.0033 | 537.7495
2590.0354 | 642.6773 | 329.7124 | 577.4344 | 483.3795 | 552.2533 | 553.2096 | 537.1073
2591.0354 | 646.6901 | 329.9443 | 577.0763 | 483.3279 | 550.8568 | 555.3067 | 537.8595
2592.0354 | 648.2371 | 329.8912 | 576.9002 | 483.0819 | 548.1951 | 555.105 | 537.9429
2593.0354 | 646.836 | 329.9147 | 576.4714 | 483.2933 | 546.6343 | 555.0262 | 536.6351
2594.0354 | 645.3561 | 329.9893 | 576.2376 | 482.9263 | 545.5378 | 554.7269 | 535.8721
2595.0354 | 644.5973 | 330.5023 | 576.1621 | 483.0362 | 545.1166 | 556.1011 | 535.4975
2596.0354 | 643.9758 | 330.4716 | 575.8852 | 483.0248 | 544.2787 | 554.4823 | 533.2116
2597.0354 | 646.2577 | 330.5123 | 575.6832 | 483.3061 | 544.6179 | 554.1375 | 531.552
2598.0354 | 645.5838 | 330.6544 | 576.3517 | 483.7174 | 544.7386 | 552.8505 | 530.6608
2599.0354 | 646.8936 | 331.0644 | 576.698 | 483.3762 | 544.4889 | 551.7752 | 530.4064
2600.0354 | 644.399 | 331.2105 | 577.2762 | 483.4999 | 544.2467 | 554.7895 | 530.9079
2601.0354 | 643.2036 | 331.2627 | 577.5472 | 483.2978 | 543.0709 | 552.9826 | 532.2844
2602.0354 | 642.3157 | 331.4099 | 577.8769 | 483.4198 | 542.7924 | 552.6699 | 533.5361
2603.0354 | 639.6104 | 331.3899 | 578.1031 | 483.5086 | 542.4943 | 551.9028 | 533.19
2604.0354 | 634.8539 | 331.6762 | 576.5972 | 483.0429 | 541.7014 | 553.555 | 531.8534
2605.0354 | 638.0834 | 331.7898 | 576.5381 | 483.0342 | 541.9948 | 557.044 | 534.6965
2606.0354 | 638.0214 | 331.7233 | 576.7668 | 482.9668 | 541.3337 | 559.723 | 533.9088
2607.0354 | 636.2223 | 332.109 | 576.4485 | 482.9027 | 540.1633 | 560.7365 | 532.9903
2608.0354 | 634.8605 | 332.1731 | 576.4249 | 482.9844 | 539.4514 | 559.5003 | 534.2834
2609.0354 | 637.7809 | 332.2331 | 576.2901 | 483.0613 | 539.033 | 559.8263 | 534.681
2610.0354 | 638.5876 | 332.1166 | 576.6199 | 483.1739 | 540.2031 | 560.1572 | 534.5361
2611.0354 | 641.9616 | 332.1747 | 577.7376 | 483.0048 | 540.7012 | 559.9396 | 534.675
2612.0354 | 643.7714 | 332.6899 | 578.4836 | 483.1393 | 540.0307 | 561.6804 | 535.3038
2613.0354 | 645.6166 | 333.0425 | 579.6446 | 483.6178 | 539.3996 | 561.7316 | 537.1001
2614.0354 | 646.503 | 333.1933 | 580.1488 | 483.199 | 539.5535 | 560.9021 | 537.2156
2615.0354 | 647.2721 | 333.2718 | 581.0493 | 483.4418 | 539.0613 | 559.3123 | 536.8036
2616.0354 | 645.8422 | 333.3464 | 581.4816 | 483.3098 | 538.3928 | 558.2392 | 537.0401
2617.0354 | 647.331 | 333.4375 | 581.56 | 483.1909 | 537.9465 | 560.4848 | 542.7912
2618.0354 | 650.2682 | 333.6174 | 579.5681 | 482.8139 | 537.6565 | 560.6578 | 543.0443
2619.0354 | 651.8487 | 333.6669 | 578.6068 | 483.4718 | 538.9429 | 563.0774 | 545.3516
2620.0354 | 652.8644 | 334.4524 | 578.57 | 484.2646 | 539.3153 | 560.3569 | 544.5494
2621.0354 | 648.1571 | 334.1921 | 578.5255 | 483.5844 | 539.6998 | 557.0327 | 541.6085
2622.0354 | 647.5294 | 334.4275 | 578.9301 | 483.0436 | 540.2903 | 561.2132 | 542.8256
2623.0354 | 645.9476 | 335.4612 | 580.096 | 483.0062 | 539.8405 | 563.9418 | 544.5362
2624.0354 | 648.0029 | 335.5616 | 580.8008 | 483.2688 | 539.6727 | 565.2967 | 547.9247
2625.0354 | 649.474 | 335.2962 | 579.9177 | 483.01 | 539.44 | 564.4844 | 550.1214
2626.0354 | 651.2913 | 335.3497 | 579.877 | 483.0455 | 539.0248 | 565.6813 | 550.89
2627.0354 | 653.6031 | 335.1327 | 580.7415 | 482.9158 | 539.966 | 565.8819 | 550.0788
2628.0354 | 656.4541 | 335.6081 | 581.3594 | 483.4863 | 540.5087 | 566.2647 | 552.3054
2629.0354 | 659.0138 | 335.9773 | 581.8231 | 483.2478 | 540.7339 | 564.8902 | 551.4756
2630.0354 | 659.4775 | 336.3345 | 581.5176 | 483.0678 | 539.337 | 564.9443 | 553.1134
2631.0354 | 659.9528 | 336.2599 | 582.2133 | 483.0103 | 540.713 | 563.3331 | 550.4599
2632.0354 | 657.5528 | 336.272 | 582.2407 | 482.8517 | 540.7395 | 562.9159 | 549.9093
2633.0354 | 654.5681 | 336.6943 | 582.5193 | 483.0215 | 540.5335 | 559.0153 | 548.2008
2634.0354 | 655.178 | 336.8429 | 583.1722 | 483.0302 | 539.606 | 560.6252 | 546.8555
2635.0354 | 654.6345 | 336.4719 | 581.8904 | 482.8823 | 538.4633 | 558.6831 | 545.0434
2636.0354 | 655.5325 | 336.6253 | 581.3206 | 483.0137 | 537.8017 | 559.3529 | 543.5791
2637.0354 | 657.8896 | 336.7873 | 581.0491 | 483.2163 | 537.0537 | 558.2084 | 542.4697
2638.0354 | 658.1281 | 336.7161 | 581.8881 | 482.889 | 536.4026 | 556.1965 | 540.8155
2639.0354 | 656.1515 | 337.0188 | 581.8344 | 482.7407 | 536.851 | 554.5074 | 538.2917
2640.0354 | 657.3172 | 337.0608 | 581.75 | 482.3875 | 537.4571 | 556.1004 | 536.9682
2641.0354 | 656.9173 | 337.093 | 581.4327 | 482.6999 | 536.7248 | 558.2129 | 536.6859
2642.0354 | 656.858 | 337.1273 | 581.328 | 483.1507 | 537.9619 | 557.0915 | 535.4313
2643.0354 | 657.9645 | 337.4693 | 581.3157 | 483.2081 | 538.1104 | 555.4681 | 533.703
2644.0354 | 659.4798 | 337.8068 | 582.0506 | 482.979 | 537.7129 | 553.2643 | 533.079
2645.0354 | 656.5896 | 338.2026 | 581.7174 | 482.3891 | 537.706 | 551.5602 | 531.4688
2646.0354 | 650.9229 | 339.1303 | 581.9843 | 482.5141 | 536.0915 | 553.833 | 530.3798
2647.0354 | 652.1107 | 338.6145 | 581.8769 | 482.3625 | 534.0303 | 554.9051 | 531.8899
2648.0354 | 650.0683 | 338.6089 | 581.976 | 482.4402 | 532.6269 | 556.7593 | 533.4353
2649.0354 | 647.9172 | 338.5149 | 582.3915 | 483.0078 | 532.7009 | 556.5965 | 532.9878
2650.0354 | 646.171 | 338.8654 | 581.6836 | 484.1976 | 533.815 | 557.7184 | 533.6502
2651.0354 | 644.4276 | 338.9546 | 581.2692 | 483.8424 | 533.497 | 555.3856 | 533.5012
2652.0354 | 642.7767 | 339.2775 | 580.9036 | 483.1198 | 534.0746 | 554.7832 | 532.1803
2653.0354 | 643.7144 | 339.3377 | 580.6361 | 482.8454 | 535.7543 | 556.1102 | 534.012
2654.0354 | 643.0006 | 339.445 | 580.5319 | 482.7541 | 538.0924 | 557.5479 | 533.8946
2655.0354 | 641.6999 | 339.9959 | 580.6973 | 482.8171 | 540.003 | 559.8342 | 535.2052
2656.0354 | 639.7136 | 340.1691 | 581.6488 | 483.4545 | 539.0279 | 560.8431 | 534.7394
2657.0354 | 638.1479 | 340.4958 | 581.3272 | 482.9947 | 538.5116 | 558.7039 | 534.2433
2658.0354 | 639.6328 | 340.3055 | 581.8762 | 483.2109 | 539.7046 | 559.4401 | 535.4008
2659.0354 | 641.1831 | 340.3951 | 581.3651 | 484.4538 | 540.5995 | 559.3725 | 536.534
2660.0354 | 641.2839 | 340.691 | 580.8956 | 484.3713 | 540.3497 | 556.0932 | 535.8772
2661.0354 | 643.2026 | 340.6965 | 580.4474 | 483.4458 | 541.7725 | 555.8153 | 535.2511
2662.0354 | 644.2034 | 340.8649 | 580.9997 | 483.6904 | 543.3029 | 555.9831 | 536.1028
2663.0354 | 644.4309 | 341.3921 | 582.3235 | 483.7808 | 543.081 | 554.0171 | 535.6098
2664.0354 | 644.8395 | 341.5259 | 582.2819 | 483.7661 | 542.6798 | 551.4275 | 535.0759
2665.0354 | 644.5325 | 342.1729 | 583.222 | 483.8712 | 542.1059 | 549.7752 | 535.4497
2666.0354 | 642.5359 | 342.3365 | 583.7452 | 484.0624 | 542.4465 | 550.3063 | 535.2912
2667.0354 | 642.2892 | 341.9608 | 584.3563 | 483.7707 | 541.1606 | 548.2996 | 533.7211
2668.0354 | 642.9103 | 342.172 | 583.9594 | 484.1037 | 541.7906 | 550.5209 | 536.8217
2669.0354 | 645.1291 | 342.8481 | 584.9906 | 484.0346 | 540.5411 | 551.7973 | 539.6802
2670.0354 | 644.7093 | 345.2455 | 586.0316 | 484.0971 | 539.6744 | 550.1027 | 540.2296
2671.0354 | 643.0959 | 344.1474 | 584.1235 | 484.4882 | 539.225 | 550.3021 | 539.1124
2672.0354 | 645.215 | 343.8748 | 583.6421 | 484.4275 | 540.5604 | 551.9058 | 540.3371
2673.0354 | 645.1182 | 344.0169 | 583.5899 | 484.342 | 540.6905 | 551.3787 | 539.2232
2674.0354 | 646.3281 | 344.5353 | 584.2001 | 484.1965 | 541.4874 | 553.7501 | 539.2838
2675.0354 | 646.2991 | 345.2799 | 584.209 | 484.2943 | 541.0568 | 553.5606 | 539.2527
2676.0354 | 646.5402 | 345.102 | 583.6987 | 484.3857 | 540.1169 | 553.1725 | 537.7845
2677.0354 | 650.9262 | 345.3732 | 583.8153 | 484.5326 | 540.7979 | 552.4513 | 537.7681
2678.0354 | 651.1137 | 344.885 | 584.2362 | 484.1035 | 541.3281 | 553.314 | 536.717
2679.0354 | 651.1936 | 346.154 | 585.522 | 484.3184 | 541.8665 | 552.8259 | 536.046
2680.0354 | 651.7946 | 346.5004 | 585.5661 | 484.1654 | 540.8164 | 553.3648 | 538.3445
2681.0354 | 653.6252 | 346.4865 | 584.7524 | 484.5601 | 541.5815 | 554.767 | 538.9963
2682.0354 | 652.2303 | 347.2851 | 585.4416 | 484.8849 | 541.0673 | 552.9696 | 538.9442
2683.0354 | 650.4843 | 347.6844 | 585.0568 | 484.6692 | 540.369 | 551.6433 | 537.4355
2684.0354 | 649.2079 | 347.6665 | 583.9572 | 484.6167 | 540.1857 | 550.1523 | 537.1455
2685.0354 | 651.3009 | 348.136 | 583.9027 | 484.512 | 541.0345 | 550.6508 | 536.163
2686.0354 | 651.7913 | 348.0273 | 584.4448 | 484.8633 | 541.5809 | 549.7691 | 535.0724
2687.0354 | 651.5467 | 347.3742 | 583.6937 | 485.1311 | 541.6335 | 550.9715 | 536.2287
2688.0354 | 652.8768 | 348.0325 | 583.7579 | 484.9017 | 542.5035 | 551.3322 | 534.827
2689.0354 | 654.5552 | 348.643 | 583.7961 | 485.3744 | 543.526 | 552.5879 | 534.9098
2690.0354 | 654.0805 | 348.8702 | 583.4519 | 485.4128 | 544.4806 | 551.8442 | 534.4812
2691.0354 | 653.4663 | 348.6561 | 583.6245 | 484.9805 | 544.8999 | 550.6814 | 534.8358
2692.0354 | 649.7579 | 349.0116 | 583.8136 | 484.8285 | 545.8413 | 550.2514 | 533.5426
2693.0354 | 646.2644 | 350.2914 | 584.1479 | 485.3212 | 545.8469 | 551.5307 | 533.3769
2694.0354 | 646.9369 | 350.7661 | 583.9169 | 485.1252 | 545.453 | 552.1182 | 534.4521
2695.0354 | 651.2495 | 351.409 | 584.5755 | 485.1321 | 546.5794 | 552.9639 | 534.9384
2696.0354 | 652.4799 | 352.0643 | 584.1076 | 485.6506 | 546.5935 | 555.0277 | 533.534
2697.0354 | 650.6591 | 352.4057 | 584.0097 | 486.6239 | 545.2585 | 552.7647 | 531.8074
2698.0354 | 650.1418 | 353.31 | 585.3576 | 486.0676 | 549.8499 | 551.7183 | 531.7556
2699.0354 | 645.6741 | 352.1982 | 585.5306 | 485.4847 | 551.4268 | 549.6405 | 531.6986
2700.0354 | 647.5947 | 352.1887 | 584.7017 | 485.9355 | 552.831 | 549.2193 | 531.9538
2701.0354 | 649.0448 | 352.9199 | 584.8782 | 485.5476 | 552.8701 | 553.7955 | 534.6597
2702.0354 | 652.702 | 354.5653 | 584.0833 | 485.7976 | 559.8344 | 555.2043 | 534.9505
2703.0354 | 653.7637 | 354.7047 | 584.3904 | 485.9492 | 559.0208 | 553.0006 | 535.151
2704.0354 | 654.0026 | 357.2882 | 584.9219 | 486.7863 | 557.8783 | 553.3865 | 535.5838
2705.0354 | 651.6978 | 358.9697 | 584.1563 | 487.3269 | 561.1741 | 551.8899 | 534.8179
2706.0354 | 649.5182 | 357.9527 | 584.8347 | 486.2254 | 562.2138 | 548.8522 | 531.8566
2707.0354 | 650.5617 | 357.0432 | 585.6958 | 486.189 | 562.039 | 548.5153 | 530.6749
2708.0354 | 651.5207 | 357.7679 | 584.3972 | 486.131 | 567.8769 | 551.6819 | 530.9895
2709.0354 | 653.2292 | 357.7346 | 584.5804 | 486.4039 | 571.9681 | 554.7066 | 531.9168
2710.0354 | 652.1131 | 357.9652 | 584.5442 | 487.9644 | 571.2376 | 555.0882 | 533.0222
2711.0354 | 647.9767 | 358.3843 | 584.9398 | 488.0536 | 577.1145 | 552.649 | 532.4919
2712.0354 | 648.3416 | 358.1839 | 584.2728 | 486.7546 | 575.1362 | 554.0793 | 531.2919
2713.0354 | 650.6897 | 359.3886 | 584.9695 | 487.4341 | 575.8263 | 557.6916 | 534.3694
2714.0354 | 652.8235 | 359.5325 | 584.3773 | 487.3031 | 574.9802 | 562.6711 | 536.9701
2715.0354 | 655.518 | 358.8399 | 584.3068 | 487.9105 | 573.8984 | 563.346 | 537.9015
2716.0354 | 656.5331 | 360.7312 | 584.8681 | 487.4999 | 571.7402 | 562.5306 | 536.4445
2717.0354 | 652.8703 | 360.4133 | 585.2782 | 487.7621 | 569.1439 | 560.2916 | 535.2673
2718.0354 | 650.8219 | 359.3947 | 584.5784 | 488.8538 | 566.6528 | 557.671 | 533.1892
2719.0354 | 649.9733 | 359.1582 | 585.2782 | 488.8925 | 565.2754 | 556.5823 | 534.2999
2720.0354 | 649.1347 | 358.9026 | 586.1955 | 488.8157 | 566.1047 | 556.6573 | 536.3723
2721.0354 | 653.5576 | 359.503 | 587.3346 | 488.6147 | 569.8402 | 559.3301 | 540.1826
2722.0354 | 654.4105 | 359.8186 | 586.5393 | 488.9891 | 573.7379 | 560.2362 | 541.9058
2723.0354 | 657.9572 | 359.9438 | 587.1993 | 488.8775 | 581.5989 | 558.0044 | 542.3013
2724.0354 | 660.3237 | 360.4647 | 586.9935 | 489.3944 | 583.0156 | 557.8932 | 543.6369
2725.0354 | 662.3145 | 360.8266 | 585.9576 | 489.1304 | 584.6945 | 560.1762 | 546.9603
2726.0354 | 663.5656 | 362.6055 | 585.5141 | 488.5881 | 591.4879 | 564.8952 | 549.2677
2727.0354 | 667.0522 | 364.552 | 585.1079 | 488.9014 | 593.5919 | 570.6807 | 550.3814
2728.0354 | 669.9466 | 365.1931 | 585.659 | 489.4967 | 593.6295 | 568.2647 | 547.7802
2729.0354 | 671.3681 | 364.2592 | 585.7213 | 489.5878 | 591.925 | 568.5571 | 546.2949
2730.0354 | 670.4388 | 363.7836 | 587.5351 | 489.668 | 588.0179 | 567.1957 | 546.4313
2731.0354 | 668.9116 | 363.4919 | 586.7926 | 489.4593 | 585.9784 | 566.4006 | 546.051
2732.0354 | 670.0941 | 363.9779 | 585.6956 | 489.5996 | 590.5782 | 570.0615 | 547.1149
2733.0354 | 672.4487 | 365.5655 | 585.163 | 489.3087 | 591.6105 | 571.903 | 547.6011
2734.0354 | 673.4601 | 365.7644 | 585.1628 | 489.6224 | 592.4743 | 570.3928 | 546.4544
2735.0354 | 672.9885 | 365.258 | 585.6524 | 490.0792 | 591.6706 | 567.6387 | 544.3154
2736.0354 | 669.1611 | 365.7728 | 586.1421 | 489.9849 | 589.7267 | 564.9115 | 542.5681
2737.0354 | 668.0317 | 367.5317 | 585.6058 | 490.2753 | 586.5375 | 564.2606 | 540.4752
2738.0354 | 669.7633 | 366.8287 | 584.7986 | 489.9221 | 585.7897 | 567.5269 | 541.1218
2739.0354 | 670.0454 | 366.657 | 584.5818 | 489.6927 | 587.7738 | 565.781 | 540.4452
2740.0354 | 673.6422 | 366.5433 | 584.4407 | 489.7008 | 587.9669 | 565.4535 | 539.9422
2741.0354 | 677.6443 | 367.3287 | 585.6876 | 490.4305 | 585.9434 | 566.2491 | 539.806
2742.0354 | 679.5986 | 367.8891 | 584.8325 | 491.0644 | 583.3467 | 566.5719 | 538.9087
2743.0354 | 683.8807 | 368.1095 | 584.5167 | 490.2603 | 583.6378 | 566.6553 | 537.8993
2744.0354 | 683.8186 | 369.6664 | 585.5856 | 490.2221 | 581.3527 | 566.104 | 539.5849
2745.0354 | 683.0171 | 371.0249 | 585.5664 | 490.5625 | 577.9447 | 568.6859 | 540.615
2746.0354 | 680.9445 | 370.5391 | 584.7652 | 490.3466 | 574.7429 | 569.319 | 542.0471
2747.0354 | 681.7018 | 371.8634 | 584.0341 | 490.3805 | 573.7006 | 570.447 | 542.4156
2748.0354 | 682.6891 | 371.5888 | 583.83 | 490.6075 | 576.3565 | 571.5572 | 539.9131
2749.0354 | 684.4158 | 372.1014 | 583.5678 | 490.3105 | 577.5866 | 569.7166 | 537.9824
2750.0354 | 683.5369 | 370.7448 | 583.9343 | 490.9206 | 576.311 | 567.9255 | 540.1175
2751.0354 | 683.217 | 371.4321 | 583.5318 | 491.053 | 576.1016 | 568.583 | 540.8482
2752.0354 | 681.8222 | 372.3405 | 583.2095 | 490.7176 | 577.4346 | 570.4982 | 541.3624
2753.0354 | 681.7705 | 372.5009 | 583.147 | 490.7494 | 578.8219 | 571.3114 | 539.8156
2754.0354 | 682.1442 | 372.4484 | 583.416 | 491.3007 | 579.6343 | 569.4055 | 539.8561
2755.0354 | 681.0706 | 372.2509 | 582.9356 | 491.369 | 578.186 | 569.094 | 539.4459
2756.0354 | 679.9018 | 372.636 | 582.5509 | 492.1839 | 576.6723 | 567.207 | 538.2656
2757.0354 | 676.1642 | 372.303 | 583.1228 | 491.8793 | 576.7078 | 565.3167 | 536.8904
2758.0354 | 673.9994 | 373.4241 | 582.5154 | 491.6199 | 575.3175 | 565.4222 | 536.6202
2759.0354 | 673.6471 | 374.6034 | 582.6188 | 492.1048 | 578.0862 | 567.9608 | 537.1816
2760.0354 | 671.7414 | 373.8673 | 581.96 | 492.185 | 578.4255 | 567.7891 | 537.5213
2761.0354 | 671.6801 | 373.6033 | 581.8358 | 492.8147 | 577.7082 | 566.4238 | 536.8368
2762.0354 | 671.3941 | 374.3066 | 581.6281 | 493.2935 | 577.8311 | 565.1584 | 534.782
2763.0354 | 673.2249 | 373.8792 | 581.2499 | 492.6481 | 580.2329 | 568.352 | 536.2537
2764.0354 | 675.9006 | 375.1668 | 581.0788 | 492.8269 | 581.6287 | 568.2651 | 536.5643
2765.0354 | 677.0654 | 375.4705 | 580.8074 | 493.5077 | 582.1568 | 567.4151 | 535.9556
2766.0354 | 678.5907 | 375.7017 | 580.492 | 493.3397 | 581.7897 | 564.867 | 534.6077
2767.0354 | 679.4154 | 375.7358 | 580.4934 | 493.8537 | 581.2055 | 564.868 | 533.4183
2768.0354 | 680.7161 | 375.8111 | 580.1961 | 493.7962 | 584.7423 | 564.9376 | 535.3573
2769.0354 | 681.3573 | 376.5514 | 579.8945 | 493.9074 | 586.9287 | 567.0836 | 536.6722
2770.0354 | 683.7647 | 377.8764 | 579.6789 | 493.7132 | 588.6532 | 567.8876 | 536.6859
2771.0354 | 684.6797 | 377.2931 | 579.3257 | 493.8409 | 590.2848 | 568.2617 | 536.8032
2772.0354 | 685.4523 | 377.9928 | 579.0741 | 493.8923 | 592.0957 | 569.3378 | 536.6344
2773.0354 | 684.5551 | 378.6237 | 579.1894 | 494.6994 | 592.0669 | 567.7032 | 536.2986
2774.0354 | 684.2632 | 377.8566 | 578.8482 | 494.1743 | 589.4303 | 568.3014 | 534.7377
2775.0354 | 682.9094 | 379.1863 | 579.9613 | 494.7682 | 588.7817 | 568.6963 | 535.248
2776.0354 | 679.0852 | 378.686 | 578.864 | 495.2033 | 587.7153 | 567.9772 | 535.2311
2777.0354 | 682.0165 | 378.63 | 578.464 | 495.6343 | 587.9774 | 567.7715 | 533.8286
2778.0354 | 685.4396 | 379.1651 | 578.1612 | 495.2397 | 587.5027 | 565.7777 | 533.9927
2779.0354 | 681.6429 | 380.0836 | 578.3456 | 496.2514 | 587.5342 | 563.9763 | 533.7396
2780.0354 | 680.7098 | 381.423 | 578.4779 | 496.0446 | 585.9665 | 561.8287 | 531.4307
2781.0354 | 681.4204 | 379.9319 | 578.4095 | 495.7726 | 584.0954 | 561.2384 | 530.9056
2782.0354 | 684.5355 | 379.7469 | 577.8537 | 496.8116 | 582.6875 | 562.5483 | 530.9163
2783.0354 | 687.2469 | 379.6952 | 577.358 | 496.8666 | 583.5002 | 562.1485 | 531.5721
2784.0354 | 688.7055 | 380.0349 | 577.5062 | 496.5844 | 584.0111 | 562.2422 | 532.3624
2785.0354 | 687.8869 | 381.1045 | 578.2037 | 497.274 | 584.1144 | 561.1146 | 532.3239
2786.0354 | 683.8839 | 380.7489 | 577.4729 | 498.4418 | 581.9922 | 559.793 | 531.5256
2787.0354 | 680.4578 | 380.3833 | 577.1412 | 498.0888 | 581.1337 | 558.3639 | 530.3117
2788.0354 | 687.2569 | 382.007 | 576.6009 | 497.6719 | 580.2585 | 557.716 | 528.2178
2789.0354 | 687.7337 | 381.505 | 576.2632 | 498.0485 | 582.1887 | 558.3377 | 528.0388
2790.0354 | 690.5419 | 381.3595 | 576.1006 | 498.7639 | 583.1456 | 557.8667 | 528.1397
2791.0354 | 688.4007 | 382.5754 | 575.6578 | 498.8039 | 582.1501 | 556.5325 | 528.2809
2792.0354 | 688.0984 | 381.8453 | 575.6626 | 499.3752 | 581.5643 | 555.6536 | 527.6938
2793.0354 | 689.0872 | 381.578 | 575.4382 | 500.7483 | 582.2146 | 554.1419 | 526.4947
2794.0354 | 689.0565 | 383.2665 | 576.276 | 500.8998 | 581.2109 | 553.3856 | 526.3642
2795.0354 | 685.5856 | 385.5498 | 575.8933 | 500.4935 | 579.5527 | 553.6164 | 527.5504
2796.0354 | 682.3972 | 385.6694 | 575.2557 | 501.2893 | 578.6672 | 554.8468 | 528.6338
2797.0354 | 680.7934 | 385.0876 | 575.3759 | 502.0343 | 578.4166 | 554.4475 | 529.744
2798.0354 | 678.0251 | 385.1791 | 576.5029 | 501.3726 | 579.137 | 554.0254 | 529.5895
2799.0354 | 673.873 | 386.6048 | 576.7783 | 501.0913 | 576.9401 | 552.5456 | 528.5743
2800.0354 | 672.722 | 386.2312 | 576.8627 | 501.8941 | 576.4618 | 554.3388 | 528.9173
2801.0354 | 671.045 | 387.4751 | 576.1068 | 503.2786 | 577.2494 | 555.8997 | 530.2984
2802.0354 | 667.4674 | 386.946 | 577.3402 | 504.2512 | 576.8564 | 556.2536 | 530.4763
2803.0354 | 663.1662 | 389.5452 | 576.6716 | 503.2406 | 581.1368 | 555.1947 | 528.5403
2804.0354 | 664.0068 | 388.6544 | 575.6556 | 503.2391 | 581.4071 | 560.1359 | 531.3956
2805.0354 | 661.6375 | 388.0919 | 575.9736 | 504.872 | 582.1373 | 561.0449 | 532.4693
2806.0354 | 660.8393 | 387.6 | 575.8496 | 505.657 | 583.602 | 561.4697 | 533.4501
2807.0354 | 661.7 | 389.3721 | 575.6984 | 505.9718 | 583.5801 | 560.9049 | 533.636
2808.0354 | 661.5222 | 389.8704 | 575.2222 | 505.55 | 584.0249 | 560.6877 | 533.2028
2809.0354 | 664.1534 | 388.8923 | 574.824 | 505.6569 | 583.3264 | 562.2986 | 534.8152
2810.0354 | 661.6445 | 390.1975 | 575.0946 | 505.8211 | 582.8456 | 562.9132 | 536.3512
2811.0354 | 662.2451 | 390.2009 | 576.1009 | 506.3867 | 581.3481 | 561.9365 | 536.5293
2812.0354 | 661.54 | 389.9201 | 575.9299 | 506.1172 | 581.3443 | 563.0732 | 536.335
2813.0354 | 658.5629 | 391.0372 | 576.4796 | 506.941 | 580.3886 | 562.7641 | 536.1374
2814.0354 | 657.9283 | 390.4424 | 575.7307 | 507.8598 | 578.5946 | 562.7754 | 535.8088
2815.0354 | 660.7957 | 389.5549 | 575.9985 | 507.7838 | 578.8348 | 563.7542 | 534.7543
2816.0354 | 661.2334 | 389.2416 | 575.6566 | 507.9143 | 579.2318 | 567.0025 | 537.2125
2817.0354 | 660.0415 | 389.3667 | 578.0841 | 509.5287 | 579.5271 | 569.3591 | 539.4197
2818.0354 | 659.3189 | 389.9213 | 578.1895 | 508.726 | 588.0551 | 567.2058 | 539.4337
2819.0354 | 656.8059 | 390.6109 | 578.5851 | 508.62 | 587.95 | 566.7967 | 538.987
2820.0354 | 655.9759 | 390.6334 | 577.9527 | 508.6264 | 585.6922 | 567.7722 | 538.96
2821.0354 | 654.9877 | 392.8718 | 578.7598 | 509.2436 | 583.7814 | 566.7257 | 538.5332
2822.0354 | 654.2598 | 392.4442 | 577.2695 | 509.2566 | 582.0147 | 564.4934 | 536.8606
2823.0354 | 653.7081 | 391.7193 | 577.596 | 509.5662 | 583.464 | 565.2593 | 537.1801
2824.0354 | 651.4188 | 392.1607 | 577.3794 | 509.894 | 584.1483 | 568.3335 | 537.7327
2825.0354 | 654.8689 | 393.1006 | 577.2133 | 509.9553 | 583.7113 | 570.8059 | 539.2132
2826.0354 | 657.0847 | 394.7545 | 578.0361 | 509.8856 | 583.1633 | 571.6901 | 540.5865
2827.0354 | 656.438 | 394.6105 | 577.2744 | 510.3493 | 581.4117 | 572.9107 | 541.3395
2828.0354 | 660.1746 | 394.8926 | 579.4987 | 510.9516 | 581.6941 | 574.522 | 541.7802
2829.0354 | 659.5158 | 395.0168 | 578.6405 | 511.489 | 580.9742 | 572.8264 | 541.1405
2830.0354 | 660.0609 | 396.5708 | 578.2335 | 511.5641 | 579.4401 | 569.671 | 539.0196
2831.0354 | 659.9503 | 397.884 | 577.5209 | 512.7247 | 578.5722 | 567.5669 | 537.3905
2832.0354 | 661.9586 | 397.4955 | 577.3267 | 512.3254 | 578.9855 | 565.6208 | 536.7658
2833.0354 | 666.2018 | 398.5207 | 577.4485 | 513.1298 | 578.9663 | 563.6726 | 535.1689
2834.0354 | 668.9924 | 398.286 | 577.6366 | 512.7554 | 581.3197 | 564.8891 | 535.0498
2835.0354 | 668.6412 | 398.4581 | 577.454 | 512.9481 | 583.041 | 567.7573 | 535.8158
2836.0354 | 672.1269 | 397.9133 | 577.8736 | 513.0257 | 583.0549 | 567.9342 | 536.2872
2837.0354 | 675.4975 | 399.5134 | 577.0258 | 513.3717 | 583.8878 | 568.7236 | 536.2896
2838.0354 | 677.8162 | 399.7756 | 576.8178 | 513.0958 | 583.7124 | 571.4739 | 538.0032
2839.0354 | 675.7242 | 399.0798 | 577.2347 | 514.1257 | 584.8587 | 570.0721 | 537.2418
2840.0354 | 673.6961 | 399.3223 | 577.124 | 514.4599 | 583.8055 | 569.2232 | 536.7706
2841.0354 | 675.7886 | 401.566 | 576.7425 | 514.3314 | 583.7952 | 567.5685 | 535.4713
2842.0354 | 678.9757 | 400.4029 | 576.0468 | 514.0787 | 585.6055 | 570.1757 | 537.1859
2843.0354 | 680.8314 | 400.8629 | 576.5301 | 514.3662 | 585.5792 | 568.8766 | 537.0708
2844.0354 | 680.0597 | 401.5755 | 576.9323 | 514.5053 | 585.4671 | 567.5602 | 536.9621
2845.0354 | 680.8566 | 400.8473 | 576.1733 | 514.7605 | 584.9251 | 568.0328 | 537.235
2846.0354 | 682.1221 | 402.091 | 576.1776 | 515.7301 | 586.1807 | 566.5455 | 536.0537
2847.0354 | 680.6821 | 402.4816 | 576.3687 | 515.6231 | 585.4589 | 567.9036 | 536.3181
2848.0354 | 679.5124 | 402.0525 | 576.5177 | 515.9394 | 587.526 | 568.2161 | 536.8567
2849.0354 | 677.5195 | 400.7287 | 577.291 | 516.75 | 588.7853 | 566.6321 | 535.9451
2850.0354 | 676.2122 | 400.4203 | 576.9341 | 517.3134 | 589.7184 | 565.8443 | 535.7226
2851.0354 | 673.8159 | 400.2873 | 576.5182 | 516.7551 | 589.2946 | 566.9851 | 535.9925
2852.0354 | 672.9303 | 400.0753 | 576.7035 | 517.1336 | 589.4157 | 567.8541 | 537.5037
2853.0354 | 671.5301 | 400.9876 | 577.4811 | 517.2158 | 588.3197 | 568.3824 | 538.2015
2854.0354 | 668.7964 | 400.6299 | 577.6867 | 517.8802 | 587.5684 | 568.8273 | 538.9667
2855.0354 | 667.7086 | 400.5192 | 578.1176 | 518.9935 | 586.9986 | 569.7265 | 539.2575
2856.0354 | 665.7765 | 400.5355 | 577.4874 | 518.6807 | 586.5953 | 569.4427 | 539.179
2857.0354 | 666.5085 | 400.3287 | 576.5843 | 518.809 | 587.8276 | 570.972 | 539.9697
2858.0354 | 667.9972 | 400.1413 | 576.7239 | 518.5485 | 589.3736 | 572.0451 | 540.6214
2859.0354 | 670.1628 | 400.0909 | 576.473 | 519.0081 | 589.4074 | 572.5963 | 540.4272
2860.0354 | 671.7017 | 400.7134 | 576.2181 | 519.283 | 590.7742 | 571.6424 | 540.048
2861.0354 | 678.459 | 401.2919 | 575.9237 | 519.8759 | 592.7308 | 569.4374 | 538.886
2862.0354 | 685.1301 | 402.9426 | 575.5067 | 519.7013 | 593.5914 | 567.6357 | 537.3916
2863.0354 | 687.7165 | 403.1275 | 576.863 | 520.4087 | 594.107 | 567.1336 | 536.8351
2864.0354 | 687.054 | 402.5434 | 577.6049 | 521.6673 | 593.3546 | 566.4763 | 536.3439
2865.0354 | 685.3083 | 402.9502 | 576.8853 | 522.1821 | 595.981 | 565.7333 | 535.9175
2866.0354 | 683.1133 | 402.8293 | 576.2448 | 521.2825 | 596.4852 | 566.4495 | 536.7488
2867.0354 | 680.0514 | 402.7281 | 576.2459 | 522.0581 | 595.4668 | 567.4096 | 537.129
2868.0354 | 679.7893 | 403.4682 | 576.5544 | 523.0499 | 595.0182 | 567.1353 | 536.5094
2869.0354 | 677.7428 | 404.0942 | 575.8475 | 523.1854 | 594.2056 | 565.4824 | 535.0419
2870.0354 | 676.5315 | 404.1368 | 575.8856 | 523.106 | 593.6037 | 564.3705 | 534.56
2871.0354 | 673.1427 | 404.4893 | 576.0946 | 523.255 | 593.4532 | 564.213 | 534.3739
2872.0354 | 670.5189 | 403.6402 | 576.5874 | 523.6985 | 592.4094 | 564.3758 | 534.6752
2873.0354 | 670.0285 | 403.1938 | 576.5936 | 523.7361 | 594.0141 | 566.0265 | 535.3276
2874.0354 | 667.0866 | 403.7724 | 576.1753 | 523.6762 | 594.4003 | 568.1125 | 537.056
2875.0354 | 670.1706 | 403.8129 | 576.087 | 523.9616 | 597.2944 | 570.4569 | 539.4844
2876.0354 | 669.6139 | 404.9119 | 577.281 | 524.9447 | 597.3928 | 572.4361 | 541.265
2877.0354 | 669.2609 | 409.2918 | 577.1153 | 524.8782 | 597.0537 | 573.4444 | 541.6234
2878.0354 | 666.2885 | 406.6606 | 577.1434 | 526.0252 | 596.2466 | 573.8149 | 542.9643
2879.0354 | 664.881 | 405.3652 | 576.2649 | 526.092 | 595.7485 | 573.1983 | 542.8002
2880.0354 | 665.6684 | 405.3778 | 575.9298 | 525.4764 | 593.9593 | 575.1809 | 543.0216
2881.0354 | 663.1517 | 406.2761 | 576.8515 | 525.8382 | 596.2822 | 574.5431 | 543.0357
2882.0354 | 664.1267 | 407.3899 | 577.1061 | 526.3034 | 597.9261 | 575.529 | 542.4205
2883.0354 | 665.5937 | 409.3201 | 576.7429 | 526.6598 | 599.2341 | 575.8229 | 543.7117
2884.0354 | 664.8675 | 408.2464 | 576.8185 | 527.9912 | 598.5736 | 575.8871 | 544.8187
2885.0354 | 666.7203 | 408.0182 | 576.0142 | 527.7289 | 601.0445 | 577.8111 | 545.4664
2886.0354 | 668.1116 | 409.1051 | 576.2528 | 527.2723 | 601.2096 | 575.4737 | 543.9554
2887.0354 | 668.9638 | 409.4873 | 576.6457 | 527.8341 | 602.1543 | 573.0665 | 542.8354
2888.0354 | 670.4969 | 410.2816 | 576.5465 | 528.1704 | 601.4603 | 571.8871 | 541.1899
2889.0354 | 676.8561 | 410.1234 | 577.0577 | 528.2296 | 601.3548 | 570.8132 | 540.932
2890.0354 | 676.5157 | 410.305 | 577.7065 | 529.2009 | 600.8856 | 572.5142 | 542.4578
2891.0354 | 673.8379 | 409.4069 | 577.8887 | 528.8809 | 601.9838 | 573.9697 | 543.5761
2892.0354 | 673.013 | 408.6433 | 577.6412 | 529.4133 | 600.0932 | 573.8711 | 542.6081
2893.0354 | 671.8153 | 408.3852 | 577.3196 | 530.4073 | 600.2124 | 574.943 | 542.4463
2894.0354 | 671.149 | 408.3116 | 576.821 | 530.0414 | 598.2502 | 573.3601 | 541.5889
2895.0354 | 670.3726 | 409.3652 | 578.3985 | 530.0819 | 597.5287 | 571.7792 | 539.8031
2896.0354 | 665.4301 | 409.6528 | 578.3719 | 530.5123 | 597.1813 | 570.9674 | 539.7245
2897.0354 | 670.0923 | 410.2307 | 579.7094 | 531.1724 | 597.0423 | 571.7757 | 540.6059
2898.0354 | 670.0114 | 410.3455 | 579.3623 | 531.825 | 598.6884 | 570.7043 | 541.7855
2899.0354 | 667.4775 | 412.3701 | 578.2656 | 531.817 | 600.4969 | 570.1936 | 541.92
2900.0354 | 665.8302 | 413.5641 | 578.0248 | 530.9484 | 599.4506 | 570.8594 | 542.3417
2901.0354 | 668.3736 | 411.8587 | 578.4547 | 531.7928 | 600.2294 | 572.1824 | 542.0848
2902.0354 | 667.7486 | 411.2936 | 580.1654 | 532.5442 | 602.0643 | 573.4191 | 542.9217
2903.0354 | 661.7338 | 410.5989 | 579.7381 | 532.438 | 601.6438 | 573.1434 | 542.6842
2904.0354 | 663.9065 | 410.4245 | 579.4186 | 532.682 | 601.1025 | 573.6911 | 543.327
2905.0354 | 664.8531 | 411.0815 | 579.7334 | 532.8987 | 602.0759 | 574.6219 | 542.4815
2906.0354 | 667.7245 | 410.1884 | 578.8141 | 533.1314 | 602.4241 | 575.5072 | 543.3232
2907.0354 | 667.0412 | 410.403 | 578.6349 | 533.264 | 602.6557 | 575.4856 | 542.3357
2908.0354 | 675.6382 | 412.5085 | 578.4836 | 533.2206 | 603.2239 | 573.6981 | 541.1865
2909.0354 | 675.93 | 412.3413 | 579.8095 | 533.2874 | 603.2599 | 573.6745 | 540.3692
2910.0354 | 674.4691 | 413.4051 | 579.7757 | 533.4679 | 602.593 | 573.9672 | 540.5872
2911.0354 | 673.1238 | 412.949 | 580.2237 | 533.6288 | 601.627 | 574.0867 | 540.3563
2912.0354 | 671.8396 | 412.734 | 579.4744 | 533.6842 | 602.0724 | 574.5855 | 540.2626
2913.0354 | 675.5809 | 412.5999 | 578.5436 | 533.6798 | 602.2435 | 576.3993 | 540.3358
2914.0354 | 679.6325 | 413.4581 | 578.5222 | 533.5832 | 602.4742 | 574.7617 | 540.1344
2915.0354 | 678.9946 | 413.9953 | 579.199 | 533.6479 | 602.4453 | 574.3589 | 539.9641
2916.0354 | 679.6521 | 416.6216 | 579.3007 | 533.9498 | 601.304 | 574.7661 | 539.4365
2917.0354 | 686.9938 | 414.2851 | 578.2475 | 534.0374 | 600.2416 | 574.246 | 537.8042
2918.0354 | 689.8281 | 415.0082 | 578.3414 | 534.2175 | 600.5358 | 573.072 | 537.1153
2919.0354 | 689.7261 | 414.0895 | 578.2729 | 534.265 | 600.1699 | 574.0407 | 537.8455
2920.0354 | 689.6945 | 414.0462 | 577.8377 | 534.0572 | 599.2833 | 575.8956 | 539.3624
2921.0354 | 687.8949 | 415.0795 | 578.0211 | 535.3788 | 598.5185 | 575.6876 | 539.245
2922.0354 | 684.7615 | 415.0499 | 578.4947 | 535.882 | 599.3979 | 576.526 | 540.1747
2923.0354 | 686.3756 | 414.5445 | 578.2222 | 535.9394 | 599.3061 | 576.7895 | 540.1929
2924.0354 | 686.5609 | 414.4295 | 578.4136 | 536.4545 | 600.8101 | 576.1727 | 540.7776
2925.0354 | 685.5027 | 414.4323 | 578.117 | 536.5515 | 602.5522 | 576.7416 | 542.75
2926.0354 | 686.3844 | 414.2403 | 577.8549 | 536.7351 | 603.9081 | 576.1838 | 543.2271
2927.0354 | 686.3536 | 414.2864 | 577.8291 | 537.0638 | 605.2905 | 577.0614 | 544.7855
2928.0354 | 684.6158 | 414.286 | 578.0773 | 536.2579 | 605.3506 | 577.0405 | 544.866
2929.0354 | 683.1146 | 414.5477 | 580.067 | 536.7984 | 604.6944 | 576.8035 | 545.4539
2930.0354 | 679.3131 | 414.8051 | 579.1885 | 537.3466 | 603.0146 | 576.5916 | 545.3966
2931.0354 | 680.3896 | 416.2753 | 578.4648 | 537.3655 | 603.7014 | 576.9648 | 544.5545
2932.0354 | 679.5496 | 417.2872 | 578.1583 | 537.2325 | 604.9168 | 576.2495 | 543.1508
2933.0354 | 681.5935 | 416.4749 | 577.9902 | 537.2751 | 604.2594 | 575.7069 | 542.2787
2934.0354 | 685.6857 | 415.6328 | 579.941 | 537.5528 | 603.0786 | 574.7166 | 542.3097
2935.0354 | 684.4264 | 415.4616 | 580.865 | 538.3382 | 601.1165 | 575.2604 | 543.3838
2936.0354 | 680.224 | 415.4432 | 579.9287 | 538.1323 | 600.2681 | 575.0652 | 542.8359
2937.0354 | 677.7796 | 415.9332 | 578.8745 | 537.869 | 601.0991 | 579.1136 | 545.1719
2938.0354 | 677.1827 | 416.1814 | 578.869 | 538.7843 | 600.5476 | 579.1712 | 545.007
2939.0354 | 677.0105 | 416.4386 | 578.5961 | 538.9596 | 600.5851 | 576.9305 | 543.9593
2940.0354 | 676.3647 | 417.6248 | 579.0483 | 539.2318 | 599.4727 | 575.2387 | 543.0894
2941.0354 | 673.2264 | 418.1348 | 580.3879 | 538.8114 | 597.9345 | 574.7105 | 542.4347
2942.0354 | 662.8663 | 417.902 | 579.601 | 539.1122 | 599.5116 | 576.2618 | 542.4644
2943.0354 | 661.8367 | 420.4404 | 578.7522 | 538.6678 | 599.1862 | 578.382 | 544.2621
2944.0354 | 662.6609 | 418.8843 | 578.8142 | 538.6752 | 598.2818 | 578.1274 | 544.1194
2945.0354 | 666.2442 | 418.3583 | 578.2274 | 538.9043 | 598.8342 | 581.1735 | 544.8726
2946.0354 | 671.8419 | 418.7747 | 578.3206 | 539.0181 | 599.5481 | 582.3892 | 544.8738
2947.0354 | 684.3703 | 418.6124 | 578.3812 | 539.3151 | 599.4189 | 581.1005 | 543.7834
2948.0354 | 685.8967 | 418.11 | 577.9846 | 539.364 | 601.1036 | 581.2593 | 542.8414
2949.0354 | 687.6546 | 418.1769 | 577.8179 | 539.2904 | 602.6421 | 581.5779 | 542.5161
2950.0354 | 691.7084 | 420.8052 | 577.8728 | 539.147 | 601.7248 | 581.7001 | 542.1215
2951.0354 | 691.7676 | 421.3457 | 577.8172 | 539.4179 | 601.7651 | 582.6314 | 542.346
2952.0354 | 690.659 | 421.789 | 577.3106 | 540.2311 | 600.3499 | 582.4527 | 541.7106
2953.0354 | 692.5642 | 420.0761 | 576.9485 | 539.8073 | 600.3831 | 581.1494 | 541.6787
2954.0354 | 693.4522 | 420.2965 | 576.9996 | 540.0524 | 601.7897 | 578.1437 | 539.068
2955.0354 | 692.7032 | 420.7022 | 578.1956 | 541.1245 | 602.2694 | 576.3932 | 538.7654
2956.0354 | 689.2774 | 420.9854 | 577.3875 | 541.709 | 600.5632 | 574.4382 | 537.4141
2957.0354 | 691.6194 | 422.1137 | 576.9706 | 541.2039 | 601.1946 | 574.7594 | 538.1506
2958.0354 | 691.7144 | 423.2291 | 577.0856 | 540.6289 | 602.0189 | 575.3665 | 538.4453
2959.0354 | 690.77 | 422.3221 | 577.4952 | 541.238 | 602.4146 | 577.6481 | 539.9353
2960.0354 | 689.1604 | 421.1117 | 577.0084 | 541.4015 | 601.1321 | 578.4477 | 540.0148
2961.0354 | 688.9785 | 422.1776 | 577.8989 | 540.8807 | 600.8202 | 580.7459 | 542.8643
2962.0354 | 684.7778 | 422.1939 | 577.2957 | 540.9757 | 598.8251 | 579.9508 | 543.7002
2963.0354 | 680.3418 | 422.4959 | 576.6428 | 541.1772 | 598.3575 | 579.846 | 543.6743
2964.0354 | 681.9014 | 422.233 | 576.1905 | 541.7706 | 600.5142 | 582.0257 | 543.87
2965.0354 | 682.9194 | 422.2295 | 576.0762 | 541.9348 | 601.6437 | 579.824 | 544.6471
2966.0354 | 685.1466 | 423.1486 | 576.4606 | 542.8364 | 600.9353 | 577.8453 | 545.2585
2967.0354 | 684.1437 | 424.7392 | 577.0684 | 543.5065 | 603.5599 | 576.5882 | 547.9855
2968.0354 | 682.0848 | 423.9091 | 577.1334 | 543.8573 | 605.8713 | 574.9615 | 547.4404
2969.0354 | 680.0866 | 423.4423 | 576.6786 | 543.489 | 607.614 | 574.1673 | 546.0831
2970.0354 | 677.7422 | 423.8279 | 576.975 | 543.9033 | 608.1575 | 575.0042 | 546.4028
2971.0354 | 670.9314 | 424.5414 | 576.8028 | 544.8553 | 607.3518 | 576.2726 | 546.0193
2972.0354 | 657.8918 | 424.4988 | 576.7088 | 544.6624 | 605.3801 | 575.8647 | 545.6566
2973.0354 | 654.1647 | 424.4953 | 577.4456 | 544.6251 | 604.0919 | 574.4036 | 544.7294
2974.0354 | 653.156 | 425.355 | 576.9093 | 544.293 | 603.708 | 574.9944 | 544.2674
2975.0354 | 651.452 | 427.2604 | 577.8314 | 544.4135 | 603.3183 | 575.277 | 545.3248
2976.0354 | 648.3486 | 427.2804 | 576.8732 | 544.6726 | 601.6398 | 575.2743 | 545.0462
2977.0354 | 650.9371 | 426.7728 | 577.2556 | 545.0474 | 601.1819 | 575.99 | 544.0718
2978.0354 | 652.3311 | 428.5531 | 578.6606 | 546.1882 | 601.7156 | 575.4125 | 544.925
2979.0354 | 658.3044 | 427.8736 | 577.5553 | 546.099 | 600.5669 | 573.5536 | 543.9494
2980.0354 | 664.9024 | 428.539 | 576.3923 | 545.6145 | 601.776 | 572.9201 | 542.5087
2981.0354 | 654.2427 | 427.5696 | 577.1514 | 545.2624 | 602.514 | 572.2447 | 541.6616
2982.0354 | 657.2034 | 428.4105 | 577.083 | 545.3575 | 601.9488 | 574.1621 | 541.5948
2983.0354 | 658.6592 | 428.3629 | 576.9454 | 545.8779 | 602.1821 | 575.9584 | 541.2597
2984.0354 | 660.0658 | 428.49 | 577.5701 | 546.1394 | 603.4866 | 576.1024 | 541.1949
2985.0354 | 659.1641 | 428.681 | 578.9679 | 545.9756 | 603.3761 | 576.1025 | 541.6834
2986.0354 | 658.5026 | 428.7255 | 578.3298 | 545.9399 | 602.9517 | 577.2847 | 542.5655
2987.0354 | 657.5647 | 430.3385 | 577.3175 | 546.3241 | 603.0974 | 578.6949 | 542.7339
2988.0354 | 658.3547 | 430.6211 | 577.5506 | 546.194 | 603.7948 | 580.5905 | 543.5534
2989.0354 | 657.5524 | 430.3836 | 577.864 | 546.2752 | 603.0238 | 585.418 | 546.1839
2990.0354 | 657.6578 | 429.8742 | 578.1364 | 546.0966 | 602.6824 | 585.0077 | 545.1119
2991.0354 | 672.8202 | 428.6849 | 578.1341 | 547.4525 | 600.6464 | 583.8762 | 545.4743
2992.0354 | 674.5532 | 428.6739 | 578.1923 | 546.843 | 601.21 | 584.3773 | 544.6446
2993.0354 | 671.5027 | 433.3442 | 573.9825 | 546.8272 | 606.648 | 586.1133 | 542.1793
2994.0354 | 679.6986 | 428.3089 | 576.9943 | 546.4533 | 603.3337 | 587.5258 | 545.8572
2995.0354 | 682.8587 | 430.1578 | 577.442 | 546.7371 | 603.1854 | 590.4843 | 547.9946
2996.0354 | 675.13 | 430.2655 | 577.4445 | 547.0896 | 602.0409 | 590.0481 | 548.9922
2997.0354 | 660.7644 | 429.878 | 577.8973 | 547.1198 | 602.5497 | 590.966 | 549.926
2998.0354 | 659.1674 | 430.42 | 578.0464 | 548.4059 | 602.5225 | 588.7133 | 549.4296
2999.0354 | 656.562 | 430.5012 | 579.467 | 548.8724 | 601.4606 | 586.6182 | 548.5627
3000.0354 | 656.2683 | 430.6941 | 578.3623 | 549.0919 | 600.3398 | 584.6367 | 548.0177
3001.0354 | 654.6103 | 430.2508 | 577.5771 | 548.6941 | 600.2776 | 583.8116 | 546.5909
3002.0354 | 670.2857 | 430.1135 | 577.5871 | 548.7092 | 600.4039 | 582.269 | 546.0554
3003.0354 | 654.7575 | 429.9988 | 577.9534 | 549.2009 | 601.0633 | 581.7058 | 546.0226
3004.0354 | 653.9395 | 431.5535 | 577.9301 | 548.6003 | 602.6754 | 581.7025 | 545.7958
3005.0354 | 653.7406 | 431.17 | 578.2018 | 548.9779 | 604.7894 | 583.9409 | 547.4384
3006.0354 | 651.9116 | 430.977 | 578.5803 | 549.0934 | 604.2778 | 584.4726 | 548.1114
3007.0354 | 650.4201 | 432.6698 | 578.2515 | 548.9142 | 603.6667 | 585.3636 | 548.1093
3008.0354 | 652.1198 | 431.7021 | 577.3959 | 549.1315 | 601.5512 | 584.1749 | 548.0992
3009.0354 | 656.153 | 433.3205 | 577.4242 | 548.7722 | 601.2943 | 583.0019 | 545.9564
3010.0354 | 665.5231 | 432.8366 | 577.4998 | 550.4682 | 601.6151 | 580.9816 | 544.9515
3011.0354 | 659.3627 | 433.0335 | 577.3545 | 552.9523 | 601.8555 | 579.9659 | 544.5976
3012.0354 | 656.5986 | 432.4216 | 577.1116 | 552.3637 | 603.2377 | 576.8887 | 543.4675
3013.0354 | 657.4708 | 434.4645 | 577.0219 | 550.6383 | 604.6087 | 575.0851 | 541.9302
3014.0354 | 660.2484 | 434.6885 | 577.4868 | 550.9216 | 605.1488 | 575.9224 | 541.7883
3015.0354 | 676.4668 | 433.0596 | 577.5964 | 551.3273 | 605.4735 | 578.3507 | 542.7004
3016.0354 | 665.4928 | 434.0311 | 578.672 | 551.3202 | 606.3269 | 580.1783 | 543.6915
3017.0354 | 666.9275 | 435.0044 | 578.5717 | 551.7101 | 604.8182 | 580.2866 | 544.0184
3018.0354 | 677.4658 | 435.8683 | 578.0798 | 552.1875 | 604.1814 | 582.1063 | 544.9032
3019.0354 | 660.8065 | 435.9972 | 579.0877 | 551.9108 | 603.76 | 583.2041 | 546.7459
3020.0354 | 657.9955 | 438.4486 | 578.1559 | 552.4155 | 604.0927 | 583.8258 | 546.2614
3021.0354 | 655.1197 | 439.0326 | 579.5122 | 552.3809 | 603.2296 | 582.3367 | 546.383
3022.0354 | 671.5044 | 439.3038 | 579.6597 | 552.209 | 602.0398 | 580.4168 | 545.8484
3023.0354 | 647.7754 | 438.867 | 580.6661 | 552.4729 | 601.1619 | 580.301 | 546.1001
3024.0354 | 660.6313 | 437.1788 | 578.8645 | 553.1532 | 601.4411 | 580.1573 | 545.5265
3025.0354 | 643.8619 | 435.9632 | 578.4409 | 553.0102 | 603.8528 | 582.0114 | 545.4769
3026.0354 | 645.2337 | 435.7689 | 578.1079 | 552.8246 | 603.5569 | 581.5469 | 544.6594
3027.0354 | 645.403 | 436.8465 | 578.4815 | 553.2874 | 603.8155 | 579.1158 | 544.1936
3028.0354 | 646.5495 | 438.6836 | 578.9184 | 554.2032 | 605.1478 | 578.6334 | 543.5012
3029.0354 | 645.402 | 439.7415 | 578.8419 | 554.2384 | 604.2337 | 577.0106 | 543.662
3030.0354 | 644.2747 | 440.2145 | 579.1954 | 553.4977 | 603.5486 | 576.7018 | 543.2078
3031.0354 | 643.3927 | 439.4815 | 579.1481 | 554.3782 | 604.3365 | 578.6446 | 545.1973
3032.0354 | 645.4571 | 440.4441 | 579.0661 | 555.1115 | 604.271 | 578.0411 | 545.4067
3033.0354 | 645.0496 | 440.8159 | 578.974 | 554.5047 | 602.8222 | 576.4919 | 544.799
3034.0354 | 657.4703 | 442.1097 | 579.1622 | 554.8547 | 601.3935 | 576.3563 | 545.1795
3035.0354 | 644.6594 | 442.7934 | 580.1821 | 554.8561 | 601.2434 | 575.1514 | 544.6388
3036.0354 | 643.4462 | 443.8836 | 578.89 | 554.4418 | 600.3217 | 575.4118 | 544.7301
3037.0354 | 647.0187 | 445.2574 | 579.8659 | 555.3486 | 600.243 | 576.3907 | 545.0196
3038.0354 | 646.2186 | 445.2967 | 579.602 | 555.406 | 600.78 | 577.5531 | 545.7492
3039.0354 | 671.6821 | 443.7642 | 579.4129 | 555.3015 | 601.3453 | 579.4068 | 545.8813
3040.0354 | 672.487 | 445.4455 | 579.2941 | 555.3322 | 601.3061 | 579.9005 | 546.397
3041.0354 | 643.1134 | 446.1405 | 578.9568 | 555.6197 | 600.8495 | 579.7725 | 546.239
3042.0354 | 641.783 | 443.1643 | 579.4779 | 555.6178 | 600.9326 | 580.4025 | 546.0012
3043.0354 | 640.7766 | 442.6796 | 579.3832 | 555.6115 | 600.9168 | 579.7721 | 545.079
3044.0354 | 639.6918 | 447.4985 | 580.4485 | 556.0654 | 600.3355 | 578.8686 | 544.0394
3045.0354 | 637.9093 | 445.3974 | 579.4583 | 555.6222 | 600.283 | 578.6974 | 543.8189
3046.0354 | 640.4806 | 446.5125 | 579.4083 | 556.2011 | 600.0618 | 577.1215 | 543.2451
3047.0354 | 639.4791 | 445.8287 | 579.3147 | 557.0631 | 599.1404 | 575.1319 | 542.8621
3048.0354 | 651.2911 | 447.1514 | 579.3036 | 557.4524 | 599.0912 | 574.7734 | 542.1414
3049.0354 | 650.3963 | 446.7518 | 579.1331 | 557.6453 | 597.6289 | 572.4185 | 541.3991
3050.0354 | 649.3012 | 445.9576 | 579.6159 | 557.7041 | 596.769 | 571.6824 | 541.1697
3051.0354 | 648.3721 | 447.4379 | 579.0897 | 557.1482 | 595.7874 | 571.1361 | 541.022
3052.0354 | 647.4003 | 447.6662 | 579.8137 | 557.3708 | 595.0153 | 572.044 | 540.9948
3053.0354 | 645.4697 | 448.2431 | 579.3355 | 557.3536 | 595.6323 | 573.1658 | 540.9168
3054.0354 | 644.7744 | 447.841 | 578.5483 | 558.662 | 596.2153 | 572.5559 | 540.7301
3055.0354 | 644.2082 | 448.5912 | 578.7441 | 558.322 | 597.4952 | 572.2122 | 540.5806
3056.0354 | 642.5701 | 450.2529 | 579.0248 | 557.9587 | 596.665 | 573.4556 | 541.1947
3057.0354 | 644.1786 | 450.6558 | 578.5503 | 557.8497 | 597.691 | 574.2558 | 542.3134
3058.0354 | 644.3718 | 451.2883 | 579.0246 | 557.7929 | 599.5009 | 575.5609 | 542.8652
3059.0354 | 642.2144 | 451.5838 | 581.4558 | 558.1655 | 599.6285 | 576.7197 | 544.0982
3060.0354 | 640.5232 | 449.5574 | 580.0433 | 558.4089 | 598.531 | 577.844 | 544.9872
3061.0354 | 641.7408 | 449.5606 | 579.6525 | 558.2505 | 597.4292 | 583.1418 | 548.6105
3062.0354 | 642.1361 | 452.3174 | 581.1091 | 558.5318 | 596.7608 | 581.4383 | 547.9816
3063.0354 | 637.9084 | 451.3782 | 581.6462 | 558.5747 | 594.5979 | 579.1955 | 547.305
3064.0354 | 635.0626 | 452.6554 | 580.4425 | 558.9063 | 592.9333 | 577.4243 | 545.9975
3065.0354 | 634.9385 | 451.3792 | 579.9785 | 558.8021 | 592.5803 | 576.9966 | 546.5654
3066.0354 | 647.676 | 451.7066 | 582.6766 | 558.9962 | 592.3362 | 576.8079 | 547.4736
3067.0354 | 667.093 | 452.7488 | 582.6248 | 559.5577 | 593.0727 | 576.6985 | 547.8525
3068.0354 | 665.9403 | 452.3831 | 582.8988 | 559.3459 | 592.7682 | 576.2675 | 547.6744
3069.0354 | 664.5505 | 454.8981 | 583.0603 | 559.4198 | 592.9069 | 574.3679 | 546.6092
3070.0354 | 663.5493 | 453.7842 | 584.4311 | 559.9374 | 592.7676 | 573.9798 | 545.745
3071.0354 | 663.5711 | 454.616 | 583.1999 | 559.5919 | 592.2068 | 572.5155 | 545.177
3072.0354 | 665.961 | 453.7763 | 581.867 | 558.9019 | 593.5168 | 576.4353 | 546.4862
3073.0354 | 658.2925 | 455.6008 | 581.9562 | 560.0577 | 593.9117 | 578.9743 | 548.3562
3074.0354 | 665.1856 | 456.7643 | 583.3925 | 559.6482 | 594.3222 | 578.5514 | 548.173
3075.0354 | 663.0743 | 455.7249 | 583.6458 | 559.4953 | 592.4405 | 576.8316 | 547.3346
3076.0354 | 665.0637 | 455.5297 | 583.3578 | 559.329 | 592.3104 | 576.4312 | 546.3798
3077.0354 | 664.1911 | 456.9426 | 585.9026 | 559.5623 | 592.3982 | 576.9747 | 546.5089
3078.0354 | 665.9827 | 456.4852 | 586.2566 | 560.2814 | 592.1729 | 577.696 | 547.7332
3079.0354 | 667.8883 | 457.1874 | 588.2455 | 559.987 | 591.7373 | 579.5222 | 549.4589
3080.0354 | 666.7174 | 455.7815 | 588.3105 | 559.7421 | 590.7961 | 578.204 | 549.4559
3081.0354 | 665.1549 | 454.7685 | 588.667 | 560.1952 | 589.4959 | 578.1712 | 550.2744
3082.0354 | 664.8954 | 455.8628 | 587.1144 | 560.5327 | 588.6714 | 575.7688 | 549.4581
3083.0354 | 666.8724 | 458.4047 | 586.7862 | 560.0181 | 587.2861 | 575.0568 | 548.8309
3084.0354 | 667.3709 | 457.8823 | 588.651 | 560.6713 | 586.2216 | 574.1128 | 548.6261
3085.0354 | 664.682 | 456.2897 | 588.7639 | 560.5108 | 586.6592 | 573.1587 | 548.2234
3086.0354 | 663.1958 | 458.0376 | 589.0068 | 560.6034 | 585.866 | 572.0458 | 547.4135
3087.0354 | 662.604 | 460.2766 | 587.445 | 560.4165 | 586.9614 | 572.3711 | 547.7797
3088.0354 | 665.2005 | 460.9583 | 586.823 | 560.2419 | 589.0766 | 574.4399 | 548.3367
3089.0354 | 667.9599 | 461.5373 | 587.0144 | 560.065 | 591.7921 | 575.8334 | 548.2232
3090.0354 | 669.0016 | 460.8001 | 586.8857 | 560.0459 | 592.512 | 574.9348 | 547.2295
3091.0354 | 672.0469 | 461.2949 | 586.9384 | 560.101 | 593.1108 | 573.873 | 545.9213
3092.0354 | 677.9516 | 459.8722 | 586.591 | 559.9739 | 594.3264 | 574.6774 | 545.4454
3093.0354 | 678.9701 | 461.835 | 586.9326 | 559.8869 | 594.1072 | 574.2698 | 546.0322
3094.0354 | 677.2579 | 461.209 | 587.397 | 559.8535 | 592.2989 | 572.1191 | 545.4571
3095.0354 | 677.1115 | 460.4519 | 587.2635 | 560.3786 | 591.8291 | 573.6315 | 545.154
3096.0354 | 680.8895 | 460.061 | 586.8323 | 560.1991 | 594.2412 | 577.294 | 545.9765
3097.0354 | 684.5279 | 460.1883 | 586.596 | 559.8786 | 595.5884 | 578.7475 | 547.8532
3098.0354 | 685.6551 | 460.8308 | 586.7965 | 560.371 | 595.1824 | 579.2379 | 549.864
3099.0354 | 684.4413 | 462.6836 | 587.2923 | 560.148 | 594.0975 | 579.2138 | 550.678
3100.0354 | 685.6685 | 463.9187 | 586.8583 | 561.2794 | 594.163 | 578.3182 | 549.8667
3101.0354 | 683.2743 | 464.3444 | 587.0006 | 560.6855 | 593.4851 | 577.4215 | 550.2006
3102.0354 | 684.1014 | 462.6381 | 587.3323 | 560.6881 | 593.3569 | 577.7343 | 549.2403
3103.0354 | 684.539 | 463.1739 | 586.5007 | 560.4119 | 594.6896 | 577.4254 | 549.3431
3104.0354 | 683.5939 | 464.5276 | 586.4687 | 560.4669 | 594.2499 | 575.7693 | 547.8348
3105.0354 | 687.1671 | 465.2536 | 586.6361 | 560.5473 | 593.6098 | 573.82 | 546.1522
3106.0354 | 687.715 | 465.3656 | 587.4703 | 560.756 | 592.4993 | 573.1295 | 545.6404
3107.0354 | 688.7528 | 463.6432 | 586.7957 | 561.2702 | 591.017 | 572.3349 | 545.5494
3108.0354 | 691.8426 | 462.8653 | 586.4426 | 562.0496 | 592.1961 | 571.3039 | 545.2228
3109.0354 | 693.2264 | 462.5102 | 586.7069 | 562.2127 | 592.6184 | 570.8599 | 544.2183
3110.0354 | 697.0897 | 464.824 | 587.1753 | 562.395 | 592.0008 | 570.6229 | 544.1033
3111.0354 | 694.8193 | 465.3236 | 586.5465 | 562.3331 | 592.3114 | 569.8219 | 544.6395
3112.0354 | 694.1529 | 465.7354 | 586.513 | 562.2276 | 592.8038 | 570.0374 | 544.4591
3113.0354 | 695.9729 | 465.7526 | 586.2337 | 561.5727 | 593.3997 | 571.1813 | 545.0233
3114.0354 | 698.2536 | 465.9123 | 586.2367 | 561.9528 | 593.9083 | 570.4022 | 544.3238
3115.0354 | 698.1703 | 466.2742 | 585.7003 | 561.4678 | 597.0185 | 573.1504 | 544.5948
3116.0354 | 700.4345 | 466.2921 | 585.9166 | 561.8523 | 598.2492 | 573.9186 | 545.0784
3117.0354 | 699.1236 | 466.3254 | 585.9915 | 562.2401 | 598.0915 | 573.5907 | 544.9546
3118.0354 | 697.289 | 466.2582 | 586.7463 | 562.6156 | 597.1956 | 573.1545 | 544.9362
3119.0354 | 694.3192 | 467.5933 | 585.9482 | 562.2586 | 595.8327 | 573.1233 | 545.1917
3120.0354 | 689.0005 | 468.2277 | 586.7373 | 562.7351 | 595.1224 | 573.0257 | 545.5085
3121.0354 | 684.9257 | 466.6599 | 587.9938 | 562.5218 | 594.4835 | 572.6874 | 545.9453
3122.0354 | 682.2873 | 466.2776 | 588.8277 | 562.3582 | 593.1812 | 572.5958 | 546.3737
3123.0354 | 678.3936 | 466.2993 | 588.5765 | 562.2619 | 591.1498 | 572.7854 | 547.4484
3124.0354 | 675.839 | 468.5841 | 588.5678 | 562.1887 | 588.6166 | 572.6352 | 549.0172
3125.0354 | 673.3412 | 468.8362 | 588.9458 | 562.0551 | 586.4393 | 573.0336 | 549.7425
3126.0354 | 670.194 | 470.114 | 589.277 | 562.2171 | 585.1964 | 572.1405 | 548.9587
3127.0354 | 667.4698 | 468.6601 | 588.7917 | 561.8647 | 583.7991 | 571.2934 | 548.7338
3128.0354 | 667.3989 | 469.009 | 588.1606 | 561.9101 | 582.5307 | 571.6283 | 548.1364
3129.0354 | 666.1365 | 471.327 | 587.6171 | 561.6869 | 584.0652 | 574.1209 | 548.6646
3130.0354 | 666.8338 | 472.4681 | 588.7904 | 562.9344 | 583.9669 | 573.2229 | 548.5687
3131.0354 | 666.1995 | 471.3673 | 590.4429 | 562.0541 | 583.7383 | 573.3742 | 548.8996
3132.0354 | 667.3531 | 472.5395 | 588.6401 | 561.9682 | 582.9018 | 572.5437 | 548.903
3133.0354 | 658.2822 | 473.023 | 588.0454 | 562.8532 | 583.2057 | 573.5788 | 549.1868
3134.0354 | 671.5779 | 473.5778 | 588.3759 | 562.283 | 584.3255 | 574.2143 | 549.4716
3135.0354 | 670.9921 | 473.0027 | 589.2431 | 562.2349 | 583.7236 | 573.7356 | 549.2966
3136.0354 | 670.6283 | 472.1186 | 589.9448 | 562.0709 | 583.074 | 573.1364 | 549.6301
3137.0354 | 668.9219 | 474.9669 | 589.8135 | 562.6185 | 582.8406 | 573.2427 | 549.9233
3138.0354 | 670.1548 | 472.5199 | 590.5582 | 563.1761 | 582.5568 | 575.8527 | 550.3316
3139.0354 | 667.4742 | 472.2055 | 590.3205 | 562.8475 | 582.9251 | 577.032 | 552.1767
3140.0354 | 668.9762 | 473.7752 | 591.17 | 563.436 | 582.6493 | 576.4626 | 551.5544
3141.0354 | 666.3835 | 473.3668 | 591.4571 | 563.1317 | 582.3727 | 575.7537 | 551.0124
3142.0354 | 666.969 | 475.4516 | 591.4996 | 563.7668 | 582.6328 | 576.5065 | 551.4105
3143.0354 | 667.5539 | 475.5735 | 592.7249 | 563.4734 | 583.4084 | 577.059 | 552.9744
3144.0354 | 663.3982 | 474.1446 | 593.4092 | 562.716 | 583.5652 | 576.6397 | 553.3698
3145.0354 | 665.2442 | 475.3328 | 595.5143 | 562.6172 | 583.2177 | 575.9797 | 553.0297
3146.0354 | 663.4125 | 474.4555 | 595.3529 | 562.3555 | 582.2092 | 575.3469 | 553.5544
3147.0354 | 665.0591 | 474.6325 | 594.4062 | 562.398 | 581.7051 | 574.6275 | 553.614
3148.0354 | 663.6912 | 476.4456 | 593.5719 | 562.2569 | 579.8653 | 573.741 | 553.7698
3149.0354 | 665.2576 | 477.6646 | 592.4342 | 562.6121 | 580.1653 | 575.4571 | 554.1376
3150.0354 | 670.67 | 477.007 | 593.7037 | 563.4092 | 581.1816 | 573.7558 | 553.2455
3151.0354 | 671.1209 | 476.312 | 593.3679 | 563.2158 | 580.6063 | 572.1946 | 551.6341
3152.0354 | 667.2958 | 476.5646 | 594.0078 | 563.4294 | 578.8882 | 570.3363 | 551.7518
3153.0354 | 665.1631 | 476.9572 | 593.8598 | 563.0529 | 577.9912 | 569.3643 | 551.3902
3154.0354 | 666.513 | 478.1393 | 593.2215 | 562.6446 | 576.7398 | 568.8621 | 551.6418
3155.0354 | 665.5204 | 477.9285 | 593.2555 | 562.3659 | 577.9345 | 574.3055 | 553.7548
3156.0354 | 669.5284 | 476.0806 | 594.2031 | 562.5852 | 579.2335 | 576.1165 | 554.3718
3157.0354 | 668.168 | 475.581 | 593.9062 | 563.5951 | 579.9552 | 575.8531 | 554.2581
3158.0354 | 669.7597 | 475.4717 | 595.1969 | 563.445 | 580.6552 | 574.3957 | 553.5572
3159.0354 | 670.7011 | 476.6166 | 596.5508 | 563.5212 | 580.3165 | 573.8982 | 553.4621
3160.0354 | 671.0388 | 476.3298 | 595.5251 | 562.7504 | 580.1985 | 573.8126 | 553.0794
3161.0354 | 671.2279 | 476.5792 | 595.5814 | 563.0808 | 580.4003 | 574.3551 | 553.8302
3162.0354 | 673.3652 | 476.1493 | 595.3172 | 562.8306 | 580.2354 | 574.2362 | 553.627
3163.0354 | 672.4309 | 477.2723 | 595.2569 | 562.9796 | 579.2647 | 574.0283 | 552.9723
3164.0354 | 669.8301 | 478.4199 | 595.9509 | 563.7517 | 579.2095 | 573.0152 | 552.4137
3165.0354 | 670.731 | 480.0016 | 595.82 | 564.0135 | 579.539 | 573.4245 | 551.924
3166.0354 | 672.4739 | 479.94 | 595.1602 | 564.265 | 579.7176 | 572.7936 | 551.5351
3167.0354 | 677.7625 | 479.0065 | 594.8403 | 563.4678 | 579.9979 | 573.0839 | 551.3859
3168.0354 | 682.0059 | 479.5226 | 595.3582 | 563.5665 | 580.397 | 573.1007 | 551.2051
3169.0354 | 684.2804 | 478.5089 | 595.9863 | 562.9951 | 581.6584 | 573.3031 | 551.4183
3170.0354 | 686.4223 | 477.5482 | 595.6802 | 562.9126 | 582.2964 | 575.3492 | 552.6737
3171.0354 | 685.6327 | 477.5151 | 595.5218 | 563.137 | 583.2312 | 578.3896 | 554.4878
3172.0354 | 687.5566 | 477.5851 | 595.4458 | 562.9657 | 584.4647 | 580.7318 | 554.9835
3173.0354 | 687.7328 | 480.6487 | 596.4977 | 563.0242 | 585.2078 | 581.3066 | 555.5504
3174.0354 | 685.1859 | 481.3526 | 596.4543 | 562.6423 | 584.5466 | 581.0922 | 555.6618
3175.0354 | 683.4898 | 480.0537 | 596.4004 | 562.6342 | 583.9288 | 580.8509 | 555.2783
3176.0354 | 686.0897 | 482.304 | 596.5038 | 562.4724 | 583.7121 | 581.6191 | 557.538
3177.0354 | 686.4573 | 480.5483 | 597.206 | 562.7049 | 582.3471 | 582.6159 | 558.957
3178.0354 | 686.6062 | 481.3069 | 597.461 | 562.609 | 581.6472 | 580.8851 | 559.4422
3179.0354 | 703.3777 | 481.5426 | 596.7046 | 562.7712 | 580.7528 | 580.7497 | 560.6095
3180.0354 | 702.9231 | 482.4591 | 596.3272 | 562.3149 | 580.6761 | 580.9731 | 559.5981
3181.0354 | 705.9576 | 481.9947 | 597.2652 | 562.3835 | 579.5207 | 580.0185 | 558.7272
3182.0354 | 712.6225 | 483.1025 | 598.6423 | 562.8829 | 579.1007 | 579.3206 | 558.9466
3183.0354 | 722.5439 | 483.377 | 598.9773 | 563.336 | 579.8452 | 579.5317 | 558.6103
3184.0354 | 723.1735 | 482.9928 | 600.8502 | 562.737 | 578.3257 | 577.654 | 557.2033
3185.0354 | 764.7296 | 484.0705 | 600.4956 | 563.1622 | 577.3785 | 576.0975 | 557.7156
3186.0354 | 765.3588 | 483.9429 | 599.6774 | 562.8706 | 577.7731 | 574.7007 | 557.554
3187.0354 | 744.668 | 483.313 | 599.3434 | 563.8906 | 576.8327 | 573.4614 | 556.4586
3188.0354 | 768.6468 | 484.6205 | 598.4063 | 563.6993 | 576.8477 | 573.0904 | 556.2635
3189.0354 | 793.0955 | 484.5335 | 597.9805 | 564.27 | 578.2258 | 572.824 | 555.5084
3190.0354 | 819.3097 | 484.1635 | 598.0455 | 564.4283 | 579.3127 | 570.3854 | 553.2294
3191.0354 | 843.2397 | 484.8776 | 598.6674 | 564.1006 | 578.053 | 567.6039 | 550.8971
3192.0354 | 840.3063 | 485.334 | 598.9024 | 563.6153 | 577.3029 | 566.2083 | 549.3601
3193.0354 | 870.5042 | 485.2868 | 599.052 | 564.2345 | 577.4252 | 566.499 | 549.3566
3194.0354 | 871.7845 | 485.821 | 599.2083 | 564.1821 | 577.8236 | 566.0405 | 548.8172
3195.0354 | 872.302 | 486.5884 | 599.3865 | 563.7469 | 576.4209 | 566.6789 | 548.7979
3196.0354 | 877.6379 | 486.1332 | 599.4243 | 563.417 | 576.0776 | 570.037 | 550.1002
3197.0354 | 878.4096 | 486.0275 | 599.0456 | 563.3953 | 576.4797 | 574.0022 | 552.5808
3198.0354 | 880.1524 | 485.7648 | 600.3486 | 563.5481 | 576.6041 | 575.2949 | 553.566
3199.0354 | 882.2694 | 486.8638 | 599.9535 | 563.8763 | 576.6042 | 575.0466 | 553.5775
3200.0354 | 882.3124 | 489.3066 | 598.6073 | 563.2229 | 577.168 | 576.5143 | 556.6436
3201.0354 | 886.2271 | 488.7945 | 599.7637 | 563.096 | 577.4174 | 575.008 | 558.0199
3202.0354 | 884.8664 | 488.5658 | 599.7457 | 562.9464 | 576.8153 | 574.3997 | 558.8393
3203.0354 | 885.2072 | 488.9685 | 600.0434 | 562.9172 | 576.6867 | 575.926 | 559.8028
3204.0354 | 883.7535 | 490.6424 | 599.8197 | 563.3646 | 576.1129 | 576.2035 | 560.4204
3205.0354 | 883.6441 | 489.9983 | 599.8882 | 563.363 | 575.719 | 575.2335 | 558.7434
3206.0354 | 883.8952 | 489.0276 | 600.4321 | 563.4173 | 575.9474 | 574.348 | 558.0166
3207.0354 | 881.6382 | 490.5672 | 600.0249 | 563.3558 | 575.8935 | 575.8124 | 557.8986
3208.0354 | 881.019 | 491.0388 | 600.2654 | 563.1363 | 576.5842 | 577.7302 | 559.1833
3209.0354 | 886.1072 | 491.9027 | 599.3707 | 562.7768 | 579.3984 | 583.1777 | 561.8936
3210.0354 | 888.319 | 491.6384 | 599.5346 | 563.0804 | 579.5779 | 583.0773 | 561.454
3211.0354 | 889.5116 | 491.8369 | 599.0472 | 562.8906 | 580.1116 | 584.8442 | 561.674
3212.0354 | 888.4966 | 490.9221 | 599.0778 | 562.373 | 579.6176 | 585.4636 | 564.1223
3213.0354 | 892.392 | 491.1382 | 599.5023 | 562.4731 | 578.5833 | 584.8462 | 563.2238
3214.0354 | 894.919 | 490.3315 | 599.2249 | 562.8972 | 577.3304 | 584.8784 | 563.3388
3215.0354 | 896.0728 | 491.2756 | 601.1317 | 563.06 | 578.711 | 584.7783 | 561.7012
3216.0354 | 892.9514 | 491.213 | 601.1167 | 563.1778 | 577.9382 | 583.1964 | 561.3037
3217.0354 | 891.4895 | 491.1763 | 602.5795 | 563.0214 | 577.556 | 581.8357 | 560.8333
3218.0354 | 888.3369 | 491.2147 | 601.8642 | 563.9164 | 578.0445 | 581.1647 | 559.9405
3219.0354 | 889.8868 | 493.3339 | 602.3344 | 563.3037 | 578.3618 | 581.2949 | 560.1856
3220.0354 | 888.0852 | 493.3973 | 601.6783 | 564.2596 | 578.7308 | 582.1538 | 560.9794
3221.0354 | 887.8817 | 493.1731 | 600.8692 | 563.3723 | 578.4394 | 581.0023 | 559.9542
3222.0354 | 886.968 | 494.7377 | 600.8785 | 563.2355 | 577.4891 | 580.1062 | 559.6404
3223.0354 | 892.039 | 495.8209 | 601.5285 | 563.7768 | 576.9297 | 578.8029 | 558.1308
3224.0354 | 890.8239 | 494.184 | 602.5559 | 564.3068 | 576.9928 | 576.6175 | 557.776
3225.0354 | 890.8167 | 494.3696 | 603.9196 | 563.2682 | 576.6584 | 576.2499 | 557.1343
3226.0354 | 889.4171 | 495.277 | 603.9405 | 564.4342 | 577.1343 | 577.7214 | 558.0476
3227.0354 | 559.2128 | 495.4388 | 603.2223 | 564.3225 | 577.2176 | 577.448 | 558.8725
3228.0354 | 562.6858 | 495.6068 | 602.8945 | 563.9845 | 576.1139 | 576.6524 | 558.0556
3229.0354 | 560.3757 | 495.5327 | 603.6514 | 563.5832 | 576.1513 | 577.1229 | 558.2037
3230.0354 | 552.0379 | 496.5625 | 605.2606 | 563.7812 | 575.944 | 577.5811 | 558.9686
3231.0354 | 551.1532 | 495.5549 | 605.5815 | 564.5588 | 574.8517 | 576.4828 | 559.7358
3232.0354 | 542.7096 | 496.165 | 604.4822 | 565.7751 | 574.4332 | 576 | 559.2389
3233.0354 | 541.3645 | 496.2244 | 604.0058 | 564.9322 | 573.9014 | 575.1204 | 558.2179
3234.0354 | 536.6949 | 497.0822 | 604.383 | 564.4229 | 573.8701 | 573.5765 | 556.8606
3235.0354 | 532.9501 | 498.7425 | 605.0217 | 564.2835 | 573.9937 | 572.811 | 555.6543
3236.0354 | 534.6493 | 498.1431 | 605.3246 | 564.6776 | 574.4959 | 573.8527 | 555.3738
3237.0354 | 536.3117 | 498.6932 | 607.9934 | 564.0633 | 574.9822 | 575.1269 | 556.4021
3238.0354 | 537.9383 | 499.0034 | 607.9178 | 564.2239 | 575.9294 | 575.2378 | 557.7217
3239.0354 | 538.7154 | 499.9936 | 608.3813 | 564.9623 | 574.8821 | 575.7691 | 558.7337
3240.0354 | 537.1603 | 501.0077 | 608.0397 | 564.4266 | 575.0611 | 575.7291 | 560.5369
3241.0354 | 535.6802 | 500.6482 | 609.8276 | 564.1512 | 575.2908 | 575.7716 | 562.5073
3242.0354 | 608.1106 | 500.6021 | 609.0402 | 564.3913 | 574.6005 | 576.5352 | 564.8803
3243.0354 | 561.5501 | 500.0837 | 609.882 | 564.4452 | 573.5917 | 574.8175 | 566.1718
3244.0354 | 560.4109 | 501.2733 | 610.3322 | 564.4849 | 574.2656 | 574.9508 | 566.1353
3245.0354 | 570.2427 | 501.7692 | 610.9953 | 565.2778 | 574.822 | 574.3422 | 565.3873
3246.0354 | 625.3694 | 500.7114 | 609.72 | 564.6478 | 574.3329 | 574.2225 | 563.934
3247.0354 | 770.3582 | 501.7167 | 610.4689 | 564.9526 | 574.2357 | 575.102 | 563.1609
3248.0354 | 839.6466 | 500.9226 | 610.4487 | 565.0128 | 574.1012 | 573.7576 | 561.3282
3249.0354 | 848.1396 | 501.4037 | 609.7797 | 564.4034 | 573.6907 | 572.4278 | 558.8274
3250.0354 | 846.5696 | 500.9427 | 609.4763 | 564.6078 | 575.118 | 572.4449 | 563.3457
3251.0354 | 851.7338 | 502.4506 | 610.9044 | 566.4789 | 575.7409 | 573.4114 | 564.6637
3252.0354 | 853.5143 | 502.6175 | 611.4802 | 566.0249 | 576.6001 | 574.9005 | 564.6202
3253.0354 | 855.9861 | 502.5259 | 612.7567 | 566.2622 | 576.4863 | 575.4294 | 565.4326
3254.0354 | 854.8754 | 502.3812 | 612.2055 | 565.3883 | 575.6464 | 573.5345 | 564.7063
3255.0354 | 853.1881 | 502.3501 | 612.2851 | 564.7485 | 574.8185 | 573.3582 | 563.8958
3256.0354 | 854.4506 | 503.1437 | 612.3718 | 565.1101 | 573.7769 | 573.4961 | 563.6638
3257.0354 | 855.2178 | 502.6316 | 611.7578 | 565.2403 | 573.7505 | 575.1658 | 563.547
3258.0354 | 853.3098 | 501.894 | 611.9426 | 566.762 | 573.6429 | 574.3389 | 563.3085
3259.0354 | 853.2522 | 501.9967 | 612.9596 | 565.6208 | 573.773 | 573.8157 | 562.0233
3260.0354 | 852.858 | 501.7748 | 612.5751 | 565.0311 | 573.2885 | 573.2546 | 561.2895
3261.0354 | 853.102 | 501.9571 | 612.0132 | 566.2152 | 573.3379 | 573.5892 | 560.6429
3262.0354 | 852.5226 | 501.7361 | 612.6332 | 566.3765 | 573.325 | 573.3219 | 559.6507
3263.0354 | 853.9296 | 501.7562 | 613.6738 | 565.8822 | 573.2001 | 573.5892 | 559.3397
3264.0354 | 851.8967 | 503.8094 | 612.7622 | 565.7727 | 572.5803 | 572.8868 | 558.6298
3265.0354 | 853.6724 | 505.6223 | 612.5708 | 565.5665 | 571.9078 | 573.6714 | 559.1132
3266.0354 | 853.2933 | 505.2871 | 612.73 | 567.01 | 572.1973 | 572.9594 | 558.6169
3267.0354 | 857.0511 | 505.6712 | 612.8243 | 568.3847 | 572.7869 | 571.3137 | 557.2383
3268.0354 | 858.0353 | 504.836 | 613.3044 | 566.9373 | 573.217 | 569.3464 | 555.7727
3269.0354 | 854.0655 | 505.5737 | 612.7357 | 566.4398 | 572.0092 | 568.365 | 554.0978
3270.0354 | 854.7686 | 506.5155 | 612.7043 | 565.8529 | 571.5497 | 569.9235 | 554.7706
3271.0354 | 855.6767 | 507.4713 | 612.271 | 566.3697 | 571.3821 | 571.9408 | 555.5453
3272.0354 | 856.2518 | 508.2295 | 612.7163 | 566.5414 | 571.8622 | 573.1608 | 555.7777
3273.0354 | 865.508 | 506.847 | 612.4645 | 567.4097 | 572.063 | 572.3595 | 555.054
3274.0354 | 856.0997 | 507.4102 | 612.335 | 568.1301 | 571.7914 | 570.2323 | 553.8946
3275.0354 | 861.586 | 508.277 | 613.8699 | 567.7878 | 571.4284 | 568.0087 | 552.8039
3276.0354 | 876.8898 | 508.2619 | 613.9028 | 567.8256 | 571.242 | 567.669 | 553.2264
3277.0354 | 878.6495 | 508.0932 | 614.1148 | 567.5856 | 571.7199 | 568.8349 | 553.8121
3278.0354 | 759.1303 | 507.705 | 615.0396 | 567.5937 | 571.2961 | 567.4407 | 553.1329
3279.0354 | 876.7145 | 508.5322 | 615.1425 | 568.1711 | 571.142 | 568.593 | 553.9288
3280.0354 | 881.6396 | 507.8365 | 614.9488 | 568.1722 | 570.3059 | 567.188 | 554.7436
3281.0354 | 812.078 | 509.0474 | 614.3958 | 568.4567 | 570.1353 | 566.6972 | 554.3784
3282.0354 | 886.2386 | 509.1101 | 614.8722 | 567.7491 | 569.6738 | 566.2366 | 553.665
3283.0354 | 887.766 | 508.4611 | 615.4763 | 567.7632 | 569.191 | 566.5768 | 554.4471
3284.0354 | 887.4797 | 508.5616 | 616.4131 | 568.0343 | 568.9622 | 567.049 | 556.3882
3285.0354 | 892.6258 | 509.1626 | 614.8751 | 568.1255 | 568.3537 | 567.6051 | 557.2073
3286.0354 | 890.1848 | 511.0446 | 614.0871 | 567.6713 | 569.4392 | 569.5974 | 556.822
3287.0354 | 894.4307 | 509.8111 | 614.4414 | 567.2725 | 570.7408 | 572.1647 | 558.664
3288.0354 | 898.3502 | 509.0612 | 614.0738 | 567.237 | 572.2657 | 574.0522 | 559.7226
3289.0354 | 896.4228 | 508.768 | 615.0439 | 568.081 | 572.2796 | 573.5194 | 560.609
3290.0354 | 899.4336 | 510.9548 | 614.9033 | 567.6141 | 572.5318 | 573.8484 | 560.5421
3291.0354 | 899.0242 | 510.7135 | 616.2364 | 567.871 | 572.6118 | 573.8727 | 560.4794
3292.0354 | 897.1344 | 509.5641 | 614.9373 | 567.9479 | 572.46 | 573.0665 | 559.7517
3293.0354 | 893.4621 | 510.0092 | 614.5602 | 569.5142 | 572.44 | 571.8678 | 558.273
3294.0354 | 896.9836 | 510.3792 | 614.8508 | 569.1637 | 572.5108 | 569.5378 | 556.2973
3295.0354 | 898.3528 | 511.7826 | 614.4617 | 568.6193 | 572.8028 | 566.9769 | 553.9516
3296.0354 | 903.3835 | 511.1583 | 614.9749 | 568.2432 | 571.8389 | 565.6945 | 553.2071
3297.0354 | 906.8745 | 511.9684 | 614.3404 | 568.0921 | 571.9718 | 565.9349 | 553.2621
3298.0354 | 906.4032 | 512.7358 | 613.9985 | 568.2581 | 571.5098 | 565.9431 | 552.883
3299.0354 | 910.7228 | 512.6493 | 613.9521 | 569.3743 | 571.737 | 566.3386 | 552.3392
3300.0354 | 910.9254 | 513.5333 | 614.1582 | 568.8408 | 573.4461 | 566.655 | 551.5159
3301.0354 | 911.5467 | 514.5812 | 615.0441 | 569.5435 | 573.3236 | 566.3014 | 551.3382
3302.0354 | 914.9889 | 512.8162 | 615.2929 | 570.0886 | 573.4335 | 565.2656 | 551.0796
3303.0354 | 917.3604 | 513.3734 | 616.5605 | 569.5763 | 573.0049 | 564.8933 | 551.4415
3304.0354 | 918.769 | 514.0708 | 615.5845 | 569.4289 | 572.4062 | 563.9967 | 551.6121
3305.0354 | 914.5368 | 513.6209 | 615.3205 | 568.7957 | 571.8382 | 563.2803 | 550.5878
3306.0354 | 913.8394 | 513.2537 | 615.2677 | 569.2493 | 570.9537 | 563.4417 | 550.2724
3307.0354 | 916.7056 | 512.8991 | 614.7462 | 569.9313 | 571.0087 | 564.091 | 551.6242
3308.0354 | 930.7648 | 513.7503 | 613.8445 | 569.1952 | 571.2279 | 565.1934 | 551.6269
3309.0354 | 934.5951 | 515.3348 | 613.6888 | 568.896 | 571.1918 | 564.5802 | 551.2196
3310.0354 | 937.0141 | 515.426 | 613.6237 | 568.5898 | 571.8118 | 563.5292 | 549.7829
3311.0354 | 938.2795 | 514.8707 | 614.0469 | 568.4986 | 571.4795 | 562.9839 | 548.9861
3312.0354 | 940.5429 | 515.4938 | 614.1867 | 569.5086 | 570.4249 | 563.1309 | 549.0986
3313.0354 | 939.6745 | 514.3614 | 613.363 | 569.2737 | 569.8623 | 561.4505 | 548.2025
3314.0354 | 941.0445 | 514.6998 | 612.9427 | 568.6261 | 569.3732 | 561.9903 | 547.6665
3315.0354 | 942.3837 | 515.5376 | 612.8997 | 568.3141 | 568.9154 | 563.5793 | 551.0819
3316.0198 | 948.5048 | 514.6826 | 612.7411 | 568.3732 | 569.1921 | 566.9262 | 555.0712
3317.0354 | 948.4478 | 515.0517 | 612.4505 | 568.4326 | 568.6919 | 567.6893 | 557.0321
3318.0354 | 946.0841 | 514.6267 | 612.3241 | 568.2245 | 568.0295 | 568.1055 | 556.2983
3319.0354 | 947.7935 | 515.6915 | 612.2479 | 568.5828 | 567.5395 | 567.3011 | 555.0176
3320.0354 | 948.1856 | 516.6011 | 612.3655 | 568.8052 | 567.4177 | 565.9668 | 554.1298
3321.0354 | 945.8409 | 515.5711 | 612.6282 | 568.867 | 566.8429 | 565.1877 | 552.7257
3322.0354 | 944.2688 | 515.5534 | 611.8392 | 569.7192 | 566.5297 | 564.0448 | 551.0904
3323.0354 | 944.3011 | 516.0786 | 611.5332 | 569.4436 | 566.7145 | 562.9856 | 552.9792
3324.0354 | 942.1525 | 516.2107 | 610.9551 | 569.4516 | 567.1187 | 561.8714 | 551.7804
3325.0354 | 946.6596 | 517.0998 | 611.064 | 569.838 | 567.0071 | 560.1945 | 550.629
3326.0354 | 819.367 | 517.0892 | 611.1613 | 569.6617 | 566.8698 | 559.7871 | 549.5801
3327.0354 | 949.3192 | 517.8191 | 611.0356 | 569.2949 | 567.4296 | 559.9686 | 549.37
3328.0354 | 831.0538 | 518.2523 | 610.829 | 569.5804 | 567.0968 | 561.187 | 551.4615
3329.0354 | 959.5353 | 518.0472 | 610.7577 | 569.3344 | 567.1976 | 561.7626 | 551.3645
3330.0354 | 963.63 | 518.1687 | 610.4408 | 569.3137 | 567.7713 | 561.1984 | 550.7538
3331.0354 | 963.0529 | 518.7862 | 610.1219 | 569.4913 | 567.7783 | 560.5744 | 549.8415
3332.0354 | 958.9388 | 519.394 | 610.0386 | 569.8216 | 567.4509 | 560.0335 | 549.2318
3333.0354 | 962.5994 | 519.5219 | 609.4132 | 569.1112 | 568.1352 | 560.6199 | 548.6223
3334.0354 | 960.8288 | 519.5712 | 608.9585 | 568.6371 | 567.6269 | 560.0364 | 548.9158
3335.0354 | 964.304 | 519.3028 | 610.2529 | 568.3983 | 566.8195 | 558.7675 | 548.2612
3336.0354 | 967.1099 | 518.0147 | 610.5844 | 568.758 | 566.4831 | 560.1067 | 549.8179
3337.0354 | 969.5486 | 517.8447 | 609.7369 | 568.6139 | 566.3119 | 562.0265 | 553.6867
3338.0354 | 971.3703 | 519.8814 | 609.0106 | 568.4177 | 567.7638 | 563.8002 | 554.914
3339.0354 | 967.8349 | 518.6004 | 609.0233 | 568.2039 | 567.8805 | 563.6844 | 554.5376
3340.0354 | 966.4045 | 519.17 | 610.0641 | 568.1239 | 567.1448 | 562.9301 | 554.0758
3341.0354 | 970.3983 | 520.3541 | 609.2282 | 568.0178 | 566.9538 | 564.3377 | 555.3309
3342.0354 | 968.865 | 519.5223 | 609.8093 | 568.242 | 566.047 | 563.8559 | 555.8248
3343.0354 | 976.332 | 518.6884 | 610.4843 | 568.0721 | 565.5095 | 565.2599 | 558.1607
3344.0354 | 978.3716 | 518.7222 | 610.1506 | 568.7126 | 565.1871 | 566.0803 | 559.295
3345.0354 | 980.4104 | 518.7821 | 609.4941 | 568.787 | 565.4613 | 566.125 | 558.2067
3346.0354 | 980.1873 | 518.8042 | 609.2591 | 568.4875 | 565.6243 | 565.8156 | 557.6073
3347.0354 | 982.5833 | 521.5445 | 608.669 | 568.0444 | 565.8439 | 566.278 | 557.2434
3348.0354 | 986.8834 | 521.4167 | 608.9561 | 567.83 | 565.7603 | 566.2367 | 559.5112
3349.0354 | 990.622 | 521.5738 | 611.0594 | 567.9839 | 566.3969 | 566.8824 | 558.9308
3350.0354 | 989.3078 | 520.9546 | 610.387 | 568.5521 | 567.7266 | 569.4116 | 561.2707
3351.0354 | 991.772 | 520.4037 | 612.1706 | 568.7438 | 566.4253 | 567.7525 | 563.5485
3352.0354 | 993.0948 | 522.0802 | 611.9439 | 568.2404 | 565.8202 | 566.4174 | 563.7385
3353.0354 | 995.5019 | 525.3287 | 613.1501 | 568.5103 | 566.1519 | 565.919 | 564.3486
3354.0354 | 998.7569 | 521.8605 | 612.8748 | 569.1052 | 564.839 | 565.4842 | 565.0142
3355.0354 | 1005.944 | 522.9824 | 613.5847 | 568.6449 | 564.5933 | 565.1213 | 563.8508
3356.0354 | 1007.9049 | 522.55 | 613.5851 | 568.4642 | 563.9124 | 564.6353 | 561.9762
3357.0354 | 1016.7805 | 525.4235 | 615.154 | 569.9904 | 564.9162 | 565.3835 | 560.0106
3358.0354 | 867.9686 | 521.4791 | 612.4525 | 569.2138 | 563.4915 | 565.112 | 561.3369
3359.0354 | 1020.7073 | 521.7008 | 612.6643 | 569.2697 | 564.1345 | 565.5274 | 560.2407
3360.0354 | 1022.4007 | 521.017 | 611.7912 | 568.2075 | 564.2484 | 565.0096 | 558.9807
3361.0354 | 920.5918 | 521.2906 | 613.288 | 568.4149 | 564.5389 | 564.964 | 558.1827
3362.0354 | 1024.9726 | 521.2505 | 613.065 | 568.6965 | 564.7988 | 566.0312 | 557.6149
3363.0354 | 1027.5259 | 521.3358 | 613.2711 | 569.3609 | 564.5892 | 566.0727 | 557.2748
3364.0354 | 1029.5495 | 521.6496 | 613.8522 | 569.2105 | 564.512 | 565.7659 | 557.5873
3365.0354 | 1032.1822 | 522.0116 | 614.8474 | 568.9556 | 563.4612 | 564.1675 | 556.8754
3366.0354 | 1032.3162 | 523.1172 | 613.7454 | 568.7163 | 562.5555 | 562.9746 | 556.6415
3367.0354 | 1031.1175 | 524.2428 | 613.3344 | 567.9947 | 561.9505 | 563.5858 | 556.8137
3368.0354 | 1030.915 | 523.5491 | 612.4538 | 567.979 | 562.144 | 565.1811 | 557.0139
3369.0354 | 1029.4949 | 523.8888 | 612.0616 | 568.5297 | 562.2084 | 564.3947 | 555.9174
3370.0354 | 1030.0929 | 523.0766 | 612.0668 | 568.551 | 561.5282 | 563.2324 | 554.3617
3371.0354 | 1032.1133 | 522.3368 | 611.8527 | 568.0402 | 561.2082 | 562.3783 | 553.4045
3372.0354 | 902.6847 | 523.5659 | 611.3829 | 567.6986 | 562.0451 | 562.7336 | 553.0017
3373.0354 | 867.0205 | 523.1244 | 610.8443 | 567.1691 | 563.3894 | 565.4058 | 554.4867
3374.0354 | 1029.5088 | 524.8683 | 610.5679 | 567.2754 | 564.6271 | 565.2253 | 553.6054
3375.0354 | 1036.1878 | 524.2081 | 610.1809 | 567.2225 | 565.8863 | 565.4791 | 555.4099
3376.0354 | 1036.6467 | 523.2691 | 610.4654 | 567.0921 | 565.2227 | 563.5235 | 555.7977
3377.0354 | 1033.9987 | 523.166 | 610.8898 | 567.2514 | 563.9645 | 562.545 | 554.6967
3378.0354 | 1033.8431 | 524.5421 | 610.099 | 568.0458 | 563.0464 | 561.9082 | 554.1783
3379.0354 | 1033.6863 | 524.5155 | 610.9107 | 567.6219 | 562.2211 | 560.8585 | 553.132
3380.0354 | 972.7456 | 523.5614 | 610.7306 | 567.3558 | 561.2595 | 559.8357 | 551.3139
3381.0354 | 1035.879 | 523.4585 | 610.5601 | 567.9445 | 561.3637 | 559.5553 | 553.2774
3382.0354 | 1031.965 | 523.4546 | 609.804 | 567.3303 | 561.5386 | 559.2414 | 552.3587
3383.0354 | 1033.2035 | 525.6246 | 609.126 | 567.0548 | 561.562 | 557.7734 | 550.9572
3384.0354 | 1033.9015 | 525.3554 | 608.8277 | 567.2424 | 561.9946 | 556.7286 | 551.7052
3385.0354 | 1033.5137 | 524.7754 | 608.853 | 566.8736 | 561.2136 | 554.8926 | 552.6694
3386.0354 | 1036.0814 | 524.4927 | 610.265 | 566.7281 | 559.4414 | 552.9893 | 552.2562
3387.0354 | 1030.2808 | 523.7161 | 609.6085 | 567.1617 | 557.9323 | 552.8669 | 551.1157
3388.0354 | 1029.8687 | 523.6898 | 609.4773 | 566.681 | 557.4434 | 553.467 | 551.0634
3389.0354 | 1022.6822 | 524.5418 | 609.1097 | 566.645 | 557.3916 | 554.8628 | 551.9734
3390.0354 | 1020.242 | 525.4206 | 609.3127 | 567.3174 | 557.4731 | 555.6975 | 551.7223
3391.0354 | 1022.8664 | 524.8858 | 608.7614 | 567.8627 | 557.5746 | 555.8111 | 550.9232
3392.0354 | 1020.3093 | 525.6888 | 607.9764 | 566.6749 | 557.7744 | 556.308 | 549.9593
3393.0354 | 1010.2714 | 525.0521 | 609.2286 | 567.4403 | 557.8894 | 556.4511 | 549.7752
3394.0354 | 1017.4759 | 524.9346 | 608.574 | 566.8167 | 557.2236 | 556.3223 | 549.7257
3395.0354 | 1016.2849 | 524.6636 | 611.3222 | 566.7301 | 556.9295 | 556.2101 | 549.0612
3396.0354 | 1025.4538 | 524.9593 | 610.1088 | 566.8152 | 556.7014 | 555.7151 | 549.1579
3397.0354 | 1028.3373 | 524.8068 | 609.8208 | 566.3807 | 556.4473 | 556.3704 | 548.7973
3398.0354 | 1032.7684 | 524.8056 | 609.7576 | 566.5422 | 557.0742 | 557.613 | 549.9422
3399.0354 | 1034.9257 | 524.3813 | 609.7253 | 567.2874 | 558.2377 | 558.329 | 549.4666
3400.0354 | 1038.6092 | 524.9263 | 610.6845 | 567.5046 | 559.2098 | 559.2948 | 552.968
3401.0354 | 1040.8556 | 526.0383 | 609.4736 | 567.3867 | 560.1691 | 560.0778 | 558.1766
3402.0354 | 1036.6693 | 525.3961 | 609.9035 | 567.9503 | 560.2079 | 558.7066 | 556.7417
3403.0354 | 1037.6199 | 524.9212 | 609.0341 | 569.1938 | 560.428 | 558.0224 | 555.8093
3404.0354 | 1038.3436 | 525.4543 | 609.676 | 569.1998 | 559.4798 | 556.754 | 554.6978
3405.0354 | 1038.223 | 526.652 | 608.8636 | 567.5609 | 557.5697 | 554.648 | 552.8739
3406.0354 | 1039.6518 | 527.0951 | 609.7156 | 567.8055 | 556.7406 | 554.2183 | 551.2352
3407.0354 | 1043.7232 | 526.2407 | 609.3384 | 568.1231 | 557.3673 | 555.5513 | 551.3452
3408.0354 | 1055.4734 | 525.7047 | 608.9527 | 568.2241 | 557.8896 | 554.8514 | 551.0208
3409.0354 | 1056.8245 | 525.9401 | 609.3106 | 569.0091 | 557.9881 | 554.2227 | 549.8214
3410.0354 | 1062.1922 | 526.8098 | 609.1703 | 568.7157 | 557.4663 | 553.0318 | 549.0957
3411.0354 | 1055.2024 | 525.9735 | 608.9955 | 567.9378 | 556.8378 | 552.2964 | 548.7872
3412.0354 | 1059.5416 | 525.5494 | 611.0646 | 567.7315 | 556.0341 | 552.7441 | 548.7906
3413.0354 | 1061.7327 | 525.7103 | 609.2671 | 568.33 | 555.7531 | 553.8094 | 549.5065
3414.0354 | 1065.7097 | 525.4065 | 609.2597 | 567.9497 | 555.9602 | 554.1187 | 550.0719
3415.0354 | 1065.8245 | 525.0981 | 610.3574 | 568.7223 | 556.2442 | 554.7838 | 550.3554
3416.0354 | 986.5072 | 525.1624 | 612.0429 | 569.0918 | 556.1534 | 555.0943 | 550.0758
3417.0354 | 1005.1189 | 525.2608 | 611.896 | 568.7854 | 557.7861 | 557.226 | 551.94
3418.0354 | 651.561 | 525.7541 | 611.6233 | 568.8023 | 557.8492 | 558.1697 | 554.7981
3419.0354 | 644.4473 | 527.226 | 610.7005 | 569.0553 | 556.1457 | 556.3468 | 553.9143
3420.0354 | 644.6189 | 526.7467 | 611.4045 | 568.5781 | 556.1575 | 555.7282 | 552.863
3421.0354 | 642.8469 | 526.66 | 611.6705 | 568.7426 | 555.4712 | 556.2671 | 552.5996
3422.0354 | 643.145 | 526.3404 | 611.2126 | 568.4315 | 556.1488 | 557.1624 | 552.3391
3423.0354 | 643.3116 | 526.7672 | 610.8193 | 568.2578 | 556.7214 | 560.4047 | 554.2116
3424.0354 | 644.0502 | 526.9211 | 611.342 | 568.3515 | 557.6961 | 561.0033 | 553.7842
3425.0354 | 644.7642 | 526.2339 | 610.3621 | 568.1132 | 558.9323 | 562.18 | 554.1043
3426.0354 | 644.1693 | 526.8557 | 609.6168 | 567.6661 | 559.9946 | 563.8629 | 553.6308
3427.0354 | 646.4383 | 527.5235 | 610.3864 | 567.9761 | 559.4479 | 563.4559 | 553.7804
3428.0354 | 643.5346 | 526.5344 | 609.669 | 567.6197 | 559.519 | 564.5362 | 553.9764
3429.0354 | 628.3253 | 527.1493 | 609.9026 | 567.6619 | 559.9468 | 563.6606 | 553.7284
3430.0354 | 605.1332 | 527.008 | 609.6395 | 567.2464 | 559.4701 | 562.5799 | 552.4787
3431.0354 | 636.8467 | 526.8742 | 609.1086 | 567.3284 | 558.9481 | 561.4899 | 551.2903
3432.0354 | 636.1612 | 526.9761 | 608.6295 | 567.2557 | 558.0108 | 560.7544 | 550.247
3433.0354 | 625.6448 | 527.1222 | 608.4135 | 566.7292 | 557.83 | 559.6601 | 549.3146
3434.0354 | 638.6032 | 527.8496 | 608.175 | 566.7231 | 557.6085 | 558.8042 | 548.3656
3435.0354 | 638.6342 | 528.342 | 608.1955 | 567.0323 | 558.1217 | 558.5263 | 548.0104
3436.0354 | 639.2276 | 529.3523 | 607.6534 | 566.8173 | 558.7414 | 558.0962 | 546.8821
3437.0354 | 638.602 | 528.8188 | 608.0974 | 566.7441 | 558.1184 | 557.0328 | 546.2307
3438.0354 | 638.1995 | 528.2869 | 608.6984 | 566.7056 | 557.4836 | 555.9488 | 545.3861
3439.0354 | 638.8614 | 527.3791 | 608.2228 | 566.6829 | 556.6958 | 554.4443 | 543.9515
3440.0354 | 639.3335 | 527.2453 | 608.7606 | 566.3864 | 556.4762 | 554.6648 | 543.522
3441.0354 | 637.7676 | 526.9787 | 609.9715 | 566.4868 | 556.1446 | 555.0038 | 543.9351
3442.0354 | 636.3293 | 527.1282 | 610.784 | 566.4958 | 556.0765 | 555.0811 | 544.1583
3443.0354 | 635.7373 | 527.3982 | 611.1481 | 566.2868 | 556.0208 | 555.813 | 545.6298
3444.0354 | 635.8551 | 527.2854 | 611.611 | 566.0766 | 555.4342 | 556.0417 | 547.0666
3445.0354 | 635.4847 | 527.4517 | 611.4889 | 566.1171 | 554.6153 | 555.4204 | 548.1852
3446.0354 | 635.5332 | 527.542 | 610.1269 | 566.0881 | 554.4975 | 556.2491 | 549.0263
3447.0354 | 636.2822 | 527.6661 | 610.6778 | 566.006 | 554.1418 | 557.4226 | 549.8219
3448.0354 | 638.3168 | 527.3073 | 610.8246 | 566.0732 | 555.2275 | 558.0509 | 550.0848
3449.0354 | 638.3413 | 527.3419 | 611.9063 | 565.8025 | 555.8776 | 558.2699 | 550.6078
3450.0354 | 638.4347 | 527.2467 | 611.4393 | 566.5653 | 556.3642 | 557.9975 | 551.5173
3451.0354 | 641.5016 | 527.6358 | 612.3239 | 566.7941 | 556.5844 | 558.5712 | 552.6622
3452.0354 | 640.7517 | 528.2445 | 612.6135 | 566.153 | 556.6852 | 558.8136 | 553.943
3453.0354 | 640.7284 | 528.5377 | 612.2156 | 566.3638 | 556.7447 | 558.6441 | 554.2805
3454.0354 | 640.9346 | 528.3589 | 611.0084 | 566.0042 | 556.3075 | 557.7943 | 553.4145
3455.0354 | 641.3251 | 527.829 | 611.1012 | 566.8527 | 556.2738 | 557.5527 | 552.812
3456.0354 | 641.6964 | 527.6771 | 612.1682 | 566.3467 | 556.187 | 557.6673 | 552.7728
3457.0354 | 640.1497 | 527.8633 | 612.6091 | 566.1882 | 555.3545 | 556.1014 | 554.0229
3458.0354 | 637.2366 | 527.8983 | 613.9444 | 565.752 | 554.4598 | 554.7563 | 554.693
3459.0354 | 635.7722 | 528.7456 | 614.8016 | 565.7187 | 553.446 | 554.3685 | 553.9782
3460.0354 | 638.316 | 529.1972 | 614.9632 | 565.6966 | 552.6867 | 554.2967 | 554.0416
3461.0354 | 637.6806 | 529.2592 | 615.5035 | 565.494 | 553.1839 | 555.6237 | 554.9282
3462.0354 | 635.8795 | 529.0862 | 615.9768 | 565.1263 | 552.6984 | 556.6564 | 554.9656
3463.0354 | 636.0908 | 528.5787 | 614.3209 | 564.9883 | 552.4767 | 556.5861 | 554.981
3464.0354 | 638.2091 | 528.9988 | 616.0422 | 564.9455 | 552.4068 | 558.0253 | 555.9518
3465.0354 | 640.2343 | 529.4881 | 617.6515 | 565.2013 | 552.8389 | 560.247 | 558.6368
3466.0354 | 640.3669 | 529.1282 | 618.7072 | 564.7193 | 553.5066 | 561.7143 | 561.6364
3467.0354 | 641.2724 | 528.8487 | 619.1194 | 564.821 | 552.7078 | 562.4335 | 562.3425
3468.0354 | 643.5571 | 528.7302 | 618.3211 | 564.5835 | 552.177 | 562.5763 | 564.0266
3469.0354 | 639.9275 | 528.5987 | 619.3199 | 564.5411 | 551.7799 | 561.8803 | 563.1001
3470.0354 | 638.9571 | 529.2337 | 618.296 | 564.9569 | 551.736 | 562.3959 | 565.4972
3471.0354 | 636.6575 | 528.942 | 618.5644 | 564.8771 | 550.3664 | 560.7904 | 565.5676
3472.0354 | 636.739 | 528.9946 | 619.9554 | 564.3954 | 550.194 | 559.6793 | 563.2629
3473.0354 | 636.7965 | 529.0014 | 619.9154 | 564.345 | 551.4708 | 559.1919 | 562.0749
3474.0354 | 637.7774 | 528.5805 | 620.0806 | 564.7347 | 551.971 | 559.235 | 560.0551
3475.0354 | 638.9789 | 528.6553 | 619.7582 | 565.3114 | 552.9746 | 560.2453 | 559.2689
3476.0354 | 638.5715 | 528.5235 | 620.8196 | 564.7297 | 553.4336 | 560.4733 | 558.6837
3477.0354 | 638.6547 | 528.3657 | 622.33 | 564.4715 | 553.433 | 559.4719 | 558.3327
3478.0354 | 635.6082 | 528.499 | 621.9056 | 564.1875 | 552.8928 | 558.9564 | 557.4207
3479.0354 | 635.8629 | 528.716 | 620.979 | 564.4732 | 552.7689 | 558.4121 | 557.0112
3480.0354 | 635.3707 | 529.0464 | 620.2477 | 564.9797 | 553.4593 | 557.5468 | 555.5894
3481.0354 | 635.2596 | 529.021 | 621.8956 | 564.6428 | 553.8082 | 556.5404 | 554.0517
3482.0354 | 636.1096 | 528.9479 | 622.5826 | 564.0201 | 554.2005 | 557.5608 | 554.2374
3483.0354 | 637.3396 | 528.9413 | 621.3398 | 564.504 | 555.1338 | 558.2694 | 554.1803
3484.0354 | 638.0689 | 528.7866 | 620.9633 | 564.5774 | 556.164 | 559.4037 | 553.8469
3485.0354 | 638.224 | 528.6784 | 620.341 | 563.9372 | 556.2125 | 558.3197 | 552.2963
3486.0354 | 603.4234 | 528.7512 | 620.4911 | 564.0591 | 555.3864 | 556.8928 | 551.7962
3487.0354 | 612.471 | 528.2233 | 620.6333 | 564.315 | 554.8499 | 556.8076 | 550.9884
3488.0354 | 595.8876 | 528.2053 | 620.1972 | 564.1926 | 554.669 | 555.9415 | 550.1092
3489.0354 | 605.5926 | 528.509 | 620.2678 | 563.6223 | 554.7236 | 556.2353 | 549.2743
3490.0354 | 651.7989 | 529.6325 | 619.5075 | 563.1782 | 554.526 | 557.4669 | 555.0932
3491.0354 | 603.0145 | 529.5737 | 619.8905 | 563.0863 | 553.5362 | 558.4695 | 555.4423
3492.0354 | 623.0523 | 529.779 | 620.0092 | 563.1371 | 552.9209 | 558.594 | 554.132
3493.0354 | 634.1326 | 528.4077 | 619.5461 | 563.0953 | 551.8603 | 557.9433 | 556.543
3494.0354 | 633.4611 | 528.8277 | 619.2461 | 562.9187 | 551.4521 | 557.8594 | 555.0168
3495.0354 | 633.8973 | 528.1151 | 618.9414 | 563.1152 | 551.8144 | 557.2817 | 554.4866
3496.0354 | 632.2659 | 527.7027 | 621.3964 | 562.9446 | 551.7952 | 556.3188 | 552.8449
3497.0354 | 630.8115 | 528.3085 | 621.2845 | 562.7405 | 552.4096 | 555.5541 | 551.5623
3498.0354 | 629.3316 | 528.6524 | 619.6978 | 563.2402 | 552.6454 | 555.5774 | 550.225
3499.0354 | 628.7878 | 528.1457 | 620.4251 | 563.6405 | 552.8571 | 554.4348 | 550.3591
3500.0354 | 625.9642 | 527.8551 | 619.7913 | 564.1173 | 552.872 | 554.0135 | 549.6966
3501.0354 | 624.6084 | 528.9167 | 619.417 | 563.6532 | 553.0186 | 553.3294 | 548.4613
3502.0354 | 623.3098 | 528.5226 | 621.1106 | 562.9975 | 552.8351 | 552.3597 | 547.2191
3503.0354 | 623.9981 | 529.4683 | 620.0196 | 563.1763 | 552.6286 | 551.7896 | 546.4881
3504.0354 | 623.541 | 528.4078 | 620.6561 | 563.8152 | 553.4834 | 551.7989 | 546.4023
3505.0354 | 622.2027 | 527.9955 | 620.6501 | 564.3715 | 553.1707 | 551.3552 | 548.094
3506.0354 | 620.7425 | 528.2348 | 619.4386 | 563.9898 | 553.0836 | 550.649 | 548.2939
3507.0354 | 615.0083 | 529.4664 | 619.9842 | 564.1955 | 553.0186 | 549.4798 | 548.5007
3508.0354 | 615.7429 | 529.1822 | 620.3483 | 563.8795 | 551.6659 | 547.7856 | 548.1327
3509.0354 | 613.9934 | 529.3271 | 619.3335 | 563.7798 | 550.7474 | 545.626 | 546.6839
3510.0354 | 613.4871 | 528.7072 | 620.1189 | 563.3827 | 549.7921 | 544.8466 | 545.1755
3511.0354 | 613.0674 | 528.554 | 621.5549 | 563.1266 | 549.5543 | 545.2642 | 544.6756
3512.0354 | 611.7818 | 529.6961 | 619.9261 | 564.6416 | 549.9747 | 545.1216 | 544.1412
3513.0354 | 611.4649 | 528.8824 | 620.779 | 564.0033 | 551.1266 | 545.9138 | 543.2515
3514.0354 | 612.783 | 528.202 | 620.4285 | 564.2119 | 551.693 | 546.1782 | 543.2735
3515.0354 | 612.9552 | 528.1281 | 619.3654 | 563.6522 | 551.4121 | 545.0788 | 542.373
3516.0354 | 612.8281 | 528.1156 | 620.2063 | 564.1708 | 551.6601 | 544.3341 | 543.3426
3517.0354 | 612.5973 | 528.5111 | 619.9806 | 564.6533 | 551.7337 | 544.454 | 542.854
3518.0354 | 612.8154 | 528.4936 | 620.4039 | 563.6525 | 552.9204 | 545.3909 | 542.8763
3519.0354 | 612.9542 | 529.0461 | 620.6208 | 563.5735 | 552.8245 | 546.8209 | 543.5343
3520.0354 | 612.8688 | 528.8651 | 619.1181 | 564.2957 | 553.0773 | 548.3165 | 543.9394
3521.0354 | 612.5285 | 528.5947 | 619.2334 | 564.5435 | 553.8477 | 548.6237 | 543.6432
3522.0354 | 612.0135 | 528.4047 | 620.7154 | 563.9508 | 553.8371 | 548.3609 | 543.3497
3523.0354 | 612.1517 | 528.9031 | 619.1448 | 563.9861 | 554.1996 | 548.8047 | 542.8822
3524.0354 | 611.8052 | 528.3886 | 618.7162 | 564.0659 | 554.2018 | 548.2833 | 541.9531
3525.0354 | 611.9207 | 528.1319 | 618.9291 | 563.6547 | 553.9787 | 548.3179 | 541.4368
3526.0354 | 612.4475 | 527.884 | 620.0159 | 564.7151 | 554.0421 | 548.4203 | 541.2843
3527.0354 | 612.0455 | 527.7816 | 619.9108 | 564.6558 | 553.8642 | 548.6017 | 542.0114
3528.0354 | 611.0096 | 527.6122 | 618.3383 | 564.3877 | 553.5828 | 548.0738 | 541.3062
3529.0354 | 609.8572 | 527.4711 | 618.0623 | 564.5012 | 554.2638 | 547.4347 | 541.6802
3530.0354 | 608.909 | 527.6059 | 618.2987 | 564.4799 | 554.154 | 545.9296 | 541.6939
3531.0354 | 608.3579 | 529.0126 | 618.9383 | 565.3114 | 553.3766 | 544.9199 | 541.5314
3532.0354 | 608.5112 | 528.0523 | 618.2302 | 564.5088 | 553.2473 | 543.7712 | 541.4039
3533.0354 | 607.9963 | 527.5979 | 617.9216 | 564.2864 | 552.7822 | 544.0106 | 542.27
3534.0354 | 608.2198 | 527.1661 | 617.1747 | 563.7981 | 552.432 | 544.7786 | 543.0144
3535.0354 | 607.4408 | 527.5293 | 616.8336 | 563.688 | 552.6736 | 545.7384 | 542.1267
3536.0354 | 606.1059 | 527.1685 | 618.0671 | 563.9565 | 552.2266 | 545.0791 | 540.2922
3537.0354 | 605.2641 | 527.1453 | 618.0327 | 563.5748 | 551.5112 | 544.4266 | 539.1296
3538.0354 | 605.2664 | 527.0601 | 618.1707 | 563.5664 | 551.1604 | 544.5319 | 538.7523
3539.0354 | 604.97 | 526.8576 | 618.5253 | 563.4711 | 550.5143 | 544.8332 | 539.1898
3540.0354 | 604.3631 | 526.8907 | 616.7564 | 563.4533 | 550.1602 | 544.9811 | 538.889
3541.0354 | 602.8285 | 526.9397 | 615.9881 | 562.9414 | 549.5855 | 544.1424 | 538.0299
3542.0354 | 602.419 | 527.2973 | 615.935 | 562.8408 | 549.1152 | 543.962 | 538.2455
3543.0354 | 601.1623 | 527.1564 | 615.6308 | 562.7494 | 548.4008 | 543.8525 | 538.2723
3544.0354 | 600.7644 | 526.9419 | 615.1235 | 562.5211 | 547.2053 | 543.857 | 538.315
3545.0354 | 601.1055 | 526.843 | 614.7476 | 562.1116 | 546.6538 | 544.5784 | 538.8449
3546.0354 | 601.8343 | 527.4854 | 614.6538 | 562.0578 | 545.6301 | 546.4902 | 540.1581
3547.0354 | 582.3961 | 526.8937 | 614.7391 | 562.3932 | 544.853 | 545.8482 | 541.2014
3548.0354 | 581.5128 | 526.7401 | 616.1969 | 562.4064 | 544.3562 | 544.8222 | 540.955
3549.0354 | 581.7734 | 526.3328 | 616.2342 | 562.2159 | 543.723 | 544.8198 | 540.8864
3550.0354 | 580.7805 | 525.8943 | 615.0877 | 562.1692 | 543.2095 | 544.6126 | 539.9142
3551.0354 | 581.2133 | 525.7877 | 614.1745 | 561.7587 | 543.9921 | 544.79 | 539.613
3552.0354 | 582.9913 | 526.1765 | 613.572 | 561.4807 | 544.9454 | 545.585 | 539.1153
3553.0354 | 582.1601 | 525.8945 | 613.0285 | 561.5177 | 544.9635 | 545.3711 | 538.6412
3554.0354 | 580.8687 | 525.5508 | 613.8399 | 561.8769 | 543.9605 | 543.3387 | 537.0888
3555.0354 | 580.5351 | 525.3204 | 613.1443 | 561.8328 | 543.4166 | 542.3219 | 536.4226
3556.0354 | 579.6238 | 525.4069 | 612.8792 | 562.9313 | 543.1457 | 541.1951 | 534.8881
3557.0354 | 579.8465 | 525.3081 | 612.7278 | 562.543 | 543.351 | 540.0235 | 533.4913
3558.0354 | 578.6645 | 524.97 | 612.1852 | 562.7102 | 543.6973 | 538.5827 | 531.8952
3559.0354 | 595.1117 | 525.5646 | 612.6056 | 562.815 | 544.1495 | 537.1038 | 530.1485
3560.0354 | 598.8699 | 525.1161 | 612.5775 | 561.7156 | 543.673 | 536.3323 | 528.9443
3561.0354 | 598.8787 | 524.9715 | 611.7187 | 561.3525 | 544.9043 | 537.527 | 534.754
3562.0354 | 599.4548 | 524.6926 | 611.9603 | 562.1999 | 545.1967 | 537.3578 | 534.6827
3563.0354 | 599.8011 | 524.2754 | 611.7679 | 562.3505 | 545.4543 | 537.6056 | 533.6509
3564.0354 | 596.2213 | 524.0938 | 612.9481 | 561.9244 | 546.328 | 537.557 | 532.6589
3565.0354 | 589.6059 | 523.9746 | 612.5077 | 562.0993 | 546.3561 | 538.0161 | 532.2613
3566.0354 | 600.7868 | 523.9003 | 611.8194 | 561.5134 | 547.604 | 539.173 | 532.3496
3567.0354 | 600.9103 | 523.7294 | 610.848 | 561.4283 | 548.255 | 538.5571 | 531.9043
3568.0354 | 601.3587 | 523.49 | 611.2489 | 561.1389 | 548.1199 | 537.6446 | 531.2874
3569.0354 | 601.5308 | 523.3432 | 612.6565 | 561.5649 | 547.447 | 537.5324 | 531.2036
3570.0354 | 602.5879 | 523.2179 | 611.8816 | 562.08 | 546.996 | 537.8889 | 531.1511
3571.0354 | 601.3775 | 522.984 | 611.0338 | 562.8698 | 547.8557 | 538.1724 | 530.9565
3572.0354 | 600.5403 | 522.9701 | 611.9777 | 561.7686 | 547.5946 | 537.5082 | 529.7971
3573.0354 | 602.0123 | 523.3734 | 611.496 | 561.7023 | 547.1184 | 537.8577 | 529.1278
3574.0354 | 602.2411 | 523.3372 | 611.0657 | 561.4477 | 547.8025 | 539.9759 | 529.7704
3575.0354 | 603.0104 | 522.6264 | 610.9232 | 561.4508 | 548.4941 | 540.4903 | 529.1389
3576.0354 | 604.8192 | 522.4671 | 613.416 | 561.4317 | 550.657 | 543.7022 | 530.7147
3577.0354 | 603.985 | 522.4545 | 613.3522 | 561.5729 | 550.2143 | 544.8753 | 532.6024
3578.0354 | 604.3332 | 522.3415 | 612.4046 | 561.7802 | 550.1102 | 546.3893 | 533.898
3579.0354 | 604.4872 | 522.0606 | 611.3412 | 561.6315 | 549.1537 | 545.2981 | 533.3901
3580.0354 | 606.1391 | 521.8676 | 613.6532 | 561.0938 | 549.0015 | 545.7147 | 533.1634
3581.0354 | 607.0911 | 521.7373 | 612.6469 | 562.1458 | 549.2536 | 546.11 | 533.7271
3582.0354 | 607.4277 | 521.6057 | 611.7249 | 563.3108 | 549.708 | 544.9402 | 534.3422
3583.0354 | 607.7695 | 521.5381 | 611.5689 | 563.0038 | 550.9216 | 544.6866 | 533.9163
3584.0354 | 606.8496 | 521.5664 | 611.5198 | 563.3507 | 551.615 | 543.4393 | 533.105
3585.0354 | 606.8596 | 521.8265 | 611.7545 | 563.0977 | 551.4174 | 542.4843 | 531.9813
3586.0354 | 606.4925 | 521.315 | 612.8728 | 562.5127 | 551.5943 | 542.2325 | 531.9572
3587.0354 | 605.614 | 521.1748 | 614.2241 | 562.0814 | 550.6344 | 541.2485 | 531.3521
3588.0354 | 605.3949 | 521.0004 | 613.0977 | 562.3765 | 549.3097 | 540.4387 | 530.0324
3589.0354 | 605.3621 | 521.2918 | 611.6729 | 563.338 | 549.0947 | 540.4136 | 529.3819
3590.0354 | 603.9034 | 520.9373 | 612.8237 | 563.1086 | 549.4918 | 540.6122 | 528.8442
3591.0354 | 604.6947 | 520.5053 | 612.8102 | 563.0105 | 549.2683 | 540.4854 | 528.1378
3592.0354 | 606.8504 | 520.773 | 611.6652 | 562.4816 | 549.3738 | 541.0562 | 527.3461
3593.0354 | 607.477 | 520.6076 | 613.3189 | 562.3105 | 549.342 | 542.3945 | 527.863
3594.0354 | 608.4242 | 520.5519 | 611.7298 | 563.1066 | 549.0644 | 542.8955 | 528.5302
3595.0354 | 610.5666 | 520.3669 | 612.1606 | 563.7752 | 549.3557 | 543.1554 | 528.5741
3596.0354 | 610.0962 | 519.9989 | 611.8859 | 563.9884 | 549.1269 | 541.9915 | 527.7218
3597.0354 | 608.6629 | 519.633 | 611.5648 | 563.7734 | 548.7186 | 540.7468 | 526.8179
3598.0354 | 609.1429 | 519.5196 | 612.337 | 563.4295 | 549.2643 | 541.0422 | 526.9304
3599.0354 | 610.5978 | 519.4601 | 614.0285 | 564.3954 | 549.5507 | 541.8526 | 527.409
3600.0354 | 610.4035 | 519.5319 | 613.1805 | 563.8235 | 548.8163 | 541.1664 | 526.6501
3601.0354 | 610.8835 | 519.0739 | 614.5631 | 563.6104 | 547.8729 | 541.5163 | 526.7581
3602.0354 | 611.853 | 519.161 | 615.072 | 562.8613 | 547.5446 | 543.4002 | 528.4296
3603.0354 | 611.1565 | 519.2849 | 614.1286 | 562.7114 | 545.9742 | 542.5658 | 527.8626
3604.0354 | 607.6368 | 518.9565 | 613.2178 | 562.5757 | 545.7548 | 542.6215 | 527.2487
3605.0354 | 608.9983 | 518.7807 | 611.7415 | 563.8648 | 545.5166 | 542.0505 | 526.7143
3606.0354 | 609.9097 | 518.8443 | 611.6432 | 564.295 | 546.4531 | 541.5176 | 526.2022
3607.0354 | 608.8304 | 518.7189 | 611.8113 | 564.2773 | 547.2563 | 541.2503 | 525.856
3608.0354 | 610.3273 | 518.1639 | 613.4644 | 563.5435 | 547.2907 | 541.5164 | 525.8885
3609.0354 | 600.347 | 518.4804 | 613.0523 | 564.7122 | 547.9694 | 542.7776 | 526.4324
3610.0354 | 600.8233 | 518.1728 | 612.1847 | 565.8211 | 547.5977 | 542.3198 | 526.0791
3611.0354 | 602.6398 | 518.4784 | 610.6793 | 564.5737 | 547.5604 | 542.0867 | 524.9511
3612.0354 | 601.1774 | 518.7631 | 610.2225 | 564.8619 | 548.6563 | 542.4407 | 524.6991
3613.0354 | 597.9727 | 517.8185 | 610.1724 | 565.4466 | 548.4751 | 540.4375 | 523.6741
3614.0354 | 602.3432 | 518.3147 | 611.2687 | 564.7524 | 548.1995 | 539.9184 | 523.2811
3615.0354 | 602.6559 | 518.1186 | 611.8085 | 564.6594 | 547.9699 | 539.905 | 523.3951
3616.0354 | 603.7725 | 517.6834 | 611.5354 | 564.8601 | 548.1523 | 541.2198 | 523.866
3617.0354 | 603.2795 | 517.6843 | 611.6442 | 564.7688 | 547.7936 | 540.9617 | 524.1811
3618.0354 | 602.9863 | 517.1837 | 612.8927 | 565.3925 | 547.7347 | 541.158 | 524.1252
3619.0354 | 602.694 | 517.3167 | 612.4498 | 565.176 | 547.2785 | 541.1565 | 524.5305
3620.0354 | 607.5381 | 517.3364 | 613.4344 | 565.1491 | 547.5923 | 542.241 | 524.6664
3621.0354 | 604.1229 | 517.4215 | 614.015 | 565.2737 | 547.4346 | 542.5703 | 524.682
3622.0354 | 603.8218 | 517.4476 | 611.8889 | 566.0179 | 547.137 | 542.2194 | 524.4941
3623.0354 | 604.5866 | 517.2226 | 613.7117 | 565.2753 | 546.9425 | 542.0555 | 524.1997
3624.0354 | 604.7712 | 516.8549 | 612.1088 | 566.1429 | 546.7705 | 541.3806 | 523.3539
3625.0354 | 604.1114 | 517.0834 | 611.2049 | 567.7673 | 546.9208 | 541.0116 | 522.5444
3626.0354 | 603.1861 | 516.9159 | 611.0456 | 568.1361 | 547.3474 | 540.6775 | 521.8137
3627.0354 | 602.7857 | 516.8717 | 611.4815 | 566.6757 | 547.8059 | 539.7577 | 521.2461
3628.0354 | 603.7 | 516.4371 | 612.1457 | 566.0313 | 547.7973 | 539.9055 | 521.5125
3629.0354 | 602.101 | 516.0131 | 614.2108 | 566.8095 | 546.8893 | 539.4465 | 521.5794
3630.0354 | 601.9065 | 515.6489 | 614.1378 | 566.7761 | 545.7539 | 539.6717 | 521.7829
3631.0354 | 602.6395 | 515.8379 | 616.0819 | 566.3193 | 545.3891 | 541.4688 | 523.168
3632.0354 | 604.0911 | 515.8184 | 614.7532 | 566.5768 | 545.4896 | 542.9208 | 524.7826
3633.0354 | 603.9786 | 515.3795 | 613.5539 | 566.8707 | 546.5192 | 543.5015 | 526.0725
3634.0354 | 604.3992 | 515.1902 | 613.7541 | 567.1407 | 547.1241 | 542.8818 | 525.7131
3635.0354 | 607.1507 | 514.9756 | 613.1189 | 567.3707 | 547.2877 | 542.5582 | 525.4054
3636.0354 | 607.4489 | 514.8387 | 614.0032 | 567.3334 | 547.0683 | 542.0743 | 524.9949
3637.0354 | 607.3441 | 514.7332 | 613.7145 | 568.009 | 547.1142 | 540.5695 | 524.4302
3638.0354 | 608.9961 | 514.4426 | 614.3587 | 567.1866 | 547.3844 | 540.7629 | 523.8258
3639.0354 | 607.0594 | 514.3709 | 612.8716 | 567.361 | 547.9854 | 542.3663 | 524.1076
3640.0354 | 610.3259 | 514.2079 | 612.9064 | 567.8386 | 548.1641 | 542.9775 | 523.4138
3641.0354 | 613.1901 | 514.1976 | 613.6667 | 568.1633 | 548.9 | 542.861 | 523.3459
3642.0354 | 613.2025 | 513.8391 | 612.7064 | 570.0144 | 550.5572 | 542.2671 | 523.0255
3643.0354 | 608.9121 | 513.7703 | 612.7989 | 569.8279 | 550.8151 | 540.7375 | 521.2882
3644.0354 | 612.2754 | 513.6458 | 613.7263 | 570.2628 | 550.5958 | 540.5723 | 520.987
3645.0354 | 612.7585 | 513.3943 | 613.6376 | 570.7673 | 550.5114 | 540.6677 | 520.9017
3646.0354 | 613.24 | 513.1443 | 613.5897 | 570.8407 | 551.3319 | 540.3168 | 520.8272
3647.0354 | 614.8283 | 512.9788 | 614.8676 | 569.5854 | 551.5141 | 540.2088 | 520.7686
3648.0354 | 614.831 | 512.9108 | 613.4452 | 568.6511 | 551.1271 | 540.8485 | 520.7903
3649.0354 | 611.5515 | 513.2218 | 615.3188 | 569.1046 | 550.4135 | 541.0767 | 520.9936
3650.0354 | 612.5336 | 512.7434 | 612.9641 | 569.8941 | 549.8575 | 541.8953 | 521.534
3651.0354 | 575.5338 | 513.4585 | 613.163 | 570.1845 | 550.1308 | 541.4069 | 520.8471
3652.0354 | 607.8748 | 512.3322 | 612.6035 | 570.1314 | 550.2856 | 541.8906 | 520.5992
3653.0354 | 611.8799 | 512.0811 | 613.5488 | 569.9156 | 551.4421 | 542.8394 | 520.6325
3654.0354 | 611.7968 | 512.0046 | 612.8732 | 569.4459 | 552.2782 | 543.8077 | 521.5338
3655.0354 | 610.9511 | 511.655 | 611.9147 | 569.1514 | 552.9492 | 544.5648 | 521.4358
3656.0354 | 613.7912 | 511.5317 | 611.937 | 570.5727 | 552.6686 | 544.6306 | 520.9802
3657.0354 | 612.8331 | 511.3599 | 611.9946 | 570.5397 | 552.8183 | 543.4558 | 520.5585
3658.0354 | 613.9178 | 511.0862 | 611.6807 | 570.1766 | 552.4329 | 542.5267 | 519.766
3659.0354 | 615.6075 | 510.8865 | 610.945 | 570.058 | 553.2615 | 542.1606 | 518.8651
3660.0354 | 616.5247 | 510.9188 | 610.8783 | 570.0115 | 554.2626 | 542.6495 | 518.4865
3661.0354 | 618.019 | 510.7225 | 610.5554 | 570.7015 | 554.8013 | 542.5884 | 517.5939
3662.0354 | 616.5549 | 510.2477 | 610.1751 | 571.4424 | 555.6347 | 541.4547 | 517.1013
3663.0354 | 618.0573 | 509.9166 | 609.9891 | 571.1511 | 556.295 | 540.5395 | 515.9693
3664.0354 | 608.9892 | 509.9928 | 610.7781 | 571.3623 | 556.0382 | 539.6078 | 515.1262
3665.0354 | 571.6504 | 509.7439 | 610.5705 | 570.4552 | 556.0644 | 540.501 | 515.8824
3666.0354 | 566.4075 | 509.7895 | 610.9043 | 571.4429 | 555.7276 | 541.0772 | 515.9595
3667.0354 | 565.8878 | 509.5072 | 610.0253 | 571.5526 | 555.7307 | 541.8627 | 516.6882
3668.0354 | 566.8372 | 509.5369 | 609.2213 | 571.0777 | 555.7638 | 542.8354 | 516.2745
3669.0354 | 565.4206 | 509.5903 | 609.2776 | 571.4541 | 555.1599 | 542.2358 | 515.7481
3670.0354 | 564.7972 | 509.4537 | 609.5482 | 573.0302 | 554.9091 | 541.9622 | 515.6049
3671.0354 | 564.9315 | 509.9114 | 610.0787 | 574.6739 | 554.8267 | 540.1903 | 514.516
3672.0354 | 563.7899 | 509.2496 | 609.3044 | 574.8656 | 554.5377 | 538.9108 | 514.1834
3673.0354 | 560.3998 | 509.0144 | 609.0448 | 573.669 | 553.8409 | 537.713 | 514.0885
3674.0354 | 561.18 | 509.3301 | 609.3099 | 573.9367 | 553.3958 | 535.995 | 513.1175
3675.0354 | 611.0738 | 508.475 | 610.3889 | 573.0296 | 552.4719 | 535.3989 | 512.5926
3676.0354 | 654.2854 | 508.0662 | 610.7411 | 574.0871 | 551.7151 | 534.76 | 512.3988
3677.0354 | 652.391 | 507.9393 | 609.2259 | 574.6305 | 550.4588 | 533.4493 | 512.0432
3678.0354 | 657.0322 | 507.885 | 610.628 | 573.4283 | 550.5533 | 535.158 | 512.6007
3679.0354 | 658.9868 | 507.6948 | 609.5878 | 573.4644 | 550.6099 | 535.5919 | 513.6331
3680.0354 | 649.7254 | 507.5115 | 610.9047 | 573.3114 | 550.3627 | 536.5167 | 514.3315
3681.0354 | 652.911 | 507.3748 | 609.9123 | 573.13 | 550.3589 | 537.9738 | 515.0381
3682.0354 | 644.1422 | 507.1036 | 608.9285 | 573.768 | 551.1214 | 539.5324 | 515.436
3683.0354 | 645.8869 | 506.7918 | 608.3207 | 575.2541 | 552.0007 | 538.8573 | 514.6958
3684.0354 | 642.6323 | 506.6693 | 608.5361 | 575.1775 | 552.4972 | 538.4104 | 514.1991
3685.0354 | 640.4061 | 506.2741 | 608.6376 | 576.1415 | 553.0624 | 537.624 | 514.1357
3686.0354 | 639.8446 | 506.2499 | 609.354 | 575.347 | 552.4104 | 537.3784 | 512.9522
3687.0354 | 644.9055 | 506.0513 | 608.543 | 574.4932 | 552.1536 | 538.5243 | 514.0663
3688.0354 | 643.8619 | 505.9337 | 608.7447 | 575.8747 | 551.4367 | 538.4797 | 513.6525
3689.0354 | 644.5063 | 505.7445 | 610.9858 | 576.8688 | 551.3482 | 538.0048 | 513.7611
3690.0354 | 645.9332 | 505.6174 | 610.87 | 576.8738 | 551.4659 | 538.6632 | 513.9683
3691.0354 | 646.7978 | 505.5744 | 611.3086 | 575.924 | 551.0916 | 538.4252 | 513.9765
3692.0354 | 648.7027 | 505.386 | 610.6666 | 576.5784 | 550.8977 | 539.0448 | 514.0987
3693.0354 | 651.4346 | 505.4677 | 611.0118 | 576.3591 | 551.2328 | 539.9248 | 514.4241
3694.0354 | 651.1177 | 505.2286 | 609.5525 | 578.1846 | 553.5852 | 541.1467 | 515.2046
3695.0354 | 649.4851 | 505.4898 | 610.1222 | 578.6012 | 555.861 | 540.9338 | 515.2006
3696.0354 | 651.1388 | 505.463 | 611.9251 | 577.6254 | 556.2913 | 541.0251 | 514.9522
3697.0354 | 649.1019 | 505.2618 | 611.102 | 578.19 | 555.5872 | 540.9593 | 514.3982
3698.0354 | 650.8354 | 505.2128 | 611.2136 | 576.8955 | 554.1281 | 540.1569 | 513.7486
3699.0354 | 657.5056 | 504.9557 | 611.0955 | 576.5597 | 552.8409 | 540.8381 | 515.2992
3700.0354 | 653.9205 | 504.6669 | 609.7085 | 577.0141 | 552.6817 | 542.5146 | 515.6123
3701.0354 | 657.1879 | 504.2663 | 609.4662 | 576.4978 | 552.4903 | 544.3405 | 515.7596
3702.0354 | 659.3043 | 504.3855 | 610.0298 | 576.6953 | 552.8486 | 545.606 | 516.4063
3703.0354 | 659.3835 | 504.0502 | 609.6354 | 577.0905 | 553.2381 | 545.7434 | 516.8934
3704.0354 | 660.4198 | 503.9992 | 609.0639 | 576.4316 | 553.1066 | 545.9089 | 517.3419
3705.0354 | 678.4109 | 503.8007 | 609.2747 | 576.2528 | 553.2999 | 546.2982 | 517.454
3706.0354 | 689.1907 | 503.5789 | 610.1807 | 577.0653 | 553.6042 | 546.4687 | 517.6708
3707.0354 | 668.1109 | 503.5034 | 609.7414 | 578.0624 | 554.1906 | 545.9997 | 517.6447
3708.0354 | 663.5747 | 503.3385 | 609.7589 | 578.3873 | 554.6225 | 545.7386 | 517.5141
3709.0354 | 672.8641 | 503.1457 | 609.7155 | 578.4617 | 555.6003 | 545.3495 | 517.0231
3710.0354 | 659.5463 | 502.9051 | 609.7887 | 577.8797 | 555.2704 | 544.205 | 516.7901
3711.0354 | 660.7023 | 502.8316 | 610.6146 | 577.6924 | 554.5997 | 544.2249 | 517.4279
3712.0354 | 662.2376 | 502.5627 | 612.0993 | 578.2927 | 554.8669 | 544.362 | 518.9607
3713.0354 | 660.9819 | 502.4923 | 612.3985 | 578.4037 | 553.9301 | 544.2871 | 518.9676
3714.0354 | 662.2372 | 502.6301 | 611.3574 | 579.0459 | 554.0383 | 544.9165 | 519.1299
3715.0354 | 658.2219 | 502.4736 | 611.2518 | 578.3695 | 553.9645 | 544.024 | 518.5004
3716.0354 | 660.3714 | 502.3063 | 610.7439 | 579.0139 | 553.5116 | 543.3591 | 518.1684
3717.0354 | 662.6658 | 502.2354 | 610.8007 | 578.061 | 553.1256 | 542.3911 | 517.5165
3718.0354 | 662.1787 | 501.8931 | 610.9588 | 577.8776 | 553.0522 | 542.4432 | 517.1869
3719.0354 | 662.276 | 501.7188 | 610.5835 | 578.0029 | 553.3341 | 542.8177 | 517.7054
3720.0354 | 662.1698 | 501.9013 | 610.0707 | 580.1906 | 553.7211 | 543.6057 | 517.5827
3721.0354 | 663.4554 | 501.8673 | 610.6395 | 579.1891 | 553.7963 | 543.1344 | 516.9975
3722.0354 | 666.6125 | 502.1249 | 610.2306 | 579.2117 | 554.0424 | 542.9208 | 517.1203
3723.0354 | 670.1979 | 501.5504 | 610.2986 | 578.5765 | 553.738 | 542.4514 | 516.5563
3724.0354 | 668.2382 | 501.336 | 609.7522 | 579.8533 | 553.3414 | 541.9135 | 515.9439
3725.0354 | 669.7434 | 501.4938 | 610.978 | 579.4936 | 553.7111 | 542.1524 | 515.875
3726.0354 | 651.949 | 501.0021 | 609.8623 | 579.4745 | 555.0168 | 543.6343 | 516.8435
3727.0354 | 704.379 | 500.6194 | 609.2727 | 579.6869 | 555.7502 | 542.8798 | 516.83
3728.0354 | 706.5612 | 500.7471 | 610.1323 | 580.0393 | 555.1451 | 541.9488 | 516.1663
3729.0354 | 708.5182 | 500.7956 | 609.762 | 580.8063 | 554.8712 | 543.169 | 516.8423
3730.0354 | 711.8753 | 500.4613 | 610.2169 | 580.8192 | 554.887 | 542.9285 | 516.9711
3731.0354 | 706.9545 | 500.2176 | 610.8437 | 580.527 | 555.1686 | 542.1444 | 517.0229
3732.0354 | 689.2571 | 499.9599 | 609.6352 | 579.7576 | 556.3838 | 542.8227 | 517.1981
3733.0354 | 690.8223 | 499.8301 | 608.6026 | 581.2171 | 557.3917 | 543.2645 | 517.1578
3734.0354 | 688.8847 | 499.6652 | 608.9472 | 581.0189 | 557.5211 | 543.5852 | 517.0687
3735.0354 | 673.1066 | 499.7849 | 609.3673 | 580.4462 | 557.8711 | 542.8557 | 516.7896
3736.0354 | 671.8827 | 499.7575 | 609.2603 | 580.9527 | 557.747 | 541.9812 | 516.5765
3737.0354 | 671.3512 | 500.0854 | 608.6513 | 580.4885 | 556.7965 | 541.2335 | 516.0675
3738.0354 | 670.9785 | 499.5577 | 608.3517 | 579.9637 | 556.2651 | 541.8835 | 516.1421
3739.0354 | 666.6667 | 499.3331 | 607.8629 | 579.9809 | 556.8613 | 543.5962 | 515.6726
3740.0354 | 666.5716 | 499.0716 | 607.768 | 579.7276 | 558.051 | 544.3093 | 515.8819
3741.0354 | 666.9224 | 499.1363 | 608.0478 | 580.096 | 558.7632 | 545.0943 | 515.3591
3742.0354 | 670.4463 | 498.777 | 607.1062 | 579.5297 | 558.9439 | 545.0273 | 515.4397
3743.0354 | 668.9664 | 498.4816 | 607.2038 | 579.9468 | 558.1664 | 544.1636 | 514.5513
3744.0354 | 670.6198 | 498.5038 | 607.1017 | 579.6776 | 557.3031 | 542.7944 | 513.6705
3745.0354 | 671.1778 | 498.7479 | 606.625 | 579.7955 | 557.0909 | 542.4008 | 513.4875
3746.0354 | 673.1828 | 498.2354 | 606.2599 | 579.5189 | 557.78 | 542.2094 | 512.6529
3747.0354 | 678.6191 | 497.9352 | 605.7169 | 579.3036 | 559.3081 | 543.872 | 512.4111
3748.0354 | 679.0235 | 498.1883 | 605.2674 | 579.0163 | 560.2959 | 543.0651 | 511.4306
3749.0354 | 682.6918 | 498.1564 | 604.87 | 578.9398 | 560.4924 | 541.686 | 510.226
3750.0354 | 685.2406 | 498.6831 | 604.8583 | 579.0616 | 559.2216 | 540.1284 | 509.3875
3751.0354 | 687.0547 | 498.3815 | 605.4082 | 579.1535 | 558.6144 | 540.4734 | 509.1582
3752.0354 | 690.33 | 497.8021 | 605.0737 | 579.2809 | 558.6419 | 541.4883 | 510.3562
3753.0354 | 695.857 | 497.4706 | 605.3416 | 578.7003 | 557.8589 | 541.1128 | 510.446
3754.0354 | 691.1809 | 497.3921 | 604.7289 | 578.7444 | 557.0866 | 540.5874 | 510.3287
3755.0354 | 702.3369 | 497.1581 | 605.0074 | 578.4336 | 555.998 | 540.5879 | 510.7387
3756.0354 | 704.2674 | 497.3193 | 603.7952 | 578.9879 | 555.3664 | 540.4301 | 511.2434
3757.0354 | 701.779 | 497.2481 | 604.0824 | 579.0192 | 554.8452 | 539.8051 | 510.8332
3758.0354 | 695.7056 | 497.0915 | 603.8838 | 578.6762 | 554.9542 | 539.5788 | 510.5688
3759.0354 | 693.1323 | 496.841 | 604.1173 | 578.4119 | 554.6308 | 539.2141 | 510.5286
3760.0354 | 696.4967 | 496.7774 | 603.521 | 578.3236 | 553.9562 | 540.0287 | 511.4318
3761.0354 | 700.2194 | 496.5917 | 602.5868 | 578.0306 | 553.5992 | 542.5679 | 512.9484
3762.0354 | 703.2926 | 496.2351 | 602.8312 | 577.8425 | 553.2274 | 543.9937 | 513.8427
3763.0354 | 697.751 | 496.1986 | 602.3505 | 577.6375 | 553.2356 | 544.3612 | 514.1734
3764.0354 | 696.4741 | 496.4686 | 601.8071 | 577.6897 | 554.0775 | 544.0991 | 513.904
3765.0354 | 701.0055 | 496.8692 | 602.0371 | 578.1532 | 554.7256 | 543.7884 | 513.7345
3766.0354 | 699.1551 | 496.5973 | 601.6721 | 577.5433 | 554.4723 | 543.4659 | 513.2561
3767.0354 | 700.4467 | 497.4393 | 600.8967 | 577.5717 | 554.8622 | 544.5233 | 513.0674
3768.0354 | 705.0932 | 497.0179 | 601.0278 | 577.6001 | 555.1647 | 545.1723 | 512.8745
3769.0354 | 700.6597 | 496.7663 | 600.6268 | 577.7575 | 554.3425 | 543.0296 | 511.4947
3770.0354 | 708.7904 | 495.9695 | 600.1407 | 577.874 | 554.5894 | 542.2605 | 510.7282
3771.0354 | 708.027 | 496.3439 | 599.7241 | 577.0289 | 554.9393 | 541.8521 | 510.122
3772.0354 | 711.4887 | 496.2488 | 599.797 | 576.8995 | 554.8539 | 541.0313 | 509.3495
3773.0354 | 718.2538 | 495.5636 | 600.5012 | 576.8035 | 553.8039 | 540.7321 | 509.4292
3774.0354 | 713.6761 | 495.3755 | 599.8252 | 576.888 | 552.984 | 541.908 | 510.3762
3775.0354 | 711.0113 | 495.2101 | 599.0955 | 576.8655 | 552.865 | 542.177 | 510.6696
3776.0354 | 717.838 | 494.9595 | 598.88 | 577.0813 | 553.1992 | 540.8416 | 509.4982
3777.0354 | 715.1718 | 495.0346 | 598.4009 | 577.6366 | 554.3351 | 539.5992 | 508.7762
3778.0354 | 715.1101 | 494.9428 | 598.1785 | 576.5925 | 554.4719 | 539.0715 | 507.7911
3779.0354 | 715.1443 | 494.7263 | 598.1825 | 577.0694 | 554.3247 | 537.6334 | 507.3701
3780.0354 | 715.0018 | 494.6217 | 598.7214 | 576.7536 | 553.8201 | 536.88 | 507.0585
3781.0354 | 711.6555 | 494.3242 | 597.9022 | 576.2551 | 553.4152 | 537.0705 | 507.6551
3782.0354 | 711.0623 | 494.4309 | 597.3412 | 575.7449 | 553.1608 | 538.7386 | 508.9253
3783.0354 | 713.3983 | 494.4034 | 597.0344 | 576.2403 | 552.867 | 540.6356 | 509.6533
3784.0354 | 709.1787 | 494.2982 | 596.633 | 575.9252 | 552.6509 | 541.0463 | 509.1435
3785.0354 | 712.5382 | 494.7896 | 596.1173 | 575.436 | 553.1549 | 540.7711 | 508.6951
3786.0354 | 714.5291 | 495.3191 | 595.9268 | 575.4779 | 553.3175 | 540.0398 | 508.3147
3787.0354 | 704.8623 | 494.4455 | 595.476 | 575.2062 | 553.3145 | 539.1754 | 507.4765
3788.0354 | 708.9248 | 493.9025 | 595.8475 | 575.0939 | 552.9762 | 538.5915 | 506.7604
3789.0354 | 713.886 | 493.9826 | 595.0688 | 574.6665 | 552.7787 | 539.1775 | 507.6996
3790.0354 | 713.8967 | 494.189 | 594.6293 | 574.7403 | 552.3381 | 538.951 | 507.3335
3791.0354 | 713.3816 | 493.9085 | 594.4733 | 574.5191 | 552.3179 | 538.1489 | 506.7337
3792.0354 | 717.5099 | 493.4875 | 595.7024 | 574.6619 | 551.6597 | 537.9841 | 506.3386
3793.0354 | 707.2952 | 493.2692 | 593.9901 | 574.5534 | 551.8445 | 538.2066 | 506.7748
3794.0354 | 718.2741 | 493.2563 | 593.5581 | 574.0403 | 552.8642 | 539.1957 | 506.2802
3795.0354 | 724.6554 | 493.4789 | 593.0212 | 574.1874 | 553.911 | 538.0901 | 505.4424
3796.0354 | 724.1562 | 493.1097 | 592.9822 | 573.6518 | 553.898 | 537.0113 | 504.5135
3797.0354 | 729.7716 | 492.6861 | 592.6281 | 573.6103 | 554.915 | 537.0887 | 503.9195
3798.0354 | 726.0854 | 492.683 | 592.4926 | 573.5674 | 555.4246 | 536.4037 | 503.6113
3799.0354 | 727.4068 | 492.4926 | 592.3892 | 573.6099 | 555.3252 | 535.8448 | 503.3897
3800.0354 | 728.7223 | 492.1965 | 592.1345 | 573.6744 | 556.1573 | 534.9887 | 502.6707
3801.0354 | 722.8009 | 491.9811 | 591.4622 | 574.1987 | 555.891 | 533.7165 | 502.1057
3802.0354 | 725.4542 | 492.2147 | 591.9234 | 574.6661 | 555.5391 | 532.612 | 501.6499
3803.0354 | 731.4743 | 492.0283 | 592.3922 | 573.9818 | 554.9305 | 533.0955 | 501.9794
3804.0354 | 729.8527 | 491.7421 | 591.9544 | 574.0198 | 555.1144 | 534.1804 | 502.311
3805.0354 | 726.5262 | 491.6951 | 591.7432 | 573.3433 | 555.8269 | 535.4455 | 502.7555
3806.0354 | 785.2077 | 491.8194 | 591.3921 | 573.5333 | 556.6555 | 536.5661 | 503.0782
3807.0354 | 798.7493 | 491.4442 | 591.0536 | 574.3331 | 556.8627 | 537.125 | 503.1556
3808.0354 | 806.3222 | 491.3778 | 590.421 | 573.9813 | 557.499 | 537.2116 | 503.5326
3809.0354 | 823.5898 | 490.9691 | 589.6629 | 573.5635 | 558.7377 | 536.8845 | 503.0679
3810.0354 | 816.0198 | 490.8383 | 589.4135 | 572.8598 | 558.4534 | 536.2048 | 502.5782
3811.0354 | 790.0549 | 490.8211 | 589.8807 | 573.5235 | 557.3517 | 535.1974 | 501.9835
3812.0354 | 777.4527 | 490.7281 | 590.2163 | 573.8842 | 556.803 | 534.9957 | 501.9929
3813.0354 | 789.845 | 490.4838 | 589.3427 | 574.1632 | 556.6913 | 535.6398 | 501.8115
3814.0354 | 791.471 | 490.5046 | 588.9922 | 573.3334 | 556.9139 | 535.2272 | 501.5296
3815.0354 | 796.1349 | 490.4726 | 588.8667 | 573.2539 | 556.7247 | 535.0973 | 501.3038
3816.0354 | 787.8596 | 490.45 | 588.4835 | 574.0144 | 557.1571 | 535.2745 | 501.514
3817.0354 | 783.0761 | 490.2859 | 587.9122 | 573.912 | 558.0081 | 535.5474 | 501.9633
3818.0354 | 780.9996 | 490.0805 | 587.5279 | 573.0511 | 558.8494 | 536.5822 | 501.9103
3819.0354 | 792.6328 | 489.8535 | 587.3654 | 572.5882 | 559.0265 | 537.7435 | 502.641
3820.0354 | 791.7286 | 489.9489 | 588.1081 | 573.3977 | 559.3679 | 537.755 | 502.9311
3821.0354 | 793.1028 | 489.7752 | 587.6022 | 572.8798 | 558.9547 | 538.7745 | 503.2957
3822.0354 | 794.3742 | 489.614 | 587.5686 | 573.7158 | 558.9623 | 540.109 | 504.4239
3823.0354 | 800.3152 | 489.9558 | 587.2223 | 573.3925 | 560.3974 | 540.5854 | 504.9586
3824.0354 | 849.4761 | 489.862 | 586.2452 | 573.5583 | 561.5724 | 540.4327 | 505.1519
3825.0354 | 856.9363 | 489.9922 | 586.9605 | 574.0601 | 561.0806 | 539.0389 | 504.6857
3826.0354 | 854.2734 | 489.2863 | 586.8213 | 574.2481 | 560.2762 | 538.4568 | 504.7917
3827.0354 | 852.5529 | 489.285 | 586.0182 | 575.915 | 560.4129 | 538.7573 | 505.5956
3828.0354 | 856.9459 | 489.5449 | 585.6533 | 576.6158 | 561.3593 | 538.4037 | 505.8221
3829.0354 | 839.9362 | 489.8589 | 585.1571 | 575.9587 | 561.21 | 536.4875 | 504.3763
3830.0354 | 835.4853 | 490.1986 | 585.1254 | 574.7194 | 560.9249 | 535.8288 | 503.8657
3831.0354 | 833.4376 | 489.2698 | 586.0138 | 575.0946 | 559.8229 | 536.2975 | 503.5728
3832.0354 | 829.959 | 488.9758 | 585.5333 | 574.5795 | 559.337 | 537.6093 | 504.8119
3833.0354 | 845.5681 | 488.7244 | 585.1175 | 576.1307 | 558.7274 | 537.5532 | 504.7703
3834.0354 | 844.258 | 488.8615 | 584.776 | 576.1016 | 558.54 | 537.0001 | 504.7816
3835.0354 | 852.1342 | 488.8265 | 585.8425 | 575.2359 | 558.1984 | 536.4316 | 504.881
3836.0354 | 856.6957 | 488.7225 | 585.3796 | 574.3904 | 557.5125 | 537.5405 | 506.0833
3837.0354 | 853.914 | 488.4818 | 584.6623 | 574.4112 | 557.5511 | 538.492 | 507.8579
3838.0354 | 854.348 | 488.0645 | 584.3783 | 574.3921 | 557.3709 | 538.6879 | 509.9129
3839.0354 | 852.7555 | 488.0702 | 583.8046 | 573.891 | 556.9617 | 539.4154 | 513.1175
3840.0354 | 857.4992 | 488.0394 | 584.0719 | 573.7394 | 556.7295 | 540.9228 | 515.9237
3841.0354 | 853.375 | 487.7431 | 583.2843 | 574.767 | 556.0733 | 540.434 | 518.3811
3842.0354 | 861.5533 | 487.6347 | 582.8354 | 574.8057 | 556.5141 | 540.404 | 520.7307
3843.0354 | 876.1994 | 487.5807 | 582.5446 | 575.2437 | 557.4652 | 539.7315 | 522.1439
3844.0354 | 880.9615 | 487.451 | 582.8936 | 576.0069 | 557.2369 | 538.2321 | 524.7378
3845.0354 | 881.4985 | 487.6838 | 582.973 | 576.2087 | 556.4431 | 537.1888 | 526.6876
3846.0354 | 878.1354 | 487.674 | 584.0792 | 576.867 | 557.8233 | 537.8353 | 529.4902
3847.0354 | 881.0969 | 487.3886 | 583.5785 | 576.8399 | 559.6479 | 537.9564 | 532.0656
3848.0354 | 881.9264 | 487.3455 | 582.6888 | 576.9234 | 560.9707 | 538.1677 | 535.2285
3849.0354 | 881.08 | 487.4463 | 583.852 | 576.2114 | 561.8187 | 538.196 | 537.3006
3850.0354 | 878.5374 | 487.1401 | 584.6411 | 575.6322 | 561.9994 | 539.2232 | 541.8946
3851.0354 | 886.8264 | 486.7871 | 583.7144 | 575.7034 | 562.6738 | 540.1634 | 547.7231
3852.0354 | 887.6769 | 486.7119 | 583.6789 | 576.1111 | 562.8884 | 541.791 | 553.5122
3853.0354 | 890.3343 | 486.5522 | 582.9553 | 577.3386 | 562.5951 | 542.195 | 560.4891
3854.0354 | 890.9982 | 486.391 | 584.0646 | 577.9201 | 562.6503 | 542.3435 | 566.646
3855.0354 | 889.6259 | 486.2393 | 584.7717 | 576.8791 | 562.6551 | 540.9008 | 572.5764
3856.0354 | 890.8053 | 486.0431 | 584.4811 | 577.7662 | 562.0538 | 540.281 | 579.8924
3857.0354 | 895.5412 | 486.0659 | 583.5628 | 577.831 | 560.9107 | 539.8155 | 585.2619
3858.0354 | 895.0848 | 486.104 | 584.1733 | 578.274 | 560.6738 | 540.1923 | 593.5266
3859.0354 | 892.8526 | 485.8367 | 583.7296 | 579.1448 | 560.5962 | 539.9612 | 600.9217
3860.0354 | 903.0961 | 485.8695 | 583.7916 | 578.1142 | 560.5673 | 540.4261 | 607.4614
3861.0354 | 897.2493 | 485.6007 | 583.0826 | 578.5038 | 559.7545 | 539.6304 | 612.0852
3862.0354 | 905.6166 | 485.4238 | 584.5737 | 578.3421 | 559.6273 | 539.7012 | 618.3417
3863.0354 | 904.3451 | 485.3914 | 585.3976 | 578.964 | 560.2153 | 540.2524 | 624.3541
3864.0354 | 897.2711 | 485.2164 | 584.1206 | 579.643 | 561.0647 | 541.0871 | 629.6275
3865.0354 | 894.8773 | 485.1432 | 583.4272 | 580.1046 | 560.482 | 539.9898 | 633.1278
3866.0354 | 891.6847 | 484.9979 | 583.3643 | 578.4123 | 559.6913 | 539.6784 | 636.299
3867.0354 | 893.5955 | 484.8867 | 584.7331 | 579.2625 | 559.8439 | 540.9598 | 636.5085
3868.0354 | 908.8496 | 484.9577 | 585.3996 | 580.523 | 560.0264 | 543.1858 | 639.789
3869.0354 | 902.9439 | 484.7941 | 586.0069 | 580.6566 | 560.3658 | 543.5485 | 645.0839
3870.0354 | 899.3636 | 484.6044 | 586.7839 | 579.922 | 561.4635 | 543.9933 | 649.3449
3871.0354 | 897.5888 | 484.6735 | 586.9712 | 579.8625 | 561.2949 | 543.4291 | 652.3008
3872.0354 | 895.7956 | 484.512 | 587.7619 | 579.3124 | 560.4617 | 543.3436 | 654.9162
3873.0354 | 901.3951 | 484.4382 | 586.7098 | 579.5057 | 560.829 | 544.4347 | 655.0811
3874.0354 | 899.7564 | 484.0486 | 585.9696 | 581.2902 | 561.1422 | 544.5628 | 651.2302
3875.0354 | 898.5584 | 483.8248 | 585.8033 | 581.9719 | 560.545 | 543.9577 | 650.7104
3876.0354 | 910.9767 | 483.8051 | 585.6065 | 582.325 | 560.85 | 543.8501 | 648.2439
3877.0354 | 908.0016 | 483.8571 | 585.5877 | 582.9715 | 561.4461 | 543.8322 | 642.4883
3878.0354 | 903.1849 | 483.8965 | 586.3974 | 583.451 | 561.2455 | 542.9459 | 635.4993
3879.0354 | 920.5745 | 483.5852 | 587.2505 | 582.165 | 560.5327 | 542.1006 | 626.3547
3880.0354 | 913.2502 | 483.6043 | 586.1982 | 582.9428 | 559.2166 | 541.1206 | 621.4967
3881.0354 | 904.7422 | 483.4823 | 586.5918 | 583.3136 | 559.121 | 541.5921 | 608.2421
3882.0354 | 905.4121 | 483.292 | 587.289 | 582.8429 | 558.9274 | 543.0767 | 598.0197
3883.0354 | 906.3649 | 483.2745 | 586.4852 | 583.0647 | 559.3954 | 545.1749 | 587.3699
3884.0354 | 912.1774 | 483.0069 | 585.8818 | 582.7498 | 559.9403 | 545.4798 | 582.3598
3885.0354 | 920.2805 | 482.8167 | 585.8747 | 583.371 | 560.658 | 545.4432 | 578.5064
3886.0354 | 916.8093 | 482.776 | 586.4196 | 583.6499 | 561.0017 | 545.314 | 576.675
3887.0354 | 919.5075 | 482.6629 | 587.0661 | 584.9664 | 561.7377 | 545.3866 | 576.4365
3888.0354 | 914.3902 | 482.5302 | 587.6382 | 584.6832 | 562.8964 | 545.761 | 577.1734
3889.0354 | 910.6541 | 482.3775 | 589.6968 | 583.9469 | 562.7399 | 546.3959 | 577.2472
3890.0354 | 910.984 | 482.4827 | 590.1389 | 583.4642 | 561.4279 | 546.3969 | 578.0737
3891.0354 | 905.7002 | 482.9076 | 591.1725 | 583.2822 | 560.0838 | 546.3081 | 577.3504
3892.0354 | 894.1367 | 482.6395 | 589.856 | 583.4795 | 558.8784 | 546.3533 | 577.868
3893.0354 | 879.4524 | 482.7568 | 591.643 | 583.3071 | 558.4153 | 546.4438 | 578.8872
3894.0354 | 891.9508 | 482.5089 | 589.9711 | 583.7108 | 558.1237 | 547.6473 | 581.7136
3895.0354 | 898.0327 | 482.4679 | 590.0729 | 585.0072 | 558.7268 | 548.1568 | 581.6936
3896.0354 | 893.6781 | 482.3186 | 590.3033 | 584.6383 | 559.0148 | 547.6556 | 582.1642
3897.0354 | 899.349 | 482.1124 | 590.4223 | 585.0069 | 559.835 | 547.0965 | 581.8056
3898.0354 | 918.8055 | 482.0385 | 590.174 | 584.0152 | 560.3301 | 547.4834 | 583.4099
3899.0354 | 923.372 | 481.8827 | 589.6797 | 583.9997 | 562.0137 | 551.7378 | 585.1583
3900.0354 | 926.429 | 481.7114 | 588.896 | 583.3515 | 562.9599 | 555.3925 | 586.6809
3901.0354 | 925.8865 | 481.3803 | 589.5076 | 584.3431 | 563.3071 | 554.1032 | 587.4625
3902.0354 | 929.5046 | 481.4181 | 589.1663 | 585.0322 | 562.725 | 552.624 | 588.7728
3903.0354 | 919.5812 | 481.3187 | 588.7777 | 584.4262 | 562.2215 | 551.2274 | 587.831
3904.0354 | 920.9473 | 481.0478 | 588.4068 | 583.5752 | 561.485 | 551.2114 | 588.3029
3905.0354 | 929.9275 | 480.9816 | 588.6454 | 584.3107 | 560.8264 | 550.4632 | 585.7297
3906.0354 | 928.0674 | 480.9903 | 589.5204 | 585.8012 | 560.6455 | 550.0194 | 587.1695
3907.0354 | 925.3114 | 480.925 | 588.4173 | 586.8723 | 560.9927 | 548.3522 | 587.6778
3908.0354 | 924.7175 | 480.7642 | 589.2597 | 586.9456 | 561.1063 | 546.8457 | 588.2261
3909.0354 | 922.8346 | 480.8155 | 589.8983 | 586.283 | 560.807 | 545.7096 | 589.2147
3910.0354 | 927.0085 | 480.6558 | 589.893 | 586.9122 | 560.7347 | 545.3152 | 591.471
3911.0354 | 932.1896 | 480.4676 | 588.8617 | 586.505 | 559.7438 | 543.8636 | 591.3589
3912.0354 | 930.2365 | 480.4585 | 588.9025 | 586.8534 | 559.6765 | 542.4596 | 591.4665
3913.0354 | 933.5202 | 480.2993 | 588.7413 | 586.3982 | 560.1638 | 541.8289 | 592.4526
3914.0354 | 925.6122 | 480.2873 | 589.1261 | 586.8577 | 559.207 | 541.2339 | 594.7773
3915.0354 | 923.4005 | 480.3734 | 589.6673 | 586.5612 | 559.0014 | 541.1109 | 595.5902
3916.0354 | 925.6281 | 480.1191 | 591.6674 | 586.2267 | 559.6176 | 542.1493 | 595.4909
3917.051 | 928.5328 | 480.0929 | 591.1553 | 586.3829 | 559.6541 | 543.1206 | 595.8991
3918.0354 | 925.097 | 480.2017 | 590.3995 | 587.2016 | 559.5704 | 542.9842 | 595.4259
3919.0354 | 928.8317 | 479.7683 | 590.0683 | 586.4265 | 559.4042 | 542.4478 | 597.0481
3920.0354 | 931.1949 | 479.6192 | 589.7482 | 587.4461 | 559.0262 | 542.4414 | 597.2583
3921.0354 | 930.6075 | 479.5121 | 591.1207 | 587.5516 | 559.6514 | 542.1336 | 598.3994
3922.0354 | 931.2308 | 479.413 | 590.6512 | 587.2039 | 559.5942 | 541.4045 | 598.6448
3923.0354 | 935.1547 | 479.283 | 589.6055 | 586.7029 | 560.4954 | 542.8294 | 598.9905
3924.0354 | 932.6013 | 479.3637 | 589.2707 | 586.7368 | 561.4947 | 544.5592 | 599.8073
3925.0354 | 935.6026 | 479.3868 | 590.2152 | 587.634 | 561.7903 | 544.5003 | 600.1631
3926.0354 | 931.1031 | 479.0704 | 589.8375 | 588.7805 | 561.8819 | 544.2036 | 601.2284
3927.0354 | 934.418 | 479.2738 | 589.7861 | 588.206 | 563.5246 | 543.5167 | 600.5458
3928.0354 | 938.556 | 479.2409 | 589.1709 | 587.9199 | 563.7214 | 543.9597 | 602.0761
3929.0354 | 932.0858 | 479.5098 | 588.9529 | 589.5952 | 563.5263 | 543.3428 | 602.7762
3930.0354 | 935.7688 | 478.9777 | 589.4699 | 591.2631 | 563.4652 | 541.9097 | 604.335
3931.0354 | 935.8437 | 478.6867 | 588.4793 | 590.3014 | 562.9087 | 540.297 | 604.8968
3932.0354 | 930.5391 | 478.6115 | 588.1563 | 590.4384 | 562.5369 | 539.4233 | 604.9873
3933.0354 | 933.9195 | 478.4281 | 589.3191 | 590.2828 | 562.6429 | 539.6261 | 605.7101
3934.0354 | 931.8433 | 478.5584 | 588.3613 | 591.1285 | 563.0436 | 540.3875 | 606.3503
3935.0354 | 938.3787 | 478.1875 | 588.4165 | 592.7439 | 563.4395 | 540.3298 | 606.2248
3936.0354 | 935.5701 | 478.1741 | 588.8395 | 593.0179 | 563.6386 | 539.385 | 607.3259
3937.0354 | 927.4563 | 478.1293 | 590.7083 | 592.0866 | 563.6508 | 538.9817 | 608.0204
3938.0354 | 925.1196 | 478.064 | 589.5603 | 594.1908 | 562.6305 | 538.5524 | 607.942
3939.0198 | 925.3919 | 477.9887 | 589.5725 | 594.0288 | 563.2538 | 538.1276 | 608.0856
3940.0354 | 914.5639 | 478.3844 | 589.4185 | 593.2787 | 562.6446 | 536.8935 | 608.1171
3941.0354 | 854.5525 | 478.1457 | 588.7397 | 593.5314 | 561.6241 | 536.3929 | 610.2505
3942.0354 | 881.8457 | 478.6025 | 589.2957 | 593.556 | 561.2733 | 536.7101 | 611.5181
3943.0354 | 592.2778 | 478.2529 | 590.2596 | 592.8436 | 560.7243 | 536.4807 | 610.299
3944.0354 | 428.6879 | 477.749 | 589.8811 | 592.4078 | 559.3837 | 536.743 | 611.5927
3945.0354 | 468.9173 | 477.7103 | 589.1589 | 592.3381 | 558.747 | 540.3343 | 611.6278
3946.0354 | 705.8976 | 478.8784 | 588.907 | 592.1379 | 560.7506 | 543.1924 | 607.2625
3947.0354 | 417.3308 | 477.5346 | 587.787 | 591.9499 | 560.3932 | 543.2937 | 610.1138
3948.0354 | 417.0034 | 477.7756 | 587.918 | 592.6492 | 560.9537 | 542.8412 | 609.7905
3949.0354 | 417.1624 | 477.2661 | 587.2355 | 592.4159 | 562.5555 | 542.7401 | 609.4574
3950.0354 | 415.7347 | 477.6412 | 587.2037 | 593.3624 | 562.795 | 541.4396 | 609.7547
3951.0354 | 413.9259 | 477.3201 | 587.2043 | 593.4685 | 562.2103 | 539.7783 | 607.536
3952.0354 | 412.7522 | 477.3207 | 586.8014 | 595.6838 | 561.5286 | 538.0941 | 606.4127
3953.0354 | 409.3918 | 477.1641 | 587.5689 | 595.0888 | 561.5132 | 536.1875 | 605.3935
3954.0354 | 410.8938 | 477.1913 | 588.1673 | 594.1781 | 560.8219 | 535.9149 | 603.7054
3955.0354 | 412.2412 | 477.0103 | 587.8153 | 593.7597 | 560.3217 | 536.5918 | 601.8866
3956.0354 | 410.4051 | 476.8776 | 589.7129 | 595.7744 | 560.5992 | 540.3004 | 597.0014
3957.0354 | 409.3988 | 476.6696 | 590.4779 | 596.1653 | 562.2635 | 542.153 | 599.7248
3958.0354 | 410.9456 | 476.7438 | 589.0011 | 595.4542 | 562.3457 | 541.3507 | 602.2885
3959.0354 | 412.2395 | 476.6154 | 590.7381 | 594.7775 | 561.3798 | 540.9088 | 603.3653
3960.0354 | 410.9456 | 476.5438 | 588.9955 | 595.2647 | 561.2599 | 539.8296 | 602.7528
3961.0354 | 411.8736 | 476.3069 | 589.3029 | 595.6625 | 561.46 | 539.549 | 601.1364
3962.0354 | 411.6573 | 476.2702 | 589.6569 | 596.1316 | 562.7302 | 539.9062 | 599.9955
3963.0354 | 409.7483 | 476.1565 | 588.6568 | 595.6387 | 562.0965 | 539.6358 | 597.5648
3964.0354 | 407.3002 | 476.0095 | 588.2743 | 596.8782 | 562.0982 | 540.35 | 593.4678
3965.0354 | 415.9944 | 475.9712 | 587.7692 | 595.0236 | 563.89 | 544.8482 | 591.9959
3966.0354 | 415.4109 | 475.8223 | 587.2651 | 594.9625 | 564.5801 | 544.9263 | 589.409
3967.0354 | 408.019 | 476.1199 | 586.8858 | 595.2849 | 564.9037 | 543.2849 | 586.2758
3968.0354 | 408.3008 | 476.016 | 586.6993 | 595.2105 | 565.478 | 541.9768 | 582.8778
3969.0354 | 405.9256 | 475.8425 | 586.4648 | 595.6276 | 565.1277 | 540.2741 | 581.5909
3970.0354 | 405.362 | 475.5276 | 586.5235 | 596.5518 | 565.0057 | 539.4465 | 580.0351
3971.0354 | 405.0036 | 475.4711 | 587.4795 | 597.0161 | 565.0402 | 539.3446 | 579.3215
3972.0354 | 400.3845 | 475.3462 | 588.2126 | 597.3389 | 564.5225 | 539.5436 | 577.4679
3973.0354 | 398.5674 | 475.3176 | 588.7918 | 597.5207 | 563.9725 | 540.2121 | 577.1071
3974.0354 | 400.0227 | 475.3131 | 587.7597 | 599.1139 | 563.8893 | 539.5007 | 575.3668
3975.0354 | 401.302 | 475.2481 | 586.8932 | 599.1854 | 563.527 | 538.4809 | 575.5917
3976.0354 | 383.6923 | 475.2885 | 586.6208 | 597.906 | 562.6665 | 537.086 | 574.0756
3977.0354 | 384.5092 | 475.1163 | 586.0929 | 598.1819 | 562.0072 | 537.3504 | 573.4349
3978.0354 | 386.9961 | 474.9442 | 585.4331 | 598.0575 | 562.2706 | 537.4353 | 573.2879
3979.0354 | 382.6967 | 474.9847 | 585.2921 | 598.0163 | 562.769 | 536.5971 | 570.9932
3980.0354 | 379.859 | 474.7842 | 585.1639 | 598.5114 | 562.4347 | 535.4768 | 568.1566
3981.0354 | 388.8716 | 474.7593 | 584.8291 | 598.188 | 562.667 | 536.3811 | 564.2834
3982.0354 | 387.7933 | 474.7318 | 584.8043 | 597.6822 | 563.278 | 536.1394 | 562.5611
3983.0354 | 389.4182 | 474.5181 | 584.4095 | 598.878 | 563.4583 | 536.9979 | 562.4376
3984.0354 | 384.8835 | 474.5424 | 584.2006 | 598.3738 | 564.1502 | 537.1247 | 562.4884
3985.0354 | 391.0828 | 474.4438 | 584.8128 | 600.399 | 564.5398 | 536.3968 | 563.1618
3986.0354 | 385.63 | 474.3905 | 585.5881 | 601.305 | 564.8328 | 536.2751 | 563.2975
3987.0354 | 358.5803 | 474.0846 | 585.9134 | 601.0428 | 566.5284 | 536.8674 | 562.734
3988.0354 | 347.2055 | 474.0093 | 585.311 | 601.1719 | 565.9459 | 535.2295 | 563.2717
3989.0354 | 391.8436 | 474.0382 | 585.1853 | 601.6093 | 565.0539 | 534.8509 | 563.5039
3990.0354 | 391.3699 | 474.1538 | 584.9033 | 601.8438 | 564.6899 | 535.7234 | 564.5627
3991.0354 | 389.964 | 474.0366 | 584.1911 | 601.6071 | 563.8202 | 535.1744 | 564.0846
3992.0354 | 383.8182 | 473.9191 | 584.0526 | 600.568 | 563.8444 | 535.4042 | 563.1234
3993.0354 | 377.7934 | 473.9056 | 583.9394 | 600.4791 | 563.3182 | 535.3455 | 562.3778
3994.0354 | 384.3348 | 473.5464 | 584.749 | 601.4765 | 563.5166 | 536.7653 | 562.596
3995.0354 | 378.9182 | 473.29 | 585.864 | 602.4003 | 565.6773 | 538.0919 | 563.1767
3996.0354 | 387.4618 | 473.2527 | 585.8703 | 601.8574 | 566.6925 | 538.4333 | 562.5858
3997.0354 | 400.4869 | 473.2644 | 584.1964 | 602.6745 | 566.6988 | 540.2391 | 563.9077
3998.0354 | 395.2405 | 473.3699 | 585.5598 | 602.0615 | 566.0036 | 539.7898 | 563.5259
3999.0354 | 396.8775 | 473.1624 | 585.3116 | 601.4518 | 565.1331 | 539.7892 | 563.9492
4000.0354 | 396.1765 | 473.0715 | 584.6207 | 600.9814 | 564.8533 | 540.145 | 563.9716
4001.0354 | 393.6606 | 473.1021 | 586.5749 | 601.6534 | 564.6896 | 541.7026 | 563.4629
4002.0198 | 393.4993 | 473.0058 | 585.3217 | 601.9749 | 564.524 | 542.6809 | 564.9488
4003.0354 | 398.0026 | 472.7454 | 584.2017 | 602.356 | 565.3861 | 542.9273 | 564.5798
4004.0354 | 394.4967 | 472.7503 | 584.668 | 602.3551 | 565.8774 | 540.6791 | 564.6986
4005.0354 | 384.8389 | 472.6836 | 585.3815 | 602.7675 | 565.9736 | 539.7895 | 565.5847
4006.0354 | 392.4127 | 472.4564 | 584.2318 | 602.8289 | 566.4607 | 540.0869 | 566.1677
4007.0354 | 320.6344 | 472.3594 | 584.7496 | 603.5572 | 566.0274 | 539.7397 | 567.0496
4008.0354 | 323.918 | 472.2884 | 585.5381 | 602.632 | 566.196 | 539.8562 | 567.2399
4009.0354 | 397.1131 | 472.1888 | 585.0049 | 602.8832 | 565.7008 | 539.8467 | 569.3655
4010.0354 | 363.2371 | 472.2439 | 585.0691 | 602.5476 | 565.2611 | 540.4953 | 570.7798
4011.0354 | 506.1494 | 472.2418 | 584.8775 | 601.9473 | 564.8637 | 540.3714 | 570.3967
4012.0354 | 414.5511 | 471.9204 | 583.6545 | 602.7746 | 564.3183 | 540.694 | 571.1559
4013.0354 | 317.3925 | 471.8978 | 583.0424 | 605.0672 | 564.7916 | 540.5119 | 571.968
4014.0354 | 288.3612 | 471.8659 | 583.8295 | 604.1039 | 565.9217 | 540.5248 | 571.7755
4015.0354 | 306.9897 | 471.8663 | 584.551 | 603.2234 | 565.498 | 539.4987 | 569.5475
4016.0354 | 399.7024 | 471.7735 | 585.2409 | 602.3379 | 564.3925 | 540.3832 | 568.6153
4017.0354 | 398.6085 | 471.7203 | 585.2954 | 602.9946 | 562.8645 | 540.3393 | 567.4076
4018.0354 | 391.6704 | 471.6904 | 586.328 | 604.9268 | 562.7894 | 541.3564 | 567.6232
4019.0354 | 398.1605 | 471.4208 | 585.0263 | 604.6789 | 562.4561 | 540.6961 | 567.8166
4020.0354 | 392.3684 | 471.2578 | 584.6335 | 604.9091 | 562.3038 | 540.6515 | 566.6699
4021.0354 | 398.2934 | 471.4579 | 583.9896 | 603.9965 | 562.3582 | 541.3199 | 564.9315
4022.0354 | 404.1603 | 471.2175 | 583.5418 | 604.7281 | 562.6304 | 540.5728 | 565.1862
4023.0354 | 406.9414 | 471.1339 | 582.9805 | 604.7241 | 563.734 | 539.5177 | 564.3441
4024.0354 | 392.7121 | 471.3377 | 583.0792 | 603.6945 | 564.3615 | 539.2394 | 564.9826
4025.0354 | 388.3393 | 471.2791 | 582.6508 | 603.2047 | 565.4558 | 541.8779 | 564.2917
4026.0354 | 397.9735 | 471.1695 | 582.1783 | 603.167 | 566.8135 | 542.7624 | 563.7007
4027.0354 | 386.1899 | 471.0398 | 581.8205 | 603.5274 | 567.635 | 541.7917 | 562.9646
4028.0354 | 402.6085 | 470.9993 | 581.5849 | 603.3004 | 568.1611 | 541.0093 | 562.432
4029.0354 | 390.7423 | 470.8941 | 581.6705 | 603.5825 | 569.0725 | 540.3626 | 561.73
4030.0354 | 385.2684 | 470.7958 | 581.3608 | 603.9256 | 569.8267 | 539.7907 | 561.8109
4031.0354 | 386.6274 | 470.6269 | 583.0609 | 604.4621 | 570.0744 | 539.006 | 561.7464
4032.0354 | 385.2654 | 470.4705 | 581.916 | 603.2387 | 569.7293 | 539.124 | 561.0576
4033.0354 | 386.8716 | 470.3247 | 581.8458 | 603.1834 | 569.8486 | 539.8751 | 560.0918
4034.0354 | 389.9418 | 470.2536 | 581.0761 | 602.7152 | 572.3106 | 540.703 | 560.6709
4035.0354 | 390.9275 | 470.1626 | 580.7005 | 602.7498 | 574.0846 | 544.0125 | 560.49
4036.0354 | 384.3439 | 470.5703 | 580.4398 | 604.1618 | 573.9158 | 542.3203 | 557.7944
4037.0354 | 593.137 | 470.21 | 580.1975 | 604.296 | 573.0108 | 539.9748 | 557.5639
4038.0354 | 895.2747 | 470.0016 | 580.259 | 603.5455 | 572.4915 | 538.9358 | 556.638
4039.0354 | 879.4367 | 469.8787 | 580.2828 | 602.9328 | 571.1264 | 538.1304 | 556.5439
4040.0354 | 937.4302 | 469.9967 | 579.3968 | 602.8206 | 572.2548 | 538.8026 | 555.9083
4041.0354 | 432.9703 | 469.9212 | 579.0925 | 602.8571 | 573.1897 | 537.7036 | 555.7559
4042.0354 | 429.6651 | 469.6507 | 578.8305 | 602.6277 | 572.766 | 536.0107 | 555.6885
4043.0354 | 385.6002 | 469.6864 | 578.6505 | 602.9934 | 573.739 | 535.1836 | 555.814
4044.0354 | 406.2428 | 469.5275 | 578.297 | 603.7992 | 574.2369 | 533.6029 | 555.4829
4045.0354 | 385.6196 | 469.3981 | 578.0549 | 603.2556 | 573.657 | 532.6847 | 554.9125
4046.0354 | 382.7717 | 469.476 | 577.8873 | 602.6654 | 573.0788 | 531.8223 | 555.1875
4047.0354 | 381.304 | 469.3953 | 577.5702 | 602.4483 | 571.8954 | 531.39 | 556.5877
4048.0354 | 799.4675 | 469.2045 | 577.0702 | 602.4644 | 573.4042 | 530.502 | 556.1845
4049.0354 | 791.379 | 469.0366 | 577.0443 | 602.1332 | 575.2245 | 530.4935 | 555.6091
4050.0354 | 554.1376 | 469.049 | 576.5169 | 601.4642 | 578.5698 | 530.5975 | 556.0995
4051.0354 | 519.6926 | 468.9801 | 576.5839 | 601.5511 | 577.801 | 529.2037 | 553.8221
4052.0354 | 473.831 | 469.2817 | 576.1053 | 601.8259 | 576.6893 | 528.7228 | 552.9998
4053.0354 | 469.8983 | 469.0081 | 576.035 | 601.5551 | 577.6076 | 529.1647 | 553.3687
4054.0354 | 440.8901 | 468.8342 | 575.8094 | 601.4809 | 579.0446 | 529.4019 | 554.6532
4055.0354 | 415.6805 | 468.8129 | 575.261 | 601.0318 | 579.1046 | 529.7228 | 554.7677
4056.0354 | 411.8642 | 469.1295 | 575.1767 | 601.4455 | 577.7277 | 528.9263 | 554.8441
4057.0354 | 421.2964 | 468.8681 | 575.1099 | 600.7486 | 577.0094 | 528.9233 | 555.9839
4058.0354 | 437.8289 | 468.5729 | 576.2033 | 600.5592 | 575.5998 | 528.9069 | 556.7921
4059.0354 | 439.5087 | 468.6023 | 575.2077 | 600.1021 | 574.8745 | 530.1169 | 556.8224
4060.0354 | 435.5307 | 468.4009 | 574.986 | 600.9168 | 574.1498 | 531.2226 | 558.762
4061.0354 | 443.2035 | 468.4587 | 574.173 | 600.1834 | 576.8067 | 532.3404 | 550.2697
4062.0354 | 414.841 | 468.1854 | 573.7648 | 599.9522 | 575.5411 | 531.8539 | 558.9177
4063.0354 | 442.9753 | 468.0076 | 574.0293 | 599.9201 | 575.1369 | 531.1039 | 559.1025
4064.0354 | 435.8976 | 467.8958 | 574.077 | 599.9791 | 574.8509 | 531.2381 | 560.1319
4065.0354 | 434.8019 | 467.8271 | 573.8369 | 600.2516 | 575.5366 | 531.0336 | 559.9477
4066.0354 | 580.2767 | 467.8444 | 573.1195 | 599.8521 | 575.0693 | 530.1329 | 560.3726
4067.0354 | 580.034 | 468.2439 | 572.9279 | 599.7747 | 574.3424 | 528.2149 | 560.0099
4068.0354 | 634.1066 | 467.9189 | 572.9152 | 599.5208 | 573.1906 | 527.2868 | 559.198
4069.0354 | 416.0043 | 467.598 | 572.935 | 599.8589 | 572.6667 | 528.3353 | 559.5505
4070.0354 | 409.9102 | 467.484 | 572.8942 | 599.1149 | 572.9565 | 529.185 | 559.8024
4071.0354 | 409.8722 | 467.3593 | 572.2979 | 599.2108 | 572.8006 | 528.7583 | 559.5725
4072.0354 | 640.5696 | 467.4806 | 572.2812 | 602.0619 | 572.2274 | 528.0685 | 558.6584
4073.0354 | 760.558 | 467.2944 | 571.8899 | 600.7446 | 571.3862 | 528.1052 | 559.6034
4074.0354 | 436.6448 | 467.1797 | 572.8368 | 600.1208 | 571.1369 | 528.1927 | 558.9529
4075.0354 | 395.6816 | 467.14 | 571.99 | 601.1723 | 570.5611 | 528.7534 | 559.3504
4076.0354 | 395.6456 | 467.0493 | 571.76 | 601.403 | 569.962 | 528.5974 | 559.4637
4077.0354 | 376.9576 | 467.0753 | 572.3012 | 602.0388 | 569.4235 | 528.5889 | 559.2382
4078.0354 | 359.9567 | 466.9097 | 574.3212 | 601.3993 | 569.8386 | 528.4078 | 559.177
4079.0354 | 351.5408 | 466.7647 | 574.6084 | 600.8164 | 570.0305 | 528.9598 | 558.7313
4080.0354 | 357.2682 | 466.7899 | 576.0201 | 600.2595 | 570.8555 | 530.9821 | 559.3448
4081.0354 | 351.1699 | 466.6395 | 573.4105 | 600.4447 | 569.6068 | 532.8805 | 560.0674
4082.0354 | 348.3298 | 466.4739 | 572.4611 | 600.8701 | 569.1359 | 532.325 | 560.0939
4083.0354 | 341.2687 | 466.5307 | 573.1881 | 600.898 | 568.1645 | 531.6544 | 560.1514
4084.0354 | 404.0546 | 466.5821 | 572.4274 | 599.5209 | 567.9544 | 533.6369 | 561.1124
4085.0354 | 401.8891 | 466.5145 | 574.6252 | 599.5634 | 565.844 | 535.4128 | 562.1504
4086.0354 | 398.3049 | 466.3267 | 573.9392 | 600.1025 | 566.7779 | 537.7642 | 562.9213
4087.0354 | 398.7207 | 466.2128 | 574.1567 | 600.161 | 566.1335 | 538.6529 | 563.3175
4088.0354 | 419.3743 | 466.1151 | 572.9781 | 600.9766 | 566.4451 | 539.4449 | 563.8149
4089.0354 | 401.8203 | 465.9314 | 572.5153 | 600.0081 | 566.0481 | 537.978 | 562.7056
4090.0354 | 380.869 | 465.8015 | 572.2556 | 600.7197 | 566.0225 | 537.1474 | 562.7849
4091.0354 | 376.9596 | 465.8547 | 572.4044 | 601.9024 | 565.6744 | 536.0367 | 561.8686
4092.0354 | 370.4737 | 465.8694 | 572.9005 | 600.5563 | 564.4211 | 535.6183 | 561.5334
4093.0354 | 370.7874 | 465.7627 | 574.0729 | 600.0721 | 564.0192 | 537.0267 | 562.2032
4094.0354 | 370.512 | 465.5194 | 573.0318 | 600.0587 | 563.486 | 537.8224 | 562.548
4095.0354 | 367.1444 | 465.2955 | 572.7598 | 599.6084 | 563.0407 | 539.3483 | 562.4647
4096.0354 | 373.4573 | 465.2466 | 572.7784 | 599.6154 | 562.8996 | 538.589 | 562.5487
4097.0354 | 375.0018 | 465.1925 | 572.1073 | 599.4105 | 562.5633 | 538.1985 | 561.3999
4098.0354 | 365.9518 | 465.291 | 572.759 | 598.6414 | 561.8833 | 538.7812 | 561.4412
4099.0354 | 359.4609 | 465.2853 | 572.6796 | 598.4344 | 561.5014 | 539.6581 | 561.8252
4100.0354 | 370.8694 | 465.1389 | 572.9913 | 598.8405 | 560.1848 | 540.1802 | 562.4319
4101.0354 | 357.0156 | 465.1255 | 572.0258 | 599.3566 | 561.059 | 540.2403 | 561.2065
4102.0354 | 345.1645 | 464.9076 | 571.2947 | 598.7356 | 561.992 | 539.3245 | 559.5972
4103.0354 | 341.8525 | 464.8238 | 571.0223 | 599.5101 | 562.3709 | 536.9748 | 558.004
4104.0354 | 329.017 | 464.8697 | 571.2185 | 599.7726 | 561.9149 | 535.1483 | 556.8105
4105.0354 | 326.5933 | 464.7849 | 572.1638 | 599.9142 | 561.9532 | 533.4424 | 555.1266
4106.0354 | 802.1781 | 464.7216 | 571.4588 | 599.3982 | 562.135 | 533.0716 | 554.1943
4107.0354 | 392.3949 | 464.7251 | 572.1845 | 599.2631 | 561.6862 | 532.9468 | 554.2841
4108.0354 | 343.8611 | 464.5306 | 571.171 | 598.6051 | 562.0865 | 532.2595 | 555.7494
4109.0354 | 343.7506 | 464.5205 | 571.1081 | 598.0103 | 563.4042 | 532.1213 | 555.8261
4110.0354 | 782.3965 | 464.4265 | 570.875 | 598.797 | 563.6775 | 531.7329 | 554.3016
4111.0354 | 647.4296 | 464.5773 | 570.2474 | 598.6056 | 565.8236 | 532.6836 | 552.5341
4112.0354 | 355.9589 | 464.2257 | 569.9448 | 598.6351 | 566.0653 | 531.9851 | 552.6745
4113.0354 | 351.3561 | 464.2302 | 569.6687 | 597.8253 | 567.7345 | 533.1242 | 551.2519
4114.0354 | 348.1222 | 464.042 | 569.3824 | 597.6112 | 567.7619 | 532.7839 | 550.0732
4115.0354 | 342.8672 | 463.9538 | 569.3157 | 597.2028 | 567.2572 | 531.9707 | 548.8376
4116.0354 | 343.5023 | 463.797 | 569.3623 | 597.2644 | 566.7535 | 530.8783 | 547.8916
4117.0354 | 336.9567 | 463.7514 | 569.0806 | 596.9159 | 566.9115 | 531.2973 | 547.4082
4118.0354 | 337.3894 | 463.4645 | 569.2215 | 596.8564 | 566.4141 | 531.3908 | 547.0349
4119.0354 | 377.7577 | 463.4287 | 568.6972 | 596.7142 | 566.2377 | 531.3327 | 546.6695
4120.0354 | 333.265 | 463.5143 | 568.2152 | 596.7833 | 566.0507 | 530.6782 | 546.6953
4121.0354 | 326.7739 | 463.5348 | 568.6906 | 597.2197 | 565.9656 | 529.7404 | 546.4322
4122.0354 | 321.7839 | 463.3853 | 568.3466 | 596.3107 | 566.7213 | 529.6994 | 545.8492
4123.0354 | 320.4141 | 463.2275 | 567.6648 | 596.0662 | 567.9985 | 529.4661 | 545.5548
4124.0354 | 317.5301 | 463.1205 | 567.7036 | 596.1676 | 568.7006 | 529.1745 | 544.6158
4125.0354 | 311.5269 | 463.0983 | 567.2838 | 595.8925 | 568.7727 | 528.9963 | 543.5518
4126.0354 | 307.6699 | 463.0926 | 567.6001 | 596.6891 | 568.4824 | 527.6101 | 541.8912
4127.0354 | 307.3678 | 462.8895 | 567.7148 | 598.5589 | 568.4865 | 526.7799 | 540.4392
4128.0354 | 828.8204 | 462.7665 | 568.0457 | 597.7618 | 568.7225 | 527.443 | 538.9073
4129.0354 | 973.2111 | 462.7802 | 567.8828 | 597.9825 | 568.7736 | 528.5226 | 538.7639
4130.0354 | 996.2922 | 462.8313 | 569.3614 | 598.3435 | 569.0496 | 529.5612 | 538.7868
4131.0354 | 987.7174 | 462.7142 | 568.421 | 598.0213 | 568.8693 | 529.476 | 538.5287
4132.0354 | 987.647 | 462.6498 | 568.0889 | 598.245 | 568.2868 | 529.0886 | 537.327
4133.0354 | 991.8182 | 462.6707 | 568.4094 | 597.525 | 568.3755 | 530.0963 | 537.3353
4134.0354 | 997.1707 | 462.5431 | 570.4083 | 596.8455 | 567.317 | 530.3876 | 538.2912
4135.0354 | 1003.945 | 462.2733 | 569.2981 | 596.9324 | 566.2957 | 530.7891 | 539.1692
4136.0354 | 1004.6833 | 462.0471 | 568.6174 | 596.9554 | 566.2522 | 531.0635 | 539.9071
4137.0354 | 1003.9486 | 461.9735 | 568.389 | 596.7747 | 565.5079 | 530.8237 | 540.5564
4138.0354 | 1008.8063 | 462.0898 | 568.0977 | 596.8256 | 565.8458 | 531.0091 | 540.9404
4139.0354 | 1016.764 | 461.9262 | 567.4523 | 596.6689 | 565.8295 | 532.1639 | 540.4773
4140.0354 | 1034.3161 | 461.9568 | 567.1976 | 597.015 | 566.6338 | 533.0489 | 539.5262
4141.0354 | 1049.8034 | 461.7373 | 566.7169 | 596.5878 | 567.7969 | 532.9379 | 539.4481
4142.0354 | 1051.9732 | 461.7147 | 566.6322 | 597.6139 | 567.7617 | 531.4086 | 538.7366
4143.0354 | 1050.9324 | 461.7229 | 566.6422 | 597.4166 | 567.6247 | 530.3657 | 538.415
4144.0354 | 1056.363 | 461.7087 | 567.5471 | 596.5851 | 567.387 | 529.7919 | 538.9815
4145.0354 | 1047.4159 | 461.6469 | 567.4279 | 596.6668 | 567.246 | 530.7603 | 539.5198
4146.0354 | 1051.9236 | 461.4921 | 567.0987 | 597.1905 | 567.8602 | 531.5858 | 539.6474
4147.0354 | 1056.3181 | 461.2036 | 566.255 | 596.8841 | 567.3267 | 531.4955 | 538.9758
4148.0354 | 1053.1869 | 461.24 | 566.2837 | 597.1488 | 566.8255 | 530.6529 | 537.9483
4149.0354 | 1070.0202 | 461.2316 | 566.4666 | 596.3759 | 567.0605 | 530.4109 | 537.1014
4150.0354 | 1063.3701 | 461.046 | 565.9883 | 597.3981 | 566.8379 | 530.1749 | 536.1218
4151.0354 | 1079.7391 | 460.9979 | 566.1406 | 598.414 | 566.6645 | 529.0578 | 535.2796
4152.0354 | 1074.5228 | 461.0462 | 565.5573 | 598.721 | 566.9054 | 529.5008 | 534.208
4153.0354 | 1081.6607 | 460.9479 | 566.6546 | 598.5333 | 566.9133 | 529.8979 | 534.091
4154.0354 | 1041.1594 | 460.8706 | 567.3578 | 597.6584 | 567.5117 | 530.8796 | 533.9882
4155.0354 | 1061.4511 | 460.6616 | 566.6993 | 598.7529 | 567.3781 | 532.583 | 534.111
4156.0354 | 1024.1726 | 460.6683 | 566.4233 | 599.5693 | 568.0736 | 533.2844 | 534.1005
4157.0354 | 1037.167 | 460.5465 | 566.2849 | 599.6981 | 567.5439 | 532.7041 | 533.5204
4158.0354 | 960.2392 | 460.5353 | 565.9079 | 599.1855 | 567.5191 | 531.5093 | 532.6193
4159.0354 | 1034.0883 | 460.5334 | 566.2206 | 597.9799 | 566.4778 | 531.5231 | 532.6785
4160.0354 | 1045.6423 | 460.4241 | 565.8638 | 598.3942 | 565.6967 | 534.0457 | 533.6444
4161.0354 | 1026.7576 | 460.2839 | 565.3449 | 598.8758 | 565.8888 | 533.3525 | 532.8975
4162.0354 | 1070.9881 | 460.1515 | 566.1711 | 597.9126 | 566.2335 | 533.2499 | 532.401
4163.0354 | 1114.6505 | 460.0549 | 565.7917 | 597.9252 | 566.0933 | 532.9405 | 531.4435
4164.0354 | 863.9458 | 460.0456 | 565.3126 | 598.0232 | 565.6679 | 532.2143 | 531.0011
4165.0354 | 1025.4001 | 460.061 | 565.3897 | 598.6017 | 565.7121 | 533.293 | 530.7649
4166.0354 | 970.8456 | 459.7932 | 565.8275 | 598.7064 | 566.4864 | 533.9756 | 530.6771
4167.0354 | 1077.5397 | 459.6826 | 565.7014 | 599.5853 | 567.4422 | 534.5274 | 530.8227
4168.0354 | 1057.3812 | 459.7572 | 565.1231 | 599.7105 | 567.5874 | 533.4035 | 530.2794
4169.0354 | 1112.1945 | 459.6816 | 564.6841 | 598.6828 | 567.4535 | 532.5778 | 529.6287
4170.0354 | 1129.1033 | 459.6521 | 564.3966 | 599.6574 | 568.1132 | 531.9841 | 528.7324
4171.0354 | 970.5966 | 459.6603 | 564.0747 | 599.7526 | 568.177 | 530.8903 | 528.096
4172.0354 | 961.6668 | 459.5856 | 564.1768 | 600.6239 | 568.5319 | 530.7014 | 528.8422
4173.0354 | 985.326 | 459.5459 | 563.9978 | 600.2638 | 568.9801 | 530.5975 | 528.6351
4174.0354 | 1140.751 | 459.4815 | 563.3716 | 598.6381 | 569.3824 | 532.8271 | 529.2788
4175.0354 | 1153.6491 | 459.5655 | 562.9564 | 597.8523 | 571.2016 | 536.3519 | 529.936
4176.0354 | 1156.2429 | 459.3611 | 563.2017 | 597.8832 | 570.3744 | 535.9442 | 529.131
4177.0354 | 1163.6412 | 459.281 | 562.8111 | 598.0191 | 570.1402 | 537.9494 | 528.6094
4178.0354 | 998.1982 | 459.1688 | 562.5176 | 597.4745 | 570.5151 | 537.4853 | 528.6105
4179.0354 | 1069.7593 | 458.9296 | 562.1834 | 597.0948 | 571.3883 | 537.6473 | 527.9012
4180.0354 | 1075.9236 | 458.9628 | 561.9713 | 596.7862 | 570.7683 | 536.2472 | 526.5753
4181.0354 | 1070.2478 | 458.8303 | 563.1074 | 596.9355 | 569.7191 | 535.0825 | 525.618
4182.0354 | 1091.7067 | 458.8053 | 564.0955 | 597.1488 | 568.3943 | 534.1962 | 525.5941
4183.0354 | 1067.0178 | 458.7491 | 562.3574 | 598.3685 | 568.0387 | 533.4986 | 525.9127
4184.0354 | 1068.3341 | 458.561 | 561.7771 | 597.3497 | 568.1065 | 532.8579 | 525.0448
4185.0354 | 1087.1508 | 458.4718 | 561.6781 | 597.5622 | 567.2001 | 530.9029 | 523.5638
4186.0354 | 1091.3253 | 458.517 | 561.2945 | 598.1557 | 566.6476 | 530.0498 | 523.4412
4187.0354 | 1104.1955 | 458.3367 | 561.2171 | 597.4643 | 565.8561 | 528.197 | 522.3543
4188.0354 | 1110.0934 | 458.3469 | 561.2161 | 596.7389 | 565.47 | 527.5742 | 522.4149
4189.0354 | 1078.9032 | 458.3682 | 561.5254 | 596.8239 | 564.488 | 526.8117 | 521.8941
4190.0354 | 1079.7857 | 458.3348 | 560.6541 | 596.1658 | 563.9321 | 527.1083 | 522.175
4191.0354 | 1087.3409 | 458.1796 | 560.8575 | 596.3656 | 563.296 | 528.4017 | 521.862
4192.0354 | 1070.3055 | 458.1617 | 560.9887 | 596.0168 | 563.6603 | 528.8826 | 521.0018
4193.0354 | 1087.9854 | 457.9612 | 561.1513 | 595.9275 | 563.9244 | 528.5607 | 521.0644
4194.0354 | 1083.595 | 457.9463 | 560.468 | 595.8485 | 563.8773 | 528.9178 | 521.3
4195.0354 | 1095.404 | 457.9457 | 560.8043 | 595.9616 | 564.8312 | 529.6339 | 521.1793
4196.0354 | 1083.7862 | 457.9258 | 561.3471 | 596.4177 | 564.7166 | 529.1587 | 521.2804
4197.0354 | 1059.2628 | 457.8468 | 560.4825 | 596.7938 | 565.6517 | 529.5979 | 521.9969
4198.0354 | 1110.0444 | 457.6372 | 559.9223 | 596.3678 | 566.5396 | 529.559 | 522.1148
4199.0354 | 1086.4775 | 457.7333 | 559.9974 | 595.5591 | 567.4458 | 528.9663 | 522.0712
4200.0354 | 1120.0821 | 457.6146 | 560.8343 | 595.4871 | 566.4364 | 528.6729 | 520.9807
4201.0354 | 1107.8425 | 457.5869 | 560.6496 | 596.0998 | 566.4141 | 529.1906 | 521.624
4202.0354 | 1105.7634 | 457.5274 | 559.607 | 596.2433 | 566.8993 | 529.7775 | 521.0981
4203.0354 | 1124.2329 | 457.4975 | 559.2059 | 595.1043 | 567.6099 | 531.2755 | 520.3742
4204.0354 | 1106.9846 | 457.2914 | 558.8772 | 594.5791 | 568.1895 | 532.3722 | 520.6462
4205.0354 | 1088.9638 | 457.337 | 558.8634 | 594.5618 | 568.2833 | 532.8485 | 520.2317
4206.0354 | 1127.4425 | 457.2975 | 559.442 | 594.5359 | 568.0182 | 532.7757 | 519.7985
4207.0354 | 1152.4517 | 457.15 | 558.6837 | 594.2621 | 568.3797 | 533.7591 | 521.1917
4208.0354 | 1148.371 | 457.0653 | 558.7627 | 594.2648 | 568.5105 | 534.0289 | 522.6858
4209.0354 | 1151.4529 | 456.9519 | 558.2109 | 593.5414 | 568.8432 | 535.4613 | 522.8412
4210.0354 | 1157.9112 | 456.9056 | 557.778 | 593.4349 | 568.8728 | 536.2045 | 522.8409
4211.0354 | 1152.0659 | 456.8424 | 557.496 | 593.4289 | 568.883 | 535.3753 | 522.4784
4212.0354 | 1150.3933 | 456.7065 | 557.2299 | 592.991 | 567.7071 | 534.162 | 520.7761
4213.0354 | 1156.0636 | 456.6606 | 557.0125 | 592.6483 | 566.1997 | 531.9595 | 518.8747
4214.0354 | 1180.4374 | 456.5935 | 556.9083 | 593.0696 | 564.5881 | 530.222 | 518.1538
4215.0354 | 1182.4907 | 456.5286 | 557.3832 | 592.8723 | 564.2467 | 529.5172 | 517.6499
4216.0667 | 1193.4324 | 456.4266 | 556.9574 | 592.2788 | 564.6999 | 530.8657 | 518.5001
4217.0354 | 1188.422 | 456.2983 | 556.5788 | 591.9167 | 565.4096 | 534.0326 | 519.416
4218.0354 | 1190.0602 | 456.1853 | 556.2018 | 591.6266 | 566.4095 | 535.937 | 519.5419
4219.0354 | 1186.065 | 456.1682 | 556.0426 | 591.4577 | 567.4065 | 535.1157 | 519.3133
4220.0354 | 1196.2149 | 456.0609 | 556.9312 | 591.6523 | 566.1432 | 533.2222 | 518.7209
4221.0354 | 1205.7253 | 455.8574 | 556.0533 | 591.0748 | 565.4984 | 532.7627 | 518.786
4222.0354 | 1207.6753 | 455.8644 | 555.4958 | 590.6489 | 564.8695 | 533.4785 | 518.9121
4223.0354 | 1211.1624 | 455.924 | 555.3673 | 590.6096 | 564.41 | 533.6018 | 518.9351
4224.0354 | 1248.3052 | 455.8375 | 555.0196 | 590.3878 | 565.5135 | 534.1118 | 519.0509
4225.0354 | 1225.3716 | 455.9446 | 555.1131 | 590.0048 | 566.692 | 534.2824 | 518.3932
4226.0354 | 1218.4017 | 456.0155 | 554.4862 | 589.7203 | 567.1626 | 534.5393 | 518.9729
4227.0354 | 1246.6061 | 455.807 | 554.455 | 589.6512 | 566.7518 | 533.2377 | 518.1777
4228.0354 | 1248.8666 | 455.7196 | 554.0912 | 589.4664 | 566.5879 | 533.7524 | 518.3801
4229.0354 | 1246.1465 | 455.5636 | 553.7274 | 588.9646 | 567.3612 | 535.1022 | 518.5259
4230.0354 | 1247.1699 | 455.4958 | 553.9885 | 589.0917 | 566.8131 | 534.0884 | 518.4748
4231.0354 | 1249.1683 | 455.3339 | 553.4012 | 589.2451 | 566.1614 | 532.5597 | 517.608
4232.0354 | 1249.1697 | 455.3173 | 553.1315 | 588.6628 | 566.6015 | 531.9319 | 517.3318
4233.0354 | 1249.1707 | 455.2257 | 553.1726 | 588.6586 | 566.3983 | 531.1663 | 517.7939
4234.0354 | 1249.1717 | 455.2016 | 552.7962 | 589.0738 | 566.7038 | 530.9792 | 517.3845
4235.0354 | 1249.1721 | 455.1604 | 552.5963 | 589.8108 | 567.0749 | 530.0237 | 516.9976
4236.0354 | 1249.1723 | 455.1067 | 552.3146 | 589.2604 | 566.869 | 528.7335 | 517.2658
4237.0354 | 1249.1736 | 455.0092 | 552.2041 | 589.1108 | 566.7188 | 529.2454 | 516.5427
4238.0354 | 1249.1736 | 455.018 | 551.943 | 588.3451 | 566.6493 | 529.6909 | 516.4293
4239.0354 | 874.6343 | 455.0685 | 552.0338 | 588.5515 | 565.7918 | 529.0072 | 520.0935
4240.0354 | 871.4536 | 455.1013 | 555.1487 | 588.0018 | 565.3108 | 529.0455 | 521.7249
4241.0354 | 675.5169 | 454.892 | 553.377 | 587.6912 | 564.025 | 529.1574 | 525.0138
4242.0354 | 686.615 | 454.7239 | 553.3421 | 587.7483 | 562.9642 | 529.2201 | 524.9264
4243.0354 | 1061.4112 | 454.3507 | 552.8776 | 587.3695 | 562.9869 | 530.3102 | 523.0518
4244.0354 | 1045.7785 | 454.446 | 552.1654 | 587.4331 | 564.6778 | 530.7804 | 524.0899
4245.0354 | 1055.951 | 454.4108 | 552.1991 | 588.2298 | 564.866 | 529.6921 | 524.5197
4246.0354 | 1054.5921 | 454.3867 | 553.3094 | 587.3979 | 564.6294 | 529.1178 | 525.1361
4247.0354 | 1035.8889 | 454.2877 | 553.2177 | 586.7857 | 563.7302 | 529.3937 | 525.5382
4248.0354 | 1112.8283 | 454.0976 | 552.4904 | 586.9416 | 562.2506 | 528.869 | 525.0516
4249.0354 | 1037.1207 | 454.0571 | 551.7953 | 586.9286 | 561.1595 | 528.5771 | 525.7168
4250.0354 | 1000.8806 | 454.0683 | 553.0964 | 586.9792 | 560.1632 | 527.5592 | 524.999
4251.0354 | 916.0085 | 454.1304 | 553.911 | 586.4621 | 559.3475 | 526.8387 | 526.9334
4252.0354 | 1158.2505 | 453.9027 | 552.2983 | 586.0859 | 558.5787 | 526.1562 | 525.109
4253.0354 | 416.7923 | 453.7623 | 552.5075 | 586.6946 | 557.2243 | 525.3342 | 532.9505
4254.0354 | 494.9661 | 453.7138 | 552.4478 | 587.4202 | 556.4996 | 525.1577 | 531.6579
4255.0354 | 300.3608 | 453.692 | 552.4476 | 587.6891 | 556.2299 | 525.4538 | 535.8128
4256.0354 | 285.8381 | 453.6918 | 552.3834 | 587.5398 | 555.6896 | 524.7537 | 537.4956
4257.0354 | 298.1264 | 453.6564 | 552.3596 | 587.0579 | 555.3686 | 524.4617 | 538.483
4258.0354 | 279.7954 | 453.6095 | 553.3235 | 587.6235 | 555.9298 | 524.1676 | 538.7833
4259.0354 | 305.5011 | 453.4778 | 553.8399 | 587.6964 | 557.1911 | 525.4902 | 539.5005
4260.0354 | 932.7932 | 453.6185 | 553.6336 | 587.1924 | 557.3015 | 526.1346 | 532.4606
4261.0354 | 1249.1919 | 453.4599 | 553.9961 | 586.7952 | 556.5533 | 526.1366 | 528.6023
4262.0354 | 1233.4261 | 453.5035 | 554.1554 | 587.1444 | 556.6701 | 527.6409 | 530.4443
4263.0354 | 1249.1935 | 453.5006 | 554.4492 | 587.1076 | 556.2295 | 528.8432 | 530.5889
4264.0354 | 1249.1943 | 453.2844 | 554.5442 | 587.318 | 556.0975 | 529.915 | 531.7076
4265.0354 | 1249.1948 | 453.1719 | 553.8272 | 586.2973 | 556.0607 | 530.224 | 532.0368
4266.0354 | 1249.1951 | 453.1674 | 553.7646 | 585.9532 | 555.7996 | 531.1619 | 532.6414
4267.0354 | 1249.1963 | 452.9404 | 553.475 | 585.4714 | 554.9582 | 532.1034 | 533.7857
4268.0354 | 1249.1972 | 452.7918 | 553.0377 | 585.1611 | 555.1771 | 533.3366 | 533.7856
4269.0354 | 1249.1979 | 452.7749 | 552.6063 | 585.0907 | 555.14 | 533.752 | 532.8799
4270.0354 | 1249.1988 | 452.6695 | 552.5706 | 584.7272 | 554.5803 | 532.0936 | 532.0442
4271.0354 | 1249.2002 | 452.6645 | 552.232 | 584.4868 | 553.5065 | 531.0221 | 532.232
4272.0354 | 1249.2 | 452.642 | 552.152 | 584.2543 | 552.958 | 529.7433 | 532.0927
4273.0354 | 1249.2013 | 452.612 | 551.8233 | 584.2738 | 554.2422 | 528.9363 | 532.6274
4274.0354 | 1249.2012 | 452.5323 | 551.8973 | 585.0876 | 553.0609 | 527.1431 | 533.9193
4275.0354 | 1249.2026 | 452.4712 | 552.4143 | 585.1414 | 551.9675 | 526.4723 | 534.8233
4276.0354 | 1249.2029 | 452.3519 | 551.7741 | 584.3762 | 552.0519 | 526.3129 | 534.6227
4277.0354 | 1249.205 | 452.2163 | 551.8222 | 583.9628 | 551.8282 | 525.8813 | 533.176
4278.0354 | 1249.2053 | 452.0841 | 551.5397 | 583.6954 | 551.8837 | 526.2861 | 533.8602
4279.0354 | 1249.206 | 452.0844 | 551.3271 | 584.9783 | 551.5595 | 525.4359 | 533.912
4280.0354 | 1249.2063 | 451.9691 | 551.1081 | 583.5607 | 551.7904 | 525.5215 | 532.7898
4281.0354 | 1249.2066 | 452.0126 | 550.7741 | 583.2923 | 552.1612 | 525.7285 | 532.996
4282.0354 | 1249.2073 | 451.9236 | 550.7687 | 583.2837 | 551.7425 | 526.5411 | 534.5205
4283.0354 | 1249.2077 | 451.6233 | 550.4627 | 582.9868 | 551.7533 | 526.3996 | 534.8915
4284.0354 | 1249.2093 | 451.7051 | 550.6229 | 582.6109 | 551.1326 | 526.5777 | 534.7887
4285.0354 | 1249.2104 | 451.5796 | 550.6297 | 582.4825 | 551.1521 | 527.8627 | 535.026
4286.0354 | 1249.2103 | 451.6327 | 549.9388 | 582.019 | 551.8203 | 528.6913 | 533.6779
4287.0354 | 1249.2118 | 451.4894 | 549.7271 | 581.8601 | 551.8844 | 528.5671 | 533.0205
4288.0354 | 1249.2107 | 451.3551 | 549.8214 | 582.1983 | 551.4243 | 527.7929 | 533.2033
4289.0354 | 1249.2133 | 451.2259 | 549.631 | 581.8674 | 551.3956 | 527.7253 | 534.2715
4290.0354 | 1249.2131 | 451.2431 | 549.2883 | 581.7982 | 552.1474 | 526.8337 | 534.7964
4291.0354 | 1249.2148 | 451.1475 | 549.0696 | 581.6496 | 552.0326 | 526.6094 | 536.199
4292.0354 | 1249.2138 | 451.0843 | 548.8332 | 581.9527 | 551.4039 | 525.6926 | 538.3234
4293.0354 | 1249.2156 | 451.1159 | 548.939 | 581.5246 | 551.3063 | 525.7356 | 539.3804
4294.0354 | 1249.2169 | 451.0011 | 548.7132 | 581.1534 | 552.0177 | 526.0767 | 540.5931
4295.0354 | 1249.2175 | 450.9931 | 548.9867 | 582.2215 | 551.8443 | 525.2509 | 539.6837
4296.0354 | 1249.2175 | 450.8599 | 548.865 | 581.2827 | 551.7347 | 525.6059 | 540.2262
4297.0354 | 1249.2193 | 450.7286 | 548.4077 | 581.3344 | 551.1829 | 525.5837 | 540.5196
4298.0354 | 1249.2179 | 450.6196 | 548.5087 | 581.8117 | 551.1497 | 526.4196 | 539.7074
4299.0354 | 1249.2209 | 450.4189 | 548.0479 | 581.5953 | 551.7764 | 526.9614 | 538.7804
4300.0354 | 1249.2216 | 450.4153 | 548.8593 | 580.941 | 552.2696 | 526.8562 | 538.8939
4301.0354 | 1249.2211 | 450.3538 | 548.9277 | 580.8416 | 552.0088 | 526.9753 | 538.8165
4302.0354 | 1249.2226 | 450.2598 | 548.3026 | 581.9747 | 551.9056 | 527.7506 | 537.9944
4303.0354 | 1249.222 | 450.2347 | 547.9019 | 581.7925 | 552.9822 | 527.8169 | 537.5404
4304.0354 | 1249.2242 | 450.1958 | 547.5301 | 581.3376 | 553.2657 | 527.3065 | 536.0623
4305.0354 | 1249.225 | 450.2062 | 547.793 | 581.0307 | 553.5256 | 528.3027 | 535.3882
4306.0354 | 1249.2261 | 450.0277 | 547.302 | 581.0214 | 553.8392 | 529.0018 | 535.346
4307.0354 | 1249.2268 | 449.8487 | 547.8513 | 580.3509 | 553.37 | 528.3459 | 533.8784
4308.0354 | 1249.2272 | 449.8372 | 547.5698 | 580.0527 | 552.6549 | 528.62 | 532.3517
4309.0354 | 1249.2277 | 449.8241 | 547.1295 | 579.7228 | 552.4881 | 530.5166 | 532.3067
4310.0354 | 1249.228 | 449.8079 | 547.4429 | 579.645 | 551.8296 | 531.4754 | 530.9117
4311.0354 | 1249.2299 | 449.8239 | 546.8672 | 579.4928 | 551.1142 | 531.1719 | 529.4417
4312.0354 | 1249.2293 | 449.7549 | 546.8147 | 579.4887 | 550.0993 | 530.2642 | 526.6555
4313.0354 | 1249.2311 | 449.6217 | 546.7457 | 579.2599 | 549.3781 | 530.1514 | 524.7423
4314.0354 | 1249.2311 | 449.4654 | 546.2605 | 578.7314 | 549.3889 | 530.7272 | 521.9413
4315.0354 | 584.3947 | 449.4424 | 545.9737 | 578.7547 | 549.7698 | 532.144 | 522.9425
4316.0354 | 1249.2322 | 449.4284 | 545.8053 | 578.7621 | 550.2654 | 531.8735 | 518.2809
4317.0354 | 1249.2342 | 449.2684 | 545.8112 | 578.757 | 550.1526 | 530.0819 | 515.4335
4318.0354 | 1249.2342 | 449.2608 | 545.8716 | 577.9506 | 549.2177 | 528.9078 | 513.281
4319.0354 | 1249.2343 | 449.07 | 545.5383 | 577.8602 | 548.2754 | 529.3183 | 512.6046
4320.0354 | 1249.2353 | 449.1061 | 546.0542 | 578.0194 | 547.2796 | 528.7275 | 511.5016
4321.0354 | 1249.2361 | 449.1102 | 546.0536 | 578.0656 | 547.2622 | 529.291 | 510.0678
4322.0354 | 1249.237 | 449.0337 | 545.7048 | 578.903 | 548.144 | 530.1992 | 508.9211
4323.0354 | 1249.2381 | 449.0116 | 545.1315 | 579.6983 | 550.0535 | 530.4189 | 508.0212
4324.0354 | 1249.2377 | 448.98 | 545.0363 | 579.4333 | 550.5293 | 529.0016 | 507.2477
4325.0354 | 1249.2385 | 448.8596 | 546.058 | 578.8726 | 550.2879 | 527.604 | 506.5084
4326.0354 | 1249.2392 | 448.7978 | 546.6027 | 578.3221 | 549.8278 | 528.2844 | 507.2598
4327.0354 | 1249.2397 | 448.736 | 545.9377 | 578.7424 | 549.3377 | 528.3354 | 508.2983
4328.0354 | 1249.2407 | 448.6333 | 545.3343 | 578.9601 | 548.776 | 528.9157 | 507.9583
4329.0354 | 1249.2412 | 448.6445 | 545.4415 | 579.933 | 548.9914 | 528.6026 | 507.6216
4330.0354 | 1249.2418 | 448.5736 | 544.7619 | 579.6454 | 549.3017 | 529.0196 | 508.229
4331.0354 | 1249.2426 | 448.5409 | 544.5789 | 579.0221 | 550.0118 | 528.27 | 507.8828
4332.0354 | 1249.2436 | 448.4838 | 544.4099 | 578.5697 | 549.9131 | 527.1949 | 505.3307
4333.0354 | 1249.2443 | 448.4518 | 544.8682 | 578.2161 | 550.096 | 526.8059 | 504.9386
4334.0354 | 1030.4482 | 448.5675 | 545.0907 | 578.7354 | 549.6259 | 527.3882 | 505.1141
4335.0354 | 1249.2444 | 448.2421 | 544.5331 | 578.0906 | 550.7111 | 529.5017 | 504.9192
4336.0354 | 1249.2454 | 448.1657 | 544.3192 | 578.1672 | 551.0231 | 529.9305 | 505.9063
4337.0354 | 1249.2472 | 447.9991 | 544.1767 | 579.2699 | 551.5109 | 529.7184 | 504.0923
4338.0354 | 1249.2484 | 448.1009 | 544.6978 | 579.0373 | 552.288 | 528.9598 | 502.8994
4339.0354 | 1249.248 | 447.9874 | 544.2297 | 579.1436 | 552.6015 | 528.9003 | 504.3568
4340.0354 | 1249.2487 | 447.9395 | 544.8113 | 579.704 | 552.9981 | 529.4267 | 505.7542
4341.0354 | 1249.249 | 447.9634 | 544.9681 | 579.7527 | 553.4721 | 529.9271 | 507.3176
4342.0354 | 1249.2496 | 447.817 | 544.2782 | 581.9312 | 554.2722 | 530.9532 | 508.1082
4343.0354 | 1249.2511 | 447.8077 | 544.779 | 580.4555 | 555.0688 | 531.4827 | 508.2893
4344.0354 | 1249.2508 | 447.7365 | 545.4421 | 580.3482 | 555.0129 | 530.3939 | 507.3585
4345.0354 | 1249.2529 | 447.6307 | 545.39 | 580.4306 | 554.4564 | 529.1781 | 506.4568
4346.0354 | 1249.2532 | 447.5771 | 544.6983 | 580.7771 | 554.4678 | 530.0063 | 506.8025
4347.0354 | 1249.2537 | 447.5224 | 543.968 | 580.1712 | 554.5702 | 529.6674 | 506.7827
4348.0354 | 1249.2533 | 447.5069 | 543.7977 | 580.5604 | 555.0635 | 529.612 | 506.6727
4349.0354 | 1249.2562 | 447.393 | 543.9459 | 580.0029 | 555.2932 | 529.6597 | 506.0053
4350.0354 | 1249.2564 | 447.3527 | 543.7497 | 581.6381 | 555.0719 | 529.1181 | 505.8601
4351.0354 | 1249.2576 | 447.3217 | 543.8798 | 580.8928 | 555.3895 | 529.4013 | 505.613
4352.0354 | 1249.2578 | 447.223 | 543.4904 | 580.4226 | 555.269 | 530.6874 | 504.9567
4353.0354 | 1249.2578 | 447.217 | 543.2305 | 579.8184 | 555.3682 | 531.9206 | 504.6422
4354.0354 | 1249.258 | 447.1843 | 542.7962 | 579.784 | 555.6405 | 532.2669 | 504.2255
4355.0354 | 1249.2589 | 447.1316 | 542.9517 | 580.2392 | 555.4182 | 531.9871 | 503.4973
4356.0354 | 1249.2603 | 447.1064 | 543.3973 | 579.7002 | 554.6762 | 531.3669 | 502.7003
4357.0354 | 1249.2602 | 446.9236 | 543.8327 | 580.014 | 553.821 | 531.4301 | 502.7116
4358.0354 | 1249.2618 | 446.8343 | 543.0502 | 580.209 | 553.7848 | 531.6516 | 502.41
4359.0354 | 1249.2618 | 446.7824 | 543.2267 | 580.2907 | 553.9886 | 530.2693 | 501.2029
4360.0354 | 1249.2617 | 446.6885 | 542.9894 | 580.1531 | 553.6199 | 529.3179 | 500.2034
4361.0354 | 1249.2633 | 446.7347 | 543.6877 | 581.0414 | 552.7554 | 528.1147 | 499.4427
4362.0354 | 1249.2636 | 446.7388 | 544.3566 | 581.9291 | 552.9963 | 528.454 | 500.2453
4363.0354 | 1249.2643 | 446.7585 | 544.4966 | 582.731 | 554.33 | 529.604 | 501.8122
4364.0354 | 1249.2654 | 446.5888 | 544.3011 | 581.8216 | 554.3571 | 528.7143 | 501.9543
4365.0354 | 1249.2661 | 446.365 | 543.2298 | 581.6727 | 554.996 | 529.5871 | 501.3964
4366.0354 | 1249.2662 | 446.4342 | 542.6854 | 581.0989 | 554.8296 | 528.3214 | 500.5738
4367.0354 | 1249.2662 | 446.4114 | 542.5333 | 581.768 | 554.4014 | 527.2797 | 500.0679
4368.0354 | 1249.2673 | 446.3625 | 542.0823 | 580.9483 | 554.1033 | 527.5353 | 499.8692
4369.0354 | 1249.2684 | 446.3245 | 542.6218 | 580.5352 | 553.8896 | 528.8229 | 500.3138
4370.0354 | 1249.2699 | 446.2835 | 542.8111 | 580.4742 | 553.5163 | 529.6318 | 500.7374
4371.0354 | 1249.2692 | 446.2324 | 542.3431 | 580.3977 | 554.4635 | 530.524 | 501.7566
4372.0354 | 1249.2708 | 445.9692 | 542.3427 | 580.5198 | 554.0268 | 530.3884 | 501.9651
4373.0354 | 1249.2713 | 445.9638 | 541.9538 | 580.229 | 553.9952 | 530.4134 | 501.5855
4374.0354 | 1249.2712 | 445.9837 | 542.1828 | 580.8736 | 553.6885 | 529.1415 | 499.8132
4375.0354 | 1249.2729 | 445.9447 | 541.4828 | 579.9862 | 554.0449 | 528.4225 | 498.7162
4376.0354 | 1249.2733 | 445.8074 | 541.6836 | 579.5592 | 554.4473 | 529.0188 | 498.1253
4377.0354 | 1249.2738 | 445.6444 | 541.9727 | 579.7991 | 553.8826 | 528.262 | 497.4674
4378.0354 | 1249.2741 | 445.4979 | 541.4856 | 579.7467 | 553.8918 | 528.4082 | 497.3372
4379.0354 | 1249.2749 | 445.5138 | 541.919 | 579.4192 | 553.9293 | 527.3952 | 496.4052
4380.0354 | 1249.2752 | 445.5505 | 541.5053 | 579.6018 | 553.6099 | 527.7648 | 496.2142