## Test Conditions
DESIREE-FIRE Intermediate Scale Test 1 - Circuit Simulator Data Only
Test Date: | 2010-02-23
DCSim DAQ Start Time | 12:09
DCSim Time for Synchronization | 13:03
Heat Source Synchronization | 0:02 | hour:minutes:seconds
Heat Source DAQ Start Time | 13:01
Fire Time | 13:56
Offset | 1:47 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 6420 | seconds
Heat Source Offset | 0:55 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 3299 | seconds
Heat Source Stop Time | 15:09
Test Duration | 1:13 | hour:minutes:seconds
| 4380 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 2, 3, and 4 represents the conduit temperature 3', 5', and 7' down the conduit located in B Position. These are labeled as "B Position - Conduit - 3'", "B Position - Conduit - Middle", " B Position - Conduit - 7'", respectively.
SOV 2 | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 8, 9, and 10 represents the air temperature 3', 5', and 7' down the tray located in D Position. These are labeled as "D Position - 3'", "D Position - Middle", "D Position - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-1.2188 | 123.3078 | -61.6653 | 61.4685 | 1.4211e-13 | -0.0046859 | -0.011218 | 0.039384 | -0.021439 | 0.04908 | 0.0036627 | -0.011507 | 0.02969 | 0.044798 | -0.0016475 | 0.047647 | -61.5187 | -0.026065 | -61.6229 | 61.517 | 61.3167 | 61.4495 | -61.6587 | -61.5826 | 0.004938 | -61.6492 | 61.3722 | 61.5181 | 61.4114 | -61.8408 | 0.006594 | 0.048479 | 0.14659 | 0.042435 | 0.035841 | -0.15177 | -0.019052 | -0.17547 | -0.096261 | 0.082744 | 0.016188 | 0.19166 | 0.049568 | -0.057117 | 123.1823 | 122.9821 | 123.1148 | 61.6393 | -123.1273 | 123.0376 | 123.1834 | 123.0767 | 61.6703 | -123.3093
0.53125 | 123.2941 | -61.6425 | 61.5738 | 1.4211e-13 | -0.0042585 | -0.011004 | 0.039598 | -0.021012 | 0.04908 | 0.011293 | -0.01172 | 0.029476 | 0.044798 | -0.0020749 | 0.047433 | -61.5142 | -0.016908 | -61.6275 | 61.5124 | 61.3167 | 61.4311 | -61.6679 | -61.5826 | 0.000359 | -61.64 | 61.3631 | 61.5043 | 61.3473 | -61.8408 | -0.025452 | -0.061386 | 0.12828 | 0.014969 | 0.040421 | -0.25705 | -0.14265 | -0.19836 | -0.2107 | 0.059856 | 0.002457 | 0.20082 | -0.069454 | -0.2265 | 123.1549 | 122.9592 | 123.0736 | 61.6255 | -123.2417 | 123.0055 | 123.1468 | 122.9897 | 61.6428 | -123.4146
2.2188 | 123.3902 | -61.647 | 61.4868 | 1.4211e-13 | -0.0044721 | -0.011004 | 0.040025 | -0.021012 | 0.049294 | 0.011293 | -0.011507 | 0.029904 | 0.045011 | -0.0018611 | 0.047433 | -61.5187 | -0.016908 | -61.6275 | 61.5124 | 61.3122 | 61.4403 | -61.6633 | -61.578 | -0.008798 | -61.6263 | 61.3722 | 61.5089 | 61.3977 | -61.85 | -0.016295 | 0.02559 | 0.12828 | 0.019547 | 0.035842 | -0.17466 | -0.04652 | -0.20294 | -0.11457 | 0.069013 | 0.020771 | 0.22371 | 0.022101 | -0.089163 | 123.1594 | 122.9592 | 123.0873 | 61.6301 | -123.1501 | 123.0193 | 123.156 | 123.0447 | 61.6382 | -123.3368
3.9844 | 123.3444 | -61.6425 | 61.5143 | 1.4211e-13 | -0.0044721 | -0.011004 | 0.039598 | -0.021439 | 0.04908 | -0.0039678 | -0.011293 | 0.029263 | 0.045011 | -0.0012201 | 0.047433 | -61.5187 | -0.016908 | -61.6275 | 61.5124 | 61.3213 | 61.4403 | -61.6679 | -61.5826 | 0.000359 | -61.6354 | 61.3631 | 61.5043 | 61.3702 | -61.8362 | -0.025452 | -0.001876 | 0.12371 | 0.014969 | 0.040421 | -0.19297 | -0.073986 | -0.19378 | -0.15119 | 0.059856 | 0.007036 | 0.20082 | -0.009944 | -0.1441 | 123.1549 | 122.9638 | 123.0828 | 61.6255 | -123.1822 | 123.0055 | 123.1468 | 123.0126 | 61.6428 | -123.3505
5.6562 | 123.2941 | -61.615 | 61.5829 | 1.4211e-13 | -0.0046859 | -0.011004 | 0.039811 | -0.021866 | 0.049294 | -0.011598 | -0.011507 | 0.029476 | 0.044798 | -0.0016475 | 0.047433 | -61.5096 | -0.021486 | -61.6229 | 61.5124 | 61.3122 | 61.4357 | -61.6587 | -61.578 | 0.000359 | -61.64 | 61.3539 | 61.4906 | 61.3519 | -61.8408 | -0.04376 | -0.070541 | 0.1054 | -0.007919 | 0.035841 | -0.27079 | -0.14723 | -0.22583 | -0.22902 | 0.036969 | -0.025009 | 0.20082 | -0.092344 | -0.23108 | 123.1274 | 122.9271 | 123.0507 | 61.5935 | -123.2417 | 122.9689 | 123.1056 | 122.9669 | 61.6153 | -123.4238
7.4062 | 123.4085 | -61.5967 | 61.5234 | 1.4211e-13 | -0.0042585 | -0.011218 | 0.039598 | -0.021225 | 0.049508 | 0.0036627 | -0.011507 | 0.02969 | 0.045011 | -0.0016475 | 0.047433 | -61.5142 | -0.021486 | -61.6183 | 61.5124 | 61.3076 | 61.4357 | -61.6587 | -61.578 | -0.00422 | -61.6308 | 61.3585 | 61.5135 | 61.3519 | -61.8408 | -0.06207 | -0.011031 | 0.082508 | -0.021651 | 0.040419 | -0.21586 | -0.087719 | -0.24414 | -0.16493 | 0.018659 | -0.034161 | 0.20998 | -0.009941 | -0.17157 | 123.1091 | 122.9043 | 123.0324 | 61.5752 | -123.1822 | 122.9552 | 123.1102 | 122.9485 | 61.5925 | -123.3643
9.1562 | 123.3444 | -61.6516 | 61.496 | 1.4211e-13 | -0.0042585 | -0.011004 | 0.040239 | -0.021012 | 0.048867 | 0.0036627 | -0.01172 | 0.02969 | 0.045225 | -0.0014337 | 0.047647 | -61.5142 | -0.026065 | -61.6183 | 61.5124 | 61.303 | 61.4357 | -61.645 | -61.5689 | -0.00422 | -61.6354 | 61.3631 | 61.4998 | 61.274 | -61.8317 | 0.006598 | 0.016434 | 0.13744 | 0.03328 | 0.026682 | -0.19297 | -0.060254 | -0.18005 | -0.13288 | 0.082747 | 0.016191 | 0.19624 | 0.003788 | -0.22194 | 123.164 | 122.9546 | 123.0873 | 61.6255 | -123.141 | 123.0147 | 123.1514 | 122.9256 | 61.6474 | -123.3276
10.9062 | 123.2574 | -61.6745 | 61.5234 | 1.4211e-13 | -0.0044721 | -0.011218 | 0.039811 | -0.021225 | 0.049508 | 0.0036627 | -0.012148 | 0.029904 | 0.045011 | -0.0014337 | 0.047647 | -61.5096 | -0.021486 | -61.6229 | 61.5124 | 61.303 | 61.4403 | -61.6542 | -61.5734 | 0.004938 | -61.6308 | 61.3539 | 61.4998 | 61.2923 | -61.8408 | 0.020329 | -0.011031 | 0.16491 | 0.051591 | 0.031262 | -0.22044 | -0.083141 | -0.16632 | -0.16951 | 0.10106 | 0.043659 | 0.20998 | -0.023677 | -0.23109 | 123.1869 | 122.9775 | 123.1148 | 61.653 | -123.1776 | 123.0284 | 123.1743 | 122.9668 | 61.6794 | -123.3643
12.6094 | 123.3536 | -61.6287 | 61.4914 | 1.4211e-13 | -0.0044721 | -0.011004 | 0.040025 | -0.021439 | 0.049294 | -0.0039678 | -0.011507 | 0.02969 | 0.044798 | -0.0014337 | 0.04786 | -61.5096 | -0.026065 | -61.6138 | 61.5033 | 61.2984 | 61.4357 | -61.6542 | -61.578 | -0.008798 | -61.6308 | 61.3539 | 61.4998 | 61.2878 | -61.8317 | -0.025448 | 0.011856 | 0.11913 | 0.014971 | 0.040419 | -0.19297 | -0.055676 | -0.20294 | -0.13746 | 0.050702 | -0.002118 | 0.20082 | 0.008366 | -0.20363 | 123.132 | 122.9271 | 123.0644 | 61.6027 | -123.1456 | 122.9827 | 123.1285 | 122.9165 | 61.6199 | -123.3231
14.3438 | 123.3032 | -61.6379 | 61.5005 | 1.4211e-13 | -0.0044721 | -0.011004 | 0.039811 | -0.021225 | 0.048867 | 0.0036627 | -0.01172 | 0.02969 | 0.045225 | -0.0016475 | 0.047647 | -61.5142 | -0.021486 | -61.6092 | 61.5078 | 61.3122 | 61.4357 | -61.6587 | -61.5689 | 0.009516 | -61.6308 | 61.3539 | 61.5043 | 61.3427 | -61.8362 | -0.020872 | 0.007279 | 0.12371 | 0.028704 | 0.049576 | -0.18839 | -0.064831 | -0.19836 | -0.14662 | 0.069014 | 0.007037 | 0.2054 | 0.003789 | -0.15784 | 123.1457 | 122.95 | 123.0736 | 61.6164 | -123.1593 | 122.9918 | 123.1422 | 122.9806 | 61.6474 | -123.3368
16.0469 | 123.3582 | -61.6196 | 61.5097 | 1.4211e-13 | -0.0042585 | -0.011004 | 0.040025 | -0.021439 | 0.04908 | -0.0039678 | -0.011934 | 0.029476 | 0.045011 | -0.0012201 | 0.04786 | -61.5096 | -0.016908 | -61.6183 | 61.5033 | 61.303 | 61.4403 | -61.6496 | -61.5689 | 0.000359 | -61.6354 | 61.3539 | 61.5043 | 61.2832 | -61.8317 | -0.030024 | -0.006455 | 0.10997 | 0.001237 | 0.031261 | -0.2067 | -0.069409 | -0.21209 | -0.15577 | 0.050704 | -0.015852 | 0.19624 | -0.005367 | -0.22652 | 123.1228 | 122.9226 | 123.0599 | 61.6027 | -123.1593 | 122.9735 | 123.1239 | 122.9028 | 61.6199 | -123.3414
17.8125 | 123.3124 | -61.6791 | 61.4594 | 1.4211e-13 | -0.0042585 | -0.011004 | 0.039811 | -0.021012 | 0.04908 | -0.0039678 | -0.01172 | 0.029476 | 0.044798 | -0.0014337 | 0.047647 | -61.5142 | -0.021486 | -61.6138 | 61.5033 | 61.3076 | 61.4449 | -61.6496 | -61.5734 | 0.004938 | -61.6217 | 61.3539 | 61.5043 | 61.3015 | -61.8362 | 0.029485 | 0.043899 | 0.1649 | 0.065325 | 0.03584 | -0.15177 | -0.014476 | -0.15716 | -0.10542 | 0.10563 | 0.057393 | 0.21455 | 0.044987 | -0.15785 | 123.1823 | 122.9867 | 123.124 | 61.6576 | -123.1089 | 123.033 | 123.1834 | 122.9806 | 61.684 | -123.2956
19.5781 | 123.3536 | -61.6516 | 61.441 | 1.4211e-13 | -0.0040449 | -0.011218 | 0.039811 | -0.021225 | 0.04908 | -0.0039678 | -0.011934 | 0.029904 | 0.044798 | -0.0016475 | 0.047219 | -61.5004 | -0.030644 | -61.6092 | 61.4987 | 61.2984 | 61.4311 | -61.6587 | -61.5689 | 0.004938 | -61.6217 | 61.3539 | 61.4952 | 61.3473 | -61.8362 | -0.007139 | 0.057631 | 0.15117 | 0.042437 | 0.049576 | -0.14262 | -0.009901 | -0.18463 | -0.087109 | 0.082747 | 0.029927 | 0.21455 | 0.054141 | -0.093751 | 123.1503 | 122.95 | 123.0828 | 61.621 | -123.0998 | 123.0055 | 123.1468 | 122.9989 | 61.6565 | -123.2773
21.3281 | 123.3353 | -61.5738 | 61.528 | 1.4211e-13 | -0.0044721 | -0.011004 | 0.039811 | -0.021225 | 0.04908 | -0.0039678 | -0.01172 | 0.02969 | 0.045011 | -0.0014337 | 0.047647 | -61.5004 | -0.026065 | -61.6046 | 61.5033 | 61.3076 | 61.4357 | -61.6496 | -61.5689 | -0.00422 | -61.6263 | 61.3494 | 61.5043 | 61.3107 | -61.8317 | -0.0758 | -0.024765 | 0.073355 | -0.030804 | 0.044996 | -0.22044 | -0.092297 | -0.25787 | -0.17866 | 0.004928 | -0.052471 | 0.2054 | -0.023677 | -0.21736 | 123.077 | 122.8814 | 123.0095 | 61.5477 | -123.1776 | 122.9231 | 123.0781 | 122.8845 | 61.5696 | -123.3597
23.0938 | 123.3765 | -61.6241 | 61.4456 | 1.4211e-13 | -0.0042585 | -0.011004 | 0.039811 | -0.021225 | 0.048867 | 0.011293 | -0.011507 | 0.02969 | 0.044798 | -0.0016475 | 0.04786 | -61.505 | -0.021486 | -61.6046 | 61.4941 | 61.303 | 61.4357 | -61.6496 | -61.5597 | 0.000359 | -61.6263 | 61.3494 | 61.4906 | 61.3061 | -61.8317 | -0.025446 | 0.048475 | 0.11913 | 0.01955 | 0.044996 | -0.14262 | -0.0099 | -0.20751 | -0.096266 | 0.06444 | -0.002117 | 0.2054 | 0.044985 | -0.13954 | 123.1182 | 122.9271 | 123.0599 | 61.6027 | -123.0952 | 122.9735 | 123.1147 | 122.9302 | 61.6245 | -123.2773
24.8438 | 123.2849 | -61.5967 | 61.5417 | 1.4211e-13 | -0.0040449 | -0.011004 | 0.039598 | -0.021225 | 0.049294 | 0.011293 | -0.011507 | 0.029476 | 0.045011 | -0.0012201 | 0.047647 | -61.505 | -0.026065 | -61.6046 | 61.5033 | 61.2984 | 61.4311 | -61.645 | -61.5689 | -0.00422 | -61.6217 | 61.3539 | 61.4952 | 61.2969 | -61.8317 | -0.048333 | -0.038498 | 0.091665 | -0.007916 | 0.040417 | -0.24333 | -0.11061 | -0.23498 | -0.18782 | 0.027816 | -0.025004 | 0.20998 | -0.046567 | -0.24482 | 123.0999 | 122.8951 | 123.0278 | 61.5706 | -123.1868 | 122.9506 | 123.0919 | 122.8936 | 61.5925 | -123.3734
26.5312 | 123.317 | -61.6013 | 61.496 | 1.4211e-13 | -0.0042585 | -0.011004 | 0.039811 | -0.021225 | 0.048867 | -0.0039678 | -0.011507 | 0.029476 | 0.045225 | -0.0012201 | 0.04786 | -61.5004 | -0.021486 | -61.6138 | 61.4941 | 61.2938 | 61.422 | -61.6496 | -61.5551 | -0.00422 | -61.6217 | 61.3402 | 61.4952 | 61.2969 | -61.8317 | -0.048335 | -0.001879 | 0.10082 | -0.012495 | 0.03584 | -0.20213 | -0.07399 | -0.2304 | -0.15578 | 0.046129 | -0.020427 | 0.20998 | -0.000791 | -0.19905 | 123.0953 | 122.8951 | 123.0232 | 61.5798 | -123.1456 | 122.9415 | 123.0964 | 122.8982 | 61.597 | -123.3276
28.2969 | 123.317 | -61.6287 | 61.4868 | 1.4211e-13 | -0.0042585 | -0.011004 | 0.040025 | -0.020798 | 0.048653 | -0.0039678 | -0.011507 | 0.029904 | 0.045011 | -0.0018611 | 0.04786 | -61.5004 | -0.021486 | -61.6138 | 61.4987 | 61.3076 | 61.4357 | -61.6404 | -61.5643 | -0.00422 | -61.6171 | 61.3494 | 61.4998 | 61.2878 | -61.8317 | -0.011712 | 0.011855 | 0.12829 | 0.014971 | 0.026683 | -0.17924 | -0.051098 | -0.20294 | -0.13746 | 0.064438 | 0.011618 | 0.21455 | 0.012944 | -0.19905 | 123.1274 | 122.9363 | 123.0644 | 61.6072 | -123.1273 | 122.9781 | 123.1285 | 122.9165 | 61.6245 | -123.3185
30.0625 | 123.2574 | -61.6653 | 61.5005 | 1.4211e-13 | -0.0042585 | -0.011004 | 0.039811 | -0.021225 | 0.049294 | 0.011293 | -0.01172 | 0.02969 | 0.044798 | -0.0014337 | 0.047647 | -61.5004 | -0.021486 | -61.6092 | 61.5078 | 61.2984 | 61.4266 | -61.645 | -61.5734 | 0.000359 | -61.6217 | 61.3448 | 61.4998 | 61.2786 | -61.8225 | 0.020331 | 0.007279 | 0.16491 | 0.05617 | 0.035839 | -0.20213 | -0.073988 | -0.15716 | -0.15577 | 0.091901 | 0.04366 | 0.20082 | -0.000789 | -0.22194 | 123.1732 | 122.9638 | 123.0919 | 61.6439 | -123.1456 | 123.0101 | 123.1651 | 122.944 | 61.6657 | -123.323
31.75 | 123.3856 | -61.6241 | 61.4273 | 1.4211e-13 | -0.0040449 | -0.011218 | 0.040025 | -0.021012 | 0.048653 | 0.0036627 | -0.01172 | 0.02969 | 0.045225 | -0.0014337 | 0.04786 | -61.5004 | -0.026065 | -61.6046 | 61.4849 | 61.2984 | 61.4357 | -61.6359 | -61.5551 | 0.000359 | -61.6171 | 61.3448 | 61.4906 | 61.3519 | -61.8271 | -0.01171 | 0.057629 | 0.12371 | 0.01955 | 0.03126 | -0.12888 | 0.008411 | -0.20293 | -0.082533 | 0.069018 | 0.007041 | 0.20998 | 0.063296 | -0.07544 | 123.1091 | 122.9226 | 123.0599 | 61.5981 | -123.0632 | 122.9689 | 123.1147 | 122.976 | 61.6245 | -123.2544
33.5156 | 123.2986 | -61.6196 | 61.4731 | 1.4211e-13 | -0.0040449 | -0.011218 | 0.039811 | -0.021439 | 0.04908 | -0.0039678 | -0.011507 | 0.02969 | 0.045225 | -0.0012201 | 0.047433 | -61.4959 | -0.021486 | -61.6092 | 61.4941 | 61.2984 | 61.422 | -61.6313 | -61.5597 | -0.00422 | -61.6171 | 61.3448 | 61.4998 | 61.3198 | -61.8317 | -0.011709 | 0.02101 | 0.12371 | 0.010394 | 0.022103 | -0.17466 | -0.051101 | -0.21209 | -0.12831 | 0.059862 | 0.002463 | 0.21455 | 0.026677 | -0.15327 | 123.1137 | 122.918 | 123.0416 | 61.5981 | -123.1044 | 122.9643 | 123.1193 | 122.9394 | 61.6153 | -123.3047
35.2188 | 123.23 | -61.6974 | 61.4868 | 1.4211e-13 | -0.0040449 | -0.011004 | 0.039811 | -0.021225 | 0.04908 | 0.0036627 | -0.011934 | 0.029476 | 0.045011 | -0.0012201 | 0.047647 | -61.4959 | -0.016908 | -61.6 | 61.4941 | 61.303 | 61.4311 | -61.645 | -61.5551 | 0.004938 | -61.6079 | 61.3448 | 61.4998 | 61.2923 | -61.8317 | 0.052375 | 0.007277 | 0.20153 | 0.097371 | 0.044996 | -0.18381 | -0.055677 | -0.13427 | -0.14204 | 0.14226 | 0.08944 | 0.22371 | 0.012944 | -0.19447 | 123.1915 | 123.0004 | 123.1285 | 61.6805 | -123.1318 | 123.0422 | 123.1971 | 122.9897 | 61.7023 | -123.3185
36.9844 | 123.3215 | -61.6241 | 61.4502 | 1.4211e-13 | -0.0042585 | -0.010791 | 0.040025 | -0.021653 | 0.04908 | -0.0039678 | -0.012148 | 0.029476 | 0.045011 | -0.0010065 | 0.047647 | -61.4959 | -0.016908 | -61.6 | 61.4895 | 61.2893 | 61.422 | -61.6404 | -61.5551 | -0.00422 | -61.6217 | 61.3402 | 61.486 | 61.3336 | -61.8317 | -0.016289 | 0.039319 | 0.12829 | 0.024129 | 0.040418 | -0.16093 | -0.028213 | -0.20751 | -0.11 | 0.069018 | 0.002462 | 0.20998 | 0.035829 | -0.11664 | 123.1137 | 122.9134 | 123.0461 | 61.6072 | -123.0906 | 122.9643 | 123.1102 | 122.9577 | 61.6199 | -123.2819
38.7344 | 123.3398 | -61.6379 | 61.4182 | 1.4211e-13 | -0.0038311 | -0.011218 | 0.039811 | -0.021439 | 0.04908 | 0.0036627 | -0.01172 | 0.029476 | 0.044798 | -0.0014337 | 0.047647 | -61.4959 | -0.016908 | -61.6046 | 61.4941 | 61.2938 | 61.4311 | -61.6404 | -61.5551 | -0.00422 | -61.6171 | 61.3402 | 61.486 | 61.3519 | -61.8133 | -0.002557 | 0.075941 | 0.14202 | 0.033282 | 0.035839 | -0.12431 | 0.012987 | -0.17547 | -0.077957 | 0.08275 | 0.020773 | 0.19624 | 0.067872 | -0.066285 | 123.132 | 122.9317 | 123.069 | 61.621 | -123.0586 | 122.9781 | 123.1239 | 122.9897 | 61.6337 | -123.2315
40.4219 | 123.3307 | -61.6196 | 61.4227 | 1.4211e-13 | -0.0042585 | -0.010791 | 0.039811 | -0.021439 | 0.04908 | 0.0036627 | -0.01172 | 0.02969 | 0.044584 | -0.0014337 | 0.04786 | -61.4959 | -0.016908 | -61.6046 | 61.4849 | 61.2893 | 61.4311 | -61.6359 | -61.5505 | 0.004938 | -61.6171 | 61.3448 | 61.4952 | 61.3061 | -61.8225 | -0.016288 | 0.062207 | 0.12371 | 0.014972 | 0.03126 | -0.13346 | 0.00841 | -0.20293 | -0.077955 | 0.069019 | 0.002463 | 0.2054 | 0.072452 | -0.11665 | 123.1045 | 122.9088 | 123.0507 | 61.6027 | -123.0586 | 122.9643 | 123.1147 | 122.9256 | 61.6245 | -123.2452
42.1875 | 123.3398 | -61.6287 | 61.4731 | 1.4211e-13 | -0.0036175 | -0.011004 | 0.039811 | -0.021439 | 0.048867 | 0.011293 | -0.011507 | 0.029904 | 0.044798 | -0.0014337 | 0.047647 | -61.4959 | -0.021486 | -61.6 | 61.4895 | 61.2893 | 61.4266 | -61.6404 | -61.5551 | -0.008798 | -61.6217 | 61.3448 | 61.4906 | 61.3473 | -61.8225 | -0.011712 | 0.016431 | 0.13287 | 0.028706 | 0.040418 | -0.18382 | -0.046522 | -0.19378 | -0.12831 | 0.073595 | 0.007039 | 0.20082 | 0.01752 | -0.12579 | 123.1182 | 122.918 | 123.0553 | 61.6072 | -123.1135 | 122.9735 | 123.1193 | 122.976 | 61.6199 | -123.2956
43.9531 | 123.3032 | -61.6196 | 61.4685 | 1.4211e-13 | -0.0038311 | -0.011004 | 0.040025 | -0.021225 | 0.04908 | -0.0039678 | -0.011507 | 0.02969 | 0.044584 | -0.0012201 | 0.047647 | -61.4959 | -0.021486 | -61.5954 | 61.4895 | 61.2893 | 61.4311 | -61.6404 | -61.5505 | -0.008798 | -61.6079 | 61.3448 | 61.486 | 61.2923 | -61.8179 | -0.020867 | 0.021008 | 0.12371 | 0.024129 | 0.044996 | -0.17924 | -0.037367 | -0.19835 | -0.12373 | 0.069019 | 0.01162 | 0.20997 | 0.017518 | -0.17616 | 123.1091 | 122.9088 | 123.0507 | 61.5981 | -123.1089 | 122.9643 | 123.1056 | 122.9119 | 61.6108 | -123.2864
45.7031 | 123.23 | -61.615 | 61.5326 | 1.4211e-13 | -0.0040449 | -0.011004 | 0.040025 | -0.021653 | 0.048867 | 0.0036627 | -0.01172 | 0.029049 | 0.044584 | -0.0016475 | 0.047219 | -61.4913 | -0.021486 | -61.6 | 61.4849 | 61.2893 | 61.422 | -61.6313 | -61.5505 | -0.00422 | -61.6125 | 61.3448 | 61.4814 | 61.3244 | -61.8225 | -0.016287 | -0.047657 | 0.12371 | 0.014973 | 0.03126 | -0.24333 | -0.11061 | -0.20751 | -0.18782 | 0.064441 | 0.002464 | 0.20998 | -0.051148 | -0.2082 | 123.0999 | 122.9043 | 123.037 | 61.5935 | -123.1639 | 122.9598 | 123.0964 | 122.9394 | 61.6108 | -123.3551
47.4062 | 123.2666 | -61.6196 | 61.5143 | 1.4211e-13 | -0.0044721 | -0.010791 | 0.039811 | -0.021439 | 0.04908 | 0.011293 | -0.011934 | 0.02969 | 0.044798 | -0.0010065 | 0.047219 | -61.4913 | -0.021486 | -61.6 | 61.4849 | 61.2938 | 61.4266 | -61.6313 | -61.5597 | 0.000359 | -61.6125 | 61.3356 | 61.4814 | 61.274 | -61.8271 | -0.011709 | -0.029346 | 0.12829 | 0.019551 | 0.03126 | -0.22044 | -0.087721 | -0.20751 | -0.17867 | 0.059862 | 0.007042 | 0.21455 | -0.032837 | -0.24025 | 123.1045 | 122.9134 | 123.0461 | 61.5981 | -123.1456 | 122.9552 | 123.101 | 122.8936 | 61.6199 | -123.3414
49.1719 | 123.3398 | -61.5967 | 61.4822 | 1.4211e-13 | -0.0040449 | -0.010577 | 0.040025 | -0.021439 | 0.04908 | 0.0036627 | -0.01172 | 0.029263 | 0.044798 | -0.0012201 | 0.047433 | -61.4913 | -0.016908 | -61.6046 | 61.4849 | 61.2847 | 61.4311 | -61.6267 | -61.5505 | 0.000359 | -61.6125 | 61.3356 | 61.4814 | 61.3381 | -61.8225 | -0.030018 | 0.002697 | 0.1054 | -0.007916 | 0.022102 | -0.19755 | -0.0511 | -0.22582 | -0.14662 | 0.046131 | -0.015846 | 0.20998 | -0.000794 | -0.14411 | 123.0816 | 122.8814 | 123.0278 | 61.5798 | -123.1089 | 122.9323 | 123.0781 | 122.9348 | 61.597 | -123.3047
50.9219 | 123.23 | -61.5921 | 61.5784 | 1.4211e-13 | -0.0042585 | -0.011004 | 0.039598 | -0.021439 | 0.04908 | 0.011293 | -0.01172 | 0.029476 | 0.044798 | -0.0014337 | 0.04786 | -61.4867 | -0.021486 | -61.5954 | 61.4804 | 61.2893 | 61.4174 | -61.6313 | -61.5505 | -0.00422 | -61.6079 | 61.3265 | 61.4814 | 61.3473 | -61.8179 | -0.039175 | -0.098011 | 0.1054 | -0.003337 | 0.035838 | -0.2891 | -0.16097 | -0.22582 | -0.25191 | 0.041553 | -0.015846 | 0.20997 | -0.096924 | -0.23108 | 123.0725 | 122.8814 | 123.0095 | 61.5706 | -123.2096 | 122.9186 | 123.0735 | 122.9394 | 61.5879 | -123.3963
52.625 | 123.2849 | -61.5921 | 61.5051 | 1.4211e-13 | -0.0040449 | -0.010577 | 0.039598 | -0.021439 | 0.049294 | 0.0036627 | -0.011934 | 0.029476 | 0.044798 | -0.0018611 | 0.047647 | -61.4821 | -0.021486 | -61.5909 | 61.4849 | 61.2893 | 61.422 | -61.6267 | -61.5505 | -0.00422 | -61.5988 | 61.331 | 61.4769 | 61.3015 | -61.8179 | -0.034596 | -0.020191 | 0.10998 | 0.001241 | 0.035837 | -0.21586 | -0.083145 | -0.22582 | -0.17409 | 0.041553 | -0.006688 | 0.21913 | -0.02826 | -0.20362 | 123.077 | 122.8814 | 123.0141 | 61.5706 | -123.1318 | 122.9231 | 123.069 | 122.8936 | 61.5879 | -123.323
54.375 | 123.3032 | -61.5967 | 61.4639 | 1.4211e-13 | -0.0042585 | -0.010791 | 0.039811 | -0.021225 | 0.049294 | 0.0036627 | -0.01172 | 0.029476 | 0.044798 | -0.0014337 | 0.047433 | -61.4821 | -0.016908 | -61.5909 | 61.4849 | 61.2847 | 61.422 | -61.6313 | -61.5414 | 0.004938 | -61.6034 | 61.331 | 61.4814 | 61.329 | -61.8225 | -0.034597 | 0.021008 | 0.11456 | 0.005819 | 0.040416 | -0.17924 | -0.041946 | -0.22582 | -0.13289 | 0.055288 | -0.006689 | 0.21913 | 0.017517 | -0.13495 | 123.0816 | 122.8814 | 123.0187 | 61.5798 | -123.0952 | 122.9277 | 123.0781 | 122.9257 | 61.6016 | -123.2864
56.125 | 123.349 | -61.5555 | 61.5097 | 1.4211e-13 | -0.0042585 | -0.011218 | 0.039811 | -0.021439 | 0.048867 | 0.011293 | -0.011934 | 0.029476 | 0.044798 | -0.0012201 | 0.047647 | -61.4867 | -0.026065 | -61.5954 | 61.4804 | 61.2755 | 61.4174 | -61.6267 | -61.5551 | 0.004938 | -61.6079 | 61.331 | 61.4814 | 61.2511 | -61.8225 | -0.071217 | -0.029347 | 0.06878 | -0.039958 | 0.031259 | -0.23418 | -0.092302 | -0.26702 | -0.17867 | 0.000353 | -0.052467 | 0.21455 | -0.02826 | -0.25857 | 123.0358 | 122.831 | 122.9729 | 61.5294 | -123.1364 | 122.8865 | 123.0369 | 122.8066 | 61.5604 | -123.3322
57.8906 | 123.1888 | -61.6562 | 61.4868 | 1.4211e-13 | -0.0040449 | -0.011218 | 0.039811 | -0.021439 | 0.048867 | 0.0036627 | -0.011934 | 0.029263 | 0.045011 | -0.0012201 | 0.047647 | -61.4821 | -0.021486 | -61.5954 | 61.4849 | 61.2847 | 61.4128 | -61.6267 | -61.546 | 0.000359 | -61.5988 | 61.3356 | 61.4723 | 61.2923 | -61.8133 | 0.029491 | -0.00188 | 0.17407 | 0.06075 | 0.031259 | -0.20213 | -0.073991 | -0.15715 | -0.1512 | 0.11022 | 0.057399 | 0.21455 | -0.014528 | -0.19447 | 123.1411 | 122.9409 | 123.069 | 61.6347 | -123.1135 | 122.9918 | 123.1285 | 122.9485 | 61.6565 | -123.3002
59.5781 | 123.3398 | -61.5784 | 61.4639 | 1.4211e-13 | -0.0042585 | -0.010791 | 0.040239 | -0.021439 | 0.049294 | 0.0036627 | -0.011934 | 0.029476 | 0.045011 | -0.0014337 | 0.047219 | -61.4821 | -0.021486 | -61.5863 | 61.4804 | 61.2755 | 61.422 | -61.6221 | -61.5414 | 0.000359 | -61.6079 | 61.3265 | 61.4769 | 61.329 | -61.8179 | -0.04375 | 0.01643 | 0.096246 | -0.007914 | 0.035836 | -0.1884 | -0.041946 | -0.23955 | -0.13747 | 0.036977 | -0.029579 | 0.20997 | 0.012939 | -0.13495 | 123.0587 | 122.8539 | 123.0004 | 61.5569 | -123.086 | 122.9048 | 123.0552 | 122.9073 | 61.5787 | -123.2819
61.3281 | 123.2025 | -61.6562 | 61.4594 | 1.4211e-13 | -0.0038311 | -0.011004 | 0.040239 | -0.021225 | 0.04908 | 0.011293 | -0.01172 | 0.029904 | 0.044798 | -0.0014337 | 0.04786 | -61.4867 | -0.016908 | -61.5909 | 61.4849 | 61.2847 | 61.422 | -61.6313 | -61.5414 | 0.000359 | -61.5942 | 61.331 | 61.4723 | 61.3244 | -61.8133 | 0.024912 | 0.025585 | 0.16949 | 0.065328 | 0.040416 | -0.17467 | -0.037369 | -0.15715 | -0.12831 | 0.1148 | 0.061977 | 0.21913 | 0.012937 | -0.13495 | 123.1411 | 122.9409 | 123.0782 | 61.6393 | -123.0906 | 122.9872 | 123.1285 | 122.9806 | 61.6565 | -123.2727
63.1094 | 123.3444 | -61.5417 | 61.5051 | 1.4211e-13 | -0.0040449 | -0.011004 | 0.039598 | -0.021225 | 0.048867 | 0.0036627 | -0.011934 | 0.029904 | 0.045011 | -0.0012201 | 0.047647 | -61.4775 | -0.026065 | -61.5863 | 61.4712 | 61.2801 | 61.4174 | -61.613 | -61.5368 | 0.000359 | -61.5988 | 61.3265 | 61.4769 | 61.3244 | -61.8225 | -0.071213 | -0.033926 | 0.064203 | -0.044535 | 0.026678 | -0.22502 | -0.087724 | -0.28075 | -0.17867 | 0.004935 | -0.057042 | 0.22371 | -0.02826 | -0.18073 | 123.0129 | 122.8219 | 122.9592 | 61.5157 | -123.1181 | 122.8682 | 123.0186 | 122.8661 | 61.5421 | -123.3276
64.7969 | 123.2254 | -61.5646 | 61.5143 | 1.4211e-13 | -0.0038311 | -0.011004 | 0.039811 | -0.021225 | 0.048867 | 0.0036627 | -0.011934 | 0.02969 | 0.045011 | -0.0012201 | 0.047647 | -61.4775 | -0.030644 | -61.5863 | 61.4758 | 61.2801 | 61.4082 | -61.6221 | -61.5414 | -0.00422 | -61.6034 | 61.3265 | 61.4677 | 61.2786 | -61.8133 | -0.057483 | -0.038503 | 0.087091 | -0.021647 | 0.035836 | -0.23418 | -0.10604 | -0.24871 | -0.18782 | 0.023244 | -0.038733 | 0.20997 | -0.046573 | -0.23567 | 123.0404 | 122.8447 | 122.9729 | 61.534 | -123.1364 | 122.8911 | 123.0323 | 122.8432 | 61.5604 | -123.3276
66.5469 | 123.3398 | -61.5417 | 61.4868 | 1.4211e-13 | -0.0038311 | -0.010791 | 0.039811 | -0.021439 | 0.04908 | 0.011293 | -0.01172 | 0.029476 | 0.044798 | -0.0010065 | 0.047433 | -61.473 | -0.026065 | -61.5863 | 61.4666 | 61.2755 | 61.4128 | -61.6221 | -61.5368 | 0.000359 | -61.5896 | 61.3265 | 61.4769 | 61.2786 | -61.8179 | -0.080371 | -0.020194 | 0.068782 | -0.044535 | 0.035836 | -0.21129 | -0.073991 | -0.27617 | -0.16036 | 0.004935 | -0.047885 | 0.22829 | -0.009949 | -0.20821 | 123.0084 | 122.8173 | 122.9546 | 61.5157 | -123.1089 | 122.8682 | 123.0186 | 122.8204 | 61.5421 | -123.3047
68.25 | 123.3353 | -61.5463 | 61.4868 | 1.4211e-13 | -0.0038311 | -0.010791 | 0.040025 | -0.021225 | 0.048867 | -0.0039678 | -0.011934 | 0.029476 | 0.044798 | -0.0010065 | 0.04786 | -61.4684 | -0.026065 | -61.5863 | 61.4666 | 61.2801 | 61.4174 | -61.6175 | -61.5368 | -0.00422 | -61.5988 | 61.3173 | 61.4631 | 61.2832 | -61.8133 | -0.071214 | -0.020194 | 0.077938 | -0.039957 | 0.031257 | -0.20671 | -0.069413 | -0.26702 | -0.16951 | 0.009513 | -0.052464 | 0.21455 | -0.023685 | -0.20363 | 123.0129 | 122.8264 | 122.9637 | 61.5203 | -123.1044 | 122.8636 | 123.0095 | 122.8295 | 61.5421 | -123.3002
70 | 123.3307 | -61.5463 | 61.4822 | 1.4211e-13 | -0.0036175 | -0.011432 | 0.039811 | -0.021225 | 0.048867 | 0.011293 | -0.011934 | 0.029476 | 0.044584 | -0.0012201 | 0.047219 | -61.473 | -0.021486 | -61.5817 | 61.4758 | 61.2709 | 61.4128 | -61.6175 | -61.5368 | -0.008798 | -61.5896 | 61.3219 | 61.4723 | 61.274 | -61.8133 | -0.071214 | -0.00646 | 0.07336 | -0.035378 | 0.035836 | -0.21129 | -0.069414 | -0.26702 | -0.16036 | 0.009513 | -0.043307 | 0.22371 | -0.009951 | -0.20821 | 123.0221 | 122.8173 | 122.9592 | 61.5248 | -123.0998 | 122.8682 | 123.0186 | 122.8204 | 61.5375 | -123.2956
71.6719 | 123.3307 | -61.6287 | 61.3861 | 1.4211e-13 | -0.0036175 | -0.011004 | 0.039598 | -0.021225 | 0.048867 | -0.0039678 | -0.01172 | 0.029476 | 0.044798 | -0.0010065 | 0.047433 | -61.4775 | -0.016908 | -61.5863 | 61.4758 | 61.2755 | 61.4128 | -61.6084 | -61.5368 | -0.00422 | -61.5896 | 61.3265 | 61.4677 | 61.2786 | -61.8133 | 0.020341 | 0.089671 | 0.15118 | 0.04244 | 0.022099 | -0.11058 | 0.026717 | -0.18462 | -0.059648 | 0.09191 | 0.03909 | 0.22371 | 0.081601 | -0.1075 | 123.1045 | 122.9042 | 123.0415 | 61.6118 | -122.9945 | 122.9552 | 123.0964 | 122.9073 | 61.6245 | -123.1995
73.4375 | 123.2117 | -61.6333 | 61.4502 | 1.4211e-13 | -0.0040449 | -0.011004 | 0.039811 | -0.021653 | 0.048867 | 0.011293 | -0.012148 | 0.02969 | 0.045011 | -0.0012201 | 0.04786 | -61.473 | -0.016908 | -61.5863 | 61.4712 | 61.2755 | 61.422 | -61.6175 | -61.546 | 0.004938 | -61.5942 | 61.331 | 61.4677 | 61.3107 | -61.8042 | 0.015761 | 0.021006 | 0.16034 | 0.047018 | 0.031257 | -0.17467 | -0.028213 | -0.17088 | -0.11916 | 0.087331 | 0.039089 | 0.20997 | 0.017514 | -0.13954 | 123.1045 | 122.9088 | 123.0553 | 61.6164 | -123.0677 | 122.9643 | 123.101 | 122.944 | 61.6382 | -123.2544
75.1875 | 123.2025 | -61.647 | 61.4502 | 1.4211e-13 | -0.0038311 | -0.010791 | 0.039598 | -0.021225 | 0.048867 | 0.011293 | -0.011934 | 0.02969 | 0.044584 | -0.00079267 | 0.047647 | -61.4684 | -0.021486 | -61.5771 | 61.4666 | 61.2801 | 61.4082 | -61.6084 | -61.5414 | 0.004938 | -61.5942 | 61.3173 | 61.4677 | 61.3152 | -61.8088 | 0.038652 | 0.016427 | 0.17865 | 0.069908 | 0.031256 | -0.17009 | -0.041949 | -0.16173 | -0.13289 | 0.10564 | 0.052822 | 0.21455 | 0.017514 | -0.13496 | 123.1137 | 122.9271 | 123.0553 | 61.6255 | -123.0586 | 122.9643 | 123.1147 | 122.9623 | 61.652 | -123.259
76.875 | 123.1705 | -61.6699 | 61.4777 | 1.4211e-13 | -0.0038311 | -0.011004 | 0.039598 | -0.021439 | 0.049294 | 0.0036627 | -0.01172 | 0.02969 | 0.045225 | -0.00079267 | 0.047647 | -61.4684 | -0.016908 | -61.5817 | 61.4758 | 61.2709 | 61.4037 | -61.613 | -61.5368 | -0.00422 | -61.5942 | 61.3265 | 61.4677 | 61.2832 | -61.8088 | 0.056961 | -0.001882 | 0.20153 | 0.088218 | 0.031257 | -0.20671 | -0.073993 | -0.13884 | -0.1512 | 0.13311 | 0.07571 | 0.21455 | -0.009952 | -0.19447 | 123.1457 | 122.9409 | 123.0736 | 61.653 | -123.0906 | 122.9964 | 123.1376 | 122.9531 | 61.6657 | -123.2864
78.6406 | 123.2712 | -61.6013 | 61.4548 | 1.4211e-13 | -0.0040449 | -0.010577 | 0.039598 | -0.021439 | 0.048867 | -0.0039678 | -0.01172 | 0.029263 | 0.044798 | -0.0014337 | 0.04786 | -61.4684 | -0.021486 | -61.5771 | 61.4712 | 61.2664 | 61.4037 | -61.6084 | -61.5322 | -0.00422 | -61.5942 | 61.3219 | 61.4631 | 61.274 | -61.8042 | -0.007125 | 0.016428 | 0.13287 | 0.024131 | 0.031256 | -0.1884 | -0.051105 | -0.20293 | -0.13289 | 0.069023 | 0.007045 | 0.20997 | 0.008358 | -0.18074 | 123.0725 | 122.8676 | 123.0049 | 61.5798 | -123.0632 | 122.9231 | 123.0644 | 122.8753 | 61.597 | -123.259
80.3906 | 123.2666 | -61.5417 | 61.5097 | 1.4211e-13 | -0.0038311 | -0.010791 | 0.040025 | -0.021439 | 0.048653 | 0.011293 | -0.011934 | 0.029476 | 0.045225 | -0.00079267 | 0.048074 | -61.4684 | -0.021486 | -61.5817 | 61.4666 | 61.2755 | 61.4037 | -61.6084 | -61.5277 | -0.00422 | -61.5851 | 61.3219 | 61.4631 | 61.3198 | -61.8042 | -0.066634 | -0.043083 | 0.07336 | -0.039956 | 0.026678 | -0.23418 | -0.10604 | -0.26244 | -0.18782 | 0.014093 | -0.043306 | 0.21913 | -0.046574 | -0.18989 | 123.0084 | 122.8173 | 122.9454 | 61.5203 | -123.1181 | 122.8636 | 123.0049 | 122.8616 | 61.5375 | -123.3139
82.1562 | 123.3215 | -61.5692 | 61.4685 | 1.4211e-13 | -0.0036175 | -0.010791 | 0.039811 | -0.021439 | 0.048867 | -0.0039678 | -0.011507 | 0.029476 | 0.045225 | -0.0010065 | 0.047647 | -61.4684 | -0.021486 | -61.5771 | 61.462 | 61.2755 | 61.4128 | -61.6084 | -61.5322 | 0.000359 | -61.5851 | 61.3173 | 61.4631 | 61.3107 | -61.8088 | -0.039168 | -0.006462 | 0.10083 | -0.007912 | 0.031256 | -0.19298 | -0.055681 | -0.23955 | -0.1512 | 0.03698 | -0.01584 | 0.22371 | -0.005375 | -0.15785 | 123.0313 | 122.8447 | 122.982 | 61.5477 | -123.0769 | 122.8865 | 123.0323 | 122.8799 | 61.5696 | -123.2773
83.9219 | 123.1888 | -61.6287 | 61.4456 | 1.4211e-13 | -0.0040449 | -0.010577 | 0.040239 | -0.021439 | 0.048653 | 0.0036627 | -0.01172 | 0.029904 | 0.044798 | -0.0010065 | 0.04786 | -61.4638 | -0.016908 | -61.5771 | 61.4666 | 61.2755 | 61.4037 | -61.6038 | -61.5322 | 0.000359 | -61.5942 | 61.3127 | 61.4586 | 61.3061 | -61.7996 | 0.02492 | 0.021004 | 0.16491 | 0.051597 | 0.026677 | -0.17009 | -0.04195 | -0.17088 | -0.13289 | 0.096489 | 0.034511 | 0.2054 | 0.012934 | -0.13954 | 123.0953 | 122.9042 | 123.0324 | 61.6118 | -123.0494 | 122.9414 | 123.0873 | 122.9348 | 61.6291 | -123.2452
85.6875 | 123.2483 | -61.6104 | 61.3953 | 1.4211e-13 | -0.0036175 | -0.010791 | 0.039811 | -0.021225 | 0.048867 | 0.0036627 | -0.01172 | 0.029476 | 0.044584 | -0.0012201 | 0.048074 | -61.4592 | -0.026065 | -61.5725 | 61.4666 | 61.2755 | 61.4082 | -61.6084 | -61.5277 | 0.004938 | -61.5851 | 61.3127 | 61.454 | 61.2557 | -61.795 | 0.002031 | 0.071358 | 0.15118 | 0.037865 | 0.035834 | -0.11974 | 0.012982 | -0.18462 | -0.08254 | 0.082758 | 0.025359 | 0.20997 | 0.05871 | -0.13955 | 123.077 | 122.8859 | 123.0187 | 61.5843 | -123.0036 | 122.9231 | 123.0644 | 122.8661 | 61.6154 | -123.1903
87.3906 | 123.2758 | -61.5829 | 61.4044 | 1.4211e-13 | -0.0036175 | -0.011004 | 0.040025 | -0.021439 | 0.048439 | 0.0036627 | -0.01172 | 0.02969 | 0.044584 | -0.00079267 | 0.047647 | -61.4592 | -0.021486 | -61.5725 | 61.4666 | 61.2755 | 61.4037 | -61.613 | -61.5322 | 0.004938 | -61.5851 | 61.3081 | 61.4631 | 61.3198 | -61.8042 | -0.030014 | 0.062203 | 0.12372 | 0.010399 | 0.040413 | -0.12889 | -0.000751 | -0.22124 | -0.096273 | 0.050713 | -0.002107 | 0.21913 | 0.058712 | -0.084602 | 123.0496 | 122.8585 | 122.9866 | 61.5615 | -123.0174 | 122.8911 | 123.0461 | 122.9028 | 61.5879 | -123.2086
89.1406 | 123.1979 | -61.6516 | 61.4456 | 1.4211e-13 | -0.0036175 | -0.010791 | 0.039811 | -0.021225 | 0.048867 | 0.0036627 | -0.011934 | 0.02969 | 0.044798 | -0.0010065 | 0.048074 | -61.4638 | -0.021486 | -61.5771 | 61.4575 | 61.2709 | 61.4037 | -61.6221 | -61.5231 | -0.00422 | -61.5851 | 61.3127 | 61.4586 | 61.3152 | -61.8042 | 0.029492 | 0.011848 | 0.1878 | 0.074485 | 0.044993 | -0.17467 | -0.04195 | -0.15257 | -0.13289 | 0.12853 | 0.066557 | 0.21913 | 0.012934 | -0.13038 | 123.1091 | 122.9226 | 123.0553 | 61.6301 | -123.0677 | 122.9643 | 123.1102 | 122.9668 | 61.6474 | -123.2498
90.9062 | 123.2712 | -61.5509 | 61.4594 | 1.4211e-13 | -0.0038311 | -0.011004 | 0.040025 | -0.021653 | 0.04908 | 0.0036627 | -0.012148 | 0.029476 | 0.045011 | -0.0010065 | 0.047647 | -61.4638 | -0.016908 | -61.568 | 61.4575 | 61.2572 | 61.3991 | -61.5946 | -61.5231 | -0.008798 | -61.5805 | 61.3173 | 61.4586 | 61.3336 | -61.795 | -0.043742 | -0.001885 | 0.087094 | -0.017067 | 0.026675 | -0.20214 | -0.060262 | -0.24413 | -0.14205 | 0.027826 | -0.029572 | 0.21455 | -0.000799 | -0.1258 | 123.0084 | 122.8081 | 122.95 | 61.534 | -123.054 | 122.8682 | 123.0095 | 122.8845 | 61.5421 | -123.2544
92.6094 | 123.2986 | -61.5601 | 61.4685 | 1.4211e-13 | -0.0034037 | -0.010363 | 0.040239 | -0.021439 | 0.048867 | 0.011293 | -0.011934 | 0.02969 | 0.044798 | -0.0010065 | 0.04786 | -61.4592 | -0.021486 | -61.5725 | 61.4575 | 61.2664 | 61.3991 | -61.6038 | -61.5322 | 0.000359 | -61.5851 | 61.3081 | 61.454 | 61.3336 | -61.795 | -0.043744 | -0.01104 | 0.10083 | -0.012489 | 0.031255 | -0.20214 | -0.069417 | -0.23497 | -0.16036 | 0.027825 | -0.024995 | 0.20997 | -0.014532 | -0.13495 | 123.0175 | 122.8264 | 122.9591 | 61.5386 | -123.0723 | 122.8682 | 123.014 | 122.8936 | 61.5604 | -123.2635
94.3594 | 123.2254 | -61.5921 | 61.4548 | 1.4211e-13 | -0.0034037 | -0.011004 | 0.039811 | -0.021653 | 0.04908 | 0.0036627 | -0.011507 | 0.029476 | 0.044584 | -0.0010065 | 0.047647 | -61.4592 | -0.021486 | -61.5725 | 61.4529 | 61.2709 | 61.4037 | -61.6084 | -61.5185 | 0.004938 | -61.5805 | 61.3127 | 61.4494 | 61.2878 | -61.7996 | -0.01628 | -0.001886 | 0.13287 | 0.019554 | 0.035834 | -0.18383 | -0.051105 | -0.20751 | -0.14205 | 0.073604 | 0.011627 | 0.21913 | -0.005378 | -0.16701 | 123.045 | 122.863 | 122.9958 | 61.5706 | -123.0632 | 122.9048 | 123.0415 | 122.8799 | 61.597 | -123.2544
96.1094 | 123.2162 | -61.5372 | 61.4822 | 1.4211e-13 | -0.0036175 | -0.010791 | 0.039811 | -0.021439 | 0.04908 | 0.011293 | -0.011934 | 0.029476 | 0.045011 | -0.0010065 | 0.047433 | -61.4501 | -0.021486 | -61.5725 | 61.4529 | 61.2664 | 61.4082 | -61.6038 | -61.5231 | -0.008798 | -61.5805 | 61.3173 | 61.4494 | 61.274 | -61.8042 | -0.066633 | -0.029352 | 0.087096 | -0.035378 | 0.031255 | -0.21587 | -0.073993 | -0.26702 | -0.16494 | 0.014093 | -0.043305 | 0.22371 | -0.032844 | -0.20821 | 122.9901 | 122.8035 | 122.9454 | 61.5157 | -123.086 | 122.8545 | 122.9866 | 122.8112 | 61.5284 | -123.2864
97.8594 | 123.2529 | -61.5829 | 61.4319 | 1.4211e-13 | -0.0038311 | -0.011004 | 0.039811 | -0.021225 | 0.048867 | 0.011293 | -0.01172 | 0.029476 | 0.044798 | -0.0010065 | 0.047433 | -61.4547 | -0.016908 | -61.5725 | 61.4575 | 61.2664 | 61.4037 | -61.5992 | -61.5231 | 0.004938 | -61.5805 | 61.3081 | 61.4494 | 61.3061 | -61.7904 | -0.016277 | 0.025581 | 0.12829 | 0.010399 | 0.026676 | -0.16552 | -0.028217 | -0.2075 | -0.12374 | 0.05987 | 0.002472 | 0.20997 | 0.01751 | -0.1258 | 123.0404 | 122.8493 | 122.9866 | 61.566 | -123.0311 | 122.8911 | 123.0323 | 122.889 | 61.5879 | -123.2223
99.6094 | 123.2483 | -61.5829 | 61.4365 | 1.4211e-13 | -0.0036175 | -0.011004 | 0.039811 | -0.021653 | 0.04908 | 0.0036627 | -0.011934 | 0.029049 | 0.044798 | -0.0012201 | 0.047647 | -61.4592 | -0.021486 | -61.568 | 61.462 | 61.2664 | 61.3991 | -61.5992 | -61.5185 | -0.00422 | -61.5759 | 61.3036 | 61.454 | 61.2557 | -61.795 | -0.016277 | 0.025582 | 0.12372 | 0.014977 | 0.031254 | -0.17009 | -0.037373 | -0.21208 | -0.13289 | 0.064449 | 0.00705 | 0.21913 | 0.017512 | -0.18075 | 123.045 | 122.8493 | 122.982 | 61.5615 | -123.0357 | 122.8865 | 123.0369 | 122.8387 | 61.5787 | -123.2315
101.375 | 123.1659 | -61.5829 | 61.5234 | 1.4211e-13 | -0.0036175 | -0.011004 | 0.039811 | -0.021225 | 0.048867 | -0.0039678 | -0.011934 | 0.029476 | 0.044584 | -0.0010065 | 0.047647 | -61.4455 | -0.012329 | -61.5725 | 61.4575 | 61.2572 | 61.3945 | -61.6038 | -61.5185 | -0.00422 | -61.5805 | 61.3081 | 61.4494 | 61.329 | -61.795 | -0.020856 | -0.065971 | 0.13745 | 0.010399 | 0.031255 | -0.26622 | -0.12893 | -0.21208 | -0.21529 | 0.064449 | 0.002472 | 0.21455 | -0.074042 | -0.19446 | 123.0404 | 122.8402 | 122.9775 | 61.5706 | -123.1272 | 122.8911 | 123.0323 | 122.9119 | 61.5787 | -123.3185
103.0781 | 123.2208 | -61.5829 | 61.4685 | 1.4211e-13 | -0.0036175 | -0.010791 | 0.040025 | -0.021439 | 0.048653 | -0.0039678 | -0.012148 | 0.029476 | 0.045011 | -0.0010065 | 0.047647 | -61.4547 | -0.016908 | -61.5634 | 61.4575 | 61.2572 | 61.3991 | -61.6038 | -61.5277 | 0.004938 | -61.5759 | 61.3081 | 61.4448 | 61.3381 | -61.7904 | -0.020856 | -0.01104 | 0.12829 | 0.019556 | 0.040412 | -0.21129 | -0.069417 | -0.2075 | -0.16036 | 0.055292 | 0.00705 | 0.21455 | -0.02369 | -0.13038 | 123.0404 | 122.8402 | 122.982 | 61.566 | -123.0723 | 122.8911 | 123.0278 | 122.9211 | 61.5879 | -123.259
104.8125 | 123.2895 | -61.5921 | 61.3998 | 1.4211e-13 | -0.0040449 | -0.010577 | 0.040025 | -0.021653 | 0.048867 | -0.0039678 | -0.01172 | 0.029476 | 0.044584 | -0.0012201 | 0.047647 | -61.4547 | -0.016908 | -61.5634 | 61.4575 | 61.2709 | 61.3991 | -61.5992 | -61.5185 | 0.004938 | -61.5713 | 61.3081 | 61.4448 | 61.2649 | -61.795 | -0.007122 | 0.057625 | 0.13745 | 0.028711 | 0.035833 | -0.12889 | -0.000752 | -0.20293 | -0.091695 | 0.073604 | 0.020784 | 0.22371 | 0.044975 | -0.13497 | 123.0496 | 122.863 | 122.9912 | 61.5752 | -122.9991 | 122.9002 | 123.0369 | 122.857 | 61.597 | -123.1949
106.5625 | 123.1796 | -61.5601 | 61.4914 | 1.4211e-13 | -0.0036175 | -0.010577 | 0.040025 | -0.021225 | 0.04908 | 0.0036627 | -0.012148 | 0.029476 | 0.044798 | -0.0010065 | 0.047647 | -61.4501 | -0.016908 | -61.5634 | 61.4575 | 61.2618 | 61.3945 | -61.5946 | -61.5231 | 0.004938 | -61.5759 | 61.3036 | 61.4448 | 61.274 | -61.795 | -0.034586 | -0.033928 | 0.10999 | -0.003332 | 0.031254 | -0.2296 | -0.096884 | -0.23497 | -0.18783 | 0.036982 | -0.015838 | 0.21913 | -0.046578 | -0.21736 | 123.0175 | 122.8218 | 122.9546 | 61.5432 | -123.086 | 122.8636 | 123.0049 | 122.8341 | 61.565 | -123.2864
108.2812 | 123.2895 | -61.5784 | 61.3678 | 1.4211e-13 | -0.0038311 | -0.010791 | 0.039598 | -0.021439 | 0.048867 | 0.011293 | -0.01172 | 0.029263 | 0.044798 | -0.00057907 | 0.047647 | -61.4455 | -0.012329 | -61.5634 | 61.4575 | 61.2618 | 61.3945 | -61.5992 | -61.5185 | 0.000359 | -61.5759 | 61.299 | 61.4402 | 61.274 | -61.7996 | -0.020855 | 0.089668 | 0.13287 | 0.014978 | 0.035833 | -0.10601 | 0.026712 | -0.22124 | -0.068809 | 0.059871 | 0.002472 | 0.22371 | 0.07244 | -0.093767 | 123.0358 | 122.8402 | 122.9729 | 61.566 | -122.967 | 122.8774 | 123.0186 | 122.8524 | 61.5787 | -123.1674
110.0312 | 123.2071 | -61.5829 | 61.4456 | 1.4211e-13 | -0.0038311 | -0.010791 | 0.039598 | -0.021653 | 0.048867 | 0.0036627 | -0.01172 | 0.029049 | 0.045225 | -0.00079267 | 0.047433 | -61.4455 | -0.026065 | -61.5634 | 61.4483 | 61.2572 | 61.4037 | -61.5992 | -61.5139 | 0.000359 | -61.5667 | 61.3036 | 61.4494 | 61.2603 | -61.7813 | -0.016277 | 0.002691 | 0.13745 | 0.019556 | 0.035833 | -0.18841 | -0.04195 | -0.19835 | -0.14205 | 0.069028 | 0.016208 | 0.21455 | 0.003777 | -0.18532 | 123.0313 | 122.8402 | 122.9866 | 61.5569 | -123.0448 | 122.8865 | 123.0323 | 122.8432 | 61.5833 | -123.2269
111.7969 | 123.2986 | -61.5234 | 61.4365 | 1.4211e-13 | -0.0034037 | -0.011004 | 0.039811 | -0.021439 | 0.048867 | -0.011598 | -0.012148 | 0.02969 | 0.044798 | -0.00079267 | 0.047433 | -61.4501 | -0.016908 | -61.5588 | 61.4483 | 61.2572 | 61.3991 | -61.5946 | -61.5139 | 0.000359 | -61.5713 | 61.3036 | 61.4448 | 61.3107 | -61.7904 | -0.071208 | 0.011847 | 0.073363 | -0.035376 | 0.035832 | -0.17925 | -0.037373 | -0.26701 | -0.13289 | 0.009518 | -0.047881 | 0.21913 | 0.008354 | -0.1258 | 122.9717 | 122.7806 | 122.9225 | 61.5065 | -123.0311 | 122.827 | 122.9683 | 122.8341 | 61.5238 | -123.2269
113.4844 | 123.1293 | -61.5555 | 61.5143 | 1.4211e-13 | -0.0034037 | -0.010577 | 0.039811 | -0.021439 | 0.048653 | 0.0036627 | -0.01172 | 0.029263 | 0.044798 | -0.0012201 | 0.047219 | -61.4455 | -0.016908 | -61.5588 | 61.4483 | 61.2572 | 61.3945 | -61.5946 | -61.5185 | -0.008798 | -61.5713 | 61.3081 | 61.454 | 61.2923 | -61.7904 | -0.039164 | -0.065973 | 0.10999 | -0.003332 | 0.035832 | -0.25707 | -0.11977 | -0.23497 | -0.20614 | 0.036983 | -0.015837 | 0.21913 | -0.060308 | -0.22194 | 123.0038 | 122.8127 | 122.95 | 61.5386 | -123.1089 | 122.8636 | 123.0095 | 122.8478 | 61.5467 | -123.3047
115.25 | 123.1476 | -61.5417 | 61.5463 | 1.4211e-13 | -0.0036175 | -0.010791 | 0.040025 | -0.021439 | 0.048867 | 0.0036627 | -0.011934 | 0.029476 | 0.044798 | -0.0010065 | 0.047219 | -61.4501 | -0.021486 | -61.5542 | 61.4529 | 61.2481 | 61.3854 | -61.5946 | -61.5093 | 0.000359 | -61.5713 | 61.2944 | 61.4402 | 61.274 | -61.7859 | -0.052897 | -0.093439 | 0.091674 | -0.012487 | 0.04041 | -0.29827 | -0.16097 | -0.24412 | -0.25192 | 0.032407 | -0.02957 | 0.21455 | -0.10609 | -0.27229 | 122.9946 | 122.7898 | 122.9271 | 61.5203 | -123.141 | 122.8362 | 122.982 | 122.8158 | 61.5421 | -123.3322
117.0156 | 123.1476 | -61.5601 | 61.5143 | 1.4211e-13 | -0.0031901 | -0.010577 | 0.040025 | -0.021439 | 0.049294 | -0.0039678 | -0.011934 | 0.029476 | 0.044584 | -0.00079267 | 0.047433 | -61.4501 | -0.026065 | -61.5634 | 61.4483 | 61.2618 | 61.3945 | -61.5855 | -61.5231 | 0.000359 | -61.5667 | 61.299 | 61.4448 | 61.2786 | -61.795 | -0.025428 | -0.065973 | 0.10999 | -0.003332 | 0.022096 | -0.25249 | -0.11977 | -0.23497 | -0.21529 | 0.036982 | -0.00668 | 0.22829 | -0.069466 | -0.23567 | 123.0084 | 122.8218 | 122.9546 | 61.534 | -123.0998 | 122.859 | 123.0049 | 122.8387 | 61.5604 | -123.3093
118.7812 | 123.2666 | -61.5234 | 61.441 | 1.4211e-13 | -0.0034037 | -0.011004 | 0.039811 | -0.021439 | 0.048653 | 0.0036627 | -0.011934 | 0.029263 | 0.044798 | -0.0010065 | 0.047647 | -61.4501 | -0.021486 | -61.5542 | 61.4529 | 61.2481 | 61.3899 | -61.5901 | -61.5093 | 0.000359 | -61.5667 | 61.299 | 61.4448 | 61.2969 | -61.7904 | -0.066629 | 0.011847 | 0.073363 | -0.030798 | 0.035831 | -0.19299 | -0.051108 | -0.26701 | -0.14205 | 0.014096 | -0.043302 | 0.22371 | 0.003776 | -0.14412 | 122.9763 | 122.7715 | 122.9134 | 61.502 | -123.0311 | 122.8224 | 122.9683 | 122.8204 | 61.5238 | -123.2315
120.4688 | 123.2162 | -61.5555 | 61.4227 | 1.4211e-13 | -0.0034037 | -0.010363 | 0.039811 | -0.021653 | 0.04908 | 0.011293 | -0.011934 | 0.029476 | 0.044798 | -0.0012201 | 0.047647 | -61.4363 | -0.026065 | -61.5542 | 61.4437 | 61.2572 | 61.3899 | -61.5946 | -61.5048 | -0.00422 | -61.5667 | 61.299 | 61.4402 | 61.2695 | -61.795 | -0.039164 | 0.021002 | 0.11914 | 0.001246 | 0.04041 | -0.16552 | -0.032797 | -0.23955 | -0.12374 | 0.050719 | -0.011258 | 0.22829 | 0.017509 | -0.15328 | 122.9992 | 122.8127 | 122.9454 | 61.5294 | -123.0174 | 122.8545 | 122.9957 | 122.8249 | 61.5513 | -123.2178
122.1562 | 123.1705 | -61.5463 | 61.496 | 1.4211e-13 | -0.0036175 | -0.010363 | 0.039811 | -0.021653 | 0.04908 | 0.0036627 | -0.012148 | 0.029263 | 0.044798 | -0.00079267 | 0.047647 | -61.4455 | -0.016908 | -61.5542 | 61.4437 | 61.2526 | 61.3945 | -61.5946 | -61.5139 | 0.000359 | -61.5667 | 61.2944 | 61.4448 | 61.3015 | -61.7904 | -0.048319 | -0.052241 | 0.10083 | -0.007909 | 0.04041 | -0.24334 | -0.10146 | -0.24412 | -0.20156 | 0.032407 | -0.020413 | 0.22371 | -0.051156 | -0.19447 | 122.9901 | 122.799 | 122.9408 | 61.5294 | -123.0906 | 122.8407 | 122.9911 | 122.8478 | 61.5467 | -123.2864
123.8594 | 123.1338 | -61.6333 | 61.3998 | 1.4211e-13 | -0.0036175 | -0.010791 | 0.039811 | -0.021866 | 0.048867 | 0.0036627 | -0.012361 | 0.029476 | 0.044584 | -0.0010065 | 0.047647 | -61.4409 | -0.016908 | -61.5497 | 61.4392 | 61.2618 | 61.3991 | -61.5809 | -61.5093 | -0.00422 | -61.5576 | 61.299 | 61.4402 | 61.274 | -61.7813 | 0.052393 | 0.039311 | 0.19238 | 0.083645 | 0.031252 | -0.13805 | -0.000752 | -0.14799 | -0.10085 | 0.12396 | 0.075719 | 0.22371 | 0.040397 | -0.12581 | 123.0725 | 122.8951 | 123.0324 | 61.6164 | -122.9807 | 122.9323 | 123.0735 | 122.9073 | 61.6291 | -123.1811
125.625 | 123.1522 | -61.6058 | 61.4136 | 1.4211e-13 | -0.0038311 | -0.010791 | 0.040025 | -0.021653 | 0.048867 | 0.011293 | -0.01172 | 0.029476 | 0.044798 | -0.0010065 | 0.04786 | -61.4409 | -0.016908 | -61.5542 | 61.4437 | 61.2893 | 61.3899 | -61.5946 | -61.5002 | -0.00422 | -61.5576 | 61.2853 | 61.4494 | 61.3473 | -61.7813 | 0.01119 | 0.030157 | 0.16492 | 0.0516 | 0.04041 | -0.12431 | -0.023642 | -0.17546 | -0.12832 | 0.10565 | 0.048253 | 0.22371 | 0.035821 | -0.066285 | 123.0496 | 122.8951 | 122.9958 | 61.5889 | -123.0082 | 122.8911 | 123.0552 | 122.9531 | 61.6016 | -123.1949
127.3438 | 123.1522 | -61.5921 | 61.4044 | 1.4211e-13 | -0.0029765 | -0.011004 | 0.040025 | -0.021653 | 0.048867 | 0.0036627 | -0.01172 | 0.02969 | 0.044584 | -0.00079267 | 0.047647 | -61.4409 | -0.012329 | -61.5497 | 61.4437 | 61.2664 | 61.3945 | -61.5809 | -61.5093 | -0.00422 | -61.553 | 61.2898 | 61.4402 | 61.2969 | -61.7859 | 0.011194 | 0.039312 | 0.15118 | 0.042446 | 0.031252 | -0.13805 | -0.009909 | -0.19377 | -0.11459 | 0.082761 | 0.039099 | 0.23287 | 0.035819 | -0.1075 | 123.0358 | 122.8585 | 122.9866 | 61.5798 | -122.9853 | 122.8819 | 123.0323 | 122.889 | 61.5879 | -123.1903
129.1094 | 123.1705 | -61.5555 | 61.4685 | 1.4211e-13 | -0.0034037 | -0.010577 | 0.040025 | -0.021653 | 0.048653 | 0.0036627 | -0.011934 | 0.029476 | 0.044584 | -0.00079267 | 0.047647 | -61.4455 | -0.021486 | -61.5542 | 61.4346 | 61.2709 | 61.3854 | -61.5809 | -61.5093 | 0.004938 | -61.553 | 61.2944 | 61.4357 | 61.274 | -61.7813 | -0.025427 | -0.033932 | 0.10999 | 0.001246 | 0.026673 | -0.19756 | -0.083153 | -0.22581 | -0.1741 | 0.04614 | 0.002478 | 0.22829 | -0.032847 | -0.19447 | 122.9901 | 122.8264 | 122.9408 | 61.534 | -123.0494 | 122.8499 | 122.9911 | 122.8295 | 61.5604 | -123.2498
130.7969 | 123.2574 | -61.5692 | 61.3678 | 1.4211e-13 | -0.0034037 | -0.010577 | 0.040025 | -0.021225 | 0.04908 | 0.018923 | -0.012148 | 0.029476 | 0.044584 | -0.00079267 | 0.047647 | -61.4318 | -0.016908 | -61.5497 | 61.4346 | 61.2481 | 61.3899 | -61.5763 | -61.5048 | 0.000359 | -61.5576 | 61.2898 | 61.4357 | 61.2557 | -61.7813 | -0.007116 | 0.066776 | 0.13745 | 0.019558 | 0.026674 | -0.11974 | 0.022134 | -0.21208 | -0.077966 | 0.064452 | 0.011632 | 0.22371 | 0.067861 | -0.11208 | 123.0038 | 122.8173 | 122.9591 | 61.5523 | -122.9441 | 122.859 | 123.0049 | 122.8249 | 61.5696 | -123.1491
132.7344 | 123.23 | -61.5829 | 61.377 | 1.4211e-13 | -0.0036175 | -0.010791 | 0.040025 | -0.021866 | 0.048867 | 0.011293 | -0.012148 | 0.02969 | 0.044584 | -0.00057907 | 0.047219 | -61.4363 | -0.016908 | -61.5451 | 61.4392 | 61.2801 | 61.3854 | -61.5901 | -61.5002 | 0.000359 | -61.5576 | 61.2898 | 61.4265 | 61.3473 | -61.7813 | -0.007119 | 0.062199 | 0.14661 | 0.037869 | 0.044988 | -0.096847 | 0.0084 | -0.19835 | -0.087121 | 0.082764 | 0.025365 | 0.22371 | 0.049549 | -0.029664 | 123.0221 | 122.8631 | 122.9683 | 61.566 | -122.967 | 122.8728 | 123.0094 | 122.9302 | 61.5833 | -123.1582
134.5469 | 123.2025 | -61.5372 | 61.441 | 1.4211e-13 | -0.0031901 | -0.010577 | 0.039598 | -0.021653 | 0.04908 | 0.0036627 | -0.01172 | 0.029263 | 0.044584 | -0.00057907 | 0.047219 | -61.4318 | -0.016908 | -61.5451 | 61.4346 | 61.2755 | 61.3762 | -61.5901 | -61.5002 | -0.00422 | -61.5576 | 61.2898 | 61.4402 | 61.329 | -61.7767 | -0.052896 | -0.006466 | 0.10541 | -0.007908 | 0.044988 | -0.16551 | -0.064844 | -0.23954 | -0.15121 | 0.036987 | -0.020412 | 0.21913 | -0.000802 | -0.11207 | 122.9717 | 122.8127 | 122.9134 | 61.5203 | -123.0311 | 122.827 | 122.9774 | 122.8661 | 61.533 | -123.2178
136.25 | 123.2483 | -61.5005 | 61.4365 | 1.4211e-13 | -0.0031901 | -0.011004 | 0.039811 | -0.021653 | 0.048653 | 0.011293 | -0.012148 | 0.029476 | 0.044798 | -0.00057907 | 0.047433 | -61.4455 | -0.021486 | -61.5451 | 61.43 | 61.2755 | 61.3854 | -61.5809 | -61.5093 | 0.000359 | -61.553 | 61.2898 | 61.4357 | 61.2832 | -61.7813 | -0.080359 | -0.006467 | 0.055053 | -0.044529 | 0.03583 | -0.16094 | -0.051109 | -0.28074 | -0.14663 | -0.008792 | -0.052454 | 0.22829 | -0.000803 | -0.15327 | 122.9305 | 122.7761 | 122.8859 | 61.4791 | -123.0174 | 122.7904 | 122.9362 | 122.7837 | 61.5009 | -123.2178
137.9844 | 123.1155 | -61.5463 | 61.496 | 1.4211e-13 | -0.0031901 | -0.011004 | 0.039811 | -0.021439 | 0.048867 | -0.0039678 | -0.01172 | 0.02969 | 0.044798 | -0.00057907 | 0.047433 | -61.4363 | -0.026065 | -61.5359 | 61.4392 | 61.2389 | 61.3854 | -61.5809 | -61.4956 | 0.000359 | -61.5576 | 61.2898 | 61.4311 | 61.2603 | -61.7813 | -0.034582 | -0.05682 | 0.10999 | 0.010404 | 0.044986 | -0.25708 | -0.11062 | -0.23497 | -0.20614 | 0.050722 | -0.011256 | 0.22371 | -0.064891 | -0.23568 | 122.9855 | 122.7852 | 122.9317 | 61.5203 | -123.0769 | 122.8362 | 122.9774 | 122.8066 | 61.5467 | -123.2773
139.7188 | 123.1476 | -61.5692 | 61.4227 | 1.4211e-13 | -0.0036175 | -0.010791 | 0.040025 | -0.021439 | 0.048653 | 0.0036627 | -0.011507 | 0.02969 | 0.045011 | -0.00057907 | 0.047433 | -61.4272 | -0.021486 | -61.5451 | 61.4346 | 61.2481 | 61.3808 | -61.5809 | -61.5002 | 0.000359 | -61.553 | 61.2898 | 61.4311 | 61.2923 | -61.7767 | -0.011694 | 0.011845 | 0.14203 | 0.024136 | 0.03583 | -0.17467 | -0.041954 | -0.2075 | -0.1329 | 0.069031 | 0.016211 | 0.22371 | 0.008352 | -0.13038 | 123.0038 | 122.8173 | 122.95 | 61.5477 | -123.0036 | 122.859 | 123.0003 | 122.8616 | 61.5696 | -123.1994
141.4062 | 123.1705 | -61.528 | 61.4731 | 1.4211e-13 | -0.0031901 | -0.010791 | 0.040025 | -0.021439 | 0.04908 | 0.0036627 | -0.01172 | 0.02969 | 0.044798 | -0.0010065 | 0.047647 | -61.4318 | -0.026065 | -61.5405 | 61.4254 | 61.2526 | 61.3808 | -61.5809 | -61.4956 | 0.004938 | -61.553 | 61.2898 | 61.4357 | 61.2878 | -61.7813 | -0.052893 | -0.047666 | 0.096254 | -0.012485 | 0.040408 | -0.22045 | -0.092308 | -0.25328 | -0.18325 | 0.032411 | -0.024988 | 0.22829 | -0.037424 | -0.18532 | 122.9534 | 122.7806 | 122.9088 | 61.502 | -123.054 | 122.8178 | 122.9637 | 122.8158 | 61.533 | -123.2544
143.0781 | 123.1659 | -61.5601 | 61.4227 | 1.4211e-13 | -0.0029765 | -0.010791 | 0.039384 | -0.021866 | 0.048653 | -0.0039678 | -0.011934 | 0.029476 | 0.045011 | -0.00036547 | 0.047433 | -61.4226 | -0.012329 | -61.5405 | 61.4392 | 61.2572 | 61.3808 | -61.5809 | -61.5002 | 0.000359 | -61.553 | 61.2807 | 61.4265 | 61.274 | -61.7767 | -0.020849 | 0.016423 | 0.13746 | 0.019559 | 0.040408 | -0.16552 | -0.041954 | -0.21665 | -0.14205 | 0.059876 | 0.007056 | 0.22371 | 0.003773 | -0.1487 | 122.9992 | 122.8173 | 122.9408 | 61.5477 | -123.0036 | 122.8407 | 122.9866 | 122.8341 | 61.5604 | -123.1994
144.75 | 123.1293 | -61.5967 | 61.3815 | 1.4211e-13 | -0.0031901 | -0.010791 | 0.039598 | -0.021653 | 0.048867 | 0.0036627 | -0.011934 | 0.029476 | 0.044798 | -0.00057907 | 0.047647 | -61.4363 | -0.021486 | -61.5451 | 61.4392 | 61.2435 | 61.3716 | -61.5763 | -61.4956 | 0.000359 | -61.5438 | 61.2761 | 61.4357 | 61.2969 | -61.7767 | 0.02035 | 0.057621 | 0.16034 | 0.051602 | 0.031252 | -0.13806 | -0.009914 | -0.18003 | -0.10543 | 0.10108 | 0.052834 | 0.23287 | 0.054128 | -0.084607 | 123.0358 | 122.8402 | 122.9683 | 61.5752 | -122.9579 | 122.8728 | 123.0323 | 122.8936 | 61.597 | -123.1582
146.4375 | 123.23 | -61.528 | 61.4594 | 1.4211e-13 | -0.0031901 | -0.011004 | 0.040025 | -0.021225 | 0.048653 | -0.0039678 | -0.012361 | 0.029476 | 0.044584 | -0.00057907 | 0.047647 | -61.4318 | -0.016908 | -61.5451 | 61.43 | 61.2481 | 61.3808 | -61.5763 | -61.4956 | -0.00422 | -61.553 | 61.2898 | 61.4311 | 61.3107 | -61.7859 | -0.048315 | -0.029356 | 0.096254 | -0.017063 | 0.031252 | -0.2113 | -0.078576 | -0.25786 | -0.16952 | 0.032411 | -0.024988 | 0.23287 | -0.02827 | -0.14869 | 122.958 | 122.7761 | 122.9088 | 61.5111 | -123.0357 | 122.8178 | 122.9591 | 122.8387 | 61.5238 | -123.2452
148.1562 | 123.2758 | -61.4868 | 61.4365 | 1.4211e-13 | -0.0031901 | -0.010791 | 0.039811 | -0.021653 | 0.04908 | 0.0036627 | -0.01172 | 0.029904 | 0.044584 | -0.00079267 | 0.047647 | -61.4363 | -0.026065 | -61.5405 | 61.43 | 61.2481 | 61.3716 | -61.5672 | -61.5002 | 0.000359 | -61.5438 | 61.2853 | 61.4311 | 61.2557 | -61.7721 | -0.080356 | -0.006467 | 0.050477 | -0.053684 | 0.026672 | -0.18841 | -0.064845 | -0.28532 | -0.15121 | -0.013367 | -0.05703 | 0.22829 | -0.005381 | -0.18075 | 122.9168 | 122.7349 | 122.8584 | 61.4608 | -123.0036 | 122.7721 | 122.9179 | 122.7425 | 61.4872 | -123.2086
149.875 | 123.1155 | -61.5646 | 61.4777 | 1.4211e-13 | -0.0031901 | -0.010791 | 0.039811 | -0.021653 | 0.048653 | -0.0039678 | -0.011934 | 0.029476 | 0.045225 | -0.00079267 | 0.047219 | -61.4363 | -0.021486 | -61.5405 | 61.4346 | 61.2664 | 61.3808 | -61.5718 | -61.4956 | 0.000359 | -61.5393 | 61.2807 | 61.4311 | 61.329 | -61.7813 | -0.007115 | -0.043087 | 0.1283 | 0.024136 | 0.031251 | -0.21129 | -0.096886 | -0.21666 | -0.19699 | 0.069032 | 0.025369 | 0.24202 | -0.04658 | -0.14869 | 122.9992 | 122.831 | 122.9454 | 61.5431 | -123.0494 | 122.8453 | 122.9957 | 122.8936 | 61.565 | -123.259
151.5625 | 123.143 | -61.6058 | 61.3678 | 1.4211e-13 | -0.0027627 | -0.011004 | 0.040025 | -0.021439 | 0.04908 | 0.0036627 | -0.012361 | 0.029476 | 0.045011 | -0.00079267 | 0.047647 | -61.4226 | -0.026065 | -61.5313 | 61.4346 | 61.2618 | 61.3808 | -61.5855 | -61.491 | -0.00422 | -61.553 | 61.2807 | 61.4265 | 61.3107 | -61.7721 | 0.020348 | 0.066776 | 0.18323 | 0.074492 | 0.054144 | -0.10601 | 0.012977 | -0.1663 | -0.087123 | 0.11481 | 0.052832 | 0.21913 | 0.058704 | -0.057138 | 123.0404 | 122.8676 | 122.9866 | 61.5798 | -122.9533 | 122.8865 | 123.0323 | 122.9165 | 61.6016 | -123.1399
153.2344 | 123.175 | -61.5646 | 61.3632 | 1.4211e-13 | -0.0031901 | -0.010791 | 0.040025 | -0.021439 | 0.048867 | 0.0036627 | -0.01172 | 0.029263 | 0.044584 | -0.00079267 | 0.047433 | -61.4226 | -0.012329 | -61.5405 | 61.43 | 61.2526 | 61.3762 | -61.5672 | -61.4956 | 0.004938 | -61.5484 | 61.2807 | 61.4311 | 61.2557 | -61.7767 | -0.002536 | 0.066775 | 0.14203 | 0.024136 | 0.026672 | -0.11059 | 0.012976 | -0.21208 | -0.082545 | 0.069032 | 0.016212 | 0.22829 | 0.067861 | -0.1075 | 122.9946 | 122.8173 | 122.9408 | 61.5523 | -122.9304 | 122.8453 | 122.9957 | 122.8204 | 61.5696 | -123.1399
154.9062 | 123.262 | -61.4914 | 61.4227 | 1.4211e-13 | -0.0031901 | -0.011004 | 0.039598 | -0.021866 | 0.048653 | -0.0039678 | -0.01172 | 0.029904 | 0.044798 | -0.00057907 | 0.047433 | -61.4272 | -0.021486 | -61.5405 | 61.43 | 61.2389 | 61.3762 | -61.5672 | -61.491 | -0.00422 | -61.5484 | 61.2853 | 61.4311 | 61.2557 | -61.7721 | -0.075778 | 0.007266 | 0.064212 | -0.049106 | 0.026672 | -0.18383 | -0.046533 | -0.28074 | -0.13748 | 0.000368 | -0.05703 | 0.22371 | 0.008352 | -0.16701 | 122.9214 | 122.7303 | 122.8676 | 61.4699 | -122.9899 | 122.7766 | 122.9225 | 122.7471 | 61.4872 | -123.1949
156.5938 | 123.111 | -61.5555 | 61.3815 | 1.4211e-13 | -0.0034037 | -0.011004 | 0.040025 | -0.021653 | 0.048653 | 0.0036627 | -0.012148 | 0.029263 | 0.044584 | -0.00079267 | 0.047433 | -61.4226 | -0.016908 | -61.5405 | 61.4254 | 61.2709 | 61.3762 | -61.5718 | -61.4956 | 0.000359 | -61.553 | 61.2807 | 61.4357 | 61.2969 | -61.7767 | -0.01627 | 0.043886 | 0.13288 | 0.014981 | 0.031251 | -0.11058 | -0.005335 | -0.22123 | -0.10086 | 0.059877 | 0.002478 | 0.22371 | 0.054128 | -0.084607 | 122.9809 | 122.8264 | 122.9317 | 61.5386 | -122.9533 | 122.8362 | 122.9911 | 122.8524 | 61.5558 | -123.1582
158.3281 | 123.143 | -61.5372 | 61.4319 | 1.4211e-13 | -0.0031901 | -0.010577 | 0.040025 | -0.021653 | 0.048867 | -0.0039678 | -0.012148 | 0.029263 | 0.044584 | -0.00057907 | 0.047219 | -61.4226 | -0.021486 | -61.5405 | 61.43 | 61.2984 | 61.3716 | -61.5763 | -61.4956 | 0.000359 | -61.5393 | 61.2761 | 61.4311 | 61.3564 | -61.763 | -0.03916 | -0.00189 | 0.11457 | -0.00333 | 0.03583 | -0.13346 | -0.060268 | -0.22581 | -0.15579 | 0.041566 | -0.002097 | 0.22371 | -0.000804 | -0.075439 | 122.9672 | 122.8356 | 122.9088 | 61.5157 | -123.0082 | 122.8133 | 122.9683 | 122.8936 | 61.5375 | -123.1949
160.0156 | 123.2346 | -61.5601 | 61.3495 | 1.4211e-13 | -0.0029765 | -0.010577 | 0.039811 | -0.021866 | 0.048653 | 0.011293 | -0.011934 | 0.029049 | 0.04437 | -0.00057907 | 0.047647 | -61.4226 | -0.016908 | -61.5313 | 61.43 | 61.2709 | 61.3762 | -61.5718 | -61.4864 | 0.000359 | -61.5438 | 61.2761 | 61.4265 | 61.3061 | -61.7767 | -0.011692 | 0.080508 | 0.13746 | 0.028716 | 0.040408 | -0.078539 | 0.026709 | -0.21665 | -0.073391 | 0.073612 | 0.016213 | 0.23287 | 0.077015 | -0.043406 | 122.9901 | 122.831 | 122.9363 | 61.5432 | -122.9212 | 122.8362 | 122.9866 | 122.8661 | 61.5604 | -123.1262
161.6875 | 123.1613 | -61.5234 | 61.3953 | 1.4211e-13 | -0.0036175 | -0.010577 | 0.039811 | -0.021439 | 0.048867 | 0.0036627 | -0.012361 | 0.029263 | 0.045011 | -0.00036547 | 0.047433 | -61.418 | -0.016908 | -61.5405 | 61.4254 | 61.2435 | 61.3762 | -61.5718 | -61.491 | 0.004938 | -61.5438 | 61.2715 | 61.4219 | 61.3015 | -61.7721 | -0.048314 | 0.030153 | 0.10541 | -0.017063 | 0.031251 | -0.15179 | -0.019068 | -0.2487 | -0.12375 | 0.032411 | -0.020409 | 0.22829 | 0.026659 | -0.093761 | 122.9489 | 122.7669 | 122.8996 | 61.5065 | -122.967 | 122.795 | 122.9454 | 122.8249 | 61.5284 | -123.1674
163.4219 | 123.1659 | -61.528 | 61.4182 | 1.4211e-13 | -0.0031901 | -0.010791 | 0.039811 | -0.021653 | 0.048653 | 0.011293 | -0.012148 | 0.029476 | 0.044798 | -0.00079267 | 0.047219 | -61.4134 | -0.016908 | -61.5313 | 61.4208 | 61.2755 | 61.3716 | -61.5672 | -61.4819 | 0.000359 | -61.5438 | 61.2761 | 61.4219 | 61.3381 | -61.763 | -0.039157 | 0.002687 | 0.11457 | -0.003328 | 0.035829 | -0.14263 | -0.046535 | -0.23496 | -0.14206 | 0.046147 | -0.015831 | 0.21913 | 0.003771 | -0.080021 | 122.9489 | 122.8035 | 122.8996 | 61.5111 | -122.9853 | 122.8041 | 122.9499 | 122.8661 | 61.5284 | -123.1811
165.1562 | 123.1659 | -61.5555 | 61.3907 | 1.4211e-13 | -0.0031901 | -0.010791 | 0.040025 | -0.021866 | 0.04908 | -0.0039678 | -0.011934 | 0.029476 | 0.044798 | -0.00079267 | 0.047006 | -61.4134 | -0.026065 | -61.5268 | 61.4208 | 61.2938 | 61.3716 | -61.5534 | -61.491 | 0.000359 | -61.5484 | 61.2715 | 61.4265 | 61.3152 | -61.7721 | 0.002046 | 0.030153 | 0.14203 | 0.028716 | 0.02667 | -0.096843 | -0.019069 | -0.21665 | -0.11917 | 0.064455 | 0.007057 | 0.22371 | 0.035816 | -0.075448 | 122.9763 | 122.8493 | 122.9271 | 61.5294 | -122.9441 | 122.827 | 122.982 | 122.8707 | 61.5558 | -123.1628
166.9375 | 123.23 | -61.5051 | 61.4227 | 1.4211e-13 | -0.0031901 | -0.010577 | 0.040025 | -0.021653 | 0.048653 | 0.018923 | -0.011934 | 0.029476 | 0.044798 | -0.00036547 | 0.047006 | -61.4226 | -0.026065 | -61.5222 | 61.4208 | 61.2481 | 61.3808 | -61.5626 | -61.4864 | 0.000359 | -61.5438 | 61.2761 | 61.4219 | 61.3244 | -61.7767 | -0.057466 | -0.00189 | 0.082523 | -0.01706 | 0.040406 | -0.17467 | -0.041954 | -0.27159 | -0.14663 | 0.01868 | -0.038719 | 0.23287 | -0.000806 | -0.098333 | 122.926 | 122.7532 | 122.8859 | 61.4791 | -122.9853 | 122.7812 | 122.9271 | 122.8295 | 61.5055 | -123.1994
168.8281 | 123.0972 | -61.5234 | 61.4731 | 1.4211e-13 | -0.0029765 | -0.010577 | 0.040025 | -0.021439 | 0.048867 | 0.011293 | -0.01172 | 0.029263 | 0.044798 | -0.00057907 | 0.047006 | -61.4134 | -0.021486 | -61.5268 | 61.4254 | 61.2572 | 61.3716 | -61.5672 | -61.4864 | 0.000359 | -61.5393 | 61.2715 | 61.4265 | 61.3381 | -61.763 | -0.043735 | -0.047666 | 0.10999 | -0.003328 | 0.040407 | -0.21587 | -0.10147 | -0.23954 | -0.20157 | 0.03699 | -0.01583 | 0.22371 | -0.046581 | -0.13495 | 122.9489 | 122.7806 | 122.8951 | 61.502 | -123.0403 | 122.795 | 122.9499 | 122.8616 | 61.5238 | -123.2361
170.8281 | 123.1659 | -61.4914 | 61.4594 | 1.4211e-13 | -0.0031901 | -0.010791 | 0.039811 | -0.021653 | 0.048867 | 0.018923 | -0.011934 | 0.029476 | 0.045011 | -0.00079267 | 0.047219 | -61.4089 | -0.016908 | -61.5359 | 61.4163 | 61.3076 | 61.3716 | -61.5672 | -61.4819 | -0.00422 | -61.5438 | 61.2715 | 61.4128 | 61.3061 | -61.7676 | -0.075778 | -0.043091 | 0.082525 | -0.044528 | 0.03125 | -0.15177 | -0.087734 | -0.27616 | -0.18783 | 0.009526 | -0.052452 | 0.22371 | -0.046585 | -0.15327 | 122.9077 | 122.799 | 122.863 | 61.4745 | -123.0265 | 122.7629 | 122.9042 | 122.7975 | 61.4872 | -123.2269
173.0156 | 123.1796 | -61.5326 | 61.409 | 1.4211e-13 | -0.0038311 | -0.010577 | 0.039384 | -0.021439 | 0.048653 | -0.0039678 | -0.01172 | 0.029476 | 0.044798 | -0.00057907 | 0.046578 | -61.4134 | -0.021486 | -61.5313 | 61.4254 | 61.3122 | 61.367 | -61.5718 | -61.4819 | -0.00422 | -61.5393 | 61.2715 | 61.4128 | 61.3473 | -61.7676 | -0.039158 | 0.01642 | 0.11915 | 0.00125 | 0.040408 | -0.096838 | -0.041958 | -0.23496 | -0.13748 | 0.050725 | -0.006674 | 0.22829 | 0.003769 | -0.061708 | 122.958 | 122.8448 | 122.8996 | 61.5111 | -122.9807 | 122.8041 | 122.9454 | 122.8799 | 61.5284 | -123.1766
174.7656 | 123.1384 | -61.5509 | 61.4319 | 1.4211e-13 | -0.0029765 | -0.011004 | 0.040025 | -0.021653 | 0.04908 | -0.0039678 | -0.012148 | 0.029476 | 0.044798 | -0.00057907 | 0.047219 | -61.4134 | -0.016908 | -61.5176 | 61.4208 | 61.3122 | 61.3762 | -61.5718 | -61.4727 | -0.00422 | -61.5301 | 61.2715 | 61.4173 | 61.3427 | -61.7721 | -0.020848 | -0.011046 | 0.13746 | 0.033295 | 0.054143 | -0.11973 | -0.055689 | -0.22123 | -0.16037 | 0.078192 | 0.020793 | 0.24202 | -0.01454 | -0.089175 | 122.9717 | 122.8631 | 122.9271 | 61.534 | -123.0036 | 122.8224 | 122.9682 | 122.8936 | 61.5467 | -123.204
176.7656 | 123.143 | -61.5417 | 61.3724 | 1.4211e-13 | -0.0029765 | -0.010577 | 0.040025 | -0.021866 | 0.048653 | -0.0039678 | -0.011934 | 0.02969 | 0.044798 | -0.00036547 | 0.047006 | -61.4089 | -0.016908 | -61.5268 | 61.4071 | 61.2847 | 61.367 | -61.558 | -61.4681 | 0.009516 | -61.5347 | 61.2761 | 61.4082 | 61.3198 | -61.763 | -0.016266 | 0.034728 | 0.13288 | 0.014983 | 0.031249 | -0.08769 | -0.005336 | -0.22123 | -0.096279 | 0.073616 | 0.00706 | 0.22829 | 0.035813 | -0.052558 | 122.9489 | 122.8264 | 122.9088 | 61.5248 | -122.9304 | 122.8178 | 122.9499 | 122.8616 | 61.5513 | -123.1354
179.6094 | 123.0789 | -61.5738 | 61.3815 | 1.4211e-13 | -0.0031901 | -0.010577 | 0.040239 | -0.021866 | 0.048653 | 0.011293 | -0.01172 | 0.029476 | 0.044584 | -0.00079267 | 0.047219 | -61.4043 | -0.021486 | -61.5313 | 61.4208 | 61.3351 | 61.367 | -61.5626 | -61.4773 | 0.000359 | -61.5347 | 61.2624 | 61.4173 | 61.3427 | -61.7676 | 0.011199 | 0.039308 | 0.1695 | 0.042449 | 0.03125 | -0.046478 | -0.014492 | -0.19376 | -0.11917 | 0.096502 | 0.039104 | 0.23287 | 0.035814 | -0.038821 | 122.9946 | 122.9088 | 122.9408 | 61.5523 | -122.9441 | 122.8362 | 122.9911 | 122.9165 | 61.5742 | -123.1491
181.3125 | 123.1201 | -61.5372 | 61.4227 | 1.4211e-13 | -0.0029765 | -0.010577 | 0.040239 | -0.021653 | 0.049294 | -0.0039678 | -0.01172 | 0.029476 | 0.044798 | -0.00079267 | 0.046792 | -61.4134 | -0.012329 | -61.5268 | 61.4163 | 61.3351 | 61.367 | -61.5626 | -61.4819 | 0.000359 | -61.5301 | 61.2669 | 61.4128 | 61.3244 | -61.7584 | -0.025423 | -0.006469 | 0.12372 | 0.010405 | 0.035828 | -0.087676 | -0.05569 | -0.22123 | -0.15579 | 0.055302 | 0.00706 | 0.22829 | -0.009963 | -0.098333 | 122.9534 | 122.8722 | 122.9042 | 61.5248 | -122.9853 | 122.8041 | 122.9499 | 122.8616 | 61.5375 | -123.1811
183 | 123.0606 | -61.5005 | 61.4502 | 1.4211e-13 | -0.0031901 | -0.010363 | 0.040025 | -0.021866 | 0.048867 | -0.011598 | -0.01172 | 0.029476 | 0.044584 | -0.00036547 | 0.047006 | -61.4043 | -0.021486 | -61.5268 | 61.4208 | 61.3259 | 61.3625 | -61.5626 | -61.4773 | 0.004938 | -61.5347 | 61.2669 | 61.4173 | 61.3336 | -61.763 | -0.062044 | -0.029356 | 0.096259 | -0.026216 | 0.035828 | -0.1243 | -0.087735 | -0.26243 | -0.18326 | 0.023259 | -0.034139 | 0.22829 | -0.03285 | -0.11664 | 122.9214 | 122.8264 | 122.863 | 61.4791 | -123.0128 | 122.7675 | 122.9179 | 122.8341 | 61.5055 | -123.2132
184.7188 | 123.1155 | -61.528 | 61.4365 | 1.4211e-13 | -0.0029765 | -0.01015 | 0.039811 | -0.021866 | 0.048653 | 0.0036627 | -0.012148 | 0.029049 | 0.044584 | -0.00036547 | 0.047219 | -61.4134 | -0.021486 | -61.5176 | 61.4117 | 61.3259 | 61.367 | -61.558 | -61.4773 | 0.000359 | -61.5301 | 61.2715 | 61.4173 | 61.3107 | -61.7538 | -0.029999 | -0.02478 | 0.11457 | 0.010407 | 0.040406 | -0.11057 | -0.069423 | -0.2258 | -0.16494 | 0.050725 | -0.002095 | 0.22371 | -0.019117 | -0.1258 | 122.9397 | 122.8539 | 122.8951 | 61.5065 | -122.9945 | 122.7995 | 122.9454 | 122.8387 | 61.5284 | -123.1903
186.4062 | 123.0789 | -61.5143 | 61.4456 | 1.4211e-13 | -0.0031901 | -0.010791 | 0.040025 | -0.02208 | 0.048867 | -0.0039678 | -0.011934 | 0.029476 | 0.044584 | -0.00036547 | 0.047006 | -61.4134 | -0.016908 | -61.5268 | 61.4071 | 61.3259 | 61.3579 | -61.558 | -61.4681 | -0.00422 | -61.5255 | 61.2669 | 61.4128 | 61.329 | -61.7676 | -0.043732 | -0.038515 | 0.10084 | -0.012483 | 0.031249 | -0.11972 | -0.087736 | -0.25327 | -0.17868 | 0.04615 | -0.011249 | 0.24202 | -0.032852 | -0.11664 | 122.9214 | 122.8402 | 122.8722 | 61.4974 | -123.0036 | 122.7812 | 122.927 | 122.8433 | 61.5101 | -123.2132
188.0938 | 123.1979 | -61.4685 | 61.4136 | 1.4211e-13 | -0.0029765 | -0.010577 | 0.040025 | -0.021653 | 0.04908 | 0.018923 | -0.012361 | 0.029263 | 0.044798 | -0.00036547 | 0.047006 | -61.4043 | -0.016908 | -61.5176 | 61.4117 | 61.3259 | 61.3579 | -61.5534 | -61.4773 | 0.009516 | -61.521 | 61.2669 | 61.4128 | 61.3244 | -61.7584 | -0.084929 | -0.001892 | 0.064216 | -0.049102 | 0.035827 | -0.087679 | -0.055692 | -0.28989 | -0.14663 | -0.008784 | -0.052446 | 0.23745 | -0.000808 | -0.089178 | 122.8802 | 122.7944 | 122.8264 | 61.4516 | -122.967 | 122.7354 | 122.8813 | 122.7929 | 61.478 | -123.172
189.7812 | 123.0606 | -61.5051 | 61.4731 | 1.4211e-13 | -0.0034037 | -0.010363 | 0.040025 | -0.021439 | 0.048653 | 0.018923 | -0.012148 | 0.029049 | 0.045011 | -0.00057907 | 0.047006 | -61.4134 | -0.016908 | -61.5176 | 61.4071 | 61.3213 | 61.3625 | -61.5534 | -61.4681 | 0.004938 | -61.5255 | 61.2624 | 61.4128 | 61.3107 | -61.7584 | -0.048308 | -0.06598 | 0.09168 | -0.012481 | 0.035827 | -0.15177 | -0.11062 | -0.25327 | -0.21072 | 0.036995 | -0.020404 | 0.23287 | -0.060317 | -0.16242 | 122.9122 | 122.8264 | 122.8676 | 61.4882 | -123.0265 | 122.7675 | 122.9179 | 122.8158 | 61.5101 | -123.2315
191.4531 | 123.1293 | -61.5234 | 61.3998 | 1.4211e-13 | -0.0034037 | -0.010577 | 0.040025 | -0.021653 | 0.048653 | 0.011293 | -0.012148 | 0.029263 | 0.044798 | 6.1934e-05 | 0.046792 | -61.4043 | -0.021486 | -61.5176 | 61.4117 | 61.3167 | 61.3579 | -61.558 | -61.4681 | 0.000359 | -61.521 | 61.2669 | 61.4128 | 61.2969 | -61.7538 | -0.034577 | 0.011841 | 0.11915 | 0.005829 | 0.040406 | -0.083103 | -0.041959 | -0.23038 | -0.1329 | 0.055305 | 0.002485 | 0.23287 | 0.012925 | -0.10292 | 122.9351 | 122.8402 | 122.8813 | 61.502 | -122.9579 | 122.7904 | 122.9362 | 122.8204 | 61.5238 | -123.1537
193.1406 | 123.0743 | -61.5005 | 61.4731 | 1.4211e-13 | -0.0029765 | -0.010577 | 0.040239 | -0.021439 | 0.04908 | 0.011293 | -0.011934 | 0.029476 | 0.044584 | -0.00036547 | 0.047433 | -61.4043 | -0.016908 | -61.5176 | 61.4117 | 61.3351 | 61.3579 | -61.5534 | -61.4681 | -0.00422 | -61.5255 | 61.2578 | 61.399 | 61.3336 | -61.7538 | -0.052886 | -0.061401 | 0.096259 | -0.017059 | 0.035827 | -0.13803 | -0.1152 | -0.25327 | -0.2153 | 0.032417 | -0.024982 | 0.22829 | -0.074053 | -0.13953 | 122.9122 | 122.8356 | 122.8584 | 61.4836 | -123.0265 | 122.7583 | 122.8996 | 122.8341 | 61.4963 | -123.2269
194.875 | 123.1567 | -61.4868 | 61.4365 | 1.4211e-13 | -0.0031901 | -0.010577 | 0.040025 | -0.021866 | 0.048867 | 0.011293 | -0.01172 | 0.02969 | 0.044584 | -0.00036547 | 0.047006 | -61.4043 | -0.016908 | -61.5085 | 61.4071 | 61.3076 | 61.3625 | -61.5534 | -61.4681 | 0.009516 | -61.5301 | 61.2624 | 61.4082 | 61.3244 | -61.7584 | -0.066619 | -0.029359 | 0.082526 | -0.021636 | 0.044983 | -0.12888 | -0.074002 | -0.27158 | -0.1741 | 0.018684 | -0.043294 | 0.22829 | -0.028274 | -0.11207 | 122.8939 | 122.7944 | 122.8493 | 61.4699 | -122.9899 | 122.7492 | 122.895 | 122.8112 | 61.4963 | -123.1949
196.5625 | 123.1384 | -61.5143 | 61.4044 | 1.4211e-13 | -0.0031901 | -0.010577 | 0.040025 | -0.021866 | 0.048867 | 0.0036627 | -0.01172 | 0.029476 | 0.044798 | -0.00036547 | 0.047006 | -61.3997 | -0.016908 | -61.5222 | 61.4071 | 61.2938 | 61.3625 | -61.5397 | -61.4636 | 0.000359 | -61.5255 | 61.2624 | 61.4128 | 61.3015 | -61.7447 | -0.025416 | 0.002684 | 0.11457 | -0.007905 | 0.017511 | -0.11058 | -0.041959 | -0.23038 | -0.14206 | 0.050729 | -0.011249 | 0.21913 | 0.008347 | -0.10292 | 122.9214 | 122.8081 | 122.8767 | 61.4974 | -122.9441 | 122.7766 | 122.927 | 122.8158 | 61.5146 | -123.1491
198.2344 | 123.0606 | -61.496 | 61.4639 | 1.4211e-13 | -0.0029765 | -0.010791 | 0.039384 | -0.021866 | 0.048867 | 0.011293 | -0.011934 | 0.029476 | 0.044584 | -0.00057907 | 0.047219 | -61.4043 | -0.016908 | -61.5176 | 61.4071 | 61.303 | 61.3579 | -61.558 | -61.4681 | 0.004938 | -61.5255 | 61.2624 | 61.4082 | 61.3198 | -61.7492 | -0.062042 | -0.056825 | 0.091682 | -0.021636 | 0.040406 | -0.16093 | -0.10605 | -0.25327 | -0.20157 | 0.02784 | -0.029559 | 0.22371 | -0.05574 | -0.14411 | 122.9031 | 122.799 | 122.8539 | 61.4791 | -123.0219 | 122.7583 | 122.9042 | 122.8158 | 61.5009 | -123.2132
199.9219 | 123.1476 | -61.5005 | 61.377 | 1.4211e-13 | -0.0027627 | -0.010363 | 0.039598 | -0.021866 | 0.04908 | 0.0036627 | -0.012148 | 0.029476 | 0.044584 | -0.00036547 | 0.047219 | -61.3997 | -0.021486 | -61.5176 | 61.4025 | 61.3076 | 61.3579 | -61.558 | -61.4636 | 0.004938 | -61.521 | 61.2486 | 61.4036 | 61.329 | -61.7492 | -0.057465 | 0.025572 | 0.10084 | -0.017059 | 0.040406 | -0.069373 | -0.019071 | -0.24869 | -0.12833 | 0.036996 | -0.020403 | 0.22829 | 0.026656 | -0.047979 | 122.9031 | 122.8081 | 122.8584 | 61.4791 | -122.935 | 122.7492 | 122.9042 | 122.8295 | 61.5055 | -123.1262
201.625 | 123.1293 | -61.4594 | 61.4319 | 1.4211e-13 | -0.0029765 | -0.010791 | 0.039811 | -0.021653 | 0.048653 | 0.0036627 | -0.01172 | 0.029263 | 0.044584 | -0.00036547 | 0.047219 | -61.3997 | -0.012329 | -61.5085 | 61.4025 | 61.3259 | 61.3579 | -61.5534 | -61.4681 | -0.00422 | -61.5255 | 61.2532 | 61.4036 | 61.3244 | -61.7538 | -0.094084 | -0.02936 | 0.059639 | -0.049101 | 0.044983 | -0.10599 | -0.074003 | -0.29447 | -0.17868 | -0.008781 | -0.06618 | 0.22829 | -0.028276 | -0.10749 | 122.8619 | 122.7852 | 122.8172 | 61.447 | -122.9853 | 122.7126 | 122.863 | 122.7837 | 61.4551 | -123.1857
203.3281 | 123.0286 | -61.5463 | 61.3953 | 1.4211e-13 | -0.0031901 | -0.010791 | 0.039811 | -0.021866 | 0.048867 | 0.011293 | -0.011934 | 0.029263 | 0.044798 | -0.00036547 | 0.047433 | -61.3997 | -0.012329 | -61.513 | 61.3979 | 61.3259 | 61.3533 | -61.5443 | -61.4636 | -0.00422 | -61.5164 | 61.2578 | 61.4082 | 61.329 | -61.7538 | 0.002049 | 0.002683 | 0.14661 | 0.033296 | 0.031247 | -0.069369 | -0.041961 | -0.20749 | -0.13748 | 0.082773 | 0.029953 | 0.23745 | 0.012924 | -0.06629 | 122.9443 | 122.8722 | 122.8996 | 61.534 | -122.9395 | 122.8041 | 122.9545 | 122.8753 | 61.5421 | -123.1491
205.0156 | 123.143 | -61.5234 | 61.3266 | 1.4211e-13 | -0.0029765 | -0.010577 | 0.039811 | -0.021653 | 0.048867 | 0.018923 | -0.012148 | 0.029049 | 0.044584 | -0.00015167 | 0.047219 | -61.3951 | -0.007751 | -61.5085 | 61.4025 | 61.3167 | 61.3579 | -61.5489 | -61.4636 | -0.00422 | -61.5255 | 61.2532 | 61.399 | 61.3198 | -61.7538 | -0.025419 | 0.075926 | 0.1283 | 0.014985 | 0.040404 | -0.009861 | 0.031283 | -0.23038 | -0.073395 | 0.059884 | -0.002094 | 0.22829 | 0.072431 | -0.006782 | 122.926 | 122.8402 | 122.8813 | 61.5157 | -122.8755 | 122.7766 | 122.9225 | 122.8433 | 61.5192 | -123.0804
206.7188 | 123.1705 | -61.5326 | 61.3632 | 1.4211e-13 | -0.0029765 | -0.010363 | 0.039811 | -0.021866 | 0.048867 | 0.0036627 | -0.011934 | 0.029476 | 0.044584 | 6.1934e-05 | 0.047006 | -61.3951 | -0.012329 | -61.5085 | 61.3979 | 61.3259 | 61.3487 | -61.5397 | -61.459 | 0.000359 | -61.5164 | 61.2486 | 61.399 | 61.329 | -61.7492 | -0.007105 | 0.034727 | 0.13746 | 0.024141 | 0.031246 | -0.037325 | -0.014496 | -0.21665 | -0.1146 | 0.073618 | 0.01622 | 0.23287 | 0.03581 | -0.034246 | 122.9305 | 122.8585 | 122.8813 | 61.5203 | -122.9029 | 122.7812 | 122.9316 | 122.8616 | 61.533 | -123.1125
208.4688 | 123.056 | -61.5784 | 61.3907 | 1.4211e-13 | -0.0031901 | -0.010791 | 0.040025 | -0.02208 | 0.048867 | 0.0036627 | -0.011934 | 0.029049 | 0.044798 | -0.00036547 | 0.047219 | -61.3951 | -0.012329 | -61.513 | 61.4071 | 61.3122 | 61.3487 | -61.5534 | -61.4636 | 0.009516 | -61.5072 | 61.2578 | 61.4036 | 61.3107 | -61.7492 | 0.024934 | 0.016417 | 0.18324 | 0.065339 | 0.040405 | -0.078527 | -0.041962 | -0.17087 | -0.1329 | 0.11482 | 0.071153 | 0.24202 | 0.012923 | -0.080026 | 122.9855 | 122.8905 | 122.9271 | 61.566 | -122.9441 | 122.8362 | 122.982 | 122.889 | 61.5879 | -123.1399
210.1719 | 123.056 | -61.5875 | 61.3632 | 1.4211e-13 | -0.0029765 | -0.010577 | 0.039811 | -0.021866 | 0.048653 | 0.011293 | -0.012148 | 0.029263 | 0.044584 | -0.00015167 | 0.047219 | -61.3951 | -0.016908 | -61.5085 | 61.3979 | 61.3213 | 61.3579 | -61.5489 | -61.459 | 0.000359 | -61.5164 | 61.2532 | 61.4128 | 61.3244 | -61.7401 | 0.038668 | 0.034727 | 0.19239 | 0.079072 | 0.040404 | -0.041904 | -0.005338 | -0.15256 | -0.11002 | 0.12855 | 0.071151 | 0.22371 | 0.049546 | -0.038824 | 122.9855 | 122.9088 | 122.9454 | 61.5706 | -122.9121 | 122.8407 | 123.0003 | 122.9119 | 61.5879 | -123.1033
211.9062 | 123.0881 | -61.5005 | 61.409 | 1.4211e-13 | -0.0031901 | -0.010363 | 0.040025 | -0.021866 | 0.04908 | 0.011293 | -0.011934 | 0.029263 | 0.044798 | -0.00036547 | 0.047006 | -61.3951 | -0.012329 | -61.5085 | 61.4025 | 61.3122 | 61.3441 | -61.5489 | -61.459 | 0.004938 | -61.5118 | 61.2486 | 61.4036 | 61.3198 | -61.7492 | -0.048307 | -0.006472 | 0.10542 | -0.007903 | 0.040404 | -0.096838 | -0.064851 | -0.24869 | -0.16037 | 0.041574 | -0.011246 | 0.23745 | -0.005388 | -0.08918 | 122.9031 | 122.8127 | 122.8447 | 61.4882 | -122.9579 | 122.7492 | 122.9042 | 122.8204 | 61.5055 | -123.1582
213.5781 | 123.1522 | -61.4731 | 61.3907 | 1.4211e-13 | -0.0031901 | -0.010363 | 0.040025 | -0.021653 | 0.048867 | -0.0039678 | -0.01172 | 0.02969 | 0.044584 | -0.00036547 | 0.047433 | -61.386 | -0.012329 | -61.5085 | 61.3979 | 61.3122 | 61.3487 | -61.5443 | -61.4544 | 0.004938 | -61.5118 | 61.2486 | 61.399 | 61.3107 | -61.7492 | -0.071194 | 0.007261 | 0.087106 | -0.035369 | 0.035825 | -0.078527 | -0.041962 | -0.27616 | -0.14206 | 0.018687 | -0.038712 | 0.23745 | 0.008344 | -0.080026 | 122.871 | 122.7852 | 122.8218 | 61.4608 | -122.935 | 122.7217 | 122.8721 | 122.7837 | 61.478 | -123.1399
215.2812 | 123.0835 | -61.5051 | 61.4319 | 1.4211e-13 | -0.0027627 | -0.010363 | 0.039811 | -0.021866 | 0.048653 | 0.011293 | -0.012148 | 0.029476 | 0.044584 | -0.00057907 | 0.047006 | -61.3951 | -0.021486 | -61.5039 | 61.3934 | 61.2847 | 61.3441 | -61.5489 | -61.4681 | 0.004938 | -61.5072 | 61.2486 | 61.4036 | 61.3244 | -61.7492 | -0.043729 | -0.038517 | 0.10999 | 0.001253 | 0.044982 | -0.1472 | -0.087739 | -0.24411 | -0.18326 | 0.036995 | -0.002089 | 0.24202 | -0.028276 | -0.10749 | 122.8985 | 122.7898 | 122.8493 | 61.4836 | -122.9807 | 122.7538 | 122.9087 | 122.8295 | 61.5101 | -123.1811
217.0156 | 123.0515 | -61.5097 | 61.4502 | 1.4211e-13 | -0.0029765 | -0.010363 | 0.039598 | -0.021866 | 0.048867 | 0.0036627 | -0.01172 | 0.029476 | 0.044584 | -0.00015167 | 0.047219 | -61.3906 | -0.016908 | -61.4947 | 61.3934 | 61.3122 | 61.3487 | -61.5397 | -61.4544 | 0.004938 | -61.5118 | 61.2486 | 61.4036 | 61.2878 | -61.7492 | -0.029993 | -0.056827 | 0.11915 | 0.014988 | 0.044981 | -0.13804 | -0.10147 | -0.23954 | -0.20157 | 0.055309 | -0.00209 | 0.23745 | -0.046586 | -0.16243 | 122.9031 | 122.8219 | 122.8584 | 61.4928 | -122.9899 | 122.7583 | 122.9133 | 122.7975 | 61.5146 | -123.1994
218.7031 | 123.1659 | -61.5143 | 61.3037 | 1.4211e-13 | -0.0031901 | -0.010363 | 0.039598 | -0.02208 | 0.048653 | 0.0036627 | -0.012148 | 0.029263 | 0.044584 | -0.00015167 | 0.047219 | -61.386 | -0.016908 | -61.5085 | 61.3979 | 61.3213 | 61.3533 | -61.5489 | -61.4544 | 0.004938 | -61.5072 | 61.2532 | 61.399 | 61.3198 | -61.7447 | -0.034574 | 0.094236 | 0.12831 | 0.00583 | 0.040404 | 0.017605 | 0.049592 | -0.23038 | -0.050507 | 0.059886 | 0.007066 | 0.23745 | 0.095319 | 0.016106 | 122.9122 | 122.8356 | 122.8676 | 61.4974 | -122.8526 | 122.7675 | 122.9133 | 122.8341 | 61.5192 | -123.0484
220.4062 | 123.0743 | -61.5509 | 61.3449 | 1.4211e-13 | -0.0027627 | -0.011004 | 0.040452 | -0.021866 | 0.04908 | 0.0036627 | -0.01172 | 0.029476 | 0.045011 | -0.00057907 | 0.047219 | -61.3906 | -0.016908 | -61.5039 | 61.3934 | 61.3213 | 61.3441 | -61.5443 | -61.4544 | 0.014095 | -61.5072 | 61.244 | 61.4082 | 61.3152 | -61.7401 | 0.006626 | 0.048458 | 0.16035 | 0.047029 | 0.040403 | -0.023594 | -0.000764 | -0.18918 | -0.10086 | 0.096507 | 0.043687 | 0.23287 | 0.063278 | -0.029672 | 122.9443 | 122.8722 | 122.895 | 61.534 | -122.8892 | 122.795 | 122.9591 | 122.8661 | 61.565 | -123.085
222.0938 | 123.1522 | -61.4685 | 61.4136 | 1.4211e-13 | -0.0029765 | -0.010791 | 0.039811 | -0.021866 | 0.048867 | -0.0039678 | -0.01172 | 0.028835 | 0.044584 | -0.00036547 | 0.047006 | -61.3906 | -0.016908 | -61.4947 | 61.3934 | 61.3122 | 61.3487 | -61.5443 | -61.4498 | 0.009516 | -61.5118 | 61.244 | 61.4036 | 61.3107 | -61.7447 | -0.075771 | -0.020206 | 0.077951 | -0.026211 | 0.04956 | -0.10141 | -0.06485 | -0.27616 | -0.16953 | 0.018689 | -0.043289 | 0.23287 | -0.009965 | -0.10291 | 122.8619 | 122.7807 | 122.8172 | 61.4516 | -122.9579 | 122.7126 | 122.8721 | 122.7792 | 61.478 | -123.1582
223.7969 | 123.0515 | -61.5143 | 61.3953 | 1.4211e-13 | -0.0031901 | -0.010791 | 0.040025 | -0.021866 | 0.048867 | 0.0036627 | -0.01172 | 0.029476 | 0.044584 | -0.00036547 | 0.047433 | -61.3814 | -0.007751 | -61.4993 | 61.3934 | 61.3122 | 61.3441 | -61.5397 | -61.4544 | 0.004938 | -61.5026 | 61.244 | 61.4082 | 61.3244 | -61.7492 | -0.025416 | -0.001896 | 0.13288 | 0.014987 | 0.040403 | -0.083105 | -0.051118 | -0.23496 | -0.15122 | 0.059886 | 0.011645 | 0.2466 | 0.012924 | -0.070868 | 122.9077 | 122.8264 | 122.8584 | 61.5065 | -122.935 | 122.7583 | 122.9225 | 122.8387 | 61.5192 | -123.1445
225.4688 | 123.0881 | -61.4548 | 61.4319 | 1.4211e-13 | -0.0029765 | -0.01015 | 0.039811 | -0.021653 | 0.049294 | -0.0039678 | -0.012148 | 0.029263 | 0.044798 | -0.00036547 | 0.046792 | -61.386 | -0.021486 | -61.4901 | 61.3842 | 61.2938 | 61.3396 | -61.5305 | -61.459 | 0.000359 | -61.5072 | 61.2486 | 61.399 | 61.2695 | -61.7401 | -0.075767 | -0.047674 | 0.068796 | -0.035366 | 0.040401 | -0.13804 | -0.092318 | -0.28531 | -0.18326 | -0.004202 | -0.052443 | 0.23287 | -0.032855 | -0.16243 | 122.839 | 122.7486 | 122.7943 | 61.4333 | -122.9624 | 122.7034 | 122.8538 | 122.7242 | 61.4551 | -123.172
227.2031 | 123.1155 | -61.4548 | 61.4044 | 1.4211e-13 | -0.0029765 | -0.01015 | 0.039598 | -0.021653 | 0.048867 | 0.0036627 | -0.011934 | 0.029263 | 0.044798 | -0.00036547 | 0.047219 | -61.386 | -0.016908 | -61.4993 | 61.3934 | 61.303 | 61.3396 | -61.5351 | -61.4544 | 0.000359 | -61.5026 | 61.2395 | 61.4036 | 61.2923 | -61.7447 | -0.080346 | -0.011051 | 0.068796 | -0.044522 | 0.035824 | -0.10142 | -0.064852 | -0.28989 | -0.16495 | 0.000377 | -0.047864 | 0.24202 | -0.00081 | -0.11207 | 122.8481 | 122.7578 | 122.7943 | 61.4379 | -122.9395 | 122.6942 | 122.8584 | 122.7471 | 61.4551 | -123.1491
228.9375 | 123.0331 | -61.5326 | 61.3724 | 1.4211e-13 | -0.0034037 | -0.010577 | 0.039811 | -0.021653 | 0.048867 | 0.0036627 | -0.011934 | 0.029263 | 0.044584 | -0.00015167 | 0.047219 | -61.386 | -0.007751 | -61.4993 | 61.3888 | 61.3167 | 61.3533 | -61.5397 | -61.4498 | 0.004938 | -61.5026 | 61.2303 | 61.399 | 61.2923 | -61.7401 | -0.007105 | 0.016415 | 0.14662 | 0.033298 | 0.040403 | -0.055637 | -0.019072 | -0.20749 | -0.14206 | 0.082776 | 0.029956 | 0.23745 | 0.026655 | -0.08003 | 122.9214 | 122.8493 | 122.8859 | 61.5248 | -122.9121 | 122.7629 | 122.9316 | 122.8249 | 61.5375 | -123.1125
230.6562 | 123.0606 | -61.5005 | 61.4182 | 1.4211e-13 | -0.0027627 | -0.010363 | 0.040025 | -0.021866 | 0.048867 | 0.0036627 | -0.01172 | 0.029476 | 0.045011 | -0.00015167 | 0.047647 | -61.3814 | -0.016908 | -61.4993 | 61.3796 | 61.3167 | 61.3396 | -61.5397 | -61.4498 | 0.000359 | -61.5026 | 61.2303 | 61.399 | 61.274 | -61.7492 | -0.039149 | -0.038519 | 0.11915 | 0.001254 | 0.040403 | -0.10141 | -0.078585 | -0.24869 | -0.18784 | 0.050732 | -0.002088 | 0.2466 | -0.019122 | -0.14412 | 122.8802 | 122.8173 | 122.8401 | 61.4836 | -122.9579 | 122.7309 | 122.8996 | 122.7746 | 61.5009 | -123.1674
232.3438 | 123.0698 | -61.5234 | 61.4136 | 1.4211e-13 | -0.0027627 | -0.010791 | 0.039811 | -0.021866 | 0.048867 | 0.0036627 | -0.012361 | 0.029263 | 0.04437 | -0.00036547 | 0.047219 | -61.3814 | -0.012329 | -61.4993 | 61.3888 | 61.3213 | 61.3487 | -61.5397 | -61.4544 | 0.000359 | -61.4935 | 61.2395 | 61.399 | 61.3152 | -61.7401 | -0.016261 | -0.024784 | 0.14204 | 0.024142 | 0.040403 | -0.092258 | -0.06485 | -0.21664 | -0.17411 | 0.069041 | 0.029957 | 0.2466 | -0.014544 | -0.098336 | 122.9122 | 122.8448 | 122.8722 | 61.5111 | -122.9533 | 122.7629 | 122.9225 | 122.8387 | 61.5238 | -123.1537
234.0312 | 123.0469 | -61.5189 | 61.4182 | 1.4211e-13 | -0.0027627 | -0.010363 | 0.040025 | -0.021866 | 0.048867 | -0.0039678 | -0.011934 | 0.029476 | 0.044584 | -0.00036547 | 0.047006 | -61.386 | -0.007751 | -61.4947 | 61.3842 | 61.3167 | 61.3441 | -61.5351 | -61.4452 | -0.00422 | -61.5072 | 61.2349 | 61.3945 | 61.3061 | -61.7355 | -0.016259 | -0.033941 | 0.13288 | 0.024143 | 0.040402 | -0.10141 | -0.074006 | -0.21664 | -0.18326 | 0.073621 | 0.011644 | 0.22829 | -0.0237 | -0.11207 | 122.9031 | 122.8356 | 122.863 | 61.5111 | -122.9533 | 122.7537 | 122.9133 | 122.8249 | 61.5146 | -123.1537
235.7031 | 123.111 | -61.4822 | 61.3998 | 1.4211e-13 | -0.0027627 | -0.010577 | 0.039811 | -0.02208 | 0.048653 | 0.0036627 | -0.01172 | 0.029263 | 0.044584 | 0.00027553 | 0.047006 | -61.3814 | -0.016908 | -61.4993 | 61.3888 | 61.2984 | 61.3396 | -61.5305 | -61.4407 | 0.000359 | -61.4935 | 61.2349 | 61.399 | 61.2603 | -61.7447 | -0.048301 | -0.011051 | 0.10084 | -0.017056 | 0.031245 | -0.10142 | -0.060274 | -0.26242 | -0.16495 | 0.041579 | -0.011241 | 0.25118 | -0.000811 | -0.13955 | 122.871 | 122.7807 | 122.8218 | 61.4653 | -122.9304 | 122.7171 | 122.8813 | 122.7425 | 61.4826 | -123.1445
237.4062 | 123.1338 | -61.528 | 61.3083 | 1.4211e-13 | -0.0027627 | -0.011004 | 0.040025 | -0.02208 | 0.048653 | 0.0036627 | -0.012148 | 0.02969 | 0.044798 | -0.00015167 | 0.047219 | -61.3814 | -0.012329 | -61.4993 | 61.3934 | 61.3122 | 61.335 | -61.5305 | -61.4452 | 0.004938 | -61.4935 | 61.2349 | 61.399 | 61.3152 | -61.7401 | -0.002525 | 0.085079 | 0.14662 | 0.02872 | 0.031245 | 0.00387 | 0.0267 | -0.21207 | -0.073399 | 0.082776 | 0.034535 | 0.2466 | 0.090741 | 0.006949 | 122.9214 | 122.8402 | 122.863 | 61.5157 | -122.8388 | 122.7629 | 122.927 | 122.8433 | 61.533 | -123.0484
239.0938 | 123.1293 | -61.4868 | 61.377 | 1.4211e-13 | -0.0031901 | -0.010363 | 0.039598 | -0.021866 | 0.048653 | 0.011293 | -0.012148 | 0.02969 | 0.04437 | 6.1934e-05 | 0.047219 | -61.3814 | -0.007751 | -61.4947 | 61.3796 | 61.3076 | 61.335 | -61.526 | -61.4452 | -0.00422 | -61.4981 | 61.2349 | 61.4036 | 61.2878 | -61.7401 | -0.039145 | 0.00268 | 0.10542 | -0.007901 | 0.031244 | -0.069373 | -0.041964 | -0.25327 | -0.14206 | 0.041577 | -0.011243 | 0.24202 | 0.026656 | -0.089186 | 122.8664 | 122.7944 | 122.8218 | 61.4791 | -122.9029 | 122.7217 | 122.8904 | 122.7746 | 61.4826 | -123.117
240.7969 | 123.1338 | -61.5143 | 61.3403 | 1.4211e-13 | -0.0031901 | -0.010577 | 0.040025 | -0.02208 | 0.048867 | 0.011293 | -0.012148 | 0.029049 | 0.04437 | -0.00015167 | 0.047433 | -61.3768 | -0.016908 | -61.4947 | 61.3842 | 61.3122 | 61.335 | -61.5305 | -61.4498 | 0.004938 | -61.4935 | 61.244 | 61.4036 | 61.2969 | -61.7401 | -0.016258 | 0.043879 | 0.13746 | 0.019565 | 0.035823 | -0.028173 | -0.005343 | -0.2258 | -0.096285 | 0.064465 | 0.020802 | 0.2466 | 0.063277 | -0.043408 | 122.8985 | 122.8264 | 122.8493 | 61.4974 | -122.8709 | 122.7583 | 122.9179 | 122.8112 | 61.5192 | -123.0804
242.5 | 123.143 | -61.4456 | 61.3815 | 1.4211e-13 | -0.0029765 | -0.010577 | 0.040239 | -0.021653 | 0.048653 | 0.0036627 | -0.011934 | 0.029263 | 0.044584 | -0.00036547 | 0.047433 | -61.3768 | -0.012329 | -61.4856 | 61.3842 | 61.3122 | 61.335 | -61.526 | -61.4498 | 0.004938 | -61.4981 | 61.2395 | 61.399 | 61.3107 | -61.7355 | -0.080343 | 0.00268 | 0.068798 | -0.039942 | 0.040401 | -0.069372 | -0.046542 | -0.28989 | -0.14206 | -0.004199 | -0.052441 | 0.23745 | 0.017499 | -0.070871 | 122.8298 | 122.7578 | 122.7806 | 61.4333 | -122.9075 | 122.6851 | 122.8446 | 122.7563 | 61.4506 | -123.117
244.1875 | 123.0835 | -61.5097 | 61.3678 | 1.4211e-13 | -0.0031901 | -0.010363 | 0.039811 | -0.021653 | 0.04908 | 0.0036627 | -0.011934 | 0.029263 | 0.04437 | 6.1934e-05 | 0.047433 | -61.386 | -0.012329 | -61.4856 | 61.3796 | 61.3076 | 61.3396 | -61.526 | -61.4452 | 0.000359 | -61.4935 | 61.2395 | 61.4082 | 61.2969 | -61.7355 | -0.016256 | 0.011835 | 0.12373 | 0.024145 | 0.040401 | -0.060218 | -0.028231 | -0.2258 | -0.12833 | 0.064466 | 0.016225 | 0.24202 | 0.04039 | -0.070874 | 122.8893 | 122.8173 | 122.8493 | 61.4974 | -122.8938 | 122.7492 | 122.9179 | 122.8066 | 61.5101 | -123.1033
245.9219 | 123.143 | -61.5051 | 61.3174 | 1.4211e-13 | -0.0029765 | -0.01015 | 0.040025 | -0.021866 | 0.04908 | 0.011293 | -0.011934 | 0.029476 | 0.044584 | -0.00036547 | 0.047647 | -61.3768 | -0.012329 | -61.4856 | 61.3796 | 61.3122 | 61.3396 | -61.5214 | -61.4407 | 0.004938 | -61.4981 | 61.2349 | 61.399 | 61.274 | -61.7401 | -0.016255 | 0.062189 | 0.12831 | 0.019567 | 0.035822 | -0.005285 | 0.022123 | -0.23495 | -0.082554 | 0.064467 | 0.007068 | 0.24202 | 0.081586 | -0.043413 | 122.8848 | 122.8173 | 122.8447 | 61.4928 | -122.8388 | 122.74 | 122.9042 | 122.7792 | 61.5101 | -123.0575
247.6094 | 123.143 | -61.441 | 61.3861 | 1.4211e-13 | -0.0027627 | -0.011218 | 0.039811 | -0.021866 | 0.048653 | 0.0036627 | -0.012148 | 0.029263 | 0.044584 | -0.00015167 | 0.047433 | -61.3768 | -0.016908 | -61.4901 | 61.3842 | 61.303 | 61.3396 | -61.526 | -61.4452 | -0.00422 | -61.4935 | 61.2349 | 61.3945 | 61.3015 | -61.7309 | -0.084921 | -0.001897 | 0.06422 | -0.049099 | 0.035822 | -0.083107 | -0.046541 | -0.28988 | -0.15122 | -0.004199 | -0.05244 | 0.23745 | 0.008344 | -0.084605 | 122.8253 | 122.744 | 122.7806 | 61.4241 | -122.9121 | 122.6759 | 122.8355 | 122.7425 | 61.4368 | -123.117
249.3125 | 122.9874 | -61.5372 | 61.3815 | 1.4211e-13 | -0.0031901 | -0.010577 | 0.039811 | -0.02208 | 0.04908 | 0.0036627 | -0.011934 | 0.029476 | 0.044798 | 6.1934e-05 | 0.047647 | -61.3768 | -0.012329 | -61.4947 | 61.3888 | 61.3076 | 61.3396 | -61.5397 | -61.4452 | 0.004938 | -61.4843 | 61.2303 | 61.4082 | 61.3107 | -61.7218 | -0.002528 | 0.007259 | 0.16035 | 0.042453 | 0.044981 | -0.073951 | -0.041964 | -0.1846 | -0.15122 | 0.091931 | 0.052848 | 0.23745 | 0.026657 | -0.070871 | 122.926 | 122.8448 | 122.8767 | 61.5248 | -122.9212 | 122.7675 | 122.9454 | 122.8478 | 61.5421 | -123.1033
251.0156 | 122.9965 | -61.5189 | 61.322 | 1.4211e-13 | -0.0027627 | -0.010577 | 0.040239 | -0.021653 | 0.048653 | 0.0036627 | -0.012148 | 0.029476 | 0.044584 | 6.1934e-05 | 0.047647 | -61.3722 | -0.012329 | -61.4856 | 61.3796 | 61.3076 | 61.3304 | -61.526 | -61.4498 | -0.00422 | -61.4935 | 61.2349 | 61.3899 | 61.2649 | -61.7309 | -0.007101 | 0.057612 | 0.14662 | 0.0333 | 0.040401 | -0.014441 | 0.008389 | -0.21207 | -0.087131 | 0.069043 | 0.02538 | 0.23745 | 0.067852 | -0.057147 | 122.8985 | 122.8264 | 122.8493 | 61.5065 | -122.848 | 122.7537 | 122.9087 | 122.7837 | 61.5146 | -123.0529
252.7031 | 123.1201 | -61.4227 | 61.3998 | 1.4211e-13 | -0.0029765 | -0.010577 | 0.040025 | -0.02208 | 0.04908 | 0.0036627 | -0.011934 | 0.029263 | 0.044584 | 6.1934e-05 | 0.04786 | -61.3768 | -0.012329 | -61.481 | 61.3796 | 61.3076 | 61.335 | -61.526 | -61.4498 | -0.00422 | -61.4935 | 61.2303 | 61.3899 | 61.3015 | -61.7309 | -0.10323 | -0.020208 | 0.045909 | -0.058253 | 0.044979 | -0.092261 | -0.064852 | -0.3082 | -0.16953 | -0.027088 | -0.070751 | 0.23745 | -0.009968 | -0.098338 | 122.8024 | 122.7303 | 122.7577 | 61.4104 | -122.9258 | 122.653 | 122.8126 | 122.7242 | 61.4185 | -123.1308
254.4062 | 123.0698 | -61.4685 | 61.3586 | 1.4211e-13 | -0.0031901 | -0.010791 | 0.040025 | -0.021866 | 0.048867 | 0.011293 | -0.012361 | 0.029263 | 0.044584 | -0.00036547 | 0.047647 | -61.3722 | -0.012329 | -61.4764 | 61.3842 | 61.303 | 61.3304 | -61.5214 | -61.4361 | 0.000359 | -61.5026 | 61.2395 | 61.399 | 61.3015 | -61.7309 | -0.052876 | 0.025568 | 0.096264 | -0.007898 | 0.044978 | -0.055642 | -0.028233 | -0.26242 | -0.11917 | 0.032425 | -0.034131 | 0.22829 | 0.040387 | -0.05714 | 122.8527 | 122.7715 | 122.7989 | 61.4562 | -122.88 | 122.708 | 122.8675 | 122.77 | 61.4689 | -123.0896
256.0938 | 122.9828 | -61.5646 | 61.3632 | 1.4211e-13 | -0.0029765 | -0.010577 | 0.039811 | -0.021653 | 0.048867 | 0.011293 | -0.012148 | 0.029263 | 0.044584 | -0.00036547 | 0.047433 | -61.3677 | -0.007751 | -61.4856 | 61.3842 | 61.303 | 61.335 | -61.526 | -61.4452 | -0.00422 | -61.4889 | 61.2303 | 61.3945 | 61.2466 | -61.7218 | 0.038675 | 0.020991 | 0.19697 | 0.079076 | 0.040401 | -0.060219 | -0.028231 | -0.15713 | -0.13291 | 0.1194 | 0.075735 | 0.23287 | 0.031232 | -0.11666 | 122.9488 | 122.8676 | 122.8996 | 61.5569 | -122.8892 | 122.7949 | 122.9591 | 122.8112 | 61.5604 | -123.085
257.8594 | 123.0789 | -61.5051 | 61.3312 | 1.4211e-13 | -0.0031901 | -0.010791 | 0.040239 | -0.021653 | 0.048439 | 0.0036627 | -0.011934 | 0.029263 | 0.045011 | 6.1934e-05 | 0.047647 | -61.3722 | -0.012329 | -61.4718 | 61.3842 | 61.2938 | 61.3258 | -61.5168 | -61.4361 | 0.009516 | -61.4843 | 61.2395 | 61.3899 | 61.2649 | -61.7355 | -0.011677 | 0.053034 | 0.13289 | 0.033301 | 0.044978 | -0.037334 | -0.005346 | -0.23038 | -0.091709 | 0.069046 | 0.020805 | 0.25118 | 0.058696 | -0.066303 | 122.8893 | 122.799 | 122.831 | 61.4928 | -122.848 | 122.7446 | 122.895 | 122.77 | 61.5146 | -123.0667
259.5469 | 123.0515 | -61.4822 | 61.3861 | 1.4211e-13 | -0.0031901 | -0.010577 | 0.040025 | -0.021866 | 0.048867 | -0.0039678 | -0.012148 | 0.029476 | 0.044584 | 0.00027553 | 0.047219 | -61.3677 | -0.021486 | -61.481 | 61.3842 | 61.303 | 61.3258 | -61.526 | -61.4361 | 0.000359 | -61.4889 | 61.2257 | 61.3899 | 61.3015 | -61.7309 | -0.043722 | -0.001897 | 0.11458 | 0.001257 | 0.044979 | -0.083107 | -0.060277 | -0.24869 | -0.16038 | 0.046158 | -0.006662 | 0.24202 | 0.003765 | -0.084605 | 122.8665 | 122.7852 | 122.8081 | 61.4608 | -122.9121 | 122.708 | 122.8721 | 122.7837 | 61.4826 | -123.117
261.2812 | 122.9874 | -61.5372 | 61.3174 | 1.4211e-13 | -0.0025491 | -0.010791 | 0.040025 | -0.021866 | 0.048226 | 0.011293 | -0.011934 | 0.029049 | 0.04437 | 6.1934e-05 | 0.047433 | -61.3631 | -0.012329 | -61.4856 | 61.3751 | 61.303 | 61.335 | -61.526 | -61.4315 | 0.004938 | -61.4935 | 61.2257 | 61.4036 | 61.274 | -61.7263 | 0.011209 | 0.057611 | 0.17409 | 0.05161 | 0.040401 | -0.014443 | 0.017545 | -0.18918 | -0.091711 | 0.10567 | 0.04369 | 0.23287 | 0.086165 | -0.043413 | 122.9122 | 122.8402 | 122.8722 | 61.5248 | -122.8434 | 122.7629 | 122.9408 | 122.8112 | 61.5421 | -123.0438
262.9844 | 123.1247 | -61.4914 | 61.2991 | 1.4211e-13 | -0.0029765 | -0.010577 | 0.039811 | -0.021866 | 0.048867 | 0.0036627 | -0.012148 | 0.029263 | 0.044798 | 6.1934e-05 | 0.047006 | -61.3677 | -0.012329 | -61.4856 | 61.3751 | 61.303 | 61.3396 | -61.5168 | -61.4361 | 0.000359 | -61.4889 | 61.2303 | 61.3853 | 61.2969 | -61.7263 | -0.02541 | 0.075922 | 0.12373 | 0.005834 | 0.031244 | 0.003868 | 0.040434 | -0.23495 | -0.068822 | 0.055313 | 0.002493 | 0.23745 | 0.086162 | -0.002209 | 122.8664 | 122.7944 | 122.831 | 61.4791 | -122.8159 | 122.7217 | 122.8767 | 122.7883 | 61.4918 | -123.0255
264.6875 | 123.0743 | -61.5051 | 61.3312 | 1.4211e-13 | -0.0029765 | -0.010363 | 0.039811 | -0.02208 | 0.048867 | 0.0036627 | -0.012148 | 0.029263 | 0.04437 | -0.00036547 | 0.047647 | -61.3631 | -0.021486 | -61.481 | 61.3705 | 61.2984 | 61.335 | -61.5168 | -61.4315 | 0.004938 | -61.4843 | 61.2349 | 61.3945 | 61.3015 | -61.7218 | -0.011677 | 0.039299 | 0.14204 | 0.024145 | 0.035822 | -0.032755 | 0.003812 | -0.21664 | -0.096287 | 0.073624 | 0.020805 | 0.23745 | 0.063275 | -0.029674 | 122.8756 | 122.8035 | 122.8401 | 61.4836 | -122.848 | 122.74 | 122.8996 | 122.8066 | 61.5101 | -123.0529
266.375 | 123.111 | -61.5005 | 61.3129 | 1.4211e-13 | -0.0025491 | -0.01015 | 0.039811 | -0.021653 | 0.04908 | 0.0036627 | -0.01172 | 0.028835 | 0.04437 | 0.00027553 | 0.047219 | -61.3677 | -0.012329 | -61.481 | 61.3705 | 61.2984 | 61.3258 | -61.5168 | -61.4315 | 0.000359 | -61.4889 | 61.2349 | 61.3945 | 61.3015 | -61.7218 | -0.016255 | 0.05761 | 0.13289 | 0.019567 | 0.035822 | -0.014444 | 0.012965 | -0.22122 | -0.077976 | 0.069046 | 0.011648 | 0.23287 | 0.081586 | -0.011363 | 122.871 | 122.799 | 122.8264 | 61.4882 | -122.8297 | 122.7354 | 122.895 | 122.8021 | 61.5009 | -123.0346
268.0625 | 123.0743 | -61.4594 | 61.3861 | 1.4211e-13 | -0.0025491 | -0.010577 | 0.039811 | -0.02208 | 0.048653 | 0.0036627 | -0.012148 | 0.029476 | 0.044584 | 6.1934e-05 | 0.047006 | -61.3631 | -0.007751 | -61.481 | 61.3659 | 61.2938 | 61.3258 | -61.5168 | -61.4315 | 0.004938 | -61.4797 | 61.2212 | 61.399 | 61.2649 | -61.7218 | -0.057453 | -0.02021 | 0.096266 | -0.021631 | 0.035822 | -0.092265 | -0.060277 | -0.26242 | -0.16495 | 0.027848 | -0.020393 | 0.24202 | 0.012922 | -0.12123 | 122.8252 | 122.7532 | 122.7852 | 61.4516 | -122.9029 | 122.6805 | 122.8584 | 122.7242 | 61.4643 | -123.1079
269.75 | 122.9874 | -61.4594 | 61.4273 | 1.4211e-13 | -0.0029765 | -0.010577 | 0.039811 | -0.021653 | 0.048439 | 0.0036627 | -0.01172 | 0.028835 | 0.044584 | 6.1934e-05 | 0.047219 | -61.3631 | -0.021486 | -61.4764 | 61.3659 | 61.2984 | 61.3258 | -61.5214 | -61.4315 | 0.000359 | -61.4889 | 61.2166 | 61.3899 | 61.2969 | -61.7218 | -0.062031 | -0.061409 | 0.096266 | -0.017053 | 0.044978 | -0.12888 | -0.10148 | -0.26242 | -0.21073 | 0.027848 | -0.02955 | 0.23287 | -0.037434 | -0.13038 | 122.8252 | 122.7578 | 122.7852 | 61.4379 | -122.9487 | 122.6759 | 122.8492 | 122.7563 | 61.4597 | -123.1491
271.4531 | 123.1064 | -61.5189 | 61.3129 | 1.4211e-13 | -0.0031901 | -0.010363 | 0.040025 | -0.02208 | 0.048867 | 0.0036627 | -0.011934 | 0.029263 | 0.044798 | 6.1934e-05 | 0.047647 | -61.3631 | -0.003172 | -61.4718 | 61.3705 | 61.2984 | 61.335 | -61.5168 | -61.4269 | 0.000359 | -61.4843 | 61.2166 | 61.3899 | 61.2695 | -61.7309 | 0.002056 | 0.05761 | 0.15577 | 0.047034 | 0.044978 | -0.014444 | 0.022123 | -0.21207 | -0.09629 | 0.091936 | 0.034538 | 0.2466 | 0.077007 | -0.043414 | 122.8893 | 122.8173 | 122.8538 | 61.5157 | -122.8297 | 122.7354 | 122.9087 | 122.7883 | 61.5192 | -123.0438
273.1562 | 123.1064 | -61.4456 | 61.3678 | 1.4211e-13 | -0.0029765 | -0.010577 | 0.039811 | -0.021866 | 0.048653 | -0.0039678 | -0.012148 | 0.029263 | 0.04437 | 0.00027553 | 0.047219 | -61.3631 | -0.012329 | -61.4718 | 61.3659 | 61.2938 | 61.3213 | -61.5076 | -61.4315 | 0.000359 | -61.4843 | 61.2303 | 61.3945 | 61.2969 | -61.7263 | -0.062028 | -0.0019 | 0.082533 | -0.026208 | 0.03582 | -0.073955 | -0.046545 | -0.28073 | -0.13749 | 0.014115 | -0.038704 | 0.24202 | 0.026654 | -0.070874 | 122.8115 | 122.7395 | 122.7669 | 61.4333 | -122.8754 | 122.6759 | 122.8401 | 122.7425 | 61.446 | -123.0941
274.9062 | 123.0927 | -61.5097 | 61.3129 | 1.4211e-13 | -0.0027627 | -0.010363 | 0.039598 | -0.02208 | 0.048867 | 0.0036627 | -0.012148 | 0.029476 | 0.044584 | -0.00036547 | 0.047219 | -61.3585 | -0.007751 | -61.481 | 61.3659 | 61.2938 | 61.3304 | -61.5122 | -61.4223 | 0.000359 | -61.4752 | 61.2257 | 61.3899 | 61.2786 | -61.7172 | -0.00252 | 0.053032 | 0.1512 | 0.028723 | 0.031243 | -0.019023 | 0.017544 | -0.20748 | -0.087133 | 0.08736 | 0.03454 | 0.24202 | 0.077007 | -0.034256 | 122.8756 | 122.8035 | 122.8401 | 61.502 | -122.8251 | 122.7354 | 122.8996 | 122.7883 | 61.5101 | -123.0301
276.5938 | 123.0927 | -61.5143 | 61.3129 | 1.4211e-13 | -0.0031901 | -0.010577 | 0.040025 | -0.021653 | 0.04908 | 0.011293 | -0.011934 | 0.029263 | 0.044584 | 6.1934e-05 | 0.047433 | -61.3539 | -0.012329 | -61.4718 | 61.3751 | 61.2984 | 61.3304 | -61.5168 | -61.4223 | 0.004938 | -61.4752 | 61.2212 | 61.3807 | 61.3015 | -61.7218 | -0.002522 | 0.062189 | 0.16035 | 0.042456 | 0.044978 | -0.014444 | 0.017544 | -0.20748 | -0.091712 | 0.091937 | 0.039117 | 0.2466 | 0.06785 | -0.011363 | 122.8893 | 122.8127 | 122.8447 | 61.502 | -122.8297 | 122.7354 | 122.895 | 122.8158 | 61.5192 | -123.0346
278.2812 | 123.0881 | -61.4182 | 61.377 | 1.4211e-13 | -0.0029765 | -0.010363 | 0.039598 | -0.02208 | 0.048653 | 0.0036627 | -0.01172 | 0.029263 | 0.044584 | 0.00027553 | 0.047433 | -61.3631 | -0.016908 | -61.4672 | 61.3659 | 61.2984 | 61.3213 | -61.5031 | -61.4269 | 0.009516 | -61.4752 | 61.2166 | 61.3807 | 61.2923 | -61.7126 | -0.084915 | -0.011055 | 0.055067 | -0.049095 | 0.03582 | -0.078531 | -0.0557 | -0.29446 | -0.16038 | -0.008772 | -0.057013 | 0.23745 | 0.003763 | -0.084608 | 122.7841 | 122.7166 | 122.7394 | 61.4012 | -122.88 | 122.6347 | 122.7989 | 122.7105 | 61.4277 | -123.0896
279.9688 | 123.024 | -61.4731 | 61.3998 | 1.4211e-13 | -0.0029765 | -0.010577 | 0.039811 | -0.02208 | 0.048653 | 0.011293 | -0.012148 | 0.029049 | 0.045011 | 0.00048933 | 0.047433 | -61.3494 | -0.003172 | -61.4764 | 61.3659 | 61.2938 | 61.3167 | -61.5122 | -61.4269 | 0.000359 | -61.4797 | 61.2257 | 61.3807 | 61.274 | -61.7172 | -0.039142 | -0.033943 | 0.12373 | -0.003321 | 0.035821 | -0.106 | -0.083167 | -0.2441 | -0.17411 | 0.046159 | -0.006661 | 0.23744 | -0.019125 | -0.12581 | 122.839 | 122.7669 | 122.7898 | 61.4699 | -122.9121 | 122.6988 | 122.8538 | 122.7471 | 61.4734 | -123.117
281.6562 | 123.0881 | -61.4273 | 61.3586 | 1.4211e-13 | -0.0029765 | -0.010577 | 0.039811 | -0.022507 | 0.048653 | 0.0036627 | -0.012148 | 0.029049 | 0.044798 | 0.00027553 | 0.047433 | -61.3539 | -0.007751 | -61.4764 | 61.3613 | 61.2893 | 61.3213 | -61.5076 | -61.4223 | 0.000359 | -61.4797 | 61.2212 | 61.3761 | 61.2878 | -61.7126 | -0.080339 | 0.002677 | 0.073379 | -0.049097 | 0.031242 | -0.069379 | -0.03739 | -0.2853 | -0.13749 | 0.004962 | -0.052437 | 0.23287 | 0.017494 | -0.070876 | 122.7886 | 122.7166 | 122.7486 | 61.4196 | -122.8663 | 122.6485 | 122.8034 | 122.7151 | 61.4277 | -123.0713
283.3594 | 123.0652 | -61.4044 | 61.3586 | 1.4211e-13 | -0.0029765 | -0.010363 | 0.039598 | -0.021653 | 0.048653 | 0.0036627 | -0.01172 | 0.029476 | 0.044798 | 0.00027553 | 0.047433 | -61.3539 | -0.012329 | -61.4672 | 61.3659 | 61.2938 | 61.3258 | -61.5076 | -61.4315 | 0.004938 | -61.4752 | 61.2212 | 61.3807 | 61.2878 | -61.7218 | -0.10323 | 0.007255 | 0.050491 | -0.062828 | 0.040399 | -0.0648 | -0.032812 | -0.31735 | -0.13749 | -0.027084 | -0.070746 | 0.2466 | 0.022073 | -0.070876 | 122.7703 | 122.6983 | 122.7302 | 61.3921 | -122.8663 | 122.6256 | 122.7851 | 122.6922 | 61.4094 | -123.0804
285.0625 | 123.111 | -61.441 | 61.3541 | 1.4211e-13 | -0.0027627 | -0.010577 | 0.039811 | -0.021653 | 0.048653 | 0.011293 | -0.011507 | 0.029263 | 0.04437 | -0.00015167 | 0.047433 | -61.3585 | -0.016908 | -61.4718 | 61.3659 | 61.2893 | 61.3167 | -61.5076 | -61.4269 | 0.004938 | -61.4752 | 61.2166 | 61.3807 | 61.2786 | -61.7126 | -0.066606 | 0.011833 | 0.082533 | -0.030786 | 0.03582 | -0.064801 | -0.037391 | -0.27157 | -0.13749 | 0.014116 | -0.034125 | 0.23745 | 0.026651 | -0.075455 | 122.8069 | 122.7303 | 122.7577 | 61.4241 | -122.8617 | 122.6576 | 122.8218 | 122.7197 | 61.446 | -123.0667
286.7656 | 123.111 | -61.4365 | 61.3449 | 1.4211e-13 | -0.0025491 | -0.010363 | 0.039811 | -0.02208 | 0.048867 | 0.0036627 | -0.012148 | 0.029049 | 0.044584 | 6.1934e-05 | 0.047433 | -61.3448 | -0.012329 | -61.4672 | 61.3659 | 61.2893 | 61.3167 | -61.5076 | -61.4269 | 0.000359 | -61.4752 | 61.212 | 61.3807 | 61.2649 | -61.7172 | -0.071184 | 0.020988 | 0.091691 | -0.030785 | 0.040399 | -0.055646 | -0.028236 | -0.28073 | -0.13291 | 0.009538 | -0.038703 | 0.24202 | 0.035806 | -0.080036 | 122.8024 | 122.7257 | 122.7531 | 61.4241 | -122.8526 | 122.6485 | 122.8172 | 122.7013 | 61.4368 | -123.0621
288.4531 | 122.9599 | -61.5372 | 61.3632 | 1.4211e-13 | -0.0027627 | -0.01015 | 0.040025 | -0.021866 | 0.04908 | 0.0036627 | -0.01172 | 0.029049 | 0.04437 | 6.1934e-05 | 0.047647 | -61.3494 | -0.012329 | -61.4718 | 61.3567 | 61.2893 | 61.3213 | -61.4985 | -61.4269 | 0.000359 | -61.4797 | 61.212 | 61.3716 | 61.274 | -61.7172 | 0.038682 | -0.006479 | 0.18782 | 0.065344 | 0.026662 | -0.073956 | -0.041967 | -0.18002 | -0.15122 | 0.11025 | 0.057426 | 0.23744 | 0.008339 | -0.089189 | 122.8939 | 122.8264 | 122.8584 | 61.5248 | -122.8617 | 122.7492 | 122.9087 | 122.8112 | 61.5375 | -123.0804
290.1719 | 122.9645 | -61.5326 | 61.322 | 1.4211e-13 | -0.0027627 | -0.010363 | 0.039811 | -0.02208 | 0.048867 | 0.011293 | -0.01172 | 0.029263 | 0.044584 | 0.00027553 | 0.047219 | -61.3494 | -0.007751 | -61.4627 | 61.3659 | 61.2893 | 61.3213 | -61.5031 | -61.4178 | 0.000359 | -61.4706 | 61.212 | 61.3716 | 61.2649 | -61.7126 | 0.029526 | 0.043877 | 0.18324 | 0.069924 | 0.040398 | -0.032757 | -0.000768 | -0.18002 | -0.11002 | 0.11483 | 0.062007 | 0.24202 | 0.049538 | -0.057147 | 122.8985 | 122.8219 | 122.8538 | 61.5248 | -122.8251 | 122.7446 | 122.9042 | 122.7975 | 61.533 | -123.0346
291.9219 | 123.0331 | -61.4731 | 61.3449 | 1.4211e-13 | -0.0029765 | -0.01015 | 0.040025 | -0.021866 | 0.048653 | 0.011293 | -0.011934 | 0.029476 | 0.044798 | 0.00027553 | 0.047219 | -61.3494 | -0.016908 | -61.4627 | 61.3613 | 61.2893 | 61.3167 | -61.5031 | -61.4223 | 0.000359 | -61.4706 | 61.1983 | 61.3807 | 61.274 | -61.7126 | -0.029984 | 0.01641 | 0.12373 | 0.010414 | 0.040398 | -0.055646 | -0.028236 | -0.23953 | -0.14665 | 0.050738 | 0.002497 | 0.24202 | 0.035806 | -0.070879 | 122.8344 | 122.7623 | 122.7898 | 61.4562 | -122.848 | 122.6713 | 122.8538 | 122.7471 | 61.4734 | -123.0575
293.6562 | 122.9599 | -61.4685 | 61.4044 | 1.4211e-13 | -0.0029765 | -0.010363 | 0.039598 | -0.021866 | 0.048867 | 0.0036627 | -0.011507 | 0.029476 | 0.044798 | 6.1934e-05 | 0.047647 | -61.3494 | -0.016908 | -61.4718 | 61.3613 | 61.2847 | 61.3167 | -61.5122 | -61.4223 | -0.00422 | -61.4706 | 61.2166 | 61.3716 | 61.2923 | -61.7035 | -0.043719 | -0.043099 | 0.11916 | -0.00332 | 0.040399 | -0.11973 | -0.087745 | -0.23495 | -0.18784 | 0.046161 | -0.00208 | 0.23287 | -0.03286 | -0.11207 | 122.8298 | 122.7532 | 122.7852 | 61.4516 | -122.9166 | 122.6851 | 122.8401 | 122.7609 | 61.4643 | -123.1079
295.3438 | 123.024 | -61.4685 | 61.3129 | 1.4211e-13 | -0.0029765 | -0.010577 | 0.039598 | -0.021653 | 0.04908 | -0.0039678 | -0.011934 | 0.029263 | 0.044584 | 6.1934e-05 | 0.047433 | -61.3402 | -0.007751 | -61.4535 | 61.3613 | 61.2893 | 61.3258 | -61.5122 | -61.4178 | 0.000359 | -61.4706 | 61.212 | 61.3807 | 61.2923 | -61.7172 | -0.043719 | 0.048454 | 0.12831 | 0.014993 | 0.058712 | -0.023602 | 0.012965 | -0.24868 | -0.10087 | 0.05074 | -0.00208 | 0.2466 | 0.06785 | -0.020521 | 122.8298 | 122.7578 | 122.7943 | 61.4608 | -122.8251 | 122.6805 | 122.8492 | 122.7609 | 61.4689 | -123.0301
297.0312 | 123.0606 | -61.4319 | 61.3541 | 1.4211e-13 | -0.0027627 | -0.011004 | 0.039384 | -0.021866 | 0.048439 | 0.011293 | -0.011507 | 0.029049 | 0.044584 | 0.00027553 | 0.047219 | -61.3494 | -0.007751 | -61.4581 | 61.3476 | 61.2893 | 61.3167 | -61.4939 | -61.4132 | 0.004938 | -61.4797 | 61.2166 | 61.3761 | 61.2786 | -61.7126 | -0.062024 | -0.006481 | 0.082535 | -0.026206 | 0.035818 | -0.064801 | -0.037391 | -0.28072 | -0.13749 | 0.018697 | -0.047859 | 0.23287 | 0.022072 | -0.075455 | 122.7795 | 122.7211 | 122.7486 | 61.4241 | -122.848 | 122.6485 | 122.808 | 122.7105 | 61.4368 | -123.0667
298.75 | 122.9965 | -61.5417 | 61.3129 | 1.4211e-13 | -0.0027627 | -0.011004 | 0.039811 | -0.02208 | 0.048867 | 0.0036627 | -0.011934 | 0.029476 | 0.044584 | 6.1934e-05 | 0.047433 | -61.3448 | -0.007751 | -61.4627 | 61.3567 | 61.2938 | 61.3121 | -61.5076 | -61.4223 | 0.004938 | -61.4614 | 61.212 | 61.3716 | 61.2649 | -61.708 | 0.034102 | 0.043875 | 0.19698 | 0.079079 | 0.044977 | -0.019023 | -0.00077 | -0.16628 | -0.10087 | 0.1194 | 0.080319 | 0.2466 | 0.058693 | -0.047992 | 122.8985 | 122.8356 | 122.8538 | 61.534 | -122.8205 | 122.7537 | 122.9133 | 122.8066 | 61.5467 | -123.0209
300.4531 | 123.0469 | -61.4822 | 61.3037 | 1.4211e-13 | -0.0025491 | -0.010791 | 0.039811 | -0.021866 | 0.048653 | 0.0036627 | -0.01172 | 0.029049 | 0.044798 | 6.1934e-05 | 0.047433 | -61.3448 | -0.016908 | -61.4581 | 61.3613 | 61.2847 | 61.3213 | -61.5076 | -61.4086 | 0.004938 | -61.4614 | 61.2074 | 61.3761 | 61.2878 | -61.708 | -0.025407 | 0.057609 | 0.13747 | 0.024148 | 0.049555 | -0.019026 | 0.017542 | -0.22579 | -0.096292 | 0.07363 | 0.02081 | 0.2466 | 0.072426 | -0.015944 | 122.8436 | 122.7669 | 122.8035 | 61.4653 | -122.8114 | 122.6897 | 122.8584 | 122.77 | 61.4872 | -123.0117
302.1562 | 123.0194 | -61.4685 | 61.2946 | 1.4211e-13 | -0.0025491 | -0.010577 | 0.039811 | -0.02208 | 0.04908 | -0.0039678 | -0.011934 | 0.029263 | 0.044798 | 0.00027553 | 0.047219 | -61.3448 | -0.007751 | -61.4581 | 61.3567 | 61.2847 | 61.3121 | -61.4985 | -61.4086 | 0.000359 | -61.4706 | 61.212 | 61.3716 | 61.2832 | -61.708 | -0.029982 | 0.062185 | 0.12373 | 0.010415 | 0.040397 | -0.009871 | 0.01754 | -0.23953 | -0.082559 | 0.059897 | -0.00208 | 0.23745 | 0.077003 | -0.011368 | 122.8252 | 122.7532 | 122.7806 | 61.4608 | -122.793 | 122.6805 | 122.8401 | 122.7517 | 61.4689 | -123.0026
303.9062 | 122.9416 | -61.4456 | 61.3953 | 1.4211e-13 | -0.0027627 | -0.010791 | 0.039811 | -0.021866 | 0.048439 | 0.011293 | -0.012361 | 0.029263 | 0.044584 | 0.00027553 | 0.047006 | -61.3402 | -0.012329 | -61.4535 | 61.3522 | 61.2801 | 61.3167 | -61.5031 | -61.4132 | 0.004938 | -61.466 | 61.2028 | 61.3716 | 61.2878 | -61.7035 | -0.057449 | -0.043101 | 0.10543 | -0.007895 | 0.049554 | -0.11516 | -0.07859 | -0.25783 | -0.19242 | 0.03243 | -0.02039 | 0.23744 | -0.023705 | -0.1075 | 122.7978 | 122.7257 | 122.7623 | 61.4333 | -122.8983 | 122.6485 | 122.8172 | 122.7334 | 61.4506 | -123.0987
305.5938 | 122.9553 | -61.4548 | 61.4136 | 1.4211e-13 | -0.0025491 | -0.010363 | 0.039811 | -0.02208 | 0.048439 | -0.0039678 | -0.011934 | 0.029476 | 0.044584 | 6.1934e-05 | 0.047219 | -61.331 | -0.007751 | -61.4535 | 61.3522 | 61.2847 | 61.3121 | -61.4939 | -61.4086 | 0.004938 | -61.4706 | 61.1937 | 61.3716 | 61.2832 | -61.708 | -0.039136 | -0.061411 | 0.12374 | 0.00126 | 0.040396 | -0.12889 | -0.10148 | -0.25326 | -0.21989 | 0.046164 | -0.015813 | 0.23745 | -0.042015 | -0.13039 | 122.8069 | 122.7395 | 122.7669 | 61.447 | -122.9075 | 122.6485 | 122.8263 | 122.738 | 61.4597 | -123.1216
307.2969 | 122.9553 | -61.4273 | 61.3953 | 1.4211e-13 | -0.0029765 | -0.011004 | 0.039811 | -0.021866 | 0.048653 | -0.0039678 | -0.012148 | 0.029476 | 0.044584 | 6.1934e-05 | 0.047433 | -61.3402 | -0.016908 | -61.4581 | 61.3567 | 61.2893 | 61.3167 | -61.4939 | -61.4132 | 0.000359 | -61.466 | 61.212 | 61.367 | 61.2832 | -61.708 | -0.066602 | -0.038523 | 0.087114 | -0.030784 | 0.035818 | -0.106 | -0.07859 | -0.28072 | -0.18327 | 0.014119 | -0.038701 | 0.24202 | -0.028284 | -0.11208 | 122.784 | 122.7166 | 122.744 | 61.4104 | -122.8892 | 122.6393 | 122.7943 | 122.7105 | 61.4277 | -123.1033
308.9844 | 122.9553 | -61.4273 | 61.3861 | 1.4211e-13 | -0.0025491 | -0.010363 | 0.039811 | -0.02208 | 0.048867 | -0.0039678 | -0.011934 | 0.029476 | 0.044798 | 0.00027553 | 0.047219 | -61.3402 | -0.016908 | -61.4535 | 61.3567 | 61.2847 | 61.3167 | -61.4939 | -61.4178 | -0.00422 | -61.4569 | 61.1983 | 61.3624 | 61.274 | -61.7126 | -0.066602 | -0.029367 | 0.087114 | -0.026206 | 0.040396 | -0.10142 | -0.069434 | -0.2853 | -0.18785 | 0.009541 | -0.029543 | 0.25576 | -0.023706 | -0.11208 | 122.784 | 122.712 | 122.744 | 61.4104 | -122.88 | 122.6256 | 122.7897 | 122.7013 | 61.4231 | -123.0987
310.6875 | 122.9324 | -61.5051 | 61.3358 | 1.4211e-13 | -0.0029765 | -0.010791 | 0.040025 | -0.02208 | 0.048867 | 0.0036627 | -0.01172 | 0.029049 | 0.044798 | 0.00048933 | 0.047647 | -61.3356 | -0.012329 | -61.4489 | 61.3522 | 61.2801 | 61.3121 | -61.5031 | -61.404 | 0.004938 | -61.4614 | 61.2074 | 61.3716 | 61.2923 | -61.7126 | 0.00206 | 0.016409 | 0.16951 | 0.056193 | 0.054133 | -0.055648 | -0.023658 | -0.20748 | -0.12833 | 0.1011 | 0.043698 | 0.25118 | 0.035805 | -0.043409 | 122.8573 | 122.7852 | 122.8172 | 61.4928 | -122.8388 | 122.7125 | 122.8767 | 122.7975 | 61.5101 | -123.0484
312.3906 | 122.9691 | -61.5189 | 61.2671 | 1.4211e-13 | -0.0025491 | -0.010577 | 0.039384 | -0.022294 | 0.048867 | 0.0036627 | -0.011934 | 0.029049 | 0.04437 | 0.00027553 | 0.047219 | -61.3356 | -0.003172 | -61.4581 | 61.3567 | 61.2801 | 61.3121 | -61.5031 | -61.404 | 0.004938 | -61.466 | 61.2028 | 61.3716 | 61.2832 | -61.708 | 0.015793 | 0.089651 | 0.18324 | 0.060769 | 0.044976 | 0.013016 | 0.045006 | -0.18917 | -0.06425 | 0.11483 | 0.052852 | 0.24202 | 0.10447 | 0.016098 | 122.8756 | 122.799 | 122.831 | 61.5157 | -122.7702 | 122.7217 | 122.8904 | 122.802 | 61.5238 | -122.9751
314.0781 | 123.0698 | -61.4731 | 61.2671 | 1.4211e-13 | -0.0023355 | -0.010577 | 0.039598 | -0.02208 | 0.048439 | 0.011293 | -0.01172 | 0.029049 | 0.044584 | 6.1934e-05 | 0.047433 | -61.331 | -0.012329 | -61.4489 | 61.3522 | 61.2847 | 61.3121 | -61.4893 | -61.4132 | 0.000359 | -61.4614 | 61.1983 | 61.367 | 61.2603 | -61.6989 | -0.016247 | 0.085073 | 0.14205 | 0.024149 | 0.040396 | 0.017595 | 0.045006 | -0.22579 | -0.068828 | 0.059895 | 0.011654 | 0.23744 | 0.09989 | -0.006795 | 122.8252 | 122.7578 | 122.7852 | 61.4608 | -122.7564 | 122.6713 | 122.8401 | 122.7334 | 61.4734 | -122.966
315.7656 | 123.0011 | -61.441 | 61.322 | 1.4211e-13 | -0.0023355 | -0.010363 | 0.039598 | -0.02208 | 0.048439 | 0.011293 | -0.01172 | 0.029263 | 0.044798 | 6.1934e-05 | 0.047006 | -61.331 | -0.007751 | -61.4489 | 61.3476 | 61.2801 | 61.3121 | -61.4893 | -61.4086 | -0.00422 | -61.4477 | 61.1983 | 61.3716 | 61.2786 | -61.7035 | -0.04829 | 0.025563 | 0.11 | -0.007894 | 0.040396 | -0.041915 | -0.009925 | -0.26241 | -0.12376 | 0.032431 | -0.006653 | 0.25576 | 0.049538 | -0.043411 | 122.7886 | 122.7211 | 122.7531 | 61.4333 | -122.8114 | 122.6393 | 122.8126 | 122.7197 | 61.4368 | -123.0255
317.4531 | 123.0606 | -61.409 | 61.3678 | 1.4211e-13 | -0.0025491 | -0.010577 | 0.039598 | -0.022294 | 0.048439 | -0.0039678 | -0.01172 | 0.028835 | 0.044584 | 0.00027553 | 0.047006 | -61.3356 | -0.007751 | -61.4489 | 61.343 | 61.2755 | 61.3075 | -61.4985 | -61.3995 | 0.009516 | -61.4569 | 61.1983 | 61.367 | 61.274 | -61.7035 | -0.089491 | -0.024792 | 0.073382 | -0.039937 | 0.049554 | -0.092271 | -0.060281 | -0.29445 | -0.16954 | 0.009545 | -0.047853 | 0.2466 | -0.000818 | -0.093767 | 122.752 | 122.6845 | 122.7165 | 61.4012 | -122.8663 | 122.6073 | 122.776 | 122.683 | 61.4185 | -123.0712
319.1406 | 122.9233 | -61.4456 | 61.3861 | 1.4211e-13 | -0.0027627 | -0.01015 | 0.039384 | -0.021866 | 0.048867 | 0.018923 | -0.011934 | 0.029049 | 0.044584 | 0.00027553 | 0.047647 | -61.3356 | -0.007751 | -61.4489 | 61.343 | 61.2755 | 61.3075 | -61.4802 | -61.4132 | 0.004938 | -61.4569 | 61.1937 | 61.3624 | 61.2786 | -61.7035 | -0.034554 | -0.043102 | 0.11 | -0.003316 | 0.031238 | -0.11058 | -0.078591 | -0.25783 | -0.19243 | 0.03243 | -0.011232 | 0.2466 | -0.023706 | -0.1075 | 122.7886 | 122.7211 | 122.7531 | 61.4379 | -122.8663 | 122.6393 | 122.808 | 122.7242 | 61.4506 | -123.0896
320.8281 | 122.9645 | -61.4594 | 61.3495 | 1.4211e-13 | -0.0027627 | -0.010791 | 0.039598 | -0.021866 | 0.048653 | 0.0036627 | -0.012148 | 0.029263 | 0.044584 | 6.1934e-05 | 0.047433 | -61.331 | -0.007751 | -61.4489 | 61.3476 | 61.2755 | 61.3121 | -61.4893 | -61.4132 | 0.004938 | -61.4523 | 61.1983 | 61.3624 | 61.2832 | -61.708 | -0.029979 | -0.001903 | 0.12832 | 0.010417 | 0.040396 | -0.07396 | -0.037391 | -0.24868 | -0.15123 | 0.046163 | 0.007079 | 0.25576 | 0.012915 | -0.066299 | 122.8069 | 122.7349 | 122.7714 | 61.4516 | -122.8388 | 122.6576 | 122.8218 | 122.7425 | 61.4643 | -123.0575
322.5625 | 123.056 | -61.4777 | 61.2579 | 1.4211e-13 | -0.0025491 | -0.01015 | 0.039598 | -0.02208 | 0.048439 | 0.011293 | -0.011934 | 0.029049 | 0.04437 | 0.00048933 | 0.047219 | -61.3265 | -0.007751 | -61.4489 | 61.343 | 61.2755 | 61.3121 | -61.4939 | -61.3995 | 0.000359 | -61.4614 | 61.2028 | 61.3578 | 61.274 | -61.708 | -0.016248 | 0.085071 | 0.1512 | 0.028727 | 0.044975 | 0.017592 | 0.054161 | -0.23037 | -0.055095 | 0.078209 | 0.016232 | 0.2466 | 0.099888 | 0.016096 | 122.8207 | 122.7532 | 122.7898 | 61.4699 | -122.7518 | 122.6805 | 122.8355 | 122.7517 | 61.478 | -122.966
324.2656 | 123.0148 | -61.4502 | 61.2946 | 1.4211e-13 | -0.0023355 | -0.010577 | 0.039598 | -0.02208 | 0.048867 | -0.0039678 | -0.011934 | 0.029476 | 0.04437 | 0.00027553 | 0.047433 | -61.3265 | -0.016908 | -61.4444 | 61.343 | 61.2755 | 61.3075 | -61.4893 | -61.404 | -0.00422 | -61.4523 | 61.1983 | 61.3624 | 61.2695 | -61.6989 | -0.039135 | 0.04845 | 0.12374 | 0.005839 | 0.044974 | -0.019029 | 0.012961 | -0.24868 | -0.096294 | 0.046165 | -0.002077 | 0.2466 | 0.067846 | -0.025104 | 122.7932 | 122.7257 | 122.7577 | 61.4333 | -122.7839 | 122.6485 | 122.8126 | 122.7196 | 61.446 | -122.9934
325.9844 | 122.9416 | -61.4136 | 61.3953 | 1.4211e-13 | -0.0023355 | -0.010791 | 0.03917 | -0.022294 | 0.048867 | 0.0036627 | -0.012361 | 0.029049 | 0.044584 | 6.1934e-05 | 0.04786 | -61.3265 | -0.007751 | -61.4398 | 61.343 | 61.2755 | 61.3121 | -61.4893 | -61.3995 | 0.000359 | -61.4523 | 61.2028 | 61.3532 | 61.274 | -61.6989 | -0.075756 | -0.052258 | 0.087116 | -0.026204 | 0.049552 | -0.11974 | -0.083168 | -0.2853 | -0.19242 | 0.014122 | -0.038698 | 0.2466 | -0.04202 | -0.12123 | 122.7566 | 122.6891 | 122.7257 | 61.4058 | -122.8846 | 122.6164 | 122.7668 | 122.6876 | 61.4139 | -123.0941
327.6719 | 123.0148 | -61.4639 | 61.2488 | 1.4211e-13 | -0.0025491 | -0.010363 | 0.039384 | -0.022294 | 0.04908 | 0.0036627 | -0.01172 | 0.029263 | 0.044584 | 6.1934e-05 | 0.047647 | -61.3265 | -0.007751 | -61.4444 | 61.343 | 61.2755 | 61.3075 | -61.4893 | -61.404 | 0.004938 | -61.4569 | 61.1983 | 61.3624 | 61.274 | -61.6943 | -0.025402 | 0.094227 | 0.13747 | 0.019572 | 0.044974 | 0.026748 | 0.058738 | -0.23037 | -0.050517 | 0.059898 | 0.007078 | 0.23744 | 0.11362 | 0.025252 | 122.8069 | 122.7395 | 122.7714 | 61.4562 | -122.7381 | 122.6622 | 122.8263 | 122.738 | 61.4689 | -122.9431
329.375 | 122.9691 | -61.4868 | 61.3586 | 1.4211e-13 | -0.0027627 | -0.010363 | 0.039598 | -0.02208 | 0.048439 | 0.018923 | -0.011934 | 0.029263 | 0.044584 | 0.00027553 | 0.047219 | -61.3219 | -0.012329 | -61.4535 | 61.3384 | 61.2755 | 61.3075 | -61.4893 | -61.3995 | 0.000359 | -61.4431 | 61.1937 | 61.3532 | 61.274 | -61.6943 | -0.002514 | -0.020215 | 0.16494 | 0.033303 | 0.035817 | -0.083116 | -0.051126 | -0.20748 | -0.16496 | 0.087364 | 0.043702 | 0.25118 | -0.005399 | -0.084612 | 122.8252 | 122.7623 | 122.7943 | 61.4745 | -122.848 | 122.6805 | 122.8401 | 122.7608 | 61.4872 | -123.0529
331.0781 | 122.9324 | -61.5005 | 61.3266 | 1.4211e-13 | -0.0029765 | -0.010577 | 0.039598 | -0.02208 | 0.048867 | 0.011293 | -0.011934 | 0.029476 | 0.044798 | 0.00048933 | 0.047219 | -61.3265 | -0.012329 | -61.4444 | 61.3476 | 61.2755 | 61.3029 | -61.4893 | -61.3995 | 0.000359 | -61.4523 | 61.1891 | 61.3532 | 61.274 | -61.6989 | 0.011219 | 0.020985 | 0.17409 | 0.056193 | 0.044974 | -0.051072 | -0.023661 | -0.19832 | -0.13749 | 0.1011 | 0.048277 | 0.2466 | 0.026645 | -0.052568 | 122.8481 | 122.7761 | 122.8035 | 61.4882 | -122.8159 | 122.6897 | 122.8538 | 122.7746 | 61.5009 | -123.0255
332.7812 | 123.0194 | -61.4731 | 61.3083 | 1.4211e-13 | -0.0027627 | -0.01015 | 0.039811 | -0.02208 | 0.048653 | 0.0036627 | -0.01172 | 0.029263 | 0.04437 | 0.00027553 | 0.047433 | -61.331 | -0.016908 | -61.4398 | 61.3338 | 61.2664 | 61.2984 | -61.4756 | -61.3949 | 0.004938 | -61.4523 | 61.1983 | 61.3578 | 61.2695 | -61.6943 | -0.00251 | 0.02556 | 0.14205 | 0.033305 | 0.035815 | -0.04192 | -0.009929 | -0.22121 | -0.11003 | 0.07821 | 0.020811 | 0.24202 | 0.049534 | -0.038837 | 122.8069 | 122.7395 | 122.7714 | 61.4562 | -122.7839 | 122.6713 | 122.8309 | 122.7425 | 61.478 | -123.0026
334.5 | 123.0194 | -61.4319 | 61.3495 | 1.4211e-13 | -0.0027627 | -0.010577 | 0.039811 | -0.02208 | 0.048439 | 0.0036627 | -0.01172 | 0.029263 | 0.044798 | 0.00027553 | 0.047433 | -61.3265 | -0.012329 | -61.4398 | 61.3338 | 61.2664 | 61.2984 | -61.4802 | -61.3949 | 0.004938 | -61.4523 | 61.1937 | 61.3624 | 61.2786 | -61.6989 | -0.048287 | -0.015638 | 0.10543 | -0.007893 | 0.040394 | -0.083118 | -0.051127 | -0.26699 | -0.1558 | 0.037012 | -0.020387 | 0.2466 | 0.012915 | -0.070877 | 122.7657 | 122.6983 | 122.7302 | 61.4196 | -122.8297 | 122.6256 | 122.7943 | 122.7105 | 61.4368 | -123.0484
336.2188 | 122.9691 | -61.4456 | 61.3449 | 1.4211e-13 | -0.0025491 | -0.010577 | 0.040025 | -0.02208 | 0.048867 | 0.011293 | -0.011934 | 0.029476 | 0.044798 | 0.00027553 | 0.047219 | -61.3265 | -0.012329 | -61.4398 | 61.3384 | 61.2755 | 61.3029 | -61.4893 | -61.3949 | 0.000359 | -61.4431 | 61.1891 | 61.3487 | 61.2099 | -61.6989 | -0.043712 | -0.006482 | 0.11916 | 0.00584 | 0.049552 | -0.069383 | -0.041972 | -0.25325 | -0.15581 | 0.050745 | 0.002504 | 0.25576 | 0.003756 | -0.13498 | 122.784 | 122.7211 | 122.7486 | 61.4333 | -122.8342 | 122.6347 | 122.7943 | 122.6555 | 61.446 | -123.0438
337.9062 | 123.0423 | -61.4456 | 61.2671 | 1.4211e-13 | -0.0027627 | -0.01015 | 0.039811 | -0.02208 | 0.048867 | 0.0036627 | -0.011934 | 0.029049 | 0.044798 | 0.00027553 | 0.047006 | -61.3219 | -0.007751 | -61.4352 | 61.343 | 61.2664 | 61.3029 | -61.4848 | -61.3995 | 0.009516 | -61.4477 | 61.1937 | 61.3624 | 61.2695 | -61.6943 | -0.039133 | 0.075916 | 0.12374 | 0.010419 | 0.049552 | -0.000721 | 0.035848 | -0.24868 | -0.073407 | 0.046166 | -0.002075 | 0.2466 | 0.095312 | 0.002362 | 122.7886 | 122.712 | 122.7486 | 61.4379 | -122.7518 | 122.6393 | 122.808 | 122.7151 | 61.4551 | -122.9614
339.5938 | 123.0423 | -61.3724 | 61.3449 | 1.4211e-13 | -0.0027627 | -0.010577 | 0.039811 | -0.02208 | 0.048653 | 0.011293 | -0.012148 | 0.029263 | 0.044584 | 0.00048933 | 0.047219 | -61.3219 | -0.012329 | -61.4398 | 61.3384 | 61.2664 | 61.2984 | -61.4802 | -61.3949 | 0.000359 | -61.4431 | 61.1891 | 61.3441 | 61.2695 | -61.6943 | -0.1078 | -0.006482 | 0.050496 | -0.067403 | 0.040394 | -0.078541 | -0.04655 | -0.32192 | -0.15581 | -0.022498 | -0.070739 | 0.25118 | -0.000823 | -0.075458 | 122.7108 | 122.6387 | 122.6707 | 61.36 | -122.8251 | 122.5615 | 122.7165 | 122.6418 | 61.3727 | -123.0392
341.2812 | 122.9553 | -61.4594 | 61.3403 | 1.4211e-13 | -0.0027627 | -0.010577 | 0.039811 | -0.021866 | 0.048867 | -0.0039678 | -0.012148 | 0.029049 | 0.044798 | 0.00048933 | 0.047219 | -61.3265 | -0.012329 | -61.4306 | 61.3384 | 61.2755 | 61.3075 | -61.4802 | -61.3949 | 0.004938 | -61.4477 | 61.1845 | 61.3578 | 61.2649 | -61.6897 | -0.020821 | -0.001904 | 0.13289 | 0.02873 | 0.049551 | -0.064805 | -0.032815 | -0.23036 | -0.15581 | 0.064478 | 0.011658 | 0.24202 | 0.017491 | -0.075458 | 122.7978 | 122.7349 | 122.7669 | 61.447 | -122.8205 | 122.6439 | 122.8172 | 122.7242 | 61.4643 | -123.03
343 | 122.9095 | -61.4868 | 61.2991 | 1.4211e-13 | -0.0027627 | -0.010363 | 0.039384 | -0.02208 | 0.048867 | 0.011293 | -0.012148 | 0.029049 | 0.04437 | 0.00027553 | 0.047006 | -61.3265 | -0.007751 | -61.4352 | 61.3384 | 61.2664 | 61.2938 | -61.4802 | -61.3995 | -0.00422 | -61.4477 | 61.1891 | 61.3532 | 61.2649 | -61.6897 | 0.006644 | 0.039295 | 0.16036 | 0.051617 | 0.044973 | -0.032764 | -0.005352 | -0.2029 | -0.11003 | 0.087364 | 0.039123 | 0.24202 | 0.054111 | -0.034259 | 122.8252 | 122.7532 | 122.7806 | 61.4791 | -122.7793 | 122.6759 | 122.8401 | 122.7517 | 61.4826 | -122.9888
344.6875 | 122.8912 | -61.5189 | 61.2991 | 1.4211e-13 | -0.0025491 | -0.010577 | 0.039598 | -0.02208 | 0.048653 | 0.011293 | -0.012148 | 0.028835 | 0.044584 | 6.1934e-05 | 0.047219 | -61.3219 | -0.003172 | -61.4352 | 61.3293 | 61.2664 | 61.3029 | -61.4802 | -61.3995 | 0.000359 | -61.4431 | 61.1891 | 61.3578 | 61.2695 | -61.6897 | 0.038688 | 0.030138 | 0.19698 | 0.083661 | 0.044973 | -0.032764 | 0.003805 | -0.17086 | -0.11003 | 0.11941 | 0.075746 | 0.2466 | 0.05869 | -0.029681 | 122.8481 | 122.7852 | 122.8218 | 61.5157 | -122.7793 | 122.708 | 122.8767 | 122.7883 | 61.5192 | -122.9888
346.375 | 123.024 | -61.4731 | 61.2625 | 1.4211e-13 | -0.0025491 | -0.010363 | 0.039384 | -0.022294 | 0.048653 | -0.0039678 | -0.011934 | 0.029049 | 0.044584 | 6.1934e-05 | 0.047433 | -61.3265 | -0.012329 | -61.4306 | 61.3384 | 61.2664 | 61.2984 | -61.4848 | -61.3903 | 0.004938 | -61.4385 | 61.1891 | 61.3578 | 61.274 | -61.6897 | -0.011668 | 0.075916 | 0.14663 | 0.042462 | 0.05413 | 0.003857 | 0.035848 | -0.21663 | -0.073407 | 0.082789 | 0.034548 | 0.25118 | 0.095311 | 0.011519 | 122.8115 | 122.7395 | 122.7714 | 61.4608 | -122.7473 | 122.6622 | 122.8309 | 122.7471 | 61.478 | -122.9522
348.0625 | 122.9736 | -61.4685 | 61.3083 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.040025 | -0.021866 | 0.048653 | 0.0036627 | -0.01172 | 0.029049 | 0.044798 | 0.00027553 | 0.047433 | -61.3127 | -0.016908 | -61.4352 | 61.3293 | 61.2572 | 61.2984 | -61.4756 | -61.3903 | 0.000359 | -61.4385 | 61.1891 | 61.3624 | 61.2695 | -61.6897 | -0.007087 | 0.020982 | 0.15578 | 0.033307 | 0.040394 | -0.051077 | -0.009929 | -0.22121 | -0.11918 | 0.078212 | 0.029971 | 0.25118 | 0.054113 | -0.038837 | 122.7978 | 122.7257 | 122.7669 | 61.4516 | -122.7839 | 122.6576 | 122.8309 | 122.738 | 61.4689 | -122.998
349.75 | 123.0057 | -61.4777 | 61.2717 | 1.4211e-13 | -0.0025491 | -0.010577 | 0.040025 | -0.02208 | 0.048867 | 0.0036627 | -0.012148 | 0.029263 | 0.044798 | 0.00048933 | 0.047433 | -61.3173 | -0.007751 | -61.4306 | 61.3384 | 61.2709 | 61.3029 | -61.4756 | -61.3903 | -0.00422 | -61.4385 | 61.1891 | 61.3441 | 61.2649 | -61.6897 | 0.002068 | 0.066761 | 0.16036 | 0.04704 | 0.044972 | -0.000719 | 0.031271 | -0.21205 | -0.082562 | 0.087367 | 0.039126 | 0.25118 | 0.07242 | -0.006793 | 122.8161 | 122.7486 | 122.7806 | 61.4699 | -122.7473 | 122.6668 | 122.8217 | 122.7425 | 61.4734 | -122.9614
351.4844 | 122.9919 | -61.377 | 61.3495 | 1.4211e-13 | -0.0021217 | -0.010577 | 0.039384 | -0.021866 | 0.048653 | 0.011293 | -0.011934 | 0.029263 | 0.045225 | 0.00048933 | 0.047006 | -61.3173 | -0.007751 | -61.426 | 61.3293 | 61.2664 | 61.3029 | -61.4664 | -61.3903 | 0.000359 | -61.4385 | 61.1845 | 61.3487 | 61.2374 | -61.6897 | -0.089482 | -0.020216 | 0.059652 | -0.04909 | 0.040392 | -0.083118 | -0.046549 | -0.31276 | -0.16496 | -0.013341 | -0.061582 | 0.25118 | -0.000821 | -0.11209 | 122.7062 | 122.6433 | 122.6799 | 61.3692 | -122.8159 | 122.5615 | 122.7256 | 122.6144 | 61.3773 | -123.0392
353.2969 | 122.9828 | -61.4639 | 61.3037 | 1.4211e-13 | -0.0027627 | -0.010577 | 0.039598 | -0.02208 | 0.048653 | 0.0036627 | -0.011934 | 0.029049 | 0.044584 | 6.1934e-05 | 0.047219 | -61.3127 | -0.012329 | -61.426 | 61.3384 | 61.2709 | 61.2938 | -61.4756 | -61.3903 | 0.004938 | -61.434 | 61.1845 | 61.3441 | 61.2649 | -61.6943 | -0.011665 | 0.034717 | 0.15121 | 0.037885 | 0.04955 | -0.032763 | -0.00993 | -0.23037 | -0.11919 | 0.073634 | 0.029971 | 0.26034 | 0.040376 | -0.038837 | 122.8024 | 122.7349 | 122.7577 | 61.4516 | -122.7793 | 122.6485 | 122.808 | 122.7288 | 61.4689 | -122.998
355.0938 | 123.0011 | -61.4502 | 61.2808 | 1.4211e-13 | -0.0025491 | -0.01015 | 0.039811 | -0.021866 | 0.048439 | 0.018923 | -0.011507 | 0.029049 | 0.044584 | 6.1934e-05 | 0.047219 | -61.3173 | -0.007751 | -61.4352 | 61.3293 | 61.2618 | 61.2938 | -61.4756 | -61.3857 | 0.000359 | -61.4385 | 61.1799 | 61.3532 | 61.2649 | -61.6806 | -0.025398 | 0.048448 | 0.13289 | 0.014996 | 0.040394 | -0.019033 | 0.012958 | -0.23036 | -0.10087 | 0.06448 | 0.01166 | 0.24202 | 0.072421 | -0.015949 | 122.7795 | 122.712 | 122.744 | 61.4424 | -122.7564 | 122.6301 | 122.8034 | 122.7151 | 61.4506 | -122.9614
356.7969 | 122.937 | -61.441 | 61.3358 | 1.4211e-13 | -0.0025491 | -0.010363 | 0.039811 | -0.021866 | 0.048653 | 0.011293 | -0.011934 | 0.029049 | 0.044584 | 0.00048933 | 0.047433 | -61.3081 | -0.012329 | -61.426 | 61.3293 | 61.2618 | 61.2938 | -61.4802 | -61.3857 | -0.00422 | -61.434 | 61.1845 | 61.3487 | 61.2649 | -61.6943 | -0.039132 | -0.006483 | 0.1329 | 0.014997 | 0.054129 | -0.073964 | -0.041973 | -0.25325 | -0.15123 | 0.055325 | 0.007083 | 0.26034 | 0.012912 | -0.07088 | 122.7703 | 122.7028 | 122.7348 | 61.4287 | -122.8159 | 122.6256 | 122.7897 | 122.7059 | 61.4368 | -123.03
358.5469 | 122.8867 | -61.4319 | 61.3724 | 1.4211e-13 | -0.0027627 | -0.010363 | 0.040025 | -0.02208 | 0.048653 | 0.018923 | -0.011934 | 0.029049 | 0.044584 | 0.00048933 | 0.047219 | -61.3127 | -0.016908 | -61.426 | 61.3293 | 61.2709 | 61.2938 | -61.4756 | -61.3903 | 0.000359 | -61.4385 | 61.1754 | 61.3441 | 61.2557 | -61.6806 | -0.043708 | -0.043104 | 0.11916 | 0.005842 | 0.04955 | -0.10143 | -0.078594 | -0.24867 | -0.19701 | 0.041591 | -0.00665 | 0.24202 | -0.028288 | -0.11666 | 122.7612 | 122.7028 | 122.7257 | 61.415 | -122.848 | 122.6073 | 122.776 | 122.6876 | 61.4322 | -123.0529
360.2656 | 122.9462 | -61.4548 | 61.3266 | 1.4211e-13 | -0.0025491 | -0.010577 | 0.039598 | -0.02208 | 0.048439 | 0.0036627 | -0.01172 | 0.029263 | 0.04437 | 0.00027553 | 0.047433 | -61.3081 | -0.007751 | -61.426 | 61.3293 | 61.2618 | 61.2984 | -61.4802 | -61.3903 | 0.000359 | -61.4431 | 61.1845 | 61.3395 | 61.2557 | -61.6851 | -0.025399 | 0.002672 | 0.14663 | 0.02873 | 0.054129 | -0.064809 | -0.028239 | -0.23036 | -0.14207 | 0.064479 | 0.011659 | 0.24202 | 0.01291 | -0.070882 | 122.784 | 122.7166 | 122.7531 | 61.447 | -122.8068 | 122.6393 | 122.7943 | 122.7105 | 61.4551 | -123.0117
362.0312 | 122.9599 | -61.3815 | 61.3678 | 1.4211e-13 | -0.0025491 | -0.01015 | 0.039598 | -0.02208 | 0.048439 | 0.0036627 | -0.011934 | 0.029049 | 0.044798 | 0.00027553 | 0.047219 | -61.3127 | -0.007751 | -61.426 | 61.3247 | 61.2664 | 61.2938 | -61.4802 | -61.3903 | 0.004938 | -61.4431 | 61.1799 | 61.3395 | 61.2557 | -61.6806 | -0.098641 | -0.043106 | 0.068808 | -0.044512 | 0.054129 | -0.10143 | -0.074017 | -0.29903 | -0.18785 | -0.008763 | -0.061583 | 0.23744 | -0.028289 | -0.11208 | 122.7062 | 122.6479 | 122.6753 | 61.3738 | -122.848 | 122.5615 | 122.721 | 122.6372 | 61.3865 | -123.0484
363.7344 | 123.0103 | -61.377 | 61.3174 | 1.4211e-13 | -0.0027627 | -0.01015 | 0.039811 | -0.02208 | 0.048867 | 0.018923 | -0.012148 | 0.029263 | 0.04437 | 0.00027553 | 0.047006 | -61.3173 | -0.007751 | -61.426 | 61.3293 | 61.2618 | 61.2892 | -61.4664 | -61.3811 | 0.004938 | -61.4431 | 61.1845 | 61.3441 | 61.2466 | -61.6806 | -0.089482 | 0.011827 | 0.059652 | -0.04909 | 0.040392 | -0.055654 | -0.028241 | -0.3036 | -0.13292 | -0.004184 | -0.066161 | 0.23744 | 0.026643 | -0.070885 | 122.7062 | 122.6387 | 122.6662 | 61.3692 | -122.7839 | 122.5615 | 122.721 | 122.6235 | 61.3819 | -122.998
365.5 | 122.8638 | -61.4777 | 61.2854 | 1.4211e-13 | -0.0025491 | -0.010577 | 0.039598 | -0.022294 | 0.048653 | 0.011293 | -0.012148 | 0.029263 | 0.044798 | 0.00070293 | 0.047219 | -61.3173 | -0.007751 | -61.4169 | 61.3338 | 61.2618 | 61.2938 | -61.4756 | -61.3857 | 0.009516 | -61.4294 | 61.1845 | 61.3487 | 61.2282 | -61.6851 | 0.002068 | 0.048449 | 0.16036 | 0.060775 | 0.058707 | -0.02361 | 0.008381 | -0.20748 | -0.10087 | 0.091946 | 0.048283 | 0.25576 | 0.063266 | -0.057155 | 122.8115 | 122.7395 | 122.7714 | 61.4699 | -122.761 | 122.6622 | 122.8263 | 122.7059 | 61.4872 | -122.9705
367.2188 | 122.9279 | -61.4273 | 61.3358 | 1.4211e-13 | -0.0023355 | -0.010577 | 0.039598 | -0.02208 | 0.048653 | -0.0039678 | -0.011934 | 0.029049 | 0.045011 | 6.1934e-05 | 0.047006 | -61.3127 | -0.016908 | -61.426 | 61.3247 | 61.2526 | 61.2938 | -61.471 | -61.3811 | 0.000359 | -61.434 | 61.1754 | 61.3441 | 61.2557 | -61.6714 | -0.043707 | -0.011062 | 0.11458 | 0.001264 | 0.044971 | -0.083121 | -0.041973 | -0.24409 | -0.16038 | 0.04617 | -0.00665 | 0.23744 | 0.008333 | -0.080037 | 122.752 | 122.6799 | 122.7211 | 61.4104 | -122.8068 | 122.6027 | 122.7714 | 122.683 | 61.4277 | -123.0072
368.9219 | 122.9919 | -61.4273 | 61.2396 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.039598 | -0.022294 | 0.048653 | 0.0036627 | -0.01172 | 0.029049 | 0.044798 | 0.00027553 | 0.047219 | -61.3127 | -0.012329 | -61.4123 | 61.3293 | 61.2526 | 61.2938 | -61.4664 | -61.3857 | 0.000359 | -61.434 | 61.1799 | 61.3441 | 61.2511 | -61.6851 | -0.039128 | 0.089647 | 0.11458 | 0.014999 | 0.054127 | 0.013009 | 0.054157 | -0.25783 | -0.059676 | 0.041592 | -0.00665 | 0.25118 | 0.10446 | 0.011514 | 122.7566 | 122.6799 | 122.7211 | 61.415 | -122.7061 | 122.6073 | 122.7714 | 122.6784 | 61.4277 | -122.9248
370.7031 | 122.9507 | -61.4182 | 61.2717 | 1.4211e-13 | -0.0025491 | -0.010363 | 0.039811 | -0.02208 | 0.048653 | -0.0039678 | -0.011934 | 0.029263 | 0.044798 | 0.00027553 | 0.047219 | -61.3127 | -0.012329 | -61.4169 | 61.3155 | 61.2618 | 61.2846 | -61.4664 | -61.3811 | 0.004938 | -61.4294 | 61.1845 | 61.3395 | 61.2557 | -61.6806 | -0.048283 | 0.043869 | 0.10543 | 0.001266 | 0.049549 | -0.009877 | 0.012957 | -0.26241 | -0.087141 | 0.037015 | -0.011226 | 0.25118 | 0.067842 | -0.01595 | 122.7337 | 122.6799 | 122.7028 | 61.4058 | -122.7381 | 122.6027 | 122.7577 | 122.6739 | 61.4231 | -122.9522
372.4688 | 122.9645 | -61.409 | 61.2671 | 1.4211e-13 | -0.0027627 | -0.01015 | 0.040025 | -0.022507 | 0.048439 | 0.011293 | -0.012148 | 0.028835 | 0.04437 | 0.00048933 | 0.047433 | -61.3173 | -0.007751 | -61.4215 | 61.3247 | 61.2664 | 61.2846 | -61.4664 | -61.3857 | 0.004938 | -61.4294 | 61.1708 | 61.3487 | 61.2511 | -61.6806 | -0.057438 | 0.057602 | 0.091696 | -0.012468 | 0.04497 | -0.000721 | 0.017534 | -0.27156 | -0.096299 | 0.023282 | -0.020381 | 0.25118 | 0.081576 | -0.015952 | 122.7337 | 122.6754 | 122.6936 | 61.4012 | -122.7335 | 122.5798 | 122.7577 | 122.6601 | 61.4139 | -122.9476
374.1875 | 122.9599 | -61.4273 | 61.2991 | 1.4211e-13 | -0.0025491 | -0.010577 | 0.039811 | -0.02208 | 0.048439 | -0.0039678 | -0.011934 | 0.029049 | 0.044798 | 0.00048933 | 0.047006 | -61.3036 | -0.016908 | -61.4215 | 61.3247 | 61.2572 | 61.2984 | -61.4664 | -61.3811 | 0.004938 | -61.434 | 61.1754 | 61.3441 | 61.2511 | -61.676 | -0.039128 | 0.025559 | 0.12374 | 0.005842 | 0.04497 | -0.041921 | -0.000773 | -0.24867 | -0.12376 | 0.04617 | -0.00665 | 0.24202 | 0.044954 | -0.047995 | 122.752 | 122.6845 | 122.7257 | 61.4104 | -122.7656 | 122.6027 | 122.7714 | 122.6784 | 61.4322 | -122.9751
375.875 | 122.9141 | -61.4044 | 61.377 | 1.4211e-13 | -0.0027627 | -0.010363 | 0.039598 | -0.022294 | 0.048653 | 0.011293 | -0.011934 | 0.028835 | 0.044157 | 0.00048933 | 0.047219 | -61.3127 | -0.016908 | -61.4169 | 61.3155 | 61.2481 | 61.2846 | -61.4619 | -61.3811 | 0.000359 | -61.4202 | 61.1754 | 61.3395 | 61.242 | -61.676 | -0.057437 | -0.061417 | 0.091696 | -0.012467 | 0.04497 | -0.1289 | -0.092329 | -0.27156 | -0.20158 | 0.023282 | -0.015802 | 0.25576 | -0.037444 | -0.13497 | 122.72 | 122.6525 | 122.689 | 61.3875 | -122.8388 | 122.5798 | 122.7439 | 122.6464 | 61.4048 | -123.0529
377.5938 | 122.9965 | -61.377 | 61.3312 | 1.4211e-13 | -0.0023355 | -0.010363 | 0.039598 | -0.022294 | 0.048226 | 0.0036627 | -0.011934 | 0.029263 | 0.04437 | 0.00070293 | 0.047219 | -61.3036 | -0.007751 | -61.4215 | 61.3155 | 61.2526 | 61.2892 | -61.4619 | -61.372 | -0.00422 | -61.434 | 61.1754 | 61.3441 | 61.2374 | -61.676 | -0.084903 | -0.015641 | 0.073387 | -0.044512 | 0.040391 | -0.078544 | -0.041974 | -0.29903 | -0.15581 | 0.004974 | -0.057004 | 0.24202 | 0.01291 | -0.093775 | 122.6925 | 122.6296 | 122.6662 | 61.3692 | -122.793 | 122.5523 | 122.721 | 122.6144 | 61.3727 | -123.0072
379.375 | 122.9141 | -61.4319 | 61.3129 | 1.4211e-13 | -0.0027627 | -0.010363 | 0.039811 | -0.022294 | 0.048867 | 0.018923 | -0.01172 | 0.028835 | 0.044798 | 0.00048933 | 0.047219 | -61.3081 | -0.016908 | -61.4169 | 61.3201 | 61.2526 | 61.2892 | -61.4664 | -61.3811 | 0.004938 | -61.4248 | 61.1708 | 61.3441 | 61.2466 | -61.676 | -0.03455 | 0.007248 | 0.12374 | 0.014999 | 0.049549 | -0.060233 | -0.023663 | -0.24409 | -0.14207 | 0.050748 | 0.007086 | 0.25118 | 0.031221 | -0.066307 | 122.752 | 122.6845 | 122.7211 | 61.415 | -122.7793 | 122.6027 | 122.776 | 122.6784 | 61.4368 | -122.9888
381.0781 | 122.8409 | -61.4868 | 61.2946 | 1.4211e-13 | -0.0025491 | -0.010363 | 0.040239 | -0.02208 | 0.048653 | -0.0039678 | -0.011934 | 0.029263 | 0.04437 | 0.00048933 | 0.046792 | -61.3081 | -0.003172 | -61.4169 | 61.3201 | 61.2664 | 61.2846 | -61.4664 | -61.3811 | 0.000359 | -61.434 | 61.1708 | 61.3441 | 61.2511 | -61.676 | 0.020381 | 0.025558 | 0.17867 | 0.06993 | 0.049549 | -0.028187 | -0.009932 | -0.18916 | -0.12376 | 0.10568 | 0.052859 | 0.24202 | 0.049531 | -0.043418 | 122.8069 | 122.7532 | 122.7714 | 61.4836 | -122.761 | 122.6576 | 122.8309 | 122.738 | 61.4872 | -122.9705
382.8594 | 122.9965 | -61.377 | 61.3129 | 1.4211e-13 | -0.0027627 | -0.010363 | 0.039598 | -0.02208 | 0.048653 | -0.0039678 | -0.01172 | 0.029049 | 0.04437 | 0.00048933 | 0.047219 | -61.3081 | -0.007751 | -61.4169 | 61.3201 | 61.2572 | 61.2938 | -61.4573 | -61.3766 | 0.004938 | -61.434 | 61.1754 | 61.3395 | 61.2511 | -61.6668 | -0.080325 | 0.007248 | 0.068809 | -0.039933 | 0.040392 | -0.055654 | -0.019085 | -0.28987 | -0.1375 | 0.000395 | -0.057004 | 0.23286 | 0.026643 | -0.061728 | 122.6971 | 122.6342 | 122.6707 | 61.3692 | -122.7701 | 122.5523 | 122.7165 | 122.6281 | 61.3819 | -122.9797
384.625 | 122.8729 | -61.3998 | 61.3907 | 1.4211e-13 | -0.0021217 | -0.010363 | 0.03917 | -0.02208 | 0.048653 | -0.0039678 | -0.012148 | 0.029049 | 0.044584 | 0.00048933 | 0.047006 | -61.3036 | -0.007751 | -61.4169 | 61.3201 | 61.2481 | 61.2892 | -61.4619 | -61.3766 | 0.004938 | -61.4248 | 61.1708 | 61.3258 | 61.2466 | -61.6622 | -0.062015 | -0.070572 | 0.096275 | -0.017045 | 0.04497 | -0.14263 | -0.10148 | -0.2624 | -0.2199 | 0.023283 | -0.024958 | 0.23744 | -0.064913 | -0.14413 | 122.72 | 122.6479 | 122.689 | 61.3921 | -122.8525 | 122.5706 | 122.7256 | 122.6464 | 61.4048 | -123.0529
386.3438 | 122.9919 | -61.4502 | 61.2488 | 1.4211e-13 | -0.0025491 | -0.010363 | 0.039384 | -0.02208 | 0.048653 | 0.0036627 | -0.011934 | 0.028835 | 0.044584 | 0.00027553 | 0.047006 | -61.299 | -0.007751 | -61.4169 | 61.3155 | 61.2618 | 61.2846 | -61.4619 | -61.3811 | 0.000359 | -61.4248 | 61.1662 | 61.3349 | 61.2374 | -61.6714 | -0.011661 | 0.066757 | 0.15121 | 0.033309 | 0.04497 | 0.013011 | 0.035845 | -0.2212 | -0.082567 | 0.069058 | 0.025396 | 0.2466 | 0.086151 | -0.011377 | 122.7657 | 122.712 | 122.7348 | 61.4424 | -122.7106 | 122.6164 | 122.7851 | 122.6876 | 61.4506 | -122.9202
388.125 | 122.85 | -61.3998 | 61.377 | 1.4211e-13 | -0.0027627 | -0.010363 | 0.039384 | -0.022294 | 0.048226 | 0.0036627 | -0.011934 | 0.028835 | 0.044798 | 0.00048933 | 0.047219 | -61.3036 | -0.012329 | -61.4169 | 61.3155 | 61.2526 | 61.28 | -61.4573 | -61.372 | -0.00422 | -61.4202 | 61.1708 | 61.3304 | 61.242 | -61.676 | -0.057437 | -0.061417 | 0.096275 | -0.017045 | 0.040392 | -0.12432 | -0.096908 | -0.27614 | -0.20616 | 0.027862 | -0.02038 | 0.25576 | -0.046602 | -0.13497 | 122.7154 | 122.6525 | 122.6799 | 61.3875 | -122.8342 | 122.5706 | 122.7302 | 122.6418 | 61.3956 | -123.0529
389.8281 | 122.8363 | -61.4868 | 61.2946 | 1.4211e-13 | -0.0025491 | -0.01015 | 0.038957 | -0.022294 | 0.048653 | 0.0036627 | -0.011934 | 0.029263 | 0.044798 | 6.1934e-05 | 0.047219 | -61.3036 | -0.012329 | -61.4077 | 61.3155 | 61.2618 | 61.2846 | -61.4664 | -61.3674 | 0.004938 | -61.4202 | 61.1662 | 61.3304 | 61.2511 | -61.6714 | 0.020381 | 0.02098 | 0.18325 | 0.079086 | 0.058705 | -0.032766 | -0.009932 | -0.18458 | -0.12834 | 0.11941 | 0.066595 | 0.25118 | 0.035795 | -0.043418 | 122.8024 | 122.7486 | 122.7714 | 61.4745 | -122.761 | 122.653 | 122.8172 | 122.738 | 61.4918 | -122.966
391.5625 | 122.8821 | -61.4594 | 61.2808 | 1.4211e-13 | -0.0025491 | -0.01015 | 0.03917 | -0.022294 | 0.048867 | -0.0039678 | -0.012148 | 0.029049 | 0.04437 | 0.00048933 | 0.047433 | -61.299 | -0.003172 | -61.4169 | 61.3155 | 61.2526 | 61.28 | -61.471 | -61.3766 | 0.000359 | -61.4248 | 61.1708 | 61.3349 | 61.2511 | -61.6668 | -0.011663 | 0.034713 | 0.16036 | 0.042465 | 0.054128 | -0.02819 | -0.000778 | -0.20747 | -0.11003 | 0.082793 | 0.034552 | 0.24202 | 0.054107 | -0.029685 | 122.7749 | 122.712 | 122.7394 | 61.4562 | -122.7518 | 122.6301 | 122.7943 | 122.7105 | 61.4597 | -122.9476
393.2812 | 122.8683 | -61.4319 | 61.3037 | 1.4211e-13 | -0.0023355 | -0.0097224 | 0.038957 | -0.02208 | 0.048439 | 0.011293 | -0.011934 | 0.029476 | 0.044584 | 0.00048933 | 0.047219 | -61.3036 | -0.021486 | -61.4123 | 61.3155 | 61.2481 | 61.28 | -61.4664 | -61.3766 | 0.000359 | -61.4202 | 61.1708 | 61.3349 | 61.242 | -61.6622 | -0.03455 | 0.011825 | 0.12832 | 0.019577 | 0.054127 | -0.055657 | -0.023666 | -0.23036 | -0.13292 | 0.055327 | 0.011664 | 0.24202 | 0.031219 | -0.06173 | 122.7474 | 122.6799 | 122.7119 | 61.4104 | -122.7701 | 122.6027 | 122.7668 | 122.6739 | 61.4322 | -122.966
395.0469 | 122.905 | -61.4273 | 61.322 | 1.4211e-13 | -0.0025491 | -0.010577 | 0.039384 | -0.022294 | 0.048653 | 0.0036627 | -0.011934 | 0.029049 | 0.044584 | 0.00048933 | 0.047006 | -61.2944 | -0.012329 | -61.4169 | 61.311 | 61.2526 | 61.2846 | -61.4619 | -61.3766 | 0.009516 | -61.4202 | 61.1616 | 61.3349 | 61.2466 | -61.6622 | -0.034549 | -0.011064 | 0.1329 | 0.010421 | 0.04497 | -0.069388 | -0.037397 | -0.23494 | -0.16039 | 0.050749 | 0.007086 | 0.24202 | 0.012909 | -0.075462 | 122.7383 | 122.6799 | 122.7119 | 61.415 | -122.7839 | 122.5889 | 122.7622 | 122.6739 | 61.4368 | -122.9843
396.75 | 122.9233 | -61.4182 | 61.2854 | 1.4211e-13 | -0.0023355 | -0.010363 | 0.03917 | -0.02208 | 0.048439 | 0.0036627 | -0.01172 | 0.029049 | 0.04437 | 0.00048933 | 0.046792 | -61.299 | -0.007751 | -61.4215 | 61.3064 | 61.2481 | 61.2846 | -61.4527 | -61.372 | -0.00422 | -61.4156 | 61.1662 | 61.3304 | 61.2374 | -61.6668 | -0.034547 | 0.020979 | 0.11916 | -0.003313 | 0.031234 | -0.037346 | -0.000776 | -0.24867 | -0.11919 | 0.046173 | 0.00251 | 0.25118 | 0.044951 | -0.047998 | 122.7245 | 122.6662 | 122.7028 | 61.4104 | -122.7381 | 122.5844 | 122.7485 | 122.6556 | 61.4139 | -122.9522
398.5312 | 122.9828 | -61.4227 | 61.235 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.039384 | -0.022507 | 0.048226 | 0.011293 | -0.01172 | 0.028835 | 0.04437 | 0.00070293 | 0.047219 | -61.2898 | -0.012329 | -61.4123 | 61.3155 | 61.2481 | 61.28 | -61.4527 | -61.3674 | -0.00422 | -61.4202 | 61.1616 | 61.3349 | 61.2328 | -61.6668 | -0.02997 | 0.08049 | 0.1329 | 0.010421 | 0.040391 | 0.013008 | 0.044999 | -0.24409 | -0.073412 | 0.055328 | 0.002508 | 0.2466 | 0.099884 | -0.002222 | 122.7383 | 122.6708 | 122.7028 | 61.4104 | -122.6877 | 122.5844 | 122.7577 | 122.6556 | 61.4185 | -122.9019
400.25 | 122.9828 | -61.441 | 61.2305 | 1.4211e-13 | -0.0027627 | -0.010363 | 0.039384 | -0.02208 | 0.048653 | -0.0039678 | -0.011934 | 0.029049 | 0.044584 | 0.00048933 | 0.047219 | -61.2944 | -0.007751 | -61.4123 | 61.3293 | 61.2481 | 61.28 | -61.4527 | -61.372 | 0.000359 | -61.4156 | 61.1616 | 61.3258 | 61.2374 | -61.6668 | -0.011659 | 0.098802 | 0.14663 | 0.028732 | 0.040391 | 0.017585 | 0.049576 | -0.22578 | -0.068835 | 0.069061 | 0.025398 | 0.25118 | 0.095304 | 0.006933 | 122.7703 | 122.6891 | 122.7211 | 61.4333 | -122.6832 | 122.6027 | 122.7668 | 122.6784 | 61.4414 | -122.8973
401.9531 | 122.9233 | -61.4273 | 61.2854 | 1.4211e-13 | -0.0023355 | -0.010363 | 0.039384 | -0.02208 | 0.048653 | 0.0036627 | -0.011507 | 0.029049 | 0.04437 | 0.00048933 | 0.047219 | -61.299 | -0.012329 | -61.4077 | 61.311 | 61.2435 | 61.28 | -61.4573 | -61.3674 | 0.004938 | -61.4248 | 61.1662 | 61.3212 | 61.2374 | -61.6668 | -0.029971 | 0.025557 | 0.12832 | 0.019577 | 0.049548 | -0.041925 | -0.005355 | -0.23951 | -0.11919 | 0.059906 | 0.002508 | 0.24202 | 0.035794 | -0.047998 | 122.7383 | 122.6708 | 122.7074 | 61.415 | -122.7427 | 122.5935 | 122.7485 | 122.6647 | 61.4322 | -122.9522
403.7344 | 122.9279 | -61.4227 | 61.2991 | 1.4211e-13 | -0.0025491 | -0.010363 | 0.038957 | -0.02208 | 0.048439 | 0.0036627 | -0.01172 | 0.029476 | 0.044798 | 0.00091673 | 0.046792 | -61.2898 | -0.007751 | -61.4123 | 61.3064 | 61.2481 | 61.2755 | -61.4573 | -61.3674 | 0.004938 | -61.4156 | 61.1571 | 61.3212 | 61.2374 | -61.6668 | -0.034549 | 0.007246 | 0.1329 | 0.010421 | 0.04497 | -0.051079 | -0.023666 | -0.24409 | -0.14208 | 0.055328 | 0.007087 | 0.25118 | 0.022061 | -0.061731 | 122.7291 | 122.6708 | 122.6982 | 61.415 | -122.7564 | 122.5798 | 122.7439 | 122.6601 | 61.4277 | -122.966
405.5 | 122.9462 | -61.4502 | 61.2259 | 1.4211e-13 | -0.0023355 | -0.010363 | 0.03917 | -0.02208 | 0.048226 | 0.011293 | -0.01172 | 0.029049 | 0.04437 | 0.00070293 | 0.046792 | -61.2944 | -0.021486 | -61.4123 | 61.311 | 61.2389 | 61.28 | -61.4527 | -61.3674 | 0.009516 | -61.4156 | 61.1616 | 61.3258 | 61.2328 | -61.6622 | -0.002504 | 0.085066 | 0.15579 | 0.037887 | 0.040391 | 0.013005 | 0.054154 | -0.21205 | -0.064257 | 0.082794 | 0.034553 | 0.2466 | 0.099882 | 0.006933 | 122.7612 | 122.6891 | 122.7302 | 61.4287 | -122.6786 | 122.6118 | 122.776 | 122.683 | 61.4597 | -122.8881
407.2344 | 122.937 | -61.3541 | 61.3266 | 1.4211e-13 | -0.0021217 | -0.010577 | 0.039598 | -0.02208 | 0.048653 | -0.0039678 | -0.011934 | 0.029049 | 0.04437 | 0.00027553 | 0.047647 | -61.2944 | -0.016908 | -61.4215 | 61.311 | 61.2435 | 61.2755 | -61.4573 | -61.3674 | 0.000359 | -61.4156 | 61.1662 | 61.3212 | 61.2328 | -61.6622 | -0.10321 | -0.015642 | 0.059656 | -0.0674 | 0.035813 | -0.083124 | -0.051132 | -0.30818 | -0.16039 | -0.013336 | -0.061577 | 0.2466 | -0.005405 | -0.093775 | 122.665 | 122.5975 | 122.6295 | 61.3372 | -122.7839 | 122.5203 | 122.6753 | 122.5869 | 61.3544 | -122.9888
409.0156 | 122.8317 | -61.4182 | 61.3724 | 1.4211e-13 | -0.0025491 | -0.009936 | 0.038957 | -0.02208 | 0.048226 | 0.0036627 | -0.012148 | 0.029049 | 0.044584 | 0.00070293 | 0.047219 | -61.299 | -0.012329 | -61.4077 | 61.311 | 61.2435 | 61.2755 | -61.4527 | -61.3628 | 0.000359 | -61.4111 | 61.1571 | 61.3166 | 61.2328 | -61.6622 | -0.034547 | -0.061418 | 0.11916 | 0.010422 | 0.044969 | -0.1289 | -0.096908 | -0.24409 | -0.21532 | 0.05533 | 0.007089 | 0.25118 | -0.055759 | -0.13955 | 122.7291 | 122.6616 | 122.6936 | 61.4058 | -122.8251 | 122.5752 | 122.7348 | 122.651 | 61.4185 | -123.0346
410.7969 | 122.905 | -61.4182 | 61.2946 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.039384 | -0.02208 | 0.048653 | 0.0036627 | -0.01172 | 0.028622 | 0.044584 | 0.00070293 | 0.046792 | -61.2898 | -0.021486 | -61.4123 | 61.3064 | 61.2389 | 61.28 | -61.4527 | -61.3582 | 0.000359 | -61.4111 | 61.1662 | 61.3212 | 61.2328 | -61.6668 | -0.034547 | 0.011823 | 0.12832 | 0.005844 | 0.040391 | -0.05566 | -0.014511 | -0.24867 | -0.12834 | 0.059909 | 0.007089 | 0.25576 | 0.026638 | -0.061732 | 122.7245 | 122.657 | 122.6982 | 61.3967 | -122.7473 | 122.5844 | 122.7393 | 122.651 | 61.4185 | -122.9614
412.5938 | 122.9782 | -61.4182 | 61.2076 | 1.4211e-13 | -0.0023355 | -0.010363 | 0.039384 | -0.02208 | 0.048867 | 0.018923 | -0.012148 | 0.029049 | 0.044157 | 0.00048933 | 0.047219 | -61.2898 | -0.007751 | -61.4123 | 61.311 | 61.2481 | 61.2709 | -61.4573 | -61.3628 | 0.004938 | -61.4156 | 61.1525 | 61.3258 | 61.2374 | -61.6577 | -0.039126 | 0.10338 | 0.12832 | 0.005844 | 0.04497 | 0.040473 | 0.063307 | -0.23951 | -0.055104 | 0.05533 | 0.00251 | 0.24202 | 0.11819 | 0.029821 | 122.7291 | 122.6662 | 122.689 | 61.4104 | -122.6649 | 122.5706 | 122.7439 | 122.6556 | 61.4231 | -122.8652
414.3125 | 122.9599 | -61.4456 | 61.2396 | 1.4211e-13 | -0.0023355 | -0.010363 | 0.03917 | -0.022507 | 0.048439 | 0.0036627 | -0.011934 | 0.029263 | 0.044584 | 0.00048933 | 0.046578 | -61.2853 | -0.012329 | -61.4123 | 61.311 | 61.2435 | 61.2709 | -61.4481 | -61.3628 | 0.004938 | -61.4111 | 61.1616 | 61.3212 | 61.2328 | -61.6531 | -0.002502 | 0.071333 | 0.16037 | 0.03331 | 0.035812 | 0.003851 | 0.031264 | -0.20747 | -0.07799 | 0.082796 | 0.034555 | 0.24202 | 0.08157 | -0.0068 | 122.7566 | 122.6891 | 122.7165 | 61.4333 | -122.6877 | 122.6073 | 122.7668 | 122.6784 | 61.4506 | -122.8927
416.0781 | 122.9507 | -61.4456 | 61.2396 | 1.4211e-13 | -0.0025491 | -0.010363 | 0.03917 | -0.022507 | 0.048653 | 0.0036627 | -0.011934 | 0.029263 | 0.04437 | 0.00048933 | 0.047006 | -61.2944 | -0.012329 | -61.4032 | 61.3018 | 61.2389 | 61.2755 | -61.4527 | -61.3628 | 0.004938 | -61.4156 | 61.1571 | 61.3258 | 61.2282 | -61.6577 | -0.007081 | 0.062176 | 0.15121 | 0.042467 | 0.049548 | -0.000728 | 0.035843 | -0.21205 | -0.082569 | 0.082796 | 0.029976 | 0.24202 | 0.086149 | -0.011379 | 122.7474 | 122.6845 | 122.7211 | 61.4333 | -122.6923 | 122.6027 | 122.7714 | 122.6739 | 61.4506 | -122.8973
417.8438 | 122.9187 | -61.409 | 61.2671 | 1.4211e-13 | -0.0023355 | -0.010363 | 0.03917 | -0.022721 | 0.048439 | 0.0036627 | -0.012148 | 0.029049 | 0.04437 | 0.00070293 | 0.046792 | -61.2898 | -0.012329 | -61.4077 | 61.3018 | 61.2343 | 61.2755 | -61.4481 | -61.3628 | 0.000359 | -61.4065 | 61.1616 | 61.3258 | 61.2328 | -61.6622 | -0.039123 | 0.03471 | 0.11917 | 0.001267 | 0.04039 | -0.032773 | 0.008377 | -0.25325 | -0.10546 | 0.046175 | 0.002513 | 0.25576 | 0.058683 | -0.034266 | 122.7108 | 122.6433 | 122.6845 | 61.3967 | -122.7152 | 122.5706 | 122.7348 | 122.6418 | 61.4094 | -122.9293
419.6406 | 122.9507 | -61.3632 | 61.3083 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.03917 | -0.022507 | 0.048653 | -0.0039678 | -0.01172 | 0.029263 | 0.044798 | 0.00048933 | 0.046792 | -61.2898 | -0.003172 | -61.4032 | 61.3018 | 61.2343 | 61.2709 | -61.4481 | -61.3628 | -0.00422 | -61.4065 | 61.1571 | 61.3258 | 61.2328 | -61.6531 | -0.0849 | -0.006489 | 0.073389 | -0.039931 | 0.044969 | -0.073972 | -0.037401 | -0.28986 | -0.15123 | 0.000398 | -0.043264 | 0.2466 | 0.017484 | -0.075465 | 122.665 | 122.5975 | 122.6341 | 61.36 | -122.7564 | 122.5203 | 122.689 | 122.596 | 61.359 | -122.9614
421.3438 | 122.8912 | -61.4685 | 61.2579 | 1.4211e-13 | -0.0025491 | -0.010363 | 0.039384 | -0.02208 | 0.048439 | 0.011293 | -0.011934 | 0.029263 | 0.04437 | 0.00091673 | 0.046792 | -61.2853 | -0.007751 | -61.4032 | 61.3018 | 61.2343 | 61.2755 | -61.4435 | -61.3628 | 0.000359 | -61.4065 | 61.1525 | 61.312 | 61.2374 | -61.6577 | 0.024965 | 0.043865 | 0.18325 | 0.065355 | 0.04039 | -0.023618 | 0.017532 | -0.18916 | -0.10546 | 0.10568 | 0.062022 | 0.25118 | 0.054102 | -0.020533 | 122.7703 | 122.7028 | 122.744 | 61.4608 | -122.7015 | 122.621 | 122.7805 | 122.7059 | 61.4689 | -122.9156
423.125 | 122.9462 | -61.441 | 61.2305 | 1.4211e-13 | -0.0027627 | -0.009936 | 0.038957 | -0.021866 | 0.048439 | 0.018923 | -0.011934 | 0.028835 | 0.044584 | 0.00048933 | 0.047006 | -61.2898 | -0.007751 | -61.4032 | 61.3018 | 61.2435 | 61.2755 | -61.4435 | -61.3582 | 0.004938 | -61.4065 | 61.1616 | 61.3212 | 61.2374 | -61.6531 | -0.002501 | 0.071331 | 0.15121 | 0.037889 | 0.04039 | 0.013006 | 0.044998 | -0.21204 | -0.068835 | 0.082797 | 0.034556 | 0.2466 | 0.090725 | 0.006933 | 122.7428 | 122.6845 | 122.7165 | 61.4333 | -122.674 | 122.6027 | 122.7622 | 122.6784 | 61.446 | -122.8836
424.8906 | 122.8775 | -61.409 | 61.322 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.03917 | -0.022294 | 0.048439 | 0.018923 | -0.012148 | 0.029263 | 0.044584 | 0.00070293 | 0.046792 | -61.2898 | -0.003172 | -61.3986 | 61.3018 | 61.2389 | 61.2709 | -61.4435 | -61.3628 | 0.004938 | -61.4065 | 61.1662 | 61.3166 | 61.2282 | -61.6485 | -0.034544 | -0.020221 | 0.11917 | 0.010424 | 0.044968 | -0.083125 | -0.051133 | -0.23951 | -0.15581 | 0.046175 | 0.002513 | 0.24202 | -0.005405 | -0.093776 | 122.7108 | 122.6479 | 122.6799 | 61.4058 | -122.7656 | 122.5752 | 122.7256 | 122.6372 | 61.4139 | -122.9705
426.6719 | 122.9187 | -61.441 | 61.235 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.03917 | -0.02208 | 0.048653 | 0.011293 | -0.011934 | 0.029263 | 0.045011 | 0.00070293 | 0.047219 | -61.2807 | -0.003172 | -61.3986 | 61.3018 | 61.2297 | 61.28 | -61.4435 | -61.3491 | 0.000359 | -61.4019 | 61.1616 | 61.312 | 61.2282 | -61.6485 | -0.002501 | 0.066754 | 0.16037 | 0.042467 | 0.044968 | -0.005308 | 0.044999 | -0.20747 | -0.073412 | 0.091954 | 0.039134 | 0.2466 | 0.076991 | -0.006801 | 122.7428 | 122.6708 | 122.7211 | 61.4379 | -122.6786 | 122.6027 | 122.7531 | 122.6693 | 61.4414 | -122.8836
428.3906 | 122.9233 | -61.4365 | 61.2305 | 1.4211e-13 | -0.0023355 | -0.010577 | 0.03917 | -0.02208 | 0.048012 | 0.0036627 | -0.011934 | 0.029049 | 0.04437 | 0.00070293 | 0.047006 | -61.2807 | -0.016908 | -61.394 | 61.3018 | 61.2343 | 61.2709 | -61.4481 | -61.3582 | 0.004938 | -61.4065 | 61.1616 | 61.312 | 61.2328 | -61.6485 | -0.011658 | 0.071331 | 0.15579 | 0.042467 | 0.054125 | 0.003848 | 0.040419 | -0.21204 | -0.068835 | 0.078219 | 0.029978 | 0.24202 | 0.081568 | 0.002355 | 122.7383 | 122.6708 | 122.7073 | 61.4196 | -122.6786 | 122.5981 | 122.7485 | 122.6693 | 61.4414 | -122.879
430.1094 | 122.8867 | -61.4136 | 61.2808 | 1.4211e-13 | -0.0023355 | -0.010363 | 0.039384 | -0.02208 | 0.048439 | -0.011598 | -0.011934 | 0.028835 | 0.044157 | 0.00070293 | 0.047219 | -61.2853 | -0.007751 | -61.394 | 61.2926 | 61.2252 | 61.2709 | -61.4344 | -61.3537 | 0.000359 | -61.4111 | 61.1662 | 61.312 | 61.2191 | -61.6485 | -0.020809 | 0.011821 | 0.12832 | 0.019579 | 0.040388 | -0.055664 | -0.009935 | -0.23493 | -0.11461 | 0.05991 | 0.002511 | 0.23744 | 0.031214 | -0.061735 | 122.7062 | 122.6387 | 122.6845 | 61.4058 | -122.7152 | 122.5798 | 122.7256 | 122.6327 | 61.4139 | -122.9293
431.875 | 122.9279 | -61.3495 | 61.3174 | 1.4211e-13 | -0.0025491 | -0.01015 | 0.039384 | -0.022507 | 0.048439 | 0.0036627 | -0.011934 | 0.028835 | 0.044584 | 0.00070293 | 0.047006 | -61.2807 | -0.007751 | -61.4077 | 61.2926 | 61.2252 | 61.2663 | -61.439 | -61.3582 | 0.004938 | -61.4019 | 61.1616 | 61.312 | 61.2237 | -61.6485 | -0.089475 | -0.0248 | 0.068813 | -0.058243 | 0.031232 | -0.092285 | -0.051134 | -0.29902 | -0.15581 | -0.008756 | -0.052419 | 0.2466 | -0.005407 | -0.093778 | 122.6421 | 122.5746 | 122.6158 | 61.3417 | -122.7564 | 122.5111 | 122.6615 | 122.5732 | 61.3544 | -122.9659
433.6719 | 122.8134 | -61.4319 | 61.2671 | 1.4211e-13 | -0.0021217 | -0.010363 | 0.039384 | -0.022294 | 0.048226 | 0.0036627 | -0.012148 | 0.029049 | 0.044157 | 0.00048933 | 0.047219 | -61.2853 | -0.007751 | -61.394 | 61.2972 | 61.2343 | 61.2663 | -61.439 | -61.3582 | 0.004938 | -61.3973 | 61.1616 | 61.3166 | 61.2282 | -61.6393 | -0.007077 | 0.030132 | 0.14663 | 0.03789 | 0.044967 | -0.032773 | -0.00078 | -0.20746 | -0.10546 | 0.073642 | 0.034558 | 0.24202 | 0.049526 | -0.038845 | 122.7291 | 122.6662 | 122.6982 | 61.4241 | -122.7061 | 122.5935 | 122.7485 | 122.6601 | 61.4368 | -122.9064
435.3906 | 122.9553 | -61.4273 | 61.1984 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.03917 | -0.02208 | 0.048439 | 0.0036627 | -0.011934 | 0.028622 | 0.044798 | 0.00091673 | 0.046792 | -61.2807 | -0.007751 | -61.3986 | 61.2926 | 61.2343 | 61.2709 | -61.4435 | -61.3582 | 0.009516 | -61.4065 | 61.1525 | 61.3166 | 61.2237 | -61.6577 | -0.016234 | 0.094219 | 0.14663 | 0.028734 | 0.044968 | 0.035892 | 0.072463 | -0.23036 | -0.045948 | 0.069064 | 0.020823 | 0.25118 | 0.11819 | 0.025241 | 122.72 | 122.6616 | 122.6982 | 61.4196 | -122.642 | 122.5798 | 122.7439 | 122.651 | 61.4368 | -122.8561
437.1719 | 122.8134 | -61.441 | 61.2534 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.038957 | -0.022507 | 0.048226 | 0.0036627 | -0.012148 | 0.029049 | 0.044157 | 0.00070293 | 0.047006 | -61.2853 | -0.012329 | -61.3894 | 61.2926 | 61.2252 | 61.2709 | -61.439 | -61.3628 | 0.009516 | -61.4019 | 61.1525 | 61.3075 | 61.2237 | -61.6531 | 0.002078 | 0.039287 | 0.15579 | 0.051623 | 0.049545 | -0.028198 | 0.017531 | -0.21204 | -0.10088 | 0.078218 | 0.039134 | 0.25118 | 0.054101 | -0.029691 | 122.7337 | 122.6662 | 122.7119 | 61.4287 | -122.6923 | 122.5935 | 122.7485 | 122.6647 | 61.4506 | -122.9064
438.9531 | 122.8592 | -61.3861 | 61.2991 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.03917 | -0.022294 | 0.048226 | 0.0036627 | -0.011934 | 0.029263 | 0.044157 | 0.00091673 | 0.047006 | -61.2715 | -0.007751 | -61.3894 | 61.3064 | 61.2252 | 61.2663 | -61.4344 | -61.3537 | -0.00422 | -61.4019 | 61.1616 | 61.312 | 61.2191 | -61.6485 | -0.048275 | 0.007246 | 0.11459 | -0.003309 | 0.044966 | -0.073974 | -0.032823 | -0.2624 | -0.1375 | 0.032444 | -0.015798 | 0.2466 | 0.012904 | -0.080045 | 122.6925 | 122.6113 | 122.6524 | 61.3784 | -122.7335 | 122.5477 | 122.6981 | 122.6052 | 61.3819 | -122.9476
440.6719 | 122.8912 | -61.409 | 61.2717 | 1.4211e-13 | -0.0023355 | -0.010363 | 0.03917 | -0.02208 | 0.048653 | 0.0036627 | -0.011934 | 0.029049 | 0.044157 | 0.00048933 | 0.047006 | -61.2761 | -0.007751 | -61.3803 | 61.2972 | 61.2297 | 61.2663 | -61.4435 | -61.3537 | -0.00422 | -61.4019 | 61.1571 | 61.3212 | 61.2191 | -61.6439 | -0.034544 | 0.025555 | 0.1329 | 0.028737 | 0.063281 | -0.041929 | -0.005357 | -0.23493 | -0.11461 | 0.055333 | 0.007091 | 0.24202 | 0.049527 | -0.052579 | 122.7062 | 122.6387 | 122.6753 | 61.4012 | -122.7152 | 122.5661 | 122.7302 | 122.6281 | 61.4048 | -122.9156
442.375 | 122.8409 | -61.3907 | 61.3312 | 1.4211e-13 | -0.0019081 | -0.010363 | 0.03917 | -0.022294 | 0.048653 | 0.0036627 | -0.011934 | 0.029049 | 0.04437 | 0.00070293 | 0.047219 | -61.2761 | -0.007751 | -61.3848 | 61.2926 | 61.2252 | 61.2663 | -61.439 | -61.3537 | -0.00422 | -61.4019 | 61.1616 | 61.3029 | 61.2191 | -61.6439 | -0.048276 | -0.038533 | 0.11459 | 0.005848 | 0.054124 | -0.10602 | -0.064867 | -0.25324 | -0.16954 | 0.037022 | -0.01122 | 0.24202 | -0.028297 | -0.11209 | 122.6833 | 122.6158 | 122.657 | 61.3829 | -122.7701 | 122.5523 | 122.6936 | 122.6098 | 61.3865 | -122.9751
444.1406 | 122.8134 | -61.3861 | 61.3495 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.039384 | -0.022294 | 0.048439 | -0.0039678 | -0.01172 | 0.029263 | 0.04437 | 0.00070293 | 0.047006 | -61.2761 | -0.007751 | -61.3894 | 61.2835 | 61.2297 | 61.2617 | -61.439 | -61.3537 | -0.008798 | -61.3927 | 61.1525 | 61.3166 | 61.2191 | -61.6439 | -0.052854 | -0.066 | 0.11001 | -0.003309 | 0.049545 | -0.11975 | -0.087756 | -0.25782 | -0.19701 | 0.032444 | -0.00664 | 0.25118 | -0.032871 | -0.1304 | 122.6696 | 122.6158 | 122.6478 | 61.3784 | -122.7884 | 122.5386 | 122.7027 | 122.6052 | 61.3773 | -122.9934
445.9062 | 122.9279 | -61.3174 | 61.2991 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.038957 | -0.02208 | 0.048439 | -0.011598 | -0.012148 | 0.028835 | 0.044584 | 0.00070293 | 0.047006 | -61.2715 | -0.007751 | -61.3894 | 61.2835 | 61.2252 | 61.2526 | -61.439 | -61.3445 | 0.000359 | -61.4019 | 61.1525 | 61.3075 | 61.2145 | -61.6439 | -0.12152 | -0.015646 | 0.045927 | -0.071973 | 0.049545 | -0.073974 | -0.046559 | -0.32648 | -0.14666 | -0.027063 | -0.084462 | 0.24202 | 0.008325 | -0.084624 | 122.6009 | 122.5426 | 122.57 | 61.3097 | -122.7381 | 122.4699 | 122.6249 | 122.532 | 61.3178 | -122.9431
447.6719 | 122.9416 | -61.3358 | 61.2762 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.038743 | -0.021866 | 0.048226 | -0.0039678 | -0.011934 | 0.029263 | 0.044798 | 0.00091673 | 0.046792 | -61.2715 | -0.007751 | -61.3894 | 61.2926 | 61.2252 | 61.2572 | -61.4298 | -61.3582 | 0.004938 | -61.4019 | 61.1479 | 61.312 | 61.1962 | -61.6485 | -0.09405 | 0.016399 | 0.064237 | -0.053663 | 0.040387 | -0.051086 | -0.019093 | -0.31275 | -0.12835 | -0.022489 | -0.066152 | 0.2466 | 0.035792 | -0.08005 | 122.6284 | 122.5609 | 122.5929 | 61.328 | -122.706 | 122.4837 | 122.6478 | 122.5319 | 61.3407 | -122.9248
449.4531 | 122.85 | -61.3724 | 61.2991 | 1.4211e-13 | -0.0025491 | -0.010363 | 0.039598 | -0.022294 | 0.048653 | 0.0036627 | -0.012148 | 0.029263 | 0.044584 | 0.00091673 | 0.047006 | -61.2715 | -0.007751 | -61.3894 | 61.2926 | 61.2297 | 61.2663 | -61.4344 | -61.3491 | 0.004938 | -61.3882 | 61.1525 | 61.3075 | 61.2145 | -61.6439 | -0.062008 | -0.006489 | 0.10086 | -0.017042 | 0.044966 | -0.069395 | -0.032823 | -0.27155 | -0.14666 | 0.023289 | -0.015795 | 0.25576 | 0.008325 | -0.084624 | 122.665 | 122.6021 | 122.6387 | 61.3646 | -122.7335 | 122.5249 | 122.6798 | 122.5869 | 61.3773 | -122.9431
451.1719 | 122.8775 | -61.441 | 61.2305 | 1.4211e-13 | -0.0023355 | -0.010577 | 0.039384 | -0.022507 | 0.048226 | 0.0036627 | -0.012148 | 0.029049 | 0.044157 | 0.00091673 | 0.047006 | -61.2761 | -0.007751 | -61.394 | 61.2972 | 61.2297 | 61.2572 | -61.4344 | -61.3491 | 0.009516 | -61.3927 | 61.1479 | 61.3075 | 61.2145 | -61.6348 | 0.006657 | 0.066753 | 0.16494 | 0.047045 | 0.040388 | -0.000731 | 0.026683 | -0.19373 | -0.082571 | 0.091954 | 0.048292 | 0.24202 | 0.076989 | -0.01596 | 122.7383 | 122.6708 | 122.6982 | 61.4333 | -122.6649 | 122.5889 | 122.7485 | 122.6555 | 61.4506 | -122.8652
452.9375 | 122.937 | -61.3358 | 61.29 | 1.4211e-13 | -0.0021217 | -0.010363 | 0.039384 | -0.022294 | 0.048653 | -0.0039678 | -0.011934 | 0.029263 | 0.04437 | 0.00070293 | 0.047219 | -61.2669 | -0.012329 | -61.3848 | 61.2926 | 61.2252 | 61.2572 | -61.4298 | -61.3445 | 0.000359 | -61.3882 | 61.1525 | 61.3166 | 61.2099 | -61.6439 | -0.09405 | 0.002666 | 0.068815 | -0.049084 | 0.044966 | -0.064819 | -0.032826 | -0.30817 | -0.1375 | -0.008753 | -0.052416 | 0.25576 | 0.026638 | -0.080047 | 122.6284 | 122.5609 | 122.5929 | 61.3234 | -122.7198 | 122.4882 | 122.6524 | 122.5457 | 61.3361 | -122.9339
454.6562 | 122.9095 | -61.3358 | 61.2854 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.038957 | -0.02208 | 0.048439 | 0.0036627 | -0.012148 | 0.029263 | 0.044798 | 0.00091673 | 0.047006 | -61.2669 | -0.012329 | -61.3848 | 61.2835 | 61.2206 | 61.248 | -61.4298 | -61.3491 | -0.00422 | -61.3927 | 61.1571 | 61.3029 | 61.2145 | -61.6348 | -0.09405 | -0.001913 | 0.068815 | -0.049084 | 0.044966 | -0.06482 | -0.037405 | -0.29902 | -0.12835 | -0.013332 | -0.056994 | 0.24202 | 0.01748 | -0.070891 | 122.6192 | 122.5563 | 122.5837 | 61.3234 | -122.7152 | 122.4928 | 122.6386 | 122.5503 | 61.3315 | -122.9202
456.3594 | 122.9187 | -61.3358 | 61.3037 | 1.4211e-13 | -0.0025491 | -0.01015 | 0.03917 | -0.02208 | 0.048439 | 0.011293 | -0.012148 | 0.028835 | 0.04437 | 0.00091673 | 0.047006 | -61.2669 | -0.007751 | -61.3894 | 61.2926 | 61.2252 | 61.2526 | -61.4344 | -61.3399 | 0.000359 | -61.3882 | 61.1571 | 61.3075 | 61.2191 | -61.6348 | -0.098629 | -0.011067 | 0.068815 | -0.053663 | 0.044966 | -0.078552 | -0.051137 | -0.29902 | -0.14666 | -0.004174 | -0.052416 | 0.2466 | 0.003747 | -0.084623 | 122.6284 | 122.5609 | 122.5883 | 61.328 | -122.7381 | 122.4928 | 122.6432 | 122.5548 | 61.3361 | -122.9385
458.125 | 122.8088 | -61.3724 | 61.3174 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.039384 | -0.022294 | 0.048439 | 0.0036627 | -0.011934 | 0.029263 | 0.04437 | 0.00091673 | 0.046792 | -61.2715 | -0.012329 | -61.3894 | 61.2835 | 61.216 | 61.2572 | -61.4344 | -61.3445 | 0.004938 | -61.3927 | 61.1479 | 61.312 | 61.2145 | -61.6348 | -0.062008 | -0.033957 | 0.10086 | -0.017042 | 0.044966 | -0.10144 | -0.060292 | -0.2624 | -0.16955 | 0.027868 | -0.020373 | 0.24202 | -0.005407 | -0.10294 | 122.6559 | 122.5884 | 122.6295 | 61.36 | -122.7518 | 122.5203 | 122.6844 | 122.5869 | 61.3773 | -122.9522
459.8281 | 122.8088 | -61.3632 | 61.322 | 1.4211e-13 | -0.0019081 | -0.01015 | 0.039598 | -0.022507 | 0.048226 | 0.011293 | -0.011934 | 0.029263 | 0.04437 | 0.00091673 | 0.047433 | -61.2624 | -0.012329 | -61.3894 | 61.2835 | 61.2252 | 61.2572 | -61.439 | -61.3491 | -0.00422 | -61.3927 | 61.1479 | 61.3075 | 61.2054 | -61.6348 | -0.075742 | -0.038534 | 0.10086 | -0.026197 | 0.049545 | -0.096862 | -0.064869 | -0.27155 | -0.17412 | 0.014134 | -0.029528 | 0.24202 | -0.014563 | -0.11667 | 122.6467 | 122.5884 | 122.6204 | 61.3509 | -122.761 | 122.5111 | 122.6707 | 122.5686 | 61.359 | -122.9568
461.5938 | 122.9141 | -61.3541 | 61.2808 | 1.4211e-13 | -0.0019081 | -0.01015 | 0.039384 | -0.022294 | 0.048653 | 0.0036627 | -0.011934 | 0.028835 | 0.04437 | 0.00091673 | 0.047219 | -61.2624 | -0.012329 | -61.3803 | 61.2881 | 61.2206 | 61.2617 | -61.4298 | -61.3399 | 0.004938 | -61.3927 | 61.1525 | 61.3029 | 61.2099 | -61.6393 | -0.075739 | 0.007242 | 0.091705 | -0.026195 | 0.049544 | -0.060243 | -0.019092 | -0.28528 | -0.12835 | 0.014137 | -0.038683 | 0.2466 | 0.022057 | -0.070892 | 122.6421 | 122.5746 | 122.6158 | 61.3417 | -122.7106 | 122.5065 | 122.6569 | 122.564 | 61.359 | -122.9202
463.3125 | 122.8958 | -61.3724 | 61.2213 | 1.4211e-13 | -0.0023355 | -0.010577 | 0.03917 | -0.02208 | 0.048226 | 0.011293 | -0.012148 | 0.029049 | 0.044584 | 0.00091673 | 0.046792 | -61.2715 | -0.012329 | -61.3848 | 61.2835 | 61.2206 | 61.2572 | -61.4252 | -61.3399 | 0.004938 | -61.3882 | 61.1479 | 61.3075 | 61.2099 | -61.6302 | -0.05285 | 0.062174 | 0.10086 | -0.012463 | 0.040387 | -0.000733 | 0.035839 | -0.25782 | -0.073415 | 0.032447 | -0.015795 | 0.24202 | 0.086145 | -0.011382 | 122.6559 | 122.593 | 122.6295 | 61.36 | -122.6465 | 122.5203 | 122.6798 | 122.5823 | 61.3773 | -122.8515
465.0938 | 122.7997 | -61.3632 | 61.3037 | 1.4211e-13 | -0.0025491 | -0.01015 | 0.039384 | -0.022294 | 0.048226 | -0.0039678 | -0.01172 | 0.028835 | 0.045011 | 0.00091673 | 0.046365 | -61.2669 | -0.007751 | -61.3848 | 61.2835 | 61.2252 | 61.2617 | -61.4252 | -61.3445 | 0.000359 | -61.3927 | 61.1479 | 61.3075 | 61.2099 | -61.6348 | -0.062005 | -0.020224 | 0.096281 | -0.021618 | 0.040387 | -0.078552 | -0.04198 | -0.27155 | -0.15581 | 0.018713 | -0.029528 | 0.24202 | 0.003747 | -0.09378 | 122.6467 | 122.5884 | 122.625 | 61.3555 | -122.7289 | 122.5111 | 122.6707 | 122.5732 | 61.3636 | -122.9385
466.7969 | 122.9187 | -61.3953 | 61.2167 | 1.4211e-13 | -0.0023355 | -0.010363 | 0.039384 | -0.022507 | 0.048439 | 0.011293 | -0.011934 | 0.028835 | 0.044157 | 0.00070293 | 0.046792 | -61.2624 | -0.012329 | -61.3848 | 61.2789 | 61.2252 | 61.2617 | -61.4252 | -61.3353 | 0.004938 | -61.3882 | 61.1479 | 61.3075 | 61.2099 | -61.6302 | -0.029961 | 0.062173 | 0.1329 | 0.010426 | 0.040387 | 0.008423 | 0.044995 | -0.23493 | -0.068838 | 0.059914 | 0.007094 | 0.24202 | 0.090722 | -0.006805 | 122.6742 | 122.6204 | 122.657 | 61.3829 | -122.642 | 122.5432 | 122.7027 | 122.6052 | 61.4002 | -122.8469
468.5625 | 122.8317 | -61.3678 | 61.2991 | 1.4211e-13 | -0.0021217 | -0.010363 | 0.039598 | -0.02208 | 0.048012 | 0.011293 | -0.011934 | 0.028835 | 0.044157 | 0.00091673 | 0.046792 | -61.2624 | -0.003172 | -61.3803 | 61.2835 | 61.2206 | 61.2617 | -61.439 | -61.3308 | 0.000359 | -61.3882 | 61.1433 | 61.2937 | 61.2145 | -61.6302 | -0.071164 | -0.015646 | 0.10544 | -0.012462 | 0.058702 | -0.078553 | -0.037402 | -0.26239 | -0.15581 | 0.037027 | -0.020372 | 0.24202 | -0.00541 | -0.084624 | 122.6513 | 122.5884 | 122.6295 | 61.3646 | -122.7381 | 122.5111 | 122.6615 | 122.5823 | 61.3682 | -122.9293
470.2812 | 122.8592 | -61.4136 | 61.2946 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.039384 | -0.02208 | 0.048439 | 0.0036627 | -0.011934 | 0.028835 | 0.04437 | 0.0011303 | 0.046792 | -61.2624 | -0.007751 | -61.3803 | 61.2881 | 61.216 | 61.2572 | -61.4344 | -61.3399 | 0.004938 | -61.3836 | 61.1525 | 61.3075 | 61.2145 | -61.6393 | -0.020809 | -0.006491 | 0.15121 | 0.033314 | 0.054123 | -0.078555 | -0.037404 | -0.22577 | -0.14208 | 0.073646 | 0.029983 | 0.25576 | 0.012902 | -0.080047 | 122.7016 | 122.6296 | 122.6707 | 61.4058 | -122.7289 | 122.5661 | 122.721 | 122.6281 | 61.4185 | -122.9339
472.0469 | 122.905 | -61.3495 | 61.2534 | 1.4211e-13 | -0.0023355 | -0.010363 | 0.039384 | -0.02208 | 0.048439 | 0.011293 | -0.012148 | 0.028835 | 0.04437 | 0.00091673 | 0.046792 | -61.2624 | -0.012329 | -61.3848 | 61.2881 | 61.2114 | 61.2526 | -61.4298 | -61.3353 | 0.000359 | -61.3927 | 61.1433 | 61.2891 | 61.2054 | -61.6256 | -0.080317 | 0.034708 | 0.087127 | -0.035351 | 0.044966 | -0.041935 | -0.000783 | -0.27612 | -0.11004 | 0.014137 | -0.043261 | 0.23286 | 0.035787 | -0.048005 | 122.6376 | 122.5609 | 122.6021 | 61.3372 | -122.6832 | 122.4928 | 122.6386 | 122.5548 | 61.3498 | -122.879
473.8281 | 122.7905 | -61.3953 | 61.3358 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.03917 | -0.02208 | 0.048226 | -0.0039678 | -0.01172 | 0.029049 | 0.04437 | 0.00091673 | 0.046792 | -61.2624 | -0.007751 | -61.3803 | 61.2743 | 61.2114 | 61.2526 | -61.4206 | -61.3353 | 0.004938 | -61.3927 | 61.1387 | 61.3029 | 61.2054 | -61.6256 | -0.025382 | -0.061424 | 0.1329 | 0.015004 | 0.040386 | -0.12433 | -0.08318 | -0.23035 | -0.19701 | 0.059914 | 0.002516 | 0.23286 | -0.032874 | -0.1304 | 122.6696 | 122.6067 | 122.6478 | 61.3875 | -122.7564 | 122.534 | 122.6981 | 122.6006 | 61.4002 | -122.9614
475.625 | 122.9233 | -61.322 | 61.2442 | 1.4211e-13 | -0.0019081 | -0.010363 | 0.03917 | -0.022294 | 0.048653 | 0.0036627 | -0.012361 | 0.029049 | 0.044157 | 0.0011303 | 0.046578 | -61.2578 | -0.012329 | -61.3757 | 61.2835 | 61.216 | 61.2526 | -61.4344 | -61.3353 | 0.000359 | -61.3882 | 61.1433 | 61.2983 | 61.2008 | -61.6302 | -0.11236 | 0.039285 | 0.064239 | -0.053661 | 0.058701 | -0.028201 | 0.008372 | -0.30817 | -0.10088 | -0.013329 | -0.066149 | 0.24202 | 0.054099 | -0.043429 | 122.6055 | 122.538 | 122.5746 | 61.3097 | -122.6786 | 122.4653 | 122.6203 | 122.5228 | 61.3224 | -122.8744
477.4062 | 122.8638 | -61.3724 | 61.235 | 1.4211e-13 | -0.0021217 | -0.010363 | 0.039384 | -0.02208 | 0.048012 | 0.011293 | -0.01172 | 0.028835 | 0.044584 | 0.00091673 | 0.046792 | -61.2624 | -0.012329 | -61.3757 | 61.2789 | 61.2206 | 61.2572 | -61.4161 | -61.3308 | -0.00422 | -61.3836 | 61.1479 | 61.2983 | 61.2099 | -61.6348 | -0.043692 | 0.043863 | 0.11001 | -0.003307 | 0.040385 | -0.014466 | 0.022106 | -0.2624 | -0.087148 | 0.041604 | -0.011216 | 0.25118 | 0.063255 | -0.025115 | 122.6513 | 122.593 | 122.6295 | 61.36 | -122.6511 | 122.5203 | 122.6707 | 122.5823 | 61.3682 | -122.8698
479.125 | 122.7631 | -61.4456 | 61.2579 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.03917 | -0.02208 | 0.048226 | 0.011293 | -0.011934 | 0.029049 | 0.044584 | 0.0011303 | 0.047219 | -61.2669 | -0.012329 | -61.3757 | 61.2743 | 61.2252 | 61.2526 | -61.4298 | -61.3399 | 0.009516 | -61.3836 | 61.1479 | 61.2983 | 61.2054 | -61.6302 | 0.015814 | 0.016395 | 0.17868 | 0.069936 | 0.054122 | -0.032776 | -0.005361 | -0.18457 | -0.11004 | 0.10569 | 0.062027 | 0.2466 | 0.040366 | -0.052583 | 122.7199 | 122.6708 | 122.6982 | 61.4333 | -122.6877 | 122.5935 | 122.7439 | 122.651 | 61.4551 | -122.8881
480.875 | 122.8592 | -61.3998 | 61.2442 | 1.4211e-13 | -0.0021217 | -0.010577 | 0.03917 | -0.022294 | 0.048653 | 0.0036627 | -0.01172 | 0.028835 | 0.04437 | 0.00091673 | 0.047006 | -61.2578 | -0.007751 | -61.3757 | 61.2698 | 61.216 | 61.2526 | -61.4252 | -61.3353 | 0.004938 | -61.3836 | 61.1433 | 61.3075 | 61.2099 | -61.6302 | -0.025384 | 0.02555 | 0.14206 | 0.024159 | 0.049543 | -0.028201 | 0.008372 | -0.23035 | -0.10088 | 0.064491 | 0.01625 | 0.2466 | 0.063256 | -0.034271 | 122.6696 | 122.6158 | 122.6524 | 61.3921 | -122.6694 | 122.5432 | 122.7073 | 122.6098 | 61.4048 | -122.8744
482.5938 | 122.8775 | -61.3724 | 61.2671 | 1.4211e-13 | -0.0019081 | -0.010363 | 0.038957 | -0.022507 | 0.048012 | 0.011293 | -0.011934 | 0.029049 | 0.044157 | 0.00091673 | 0.046365 | -61.2578 | -0.012329 | -61.3757 | 61.2698 | 61.216 | 61.248 | -61.4161 | -61.3399 | 0.000359 | -61.3882 | 61.1433 | 61.2937 | 61.2099 | -61.6302 | -0.043692 | 0.002662 | 0.11459 | -0.003307 | 0.040385 | -0.051089 | -0.019095 | -0.25782 | -0.12377 | 0.032447 | -0.015795 | 0.24202 | 0.026633 | -0.057159 | 122.6421 | 122.5884 | 122.6204 | 61.36 | -122.6832 | 122.5157 | 122.6661 | 122.5823 | 61.3727 | -122.8973
484.3125 | 122.7951 | -61.4136 | 61.2396 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.03917 | -0.022507 | 0.048439 | -0.0039678 | -0.011507 | 0.028835 | 0.04437 | 0.00091673 | 0.046792 | -61.2532 | -0.007751 | -61.3757 | 61.2789 | 61.2206 | 61.2434 | -61.4252 | -61.3353 | 0.009516 | -61.379 | 61.1387 | 61.2937 | 61.2099 | -61.6256 | -0.011651 | 0.039285 | 0.16037 | 0.037892 | 0.049543 | -0.019044 | 0.003793 | -0.21204 | -0.10088 | 0.078224 | 0.034562 | 0.2466 | 0.054099 | -0.029693 | 122.6925 | 122.6342 | 122.657 | 61.4058 | -122.6648 | 122.5523 | 122.7073 | 122.6235 | 61.4231 | -122.8652
486.0938 | 122.8088 | -61.3541 | 61.322 | 1.4211e-13 | -0.0025491 | -0.010363 | 0.039384 | -0.022507 | 0.048012 | 0.0036627 | -0.011934 | 0.029049 | 0.044798 | 0.0011303 | 0.046792 | -61.2578 | -0.007751 | -61.3711 | 61.2743 | 61.2114 | 61.2526 | -61.4252 | -61.3308 | 0.004938 | -61.3744 | 61.1342 | 61.2937 | 61.2054 | -61.621 | -0.07116 | -0.047691 | 0.096283 | -0.017038 | 0.054122 | -0.1106 | -0.069447 | -0.26697 | -0.18786 | 0.023294 | -0.020368 | 0.2466 | -0.028298 | -0.11667 | 122.6284 | 122.5655 | 122.6066 | 61.3463 | -122.7472 | 122.4882 | 122.6478 | 122.5594 | 61.359 | -122.9431
487.8594 | 122.7676 | -61.3403 | 61.2991 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.03917 | -0.022507 | 0.048653 | 0.0036627 | -0.01172 | 0.028835 | 0.044798 | 0.0013439 | 0.047006 | -61.2578 | -0.012329 | -61.3711 | 61.2835 | 61.216 | 61.248 | -61.4252 | -61.3308 | 0.004938 | -61.3744 | 61.1433 | 61.2937 | 61.2008 | -61.6256 | -0.084893 | -0.015646 | 0.08255 | -0.030771 | 0.054122 | -0.083132 | -0.051138 | -0.28528 | -0.15581 | 0.009561 | -0.034101 | 0.25118 | -0.00541 | -0.09836 | 122.6238 | 122.5563 | 122.5883 | 61.328 | -122.7244 | 122.4837 | 122.6341 | 122.5411 | 61.3453 | -122.9247
489.5781 | 122.9141 | -61.3312 | 61.2671 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.039598 | -0.022721 | 0.048226 | 0.0036627 | -0.012148 | 0.028835 | 0.04437 | 0.00070293 | 0.046578 | -61.244 | -0.012329 | -61.3665 | 61.2789 | 61.2068 | 61.248 | -61.4115 | -61.3308 | 0.000359 | -61.379 | 61.1342 | 61.2891 | 61.2054 | -61.6256 | -0.080311 | 0.011819 | 0.08713 | -0.035348 | 0.044963 | -0.060247 | -0.019095 | -0.29444 | -0.13293 | 0.000406 | -0.047835 | 0.2466 | 0.022054 | -0.061738 | 122.6101 | 122.538 | 122.5792 | 61.3188 | -122.6786 | 122.4653 | 122.6203 | 122.5365 | 61.3315 | -122.8927
491.2969 | 122.8271 | -61.3632 | 61.2854 | 1.4211e-13 | -0.0021217 | -0.010363 | 0.03917 | -0.022507 | 0.048012 | 0.0036627 | -0.011934 | 0.029263 | 0.04437 | 0.00070293 | 0.046578 | -61.2578 | -0.012329 | -61.3711 | 61.2652 | 61.2068 | 61.248 | -61.4252 | -61.3308 | 0.004938 | -61.3744 | 61.1387 | 61.2846 | 61.2008 | -61.621 | -0.062005 | -0.020227 | 0.10544 | -0.007883 | 0.054122 | -0.078557 | -0.037405 | -0.25781 | -0.14666 | 0.032449 | -0.011213 | 0.2466 | -0.000835 | -0.084627 | 122.6284 | 122.5701 | 122.6112 | 61.3509 | -122.7106 | 122.502 | 122.6478 | 122.564 | 61.3682 | -122.9064
493.0625 | 122.7631 | -61.4136 | 61.2762 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.039384 | -0.022721 | 0.048226 | -0.0039678 | -0.011934 | 0.029263 | 0.044584 | 0.00091673 | 0.046792 | -61.2532 | -0.003172 | -61.3665 | 61.2743 | 61.216 | 61.2526 | -61.4252 | -61.3308 | 0.000359 | -61.3836 | 61.1342 | 61.28 | 61.1962 | -61.6165 | -0.011651 | -0.001915 | 0.16037 | 0.047049 | 0.0587 | -0.060244 | -0.023671 | -0.20288 | -0.14208 | 0.082803 | 0.029983 | 0.23286 | 0.003742 | -0.08005 | 122.6879 | 122.6296 | 122.6661 | 61.4104 | -122.7015 | 122.5477 | 122.6936 | 122.6098 | 61.4139 | -122.8927
494.8594 | 122.8958 | -61.3403 | 61.2671 | 1.4211e-13 | -0.0023355 | -0.010363 | 0.03917 | -0.02208 | 0.048226 | -0.011598 | -0.012148 | 0.029263 | 0.044157 | 0.00091673 | 0.046792 | -61.2486 | -0.016908 | -61.3711 | 61.2743 | 61.2068 | 61.248 | -61.4161 | -61.3262 | 0.014095 | -61.3744 | 61.1342 | 61.2846 | 61.1962 | -61.6165 | -0.075735 | 0.00724 | 0.091707 | -0.030771 | 0.044964 | -0.060247 | -0.019095 | -0.27612 | -0.13293 | 0.01414 | -0.034101 | 0.24202 | 0.017475 | -0.070895 | 122.6147 | 122.5472 | 122.5883 | 61.3234 | -122.6832 | 122.4745 | 122.6249 | 122.5365 | 61.3544 | -122.8835
496.6406 | 122.7905 | -61.4136 | 61.2671 | 1.4211e-13 | -0.0021217 | -0.010577 | 0.039384 | -0.022507 | 0.048439 | 0.018923 | -0.012148 | 0.028622 | 0.044798 | 0.00091673 | 0.047219 | -61.244 | -0.007751 | -61.3711 | 61.2698 | 61.2206 | 61.2526 | -61.4161 | -61.3308 | 0.000359 | -61.3744 | 61.1387 | 61.2846 | 61.1916 | -61.6256 | -0.002493 | 0.002662 | 0.16953 | 0.042471 | 0.044964 | -0.04651 | -0.014516 | -0.21204 | -0.12835 | 0.082803 | 0.039141 | 0.25118 | 0.017475 | -0.075474 | 122.6833 | 122.6342 | 122.6661 | 61.4058 | -122.6832 | 122.5523 | 122.6981 | 122.6052 | 61.4139 | -122.8927
498.3438 | 122.9141 | -61.3266 | 61.2625 | 1.4211e-13 | -0.0023355 | -0.009936 | 0.039384 | -0.022294 | 0.048226 | 0.0036627 | -0.012148 | 0.028835 | 0.04437 | 0.0011303 | 0.046792 | -61.244 | -0.012329 | -61.3619 | 61.2652 | 61.2114 | 61.2434 | -61.4161 | -61.3262 | 0.004938 | -61.379 | 61.1387 | 61.2846 | 61.1962 | -61.621 | -0.089468 | 0.002661 | 0.082552 | -0.035348 | 0.05412 | -0.05109 | -0.019095 | -0.29443 | -0.12377 | 0.000407 | -0.052413 | 0.24202 | 0.022053 | -0.066317 | 122.5918 | 122.538 | 122.57 | 61.3143 | -122.6786 | 122.4653 | 122.6112 | 122.5228 | 61.3315 | -122.8835
500.125 | 122.8912 | -61.377 | 61.1893 | 1.4211e-13 | -0.0021217 | -0.010363 | 0.038957 | -0.022507 | 0.048226 | 0.018923 | -0.012148 | 0.029049 | 0.044584 | 0.00091673 | 0.046365 | -61.244 | -0.007751 | -61.3619 | 61.2789 | 61.216 | 61.2434 | -61.4069 | -61.3262 | -0.008798 | -61.3744 | 61.1387 | 61.2891 | 61.1916 | -61.6119 | -0.029956 | 0.089639 | 0.13291 | 0.015006 | 0.044962 | 0.026731 | 0.054147 | -0.23492 | -0.050529 | 0.050761 | 0.00252 | 0.23744 | 0.099874 | 0.002346 | 122.6559 | 122.593 | 122.6204 | 61.3692 | -122.5962 | 122.5157 | 122.6661 | 122.5686 | 61.3682 | -122.8011
501.8906 | 122.7448 | -61.3998 | 61.2671 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.03917 | -0.022294 | 0.048226 | -0.0039678 | -0.012148 | 0.028835 | 0.044798 | 0.00091673 | 0.046792 | -61.2624 | -0.003172 | -61.3711 | 61.2698 | 61.216 | 61.248 | -61.4115 | -61.3308 | 0.000359 | -61.3653 | 61.1296 | 61.2846 | 61.2008 | -61.6256 | -0.011647 | 0.002662 | 0.13748 | 0.028738 | 0.040385 | -0.051089 | -0.019095 | -0.22577 | -0.13751 | 0.06907 | 0.034565 | 0.26034 | 0.017475 | -0.066317 | 122.6696 | 122.6158 | 122.6478 | 61.3967 | -122.6786 | 122.5294 | 122.6844 | 122.6006 | 61.4002 | -122.8927
503.6719 | 122.7951 | -61.3678 | 61.2717 | 1.4211e-13 | -0.0019081 | -0.010363 | 0.039384 | -0.022294 | 0.048226 | 0.0036627 | -0.012148 | 0.028622 | 0.044157 | 0.00070293 | 0.046792 | -61.244 | -0.003172 | -61.3665 | 61.2743 | 61.2023 | 61.248 | -61.4115 | -61.3216 | 0.004938 | -61.3699 | 61.125 | 61.28 | 61.1916 | -61.6073 | -0.04369 | 0.002663 | 0.12375 | 0.001273 | 0.044963 | -0.069403 | -0.023672 | -0.2395 | -0.14666 | 0.046185 | -0.002057 | 0.23744 | 0.00832 | -0.080051 | 122.6421 | 122.5701 | 122.6158 | 61.3646 | -122.6832 | 122.4928 | 122.6478 | 122.5594 | 61.3727 | -122.879
505.3906 | 122.8088 | -61.3449 | 61.2762 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.039384 | -0.022507 | 0.048653 | 0.0036627 | -0.011934 | 0.029049 | 0.04437 | 0.00091673 | 0.046578 | -61.2532 | 0.001407 | -61.3665 | 61.2743 | 61.2114 | 61.2434 | -61.4161 | -61.3216 | -0.00422 | -61.3744 | 61.1342 | 61.2846 | 61.1916 | -61.6165 | -0.071157 | -0.001915 | 0.091706 | -0.021615 | 0.049542 | -0.064823 | -0.032828 | -0.27154 | -0.14208 | 0.023297 | -0.029523 | 0.24202 | 0.00832 | -0.084629 | 122.6192 | 122.5563 | 122.5883 | 61.3463 | -122.6923 | 122.4791 | 122.6295 | 122.5365 | 61.3407 | -122.8927
507.1094 | 122.8226 | -61.3724 | 61.2854 | 1.4211e-13 | -0.0019081 | -0.010363 | 0.039384 | -0.022294 | 0.048226 | 0.011293 | -0.011934 | 0.029263 | 0.044584 | 0.00091673 | 0.046792 | -61.2486 | -0.007751 | -61.3619 | 61.2606 | 61.1977 | 61.2434 | -61.4115 | -61.3216 | -0.00422 | -61.379 | 61.1296 | 61.2754 | 61.1916 | -61.6119 | -0.039113 | -0.024805 | 0.12375 | 0.010428 | 0.049541 | -0.087715 | -0.041983 | -0.2395 | -0.15582 | 0.050762 | -0.006637 | 0.23286 | -0.009992 | -0.093784 | 122.633 | 122.5701 | 122.6158 | 61.3646 | -122.6969 | 122.502 | 122.6478 | 122.564 | 61.3682 | -122.8973
508.8906 | 122.7722 | -61.3403 | 61.3083 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.03917 | -0.022721 | 0.048439 | -0.0039678 | -0.011934 | 0.028835 | 0.04437 | 0.0013439 | 0.046578 | -61.244 | -0.007751 | -61.3665 | 61.2652 | 61.216 | 61.2434 | -61.4115 | -61.3216 | 0.004938 | -61.3699 | 61.1204 | 61.2754 | 61.187 | -61.6165 | -0.071156 | -0.043116 | 0.096285 | -0.026193 | 0.044963 | -0.092288 | -0.064872 | -0.27612 | -0.18786 | 0.018719 | -0.029523 | 0.2466 | -0.032881 | -0.12125 | 122.6055 | 122.5563 | 122.5837 | 61.3326 | -122.7198 | 122.4608 | 122.6157 | 122.5274 | 61.3453 | -122.9247
510.6875 | 122.8592 | -61.3678 | 61.2213 | 1.4211e-13 | -0.0019081 | -0.010363 | 0.039384 | -0.022721 | 0.048012 | 0.0036627 | -0.01172 | 0.029263 | 0.044584 | 0.00091673 | 0.046578 | -61.244 | -0.007751 | -61.3619 | 61.2652 | 61.2023 | 61.248 | -61.4069 | -61.317 | 0.000359 | -61.3653 | 61.1342 | 61.2754 | 61.2008 | -61.6119 | -0.039111 | 0.04386 | 0.12375 | 0.005851 | 0.044962 | -0.019049 | 0.026682 | -0.24408 | -0.08715 | 0.050763 | 0.002522 | 0.2466 | 0.054095 | -0.02054 | 122.633 | 122.5701 | 122.6158 | 61.36 | -122.6282 | 122.502 | 122.6432 | 122.5686 | 61.3682 | -122.8332
512.4688 | 122.7585 | -61.3632 | 61.3266 | 1.4211e-13 | -0.0021217 | -0.010363 | 0.039384 | -0.022507 | 0.048226 | -0.0039678 | -0.012148 | 0.028835 | 0.044584 | 0.00070293 | 0.046578 | -61.244 | -0.012329 | -61.3665 | 61.2606 | 61.2023 | 61.2388 | -61.4161 | -61.317 | -0.00422 | -61.3699 | 61.1296 | 61.2846 | 61.1916 | -61.6165 | -0.052847 | -0.066004 | 0.11917 | -0.003305 | 0.049542 | -0.12434 | -0.087761 | -0.25323 | -0.19702 | 0.046185 | -0.006635 | 0.2466 | -0.042034 | -0.13498 | 122.6238 | 122.5655 | 122.6021 | 61.3509 | -122.7427 | 122.4928 | 122.6478 | 122.5548 | 61.359 | -122.9431
514.1719 | 122.7402 | -61.4182 | 61.2442 | 1.4211e-13 | -0.0023355 | -0.009936 | 0.039384 | -0.022507 | 0.048439 | 0.011293 | -0.011934 | 0.028835 | 0.04437 | 0.00091673 | 0.046792 | -61.244 | 0.001407 | -61.3619 | 61.2606 | 61.2068 | 61.2434 | -61.4115 | -61.317 | 0.004938 | -61.3699 | 61.1296 | 61.2754 | 61.1962 | -61.6165 | 0.006664 | 0.016393 | 0.1741 | 0.056205 | 0.049541 | -0.037359 | -0.000785 | -0.1983 | -0.11462 | 0.10112 | 0.048297 | 0.2466 | 0.031206 | -0.048007 | 122.6787 | 122.625 | 122.6616 | 61.4196 | -122.6557 | 122.5477 | 122.6936 | 122.6143 | 61.4231 | -122.8607
515.9375 | 122.7859 | -61.3678 | 61.2488 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.03917 | -0.022507 | 0.048439 | 0.0036627 | -0.012148 | 0.029263 | 0.044584 | 0.0011303 | 0.047006 | -61.2395 | 0.001407 | -61.3574 | 61.2698 | 61.2023 | 61.2434 | -61.4023 | -61.3216 | 0.000359 | -61.3699 | 61.125 | 61.28 | 61.1962 | -61.6165 | -0.034532 | 0.020973 | 0.12833 | 0.010429 | 0.044961 | -0.046515 | -0.005362 | -0.24866 | -0.12377 | 0.046185 | -0.002057 | 0.2466 | 0.031208 | -0.052584 | 122.6376 | 122.5701 | 122.6112 | 61.3692 | -122.6511 | 122.4928 | 122.6478 | 122.564 | 61.3682 | -122.8652
517.6875 | 122.7631 | -61.409 | 61.2579 | 1.4211e-13 | -0.0025491 | -0.01015 | 0.039598 | -0.022721 | 0.048226 | 0.0036627 | -0.011934 | 0.029476 | 0.04437 | 0.00091673 | 0.046792 | -61.244 | 0.001407 | -61.3619 | 61.2698 | 61.2023 | 61.2388 | -61.4161 | -61.3216 | 0.004938 | -61.3607 | 61.125 | 61.2754 | 61.1962 | -61.6165 | -0.00707 | 0.011817 | 0.16495 | 0.04705 | 0.05412 | -0.055671 | -0.019097 | -0.20746 | -0.13293 | 0.087384 | 0.0483 | 0.25576 | 0.017473 | -0.06174 | 122.6787 | 122.6113 | 122.6478 | 61.4104 | -122.674 | 122.534 | 122.6844 | 122.6052 | 61.4139 | -122.8744
519.4688 | 122.8775 | -61.3907 | 61.1572 | 1.4211e-13 | -0.0021217 | -0.010363 | 0.039384 | -0.022721 | 0.048439 | 0.018923 | -0.012148 | 0.029476 | 0.044584 | 0.0011303 | 0.047006 | -61.2349 | 0.005985 | -61.3574 | 61.2652 | 61.2023 | 61.248 | -61.4069 | -61.317 | 0.004938 | -61.3653 | 61.125 | 61.2754 | 61.187 | -61.6119 | -0.016223 | 0.10795 | 0.1558 | 0.033317 | 0.04954 | 0.045037 | 0.090768 | -0.22119 | -0.032221 | 0.073651 | 0.02541 | 0.2466 | 0.11818 | 0.029811 | 122.6559 | 122.593 | 122.6387 | 61.3967 | -122.5641 | 122.5157 | 122.6661 | 122.5777 | 61.3956 | -122.7691
521.1875 | 122.7951 | -61.3815 | 61.2488 | 1.4211e-13 | -0.0025491 | -0.01015 | 0.03917 | -0.022294 | 0.048012 | -0.0039678 | -0.011934 | 0.028408 | 0.04437 | 0.0011303 | 0.047006 | -61.2349 | -0.003172 | -61.3528 | 61.2652 | 61.2023 | 61.2388 | -61.4069 | -61.317 | 0.004938 | -61.3744 | 61.1204 | 61.2708 | 61.1916 | -61.6119 | -0.025378 | 0.016394 | 0.14664 | 0.028741 | 0.054119 | -0.046515 | -0.009941 | -0.23034 | -0.12835 | 0.064496 | 0.007098 | 0.23744 | 0.022051 | -0.057163 | 122.6467 | 122.5838 | 122.6204 | 61.3784 | -122.6557 | 122.502 | 122.6524 | 122.5731 | 61.3865 | -122.8607
522.9531 | 122.8638 | -61.3632 | 61.1755 | 1.4211e-13 | -0.0025491 | -0.009936 | 0.03917 | -0.022507 | 0.048439 | 0.0036627 | -0.01172 | 0.028622 | 0.044584 | 0.0011303 | 0.047006 | -61.2349 | 0.001407 | -61.3574 | 61.2652 | 61.2023 | 61.2388 | -61.4115 | -61.317 | 0.004938 | -61.3699 | 61.125 | 61.2708 | 61.1825 | -61.6119 | -0.048268 | 0.089636 | 0.12833 | 0.005851 | 0.054119 | 0.026727 | 0.063301 | -0.24866 | -0.050531 | 0.046185 | -0.006635 | 0.24202 | 0.095293 | 0.006922 | 122.6284 | 122.5655 | 122.6021 | 61.3646 | -122.587 | 122.4882 | 122.6341 | 122.5457 | 61.3682 | -122.7874
524.6719 | 122.7997 | -61.3174 | 61.2762 | 1.4211e-13 | -0.0019081 | -0.01015 | 0.039384 | -0.022721 | 0.048226 | 0.011293 | -0.012148 | 0.029049 | 0.04437 | 0.0011303 | 0.046792 | -61.244 | 0.001407 | -61.3528 | 61.2606 | 61.2023 | 61.2434 | -61.4115 | -61.317 | 0.004938 | -61.3699 | 61.125 | 61.2708 | 61.1916 | -61.6119 | -0.094044 | -0.01565 | 0.073397 | -0.035346 | 0.058698 | -0.073981 | -0.032828 | -0.29443 | -0.15124 | 0.000409 | -0.052411 | 0.24202 | -0.005415 | -0.084629 | 122.578 | 122.5197 | 122.5609 | 61.3189 | -122.6877 | 122.4425 | 122.5883 | 122.5091 | 61.3224 | -122.8881
526.3906 | 122.8821 | -61.3861 | 61.1801 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.039384 | -0.022294 | 0.048653 | 0.018923 | -0.012361 | 0.028835 | 0.044157 | 0.0011303 | 0.046792 | -61.2395 | -0.003172 | -61.3528 | 61.2606 | 61.2023 | 61.248 | -61.4023 | -61.317 | 0.004938 | -61.3653 | 61.125 | 61.28 | 61.1916 | -61.6165 | -0.016222 | 0.08048 | 0.14664 | 0.033318 | 0.04954 | 0.022149 | 0.06788 | -0.23035 | -0.055109 | 0.069073 | 0.020832 | 0.25118 | 0.099872 | 0.011501 | 122.6467 | 122.5884 | 122.6341 | 61.3829 | -122.5824 | 122.5111 | 122.6661 | 122.5777 | 61.391 | -122.7966
528.1719 | 122.7448 | -61.4182 | 61.2488 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.03917 | -0.022721 | 0.048439 | -0.0039678 | -0.011934 | 0.028835 | 0.044584 | 0.0013439 | 0.047006 | -61.2303 | 0.001407 | -61.3482 | 61.2652 | 61.1977 | 61.2388 | -61.3978 | -61.3125 | 0.004938 | -61.3607 | 61.125 | 61.28 | 61.187 | -61.6165 | 0.0204 | 0.016394 | 0.18784 | 0.06994 | 0.04954 | -0.051094 | -0.009941 | -0.1983 | -0.12377 | 0.1057 | 0.057455 | 0.25576 | 0.031208 | -0.061741 | 122.6833 | 122.6158 | 122.657 | 61.4196 | -122.6465 | 122.5432 | 122.6981 | 122.6052 | 61.4231 | -122.8652
529.9688 | 122.8546 | -61.3678 | 61.1984 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.039384 | -0.022507 | 0.048226 | 0.018923 | -0.011934 | 0.028835 | 0.044584 | 0.00070293 | 0.046578 | -61.2395 | 0.001407 | -61.3574 | 61.2606 | 61.1977 | 61.2343 | -61.4115 | -61.3125 | 0.004938 | -61.3607 | 61.1204 | 61.2754 | 61.187 | -61.6165 | -0.04369 | 0.06217 | 0.12833 | 0.010429 | 0.054119 | -0.00074 | 0.035834 | -0.24866 | -0.077998 | 0.055342 | 0.007101 | 0.25576 | 0.076983 | -0.011387 | 122.6284 | 122.5655 | 122.6021 | 61.3692 | -122.6099 | 122.4882 | 122.6432 | 122.5548 | 61.3727 | -122.8149
531.7344 | 122.8592 | -61.3586 | 61.171 | 1.4211e-13 | -0.0019081 | -0.01015 | 0.039384 | -0.022507 | 0.048439 | 0.0036627 | -0.012148 | 0.028622 | 0.04437 | 0.0013439 | 0.046792 | -61.2303 | -0.003172 | -61.3574 | 61.2606 | 61.1977 | 61.2343 | -61.4069 | -61.3125 | 0.004938 | -61.3607 | 61.1158 | 61.28 | 61.187 | -61.6027 | -0.048266 | 0.089636 | 0.12833 | 0.001274 | 0.04954 | 0.026726 | 0.0633 | -0.24408 | -0.05511 | 0.046187 | -0.002054 | 0.24202 | 0.10903 | 0.016079 | 122.6192 | 122.5563 | 122.5929 | 61.3555 | -122.5779 | 122.4745 | 122.6386 | 122.5457 | 61.3636 | -122.7737
533.4531 | 122.7264 | -61.3861 | 61.2625 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.039384 | -0.022721 | 0.048653 | 0.018923 | -0.012148 | 0.028835 | 0.044157 | 0.0011303 | 0.047006 | -61.2349 | -0.007751 | -61.3528 | 61.2606 | 61.1977 | 61.2343 | -61.4161 | -61.3125 | 0.004938 | -61.3607 | 61.1204 | 61.2708 | 61.187 | -61.6027 | -0.029959 | -0.001917 | 0.15122 | 0.033318 | 0.063277 | -0.064827 | -0.028253 | -0.21661 | -0.14209 | 0.073652 | 0.025411 | 0.24202 | 0.008318 | -0.075474 | 122.6467 | 122.5838 | 122.6204 | 61.3784 | -122.6786 | 122.5065 | 122.6569 | 122.5731 | 61.391 | -122.8652
535.1875 | 122.8226 | -61.3449 | 61.235 | 1.4211e-13 | -0.0021217 | -0.010363 | 0.03917 | -0.02208 | 0.048439 | 0.011293 | -0.011934 | 0.029049 | 0.044584 | 0.0011303 | 0.047006 | -61.2349 | -0.007751 | -61.3528 | 61.2514 | 61.1977 | 61.2297 | -61.4069 | -61.317 | 0.000359 | -61.3561 | 61.1296 | 61.2663 | 61.1825 | -61.6027 | -0.061999 | 0.016392 | 0.11002 | -0.00788 | 0.054119 | -0.037361 | -0.005365 | -0.25781 | -0.10546 | 0.027875 | -0.011209 | 0.2466 | 0.031205 | -0.052587 | 122.5963 | 122.5426 | 122.5746 | 61.3372 | -122.642 | 122.4745 | 122.6112 | 122.5274 | 61.3453 | -122.8378
536.9375 | 122.8455 | -61.2762 | 61.2671 | 1.4211e-13 | -0.0016945 | -0.010363 | 0.038743 | -0.022507 | 0.048226 | 0.0036627 | -0.012148 | 0.028835 | 0.044584 | 0.00091673 | 0.046578 | -61.2349 | -0.007751 | -61.3482 | 61.256 | 61.1885 | 61.2388 | -61.4069 | -61.3125 | 0.014095 | -61.3561 | 61.1204 | 61.2708 | 61.187 | -61.6073 | -0.13066 | -0.011073 | 0.041355 | -0.071967 | 0.058697 | -0.078562 | -0.028252 | -0.33105 | -0.14666 | -0.036211 | -0.079874 | 0.25118 | 0.00374 | -0.080052 | 122.5323 | 122.4648 | 122.5151 | 61.2685 | -122.674 | 122.3967 | 122.5471 | 122.4633 | 61.2903 | -122.8744
538.7188 | 122.8546 | -61.3815 | 61.1618 | 1.4211e-13 | -0.0023355 | -0.009936 | 0.038957 | -0.022721 | 0.048226 | -0.0039678 | -0.011934 | 0.029049 | 0.04437 | 0.0011303 | 0.046792 | -61.2349 | 0.005985 | -61.3482 | 61.256 | 61.1977 | 61.2434 | -61.4069 | -61.3125 | 0.009516 | -61.3607 | 61.1158 | 61.2708 | 61.187 | -61.6073 | -0.025378 | 0.094213 | 0.14664 | 0.033319 | 0.058697 | 0.035881 | 0.081613 | -0.22577 | -0.045955 | 0.069075 | 0.020834 | 0.2466 | 0.10903 | 0.025234 | 122.6375 | 122.5792 | 122.6249 | 61.3875 | -122.5687 | 122.4974 | 122.6524 | 122.5686 | 61.391 | -122.7691
540.5 | 122.8683 | -61.2854 | 61.2579 | 1.4211e-13 | -0.0019081 | -0.01015 | 0.03917 | -0.022507 | 0.048439 | -0.0039678 | -0.011934 | 0.028835 | 0.04437 | 0.0011303 | 0.046792 | -61.2303 | -0.003172 | -61.3528 | 61.256 | 61.1977 | 61.2388 | -61.4115 | -61.3033 | 0.000359 | -61.3515 | 61.1204 | 61.2617 | 61.1825 | -61.6027 | -0.12609 | -0.001918 | 0.055088 | -0.06739 | 0.058698 | -0.06025 | -0.019097 | -0.31732 | -0.13751 | -0.017899 | -0.06614 | 0.25118 | 0.003737 | -0.075476 | 122.5414 | 122.4831 | 122.5242 | 61.2822 | -122.6694 | 122.4058 | 122.5471 | 122.4679 | 61.2858 | -122.8607
542.2188 | 122.7814 | -61.3449 | 61.2808 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.03917 | -0.02208 | 0.048226 | -0.0039678 | -0.01172 | 0.028835 | 0.044798 | 0.00091673 | 0.046578 | -61.2349 | -0.012329 | -61.3482 | 61.2514 | 61.1977 | 61.2251 | -61.4023 | -61.3079 | 0.009516 | -61.3607 | 61.1158 | 61.2663 | 61.1825 | -61.6073 | -0.05742 | -0.029385 | 0.11002 | -0.003302 | 0.054118 | -0.083138 | -0.055721 | -0.26239 | -0.16497 | 0.037033 | -0.015787 | 0.2466 | -0.014572 | -0.098364 | 122.5963 | 122.5426 | 122.57 | 61.3326 | -122.6832 | 122.4608 | 122.6112 | 122.5274 | 61.3544 | -122.8881
544 | 122.8134 | -61.3861 | 61.1847 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.03917 | -0.022507 | 0.048226 | 0.011293 | -0.012361 | 0.028835 | 0.04437 | 0.0011303 | 0.047006 | -61.2303 | 0.001407 | -61.3528 | 61.2514 | 61.1977 | 61.2343 | -61.3978 | -61.3033 | 0.009516 | -61.3515 | 61.1158 | 61.2708 | 61.1825 | -61.5981 | -0.011644 | 0.066746 | 0.1558 | 0.033318 | 0.044962 | 0.012993 | 0.049567 | -0.21203 | -0.068843 | 0.082809 | 0.034568 | 0.2466 | 0.086138 | -0.002233 | 122.6375 | 122.5838 | 122.6204 | 61.3875 | -122.5824 | 122.502 | 122.6569 | 122.5686 | 61.3956 | -122.7828
545.7031 | 122.8409 | -61.3266 | 61.2534 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.03917 | -0.02208 | 0.048226 | 0.0036627 | -0.01172 | 0.028835 | 0.044584 | 0.0011303 | 0.046792 | -61.2303 | -0.003172 | -61.3528 | 61.2514 | 61.1885 | 61.2251 | -61.3978 | -61.3079 | 0.009516 | -61.3515 | 61.1158 | 61.2708 | 61.1825 | -61.6027 | -0.071153 | -0.001919 | 0.096287 | -0.026191 | 0.044962 | -0.064829 | -0.028255 | -0.27612 | -0.13751 | 0.018722 | -0.024941 | 0.25118 | 0.017473 | -0.070898 | 122.578 | 122.5151 | 122.5517 | 61.3234 | -122.6511 | 122.4424 | 122.5974 | 122.5091 | 61.3361 | -122.8561
547.4844 | 122.8271 | -61.3632 | 61.1984 | 1.4211e-13 | -0.0023355 | -0.010363 | 0.039384 | -0.022294 | 0.048439 | 0.0036627 | -0.011934 | 0.029049 | 0.044157 | 0.0011303 | 0.046792 | -61.2303 | 0.001407 | -61.3482 | 61.2514 | 61.1839 | 61.2343 | -61.4069 | -61.3125 | 0.004938 | -61.3515 | 61.1113 | 61.2617 | 61.187 | -61.6073 | -0.043689 | 0.053013 | 0.13291 | 0.015008 | 0.058697 | -0.014476 | 0.035834 | -0.24408 | -0.087155 | 0.050764 | 0.01168 | 0.25576 | 0.063247 | -0.011387 | 122.6147 | 122.5472 | 122.5975 | 61.3646 | -122.6053 | 122.4745 | 122.6249 | 122.5503 | 61.3682 | -122.8057
549.2031 | 122.85 | -61.2854 | 61.2762 | 1.4211e-13 | -0.0023355 | -0.009936 | 0.039598 | -0.022507 | 0.048653 | 0.011293 | -0.011934 | 0.028622 | 0.044584 | 0.0011303 | 0.046792 | -61.2257 | -0.007751 | -61.3528 | 61.2469 | 61.1885 | 61.2343 | -61.4023 | -61.3033 | 0.009516 | -61.3515 | 61.1113 | 61.2571 | 61.1779 | -61.6027 | -0.11693 | -0.029385 | 0.059667 | -0.06739 | 0.04954 | -0.087717 | -0.041986 | -0.31732 | -0.16498 | -0.017899 | -0.06614 | 0.25118 | -0.019151 | -0.098365 | 122.5323 | 122.4739 | 122.5197 | 61.2776 | -122.6786 | 122.3967 | 122.5425 | 122.4633 | 61.2949 | -122.879
550.9844 | 122.7676 | -61.3632 | 61.2396 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.039384 | -0.022721 | 0.048226 | 0.011293 | -0.01172 | 0.028835 | 0.04437 | 0.0011303 | 0.046792 | -61.2257 | -0.007751 | -61.3528 | 61.2514 | 61.1931 | 61.2297 | -61.4023 | -61.3033 | 0.004938 | -61.3561 | 61.1204 | 61.2617 | 61.1733 | -61.6073 | -0.03911 | 0.011814 | 0.13749 | 0.01043 | 0.04954 | -0.046517 | -0.009943 | -0.24408 | -0.1192 | 0.059921 | 0.007101 | 0.25118 | 0.022048 | -0.066322 | 122.6147 | 122.5563 | 122.5929 | 61.3555 | -122.642 | 122.4836 | 122.6249 | 122.5365 | 61.3682 | -122.8469
552.75 | 122.8409 | -61.3129 | 61.2625 | 1.4211e-13 | -0.0019081 | -0.01015 | 0.039384 | -0.022294 | 0.048867 | 0.0036627 | -0.012148 | 0.029049 | 0.044584 | 0.00091673 | 0.046792 | -61.2257 | -0.007751 | -61.3482 | 61.256 | 61.1931 | 61.2297 | -61.3932 | -61.3033 | 0.000359 | -61.3515 | 61.125 | 61.2663 | 61.1779 | -61.6073 | -0.080307 | -0.006495 | 0.087133 | -0.035346 | 0.044961 | -0.069405 | -0.032831 | -0.29443 | -0.13751 | 0.009567 | -0.038674 | 0.25576 | 0.003739 | -0.084632 | 122.5689 | 122.506 | 122.5425 | 61.3051 | -122.6557 | 122.4379 | 122.5791 | 122.4907 | 61.3132 | -122.8698
554.5312 | 122.7402 | -61.3953 | 61.2076 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.039598 | -0.022507 | 0.048226 | 0.018923 | -0.012361 | 0.029049 | 0.044584 | 0.0013439 | 0.047006 | -61.2257 | 0.001407 | -61.3574 | 61.256 | 61.1885 | 61.2343 | -61.4023 | -61.3033 | 0.014095 | -61.347 | 61.1158 | 61.2708 | 61.1779 | -61.6027 | -0.007066 | 0.048436 | 0.16953 | 0.037895 | 0.044961 | -0.019053 | 0.026678 | -0.20745 | -0.091732 | 0.091965 | 0.048303 | 0.25576 | 0.063249 | -0.029701 | 122.6513 | 122.5838 | 122.6295 | 61.3967 | -122.6099 | 122.5111 | 122.6661 | 122.5731 | 61.4094 | -122.8103
556.25 | 122.7676 | -61.3174 | 61.2671 | 1.4211e-13 | -0.0019081 | -0.01015 | 0.039384 | -0.022721 | 0.048012 | -0.0039678 | -0.011934 | 0.028408 | 0.044584 | 0.0013439 | 0.046792 | -61.2212 | -0.003172 | -61.3482 | 61.2469 | 61.1839 | 61.2251 | -61.3978 | -61.2987 | 0.000359 | -61.3515 | 61.1158 | 61.2663 | 61.1825 | -61.6027 | -0.080308 | -0.02023 | 0.096289 | -0.030768 | 0.04954 | -0.083141 | -0.041988 | -0.28527 | -0.15124 | 0.018724 | -0.034096 | 0.25118 | -0.000839 | -0.084631 | 122.5643 | 122.5014 | 122.5425 | 61.3143 | -122.6648 | 122.4333 | 122.5837 | 122.4999 | 61.3178 | -122.8698
558.0156 | 122.7585 | -61.3403 | 61.2808 | 1.4211e-13 | -0.0019081 | -0.0097224 | 0.039811 | -0.02208 | 0.048226 | 0.0036627 | -0.012148 | 0.029049 | 0.044584 | 0.0011303 | 0.046792 | -61.2257 | -0.003172 | -61.3482 | 61.2514 | 61.1885 | 61.2297 | -61.3978 | -61.2987 | 0.000359 | -61.3515 | 61.1067 | 61.2663 | 61.1825 | -61.5936 | -0.05742 | -0.029385 | 0.1146 | -0.00788 | 0.04954 | -0.092295 | -0.051142 | -0.25323 | -0.17413 | 0.041612 | -0.011208 | 0.24202 | -0.014572 | -0.098364 | 122.5918 | 122.5289 | 122.57 | 61.3372 | -122.6786 | 122.447 | 122.6066 | 122.5228 | 61.3407 | -122.8744
559.7812 | 122.7997 | -61.3632 | 61.1664 | 1.4211e-13 | -0.0019081 | -0.010363 | 0.039384 | -0.02208 | 0.048439 | 0.0036627 | -0.011934 | 0.028835 | 0.044584 | 0.0013439 | 0.046792 | -61.2257 | -0.003172 | -61.3482 | 61.2514 | 61.1977 | 61.2343 | -61.3932 | -61.2896 | -0.00422 | -61.3515 | 61.1204 | 61.2571 | 61.1733 | -61.6073 | -0.029953 | 0.085056 | 0.13749 | 0.015008 | 0.044961 | 0.031303 | 0.067877 | -0.24408 | -0.045955 | 0.073658 | 0.01168 | 0.25576 | 0.090712 | 0.00692 | 122.6147 | 122.5609 | 122.5975 | 61.36 | -122.5596 | 122.4836 | 122.6203 | 122.5365 | 61.359 | -122.7737
561.5 | 122.7127 | -61.3907 | 61.2305 | 1.4211e-13 | -0.0023355 | -0.010363 | 0.039384 | -0.022721 | 0.048012 | 0.018923 | -0.012575 | 0.029049 | 0.044584 | 0.00091673 | 0.047006 | -61.2212 | -0.003172 | -61.3528 | 61.2606 | 61.1885 | 61.2297 | -61.3886 | -61.2987 | 0.009516 | -61.347 | 61.1021 | 61.2708 | 61.1825 | -61.5981 | 0.002092 | 0.030126 | 0.16953 | 0.037896 | 0.035804 | -0.041941 | -0.000788 | -0.20745 | -0.12836 | 0.091966 | 0.043725 | 0.25118 | 0.040361 | -0.04801 | 122.6513 | 122.5792 | 122.6204 | 61.3875 | -122.6191 | 122.4928 | 122.6615 | 122.5731 | 61.4002 | -122.8286
563.2656 | 122.7127 | -61.3266 | 61.3174 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.03917 | -0.022721 | 0.048012 | 0.0036627 | -0.011934 | 0.029263 | 0.044157 | 0.00091673 | 0.046792 | -61.2166 | -0.003172 | -61.3482 | 61.2423 | 61.1839 | 61.2297 | -61.3932 | -61.2987 | 0.004938 | -61.347 | 61.1021 | 61.2571 | 61.1733 | -61.5981 | -0.066574 | -0.075163 | 0.11002 | -0.021613 | 0.044961 | -0.1335 | -0.087763 | -0.27154 | -0.21533 | 0.027879 | -0.020362 | 0.25118 | -0.06035 | -0.14414 | 122.5689 | 122.5105 | 122.5563 | 61.3234 | -122.7106 | 122.4287 | 122.5837 | 122.4999 | 61.3315 | -122.9156
565.0312 | 122.8409 | -61.2991 | 61.2488 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.03917 | -0.022507 | 0.048439 | -0.0039678 | -0.011934 | 0.028835 | 0.044157 | 0.0011303 | 0.046792 | -61.2257 | -0.007751 | -61.3436 | 61.2469 | 61.1794 | 61.2251 | -61.3886 | -61.2941 | 0.004938 | -61.347 | 61.1067 | 61.2617 | 61.1687 | -61.5981 | -0.089461 | -0.001919 | 0.0734 | -0.044501 | 0.04496 | -0.069409 | -0.023677 | -0.29901 | -0.14209 | 0.004992 | -0.047828 | 0.25118 | 0.012893 | -0.080056 | 122.546 | 122.4785 | 122.5242 | 61.2914 | -122.6374 | 122.4058 | 122.5608 | 122.4679 | 61.3041 | -122.8469
566.7969 | 122.8363 | -61.2991 | 61.2305 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.039598 | -0.022507 | 0.048012 | 0.0036627 | -0.012148 | 0.028408 | 0.044157 | 0.00091673 | 0.047006 | -61.2166 | -0.003172 | -61.3482 | 61.2469 | 61.1885 | 61.2251 | -61.3886 | -61.2941 | 0.000359 | -61.347 | 61.1021 | 61.2571 | 61.1779 | -61.5981 | -0.089461 | 0.016391 | 0.082556 | -0.049079 | 0.040382 | -0.041941 | -0.005367 | -0.29901 | -0.12836 | 0.004992 | -0.047828 | 0.25118 | 0.026625 | -0.052589 | 122.546 | 122.4877 | 122.5242 | 61.296 | -122.6191 | 122.4012 | 122.5562 | 122.477 | 61.2995 | -122.8286
568.5156 | 122.731 | -61.3495 | 61.2122 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.039598 | -0.022721 | 0.048226 | -0.011598 | -0.011934 | 0.028622 | 0.044157 | 0.00091673 | 0.046578 | -61.2212 | -0.007751 | -61.3436 | 61.2514 | 61.1839 | 61.2297 | -61.3932 | -61.2987 | 0.000359 | -61.3378 | 61.1021 | 61.2708 | 61.1733 | -61.5936 | -0.043686 | 0.03928 | 0.12833 | 0.005853 | 0.049539 | -0.028209 | 0.017523 | -0.24407 | -0.11004 | 0.050767 | 0.011683 | 0.25576 | 0.058672 | -0.038856 | 122.6009 | 122.5334 | 122.5792 | 61.3417 | -122.6053 | 122.4516 | 122.6203 | 122.5228 | 61.3498 | -122.8057
570.2344 | 122.85 | -61.3174 | 61.2213 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.039384 | -0.022721 | 0.048012 | 0.011293 | -0.012148 | 0.028835 | 0.044584 | 0.0013439 | 0.046792 | -61.2166 | -0.003172 | -61.3482 | 61.2377 | 61.1839 | 61.2297 | -61.3886 | -61.2987 | 0.000359 | -61.347 | 61.1021 | 61.2617 | 61.1779 | -61.5936 | -0.07115 | 0.01639 | 0.10087 | -0.030768 | 0.040382 | -0.037364 | 0.008368 | -0.27612 | -0.1192 | 0.018724 | -0.029517 | 0.2466 | 0.040359 | -0.043433 | 122.5551 | 122.5014 | 122.5471 | 61.3143 | -122.6099 | 122.4196 | 122.5791 | 122.4953 | 61.3178 | -122.8149
572 | 122.6898 | -61.377 | 61.2122 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.039384 | -0.022721 | 0.048226 | 0.0036627 | -0.012361 | 0.028835 | 0.04437 | 0.0013439 | 0.046578 | -61.2212 | -0.003172 | -61.3436 | 61.2423 | 61.1885 | 61.2297 | -61.3886 | -61.2987 | 0.000359 | -61.3378 | 61.1067 | 61.2617 | 61.1687 | -61.5936 | -0.011641 | 0.030123 | 0.1558 | 0.033319 | 0.04496 | -0.02363 | 0.017523 | -0.21661 | -0.10547 | 0.078233 | 0.039149 | 0.25576 | 0.049514 | -0.043435 | 122.6192 | 122.5655 | 122.6066 | 61.3738 | -122.6008 | 122.4836 | 122.6386 | 122.5457 | 61.3773 | -122.8057
573.7188 | 122.7402 | -61.3449 | 61.2534 | 1.4211e-13 | -0.0021217 | -0.010363 | 0.039384 | -0.022507 | 0.048226 | 0.0036627 | -0.012148 | 0.029263 | 0.04437 | 0.0011303 | 0.046792 | -61.212 | -0.012329 | -61.3391 | 61.2377 | 61.1839 | 61.2251 | -61.384 | -61.3033 | -0.00422 | -61.3424 | 61.1067 | 61.2571 | 61.1641 | -61.5936 | -0.039105 | -0.015654 | 0.13291 | 0.005855 | 0.04496 | -0.069408 | -0.028255 | -0.24865 | -0.14666 | 0.041611 | 0.002528 | 0.25118 | 0.003737 | -0.089213 | 122.5826 | 122.5289 | 122.57 | 61.3326 | -122.6374 | 122.4516 | 122.602 | 122.5091 | 61.3407 | -122.8469
575.5 | 122.7493 | -61.3449 | 61.2534 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.039384 | -0.022507 | 0.048226 | 0.0036627 | -0.012148 | 0.028835 | 0.044584 | 0.0013439 | 0.046792 | -61.2166 | -0.007751 | -61.3391 | 61.2469 | 61.1794 | 61.2205 | -61.3886 | -61.2941 | 0.004938 | -61.3378 | 61.0975 | 61.2617 | 61.1779 | -61.5981 | -0.043684 | -0.006497 | 0.12833 | 0.005855 | 0.049539 | -0.073987 | -0.032833 | -0.25323 | -0.15582 | 0.050769 | 0.007106 | 0.26034 | 0.008315 | -0.075477 | 122.5918 | 122.5243 | 122.5654 | 61.3372 | -122.642 | 122.4424 | 122.6066 | 122.5228 | 61.3498 | -122.8515
577.2031 | 122.7127 | -61.3358 | 61.2671 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.039598 | -0.022294 | 0.047799 | 0.011293 | -0.011934 | 0.028622 | 0.044157 | 0.00091673 | 0.047006 | -61.2166 | -0.007751 | -61.3482 | 61.2423 | 61.1794 | 61.2251 | -61.3886 | -61.2987 | 0.009516 | -61.3378 | 61.1021 | 61.2617 | 61.1641 | -61.5981 | -0.05284 | -0.024809 | 0.11918 | -0.012458 | 0.040382 | -0.08772 | -0.041988 | -0.26239 | -0.16498 | 0.037034 | -0.00205 | 0.26034 | -0.005418 | -0.10295 | 122.578 | 122.5151 | 122.5609 | 61.328 | -122.6557 | 122.4379 | 122.5974 | 122.4999 | 61.3453 | -122.8652
578.9688 | 122.8455 | -61.3037 | 61.235 | 1.4211e-13 | -0.0025491 | -0.009936 | 0.039384 | -0.022294 | 0.048012 | 0.0036627 | -0.011934 | 0.028835 | 0.044157 | 0.00070293 | 0.046792 | -61.2166 | 0.001407 | -61.3391 | 61.2377 | 61.1794 | 61.2297 | -61.3886 | -61.2896 | 0.004938 | -61.3424 | 61.1067 | 61.2571 | 61.1733 | -61.5981 | -0.084883 | 0.002657 | 0.087134 | -0.035344 | 0.049539 | -0.055676 | -0.005365 | -0.29443 | -0.12835 | 0.014149 | -0.038671 | 0.25576 | 0.022048 | -0.061744 | 122.5414 | 122.4831 | 122.5334 | 61.3051 | -122.6236 | 122.4104 | 122.5608 | 122.477 | 61.3086 | -122.8332
580.75 | 122.8134 | -61.2808 | 61.2488 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.039598 | -0.022294 | 0.048012 | 0.0036627 | -0.01172 | 0.028835 | 0.044157 | 0.0011303 | 0.046578 | -61.2212 | -0.007751 | -61.3345 | 61.2469 | 61.1794 | 61.2251 | -61.3794 | -61.2987 | 0.004938 | -61.3378 | 61.1067 | 61.2617 | 61.1779 | -61.5844 | -0.098613 | -0.001919 | 0.059668 | -0.053654 | 0.044959 | -0.069409 | -0.023677 | -0.30358 | -0.14209 | -0.017897 | -0.056981 | 0.2466 | 0.012893 | -0.070899 | 122.5277 | 122.4602 | 122.5059 | 61.2731 | -122.6282 | 122.3875 | 122.5425 | 122.4587 | 61.2858 | -122.8332
582.5312 | 122.8409 | -61.29 | 61.2167 | 1.4211e-13 | -0.0019081 | -0.0097224 | 0.03917 | -0.022721 | 0.048012 | -0.0039678 | -0.012148 | 0.028835 | 0.044157 | 0.00091673 | 0.046792 | -61.2212 | -0.003172 | -61.3345 | 61.2423 | 61.1794 | 61.2159 | -61.3794 | -61.285 | 0.004938 | -61.3332 | 61.1067 | 61.2617 | 61.155 | -61.6027 | -0.089458 | 0.025545 | 0.068823 | -0.044499 | 0.044959 | -0.037366 | -0.000791 | -0.31274 | -0.11004 | 0.004994 | -0.043247 | 0.26949 | 0.044936 | -0.061749 | 122.5323 | 122.4693 | 122.5059 | 61.2868 | -122.5962 | 122.3967 | 122.5516 | 122.445 | 61.2949 | -122.8195
584.25 | 122.7036 | -61.3953 | 61.2213 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.039384 | -0.022507 | 0.048226 | 0.0036627 | -0.012148 | 0.029049 | 0.044157 | 0.0011303 | 0.046578 | -61.2212 | 0.001407 | -61.3391 | 61.2377 | 61.1839 | 61.2251 | -61.384 | -61.285 | 0.004938 | -61.3424 | 61.1021 | 61.2617 | 61.1733 | -61.5936 | 0.011249 | 0.01639 | 0.17411 | 0.056209 | 0.04496 | -0.037364 | 0.003789 | -0.1983 | -0.1192 | 0.11028 | 0.052882 | 0.25118 | 0.040359 | -0.048011 | 122.633 | 122.5792 | 122.6204 | 61.3967 | -122.6053 | 122.4974 | 122.6569 | 122.5686 | 61.4002 | -122.8149
586.0156 | 122.6898 | -61.3266 | 61.2808 | 1.4211e-13 | -0.0016945 | -0.009936 | 0.039384 | -0.022935 | 0.048226 | 0.0036627 | -0.011934 | 0.028835 | 0.044584 | 0.0011303 | 0.046792 | -61.2166 | -0.007751 | -61.3391 | 61.2423 | 61.1794 | 61.2159 | -61.384 | -61.2941 | 0.000359 | -61.3332 | 61.1067 | 61.2525 | 61.1687 | -61.5981 | -0.057416 | -0.038542 | 0.11002 | -0.012456 | 0.04496 | -0.10145 | -0.064878 | -0.27154 | -0.17413 | 0.032458 | -0.006626 | 0.26491 | -0.028308 | -0.1121 | 122.5689 | 122.506 | 122.5425 | 61.3188 | -122.6648 | 122.4333 | 122.5791 | 122.4953 | 61.327 | -122.879
587.7812 | 122.8043 | -61.3403 | 61.171 | 1.4211e-13 | -0.0023355 | -0.009936 | 0.039598 | -0.022294 | 0.048012 | 0.0036627 | -0.011934 | 0.029049 | 0.044157 | 0.0013439 | 0.046792 | -61.2212 | -0.003172 | -61.3391 | 61.2423 | 61.1839 | 61.2297 | -61.3794 | -61.285 | 0.004938 | -61.3378 | 61.1021 | 61.2525 | 61.1779 | -61.589 | -0.039104 | 0.071322 | 0.11918 | 0.001277 | 0.040381 | 0.01299 | 0.058722 | -0.24865 | -0.068846 | 0.055348 | 0.002528 | 0.25118 | 0.081556 | 0.006921 | 122.5826 | 122.5243 | 122.57 | 61.3372 | -122.5504 | 122.4424 | 122.5928 | 122.5182 | 61.3453 | -122.7599
589.5 | 122.818 | -61.2946 | 61.2167 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.039384 | -0.022294 | 0.047799 | 0.011293 | -0.012148 | 0.029049 | 0.044157 | 0.0013439 | 0.046578 | -61.2166 | -0.007751 | -61.3299 | 61.2331 | 61.1702 | 61.2159 | -61.3794 | -61.2896 | 0.004938 | -61.3332 | 61.1067 | 61.2479 | 61.155 | -61.5798 | -0.08488 | 0.016389 | 0.077979 | -0.035343 | 0.049537 | -0.046524 | -0.000791 | -0.28527 | -0.11004 | 0.004994 | -0.038669 | 0.2466 | 0.031201 | -0.061749 | 122.5277 | 122.4648 | 122.5105 | 61.2868 | -122.5962 | 122.4012 | 122.5425 | 122.4495 | 61.2995 | -122.7966
591.2188 | 122.7905 | -61.3358 | 61.1572 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.039384 | -0.022721 | 0.047799 | -0.0039678 | -0.012361 | 0.028835 | 0.044157 | 0.0011303 | 0.046578 | -61.2212 | -0.003172 | -61.3391 | 61.2377 | 61.1794 | 61.2159 | -61.3794 | -61.2941 | 0.004938 | -61.3332 | 61.0975 | 61.2479 | 61.1733 | -61.5844 | -0.043682 | 0.080476 | 0.1146 | -0.003301 | 0.040381 | 0.022143 | 0.058718 | -0.24865 | -0.059692 | 0.041613 | 0.002529 | 0.25118 | 0.09071 | 0.016075 | 122.5735 | 122.5151 | 122.5517 | 61.3326 | -122.5367 | 122.4333 | 122.5837 | 122.5091 | 61.3407 | -122.7416
593 | 122.731 | -61.3266 | 61.2076 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.039598 | -0.022721 | 0.047799 | -0.0039678 | -0.011934 | 0.028408 | 0.04437 | 0.0013439 | 0.046792 | -61.212 | 0.001407 | -61.3345 | 61.2331 | 61.1794 | 61.2205 | -61.3886 | -61.285 | 0.000359 | -61.3378 | 61.0975 | 61.2571 | 61.1641 | -61.589 | -0.061995 | 0.025544 | 0.1146 | -0.007878 | 0.054117 | -0.028211 | 0.012943 | -0.26238 | -0.11005 | 0.041615 | -0.011205 | 0.25118 | 0.049513 | -0.043437 | 122.5597 | 122.506 | 122.5471 | 61.328 | -122.5962 | 122.4241 | 122.5837 | 122.4907 | 61.327 | -122.7966
594.7656 | 122.818 | -61.2625 | 61.2259 | 1.4211e-13 | -0.0023355 | -0.0095086 | 0.039384 | -0.022507 | 0.048226 | 0.0036627 | -0.012148 | 0.028835 | 0.04437 | 0.0011303 | 0.046578 | -61.2074 | -0.003172 | -61.3391 | 61.2285 | 61.1794 | 61.2114 | -61.3749 | -61.285 | 0.000359 | -61.3332 | 61.0975 | 61.2525 | 61.1687 | -61.589 | -0.11234 | 0.002655 | 0.055092 | -0.076543 | 0.035802 | -0.046521 | -0.014525 | -0.32647 | -0.12836 | -0.022472 | -0.070713 | 0.25576 | 0.026624 | -0.057168 | 122.4911 | 122.4419 | 122.4739 | 61.2593 | -122.6007 | 122.36 | 122.515 | 122.4312 | 61.2629 | -122.8149
596.5625 | 122.7127 | -61.3678 | 61.1893 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.039598 | -0.022721 | 0.047585 | 0.011293 | -0.012361 | 0.029049 | 0.044584 | 0.0013439 | 0.046578 | -61.2074 | -0.007751 | -61.3299 | 61.2377 | 61.1839 | 61.2205 | -61.3749 | -61.2896 | 0.009516 | -61.3332 | 61.0975 | 61.2571 | 61.1596 | -61.5844 | -0.007059 | 0.048433 | 0.16038 | 0.037899 | 0.044958 | -0.005321 | 0.031254 | -0.21661 | -0.091735 | 0.078236 | 0.034573 | 0.25118 | 0.067824 | -0.029704 | 122.6055 | 122.5517 | 122.5883 | 61.36 | -122.5641 | 122.4653 | 122.6249 | 122.5274 | 61.3773 | -122.7737
598.2812 | 122.7997 | -61.2671 | 61.2396 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.039811 | -0.022935 | 0.048226 | 0.0036627 | -0.011934 | 0.029049 | 0.044157 | 0.00091673 | 0.046578 | -61.212 | 0.001407 | -61.3299 | 61.2331 | 61.1794 | 61.2205 | -61.3749 | -61.285 | 0.004938 | -61.3332 | 61.093 | 61.2479 | 61.1687 | -61.589 | -0.10777 | -0.006499 | 0.055092 | -0.062809 | 0.044958 | -0.060254 | -0.0191 | -0.32189 | -0.14667 | -0.017894 | -0.066135 | 0.25576 | 0.008313 | -0.070901 | 122.5002 | 122.4465 | 122.4876 | 61.2685 | -122.6145 | 122.36 | 122.515 | 122.4358 | 61.272 | -122.8286
600.0469 | 122.7219 | -61.3449 | 61.2122 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.039384 | -0.022721 | 0.048226 | 0.018923 | -0.012148 | 0.028835 | 0.04437 | 0.00091673 | 0.046578 | -61.212 | -0.007751 | -61.3299 | 61.2331 | 61.1748 | 61.2205 | -61.3749 | -61.2941 | 0.000359 | -61.3286 | 61.093 | 61.2388 | 61.1641 | -61.5798 | -0.029947 | 0.020967 | 0.13291 | 0.015011 | 0.044958 | -0.037367 | 0.008366 | -0.23491 | -0.1192 | 0.050769 | 0.016264 | 0.25118 | 0.026621 | -0.048014 | 122.578 | 122.5197 | 122.5654 | 61.3372 | -122.587 | 122.4379 | 122.5837 | 122.5091 | 61.3453 | -122.792
601.8281 | 122.7173 | -61.3815 | 61.1893 | 1.4211e-13 | -0.0019081 | -0.01015 | 0.03917 | -0.022721 | 0.048439 | 0.011293 | -0.012575 | 0.028835 | 0.04437 | 0.00091673 | 0.047219 | -61.212 | 0.001407 | -61.3253 | 61.2331 | 61.1794 | 61.2159 | -61.3703 | -61.285 | 0.000359 | -61.3332 | 61.1067 | 61.2479 | 61.1641 | -61.589 | 0.011253 | 0.043855 | 0.16953 | 0.05621 | 0.044957 | -0.0099 | 0.026675 | -0.20745 | -0.082578 | 0.096547 | 0.048306 | 0.25576 | 0.058667 | -0.025126 | 122.6147 | 122.5609 | 122.5975 | 61.3829 | -122.5595 | 122.4882 | 122.6295 | 122.5457 | 61.3819 | -122.7783
603.6094 | 122.7493 | -61.3083 | 61.2442 | 1.4211e-13 | -0.0021217 | -0.0097224 | 0.03917 | -0.022294 | 0.047799 | 0.018923 | -0.011934 | 0.028835 | 0.044157 | 0.0015577 | 0.046792 | -61.2074 | -0.007751 | -61.3253 | 61.2285 | 61.1794 | 61.2159 | -61.3749 | -61.285 | 0.004938 | -61.3424 | 61.0975 | 61.2479 | 61.1641 | -61.5844 | -0.066568 | -0.015656 | 0.10087 | -0.017032 | 0.049536 | -0.064832 | -0.028257 | -0.27611 | -0.14667 | 0.023305 | -0.034093 | 0.24202 | 0.003735 | -0.080058 | 122.5368 | 122.4877 | 122.5242 | 61.3005 | -122.6191 | 122.4058 | 122.5562 | 122.4724 | 61.3132 | -122.8286
605.3281 | 122.6715 | -61.3724 | 61.2259 | 1.4211e-13 | -0.0023355 | -0.009936 | 0.039598 | -0.022721 | 0.048226 | 0.0036627 | -0.011934 | 0.028835 | 0.044157 | 0.0011303 | 0.046578 | -61.2074 | -0.003172 | -61.3345 | 61.2377 | 61.1794 | 61.2205 | -61.3794 | -61.2804 | 0.009516 | -61.3332 | 61.1021 | 61.2434 | 61.1641 | -61.5798 | -0.007061 | 0.011812 | 0.16495 | 0.037898 | 0.044959 | -0.046521 | -0.005367 | -0.20745 | -0.12378 | 0.09197 | 0.03915 | 0.2466 | 0.017467 | -0.061747 | 122.6101 | 122.5517 | 122.5929 | 61.3692 | -122.6053 | 122.4745 | 122.6157 | 122.5365 | 61.3819 | -122.8057
607.0938 | 122.7173 | -61.3266 | 61.2579 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.039598 | -0.022507 | 0.047585 | -0.0039678 | -0.011934 | 0.028835 | 0.044157 | 0.0011303 | 0.046792 | -61.212 | -0.007751 | -61.3299 | 61.2331 | 61.1656 | 61.2205 | -61.3749 | -61.2804 | 0.009516 | -61.3286 | 61.0975 | 61.2434 | 61.1641 | -61.5752 | -0.048258 | -0.02481 | 0.1146 | -0.0033 | 0.044958 | -0.092302 | -0.037411 | -0.24865 | -0.1604 | 0.046194 | -0.002047 | 0.2466 | -0.014577 | -0.093791 | 122.5597 | 122.4922 | 122.5471 | 61.3188 | -122.6328 | 122.4241 | 122.57 | 122.4907 | 61.3361 | -122.8332
608.8594 | 122.6761 | -61.2946 | 61.2762 | 1.4211e-13 | -0.0016945 | -0.01015 | 0.039598 | -0.022507 | 0.048012 | 0.0036627 | -0.011934 | 0.028835 | 0.04437 | 0.0013439 | 0.047219 | -61.212 | -0.007751 | -61.3299 | 61.2331 | 61.1702 | 61.2114 | -61.3749 | -61.285 | 0.004938 | -61.3241 | 61.0975 | 61.2388 | 61.1596 | -61.5798 | -0.080301 | -0.04312 | 0.082558 | -0.035343 | 0.044958 | -0.10603 | -0.064879 | -0.28527 | -0.17871 | 0.009572 | -0.029512 | 0.25576 | -0.037466 | -0.11668 | 122.5277 | 122.4648 | 122.5059 | 61.2868 | -122.6511 | 122.3921 | 122.5333 | 122.4541 | 61.2995 | -122.8561
610.6562 | 122.8043 | -61.2808 | 61.2259 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.039598 | -0.022935 | 0.048226 | -0.0039678 | -0.011934 | 0.029049 | 0.04437 | 0.0015577 | 0.046578 | -61.2166 | -0.007751 | -61.3299 | 61.224 | 61.1702 | 61.2159 | -61.3749 | -61.2804 | 0.004938 | -61.3332 | 61.093 | 61.2479 | 61.1504 | -61.5798 | -0.094034 | -0.001923 | 0.064246 | -0.049076 | 0.044958 | -0.055679 | -0.009946 | -0.299 | -0.13293 | 0.000418 | -0.052402 | 0.2466 | 0.022046 | -0.075482 | 122.5048 | 122.451 | 122.4968 | 61.2731 | -122.6007 | 122.3738 | 122.5288 | 122.4312 | 61.2858 | -122.8057
612.375 | 122.7264 | -61.3495 | 61.2259 | 1.4211e-13 | -0.0019081 | -0.01015 | 0.039598 | -0.022507 | 0.048012 | 0.0036627 | -0.012148 | 0.028622 | 0.04437 | 0.00070293 | 0.046365 | -61.2028 | -0.007751 | -61.3391 | 61.2331 | 61.1748 | 61.2159 | -61.3749 | -61.2758 | 0.004938 | -61.3241 | 61.0975 | 61.2434 | 61.1641 | -61.5844 | -0.02537 | 0.007234 | 0.14665 | 0.010432 | 0.035802 | -0.0511 | -0.009946 | -0.23492 | -0.12836 | 0.073661 | 0.025419 | 0.26034 | 0.017467 | -0.061747 | 122.5826 | 122.5243 | 122.5654 | 61.3417 | -122.6007 | 122.447 | 122.5928 | 122.5136 | 61.3544 | -122.8103
614.1562 | 122.7219 | -61.3129 | 61.2396 | 1.4211e-13 | -0.0016945 | -0.01015 | 0.039384 | -0.022507 | 0.048012 | 0.018923 | -0.01172 | 0.028835 | 0.044157 | 0.0011303 | 0.046578 | -61.2074 | 0.001407 | -61.3299 | 61.2331 | 61.1748 | 61.2114 | -61.3749 | -61.2804 | 0.004938 | -61.3286 | 61.093 | 61.2388 | 61.1687 | -61.5798 | -0.061991 | -0.006499 | 0.10545 | -0.017033 | 0.044958 | -0.064833 | -0.028258 | -0.26696 | -0.14667 | 0.032461 | -0.01578 | 0.25118 | -0.000845 | -0.070901 | 122.546 | 122.4877 | 122.5242 | 61.3143 | -122.6145 | 122.4058 | 122.5516 | 122.4816 | 61.3178 | -122.8194
615.9531 | 122.699 | -61.3129 | 61.2625 | 1.4211e-13 | -0.0019081 | -0.01015 | 0.03917 | -0.022721 | 0.047585 | 0.011293 | -0.011934 | 0.028622 | 0.04437 | 0.0011303 | 0.046151 | -61.2028 | -0.007751 | -61.3345 | 61.2285 | 61.1611 | 61.2159 | -61.3794 | -61.2804 | 0.004938 | -61.3286 | 61.0884 | 61.2388 | 61.1641 | -61.5798 | -0.06657 | -0.033966 | 0.11003 | -0.021611 | 0.044959 | -0.10146 | -0.046567 | -0.26696 | -0.17413 | 0.032461 | -0.01578 | 0.25118 | -0.023733 | -0.098368 | 122.5414 | 122.4739 | 122.5288 | 61.3051 | -122.6419 | 122.4012 | 122.5516 | 122.477 | 61.3178 | -122.8423
617.7344 | 122.7173 | -61.2946 | 61.29 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.039384 | -0.022721 | 0.047799 | 0.011293 | -0.012361 | 0.028622 | 0.04437 | 0.0011303 | 0.046365 | -61.2028 | -0.007751 | -61.3345 | 61.224 | 61.1702 | 61.2205 | -61.3749 | -61.2804 | 0.000359 | -61.3332 | 61.0884 | 61.2434 | 61.1641 | -61.589 | -0.080301 | -0.06601 | 0.091715 | -0.039921 | 0.04038 | -0.11977 | -0.069454 | -0.29442 | -0.2016 | 0.014151 | -0.038669 | 0.25576 | -0.04662 | -0.12583 | 122.5185 | 122.4648 | 122.5151 | 61.2868 | -122.6648 | 122.3829 | 122.5379 | 122.4587 | 61.2949 | -122.879
619.5 | 122.7448 | -61.3495 | 61.1618 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.040025 | -0.022721 | 0.048012 | 0.0036627 | -0.012148 | 0.028835 | 0.044157 | 0.0013439 | 0.046365 | -61.2074 | -0.003172 | -61.3345 | 61.2331 | 61.1656 | 61.2205 | -61.3657 | -61.2804 | 0.009516 | -61.3241 | 61.093 | 61.2342 | 61.155 | -61.5752 | -0.016212 | 0.071321 | 0.14207 | 0.01501 | 0.031222 | 0.003829 | 0.05872 | -0.22576 | -0.068848 | 0.069082 | 0.025419 | 0.25118 | 0.072397 | -0.006817 | 122.5826 | 122.5151 | 122.57 | 61.3463 | -122.5275 | 122.4424 | 122.5837 | 122.5045 | 61.359 | -122.737
621.2812 | 122.6532 | -61.3541 | 61.1893 | 1.4211e-13 | -0.0019081 | -0.01015 | 0.039384 | -0.022507 | 0.047799 | 0.0036627 | -0.012361 | 0.029049 | 0.04437 | 0.0013439 | 0.047006 | -61.212 | -0.007751 | -61.3482 | 61.2194 | 61.1702 | 61.2114 | -61.3749 | -61.285 | 0.014095 | -61.3241 | 61.0975 | 61.2342 | 61.1596 | -61.5798 | -0.020792 | 0.03012 | 0.14207 | 0.005853 | 0.026645 | -0.019058 | 0.022096 | -0.22576 | -0.091735 | 0.069081 | 0.029997 | 0.25576 | 0.044931 | -0.029704 | 122.5735 | 122.5243 | 122.5654 | 61.3463 | -122.5641 | 122.4516 | 122.5883 | 122.5136 | 61.3682 | -122.7691
622.9844 | 122.6807 | -61.377 | 61.1938 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.03917 | -0.022721 | 0.047799 | 0.0036627 | -0.01172 | 0.028622 | 0.04437 | 0.0011303 | 0.046365 | -61.2028 | 0.001407 | -61.3528 | 61.224 | 61.1748 | 61.2159 | -61.3657 | -61.2804 | 0.014095 | -61.3149 | 61.0884 | 61.2388 | 61.1596 | -61.5752 | 0.011254 | 0.03012 | 0.17411 | 0.024163 | 0.012909 | -0.019057 | 0.022097 | -0.19829 | -0.10547 | 0.096548 | 0.062043 | 0.26034 | 0.044931 | -0.034282 | 122.6009 | 122.5517 | 122.5929 | 61.3784 | -122.5595 | 122.4653 | 122.6157 | 122.5365 | 61.391 | -122.7691
624.75 | 122.7173 | -61.3129 | 61.2625 | 1.4211e-13 | -0.0019081 | -0.010363 | 0.039384 | -0.022507 | 0.048226 | 0.0036627 | -0.012148 | 0.028835 | 0.044157 | 0.0013439 | 0.046578 | -61.2028 | -0.021486 | -61.3482 | 61.224 | 61.1702 | 61.2114 | -61.3703 | -61.2712 | 0.004938 | -61.3241 | 61.0884 | 61.2296 | 61.1641 | -61.5798 | -0.057412 | -0.038544 | 0.11003 | -0.035346 | 0.022066 | -0.0923 | -0.051146 | -0.26696 | -0.17413 | 0.041618 | -0.011202 | 0.25576 | -0.03289 | -0.098368 | 122.5368 | 122.4831 | 122.5242 | 61.2914 | -122.6328 | 122.4012 | 122.5425 | 122.477 | 61.3178 | -122.8423
626.4531 | 122.7264 | -61.3586 | 61.1618 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.039384 | -0.022507 | 0.047799 | 0.011293 | -0.011934 | 0.029049 | 0.04437 | 0.0011303 | 0.046792 | -61.2074 | -0.003172 | -61.3482 | 61.2285 | 61.1748 | 61.2068 | -61.3611 | -61.2758 | 0.009516 | -61.3149 | 61.0884 | 61.2342 | 61.1596 | -61.5752 | -0.002477 | 0.066742 | 0.15122 | 0.010431 | 0.012908 | 0.012987 | 0.044984 | -0.2166 | -0.073426 | 0.082817 | 0.043733 | 0.26034 | 0.072397 | -0.002238 | 122.5872 | 122.5334 | 122.5654 | 61.3555 | -122.5229 | 122.447 | 122.5928 | 122.5182 | 61.3682 | -122.737
628.1562 | 122.7036 | -61.2991 | 61.2488 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.039598 | -0.022721 | 0.048012 | 0.0036627 | -0.011507 | 0.029049 | 0.044157 | 0.0011303 | 0.046578 | -61.2028 | -0.003172 | -61.3528 | 61.224 | 61.1748 | 61.2114 | -61.3657 | -61.2712 | 0.000359 | -61.3241 | 61.0884 | 61.2342 | 61.155 | -61.5798 | -0.066566 | -0.024811 | 0.096292 | -0.053657 | 0.012909 | -0.073988 | -0.037413 | -0.28069 | -0.1604 | 0.027885 | -0.024935 | 0.25576 | -0.014578 | -0.093792 | 122.5231 | 122.4739 | 122.5105 | 61.296 | -122.6145 | 122.3875 | 122.5333 | 122.4541 | 61.2995 | -122.8286
629.9531 | 122.7631 | -61.3403 | 61.1664 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.039811 | -0.022294 | 0.048226 | 0.011293 | -0.011934 | 0.029049 | 0.044584 | 0.00091673 | 0.046792 | -61.2028 | -0.007751 | -61.3574 | 61.224 | 61.1702 | 61.2068 | -61.3703 | -61.2758 | 0.004938 | -61.3195 | 61.0975 | 61.2479 | 61.155 | -61.5752 | -0.029946 | 0.057586 | 0.13749 | -0.017037 | 0.012909 | 0.00383 | 0.040406 | -0.23491 | -0.068847 | 0.064506 | 0.020843 | 0.25576 | 0.081555 | -0.011395 | 122.5643 | 122.5105 | 122.5471 | 61.3326 | -122.5367 | 122.4379 | 122.5883 | 122.4953 | 61.3453 | -122.7416
631.7344 | 122.7356 | -61.2808 | 61.2488 | 1.4211e-13 | -0.0019081 | -0.01015 | 0.039384 | -0.022507 | 0.047799 | 0.0036627 | -0.01172 | 0.028835 | 0.044157 | 0.0013439 | 0.046792 | -61.1937 | -0.007751 | -61.3528 | 61.2194 | 61.1611 | 61.2114 | -61.3657 | -61.2667 | 0.009516 | -61.3241 | 61.0838 | 61.2388 | 61.1504 | -61.5798 | -0.084876 | -0.029389 | 0.087138 | -0.071967 | 0.012909 | -0.087725 | -0.037413 | -0.299 | -0.16498 | 0.014154 | -0.043245 | 0.25576 | -0.01 | -0.09837 | 122.5002 | 122.4419 | 122.4922 | 61.2731 | -122.6145 | 122.3646 | 122.5196 | 122.4312 | 61.2903 | -122.8286
633.4375 | 122.6624 | -61.377 | 61.2122 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.039598 | -0.022507 | 0.048012 | 0.0036627 | -0.011934 | 0.028835 | 0.044157 | 0.0011303 | 0.047006 | -61.1983 | 0.005985 | -61.3482 | 61.2194 | 61.1656 | 61.2068 | -61.3657 | -61.2712 | 0.000359 | -61.3241 | 61.0838 | 61.2342 | 61.155 | -61.5798 | 0.011254 | 0.007232 | 0.17869 | 0.028741 | 0.017487 | -0.046525 | -0.00537 | -0.20287 | -0.12836 | 0.10571 | 0.052885 | 0.25576 | 0.022043 | -0.057171 | 122.5963 | 122.5426 | 122.5837 | 61.3829 | -122.5779 | 122.4608 | 122.6112 | 122.5319 | 61.3773 | -122.792
635.1406 | 122.6669 | -61.3632 | 61.1984 | 1.4211e-13 | -0.0021217 | -0.0097224 | 0.039598 | -0.022507 | 0.048012 | -0.0039678 | -0.011507 | 0.028835 | 0.043729 | 0.0011303 | 0.046578 | -61.1937 | -0.007751 | -61.3528 | 61.2194 | 61.1656 | 61.2068 | -61.3703 | -61.2712 | 0.004938 | -61.3241 | 61.0838 | 61.2342 | 61.155 | -61.5798 | -0.007058 | 0.020965 | 0.16953 | 0.01043 | 0.017488 | -0.032792 | 0.008363 | -0.2166 | -0.11463 | 0.091972 | 0.039152 | 0.25576 | 0.035776 | -0.043438 | 122.5826 | 122.5289 | 122.57 | 61.3555 | -122.5687 | 122.447 | 122.5974 | 122.5182 | 61.3682 | -122.7782
636.9062 | 122.7402 | -61.3129 | 61.2167 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.03917 | -0.022507 | 0.047799 | 0.0036627 | -0.012361 | 0.029049 | 0.044584 | 0.0013439 | 0.046578 | -61.1937 | -0.007751 | -61.3528 | 61.224 | 61.1611 | 61.2068 | -61.3657 | -61.2712 | 0.004938 | -61.3195 | 61.093 | 61.2479 | 61.155 | -61.5752 | -0.052833 | 0.007232 | 0.11918 | -0.039924 | 0.012909 | -0.055682 | -0.009948 | -0.26238 | -0.12378 | 0.041618 | -0.006623 | 0.25576 | 0.031201 | -0.061749 | 122.5368 | 122.4739 | 122.5197 | 61.3051 | -122.5824 | 122.4058 | 122.5608 | 122.4679 | 61.3178 | -122.792
638.6875 | 122.6624 | -61.3678 | 61.1801 | 1.4211e-13 | -0.0023355 | -0.010363 | 0.03917 | -0.022507 | 0.047799 | 0.011293 | -0.012148 | 0.028622 | 0.044157 | 0.0013439 | 0.046792 | -61.1983 | -0.007751 | -61.3528 | 61.2194 | 61.1656 | 61.2114 | -61.3657 | -61.2621 | 0.000359 | -61.3149 | 61.0792 | 61.2342 | 61.1641 | -61.5661 | 0.002099 | 0.039275 | 0.16954 | 0.015008 | 0.012909 | -0.014482 | 0.031251 | -0.19829 | -0.10089 | 0.10571 | 0.052888 | 0.25118 | 0.054086 | -0.015971 | 122.5872 | 122.5334 | 122.5792 | 61.36 | -122.5458 | 122.447 | 122.602 | 122.5319 | 61.3682 | -122.7462
640.4844 | 122.7951 | -61.2671 | 61.203 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.039598 | -0.022294 | 0.048226 | -0.0039678 | -0.011934 | 0.028622 | 0.04437 | 0.0013439 | 0.047006 | -61.1937 | 0.001407 | -61.3482 | 61.2194 | 61.1656 | 61.2114 | -61.3611 | -61.2667 | 0.004938 | -61.3195 | 61.0792 | 61.2434 | 61.1504 | -61.5707 | -0.09403 | 0.016387 | 0.073405 | -0.081122 | 0.012908 | -0.03737 | 0.008363 | -0.30358 | -0.12378 | 0.000421 | -0.052399 | 0.25118 | 0.040355 | -0.052594 | 122.4865 | 122.4327 | 122.4785 | 61.2685 | -122.5641 | 122.3463 | 122.5104 | 122.4175 | 61.272 | -122.7737
642.1875 | 122.699 | -61.3174 | 61.2396 | 1.4211e-13 | -0.0016945 | -0.009936 | 0.039384 | -0.022721 | 0.048012 | 0.011293 | -0.01172 | 0.028835 | 0.044157 | 0.0013439 | 0.046578 | -61.1891 | -0.003172 | -61.3436 | 61.2194 | 61.1611 | 61.2114 | -61.3657 | -61.2667 | 0.014095 | -61.3149 | 61.0746 | 61.2388 | 61.1504 | -61.5752 | -0.048255 | -0.020234 | 0.12834 | -0.02619 | 0.022065 | -0.07857 | -0.028258 | -0.2578 | -0.16498 | 0.050775 | 0.002534 | 0.26034 | -0.000845 | -0.089215 | 122.5368 | 122.4785 | 122.5288 | 61.3143 | -122.6053 | 122.3921 | 122.5562 | 122.4679 | 61.3315 | -122.8149
643.8906 | 122.6852 | -61.3312 | 61.235 | 1.4211e-13 | -0.0023355 | -0.009936 | 0.03917 | -0.022507 | 0.048012 | -0.0039678 | -0.011934 | 0.028835 | 0.044157 | 0.0015577 | 0.046792 | -61.1983 | 0.005985 | -61.3528 | 61.2148 | 61.1702 | 61.2114 | -61.3657 | -61.2667 | 0.004938 | -61.3058 | 61.0792 | 61.225 | 61.1504 | -61.5707 | -0.034522 | -0.020235 | 0.13291 | -0.021613 | 0.012909 | -0.064834 | -0.02368 | -0.23949 | -0.15583 | 0.064508 | 0.025424 | 0.26491 | -0.010002 | -0.084637 | 122.546 | 122.5014 | 122.5425 | 61.3372 | -122.6007 | 122.4104 | 122.5562 | 122.4816 | 61.3361 | -122.8057
645.6094 | 122.6578 | -61.3037 | 61.2717 | 1.4211e-13 | -0.0016945 | -0.01015 | 0.03917 | -0.022721 | 0.047799 | 0.011293 | -0.011934 | 0.028622 | 0.044157 | 0.0013439 | 0.046365 | -61.1937 | -0.007751 | -61.3436 | 61.2148 | 61.1611 | 61.1976 | -61.3565 | -61.2667 | 0.014095 | -61.3149 | 61.0838 | 61.2296 | 61.1458 | -61.5569 | -0.05283 | -0.056856 | 0.11003 | -0.039923 | 0.012907 | -0.11061 | -0.074036 | -0.25322 | -0.18787 | 0.037042 | -0.011199 | 0.24202 | -0.042045 | -0.12584 | 122.5185 | 122.4648 | 122.5013 | 61.296 | -122.6282 | 122.3875 | 122.5333 | 122.4495 | 61.3178 | -122.8286
647.3281 | 122.644 | -61.3586 | 61.1847 | 1.4211e-13 | -0.0021217 | -0.010363 | 0.039384 | -0.022294 | 0.048012 | 0.011293 | -0.011934 | 0.028835 | 0.043943 | 0.0011303 | 0.046792 | -61.1937 | 0.005985 | -61.3528 | 61.224 | 61.1656 | 61.2022 | -61.3657 | -61.2667 | 0.014095 | -61.3195 | 61.0792 | 61.2342 | 61.155 | -61.5707 | -0.007056 | 0.039276 | 0.16496 | 0.005853 | 0.012909 | -0.019059 | 0.017517 | -0.21202 | -0.10547 | 0.091974 | 0.039154 | 0.25118 | 0.049509 | -0.029705 | 122.5826 | 122.5243 | 122.5609 | 61.3646 | -122.5504 | 122.4379 | 122.5928 | 122.5136 | 61.3727 | -122.7554
649.0938 | 122.6532 | -61.3632 | 61.1938 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.03917 | -0.022507 | 0.048012 | 0.011293 | -0.012361 | 0.028835 | 0.04437 | 0.0013439 | 0.046578 | -61.1937 | 0.001407 | -61.3528 | 61.224 | 61.1611 | 61.2022 | -61.3611 | -61.2575 | 0.004938 | -61.3103 | 61.0746 | 61.2296 | 61.1458 | -61.5661 | 0.0021 | 0.03012 | 0.16953 | 0.01043 | 0.00833 | -0.032794 | 0.008361 | -0.20287 | -0.11921 | 0.10571 | 0.052888 | 0.25576 | 0.035774 | -0.048018 | 122.5872 | 122.5243 | 122.5654 | 61.3646 | -122.555 | 122.4379 | 122.5928 | 122.5091 | 61.3682 | -122.7599
650.875 | 122.7448 | -61.3129 | 61.1847 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.039384 | -0.022507 | 0.048012 | 0.011293 | -0.012148 | 0.028835 | 0.04437 | 0.0013439 | 0.046365 | -61.1937 | -0.007751 | -61.3482 | 61.2102 | 61.1611 | 61.1976 | -61.3565 | -61.2621 | 0.000359 | -61.3103 | 61.0746 | 61.2342 | 61.1504 | -61.5707 | -0.043675 | 0.025541 | 0.11918 | -0.035346 | 0.008329 | -0.023638 | 0.012939 | -0.2578 | -0.11005 | 0.050776 | 0.002534 | 0.26033 | 0.049509 | -0.034283 | 122.5231 | 122.4739 | 122.5105 | 61.3051 | -122.5412 | 122.3875 | 122.5471 | 122.4633 | 61.3132 | -122.7554
652.6875 | 122.6715 | -61.3129 | 61.2534 | 1.4211e-13 | -0.0023355 | -0.01015 | 0.039384 | -0.022721 | 0.048226 | 0.0036627 | -0.012148 | 0.028835 | 0.044157 | 0.0013439 | 0.046792 | -61.1845 | -0.003172 | -61.3528 | 61.2194 | 61.1611 | 61.2068 | -61.3657 | -61.2621 | 0.009516 | -61.3149 | 61.0746 | 61.2296 | 61.1504 | -61.5707 | -0.052833 | -0.033967 | 0.12834 | -0.039924 | 0.012909 | -0.092303 | -0.046569 | -0.2578 | -0.17872 | 0.050776 | -0.002044 | 0.25576 | -0.023735 | -0.10295 | 122.5323 | 122.4739 | 122.5197 | 61.3097 | -122.6191 | 122.3875 | 122.5425 | 122.4633 | 61.3224 | -122.824
654.4688 | 122.7173 | -61.2991 | 61.1893 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.039384 | -0.022721 | 0.047585 | 0.011293 | -0.011934 | 0.028835 | 0.044157 | 0.0011303 | 0.046151 | -61.1891 | -0.012329 | -61.3436 | 61.2148 | 61.1611 | 61.2068 | -61.3611 | -61.2621 | 0.004938 | -61.3149 | 61.0838 | 61.2296 | 61.1458 | -61.5707 | -0.061987 | 0.025541 | 0.11003 | -0.044501 | 0.017486 | -0.028216 | 0.017518 | -0.27153 | -0.10547 | 0.037043 | -0.015777 | 0.25576 | 0.040352 | -0.04344 | 122.5139 | 122.4602 | 122.5059 | 61.2868 | -122.5504 | 122.3829 | 122.5288 | 122.445 | 61.3041 | -122.7599
656.1875 | 122.6486 | -61.3724 | 61.171 | 1.4211e-13 | -0.0023355 | -0.010363 | 0.039384 | -0.022507 | 0.048012 | 0.0036627 | -0.012361 | 0.028835 | 0.044157 | 0.0015577 | 0.046365 | -61.1937 | -0.003172 | -61.3482 | 61.224 | 61.1565 | 61.2114 | -61.3565 | -61.2712 | 0.000359 | -61.3058 | 61.0746 | 61.225 | 61.1504 | -61.5752 | 0.015834 | 0.053009 | 0.17869 | 0.024163 | 0.008329 | -0.014484 | 0.040407 | -0.20287 | -0.096317 | 0.10113 | 0.066622 | 0.26949 | 0.054085 | -0.02055 | 122.5963 | 122.5289 | 122.5837 | 61.3692 | -122.5275 | 122.447 | 122.5974 | 122.5228 | 61.3727 | -122.7462
657.9688 | 122.7219 | -61.3037 | 61.203 | 1.4211e-13 | -0.0021217 | -0.010363 | 0.039598 | -0.022721 | 0.048012 | 0.0036627 | -0.011934 | 0.028835 | 0.044157 | 0.0013439 | 0.046365 | -61.1845 | -0.007751 | -61.3482 | 61.2148 | 61.1565 | 61.2114 | -61.3565 | -61.2575 | 0.000359 | -61.3103 | 61.0838 | 61.2342 | 61.1504 | -61.5707 | -0.05283 | 0.011808 | 0.11918 | -0.044501 | 0.008329 | -0.046528 | 0.008363 | -0.26696 | -0.1192 | 0.046199 | -0.006621 | 0.26033 | 0.031198 | -0.052594 | 122.5185 | 122.4602 | 122.5151 | 61.296 | -122.5595 | 122.3875 | 122.5379 | 122.4541 | 61.3041 | -122.7737
659.6719 | 122.7173 | -61.3174 | 61.1664 | 1.4211e-13 | -0.0023355 | -0.0097224 | 0.039384 | -0.022721 | 0.047799 | 0.0036627 | -0.011934 | 0.028622 | 0.043943 | 0.0011303 | 0.046578 | -61.1845 | -0.007751 | -61.3391 | 61.2102 | 61.1611 | 61.2068 | -61.3565 | -61.2575 | 0.004938 | -61.3012 | 61.0746 | 61.2296 | 61.1413 | -61.5707 | -0.039097 | 0.043851 | 0.13292 | -0.021611 | 0.017486 | -0.005328 | 0.040406 | -0.25322 | -0.09174 | 0.059932 | 0.01627 | 0.26949 | 0.06324 | -0.025131 | 122.5277 | 122.4785 | 122.5242 | 61.3097 | -122.5229 | 122.3921 | 122.5471 | 122.4587 | 61.3224 | -122.737
661.375 | 122.7951 | -61.2396 | 61.1938 | 1.4211e-13 | -0.0019081 | -0.01015 | 0.03917 | -0.022721 | 0.047799 | 0.0036627 | -0.012148 | 0.028835 | 0.044157 | 0.00091673 | 0.046151 | -61.1799 | -0.003172 | -61.3528 | 61.2148 | 61.1611 | 61.2068 | -61.3611 | -61.2621 | 0.004938 | -61.3195 | 61.0746 | 61.2296 | 61.1458 | -61.5661 | -0.1215 | 0.020963 | 0.059675 | -0.11317 | 0.00833 | -0.032794 | 0.01294 | -0.32646 | -0.11921 | -0.022466 | -0.079865 | 0.2466 | 0.035774 | -0.048018 | 122.4544 | 122.4007 | 122.4464 | 61.2365 | -122.555 | 122.3143 | 122.4692 | 122.3855 | 61.2446 | -122.7599
663.1562 | 122.6669 | -61.3495 | 61.1435 | 1.4211e-13 | -0.0019081 | -0.010363 | 0.039384 | -0.022721 | 0.048226 | 0.018923 | -0.011934 | 0.028835 | 0.044157 | 0.0013439 | 0.046365 | -61.1845 | -0.007751 | -61.3436 | 61.2194 | 61.1611 | 61.2068 | -61.3657 | -61.2621 | 0.004938 | -61.3149 | 61.0701 | 61.225 | 61.1504 | -61.5707 | -0.016212 | 0.075896 | 0.16496 | 0.005853 | 0.022065 | 0.01756 | 0.063294 | -0.22118 | -0.07343 | 0.087397 | 0.034577 | 0.25576 | 0.08155 | 0.006915 | 122.5689 | 122.5105 | 122.5563 | 61.3417 | -122.5092 | 122.4196 | 122.5745 | 122.4999 | 61.3544 | -122.7142
664.9375 | 122.7081 | -61.3129 | 61.1938 | 1.4211e-13 | -0.0019081 | -0.01015 | 0.03917 | -0.022507 | 0.047799 | -0.0039678 | -0.012148 | 0.028622 | 0.044157 | 0.0011303 | 0.046365 | -61.1891 | -0.003172 | -61.3345 | 61.2194 | 61.1519 | 61.2022 | -61.3474 | -61.2667 | 0.004938 | -61.3012 | 61.0792 | 61.2342 | 61.1504 | -61.5661 | -0.034517 | 0.025542 | 0.12376 | -0.021611 | 0.012906 | -0.041952 | 0.008361 | -0.25322 | -0.11463 | 0.046197 | 0.011692 | 0.26491 | 0.040353 | -0.043439 | 122.5323 | 122.4648 | 122.5151 | 61.3097 | -122.5412 | 122.3921 | 122.5471 | 122.4633 | 61.3178 | -122.7599
666.6406 | 122.6944 | -61.3312 | 61.1801 | 1.4211e-13 | -0.0023355 | -0.009936 | 0.039384 | -0.022935 | 0.048012 | 0.011293 | -0.011934 | 0.028835 | 0.044157 | 0.0013439 | 0.046792 | -61.1937 | -0.007751 | -61.3299 | 61.2102 | 61.1565 | 61.1931 | -61.352 | -61.2575 | 0.004938 | -61.3195 | 61.0746 | 61.225 | 61.1413 | -61.5615 | -0.020785 | 0.030118 | 0.13749 | 0.001278 | 0.022063 | -0.02364 | 0.012937 | -0.23033 | -0.10547 | 0.073665 | 0.011688 | 0.24202 | 0.044929 | -0.038864 | 122.5414 | 122.4877 | 122.5242 | 61.3234 | -122.5321 | 122.4058 | 122.5562 | 122.4724 | 61.3361 | -122.7416
668.375 | 122.6852 | -61.2991 | 61.1755 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.039384 | -0.022721 | 0.048226 | 0.0036627 | -0.012361 | 0.028622 | 0.043943 | 0.0015577 | 0.046792 | -61.1754 | 0.001407 | -61.3345 | 61.2102 | 61.1565 | 61.2022 | -61.3611 | -61.2575 | 0.004938 | -61.3058 | 61.0746 | 61.225 | 61.1458 | -61.5661 | -0.061987 | 0.034696 | 0.12376 | -0.035344 | 0.026643 | -0.019062 | 0.026672 | -0.26695 | -0.1009 | 0.041621 | -0.00662 | 0.26033 | 0.049507 | -0.029707 | 122.5094 | 122.4556 | 122.5013 | 61.3005 | -122.5367 | 122.3738 | 122.5242 | 122.445 | 61.3041 | -122.7416
670.1406 | 122.644 | -61.3449 | 61.1801 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.039384 | -0.022721 | 0.048226 | 0.011293 | -0.012148 | 0.028835 | 0.044157 | 0.0013439 | 0.046365 | -61.1799 | -0.007751 | -61.3391 | 61.2148 | 61.1565 | 61.1976 | -61.3657 | -61.2621 | 0.000359 | -61.3012 | 61.0792 | 61.225 | 61.1413 | -61.5569 | -0.020789 | 0.034696 | 0.16496 | 0.005855 | 0.026644 | -0.02364 | 0.017516 | -0.21202 | -0.10089 | 0.08282 | 0.043736 | 0.25576 | 0.044929 | -0.038864 | 122.5597 | 122.5014 | 122.5425 | 61.3372 | -122.5458 | 122.4241 | 122.57 | 122.4862 | 61.3453 | -122.737
671.9375 | 122.6532 | -61.2808 | 61.2625 | 1.4211e-13 | -0.0021217 | -0.0097224 | 0.039384 | -0.022721 | 0.047799 | 0.011293 | -0.011934 | 0.028622 | 0.04437 | 0.0013439 | 0.046365 | -61.1891 | -0.012329 | -61.3162 | 61.2148 | 61.1611 | 61.2022 | -61.3565 | -61.2621 | 0.009516 | -61.3058 | 61.0701 | 61.2205 | 61.1504 | -61.5661 | -0.075718 | -0.047701 | 0.091717 | -0.035341 | 0.040377 | -0.10146 | -0.060303 | -0.28526 | -0.19245 | 0.018733 | -0.02493 | 0.26033 | -0.042047 | -0.1121 | 122.4956 | 122.4419 | 122.483 | 61.2685 | -122.6191 | 122.3509 | 122.5013 | 122.4312 | 61.2903 | -122.8286
673.7344 | 122.7859 | -61.2579 | 61.203 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.039384 | -0.022507 | 0.048012 | 0.0036627 | -0.01172 | 0.028835 | 0.043943 | 0.0011303 | 0.046578 | -61.1845 | -0.012329 | -61.3116 | 61.2102 | 61.1565 | 61.1931 | -61.3474 | -61.2529 | 0.000359 | -61.3012 | 61.0701 | 61.2296 | 61.1367 | -61.5615 | -0.089448 | 0.00723 | 0.073407 | -0.053651 | 0.035797 | -0.046528 | -0.009951 | -0.30357 | -0.13294 | 0.005002 | -0.043239 | 0.26033 | 0.026619 | -0.06633 | 122.4682 | 122.4144 | 122.451 | 61.2456 | -122.5504 | 122.328 | 122.4876 | 122.3946 | 61.2583 | -122.7645
675.5312 | 122.7768 | -61.3312 | 61.1023 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.039811 | -0.022721 | 0.048012 | 0.011293 | -0.012361 | 0.028835 | 0.044157 | 0.0013439 | 0.046792 | -61.1799 | -0.003172 | -61.3116 | 61.2102 | 61.1611 | 61.1976 | -61.3474 | -61.2529 | 0.009516 | -61.3012 | 61.0746 | 61.2205 | 61.1504 | -61.5615 | -0.016206 | 0.10794 | 0.15123 | 0.019591 | 0.035797 | 0.058759 | 0.095336 | -0.23033 | -0.027653 | 0.078244 | 0.030003 | 0.26033 | 0.11817 | 0.048114 | 122.5414 | 122.4922 | 122.5288 | 61.328 | -122.4497 | 122.4058 | 122.5516 | 122.4816 | 61.3407 | -122.6638
677.25 | 122.7402 | -61.2946 | 61.1206 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.038957 | -0.022507 | 0.048012 | -0.0039678 | -0.011934 | 0.028835 | 0.043729 | 0.0011303 | 0.046792 | -61.1708 | -0.007751 | -61.307 | 61.2057 | 61.1565 | 61.2022 | -61.352 | -61.2575 | 0.014095 | -61.3012 | 61.0746 | 61.225 | 61.1458 | -61.5615 | -0.057406 | 0.085049 | 0.12376 | -0.012452 | 0.044954 | 0.03587 | 0.081604 | -0.26695 | -0.045963 | 0.037044 | -0.006618 | 0.26033 | 0.10444 | 0.025225 | 122.5002 | 122.451 | 122.4968 | 61.2868 | -122.4726 | 122.3692 | 122.5196 | 122.4404 | 61.3087 | -122.6821
678.9688 | 122.7539 | -61.3129 | 61.1252 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.039384 | -0.022721 | 0.048439 | 0.0036627 | -0.012148 | 0.028622 | 0.044584 | 0.0013439 | 0.046792 | -61.1799 | -0.003172 | -61.3024 | 61.2057 | 61.1565 | 61.2022 | -61.3474 | -61.2529 | 0.004938 | -61.3058 | 61.0746 | 61.2205 | 61.1413 | -61.5569 | -0.034517 | 0.080471 | 0.13292 | 0.010437 | 0.044954 | 0.031292 | 0.077026 | -0.24406 | -0.050541 | 0.059933 | 0.007113 | 0.25118 | 0.095282 | 0.016068 | 122.5185 | 122.4693 | 122.5151 | 61.3097 | -122.4726 | 122.3875 | 122.5333 | 122.4541 | 61.3178 | -122.6821
680.75 | 122.7539 | -61.3312 | 61.1206 | 1.4211e-13 | -0.0021217 | -0.0097224 | 0.039598 | -0.022507 | 0.048012 | 0.0036627 | -0.011934 | 0.028622 | 0.04437 | 0.0015577 | 0.046365 | -61.1799 | 0.001407 | -61.3024 | 61.2102 | 61.1565 | 61.1976 | -61.3428 | -61.2575 | 0.004938 | -61.3012 | 61.0792 | 61.2205 | 61.1458 | -61.5569 | -0.011627 | 0.089628 | 0.15123 | 0.028748 | 0.040375 | 0.03587 | 0.077026 | -0.22575 | -0.041384 | 0.073665 | 0.030003 | 0.25576 | 0.09986 | 0.025225 | 122.5414 | 122.4877 | 122.5288 | 61.3326 | -122.4634 | 122.4104 | 122.5516 | 122.477 | 61.3361 | -122.6775
682.5469 | 122.6349 | -61.3174 | 61.1801 | 1.4211e-13 | -0.0016945 | -0.01015 | 0.039384 | -0.022935 | 0.048012 | 0.026554 | -0.011934 | 0.028835 | 0.04437 | 0.0015577 | 0.046578 | -61.1754 | -0.007751 | -61.3024 | 61.2148 | 61.1565 | 61.2022 | -61.352 | -61.2575 | 0.000359 | -61.3012 | 61.0746 | 61.225 | 61.1458 | -61.5569 | -0.034518 | 0.034696 | 0.14207 | 0.015015 | 0.049533 | -0.02364 | 0.022094 | -0.23949 | -0.10547 | 0.059932 | 0.01627 | 0.25576 | 0.044929 | -0.034285 | 122.5323 | 122.4739 | 122.5197 | 61.3097 | -122.5321 | 122.3921 | 122.5425 | 122.4633 | 61.3178 | -122.737
684.2656 | 122.6395 | -61.3403 | 61.1618 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.039598 | -0.022935 | 0.048012 | 0.011293 | -0.012148 | 0.029049 | 0.043943 | 0.0013439 | 0.046792 | -61.1799 | -0.003172 | -61.307 | 61.2102 | 61.1473 | 61.1976 | -61.3474 | -61.2484 | 0.009516 | -61.3058 | 61.0701 | 61.2113 | 61.1413 | -61.5615 | -0.007051 | 0.048429 | 0.16038 | 0.033324 | 0.040375 | -0.014487 | 0.035827 | -0.22118 | -0.09174 | 0.091978 | 0.034579 | 0.25576 | 0.049504 | -0.020553 | 122.5506 | 122.4876 | 122.538 | 61.3372 | -122.5092 | 122.4104 | 122.5516 | 122.4816 | 61.3498 | -122.7233
686.0312 | 122.6669 | -61.2854 | 61.2213 | 1.4211e-13 | -0.0019081 | -0.0097224 | 0.03917 | -0.022721 | 0.047585 | -0.0039678 | -0.011934 | 0.028835 | 0.044157 | 0.0011303 | 0.046365 | -61.1708 | -0.012329 | -61.307 | 61.2057 | 61.1565 | 61.1976 | -61.3474 | -61.2438 | 0.009516 | -61.2966 | 61.0655 | 61.2205 | 61.1458 | -61.5615 | -0.061983 | -0.015659 | 0.11461 | -0.021608 | 0.040375 | -0.064838 | -0.023682 | -0.27611 | -0.15583 | 0.041625 | -0.011195 | 0.26491 | -0.000848 | -0.075483 | 122.4911 | 122.4419 | 122.483 | 61.2731 | -122.5687 | 122.3509 | 122.5059 | 122.4312 | 61.2949 | -122.7828
687.8125 | 122.7493 | -61.2579 | 61.203 | 1.4211e-13 | -0.0016945 | -0.009936 | 0.03917 | -0.022721 | 0.048012 | 0.018923 | -0.012361 | 0.028835 | 0.044157 | 0.0011303 | 0.046365 | -61.1799 | -0.003172 | -61.307 | 61.2057 | 61.1473 | 61.1976 | -61.3474 | -61.2529 | 0.004938 | -61.3012 | 61.0655 | 61.2205 | 61.1458 | -61.5569 | -0.089448 | 0.002651 | 0.077986 | -0.049073 | 0.040375 | -0.055686 | -0.005372 | -0.29899 | -0.13752 | 0.005002 | -0.043239 | 0.25576 | 0.017462 | -0.057173 | 122.4636 | 122.4053 | 122.4556 | 61.2548 | -122.5504 | 122.3234 | 122.4784 | 122.4038 | 61.2629 | -122.7599
689.5781 | 122.644 | -61.2991 | 61.2534 | 1.4211e-13 | -0.0019081 | -0.01015 | 0.03917 | -0.022507 | 0.048012 | 0.0036627 | -0.012148 | 0.029049 | 0.04437 | 0.0015577 | 0.046151 | -61.1754 | -0.007751 | -61.2979 | 61.2057 | 61.1473 | 61.1885 | -61.3474 | -61.2484 | 0.000359 | -61.3012 | 61.0701 | 61.2159 | 61.1367 | -61.5615 | -0.04825 | -0.047703 | 0.12376 | 0.001282 | 0.049532 | -0.10604 | -0.064884 | -0.26238 | -0.18329 | 0.050779 | -0.002041 | 0.26033 | -0.037471 | -0.11668 | 122.5048 | 122.4464 | 122.4876 | 61.2914 | -122.6007 | 122.3692 | 122.515 | 122.4358 | 61.2995 | -122.8149
691.2812 | 122.7219 | -61.2991 | 61.1664 | 1.4211e-13 | -0.0021217 | -0.0097224 | 0.03917 | -0.022721 | 0.048012 | 0.011293 | -0.012148 | 0.028408 | 0.043943 | 0.0013439 | 0.046365 | -61.1754 | -0.007751 | -61.2979 | 61.2057 | 61.1519 | 61.1976 | -61.3428 | -61.2529 | 0.004938 | -61.3058 | 61.0701 | 61.2159 | 61.1413 | -61.5615 | -0.043671 | 0.039272 | 0.12376 | 0.001282 | 0.044953 | -0.014486 | 0.031249 | -0.26238 | -0.096318 | 0.0462 | -0.00662 | 0.25576 | 0.049504 | -0.025131 | 122.5048 | 122.451 | 122.4968 | 61.2914 | -122.5092 | 122.3692 | 122.515 | 122.4404 | 61.3041 | -122.7279
693.0781 | 122.6395 | -61.2625 | 61.2717 | 1.4211e-13 | -0.0019081 | -0.010363 | 0.039384 | -0.022507 | 0.047799 | 0.0036627 | -0.011934 | 0.028622 | 0.043943 | 0.0015577 | 0.046365 | -61.1754 | -0.007751 | -61.2979 | 61.2011 | 61.1519 | 61.1931 | -61.3428 | -61.2484 | 0.009516 | -61.292 | 61.0701 | 61.2205 | 61.1413 | -61.5524 | -0.080292 | -0.070591 | 0.087141 | -0.035339 | 0.044953 | -0.11977 | -0.078615 | -0.28984 | -0.2016 | 0.014158 | -0.029505 | 0.26033 | -0.051202 | -0.13042 | 122.4636 | 122.4144 | 122.4556 | 61.2548 | -122.6145 | 122.3326 | 122.483 | 122.4038 | 61.272 | -122.824
694.8594 | 122.6761 | -61.2946 | 61.2076 | 1.4211e-13 | -0.0019081 | -0.01015 | 0.03917 | -0.022507 | 0.048012 | 0.011293 | -0.012361 | 0.028835 | 0.04437 | 0.0015577 | 0.046792 | -61.1754 | -0.003172 | -61.2979 | 61.2011 | 61.1519 | 61.1931 | -61.3474 | -61.2438 | 0.014095 | -61.292 | 61.0655 | 61.225 | 61.1367 | -61.5615 | -0.052827 | -0.006505 | 0.11919 | -0.003295 | 0.049532 | -0.055685 | -0.014529 | -0.26695 | -0.1421 | 0.050781 | 0.002539 | 0.26949 | 0.017463 | -0.070908 | 122.4956 | 122.4465 | 122.4876 | 61.2914 | -122.555 | 122.36 | 122.5196 | 122.4312 | 61.3087 | -122.7691
696.5781 | 122.7448 | -61.2534 | 61.1801 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.039384 | -0.022935 | 0.047585 | 0.0036627 | -0.011934 | 0.028408 | 0.043729 | 0.0013439 | 0.046578 | -61.1708 | 0.001407 | -61.2887 | 61.2102 | 61.1519 | 61.1931 | -61.3428 | -61.2484 | 0.009516 | -61.292 | 61.0701 | 61.2205 | 61.1275 | -61.5569 | -0.089447 | 0.030118 | 0.082564 | -0.035337 | 0.05411 | -0.028219 | 0.012937 | -0.30357 | -0.11005 | 0.005003 | -0.03866 | 0.26491 | 0.04035 | -0.052599 | 122.4636 | 122.4053 | 122.4464 | 61.2548 | -122.5229 | 122.3234 | 122.4738 | 122.3809 | 61.2629 | -122.737
698.3594 | 122.7539 | -61.2259 | 61.203 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.039384 | -0.022935 | 0.048012 | 0.0036627 | -0.012361 | 0.028835 | 0.044157 | 0.0013439 | 0.046578 | -61.1754 | -0.007751 | -61.2979 | 61.2057 | 61.1427 | 61.1885 | -61.3382 | -61.2392 | 0.000359 | -61.292 | 61.0701 | 61.2205 | 61.1413 | -61.5524 | -0.11233 | 0.002651 | 0.05052 | -0.07196 | 0.040374 | -0.060265 | -0.01453 | -0.32646 | -0.13294 | -0.013306 | -0.066126 | 0.26033 | 0.017462 | -0.061752 | 122.4315 | 122.3686 | 122.4144 | 61.2181 | -122.5412 | 122.296 | 122.4464 | 122.3671 | 61.2263 | -122.7554
700.0781 | 122.612 | -61.2625 | 61.2488 | 1.4211e-13 | -0.0021217 | -0.0097224 | 0.03917 | -0.022294 | 0.047799 | 0.0036627 | -0.012148 | 0.028835 | 0.04437 | 0.0013439 | 0.046365 | -61.1708 | -0.007751 | -61.2979 | 61.1965 | 61.1473 | 61.1885 | -61.3428 | -61.2438 | 0.004938 | -61.2966 | 61.0655 | 61.2159 | 61.1321 | -61.5524 | -0.080292 | -0.052281 | 0.091719 | -0.035339 | 0.044953 | -0.10146 | -0.060306 | -0.28984 | -0.18329 | 0.018737 | -0.034083 | 0.25576 | -0.032893 | -0.11668 | 122.459 | 122.4098 | 122.451 | 61.2548 | -122.5916 | 122.328 | 122.4784 | 122.3946 | 61.2675 | -122.8011
701.8438 | 122.7448 | -61.2808 | 61.1252 | 1.4211e-13 | -0.0016945 | -0.009936 | 0.039384 | -0.022935 | 0.048012 | 0.011293 | -0.012575 | 0.028835 | 0.043943 | 0.0011303 | 0.046151 | -61.1662 | -0.003172 | -61.2933 | 61.2057 | 61.1427 | 61.2022 | -61.3428 | -61.2438 | 0.004938 | -61.2966 | 61.0609 | 61.2205 | 61.1321 | -61.5569 | -0.061981 | 0.080471 | 0.11461 | -0.01245 | 0.049531 | 0.017555 | 0.077026 | -0.27611 | -0.064276 | 0.037048 | -0.015772 | 0.26033 | 0.095282 | 0.006911 | 122.4865 | 122.4236 | 122.483 | 61.2777 | -122.468 | 122.3417 | 122.5013 | 122.4129 | 61.2858 | -122.6821
703.6406 | 122.7448 | -61.235 | 61.1984 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.039384 | -0.022507 | 0.048012 | 0.0036627 | -0.012148 | 0.029049 | 0.043943 | 0.0011303 | 0.046578 | -61.1708 | -0.007751 | -61.2887 | 61.2011 | 61.1427 | 61.1885 | -61.3382 | -61.2438 | 0.004938 | -61.2966 | 61.0655 | 61.2205 | 61.1413 | -61.5524 | -0.10318 | 0.002651 | 0.064253 | -0.053648 | 0.049531 | -0.055687 | -0.009952 | -0.31731 | -0.13294 | -0.008729 | -0.061549 | 0.25576 | 0.02204 | -0.057174 | 122.4361 | 122.3778 | 122.4235 | 61.2273 | -122.5367 | 122.3005 | 122.4555 | 122.3763 | 61.24 | -122.7508
705.3438 | 122.6715 | -61.29 | 61.2259 | 1.4211e-13 | -0.0016945 | -0.009936 | 0.038957 | -0.022507 | 0.048012 | 0.011293 | -0.012361 | 0.028835 | 0.044157 | 0.0015577 | 0.046792 | -61.1708 | -0.003172 | -61.2933 | 61.1965 | 61.1473 | 61.1885 | -61.3428 | -61.2392 | 0.004938 | -61.292 | 61.0609 | 61.2159 | 61.1367 | -61.5524 | -0.052826 | -0.029393 | 0.11918 | -0.003295 | 0.049531 | -0.078574 | -0.037418 | -0.26237 | -0.16498 | 0.050781 | -0.002039 | 0.26033 | -0.010005 | -0.089218 | 122.4865 | 122.4373 | 122.4785 | 61.2868 | -122.5687 | 122.3509 | 122.5059 | 122.4267 | 61.2949 | -122.7782
707.1094 | 122.7036 | -61.2808 | 61.1572 | 1.4211e-13 | -0.0019081 | -0.0097224 | 0.03917 | -0.022294 | 0.048012 | 0.0036627 | -0.012361 | 0.028408 | 0.04437 | 0.0015577 | 0.046365 | -61.1708 | -0.007751 | -61.2841 | 61.1919 | 61.1473 | 61.1931 | -61.3428 | -61.2484 | 0.000359 | -61.2966 | 61.0655 | 61.2205 | 61.1321 | -61.5524 | -0.061981 | 0.034692 | 0.11003 | -0.003293 | 0.058688 | -0.00991 | 0.035825 | -0.27153 | -0.091742 | 0.032469 | -0.015772 | 0.25576 | 0.063238 | -0.025133 | 122.4727 | 122.4281 | 122.4739 | 61.2731 | -122.5 | 122.3463 | 122.5013 | 122.4129 | 61.2812 | -122.7096
708.8906 | 122.7402 | -61.2854 | 61.1252 | 1.4211e-13 | -0.0014807 | -0.0097224 | 0.038957 | -0.022935 | 0.047799 | -0.0039678 | -0.012148 | 0.028835 | 0.043943 | 0.0015577 | 0.046151 | -61.1754 | -0.007751 | -61.2887 | 61.2057 | 61.1473 | 61.1885 | -61.352 | -61.2392 | 0.004938 | -61.2874 | 61.0655 | 61.2159 | 61.1275 | -61.5524 | -0.066562 | 0.080471 | 0.11003 | -0.003294 | 0.063268 | 0.022134 | 0.06329 | -0.26695 | -0.059698 | 0.046203 | -0.002038 | 0.26491 | 0.090703 | 0.002333 | 122.4911 | 122.4327 | 122.4739 | 61.2776 | -122.4771 | 122.3509 | 122.5013 | 122.4129 | 61.2903 | -122.6775
710.6094 | 122.6624 | -61.29 | 61.1893 | 1.4211e-13 | -0.0019081 | -0.01015 | 0.03917 | -0.023148 | 0.048012 | -0.0039678 | -0.012148 | 0.029049 | 0.044584 | 0.0015577 | 0.046151 | -61.1708 | -0.007751 | -61.2887 | 61.2011 | 61.1427 | 61.1931 | -61.3382 | -61.2438 | 0.000359 | -61.292 | 61.0655 | 61.2205 | 61.1321 | -61.5432 | -0.048247 | 0.011806 | 0.11918 | 0.001284 | 0.049531 | -0.046532 | 0.003782 | -0.25322 | -0.12378 | 0.046203 | -0.002039 | 0.25118 | 0.031195 | -0.057176 | 122.4911 | 122.4327 | 122.483 | 61.2822 | -122.5275 | 122.3555 | 122.5104 | 122.4221 | 61.2903 | -122.7325
712.3281 | 122.6166 | -61.3037 | 61.171 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.039384 | -0.022721 | 0.048012 | 0.018923 | -0.012148 | 0.028835 | 0.04437 | 0.0013439 | 0.045937 | -61.1708 | -0.012329 | -61.2841 | 61.2011 | 61.1427 | 61.1931 | -61.3382 | -61.2484 | 0.004938 | -61.2966 | 61.0655 | 61.2159 | 61.1367 | -61.5432 | -0.034514 | 0.030117 | 0.13292 | 0.019595 | 0.054109 | -0.028221 | 0.022093 | -0.23948 | -0.10547 | 0.055357 | 0.007116 | 0.2466 | 0.044927 | -0.034286 | 122.5048 | 122.4464 | 122.4968 | 61.2914 | -122.5092 | 122.3692 | 122.5196 | 122.4404 | 61.3086 | -122.7142
714.1094 | 122.7722 | -61.2396 | 61.1664 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.03917 | -0.022721 | 0.047799 | 0.018923 | -0.011934 | 0.029049 | 0.044157 | 0.0015577 | 0.046578 | -61.1662 | -0.007751 | -61.2795 | 61.2011 | 61.1427 | 61.1976 | -61.3382 | -61.23 | -0.00422 | -61.2829 | 61.0701 | 61.2159 | 61.1367 | -61.5524 | -0.098601 | 0.034694 | 0.07341 | -0.039914 | 0.058687 | -0.023644 | 0.031249 | -0.31273 | -0.096318 | 0.009585 | -0.043235 | 0.26949 | 0.049504 | -0.029709 | 122.4407 | 122.3824 | 122.4373 | 61.2319 | -122.5046 | 122.3097 | 122.4555 | 122.3763 | 61.2354 | -122.7187
715.875 | 122.6898 | -61.2808 | 61.1389 | 1.4211e-13 | -0.0016945 | -0.009936 | 0.03917 | -0.023148 | 0.047799 | 0.018923 | -0.012361 | 0.028835 | 0.043943 | 0.0013439 | 0.046365 | -61.1662 | -0.007751 | -61.2841 | 61.1965 | 61.1427 | 61.1931 | -61.3336 | -61.2392 | 0.014095 | -61.2874 | 61.0655 | 61.2113 | 61.1367 | -61.5478 | -0.052824 | 0.057582 | 0.11461 | -0.003293 | 0.049531 | 0.003822 | 0.054136 | -0.26695 | -0.073431 | 0.041626 | -0.006615 | 0.26033 | 0.072392 | -0.002243 | 122.4773 | 122.4236 | 122.4739 | 61.2731 | -122.4726 | 122.3463 | 122.4921 | 122.4175 | 61.2949 | -122.6867
717.6562 | 122.6944 | -61.2213 | 61.1938 | 1.4211e-13 | -0.0019081 | -0.01015 | 0.039384 | -0.022721 | 0.047799 | -0.0039678 | -0.012148 | 0.028835 | 0.043943 | 0.0013439 | 0.046151 | -61.1662 | -0.012329 | -61.2841 | 61.1965 | 61.1427 | 61.1839 | -61.3336 | -61.2346 | 0.009516 | -61.2874 | 61.0609 | 61.2067 | 61.1321 | -61.5432 | -0.11233 | 0.00265 | 0.055099 | -0.062803 | 0.049531 | -0.05111 | -0.009953 | -0.32188 | -0.13294 | -0.013305 | -0.066125 | 0.25576 | 0.012881 | -0.061754 | 122.4178 | 122.3641 | 122.4052 | 61.209 | -122.5275 | 122.2822 | 122.428 | 122.3534 | 61.2308 | -122.737
719.375 | 122.731 | -61.2854 | 61.0977 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.039384 | -0.022721 | 0.048439 | 0.018923 | -0.012148 | 0.029049 | 0.044157 | 0.0015577 | 0.046365 | -61.1708 | -0.016908 | -61.2795 | 61.2011 | 61.1427 | 61.1885 | -61.3382 | -61.2346 | 0.000359 | -61.2829 | 61.0563 | 61.2067 | 61.1275 | -61.5524 | -0.052825 | 0.10336 | 0.11461 | 0.005862 | 0.058687 | 0.045021 | 0.090756 | -0.26695 | -0.041389 | 0.050782 | 0.002541 | 0.26949 | 0.10901 | 0.029799 | 122.4865 | 122.4281 | 122.4739 | 61.2685 | -122.4359 | 122.3417 | 122.4921 | 122.4129 | 61.2858 | -122.6501
721.1406 | 122.5845 | -61.3358 | 61.1572 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.03917 | -0.022721 | 0.047799 | 0.011293 | -0.012575 | 0.028835 | 0.044157 | 0.0013439 | 0.046365 | -61.1616 | -0.007751 | -61.275 | 61.1965 | 61.1519 | 61.1885 | -61.3382 | -61.2438 | 0.004938 | -61.2829 | 61.0655 | 61.2022 | 61.1321 | -61.5432 | -0.002471 | 0.039271 | 0.17412 | 0.060794 | 0.063265 | -0.005331 | 0.031246 | -0.20744 | -0.091742 | 0.091979 | 0.052895 | 0.26033 | 0.044924 | -0.025133 | 122.5323 | 122.4877 | 122.5242 | 61.328 | -122.4955 | 122.4012 | 122.5379 | 122.4678 | 61.3407 | -122.7004
722.9219 | 122.5754 | -61.3358 | 61.1755 | 1.4211e-13 | -0.0016945 | -0.009936 | 0.03917 | -0.022721 | 0.048012 | 0.0036627 | -0.012148 | 0.028835 | 0.043729 | 0.0011303 | 0.046151 | -61.1708 | -0.007751 | -61.2841 | 61.2011 | 61.1427 | 61.1839 | -61.3382 | -61.2346 | 0.004938 | -61.2829 | 61.0563 | 61.2113 | 61.1321 | -61.5432 | -0.002471 | 0.025539 | 0.16496 | 0.051638 | 0.054109 | -0.032799 | 0.008358 | -0.20744 | -0.11921 | 0.10114 | 0.052895 | 0.26033 | 0.035771 | -0.043443 | 122.5368 | 122.4785 | 122.5196 | 61.328 | -122.5138 | 122.3921 | 122.5471 | 122.4678 | 61.3407 | -122.7187
724.7031 | 122.6578 | -61.3312 | 61.1298 | 1.4211e-13 | -0.0016945 | -0.0097224 | 0.03917 | -0.022935 | 0.047799 | -0.0039678 | -0.012148 | 0.028835 | 0.043943 | 0.0015577 | 0.045937 | -61.1571 | -0.016908 | -61.2795 | 61.1965 | 61.1427 | 61.1931 | -61.3336 | -61.2346 | 0.009516 | -61.2829 | 61.0563 | 61.2022 | 61.1321 | -61.5478 | -0.00247 | 0.066737 | 0.17412 | 0.051639 | 0.054109 | 0.012977 | 0.063291 | -0.2166 | -0.073433 | 0.096559 | 0.048318 | 0.26491 | 0.07239 | 0.002333 | 122.5277 | 122.4739 | 122.5242 | 61.3143 | -122.4634 | 122.3875 | 122.5333 | 122.4633 | 61.3407 | -122.6775
726.4844 | 122.7264 | -61.2122 | 61.1755 | 1.4211e-13 | -0.0021217 | -0.010363 | 0.039384 | -0.022507 | 0.048012 | 0.0036627 | -0.012148 | 0.029049 | 0.044157 | 0.0013439 | 0.046151 | -61.1571 | -0.007751 | -61.2795 | 61.1919 | 61.1473 | 61.1885 | -61.3336 | -61.2346 | 0.014095 | -61.2829 | 61.0609 | 61.2067 | 61.1275 | -61.5478 | -0.12149 | 0.016382 | 0.0551 | -0.06738 | 0.054109 | -0.02822 | 0.012936 | -0.33561 | -0.11463 | -0.02246 | -0.070701 | 0.26491 | 0.031192 | -0.048021 | 122.4041 | 122.3595 | 122.4006 | 61.2044 | -122.5092 | 122.2731 | 122.4189 | 122.3397 | 61.2263 | -122.7233
728.1875 | 122.5662 | -61.3312 | 61.1938 | 1.4211e-13 | -0.0016945 | -0.0095086 | 0.039384 | -0.022935 | 0.047799 | 0.011293 | -0.012361 | 0.028835 | 0.044157 | 0.0013439 | 0.046151 | -61.1616 | -0.007751 | -61.2795 | 61.1965 | 61.1382 | 61.1839 | -61.3428 | -61.2392 | 0.009516 | -61.2829 | 61.0609 | 61.2022 | 61.1321 | -61.5386 | -0.011627 | 0.00265 | 0.16954 | 0.051639 | 0.063266 | -0.055689 | -0.009953 | -0.20744 | -0.13294 | 0.09198 | 0.048318 | 0.25576 | 0.008303 | -0.061754 | 122.5277 | 122.4693 | 122.5151 | 61.3234 | -122.5367 | 122.3921 | 122.5333 | 122.4633 | 61.3407 | -122.7325
729.9688 | 122.6624 | -61.2808 | 61.1893 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.038743 | -0.022935 | 0.048012 | 0.011293 | -0.012148 | 0.028622 | 0.043943 | 0.0015577 | 0.046578 | -61.1662 | -0.021486 | -61.2841 | 61.1965 | 61.1427 | 61.1839 | -61.3382 | -61.2392 | 0.014095 | -61.2829 | 61.0517 | 61.2067 | 61.1275 | -61.5478 | -0.057402 | 0.007228 | 0.11461 | -0.003293 | 0.054109 | -0.046532 | -0.005375 | -0.26695 | -0.13752 | 0.041626 | -0.002036 | 0.26491 | 0.017459 | -0.061754 | 122.4773 | 122.4236 | 122.4647 | 61.2593 | -122.5275 | 122.3326 | 122.4876 | 122.4083 | 61.2949 | -122.737
731.7344 | 122.5891 | -61.2442 | 61.2488 | 1.4211e-13 | -0.0016945 | -0.0097224 | 0.039384 | -0.022507 | 0.047799 | 0.011293 | -0.012148 | 0.028835 | 0.043943 | 0.0015577 | 0.046151 | -61.1662 | -0.016908 | -61.2795 | 61.1873 | 61.1473 | 61.1793 | -61.3336 | -61.23 | 0.004938 | -61.2783 | 61.0701 | 61.2067 | 61.1275 | -61.5432 | -0.089445 | -0.061438 | 0.077988 | -0.035336 | 0.054109 | -0.10146 | -0.069463 | -0.29899 | -0.17871 | 0.014163 | -0.034079 | 0.26491 | -0.04205 | -0.12126 | 122.4315 | 122.3915 | 122.4235 | 61.2273 | -122.5824 | 122.3143 | 122.4509 | 122.3717 | 61.2491 | -122.792
733.5156 | 122.6761 | -61.2488 | 61.171 | 1.4211e-13 | -0.0023355 | -0.0095086 | 0.038957 | -0.022721 | 0.047799 | 0.011293 | -0.012361 | 0.028622 | 0.043943 | 0.0015577 | 0.045937 | -61.1616 | -0.007751 | -61.275 | 61.1965 | 61.1336 | 61.1885 | -61.3291 | -61.2346 | 0.004938 | -61.2829 | 61.0563 | 61.2022 | 61.1184 | -61.5432 | -0.080289 | 0.025539 | 0.087143 | -0.026181 | 0.054108 | -0.037378 | 0.017514 | -0.29441 | -0.11463 | 0.014161 | -0.03408 | 0.26033 | 0.031192 | -0.052601 | 122.4453 | 122.3824 | 122.4373 | 61.241 | -122.5 | 122.3051 | 122.4509 | 122.3671 | 61.2537 | -122.7142
735.2188 | 122.6486 | -61.235 | 61.1435 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.039384 | -0.022721 | 0.048012 | 0.011293 | -0.012148 | 0.028835 | 0.044157 | 0.0015577 | 0.046151 | -61.1662 | -0.007751 | -61.2795 | 61.1919 | 61.1382 | 61.1793 | -61.3291 | -61.2346 | 0.000359 | -61.2829 | 61.0609 | 61.2022 | 61.1275 | -61.5432 | -0.094022 | 0.048425 | 0.068832 | -0.044492 | 0.04953 | -0.005335 | 0.035822 | -0.30815 | -0.082587 | 0.000428 | -0.047813 | 0.26033 | 0.058657 | -0.015978 | 122.427 | 122.3732 | 122.4144 | 61.2273 | -122.4726 | 122.296 | 122.4372 | 122.3626 | 61.2354 | -122.6867
737 | 122.7219 | -61.2122 | 61.1847 | 1.4211e-13 | -0.0021217 | -0.0097224 | 0.039598 | -0.022721 | 0.047585 | 0.0036627 | -0.011934 | 0.028622 | 0.043943 | 0.0011303 | 0.045937 | -61.1616 | -0.007751 | -61.2795 | 61.1965 | 61.1382 | 61.1839 | -61.3291 | -61.23 | 0.000359 | -61.2874 | 61.0655 | 61.2022 | 61.1229 | -61.5386 | -0.11691 | 0.011806 | 0.050522 | -0.06738 | 0.04953 | -0.046533 | -0.000797 | -0.32646 | -0.11921 | -0.017881 | -0.07528 | 0.25118 | 0.017459 | -0.061755 | 122.4087 | 122.3503 | 122.3961 | 61.2044 | -122.5138 | 122.2776 | 122.4143 | 122.3351 | 61.2125 | -122.7233
738.7812 | 122.6212 | -61.2762 | 61.1847 | 1.4211e-13 | -0.0019081 | -0.0097224 | 0.038957 | -0.022721 | 0.047799 | 0.0036627 | -0.012361 | 0.028622 | 0.04437 | 0.0013439 | 0.046151 | -61.1571 | -0.012329 | -61.2795 | 61.1873 | 61.1382 | 61.1885 | -61.3428 | -61.23 | 0.004938 | -61.2737 | 61.0563 | 61.2022 | 61.1229 | -61.5432 | -0.066559 | 0.002649 | 0.11919 | -0.003293 | 0.063266 | -0.046533 | 0.003781 | -0.26695 | -0.12836 | 0.046206 | 0.002543 | 0.26949 | 0.017459 | -0.061755 | 122.4636 | 122.4144 | 122.4647 | 61.2639 | -122.5275 | 122.3326 | 122.4784 | 122.3992 | 61.2812 | -122.7279
740.5625 | 122.6761 | -61.2762 | 61.1481 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.03917 | -0.022721 | 0.048226 | 0.0036627 | -0.012575 | 0.028835 | 0.043943 | 0.0015577 | 0.045937 | -61.1571 | -0.007751 | -61.275 | 61.1919 | 61.1336 | 61.1885 | -61.3291 | -61.23 | 0.004938 | -61.2829 | 61.0563 | 61.2022 | 61.1229 | -61.5386 | -0.052823 | 0.043848 | 0.11919 | 0.001285 | 0.054108 | -0.01449 | 0.040402 | -0.26237 | -0.091743 | 0.046206 | -0.006614 | 0.25576 | 0.05408 | -0.025134 | 122.4682 | 122.4098 | 122.4647 | 61.2685 | -122.4771 | 122.3326 | 122.4784 | 122.3992 | 61.2812 | -122.6867
742.2656 | 122.7127 | -61.2396 | 61.1481 | 1.4211e-13 | -0.0023355 | -0.009936 | 0.039384 | -0.022935 | 0.048226 | 0.0036627 | -0.012148 | 0.028835 | 0.043943 | 0.0013439 | 0.046365 | -61.1525 | -0.016908 | -61.275 | 61.1873 | 61.1382 | 61.1885 | -61.3336 | -61.23 | 0.000359 | -61.2829 | 61.0517 | 61.1976 | 61.1275 | -61.5478 | -0.094023 | 0.03927 | 0.087145 | -0.035336 | 0.058687 | -0.009912 | 0.040402 | -0.30815 | -0.096321 | 0.009585 | -0.043235 | 0.26491 | 0.049501 | -0.020555 | 122.427 | 122.3778 | 122.4281 | 61.2227 | -122.4817 | 122.2914 | 122.4372 | 122.3671 | 61.24 | -122.6958
744.0469 | 122.5891 | -61.2625 | 61.235 | 1.4211e-13 | -0.0016945 | -0.01015 | 0.039811 | -0.022721 | 0.048439 | 0.0036627 | -0.012148 | 0.028835 | 0.044157 | 0.0017713 | 0.046151 | -61.1525 | -0.007751 | -61.275 | 61.1873 | 61.1336 | 61.1839 | -61.3291 | -61.23 | 0.004938 | -61.2829 | 61.0563 | 61.2067 | 61.1229 | -61.5478 | -0.066556 | -0.047705 | 0.11003 | -0.012448 | 0.054108 | -0.10146 | -0.051151 | -0.28526 | -0.17872 | 0.032473 | -0.020347 | 0.26491 | -0.028317 | -0.11211 | 122.4499 | 122.3961 | 122.4464 | 61.2548 | -122.5641 | 122.3188 | 122.4692 | 122.3854 | 61.2675 | -122.7828
745.8125 | 122.5937 | -61.2305 | 61.2442 | 1.4211e-13 | -0.0019081 | -0.0097224 | 0.039384 | -0.022935 | 0.048226 | 0.011293 | -0.012148 | 0.028835 | 0.043943 | 0.0013439 | 0.046365 | -61.1616 | -0.012329 | -61.275 | 61.1919 | 61.1473 | 61.1839 | -61.3336 | -61.23 | 0.004938 | -61.2737 | 61.0517 | 61.2067 | 61.1275 | -61.5478 | -0.10318 | -0.052283 | 0.068833 | -0.044491 | 0.058687 | -0.096885 | -0.060307 | -0.3173 | -0.19245 | 0.00043 | -0.043233 | 0.27407 | -0.037473 | -0.11669 | 122.4224 | 122.3778 | 122.4144 | 61.2181 | -122.5778 | 122.2822 | 122.4372 | 122.358 | 61.2354 | -122.792
747.5938 | 122.6257 | -61.2625 | 61.2122 | 1.4211e-13 | -0.0021217 | -0.0097224 | 0.039384 | -0.022721 | 0.048012 | 0.0036627 | -0.012575 | 0.028835 | 0.044157 | 0.0015577 | 0.046578 | -61.1525 | -0.012329 | -61.2795 | 61.1919 | 61.1427 | 61.1793 | -61.3199 | -61.23 | 0.014095 | -61.2783 | 61.0517 | 61.2022 | 61.1229 | -61.5432 | -0.057398 | -0.020239 | 0.11003 | -0.017026 | 0.040372 | -0.06942 | -0.032842 | -0.28068 | -0.16041 | 0.032473 | -0.015769 | 0.26491 | -0.010007 | -0.089221 | 122.4544 | 122.4052 | 122.4418 | 61.2502 | -122.5321 | 122.3143 | 122.4647 | 122.3854 | 61.2766 | -122.7554
749.3125 | 122.6807 | -61.2854 | 61.116 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.03917 | -0.022935 | 0.047799 | 0.011293 | -0.012361 | 0.028835 | 0.044157 | 0.0013439 | 0.046578 | -61.1525 | -0.007751 | -61.275 | 61.1873 | 61.1382 | 61.1839 | -61.3245 | -61.23 | 0.009516 | -61.2783 | 61.0517 | 61.1976 | 61.1229 | -61.534 | -0.039089 | 0.071313 | 0.13292 | 0.01044 | 0.049529 | 0.022131 | 0.067867 | -0.24864 | -0.064278 | 0.055361 | 0.007119 | 0.25576 | 0.081544 | 0.006909 | 122.4727 | 122.4236 | 122.4693 | 61.2776 | -122.4405 | 122.3372 | 122.483 | 122.4083 | 61.2949 | -122.6501
751.0938 | 122.5937 | -61.2305 | 61.2305 | 1.4211e-13 | -0.0016945 | -0.010363 | 0.039384 | -0.022721 | 0.048226 | 0.011293 | -0.012361 | 0.028622 | 0.044157 | 0.0013439 | 0.046151 | -61.1616 | -0.012329 | -61.2704 | 61.1873 | 61.1382 | 61.1839 | -61.3153 | -61.2346 | 0.009516 | -61.2783 | 61.0517 | 61.2022 | 61.1184 | -61.534 | -0.084862 | -0.043128 | 0.068833 | -0.039912 | 0.04495 | -0.09231 | -0.046574 | -0.30357 | -0.17872 | -0.004149 | -0.047812 | 0.25576 | -0.028318 | -0.11211 | 122.4178 | 122.3686 | 122.4144 | 61.2181 | -122.5458 | 122.2822 | 122.4326 | 122.3488 | 61.24 | -122.7645
752.7969 | 122.5845 | -61.2579 | 61.2442 | 1.4211e-13 | -0.0023355 | -0.009936 | 0.038957 | -0.022721 | 0.047799 | 0.0036627 | -0.012148 | 0.028835 | 0.043943 | 0.0015577 | 0.045937 | -61.1433 | -0.012329 | -61.275 | 61.1828 | 61.1382 | 61.1747 | -61.3291 | -61.23 | 0.000359 | -61.2737 | 61.0517 | 61.2022 | 61.1138 | -61.5386 | -0.071133 | -0.06144 | 0.11461 | -0.017025 | 0.054108 | -0.10604 | -0.069464 | -0.28068 | -0.19245 | 0.027896 | -0.015767 | 0.26491 | -0.042051 | -0.13042 | 122.4407 | 122.3961 | 122.4327 | 61.2456 | -122.5733 | 122.3097 | 122.4601 | 122.3717 | 61.2583 | -122.7828
754.5156 | 122.7173 | -61.203 | 61.1664 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.038957 | -0.022507 | 0.048226 | 0.011293 | -0.012575 | 0.028835 | 0.04437 | 0.0013439 | 0.046151 | -61.1479 | -0.012329 | -61.275 | 61.1873 | 61.1336 | 61.1839 | -61.3245 | -61.2255 | 0.000359 | -61.2783 | 61.0563 | 61.2022 | 61.1275 | -61.5386 | -0.12149 | 0.020959 | 0.055102 | -0.071957 | 0.049529 | -0.032801 | 0.017513 | -0.33561 | -0.11005 | -0.022458 | -0.075278 | 0.26033 | 0.035769 | -0.038866 | 122.3903 | 122.3366 | 122.3869 | 61.1907 | -122.4909 | 122.2593 | 122.4052 | 122.3305 | 61.2034 | -122.705
756.2656 | 122.6532 | -61.2762 | 61.1343 | 1.4211e-13 | -0.0016945 | -0.009936 | 0.03917 | -0.022935 | 0.048012 | 0.011293 | -0.011934 | 0.028835 | 0.043943 | 0.0013439 | 0.046365 | -61.1525 | -0.007751 | -61.2704 | 61.1873 | 61.1427 | 61.1885 | -61.3291 | -61.23 | 0.004938 | -61.2737 | 61.0517 | 61.1976 | 61.1184 | -61.5295 | -0.052823 | 0.053003 | 0.12377 | 0.005864 | 0.058687 | 0.0084 | 0.054135 | -0.25321 | -0.082588 | 0.046206 | 0.002543 | 0.25576 | 0.063234 | -0.01598 | 122.4636 | 122.419 | 122.4647 | 61.2685 | -122.4634 | 122.328 | 122.4738 | 122.3946 | 61.2812 | -122.6638
757.9844 | 122.612 | -61.2717 | 61.1389 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.039384 | -0.022935 | 0.048226 | 0.0036627 | -0.011934 | 0.028835 | 0.043943 | 0.0015577 | 0.046151 | -61.1479 | -0.012329 | -61.2704 | 61.1873 | 61.1336 | 61.1793 | -61.3291 | -61.23 | 0.014095 | -61.2691 | 61.0472 | 61.2067 | 61.1184 | -61.534 | -0.057401 | 0.048425 | 0.12377 | 0.001286 | 0.058687 | -0.005335 | 0.0404 | -0.26237 | -0.091745 | 0.041628 | 0.002544 | 0.26491 | 0.067813 | -0.020558 | 122.459 | 122.4052 | 122.451 | 61.2593 | -122.468 | 122.3188 | 122.4784 | 122.39 | 61.2858 | -122.673
759.6875 | 122.7081 | -61.2991 | 61.0565 | 1.4211e-13 | -0.0016945 | -0.009936 | 0.038957 | -0.022294 | 0.048226 | 0.0036627 | -0.012361 | 0.028622 | 0.044157 | 0.0015577 | 0.046151 | -61.1525 | -0.012329 | -61.275 | 61.1873 | 61.1427 | 61.1747 | -61.3245 | -61.2255 | 0.018674 | -61.2645 | 61.0517 | 61.2022 | 61.1138 | -61.534 | -0.025356 | 0.13082 | 0.14665 | 0.024173 | 0.049529 | 0.086219 | 0.11822 | -0.2349 | -0.004769 | 0.073672 | 0.034589 | 0.26949 | 0.14563 | 0.057261 | 122.4865 | 122.4419 | 122.4739 | 61.2868 | -122.381 | 122.3509 | 122.5013 | 122.4129 | 61.3178 | -122.5906
761.4688 | 122.6212 | -61.2671 | 61.1755 | 1.4211e-13 | -0.0016945 | -0.01015 | 0.039384 | -0.022721 | 0.048012 | -0.0039678 | -0.012361 | 0.028835 | 0.044157 | 0.0011303 | 0.046151 | -61.1571 | -0.007751 | -61.2704 | 61.1919 | 61.1427 | 61.1839 | -61.3245 | -61.23 | 0.004938 | -61.2783 | 61.0517 | 61.2067 | 61.1184 | -61.5295 | -0.057399 | 0.016382 | 0.11003 | -0.003291 | 0.054108 | -0.032799 | 0.008358 | -0.26237 | -0.12379 | 0.037051 | -0.011191 | 0.25118 | 0.031192 | -0.057179 | 122.459 | 122.4098 | 122.451 | 61.2593 | -122.5 | 122.3188 | 122.4738 | 122.3854 | 61.272 | -122.705
763.1875 | 122.7036 | -61.2167 | 61.1664 | 1.4211e-13 | -0.0019081 | -0.0097224 | 0.039384 | -0.022294 | 0.048012 | 0.0036627 | -0.012575 | 0.028835 | 0.044157 | 0.0015577 | 0.046151 | -61.1525 | -0.007751 | -61.2658 | 61.1873 | 61.129 | 61.1793 | -61.3199 | -61.2209 | 0.000359 | -61.2691 | 61.0472 | 61.1976 | 61.1184 | -61.5432 | -0.10317 | 0.020959 | 0.064257 | -0.049067 | 0.054107 | -0.03738 | 0.012934 | -0.32646 | -0.11921 | -0.004146 | -0.052387 | 0.27407 | 0.03119 | -0.048024 | 122.4041 | 122.3457 | 122.3961 | 61.209 | -122.4863 | 122.2639 | 122.4143 | 122.3351 | 61.2171 | -122.7096
764.8906 | 122.7081 | -61.203 | 61.1755 | 1.4211e-13 | -0.0021217 | -0.01015 | 0.03917 | -0.022507 | 0.048012 | 0.0036627 | -0.012361 | 0.028835 | 0.043516 | 0.0017713 | 0.046151 | -61.1479 | -0.007751 | -61.2612 | 61.1873 | 61.1336 | 61.1747 | -61.3199 | -61.2209 | 0.009516 | -61.2737 | 61.0426 | 61.2022 | 61.1184 | -61.534 | -0.11691 | 0.011804 | 0.055102 | -0.058222 | 0.058685 | -0.041956 | -0.000799 | -0.33103 | -0.13294 | -0.017879 | -0.070699 | 0.26033 | 0.026614 | -0.057179 | 122.3903 | 122.3366 | 122.3777 | 61.1953 | -122.4954 | 122.2456 | 122.4052 | 122.3214 | 61.2125 | -122.7096
766.6719 | 122.58 | -61.3083 | 61.1389 | 1.4211e-13 | -0.0021217 | -0.0095086 | 0.039384 | -0.022721 | 0.048012 | 0.0036627 | -0.012148 | 0.028835 | 0.043943 | 0.0013439 | 0.046365 | -61.1525 | -0.007751 | -61.2658 | 61.1919 | 61.1382 | 61.1839 | -61.3245 | -61.2163 | 0.014095 | -61.2645 | 61.0517 | 61.2113 | 61.1229 | -61.534 | -0.0162 | 0.053003 | 0.15581 | 0.042486 | 0.058686 | -0.000757 | 0.044979 | -0.22575 | -0.087166 | 0.091986 | 0.043745 | 0.26949 | 0.072392 | -0.015979 | 122.5002 | 122.4464 | 122.4922 | 61.3005 | -122.4634 | 122.36 | 122.5196 | 122.4312 | 61.3224 | -122.673
768.3906 | 122.6715 | -61.2671 | 61.1023 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.039384 | -0.022721 | 0.047799 | 0.0036627 | -0.012148 | 0.028622 | 0.043943 | 0.0015577 | 0.046151 | -61.1479 | -0.007751 | -61.2566 | 61.1828 | 61.1382 | 61.1839 | -61.3199 | -61.2163 | 0.014095 | -61.2737 | 61.0563 | 61.2022 | 61.1184 | -61.534 | -0.05282 | 0.080467 | 0.11919 | 0.010444 | 0.063264 | 0.035864 | 0.0816 | -0.26695 | -0.045967 | 0.050787 | -0.006612 | 0.26033 | 0.099856 | 0.016063 | 122.4499 | 122.4052 | 122.451 | 61.2593 | -122.4222 | 122.3234 | 122.4692 | 122.3854 | 61.2812 | -122.6363
770.1562 | 122.5433 | -61.2991 | 61.1572 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.039384 | -0.022935 | 0.048226 | 0.0036627 | -0.012148 | 0.028622 | 0.043943 | 0.0011303 | 0.045937 | -61.1433 | -0.003172 | -61.2658 | 61.1828 | 61.1336 | 61.1747 | -61.3291 | -61.2163 | 0.009516 | -61.2645 | 61.0472 | 61.2022 | 61.1184 | -61.5295 | -0.029935 | 0.025535 | 0.15581 | 0.03333 | 0.063265 | -0.023646 | 0.017511 | -0.23032 | -0.11006 | 0.08283 | 0.034589 | 0.26491 | 0.044924 | -0.038869 | 122.4819 | 122.4327 | 122.4739 | 61.296 | -122.4863 | 122.3463 | 122.5013 | 122.4175 | 61.3086 | -122.6867
771.9219 | 122.58 | -61.2946 | 61.171 | 1.4211e-13 | -0.0016945 | -0.009936 | 0.038957 | -0.022721 | 0.048226 | 0.018923 | -0.012148 | 0.028835 | 0.043943 | 0.0013439 | 0.046365 | -61.1479 | -0.007751 | -61.2612 | 61.1873 | 61.1336 | 61.1839 | -61.3245 | -61.2209 | 0.004938 | -61.2783 | 61.0472 | 61.2022 | 61.1138 | -61.5295 | -0.029933 | 0.016382 | 0.14666 | 0.033331 | 0.063264 | -0.037378 | 0.012936 | -0.2349 | -0.12379 | 0.073674 | 0.016275 | 0.25118 | 0.031192 | -0.057179 | 122.4819 | 122.4281 | 122.4785 | 61.2868 | -122.4954 | 122.3417 | 122.4967 | 122.4083 | 61.2995 | -122.7004
773.7188 | 122.644 | -61.2808 | 61.1389 | 1.4211e-13 | -0.0019081 | -0.0097224 | 0.03917 | -0.022935 | 0.047799 | 0.0036627 | -0.012148 | 0.028622 | 0.04437 | 0.0013439 | 0.045937 | -61.1479 | -0.012329 | -61.2658 | 61.1828 | 61.129 | 61.1839 | -61.3153 | -61.2255 | 0.004938 | -61.2645 | 61.0472 | 61.2022 | 61.1092 | -61.5249 | -0.034508 | 0.043846 | 0.13292 | 0.01502 | 0.049528 | -0.009914 | 0.044979 | -0.24406 | -0.091745 | 0.055362 | 0.016279 | 0.26033 | 0.063235 | -0.029715 | 122.4636 | 122.4098 | 122.4647 | 61.2685 | -122.4542 | 122.328 | 122.483 | 122.39 | 61.2858 | -122.6638
775.5 | 122.612 | -61.2213 | 61.1847 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.039384 | -0.022935 | 0.047799 | -0.0039678 | -0.012148 | 0.028622 | 0.044157 | 0.0013439 | 0.046365 | -61.1387 | -0.012329 | -61.2704 | 61.1873 | 61.1382 | 61.1839 | -61.3153 | -61.2163 | 0.000359 | -61.2645 | 61.0426 | 61.2022 | 61.1138 | -61.5157 | -0.094018 | 0.002649 | 0.082569 | -0.049068 | 0.04495 | -0.046533 | -0.000797 | -0.29441 | -0.1421 | 0.00501 | -0.043231 | 0.25118 | 0.017459 | -0.070912 | 122.4087 | 122.3595 | 122.4052 | 61.209 | -122.5 | 122.2639 | 122.4235 | 122.3351 | 61.2217 | -122.7004
777.2031 | 122.5754 | -61.3083 | 61.1526 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.039384 | -0.022935 | 0.047799 | 0.0036627 | -0.012148 | 0.029049 | 0.043943 | 0.0015577 | 0.046365 | -61.1479 | -0.007751 | -61.2658 | 61.1965 | 61.1382 | 61.1839 | -61.3153 | -61.2209 | 0.004938 | -61.26 | 61.0472 | 61.2022 | 61.1138 | -61.534 | -0.007042 | 0.043849 | 0.16039 | 0.042486 | 0.049528 | -0.01449 | 0.031246 | -0.22575 | -0.10548 | 0.087407 | 0.048323 | 0.27407 | 0.049502 | -0.038869 | 122.5048 | 122.4464 | 122.4922 | 61.3005 | -122.468 | 122.3555 | 122.5104 | 122.4221 | 61.3132 | -122.6867
778.9844 | 122.7036 | -61.1847 | 61.1755 | 1.4211e-13 | -0.0016945 | -0.0097224 | 0.039384 | -0.022721 | 0.047799 | -0.0039678 | -0.012361 | 0.028835 | 0.043943 | 0.0013439 | 0.046365 | -61.1433 | -0.007751 | -61.2658 | 61.1828 | 61.129 | 61.1839 | -61.3199 | -61.2209 | 0.004938 | -61.2691 | 61.038 | 61.2022 | 61.1138 | -61.5295 | -0.13522 | 0.007225 | 0.04137 | -0.081111 | 0.054107 | -0.046535 | 0.008358 | -0.34477 | -0.13752 | -0.03619 | -0.084431 | 0.26033 | 0.026614 | -0.061757 | 122.3675 | 122.3137 | 122.3686 | 61.1769 | -122.4954 | 122.2227 | 122.3868 | 122.2985 | 61.1896 | -122.705
780.7656 | 122.5754 | -61.2946 | 61.1389 | 1.4211e-13 | -0.0016945 | -0.0097224 | 0.03917 | -0.022294 | 0.047799 | 0.0036627 | -0.012148 | 0.028622 | 0.044157 | 0.0015577 | 0.045937 | -61.1387 | -0.012329 | -61.2612 | 61.1782 | 61.1336 | 61.1839 | -61.3153 | -61.2163 | 0.014095 | -61.26 | 61.0472 | 61.2022 | 61.1184 | -61.5249 | -0.020775 | 0.039268 | 0.15581 | 0.033331 | 0.054106 | -0.005335 | 0.044979 | -0.23032 | -0.091745 | 0.078253 | 0.03459 | 0.26491 | 0.063235 | -0.020558 | 122.4727 | 122.4281 | 122.4785 | 61.2822 | -122.4542 | 122.3417 | 122.4967 | 122.4129 | 61.3087 | -122.6638
782.5625 | 122.5754 | -61.235 | 61.2305 | 1.4211e-13 | -0.0014807 | -0.0097224 | 0.039384 | -0.023148 | 0.047799 | 0.0036627 | -0.012361 | 0.028622 | 0.043943 | 0.0013439 | 0.045937 | -61.1479 | -0.012329 | -61.2566 | 61.1782 | 61.129 | 61.1702 | -61.3153 | -61.2255 | 0.014095 | -61.26 | 61.038 | 61.193 | 61.1138 | -61.5249 | -0.080285 | -0.052285 | 0.087145 | -0.0216 | 0.058685 | -0.10147 | -0.06031 | -0.28983 | -0.19246 | 0.009585 | -0.02492 | 0.26491 | -0.037476 | -0.11669 | 122.4132 | 122.364 | 122.4052 | 61.2227 | -122.5458 | 122.2731 | 122.428 | 122.3488 | 61.2491 | -122.7553
784.2812 | 122.6807 | -61.2213 | 61.171 | 1.4211e-13 | -0.0019081 | -0.01015 | 0.039384 | -0.022935 | 0.048226 | 0.0036627 | -0.012148 | 0.028408 | 0.04437 | 0.0013439 | 0.045937 | -61.1433 | -0.003172 | -61.2704 | 61.1782 | 61.1336 | 61.1747 | -61.3108 | -61.2163 | 0.009516 | -61.26 | 61.0426 | 61.2022 | 61.1092 | -61.5249 | -0.089439 | 0.007225 | 0.077991 | -0.049068 | 0.040371 | -0.037378 | 0.003779 | -0.30356 | -0.12837 | 0.00501 | -0.038653 | 0.26491 | 0.031192 | -0.061758 | 122.3995 | 122.3549 | 122.3961 | 61.2181 | -122.4817 | 122.2639 | 122.4235 | 122.3305 | 61.2308 | -122.6958
786.0625 | 122.6669 | -61.2259 | 61.171 | 1.4211e-13 | -0.0019081 | -0.0097224 | 0.03917 | -0.022935 | 0.048012 | 0.018923 | -0.012148 | 0.028835 | 0.043943 | 0.0017713 | 0.046365 | -61.1479 | -0.003172 | -61.2566 | 61.1828 | 61.1244 | 61.1747 | -61.3108 | -61.2117 | 0.004938 | -61.2645 | 61.0426 | 61.193 | 61.1092 | -61.5249 | -0.084861 | 0.011803 | 0.07799 | -0.030755 | 0.054106 | -0.046536 | 0.003779 | -0.29899 | -0.12837 | 0.014167 | -0.038653 | 0.26033 | 0.022034 | -0.061758 | 122.4087 | 122.3503 | 122.4006 | 61.2227 | -122.4817 | 122.2685 | 122.4189 | 122.3351 | 61.2308 | -122.6958
787.8281 | 122.6852 | -61.2991 | 61.0886 | 1.4211e-13 | -0.0016945 | -0.009936 | 0.03917 | -0.022721 | 0.048439 | 0.011293 | -0.012148 | 0.029049 | 0.044157 | 0.0013439 | 0.046151 | -61.1296 | -0.003172 | -61.2566 | 61.1828 | 61.129 | 61.1747 | -61.3199 | -61.2255 | 0.000359 | -61.2554 | 61.0472 | 61.1976 | 61.1138 | -61.5203 | -0.020777 | 0.0942 | 0.16955 | 0.042487 | 0.063264 | 0.04044 | 0.086176 | -0.22117 | -0.041391 | 0.073672 | 0.043746 | 0.26491 | 0.10901 | 0.025218 | 122.4819 | 122.4281 | 122.4739 | 61.296 | -122.4085 | 122.3463 | 122.4967 | 122.4129 | 61.2995 | -122.6089
789.6094 | 122.7081 | -61.1984 | 61.1572 | 1.4211e-13 | -0.0019081 | -0.0097224 | 0.03917 | -0.022721 | 0.047799 | 0.0036627 | -0.011934 | 0.028835 | 0.043943 | 0.0013439 | 0.046365 | -61.1342 | -0.003172 | -61.2566 | 61.1828 | 61.129 | 61.1702 | -61.3108 | -61.2163 | 0.000359 | -61.26 | 61.0426 | 61.2022 | 61.1184 | -61.5249 | -0.11233 | 0.025535 | 0.064259 | -0.058221 | 0.054106 | -0.028225 | 0.012932 | -0.32645 | -0.11463 | -0.017878 | -0.061541 | 0.26491 | 0.044924 | -0.038869 | 122.3812 | 122.3274 | 122.3686 | 61.1953 | -122.468 | 122.241 | 122.4006 | 122.3168 | 61.1988 | -122.6821
791.3281 | 122.6624 | -61.1847 | 61.1938 | 1.4211e-13 | -0.0019081 | -0.0097224 | 0.038957 | -0.022935 | 0.048226 | 0.011293 | -0.012361 | 0.028622 | 0.044157 | 0.0015577 | 0.046151 | -61.1387 | -0.012329 | -61.2566 | 61.1828 | 61.129 | 61.1747 | -61.3153 | -61.2117 | 0.004938 | -61.26 | 61.038 | 61.193 | 61.1092 | -61.5157 | -0.13064 | -0.011086 | 0.045948 | -0.071954 | 0.058685 | -0.064846 | -0.01911 | -0.33103 | -0.15583 | -0.027032 | -0.075274 | 0.25575 | -0.000855 | -0.084647 | 122.3675 | 122.3137 | 122.3594 | 61.1724 | -122.5092 | 122.2227 | 122.3777 | 122.2939 | 61.1896 | -122.7096
793.1094 | 122.5891 | -61.2991 | 61.1298 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.039384 | -0.022935 | 0.048012 | 0.011293 | -0.012361 | 0.029049 | 0.043943 | 0.0015577 | 0.046365 | -61.1387 | 0.001407 | -61.2521 | 61.1828 | 61.129 | 61.1747 | -61.3108 | -61.2209 | 0.009516 | -61.26 | 61.0517 | 61.193 | 61.1092 | -61.5249 | -0.011619 | 0.053001 | 0.16039 | 0.047065 | 0.058684 | -0.000759 | 0.044977 | -0.22575 | -0.078011 | 0.078251 | 0.039167 | 0.26491 | 0.063232 | -0.02056 | 122.4819 | 122.4281 | 122.4739 | 61.3005 | -122.4405 | 122.3509 | 122.4921 | 122.4083 | 61.3086 | -122.6546
794.8906 | 122.5616 | -61.2442 | 61.1664 | 1.4211e-13 | -0.0016945 | -0.0097224 | 0.039384 | -0.022721 | 0.048226 | 0.011293 | -0.012361 | 0.028408 | 0.043943 | 0.0011303 | 0.046365 | -61.1342 | -0.003172 | -61.2704 | 61.1828 | 61.129 | 61.1747 | -61.3153 | -61.2163 | 0.014095 | -61.2554 | 61.0426 | 61.1884 | 61.1092 | -61.5249 | -0.071129 | 0.01638 | 0.11004 | -0.026179 | 0.04495 | -0.03738 | 0.008356 | -0.28068 | -0.12379 | 0.027899 | -0.011185 | 0.26949 | 0.022033 | -0.057181 | 122.427 | 122.3732 | 122.4189 | 61.241 | -122.4817 | 122.2868 | 122.4326 | 122.3534 | 61.2583 | -122.6913
796.6562 | 122.5616 | -61.2717 | 61.2213 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.03917 | -0.022935 | 0.047799 | 0.0036627 | -0.012361 | 0.028622 | 0.043943 | 0.0011303 | 0.045937 | -61.1433 | -0.007751 | -61.2566 | 61.1782 | 61.129 | 61.1793 | -61.3108 | -61.2163 | 0.009516 | -61.2645 | 61.0426 | 61.1884 | 61.1046 | -61.5157 | -0.039085 | -0.043129 | 0.12835 | 0.015021 | 0.054106 | -0.092311 | -0.041997 | -0.24405 | -0.17872 | 0.055364 | 0.007123 | 0.25118 | -0.032898 | -0.11669 | 122.4499 | 122.4007 | 122.451 | 61.2639 | -122.5321 | 122.3143 | 122.4601 | 122.3763 | 61.2812 | -122.737
798.4219 | 122.5616 | -61.2259 | 61.235 | 1.4211e-13 | -0.0019081 | -0.0097224 | 0.038957 | -0.022935 | 0.048012 | 0.0036627 | -0.012361 | 0.028622 | 0.043943 | 0.0017713 | 0.046151 | -61.1479 | -0.007751 | -61.2475 | 61.1782 | 61.1244 | 61.1747 | -61.3062 | -61.2209 | 0.004938 | -61.26 | 61.0426 | 61.193 | 61.1092 | -61.5295 | -0.080282 | -0.056862 | 0.07799 | -0.021599 | 0.058683 | -0.11062 | -0.060308 | -0.30357 | -0.19245 | 0.005009 | -0.034075 | 0.26949 | -0.042053 | -0.12584 | 122.4041 | 122.3503 | 122.4006 | 61.2181 | -122.5412 | 122.2685 | 122.4189 | 122.3351 | 61.2308 | -122.7645
800.1406 | 122.6715 | -61.2854 | 61.0931 | 1.4211e-13 | -0.0016945 | -0.009936 | 0.038743 | -0.023148 | 0.048012 | 0.0036627 | -0.012575 | 0.029049 | 0.043943 | 0.0013439 | 0.046151 | -61.1387 | -0.012329 | -61.2475 | 61.169 | 61.1336 | 61.1793 | -61.3016 | -61.2117 | 0.014095 | -61.26 | 61.0334 | 61.193 | 61.1138 | -61.5157 | -0.016194 | 0.075887 | 0.14666 | 0.03791 | 0.054104 | 0.040441 | 0.086176 | -0.23032 | -0.059704 | 0.073676 | 0.025434 | 0.25575 | 0.099853 | 0.02064 | 122.4544 | 122.419 | 122.4647 | 61.2731 | -122.3947 | 122.3188 | 122.4784 | 122.3992 | 61.2995 | -122.6089
801.9219 | 122.5479 | -61.2259 | 61.2122 | 1.4211e-13 | -0.0014807 | -0.0097224 | 0.03917 | -0.022721 | 0.048012 | 0.0036627 | -0.012148 | 0.028835 | 0.043943 | 0.0015577 | 0.046151 | -61.1433 | -0.003172 | -61.2566 | 61.1782 | 61.1244 | 61.1747 | -61.3016 | -61.2117 | 0.004938 | -61.2508 | 61.0334 | 61.193 | 61.1138 | -61.5157 | -0.075703 | -0.033974 | 0.082569 | -0.030755 | 0.044948 | -0.087735 | -0.03742 | -0.28983 | -0.17872 | 0.014167 | -0.024917 | 0.26491 | -0.019165 | -0.098378 | 122.4041 | 122.3503 | 122.4006 | 61.2227 | -122.5138 | 122.2593 | 122.4189 | 122.3397 | 61.2308 | -122.7279
803.7031 | 122.6715 | -61.2122 | 61.1618 | 1.4211e-13 | -0.0019081 | -0.0097224 | 0.03917 | -0.022935 | 0.047371 | -0.0039678 | -0.012361 | 0.029049 | 0.04437 | 0.0015577 | 0.046151 | -61.1296 | -0.003172 | -61.2566 | 61.1782 | 61.1336 | 61.1702 | -61.3062 | -61.2117 | 0.004938 | -61.2554 | 61.038 | 61.1838 | 61.1046 | -61.5203 | -0.094015 | 0.01638 | 0.082571 | -0.044488 | 0.049527 | -0.028223 | 0.008355 | -0.30814 | -0.12379 | 0.000434 | -0.043229 | 0.26491 | 0.022032 | -0.057181 | 122.3903 | 122.3457 | 122.3823 | 61.209 | -122.468 | 122.2502 | 122.396 | 122.3168 | 61.2171 | -122.6821
805.4844 | 122.6028 | -61.3312 | 61.1114 | 1.4211e-13 | -0.0014807 | -0.01015 | 0.038957 | -0.022721 | 0.048226 | 0.0036627 | -0.012148 | 0.028622 | 0.043729 | 0.0015577 | 0.046151 | -61.1342 | 0.001407 | -61.2521 | 61.1736 | 61.129 | 61.1747 | -61.3062 | -61.2071 | 0.014095 | -61.2554 | 61.038 | 61.1884 | 61.1092 | -61.5203 | 0.025004 | 0.062156 | 0.19701 | 0.079109 | 0.054105 | 0.017552 | 0.063288 | -0.18912 | -0.073436 | 0.12403 | 0.07579 | 0.26491 | 0.076965 | -0.002249 | 122.5048 | 122.4602 | 122.5059 | 61.3326 | -122.4176 | 122.3692 | 122.5196 | 122.4404 | 61.3453 | -122.6317
807.1875 | 122.6807 | -61.2442 | 61.0977 | 1.4211e-13 | -0.0016945 | -0.009936 | 0.038957 | -0.022721 | 0.047799 | 0.011293 | -0.012148 | 0.028622 | 0.043943 | 0.0017713 | 0.045937 | -61.1296 | -0.007751 | -61.2521 | 61.1782 | 61.1244 | 61.1747 | -61.3062 | -61.2117 | 0.009516 | -61.2508 | 61.038 | 61.1884 | 61.1092 | -61.5157 | -0.061971 | 0.080467 | 0.11462 | -0.007866 | 0.054105 | 0.026706 | 0.077021 | -0.27152 | -0.059703 | 0.032478 | -0.006606 | 0.26491 | 0.090698 | 0.011484 | 122.4224 | 122.3686 | 122.4189 | 61.2365 | -122.4039 | 122.2822 | 122.4326 | 122.3534 | 61.2537 | -122.6134
808.9531 | 122.6715 | -61.203 | 61.1481 | 1.4211e-13 | -0.0016945 | -0.0097224 | 0.03917 | -0.022935 | 0.048012 | -0.0039678 | -0.011934 | 0.028622 | 0.044157 | 0.0015577 | 0.046578 | -61.1296 | -0.012329 | -61.2475 | 61.1736 | 61.1198 | 61.1656 | -61.3062 | -61.2117 | 0.009516 | -61.26 | 61.0334 | 61.1838 | 61.1092 | -61.5249 | -0.10317 | 0.025535 | 0.073416 | -0.044487 | 0.058683 | -0.028227 | 0.017509 | -0.32187 | -0.11463 | -0.008721 | -0.056963 | 0.26491 | 0.035765 | -0.03887 | 122.3766 | 122.3228 | 122.3686 | 61.1907 | -122.4542 | 122.2364 | 122.3868 | 122.3122 | 61.2125 | -122.6729
810.6719 | 122.6532 | -61.2213 | 61.1618 | 1.4211e-13 | -0.0014807 | -0.0097224 | 0.038743 | -0.022935 | 0.048012 | 0.0036627 | -0.012148 | 0.028622 | 0.043729 | 0.0015577 | 0.046151 | -61.1342 | -0.007751 | -61.2566 | 61.1782 | 61.1244 | 61.1702 | -61.3062 | -61.2071 | 0.009516 | -61.2554 | 61.0334 | 61.193 | 61.1092 | -61.5157 | -0.08486 | 0.01638 | 0.087147 | -0.035333 | 0.049527 | -0.037381 | 0.008355 | -0.29441 | -0.12837 | 0.014167 | -0.034074 | 0.26033 | 0.031189 | -0.052603 | 122.3995 | 122.3457 | 122.3915 | 61.2136 | -122.468 | 122.2547 | 122.4143 | 122.3305 | 61.2308 | -122.6775
812.375 | 122.6624 | -61.2579 | 61.0748 | 1.4211e-13 | -0.0016945 | -0.0097224 | 0.038957 | -0.022935 | 0.048012 | 0.011293 | -0.012361 | 0.029049 | 0.043943 | 0.0013439 | 0.046151 | -61.1296 | -0.007751 | -61.2566 | 61.169 | 61.1244 | 61.1702 | -61.3108 | -61.2117 | 0.009516 | -61.2554 | 61.038 | 61.1976 | 61.1138 | -61.5111 | -0.052817 | 0.094198 | 0.12835 | 0.001289 | 0.054106 | 0.049594 | 0.09533 | -0.25321 | -0.036815 | 0.046211 | 0.002548 | 0.25576 | 0.12274 | 0.038951 | 122.427 | 122.3824 | 122.4281 | 61.2502 | -122.3856 | 122.2959 | 122.4555 | 122.3717 | 61.2675 | -122.586
814.1094 | 122.6807 | -61.2717 | 61.0748 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.038957 | -0.022721 | 0.047799 | 0.0036627 | -0.012361 | 0.028835 | 0.043943 | 0.0015577 | 0.046365 | -61.1296 | -0.007751 | -61.2521 | 61.1736 | 61.1198 | 61.1702 | -61.3062 | -61.2071 | 0.000359 | -61.2508 | 61.0334 | 61.193 | 61.1 | -61.5111 | -0.034506 | 0.098777 | 0.14208 | 0.019599 | 0.054105 | 0.045015 | 0.09533 | -0.23947 | -0.041393 | 0.064521 | 0.020859 | 0.26033 | 0.11816 | 0.025215 | 122.4453 | 122.3915 | 122.4418 | 61.2639 | -122.381 | 122.3051 | 122.4647 | 122.3717 | 61.272 | -122.586
815.8281 | 122.6303 | -61.2579 | 61.1069 | 1.4211e-13 | -0.0019081 | -0.0097224 | 0.039384 | -0.022721 | 0.048012 | 0.0036627 | -0.012361 | 0.028622 | 0.043729 | 0.0017713 | 0.046151 | -61.1296 | -0.007751 | -61.2429 | 61.1736 | 61.1198 | 61.1702 | -61.297 | -61.2026 | 0.014095 | -61.2554 | 61.038 | 61.1884 | 61.1046 | -61.5111 | -0.03908 | 0.066733 | 0.12835 | 0.015023 | 0.054103 | 0.012971 | 0.063286 | -0.25321 | -0.068859 | 0.055368 | 0.002548 | 0.25576 | 0.081542 | -0.00225 | 122.4315 | 122.3778 | 122.4281 | 61.2502 | -122.4039 | 122.2959 | 122.4463 | 122.3626 | 61.272 | -122.618
817.5469 | 122.6807 | -61.1938 | 61.1481 | 1.4211e-13 | -0.0014807 | -0.0097224 | 0.03917 | -0.023362 | 0.048012 | 0.011293 | -0.012148 | 0.028408 | 0.043516 | 0.0017713 | 0.046365 | -61.1296 | -0.003172 | -61.2475 | 61.1644 | 61.1153 | 61.1702 | -61.3016 | -61.2071 | 0.009516 | -61.2554 | 61.0334 | 61.1884 | 61.1 | -61.5157 | -0.10775 | 0.016378 | 0.064261 | -0.053642 | 0.054104 | -0.032806 | 0.022088 | -0.32187 | -0.11463 | -0.013298 | -0.061539 | 0.26033 | 0.040344 | -0.048027 | 122.3583 | 122.3091 | 122.364 | 61.1907 | -122.4497 | 122.2273 | 122.3823 | 122.2939 | 61.2034 | -122.6638
819.2656 | 122.6761 | -61.2762 | 61.0657 | 1.4211e-13 | -0.0014807 | -0.009936 | 0.03917 | -0.022507 | 0.047799 | 0.011293 | -0.012361 | 0.028622 | 0.043943 | 0.0013439 | 0.046151 | -61.1296 | -0.003172 | -61.2566 | 61.169 | 61.1244 | 61.1793 | -61.3062 | -61.198 | 0.004938 | -61.2417 | 61.038 | 61.193 | 61.1046 | -61.5066 | -0.029928 | 0.10335 | 0.14666 | 0.019599 | 0.049527 | 0.058749 | 0.11364 | -0.23032 | -0.02766 | 0.078257 | 0.034594 | 0.26491 | 0.12732 | 0.038949 | 122.4453 | 122.4007 | 122.4556 | 61.2731 | -122.3718 | 122.3143 | 122.4692 | 122.3809 | 61.2812 | -122.5722
821.0469 | 122.5754 | -61.2305 | 61.1618 | 1.4211e-13 | -0.0014807 | -0.0097224 | 0.038743 | -0.022935 | 0.048012 | 0.018923 | -0.012361 | 0.028835 | 0.043943 | 0.0017713 | 0.046365 | -61.1342 | -0.007751 | -61.2521 | 61.1644 | 61.1244 | 61.161 | -61.3016 | -61.2071 | 0.009516 | -61.2462 | 61.038 | 61.1884 | 61.1138 | -61.5157 | -0.071125 | 0.002645 | 0.096303 | -0.021599 | 0.049526 | -0.037381 | -0.000802 | -0.28525 | -0.12379 | 0.023323 | -0.015761 | 0.26949 | 0.026611 | -0.048024 | 122.3949 | 122.3549 | 122.3915 | 61.2227 | -122.4634 | 122.2685 | 122.4189 | 122.3442 | 61.24 | -122.6775
822.8125 | 122.5525 | -61.2213 | 61.1755 | 1.4211e-13 | -0.0019081 | -0.0097224 | 0.038957 | -0.023148 | 0.048226 | 0.0036627 | -0.012575 | 0.028622 | 0.043729 | 0.0011303 | 0.046365 | -61.1296 | -0.007751 | -61.2521 | 61.169 | 61.1198 | 61.1747 | -61.3062 | -61.2026 | 0.009516 | -61.2462 | 61.0334 | 61.193 | 61.1 | -61.5203 | -0.08486 | -0.00651 | 0.091726 | -0.030755 | 0.054105 | -0.055693 | -0.000799 | -0.29899 | -0.1421 | 0.018746 | -0.024917 | 0.27407 | 0.017456 | -0.075493 | 122.3903 | 122.3412 | 122.3961 | 61.2136 | -122.4817 | 122.2547 | 122.4143 | 122.3214 | 61.2308 | -122.6958
824.5938 | 122.612 | -61.2167 | 61.1389 | 1.4211e-13 | -0.0019081 | -0.0095086 | 0.03917 | -0.022935 | 0.048012 | 0.0036627 | -0.012148 | 0.029049 | 0.04437 | 0.0015577 | 0.045937 | -61.125 | -0.012329 | -61.2475 | 61.169 | 61.1198 | 61.1702 | -61.3016 | -61.2071 | 0.009516 | -61.2554 | 61.0426 | 61.1838 | 61.1046 | -61.5157 | -0.084858 | 0.030111 | 0.091727 | -0.030754 | 0.054104 | -0.019072 | 0.031243 | -0.29898 | -0.096323 | 0.00959 | -0.038651 | 0.26033 | 0.04492 | -0.034293 | 122.3858 | 122.3366 | 122.3869 | 61.2044 | -122.4405 | 122.2593 | 122.4006 | 122.3214 | 61.2263 | -122.6546
826.375 | 122.5433 | -61.2762 | 61.1526 | 1.4211e-13 | -0.0016945 | -0.0095086 | 0.038957 | -0.023148 | 0.048226 | 0.011293 | -0.012361 | 0.028622 | 0.044157 | 0.0015577 | 0.046365 | -61.1296 | -0.003172 | -61.2429 | 61.1736 | 61.1244 | 61.1656 | -61.2924 | -61.2071 | 0.009516 | -61.2417 | 61.0426 | 61.1838 | 61.1046 | -61.5111 | -0.016191 | 0.020957 | 0.14666 | 0.033333 | 0.049524 | -0.028226 | 0.012931 | -0.2349 | -0.11006 | 0.069099 | 0.034594 | 0.26949 | 0.031187 | -0.048026 | 122.4499 | 122.4007 | 122.4418 | 61.2731 | -122.4451 | 122.3188 | 122.4601 | 122.3809 | 61.2858 | -122.6638
828.0938 | 122.5845 | -61.2396 | 61.1664 | 1.4211e-13 | -0.0014807 | -0.0097224 | 0.03917 | -0.022935 | 0.048012 | -0.0039678 | -0.012361 | 0.028835 | 0.044157 | 0.0015577 | 0.046151 | -61.125 | -0.003172 | -61.2475 | 61.169 | 61.1198 | 61.1656 | -61.3062 | -61.2071 | 0.009516 | -61.2554 | 61.0334 | 61.1838 | 61.1092 | -61.5111 | -0.066549 | 0.002645 | 0.11462 | -0.007866 | 0.058683 | -0.046538 | -0.000802 | -0.27152 | -0.13295 | 0.032478 | -0.015763 | 0.25576 | 0.017454 | -0.057181 | 122.4087 | 122.3595 | 122.4052 | 61.2365 | -122.4726 | 122.2731 | 122.4235 | 122.3488 | 61.2491 | -122.6775
829.8594 | 122.5204 | -61.2076 | 61.2259 | 1.4211e-13 | -0.0014807 | -0.009936 | 0.03917 | -0.023148 | 0.048012 | 0.011293 | -0.012148 | 0.028622 | 0.044157 | 0.0017713 | 0.046365 | -61.1296 | -0.003172 | -61.2521 | 61.1644 | 61.1198 | 61.1702 | -61.3016 | -61.2026 | 0.004938 | -61.2417 | 61.0289 | 61.1838 | 61.0955 | -61.5111 | -0.094013 | -0.061442 | 0.077994 | -0.044487 | 0.049526 | -0.10605 | -0.055732 | -0.30356 | -0.19703 | 0.005014 | -0.03407 | 0.26949 | -0.042055 | -0.13043 | 122.372 | 122.3274 | 122.3777 | 61.2044 | -122.5275 | 122.2364 | 122.3914 | 122.303 | 61.2125 | -122.737
831.6406 | 122.6349 | -61.2213 | 61.1526 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.038743 | -0.022721 | 0.048012 | -0.0039678 | -0.012148 | 0.028622 | 0.043943 | 0.0015577 | 0.046365 | -61.1204 | -0.007751 | -61.2521 | 61.1782 | 61.1198 | 61.1656 | -61.3016 | -61.198 | 0.004938 | -61.2371 | 61.0334 | 61.1838 | 61.1 | -61.5111 | -0.080281 | 0.025535 | 0.10088 | -0.030755 | 0.049526 | -0.032805 | 0.012931 | -0.28983 | -0.11921 | 0.023325 | -0.015759 | 0.27407 | 0.031187 | -0.052605 | 122.3995 | 122.3412 | 122.3869 | 61.2136 | -122.4542 | 122.2547 | 122.4051 | 122.3214 | 61.2263 | -122.6638
833.4062 | 122.6578 | -61.2442 | 61.0886 | 1.4211e-13 | -0.0014807 | -0.0095086 | 0.03917 | -0.022935 | 0.047585 | 0.011293 | -0.011934 | 0.028835 | 0.044157 | 0.0017713 | 0.046365 | -61.1204 | -0.003172 | -61.2521 | 61.1828 | 61.1244 | 61.1656 | -61.297 | -61.198 | 0.009516 | -61.2508 | 61.0289 | 61.1838 | 61.1 | -61.5111 | -0.052813 | 0.0942 | 0.12377 | -0.007866 | 0.044947 | 0.035861 | 0.077018 | -0.26694 | -0.059705 | 0.046214 | -0.006606 | 0.26033 | 0.095274 | 0.011482 | 122.427 | 122.3686 | 122.4098 | 61.241 | -122.3856 | 122.2731 | 122.428 | 122.3442 | 61.2537 | -122.5997
835.1094 | 122.5708 | -61.2442 | 61.1847 | 1.4211e-13 | -0.0016945 | -0.01015 | 0.039384 | -0.023148 | 0.048226 | 0.0036627 | -0.011934 | 0.028622 | 0.044157 | 0.0015577 | 0.046365 | -61.1296 | -0.003172 | -61.2521 | 61.1736 | 61.1198 | 61.1656 | -61.3016 | -61.2026 | 0.004938 | -61.2508 | 61.0334 | 61.1884 | 61.1046 | -61.5203 | -0.057392 | -0.011086 | 0.11462 | -0.007866 | 0.049526 | -0.064848 | -0.019112 | -0.2761 | -0.15126 | 0.041635 | -0.006606 | 0.26949 | 0.003723 | -0.080069 | 122.4178 | 122.364 | 122.4098 | 61.241 | -122.4863 | 122.2776 | 122.4326 | 122.3488 | 61.2491 | -122.705
836.8906 | 122.6852 | -61.1801 | 61.1481 | 1.4211e-13 | -0.0014807 | -0.009936 | 0.03917 | -0.022935 | 0.047585 | 0.0036627 | -0.011934 | 0.028408 | 0.043516 | 0.0017713 | 0.046365 | -61.125 | -0.016908 | -61.2566 | 61.169 | 61.1153 | 61.161 | -61.297 | -61.1934 | 0.004938 | -61.2508 | 61.0334 | 61.1884 | 61.0955 | -61.5111 | -0.1169 | 0.020956 | 0.055106 | -0.076531 | 0.040369 | -0.032806 | 0.012931 | -0.33103 | -0.11463 | -0.013295 | -0.070693 | 0.26033 | 0.040344 | -0.052606 | 122.3491 | 122.2954 | 122.3411 | 61.1632 | -122.4451 | 122.2136 | 122.3685 | 122.2756 | 61.1851 | -122.6592
838.6094 | 122.6761 | -61.1984 | 61.1252 | 1.4211e-13 | -0.0016945 | -0.0097224 | 0.038957 | -0.022507 | 0.047799 | 0.0036627 | -0.012575 | 0.028622 | 0.043943 | 0.0015577 | 0.046151 | -61.125 | -0.007751 | -61.2566 | 61.1644 | 61.1198 | 61.161 | -61.297 | -61.2026 | 0.004938 | -61.2371 | 61.0334 | 61.1793 | 61.1 | -61.5111 | -0.09859 | 0.039266 | 0.073416 | -0.058221 | 0.040369 | -0.005339 | 0.035819 | -0.31272 | -0.091747 | -0.004142 | -0.038647 | 0.27407 | 0.054075 | -0.025139 | 122.3629 | 122.3183 | 122.3594 | 61.1907 | -122.4222 | 122.2319 | 122.3777 | 122.2985 | 61.2034 | -122.6363
840.3125 | 122.5662 | -61.2305 | 61.1526 | 1.4211e-13 | -0.0016945 | -0.0097224 | 0.038957 | -0.022935 | 0.048012 | 0.0036627 | -0.012148 | 0.028622 | 0.043943 | 0.0017713 | 0.046578 | -61.1204 | -0.007751 | -61.2521 | 61.169 | 61.1198 | 61.1656 | -61.297 | -61.198 | 0.009516 | -61.2462 | 61.0334 | 61.1838 | 61.1092 | -61.5111 | -0.066546 | 0.016378 | 0.11004 | -0.021599 | 0.044947 | -0.032805 | 0.012931 | -0.28067 | -0.11921 | 0.032481 | -0.015761 | 0.26491 | 0.031187 | -0.043448 | 122.3995 | 122.3503 | 122.396 | 61.2227 | -122.4497 | 122.2639 | 122.4143 | 122.3397 | 61.24 | -122.6638
842.0312 | 122.5983 | -61.2534 | 61.1389 | 1.4211e-13 | -0.0014807 | -0.009936 | 0.03917 | -0.022935 | 0.047799 | 0.018923 | -0.012361 | 0.028622 | 0.043729 | 0.0017713 | 0.046578 | -61.1204 | -0.007751 | -61.2475 | 61.1599 | 61.1153 | 61.161 | -61.2879 | -61.198 | 0.004938 | -61.2371 | 61.0334 | 61.1838 | 61.1 | -61.5111 | -0.0345 | 0.020954 | 0.13293 | 0.005867 | 0.040367 | -0.023651 | 0.022086 | -0.25778 | -0.10548 | 0.055369 | 0.016285 | 0.27407 | 0.04492 | -0.038872 | 122.4132 | 122.3686 | 122.4144 | 61.2456 | -122.4268 | 122.2868 | 122.4372 | 122.3534 | 61.2583 | -122.6501
843.8125 | 122.5845 | -61.2808 | 61.1023 | 1.4211e-13 | -0.0014807 | -0.01015 | 0.039384 | -0.022721 | 0.048226 | 0.0036627 | -0.011934 | 0.028835 | 0.044157 | 0.0013439 | 0.046151 | -61.1204 | 0.001407 | -61.2521 | 61.1736 | 61.1153 | 61.1656 | -61.2924 | -61.198 | 0.004938 | -61.2462 | 61.0289 | 61.1838 | 61.1 | -61.5066 | -0.011613 | 0.071311 | 0.16039 | 0.028755 | 0.040368 | 0.01297 | 0.063285 | -0.22574 | -0.073438 | 0.082835 | 0.034593 | 0.26033 | 0.081541 | -0.002251 | 122.4544 | 122.3961 | 122.4464 | 61.2822 | -122.3947 | 122.3097 | 122.4647 | 122.3809 | 61.2858 | -122.6089
845.6094 | 122.6486 | -61.2625 | 61.0565 | 1.4211e-13 | -0.0019081 | -0.0097224 | 0.038957 | -0.023148 | 0.048012 | 0.011293 | -0.012361 | 0.028835 | 0.044157 | 0.0013439 | 0.046151 | -61.125 | -0.007751 | -61.2612 | 61.169 | 61.1198 | 61.1747 | -61.297 | -61.1843 | 0.004938 | -61.2325 | 61.0151 | 61.1701 | 61.1 | -61.502 | -0.034503 | 0.11251 | 0.1375 | 0.001287 | 0.03579 | 0.063325 | 0.11822 | -0.23947 | -0.041397 | 0.07826 | 0.030019 | 0.26949 | 0.11358 | 0.043525 | 122.4315 | 122.3824 | 122.4373 | 61.2548 | -122.3535 | 122.2776 | 122.4326 | 122.3626 | 61.2675 | -122.5585
847.3125 | 122.6486 | -61.1893 | 61.1435 | 1.4211e-13 | -0.0019081 | -0.01015 | 0.03917 | -0.022721 | 0.047799 | 0.011293 | -0.012148 | 0.028835 | 0.043729 | 0.0019849 | 0.046365 | -61.1159 | -0.007751 | -61.2475 | 61.1644 | 61.1153 | 61.1656 | -61.2924 | -61.1934 | 0.000359 | -61.2417 | 61.0197 | 61.1793 | 61.1 | -61.502 | -0.10317 | 0.020955 | 0.073418 | -0.05822 | 0.044946 | -0.028229 | 0.022086 | -0.31271 | -0.12379 | -0.00414 | -0.052381 | 0.26033 | 0.035764 | -0.04345 | 122.3537 | 122.3045 | 122.3548 | 61.1815 | -122.4359 | 122.209 | 122.3685 | 122.2893 | 61.1896 | -122.6455
849.0938 | 122.5479 | -61.2122 | 61.1664 | 1.4211e-13 | -0.0016945 | -0.009936 | 0.03917 | -0.022935 | 0.047799 | 0.0036627 | -0.012148 | 0.028622 | 0.043943 | 0.0017713 | 0.046365 | -61.1159 | -0.003172 | -61.2475 | 61.169 | 61.1107 | 61.1656 | -61.2879 | -61.198 | 0.000359 | -61.2462 | 61.0197 | 61.1793 | 61.0955 | -61.502 | -0.075699 | 0.002645 | 0.096306 | -0.035332 | 0.040367 | -0.055696 | -0.000802 | -0.28983 | -0.14668 | 0.01417 | -0.034072 | 0.25575 | 0.012876 | -0.070917 | 122.3812 | 122.3228 | 122.3777 | 61.209 | -122.4542 | 122.2319 | 122.3914 | 122.3076 | 61.2125 | -122.6684
850.875 | 122.6212 | -61.203 | 61.1023 | 1.4211e-13 | -0.0021217 | -0.009936 | 0.038743 | -0.022721 | 0.047585 | 0.0036627 | -0.012148 | 0.028622 | 0.043729 | 0.0015577 | 0.046578 | -61.1204 | -0.012329 | -61.2521 | 61.1599 | 61.1107 | 61.1656 | -61.2833 | -61.1934 | 0.009516 | -61.2371 | 61.0243 | 61.1838 | 61.0909 | -61.5066 | -0.080275 | 0.057575 | 0.082573 | -0.049065 | 0.03121 | 0.008391 | 0.063285 | -0.30356 | -0.078016 | 0.009593 | -0.034069 | 0.26949 | 0.081541 | -0.011408 | 122.3629 | 122.3137 | 122.3686 | 61.1907 | -122.3856 | 122.2273 | 122.3868 | 122.2939 | 61.2125 | -122.6089
852.6406 | 122.5937 | -61.2396 | 61.1206 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.03917 | -0.022507 | 0.047799 | 0.0036627 | -0.011934 | 0.028835 | 0.043943 | 0.0013439 | 0.046365 | -61.1113 | -0.016908 | -61.2475 | 61.169 | 61.1153 | 61.1702 | -61.2879 | -61.1888 | 0.000359 | -61.2325 | 61.0151 | 61.1838 | 61.1 | -61.5066 | -0.048233 | 0.048422 | 0.12835 | -0.007866 | 0.040367 | -0.00534 | 0.049554 | -0.26694 | -0.10548 | 0.050793 | 0.007131 | 0.27407 | 0.063231 | -0.020561 | 122.4087 | 122.3549 | 122.4098 | 61.2227 | -122.4085 | 122.2547 | 122.4235 | 122.3397 | 61.24 | -122.6272
854.3594 | 122.5754 | -61.203 | 61.1801 | 1.4211e-13 | -0.0016945 | -0.0097224 | 0.03917 | -0.022721 | 0.047799 | 0.0036627 | -0.012148 | 0.028835 | 0.044157 | 0.0015577 | 0.046578 | -61.1204 | -0.003172 | -61.275 | 61.1599 | 61.1198 | 61.1656 | -61.2924 | -61.1934 | 0.000359 | -61.2417 | 61.0197 | 61.1793 | 61.1 | -61.5066 | -0.089433 | -0.020245 | 0.082573 | -0.071957 | 0.017476 | -0.060271 | -0.014535 | -0.30356 | -0.16042 | 0.009593 | -0.038648 | 0.26491 | -0.000857 | -0.080071 | 122.3629 | 122.3228 | 122.3686 | 61.1998 | -122.4726 | 122.2227 | 122.3823 | 122.303 | 61.2034 | -122.6867
856.1719 | 122.525 | -61.2717 | 61.1526 | 1.4211e-13 | -0.0014807 | -0.0097224 | 0.039384 | -0.022935 | 0.048012 | 0.018923 | -0.012148 | 0.028835 | 0.044157 | 0.0017713 | 0.046151 | -61.1159 | -0.007751 | -61.275 | 61.1644 | 61.1244 | 61.1702 | -61.2833 | -61.1934 | 0.004938 | -61.2417 | 61.0197 | 61.1793 | 61.0955 | -61.502 | -0.011611 | 0.0118 | 0.15582 | -0.003293 | 0.008318 | -0.028226 | 0.01751 | -0.23032 | -0.13295 | 0.078257 | 0.030016 | 0.26033 | 0.026609 | -0.057184 | 122.4361 | 122.3961 | 122.4418 | 61.2639 | -122.4359 | 122.2914 | 122.4509 | 122.3671 | 61.2766 | -122.6546
857.875 | 122.5113 | -61.2671 | 61.1389 | 1.4211e-13 | -0.0016945 | -0.0097224 | 0.038957 | -0.022935 | 0.047799 | 0.018923 | -0.011934 | 0.028622 | 0.043943 | 0.0015577 | 0.046578 | -61.1159 | -0.007751 | -61.275 | 61.1644 | 61.1153 | 61.161 | -61.2924 | -61.198 | 0.000359 | -61.2325 | 61.0197 | 61.1838 | 61.1 | -61.502 | -0.025346 | 0.025533 | 0.15124 | -0.00787 | 0.017476 | -0.023651 | 0.022086 | -0.23489 | -0.11922 | 0.069102 | 0.034597 | 0.26949 | 0.04492 | -0.038872 | 122.4315 | 122.3824 | 122.4281 | 61.2593 | -122.4314 | 122.2868 | 122.4509 | 122.3671 | 61.2674 | -122.6409
859.6406 | 122.644 | -61.2534 | 61.0611 | 1.4211e-13 | -0.0016945 | -0.009936 | 0.038957 | -0.022935 | 0.047799 | -0.011598 | -0.012575 | 0.028835 | 0.043943 | 0.0019849 | 0.046365 | -61.1159 | -0.003172 | -61.2704 | 61.1644 | 61.1153 | 61.1656 | -61.297 | -61.1888 | 0.004938 | -61.2325 | 61.0151 | 61.1747 | 61.1 | -61.502 | -0.043658 | 0.10335 | 0.13751 | -0.017024 | 0.026634 | 0.054169 | 0.10448 | -0.24863 | -0.045974 | 0.064526 | 0.020864 | 0.26949 | 0.11358 | 0.038948 | 122.4178 | 122.3686 | 122.4189 | 61.2502 | -122.3581 | 122.2685 | 122.428 | 122.3534 | 61.2583 | -122.5631
861.3594 | 122.5204 | -61.2579 | 61.1206 | 1.4211e-13 | -0.0014807 | -0.0097224 | 0.039384 | -0.022721 | 0.047799 | 0.0036627 | -0.012148 | 0.028622 | 0.043729 | 0.0015577 | 0.046151 | -61.1159 | -0.007751 | -61.2704 | 61.1644 | 61.1153 | 61.161 | -61.2879 | -61.1934 | 0.009516 | -61.2371 | 61.0151 | 61.1793 | 61.0955 | -61.5066 | -0.029922 | 0.043844 | 0.14208 | -0.012446 | 0.017476 | -0.00534 | 0.040397 | -0.24863 | -0.10548 | 0.064525 | 0.020863 | 0.26949 | 0.058653 | -0.02514 | 122.4224 | 122.3732 | 122.4189 | 61.2502 | -122.4085 | 122.2731 | 122.4372 | 122.3534 | 61.2675 | -122.6272
863.125 | 122.5616 | -61.2625 | 61.1114 | 1.4211e-13 | -0.0014807 | -0.0095086 | 0.038743 | -0.022721 | 0.048226 | 0.0036627 | -0.012148 | 0.028408 | 0.04437 | 0.0015577 | 0.046365 | -61.1113 | -0.007751 | -61.275 | 61.1736 | 61.1153 | 61.1656 | -61.2879 | -61.1888 | -0.00422 | -61.2325 | 61.0151 | 61.1838 | 61.1 | -61.502 | -0.025345 | 0.062156 | 0.15124 | -0.012448 | 0.012897 | 0.003815 | 0.05413 | -0.23947 | -0.096328 | 0.073681 | 0.030019 | 0.26949 | 0.072386 | -0.011406 | 122.4361 | 122.3778 | 122.4281 | 61.2548 | -122.3993 | 122.2776 | 122.4463 | 122.3626 | 61.2583 | -122.6134
864.9062 | 122.5159 | -61.2305 | 61.1938 | 1.4211e-13 | -0.0019081 | -0.009936 | 0.03917 | -0.023148 | 0.048012 | 0.0036627 | -0.011934 | 0.028835 | 0.043943 | 0.0019849 | 0.046365 | -61.1204 | -0.007751 | -61.2795 | 61.1599 | 61.1153 | 61.1656 | -61.2833 | -61.1843 | 0.004938 | -61.2371 | 61.0151 | 61.1793 | 61.1 | -61.4974 | -0.052809 | -0.033978 | 0.11004 | -0.049069 | 0.00374 | -0.078583 | -0.028268 | -0.26694 | -0.17873 | 0.046217 | -0.006603 | 0.26033 | -0.01459 | -0.093804 | 122.3903 | 122.3457 | 122.396 | 61.2227 | -122.4771 | 122.2456 | 122.4097 | 122.3305 | 61.2354 | -122.6913
866.625 | 122.5296 | -61.2946 | 61.116 | 1.4211e-13 | -0.0016945 | -0.009936 | 0.039384 | -0.022721 | 0.048012 | -0.0039678 | -0.012575 | 0.028408 | 0.043729 | 0.0017713 | 0.046578 | -61.1113 | -0.007751 | -61.2704 | 61.169 | 61.1198 | 61.1656 | -61.2879 | -61.1843 | 0.009516 | -61.2325 | 61.0197 | 61.1793 | 61.1 | -61.502 | 0.006699 | 0.052999 | 0.18328 | 0.024175 | 0.017476 | 0.003816 | 0.049552 | -0.20743 | -0.096328 | 0.1103 | 0.062063 | 0.26949 | 0.06323 | -0.015984 | 122.4636 | 122.4144 | 122.4601 | 61.2868 | -122.4039 | 122.3143 | 122.4738 | 122.3946 | 61.3041 | -122.618
868.3281 | 122.5021 | -61.2671 | 61.1481 | 1.4211e-13 | -0.0014807 | -0.009936 | 0.03917 | -0.022935 | 0.047799 | 0.011293 | -0.012148 | 0.028408 | 0.044157 | 0.0015577 | 0.046151 | -61.1113 | -0.003172 | -61.275 | 61.169 | 61.1107 | 61.1702 | -61.2833 | -61.1888 | 0.004938 | -61.2325 | 61.0197 | 61.1838 | 61.0955 | -61.4974 | -0.016188 | 0.020956 | 0.15582 | -0.00787 | 0.008318 | -0.037385 | 0.022088 | -0.23031 | -0.12837 | 0.078259 | 0.034597 | 0.26491 | 0.035765 | -0.052606 | 122.4361 | 122.3778 | 122.4372 | 61.2639 | -122.4313 | 122.2868 | 122.4509 | 122.3626 | 61.272 | -122.6455
870.1094 | 122.5845 | -61.2167 | 61.1206 | 1.4211e-13 | -0.0016945 | -0.0097224 | 0.038743 | -0.022935 | 0.047799 | 0.011293 | -0.011934 | 0.028622 | 0.044157 | 0.0019849 | 0.045937 | -61.1113 | -0.007751 | -61.2704 | 61.1644 | 61.1107 | 61.1702 | -61.2833 | -61.1888 | 0.004938 | -61.2325 | 61.0151 | 61.1747 | 61.1 | -61.4928 | -0.066542 | 0.043844 | 0.10546 | -0.053645 | 0.012897 | -0.009919 | 0.049554 | -0.27609 | -0.10548 | 0.027905 | -0.015757 | 0.26033 | 0.054074 | -0.020561 | 122.3812 | 122.3274 | 122.3869 | 61.209 | -122.4039 | 122.2319 | 122.3914 | 122.3168 | 61.2217 | -122.6134
871.8906 | 122.6028 | -61.2259 | 61.116 | 1.4211e-13 | -0.0016945 | -0.0097224 | 0.038743 | -0.022935 | 0.048012 | -0.0039678 | -0.012148 | 0.028622 | 0.043943 | 0.0013439 | 0.045937 | -61.1113 | -0.012329 | -61.2612 | 61.1599 | 61.1061 | 61.1702 | -61.2833 | -61.1888 | 0.004938 | -61.2279 | 61.0197 | 61.1747 | 61.0863 | -61.4974 | -0.057387 | 0.043842 | 0.11462 | -0.035334 | 0.022053 | -0.009921 | 0.054131 | -0.27151 | -0.096328 | 0.03706 | -0.002024 | 0.26949 | 0.058651 | -0.02972 | 122.3858 | 122.332 | 122.3961 | 61.2136 | -122.3993 | 122.2456 | 122.4006 | 122.3122 | 61.2308 | -122.6134
873.6875 | 122.4838 | -61.2762 | 61.1298 | 1.4211e-13 | -0.0014807 | -0.0097224 | 0.038957 | -0.022721 | 0.048012 | 0.011293 | -0.011934 | 0.028622 | 0.043729 | 0.0015577 | 0.046151 | -61.1113 | -0.007751 | -61.2658 | 61.1644 | 61.1153 | 61.1656 | -61.2833 | -61.1843 | 0.009516 | -61.2325 | 61.0105 | 61.1747 | 61.0909 | -61.4928 | -0.007033 | 0.034688 | 0.16497 | 0.010442 | 0.017475 | -0.014496 | 0.035819 | -0.21658 | -0.11922 | 0.091993 | 0.043752 | 0.26033 | 0.044918 | -0.038874 | 122.4407 | 122.3915 | 122.4418 | 61.2685 | -122.413 | 122.2868 | 122.4509 | 122.3671 | 61.2858 | -122.6226
875.4062 | 122.5845 | -61.2213 | 61.1206 | 1.4211e-13 | -0.0016945 | -0.009936 | 0.038957 | -0.023148 | 0.047799 | 0.0036627 | -0.012148 | 0.028408 | 0.043729 | 0.0017713 | 0.046365 | -61.1159 | -0.012329 | -61.2612 | 61.1599 | 61.1198 | 61.1656 | -61.2833 | -61.1843 | 0.004938 | -61.2279 | 61.0151 | 61.1701 | 61.0955 | -61.4928 | -0.061965 | 0.039265 | 0.10546 | -0.039912 | 0.022053 | -0.000761 | 0.044975 | -0.27151 | -0.10548 | 0.037061 | -0.006602 | 0.26491 | 0.049495 | -0.02514 | 122.3812 | 122.3412 | 122.3869 | 61.209 | -122.4039 | 122.2364 | 122.3914 | 122.3168 | 61.2263 | -122.6134
877.125 | 122.6303 | -61.2488 | 61.0565 | 1.4211e-13 | -0.0016945 | -0.01015 | 0.03917 | -0.022721 | 0.048012 | 0.0036627 | -0.012148 | 0.028408 | 0.043729 | 0.0017713 | 0.046578 | -61.1067 | -0.007751 | -61.2658 | 61.1644 | 61.1153 | 61.1702 | -61.2879 | -61.1888 | 0.004938 | -61.2325 | 61.0197 | 61.1793 | 61.0955 | -61.4974 | -0.039078 | 0.10793 | 0.14208 | -0.017024 | 0.022054 | 0.058746 | 0.11364 | -0.24863 | -0.036819 | 0.059948 | 0.016286 | 0.26491 | 0.12274 | 0.038946 | 122.4132 | 122.364 | 122.4189 | 61.241 | -122.3444 | 122.2685 | 122.428 | 122.3442 | 61.2537 | -122.5539
878.9062 | 122.6028 | -61.2122 | 61.0748 | 1.4211e-13 | -0.0014807 | -0.009936 | 0.038957 | -0.022935 | 0.047799 | 0.011293 | -0.012148 | 0.028835 | 0.04437 | 0.0013439 | 0.046578 | -61.1021 | -0.003172 | -61.2658 | 61.1599 | 61.1153 | 61.1702 | -61.2833 | -61.1843 | 0.004938 | -61.2279 | 61.0151 | 61.1747 | 61.1 | -61.4974 | -0.07112 | 0.085041 | 0.11004 | -0.053645 | 0.017475 | 0.040436 | 0.09533 | -0.28525 | -0.059707 | 0.027906 | -0.015757 | 0.26949 | 0.09985 | 0.025215 | 122.372 | 122.3274 | 122.3823 | 61.209 | -122.3581 | 122.2273 | 122.3868 | 122.3122 | 61.2171 | -122.5722
880.6406 | 122.5021 | -61.2259 | 61.116 | 1.4211e-13 | -0.0016945 | -0.01015 | 0.038957 | -0.023148 | 0.048012 | 0.011293 | -0.011934 | 0.028835 | 0.044157 | 0.0013439 | 0.046151 | -61.1021 | -0.012329 | -61.2704 | 61.1599 | 61.1107 | 61.161 | -61.2787 | -61.1797 | 0.009516 | -61.2233 | 61.0151 | 61.1747 | 61.0909 | -61.4882 | -0.052808 | 0.043842 | 0.12377 | -0.04449 | 0.008318 | -0.005342 | 0.044974 | -0.26236 | -0.10091 | 0.046218 | 0.002555 | 0.26491 | 0.058651 | -0.025141 | 122.3858 | 122.3366 | 122.3869 | 61.2136 | -122.3947 | 122.241 | 122.4006 | 122.3168 | 61.2354 | -122.6043
882.4062 | 122.5067 | -61.1938 | 61.2213 | 1.4211e-13 | -0.0016945 | -0.0097224 | 0.038957 | -0.022935 | 0.048012 | 0.0036627 | -0.012361 | 0.028622 | 0.044157 | 0.0017713 | 0.046578 | -61.1113 | -0.007751 | -61.2566 | 61.1599 | 61.1061 | 61.161 | -61.2833 | -61.1843 | 0.009516 | -61.2325 | 61.0151 | 61.1747 | 61.0909 | -61.4882 | -0.08943 | -0.061443 | 0.082574 | -0.062798 | 0.026632 | -0.11521 | -0.060311 | -0.2944 | -0.20619 | 0.009596 | -0.038645 | 0.25575 | -0.046634 | -0.13043 | 122.3537 | 122.3 | 122.3548 | 61.1861 | -122.5046 | 122.209 | 122.3685 | 122.2847 | 61.2034 | -122.7096
884.125 | 122.5388 | -61.2808 | 61.1298 | 1.4211e-13 | -0.0014807 | -0.0097224 | 0.03917 | -0.022721 | 0.048012 | 0.018923 | -0.011934 | 0.028835 | 0.044157 | 0.0015577 | 0.046151 | -61.1067 | -0.003172 | -61.2658 | 61.1644 | 61.1198 | 61.1702 | -61.2879 | -61.1797 | 0.004938 | -61.2325 | 61.0197 | 61.1793 | 61.1046 | -61.4928 | -0.007034 | 0.034688 | 0.17413 | 0.01502 | 0.022054 | -0.009917 | 0.040398 | -0.212 | -0.11006 | 0.10115 | 0.04833 | 0.26033 | 0.049497 | -0.025138 | 122.4453 | 122.4007 | 122.451 | 61.2777 | -122.4176 | 122.3005 | 122.4601 | 122.3854 | 61.2858 | -122.6226
885.8438 | 122.5525 | -61.2213 | 61.1984 | 1.4211e-13 | -0.0021217 | -0.0095086 | 0.038743 | -0.022935 | 0.048226 | 0.0036627 | -0.01172 | 0.029049 | 0.043729 | 0.0013439 | 0.046365 | -61.1021 | -0.012329 | -61.2658 | 61.1599 | 61.1107 | 61.1656 | -61.2787 | -61.1843 | 0.004938 | -61.2233 | 61.0151 | 61.1747 | 61.0955 | -61.4882 | -0.057386 | -0.038555 | 0.1192 | -0.04449 | 0.012896 | -0.087739 | -0.032845 | -0.26693 | -0.1833 | 0.037061 | -0.002023 | 0.26491 | -0.023746 | -0.10296 | 122.3812 | 122.332 | 122.3869 | 61.209 | -122.4771 | 122.2364 | 122.396 | 122.3168 | 61.2263 | -122.6867
887.625 | 122.5616 | -61.2167 | 61.1206 | 1.4211e-13 | -0.0016945 | -0.009936 | 0.039384 | -0.022935 | 0.047799 | -0.0039678 | -0.012575 | 0.028408 | 0.043729 | 0.0017713 | 0.046365 | -61.1021 | -0.003172 | -61.2704 | 61.1644 | 61.1153 | 61.1656 | -61.2741 | -61.1797 | 0.000359 | -61.2279 | 61.0151 | 61.1793 | 61.1 | -61.4974 | -0.057385 | 0.043844 | 0.11462 | -0.053645 | 0.00374 | -0.00534 | 0.044975 | -0.28067 | -0.10548 | 0.037063 | -0.011179 | 0.26949 | 0.058653 | -0.020561 | 122.3812 | 122.332 | 122.3823 | 61.2136 | -122.3947 | 122.2319 | 122.396 | 122.3168 | 61.2171 | -122.618
889.3281 | 122.5937 | -61.2213 | 61.116 | 1.4211e-13 | -0.0012671 | -0.0095086 | 0.038743 | -0.022935 | 0.047799 | 0.011293 | -0.01172 | 0.028194 | 0.043943 | 0.0015577 | 0.045937 | -61.093 | -0.012329 | -61.2566 | 61.1644 | 61.1153 | 61.1656 | -61.2741 | -61.1797 | 0.004938 | -61.2142 | 61.0151 | 61.1793 | 61.0955 | -61.4882 | -0.052808 | 0.048421 | 0.12835 | -0.035333 | 0.017475 | -0.000763 | 0.049552 | -0.26693 | -0.10091 | 0.04164 | 0.007134 | 0.27407 | 0.06323 | -0.020563 | 122.3858 | 122.3366 | 122.3869 | 61.209 | -122.3901 | 122.2364 | 122.4006 | 122.3168 | 61.2263 | -122.6043
891.125 | 122.58 | -61.2076 | 61.1389 | 1.4211e-13 | -0.0016945 | -0.0097224 | 0.03917 | -0.022721 | 0.048012 | 0.011293 | -0.012148 | 0.028622 | 0.043943 | 0.0017713 | 0.046151 | -61.1067 | -0.016908 | -61.2612 | 61.169 | 61.1153 | 61.1702 | -61.2741 | -61.1797 | 0.000359 | -61.2233 | 61.0105 | 61.1747 | 61.0909 | -61.4928 | -0.06654 | 0.030111 | 0.10089 | -0.053644 | 0.012896 | -0.023651 | 0.031243 | -0.28525 | -0.12837 | 0.027908 | -0.015755 | 0.26949 | 0.035763 | -0.048029 | 122.3766 | 122.3228 | 122.3777 | 61.1907 | -122.413 | 122.2181 | 122.3823 | 122.2985 | 61.2079 | -122.6317
892.8906 | 122.6166 | -61.1938 | 61.1343 | 1.4211e-13 | -0.0012671 | -0.0097224 | 0.03917 | -0.022721 | 0.048012 | -0.0039678 | -0.011934 | 0.028622 | 0.043729 | 0.0017713 | 0.045937 | -61.0975 | -0.007751 | -61.2566 | 61.1644 | 61.1153 | 61.161 | -61.2741 | -61.1797 | 0.000359 | -61.2188 | 61.0151 | 61.1701 | 61.0955 | -61.4928 | -0.080273 | 0.030111 | 0.09631 | -0.062798 | 0.017475 | -0.019073 | 0.026664 | -0.29898 | -0.11922 | 0.014175 | -0.024909 | 0.27407 | 0.035762 | -0.038873 | 122.3583 | 122.3091 | 122.3548 | 61.1861 | -122.4085 | 122.209 | 122.3639 | 122.2893 | 61.1942 | -122.6272
894.5938 | 122.5113 | -61.1984 | 61.1801 | 1.4211e-13 | -0.0016945 | -0.0095086 | 0.03917 | -0.022935 | 0.047585 | 0.0036627 | -0.012361 | 0.028622 | 0.044157 | 0.0017713 | 0.046151 | -61.0975 | -0.016908 | -61.2521 | 61.1553 | 61.1153 | 61.1656 | -61.265 | -61.1705 | 0.004938 | -61.2233 | 61.0151 | 61.1838 | 61.0909 | -61.4882 | -0.066538 | -0.024823 | 0.10089 | -0.053643 | 0.012895 | -0.06485 | -0.014535 | -0.28982 | -0.16499 | 0.027909 | -0.024911 | 0.26491 | 0.003721 | -0.089228 | 122.3537 | 122.3137 | 122.364 | 61.1815 | -122.4451 | 122.2135 | 122.3823 | 122.2893 | 61.2034 | -122.6684
896.3125 | 122.5708 | -61.2213 | 61.1252 | 1.4211e-13 | -0.0019081 | -0.0097224 | 0.038957 | -0.022721 | 0.047585 | 0.0036627 | -0.011934 | 0.028408 | 0.043943 | 0.0015577 | 0.046151 | -61.093 | -0.007751 | -61.2521 | 61.1644 | 61.1153 | 61.1702 | -61.2787 | -61.1705 | 0.009516 | -61.2325 | 61.0197 | 61.1838 | 61.0909 | -61.4837 | -0.057386 | 0.039266 | 0.12835 | -0.030755 | 0.026631 | -0.009918 | 0.044976 | -0.26236 | -0.10548 | 0.050797 | -0.01118 | 0.25118 | 0.058653 | -0.034296 | 122.3858 | 122.3366 | 122.3915 | 61.2136 | -122.4039 | 122.241 | 122.4051 | 122.3122 | 61.2308 | -122.6089
898.1094 | 122.5754 | -61.1801 | 61.1343 | 1.4211e-13 | -0.0014807 | -0.0095086 | 0.038529 | -0.022935 | 0.048226 | -0.0039678 | -0.011934 | 0.028835 | 0.043943 | 0.0015577 | 0.046578 | -61.093 | -0.003172 | -61.2521 | 61.1644 | 61.1153 | 61.1656 | -61.2741 | -61.1751 | 0.000359 | -61.2233 | 61.0197 | 61.1793 | 61.0955 | -61.4882 | -0.094006 | 0.030111 | 0.087155 | -0.071953 | 0.022053 | -0.019073 | 0.031242 | -0.30813 | -0.11464 | 0.00502 | -0.043221 | 0.26491 | 0.04492 | -0.038873 | 122.3446 | 122.2954 | 122.3457 | 61.1769 | -122.4085 | 122.1998 | 122.3594 | 122.2756 | 61.1805 | -122.6226
899.875 | 122.4884 | -61.2579 | 61.1069 | 1.4211e-13 | -0.0016945 | -0.0097224 | 0.03917 | -0.023148 | 0.048012 | 0.0036627 | -0.012148 | 0.028622 | 0.043943 | 0.0015577 | 0.046365 | -61.093 | -0.003172 | -61.2566 | 61.1644 | 61.1153 | 61.161 | -61.2695 | -61.1797 | 0.004938 | -61.2188 | 61.0151 | 61.193 | 61.0909 | -61.4837 | -0.011607 | 0.057576 | 0.16498 | 0.001289 | 0.012896 | 0.008392 | 0.054129 | -0.22573 | -0.091751 | 0.078262 | 0.039178 | 0.26491 | 0.08612 | -0.015986 | 122.4224 | 122.3732 | 122.4189 | 61.2548 | -122.3764 | 122.2731 | 122.4509 | 122.3488 | 61.2629 | -122.5905
901.6094 | 122.4792 | -61.2854 | 61.1343 | 1.4211e-13 | -0.0012671 | -0.009936 | 0.03917 | -0.022935 | 0.047585 | 0.0036627 | -0.01172 | 0.028622 | 0.043729 | 0.0017713 | 0.046151 | -61.0884 | -0.012329 | -61.2521 | 61.169 | 61.1198 | 61.1747 | -61.265 | -61.1705 | 0.004938 | -61.2233 | 61.0243 | 61.1747 | 61.0955 | -61.4837 | 0.020437 | 0.034689 | 0.19702 | 0.033332 | 0.012895 | -0.014494 | 0.0404 | -0.19827 | -0.11006 | 0.11488 | 0.062064 | 0.26033 | 0.040341 | -0.038873 | 122.4544 | 122.4052 | 122.4601 | 61.2731 | -122.3993 | 122.3097 | 122.4601 | 122.3809 | 61.2903 | -122.618
903.3281 | 122.5204 | -61.2259 | 61.1343 | 1.4211e-13 | -0.0014807 | -0.0095086 | 0.038957 | -0.023148 | 0.047585 | 0.011293 | -0.011934 | 0.028622 | 0.043943 | 0.0019849 | 0.045937 | -61.0884 | -0.016908 | -61.2521 | 61.169 | 61.1153 | 61.161 | -61.2741 | -61.1659 | 0.004938 | -61.2188 | 61.0105 | 61.1793 | 61.1 | -61.4837 | -0.04823 | 0.034689 | 0.13751 | -0.026177 | 0.022053 | -0.019073 | 0.026664 | -0.25778 | -0.1238 | 0.059954 | 0.007134 | 0.26491 | 0.04492 | -0.034294 | 122.3949 | 122.3412 | 122.3869 | 61.209 | -122.4085 | 122.2364 | 122.4051 | 122.3259 | 61.2308 | -122.618
905.1094 | 122.5845 | -61.2213 | 61.1206 | 1.4211e-13 | -0.0016945 | -0.0097224 | 0.03917 | -0.022935 | 0.048012 | 0.0036627 | -0.011934 | 0.028622 | 0.043729 | 0.0015577 | 0.046365 | -61.0884 | -0.007751 | -61.2521 | 61.1553 | 61.1107 | 61.1702 | -61.2695 | -61.1705 | -0.00422 | -61.2142 | 61.0151 | 61.1747 | 61.0955 | -61.4837 | -0.048229 | 0.034687 | 0.13293 | -0.030755 | 0.017474 | -0.009919 | 0.049554 | -0.26236 | -0.10548 | 0.050797 | 0.007134 | 0.26949 | 0.054074 | -0.02514 | 122.3766 | 122.332 | 122.3915 | 61.2136 | -122.3901 | 122.2364 | 122.396 | 122.3168 | 61.2171 | -122.6043
906.875 | 122.493 | -61.1801 | 61.2213 | 1.4211e-13 | -0.0014807 | -0.01015 | 0.03917 | -0.022935 | 0.048226 | 0.011293 | -0.012361 | 0.028408 | 0.04437 | 0.0017713 | 0.046151 | -61.093 | -0.012329 | -61.2521 | 61.1644 | 61.1107 | 61.1656 | -61.265 | -61.1797 | 0.004938 | -61.2004 | 61.0151 | 61.1747 | 61.1 | -61.4699 | -0.084848 | -0.056864 | 0.087155 | -0.071953 | 0.012895 | -0.11063 | -0.055733 | -0.28982 | -0.20619 | 0.000442 | -0.020327 | 0.26949 | -0.046634 | -0.12127 | 122.3446 | 122.2908 | 122.3457 | 61.1678 | -122.4863 | 122.1952 | 122.3548 | 122.2802 | 61.1851 | -122.6912
908.5938 | 122.612 | -61.1526 | 61.1526 | 1.4211e-13 | -0.0016945 | -0.009295 | 0.038957 | -0.022935 | 0.047799 | 0.011293 | -0.011934 | 0.028622 | 0.044157 | 0.0015577 | 0.046151 | -61.0975 | -0.016908 | -61.2521 | 61.1644 | 61.1198 | 61.161 | -61.2695 | -61.1705 | 0.000359 | -61.2142 | 61.0197 | 61.1884 | 61.0955 | -61.4745 | -0.11689 | 0.0118 | 0.055111 | -0.099419 | 0.017474 | -0.032805 | 0.008353 | -0.32186 | -0.13295 | -0.017867 | -0.06153 | 0.26033 | 0.035766 | -0.057184 | 122.3171 | 122.2725 | 122.3137 | 61.1357 | -122.4222 | 122.1723 | 122.3411 | 122.2481 | 61.153 | -122.6272
910.375 | 122.493 | -61.2717 | 61.1435 | 1.4211e-13 | -0.0014807 | -0.009295 | 0.038957 | -0.023362 | 0.048439 | 0.011293 | -0.012148 | 0.028622 | 0.043943 | 0.0017713 | 0.046365 | -61.093 | -0.012329 | -61.2475 | 61.169 | 61.1153 | 61.1702 | -61.265 | -61.1705 | -0.00422 | -61.2096 | 61.0151 | 61.1793 | 61.1 | -61.4791 | 0.006704 | 0.025533 | 0.17871 | 0.024177 | 0.017473 | -0.028229 | 0.026665 | -0.20742 | -0.12837 | 0.10115 | 0.062067 | 0.26949 | 0.035764 | -0.04345 | 122.4407 | 122.3869 | 122.4418 | 61.2593 | -122.4085 | 122.2868 | 122.4509 | 122.3717 | 61.2674 | -122.6226
912.1094 | 122.5388 | -61.2122 | 61.1343 | 1.4211e-13 | -0.0016945 | -0.009936 | 0.038957 | -0.022935 | 0.047799 | 0.018923 | -0.012148 | 0.028408 | 0.04437 | 0.0015577 | 0.046151 | -61.0792 | -0.021486 | -61.2475 | 61.169 | 61.1107 | 61.1702 | -61.265 | -61.1705 | 0.000359 | -61.2096 | 61.0197 | 61.1793 | 61.0909 | -61.4837 | -0.052805 | 0.034689 | 0.13293 | -0.035332 | 0.017473 | -0.023652 | 0.035821 | -0.27151 | -0.11464 | 0.041642 | 0.002558 | 0.27407 | 0.04492 | -0.043451 | 122.3812 | 122.3228 | 122.3823 | 61.1907 | -122.3993 | 122.2319 | 122.3914 | 122.303 | 61.2125 | -122.618
913.875 | 122.6166 | -61.1572 | 61.1389 | 1.4211e-13 | -0.0012671 | -0.0097224 | 0.03917 | -0.022935 | 0.048012 | 0.018923 | -0.011934 | 0.028622 | 0.043729 | 0.0019849 | 0.046578 | -61.0884 | -0.012329 | -61.2521 | 61.1553 | 61.1153 | 61.1702 | -61.265 | -61.1614 | 0.000359 | -61.2096 | 61.0151 | 61.1884 | 61.0909 | -61.4699 | -0.10774 | 0.016376 | 0.068845 | -0.094841 | 0.012895 | -0.023651 | 0.031243 | -0.31271 | -0.12379 | -0.004132 | -0.052373 | 0.26033 | 0.049499 | -0.048029 | 122.3125 | 122.2725 | 122.3274 | 61.1449 | -122.4039 | 122.1723 | 122.3456 | 122.2481 | 61.1576 | -122.6088
915.5938 | 122.525 | -61.2122 | 61.1755 | 1.4211e-13 | -0.0012671 | -0.0097224 | 0.039384 | -0.023148 | 0.048226 | 0.0036627 | -0.012148 | 0.028408 | 0.044157 | 0.0017713 | 0.046578 | -61.0838 | -0.007751 | -61.2475 | 61.169 | 61.1153 | 61.1656 | -61.2604 | -61.1659 | 0.000359 | -61.2096 | 61.0151 | 61.1838 | 61.0955 | -61.4745 | -0.048226 | -0.00651 | 0.12835 | -0.035332 | 0.012894 | -0.060272 | -0.009957 | -0.26235 | -0.16042 | 0.046221 | 0.002558 | 0.26491 | 0.008299 | -0.080072 | 122.3812 | 122.3274 | 122.3777 | 61.2044 | -122.4359 | 122.2273 | 122.396 | 122.3076 | 61.2125 | -122.65
917.3594 | 122.5021 | -61.1755 | 61.2076 | 1.4211e-13 | -0.0012671 | -0.01015 | 0.038957 | -0.023148 | 0.047799 | 0.011293 | -0.01172 | 0.028622 | 0.04437 | 0.0013439 | 0.046578 | -61.0884 | -0.016908 | -61.2429 | 61.1599 | 61.1061 | 61.1656 | -61.265 | -61.1614 | -0.00422 | -61.2096 | 61.0197 | 61.1747 | 61.0909 | -61.4699 | -0.089426 | -0.047711 | 0.087155 | -0.067375 | 0.022051 | -0.10147 | -0.042001 | -0.2944 | -0.18788 | 0.014178 | -0.034063 | 0.26033 | -0.032902 | -0.11669 | 122.3354 | 122.2816 | 122.3411 | 61.1586 | -122.4725 | 122.1952 | 122.3502 | 122.2664 | 61.1713 | -122.6775
919.0781 | 122.4609 | -61.2671 | 61.1343 | 1.4211e-13 | -0.0019081 | -0.0095086 | 0.038743 | -0.022935 | 0.048012 | 0.011293 | -0.012361 | 0.028622 | 0.044157 | 0.0017713 | 0.046365 | -61.0884 | -0.012329 | -61.2383 | 61.1644 | 61.1153 | 61.1747 | -61.2604 | -61.1705 | 0.004938 | -61.2096 | 61.0197 | 61.1793 | 61.0909 | -61.4745 | 0.006706 | 0.030111 | 0.17871 | 0.028757 | 0.022051 | -0.019073 | 0.0404 | -0.20742 | -0.11464 | 0.096574 | 0.05749 | 0.26491 | 0.04492 | -0.043451 | 122.4315 | 122.3824 | 122.4418 | 61.2548 | -122.3947 | 122.2868 | 122.4463 | 122.358 | 61.272 | -122.6088
920.8594 | 122.4884 | -61.1938 | 61.2122 | 1.4211e-13 | -0.0014807 | -0.009936 | 0.038957 | -0.022935 | 0.047799 | 0.011293 | -0.011934 | 0.028622 | 0.043943 | 0.0013439 | 0.046151 | -61.0838 | -0.016908 | -61.2429 | 61.1644 | 61.1198 | 61.1702 | -61.2512 | -61.1659 | -0.008798 | -61.2096 | 61.0151 | 61.1747 | 61.1 | -61.4745 | -0.057378 | -0.047709 | 0.11004 | -0.049064 | 0.008314 | -0.092314 | -0.041999 | -0.28066 | -0.19704 | 0.027911 | -0.015752 | 0.26491 | -0.037479 | -0.11211 | 122.3583 | 122.3137 | 122.364 | 61.1769 | -122.4634 | 122.209 | 122.3685 | 122.2939 | 61.1851 | -122.6867
922.5781 | 122.5708 | -61.1618 | 61.1618 | 1.4211e-13 | -0.0014807 | -0.0095086 | 0.038957 | -0.023148 | 0.047585 | -0.0039678 | -0.011934 | 0.028408 | 0.043943 | 0.0017713 | 0.045937 | -61.0838 | -0.016908 | -61.2338 | 61.1599 | 61.1153 | 61.1656 | -61.2604 | -61.1614 | 0.000359 | -61.2096 | 61.0243 | 61.1884 | 61.0955 | -61.4699 | -0.09858 | -0.001934 | 0.078001 | -0.071951 | 0.026629 | -0.046539 | 0.003776 | -0.30813 | -0.13752 | 0.000445 | -0.047796 | 0.26033 | 0.026611 | -0.066339 | 122.3217 | 122.2771 | 122.3274 | 61.1449 | -122.4222 | 122.1861 | 122.3502 | 122.2573 | 61.1622 | -122.6317
924.2812 | 122.4976 | -61.1618 | 61.2167 | 1.4211e-13 | -0.0012671 | -0.009936 | 0.038743 | -0.022507 | 0.048012 | 0.011293 | -0.011934 | 0.028408 | 0.043943 | 0.0017713 | 0.046365 | -61.0792 | -0.016908 | -61.2429 | 61.1599 | 61.1198 | 61.1702 | -61.2604 | -61.1568 | 0.000359 | -61.2004 | 61.0243 | 61.1793 | 61.0955 | -61.4699 | -0.09858 | -0.056866 | 0.082579 | -0.081108 | 0.017472 | -0.096892 | -0.046577 | -0.30813 | -0.19246 | 0.005024 | -0.038638 | 0.26949 | -0.037478 | -0.12127 | 122.3217 | 122.2816 | 122.332 | 61.1449 | -122.4771 | 122.1861 | 122.3411 | 122.2573 | 61.1622 | -122.6867
926.0469 | 122.4976 | -61.1847 | 61.1984 | 1.4211e-13 | -0.0014807 | -0.0097224 | 0.03917 | -0.022935 | 0.047585 | 0.011293 | -0.011934 | 0.028835 | 0.043943 | 0.0015577 | 0.046365 | -61.0792 | -0.012329 | -61.2429 | 61.169 | 61.1198 | 61.1702 | -61.2558 | -61.1659 | 0.004938 | -61.2096 | 61.0243 | 61.1793 | 61.1 | -61.4699 | -0.071113 | -0.029398 | 0.10547 | -0.05822 | 0.012893 | -0.078581 | -0.028266 | -0.28524 | -0.17415 | 0.018755 | -0.024908 | 0.26033 | -0.019167 | -0.098381 | 122.3537 | 122.3045 | 122.3549 | 61.1724 | -122.4542 | 122.209 | 122.3639 | 122.2847 | 61.1896 | -122.6684
927.8125 | 122.6166 | -61.1343 | 61.1664 | 1.4211e-13 | -0.0016945 | -0.0097224 | 0.03917 | -0.022721 | 0.047371 | 0.0036627 | -0.012361 | 0.028835 | 0.043943 | 0.0017713 | 0.046365 | -61.0746 | -0.012329 | -61.2429 | 61.1599 | 61.1107 | 61.1656 | -61.2558 | -61.1522 | 0.000359 | -61.2096 | 61.0151 | 61.1838 | 61.1 | -61.4654 | -0.12147 | -0.006512 | 0.059691 | -0.10857 | 0.012893 | -0.055696 | -0.000802 | -0.33102 | -0.15126 | -0.017863 | -0.075262 | 0.25575 | 0.017454 | -0.066338 | 122.2942 | 122.245 | 122.2999 | 61.122 | -122.4222 | 122.1495 | 122.3182 | 122.2344 | 61.1347 | -122.6317
929.5781 | 122.5845 | -61.1481 | 61.1847 | 1.4211e-13 | -0.0012671 | -0.0097224 | 0.038957 | -0.022935 | 0.047371 | 0.011293 | -0.012148 | 0.028835 | 0.043943 | 0.0015577 | 0.046151 | -61.0701 | -0.016908 | -61.2429 | 61.169 | 61.1153 | 61.1702 | -61.2604 | -61.1568 | 0.000359 | -61.1913 | 61.0151 | 61.1701 | 61.1046 | -61.4654 | -0.11231 | -0.015665 | 0.078003 | -0.094841 | 0.017472 | -0.069427 | -0.014533 | -0.31728 | -0.16957 | -0.008709 | -0.043214 | 0.27407 | -0.014592 | -0.080069 | 122.3171 | 122.2633 | 122.3182 | 61.1312 | -122.4451 | 122.1632 | 122.3182 | 122.2527 | 61.1484 | -122.65
931.2969 | 122.5754 | -61.2213 | 61.0703 | 1.4211e-13 | -0.0016945 | -0.009936 | 0.038743 | -0.022935 | 0.047799 | 0.011293 | -0.012361 | 0.028622 | 0.043943 | 0.0017713 | 0.046151 | -61.0792 | -0.007751 | -61.2383 | 61.169 | 61.1198 | 61.1702 | -61.2604 | -61.1522 | -0.00422 | -61.1959 | 61.0151 | 61.1884 | 61.0955 | -61.4654 | -0.039071 | 0.098776 | 0.14209 | -0.01702 | 0.022051 | 0.049593 | 0.099908 | -0.24404 | -0.055129 | 0.069112 | 0.025449 | 0.26949 | 0.11816 | 0.025214 | 122.3903 | 122.3412 | 122.3915 | 61.2136 | -122.3306 | 122.2364 | 122.4097 | 122.3168 | 61.2171 | -122.5356
933.0781 | 122.6166 | -61.1298 | 61.1435 | 1.4211e-13 | -0.0012671 | -0.0095086 | 0.038743 | -0.022721 | 0.048226 | 0.011293 | -0.011934 | 0.028408 | 0.043943 | 0.0017713 | 0.046578 | -61.0701 | -0.016908 | -61.2475 | 61.1644 | 61.1198 | 61.1702 | -61.2512 | -61.1568 | 0.000359 | -61.2004 | 61.0243 | 61.1838 | 61.1 | -61.4654 | -0.12147 | 0.020955 | 0.059693 | -0.11773 | 0.003736 | -0.02365 | 0.026665 | -0.33559 | -0.11921 | -0.027019 | -0.070681 | 0.26491 | 0.040342 | -0.04345 | 122.2942 | 122.2496 | 122.2999 | 61.1129 | -122.3947 | 122.154 | 122.3136 | 122.2298 | 61.1301 | -122.6088
934.8438 | 122.6212 | -61.1755 | 61.1435 | 1.4211e-13 | -0.0012671 | -0.009295 | 0.038957 | -0.023148 | 0.047799 | 0.0036627 | -0.012148 | 0.028622 | 0.043943 | 0.0015577 | 0.046151 | -61.0746 | -0.012329 | -61.2338 | 61.1599 | 61.1107 | 61.1702 | -61.2558 | -61.1476 | 0.004938 | -61.1959 | 61.0197 | 61.1838 | 61.0955 | -61.4654 | -0.080268 | 0.016376 | 0.10089 | -0.058218 | 0.02205 | -0.032808 | 0.026665 | -0.28982 | -0.12379 | 0.027915 | -0.020327 | 0.26949 | 0.040342 | -0.048029 | 122.3354 | 122.2862 | 122.3457 | 61.1632 | -122.3993 | 122.1952 | 122.3594 | 122.271 | 61.1805 | -122.6088
936.625 | 122.4701 | -61.2534 | 61.116 | 1.4211e-13 | -0.0016945 | -0.0097224 | 0.038743 | -0.022935 | 0.048012 | 0.011293 | -0.012148 | 0.028622 | 0.043729 | 0.0015577 | 0.046578 | -61.0792 | -0.021486 | -61.2338 | 61.169 | 61.1244 | 61.1747 | -61.2512 | -61.1522 | 0.000359 | -61.1913 | 61.0243 | 61.1838 | 61.1 | -61.4562 | 0.002131 | 0.052999 | 0.17413 | 0.019602 | 0.017471 | 0.008395 | 0.05871 | -0.20284 | -0.091749 | 0.10116 | 0.062072 | 0.26491 | 0.067808 | -0.015984 | 122.4224 | 122.3778 | 122.4281 | 61.2319 | -122.3673 | 122.2776 | 122.4372 | 122.3534 | 61.2537 | -122.5722
938.4062 | 122.5662 | -61.2213 | 61.084 | 1.4211e-13 | -0.0014807 | -0.009936 | 0.038743 | -0.022935 | 0.047799 | 0.0036627 | -0.011934 | 0.028408 | 0.043729 | 0.0015577 | 0.046365 | -61.0701 | -0.021486 | -61.2338 | 61.1644 | 61.1244 | 61.161 | -61.2604 | -61.1522 | 0.004938 | -61.2004 | 61.0197 | 61.1793 | 61.0909 | -61.4608 | -0.039071 | 0.080465 | 0.15125 | -0.012442 | 0.026629 | 0.040439 | 0.077018 | -0.23946 | -0.064284 | 0.069112 | 0.020871 | 0.26033 | 0.095274 | 0.006903 | 122.3858 | 122.3457 | 122.3823 | 61.1998 | -122.3444 | 122.241 | 122.4006 | 122.3122 | 61.2263 | -122.5448
940.1094 | 122.4792 | -61.2442 | 61.1664 | 1.4211e-13 | -0.0014807 | -0.009936 | 0.038957 | -0.022721 | 0.047585 | 0.011293 | -0.01172 | 0.028408 | 0.044157 | 0.0017713 | 0.046151 | -61.0746 | -0.021486 | -61.2383 | 61.1736 | 61.1198 | 61.1702 | -61.2466 | -61.1568 | -0.00422 | -61.1913 | 61.0197 | 61.1838 | 61.0955 | -61.4562 | -0.002445 | 0.007224 | 0.16956 | 0.005869 | 0.008314 | -0.046538 | 0.003777 | -0.21199 | -0.14668 | 0.087422 | 0.052917 | 0.26491 | 0.017454 | -0.070917 | 122.4178 | 122.364 | 122.4144 | 61.2227 | -122.413 | 122.2639 | 122.428 | 122.3397 | 61.24 | -122.6226
941.8906 | 122.5021 | -61.2213 | 61.1526 | 1.4211e-13 | -0.0012671 | -0.01015 | 0.038529 | -0.023148 | 0.047585 | 0.0036627 | -0.011934 | 0.028408 | 0.044157 | 0.0013439 | 0.046151 | -61.0609 | -0.021486 | -61.2338 | 61.169 | 61.1198 | 61.1702 | -61.2512 | -61.1476 | 0.000359 | -61.1867 | 61.0197 | 61.1747 | 61.1092 | -61.4608 | -0.029913 | 0.016378 | 0.1604 | -0.012442 | 0.017471 | -0.032805 | 0.01751 | -0.23946 | -0.13295 | 0.073691 | 0.034607 | 0.27407 | 0.02203 | -0.043448 | 122.3903 | 122.3412 | 122.3915 | 61.1998 | -122.4039 | 122.241 | 122.396 | 122.3305 | 61.2217 | -122.6134
943.6875 | 122.4747 | -61.2396 | 61.1343 | 1.4211e-13 | -0.0010533 | -0.0097224 | 0.039384 | -0.022935 | 0.047799 | 0.011293 | -0.012148 | 0.028622 | 0.043729 | 0.0017713 | 0.046365 | -61.0655 | -0.016908 | -61.2246 | 61.1644 | 61.1244 | 61.1747 | -61.2466 | -61.1476 | 0.000359 | -61.1959 | 61.0197 | 61.1793 | 61.1046 | -61.4562 | -0.007023 | 0.030111 | 0.17413 | 0.015026 | 0.022049 | -0.009915 | 0.0404 | -0.21657 | -0.11464 | 0.092002 | 0.04376 | 0.26033 | 0.04492 | -0.029715 | 122.4041 | 122.364 | 122.4144 | 61.2227 | -122.381 | 122.2593 | 122.4189 | 122.3442 | 61.24 | -122.5905
945.4531 | 122.5067 | -61.2122 | 61.1389 | 1.4211e-13 | -0.0012671 | -0.009936 | 0.038743 | -0.023362 | 0.047585 | 0.0036627 | -0.012148 | 0.028622 | 0.044157 | 0.0017713 | 0.046365 | -61.0609 | -0.016908 | -61.2338 | 61.169 | 61.1244 | 61.1793 | -61.2466 | -61.1522 | 0.000359 | -61.1867 | 61.0289 | 61.1747 | 61.1046 | -61.4516 | -0.034489 | 0.030111 | 0.15125 | -0.021597 | 0.012892 | -0.014493 | 0.0404 | -0.23946 | -0.11006 | 0.059957 | 0.025452 | 0.26491 | 0.035763 | -0.034293 | 122.3812 | 122.3366 | 122.3915 | 61.1953 | -122.3856 | 122.241 | 122.3868 | 122.3168 | 61.2125 | -122.5905
947.1875 | 122.5433 | -61.1664 | 61.1481 | 1.4211e-13 | -0.0014807 | -0.0095086 | 0.03917 | -0.022935 | 0.047585 | 0.0036627 | -0.01172 | 0.029049 | 0.043729 | 0.0017713 | 0.046578 | -61.0655 | -0.016908 | -61.2338 | 61.1644 | 61.1153 | 61.1747 | -61.2421 | -61.143 | -0.00422 | -61.1913 | 61.0289 | 61.1793 | 61.0955 | -61.4516 | -0.075686 | 0.016378 | 0.10089 | -0.067373 | 0.008313 | -0.032806 | 0.026667 | -0.28524 | -0.11921 | 0.023338 | -0.024903 | 0.26033 | 0.031187 | -0.052606 | 122.3308 | 122.2816 | 122.3411 | 61.1495 | -122.3901 | 122.1952 | 122.3456 | 122.2618 | 61.1622 | -122.5997
948.9688 | 122.5204 | -61.1572 | 61.1755 | 1.4211e-13 | -0.0012671 | -0.0095086 | 0.038957 | -0.022935 | 0.048012 | 0.011293 | -0.012148 | 0.028408 | 0.043729 | 0.0017713 | 0.046578 | -61.0609 | -0.012329 | -61.2292 | 61.169 | 61.1244 | 61.1702 | -61.2466 | -61.1385 | 0.004938 | -61.1913 | 61.0289 | 61.1793 | 61.1 | -61.4516 | -0.08942 | -0.00651 | 0.096316 | -0.07195 | 0.01747 | -0.051114 | -0.005378 | -0.29439 | -0.14668 | 0.018762 | -0.034058 | 0.26033 | 0.003721 | -0.075493 | 122.3263 | 122.2816 | 122.3274 | 61.1449 | -122.4222 | 122.1861 | 122.3365 | 122.2573 | 61.1622 | -122.6272
950.7344 | 122.4701 | -61.203 | 61.1664 | 1.4211e-13 | -0.0012671 | -0.0097224 | 0.039384 | -0.023148 | 0.048012 | 0.0036627 | -0.012361 | 0.028408 | 0.044157 | 0.0017713 | 0.046365 | -61.0655 | -0.016908 | -61.2292 | 61.1736 | 61.1153 | 61.1793 | -61.2375 | -61.1385 | 0.009516 | -61.1821 | 61.0289 | 61.1884 | 61.1 | -61.4516 | -0.034486 | 0.007224 | 0.13751 | -0.026174 | 0.008312 | -0.051117 | 0.012934 | -0.24861 | -0.13752 | 0.064538 | 0.020875 | 0.26949 | 0.022033 | -0.066338 | 122.3766 | 122.3183 | 122.3823 | 61.1861 | -122.4039 | 122.2319 | 122.3914 | 122.303 | 61.2125 | -122.618
952.5 | 122.4884 | -61.2076 | 61.1481 | 1.4211e-13 | -0.0014807 | -0.0097224 | 0.039384 | -0.022935 | 0.048012 | 0.011293 | -0.012148 | 0.028835 | 0.044157 | 0.0017713 | 0.046578 | -61.0609 | -0.016908 | -61.2292 | 61.1736 | 61.1244 | 61.1747 | -61.2421 | -61.1339 | 0.004938 | -61.1821 | 61.0243 | 61.1838 | 61.1 | -61.4516 | -0.034487 | 0.025535 | 0.14667 | -0.021596 | 0.012891 | -0.023648 | 0.026667 | -0.24404 | -0.12379 | 0.073695 | 0.025453 | 0.26949 | 0.035765 | -0.048027 | 122.3812 | 122.332 | 122.3823 | 61.1907 | -122.3901 | 122.2319 | 122.3914 | 122.3076 | 61.2125 | -122.5997
954.2188 | 122.4792 | -61.1984 | 61.1526 | 1.4211e-13 | -0.0012671 | -0.009936 | 0.03917 | -0.023148 | 0.048012 | -0.0039678 | -0.012148 | 0.028408 | 0.044157 | 0.0015577 | 0.046365 | -61.0655 | -0.021486 | -61.2246 | 61.1736 | 61.1198 | 61.1747 | -61.2329 | -61.1339 | -0.00422 | -61.1775 | 61.0243 | 61.1884 | 61.1092 | -61.4425 | -0.034485 | 0.020957 | 0.13294 | -0.026173 | 0.008312 | -0.032805 | 0.022089 | -0.24403 | -0.12837 | 0.064539 | 0.020876 | 0.26491 | 0.035766 | -0.043448 | 122.372 | 122.3183 | 122.3732 | 61.1769 | -122.3856 | 122.2227 | 122.3868 | 122.3076 | 61.1942 | -122.5951
956 | 122.5891 | -61.203 | 61.0886 | 1.4211e-13 | -0.0014807 | -0.0097224 | 0.03917 | -0.022935 | 0.047799 | 0.011293 | -0.012148 | 0.028408 | 0.04437 | 0.0015577 | 0.046365 | -61.0518 | -0.016908 | -61.2154 | 61.169 | 61.129 | 61.1885 | -61.2375 | -61.1385 | 0.000359 | -61.1775 | 61.0243 | 61.193 | 61.1092 | -61.4425 | -0.034486 | 0.080465 | 0.15125 | -0.012439 | 0.022047 | 0.04044 | 0.099911 | -0.23946 | -0.064283 | 0.064538 | 0.025454 | 0.26491 | 0.10443 | 0.020639 | 122.372 | 122.332 | 122.3915 | 61.1861 | -122.3261 | 122.2273 | 122.396 | 122.3122 | 61.2034 | -122.531
957.7031 | 122.4335 | -61.2305 | 61.1618 | 1.4211e-13 | -0.0014807 | -0.009936 | 0.03917 | -0.023148 | 0.048226 | 0.011293 | -0.012361 | 0.028408 | 0.044157 | 0.0015577 | 0.046578 | -61.0609 | -0.016908 | -61.2246 | 61.1782 | 61.1382 | 61.1747 | -61.2329 | -61.1385 | 0.004938 | -61.1775 | 61.0289 | 61.1884 | 61.1046 | -61.4516 | -0.002441 | 0.01638 | 0.16956 | 0.005871 | 0.008312 | -0.023645 | 0.012934 | -0.22115 | -0.13295 | 0.092004 | 0.05292 | 0.27407 | 0.026611 | -0.057181 | 122.4087 | 122.3686 | 122.4052 | 61.2136 | -122.3947 | 122.2593 | 122.4189 | 122.3351 | 61.2354 | -122.6134
959.4844 | 122.4792 | -61.2167 | 61.1114 | 1.4211e-13 | -0.0012671 | -0.0095086 | 0.038957 | -0.023362 | 0.047799 | 0.011293 | -0.012361 | 0.028622 | 0.04437 | 0.0017713 | 0.046365 | -61.0563 | -0.016908 | -61.2246 | 61.169 | 61.1336 | 61.1793 | -61.2329 | -61.1339 | -0.00422 | -61.1684 | 61.0289 | 61.1976 | 61.1 | -61.4425 | -0.016174 | 0.057577 | 0.1604 | -0.007862 | 0.008312 | 0.022131 | 0.067866 | -0.22572 | -0.082593 | 0.08285 | 0.048344 | 0.27407 | 0.086122 | -0.011406 | 122.3858 | 122.3503 | 122.3961 | 61.1998 | -122.3444 | 122.2456 | 122.4143 | 122.3168 | 61.2125 | -122.5539
961.2188 | 122.4701 | -61.1526 | 61.1893 | 1.4211e-13 | -0.0014807 | -0.0095086 | 0.038743 | -0.022935 | 0.047585 | 0.0036627 | -0.011934 | 0.028622 | 0.043302 | 0.0017713 | 0.045937 | -61.0518 | -0.021486 | -61.2154 | 61.1644 | 61.1336 | 61.1839 | -61.2375 | -61.1339 | 0.000359 | -61.1867 | 61.0243 | 61.1884 | 61.1046 | -61.4379 | -0.08484 | -0.024821 | 0.10089 | -0.062793 | 0.022047 | -0.055689 | -0.005375 | -0.28523 | -0.16499 | 0.018763 | -0.034057 | 0.25117 | -0.000855 | -0.084647 | 122.3171 | 122.2862 | 122.3365 | 61.1312 | -122.4268 | 122.1769 | 122.3411 | 122.2573 | 61.153 | -122.6272
963 | 122.4747 | -61.1984 | 61.1389 | 1.4211e-13 | -0.0014807 | -0.0095086 | 0.03917 | -0.022935 | 0.047585 | 0.0036627 | -0.012148 | 0.028622 | 0.043943 | 0.0013439 | 0.046151 | -61.0518 | -0.016908 | -61.2154 | 61.1782 | 61.129 | 61.1839 | -61.2283 | -61.1247 | 0.000359 | -61.173 | 61.0334 | 61.1976 | 61.1092 | -61.447 | -0.029906 | 0.039268 | 0.14667 | -0.017017 | 0.012889 | -0.009914 | 0.044979 | -0.24861 | -0.10548 | 0.073696 | 0.025455 | 0.27407 | 0.058656 | -0.029715 | 122.3766 | 122.3274 | 122.3823 | 61.1815 | -122.3672 | 122.2319 | 122.396 | 122.3076 | 61.1988 | -122.586
964.7188 | 122.4472 | -61.2076 | 61.116 | 1.4211e-13 | -0.0012671 | -0.0095086 | 0.038957 | -0.022935 | 0.047799 | -0.0039678 | -0.011934 | 0.028835 | 0.043943 | 0.0015577 | 0.046151 | -61.038 | -0.021486 | -61.2154 | 61.1782 | 61.1336 | 61.1839 | -61.2283 | -61.1293 | 0.004938 | -61.1775 | 61.0289 | 61.2022 | 61.1046 | -61.4333 | -0.02075 | 0.062156 | 0.16956 | -0.007861 | 0.012889 | 0.017553 | 0.067867 | -0.22572 | -0.087171 | 0.078273 | 0.030032 | 0.25575 | 0.086123 | -0.011405 | 122.3858 | 122.3412 | 122.3915 | 61.1861 | -122.3444 | 122.2364 | 122.4097 | 122.3122 | 61.2125 | -122.5493
966.4375 | 122.4747 | -61.1526 | 61.2213 | 1.4211e-13 | -0.0012671 | -0.0090814 | 0.038957 | -0.022935 | 0.048012 | 0.011293 | -0.012148 | 0.028622 | 0.043943 | 0.0017713 | 0.046365 | -61.0472 | -0.021486 | -61.2063 | 61.1782 | 61.129 | 61.1839 | -61.2238 | -61.1293 | -0.00422 | -61.173 | 61.0289 | 61.2022 | 61.1092 | -61.4379 | -0.071103 | -0.043129 | 0.10547 | -0.053636 | 0.017467 | -0.092311 | -0.037418 | -0.28523 | -0.19246 | 0.023341 | -0.020321 | 0.26491 | -0.019162 | -0.11211 | 122.3308 | 122.2817 | 122.3365 | 61.1312 | -122.4451 | 122.1815 | 122.3548 | 122.2618 | 61.1484 | -122.6592
968.1406 | 122.5159 | -61.1572 | 61.1801 | 1.4211e-13 | -0.0012671 | -0.009936 | 0.038957 | -0.022935 | 0.047799 | 0.0036627 | -0.011934 | 0.028194 | 0.043943 | 0.0017713 | 0.046365 | -61.0426 | -0.012329 | -61.22 | 61.1736 | 61.1336 | 61.1839 | -61.2283 | -61.1202 | -0.00422 | -61.173 | 61.0289 | 61.1976 | 61.1046 | -61.4379 | -0.071104 | -0.006509 | 0.11463 | -0.062793 | 0.008311 | -0.046534 | 0.00378 | -0.28065 | -0.15126 | 0.037077 | -0.015743 | 0.26491 | 0.017457 | -0.075492 | 122.3308 | 122.2908 | 122.3411 | 61.1449 | -122.4084 | 122.1861 | 122.3548 | 122.2618 | 61.153 | -122.618
969.8906 | 122.5983 | -61.1893 | 61.0703 | 1.4211e-13 | -0.0014807 | -0.009936 | 0.038957 | -0.022507 | 0.048226 | 0.011293 | -0.011934 | 0.028194 | 0.044157 | 0.0019849 | 0.046365 | -61.0426 | -0.026065 | -61.2063 | 61.1828 | 61.1336 | 61.1885 | -61.2146 | -61.1156 | 0.004938 | -61.173 | 61.0289 | 61.193 | 61.1138 | -61.4287 | -0.025325 | 0.11251 | 0.14667 | -0.017015 | 0.00831 | 0.06333 | 0.11822 | -0.23945 | -0.041394 | 0.073698 | 0.0163 | 0.25575 | 0.12274 | 0.043529 | 122.372 | 122.3229 | 122.3777 | 61.1632 | -122.2848 | 122.2181 | 122.3823 | 122.303 | 61.1942 | -122.499
971.6094 | 122.5891 | -61.1847 | 61.116 | 1.4211e-13 | -0.0012671 | -0.0097224 | 0.039384 | -0.023148 | 0.048439 | 0.011293 | -0.011934 | 0.028622 | 0.043943 | 0.0015577 | 0.046365 | -61.038 | -0.016908 | -61.1971 | 61.1736 | 61.1336 | 61.1931 | -61.2192 | -61.1247 | 0.000359 | -61.1638 | 61.0334 | 61.1976 | 61.1138 | -61.4333 | -0.034481 | 0.057578 | 0.14667 | -0.012437 | 0.022044 | 0.017553 | 0.077024 | -0.24861 | -0.082592 | 0.059963 | 0.020879 | 0.26949 | 0.081544 | -0.002248 | 122.3583 | 122.3183 | 122.3777 | 61.1678 | -122.3352 | 122.2181 | 122.3823 | 122.2985 | 61.1851 | -122.5493
973.3125 | 122.5845 | -61.1206 | 61.1481 | 1.4211e-13 | -0.0016945 | -0.0097224 | 0.03917 | -0.023148 | 0.047799 | 0.0036627 | -0.012148 | 0.028835 | 0.043729 | 0.0017713 | 0.045937 | -61.0426 | -0.016908 | -61.2063 | 61.1873 | 61.1382 | 61.1885 | -61.2283 | -61.1202 | 0.000359 | -61.1684 | 61.0334 | 61.2022 | 61.1092 | -61.4241 | -0.10773 | 0.03927 | 0.078007 | -0.08568 | 0.022046 | -0.009912 | 0.040402 | -0.30354 | -0.11463 | 0.000455 | -0.047787 | 0.25575 | 0.05408 | -0.03887 | 122.3079 | 122.2588 | 122.3091 | 61.1037 | -122.3764 | 122.154 | 122.3228 | 122.2298 | 61.121 | -122.5722
975.0781 | 122.5433 | -61.1572 | 61.1298 | 1.4211e-13 | -0.0016945 | -0.0097224 | 0.038957 | -0.022935 | 0.047799 | 0.011293 | -0.012148 | 0.028408 | 0.043943 | 0.0021987 | 0.046151 | -61.0334 | -0.021486 | -61.2017 | 61.1828 | 61.1336 | 61.1885 | -61.2146 | -61.1202 | 0.004938 | -61.1547 | 61.0426 | 61.2067 | 61.1184 | -61.4333 | -0.057368 | 0.053001 | 0.12379 | -0.04448 | 0.012888 | 0.00382 | 0.058712 | -0.27607 | -0.087168 | 0.037077 | 0.002572 | 0.27865 | 0.076968 | -0.011403 | 122.34 | 122.2908 | 122.3457 | 61.1357 | -122.3444 | 122.1998 | 122.364 | 122.2756 | 61.1622 | -122.5631
976.7969 | 122.4701 | -61.1069 | 61.2076 | 1.4211e-13 | -0.0012671 | -0.0097224 | 0.03917 | -0.022721 | 0.048012 | 0.011293 | -0.01172 | 0.028194 | 0.044157 | 0.0015577 | 0.045937 | -61.0426 | -0.021486 | -61.2017 | 61.1782 | 61.1336 | 61.1839 | -61.2146 | -61.1156 | 0.000359 | -61.1638 | 61.0334 | 61.2022 | 61.1138 | -61.4287 | -0.10772 | -0.029397 | 0.064275 | -0.094834 | 0.012888 | -0.074 | -0.023686 | -0.32185 | -0.17414 | -0.008699 | -0.05694 | 0.26491 | -0.00543 | -0.093801 | 122.2851 | 122.2405 | 122.2908 | 61.0854 | -122.4222 | 122.1403 | 122.309 | 122.2207 | 61.1072 | -122.6363
978.5781 | 122.4655 | -61.1893 | 61.1526 | 1.4211e-13 | -0.0014807 | -0.009936 | 0.03917 | -0.023362 | 0.047371 | 0.011293 | -0.011934 | 0.029049 | 0.044157 | 0.0019849 | 0.046365 | -61.0426 | -0.021486 | -61.2017 | 61.1873 | 61.1473 | 61.1885 | -61.2146 | -61.1156 | 0.000359 | -61.1547 | 61.038 | 61.2067 | 61.1138 | -61.4287 | -0.025325 | 0.034692 | 0.14667 | -0.012437 | 0.012888 | -0.005332 | 0.035824 | -0.23945 | -0.11463 | 0.073698 | 0.034615 | 0.27407 | 0.05408 | -0.038869 | 122.3766 | 122.3366 | 122.3777 | 61.1678 | -122.3672 | 122.2273 | 122.396 | 122.303 | 61.1896 | -122.5814
980.2969 | 122.4701 | -61.1206 | 61.2534 | 1.4211e-13 | -0.0014807 | -0.009295 | 0.03917 | -0.022721 | 0.047585 | 0.0036627 | -0.011934 | 0.028408 | 0.04437 | 0.0019849 | 0.046151 | -61.0334 | -0.026065 | -61.2017 | 61.1828 | 61.1519 | 61.1976 | -61.21 | -61.1156 | -0.00422 | -61.1592 | 61.038 | 61.2022 | 61.1138 | -61.4196 | -0.089411 | -0.070595 | 0.087164 | -0.081102 | 0.008309 | -0.10146 | -0.055726 | -0.29896 | -0.21534 | 0.005033 | -0.038629 | 0.26033 | -0.051206 | -0.13958 | 122.3034 | 122.2725 | 122.3182 | 61.0945 | -122.4634 | 122.1586 | 122.3228 | 122.2344 | 61.1164 | -122.6729
982.0938 | 122.5388 | -61.1435 | 61.1526 | 1.4211e-13 | -0.0012671 | -0.0097224 | 0.038743 | -0.022721 | 0.048012 | 0.026554 | -0.012575 | 0.028622 | 0.044157 | 0.0015577 | 0.046151 | -61.0334 | -0.026065 | -61.1971 | 61.1919 | 61.1336 | 61.1976 | -61.2054 | -61.1018 | -0.008798 | -61.1638 | 61.0334 | 61.2067 | 61.1184 | -61.415 | -0.061943 | 0.03927 | 0.11005 | -0.053635 | 0.008308 | -0.019068 | 0.044982 | -0.27149 | -0.11921 | 0.041659 | -0.020319 | 0.25117 | 0.05408 | -0.034291 | 122.3354 | 122.2771 | 122.3411 | 61.1174 | -122.3581 | 122.1769 | 122.3502 | 122.2619 | 61.1347 | -122.5676
983.7969 | 122.5845 | -61.1481 | 61.1114 | 1.4211e-13 | -0.0010533 | -0.0095086 | 0.03917 | -0.022721 | 0.048012 | 0.0036627 | -0.011934 | 0.028194 | 0.044157 | 0.0017713 | 0.046578 | -61.0334 | -0.016908 | -61.1834 | 61.1828 | 61.1427 | 61.2022 | -61.21 | -61.1064 | 0.000359 | -61.1501 | 61.0426 | 61.2067 | 61.1184 | -61.4196 | -0.061945 | 0.071312 | 0.11463 | -0.035323 | 0.026622 | 0.031288 | 0.090759 | -0.27149 | -0.068857 | 0.041657 | -0.002006 | 0.26949 | 0.095279 | 0.006908 | 122.3308 | 122.2908 | 122.3503 | 61.1312 | -122.3215 | 122.1907 | 122.3548 | 122.2664 | 61.1484 | -122.531
985.5625 | 122.4838 | -61.1847 | 61.1481 | 1.4211e-13 | -0.0016945 | -0.0095086 | 0.039384 | -0.022935 | 0.048012 | 0.011293 | -0.012361 | 0.028194 | 0.043943 | 0.0015577 | 0.046365 | -61.0151 | -0.021486 | -61.1926 | 61.1965 | 61.1565 | 61.2022 | -61.2054 | -61.1018 | 0.000359 | -61.1547 | 61.0472 | 61.2022 | 61.1229 | -61.4241 | -0.020745 | 0.048427 | 0.16956 | -0.007859 | 0.012886 | 0.008404 | 0.054138 | -0.23945 | -0.1009 | 0.082857 | 0.030037 | 0.26949 | 0.05408 | -0.025134 | 122.3812 | 122.3412 | 122.3869 | 61.1632 | -122.3535 | 122.2319 | 122.3868 | 122.3076 | 61.1851 | -122.5722
987.2812 | 122.5113 | -61.1618 | 61.0977 | 1.4211e-13 | -0.0010533 | -0.0097224 | 0.038743 | -0.022935 | 0.048012 | 0.0036627 | -0.012148 | 0.028408 | 0.043943 | 0.0017713 | 0.046151 | -61.0197 | -0.026065 | -61.1834 | 61.1965 | 61.1473 | 61.1931 | -61.1963 | -61.0973 | 0.004938 | -61.1455 | 61.0426 | 61.2113 | 61.1229 | -61.415 | -0.034475 | 0.098781 | 0.1421 | -0.02159 | 0.012885 | 0.0496 | 0.095335 | -0.25318 | -0.055124 | 0.064547 | 0.016306 | 0.26949 | 0.11359 | 0.02522 | 122.3583 | 122.3091 | 122.3549 | 61.1357 | -122.294 | 122.2044 | 122.3731 | 122.2847 | 61.1667 | -122.5127
988.9844 | 122.5571 | -61.1343 | 61.1572 | 1.4211e-13 | -0.0012671 | -0.0095086 | 0.03917 | -0.022935 | 0.047799 | 0.0036627 | -0.012361 | 0.028408 | 0.043516 | 0.0017713 | 0.046151 | -61.0151 | -0.021486 | -61.1788 | 61.1965 | 61.1473 | 61.1976 | -61.1917 | -61.1018 | 0.004938 | -61.1409 | 61.0472 | 61.2113 | 61.1229 | -61.4104 | -0.057362 | 0.039271 | 0.11921 | -0.044478 | 0.012884 | -0.00991 | 0.040404 | -0.27607 | -0.11006 | 0.032503 | -0.006581 | 0.26949 | 0.054081 | -0.03429 | 122.3308 | 122.2817 | 122.332 | 61.1129 | -122.3489 | 122.1815 | 122.3456 | 122.2573 | 61.1393 | -122.5676
990.75 | 122.5296 | -61.1435 | 61.171 | 1.4211e-13 | -0.0012671 | -0.0097224 | 0.038957 | -0.023148 | 0.047585 | -0.0039678 | -0.012361 | 0.028408 | 0.043943 | 0.0017713 | 0.046151 | -61.0105 | -0.021486 | -61.1834 | 61.1965 | 61.1473 | 61.1931 | -61.1825 | -61.0973 | 0.000359 | -61.1455 | 61.0563 | 61.2067 | 61.1275 | -61.4104 | -0.039048 | 0.025539 | 0.13294 | -0.0399 | -0.000852 | -0.023642 | 0.022093 | -0.26691 | -0.11463 | 0.046237 | -0.002004 | 0.26491 | 0.03577 | -0.043443 | 122.34 | 122.2908 | 122.3365 | 61.122 | -122.3535 | 122.1998 | 122.3502 | 122.271 | 61.1439 | -122.5814
992.4688 | 122.4747 | -61.1298 | 61.235 | 1.4211e-13 | -0.0012671 | -0.0097224 | 0.038957 | -0.023148 | 0.048012 | 0.0036627 | -0.012361 | 0.028622 | 0.043943 | 0.0015577 | 0.046365 | -61.0105 | -0.026065 | -61.1788 | 61.1919 | 61.1565 | 61.2114 | -61.1963 | -61.0973 | 0.000359 | -61.1363 | 61.0517 | 61.2113 | 61.1367 | -61.4058 | -0.066518 | -0.043127 | 0.11921 | -0.049055 | 0.017463 | -0.078571 | -0.02368 | -0.27607 | -0.1833 | 0.032504 | -0.00658 | 0.26949 | -0.023738 | -0.098373 | 122.3217 | 122.2862 | 122.3411 | 61.1037 | -122.4313 | 122.1815 | 122.3411 | 122.2664 | 61.1301 | -122.6409
994.1875 | 122.5342 | -61.1114 | 61.1801 | 1.4211e-13 | -0.0012671 | -0.0097224 | 0.03917 | -0.022507 | 0.048012 | 0.0036627 | -0.012148 | 0.028622 | 0.043729 | 0.0015577 | 0.046365 | -61.0105 | -0.021486 | -61.1697 | 61.1965 | 61.1565 | 61.2114 | -61.1871 | -61.0927 | 0.000359 | -61.1409 | 61.0517 | 61.2113 | 61.1275 | -61.4058 | -0.075671 | 0.016383 | 0.1009 | -0.058209 | 0.017462 | -0.02364 | 0.031251 | -0.29438 | -0.12837 | 0.018772 | -0.029469 | 0.26491 | 0.031193 | -0.052599 | 122.3079 | 122.2679 | 122.3228 | 61.09 | -122.3672 | 122.1632 | 122.3228 | 122.239 | 61.1118 | -122.5859
995.9531 | 122.58 | -61.1343 | 61.1114 | 1.4211e-13 | -0.0010533 | -0.0097224 | 0.03917 | -0.023148 | 0.047585 | 0.0036627 | -0.012361 | 0.028408 | 0.043943 | 0.0015577 | 0.046151 | -61.0014 | -0.021486 | -61.1697 | 61.1965 | 61.1565 | 61.2068 | -61.1917 | -61.0835 | 0.009516 | -61.1363 | 61.0655 | 61.2159 | 61.1413 | -61.3967 | -0.057362 | 0.085048 | 0.13295 | -0.035321 | 0.022041 | 0.045025 | 0.095338 | -0.26233 | -0.045965 | 0.050817 | -0.002003 | 0.26033 | 0.10444 | 0.029801 | 122.3308 | 122.2908 | 122.3411 | 61.1129 | -122.3031 | 122.1998 | 122.3502 | 122.2756 | 61.1439 | -122.5081
997.7188 | 122.5342 | -61.1481 | 61.116 | 1.4211e-13 | -0.0014807 | -0.0095086 | 0.038743 | -0.022721 | 0.047585 | 0.011293 | -0.012148 | 0.028408 | 0.043516 | 0.0017713 | 0.046365 | -61.006 | -0.021486 | -61.1651 | 61.2011 | 61.1473 | 61.2114 | -61.1871 | -61.0835 | -0.00422 | -61.1272 | 61.0609 | 61.225 | 61.1413 | -61.3921 | -0.03905 | 0.085048 | 0.1421 | -0.01701 | 0.02204 | 0.031289 | 0.095338 | -0.24402 | -0.055121 | 0.06455 | 0.020888 | 0.26491 | 0.10902 | 0.025223 | 122.3491 | 122.2954 | 122.3594 | 61.1266 | -122.3031 | 122.209 | 122.3731 | 122.2893 | 61.1439 | -122.5081
999.4844 | 122.4243 | -61.171 | 61.1618 | 1.4211e-13 | -0.0012671 | -0.0097224 | 0.039598 | -0.023148 | 0.048012 | 0.011293 | -0.012361 | 0.028622 | 0.04437 | 0.0013439 | 0.046151 | -61.0014 | -0.021486 | -61.1697 | 61.2102 | 61.1656 | 61.2159 | -61.1871 | -61.0835 | -0.008798 | -61.1272 | 61.0655 | 61.225 | 61.1413 | -61.3921 | -0.016162 | 0.048429 | 0.16957 | 0.0013 | 0.017462 | 0.003829 | 0.054141 | -0.22113 | -0.096319 | 0.087438 | 0.043776 | 0.26491 | 0.06324 | -0.020553 | 122.3812 | 122.3366 | 122.3869 | 61.1495 | -122.3489 | 122.2364 | 122.396 | 122.3122 | 61.1622 | -122.5539
1001.2188 | 122.4335 | -61.1114 | 61.2488 | 1.4211e-13 | -0.0014807 | -0.0097224 | 0.038957 | -0.023148 | 0.048012 | 0.0036627 | -0.012361 | 0.028622 | 0.043729 | 0.0019849 | 0.046365 | -61.0151 | -0.021486 | -61.1651 | 61.2102 | 61.1656 | 61.2251 | -61.1825 | -61.0835 | 0.000359 | -61.1272 | 61.0609 | 61.225 | 61.1367 | -61.3921 | -0.071092 | -0.038546 | 0.096323 | -0.053631 | 0.017461 | -0.083146 | -0.023677 | -0.28064 | -0.18787 | 0.027929 | -0.015733 | 0.26491 | -0.023735 | -0.11211 | 122.3217 | 122.2771 | 122.3366 | 61.09 | -122.4313 | 122.1724 | 122.3365 | 122.2481 | 61.1118 | -122.6409
1002.9844 | 122.5204 | -61.1114 | 61.1572 | 1.4211e-13 | -0.0014807 | -0.009936 | 0.038957 | -0.022935 | 0.047371 | 0.0036627 | -0.011934 | 0.028622 | 0.043943 | 0.0015577 | 0.046151 | -60.9968 | -0.026065 | -61.1605 | 61.2057 | 61.1656 | 61.2205 | -61.1734 | -61.0744 | 0.000359 | -61.118 | 61.0609 | 61.2342 | 61.1413 | -61.3829 | -0.061934 | 0.048427 | 0.11464 | -0.049053 | 0.012881 | 0.008406 | 0.063297 | -0.27149 | -0.09632 | 0.037087 | -0.006576 | 0.26491 | 0.076974 | -0.015976 | 122.3171 | 122.2771 | 122.332 | 61.0854 | -122.3306 | 122.1724 | 122.3457 | 122.2527 | 61.1118 | -122.5402
1004.7656 | 122.5708 | -61.1298 | 61.116 | 1.4211e-13 | -0.00083973 | -0.0097224 | 0.03917 | -0.023148 | 0.047799 | 0.018923 | -0.011934 | 0.028408 | 0.04437 | 0.0017713 | 0.046365 | -60.9831 | -0.026065 | -61.1468 | 61.2011 | 61.1656 | 61.2159 | -61.1642 | -61.0652 | 0.004938 | -61.1134 | 61.0655 | 61.2342 | 61.1367 | -61.3875 | -0.034465 | 0.085048 | 0.14668 | -0.017007 | 0.017458 | 0.049605 | 0.099917 | -0.25775 | -0.050543 | 0.064555 | 0.016314 | 0.27407 | 0.11817 | 0.020645 | 122.3308 | 122.2954 | 122.3457 | 61.1037 | -122.2803 | 122.1952 | 122.364 | 122.2664 | 61.1347 | -122.5035
1006.5312 | 122.4472 | -61.1664 | 61.1618 | 1.4211e-13 | -0.0010533 | -0.0095086 | 0.039384 | -0.022935 | 0.048226 | 0.0036627 | -0.012361 | 0.028194 | 0.044157 | 0.0013439 | 0.045937 | -60.9922 | -0.026065 | -61.1559 | 61.224 | 61.1748 | 61.2297 | -61.1734 | -61.0698 | 0.004938 | -61.118 | 61.0701 | 61.2296 | 61.1458 | -61.3784 | -0.007002 | 0.062164 | 0.17415 | 0.010458 | 0.01746 | 0.012987 | 0.067877 | -0.21197 | -0.09174 | 0.096598 | 0.048356 | 0.26033 | 0.067818 | -0.015974 | 122.3903 | 122.3412 | 122.3961 | 61.1403 | -122.3352 | 122.2364 | 122.396 | 122.3122 | 61.1713 | -122.5402
1008.3281 | 122.4426 | -61.1435 | 61.2122 | 1.4211e-13 | -0.0012671 | -0.0095086 | 0.039384 | -0.023148 | 0.048012 | 0.0036627 | -0.012361 | 0.028835 | 0.043943 | 0.0017713 | 0.046792 | -60.9877 | -0.021486 | -61.1513 | 61.2148 | 61.1748 | 61.2251 | -61.1688 | -61.0698 | 0.004938 | -61.1089 | 61.0746 | 61.2296 | 61.1504 | -61.3784 | -0.025311 | 0.002653 | 0.15584 | -0.007852 | 0.017459 | -0.037367 | 0.012944 | -0.23486 | -0.13752 | 0.07371 | 0.034626 | 0.26949 | 0.017464 | -0.061749 | 122.3583 | 122.3183 | 122.3686 | 61.122 | -122.381 | 122.2181 | 122.3731 | 122.2939 | 61.1484 | -122.5905
1010.0469 | 122.5754 | -61.0519 | 61.203 | 1.4211e-13 | -0.0012671 | -0.0095086 | 0.038957 | -0.022935 | 0.047799 | -0.0039678 | -0.012361 | 0.028408 | 0.043943 | 0.0021987 | 0.046365 | -60.9877 | -0.021486 | -61.1468 | 61.224 | 61.1794 | 61.2251 | -61.1642 | -61.0652 | 0.000359 | -61.1089 | 61.0792 | 61.2342 | 61.155 | -61.3738 | -0.11228 | 0.020965 | 0.064284 | -0.094827 | 0.017458 | -0.023633 | 0.022099 | -0.32184 | -0.12378 | -0.013265 | -0.056927 | 0.26491 | 0.031198 | -0.048016 | 122.2759 | 122.2313 | 122.277 | 61.0305 | -122.3672 | 122.1312 | 122.2861 | 122.2069 | 61.0523 | -122.5768
1011.8125 | 122.438 | -61.0931 | 61.2534 | 1.4211e-13 | -0.0012671 | -0.009295 | 0.03917 | -0.022935 | 0.047799 | 0.011293 | -0.011934 | 0.028408 | 0.043943 | 0.0015577 | 0.045937 | -60.9785 | -0.026065 | -61.1376 | 61.2194 | 61.1794 | 61.2297 | -61.1551 | -61.056 | 0.004938 | -61.1043 | 61.0746 | 61.2525 | 61.1504 | -61.3738 | -0.061929 | -0.033967 | 0.11464 | -0.044471 | 0.017458 | -0.073987 | -0.023676 | -0.28064 | -0.17872 | 0.037092 | -0.01115 | 0.26949 | -0.000842 | -0.10295 | 122.3125 | 122.2725 | 122.3228 | 61.0671 | -122.4084 | 122.1678 | 122.3457 | 122.2435 | 61.0981 | -122.6271
1013.5312 | 122.4884 | -61.0977 | 61.235 | 1.4211e-13 | -0.0014807 | -0.009936 | 0.03917 | -0.022721 | 0.047799 | 0.0036627 | -0.011934 | 0.028622 | 0.043943 | 0.0015577 | 0.046365 | -60.9785 | -0.026065 | -61.1285 | 61.2285 | 61.1839 | 61.2343 | -61.1596 | -61.056 | 0.000359 | -61.1043 | 61.0746 | 61.2434 | 61.155 | -61.3646 | -0.06193 | -0.0065 | 0.11922 | -0.030738 | 0.031192 | -0.051097 | -0.000787 | -0.2669 | -0.1604 | 0.041669 | -0.006573 | 0.26033 | 0.008312 | -0.080059 | 122.3263 | 122.2817 | 122.332 | 61.0717 | -122.3947 | 122.1724 | 122.3411 | 122.2527 | 61.0981 | -122.5997
1015.25 | 122.4426 | -61.0748 | 61.2717 | 1.4211e-13 | -0.0010533 | -0.0097224 | 0.039384 | -0.022935 | 0.048012 | 0.011293 | -0.011934 | 0.028622 | 0.044157 | 0.0017713 | 0.046151 | -60.9785 | -0.030644 | -61.133 | 61.224 | 61.1794 | 61.2434 | -61.1551 | -61.056 | 0.000359 | -61.0997 | 61.0884 | 61.2434 | 61.155 | -61.3692 | -0.08024 | -0.047699 | 0.096329 | -0.058204 | 0.022036 | -0.092297 | -0.02825 | -0.29437 | -0.18329 | 0.018781 | -0.024882 | 0.26949 | -0.028309 | -0.11668 | 122.2988 | 122.2542 | 122.3182 | 61.0442 | -122.4267 | 122.1632 | 122.3182 | 122.2298 | 61.0752 | -122.6409
1017.0312 | 122.4426 | -61.116 | 61.1938 | 1.4211e-13 | -0.0010533 | -0.0095086 | 0.038743 | -0.023148 | 0.047799 | 0.0036627 | -0.011934 | 0.028408 | 0.043729 | 0.0015577 | 0.046151 | -60.9739 | -0.030644 | -61.1239 | 61.2423 | 61.1931 | 61.2388 | -61.1505 | -61.0423 | -0.00422 | -61.0951 | 61.0884 | 61.2525 | 61.1641 | -61.3646 | -0.034462 | 0.048433 | 0.14211 | -0.007848 | 0.026614 | -0.000741 | 0.04499 | -0.24859 | -0.10547 | 0.073716 | 0.020896 | 0.26949 | 0.058667 | -0.029704 | 122.3583 | 122.3091 | 122.3549 | 61.0854 | -122.3443 | 122.2044 | 122.3685 | 122.2802 | 61.1118 | -122.5585
1018.8125 | 122.4884 | -61.0931 | 61.235 | 1.4211e-13 | -0.0010533 | -0.0097224 | 0.039384 | -0.022721 | 0.047371 | 0.018923 | -0.012361 | 0.028194 | 0.043729 | 0.0017713 | 0.046151 | -60.9648 | -0.030644 | -61.1239 | 61.2331 | 61.1885 | 61.2434 | -61.1505 | -61.0469 | 0.004938 | -61.0951 | 61.093 | 61.2571 | 61.1687 | -61.36 | -0.05735 | -0.001921 | 0.12837 | -0.030736 | 0.026614 | -0.046518 | 0.008371 | -0.2669 | -0.14209 | 0.046249 | -0.001992 | 0.26491 | 0.022048 | -0.066323 | 122.3263 | 122.2817 | 122.3366 | 61.0625 | -122.3855 | 122.1861 | 122.3502 | 122.2619 | 61.0981 | -122.5951
1020.5469 | 122.438 | -61.0565 | 61.3037 | 1.4211e-13 | -0.00083973 | -0.0095086 | 0.039384 | -0.023148 | 0.048012 | 0.011293 | -0.011934 | 0.028835 | 0.043943 | 0.0019849 | 0.046365 | -60.9693 | -0.030644 | -61.1193 | 61.2377 | 61.1885 | 61.248 | -61.1459 | -61.0332 | -0.00422 | -61.0906 | 61.0975 | 61.2525 | 61.1733 | -61.3509 | -0.089392 | -0.066008 | 0.087175 | -0.062779 | 0.026613 | -0.11518 | -0.055716 | -0.29436 | -0.20618 | 0.023364 | -0.034034 | 0.26033 | -0.051196 | -0.13041 | 122.2942 | 122.245 | 122.3045 | 61.0259 | -122.4496 | 122.1541 | 122.309 | 122.2298 | 61.0523 | -122.6546
1022.2812 | 122.4609 | -61.0657 | 61.2762 | 1.4211e-13 | -0.0014807 | -0.0097224 | 0.038957 | -0.022721 | 0.047799 | 0.0036627 | -0.011934 | 0.028194 | 0.043729 | 0.0013439 | 0.046151 | -60.9556 | -0.030644 | -61.1239 | 61.2423 | 61.1977 | 61.248 | -61.1322 | -61.0377 | 0.004938 | -61.086 | 61.093 | 61.2571 | 61.1687 | -61.3509 | -0.0665 | -0.033964 | 0.11007 | -0.058202 | 0.008298 | -0.07856 | -0.02825 | -0.28521 | -0.18329 | 0.027941 | -0.020301 | 0.26491 | -0.019151 | -0.10752 | 122.308 | 122.2634 | 122.3137 | 61.035 | -122.4084 | 122.1586 | 122.3228 | 122.2344 | 61.0706 | -122.6271
1024.0625 | 122.525 | -61.084 | 61.1847 | 1.4211e-13 | -0.0010533 | -0.0097224 | 0.03917 | -0.022721 | 0.048012 | 0.011293 | -0.011934 | 0.028408 | 0.043943 | 0.0017713 | 0.046151 | -60.9602 | -0.026065 | -61.1147 | 61.2377 | 61.2023 | 61.248 | -61.1368 | -61.0377 | 0.004938 | -61.0814 | 61.0884 | 61.2571 | 61.1687 | -61.3417 | -0.052769 | 0.053011 | 0.1238 | -0.030736 | 0.022033 | 0.017572 | 0.063303 | -0.25774 | -0.096314 | 0.046251 | 0.002588 | 0.26033 | 0.072402 | -0.015969 | 122.3217 | 122.2862 | 122.332 | 61.0579 | -122.3214 | 122.1724 | 122.3411 | 122.2527 | 61.0889 | -122.5264
1025.8438 | 122.5845 | -61.0107 | 61.235 | 1.4211e-13 | -0.0010533 | -0.0097224 | 0.03917 | -0.023148 | 0.048226 | 0.011293 | -0.011934 | 0.028408 | 0.043943 | 0.0017713 | 0.045937 | -60.9465 | -0.030644 | -61.1101 | 61.2469 | 61.2068 | 61.2617 | -61.1322 | -61.0286 | 0.000359 | -61.0814 | 61.1021 | 61.2617 | 61.1825 | -61.3463 | -0.12143 | 0.011814 | 0.06429 | -0.099399 | 0.022033 | -0.028203 | 0.026685 | -0.33556 | -0.13293 | -0.017834 | -0.070654 | 0.26491 | 0.026626 | -0.052587 | 122.2576 | 122.2176 | 122.2725 | 60.9801 | -122.3672 | 122.1129 | 122.2724 | 122.1932 | 61.0111 | -122.5814
1027.6406 | 122.438 | -61.0291 | 61.2717 | 1.4211e-13 | -0.0010533 | -0.0097224 | 0.038957 | -0.022507 | 0.048012 | 0.0036627 | -0.012148 | 0.028408 | 0.043516 | 0.0015577 | 0.045937 | -60.9465 | -0.030644 | -61.101 | 61.2514 | 61.2114 | 61.2526 | -61.1276 | -61.024 | -0.00422 | -61.0722 | 61.0975 | 61.2708 | 61.187 | -61.3417 | -0.098542 | -0.020229 | 0.082601 | -0.071932 | 0.02661 | -0.060245 | -0.019093 | -0.31267 | -0.17413 | 0.005056 | -0.043186 | 0.26949 | -0.000837 | -0.084629 | 122.2805 | 122.2405 | 122.2816 | 60.9984 | -122.3993 | 122.1266 | 122.2999 | 122.2161 | 61.0248 | -122.6134
1029.3438 | 122.5754 | -61.0199 | 61.2625 | 1.4211e-13 | -0.0014807 | -0.0095086 | 0.038957 | -0.022935 | 0.047799 | 0.011293 | -0.012361 | 0.028194 | 0.043516 | 0.0019849 | 0.046151 | -60.9373 | -0.026065 | -61.101 | 61.2423 | 61.2023 | 61.2572 | -61.123 | -61.0148 | 0.000359 | -61.0677 | 61.1113 | 61.28 | 61.1779 | -61.3417 | -0.10312 | -0.020231 | 0.082602 | -0.081088 | 0.022031 | -0.060248 | -0.00536 | -0.32183 | -0.15124 | 0.005057 | -0.047763 | 0.27407 | 0.017475 | -0.084632 | 122.2622 | 122.2222 | 122.277 | 60.9938 | -122.3855 | 122.1312 | 122.2999 | 122.1978 | 61.0203 | -122.6042
1031.125 | 122.4426 | -61.1114 | 61.2076 | 1.4211e-13 | -0.0010533 | -0.01015 | 0.039384 | -0.023148 | 0.047585 | 0.011293 | -0.011934 | 0.028622 | 0.043943 | 0.0013439 | 0.046151 | -60.9419 | -0.026065 | -61.1056 | 61.2606 | 61.2068 | 61.2755 | -61.1184 | -61.0194 | 0.004938 | -61.0677 | 61.1113 | 61.2754 | 61.1916 | -61.3326 | -0.006987 | 0.053014 | 0.16958 | 0.005887 | 0.012874 | -0.000738 | 0.067886 | -0.22112 | -0.096311 | 0.092031 | 0.04379 | 0.26491 | 0.067827 | -0.015965 | 122.372 | 122.3183 | 122.3869 | 61.0854 | -122.326 | 122.2227 | 122.3869 | 122.3031 | 61.1164 | -122.5401
1032.8438 | 122.5571 | -60.9741 | 61.2671 | 1.4211e-13 | -0.0012671 | -0.0097224 | 0.03917 | -0.023148 | 0.047799 | 0.011293 | -0.011934 | 0.028408 | 0.043729 | 0.0017713 | 0.045937 | -60.9419 | -0.035222 | -61.0964 | 61.2606 | 61.2068 | 61.2663 | -61.1139 | -61.0148 | -0.00422 | -61.0677 | 61.1113 | 61.28 | 61.1962 | -61.3326 | -0.13974 | -0.006495 | 0.032248 | -0.12229 | 0.017451 | -0.060247 | -0.00078 | -0.35845 | -0.15582 | -0.040719 | -0.093539 | 0.26491 | 0.012897 | -0.070895 | 122.2347 | 122.181 | 122.2404 | 60.9389 | -122.3809 | 122.0854 | 122.2541 | 122.1703 | 60.9699 | -122.5997
1034.625 | 122.4701 | -61.0703 | 61.2488 | 1.4211e-13 | -0.00062613 | -0.009936 | 0.039598 | -0.023362 | 0.047799 | 0.0036627 | -0.012148 | 0.028622 | 0.044157 | 0.0015577 | 0.045937 | -60.9373 | -0.021486 | -61.0964 | 61.256 | 61.216 | 61.2663 | -61.1184 | -61.0148 | -0.00422 | -61.0585 | 61.1158 | 61.2846 | 61.2008 | -61.3234 | -0.048186 | 0.007238 | 0.13296 | -0.026156 | 0.02203 | -0.032778 | 0.017531 | -0.25316 | -0.13293 | 0.055411 | 0.011749 | 0.26491 | 0.035786 | -0.048006 | 122.3263 | 122.2863 | 122.3366 | 61.0488 | -122.3672 | 122.1861 | 122.3548 | 122.271 | 61.066 | -122.5722
1036.3438 | 122.4701 | -61.0611 | 61.2762 | 1.4211e-13 | -0.0010533 | -0.0095086 | 0.038957 | -0.023148 | 0.047799 | 0.011293 | -0.012361 | 0.028194 | 0.044157 | 0.0017713 | 0.046151 | -60.9327 | -0.030644 | -61.0964 | 61.2698 | 61.2252 | 61.2755 | -61.1139 | -61.0057 | -0.00422 | -61.0493 | 61.125 | 61.2846 | 61.187 | -61.3188 | -0.052762 | -0.006493 | 0.12838 | -0.035311 | 0.017451 | -0.051086 | -0.000778 | -0.25774 | -0.15124 | 0.055414 | 0.011751 | 0.26949 | 0.00832 | -0.089207 | 122.3308 | 122.2863 | 122.3366 | 61.0305 | -122.3901 | 122.1861 | 122.3457 | 122.2481 | 61.0569 | -122.5951
1038.125 | 122.4976 | -61.0153 | 61.2671 | 1.4211e-13 | -0.00083973 | -0.0097224 | 0.038957 | -0.023148 | 0.048012 | -0.0039678 | -0.011934 | 0.028194 | 0.043943 | 0.0019849 | 0.046151 | -60.919 | -0.026065 | -61.0918 | 61.2652 | 61.2252 | 61.2846 | -61.1093 | -61.0057 | 0.000359 | -61.0448 | 61.1296 | 61.2891 | 61.2008 | -61.3051 | -0.093959 | -0.001917 | 0.096339 | -0.076508 | 0.017451 | -0.041931 | 0.017534 | -0.28977 | -0.13751 | 0.009638 | -0.029446 | 0.26033 | 0.022054 | -0.066317 | 122.2805 | 122.2405 | 122.2999 | 60.9893 | -122.3764 | 122.1449 | 122.3045 | 122.2161 | 61.0157 | -122.5722
1039.9062 | 122.5571 | -61.0657 | 61.1664 | 1.4211e-13 | -0.0010533 | -0.0095086 | 0.038957 | -0.022935 | 0.047585 | -0.0039678 | -0.012148 | 0.028622 | 0.043943 | 0.0019849 | 0.045937 | -60.9236 | -0.016908 | -61.0872 | 61.2698 | 61.2343 | 61.2846 | -61.0955 | -60.9965 | 0.004938 | -61.0448 | 61.1296 | 61.2891 | 61.2008 | -61.3143 | -0.029868 | 0.10337 | 0.14211 | -0.021576 | 0.008292 | 0.067935 | 0.11824 | -0.24858 | -0.036798 | 0.069149 | 0.020908 | 0.26949 | 0.12276 | 0.034391 | 122.3354 | 122.3 | 122.3503 | 61.0488 | -122.2619 | 122.1953 | 122.3548 | 122.2664 | 61.0706 | -122.4806
1041.6875 | 122.5525 | -61.0336 | 61.1893 | 1.4211e-13 | -0.0012671 | -0.0095086 | 0.038957 | -0.023362 | 0.048012 | 0.011293 | -0.011934 | 0.028408 | 0.044157 | 0.0015577 | 0.046151 | -60.9098 | -0.026065 | -61.0689 | 61.2789 | 61.2343 | 61.2846 | -61.0864 | -60.9965 | 0.000359 | -61.0356 | 61.1296 | 61.2891 | 61.2099 | -61.3005 | -0.052755 | 0.089639 | 0.12381 | -0.035307 | 0.017448 | 0.045047 | 0.095354 | -0.26689 | -0.059686 | 0.037105 | -0.001979 | 0.26491 | 0.099874 | 0.020661 | 122.3125 | 122.2679 | 122.3183 | 61.0076 | -122.2757 | 122.1632 | 122.3228 | 122.2436 | 61.034 | -122.4898
1043.4688 | 122.4243 | -61.1023 | 61.2305 | 1.4211e-13 | -0.0012671 | -0.009295 | 0.039384 | -0.022721 | 0.048012 | -0.011598 | -0.012148 | 0.028194 | 0.044157 | 0.0013439 | 0.046151 | -60.9144 | -0.026065 | -61.0689 | 61.2789 | 61.2435 | 61.2938 | -61.091 | -60.9874 | 0.000359 | -61.031 | 61.1387 | 61.2937 | 61.2099 | -61.3005 | 0.011331 | 0.04844 | 0.18789 | 0.033358 | 0.022027 | 0.013006 | 0.063312 | -0.19822 | -0.091728 | 0.11493 | 0.071265 | 0.26949 | 0.063254 | -0.020538 | 122.3812 | 122.3458 | 122.3961 | 61.0762 | -122.3214 | 122.241 | 122.396 | 122.3122 | 61.1027 | -122.531
1045.1875 | 122.4518 | -61.0474 | 61.2625 | 1.4211e-13 | -0.0014807 | -0.0095086 | 0.039384 | -0.022935 | 0.047799 | 0.011293 | -0.012148 | 0.028408 | 0.043943 | 0.0017713 | 0.045724 | -60.9098 | -0.021486 | -61.0689 | 61.2881 | 61.2481 | 61.2938 | -61.091 | -60.9919 | 0.000359 | -61.0356 | 61.1342 | 61.3075 | 61.2145 | -61.3005 | -0.043601 | 0.025553 | 0.13754 | -0.021574 | 0.022027 | -0.014458 | 0.031269 | -0.25315 | -0.12835 | 0.055417 | 0.011754 | 0.26491 | 0.044946 | -0.048003 | 122.3354 | 122.2954 | 122.3411 | 61.0259 | -122.3535 | 122.1815 | 122.3548 | 122.2619 | 61.0477 | -122.563
1046.9688 | 122.5067 | -61.0382 | 61.235 | 1.4211e-13 | -0.0012671 | -0.0097224 | 0.03917 | -0.023148 | 0.047799 | 0.0036627 | -0.011934 | 0.028622 | 0.043729 | 0.0017713 | 0.045937 | -60.9007 | -0.026065 | -61.0644 | 61.2881 | 61.2435 | 61.2938 | -61.0818 | -60.9736 | 0.004938 | -61.031 | 61.1387 | 61.312 | 61.2145 | -61.3005 | -0.043598 | 0.053019 | 0.13754 | -0.026151 | 0.017447 | 0.008429 | 0.058735 | -0.26231 | -0.096305 | 0.064576 | 0.007178 | 0.26949 | 0.076991 | -0.020537 | 122.3263 | 122.2817 | 122.332 | 61.0121 | -122.3169 | 122.1769 | 122.3502 | 122.2527 | 61.0431 | -122.5356
1048.75 | 122.4152 | -60.9695 | 61.3495 | 1.4211e-13 | -0.0012671 | -0.0097224 | 0.03917 | -0.023148 | 0.048012 | 0.011293 | -0.012148 | 0.028408 | 0.044157 | 0.0013439 | 0.046151 | -60.9007 | -0.030644 | -61.0598 | 61.2881 | 61.2435 | 61.2984 | -61.0772 | -60.9782 | 0.000359 | -61.031 | 61.1433 | 61.3075 | 61.2145 | -61.2868 | -0.10768 | -0.061422 | 0.068875 | -0.090237 | 0.017447 | -0.10601 | -0.051127 | -0.31724 | -0.20617 | -0.008667 | -0.061487 | 0.25575 | -0.042029 | -0.13498 | 122.2576 | 122.213 | 122.2679 | 60.9389 | -122.4267 | 122.1129 | 122.277 | 122.1841 | 60.9699 | -122.6363
1050.5312 | 122.5525 | -60.9695 | 61.2991 | 1.4211e-13 | -0.0014807 | -0.0097224 | 0.038743 | -0.022935 | 0.047585 | -0.0039678 | -0.011934 | 0.028194 | 0.043302 | 0.0017713 | 0.045724 | -60.8915 | -0.026065 | -61.0506 | 61.2926 | 61.2572 | 61.3029 | -61.0818 | -60.9736 | 0.000359 | -61.0219 | 61.1433 | 61.3075 | 61.2282 | -61.2822 | -0.11226 | -0.006489 | 0.078032 | -0.081081 | 0.031182 | -0.041921 | 0.003805 | -0.31266 | -0.15581 | -0.004089 | -0.05233 | 0.26033 | 0.008325 | -0.070888 | 122.2622 | 122.2268 | 122.2725 | 60.9435 | -122.3809 | 122.1129 | 122.277 | 122.1978 | 60.9699 | -122.5813
1052.3125 | 122.5067 | -60.9833 | 61.2671 | 1.4211e-13 | -0.00083973 | -0.0097224 | 0.038957 | -0.023148 | 0.047799 | 0.011293 | -0.011934 | 0.028194 | 0.043729 | 0.0017713 | 0.046151 | -60.8961 | -0.026065 | -61.046 | 61.3018 | 61.2572 | 61.3029 | -61.0726 | -60.9691 | 0.000359 | -61.0081 | 61.1571 | 61.312 | 61.2237 | -61.2776 | -0.089372 | 0.03471 | 0.087187 | -0.06277 | 0.026602 | -0.009878 | 0.035848 | -0.29435 | -0.11004 | 0.014223 | -0.024861 | 0.26949 | 0.044947 | -0.043424 | 122.2851 | 122.2405 | 122.2862 | 60.9572 | -122.3397 | 122.1403 | 122.2953 | 122.2069 | 60.9836 | -122.5447
1054.0312 | 122.5845 | -60.965 | 61.2854 | 1.4211e-13 | -0.0010533 | -0.01015 | 0.03917 | -0.022935 | 0.048012 | 0.0036627 | -0.012148 | 0.027981 | 0.043729 | 0.0013439 | 0.046151 | -60.8869 | -0.030644 | -61.0415 | 61.2972 | 61.2572 | 61.3121 | -61.0635 | -60.9645 | 0.000359 | -61.0127 | 61.1525 | 61.312 | 61.2328 | -61.2776 | -0.098524 | 0.011822 | 0.078033 | -0.076501 | 0.022023 | -0.028188 | 0.026696 | -0.31266 | -0.13292 | 0.000492 | -0.047749 | 0.26491 | 0.026637 | -0.052576 | 122.2622 | 122.2222 | 122.2771 | 60.9343 | -122.3489 | 122.1174 | 122.277 | 122.1978 | 60.9653 | -122.563
1055.7344 | 122.4976 | -60.9833 | 61.2534 | 1.4211e-13 | -0.00083973 | -0.009936 | 0.039384 | -0.022935 | 0.047585 | 0.011293 | -0.012148 | 0.028408 | 0.043729 | 0.0017713 | 0.046365 | -60.8778 | -0.030644 | -61.0323 | 61.311 | 61.2572 | 61.3121 | -61.0681 | -60.9599 | 0.000359 | -61.0081 | 61.1571 | 61.3166 | 61.2374 | -61.2685 | -0.084793 | 0.0576 | 0.1055 | -0.049035 | 0.035758 | 0.003855 | 0.058739 | -0.28519 | -0.096302 | 0.023381 | -0.024861 | 0.26033 | 0.063259 | -0.015955 | 122.2942 | 122.2405 | 122.2954 | 60.9526 | -122.3214 | 122.1403 | 122.2999 | 122.2207 | 60.9836 | -122.5218
1057.5 | 122.5433 | -60.9467 | 61.2854 | 1.4211e-13 | -0.0010533 | -0.0095086 | 0.03917 | -0.023362 | 0.047799 | -0.0039678 | -0.01172 | 0.028408 | 0.043943 | 0.0017713 | 0.046151 | -60.8778 | -0.030644 | -61.0369 | 61.311 | 61.2664 | 61.3167 | -61.0543 | -60.9553 | 0.000359 | -60.999 | 61.1662 | 61.3166 | 61.242 | -61.273 | -0.10768 | 0.025557 | 0.068879 | -0.090234 | 0.017443 | -0.019031 | 0.031274 | -0.32639 | -0.11919 | -0.008662 | -0.052324 | 0.27406 | 0.031216 | -0.043419 | 122.2576 | 122.213 | 122.2633 | 60.916 | -122.3397 | 122.1129 | 122.2633 | 122.1886 | 60.947 | -122.5584
1059.2188 | 122.406 | -61.0519 | 61.2854 | 1.4211e-13 | -0.0014807 | -0.0095086 | 0.03917 | -0.023148 | 0.047799 | 0.011293 | -0.011934 | 0.028622 | 0.044157 | 0.0017713 | 0.045937 | -60.8732 | -0.026065 | -61.0323 | 61.3064 | 61.2755 | 61.3213 | -61.0589 | -60.9507 | 0.000359 | -60.9944 | 61.1708 | 61.3212 | 61.2374 | -61.2639 | -0.00697 | 0.020979 | 0.17874 | 0.01963 | 0.0266 | -0.009873 | 0.035853 | -0.21194 | -0.11461 | 0.1012 | 0.05754 | 0.26948 | 0.035794 | -0.047998 | 122.3583 | 122.3275 | 122.3732 | 61.0259 | -122.3443 | 122.2227 | 122.3731 | 122.2893 | 61.0523 | -122.5493
1061 | 122.525 | -60.9833 | 61.2625 | 1.4211e-13 | -0.0010533 | -0.0095086 | 0.03917 | -0.022935 | 0.047799 | 0.011293 | -0.012148 | 0.028194 | 0.043729 | 0.0015577 | 0.046151 | -60.864 | -0.026065 | -61.0323 | 61.3201 | 61.2755 | 61.3213 | -61.0498 | -60.9416 | 0.009516 | -60.9852 | 61.1708 | 61.3304 | 61.2511 | -61.2593 | -0.066477 | 0.057602 | 0.11923 | -0.049035 | 0.017442 | 0.013015 | 0.058741 | -0.27603 | -0.091721 | 0.041695 | -0.001967 | 0.27406 | 0.067839 | -0.011374 | 122.3034 | 122.2588 | 122.3045 | 60.9572 | -122.3123 | 122.1541 | 122.3136 | 122.2344 | 60.9928 | -122.5218
1062.7656 | 122.5616 | -60.9604 | 61.2946 | 1.4211e-13 | -0.0012671 | -0.0097224 | 0.039598 | -0.023148 | 0.047799 | 0.0036627 | -0.01172 | 0.028408 | 0.043943 | 0.0017713 | 0.046151 | -60.864 | -0.030644 | -61.0277 | 61.3247 | 61.2755 | 61.335 | -61.036 | -60.9416 | 0.009516 | -60.9852 | 61.1754 | 61.3349 | 61.2511 | -61.2547 | -0.075628 | 0.030136 | 0.096347 | -0.067344 | 0.008284 | -0.019029 | 0.040433 | -0.29434 | -0.11919 | 0.018807 | -0.024855 | 0.26949 | 0.040374 | -0.043418 | 122.2851 | 122.2359 | 122.2954 | 60.9297 | -122.3306 | 122.1358 | 122.2953 | 122.2115 | 60.9699 | -122.5493
1064.4688 | 122.4152 | -60.9604 | 61.3678 | 1.4211e-13 | -0.0010533 | -0.0097224 | 0.039384 | -0.023148 | 0.047799 | 0.0036627 | -0.012148 | 0.028408 | 0.044157 | 0.0017713 | 0.046365 | -60.8595 | -0.030644 | -61.0232 | 61.3247 | 61.2801 | 61.335 | -61.0406 | -60.9324 | 0.000359 | -60.9807 | 61.1754 | 61.3441 | 61.2511 | -61.2547 | -0.080207 | -0.043106 | 0.10093 | -0.062766 | 0.017441 | -0.087692 | -0.032809 | -0.29434 | -0.19243 | 0.027965 | -0.020276 | 0.27406 | -0.023711 | -0.11666 | 122.2851 | 122.2405 | 122.2954 | 60.9297 | -122.4084 | 122.1358 | 122.3045 | 122.2115 | 60.9607 | -122.6225
1066.1875 | 122.406 | -60.9467 | 61.3724 | 1.4211e-13 | -0.0010533 | -0.0097224 | 0.038743 | -0.023148 | 0.048226 | 0.011293 | -0.012148 | 0.028408 | 0.043729 | 0.0019849 | 0.046151 | -60.8503 | -0.026065 | -61.0094 | 61.3338 | 61.2847 | 61.3396 | -61.036 | -60.9278 | 0.000359 | -60.9807 | 61.1799 | 61.3441 | 61.2603 | -61.2456 | -0.089361 | -0.038526 | 0.096349 | -0.062764 | 0.026597 | -0.08769 | -0.032808 | -0.29892 | -0.19243 | 0.018811 | -0.034009 | 0.26491 | -0.028288 | -0.11208 | 122.2805 | 122.2313 | 122.2862 | 60.9206 | -122.4084 | 122.1266 | 122.2907 | 122.207 | 60.947 | -122.6179
1067.8906 | 122.4518 | -60.9879 | 61.3266 | 1.4211e-13 | -0.0010533 | -0.009295 | 0.03917 | -0.023148 | 0.048226 | 0.0036627 | -0.012148 | 0.028622 | 0.044157 | 0.0019849 | 0.046151 | -60.8503 | -0.026065 | -61.0048 | 61.3338 | 61.2938 | 61.3441 | -61.0269 | -60.9324 | 0.000359 | -60.9715 | 61.1891 | 61.3487 | 61.2649 | -61.2456 | -0.039005 | 0.00725 | 0.13755 | -0.016987 | 0.022018 | -0.032756 | 0.017547 | -0.25772 | -0.13749 | 0.055431 | 0.016347 | 0.27406 | 0.022067 | -0.061725 | 122.3217 | 122.2817 | 122.332 | 60.9618 | -122.3535 | 122.177 | 122.3365 | 122.2527 | 60.9882 | -122.5722
1069.6094 | 122.4518 | -61.0291 | 61.2854 | 1.4211e-13 | -0.0012671 | -0.0097224 | 0.03917 | -0.023148 | 0.048012 | 0.011293 | -0.012361 | 0.028408 | 0.043729 | 0.0013439 | 0.045937 | -60.8457 | -0.026065 | -61.0048 | 61.3338 | 61.2893 | 61.3487 | -61.0223 | -60.9233 | 0.004938 | -60.9624 | 61.1845 | 61.3578 | 61.2695 | -61.2318 | 0.006773 | 0.048449 | 0.18333 | 0.024212 | 0.017439 | 0.003864 | 0.063324 | -0.20278 | -0.10087 | 0.10579 | 0.066703 | 0.26948 | 0.072423 | -0.015948 | 122.3629 | 122.3183 | 122.3778 | 61.003 | -122.3077 | 122.2136 | 122.3869 | 122.2985 | 61.034 | -122.5172
1071.3438 | 122.5525 | -60.9009 | 61.3129 | 1.4211e-13 | -0.00083973 | -0.009936 | 0.038957 | -0.022935 | 0.047799 | 0.011293 | -0.011934 | 0.028194 | 0.043943 | 0.0015577 | 0.045937 | -60.832 | -0.026065 | -61.0003 | 61.3384 | 61.303 | 61.3533 | -61.0131 | -60.9141 | 0.009516 | -60.9624 | 61.2074 | 61.3578 | 61.274 | -61.2318 | -0.11224 | 0.025562 | 0.068887 | -0.099384 | 0.012859 | -0.009865 | 0.040437 | -0.33095 | -0.10545 | -0.013229 | -0.061471 | 0.26948 | 0.044957 | -0.038835 | 122.2393 | 122.2039 | 122.2542 | 60.8748 | -122.326 | 122.1083 | 122.2587 | 122.1749 | 60.9104 | -122.5447
1073.1406 | 122.406 | -60.9375 | 61.3678 | 1.4211e-13 | -0.0010533 | -0.0097224 | 0.03917 | -0.023148 | 0.047585 | -0.0039678 | -0.011934 | 0.028408 | 0.043729 | 0.0021987 | 0.045937 | -60.8183 | -0.030644 | -60.9911 | 61.3476 | 61.3122 | 61.3625 | -60.9994 | -60.9095 | 0.000359 | -60.9532 | 61.212 | 61.3716 | 61.2832 | -61.2181 | -0.061885 | -0.020214 | 0.11924 | -0.053606 | 0.008279 | -0.055639 | -0.005338 | -0.2806 | -0.1558 | 0.02797 | -0.015692 | 0.2649 | 0.003761 | -0.08461 | 122.2851 | 122.2497 | 122.3 | 60.9069 | -122.3672 | 122.1495 | 122.3091 | 122.2207 | 60.9379 | -122.5859
1074.9219 | 122.4609 | -60.9833 | 61.2762 | 1.4211e-13 | -0.00083973 | -0.0095086 | 0.039598 | -0.023148 | 0.047799 | 0.0036627 | -0.011934 | 0.028408 | 0.043516 | 0.0015577 | 0.046151 | -60.8183 | -0.026065 | -60.9774 | 61.3567 | 61.3122 | 61.367 | -60.9994 | -60.8958 | 0.000359 | -60.9395 | 61.212 | 61.3853 | 61.2923 | -61.2044 | -0.016109 | 0.080496 | 0.16502 | 0.005905 | 0.022014 | 0.035914 | 0.090794 | -0.22109 | -0.064248 | 0.087483 | 0.04382 | 0.2649 | 0.10905 | 0.0161 | 122.34 | 122.2954 | 122.3503 | 60.9572 | -122.2756 | 122.1953 | 122.3686 | 122.2756 | 60.9836 | -122.4806
1076.6875 | 122.5433 | -60.9604 | 61.2534 | 1.4211e-13 | -0.0012671 | -0.009936 | 0.03917 | -0.023148 | 0.047371 | 0.018923 | -0.012148 | 0.028835 | 0.043729 | 0.0015577 | 0.045724 | -60.8045 | -0.026065 | -60.9728 | 61.3659 | 61.3259 | 61.3762 | -60.9994 | -60.8912 | 0.000359 | -60.9349 | 61.2212 | 61.3853 | 61.2923 | -61.2044 | -0.038997 | 0.11254 | 0.15587 | -0.012405 | 0.026592 | 0.072538 | 0.12284 | -0.24397 | -0.032203 | 0.069173 | 0.025511 | 0.26948 | 0.13194 | 0.038988 | 122.3263 | 122.2863 | 122.3366 | 60.9343 | -122.2527 | 122.1815 | 122.3457 | 122.2527 | 60.9607 | -122.4577
1078.4219 | 122.4884 | -60.9604 | 61.2991 | 1.4211e-13 | -0.00083973 | -0.009936 | 0.038743 | -0.023362 | 0.047585 | 0.0036627 | -0.012148 | 0.028622 | 0.043943 | 0.0017713 | 0.046151 | -60.7999 | -0.026065 | -60.9636 | 61.3705 | 61.3305 | 61.3854 | -60.9811 | -60.8912 | 0.009516 | -60.9303 | 61.2257 | 61.3853 | 61.3015 | -61.1998 | -0.020681 | 0.071343 | 0.16045 | -0.003248 | 0.017433 | 0.031341 | 0.08622 | -0.23939 | -0.0734 | 0.069173 | 0.030089 | 0.26948 | 0.086162 | 0.00237 | 122.3309 | 122.2909 | 122.3457 | 60.9343 | -122.2802 | 122.1861 | 122.3457 | 122.2619 | 60.9699 | -122.4989
1080.1406 | 122.493 | -60.9238 | 61.3403 | 1.4211e-13 | -0.0010533 | -0.009295 | 0.038957 | -0.023362 | 0.047799 | 0.011293 | -0.012361 | 0.028408 | 0.043729 | 0.0017713 | 0.045937 | -60.7954 | -0.021486 | -60.9591 | 61.3796 | 61.3351 | 61.3899 | -60.9811 | -60.8775 | 0.009516 | -60.9257 | 61.2303 | 61.3899 | 61.3061 | -61.1952 | -0.057302 | 0.039301 | 0.1284 | -0.035291 | 0.022011 | -0.005279 | 0.0496 | -0.27144 | -0.11002 | 0.046288 | -0.001953 | 0.26948 | 0.049541 | -0.034251 | 122.3034 | 122.2588 | 122.3137 | 60.9023 | -122.3214 | 122.1541 | 122.3136 | 122.2298 | 60.9333 | -122.5355
1081.9219 | 122.4197 | -60.8917 | 61.4319 | 1.4211e-13 | -0.0012671 | -0.0095086 | 0.03917 | -0.023148 | 0.048012 | 0.011293 | -0.012148 | 0.028408 | 0.044157 | 0.0015577 | 0.045937 | -60.7862 | -0.030644 | -60.9545 | 61.3796 | 61.3351 | 61.3899 | -60.9765 | -60.8775 | 0.000359 | -60.9211 | 61.2303 | 61.399 | 61.3107 | -61.186 | -0.084766 | -0.052252 | 0.10552 | -0.062756 | 0.02201 | -0.096832 | -0.041953 | -0.29432 | -0.20157 | 0.014245 | -0.029417 | 0.2649 | -0.032855 | -0.12123 | 122.2714 | 122.2268 | 122.2817 | 60.8611 | -122.4084 | 122.122 | 122.2908 | 122.2024 | 60.8921 | -122.6179
1083.6406 | 122.4152 | -60.91 | 61.4273 | 1.4211e-13 | -0.0012671 | -0.0095086 | 0.039384 | -0.022935 | 0.048012 | 0.011293 | -0.012148 | 0.028194 | 0.043943 | 0.0015577 | 0.046151 | -60.7908 | -0.021486 | -60.9499 | 61.3888 | 61.3534 | 61.3991 | -60.9673 | -60.8683 | -0.00422 | -60.9166 | 61.2395 | 61.4082 | 61.3152 | -61.1815 | -0.057299 | -0.038517 | 0.11925 | -0.039868 | 0.017431 | -0.073938 | -0.028218 | -0.27143 | -0.18784 | 0.041713 | -0.006528 | 0.2649 | -0.019119 | -0.11207 | 122.2988 | 122.2634 | 122.3091 | 60.8885 | -122.3946 | 122.1495 | 122.3182 | 122.2253 | 60.9058 | -122.6088
1085.4219 | 122.4472 | -60.9009 | 61.3953 | 1.4211e-13 | -0.00083973 | -0.0097224 | 0.038957 | -0.023148 | 0.047585 | 0.011293 | -0.011934 | 0.028835 | 0.043943 | 0.0017713 | 0.046151 | -60.7816 | -0.026065 | -60.9407 | 61.3934 | 61.3442 | 61.4037 | -60.9582 | -60.8454 | -0.00422 | -60.8982 | 61.2486 | 61.4082 | 61.3336 | -61.1723 | -0.057296 | -0.001896 | 0.11925 | -0.039866 | 0.01743 | -0.051053 | 0.008404 | -0.27143 | -0.14664 | 0.055451 | 0.002631 | 0.27406 | 0.012924 | -0.061711 | 122.2942 | 122.2451 | 122.3045 | 60.8748 | -122.3534 | 122.1495 | 122.3091 | 122.2344 | 60.8967 | -122.5676
1087.1406 | 122.5296 | -60.91 | 61.3174 | 1.4211e-13 | -0.0012671 | -0.0095086 | 0.038957 | -0.023148 | 0.047799 | 0.0036627 | -0.011934 | 0.028408 | 0.044157 | 0.0017713 | 0.045937 | -60.7771 | -0.021486 | -60.9362 | 61.4071 | 61.3579 | 61.4174 | -60.9444 | -60.85 | 0.004938 | -60.9028 | 61.2624 | 61.4265 | 61.329 | -61.1586 | -0.034404 | 0.089659 | 0.13298 | -0.026133 | 0.008271 | 0.040504 | 0.099959 | -0.24854 | -0.055083 | 0.060028 | 0.007208 | 0.25575 | 0.10906 | 0.01153 | 122.3171 | 122.268 | 122.3274 | 60.8885 | -122.2619 | 122.1724 | 122.3365 | 122.239 | 60.915 | -122.476
1088.9375 | 122.4609 | -60.8963 | 61.3998 | 1.4211e-13 | -0.0014807 | -0.009295 | 0.038957 | -0.022721 | 0.047799 | 0.0036627 | -0.011934 | 0.028408 | 0.044157 | 0.0015577 | 0.046151 | -60.7587 | -0.021486 | -60.9316 | 61.4163 | 61.3625 | 61.422 | -60.949 | -60.8363 | -0.00422 | -60.8937 | 61.2669 | 61.4219 | 61.3381 | -61.154 | -0.052716 | 0.016419 | 0.13756 | -0.035288 | 0.017428 | -0.037314 | 0.022141 | -0.25769 | -0.1329 | 0.060031 | 0.002632 | 0.26032 | 0.022082 | -0.06171 | 122.3126 | 122.2588 | 122.3183 | 60.8748 | -122.3489 | 122.1632 | 122.3182 | 122.2344 | 60.8921 | -122.5538
1090.7188 | 122.5021 | -60.9055 | 61.3312 | 1.4211e-13 | -0.0012671 | -0.0097224 | 0.03917 | -0.023148 | 0.048012 | 0.0036627 | -0.012148 | 0.027981 | 0.043943 | 0.0017713 | 0.045937 | -60.7542 | -0.026065 | -60.9224 | 61.4163 | 61.3763 | 61.4311 | -60.9353 | -60.8271 | 0.004938 | -60.8799 | 61.2761 | 61.4357 | 61.3427 | -61.1494 | -0.029823 | 0.085083 | 0.1513 | -0.016975 | 0.012848 | 0.045087 | 0.099962 | -0.24396 | -0.055081 | 0.078344 | 0.025524 | 0.26948 | 0.10448 | 0.011533 | 122.3217 | 122.2817 | 122.3366 | 60.8794 | -122.2665 | 122.1816 | 122.3411 | 122.2482 | 60.9104 | -122.4806
1092.4844 | 122.5479 | -60.8871 | 61.3358 | 1.4211e-13 | -0.0010533 | -0.009295 | 0.038743 | -0.022935 | 0.047799 | 0.011293 | -0.012148 | 0.028194 | 0.043943 | 0.0019849 | 0.046151 | -60.7358 | -0.016908 | -60.9041 | 61.4208 | 61.3808 | 61.4266 | -60.9307 | -60.8271 | -0.00422 | -60.8708 | 61.2761 | 61.4402 | 61.3519 | -61.1448 | -0.043555 | 0.085085 | 0.1513 | -0.016973 | 0.026582 | 0.045088 | 0.090807 | -0.25769 | -0.059658 | 0.060033 | 0.016371 | 0.27406 | 0.10448 | 0.016113 | 122.308 | 122.268 | 122.3137 | 60.8702 | -122.2665 | 122.1632 | 122.3274 | 122.239 | 60.8829 | -122.4806
1094.2031 | 122.4472 | -60.8322 | 61.4456 | 1.4211e-13 | -0.0012671 | -0.0097224 | 0.03917 | -0.022935 | 0.048012 | 0.011293 | -0.012148 | 0.028194 | 0.043729 | 0.0015577 | 0.046151 | -60.7313 | -0.030644 | -60.8995 | 61.4346 | 61.39 | 61.454 | -60.9215 | -60.818 | 0.000359 | -60.8754 | 61.2898 | 61.4494 | 61.3656 | -61.1219 | -0.089329 | -0.011044 | 0.10095 | -0.067327 | 0.022002 | -0.055618 | 0.008414 | -0.28973 | -0.15579 | 0.014259 | -0.04314 | 0.24659 | 0.003777 | -0.080015 | 122.2668 | 122.2222 | 122.2862 | 60.8016 | -122.3672 | 122.122 | 122.2816 | 122.1978 | 60.8326 | -122.5676
1095.9844 | 122.4472 | -60.8871 | 61.3907 | 1.4211e-13 | -0.0014807 | -0.0097224 | 0.03917 | -0.023148 | 0.047799 | 0.011293 | -0.011934 | 0.028622 | 0.043943 | 0.0015577 | 0.046151 | -60.7267 | -0.026065 | -60.8995 | 61.4346 | 61.3992 | 61.454 | -60.9124 | -60.8088 | 0.014095 | -60.8525 | 61.2944 | 61.454 | 61.3702 | -61.1174 | -0.02524 | 0.043888 | 0.16046 | -0.012395 | 0.012845 | 0.008472 | 0.063346 | -0.23022 | -0.096276 | 0.078348 | 0.034685 | 0.2649 | 0.063288 | -0.020504 | 122.3217 | 122.2863 | 122.3412 | 60.8611 | -122.3031 | 122.1816 | 122.3411 | 122.2573 | 60.9012 | -122.508
1097.6875 | 122.438 | -60.8414 | 61.4182 | 1.4211e-13 | -0.00083973 | -0.0095086 | 0.039384 | -0.023148 | 0.047799 | -0.0039678 | -0.012148 | 0.028194 | 0.043729 | 0.0015577 | 0.046151 | -60.7084 | -0.030644 | -60.8766 | 61.4483 | 61.4083 | 61.4678 | -60.8941 | -60.8042 | 0.000359 | -60.8387 | 61.3081 | 61.4723 | 61.3839 | -61.1128 | -0.0527 | 0.030157 | 0.133 | -0.035279 | 0.017421 | -0.009836 | 0.049616 | -0.27141 | -0.11001 | 0.037151 | 0.002646 | 0.27406 | 0.054136 | -0.034235 | 122.2897 | 122.2497 | 122.3091 | 60.8107 | -122.3122 | 122.1495 | 122.3137 | 122.2253 | 60.8417 | -122.5309
1099.4688 | 122.525 | -60.7681 | 61.4456 | 1.4211e-13 | -0.00083973 | -0.009936 | 0.03917 | -0.023148 | 0.047585 | 0.0036627 | -0.011934 | 0.028408 | 0.043729 | 0.0015577 | 0.046151 | -60.6992 | -0.026065 | -60.8675 | 61.4666 | 61.4129 | 61.4678 | -60.8849 | -60.7813 | -0.008798 | -60.8387 | 61.3127 | 61.4769 | 61.3885 | -61.099 | -0.11679 | 0.021004 | 0.068908 | -0.099366 | 0.017419 | -0.032723 | 0.02215 | -0.33092 | -0.13289 | -0.013199 | -0.070597 | 0.26032 | 0.031249 | -0.057122 | 122.2347 | 122.181 | 122.2359 | 60.7421 | -122.3305 | 122.0809 | 122.245 | 122.1566 | 60.7593 | -122.5447
1101.1875 | 122.4106 | -60.8826 | 61.4319 | 1.4211e-13 | -0.0010533 | -0.0095086 | 0.03917 | -0.023362 | 0.047585 | 0.018923 | -0.012148 | 0.028194 | 0.044157 | 0.0015577 | 0.045937 | -60.6992 | -0.035222 | -60.8675 | 61.4666 | 61.4175 | 61.4815 | -60.8849 | -60.7905 | 0.004938 | -60.8341 | 61.3173 | 61.4814 | 61.3839 | -61.0945 | -0.002344 | 0.034737 | 0.18335 | 0.015075 | 0.017419 | -0.014411 | 0.049619 | -0.2119 | -0.11458 | 0.092085 | 0.048422 | 0.26032 | 0.04956 | -0.047968 | 122.3492 | 122.3 | 122.3641 | 60.8473 | -122.3168 | 122.1999 | 122.364 | 122.2665 | 60.8875 | -122.5264
1102.9688 | 122.3969 | -60.8643 | 61.4227 | 1.4211e-13 | -0.00062613 | -0.0097224 | 0.039384 | -0.022935 | 0.047799 | 0.011293 | -0.012361 | 0.028408 | 0.043729 | 0.0017713 | 0.045937 | -60.6901 | -0.030644 | -60.8629 | 61.4758 | 61.4358 | 61.4907 | -60.8849 | -60.7722 | 0.009516 | -60.8296 | 61.3173 | 61.486 | 61.4068 | -61.0899 | -0.020654 | 0.05305 | 0.1742 | 0.001344 | 0.021998 | 0.013061 | 0.067932 | -0.22563 | -0.10543 | 0.09209 | 0.034691 | 0.26032 | 0.063295 | -0.015919 | 122.34 | 122.3 | 122.3549 | 60.8336 | -122.3076 | 122.1816 | 122.3503 | 122.2711 | 60.8738 | -122.5126
1104.75 | 122.3877 | -60.8688 | 61.4548 | 1.4211e-13 | -0.0010533 | -0.0095086 | 0.03917 | -0.023362 | 0.048012 | 0.011293 | -0.012148 | 0.028408 | 0.044157 | 0.0017713 | 0.046151 | -60.6855 | -0.026065 | -60.8538 | 61.4849 | 61.4404 | 61.4952 | -60.8712 | -60.7676 | 0.004938 | -60.8158 | 61.331 | 61.4998 | 61.4114 | -61.0853 | -0.00234 | 0.030163 | 0.18335 | 0.015077 | 0.017417 | -0.014405 | 0.040467 | -0.21648 | -0.12374 | 0.10124 | 0.053004 | 0.26948 | 0.044987 | -0.043384 | 122.3538 | 122.3092 | 122.3641 | 60.8428 | -122.3259 | 122.1999 | 122.3686 | 122.2802 | 60.8738 | -122.5401
1106.5312 | 122.4426 | -60.7864 | 61.5005 | 1.4211e-13 | -0.00041233 | -0.0095086 | 0.039384 | -0.022935 | 0.047799 | 0.011293 | -0.012148 | 0.028408 | 0.044157 | 0.0015577 | 0.046151 | -60.6672 | -0.044379 | -60.84 | 61.4895 | 61.4495 | 61.5044 | -60.862 | -60.7539 | 0.004938 | -60.8021 | 61.3494 | 61.4952 | 61.416 | -61.0624 | -0.075579 | -0.011035 | 0.11927 | -0.053585 | 0.021994 | -0.051023 | 0.003848 | -0.27598 | -0.1512 | 0.032585 | -0.015657 | 0.26032 | -0.005368 | -0.084581 | 122.276 | 122.236 | 122.2908 | 60.7421 | -122.3626 | 122.1358 | 122.2816 | 122.2024 | 60.7914 | -122.563
1108.2656 | 122.3969 | -60.8139 | 61.5005 | 1.4211e-13 | -0.0010533 | -0.0097224 | 0.038957 | -0.023148 | 0.047585 | 0.011293 | -0.012148 | 0.028408 | 0.043729 | 0.0017713 | 0.046151 | -60.6397 | -0.035222 | -60.8126 | 61.5216 | 61.4724 | 61.5227 | -60.8437 | -60.731 | 0.000359 | -60.7792 | 61.3677 | 61.5272 | 61.4389 | -61.0533 | -0.029798 | 0.021014 | 0.1742 | 0.001351 | 0.031149 | -0.028128 | 0.022162 | -0.23936 | -0.13288 | 0.082944 | 0.034703 | 0.27406 | 0.026682 | -0.061688 | 122.3355 | 122.2863 | 122.3366 | 60.7787 | -122.3443 | 122.1816 | 122.3411 | 122.2528 | 60.8143 | -122.5538
1110.0469 | 122.4976 | -60.7544 | 61.5005 | 1.4211e-13 | -0.00062613 | -0.0097224 | 0.03917 | -0.023148 | 0.047799 | 0.0036627 | -0.011934 | 0.028194 | 0.043943 | 0.0015577 | 0.046151 | -60.6351 | -0.039801 | -60.7988 | 61.5261 | 61.4816 | 61.5319 | -60.8116 | -60.7218 | 0.000359 | -60.7655 | 61.3814 | 61.541 | 61.4572 | -61.0304 | -0.057254 | 0.025592 | 0.11927 | -0.044423 | 0.012831 | -0.01897 | 0.03132 | -0.27597 | -0.11915 | 0.032593 | -0.01107 | 0.2649 | 0.040418 | -0.043374 | 122.2805 | 122.236 | 122.2863 | 60.7146 | -122.3122 | 122.1358 | 122.2954 | 122.2116 | 60.7548 | -122.5309
1111.8125 | 122.4884 | -60.7407 | 61.4685 | 1.4211e-13 | -0.0012671 | -0.0095086 | 0.03917 | -0.022935 | 0.048012 | 0.0036627 | -0.011934 | 0.028194 | 0.043943 | 0.0019849 | 0.045937 | -60.6122 | -0.048958 | -60.7805 | 61.5399 | 61.4953 | 61.5502 | -60.8071 | -60.7035 | 0.009516 | -60.7517 | 61.3951 | 61.5593 | 61.4709 | -61.0166 | -0.066408 | 0.071371 | 0.12843 | -0.039843 | 0.026565 | 0.02681 | 0.081677 | -0.27597 | -0.073369 | 0.037174 | -0.011067 | 0.2649 | 0.090776 | 0.002405 | 122.2805 | 122.236 | 122.2908 | 60.6917 | -122.2756 | 122.1358 | 122.2999 | 122.2116 | 60.7502 | -122.4851
1113.5938 | 122.4564 | -60.7681 | 61.4594 | 1.4211e-13 | -0.00062613 | -0.0090814 | 0.038957 | -0.023148 | 0.048012 | 0.018923 | -0.012361 | 0.027981 | 0.044157 | 0.0015577 | 0.045937 | -60.6031 | -0.044379 | -60.7851 | 61.5399 | 61.4999 | 61.5548 | -60.8071 | -60.6943 | 0.000359 | -60.7426 | 61.4043 | 61.5593 | 61.4755 | -61.0121 | -0.038943 | 0.080526 | 0.16505 | -0.016957 | 0.021986 | 0.040544 | 0.095411 | -0.24392 | -0.055057 | 0.073797 | 0.025555 | 0.26948 | 0.099931 | 0.016138 | 122.308 | 122.268 | 122.3229 | 60.7237 | -122.2664 | 122.1724 | 122.3274 | 122.2436 | 60.7685 | -122.4714
1115.3125 | 122.4838 | -60.7361 | 61.5189 | 1.4211e-13 | -0.00041233 | -0.0095086 | 0.038743 | -0.023148 | 0.047585 | 0.011293 | -0.012148 | 0.028622 | 0.043943 | 0.0015577 | 0.046151 | -60.5939 | -0.044379 | -60.7713 | 61.549 | 61.4999 | 61.5639 | -60.7888 | -60.6943 | 0.000359 | -60.738 | 61.4089 | 61.5639 | 61.4709 | -61.0029 | -0.052671 | 0.030173 | 0.14217 | -0.035265 | 0.017406 | -0.018965 | 0.045059 | -0.26681 | -0.10999 | 0.041754 | -0.001909 | 0.2649 | 0.045 | -0.047949 | 122.2851 | 122.236 | 122.3 | 60.6917 | -122.3076 | 122.145 | 122.2999 | 122.207 | 60.7364 | -122.5218
1117.1094 | 122.4014 | -60.7315 | 61.528 | 1.4211e-13 | -0.00083973 | -0.0095086 | 0.03917 | -0.023362 | 0.047585 | 0.011293 | -0.011934 | 0.028408 | 0.043943 | 0.0017713 | 0.045937 | -60.5939 | -0.053537 | -60.7622 | 61.5628 | 61.5228 | 61.5777 | -60.7796 | -60.676 | 0.004938 | -60.7243 | 61.4089 | 61.5776 | 61.4984 | -60.9846 | -0.048091 | 0.034754 | 0.13759 | -0.030686 | 0.017405 | -0.005226 | 0.04964 | -0.25307 | -0.11914 | 0.055491 | 0.007249 | 0.26032 | 0.049581 | -0.029633 | 122.2943 | 122.2543 | 122.3092 | 60.678 | -122.3076 | 122.1404 | 122.3091 | 122.2299 | 60.7364 | -122.5126
1118.9062 | 122.3969 | -60.6857 | 61.6241 | 1.4211e-13 | -0.00083973 | -0.0097224 | 0.039384 | -0.023148 | 0.047585 | 0.018923 | -0.012148 | 0.028408 | 0.044157 | 0.0015577 | 0.045937 | -60.5664 | -0.058115 | -60.7485 | 61.5765 | 61.5319 | 61.5868 | -60.7704 | -60.6669 | 0.004938 | -60.7151 | 61.4272 | 61.5959 | 61.503 | -60.9846 | -0.084709 | -0.047642 | 0.11928 | -0.062727 | 0.021982 | -0.092199 | -0.037334 | -0.29885 | -0.19696 | 0.018872 | -0.029369 | 0.26948 | -0.028236 | -0.12119 | 122.2622 | 122.2177 | 122.2725 | 60.6276 | -122.3946 | 122.1129 | 122.2816 | 122.1887 | 60.6907 | -122.6087
1120.6719 | 122.525 | -60.6583 | 61.5646 | 1.4211e-13 | -0.0010533 | -0.0095086 | 0.03917 | -0.022935 | 0.047585 | 0.0036627 | -0.011934 | 0.028194 | 0.04437 | 0.0017713 | 0.04551 | -60.5527 | -0.058115 | -60.7393 | 61.5902 | 61.5411 | 61.6005 | -60.7521 | -60.6485 | 0.004938 | -60.7059 | 61.4363 | 61.6005 | 61.5167 | -60.9708 | -0.093859 | 0.025603 | 0.10555 | -0.081037 | 0.012822 | -0.023531 | 0.035912 | -0.31258 | -0.12829 | 0.009721 | -0.047678 | 0.2649 | 0.035853 | -0.047939 | 122.2485 | 122.1994 | 122.2588 | 60.6001 | -122.3168 | 122.0946 | 122.2588 | 122.175 | 60.6632 | -122.5355
1122.3906 | 122.5021 | -60.6491 | 61.5967 | 1.4211e-13 | -0.00083973 | -0.01015 | 0.03917 | -0.022935 | 0.048226 | 0.0036627 | -0.01172 | 0.028408 | 0.043943 | 0.0015577 | 0.045724 | -60.5344 | -0.07643 | -60.7164 | 61.5994 | 61.5548 | 61.6143 | -60.743 | -60.644 | 0.000359 | -60.6922 | 61.4592 | 61.6096 | 61.535 | -60.9525 | -0.093856 | 0.002716 | 0.11471 | -0.0673 | 0.026556 | -0.041838 | 0.017603 | -0.30342 | -0.13744 | 0.005145 | -0.043097 | 0.26032 | 0.012966 | -0.061669 | 122.2485 | 122.204 | 122.2634 | 60.5727 | -122.3396 | 122.1083 | 122.2588 | 122.1841 | 60.6495 | -122.5492
1124.1719 | 122.4701 | -60.672 | 61.5601 | 1.4211e-13 | -0.00083973 | -0.009936 | 0.038957 | -0.023148 | 0.047799 | 0.0036627 | -0.012148 | 0.028194 | 0.043729 | 0.0019849 | 0.045937 | -60.5207 | -0.085587 | -60.7164 | 61.6177 | 61.5686 | 61.628 | -60.7292 | -60.6165 | 0.000359 | -60.6785 | 61.4684 | 61.628 | 61.5396 | -60.9434 | -0.057232 | 0.05765 | 0.15133 | -0.044412 | 0.01282 | 0.008519 | 0.06796 | -0.27137 | -0.091666 | 0.055505 | -0.006473 | 0.2649 | 0.067902 | -0.020469 | 122.2897 | 122.2406 | 122.3 | 60.5864 | -122.2893 | 122.1404 | 122.3 | 122.2116 | 60.6724 | -122.5034
1125.875 | 122.5479 | -60.64 | 61.6104 | 1.4211e-13 | -0.00041233 | -0.0095086 | 0.038957 | -0.023148 | 0.047585 | 0.018923 | -0.011934 | 0.028194 | 0.043729 | 0.0015577 | 0.045937 | -60.5207 | -0.099323 | -60.6935 | 61.6269 | 61.5823 | 61.6372 | -60.7201 | -60.6119 | 0.004938 | -60.6693 | 61.4776 | 61.6417 | 61.5533 | -60.9342 | -0.080117 | 0.016453 | 0.11929 | -0.053564 | 0.026553 | -0.028098 | 0.026763 | -0.29426 | -0.13286 | 0.028041 | -0.029358 | 0.2649 | 0.031283 | -0.057087 | 122.2668 | 122.2223 | 122.2771 | 60.5406 | -122.3305 | 122.1175 | 122.2817 | 122.1933 | 60.6449 | -122.5446
1127.6562 | 122.4335 | -60.6354 | 61.6562 | 1.4211e-13 | -0.00083973 | -0.0097224 | 0.03917 | -0.023362 | 0.048012 | 0.011293 | -0.012361 | 0.028408 | 0.043729 | 0.0017713 | 0.045937 | -60.4932 | -0.11306 | -60.6889 | 61.6406 | 61.5869 | 61.6463 | -60.7155 | -60.6028 | 0.004938 | -60.6464 | 61.4913 | 61.6463 | 61.5762 | -60.9159 | -0.080116 | -0.015588 | 0.14218 | -0.053564 | 0.026552 | -0.069295 | -0.009855 | -0.28052 | -0.1649 | 0.03262 | -0.011043 | 0.26948 | -0.009914 | -0.07997 | 122.276 | 122.2223 | 122.2817 | 60.5223 | -122.3717 | 122.1267 | 122.2817 | 122.2116 | 60.6403 | -122.5721
1129.4531 | 122.493 | -60.5804 | 61.6608 | 1.4211e-13 | -0.00083973 | -0.0097224 | 0.03917 | -0.023148 | 0.047585 | 0.0036627 | -0.011934 | 0.028194 | 0.044157 | 0.0015577 | 0.046151 | -60.4795 | -0.14511 | -60.6615 | 61.6589 | 61.6006 | 61.6646 | -60.6926 | -60.5844 | 0.004938 | -60.6327 | 61.5142 | 61.6737 | 61.5808 | -60.9067 | -0.11215 | -0.001852 | 0.10099 | -0.081026 | 0.031127 | -0.060136 | 0.003881 | -0.32629 | -0.14659 | -0.003997 | -0.052238 | 0.27406 | 0.01298 | -0.07997 | 122.2394 | 122.1811 | 122.2451 | 60.4353 | -122.3534 | 122.0946 | 122.2542 | 122.1612 | 60.5854 | -122.5675
1131.1875 | 122.5159 | -60.5621 | 61.6653 | 1.4211e-13 | -0.00083973 | -0.0095086 | 0.038957 | -0.023362 | 0.047799 | 0.018923 | -0.011934 | 0.028408 | 0.043943 | 0.0013439 | 0.046151 | -60.4749 | -0.16342 | -60.6569 | 61.6635 | 61.6189 | 61.683 | -60.6743 | -60.5753 | -0.00422 | -60.6144 | 61.5142 | 61.6875 | 61.5991 | -60.8884 | -0.11215 | -0.001851 | 0.087256 | -0.094758 | 0.017389 | -0.046397 | 0.017618 | -0.32629 | -0.15117 | -0.01315 | -0.052234 | 0.27405 | 0.022138 | -0.066232 | 122.2256 | 122.1811 | 122.2451 | 60.3987 | -122.3396 | 122.0763 | 122.2496 | 122.1612 | 60.5579 | -122.5538
1132.9688 | 122.3602 | -60.6354 | 61.6653 | 1.4211e-13 | -0.0010533 | -0.0097224 | 0.038957 | -0.023148 | 0.047799 | 0.011293 | -0.012361 | 0.028622 | 0.044157 | 0.0017713 | 0.046365 | -60.4474 | -0.1909 | -60.6294 | 61.691 | 61.6418 | 61.7013 | -60.656 | -60.5478 | 0.004938 | -60.6006 | 61.5416 | 61.7012 | 61.6174 | -60.8655 | -0.02059 | 0.025619 | 0.18797 | 0.005954 | 0.026544 | -0.023503 | 0.035933 | -0.23015 | -0.12369 | 0.087565 | 0.034745 | 0.2649 | 0.035874 | -0.047918 | 122.3263 | 122.2772 | 122.3367 | 60.4445 | -122.3213 | 122.177 | 122.3366 | 122.2528 | 60.6403 | -122.5309
1134.75 | 122.525 | -60.553 | 61.6837 | 1.4211e-13 | -0.00062613 | -0.0095086 | 0.038743 | -0.022935 | 0.047799 | -0.0039678 | -0.011934 | 0.028408 | 0.043729 | 0.0017713 | 0.046151 | -60.4154 | -0.22295 | -60.6065 | 61.7139 | 61.6647 | 61.715 | -60.6239 | -60.5295 | 0.004938 | -60.5777 | 61.5554 | 61.7287 | 61.6403 | -60.8426 | -0.070934 | 0.0302 | 0.13762 | -0.053552 | 0.017382 | -0.018919 | 0.031358 | -0.28965 | -0.12827 | 0.023482 | -0.024759 | 0.2649 | 0.045035 | -0.043336 | 122.2668 | 122.2177 | 122.268 | 60.33 | -122.3076 | 122.1084 | 122.2817 | 122.1933 | 60.5579 | -122.5263
1136.4844 | 122.3785 | -60.585 | 61.6882 | 1.4211e-13 | -0.00062613 | -0.009295 | 0.039384 | -0.022935 | 0.047585 | 0.011293 | -0.012148 | 0.028194 | 0.043729 | 0.0013439 | 0.046151 | -60.4062 | -0.25957 | -60.5974 | 61.723 | 61.6785 | 61.7379 | -60.6148 | -60.5112 | 0.004938 | -60.564 | 61.5737 | 61.7378 | 61.6495 | -60.8243 | -0.029733 | 0.03478 | 0.17882 | -0.012352 | 0.017381 | -0.009759 | 0.049674 | -0.2393 | -0.11453 | 0.07384 | 0.02102 | 0.26032 | 0.049615 | -0.038756 | 122.308 | 122.2635 | 122.3229 | 60.3254 | -122.303 | 122.1587 | 122.3229 | 122.2345 | 60.59 | -122.5126
1138.1875 | 122.4747 | -60.5621 | 61.6562 | 1.4211e-13 | -0.00083973 | -0.0097224 | 0.038957 | -0.023148 | 0.047585 | 0.0036627 | -0.012148 | 0.028408 | 0.043729 | 0.0015577 | 0.046151 | -60.3833 | -0.2962 | -60.5699 | 61.7459 | 61.7014 | 61.7608 | -60.5964 | -60.4883 | 0.004938 | -60.5457 | 61.6012 | 61.7653 | 61.6769 | -60.806 | -0.034306 | 0.089715 | 0.17882 | -0.00777 | 0.026536 | 0.045178 | 0.10461 | -0.24387 | -0.05502 | 0.073846 | 0.016447 | 0.26032 | 0.10913 | 0.020759 | 122.308 | 122.2635 | 122.3229 | 60.2659 | -122.2526 | 122.1633 | 122.3275 | 122.2391 | 60.5671 | -122.4622
1139.9531 | 122.4747 | -60.4889 | 61.734 | 1.4211e-13 | -0.00062613 | -0.0095086 | 0.03917 | -0.022935 | 0.047799 | 0.026554 | -0.012148 | 0.028194 | 0.043729 | 0.0013439 | 0.046151 | -60.3604 | -0.33283 | -60.547 | 61.7688 | 61.7243 | 61.7791 | -60.5735 | -60.4608 | 0.009516 | -60.5182 | 61.6286 | 61.7836 | 61.6998 | -60.7877 | -0.084653 | 0.034787 | 0.12847 | -0.058121 | 0.026532 | -0.009747 | 0.045104 | -0.2988 | -0.10537 | 0.028076 | -0.029323 | 0.26947 | 0.049624 | -0.034168 | 122.2577 | 122.2132 | 122.268 | 60.1561 | -122.3076 | 122.1175 | 122.2725 | 122.1887 | 60.4984 | -122.5217
1141.7188 | 122.4197 | -60.5118 | 61.7523 | 1.4211e-13 | -0.00041233 | -0.0095086 | 0.03917 | -0.022935 | 0.047799 | 0.011293 | -0.012361 | 0.028194 | 0.044157 | 0.0015577 | 0.045937 | -60.3284 | -0.39235 | -60.5241 | 61.7963 | 61.7563 | 61.8066 | -60.5461 | -60.4379 | 0.004938 | -60.4907 | 61.6424 | 61.8065 | 61.7273 | -60.7602 | -0.034292 | 0.043947 | 0.18341 | -0.012342 | 0.02195 | 0.003995 | 0.054266 | -0.24844 | -0.10994 | 0.073858 | 0.021038 | 0.26947 | 0.054207 | -0.025006 | 122.308 | 122.2681 | 122.3184 | 60.1194 | -122.2984 | 122.1542 | 122.3183 | 122.2391 | 60.5167 | -122.5125
1143.4375 | 122.5204 | -60.4202 | 61.8027 | 1.4211e-13 | -0.0010533 | -0.0095086 | 0.03917 | -0.022721 | 0.047799 | 0.011293 | -0.01172 | 0.028408 | 0.044157 | 0.0017713 | 0.046151 | -60.3009 | -0.44272 | -60.4921 | 61.8192 | 61.7838 | 61.8386 | -60.5186 | -60.4059 | 0.004938 | -60.4541 | 61.6698 | 61.834 | 61.7456 | -60.7282 | -0.098371 | 0.016485 | 0.11933 | -0.071847 | 0.026524 | -0.018885 | 0.035962 | -0.30794 | -0.13283 | 0.014356 | -0.033886 | 0.27405 | 0.031325 | -0.057046 | 122.2394 | 122.204 | 122.2589 | 59.9775 | -122.3213 | 122.0901 | 122.2542 | 122.1659 | 60.4252 | -122.5308
1145.1562 | 122.4747 | -60.4111 | 61.8256 | 1.4211e-13 | -0.00083973 | -0.0095086 | 0.038957 | -0.023148 | 0.048012 | 0.011293 | -0.012148 | 0.028408 | 0.043943 | 0.0015577 | 0.045937 | -60.2551 | -0.4885 | -60.4371 | 61.8604 | 61.825 | 61.8798 | -60.4682 | -60.3647 | 0.000359 | -60.4266 | 61.7156 | 61.8798 | 61.7868 | -60.6824 | -0.057158 | 0.034802 | 0.15596 | -0.026062 | 0.031096 | -0.000564 | 0.05428 | -0.2713 | -0.10993 | 0.046409 | -0.015569 | 0.25574 | 0.054222 | -0.038728 | 122.2714 | 122.2361 | 122.2909 | 59.9226 | -122.2938 | 122.1267 | 122.2909 | 122.1979 | 60.4114 | -122.5079
1146.9219 | 122.4701 | -60.4111 | 61.821 | 1.4211e-13 | -0.00062613 | -0.0095086 | 0.03917 | -0.023148 | 0.048012 | 0.0036627 | -0.01172 | 0.027981 | 0.043943 | 0.0015577 | 0.046151 | -60.246 | -0.53429 | -60.4463 | 61.8649 | 61.825 | 61.8753 | -60.4637 | -60.3555 | 0.004938 | -60.4129 | 61.7202 | 61.8889 | 61.796 | -60.6778 | -0.052579 | 0.043958 | 0.16511 | -0.035219 | 0.01736 | 0.004014 | 0.05428 | -0.26673 | -0.10077 | 0.055566 | -0.001832 | 0.26489 | 0.067957 | -0.024992 | 122.276 | 122.2361 | 122.2863 | 59.8768 | -122.2846 | 122.1313 | 122.3 | 122.2071 | 60.416 | -122.4988
1148.6875 | 122.5204 | -60.2966 | 61.8896 | 1.4211e-13 | -0.0010533 | -0.0097224 | 0.03917 | -0.023148 | 0.047585 | 0.018923 | -0.011934 | 0.027981 | 0.043516 | 0.0015577 | 0.045937 | -60.2048 | -0.59839 | -60.4005 | 61.9107 | 61.8662 | 61.9302 | -60.4224 | -60.3235 | 0.000359 | -60.3717 | 61.7614 | 61.9256 | 61.8464 | -60.6366 | -0.12581 | 0.021078 | 0.091878 | -0.10388 | 0.021933 | -0.02344 | 0.040559 | -0.33996 | -0.12823 | -0.026824 | -0.075065 | 0.26489 | 0.035922 | -0.043292 | 122.2074 | 122.1628 | 122.2268 | 59.6982 | -122.3121 | 122.058 | 122.2222 | 122.143 | 60.297 | -122.5262
1150.4844 | 122.5204 | -60.2737 | 61.9354 | 1.4211e-13 | -0.00062613 | -0.0095086 | 0.038957 | -0.022721 | 0.047799 | 0.0036627 | -0.011934 | 0.028622 | 0.043943 | 0.0017713 | 0.046151 | -60.1681 | -0.64418 | -60.3547 | 61.9428 | 61.9074 | 61.9623 | -60.3812 | -60.2822 | 0.000359 | -60.3396 | 61.8026 | 61.9759 | 61.8738 | -60.5954 | -0.10749 | 0.00735 | 0.10562 | -0.080982 | 0.026505 | -0.028006 | 0.026832 | -0.32163 | -0.1328 | -0.008503 | -0.065902 | 0.25573 | 0.040509 | -0.061597 | 122.2165 | 122.1812 | 122.236 | 59.6296 | -122.3167 | 122.0764 | 122.2497 | 122.1476 | 60.2741 | -122.5308
1152.2031 | 122.5113 | -60.2737 | 61.8942 | 1.4211e-13 | -0.0010533 | -0.009295 | 0.03917 | -0.023148 | 0.047585 | 0.0036627 | -0.011934 | 0.028622 | 0.043729 | 0.0017713 | 0.046365 | -60.1178 | -0.69912 | -60.3227 | 61.9886 | 61.9395 | 62.0035 | -60.3492 | -60.2456 | 0.004938 | -60.303 | 61.8347 | 61.9988 | 61.915 | -60.5633 | -0.075435 | 0.094333 | 0.15598 | -0.048934 | 0.026501 | 0.045245 | 0.10924 | -0.28958 | -0.059553 | 0.028126 | -0.029272 | 0.26031 | 0.1046 | 0.020809 | 122.2623 | 122.2132 | 122.2772 | 59.5746 | -122.2434 | 122.1084 | 122.2726 | 122.1888 | 60.2787 | -122.4576
1153.9844 | 122.374 | -60.3241 | 61.9583 | 1.4211e-13 | -0.00062613 | -0.0090814 | 0.038957 | -0.022935 | 0.047799 | 0.018923 | -0.012361 | 0.028835 | 0.043943 | 0.0013439 | 0.046151 | -60.0903 | -0.76322 | -60.2952 | 62.0115 | 61.9853 | 62.0309 | -60.3217 | -60.2136 | 0.000359 | -60.2664 | 61.8713 | 62.0309 | 61.9379 | -60.5404 | 0.002393 | 0.053138 | 0.2338 | 0.028889 | 0.026496 | 0.026948 | 0.072623 | -0.21634 | -0.087012 | 0.11053 | 0.057711 | 0.27405 | 0.072565 | -0.020385 | 122.3355 | 122.3094 | 122.355 | 59.5609 | -122.28 | 122.1954 | 122.355 | 122.262 | 60.3245 | -122.4987
1155.6875 | 122.5204 | -60.141 | 62.0407 | 1.4211e-13 | -0.00083973 | -0.009295 | 0.03917 | -0.023148 | 0.047799 | 0.0036627 | -0.011507 | 0.028194 | 0.043943 | 0.0015577 | 0.045724 | -60.0308 | -0.80443 | -60.2357 | 62.071 | 62.0265 | 62.0813 | -60.2622 | -60.1632 | 0.004938 | -60.2114 | 61.9171 | 62.0767 | 61.9929 | -60.4763 | -0.12119 | 0.03026 | 0.11022 | -0.094699 | 0.026488 | -0.014239 | 0.040591 | -0.33534 | -0.12362 | -0.022209 | -0.07045 | 0.26489 | 0.035954 | -0.047838 | 122.212 | 122.1675 | 122.2223 | 59.3366 | -122.3029 | 122.0581 | 122.2177 | 122.1339 | 60.1459 | -122.517
1157.4844 | 122.5067 | -60.1639 | 62.0178 | 1.4211e-13 | -0.0012671 | -0.0097224 | 0.038957 | -0.022721 | 0.047585 | 0.011293 | -0.012148 | 0.028408 | 0.044157 | 0.0013439 | 0.045937 | -59.9941 | -0.86395 | -60.1945 | 62.1076 | 62.0723 | 62.1225 | -60.221 | -60.1266 | 0.009516 | -60.1794 | 61.9583 | 62.1316 | 62.0432 | -60.4397 | -0.057089 | 0.089775 | 0.16973 | -0.030606 | 0.026483 | 0.054438 | 0.10469 | -0.27582 | -0.05953 | 0.037309 | -0.015511 | 0.26031 | 0.11379 | 0.025414 | 122.2715 | 122.2361 | 122.2864 | 59.2999 | -122.2388 | 122.1222 | 122.2955 | 122.2071 | 60.1734 | -122.4575
1159.2031 | 122.3831 | -60.1181 | 62.1552 | 1.4211e-13 | -0.0010533 | -0.009295 | 0.039384 | -0.023362 | 0.048012 | 0.011293 | -0.011934 | 0.028622 | 0.043729 | 0.0015577 | 0.046365 | -59.9026 | -0.90973 | -60.1075 | 62.1809 | 62.1547 | 62.2095 | -60.1431 | -60.0396 | 0.004938 | -60.0832 | 62.0407 | 62.2094 | 62.1165 | -60.3435 | -0.025023 | 0.0257 | 0.21552 | 0.010605 | 0.035628 | -0.00047 | 0.054351 | -0.22544 | -0.11445 | 0.078528 | 0.034866 | 0.26031 | 0.054292 | -0.038657 | 122.299 | 122.2728 | 122.3276 | 59.2084 | -122.2983 | 122.1588 | 122.3275 | 122.2346 | 60.123 | -122.4987
1160.9844 | 122.493 | -60.0403 | 62.1597 | 1.4211e-13 | -0.00083973 | -0.009295 | 0.03917 | -0.023148 | 0.047799 | 0.011293 | -0.012148 | 0.028194 | 0.043729 | 0.0013439 | 0.045724 | -59.8385 | -0.95094 | -60.048 | 62.2449 | 62.2096 | 62.2599 | -60.0744 | -59.9801 | 0.009516 | -60.0329 | 62.0956 | 62.2644 | 62.1669 | -60.3069 | -0.034159 | 0.085219 | 0.2018 | -0.007697 | 0.026462 | 0.049899 | 0.10014 | -0.26663 | -0.064082 | 0.060232 | 0.007412 | 0.27404 | 0.10466 | 0.007129 | 122.2852 | 122.2499 | 122.3001 | 59.0893 | -122.2342 | 122.1359 | 122.3047 | 122.2071 | 60.0498 | -122.4666
1162.75 | 122.3419 | -60.0815 | 62.2009 | 1.4211e-13 | -0.00083973 | -0.0097224 | 0.03917 | -0.023362 | 0.048012 | 0.011293 | -0.011934 | 0.028194 | 0.044157 | 0.0019849 | 0.045724 | -59.8431 | -0.99673 | -60.0526 | 62.2449 | 62.205 | 62.2599 | -60.0882 | -59.9846 | 0.009516 | -60.0374 | 62.0956 | 62.2552 | 62.1714 | -60.3023 | -0.006697 | 0.04402 | 0.23842 | 0.028923 | 0.03562 | 0.004121 | 0.058938 | -0.22085 | -0.10528 | 0.096852 | 0.044032 | 0.26488 | 0.054301 | -0.029491 | 122.3264 | 122.2865 | 122.3413 | 59.0848 | -122.2891 | 122.1771 | 122.3367 | 122.2529 | 60.091 | -122.5033
1164.5312 | 122.4426 | -59.967 | 62.2833 | 1.4211e-13 | -0.00041233 | -0.0095086 | 0.03917 | -0.023148 | 0.048012 | 0.011293 | -0.011934 | 0.028194 | 0.043943 | 0.0013439 | 0.046151 | -59.7561 | -1.0242 | -59.9656 | 62.3274 | 62.2875 | 62.3469 | -60.0012 | -59.9068 | 0.004938 | -59.9505 | 62.1781 | 62.3422 | 62.2584 | -60.2153 | -0.034139 | 0.044034 | 0.21097 | 0.00147 | 0.035609 | 0.004145 | 0.063535 | -0.24829 | -0.10526 | 0.060249 | 0.016586 | 0.26488 | 0.058898 | -0.024895 | 122.2944 | 122.2545 | 122.3139 | 58.9428 | -122.2845 | 122.1451 | 122.3093 | 122.2255 | 59.972 | -122.4987
1166.2656 | 122.4747 | -59.9442 | 62.2467 | 1.4211e-13 | -0.00083973 | -0.0095086 | 0.039384 | -0.023148 | 0.047585 | 0.018923 | -0.012148 | 0.028408 | 0.043943 | 0.0013439 | 0.045937 | -59.779 | -1.0746 | -59.9885 | 62.2953 | 62.2554 | 62.3148 | -60.0332 | -59.9297 | -0.008798 | -59.9733 | 62.1552 | 62.3193 | 62.2355 | -60.2382 | -0.089079 | 0.048607 | 0.16519 | -0.04431 | 0.044769 | 0.008713 | 0.068106 | -0.29408 | -0.091537 | 0.014467 | -0.029195 | 0.26488 | 0.072626 | -0.011167 | 122.2395 | 122.1996 | 122.259 | 58.8696 | -122.2799 | 122.0993 | 122.2635 | 122.1797 | 59.9354 | -122.4849
1168.0469 | 122.4792 | -59.8755 | 62.352 | 1.4211e-13 | -0.00062613 | -0.009295 | 0.038957 | -0.022935 | 0.047799 | 0.0036627 | -0.011934 | 0.028408 | 0.043729 | 0.0015577 | 0.046151 | -59.7194 | -1.0929 | -59.9335 | 62.3594 | 62.3149 | 62.3652 | -59.9783 | -59.8656 | 0.004938 | -59.9321 | 62.201 | 62.3743 | 62.2813 | -60.1833 | -0.1028 | 0.007418 | 0.15604 | -0.058035 | 0.044762 | -0.037047 | 0.013184 | -0.3078 | -0.15104 | 0.009904 | -0.056652 | 0.25115 | 0.022283 | -0.070666 | 122.2349 | 122.1904 | 122.2407 | 58.7826 | -122.3303 | 122.0764 | 122.2498 | 122.1568 | 59.8804 | -122.5353
1169.7656 | 122.5204 | -59.8251 | 62.3795 | 1.4211e-13 | -0.00083973 | -0.009936 | 0.03917 | -0.023362 | 0.047799 | -0.0039678 | -0.011934 | 0.028408 | 0.043943 | 0.0017713 | 0.045937 | -59.6874 | -1.102 | -59.9015 | 62.3823 | 62.347 | 62.4018 | -59.9417 | -59.8473 | 0.004938 | -59.8909 | 62.2284 | 62.4017 | 62.3088 | -60.1558 | -0.11652 | 0.002844 | 0.13774 | -0.076341 | 0.040179 | -0.03246 | 0.022347 | -0.33068 | -0.15103 | -0.022135 | -0.065797 | 0.26488 | 0.022288 | -0.070661 | 122.2074 | 122.1721 | 122.2269 | 58.7231 | -122.3211 | 122.0536 | 122.2269 | 122.1339 | 59.8301 | -122.5353
1171.5 | 122.374 | -59.8251 | 62.4847 | 1.4211e-13 | -0.00083973 | -0.0095086 | 0.03917 | -0.022935 | 0.047799 | 0.0036627 | -0.012361 | 0.028408 | 0.044157 | 0.0015577 | 0.045937 | -59.637 | -1.0975 | -59.842 | 62.4327 | 62.3928 | 62.4476 | -59.8959 | -59.7923 | 0.000359 | -59.8451 | 62.2879 | 62.4521 | 62.3637 | -60.11 | -0.07073 | -0.052079 | 0.1881 | -0.016824 | 0.053906 | -0.091956 | -0.037152 | -0.28489 | -0.1968 | 0.03281 | -0.02001 | 0.26488 | -0.032632 | -0.121 | 122.2578 | 122.2179 | 122.2727 | 58.7277 | -122.3806 | 122.1131 | 122.2772 | 122.1889 | 59.8255 | -122.5948
1173.2188 | 122.4609 | -59.7656 | 62.4664 | 1.4211e-13 | -0.00062613 | -0.0097224 | 0.038957 | -0.022935 | 0.048226 | 0.0036627 | -0.012361 | 0.028408 | 0.043729 | 0.0011303 | 0.045937 | -59.5775 | -1.1158 | -59.8008 | 62.4968 | 62.4432 | 62.5025 | -59.8455 | -59.7465 | 0.004938 | -59.7948 | 62.3429 | 62.5071 | 62.4141 | -60.0551 | -0.079871 | 0.030329 | 0.18811 | -0.035128 | 0.044743 | -0.023278 | 0.036101 | -0.28945 | -0.12355 | 0.019088 | -0.029154 | 0.2603 | 0.040621 | -0.052328 | 122.2624 | 122.2088 | 122.2682 | 58.6499 | -122.3119 | 122.1085 | 122.2727 | 122.1797 | 59.7706 | -122.5215
1175 | 122.4243 | -59.7427 | 62.5168 | 1.4211e-13 | -0.00083973 | -0.0095086 | 0.03917 | -0.023148 | 0.047799 | 0.0036627 | -0.011934 | 0.028408 | 0.043943 | 0.0015577 | 0.046151 | -59.5363 | -1.1341 | -59.7595 | 62.5151 | 62.4752 | 62.5392 | -59.7997 | -59.7053 | 0.004938 | -59.7627 | 62.3749 | 62.5391 | 62.4462 | -60.0184 | -0.05697 | -0.001712 | 0.20643 | -0.016812 | 0.040158 | -0.04158 | 0.022376 | -0.27571 | -0.14185 | 0.037408 | -0.019991 | 0.25572 | 0.022317 | -0.070632 | 122.2578 | 122.2179 | 122.2819 | 58.6086 | -122.3165 | 122.1177 | 122.2818 | 122.1889 | 59.7477 | -122.5352
1176.7656 | 122.4014 | -59.6466 | 62.6221 | 1.4211e-13 | -0.00062613 | -0.0097224 | 0.03917 | -0.022935 | 0.047585 | 0.011293 | -0.012148 | 0.028194 | 0.043943 | 0.0019849 | 0.045937 | -59.4951 | -1.1707 | -59.7275 | 62.5425 | 62.5073 | 62.5575 | -59.7768 | -59.6733 | 0.000359 | -59.7307 | 62.4024 | 62.562 | 62.469 | -59.9818 | -0.13021 | -0.079526 | 0.1515 | -0.080895 | 0.049311 | -0.11481 | -0.064594 | -0.33521 | -0.21966 | -0.026672 | -0.084071 | 0.25114 | -0.060075 | -0.15302 | 122.1891 | 122.1539 | 122.2041 | 58.4759 | -122.3989 | 122.049 | 122.2086 | 122.1157 | 59.647 | -122.6039
1178.5469 | 122.4518 | -59.5963 | 62.5992 | 1.4211e-13 | -0.00062613 | -0.009936 | 0.03917 | -0.023362 | 0.047799 | -0.0039678 | -0.01172 | 0.028408 | 0.044157 | 0.0011303 | 0.046365 | -59.4127 | -1.1982 | -59.6451 | 62.6341 | 62.5897 | 62.6536 | -59.6898 | -59.6 | 0.000359 | -59.6437 | 62.4802 | 62.649 | 62.5606 | -59.904 | -0.093561 | 0.034929 | 0.18356 | -0.04884 | 0.044721 | -0.009503 | 0.054444 | -0.30772 | -0.11894 | -0.003767 | -0.047429 | 0.2603 | 0.049807 | -0.038564 | 122.2304 | 122.1859 | 122.2499 | 58.3981 | -122.289 | 122.0765 | 122.2452 | 122.1569 | 59.5966 | -122.5032
1180.2656 | 122.3648 | -59.5963 | 62.6816 | 1.4211e-13 | -0.00083973 | -0.0097224 | 0.039384 | -0.022935 | 0.047799 | 0.011293 | -0.012361 | 0.028408 | 0.043943 | 0.0019849 | 0.046151 | -59.3349 | -1.244 | -59.5673 | 62.7119 | 62.6675 | 62.7223 | -59.6211 | -59.5176 | 0.009516 | -59.575 | 62.5581 | 62.7268 | 62.6385 | -59.8307 | -0.024877 | 0.030364 | 0.26139 | 0.028991 | 0.053868 | -0.01406 | 0.040725 | -0.23446 | -0.1235 | 0.07865 | 0.021252 | 0.25572 | 0.045245 | -0.043126 | 122.3082 | 122.2638 | 122.3186 | 58.3523 | -122.3027 | 122.1543 | 122.3231 | 122.2347 | 59.6058 | -122.5123
1182.0469 | 122.4472 | -59.5322 | 62.6816 | 1.4211e-13 | -0.0010533 | -0.0097224 | 0.03917 | -0.022721 | 0.047799 | 0.011293 | -0.011934 | 0.028622 | 0.044157 | 0.0019849 | 0.045937 | -59.2982 | -1.2806 | -59.5306 | 62.7348 | 62.6904 | 62.7406 | -59.5845 | -59.4947 | 0.004938 | -59.5475 | 62.581 | 62.7543 | 62.6568 | -59.8032 | -0.052331 | 0.053256 | 0.23393 | 0.001531 | 0.053862 | 0.008835 | 0.05904 | -0.27108 | -0.10061 | 0.037458 | -0.015362 | 0.25572 | 0.072717 | -0.024811 | 122.267 | 122.2226 | 122.2728 | 58.2516 | -122.2661 | 122.1131 | 122.2865 | 122.1889 | 59.5371 | -122.4848
1183.7344 | 122.3694 | -59.5001 | 62.7869 | 1.4211e-13 | -0.00083973 | -0.0097224 | 0.038957 | -0.023148 | 0.047799 | 0.0036627 | -0.01172 | 0.028622 | 0.043943 | 0.0015577 | 0.04551 | -59.2433 | -1.3401 | -59.4849 | 62.7944 | 62.7454 | 62.8139 | -59.5341 | -59.4352 | 0.014095 | -59.4926 | 62.6405 | 62.8092 | 62.7117 | -59.7437 | -0.034007 | 0.00749 | 0.25683 | 0.01527 | 0.049277 | -0.041503 | 0.027012 | -0.2436 | -0.14638 | 0.064937 | 0.007538 | 0.25113 | 0.022375 | -0.075153 | 122.2945 | 122.2455 | 122.314 | 58.16 | -122.321 | 122.1406 | 122.3094 | 122.2118 | 59.5142 | -122.5306
1185.5156 | 122.5067 | -59.3079 | 62.8738 | 1.4211e-13 | -0.00041233 | -0.0095086 | 0.039598 | -0.023362 | 0.047799 | 0.018923 | -0.01172 | 0.028194 | 0.043729 | 0.0017713 | 0.046151 | -59.1563 | -1.4042 | -59.3887 | 62.8768 | 62.8278 | 62.8917 | -59.4517 | -59.3436 | 0.009516 | -59.401 | 62.7275 | 62.8871 | 62.7987 | -59.6567 | -0.14385 | 0.002926 | 0.15156 | -0.080847 | 0.063001 | -0.046057 | 0.017873 | -0.34886 | -0.14636 | -0.03575 | -0.093149 | 0.25571 | 0.013236 | -0.075134 | 122.1846 | 122.1356 | 122.1996 | 57.9036 | -122.3255 | 122.0353 | 122.1949 | 122.1066 | 59.3174 | -122.5306
1187.2344 | 122.4197 | -59.2896 | 62.9242 | 1.4211e-13 | -0.00083973 | -0.0097224 | 0.038957 | -0.023362 | 0.048012 | 0.0036627 | -0.012148 | 0.027981 | 0.043943 | 0.0021987 | 0.045937 | -59.0647 | -1.4775 | -59.2971 | 62.9683 | 62.9239 | 62.9741 | -59.3556 | -59.2612 | 0.009516 | -59.3186 | 62.819 | 62.9741 | 62.8903 | -59.5697 | -0.066 | 0.04414 | 0.22482 | -0.007591 | 0.058409 | -0.000254 | 0.049934 | -0.28017 | -0.10515 | 0.028357 | -0.029042 | 0.25113 | 0.049876 | -0.033916 | 122.2579 | 122.2135 | 122.2637 | 57.8121 | -122.2797 | 122.1086 | 122.2636 | 122.1798 | 59.2991 | -122.4939
1188.9531 | 122.3877 | -59.2941 | 62.9471 | 1.4211e-13 | -0.00041233 | -0.009295 | 0.038957 | -0.022935 | 0.048012 | 0.018923 | -0.012148 | 0.028622 | 0.043943 | 0.0013439 | 0.045724 | -59.0281 | -1.5599 | -59.2514 | 63.005 | 62.9606 | 63.0245 | -59.3189 | -59.2291 | 0.004938 | -59.282 | 62.8511 | 63.0153 | 62.9269 | -59.5377 | -0.024792 | 0.057878 | 0.26602 | 0.042768 | 0.06756 | 0.013488 | 0.07741 | -0.24354 | -0.095984 | 0.064985 | 0.012165 | 0.25571 | 0.068194 | -0.020177 | 122.2991 | 122.2547 | 122.3186 | 57.7342 | -122.266 | 122.1452 | 122.3094 | 122.221 | 59.2991 | -122.4848
1190.6719 | 122.438 | -59.1843 | 63.0341 | 1.4211e-13 | -0.00083973 | -0.0095086 | 0.03917 | -0.023148 | 0.047585 | 0.011293 | -0.012575 | 0.028408 | 0.043943 | 0.0013439 | 0.045724 | -58.9274 | -1.656 | -59.169 | 63.0828 | 63.043 | 63.1069 | -59.2273 | -59.133 | 0.004938 | -59.1904 | 62.9472 | 63.1068 | 63.0185 | -59.4415 | -0.043076 | 0.048735 | 0.25688 | 0.015314 | 0.05839 | 0.008934 | 0.07285 | -0.25725 | -0.086811 | 0.051275 | -0.006124 | 0.25113 | 0.072791 | -0.015579 | 122.2671 | 122.2273 | 122.2912 | 57.5282 | -122.2614 | 122.1315 | 122.2911 | 122.2027 | 59.1892 | -122.4756
1192.4531 | 122.4518 | -59.0836 | 63.0936 | 1.4211e-13 | -0.00041233 | -0.0095086 | 0.039598 | -0.023148 | 0.048012 | 0.011293 | -0.011934 | 0.028194 | 0.043729 | 0.0015577 | 0.045724 | -58.8358 | -1.711 | -59.0682 | 63.1835 | 63.1437 | 63.1893 | -59.1403 | -59.046 | 0.009516 | -59.0988 | 63.0342 | 63.203 | 63.1055 | -59.3591 | -0.056785 | 0.089951 | 0.24774 | 0.015329 | 0.072114 | 0.050161 | 0.095756 | -0.27554 | -0.059329 | 0.037562 | -0.015258 | 0.26028 | 0.10943 | 0.011905 | 122.2671 | 122.2273 | 122.2729 | 57.3726 | -122.2339 | 122.1178 | 122.2866 | 122.189 | 59.0931 | -122.4527
1194.1875 | 122.438 | -59.0378 | 63.1622 | 1.4211e-13 | -0.00083973 | -0.0097224 | 0.038957 | -0.022935 | 0.048012 | 0.0036627 | -0.011934 | 0.028622 | 0.043943 | 0.0013439 | 0.045937 | -58.7763 | -1.8026 | -59.0179 | 63.2293 | 63.1895 | 63.2443 | -59.0991 | -58.9956 | 0.009516 | -59.0484 | 63.08 | 63.2442 | 63.1604 | -59.3042 | -0.06135 | 0.067071 | 0.26149 | 0.019914 | 0.081264 | 0.027287 | 0.082035 | -0.26637 | -0.082208 | 0.042152 | -0.010668 | 0.2557 | 0.081976 | -0.001816 | 122.2671 | 122.2273 | 122.282 | 57.2352 | -122.2614 | 122.1178 | 122.282 | 122.1982 | 59.0473 | -122.4664
1195.9688 | 122.4976 | -58.8181 | 63.3591 | 1.4211e-13 | -0.00062613 | -0.0095086 | 0.03917 | -0.022935 | 0.047585 | 0.018923 | -0.011934 | 0.028408 | 0.043943 | 0.0017713 | 0.04551 | -58.6298 | -1.8346 | -58.8714 | 63.3712 | 63.3269 | 63.3908 | -58.9389 | -58.8491 | 0.014095 | -58.9111 | 63.2265 | 63.3861 | 63.3024 | -59.1576 | -0.12082 | 0.012162 | 0.18827 | -0.053308 | 0.067507 | -0.032185 | 0.031711 | -0.33958 | -0.13254 | -0.031056 | -0.093034 | 0.24654 | 0.027074 | -0.056718 | 122.1893 | 122.1449 | 122.2088 | 56.9834 | -122.2979 | 122.0446 | 122.2042 | 122.1204 | 58.8321 | -122.5167
1197.7344 | 122.4152 | -58.7082 | 63.5422 | 1.4211e-13 | -0.00041233 | -0.0095086 | 0.039384 | -0.023148 | 0.048439 | 0.0036627 | -0.01172 | 0.028194 | 0.044157 | 0.0013439 | 0.045724 | -58.4604 | -1.9124 | -58.7065 | 63.5406 | 63.4963 | 63.5556 | -58.7832 | -58.6889 | 0.009516 | -58.7371 | 63.3868 | 63.5556 | 63.4626 | -58.9928 | -0.074995 | -0.001543 | 0.2478 | 0.001647 | 0.076642 | -0.045869 | 0.013436 | -0.2846 | -0.15539 | 0.019336 | -0.028906 | 0.2557 | 0.013377 | -0.079572 | 122.2488 | 122.2045 | 122.2638 | 56.7957 | -122.3254 | 122.095 | 122.2637 | 122.1708 | 58.7177 | -122.535
1199.4688 | 122.406 | -58.5526 | 63.6932 | 1.4211e-13 | -0.00062613 | -0.0097224 | 0.038957 | -0.023362 | 0.047799 | 0.0036627 | -0.012148 | 0.028408 | 0.043729 | 0.0013439 | 0.045937 | -58.3322 | -1.9994 | -58.5784 | 63.6597 | 63.6245 | 63.6884 | -58.6596 | -58.5607 | 0.009516 | -58.6089 | 63.5104 | 63.6929 | 63.5954 | -58.8692 | -0.107 | -0.033567 | 0.22036 | -0.025801 | 0.081203 | -0.068722 | -0.004847 | -0.31661 | -0.18284 | -0.0081 | -0.056342 | 0.26027 | -0.000327 | -0.097855 | 122.2122 | 122.1771 | 122.2409 | 56.5531 | -122.3528 | 122.063 | 122.2455 | 122.1479 | 58.5621 | -122.5624
1201.25 | 122.4518 | -58.5342 | 63.6475 | 1.4211e-13 | -0.00062613 | -0.009936 | 0.039384 | -0.023362 | 0.047799 | 0.0036627 | -0.011934 | 0.028408 | 0.043943 | 0.0015577 | 0.045937 | -58.2727 | -2.0773 | -58.5234 | 63.71 | 63.684 | 63.7342 | -58.5954 | -58.5011 | 0.009516 | -58.5677 | 63.5699 | 63.7433 | 63.6549 | -58.8096 | -0.061209 | 0.062572 | 0.26157 | 0.010828 | 0.072037 | 0.036581 | 0.086715 | -0.2754 | -0.077539 | 0.033113 | -0.033443 | 0.24195 | 0.095814 | 0.007443 | 122.2443 | 122.2183 | 122.2684 | 56.457 | -122.2429 | 122.1042 | 122.2775 | 122.1891 | 58.5438 | -122.4571
1203.0312 | 122.3602 | -58.5022 | 63.7665 | 1.4211e-13 | -0.00062613 | -0.0097224 | 0.03917 | -0.023148 | 0.048226 | 0.011293 | -0.011934 | 0.028408 | 0.04437 | 0.0013439 | 0.046151 | -58.2223 | -2.1551 | -58.4685 | 63.765 | 63.7253 | 63.7754 | -58.5497 | -58.4553 | 0.009516 | -58.5082 | 63.6203 | 63.7845 | 63.6961 | -58.7593 | -0.047463 | -0.001506 | 0.27989 | 0.033723 | 0.081186 | -0.041227 | 0.008905 | -0.25708 | -0.14619 | 0.046856 | -0.005964 | 0.25111 | 0.018003 | -0.070367 | 122.2672 | 122.2274 | 122.2776 | 56.3471 | -122.3161 | 122.1225 | 122.2867 | 122.1983 | 58.5117 | -122.5258
1204.7344 | 122.4792 | -58.4198 | 63.7527 | 1.4211e-13 | -0.00041233 | -0.0095086 | 0.03917 | -0.022935 | 0.047799 | 0.018923 | -0.012148 | 0.027981 | 0.043943 | 0.0017713 | 0.045937 | -58.1262 | -2.2421 | -58.3815 | 63.8565 | 63.8123 | 63.8715 | -58.4627 | -58.3683 | 0.004938 | -58.4303 | 63.6981 | 63.8806 | 63.7785 | -58.6677 | -0.042861 | 0.10379 | 0.29364 | 0.038314 | 0.081175 | 0.059504 | 0.11879 | -0.2479 | -0.054627 | 0.051454 | -0.010523 | 0.23737 | 0.12789 | 0.02578 | 122.2763 | 122.2321 | 122.2913 | 56.1777 | -122.2154 | 122.1179 | 122.3004 | 122.1983 | 58.4247 | -122.4204
1206.5156 | 122.493 | -58.3145 | 63.8535 | 1.4211e-13 | -0.00083973 | -0.0095086 | 0.039384 | -0.023148 | 0.048226 | 0.011293 | -0.011934 | 0.028194 | 0.044157 | 0.0013439 | 0.046151 | -58.0346 | -2.3383 | -58.2899 | 63.939 | 63.8901 | 63.9539 | -58.3802 | -58.2905 | 0.004938 | -58.3387 | 63.7851 | 63.9585 | 63.8655 | -58.5899 | -0.065726 | 0.085497 | 0.27992 | 0.024593 | 0.090319 | 0.036638 | 0.10049 | -0.27534 | -0.068343 | 0.024006 | -0.024235 | 0.25111 | 0.10501 | 0.012065 | 122.2535 | 122.2046 | 122.2685 | 55.9763 | -122.2337 | 122.0996 | 122.273 | 122.18 | 58.3195 | -122.4433
1208.2969 | 122.3648 | -58.2367 | 64.0411 | 1.4211e-13 | -0.00062613 | -0.0095086 | 0.039384 | -0.023148 | 0.047799 | 0.011293 | -0.011934 | 0.028835 | 0.043943 | 0.0015577 | 0.045937 | -57.943 | -2.439 | -58.1984 | 64.0259 | 63.9817 | 64.0318 | -58.2978 | -58.2035 | 0.004938 | -58.2563 | 63.8767 | 64.0455 | 63.9479 | -58.4983 | -0.061126 | -0.015197 | 0.29366 | 0.038339 | 0.099465 | -0.059466 | -0.009352 | -0.26159 | -0.16446 | 0.033182 | -0.019638 | 0.24195 | 0.004325 | -0.093203 | 122.2626 | 122.2184 | 122.2685 | 55.7977 | -122.339 | 122.1134 | 122.2822 | 122.1846 | 58.2416 | -122.5394
1210.0312 | 122.5159 | -58.1039 | 64.064 | 1.4211e-13 | -0.00083973 | -0.009295 | 0.039384 | -0.023148 | 0.047371 | 0.011293 | -0.011934 | 0.028622 | 0.043943 | 0.0015577 | 0.045937 | -57.8744 | -2.526 | -58.1251 | 64.0946 | 64.0549 | 64.1096 | -58.2246 | -58.1348 | 0.004938 | -58.1877 | 63.9499 | 64.1141 | 64.0212 | -58.425 | -0.12061 | 0.030591 | 0.22959 | -0.02116 | 0.099454 | -0.009092 | 0.045596 | -0.32108 | -0.11409 | -0.030888 | -0.083708 | 0.23737 | 0.050116 | -0.042834 | 122.1986 | 122.1589 | 122.2136 | 55.578 | -122.2886 | 122.0539 | 122.2181 | 122.1251 | 58.1089 | -122.489
1211.7969 | 122.3602 | -58.0719 | 64.2517 | 1.4211e-13 | -0.00062613 | -0.0095086 | 0.03917 | -0.023148 | 0.048012 | 0.011293 | -0.011934 | 0.028622 | 0.043943 | 0.0015577 | 0.045724 | -57.7782 | -2.6038 | -58.0335 | 64.177 | 64.1328 | 64.192 | -58.1376 | -58.0478 | 0.004938 | -58.1052 | 64.0232 | 64.192 | 64.1082 | -58.3472 | -0.065658 | -0.074681 | 0.29369 | 0.038362 | 0.10402 | -0.11893 | -0.059672 | -0.27528 | -0.22852 | 0.024063 | -0.033336 | 0.24194 | -0.059731 | -0.14352 | 122.2489 | 122.2047 | 122.2639 | 55.4681 | -122.3893 | 122.0951 | 122.2639 | 122.1801 | 58.0768 | -122.5989
1213.5938 | 122.374 | -58.0307 | 64.2288 | 1.4211e-13 | -0.00062613 | -0.009295 | 0.039384 | -0.023148 | 0.048012 | 0.011293 | -0.011934 | 0.028408 | 0.044157 | 0.0011303 | 0.046365 | -57.6821 | -2.6725 | -57.9557 | 64.2732 | 64.2335 | 64.2836 | -58.0506 | -57.9517 | 0.004938 | -58.0137 | 64.1148 | 64.2881 | 64.1952 | -58.2602 | -0.019857 | 0.044353 | 0.34864 | 0.074995 | 0.094852 | 0.004691 | 0.054788 | -0.22948 | -0.11406 | 0.079018 | 0.017041 | 0.24652 | 0.059308 | -0.033642 | 122.3039 | 122.2642 | 122.3143 | 55.3582 | -122.2794 | 122.1455 | 122.3188 | 122.2259 | 58.0356 | -122.489
1215.3125 | 122.4197 | -57.8751 | 64.357 | 1.4211e-13 | -0.00041233 | -0.0097224 | 0.039384 | -0.022935 | 0.048012 | 0.011293 | -0.011934 | 0.028408 | 0.043943 | 0.0017713 | 0.045937 | -57.6225 | -2.787 | -57.887 | 64.3281 | 64.2747 | 64.334 | -57.9956 | -57.9013 | 0.014095 | -57.9587 | 64.1697 | 64.3431 | 64.2547 | -58.2007 | -0.12055 | -0.02888 | 0.25252 | -0.011971 | 0.10858 | -0.082272 | -0.023022 | -0.3256 | -0.18729 | -0.026256 | -0.083655 | 0.24194 | -0.013923 | -0.10229 | 122.2032 | 122.1498 | 122.209 | 55.0881 | -122.3526 | 122.0448 | 122.2181 | 122.1298 | 57.8892 | -122.5577
1217.0781 | 122.406 | -57.8384 | 64.389 | 1.4211e-13 | -0.00041233 | -0.0097224 | 0.03917 | -0.023362 | 0.047585 | 0.0036627 | -0.01172 | 0.028194 | 0.043943 | 0.0017713 | 0.045724 | -57.5218 | -2.8923 | -57.7955 | 64.4197 | 64.3709 | 64.4347 | -57.9086 | -57.8052 | 0.000359 | -57.8671 | 64.2659 | 64.4392 | 64.3417 | -58.0953 | -0.070171 | 0.030645 | 0.31662 | 0.042974 | 0.11315 | -0.018158 | 0.045665 | -0.2569 | -0.12318 | 0.033276 | -0.028702 | 0.2282 | 0.050185 | -0.047343 | 122.2581 | 122.2093 | 122.2731 | 54.9462 | -122.2976 | 122.1043 | 122.2777 | 122.1801 | 57.8388 | -122.4844
1218.8438 | 122.3557 | -57.7103 | 64.5538 | 1.4211e-13 | -0.00019873 | -0.0097224 | 0.03917 | -0.023362 | 0.048226 | 0.0036627 | -0.011934 | 0.028408 | 0.043729 | 0.0017713 | 0.045937 | -57.3799 | -2.9609 | -57.649 | 64.5479 | 64.5128 | 64.5629 | -57.7621 | -57.677 | 0.004938 | -57.7252 | 64.3986 | 64.5628 | 64.4745 | -57.9763 | -0.051819 | -0.005956 | 0.33038 | 0.061305 | 0.11312 | -0.041006 | 0.00907 | -0.26603 | -0.1552 | 0.033306 | -0.014936 | 0.25109 | 0.009012 | -0.079359 | 122.2581 | 122.2231 | 122.2732 | 54.7493 | -122.3159 | 122.1089 | 122.2731 | 122.1847 | 57.7152 | -122.5301
1220.5781 | 122.3785 | -57.6965 | 64.5264 | 1.4211e-13 | -0.00083973 | -0.0097224 | 0.03917 | -0.022935 | 0.048226 | 0.011293 | -0.011934 | 0.028194 | 0.043943 | 0.0013439 | 0.045724 | -57.3295 | -3.0571 | -57.6123 | 64.5891 | 64.5495 | 64.6087 | -57.7209 | -57.6266 | 0.004938 | -57.6932 | 64.4307 | 64.5995 | 64.5157 | -57.9397 | -0.024342 | 0.062716 | 0.36701 | 0.084198 | 0.10854 | 0.023091 | 0.082322 | -0.24313 | -0.095688 | 0.069938 | 0.003382 | 0.24651 | 0.073107 | -0.010685 | 122.2856 | 122.246 | 122.3052 | 54.6394 | -122.2472 | 122.1272 | 122.296 | 122.2122 | 57.7015 | -122.466
1222.3594 | 122.4747 | -57.5226 | 64.6225 | 1.4211e-13 | -0.00083973 | -0.0095086 | 0.039598 | -0.022935 | 0.048226 | 0.0036627 | -0.011934 | 0.028408 | 0.044157 | 0.0021987 | 0.045937 | -57.2242 | -3.1258 | -57.5025 | 64.6944 | 64.6502 | 64.7094 | -57.6201 | -57.535 | 0.014095 | -57.5924 | 64.5406 | 64.7002 | 64.621 | -57.8252 | -0.097556 | 0.071888 | 0.29836 | 0.020127 | 0.11768 | 0.027697 | 0.086921 | -0.30261 | -0.081935 | -0.012437 | -0.069836 | 0.23278 | 0.077705 | -0.001509 | 122.217 | 122.1728 | 122.232 | 54.3968 | -122.2426 | 122.0631 | 122.2228 | 122.1436 | 57.5367 | -122.4477
1224.1406 | 122.374 | -57.5226 | 64.7461 | 1.4211e-13 | -0.00062613 | -0.0095086 | 0.03917 | -0.022935 | 0.047799 | 0.011293 | -0.01172 | 0.028194 | 0.043943 | 0.0015577 | 0.045724 | -57.1922 | -3.2677 | -57.4887 | 64.699 | 64.6639 | 64.7186 | -57.6064 | -57.5259 | 0.004938 | -57.5787 | 64.5543 | 64.7139 | 64.6301 | -57.816 | -0.083819 | -0.04713 | 0.33041 | 0.033861 | 0.11768 | -0.082163 | -0.027518 | -0.29345 | -0.19179 | -0.00328 | -0.0561 | 0.23735 | -0.032155 | -0.11595 | 122.2215 | 122.1865 | 122.2412 | 54.2549 | -122.3525 | 122.0769 | 122.2365 | 122.1527 | 57.5275 | -122.5621
1225.9219 | 122.3602 | -57.4493 | 64.8056 | 1.4211e-13 | -0.00041233 | -0.0095086 | 0.03917 | -0.023148 | 0.048226 | -0.0039678 | -0.01172 | 0.028408 | 0.04437 | 0.0013439 | 0.045937 | -57.0457 | -3.3318 | -57.3422 | 64.8455 | 64.7921 | 64.8559 | -57.4736 | -57.3839 | 0.004938 | -57.4413 | 64.6917 | 64.8559 | 64.7721 | -57.6833 | -0.024272 | 0.03987 | 0.40368 | 0.10712 | 0.1314 | -0.013462 | 0.050331 | -0.23391 | -0.11395 | 0.065418 | 0.008019 | 0.24193 | 0.050272 | -0.03352 | 122.2948 | 122.2415 | 122.3053 | 54.1175 | -122.2792 | 122.141 | 122.3052 | 122.2214 | 57.4543 | -122.4889
1227.7031 | 122.3877 | -56.8588 | 65.3229 | 1.4211e-13 | -0.00062613 | -0.009295 | 0.039384 | -0.023148 | 0.048012 | 0.018923 | -0.012148 | 0.028194 | 0.044157 | 0.0015577 | 0.046151 | -56.8808 | -3.3959 | -57.1911 | 64.992 | 64.9524 | 65.007 | -57.3179 | -57.2328 | 0.018674 | -57.2856 | 64.8382 | 65.0115 | 64.9186 | -57.5321 | -0.4591 | -0.33089 | -0.022017 | -0.33231 | 0.1268 | -0.37047 | -0.31585 | -0.67332 | -0.48471 | -0.374 | -0.42682 | 0.2465 | -0.31133 | -0.40428 | 121.8508 | 121.8112 | 121.8659 | 53.4629 | -122.6408 | 121.697 | 121.8704 | 121.7774 | 56.8775 | -122.855
1229.4219 | 122.3373 | -56.6711 | 65.5701 | 1.4211e-13 | -0.00062613 | -0.0097224 | 0.03917 | -0.023362 | 0.048012 | 0.0036627 | -0.012148 | 0.028408 | 0.043943 | 0.0015577 | 0.046578 | -56.2628 | -3.547 | -56.5685 | 65.6146 | 65.5706 | 65.616 | -56.7044 | -56.6193 | 0.014095 | -56.6858 | 65.4563 | 65.6251 | 65.5321 | -56.9049 | -0.033211 | 0.044574 | 0.40838 | 0.10266 | 0.13587 | 0.00049 | 0.045914 | -0.23371 | -0.11381 | 0.051865 | -0.014692 | 0.21902 | 0.055013 | -0.037937 | 122.2858 | 122.2417 | 122.2871 | 53.1241 | -122.2744 | 122.1274 | 122.2962 | 122.2033 | 56.6852 | -122.4749
1231.2188 | 122.3969 | -56.5063 | 65.744 | 1.4211e-13 | -0.00062613 | -0.0097224 | 0.03917 | -0.022935 | 0.048226 | 0.011293 | -0.012148 | 0.028622 | 0.043943 | 0.0017713 | 0.046151 | -56.0888 | -3.7988 | -56.4174 | 65.7749 | 65.7354 | 65.79 | -56.5395 | -56.4499 | 0.014095 | -56.521 | 65.6119 | 65.7853 | 65.7061 | -56.7446 | -0.033165 | 0.030866 | 0.41757 | 0.088944 | 0.12211 | -0.008619 | 0.04595 | -0.23824 | -0.13209 | 0.056482 | -0.014653 | 0.22359 | 0.041313 | -0.037901 | 122.2812 | 122.2417 | 122.2963 | 52.7075 | -122.2835 | 122.1183 | 122.2917 | 122.2125 | 56.5204 | -122.4886
1233 | 122.5067 | -56.1493 | 66.0095 | 1.4211e-13 | -0.00062613 | -0.0095086 | 0.03917 | -0.023362 | 0.048012 | -0.0039678 | -0.012148 | 0.028408 | 0.043943 | 0.0015577 | 0.046151 | -55.8461 | -3.9179 | -56.1702 | 66.0084 | 65.9643 | 66.0189 | -56.306 | -56.2301 | 0.009516 | -56.2829 | 65.8454 | 66.0188 | 65.9305 | -56.5111 | -0.15669 | -0.001138 | 0.30316 | -0.020885 | 0.13581 | -0.045175 | 0.009378 | -0.36178 | -0.16409 | -0.080796 | -0.13362 | 0.22817 | 0.009319 | -0.079051 | 122.1577 | 122.1136 | 122.1682 | 52.2314 | -122.3155 | 121.9947 | 122.1681 | 122.0798 | 56.1588 | -122.5206
1234.7656 | 122.3648 | -56.1081 | 66.1606 | 1.4211e-13 | -0.00041233 | -0.009295 | 0.039384 | -0.022721 | 0.048012 | -0.0039678 | -0.012148 | 0.028408 | 0.043943 | 0.0013439 | 0.045724 | -55.6859 | -4.0049 | -56.0237 | 66.1595 | 66.1063 | 66.1654 | -56.164 | -56.079 | 0.018674 | -56.141 | 65.9965 | 66.1654 | 66.077 | -56.3691 | -0.055948 | -0.001113 | 0.42221 | 0.084421 | 0.14037 | -0.05429 | 0.004831 | -0.26104 | -0.16406 | 0.029102 | -0.032875 | 0.22816 | 0.004773 | -0.083598 | 122.2676 | 122.2144 | 122.2735 | 52.1032 | -122.3246 | 122.1046 | 122.2734 | 122.1851 | 56.1268 | -122.5297
1236.5625 | 122.4289 | -56.044 | 66.1606 | 1.4211e-13 | -0.00019873 | -0.0095086 | 0.03917 | -0.022935 | 0.047799 | 0.011293 | -0.01172 | 0.028408 | 0.043516 | 0.0015577 | 0.046151 | -55.6172 | -4.1102 | -55.955 | 66.2098 | 66.1658 | 66.2204 | -56.0954 | -56.024 | 0.004938 | -56.0769 | 66.056 | 66.2295 | 66.1365 | -56.3004 | -0.051351 | 0.049249 | 0.4268 | 0.089008 | 0.14036 | 0.005236 | 0.059775 | -0.25644 | -0.10454 | 0.01996 | -0.03286 | 0.22358 | 0.068873 | -0.024076 | 122.2538 | 122.2098 | 122.2644 | 51.9338 | -122.2559 | 122.1001 | 122.2735 | 122.1805 | 56.0489 | -122.461
1238.2969 | 122.493 | -55.9845 | 66.1972 | 1.4211e-13 | -0.00083973 | -0.009295 | 0.03917 | -0.023148 | 0.048226 | 0.011293 | -0.012148 | 0.028408 | 0.043943 | 0.0017713 | 0.045937 | -55.5165 | -4.2246 | -55.868 | 66.3014 | 66.2528 | 66.3165 | -56.0129 | -55.9325 | 0.009516 | -55.999 | 66.1385 | 66.3119 | 66.2143 | -56.2226 | -0.028439 | 0.1042 | 0.46801 | 0.11649 | 0.14493 | 0.055613 | 0.1193 | -0.23811 | -0.058747 | 0.052025 | -0.014531 | 0.22358 | 0.11467 | 0.017138 | 122.2859 | 122.2373 | 122.301 | 51.7599 | -122.2101 | 122.123 | 122.2964 | 122.1988 | 55.994 | -122.4198
1240.0781 | 122.493 | -55.9387 | 66.2384 | 1.4211e-13 | -0.00062613 | -0.0090814 | 0.039384 | -0.023148 | 0.048012 | 0.018923 | -0.011934 | 0.028408 | 0.044157 | 0.0015577 | 0.045937 | -55.5256 | -4.3528 | -55.8863 | 66.2739 | 66.2253 | 66.2799 | -56.0404 | -55.9554 | 0.009516 | -56.0219 | 66.1201 | 66.289 | 66.196 | -56.2501 | -0.10169 | 0.035527 | 0.41308 | 0.052398 | 0.15409 | -0.013058 | 0.041476 | -0.31136 | -0.11826 | -0.016645 | -0.083201 | 0.22816 | 0.050575 | -0.042374 | 122.2127 | 122.1641 | 122.2186 | 51.5859 | -122.2788 | 122.0589 | 122.2277 | 122.1347 | 55.9482 | -122.4885
1241.7812 | 122.5113 | -55.9296 | 66.2704 | 1.4211e-13 | -0.00041233 | -0.009295 | 0.039384 | -0.023148 | 0.048226 | 0.0036627 | -0.012361 | 0.028408 | 0.043943 | 0.0013439 | 0.045937 | -55.4753 | -4.5039 | -55.8451 | 66.3106 | 66.2711 | 66.3302 | -55.9992 | -55.9233 | -0.00422 | -55.9807 | 66.1522 | 66.3256 | 66.2372 | -56.1997 | -0.069634 | 0.04011 | 0.45429 | 0.084446 | 0.15408 | 0.000687 | 0.059797 | -0.27015 | -0.11825 | 0.00625 | -0.051148 | 0.219 | 0.05516 | -0.033211 | 122.2401 | 122.2007 | 122.2598 | 51.4256 | -122.2696 | 122.0818 | 122.2552 | 122.1668 | 55.9253 | -122.4702
1243.5781 | 122.3648 | -55.8563 | 66.394 | 1.4211e-13 | -0.00062613 | -0.009295 | 0.039384 | -0.022935 | 0.047799 | 0.0036627 | -0.012148 | 0.028408 | 0.043729 | 0.0017713 | 0.046151 | -55.3746 | -4.6047 | -55.7536 | 66.393 | 66.3581 | 66.4081 | -55.9168 | -55.8317 | 0.004938 | -55.8846 | 66.2438 | 66.4126 | 66.3197 | -56.1173 | -0.060456 | -0.001075 | 0.48177 | 0.10277 | 0.16323 | -0.03591 | 0.014037 | -0.26097 | -0.15028 | 0.024583 | -0.028237 | 0.23273 | 0.018557 | -0.074392 | 122.2493 | 122.2145 | 122.2644 | 51.2517 | -122.3108 | 122.1001 | 122.2689 | 122.176 | 55.8613 | -122.5113
1245.2969 | 122.4426 | -55.8701 | 66.3345 | 1.4211e-13 | -0.00041233 | -0.009295 | 0.03917 | -0.022721 | 0.048012 | 0.0036627 | -0.01172 | 0.028622 | 0.044157 | 0.0017713 | 0.046151 | -55.4341 | -4.7832 | -55.8222 | 66.3334 | 66.2895 | 66.344 | -55.9763 | -55.9004 | 0.000359 | -55.967 | 66.1705 | 66.3439 | 66.2464 | -56.1906 | -0.10625 | -0.001085 | 0.43598 | 0.047829 | 0.15408 | -0.045084 | 0.009446 | -0.3205 | -0.16403 | -0.030365 | -0.096921 | 0.22358 | 0.009387 | -0.088141 | 122.2035 | 122.1595 | 122.214 | 51.0868 | -122.3108 | 122.0406 | 122.214 | 122.1164 | 55.8704 | -122.5251
1247.0781 | 122.3419 | -56.044 | 66.2384 | 1.4211e-13 | -0.00041233 | -0.009295 | 0.039384 | -0.023148 | 0.048226 | 0.018923 | -0.01172 | 0.028194 | 0.043943 | 0.0017713 | 0.045937 | -55.4799 | -4.971 | -55.8955 | 66.251 | 66.207 | 66.2661 | -56.0633 | -55.9783 | 0.014095 | -56.0402 | 66.0973 | 66.2615 | 66.1686 | -56.273 | -0.019298 | 0.012635 | 0.56415 | 0.14853 | 0.16782 | -0.031374 | 0.027741 | -0.22897 | -0.14115 | 0.065747 | 0.00377 | 0.23274 | 0.023103 | -0.069846 | 122.295 | 122.251 | 122.3101 | 51.0731 | -122.3017 | 122.1413 | 122.3055 | 122.2126 | 56.0581 | -122.5114
1248.7812 | 122.319 | -55.8517 | 66.3803 | 1.4211e-13 | -0.00062613 | -0.0090814 | 0.039598 | -0.023148 | 0.048012 | 0.011293 | -0.012361 | 0.028408 | 0.04437 | 0.0013439 | 0.045724 | -55.2601 | -5.0717 | -55.6803 | 66.4662 | 66.4177 | 66.4859 | -55.8481 | -55.7676 | 0.018674 | -55.8296 | 66.3079 | 66.4767 | 66.3883 | -56.0486 | 0.003651 | 0.085912 | 0.59165 | 0.17144 | 0.16779 | 0.037349 | 0.10561 | -0.19687 | -0.072448 | 0.084108 | 0.02213 | 0.219 | 0.096391 | 0.00802 | 122.318 | 122.2694 | 122.3377 | 50.7801 | -122.2284 | 122.1596 | 122.3284 | 122.2401 | 55.8704 | -122.4289
1250.5781 | 122.4701 | -52.977 | 69.191 | 1.4211e-13 | -0.00062613 | -0.009295 | 0.039384 | -0.022935 | 0.048012 | 0.011293 | -0.011934 | 0.028194 | 0.044157 | 0.0013439 | 0.046151 | -52.5726 | -4.5726 | -52.9883 | 69.1675 | 69.1192 | 69.1644 | -53.1374 | -53.0799 | 0.027831 | -53.1465 | 69 | 69.1781 | 69.0851 | -53.338 | -0.16038 | -0.023508 | 0.40441 | -0.011282 | 0.1491 | -0.071754 | -0.02658 | -0.36096 | -0.19096 | -0.10295 | -0.1695 | 0.19146 | -0.012903 | -0.10585 | 122.1445 | 122.0962 | 122.1414 | 48.4044 | -122.3284 | 121.977 | 122.1551 | 122.0621 | 53.0048 | -122.5289
1252.2812 | 122.3328 | -51.9928 | 70.2942 | 1.4211e-13 | -0.00062613 | -0.0095086 | 0.03917 | -0.022935 | 0.048226 | 0.018923 | -0.011934 | 0.028622 | 0.04437 | 0.0011303 | 0.045937 | -51.4234 | -4.4353 | -51.8391 | 70.3166 | 70.2685 | 70.3182 | -52.0018 | -51.9444 | 0.03241 | -52.011 | 70.1446 | 70.3273 | 70.2435 | -52.1978 | -0.009 | 0.022457 | 0.56939 | 0.15367 | 0.16268 | -0.025654 | 0.024018 | -0.20503 | -0.14955 | 0.048382 | -0.018174 | 0.18685 | 0.033116 | -0.050676 | 122.3094 | 122.2613 | 122.311 | 47.5575 | -122.296 | 122.1374 | 122.3201 | 122.2363 | 52.0252 | -122.492
1254.0625 | 122.3602 | -51.2558 | 71.022 | 1.4211e-13 | -0.00062613 | -0.009295 | 0.039384 | -0.022935 | 0.048226 | -0.0039678 | -0.011934 | 0.028194 | 0.044157 | 0.0015577 | 0.045724 | -50.7275 | -4.4169 | -51.1478 | 71.0126 | 70.9554 | 71.005 | -51.3104 | -51.2485 | 0.023253 | -51.3242 | 70.8406 | 71.0141 | 70.9166 | -51.5064 | -0.054583 | -0.009473 | 0.52831 | 0.10799 | 0.16258 | -0.06666 | -0.017037 | -0.25063 | -0.18146 | 0.007346 | -0.068367 | 0.18226 | -0.007938 | -0.10547 | 122.2684 | 122.2112 | 122.2608 | 46.8389 | -122.3324 | 122.0964 | 122.2699 | 122.1724 | 51.2791 | -122.5285
1255.8281 | 122.3328 | -49.8734 | 72.4182 | 1.4211e-13 | -0.00041233 | -0.0088676 | 0.039811 | -0.023148 | 0.047799 | 0.0036627 | -0.011934 | 0.028622 | 0.044157 | 0.0015577 | 0.045937 | -49.3723 | -4.2155 | -49.7972 | 72.3586 | 72.3107 | 72.3603 | -49.9642 | -49.9069 | 0.041567 | -49.9826 | 72.1867 | 72.3648 | 72.2764 | -50.1511 | -0.090825 | -0.059606 | 0.50106 | 0.076142 | 0.16697 | -0.10748 | -0.05795 | -0.27774 | -0.23156 | -0.033538 | -0.10925 | 0.16849 | -0.05343 | -0.1418 | 122.232 | 122.1841 | 122.2336 | 45.6579 | -122.3824 | 122.06 | 122.2381 | 122.1498 | 49.9149 | -122.5693
1257.5469 | 122.4838 | -49.4705 | 72.7112 | 1.4211e-13 | -0.00083973 | -0.0095086 | 0.039598 | -0.022935 | 0.047799 | 0.0036627 | -0.011934 | 0.028408 | 0.043943 | 0.0015577 | 0.045724 | -48.9648 | -4.2567 | -49.3989 | 72.7523 | 72.7091 | 72.7586 | -49.5567 | -49.5177 | 0.046146 | -49.5888 | 72.5804 | 72.7585 | 72.6656 | -49.7573 | -0.086133 | 0.041167 | 0.50571 | 0.07162 | 0.15775 | -0.00208 | 0.04742 | -0.2868 | -0.13078 | -0.047179 | -0.11831 | 0.16848 | 0.047361 | -0.045588 | 122.2229 | 122.1796 | 122.2291 | 45.2138 | -122.2678 | 122.0509 | 122.2291 | 122.1361 | 49.5167 | -122.4685
1259.3125 | 122.438 | -48.4085 | 73.7869 | 1.4211e-13 | -0.00062613 | -0.009295 | 0.039384 | -0.023362 | 0.048012 | 0.0036627 | -0.011934 | 0.028622 | 0.043729 | 0.0017713 | 0.045937 | -47.9438 | -4.1376 | -48.3917 | 73.7733 | 73.721 | 73.7613 | -48.5493 | -48.5058 | 0.050725 | -48.5815 | 73.5968 | 73.7796 | 73.6775 | -48.7362 | -0.14078 | -0.013597 | 0.46468 | 0.01683 | 0.15761 | -0.065882 | -0.02561 | -0.32773 | -0.1901 | -0.097297 | -0.17301 | 0.15472 | -0.007354 | -0.10946 | 122.1818 | 122.1296 | 122.1698 | 44.2709 | -122.3362 | 122.0053 | 122.1881 | 122.086 | 48.4592 | -122.5232
1261.0938 | 122.3373 | -47.6028 | 74.6704 | 1.4211e-13 | -0.00062613 | -0.009295 | 0.039598 | -0.023148 | 0.047799 | 0.011293 | -0.012148 | 0.028835 | 0.044584 | 0.0017713 | 0.045937 | -46.9045 | -4.0186 | -47.3616 | 74.8035 | 74.7513 | 74.7961 | -47.5465 | -47.4893 | 0.046146 | -47.565 | 74.6224 | 74.8098 | 74.7168 | -47.7106 | 0.056339 | 0.13306 | 0.69831 | 0.24128 | 0.18494 | 0.080892 | 0.12567 | -0.10774 | -0.048 | 0.11351 | 0.037799 | 0.14554 | 0.13935 | 0.046398 | 122.4063 | 122.3541 | 122.3989 | 43.5842 | -122.2169 | 122.2253 | 122.4126 | 122.3197 | 47.649 | -122.381
1262.8125 | 122.3419 | -46.5729 | 75.6775 | 1.4211e-13 | -0.00062613 | -0.009295 | 0.039598 | -0.023148 | 0.047799 | 0.0036627 | -0.011934 | 0.028622 | 0.043943 | 0.0013439 | 0.046151 | -45.9385 | -3.8858 | -46.4047 | 75.7603 | 75.7037 | 75.7484 | -46.5666 | -46.537 | 0.046146 | -46.6081 | 75.5747 | 75.7621 | 75.6646 | -46.749 | 0.006261 | 0.082859 | 0.63438 | 0.16817 | 0.16191 | 0.026228 | 0.070939 | -0.17616 | -0.10275 | 0.035917 | -0.035218 | 0.14094 | 0.084617 | -0.012911 | 122.3332 | 122.2766 | 122.3213 | 42.687 | -122.2441 | 122.1476 | 122.335 | 122.2375 | 46.619 | -122.4265
1264.6094 | 122.374 | -46.4264 | 75.8194 | 1.4211e-13 | -0.00062613 | -0.0090814 | 0.039384 | -0.023148 | 0.047799 | 0.0036627 | -0.01172 | 0.028194 | 0.043943 | 0.0015577 | 0.045724 | -45.8515 | -4.0736 | -46.3269 | 75.8244 | 75.7724 | 75.8125 | -46.4979 | -46.4637 | 0.041567 | -46.5486 | 75.648 | 75.8308 | 75.7333 | -46.6804 | -0.071539 | 0.00505 | 0.57489 | 0.099518 | 0.17106 | -0.046995 | -0.006867 | -0.25396 | -0.1714 | -0.037308 | -0.12218 | 0.13178 | 0.011389 | -0.086139 | 122.2508 | 122.1988 | 122.2389 | 42.3528 | -122.3173 | 122.0744 | 122.2572 | 122.1596 | 46.468 | -122.4997
1266.3438 | 122.4472 | -45.9961 | 76.1581 | 1.4211e-13 | -0.00041233 | -0.0090814 | 0.039384 | -0.023148 | 0.048226 | 0.0036627 | -0.01172 | 0.028408 | 0.043943 | 0.0013439 | 0.045937 | -45.2929 | -4.1056 | -45.7729 | 76.383 | 76.3265 | 76.3665 | -45.9439 | -45.9234 | 0.03241 | -46.0083 | 76.1837 | 76.3802 | 76.2781 | -46.1401 | 0.052213 | 0.22487 | 0.70315 | 0.22319 | 0.17098 | 0.16831 | 0.2084 | -0.14396 | 0.025535 | 0.072682 | -0.012189 | 0.13177 | 0.22208 | 0.11997 | 122.3791 | 122.3225 | 122.3626 | 41.8905 | -122.102 | 122.1798 | 122.3763 | 122.2742 | 46.0285 | -122.2982
1268.1094 | 122.4518 | -45.3964 | 76.7899 | 1.4211e-13 | -0.00041233 | -0.0090814 | 0.039598 | -0.023148 | 0.048012 | 0.018923 | -0.011507 | 0.028408 | 0.043943 | 0.0015577 | 0.045724 | -44.8397 | -4.33 | -45.3288 | 76.7996 | 76.7477 | 76.7878 | -45.5135 | -45.4976 | 0.046146 | -45.5733 | 76.6186 | 76.8106 | 76.7085 | -45.6959 | -0.11704 | 0.009787 | 0.55674 | 0.067615 | 0.18465 | -0.042143 | -0.002084 | -0.29948 | -0.17122 | -0.10117 | -0.17688 | 0.1226 | 0.020751 | -0.081356 | 122.1961 | 122.1441 | 122.1842 | 41.0665 | -122.3033 | 122.0151 | 122.207 | 122.1049 | 45.4426 | -122.4858
1269.7969 | 122.4655 | -45.1355 | 77.0691 | 1.4211e-13 | -0.00062613 | -0.0095086 | 0.03917 | -0.022935 | 0.048012 | 0.018923 | -0.011934 | 0.028408 | 0.044157 | 0.0017713 | 0.045937 | -44.7023 | -4.481 | -45.2006 | 76.9187 | 76.8668 | 76.9068 | -45.399 | -45.3877 | 0.027831 | -45.4588 | 76.7377 | 76.9205 | 76.8275 | -45.586 | -0.26349 | -0.15041 | 0.43317 | -0.065119 | 0.19837 | -0.20233 | -0.16228 | -0.45052 | -0.33142 | -0.25221 | -0.32334 | 0.12718 | -0.1486 | -0.24155 | 122.0542 | 122.0023 | 122.0423 | 40.6545 | -122.4681 | 121.8732 | 122.056 | 121.963 | 45.1633 | -122.6551
1271.5781 | 122.4655 | -44.014 | 78.1631 | 1.4211e-13 | -0.00041233 | -0.0090814 | 0.039598 | -0.022935 | 0.047799 | 0.0036627 | -0.012148 | 0.028622 | 0.043943 | 0.0017713 | 0.046151 | -43.37 | -4.2842 | -43.8638 | 78.2464 | 78.1992 | 78.2255 | -44.0665 | -44.0553 | 0.046146 | -44.1402 | 78.0609 | 78.2529 | 78.1508 | -44.2627 | -0.052545 | 0.083267 | 0.64396 | 0.15022 | 0.20276 | 0.036085 | 0.062306 | -0.24876 | -0.10229 | -0.041322 | -0.12619 | 0.12257 | 0.089719 | -0.012387 | 122.2604 | 122.2132 | 122.2394 | 39.7298 | -122.2297 | 122.0748 | 122.2668 | 122.1647 | 44.0601 | -122.4259
1273.3594 | 122.3419 | -43.428 | 78.8498 | 1.4211e-13 | -0.00041233 | -0.009295 | 0.039598 | -0.022721 | 0.048226 | 0.011293 | -0.011507 | 0.028194 | 0.044157 | 0.0015577 | 0.04551 | -42.7199 | -4.2475 | -43.2274 | 78.8782 | 78.822 | 78.8573 | -43.4484 | -43.4326 | 0.036989 | -43.5129 | 78.6835 | 78.8801 | 78.7826 | -43.6309 | -0.020327 | 0.028439 | 0.70815 | 0.20066 | 0.22099 | -0.027826 | 0.007508 | -0.20282 | -0.16626 | -0.004554 | -0.084846 | 0.11797 | 0.030343 | -0.067185 | 122.3063 | 122.25 | 122.2853 | 39.1805 | -122.2982 | 122.1116 | 122.3082 | 122.2106 | 43.465 | -122.4807
1275.0625 | 122.4609 | -42.9474 | 79.2709 | 1.4211e-13 | -0.00019873 | -0.0090814 | 0.039811 | -0.023148 | 0.048226 | -0.0039678 | -0.01172 | 0.028194 | 0.043943 | 0.0017713 | 0.045937 | -42.3674 | -4.3071 | -42.8977 | 79.2125 | 79.1425 | 79.187 | -43.1187 | -43.1121 | 0.036989 | -43.197 | 79.0178 | 79.2052 | 79.1077 | -43.292 | -0.1713 | -0.058481 | 0.58003 | 0.049647 | 0.22094 | -0.12844 | -0.083975 | -0.34464 | -0.25317 | -0.1647 | -0.24957 | 0.095073 | -0.065719 | -0.16325 | 122.1598 | 122.0899 | 122.1343 | 38.6403 | -122.3896 | 121.9652 | 122.1526 | 122.0551 | 42.9844 | -122.563
1276.8281 | 122.4609 | -43.396 | 78.7903 | 1.4211e-13 | -0.00019873 | -0.0088676 | 0.039384 | -0.022935 | 0.048226 | 0.011293 | -0.01172 | 0.028622 | 0.044157 | 0.0013439 | 0.045724 | -42.6329 | -4.6138 | -43.1724 | 78.9103 | 78.8494 | 78.8802 | -43.4117 | -43.4051 | 0.036989 | -43.49 | 78.711 | 78.903 | 78.7918 | -43.5988 | -0.01574 | 0.12 | 0.7631 | 0.22356 | 0.2393 | 0.059157 | 0.08991 | -0.20281 | -0.079277 | -0.009126 | -0.093997 | 0.10882 | 0.11275 | 0.001481 | 122.3063 | 122.2454 | 122.2762 | 38.7822 | -122.202 | 122.107 | 122.299 | 122.1878 | 43.433 | -122.3891
1278.625 | 122.4014 | -42.8375 | 79.3304 | 1.4211e-13 | -0.00041233 | -0.008654 | 0.039384 | -0.022935 | 0.048012 | 0.011293 | -0.01172 | 0.028622 | 0.044157 | 0.0017713 | 0.045937 | -42.0926 | -4.5818 | -42.6276 | 79.4276 | 79.376 | 79.4067 | -42.8943 | -42.8877 | 0.041567 | -42.9726 | 79.2375 | 79.4296 | 79.3275 | -43.0722 | -0.056793 | 0.097194 | 0.74487 | 0.2099 | 0.26669 | 0.045572 | 0.076289 | -0.23472 | -0.092911 | -0.050204 | -0.13508 | 0.099646 | 0.099123 | -0.002983 | 122.2652 | 122.2135 | 122.2443 | 38.2557 | -122.2248 | 122.0751 | 122.2671 | 122.165 | 42.8791 | -122.4027
1280.4062 | 122.4014 | -43.9362 | 78.2913 | 1.4211e-13 | -0.00062613 | -0.0090814 | 0.039384 | -0.022721 | 0.048439 | 0.011293 | -0.011507 | 0.028194 | 0.043943 | 0.0015577 | 0.046151 | -43.1457 | -5.1083 | -43.7081 | 78.3334 | 78.2725 | 78.317 | -43.9933 | -43.982 | 0.041567 | -44.0669 | 78.1387 | 78.3261 | 78.224 | -44.1712 | -0.057102 | 0.042082 | 0.79048 | 0.22806 | 0.28516 | -0.018826 | 0.025704 | -0.235 | -0.15263 | -0.045882 | -0.13075 | 0.10425 | 0.034803 | -0.067304 | 122.2696 | 122.2087 | 122.2532 | 38.8278 | -122.2846 | 122.0749 | 122.2623 | 122.1602 | 43.9777 | -122.4625
1282.125 | 122.3785 | -43.2129 | 78.9871 | 1.4211e-13 | -0.00019873 | -0.008654 | 0.039384 | -0.022935 | 0.048226 | 0.011293 | -0.011934 | 0.028408 | 0.043943 | 0.0013439 | 0.045937 | -42.4681 | -5.0625 | -43.0534 | 78.979 | 78.9181 | 78.9626 | -43.3476 | -43.341 | 0.036989 | -43.4167 | 78.7888 | 78.9717 | 78.8742 | -43.5255 | -0.13474 | -0.008166 | 0.74481 | 0.15949 | 0.29423 | -0.068999 | -0.024514 | -0.31266 | -0.19828 | -0.12813 | -0.20384 | 0.10881 | -0.015415 | -0.11294 | 122.1918 | 122.131 | 122.1755 | 38.1504 | -122.3348 | 122.0017 | 122.1846 | 122.0871 | 43.2499 | -122.5127
1283.8906 | 122.4564 | -42.8009 | 79.3625 | 1.4211e-13 | -0.00019873 | -0.0088676 | 0.039384 | -0.022935 | 0.048439 | 0.011293 | -0.011934 | 0.028622 | 0.043943 | 0.0011303 | 0.045937 | -42.0057 | -5.0625 | -42.6093 | 79.4047 | 79.344 | 79.3884 | -42.9218 | -42.9106 | 0.036989 | -42.9955 | 79.2192 | 79.4067 | 79.3046 | -43.0906 | -0.12089 | 0.042258 | 0.79524 | 0.19159 | 0.31248 | -0.018525 | 0.02593 | -0.28966 | -0.14327 | -0.10972 | -0.19459 | 0.095068 | 0.044186 | -0.05792 | 122.2056 | 122.1449 | 122.1893 | 37.7384 | -122.2843 | 122.0201 | 122.2076 | 122.1055 | 42.8379 | -122.453
1285.6719 | 122.3236 | -42.5583 | 79.6555 | 1.4211e-13 | -0.00019873 | -0.0088676 | 0.039811 | -0.022935 | 0.048226 | 0.0036627 | -0.01172 | 0.028408 | 0.04437 | 0.0017713 | 0.045937 | -41.5799 | -5.0808 | -42.1927 | 79.7985 | 79.7423 | 79.7913 | -42.528 | -42.5169 | 0.050725 | -42.6063 | 79.613 | 79.8004 | 79.6983 | -42.6876 | 0.030286 | 0.14303 | 0.97842 | 0.3656 | 0.33532 | 0.086873 | 0.13588 | -0.12933 | -0.042488 | 0.041437 | -0.048013 | 0.081322 | 0.14498 | 0.04287 | 122.3568 | 122.3006 | 122.3496 | 37.4774 | -122.1835 | 122.1713 | 122.3587 | 122.2566 | 42.609 | -122.3431
1287.4062 | 122.3236 | -42.2928 | 79.9622 | 1.4211e-13 | -0.00041233 | -0.0088676 | 0.039598 | -0.022935 | 0.048439 | 0.011293 | -0.01172 | 0.028622 | 0.04437 | 0.0013439 | 0.045937 | -41.5478 | -5.2503 | -42.1835 | 79.7939 | 79.7423 | 79.7684 | -42.528 | -42.5352 | 0.064461 | -42.6063 | 79.6038 | 79.7913 | 79.6937 | -42.7014 | -0.23522 | -0.16825 | 0.74496 | 0.10926 | 0.34447 | -0.21983 | -0.19372 | -0.40857 | -0.35835 | -0.24238 | -0.31352 | 0.095059 | -0.17088 | -0.26841 | 122.0867 | 122.0351 | 122.0612 | 37.0425 | -122.4902 | 121.8966 | 122.0841 | 121.9865 | 42.3572 | -122.6635
1289.1875 | 122.3007 | -41.8442 | 80.4199 | 1.4211e-13 | -0.00041233 | -0.0088676 | 0.039598 | -0.022721 | 0.048439 | 0.0036627 | -0.011934 | 0.028408 | 0.04437 | 0.0015577 | 0.045724 | -40.8015 | -5.1404 | -41.4418 | 80.5081 | 80.4612 | 80.4873 | -41.8045 | -41.8163 | 0.041567 | -41.8966 | 80.3226 | 80.5239 | 80.4126 | -41.9871 | 0.039644 | 0.088216 | 1.0426 | 0.40233 | 0.36268 | 0.041299 | 0.067361 | -0.14289 | -0.097286 | 0.027868 | -0.052425 | 0.090463 | 0.10393 | -0.007333 | 122.3523 | 122.3054 | 122.3315 | 36.7038 | -122.2245 | 122.1668 | 122.368 | 122.2568 | 41.8857 | -122.407
1290.9688 | 122.319 | -41.153 | 81.134 | 1.4211e-13 | -0.00019873 | -0.0090814 | 0.040025 | -0.022935 | 0.048653 | 0.0036627 | -0.011934 | 0.028408 | 0.04437 | 0.0013439 | 0.046151 | -40.1423 | -5.0305 | -40.81 | 81.1354 | 81.0748 | 81.1146 | -41.191 | -41.189 | 0.050725 | -41.2785 | 80.9407 | 81.1282 | 81.0307 | -41.3689 | -0.038004 | 0.001344 | 1.0107 | 0.34291 | 0.38091 | -0.059236 | -0.019481 | -0.21597 | -0.1933 | -0.036072 | -0.12552 | 0.090449 | -0.005804 | -0.10333 | 122.2883 | 122.2278 | 122.2675 | 36.1225 | -122.325 | 122.0937 | 122.2812 | 122.1837 | 41.2037 | -122.503
1292.6875 | 122.3785 | -41.2857 | 80.9601 | 1.4211e-13 | -0.00041233 | -0.008654 | 0.039811 | -0.022721 | 0.048439 | 0.0036627 | -0.01172 | 0.028194 | 0.043943 | 0.0013439 | 0.045724 | -40.1514 | -5.1816 | -40.8284 | 81.085 | 81.0336 | 81.0596 | -41.2459 | -41.244 | 0.041567 | -41.338 | 80.8904 | 81.0916 | 80.9758 | -41.4101 | 0.039801 | 0.12493 | 1.1343 | 0.45735 | 0.41755 | 0.073504 | 0.099525 | -0.12443 | -0.069713 | 0.041735 | -0.052293 | 0.072135 | 0.13152 | 0.015675 | 122.3707 | 122.3193 | 122.3453 | 36.1041 | -122.206 | 122.1761 | 122.3773 | 122.2615 | 41.3273 | -122.3702
1294.4688 | 122.4014 | -35.463 | 86.7783 | 1.4211e-13 | -0.00019873 | -0.008654 | 0.039811 | -0.022721 | 0.048439 | 0.0036627 | -0.01172 | 0.028835 | 0.043943 | 0.0013439 | 0.045724 | -34.4971 | -3.2906 | -35.1604 | 86.7943 | 86.7343 | 86.7645 | -35.5268 | -35.5938 | 0.082776 | -35.6558 | 86.5906 | 86.7965 | 86.6853 | -35.6958 | -0.063876 | 0.016005 | 0.96585 | 0.30251 | 0.36638 | -0.043911 | -0.013712 | -0.23282 | -0.18766 | -0.13089 | -0.19287 | 0.03995 | 0.01828 | -0.092984 | 122.2572 | 122.1973 | 122.2275 | 32.1723 | -122.3051 | 122.0535 | 122.2595 | 122.1482 | 35.5457 | -122.474
1296.2031 | 122.374 | -35.3531 | 86.8835 | 1.4211e-13 | 1.487e-05 | -0.0084402 | 0.040025 | -0.022935 | 0.048439 | 0.018923 | -0.011934 | 0.028835 | 0.044157 | 0.0013439 | 0.045724 | -34.401 | -3.3547 | -35.078 | 86.8538 | 86.7893 | 86.8195 | -35.4765 | -35.5481 | 0.082776 | -35.6146 | 86.6501 | 86.8469 | 86.7402 | -35.6408 | -0.12337 | -0.029762 | 0.95213 | 0.27505 | 0.39842 | -0.09425 | -0.064055 | -0.28774 | -0.23343 | -0.19497 | -0.26152 | 0.026212 | -0.036642 | -0.14333 | 122.2069 | 122.1424 | 122.1726 | 31.9984 | -122.36 | 122.0032 | 122.2 | 122.0933 | 35.4359 | -122.5244
1297.9688 | 122.4426 | -35.0739 | 87.1033 | 1.4211e-13 | -0.00041233 | -0.0084402 | 0.039811 | -0.022721 | 0.048653 | 0.011293 | -0.011934 | 0.028835 | 0.044157 | 0.0015577 | 0.045724 | -34.021 | -3.3272 | -34.7301 | 87.1788 | 87.119 | 87.1537 | -35.1514 | -35.2184 | 0.082776 | -35.2895 | 86.9706 | 87.1766 | 87.0607 | -35.3157 | -0.077503 | 0.075578 | 1.0529 | 0.34376 | 0.42127 | 0.015706 | 0.050457 | -0.24188 | -0.13266 | -0.14454 | -0.21567 | 0.026205 | 0.073292 | -0.042551 | 122.2527 | 122.1928 | 122.2276 | 31.7466 | -122.2546 | 122.0445 | 122.2504 | 122.1346 | 35.1566 | -122.419
1299.6719 | 122.4152 | -34.8267 | 87.3734 | 1.4211e-13 | -0.00019873 | -0.0084402 | 0.039811 | -0.022935 | 0.048439 | 0.011293 | -0.01172 | 0.028622 | 0.043729 | 0.0019849 | 0.04551 | -33.7691 | -3.3272 | -34.492 | 87.394 | 87.325 | 87.3552 | -34.9361 | -34.9803 | 0.082776 | -35.0697 | 87.1812 | 87.3918 | 87.2759 | -35.1051 | -0.10949 | 0.020681 | 1.0575 | 0.33464 | 0.44413 | -0.048323 | -0.018165 | -0.27844 | -0.19213 | -0.15364 | -0.24309 | 0.035358 | 0.018405 | -0.097437 | 122.2207 | 122.1517 | 122.1818 | 31.4994 | -122.3095 | 122.0079 | 122.2184 | 122.1026 | 34.9094 | -122.4785
1301.4688 | 122.3328 | -34.584 | 87.6663 | 1.4211e-13 | 1.487e-05 | -0.0084402 | 0.040025 | -0.022507 | 0.048653 | -0.0039678 | -0.012148 | 0.027981 | 0.04437 | 0.0013439 | 0.045937 | -33.3983 | -3.3089 | -34.1395 | 87.7145 | 87.6456 | 87.6757 | -34.6202 | -34.6506 | 0.078197 | -34.7584 | 87.5017 | 87.7123 | 87.5873 | -34.7846 | -0.036156 | 0.048199 | 1.1858 | 0.44455 | 0.48071 | -0.020767 | 0.009368 | -0.20054 | -0.1646 | -0.066584 | -0.17435 | 0.026193 | 0.045938 | -0.079061 | 122.2986 | 122.2296 | 122.2597 | 31.2751 | -122.2865 | 122.0858 | 122.2963 | 122.1713 | 34.6622 | -122.4509
1303.1875 | 122.3282 | -33.522 | 88.7741 | 1.4211e-13 | 0.00044227 | -0.0088676 | 0.040025 | -0.022721 | 0.048653 | 0.0036627 | -0.011934 | 0.028408 | 0.044157 | 0.0013439 | 0.045937 | -32.2812 | -3.0159 | -33.0315 | 88.8088 | 88.7445 | 88.7791 | -33.5258 | -33.5701 | 0.087354 | -33.6641 | 88.596 | 88.802 | 88.6907 | -33.6948 | -0.003804 | 0.034646 | 1.2409 | 0.49049 | 0.49429 | -0.029613 | 0.005023 | -0.17279 | -0.17813 | -0.048019 | -0.14205 | 0.030746 | 0.027858 | -0.083406 | 122.3308 | 122.2665 | 122.3012 | 30.5061 | -122.2999 | 122.118 | 122.324 | 122.2127 | 33.6094 | -122.4689
1304.9531 | 122.4518 | -32.9453 | 89.2227 | 1.4211e-13 | 1.487e-05 | -0.0082266 | 0.040239 | -0.022721 | 0.048653 | 0.018923 | -0.011507 | 0.028408 | 0.043943 | 0.0013439 | 0.04551 | -31.8508 | -2.9655 | -32.6332 | 89.1888 | 89.1154 | 89.15 | -33.1458 | -33.1809 | 0.087354 | -33.2932 | 88.9806 | 89.1728 | 89.0616 | -33.3056 | -0.20054 | -0.033956 | 1.0945 | 0.31201 | 0.51255 | -0.10733 | -0.072718 | -0.36038 | -0.24215 | -0.23561 | -0.34795 | 0.012422 | -0.049884 | -0.16115 | 122.134 | 122.0606 | 122.0952 | 29.9797 | -122.3685 | 121.9258 | 122.1181 | 122.0068 | 33.0326 | -122.5283
1306.7344 | 122.4106 | -33.3252 | 88.8657 | 1.4211e-13 | 1.487e-05 | -0.0084402 | 0.039811 | -0.022721 | 0.048439 | 0.0036627 | -0.01172 | 0.028835 | 0.04437 | 0.0013439 | 0.045724 | -31.892 | -3.0892 | -32.6973 | 89.088 | 89.0192 | 89.0493 | -33.2511 | -33.2953 | 0.073618 | -33.3985 | 88.8661 | 89.0858 | 88.9608 | -33.4201 | 0.074093 | 0.22237 | 1.4332 | 0.62786 | 0.55377 | 0.15357 | 0.18361 | -0.094903 | 0.000446 | 0.029865 | -0.073321 | 0.021582 | 0.22018 | 0.095178 | 122.4132 | 122.3444 | 122.3745 | 30.236 | -122.1168 | 122.1913 | 122.411 | 122.286 | 33.3988 | -122.2858
1308.4531 | 122.374 | -32.8949 | 89.3417 | 1.4211e-13 | -0.00019873 | -0.0082266 | 0.040452 | -0.022507 | 0.048653 | 0.0036627 | -0.011507 | 0.028622 | 0.044157 | 0.0015577 | 0.045724 | -31.5624 | -3.0663 | -32.3769 | 89.3673 | 89.3031 | 89.3286 | -32.9718 | -33.0023 | 0.078197 | -33.1146 | 89.1546 | 89.3651 | 89.2447 | -33.1316 | -0.076891 | 0.025582 | 1.3325 | 0.51804 | 0.59493 | -0.038612 | -0.013172 | -0.23674 | -0.18718 | -0.1074 | -0.21974 | 0.016997 | 0.023399 | -0.097022 | 122.2622 | 122.198 | 122.2235 | 29.8286 | -122.3135 | 122.0495 | 122.26 | 122.1396 | 32.9731 | -122.4734
1310.2344 | 122.4197 | -32.9544 | 89.2456 | 1.4211e-13 | 1.487e-05 | -0.0082266 | 0.040025 | -0.022721 | 0.048653 | 0.011293 | -0.011507 | 0.028622 | 0.044157 | 0.0013439 | 0.045724 | -31.686 | -3.1945 | -32.5188 | 89.1888 | 89.1154 | 89.1408 | -33.1504 | -33.1809 | 0.082776 | -33.2932 | 88.9714 | 89.182 | 89.0707 | -33.3056 | -0.19596 | -0.056844 | 1.2684 | 0.43563 | 0.63159 | -0.13022 | -0.10476 | -0.35122 | -0.27419 | -0.22646 | -0.3388 | 0.012422 | -0.063614 | -0.17488 | 122.1432 | 122.0698 | 122.0952 | 29.7599 | -122.396 | 121.9258 | 122.1364 | 122.0251 | 33.0372 | -122.5512
1312.0312 | 122.4564 | -34.1309 | 88.06 | 1.4211e-13 | 0.00022867 | -0.0084402 | 0.040452 | -0.022721 | 0.048653 | 0.011293 | -0.01172 | 0.027981 | 0.043943 | 0.0015577 | 0.045724 | -32.6612 | -3.6889 | -33.5306 | 88.1128 | 88.0485 | 88.0786 | -34.2127 | -34.2477 | 0.082776 | -34.3509 | 87.9092 | 88.1106 | 87.9993 | -34.3817 | -0.081818 | 0.052842 | 1.4697 | 0.60028 | 0.6821 | -0.011499 | 0.018608 | -0.25079 | -0.15079 | -0.11684 | -0.22003 | 0.030762 | 0.0506 | -0.060664 | 122.2437 | 122.1794 | 122.2095 | 30.4419 | -122.2727 | 122.0401 | 122.2415 | 122.1302 | 34.2136 | -122.4416
1313.8125 | 122.3969 | -34.8267 | 87.3505 | 1.4211e-13 | -0.00041233 | -0.0084402 | 0.040239 | -0.022507 | 0.048867 | -0.0039678 | -0.01172 | 0.028622 | 0.044157 | 0.0013439 | 0.046151 | -33.1144 | -3.9316 | -34.025 | 87.568 | 87.5128 | 87.5338 | -34.7576 | -34.7926 | 0.06904 | -34.8958 | 87.3644 | 87.5703 | 87.4545 | -34.9265 | 0.069091 | 0.21755 | 1.7122 | 0.80163 | 0.73253 | 0.1623 | 0.18329 | -0.099869 | 0.013898 | 0.034091 | -0.069094 | 0.030775 | 0.21986 | 0.10402 | 122.3947 | 122.3394 | 122.3604 | 30.895 | -122.108 | 122.191 | 122.397 | 122.2811 | 34.8957 | -122.277
1315.6094 | 122.2961 | -34.8083 | 87.4283 | 1.4211e-13 | 1.487e-05 | -0.008654 | 0.040239 | -0.02208 | 0.049294 | 0.0036627 | -0.011293 | 0.028622 | 0.044157 | 0.0015577 | 0.046151 | -33.0458 | -3.9682 | -34.0021 | 87.5589 | 87.4944 | 87.5292 | -34.7759 | -34.7971 | 0.050725 | -34.9049 | 87.3506 | 87.5566 | 87.4453 | -34.9311 | 0.032466 | 0.13057 | 1.7626 | 0.80621 | 0.77374 | 0.066165 | 0.10089 | -0.12276 | -0.077658 | 0.011203 | -0.096562 | 0.026196 | 0.1283 | 0.017039 | 122.3672 | 122.3028 | 122.3375 | 30.8401 | -122.2042 | 122.159 | 122.3649 | 122.2537 | 34.8591 | -122.3594
1317.3281 | 122.3648 | -34.0576 | 88.147 | 1.4211e-13 | 0.00022867 | -0.0082266 | 0.04088 | -0.022507 | 0.048867 | -0.0039678 | -0.01172 | 0.028622 | 0.044157 | 0.0015577 | 0.045724 | -32.3865 | -3.753 | -33.3612 | 88.1586 | 88.0897 | 88.1244 | -34.1623 | -34.2019 | 0.06904 | -34.3051 | 87.955 | 88.1518 | 88.036 | -34.3267 | -0.10469 | 0.011651 | 1.6711 | 0.69643 | 0.80113 | -0.057264 | -0.022581 | -0.26909 | -0.19199 | -0.1443 | -0.24748 | 0.021603 | 0.004832 | -0.11101 | 122.2162 | 122.1473 | 122.182 | 30.3046 | -122.3093 | 122.0126 | 122.2094 | 122.0936 | 34.1267 | -122.4737
1319.0938 | 122.4609 | -34.2453 | 87.9272 | 1.4211e-13 | 1.487e-05 | -0.008013 | 0.040239 | -0.022507 | 0.04908 | 0.0036627 | -0.011934 | 0.028622 | 0.04437 | 0.0017713 | 0.045937 | -32.3407 | -3.7576 | -33.3612 | 88.1037 | 88.0393 | 88.074 | -34.2218 | -34.2569 | 0.059882 | -34.36 | 87.8955 | 88.1014 | 87.9856 | -34.3817 | 0.023466 | 0.17644 | 1.9046 | 0.88412 | 0.86065 | 0.11209 | 0.14678 | -0.13635 | -0.031779 | -0.01156 | -0.11474 | 0.021605 | 0.17419 | 0.058352 | 122.349 | 122.2846 | 122.3193 | 30.4877 | -122.1491 | 122.1408 | 122.3467 | 122.2309 | 34.3052 | -122.3089
1320.8594 | 122.4243 | -33.9844 | 88.1927 | 1.4211e-13 | 0.00022867 | -0.008013 | 0.040452 | -0.02208 | 0.049294 | 0.0036627 | -0.011934 | 0.028622 | 0.04437 | 0.0013439 | 0.045937 | -31.9836 | -3.6294 | -33.0773 | 88.3509 | 88.2958 | 88.3259 | -33.97 | -34.0142 | 0.055303 | -34.1128 | 88.1427 | 88.3578 | 88.2283 | -34.1344 | 0.014381 | 0.15817 | 2.0008 | 0.90704 | 0.89266 | 0.10301 | 0.1331 | -0.15002 | -0.050043 | -0.029813 | -0.12842 | 0.021599 | 0.16509 | 0.035515 | 122.3353 | 122.2801 | 122.3102 | 30.3549 | -122.1627 | 122.1271 | 122.3422 | 122.2126 | 34.0397 | -122.3271
1322.6406 | 122.3053 | -34.4879 | 87.7213 | 1.4211e-13 | 0.00022867 | -0.0077992 | 0.040666 | -0.02208 | 0.049294 | 0.011293 | -0.01172 | 0.028835 | 0.043943 | 0.0017713 | 0.045937 | -32.4323 | -3.7943 | -33.5947 | 87.774 | 87.7234 | 87.7489 | -34.5378 | -34.5728 | 0.059882 | -34.676 | 87.5612 | 87.7809 | 87.6651 | -34.7022 | -0.049865 | 0.052787 | 2.0557 | 0.89324 | 0.9431 | 0.002143 | 0.027695 | -0.21425 | -0.16002 | -0.084875 | -0.18806 | 0.026191 | 0.059686 | -0.056156 | 122.262 | 122.2113 | 122.2369 | 30.6937 | -122.259 | 122.0492 | 122.2689 | 122.153 | 34.5478 | -122.4234
1324.3594 | 122.4243 | -34.0988 | 88.0234 | 1.4211e-13 | 0.00044227 | -0.0082266 | 0.040666 | -0.022507 | 0.049294 | 0.0036627 | -0.01172 | 0.028622 | 0.044157 | 0.00091673 | 0.04551 | -32.0706 | -3.6065 | -33.2925 | 88.0304 | 87.9615 | 87.9962 | -34.2859 | -34.3301 | 0.059882 | -34.4379 | 87.8222 | 88.0236 | 87.9078 | -34.4641 | -0.18712 | 0.007053 | 2.0283 | 0.80631 | 0.99343 | -0.061877 | -0.027185 | -0.36525 | -0.20117 | -0.2313 | -0.33907 | 0.026185 | 0.000228 | -0.11561 | 122.1292 | 122.0603 | 122.095 | 30.4923 | -122.3093 | 121.921 | 122.1224 | 122.0066 | 34.1587 | -122.4874
1326.125 | 122.3282 | -34.4604 | 87.7991 | 1.4211e-13 | 0.00044227 | -0.0075856 | 0.040452 | -0.022294 | 0.049721 | 0.0036627 | -0.01172 | 0.028408 | 0.044157 | 0.0015577 | 0.045724 | -32.1575 | -3.6111 | -33.494 | 87.7649 | 87.6959 | 87.7261 | -34.5607 | -34.6003 | 0.059882 | -34.6943 | 87.5521 | 87.758 | 87.6422 | -34.7205 | -0.10023 | -0.03419 | 2.3029 | 0.9665 | 1.0667 | -0.10315 | -0.073018 | -0.26003 | -0.24699 | -0.13981 | -0.23384 | 0.026191 | -0.041027 | -0.15687 | 122.2253 | 122.1564 | 122.1865 | 30.8493 | -122.3597 | 122.0125 | 122.2185 | 122.1027 | 34.5203 | -122.5196
1327.8281 | 122.3282 | -36.5891 | 85.6796 | 1.4211e-13 | 0.00044227 | -0.008013 | 0.040666 | -0.022507 | 0.049721 | 0.011293 | -0.011507 | 0.028622 | 0.043943 | 0.0015577 | 0.045724 | -33.2747 | -3.9362 | -34.7301 | 86.4463 | 86.3772 | 86.4074 | -35.8794 | -35.9052 | 0.064461 | -36.0084 | 86.2381 | 86.444 | 86.3373 | -36.0346 | 0.70965 | 0.76668 | 3.3144 | 1.859 | 1.1493 | 0.69757 | 0.72779 | 0.55445 | 0.55843 | 0.68386 | 0.58067 | 0.026222 | 0.76436 | 0.65767 | 123.0354 | 122.9662 | 122.9965 | 32.6529 | -121.559 | 122.8271 | 123.033 | 122.9264 | 36.6535 | -121.7142
1329.6094 | 122.406 | -36.5479 | 85.6384 | 1.4211e-13 | 0.00022867 | -0.0075856 | 0.04088 | -0.02208 | 0.050362 | -0.0039678 | -0.011934 | 0.028622 | 0.04437 | 0.0015577 | 0.045937 | -33.847 | -4.069 | -35.4397 | 85.6451 | 85.5896 | 85.6107 | -36.667 | -36.6927 | 0.050725 | -36.7959 | 85.446 | 85.6519 | 85.5315 | -36.8313 | -0.11913 | 0.006661 | 2.7009 | 1.1081 | 1.2273 | -0.048811 | -0.027689 | -0.28346 | -0.19246 | -0.14488 | -0.24807 | 0.035398 | 0.01346 | -0.10696 | 122.1929 | 122.1375 | 122.1586 | 32.4789 | -122.3054 | 121.9938 | 122.1997 | 122.0793 | 36.5986 | -122.4697
1331.3281 | 122.319 | -37.2391 | 84.9792 | 1.4211e-13 | 0.00065587 | -0.0075856 | 0.040666 | -0.02208 | 0.050362 | 0.018923 | -0.01172 | 0.028835 | 0.044157 | 0.0015577 | 0.04551 | -34.1904 | -4.0873 | -35.9113 | 85.0911 | 85.0356 | 85.075 | -37.2119 | -37.2422 | 0.055303 | -37.3408 | 84.892 | 85.0933 | 84.9729 | -37.3854 | 0.027203 | 0.11186 | 3.0487 | 1.3278 | 1.3006 | 0.056319 | 0.095795 | -0.14628 | -0.087274 | -0.003103 | -0.10171 | 0.044569 | 0.11405 | -0.00637 | 122.3302 | 122.2746 | 122.3141 | 33.1518 | -122.1911 | 122.131 | 122.3324 | 122.212 | 37.2944 | -122.3646
1333.125 | 122.3145 | -37.1017 | 85.1486 | 1.4211e-13 | 0.00065587 | -0.007372 | 0.040666 | -0.022507 | 0.050576 | 0.011293 | -0.011507 | 0.028408 | 0.044157 | 0.0013439 | 0.045724 | -33.9889 | -3.8858 | -35.8243 | 85.0911 | 85.031 | 85.0613 | -37.2165 | -37.2376 | 0.055303 | -37.3362 | 84.8966 | 85.0933 | 84.9775 | -37.3808 | -0.11471 | -0.057517 | 3.1128 | 1.2774 | 1.3922 | -0.11763 | -0.087314 | -0.27903 | -0.25207 | -0.13585 | -0.23446 | 0.044568 | -0.055323 | -0.17117 | 122.1928 | 122.1327 | 122.1631 | 33.2159 | -122.3651 | 121.9983 | 122.195 | 122.0792 | 37.157 | -122.5294
1334.8438 | 122.3557 | -36.3831 | 85.8582 | 1.4211e-13 | 0.00065587 | -0.0071582 | 0.041093 | -0.022294 | 0.05079 | 0.0036627 | -0.01172 | 0.028408 | 0.043729 | 0.0015577 | 0.045724 | -32.7436 | -3.373 | -34.9178 | 85.9244 | 85.8644 | 85.8992 | -36.3831 | -36.4089 | 0.059882 | -36.5075 | 85.7253 | 85.9266 | 85.8108 | -36.5474 | -3e-05 | 0.066216 | 3.6395 | 1.4653 | 1.4653 | 0.006198 | 0.041037 | -0.16437 | -0.13289 | -0.025796 | -0.1244 | 0.03997 | 0.06845 | -0.047392 | 122.3074 | 122.2474 | 122.2822 | 33.01 | -122.2412 | 122.1083 | 122.3097 | 122.1938 | 36.4429 | -122.4056
1336.625 | 122.4518 | -35.6277 | 86.5173 | 1.4211e-13 | 0.00044227 | -0.0071582 | 0.04088 | -0.02208 | 0.051003 | 0.011293 | -0.011507 | 0.028835 | 0.044157 | 0.0013439 | 0.045724 | -31.5303 | -2.9152 | -34.1486 | 86.6203 | 86.5466 | 86.5814 | -35.6962 | -35.7266 | 0.059882 | -35.8298 | 86.4029 | 86.6134 | 86.493 | -35.8606 | -0.068501 | 0.10295 | 4.0974 | 1.4791 | 1.5476 | 0.029278 | 0.064069 | -0.23286 | -0.11446 | -0.098878 | -0.20206 | 0.030797 | 0.096061 | -0.02436 | 122.248 | 122.1744 | 122.2091 | 32.7126 | -122.2136 | 122.0306 | 122.2411 | 122.1207 | 35.6876 | -122.3779
1338.3594 | 122.3328 | -34.9045 | 87.3459 | 1.4211e-13 | 0.0010833 | -0.0071582 | 0.040666 | -0.021866 | 0.05079 | 0.011293 | -0.011934 | 0.028622 | 0.04437 | 0.0015577 | 0.045724 | -31.2877 | -2.3749 | -33.4756 | 87.2109 | 87.1602 | 87.1766 | -35.0918 | -35.1268 | 0.073618 | -35.23 | 87.0118 | 87.2086 | 87.0973 | -35.2562 | -0.18735 | -0.13499 | 3.6168 | 1.4288 | 1.6162 | -0.1857 | -0.16926 | -0.35172 | -0.33407 | -0.22233 | -0.32552 | 0.026204 | -0.13727 | -0.24854 | 122.1154 | 122.0647 | 122.0811 | 32.5296 | -122.4377 | 121.9163 | 122.1131 | 122.0018 | 34.9781 | -122.6021
1340.1406 | 122.2778 | -32.6111 | 89.653 | 1.4211e-13 | 0.00086967 | -0.0067308 | 0.041093 | -0.021866 | 0.051003 | 0.0036627 | -0.011507 | 0.028622 | 0.044584 | 0.0015577 | 0.045297 | -28.7375 | -1.1982 | -30.9484 | 89.7107 | 89.6603 | 89.6811 | -32.6009 | -32.6406 | 0.082776 | -32.7483 | 89.5025 | 89.6994 | 89.6018 | -32.7653 | 0.010189 | 0.057682 | 3.8736 | 1.6627 | 1.6525 | 0.007265 | 0.028102 | -0.15424 | -0.1505 | -0.029491 | -0.13726 | 0.016988 | 0.046358 | -0.05117 | 122.3218 | 122.2714 | 122.2922 | 31.4129 | -122.2539 | 122.1136 | 122.3105 | 122.2129 | 32.6939 | -122.4183
1341.8438 | 122.406 | -32.0206 | 90.1794 | 1.4211e-13 | 0.00086967 | -0.0060898 | 0.041307 | -0.021866 | 0.051003 | 0.0036627 | -0.01172 | 0.028835 | 0.044157 | 0.0013439 | 0.045937 | -28.0874 | -0.76322 | -30.4173 | 90.1502 | 90.077 | 90.1161 | -32.1522 | -32.201 | 0.082776 | -32.3179 | 89.9375 | 90.1389 | 90.0322 | -32.3166 | -0.13159 | -0.029221 | 3.9332 | 1.6032 | 1.7348 | -0.10248 | -0.063359 | -0.29603 | -0.24197 | -0.18045 | -0.29737 | -0.001338 | -0.040525 | -0.14721 | 122.1708 | 122.0975 | 122.1367 | 31.2573 | -122.3316 | 121.958 | 122.1595 | 122.0528 | 32.1033 | -122.496
1343.625 | 122.3923 | -29.6402 | 92.5323 | 1.4211e-13 | 0.0012971 | -0.0060898 | 0.041734 | -0.02208 | 0.051003 | 0.0036627 | -0.01172 | 0.028622 | 0.044157 | 0.0015577 | 0.04551 | -25.8943 | 0.13876 | -28.3617 | 92.1327 | 92.078 | 92.0849 | -30.1786 | -30.2184 | 0.091933 | -30.3354 | 91.9108 | 92.126 | 92.0102 | -30.334 | -0.53845 | -0.39968 | 3.7459 | 1.2785 | 1.8169 | -0.4544 | -0.44747 | -0.69378 | -0.62154 | -0.57824 | -0.69516 | -0.001384 | -0.40632 | -0.52216 | 121.7729 | 121.7182 | 121.7251 | 29.779 | -122.711 | 121.551 | 121.7662 | 121.6504 | 29.7321 | -122.8663
1345.3438 | 122.4152 | -27.5116 | 94.6335 | 1.4211e-13 | 0.0015107 | -0.0058762 | 0.041521 | -0.021866 | 0.051644 | 0.018923 | -0.011934 | 0.028622 | 0.044157 | 0.0013439 | 0.045297 | -22.5841 | 1.2788 | -25.7841 | 94.637 | 94.5735 | 94.5894 | -27.6694 | -27.7185 | 0.091933 | -27.84 | 94.4152 | 94.6351 | 94.5147 | -27.8248 | -0.1578 | 0.003559 | 4.9275 | 1.7275 | 1.8853 | -0.060018 | -0.044105 | -0.31319 | -0.21824 | -0.20687 | -0.32837 | -0.015179 | 0.001622 | -0.1188 | 122.1486 | 122.0851 | 122.101 | 28.7904 | -122.3029 | 121.9268 | 122.1467 | 122.0263 | 27.6035 | -122.4583
1347.125 | 122.2916 | -25.7263 | 96.5561 | 1.4211e-13 | 0.0017243 | -0.0058762 | 0.041734 | -0.021439 | 0.052285 | 0.011293 | -0.011934 | 0.028622 | 0.044157 | 0.0017713 | 0.04551 | -19.892 | 2.1717 | -23.7514 | 96.5966 | 96.5241 | 96.5536 | -25.7188 | -25.7725 | 0.091933 | -25.894 | 96.3703 | 96.5902 | 96.4606 | -25.8696 | 0.007547 | 0.040502 | 5.8343 | 1.9749 | 1.9674 | -0.032003 | -0.002492 | -0.14331 | -0.18583 | -0.046192 | -0.16769 | -0.024383 | 0.034078 | -0.0955 | 122.3229 | 122.2504 | 122.2799 | 27.898 | -122.2749 | 122.0966 | 122.3165 | 122.1869 | 25.8183 | -122.4257
1348.8438 | 122.3099 | -24.5636 | 97.6364 | 1.4211e-13 | 0.0019381 | -0.0056624 | 0.041734 | -0.021439 | 0.052072 | 0.0036627 | -0.01172 | 0.028622 | 0.044157 | 0.0013439 | 0.045724 | -18.5597 | 2.7348 | -22.5931 | 97.6817 | 97.6139 | 97.625 | -24.6381 | -24.6828 | 0.10109 | -24.818 | 97.4508 | 97.6707 | 97.5457 | -24.7844 | -0.074546 | 0.045256 | 6.0039 | 1.9705 | 2.0451 | -0.022542 | -0.011422 | -0.22085 | -0.18563 | -0.11918 | -0.25442 | -0.033565 | 0.034306 | -0.090694 | 122.2453 | 122.1775 | 122.1886 | 27.2984 | -122.2746 | 122.0144 | 122.2343 | 122.1093 | 24.6647 | -122.4209
1350.6406 | 122.3648 | -27.5162 | 94.6381 | 1.4211e-13 | 0.0021517 | -0.0052352 | 0.041734 | -0.021439 | 0.052285 | 0.0036627 | -0.011507 | 0.028835 | 0.044157 | 0.0015577 | 0.045937 | -21.6089 | 1.8924 | -25.2485 | 94.8293 | 94.7475 | 94.7771 | -27.5 | -27.5399 | 0.078197 | -27.666 | 94.5938 | 94.8137 | 94.6841 | -27.6416 | 0.016201 | 0.19127 | 5.9072 | 2.2677 | 2.2515 | 0.1094 | 0.13904 | -0.12546 | -0.044256 | -0.023718 | -0.1498 | -0.024341 | 0.17561 | 0.046032 | 122.3455 | 122.2636 | 122.2933 | 29.4085 | -122.138 | 122.11 | 122.3298 | 122.2003 | 27.5944 | -122.2797
1352.3594 | 122.287 | -29.0176 | 93.2236 | 1.4211e-13 | 0.0017243 | -0.0050214 | 0.042162 | -0.021653 | 0.05314 | 0.011293 | -0.01172 | 0.028194 | 0.04437 | 0.0017713 | 0.04551 | -22.2087 | 1.5215 | -26.6586 | 93.2544 | 93.1906 | 93.2112 | -29.0568 | -29.115 | 0.073618 | -29.2182 | 93.0325 | 93.2524 | 93.1274 | -29.203 | -0.039168 | 0.030797 | 6.8089 | 2.3591 | 2.3982 | -0.032941 | -0.012353 | -0.18537 | -0.19103 | -0.097329 | -0.20051 | -0.015147 | 0.028796 | -0.096203 | 122.272 | 122.2083 | 122.2289 | 30.5391 | -122.2804 | 122.0502 | 122.27 | 122.145 | 29.0913 | -122.4266
1354.125 | 122.2824 | -31.2607 | 90.9348 | 1.4211e-13 | 0.0021517 | -0.0050214 | 0.042375 | -0.021439 | 0.053567 | 0.018923 | -0.012148 | 0.028835 | 0.044157 | 0.0015577 | 0.046151 | -23.509 | 0.93086 | -28.6089 | 91.1163 | 91.0477 | 91.0822 | -31.1906 | -31.2258 | 0.064461 | -31.3427 | 90.8944 | 91.1187 | 90.9983 | -31.3459 | 0.070095 | 0.18151 | 7.7517 | 2.6518 | 2.5817 | 0.11294 | 0.14742 | -0.085213 | -0.040371 | 0.034927 | -0.081995 | 0.003218 | 0.18399 | 0.063565 | 122.3769 | 122.3084 | 122.3428 | 32.1915 | -122.1253 | 122.1551 | 122.3794 | 122.259 | 31.3251 | -122.2806
1355.8906 | 122.3785 | -54.1397 | 67.9825 | 1.4211e-13 | 0.0015107 | -0.0058762 | 0.041948 | -0.020371 | 0.057413 | 0.011293 | -0.01172 | 0.028408 | 0.044157 | 0.0015577 | 0.045937 | -39.4418 | -5.7127 | -47.7599 | 71.1087 | 71.0195 | 71.1515 | -51.228 | -51.1981 | -0.13242 | -51.2646 | 70.8864 | 71.1148 | 70.9303 | -51.4377 | 2.9117 | 3.1262 | 14.6979 | 6.3798 | 3.4681 | 3.037 | 3.169 | 2.702 | 2.9039 | 2.9416 | 2.8751 | 0.1731 | 3.1323 | 2.9478 | 125.2484 | 125.1592 | 125.2912 | 48.427 | -119.2104 | 125.0261 | 125.2545 | 125.07 | 54.0073 | -119.4202
1357.6094 | 122.3877 | -80.0766 | 41.9861 | 1.4211e-13 | 0.0015107 | -0.0065172 | 0.041307 | -0.01973 | 0.062541 | 0.011293 | -0.012361 | 0.027981 | 0.043943 | 0.0015577 | 0.046365 | -54.9579 | -9.8472 | -69.1496 | 48.6609 | 48.5599 | 48.753 | -73.7425 | -73.6063 | -0.46209 | -73.6042 | 48.3876 | 48.5789 | 48.4723 | -73.9381 | 6.3341 | 6.6748 | 25.1187 | 10.927 | 4.5929 | 6.5738 | 6.7669 | 6.1385 | 6.4015 | 6.4703 | 6.4724 | 0.33388 | 6.5929 | 6.4862 | 128.7375 | 128.6365 | 128.8296 | 70.2294 | -115.7286 | 128.4642 | 128.6555 | 128.5489 | 79.6145 | -115.9241
1359.4062 | 122.287 | -45.3827 | 76.7578 | 1.4211e-13 | 0.0025791 | -0.0052352 | 0.042589 | -0.020798 | 0.056986 | 0.011293 | -0.01172 | 0.028622 | 0.043943 | 0.0013439 | 0.045937 | -25.5189 | -0.64418 | -33.5901 | 85.5306 | 85.3652 | 85.5604 | -37.0196 | -37.027 | -0.28352 | -37.0752 | 85.1438 | 85.4275 | 85.2018 | -37.1518 | 8.3631 | 8.7728 | 19.8638 | 11.7926 | 3.4295 | 8.6074 | 8.8026 | 8.2309 | 8.386 | 8.3557 | 8.3075 | 0.076614 | 8.6697 | 8.444 | 130.9133 | 130.7479 | 130.9431 | 44.7385 | -113.7774 | 130.5265 | 130.8102 | 130.5845 | 45.0992 | -113.9096
1361.1875 | 122.287 | -105.5603 | 16.5024 | 1.4211e-13 | 0.00086967 | -0.0084402 | 0.040452 | -0.018661 | 0.070874 | 0.0036627 | -0.012361 | 0.027767 | 0.043729 | 0.0015577 | 0.046365 | -70.2635 | -10.7995 | -92.9567 | 23.0082 | 22.8126 | 23.2044 | -99.183 | -98.9723 | -0.48498 | -98.9794 | 22.716 | 22.9525 | 22.6993 | -99.3963 | 6.3773 | 6.5058 | 35.2968 | 12.6036 | 6.2264 | 6.3102 | 6.702 | 6.164 | 6.2136 | 6.588 | 6.5809 | 0.4169 | 6.4501 | 6.1969 | 128.5685 | 128.3729 | 128.7647 | 94.7608 | -115.6854 | 128.2763 | 128.5128 | 128.2596 | 105.0753 | -115.8987
1362.9219 | 122.3236 | -114.0381 | 8.0521 | 1.4211e-13 | 0.0010833 | -0.0084402 | 0.039811 | -0.017807 | 0.075575 | 0.011293 | -0.012361 | 0.027553 | 0.043516 | 0.0013439 | 0.046578 | -77.4836 | -11.9442 | -106.7922 | 8.2566 | 8.2607 | 8.4155 | -113.973 | -113.5647 | -0.25147 | -113.5946 | 8.1747 | 8.2827 | 8.2675 | -114.2042 | 0.065123 | 0.20454 | 36.5545 | 7.2459 | 7.1807 | 0.20868 | 0.36344 | -0.16608 | 0.12265 | 0.47339 | 0.44347 | 0.60955 | 0.2306 | 0.21549 | 122.2947 | 122.2988 | 122.4536 | 102.0939 | -122.025 | 122.2128 | 122.3207 | 122.3056 | 113.7866 | -122.2562
1364.7031 | 122.1817 | -115.6631 | 6.4178 | 1.4211e-13 | 0.00086967 | -0.008013 | 0.039811 | -0.017166 | 0.080703 | 0.011293 | -0.012575 | 0.027767 | 0.043302 | 0.0017713 | 0.046365 | -77.8041 | -11.6008 | -107.9414 | 6.4893 | 6.5253 | 6.6939 | -115.6855 | -115.2771 | -0.21484 | -115.3025 | 6.4486 | 6.5565 | 6.5368 | -115.9212 | -0.022334 | 0.071494 | 37.8591 | 7.7218 | 7.7441 | 0.10748 | 0.2761 | -0.25808 | 0.030769 | 0.38602 | 0.36067 | 0.61875 | 0.13868 | 0.11899 | 122.1525 | 122.1885 | 122.3571 | 104.0624 | -122.1033 | 122.1118 | 122.2197 | 122.2 | 115.4483 | -122.3391
1366.5 | 122.2366 | -116.3773 | 5.6625 | 1.4211e-13 | 0.00086967 | -0.0084402 | 0.040025 | -0.016952 | 0.081557 | 0.0036627 | -0.012575 | 0.027981 | 0.043302 | 0.0017713 | 0.046365 | -75.0708 | -11.2848 | -108.2115 | 5.711 | 5.7652 | 5.9156 | -116.4318 | -116.0326 | -0.20568 | -116.0488 | 5.6794 | 5.7873 | 5.7722 | -116.6676 | -0.054588 | 0.048478 | 41.3065 | 8.1658 | 8.2204 | 0.10269 | 0.25305 | -0.29032 | 0.016892 | 0.34464 | 0.32845 | 0.61877 | 0.12479 | 0.10967 | 122.0883 | 122.1425 | 122.2928 | 105.0924 | -122.0944 | 122.0567 | 122.1646 | 122.1495 | 116.1716 | -122.3301
1368.2188 | 122.1313 | -116.8808 | 5.1865 | 1.4211e-13 | 0.0010833 | -0.008654 | 0.040025 | -0.016311 | 0.08348 | 0.0036627 | -0.012575 | 0.027767 | 0.043302 | 0.0019849 | 0.046792 | -74.2329 | -11.2848 | -108.1749 | 5.1708 | 5.2203 | 5.3845 | -116.9584 | -116.5454 | -0.19195 | -116.5708 | 5.1346 | 5.2516 | 5.2411 | -117.1896 | -0.077624 | -0.015697 | 42.6479 | 8.7059 | 8.7836 | 0.033871 | 0.198 | -0.30876 | -0.051874 | 0.33536 | 0.31002 | 0.61878 | 0.065166 | 0.054631 | 122.0516 | 122.1011 | 122.2653 | 105.5959 | -122.1449 | 122.0154 | 122.1324 | 122.1219 | 116.6889 | -122.376
1370 | 122.1176 | -117.0593 | 4.9805 | 1.4211e-13 | 0.00086967 | -0.008013 | 0.039811 | -0.014388 | 0.088181 | 0.011293 | -0.012148 | 0.027767 | 0.043302 | 0.0017713 | 0.046365 | -72.4519 | -11.4726 | -105.8445 | 4.8823 | 4.9273 | 5.0914 | -117.1645 | -116.8247 | -0.19653 | -116.8455 | 4.8507 | 4.9586 | 4.9481 | -117.478 | -0.10515 | -0.098142 | 44.6074 | 11.2148 | 11.32 | -0.053187 | 0.11097 | -0.4187 | -0.12975 | 0.23459 | 0.21382 | 0.63252 | -0.021872 | -0.032406 | 121.9417 | 121.9866 | 122.1508 | 105.5868 | -122.1449 | 121.91 | 122.0179 | 122.0074 | 116.8628 | -122.4585
1371.7188 | 122.1451 | -116.4047 | 5.2734 | 1.4211e-13 | 0.0010833 | -0.0082266 | 0.040239 | -0.01332 | 0.12365 | 0.011293 | -0.012361 | 0.027981 | 0.043302 | 0.0013439 | 0.046578 | -70.1811 | -12.1227 | -104.526 | 4.8137 | 4.8723 | 5.0273 | -117.2515 | -116.8705 | -0.17363 | -116.8867 | 4.7912 | 4.8991 | 4.8794 | -117.5284 | -0.84675 | -0.45979 | 46.2237 | 11.8787 | 12.7255 | -0.4011 | -0.2461 | -1.1237 | -0.48224 | -0.4658 | -0.48199 | 0.64168 | -0.37436 | -0.39405 | 121.2184 | 121.2771 | 121.4321 | 104.282 | -122.5249 | 121.1959 | 121.3038 | 121.2841 | 116.2311 | -122.8018
1373.5 | 122.2321 | -117.1555 | 4.7607 | 1.4211e-13 | 0.0012971 | -0.008013 | 0.040452 | -0.011824 | 0.16895 | 0.011293 | -0.012361 | 0.028194 | 0.043516 | 0.0013439 | 0.046792 | -66.674 | -12.1227 | -102.4245 | 4.69 | 4.735 | 4.8991 | -117.3614 | -116.9804 | -0.17821 | -117.0012 | 4.6584 | 4.7755 | 4.6962 | -117.6337 | -0.20591 | -0.070707 | 50.4814 | 14.7309 | 14.9368 | -0.025775 | 0.13839 | -0.47825 | -0.10232 | 0.17505 | 0.15428 | 0.63253 | 0.014711 | -0.064502 | 121.8455 | 121.8904 | 122.0546 | 105.0327 | -122.1221 | 121.8139 | 121.9309 | 121.8517 | 116.9772 | -122.3944
1375.2188 | 122.1405 | -87.8311 | 34.0805 | 1.4211e-13 | 1.487e-05 | -0.0069446 | -0.0089084 | -0.023148 | 0.0033567 | 0.018923 | -0.012148 | 0.027767 | 0.043516 | 0.0017713 | 0.045937 | 2.0018 | 1.3704 | 1.8321 | 32.7922 | 32.7214 | 32.911 | 1.0817 | -89.1052 | -0.10037 | -89.0939 | 32.6147 | 32.7736 | 32.7081 | -89.5427 | 88.9128 | -1.2883 | 89.8329 | 89.6632 | 0.75039 | -1.3592 | -1.1695 | -1.7115 | -1.4658 | -1.2741 | -1.2628 | 0.44872 | -1.3069 | -1.3724 | 120.6233 | 120.5525 | 120.7421 | 89.2015 | -32.9988 | 120.4458 | 120.6047 | 120.5392 | 87.7307 | -123.6232
1376.9844 | 122.0856 | -93.8736 | 28.0655 | 1.4211e-13 | 0.00022867 | -0.0058762 | -0.0035664 | -0.022721 | 0.0025021 | 0.018923 | -0.012148 | 0.028194 | 0.043516 | 0.0015577 | 0.045937 | 2.5695 | 1.6451 | 2.3036 | 41.1615 | 41.1649 | 41.2349 | 1.3747 | -80.7079 | 0.004938 | -80.7057 | 41.0163 | 41.1479 | 41.1099 | -81.136 | 95.2483 | 13.096 | 96.4431 | 96.1772 | 0.9289 | 13.0994 | 13.1694 | 12.7376 | 12.9508 | 13.1657 | 13.1679 | 0.43021 | 13.0824 | 13.0444 | 135.0351 | 135.0385 | 135.1085 | 95.5187 | -26.6908 | 134.8899 | 135.0215 | 134.9835 | 93.8785 | -109.2014
1378.7656 | 122.049 | -79.6326 | 42.3386 | 1.4211e-13 | 0.00044227 | -0.0063036 | -0.0044212 | -0.022935 | 0.0025021 | 0.011293 | -0.012361 | 0.028194 | 0.043729 | 0.0017713 | 0.047006 | 2.8625 | 1.3613 | 2.7248 | 39.4904 | 39.4753 | 39.5729 | 1.8601 | -82.3425 | 0.064461 | -82.3678 | 39.3497 | 39.4904 | 39.4753 | -82.8026 | 81.4927 | -2.8482 | 82.4951 | 82.3574 | 0.86473 | -2.8633 | -2.7657 | -3.1701 | -2.9889 | -2.7099 | -2.7352 | 0.43482 | -2.8481 | -2.8633 | 119.1229 | 119.1078 | 119.2055 | 80.9938 | -40.4785 | 118.9823 | 119.123 | 119.1079 | 79.697 | -125.1412
1380.5469 | 122.1909 | -76.7395 | 45.1263 | 1.4211e-13 | 0.00044227 | -0.003953 | -0.002498 | -0.022721 | 0.0022883 | 0.011293 | -0.012575 | 0.028194 | 0.043302 | 0.0015577 | 0.046365 | 3.5264 | 1.1644 | 3.4894 | 43.1073 | 43.0789 | 43.2037 | 2.6385 | -78.8031 | 0.03241 | -78.801 | 42.9438 | 43.1075 | 43.0649 | -79.2037 | 79.378 | -2.0191 | 80.2659 | 80.2289 | 0.85089 | -2.0475 | -1.9226 | -2.4642 | -2.1825 | -2.0636 | -2.0615 | 0.40269 | -2.0188 | -2.0614 | 119.8468 | 119.8184 | 119.9432 | 77.9039 | -42.4878 | 119.6833 | 119.847 | 119.8044 | 76.7719 | -124.33
1382.2812 | 122.2046 | -84.5993 | 37.2574 | 1.4211e-13 | 0.00044227 | -0.0056624 | -0.00784 | -0.023148 | 0.0029293 | -0.0039678 | -0.012148 | 0.028194 | 0.043302 | 0.0017713 | 0.047006 | 2.9266 | 0.87134 | 2.7431 | 34.1474 | 34.15 | 34.248 | 2.1944 | -87.64 | 0.041567 | -87.6562 | 34.0341 | 34.1701 | 34.1641 | -88.1278 | 86.7937 | -3.11 | 87.5259 | 87.3424 | 0.54878 | -3.1074 | -3.0094 | -3.5285 | -3.2233 | -3.0407 | -3.0569 | 0.47158 | -3.0873 | -3.0933 | 118.7467 | 118.7493 | 118.8473 | 85.4706 | -35.063 | 118.6334 | 118.7694 | 118.7634 | 84.6409 | -125.3852
1384.0625 | 122.0856 | -95.7092 | 26.1749 | 1.4211e-13 | 0.00022867 | -0.0052352 | -0.0080538 | -0.022935 | 0.0027157 | 0.018923 | -0.012148 | 0.028408 | 0.043516 | 0.0017713 | 0.047219 | 2.7069 | 0.73856 | 2.8164 | 33.9047 | 33.8432 | 34.0053 | 2.4004 | -88.0018 | -0.32931 | -88.0088 | 33.6815 | 33.8542 | 33.7887 | -88.4712 | 98.1096 | 7.7298 | 98.4161 | 98.5256 | 0.41599 | 7.6683 | 7.8304 | 7.238 | 7.5066 | 7.7075 | 7.7004 | 0.46243 | 7.6792 | 7.6138 | 129.614 | 129.5524 | 129.7145 | 96.4478 | -23.7745 | 129.3907 | 129.5634 | 129.4979 | 95.3799 | -114.6461
1385.8281 | 121.9437 | -84.4666 | 37.4222 | 1.4211e-13 | 0.00022867 | -0.00203 | -0.002498 | -0.022935 | 0.0037841 | 0.026554 | -0.012361 | 0.027981 | 0.043729 | 0.0015577 | 0.046792 | 3.1556 | 0.70193 | 3.2513 | 40.928 | 40.8856 | 41.006 | 2.8308 | -80.8773 | -0.045428 | -80.8706 | 40.737 | 40.9006 | 40.8535 | -81.2825 | 87.2974 | 3.5058 | 87.6221 | 87.7179 | 0.4205 | 3.4634 | 3.5838 | 3.1841 | 3.3148 | 3.5893 | 3.596 | 0.41189 | 3.4784 | 3.4313 | 125.3945 | 125.3521 | 125.4725 | 85.1685 | -34.5914 | 125.2035 | 125.3672 | 125.32 | 84.4211 | -118.7047
1387.6094 | 121.9345 | -68.7424 | 53.0365 | 1.4211e-13 | 0.00065587 | 0.00053421 | 0.001562 | -0.023148 | 0.0035703 | 0.0036627 | -0.01172 | 0.028194 | 0.043729 | 0.0015577 | 0.046578 | 4.3322 | 0.96291 | 3.9243 | 47.6216 | 47.6532 | 47.6633 | 3.4444 | -73.9955 | 0.19267 | -74.0071 | 47.5269 | 47.6495 | 47.6939 | -74.3959 | 72.1868 | -5.4149 | 73.0746 | 72.6667 | 0.47993 | -5.3833 | -5.3732 | -5.6536 | -5.5096 | -5.2531 | -5.2647 | 0.38884 | -5.387 | -5.3426 | 116.3639 | 116.3956 | 116.4057 | 69.7053 | -49.5921 | 116.2692 | 116.3919 | 116.4363 | 68.935 | -127.4324
1389.3281 | 121.8201 | -87.2635 | 34.3231 | 1.4211e-13 | 0.00044227 | -0.00096159 | -0.0039938 | -0.023576 | 0.0033567 | -0.0039678 | -0.012148 | 0.028408 | 0.043516 | 0.0015577 | 0.046792 | 3.6271 | 0.6653 | 3.0499 | 37.8879 | 37.717 | 38.0162 | 2.6751 | -83.7985 | -0.29268 | -83.801 | 37.5961 | 37.8192 | 37.6255 | -84.1946 | 89.9386 | 3.5648 | 90.8906 | 90.3134 | 0.37474 | 3.3938 | 3.693 | 3.0689 | 3.273 | 3.465 | 3.4625 | 0.39365 | 3.4961 | 3.3024 | 125.1514 | 124.9804 | 125.2797 | 87.9288 | -31.648 | 124.8596 | 125.0827 | 124.889 | 86.9708 | -118.5177
1391.1094 | 121.7651 | -83.876 | 37.5412 | 1.4211e-13 | 1.487e-05 | 0.001389 | -0.001857 | -0.023148 | 0.0037841 | 0.011293 | -0.012361 | 0.028194 | 0.043089 | 0.0017713 | 0.046578 | 3.9385 | 0.61952 | 3.2101 | 40.3145 | 40.2857 | 40.4062 | 2.8217 | -81.1291 | -0.14158 | -81.159 | 40.1463 | 40.2917 | 40.2628 | -81.5755 | 86.6977 | 2.7733 | 87.8145 | 87.0862 | 0.38846 | 2.7445 | 2.865 | 2.3005 | 2.6051 | 2.7469 | 2.717 | 0.41648 | 2.7505 | 2.7216 | 124.1905 | 124.1618 | 124.2822 | 84.4956 | -34.7195 | 124.0224 | 124.1677 | 124.1389 | 83.7345 | -119.1167
1392.8125 | 121.9208 | -71.3928 | 49.8459 | 1.4211e-13 | 0.0012971 | 0.0056624 | 0.0083998 | -0.022721 | 0.0031431 | 0.0036627 | -0.011934 | 0.027981 | 0.043729 | 0.0013439 | 0.047006 | 5.5409 | 0.8164 | 4.8583 | 55.9176 | 55.8037 | 55.9872 | 4.0351 | -65.8866 | -0.18737 | -65.9074 | 55.6766 | 55.8635 | 55.7431 | -66.1953 | 75.4279 | 6.0717 | 76.9337 | 76.2511 | 0.82322 | 5.9578 | 6.1413 | 5.1975 | 5.8307 | 5.5062 | 5.4855 | 0.28792 | 6.0176 | 5.8972 | 127.3104 | 127.1965 | 127.38 | 72.2092 | -45.8108 | 127.0694 | 127.2563 | 127.1359 | 71.2055 | -116.0412
1394.5938 | 121.907 | -54.5792 | 67.2775 | 1.4211e-13 | 0.0015107 | 0.008013 | 0.010964 | -0.023362 | 0.0037841 | 0.0036627 | -0.011934 | 0.028194 | 0.043943 | 0.0013439 | 0.046578 | 6.2231 | 0.91255 | 4.9957 | 58.509 | 58.5465 | 58.5191 | 4.5662 | -63.1806 | 0.16519 | -63.1968 | 58.3962 | 58.5145 | 58.5681 | -63.4983 | 59.1454 | -8.7685 | 60.8022 | 59.5748 | 0.42942 | -8.731 | -8.7584 | -8.9192 | -8.8813 | -8.6014 | -8.6176 | 0.30159 | -8.763 | -8.7095 | 113.0881 | 113.1257 | 113.0983 | 55.4917 | -62.7113 | 112.9754 | 113.0937 | 113.1472 | 54.7444 | -130.7759
1396.3125 | 121.9757 | -120.1813 | 1.4694 | 1.4211e-13 | -0.0010533 | -0.009936 | -0.026217 | -0.023362 | 0.0035703 | 0.011293 | -0.012575 | 0.027767 | 0.043729 | 0.0013439 | 0.047219 | 0.35816 | 0.079243 | 0.22051 | 2.7854 | 2.6973 | 2.9807 | 0.11552 | -118.7386 | -0.33847 | -118.7457 | 2.6256 | 2.7838 | 2.6725 | -119.3233 | 120.2968 | 1.316 | 120.5394 | 120.4018 | 0.10498 | 1.2279 | 1.5113 | 0.85799 | 1.1562 | 1.4426 | 1.4356 | 0.57762 | 1.3143 | 1.2031 | 122.9667 | 122.8786 | 123.162 | 120.2605 | -1.3539 | 122.8068 | 122.965 | 122.8538 | 119.8428 | -120.7927
1398.0938 | 122.0261 | -120.5566 | 1.3458 | 1.4211e-13 | -0.0010533 | -0.0097224 | -0.027285 | -0.023148 | 0.0039977 | 0.0036627 | -0.012788 | 0.027553 | 0.043302 | 0.0017713 | 0.047219 | 0.3078 | 0.065507 | 0.22966 | 1.3982 | 1.3924 | 1.5659 | 0.16131 | -120.2679 | -0.23773 | -120.2887 | 1.3207 | 1.4193 | 1.3996 | -120.9305 | 120.718 | 0.052349 | 120.8644 | 120.7863 | 0.068351 | 0.046527 | 0.22009 | -0.37381 | -0.025123 | 0.28872 | 0.26795 | 0.64176 | 0.073512 | 0.053821 | 121.9548 | 121.949 | 122.1226 | 120.6221 | -1.1845 | 121.8773 | 121.976 | 121.9563 | 120.3189 | -122.2763
1399.8594 | 122.0993 | -120.6619 | 1.2909 | 1.4211e-13 | -0.00062613 | -0.009295 | -0.027072 | -0.023576 | 0.0039977 | 0.0036627 | -0.012361 | 0.027981 | 0.043302 | 0.0017713 | 0.047433 | 0.27117 | 0.051771 | 0.14725 | 1.2654 | 1.3054 | 1.4789 | 0.028521 | -120.3915 | -0.21942 | -120.4123 | 1.2337 | 1.3369 | 1.3218 | -121.0724 | 120.6904 | -0.025494 | 120.9331 | 120.8092 | 0.11873 | 0.014458 | 0.18802 | -0.41047 | -0.057184 | 0.27038 | 0.24961 | 0.66008 | 0.046029 | 0.030916 | 121.9273 | 121.9673 | 122.1408 | 120.7137 | -1.2624 | 121.8956 | 121.9988 | 121.9837 | 120.4425 | -122.3633
1401.5781 | 122.1313 | -120.7672 | 1.1719 | 1.4211e-13 | -0.0012671 | -0.0097224 | -0.027285 | -0.023362 | 0.0039977 | 0.0036627 | -0.012788 | 0.028194 | 0.043302 | 0.0015577 | 0.047433 | 0.23455 | 0.070086 | 0.12436 | 1.183 | 1.2412 | 1.4057 | 0.042258 | -120.4969 | -0.20568 | -120.4993 | 1.165 | 1.2682 | 1.2531 | -121.1686 | 120.8095 | 0.011114 | 121.0018 | 120.8916 | 0.082103 | 0.069373 | 0.23378 | -0.40134 | -0.006842 | 0.27035 | 0.2679 | 0.66924 | 0.096369 | 0.081256 | 121.9502 | 122.0085 | 122.1729 | 120.8373 | -1.1296 | 121.9322 | 122.0355 | 122.0203 | 120.5615 | -122.3404
1403.3594 | 122.2 | -120.7626 | 1.1948 | 1.4211e-13 | -0.0012671 | -0.009295 | -0.027072 | -0.022935 | 0.0042113 | 0.0036627 | -0.012575 | 0.027553 | 0.043089 | 0.0015577 | 0.047433 | 0.19792 | 0.065507 | 0.10605 | 1.2105 | 1.2641 | 1.4331 | 0.060574 | -120.4877 | -0.21026 | -120.5131 | 1.1788 | 1.2866 | 1.2714 | -121.1731 | 120.8232 | 0.015697 | 120.9606 | 120.8687 | 0.045474 | 0.069379 | 0.23837 | -0.4105 | -0.015995 | 0.27493 | 0.24958 | 0.66008 | 0.091795 | 0.076682 | 121.9731 | 122.0268 | 122.1958 | 120.8281 | -1.1342 | 121.9414 | 122.0492 | 122.0341 | 120.5524 | -122.3679
1405.0625 | 122.1405 | -120.8221 | 1.149 | 1.4211e-13 | -0.00083973 | -0.009295 | -0.027072 | -0.023362 | 0.0042113 | 0.0036627 | -0.012148 | 0.027553 | 0.043302 | 0.0015577 | 0.047433 | 0.1796 | 0.05635 | 0.083156 | 1.1555 | 1.2046 | 1.3736 | 0.07431 | -120.5564 | -0.19653 | -120.5817 | 1.1284 | 1.2316 | 1.2211 | -121.2418 | 120.8965 | 0.006532 | 121.0017 | 120.9053 | 0.008846 | 0.055629 | 0.22462 | -0.41967 | -0.020582 | 0.26576 | 0.24041 | 0.66008 | 0.082628 | 0.072093 | 121.9777 | 122.0268 | 122.1958 | 120.8785 | -1.0747 | 121.9505 | 122.0538 | 122.0432 | 120.6256 | -122.3908
1406.8281 | 122.2046 | -120.8038 | 1.1581 | 1.4211e-13 | -0.0012671 | -0.0095086 | -0.027072 | -0.023362 | 0.0035703 | 0.0036627 | -0.012575 | 0.027553 | 0.043516 | 0.0017713 | 0.047433 | 0.17503 | 0.065507 | 0.074 | 1.1509 | 1.2 | 1.3645 | 0.088047 | -120.5793 | -0.19653 | -120.6 | 1.1192 | 1.2225 | 1.2119 | -121.2555 | 120.8919 | -0.007201 | 120.9789 | 120.8778 | -0.014047 | 0.041895 | 0.20631 | -0.45172 | -0.038894 | 0.22456 | 0.20379 | 0.6555 | 0.064316 | 0.053781 | 121.9548 | 122.0039 | 122.1683 | 120.8693 | -1.0701 | 121.9231 | 122.0263 | 122.0158 | 120.6073 | -122.4137
1408.6094 | 122.113 | -120.9778 | 1.0574 | 1.4211e-13 | -0.0012671 | -0.0095086 | -0.026858 | -0.023362 | 0.0035703 | 0.018923 | -0.012788 | 0.027767 | 0.043302 | 0.0015577 | 0.047433 | 0.17503 | 0.060928 | 0.083156 | 1.0594 | 1.1085 | 1.2775 | 0.083468 | -120.6846 | -0.19195 | -120.7054 | 1.0277 | 1.1446 | 1.1249 | -121.3609 | 121.0613 | 0.001939 | 121.1528 | 121.0609 | -0.000312 | 0.051025 | 0.22002 | -0.38308 | -0.029756 | 0.2932 | 0.27243 | 0.65551 | 0.087187 | 0.067496 | 122.0372 | 122.0862 | 122.2552 | 121.0387 | -0.97397 | 122.0055 | 122.1224 | 122.1027 | 120.7858 | -122.4183
1410.3125 | 122.1954 | -121.0373 | 0.98419 | 1.4211e-13 | -0.0012671 | -0.0097224 | -0.026858 | -0.022935 | 0.0037841 | 0.011293 | -0.012788 | 0.027767 | 0.043516 | 0.0013439 | 0.047433 | 0.15671 | 0.060928 | 0.064843 | 0.99528 | 1.0489 | 1.2134 | 0.060574 | -120.7487 | -0.19195 | -120.7786 | 0.96816 | 1.0714 | 1.0608 | -121.4341 | 121.0979 | 0.011084 | 121.194 | 121.1021 | 0.004269 | 0.064741 | 0.22917 | -0.39683 | -0.016034 | 0.2886 | 0.25868 | 0.65551 | 0.087172 | 0.076637 | 122.0326 | 122.0862 | 122.2507 | 121.0982 | -0.92362 | 122.0054 | 122.1087 | 122.0981 | 120.8453 | -122.4183
1412.0938 | 122.1222 | -121.0648 | 1.0117 | 1.4211e-13 | -0.0012671 | -0.0095086 | -0.026858 | -0.023576 | 0.0039977 | 0.018923 | -0.012575 | 0.028194 | 0.043516 | 0.0015577 | 0.047006 | 0.15671 | 0.060928 | 0.069421 | 0.99528 | 1.0398 | 1.1996 | 0.07431 | -120.767 | -0.19195 | -120.7832 | 0.96358 | 1.0714 | 1.0563 | -121.4433 | 121.1391 | -0.016382 | 121.2215 | 121.1342 | -0.004889 | 0.028117 | 0.18797 | -0.37852 | -0.048079 | 0.29775 | 0.28156 | 0.66009 | 0.059706 | 0.044593 | 122.06 | 122.1045 | 122.2644 | 121.1257 | -0.93735 | 122.0283 | 122.1361 | 122.121 | 120.8728 | -122.4549
1413.8906 | 122.1268 | -121.0739 | 1.0117 | 1.4211e-13 | -0.00083973 | -0.0095086 | -0.02643 | -0.023576 | 0.0039977 | 0.011293 | -0.012361 | 0.027767 | 0.043516 | 0.0015577 | 0.047219 | 0.17045 | 0.065507 | 0.083156 | 0.99528 | 1.0444 | 1.2042 | 0.078889 | -120.7716 | -0.19653 | -120.7832 | 0.96358 | 1.0668 | 1.0517 | -121.4479 | 121.1528 | -0.016382 | 121.2444 | 121.1571 | 0.004267 | 0.032696 | 0.19254 | -0.37394 | -0.048079 | 0.30233 | 0.29072 | 0.66466 | 0.055127 | 0.040014 | 122.0692 | 122.1183 | 122.2781 | 121.1394 | -0.93277 | 122.0375 | 122.1407 | 122.1256 | 120.8774 | -122.4595
1415.6094 | 122.1222 | -121.1884 | 0.90179 | 1.4211e-13 | -0.00083973 | -0.009295 | -0.026644 | -0.023362 | 0.0039977 | 0.026554 | -0.012575 | 0.027553 | 0.043302 | 0.0013439 | 0.047219 | 0.1796 | 0.065507 | 0.096891 | 0.91744 | 0.97109 | 1.1355 | 0.07431 | -120.8494 | -0.19195 | -120.8656 | 0.89032 | 0.99353 | 0.98757 | -121.5303 | 121.2627 | 0.015649 | 121.368 | 121.2852 | 0.022581 | 0.069297 | 0.23373 | -0.34192 | -0.011471 | 0.33893 | 0.32274 | 0.66467 | 0.091733 | 0.085778 | 122.1058 | 122.1594 | 122.3239 | 121.2539 | -0.82748 | 122.0787 | 122.1819 | 122.1759 | 120.9964 | -122.4321
1417.375 | 122.1634 | -121.7148 | 0.3891 | 1.4211e-13 | -0.00083973 | -0.0097224 | -0.027285 | -0.023576 | 0.0035703 | -0.0039678 | -0.012361 | 0.027767 | 0.043302 | 0.0013439 | 0.047219 | 0.12466 | 0.038035 | 0.037373 | 0.39551 | 0.43536 | 0.6044 | 0.019363 | -121.3897 | -0.2011 | -121.4059 | 0.35464 | 0.45325 | 0.45188 | -122.0706 | 121.7341 | 0.006408 | 121.8394 | 121.7522 | 0.01801 | 0.046258 | 0.21531 | -0.3558 | -0.03446 | 0.32507 | 0.30889 | 0.66468 | 0.064153 | 0.062776 | 122.1103 | 122.1501 | 122.3192 | 121.7528 | -0.36974 | 122.0694 | 122.168 | 122.1667 | 121.5137 | -122.4597
1419.1562 | 122.168 | -121.8018 | 0.28839 | 1.4211e-13 | -0.0010533 | -0.01015 | -0.027499 | -0.023362 | 0.0035703 | 0.011293 | -0.012575 | 0.027767 | 0.043302 | 0.0017713 | 0.047006 | 0.11093 | 0.042614 | 0.037373 | 0.29936 | 0.33462 | 0.4991 | 0.019363 | -121.4996 | -0.19653 | -121.5112 | 0.26307 | 0.37084 | 0.36946 | -122.1759 | 121.8211 | 0.01097 | 121.9127 | 121.8391 | 0.01801 | 0.046229 | 0.21071 | -0.37413 | -0.025322 | 0.30216 | 0.29055 | 0.66468 | 0.082447 | 0.081069 | 122.1011 | 122.1364 | 122.3009 | 121.8444 | -0.26903 | 122.0648 | 122.1726 | 122.1712 | 121.6052 | -122.4643
1420.9219 | 122.1405 | -121.8246 | 0.29755 | 1.4211e-13 | -0.0010533 | -0.0097224 | -0.027713 | -0.023362 | 0.0037841 | -0.0039678 | -0.012575 | 0.027767 | 0.043516 | 0.0017713 | 0.047219 | 0.10635 | 0.033457 | 0.04653 | 0.29478 | 0.32546 | 0.48994 | 0.023942 | -121.5088 | -0.19653 | -121.5249 | 0.24933 | 0.3571 | 0.34657 | -122.1988 | 121.8486 | -0.002764 | 121.931 | 121.8712 | 0.022588 | 0.027917 | 0.19239 | -0.37414 | -0.048212 | 0.31589 | 0.2997 | 0.67384 | 0.059556 | 0.049021 | 122.1194 | 122.1501 | 122.3146 | 121.8581 | -0.2736 | 122.074 | 122.1817 | 122.1712 | 121.6281 | -122.4963
1422.7031 | 122.2366 | -121.8063 | 0.26093 | 1.4211e-13 | -0.0010533 | -0.0095086 | -0.027713 | -0.023362 | 0.0039977 | 0.011293 | -0.012575 | 0.027981 | 0.043516 | 0.0017713 | 0.047647 | 0.10177 | 0.033457 | 0.041952 | 0.28105 | 0.32088 | 0.48536 | 0.023942 | -121.5316 | -0.19653 | -121.5295 | 0.24018 | 0.34794 | 0.32825 | -122.1988 | 121.8303 | 0.020122 | 121.9081 | 121.8483 | 0.01801 | 0.059959 | 0.22444 | -0.39245 | -0.020748 | 0.27469 | 0.27681 | 0.66926 | 0.087019 | 0.067328 | 122.0874 | 122.1272 | 122.2917 | 121.8398 | -0.23698 | 122.0465 | 122.1543 | 122.1346 | 121.6098 | -122.4597
1424.5156 | 122.2549 | -121.7926 | 0.24261 | 1.4211e-13 | -0.00083973 | -0.0095086 | -0.027285 | -0.023362 | 0.0037841 | -0.0039678 | -0.012788 | 0.027767 | 0.043302 | 0.0015577 | 0.047219 | 0.10635 | 0.028878 | 0.055687 | 0.2902 | 0.32088 | 0.48536 | 0.014784 | -121.5271 | -0.2011 | -121.5478 | 0.24476 | 0.34794 | 0.34199 | -122.2079 | 121.8074 | 0.047589 | 121.899 | 121.8483 | 0.040903 | 0.078269 | 0.24275 | -0.41534 | 0.00214 | 0.26553 | 0.24477 | 0.6601 | 0.10533 | 0.099374 | 122.0828 | 122.1135 | 122.278 | 121.8215 | -0.22783 | 122.0374 | 122.1405 | 122.1346 | 121.5915 | -122.4506
1426.2812 | 122.1954 | -121.8109 | 0.27924 | 1.4211e-13 | -0.0010533 | -0.0097224 | -0.027499 | -0.023576 | 0.0035703 | 0.0036627 | -0.012575 | 0.027981 | 0.043516 | 0.0013439 | 0.047219 | 0.11093 | 0.033457 | 0.064843 | 0.29478 | 0.33004 | 0.48994 | 0.028521 | -121.5133 | -0.2011 | -121.5341 | 0.24933 | 0.36626 | 0.34657 | -122.1988 | 121.8394 | 0.015546 | 121.9218 | 121.8758 | 0.036322 | 0.050806 | 0.2107 | -0.38787 | -0.029902 | 0.29758 | 0.27681 | 0.66468 | 0.087023 | 0.067331 | 122.1057 | 122.141 | 122.3009 | 121.8444 | -0.25071 | 122.0602 | 122.1772 | 122.1575 | 121.6098 | -122.478
1428 | 122.2595 | -121.7926 | 0.2655 | 1.4211e-13 | -0.00062613 | -0.0097224 | -0.027499 | -0.023576 | 0.0035703 | 0.011293 | -0.012575 | 0.027981 | 0.043089 | 0.0015577 | 0.047219 | 0.11093 | 0.033457 | 0.064843 | 0.28563 | 0.32088 | 0.4762 | 0.0331 | -121.5316 | -0.19653 | -121.5341 | 0.24933 | 0.35252 | 0.33283 | -122.2079 | 121.8257 | 0.020122 | 121.9035 | 121.8574 | 0.031743 | 0.055381 | 0.2107 | -0.41534 | -0.016169 | 0.26095 | 0.2585 | 0.67384 | 0.08702 | 0.067328 | 122.0782 | 122.1135 | 122.2688 | 121.8261 | -0.2324 | 122.0419 | 122.1451 | 122.1254 | 121.5961 | -122.4734
1429.7188 | 122.1771 | -121.8292 | 0.29755 | 1.4211e-13 | -0.0010533 | -0.0097224 | -0.027713 | -0.023362 | 0.0037841 | 0.011293 | -0.012361 | 0.027767 | 0.043516 | 0.0017713 | 0.047433 | 0.10635 | 0.033457 | 0.069421 | 0.29936 | 0.33462 | 0.4991 | 0.023942 | -121.5225 | -0.19653 | -121.5433 | 0.25391 | 0.37084 | 0.34199 | -122.2034 | 121.8532 | 0.001815 | 121.9356 | 121.8986 | 0.045479 | 0.037074 | 0.20155 | -0.37414 | -0.043634 | 0.30673 | 0.28596 | 0.6601 | 0.073292 | 0.044443 | 122.1286 | 122.1638 | 122.3283 | 121.8627 | -0.2736 | 122.0831 | 122.2001 | 122.1712 | 121.6327 | -122.5009
1431.5156 | 122.1497 | -121.8063 | 0.31586 | 1.4211e-13 | -0.00062613 | -0.0097224 | -0.027285 | -0.023362 | 0.0037841 | 0.011293 | -0.012788 | 0.027981 | 0.043729 | 0.0011303 | 0.047006 | 0.11093 | 0.0243 | 0.069421 | 0.30394 | 0.35294 | 0.51741 | 0.037679 | -121.4996 | -0.21026 | -121.5158 | 0.27223 | 0.37542 | 0.36488 | -122.1805 | 121.844 | -0.011918 | 121.9173 | 121.8758 | 0.031742 | 0.037079 | 0.20155 | -0.37413 | -0.043631 | 0.30674 | 0.29055 | 0.66468 | 0.059559 | 0.049025 | 122.1103 | 122.1593 | 122.3237 | 121.8306 | -0.27818 | 122.0786 | 122.1818 | 122.1712 | 121.5961 | -122.4963
1433.2344 | 122.2366 | -121.7972 | 0.3067 | 1.4211e-13 | -0.00062613 | -0.0095086 | -0.027285 | -0.023576 | 0.0037841 | 0.011293 | -0.012361 | 0.027767 | 0.043302 | 0.0015577 | 0.047433 | 0.11551 | 0.033457 | 0.074 | 0.3131 | 0.3392 | 0.50825 | 0.0331 | -121.5088 | -0.2011 | -121.5341 | 0.27223 | 0.36168 | 0.3603 | -122.1896 | 121.8303 | 0.006394 | 121.9127 | 121.8712 | 0.0409 | 0.032497 | 0.20155 | -0.39245 | -0.034476 | 0.28843 | 0.26308 | 0.65552 | 0.054978 | 0.053601 | 122.1103 | 122.1364 | 122.3054 | 121.8306 | -0.2736 | 122.0694 | 122.1589 | 122.1575 | 121.5961 | -122.4963
1434.9375 | 122.1588 | -121.8018 | 0.32501 | 1.4211e-13 | -0.00062613 | -0.0095086 | -0.027072 | -0.023362 | 0.0037841 | 0.0036627 | -0.012575 | 0.027553 | 0.043729 | 0.0017713 | 0.047219 | 0.11551 | 0.042614 | 0.069421 | 0.3131 | 0.35294 | 0.50825 | 0.028521 | -121.5042 | -0.19653 | -121.5295 | 0.26765 | 0.37542 | 0.36488 | -122.1896 | 121.8303 | -0.011916 | 121.9173 | 121.8712 | 0.0409 | 0.027924 | 0.18324 | -0.38787 | -0.057364 | 0.29758 | 0.27223 | 0.6601 | 0.050404 | 0.03987 | 122.1149 | 122.1547 | 122.31 | 121.8444 | -0.29649 | 122.0694 | 122.1772 | 122.1666 | 121.6052 | -122.5146
1436.7188 | 122.2824 | -121.7606 | 0.28381 | 1.4211e-13 | -0.0010533 | -0.0097224 | -0.027285 | -0.023789 | 0.0037841 | 0.011293 | -0.012361 | 0.027767 | 0.043516 | 0.0013439 | 0.047647 | 0.12009 | 0.028878 | 0.083156 | 0.30394 | 0.34836 | 0.50825 | 0.037679 | -121.5088 | -0.21484 | -121.5249 | 0.26307 | 0.37084 | 0.35572 | -122.1988 | 121.7982 | 0.020126 | 121.8806 | 121.8437 | 0.045477 | 0.064544 | 0.22444 | -0.43823 | -0.020744 | 0.25181 | 0.23561 | 0.67384 | 0.087025 | 0.071911 | 122.0645 | 122.1089 | 122.2688 | 121.7894 | -0.24613 | 122.0236 | 122.1314 | 122.1163 | 121.5457 | -122.4826
1438.5 | 122.168 | -121.8155 | 0.31586 | 1.4211e-13 | -0.0010533 | -0.0095086 | -0.027499 | -0.023148 | 0.0037841 | 0.011293 | -0.012575 | 0.027981 | 0.043516 | 0.0019849 | 0.047647 | 0.12009 | 0.033457 | 0.078578 | 0.3131 | 0.34836 | 0.51283 | 0.0331 | -121.4996 | -0.2011 | -121.5158 | 0.27223 | 0.38457 | 0.36946 | -122.1942 | 121.8486 | -0.002761 | 121.9356 | 121.8941 | 0.045478 | 0.0325 | 0.19698 | -0.37871 | -0.043631 | 0.31589 | 0.2997 | 0.67842 | 0.068716 | 0.053603 | 122.1286 | 122.1638 | 122.3283 | 121.8489 | -0.28276 | 122.0877 | 122.2001 | 122.185 | 121.6144 | -122.5101
1440.2812 | 122.0947 | -121.2479 | 0.87433 | 1.4211e-13 | -0.00083973 | -0.0088676 | -0.027072 | -0.023576 | 0.0042113 | 0.0036627 | -0.012361 | 0.027767 | 0.043302 | 0.0017713 | 0.047219 | 0.14298 | 0.042614 | 0.083156 | 0.4184 | 0.47199 | 0.6273 | 0.051416 | -121.3806 | -0.19195 | -121.4059 | 0.39127 | 0.49446 | 0.48392 | -122.0706 | 121.2993 | -0.45593 | 121.3908 | 121.331 | 0.03174 | -0.40234 | -0.24703 | -0.82271 | -0.48306 | -0.13269 | -0.15803 | 0.66468 | -0.37987 | -0.3904 | 121.6663 | 121.7199 | 121.8752 | 121.2905 | -0.82291 | 121.6391 | 121.7423 | 121.7318 | 121.0559 | -122.9449
1442.0469 | 122.1451 | -119.87 | 2.0782 | 1.4211e-13 | -0.00083973 | -0.0067308 | -0.023012 | -0.023362 | 0.0037841 | 0.011293 | -0.012148 | 0.027981 | 0.043089 | 0.0015577 | 0.047647 | 0.45431 | 0.14334 | 0.27087 | 2.0895 | 2.1433 | 2.2985 | 0.097205 | -119.5811 | -0.19653 | -119.5927 | 2.0716 | 2.1656 | 2.1002 | -120.2574 | 119.9672 | 0.011263 | 120.3243 | 120.1409 | 0.17366 | 0.065049 | 0.22024 | -0.38737 | -0.006672 | 0.28888 | 0.27727 | 0.66464 | 0.087403 | 0.021925 | 121.9595 | 122.0133 | 122.1685 | 120.0133 | -1.981 | 121.9416 | 122.0356 | 121.9702 | 119.6735 | -122.3356
1443.7656 | 122.1588 | -121.2021 | 0.75531 | 1.4211e-13 | -0.00041233 | -0.0084402 | -0.024294 | -0.023362 | 0.0035703 | 0.0036627 | -0.013002 | 0.028194 | 0.043516 | 0.0015577 | 0.047647 | 0.28491 | 0.12503 | 0.32581 | 1.0182 | 1.0672 | 1.2179 | 0.051416 | -120.6571 | -0.21484 | -120.6825 | 0.98647 | 1.0943 | 1.0242 | -121.3425 | 121.2535 | 0.26286 | 121.487 | 121.5279 | 0.27439 | 0.31194 | 0.46263 | -0.14046 | 0.23116 | 0.54497 | 0.51963 | 0.66008 | 0.33895 | 0.26889 | 122.2203 | 122.2693 | 122.42 | 121.3271 | -0.70389 | 122.1886 | 122.2963 | 122.2263 | 120.9872 | -122.0979
1445.5469 | 121.9299 | -118.9453 | 2.8702 | 1.4211e-13 | -0.00062613 | -0.0056624 | -0.017669 | -0.023148 | 0.0039977 | 0.011293 | -0.012575 | 0.027767 | 0.043302 | 0.0013439 | 0.047006 | 0.59166 | 0.32191 | 0.76074 | 2.8724 | 2.9217 | 3.0814 | 0.32615 | -118.6379 | -0.19653 | -118.6678 | 2.8499 | 2.9486 | 2.8877 | -119.3187 | 119.2715 | 0.002237 | 119.537 | 119.7061 | 0.43459 | 0.051535 | 0.21125 | -0.3734 | -0.020259 | 0.30741 | 0.27748 | 0.65088 | 0.078413 | 0.017514 | 121.8177 | 121.867 | 122.0267 | 119.2672 | -2.544 | 121.7952 | 121.8939 | 121.833 | 118.7488 | -122.1889
1447.3281 | 121.8292 | -119.0826 | 2.6871 | 1.4211e-13 | -0.00083973 | -0.0054488 | -0.017883 | -0.023362 | 0.0037841 | 0.011293 | -0.012575 | 0.027981 | 0.043302 | 0.0013439 | 0.047219 | 0.5825 | 0.29444 | 0.63713 | 2.7671 | 2.821 | 2.9715 | 0.38568 | -118.6974 | -0.2011 | -118.7136 | 2.7309 | 2.8524 | 2.7778 | -119.3553 | 119.4683 | 0.080039 | 119.6651 | 119.7198 | 0.25145 | 0.1339 | 0.28447 | -0.2727 | 0.043805 | 0.38522 | 0.36903 | 0.64172 | 0.16537 | 0.090732 | 121.8498 | 121.9036 | 122.0542 | 119.3771 | -2.3014 | 121.8135 | 121.9351 | 121.8604 | 118.8815 | -122.0424
1449.0469 | 121.907 | -119.1467 | 2.5269 | 1.4211e-13 | -0.00062613 | -0.0060898 | -0.016815 | -0.023148 | 0.0037841 | 0.0036627 | -0.012361 | 0.027767 | 0.043089 | 0.0013439 | 0.047219 | 0.46804 | 0.41348 | 0.81568 | 2.4558 | 2.5005 | 2.6602 | 0.35363 | -118.9859 | -0.2011 | -119.0021 | 2.4195 | 2.5319 | 2.4527 | -119.6621 | 119.5004 | -0.071074 | 119.6148 | 119.9624 | 0.46206 | -0.026403 | 0.13334 | -0.51539 | -0.10731 | 0.16084 | 0.14465 | 0.66004 | 0.005083 | -0.074131 | 121.6025 | 121.6472 | 121.8069 | 119.5602 | -2.1732 | 121.5663 | 121.6787 | 121.5995 | 118.9456 | -122.189
1450.8281 | 121.6049 | -117.9977 | 3.6484 | 1.4211e-13 | -0.00062613 | -0.0037394 | -0.012541 | -0.022935 | 0.0037841 | 0.0036627 | -0.012361 | 0.027981 | 0.043089 | 0.0015577 | 0.047006 | 0.66949 | 0.6882 | 1.1087 | 3.5821 | 3.6406 | 3.782 | 0.86646 | -117.7313 | -0.19195 | -117.7521 | 3.5687 | 3.672 | 3.5882 | -118.4075 | 118.8642 | -0.066311 | 118.6672 | 119.1064 | 0.24223 | -0.007772 | 0.13358 | -0.40978 | -0.079633 | 0.26642 | 0.24565 | 0.65544 | 0.023634 | -0.060158 | 121.5798 | 121.6383 | 121.7797 | 118.6859 | -2.7819 | 121.5665 | 121.6698 | 121.586 | 117.8058 | -122.0559
1452.5938 | 121.7056 | -118.9819 | 2.6642 | 1.4211e-13 | -0.00041233 | -0.0028846 | -0.017669 | -0.023362 | 0.0039977 | 0.0036627 | -0.012361 | 0.027767 | 0.043302 | 0.0011303 | 0.047647 | 0.47262 | 0.41348 | 0.69665 | 2.6252 | 2.6745 | 2.8296 | 0.60089 | -118.7066 | -0.20568 | -118.7274 | 2.5935 | 2.7013 | 2.6313 | -119.3874 | 119.5828 | -0.039003 | 119.4546 | 119.6786 | 0.095759 | 0.010266 | 0.16542 | -0.40546 | -0.070662 | 0.27535 | 0.25458 | 0.66004 | 0.037161 | -0.032895 | 121.6071 | 121.6564 | 121.8115 | 119.3954 | -2.0633 | 121.5755 | 121.6833 | 121.6132 | 118.7763 | -122.0516
1454.375 | 121.7377 | -118.9453 | 2.6688 | 1.4211e-13 | -0.00062613 | -0.0048078 | -0.017456 | -0.023362 | 0.0037841 | 0.011293 | -0.012361 | 0.027767 | 0.043302 | 0.0013439 | 0.047219 | 0.4131 | 0.35854 | 0.63713 | 2.5611 | 2.6149 | 2.7701 | 0.35363 | -118.757 | -0.2011 | -118.7731 | 2.5386 | 2.6418 | 2.5763 | -119.4332 | 119.2989 | -0.10768 | 119.3584 | 119.5824 | 0.2835 | -0.053837 | 0.10132 | -0.48787 | -0.13018 | 0.18836 | 0.17217 | 0.66004 | -0.026938 | -0.092415 | 121.5064 | 121.5602 | 121.7154 | 119.3038 | -2.3151 | 121.4839 | 121.5871 | 121.5217 | 118.7442 | -122.1019
1456.1562 | 121.6919 | -118.9453 | 2.5955 | 1.4211e-13 | -0.00062613 | -0.0065172 | -0.022157 | -0.023362 | 0.0037841 | 0.011293 | -0.012575 | 0.02734 | 0.042875 | 0.0013439 | 0.047006 | 0.27117 | 0.18455 | 0.27544 | 1.7003 | 1.7083 | 1.891 | 0.17963 | -119.6315 | -0.22858 | -119.6568 | 1.6458 | 1.7582 | 1.6789 | -120.3123 | 119.1249 | -0.89517 | 119.2165 | 119.2208 | 0.095818 | -0.88722 | -0.70453 | -1.367 | -0.94975 | -0.68617 | -0.71152 | 0.65548 | -0.83737 | -0.91658 | 120.6457 | 120.6536 | 120.8363 | 119.1299 | -2.4159 | 120.5911 | 120.7035 | 120.6243 | 118.7167 | -122.9078
1457.9219 | 121.7514 | -119.0964 | 2.4261 | 1.4211e-13 | -0.00019873 | -0.0037394 | -0.016174 | -0.023362 | 0.0035703 | 0.0036627 | -0.012361 | 0.027553 | 0.043089 | 0.0015577 | 0.047006 | 0.39021 | 0.37685 | 0.73785 | 2.497 | 2.5462 | 2.7106 | 0.32615 | -118.7844 | -0.2011 | -118.796 | 2.4699 | 2.5731 | 2.5077 | -119.4561 | 119.4225 | 0.07084 | 119.4866 | 119.8342 | 0.4117 | 0.12009 | 0.28442 | -0.3597 | 0.043757 | 0.31195 | 0.30034 | 0.66004 | 0.147 | 0.081521 | 121.5934 | 121.6426 | 121.8069 | 119.4732 | -2.1 | 121.5663 | 121.6695 | 121.604 | 118.8953 | -121.8822
1459.7031 | 121.637 | -119.6274 | 1.9089 | 1.4211e-13 | -0.00062613 | -0.0043804 | -0.02002 | -0.023148 | 0.0039977 | -0.0039678 | -0.012788 | 0.027553 | 0.043302 | 0.0013439 | 0.046792 | 0.39479 | 0.32649 | 0.50436 | 1.9705 | 2.0105 | 2.1703 | 0.2712 | -119.2652 | -0.21026 | -119.2814 | 1.9296 | 2.0374 | 1.972 | -119.9414 | 119.8986 | 0.061597 | 120.0222 | 120.1317 | 0.23315 | 0.10163 | 0.26141 | -0.31405 | 0.020767 | 0.36219 | 0.346 | 0.66005 | 0.12857 | 0.063096 | 121.5979 | 121.6379 | 121.7977 | 119.9539 | -1.6377 | 121.557 | 121.6648 | 121.5994 | 119.4171 | -121.8503
1461.4375 | 121.4859 | -119.8196 | 1.6754 | 1.4211e-13 | -0.00062613 | -0.0065172 | -0.023653 | -0.023148 | 0.0035703 | 0.0036627 | -0.012148 | 0.027767 | 0.043302 | 0.0017713 | 0.047006 | 0.23455 | 0.20744 | 0.33954 | 1.1738 | 1.2275 | 1.3873 | 0.078889 | -119.9703 | -0.20568 | -119.9865 | 1.1513 | 1.2591 | 1.189 | -120.6557 | 119.8985 | -0.50158 | 120.0542 | 120.1592 | 0.26065 | -0.4479 | -0.28807 | -0.83608 | -0.52412 | -0.15067 | -0.16686 | 0.66922 | -0.41633 | -0.48639 | 120.9935 | 121.0472 | 121.207 | 120.0271 | -1.5965 | 120.9709 | 121.0787 | 121.0087 | 119.614 | -122.3311
1463.2188 | 121.344 | -120.4697 | 0.86975 | 1.4211e-13 | -0.00041233 | -0.0075856 | -0.024294 | -0.023576 | 0.0037841 | -0.0039678 | -0.012788 | 0.027767 | 0.042875 | 0.0011303 | 0.047006 | 0.22081 | 0.17539 | 0.31207 | 0.93118 | 0.97109 | 1.1355 | 0.051416 | -120.0573 | -0.21484 | -120.0735 | 0.8949 | 1.0073 | 0.92805 | -120.7381 | 120.5211 | 0.061427 | 120.6905 | 120.7817 | 0.26065 | 0.10134 | 0.26577 | -0.26848 | 0.025151 | 0.41236 | 0.39617 | 0.66465 | 0.13751 | 0.058299 | 121.4008 | 121.4408 | 121.6052 | 120.6451 | -0.81834 | 121.3646 | 121.4769 | 121.3977 | 120.2548 | -121.6079
1465 | 121.3623 | -118.8675 | 2.3117 | 1.4211e-13 | -0.00019873 | -0.0035256 | -0.017883 | -0.023148 | 0.0042113 | 0.018923 | -0.012575 | 0.027767 | 0.042875 | 0.0013439 | 0.047006 | 0.39479 | 0.43179 | 0.69207 | 2.2772 | 2.1799 | 2.4771 | 0.33531 | -118.6104 | -0.19653 | -118.6358 | 2.241 | 2.3488 | 2.2833 | -119.305 | 119.2028 | -0.034483 | 119.2623 | 119.5596 | 0.35676 | -0.13178 | 0.16535 | -0.43748 | -0.070728 | 0.25706 | 0.23171 | 0.66919 | 0.037087 | -0.028391 | 121.1447 | 121.0474 | 121.3445 | 119.2993 | -1.9764 | 121.1085 | 121.2163 | 121.1508 | 118.671 | -121.6167
1466.7188 | 121.701 | -121.4401 | 0.13275 | 1.4211e-13 | -0.00083973 | -0.01015 | -0.02814 | -0.023148 | 0.0035703 | 0.0036627 | -0.013002 | 0.027767 | 0.042875 | 0.0011303 | 0.046792 | 0.10177 | 0.042614 | 0.037373 | 0.14827 | 0.17894 | 0.34342 | 0.037679 | -121.1058 | -0.22858 | -121.1266 | 0.10282 | 0.20601 | 0.1909 | -121.805 | 121.4778 | 0.015523 | 121.5419 | 121.4775 | -0.000306 | 0.046186 | 0.21067 | -0.36488 | -0.029929 | 0.3343 | 0.31353 | 0.67841 | 0.073257 | 0.058144 | 121.5884 | 121.6191 | 121.7835 | 121.4827 | -0.095072 | 121.5429 | 121.6461 | 121.631 | 121.2115 | -121.9378
1468.5 | 121.7239 | -121.5454 | 0.16937 | 1.4211e-13 | -0.00062613 | -0.0095086 | -0.02814 | -0.023362 | 0.0039977 | 0.011293 | -0.012575 | 0.027767 | 0.043089 | 0.0013439 | 0.047006 | 0.10635 | 0.042614 | 0.032795 | 0.15743 | 0.18352 | 0.34342 | 0.028521 | -121.234 | -0.22858 | -121.2594 | 0.1074 | 0.20601 | 0.19547 | -121.9195 | 121.5739 | -0.011942 | 121.6518 | 121.5782 | 0.004274 | 0.014143 | 0.17405 | -0.37407 | -0.061972 | 0.31138 | 0.28603 | 0.6601 | 0.036635 | 0.0261 | 121.7028 | 121.7289 | 121.8888 | 121.588 | -0.14085 | 121.6528 | 121.7514 | 121.7409 | 121.3168 | -122.0888
1470.2812 | 121.8109 | -121.582 | 0.13733 | 1.4211e-13 | -0.00041233 | -0.01015 | -0.027926 | -0.023362 | 0.0039977 | 0.011293 | -0.012575 | 0.027767 | 0.043302 | 0.0011303 | 0.047219 | 0.12924 | 0.05635 | 0.037373 | 0.15743 | 0.1881 | 0.35716 | 0.042258 | -121.2844 | -0.22858 | -121.3052 | 0.11198 | 0.21516 | 0.20463 | -121.9744 | 121.6243 | 0.020102 | 121.7113 | 121.6194 | -0.004885 | 0.050766 | 0.21983 | -0.39239 | -0.02535 | 0.29763 | 0.27686 | 0.66926 | 0.077836 | 0.067302 | 121.7395 | 121.7701 | 121.9392 | 121.6384 | -0.095071 | 121.694 | 121.7972 | 121.7867 | 121.3535 | -122.1118
1472 | 121.8704 | -121.5271 | 0.21515 | 1.4211e-13 | 0.00086967 | -0.0097224 | -0.027713 | -0.023576 | 0.0039977 | 0.011293 | -0.012361 | 0.027553 | 0.043302 | 0.0013439 | 0.047433 | 0.23455 | 0.17539 | 0.087735 | 0.26731 | 0.29341 | 0.45789 | 0.055995 | -121.2111 | -0.224 | -121.2273 | 0.21728 | 0.31589 | 0.30536 | -121.9012 | 121.5831 | 0.052163 | 121.7616 | 121.6148 | 0.03174 | 0.078261 | 0.24274 | -0.37406 | 0.002135 | 0.31596 | 0.29977 | 0.67383 | 0.10075 | 0.090211 | 121.7944 | 121.8205 | 121.985 | 121.7025 | -0.15915 | 121.7444 | 121.843 | 121.8325 | 121.3031 | -122.1163
1473.7812 | 121.8979 | -121.55 | 0.19226 | 1.4211e-13 | 0.00065587 | -0.0097224 | -0.027713 | -0.023576 | 0.0037841 | 0.0036627 | -0.012361 | 0.027767 | 0.043516 | 0.0013439 | 0.047219 | 0.18418 | 0.13419 | 0.078578 | 0.21695 | 0.24304 | 0.40753 | 0.055995 | -121.2844 | -0.23773 | -121.3052 | 0.15776 | 0.26553 | 0.26415 | -121.9836 | 121.606 | 0.024689 | 121.7342 | 121.6286 | 0.022583 | 0.050781 | 0.21526 | -0.43359 | -0.034497 | 0.26559 | 0.24482 | 0.67841 | 0.073269 | 0.071891 | 121.7669 | 121.793 | 121.9575 | 121.6842 | -0.13627 | 121.7078 | 121.8155 | 121.8141 | 121.3123 | -122.1758
1475.5 | 121.875 | -121.3028 | 0.49439 | 1.4211e-13 | 0.0047157 | -0.0084402 | -0.026858 | -0.023362 | 0.0039977 | 0.011293 | -0.012361 | 0.027767 | 0.043089 | 0.0015577 | 0.047006 | 0.46804 | 0.38143 | 0.23882 | 0.47334 | 0.51778 | 0.68682 | 0.24373 | -121.0051 | -0.23316 | -121.0259 | 0.45079 | 0.5494 | 0.54345 | -121.6905 | 121.5465 | -0.021046 | 121.7708 | 121.5416 | -0.004913 | 0.023392 | 0.19243 | -0.38774 | -0.043597 | 0.2977 | 0.27693 | 0.66467 | 0.055018 | 0.049062 | 121.7761 | 121.8206 | 121.9896 | 121.6842 | -0.25065 | 121.7536 | 121.8522 | 121.8462 | 121.0696 | -122.1849
1477.2656 | 121.8704 | -121.1197 | 0.6546 | 1.4211e-13 | 0.0057841 | -0.008654 | -0.02643 | -0.023576 | 0.0042113 | 0.018923 | -0.012575 | 0.027981 | 0.043089 | 0.0015577 | 0.047006 | 0.61455 | 0.53252 | 0.29376 | 0.61985 | 0.67804 | 0.82876 | 0.38568 | -120.8494 | -0.22858 | -120.8702 | 0.60188 | 0.69592 | 0.69454 | -121.5394 | 121.5054 | -0.034754 | 121.7342 | 121.4134 | -0.09192 | 0.023438 | 0.17415 | -0.41974 | -0.052724 | 0.27027 | 0.2495 | 0.66925 | 0.041316 | 0.039939 | 121.7395 | 121.7977 | 121.9484 | 121.6522 | -0.26893 | 121.7216 | 121.8156 | 121.8142 | 120.8911 | -122.194
1479.0469 | 121.8384 | -121.0327 | 0.74158 | 1.4211e-13 | 0.0072799 | -0.0075856 | -0.026003 | -0.023789 | 0.0042113 | 0.018923 | -0.012575 | 0.027767 | 0.043089 | 0.0013439 | 0.047219 | 0.71985 | 0.61952 | 0.38074 | 0.72515 | 0.76962 | 0.92949 | 0.47268 | -120.735 | -0.23773 | -120.774 | 0.69345 | 0.78749 | 0.78153 | -121.4433 | 121.5054 | -0.016426 | 121.7526 | 121.4135 | -0.091933 | 0.028041 | 0.18791 | -0.41057 | -0.048129 | 0.29776 | 0.25868 | 0.66924 | 0.045913 | 0.039957 | 121.7579 | 121.8023 | 121.9622 | 121.6522 | -0.2689 | 121.7262 | 121.8202 | 121.8142 | 120.795 | -122.1849
1480.7656 | 121.9574 | -120.9641 | 0.7782 | 1.4211e-13 | 0.0070661 | -0.0069446 | -0.026003 | -0.023362 | 0.0042113 | -0.0039678 | -0.012361 | 0.027767 | 0.042875 | 0.0015577 | 0.047006 | 0.77022 | 0.67904 | 0.33954 | 0.77551 | 0.83372 | 0.98901 | 0.5322 | -120.68 | -0.224 | -120.7054 | 0.75755 | 0.86075 | 0.85479 | -121.3746 | 121.4963 | -0.002685 | 121.7343 | 121.3036 | -0.19266 | 0.055525 | 0.21081 | -0.41055 | -0.020651 | 0.28404 | 0.25869 | 0.66924 | 0.08255 | 0.076594 | 121.7396 | 121.7978 | 121.9531 | 121.6431 | -0.24599 | 121.7216 | 121.8248 | 121.8188 | 120.7401 | -122.1528
1482.5469 | 121.843 | -120.9732 | 0.80109 | 1.4211e-13 | 0.0053569 | -0.0060898 | -0.025362 | -0.023789 | 0.0042113 | 0.018923 | -0.012575 | 0.027553 | 0.043089 | 0.0013439 | 0.047219 | 0.77937 | 0.69735 | 0.38074 | 0.79841 | 0.8383 | 0.99816 | 0.55052 | -120.6754 | -0.23316 | -120.687 | 0.76213 | 0.86533 | 0.85479 | -121.3654 | 121.5237 | -0.002681 | 121.7526 | 121.354 | -0.16977 | 0.037216 | 0.19708 | -0.39223 | -0.038961 | 0.29778 | 0.28617 | 0.6784 | 0.064241 | 0.053706 | 121.7716 | 121.8115 | 121.9714 | 121.6706 | -0.25057 | 121.7353 | 121.8385 | 121.828 | 120.7401 | -122.1665
1484.2656 | 121.8796 | -120.9732 | 0.80109 | 1.4211e-13 | 0.0070661 | -0.0041668 | -0.025789 | -0.023148 | 0.0042113 | 0.0036627 | -0.012361 | 0.027553 | 0.043089 | 0.0015577 | 0.047433 | 0.79769 | 0.69278 | 0.69665 | 0.78925 | 0.8383 | 0.99816 | 0.54594 | -120.6663 | -0.23316 | -120.6825 | 0.77586 | 0.86533 | 0.86853 | -121.3609 | 121.5191 | -0.011838 | 121.7709 | 121.6699 | 0.15071 | 0.037216 | 0.19708 | -0.38765 | -0.025225 | 0.30693 | 0.29074 | 0.6784 | 0.064241 | 0.067442 | 121.7625 | 121.8115 | 121.9714 | 121.666 | -0.25515 | 121.7491 | 121.8385 | 121.8417 | 120.7401 | -122.1619
1486.0312 | 121.8475 | -120.9732 | 0.8194 | 1.4211e-13 | 0.0070661 | -0.0035256 | -0.026003 | -0.023362 | 0.0035703 | -0.0039678 | -0.012788 | 0.027767 | 0.043302 | 0.0015577 | 0.047219 | 0.79769 | 0.69735 | 0.72869 | 0.79841 | 0.84746 | 1.0073 | 0.5551 | -120.6617 | -0.24231 | -120.6825 | 0.77128 | 0.87448 | 0.86395 | -121.3563 | 121.5283 | -0.020992 | 121.7709 | 121.7019 | 0.1736 | 0.028063 | 0.18793 | -0.38308 | -0.048115 | 0.31151 | 0.29074 | 0.67382 | 0.055087 | 0.044552 | 121.7716 | 121.8207 | 121.9805 | 121.6706 | -0.2643 | 121.7445 | 121.8477 | 121.8372 | 120.7309 | -122.1757
1487.75 | 121.8613 | -120.9412 | 0.85144 | 1.4211e-13 | 0.0079209 | -0.0024574 | -0.025789 | -0.023362 | 0.0037841 | 0.011293 | -0.012575 | 0.027767 | 0.043089 | 0.0015577 | 0.047219 | 0.816 | 0.72483 | 0.75616 | 0.82588 | 0.87035 | 1.0302 | 0.58257 | -120.6388 | -0.23773 | -120.655 | 0.79875 | 0.90195 | 0.89142 | -121.3334 | 121.5237 | -0.025565 | 121.7572 | 121.6973 | 0.17359 | 0.018915 | 0.17878 | -0.39223 | -0.052687 | 0.30236 | 0.28617 | 0.6784 | 0.050515 | 0.039981 | 121.767 | 121.8115 | 121.9714 | 121.666 | -0.26887 | 121.7399 | 121.8431 | 121.8326 | 120.7034 | -122.1848
1489.5469 | 121.8201 | -120.9412 | 0.85602 | 1.4211e-13 | 0.0083483 | -0.00203 | -0.025576 | -0.023362 | 0.0042113 | -0.0039678 | -0.012575 | 0.027767 | 0.043302 | 0.0015577 | 0.047006 | 0.82974 | 0.73856 | 0.76074 | 0.83961 | 0.87493 | 1.0394 | 0.58715 | -120.6296 | -0.24689 | -120.6596 | 0.80791 | 0.90653 | 0.90058 | -121.3242 | 121.5283 | -0.016408 | 121.7709 | 121.7019 | 0.17359 | 0.018916 | 0.18335 | -0.38307 | -0.048108 | 0.31152 | 0.28159 | 0.66466 | 0.050516 | 0.04456 | 121.7808 | 121.8161 | 121.9805 | 121.6797 | -0.26887 | 121.7491 | 121.8477 | 121.8417 | 120.6943 | -122.1802
1491.3281 | 121.8658 | -120.932 | 0.87891 | 1.4211e-13 | 0.0083483 | -0.0018162 | -0.025576 | -0.023576 | 0.0042113 | 0.011293 | -0.012361 | 0.027767 | 0.043302 | 0.0011303 | 0.047006 | 0.84347 | 0.73856 | 0.78363 | 0.83961 | 0.89783 | 1.044 | 0.60089 | -120.6113 | -0.25147 | -120.6367 | 0.81249 | 0.92027 | 0.90973 | -121.3151 | 121.5329 | -0.039296 | 121.7755 | 121.7156 | 0.18275 | 0.018922 | 0.16505 | -0.38307 | -0.066417 | 0.32068 | 0.29533 | 0.6784 | 0.041364 | 0.030829 | 121.7716 | 121.8298 | 121.976 | 121.6706 | -0.27802 | 121.7445 | 121.8523 | 121.8417 | 120.6805 | -122.194
1493.0312 | 121.9345 | -120.9045 | 0.82855 | 1.4211e-13 | 0.0089893 | -0.0016026 | -0.025576 | -0.023148 | 0.0035703 | 0.0036627 | -0.012575 | 0.027767 | 0.042875 | 0.0013439 | 0.047006 | 0.83889 | 0.74772 | 0.78363 | 0.84419 | 0.88867 | 1.0394 | 0.59173 | -120.6251 | -0.24689 | -120.6458 | 0.81707 | 0.92027 | 0.90516 | -121.3288 | 121.4963 | 0.015637 | 121.7434 | 121.6882 | 0.1919 | 0.060118 | 0.21082 | -0.42427 | -0.011485 | 0.27948 | 0.25871 | 0.68298 | 0.091718 | 0.076605 | 121.7487 | 121.7932 | 121.9439 | 121.6523 | -0.23682 | 121.7216 | 121.8248 | 121.8097 | 120.6576 | -122.1574
1494.8125 | 121.962 | -120.8908 | 0.81482 | 1.4211e-13 | 0.0087755 | -0.0016026 | -0.025789 | -0.023362 | 0.0039977 | 0.0036627 | -0.012575 | 0.027981 | 0.043516 | 0.0015577 | 0.047219 | 0.83431 | 0.73856 | 0.77906 | 0.83961 | 0.87951 | 1.0348 | 0.58715 | -120.6296 | -0.24231 | -120.6458 | 0.80791 | 0.91569 | 0.90516 | -121.3288 | 121.478 | 0.024791 | 121.7251 | 121.6699 | 0.19191 | 0.064693 | 0.21997 | -0.438 | -0.006909 | 0.26117 | 0.24498 | 0.68298 | 0.10087 | 0.090338 | 121.7304 | 121.7703 | 121.9256 | 121.6294 | -0.22767 | 121.6987 | 121.8065 | 121.796 | 120.6485 | -122.1436
1496.6094 | 121.8338 | -120.9229 | 0.84686 | 1.4211e-13 | 0.0087755 | -0.0018162 | -0.026644 | -0.023362 | 0.0039977 | 0.011293 | -0.012575 | 0.027553 | 0.043089 | 0.0013439 | 0.047433 | 0.83431 | 0.74772 | 0.79279 | 0.83045 | 0.88409 | 1.0394 | 0.58257 | -120.6251 | -0.25147 | -120.6413 | 0.80791 | 0.91569 | 0.90058 | -121.3151 | 121.5054 | -0.016409 | 121.7572 | 121.7156 | 0.21022 | 0.037228 | 0.19251 | -0.39222 | -0.038953 | 0.29779 | 0.2816 | 0.67382 | 0.068828 | 0.053715 | 121.7533 | 121.8069 | 121.9622 | 121.6706 | -0.26429 | 121.7308 | 121.8385 | 121.8234 | 120.6714 | -122.1619
1498.3906 | 121.907 | -120.9457 | 0.83313 | 1.4211e-13 | 0.0085619 | -0.00203 | -0.02643 | -0.023362 | 0.0037841 | 0.011293 | -0.012575 | 0.027767 | 0.042875 | 0.0013439 | 0.047219 | 0.82974 | 0.73398 | 0.78821 | 0.83503 | 0.88867 | 1.0394 | 0.58257 | -120.6251 | -0.25605 | -120.6504 | 0.80791 | 0.91111 | 0.90516 | -121.3288 | 121.5283 | 0.001902 | 121.7755 | 121.734 | 0.20564 | 0.05554 | 0.20624 | -0.38307 | -0.02522 | 0.32068 | 0.29533 | 0.6784 | 0.077983 | 0.072027 | 121.7808 | 121.8344 | 121.9851 | 121.6797 | -0.25056 | 121.7537 | 121.8569 | 121.8509 | 120.6897 | -122.1619
1500.1562 | 121.9574 | -120.8817 | 0.83313 | 1.4211e-13 | 0.0087755 | -0.0011752 | -0.026217 | -0.023362 | 0.0037841 | 0.011293 | -0.013002 | 0.027981 | 0.043089 | 0.0011303 | 0.047006 | 0.83889 | 0.73856 | 0.78821 | 0.83961 | 0.88409 | 1.044 | 0.58715 | -120.6251 | -0.26521 | -120.6504 | 0.81249 | 0.90653 | 0.90058 | -121.3242 | 121.4688 | 0.00648 | 121.7205 | 121.6699 | 0.20106 | 0.050961 | 0.21082 | -0.44258 | -0.020641 | 0.25659 | 0.23124 | 0.67382 | 0.073404 | 0.067448 | 121.7213 | 121.7657 | 121.9256 | 121.6202 | -0.24598 | 121.6941 | 121.7882 | 121.7822 | 120.6164 | -122.1574
1501.8594 | 121.8155 | -120.9229 | 0.87433 | 1.4211e-13 | 0.0085619 | -0.00203 | -0.02643 | -0.023576 | 0.0042113 | 0.0036627 | -0.012788 | 0.028194 | 0.043302 | 0.0011303 | 0.047433 | 0.84347 | 0.73398 | 0.78821 | 0.83045 | 0.89325 | 1.0394 | 0.59631 | -120.6159 | -0.25147 | -120.6458 | 0.81249 | 0.92027 | 0.90973 | -121.3151 | 121.5192 | -0.043875 | 121.7663 | 121.7111 | 0.1919 | 0.01892 | 0.16504 | -0.39222 | -0.06184 | 0.30695 | 0.27702 | 0.66924 | 0.045941 | 0.035406 | 121.7533 | 121.8161 | 121.9622 | 121.6568 | -0.27802 | 121.7353 | 121.8431 | 121.8326 | 120.6714 | -122.1894
1503.6406 | 121.907 | -120.9 | 0.83771 | 1.4211e-13 | 0.0081345 | -0.00203 | -0.027072 | -0.023148 | 0.0037841 | 0.0036627 | -0.012575 | 0.027767 | 0.043089 | 0.0015577 | 0.047219 | 0.83889 | 0.73856 | 0.78821 | 0.83961 | 0.88409 | 1.0485 | 0.58715 | -120.6159 | -0.24689 | -120.6367 | 0.80791 | 0.91111 | 0.90516 | -121.3151 | 121.4871 | 0.001902 | 121.7389 | 121.6882 | 0.20106 | 0.046383 | 0.21082 | -0.41511 | -0.029798 | 0.28406 | 0.26329 | 0.6784 | 0.073405 | 0.067449 | 121.7396 | 121.7841 | 121.9485 | 121.6385 | -0.25056 | 121.7079 | 121.8111 | 121.8051 | 120.6531 | -122.1528
1505.4219 | 121.8613 | -120.932 | 0.85144 | 1.4211e-13 | 0.0079209 | -0.0016026 | -0.026644 | -0.023576 | 0.0039977 | 0.0036627 | -0.012575 | 0.027767 | 0.043516 | 0.0017713 | 0.047006 | 0.83431 | 0.73856 | 0.78821 | 0.83961 | 0.88867 | 1.0394 | 0.58715 | -120.6205 | -0.25605 | -120.6367 | 0.81249 | 0.91569 | 0.90516 | -121.3151 | 121.5192 | -0.01183 | 121.7663 | 121.7202 | 0.20106 | 0.03723 | 0.18793 | -0.38307 | -0.038951 | 0.31152 | 0.29533 | 0.6784 | 0.064251 | 0.053717 | 121.7716 | 121.8207 | 121.9714 | 121.6706 | -0.26429 | 121.7445 | 121.8477 | 121.8372 | 120.676 | -122.1665
1507.1875 | 121.8933 | -120.8817 | 0.85602 | 1.4211e-13 | 0.0072799 | -0.0024574 | -0.026003 | -0.023576 | 0.0037841 | 0.026554 | -0.012788 | 0.027767 | 0.043302 | 0.0013439 | 0.047433 | 0.83889 | 0.74314 | 0.79279 | 0.84419 | 0.89325 | 1.0394 | 0.58715 | -120.6205 | -0.26063 | -120.6458 | 0.81707 | 0.92027 | 0.91431 | -121.3197 | 121.4688 | -0.011829 | 121.7205 | 121.6744 | 0.20564 | 0.037231 | 0.18335 | -0.438 | -0.038951 | 0.26117 | 0.23582 | 0.67382 | 0.064252 | 0.058296 | 121.7258 | 121.7749 | 121.921 | 121.6248 | -0.26887 | 121.6987 | 121.8019 | 121.796 | 120.621 | -122.1757
1508.9844 | 121.9666 | -120.8405 | 0.84686 | 1.4211e-13 | 0.0062115 | -0.003312 | -0.024507 | -0.023148 | 0.0039977 | 0.011293 | -0.012575 | 0.027553 | 0.043089 | 0.0015577 | 0.047219 | 0.85263 | 0.76145 | 0.80195 | 0.83961 | 0.90241 | 1.0531 | 0.43147 | -120.6022 | -0.26063 | -120.6275 | 0.82622 | 0.92485 | 0.91431 | -121.3013 | 121.2719 | -0.007253 | 121.6931 | 121.6424 | 0.37048 | 0.055544 | 0.20624 | -0.46088 | -0.020639 | 0.23828 | 0.21294 | 0.67382 | 0.077985 | 0.067451 | 121.6801 | 121.7429 | 121.8936 | 121.6019 | -0.4154 | 121.6667 | 121.7653 | 121.7548 | 120.5798 | -122.1482
1510.7656 | 121.8658 | -120.8725 | 0.87433 | 1.4211e-13 | 0.0059979 | -0.0035256 | -0.02408 | -0.023362 | 0.0039977 | 0.011293 | -0.012361 | 0.027553 | 0.042875 | 0.0015577 | 0.047006 | 0.86178 | 0.76603 | 0.80653 | 0.85335 | 0.90241 | 1.0623 | 0.44978 | -120.6022 | -0.26521 | -120.6184 | 0.83538 | 0.93401 | 0.92347 | -121.2968 | 121.3223 | -0.020983 | 121.7343 | 121.679 | 0.35674 | 0.028078 | 0.18794 | -0.42426 | -0.038948 | 0.27033 | 0.25414 | 0.6784 | 0.059677 | 0.049142 | 121.7258 | 121.7749 | 121.9348 | 121.6385 | -0.42455 | 121.7079 | 121.8065 | 121.796 | 120.6073 | -122.1711
1512.5469 | 121.8979 | -120.8633 | 0.84228 | 1.4211e-13 | 0.0055705 | -0.0035256 | -0.023225 | -0.023362 | 0.0037841 | -0.0039678 | -0.012575 | 0.027767 | 0.043089 | 0.0013439 | 0.047006 | 0.85721 | 0.77061 | 0.81568 | 0.8625 | 0.90699 | 1.0668 | 0.3811 | -120.5884 | -0.26978 | -120.6138 | 0.83538 | 0.94316 | 0.92805 | -121.2876 | 121.2444 | 0.020217 | 121.7205 | 121.679 | 0.43458 | 0.064701 | 0.22456 | -0.42426 | -0.006904 | 0.27491 | 0.24956 | 0.67382 | 0.10088 | 0.085765 | 121.7258 | 121.7703 | 121.9302 | 121.634 | -0.46119 | 121.6987 | 121.8065 | 121.7914 | 120.5936 | -122.1299
1514.2656 | 121.8018 | -120.9091 | 0.90179 | 1.4211e-13 | 0.0057841 | -0.0037394 | -0.023012 | -0.022935 | 0.0037841 | 0.011293 | -0.012575 | 0.027553 | 0.043089 | 0.0013439 | 0.047006 | 0.8801 | 0.78893 | 0.83399 | 0.88082 | 0.91614 | 1.0897 | 0.37652 | -120.5655 | -0.27436 | -120.5909 | 0.85827 | 0.9569 | 0.94179 | -121.2647 | 121.2856 | -0.020978 | 121.7892 | 121.7431 | 0.45748 | 0.01435 | 0.18794 | -0.35559 | -0.04352 | 0.34358 | 0.31823 | 0.67382 | 0.055105 | 0.039992 | 121.7899 | 121.8253 | 121.9989 | 121.698 | -0.52527 | 121.7674 | 121.866 | 121.8509 | 120.6348 | -122.1665
1516.0312 | 121.8842 | -121.5317 | 0.27924 | 1.4211e-13 | 0.00022867 | -0.008654 | -0.027072 | -0.023576 | 0.0039977 | 0.011293 | -0.012361 | 0.027553 | 0.043089 | 0.0013439 | 0.047006 | 0.23455 | 0.17997 | 0.19761 | 0.27189 | 0.30715 | 0.46705 | 0.07431 | -121.2295 | -0.28352 | -121.2548 | 0.23102 | 0.33879 | 0.32367 | -121.9332 | 121.606 | -0.007346 | 121.7662 | 121.7293 | 0.1233 | 0.027911 | 0.18781 | -0.40154 | -0.048216 | 0.30222 | 0.27688 | 0.67841 | 0.059551 | 0.044438 | 121.8036 | 121.8388 | 121.9987 | 121.7116 | -0.20493 | 121.7627 | 121.8705 | 121.8554 | 121.2482 | -122.2124
1517.7969 | 121.875 | -121.5363 | 0.30212 | 1.4211e-13 | 0.00022867 | -0.0088676 | -0.026858 | -0.023789 | 0.0039977 | 0.011293 | -0.012575 | 0.027767 | 0.043302 | 0.0017713 | 0.047433 | 0.24828 | 0.18913 | 0.19761 | 0.2902 | 0.32088 | 0.48536 | 0.07431 | -121.2432 | -0.27436 | -121.2594 | 0.24018 | 0.3571 | 0.33283 | -121.947 | 121.6106 | -0.01192 | 121.7845 | 121.7339 | 0.1233 | 0.01876 | 0.18324 | -0.4107 | -0.061947 | 0.29307 | 0.27688 | 0.68757 | 0.054978 | 0.030707 | 121.8265 | 121.8571 | 122.0216 | 121.7254 | -0.22781 | 121.7764 | 121.8934 | 121.8691 | 121.2619 | -122.2491
1519.5156 | 122.0078 | -121.5134 | 0.2655 | 1.4211e-13 | 0.00022867 | -0.0088676 | -0.02643 | -0.023576 | 0.0039977 | 0.011293 | -0.012788 | 0.027553 | 0.043516 | 0.0017713 | 0.047219 | 0.25744 | 0.18913 | 0.21135 | 0.2902 | 0.32546 | 0.48536 | 0.07431 | -121.2478 | -0.27436 | -121.2777 | 0.24933 | 0.36168 | 0.34199 | -121.9424 | 121.5877 | 0.024701 | 121.7708 | 121.7247 | 0.13704 | 0.05996 | 0.21986 | -0.429 | -0.016169 | 0.2656 | 0.23567 | 0.66468 | 0.096177 | 0.076486 | 121.8036 | 121.8388 | 121.9987 | 121.7025 | -0.19119 | 121.7627 | 121.875 | 121.8554 | 121.239 | -122.2079
1521.2969 | 121.8933 | -121.5866 | 0.30212 | 1.4211e-13 | 0.00065587 | -0.0090814 | -0.026858 | -0.023148 | 0.0039977 | 0.011293 | -0.012575 | 0.027553 | 0.043302 | 0.0013439 | 0.046792 | 0.25744 | 0.19829 | 0.22051 | 0.29936 | 0.34378 | 0.48994 | 0.078889 | -121.2478 | -0.28352 | -121.2823 | 0.25391 | 0.36626 | 0.35115 | -121.9561 | 121.6655 | -0.002763 | 121.844 | 121.8071 | 0.14162 | 0.041654 | 0.18782 | -0.3695 | -0.048212 | 0.33884 | 0.30434 | 0.67383 | 0.064135 | 0.049022 | 121.886 | 121.9304 | 122.0765 | 121.7849 | -0.22324 | 121.8405 | 121.9529 | 121.9378 | 121.3031 | -122.2582
1523.0625 | 122.0444 | -121.5225 | 0.30212 | 1.4211e-13 | 0.00044227 | -0.0084402 | -0.026644 | -0.023362 | 0.0037841 | 0.0036627 | -0.012361 | 0.027767 | 0.042875 | 0.0015577 | 0.047219 | 0.26659 | 0.21202 | 0.22508 | 0.29936 | 0.3392 | 0.49452 | 0.07431 | -121.2523 | -0.27894 | -121.2777 | 0.26307 | 0.38457 | 0.3603 | -121.9561 | 121.5968 | -0.002763 | 121.7891 | 121.7476 | 0.15077 | 0.037075 | 0.19239 | -0.43359 | -0.039055 | 0.27017 | 0.24483 | 0.67841 | 0.082449 | 0.058179 | 121.8219 | 121.8617 | 122.017 | 121.7345 | -0.22781 | 121.7856 | 121.9071 | 121.8828 | 121.2436 | -122.2582
1524.8438 | 122.0261 | -121.5225 | 0.28381 | 1.4211e-13 | 0.00086967 | -0.008654 | -0.02643 | -0.023789 | 0.0042113 | -0.0039678 | -0.012575 | 0.027767 | 0.043089 | 0.0013439 | 0.047219 | 0.27575 | 0.21202 | 0.22966 | 0.29936 | 0.34836 | 0.50825 | 0.078889 | -121.2523 | -0.26978 | -121.2869 | 0.27223 | 0.37542 | 0.36488 | -121.9607 | 121.6014 | 0.015548 | 121.7983 | 121.7522 | 0.15077 | 0.064544 | 0.22444 | -0.43816 | -0.011587 | 0.27017 | 0.23567 | 0.67383 | 0.091603 | 0.081069 | 121.8219 | 121.8709 | 122.0308 | 121.7345 | -0.20492 | 121.7947 | 121.8979 | 121.8874 | 121.2527 | -122.2445
1526.5625 | 121.9894 | -121.5454 | 0.28839 | 1.4211e-13 | 0.00065587 | -0.008654 | -0.026644 | -0.023362 | 0.0039977 | 0.0036627 | -0.012361 | 0.027553 | 0.043516 | 0.0013439 | 0.047219 | 0.27117 | 0.21202 | 0.22966 | 0.3131 | 0.34836 | 0.50368 | 0.078889 | -121.2661 | -0.2881 | -121.2777 | 0.26765 | 0.38457 | 0.36488 | -121.9698 | 121.6243 | 0.024705 | 121.8166 | 121.7751 | 0.15077 | 0.059966 | 0.21529 | -0.42443 | -0.020743 | 0.27933 | 0.26772 | 0.69215 | 0.096182 | 0.076491 | 121.8585 | 121.8938 | 122.0491 | 121.7574 | -0.2095 | 121.8131 | 121.93 | 121.9103 | 121.2573 | -122.2582
1528.3281 | 122.0627 | -121.5179 | 0.28381 | 1.4211e-13 | 0.00086967 | -0.008654 | -0.026217 | -0.023148 | 0.0037841 | 0.0036627 | -0.012361 | 0.027767 | 0.043516 | 0.0015577 | 0.047006 | 0.28491 | 0.22118 | 0.23424 | 0.31767 | 0.35752 | 0.51283 | 0.07431 | -121.2615 | -0.28352 | -121.2823 | 0.28596 | 0.38915 | 0.36946 | -121.9561 | 121.5923 | 0.033861 | 121.8029 | 121.7522 | 0.15993 | 0.073702 | 0.22902 | -0.43816 | 0.002149 | 0.25644 | 0.23567 | 0.67383 | 0.10534 | 0.085647 | 121.8356 | 121.8755 | 122.0308 | 121.7391 | -0.2095 | 121.8039 | 121.9071 | 121.8874 | 121.2344 | -122.2399
1530.0469 | 122.0535 | -121.5546 | 0.28381 | 1.4211e-13 | 0.0010833 | -0.0077992 | -0.026217 | -0.023148 | 0.0037841 | 0.011293 | -0.012575 | 0.027553 | 0.043302 | 0.0015577 | 0.047433 | 0.27117 | 0.22118 | 0.22966 | 0.31767 | 0.34836 | 0.50825 | 0.07431 | -121.2661 | -0.28352 | -121.2914 | 0.28138 | 0.38 | 0.36946 | -121.9653 | 121.6289 | 0.033861 | 121.8257 | 121.7842 | 0.15535 | 0.064544 | 0.22444 | -0.4107 | -0.00243 | 0.28848 | 0.26313 | 0.67383 | 0.096182 | 0.085647 | 121.8722 | 121.9029 | 122.0628 | 121.7757 | -0.2095 | 121.8359 | 121.9346 | 121.924 | 121.271 | -122.2491
1531.8125 | 122.0673 | -121.5317 | 0.3067 | 1.4211e-13 | 0.0012971 | -0.0084402 | -0.026003 | -0.023362 | 0.0037841 | -0.0039678 | -0.012788 | 0.027981 | 0.043089 | 0.0015577 | 0.047219 | 0.28491 | 0.22576 | 0.23882 | 0.31767 | 0.35752 | 0.51283 | 0.069732 | -121.2661 | -0.29268 | -121.2914 | 0.28138 | 0.38457 | 0.37862 | -121.9744 | 121.6014 | 0.010972 | 121.8166 | 121.7705 | 0.16909 | 0.050813 | 0.20613 | -0.44275 | -0.025319 | 0.26559 | 0.24025 | 0.68299 | 0.077871 | 0.071915 | 121.8494 | 121.8892 | 122.0445 | 121.7574 | -0.23697 | 121.8131 | 121.9163 | 121.9103 | 121.239 | -122.2811
1533.5938 | 122.0627 | -121.5546 | 0.3067 | 1.4211e-13 | 0.0012971 | -0.0077992 | -0.025789 | -0.023789 | 0.0037841 | -0.0039678 | -0.012575 | 0.027553 | 0.043089 | 0.0013439 | 0.047006 | 0.28949 | 0.23034 | 0.24797 | 0.32225 | 0.36667 | 0.51283 | 0.065153 | -121.2615 | -0.29268 | -121.2823 | 0.29054 | 0.38915 | 0.3832 | -121.9698 | 121.6197 | 0.015551 | 121.8441 | 121.8025 | 0.18282 | 0.059971 | 0.20613 | -0.41528 | -0.016162 | 0.29306 | 0.27229 | 0.68757 | 0.08245 | 0.076494 | 121.8768 | 121.9212 | 122.0674 | 121.7849 | -0.24155 | 121.8451 | 121.9437 | 121.9378 | 121.2619 | -122.2765
1535.375 | 122.0856 | -121.5271 | 0.29755 | 1.4211e-13 | 0.0015107 | -0.008013 | -0.025789 | -0.023789 | 0.0037841 | -0.0039678 | -0.012361 | 0.027553 | 0.043302 | 0.0015577 | 0.047433 | 0.28491 | 0.22118 | 0.23882 | 0.32225 | 0.36667 | 0.52199 | 0.07431 | -121.2707 | -0.29268 | -121.2869 | 0.29054 | 0.39373 | 0.37862 | -121.9744 | 121.6014 | 0.024707 | 121.812 | 121.7659 | 0.16451 | 0.069127 | 0.22444 | -0.44732 | -0.007006 | 0.25644 | 0.24025 | 0.68757 | 0.096185 | 0.081071 | 121.8494 | 121.8938 | 122.0491 | 121.7483 | -0.22324 | 121.8176 | 121.9208 | 121.9057 | 121.2344 | -122.272
1537.1406 | 121.9528 | -121.5683 | 0.32959 | 1.4211e-13 | 0.0019381 | -0.0088676 | -0.025576 | -0.023789 | 0.0039977 | 0.018923 | -0.013002 | 0.027553 | 0.043516 | 0.0013439 | 0.047433 | 0.28491 | 0.22118 | 0.2434 | 0.31767 | 0.35752 | 0.51741 | 0.07431 | -121.2798 | -0.29726 | -121.3006 | 0.28596 | 0.38915 | 0.3832 | -121.9882 | 121.6426 | -0.011916 | 121.8532 | 121.8117 | 0.16909 | 0.027925 | 0.18782 | -0.41986 | -0.043628 | 0.28848 | 0.26771 | 0.68757 | 0.059562 | 0.053606 | 121.886 | 121.9258 | 122.0857 | 121.7895 | -0.25528 | 121.8543 | 121.9574 | 121.9515 | 121.271 | -122.3177
1538.8594 | 122.0901 | -121.5591 | 0.28381 | 1.4211e-13 | 0.0017243 | -0.0095086 | -0.025362 | -0.023362 | 0.0039977 | 0.011293 | -0.012575 | 0.027981 | 0.042875 | 0.0015577 | 0.047006 | 0.27117 | 0.20744 | 0.23882 | 0.30852 | 0.3392 | 0.50368 | 0.065153 | -121.2981 | -0.2881 | -121.3189 | 0.27223 | 0.37542 | 0.36488 | -122.0019 | 121.6243 | 0.024704 | 121.8303 | 121.798 | 0.17367 | 0.055386 | 0.21986 | -0.44275 | -0.011587 | 0.26101 | 0.24024 | 0.68299 | 0.091603 | 0.081069 | 121.8677 | 121.8983 | 122.0628 | 121.7666 | -0.21866 | 121.8314 | 121.9346 | 121.924 | 121.271 | -122.2857
1540.6406 | 122.0627 | -121.6003 | 0.29297 | 1.4211e-13 | 0.0019381 | -0.0095086 | -0.025576 | -0.023576 | 0.0039977 | 0.0036627 | -0.012575 | 0.027767 | 0.043516 | 0.0013439 | 0.047219 | 0.27117 | 0.17997 | 0.23424 | 0.30852 | 0.34836 | 0.50368 | 0.078889 | -121.3073 | -0.30184 | -121.3235 | 0.27223 | 0.36626 | 0.36946 | -122.0111 | 121.6792 | 0.015548 | 121.8715 | 121.8346 | 0.15535 | 0.055388 | 0.21071 | -0.41071 | -0.020743 | 0.29305 | 0.27686 | 0.68757 | 0.07329 | 0.076491 | 121.9089 | 121.9487 | 122.104 | 121.7803 | -0.21408 | 121.8726 | 121.9666 | 121.9698 | 121.2985 | -122.304
1542.4219 | 121.994 | -121.6324 | 0.32501 | 1.4211e-13 | 0.0019381 | -0.0095086 | -0.025362 | -0.023576 | 0.0039977 | 0.0036627 | -0.012361 | 0.027767 | 0.043302 | 0.0011303 | 0.047006 | 0.27117 | 0.17539 | 0.23424 | 0.30852 | 0.34836 | 0.49452 | 0.07431 | -121.3119 | -0.30184 | -121.3235 | 0.26307 | 0.36626 | 0.35572 | -122.0156 | 121.7067 | -0.016495 | 121.9036 | 121.8666 | 0.15993 | 0.023345 | 0.16951 | -0.38325 | -0.061943 | 0.32052 | 0.3089 | 0.69215 | 0.041247 | 0.030712 | 121.9409 | 121.9807 | 122.1269 | 121.8078 | -0.2507 | 121.8955 | 121.9986 | 121.9881 | 121.3305 | -122.3406
1544.1875 | 121.9528 | -121.6599 | 0.29297 | 1.4211e-13 | 0.0017243 | -0.0095086 | -0.025576 | -0.023576 | 0.0037841 | 0.0036627 | -0.012361 | 0.027767 | 0.043089 | 0.0013439 | 0.047006 | 0.2437 | 0.14792 | 0.20219 | 0.2902 | 0.32088 | 0.47163 | 0.083468 | -121.3302 | -0.30184 | -121.351 | 0.24018 | 0.34794 | 0.33741 | -122.0339 | 121.7433 | -0.002765 | 121.9036 | 121.862 | 0.11872 | 0.027915 | 0.17866 | -0.3741 | -0.052792 | 0.32967 | 0.3089 | 0.68299 | 0.054975 | 0.044441 | 121.9501 | 121.9807 | 122.1315 | 121.8078 | -0.2095 | 121.9 | 122.0078 | 121.9973 | 121.358 | -122.3269
1545.9844 | 122.1085 | -121.6003 | 0.24719 | 1.4211e-13 | 0.0017243 | -0.0097224 | -0.026003 | -0.023576 | 0.0035703 | -0.0039678 | -0.012361 | 0.02734 | 0.043516 | 0.0015577 | 0.047647 | 0.23912 | 0.11587 | 0.19761 | 0.26731 | 0.31631 | 0.46705 | 0.083468 | -121.3393 | -0.30641 | -121.3647 | 0.24018 | 0.33879 | 0.32367 | -122.0385 | 121.6838 | 0.02012 | 121.8395 | 121.798 | 0.11415 | 0.069113 | 0.21985 | -0.43818 | -0.007015 | 0.261 | 0.23565 | 0.67384 | 0.091595 | 0.076482 | 121.8677 | 121.9166 | 122.0674 | 121.7162 | -0.16372 | 121.8405 | 121.9391 | 121.924 | 121.2939 | -122.2857
1547.7656 | 121.9666 | -121.669 | 0.27008 | 1.4211e-13 | 0.0017243 | -0.009936 | -0.025789 | -0.023362 | 0.0039977 | 0.011293 | -0.012361 | 0.027767 | 0.043089 | 0.0013439 | 0.047219 | 0.23912 | 0.12045 | 0.19304 | 0.26273 | 0.31631 | 0.46247 | 0.078889 | -121.3485 | -0.30641 | -121.3738 | 0.23102 | 0.32963 | 0.32367 | -122.0523 | 121.7479 | -0.007347 | 121.9081 | 121.862 | 0.11415 | 0.046224 | 0.19239 | -0.38326 | -0.039061 | 0.32051 | 0.29516 | 0.67842 | 0.059549 | 0.053593 | 121.9317 | 121.9853 | 122.1315 | 121.7895 | -0.19119 | 121.9 | 121.9986 | 121.9927 | 121.3626 | -122.3223
1549.5625 | 121.9757 | -121.6736 | 0.27924 | 1.4211e-13 | 0.0015107 | -0.0095086 | -0.025576 | -0.023576 | 0.0037841 | 0.018923 | -0.012575 | 0.027767 | 0.043516 | 0.0013439 | 0.047647 | 0.22539 | 0.11129 | 0.18388 | 0.26273 | 0.28883 | 0.45789 | 0.07431 | -121.3577 | -0.30641 | -121.383 | 0.23102 | 0.32963 | 0.30994 | -122.066 | 121.7479 | -0.016502 | 121.899 | 121.8575 | 0.10957 | 0.009595 | 0.17865 | -0.39241 | -0.048216 | 0.31593 | 0.29058 | 0.68299 | 0.050394 | 0.030702 | 121.9363 | 121.9624 | 122.1315 | 121.7849 | -0.20493 | 121.9046 | 122.0032 | 121.9835 | 121.3672 | -122.3452
1551.2969 | 122.0078 | -121.7651 | 0.16022 | 1.4211e-13 | 1.487e-05 | -0.009936 | -0.026858 | -0.023576 | 0.0039977 | 0.011293 | -0.012361 | 0.027767 | 0.043302 | 0.0013439 | 0.047433 | 0.1384 | 0.051771 | 0.087735 | 0.16659 | 0.20183 | 0.35258 | 0.028521 | -121.463 | -0.31099 | -121.4792 | 0.12114 | 0.23348 | 0.21379 | -122.1667 | 121.7937 | 0.00637 | 121.9035 | 121.8529 | 0.059214 | 0.041615 | 0.19237 | -0.4016 | -0.039081 | 0.30217 | 0.28598 | 0.68757 | 0.073262 | 0.053571 | 121.9317 | 121.967 | 122.1177 | 121.8169 | -0.1317 | 121.8863 | 121.9986 | 121.9789 | 121.4541 | -122.3269
1553.0781 | 121.9849 | -121.788 | 0.15106 | 1.4211e-13 | -0.00019873 | -0.0097224 | -0.027285 | -0.023362 | 0.0039977 | -0.011598 | -0.012575 | 0.02734 | 0.043089 | 0.0013439 | 0.047647 | 0.11093 | 0.042614 | 0.064843 | 0.14827 | 0.17436 | 0.32511 | 0.028521 | -121.4904 | -0.31099 | -121.5066 | 0.098244 | 0.21059 | 0.18632 | -122.1942 | 121.8165 | -0.002788 | 121.899 | 121.8529 | 0.036322 | 0.023296 | 0.17405 | -0.40618 | -0.052818 | 0.29758 | 0.2814 | 0.68758 | 0.059524 | 0.035254 | 121.9363 | 121.9624 | 122.1131 | 121.8306 | -0.12254 | 121.8863 | 121.9986 | 121.9743 | 121.477 | -122.3453
1554.7812 | 122.081 | -121.7514 | 0.10986 | 1.4211e-13 | -0.00041233 | -0.01015 | -0.027285 | -0.023576 | 0.0035703 | 0.011293 | -0.012575 | 0.027767 | 0.043302 | 0.0013439 | 0.047433 | 0.11551 | 0.033457 | 0.069421 | 0.14827 | 0.17436 | 0.33885 | 0.023942 | -121.4859 | -0.30641 | -121.5066 | 0.10282 | 0.20143 | 0.18632 | -122.1988 | 121.7753 | 0.038411 | 121.8669 | 121.8208 | 0.045479 | 0.064495 | 0.22898 | -0.44738 | -0.007041 | 0.26554 | 0.24477 | 0.69215 | 0.091566 | 0.076453 | 121.8997 | 121.9258 | 122.0902 | 121.7849 | -0.085921 | 121.8542 | 121.9528 | 121.9377 | 121.445 | -122.3086
1556.5781 | 122.1085 | -121.7651 | 0.11902 | 1.4211e-13 | -0.00019873 | -0.0097224 | -0.027285 | -0.023576 | 0.0039977 | 0.011293 | -0.012361 | 0.02734 | 0.043302 | 0.0013439 | 0.047647 | 0.10635 | 0.047193 | 0.069421 | 0.13912 | 0.17894 | 0.33427 | 0.0331 | -121.4904 | -0.32015 | -121.5204 | 0.10282 | 0.21059 | 0.19547 | -122.1988 | 121.7982 | 0.020098 | 121.8715 | 121.8346 | 0.036321 | 0.059918 | 0.21525 | -0.43365 | -0.016197 | 0.2747 | 0.24477 | 0.67842 | 0.091567 | 0.076454 | 121.9043 | 121.9441 | 122.0994 | 121.8123 | -0.085919 | 121.868 | 121.9757 | 121.9606 | 121.445 | -122.3178
1558.3594 | 121.9574 | -120.163 | 1.6937 | 1.4211e-13 | 0.014331 | -0.0075856 | -0.013182 | -0.023148 | 0.0031431 | 0.011293 | -0.012361 | 0.027553 | 0.043089 | 0.0013439 | 0.047433 | 1.3517 | 0.62867 | 1.2827 | 1.3432 | 1.2687 | 1.4927 | 0.24373 | -120.1992 | -0.27894 | -120.22 | 1.3207 | 1.4239 | 1.3493 | -120.9076 | 120.4067 | -0.35049 | 121.5146 | 121.4456 | 1.0389 | -0.42501 | -0.20107 | -0.74459 | -0.37302 | -0.036279 | -0.057049 | 0.68755 | -0.26981 | -0.34445 | 121.5062 | 121.4317 | 121.6556 | 120.7916 | -1.45 | 121.4837 | 121.5869 | 121.5122 | 119.884 | -122.6013
1560.1406 | 122.0581 | -121.7743 | 0.09613 | 1.4211e-13 | 0.00065587 | -0.009936 | -0.026858 | -0.023362 | 0.0037841 | 0.011293 | -0.012361 | 0.027553 | 0.043302 | 0.0011303 | 0.047219 | 0.092615 | 0.038035 | 0.04653 | 0.13912 | 0.14688 | 0.29306 | -0.099689 | -121.495 | -0.32015 | -121.5158 | 0.075351 | 0.17396 | 0.16342 | -122.2079 | 121.6746 | 0.042987 | 121.8669 | 121.8208 | 0.14622 | 0.050755 | 0.19693 | -0.43365 | -0.020779 | 0.27927 | 0.2585 | 0.69215 | 0.077828 | 0.067293 | 121.9134 | 121.9212 | 122.0674 | 121.8123 | -0.19582 | 121.8496 | 121.9483 | 121.9377 | 121.4541 | -122.3041
1561.8594 | 122.0123 | -121.8384 | 0.10986 | 1.4211e-13 | 0.00086967 | -0.0097224 | -0.026644 | -0.023362 | 0.0037841 | 0.011293 | -0.012575 | 0.027553 | 0.043516 | 0.0013439 | 0.047433 | 0.092615 | 0.038035 | 0.04653 | 0.1208 | 0.13773 | 0.29764 | 0.023942 | -121.5225 | -0.32015 | -121.5433 | 0.066194 | 0.17396 | 0.16342 | -122.2354 | 121.8623 | 0.010941 | 121.931 | 121.8849 | 0.022588 | 0.027864 | 0.18778 | -0.39704 | -0.043669 | 0.31589 | 0.29512 | 0.69215 | 0.064095 | 0.05356 | 121.9592 | 121.9761 | 122.136 | 121.8764 | -0.085921 | 121.9046 | 122.0123 | 122.0018 | 121.5182 | -122.3453
1563.6406 | 121.962 | -121.8658 | 0.1236 | 1.4211e-13 | 0.00044227 | -0.0097224 | -0.026858 | -0.023789 | 0.0037841 | -0.0039678 | -0.012575 | 0.027767 | 0.043302 | 0.0011303 | 0.047006 | 0.097194 | 0.042614 | 0.04653 | 0.1208 | 0.14231 | 0.3068 | 0.014784 | -121.55 | -0.32015 | -121.5616 | 0.066194 | 0.17854 | 0.15884 | -122.2492 | 121.8806 | -0.002792 | 121.963 | 121.9124 | 0.031746 | 0.01871 | 0.1832 | -0.38331 | -0.057402 | 0.31588 | 0.30427 | 0.68758 | 0.05494 | 0.035249 | 121.9866 | 122.0082 | 122.1726 | 121.9085 | -0.10881 | 121.932 | 122.0444 | 122.0247 | 121.5457 | -122.3727
1565.4219 | 122.0581 | -121.8521 | 0.086975 | 1.4211e-13 | 0.00044227 | -0.009936 | -0.026858 | -0.023576 | 0.0039977 | 0.011293 | -0.012575 | 0.027553 | 0.043516 | 0.0015577 | 0.047006 | 0.097194 | 0.033457 | 0.051108 | 0.11622 | 0.14231 | 0.29764 | 0.0331 | -121.55 | -0.32015 | -121.5799 | 0.066194 | 0.18311 | 0.17258 | -122.2629 | 121.8852 | 0.02925 | 121.9493 | 121.9032 | 0.018008 | 0.055331 | 0.21066 | -0.41078 | -0.020781 | 0.30215 | 0.27222 | 0.683 | 0.09614 | 0.085605 | 121.9683 | 121.9944 | 122.1498 | 121.8856 | -0.053875 | 121.9183 | 122.0352 | 122.0247 | 121.532 | -122.3499
1567.2031 | 122.0673 | -121.8567 | 0.11444 | 1.4211e-13 | 0.00065587 | -0.0097224 | -0.026858 | -0.023576 | 0.0039977 | 0.018923 | -0.012575 | 0.02734 | 0.043302 | 0.0015577 | 0.047647 | 0.10177 | 0.038035 | 0.051108 | 0.11165 | 0.14231 | 0.29764 | 0.023942 | -121.5683 | -0.32015 | -121.589 | 0.066194 | 0.17854 | 0.15884 | -122.272 | 121.8806 | -0.002794 | 121.9585 | 121.9078 | 0.027166 | 0.027865 | 0.1832 | -0.41536 | -0.048247 | 0.28841 | 0.26764 | 0.683 | 0.064095 | 0.044404 | 121.9683 | 121.999 | 122.1543 | 121.8947 | -0.090499 | 121.9229 | 122.0352 | 122.0155 | 121.5365 | -122.3865
1569.0156 | 122.049 | -121.8613 | 0.10529 | 1.4211e-13 | 0.00065587 | -0.009936 | -0.026858 | -0.023362 | 0.0037841 | 0.011293 | -0.012575 | 0.027767 | 0.043516 | 0.0011303 | 0.047219 | 0.097194 | 0.033457 | 0.051108 | 0.1208 | 0.14231 | 0.29306 | 0.023942 | -121.5683 | -0.33389 | -121.5936 | 0.066194 | 0.1648 | 0.15884 | -122.272 | 121.8852 | 0.015518 | 121.9585 | 121.9124 | 0.027166 | 0.03702 | 0.18777 | -0.41078 | -0.039092 | 0.29299 | 0.26764 | 0.67842 | 0.059514 | 0.053559 | 121.9821 | 122.0036 | 122.1543 | 121.8947 | -0.081344 | 121.9275 | 122.0261 | 122.0201 | 121.5274 | -122.3773
1570.8125 | 122.0215 | -121.8658 | 0.14191 | 1.4211e-13 | 0.00065587 | -0.0097224 | -0.027072 | -0.023576 | 0.0037841 | 0.011293 | -0.012361 | 0.027767 | 0.043302 | 0.0013439 | 0.047219 | 0.097194 | 0.033457 | 0.041952 | 0.11622 | 0.14231 | 0.30222 | 0.023942 | -121.582 | -0.32931 | -121.6028 | 0.061616 | 0.16022 | 0.16342 | -122.2904 | 121.8898 | -0.025682 | 121.963 | 121.9078 | 0.01801 | 0.000399 | 0.16031 | -0.42452 | -0.080291 | 0.28383 | 0.26306 | 0.68758 | 0.018315 | 0.021516 | 121.9821 | 122.0082 | 122.1681 | 121.8993 | -0.11797 | 121.9275 | 122.0261 | 122.0293 | 121.5365 | -122.4323
1572.5156 | 122.1497 | -121.8887 | 0.09613 | 1.4211e-13 | 0.00044227 | -0.0097224 | -0.026644 | -0.023362 | 0.0037841 | 0.0036627 | -0.012148 | 0.027767 | 0.043516 | 0.0011303 | 0.047433 | 0.097194 | 0.033457 | 0.041952 | 0.11622 | 0.13773 | 0.29306 | 0.023942 | -121.5866 | -0.32931 | -121.6119 | 0.075351 | 0.1648 | 0.15884 | -122.2858 | 121.9127 | 0.020095 | 121.9859 | 121.9307 | 0.01801 | 0.041597 | 0.19693 | -0.39705 | -0.020779 | 0.30214 | 0.27679 | 0.67384 | 0.06867 | 0.062715 | 122.005 | 122.0265 | 122.1818 | 121.9222 | -0.072188 | 121.9641 | 122.0535 | 122.0476 | 121.5594 | -122.3819
1574.2969 | 122.1039 | -121.8933 | 0.10986 | 1.4211e-13 | 0.00065587 | -0.01015 | -0.026644 | -0.023148 | 0.0039977 | 0.0036627 | -0.012148 | 0.027553 | 0.043302 | 0.0013439 | 0.047647 | 0.092615 | 0.028878 | 0.04653 | 0.1208 | 0.13773 | 0.3068 | 0.028521 | -121.5912 | -0.33847 | -121.6119 | 0.070773 | 0.1648 | 0.15427 | -122.3041 | 121.9218 | 0.010941 | 121.9859 | 121.9398 | 0.018009 | 0.027864 | 0.19693 | -0.41079 | -0.03909 | 0.30214 | 0.28137 | 0.69216 | 0.054937 | 0.044403 | 122.0141 | 122.031 | 122.2001 | 121.9222 | -0.081342 | 121.9641 | 122.0581 | 122.0476 | 121.5548 | -122.414
1576.0312 | 122.1268 | -121.8887 | 0.086975 | 1.4211e-13 | 0.00065587 | -0.01015 | -0.026644 | -0.023362 | 0.0039977 | 0.011293 | -0.012788 | 0.027126 | 0.043516 | 0.0013439 | 0.047219 | 0.097194 | 0.033457 | 0.037373 | 0.1208 | 0.14231 | 0.29306 | 0.023942 | -121.6003 | -0.32931 | -121.6165 | 0.061616 | 0.16022 | 0.15884 | -122.3041 | 121.9127 | 0.033829 | 121.9859 | 121.9261 | 0.013431 | 0.055331 | 0.20608 | -0.41536 | -0.025359 | 0.2884 | 0.27221 | 0.68758 | 0.073247 | 0.07187 | 122.0095 | 122.031 | 122.1818 | 121.9222 | -0.063033 | 121.9503 | 122.049 | 122.0476 | 121.5594 | -122.3911
1577.8125 | 122.1542 | -121.8704 | 0.082397 | 1.4211e-13 | 0.00065587 | -0.0097224 | -0.026858 | -0.023576 | 0.0037841 | 0.011293 | -0.012575 | 0.02734 | 0.043089 | 0.00091673 | 0.047219 | 0.092615 | 0.033457 | 0.037373 | 0.1208 | 0.14231 | 0.29764 | 0.023942 | -121.6049 | -0.34304 | -121.6303 | 0.061616 | 0.16022 | 0.15427 | -122.3133 | 121.8944 | 0.038407 | 121.963 | 121.9078 | 0.013431 | 0.059909 | 0.21524 | -0.44283 | -0.020781 | 0.26552 | 0.24017 | 0.683 | 0.077825 | 0.071869 | 121.9912 | 122.0127 | 122.1681 | 121.9039 | -0.058455 | 121.932 | 122.0306 | 122.0247 | 121.5274 | -122.3957
1579.6094 | 122.1863 | -121.8704 | 0.082397 | 1.4211e-13 | 0.00022867 | -0.01015 | -0.027072 | -0.023362 | 0.0037841 | 0.0036627 | -0.012575 | 0.02734 | 0.043516 | 0.0013439 | 0.046792 | 0.097194 | 0.038035 | 0.041952 | 0.11622 | 0.13773 | 0.29306 | 0.023942 | -121.6049 | -0.33847 | -121.6257 | 0.057037 | 0.1648 | 0.16342 | -122.327 | 121.8944 | 0.033828 | 121.9676 | 121.9124 | 0.01801 | 0.05533 | 0.21066 | -0.45657 | -0.02536 | 0.26552 | 0.24475 | 0.70132 | 0.082403 | 0.081026 | 121.9866 | 122.0081 | 122.1635 | 121.9085 | -0.058455 | 121.9275 | 122.0352 | 122.0338 | 121.532 | -122.4094
1581.3438 | 122.1176 | -121.9208 | 0.10529 | 1.4211e-13 | 0.00065587 | -0.010363 | -0.02643 | -0.023362 | 0.0037841 | 0.011293 | -0.012148 | 0.027553 | 0.043089 | 0.0011303 | 0.047006 | 0.097194 | 0.028878 | 0.051108 | 0.11622 | 0.13315 | 0.29764 | 0.023942 | -121.6049 | -0.34304 | -121.6303 | 0.061616 | 0.16938 | 0.15884 | -122.327 | 121.9447 | 0.010939 | 122.018 | 121.9719 | 0.027166 | 0.027862 | 0.19235 | -0.40622 | -0.04367 | 0.31587 | 0.29052 | 0.69674 | 0.064093 | 0.053559 | 122.037 | 122.0539 | 122.2184 | 121.9497 | -0.081344 | 121.9824 | 122.0902 | 122.0796 | 121.5777 | -122.4323
1583.1094 | 122.113 | -121.907 | 0.091553 | 1.4211e-13 | 0.00086967 | -0.0097224 | -0.026858 | -0.023576 | 0.0037841 | 0.011293 | -0.012788 | 0.027553 | 0.043302 | 0.0011303 | 0.047219 | 0.10177 | 0.028878 | 0.04653 | 0.11165 | 0.14231 | 0.29764 | 0.019363 | -121.6186 | -0.34304 | -121.6486 | 0.057037 | 0.16938 | 0.16342 | -122.327 | 121.9264 | 0.020094 | 122.0088 | 121.9536 | 0.027167 | 0.050753 | 0.20609 | -0.41995 | -0.034516 | 0.2884 | 0.25847 | 0.67842 | 0.077826 | 0.07187 | 122.0187 | 122.0493 | 122.2047 | 121.9359 | -0.07219 | 121.9641 | 122.0764 | 122.0705 | 121.564 | -122.4185
1584.8281 | 122.0581 | -121.9299 | 0.10986 | 1.4211e-13 | 0.00086967 | -0.01015 | -0.026858 | -0.023576 | 0.0039977 | 0.011293 | -0.012148 | 0.027553 | 0.043302 | 0.0011303 | 0.047219 | 0.092615 | 0.038035 | 0.051108 | 0.1208 | 0.13773 | 0.29764 | 0.028521 | -121.6232 | -0.33847 | -121.644 | 0.061616 | 0.1648 | 0.15884 | -122.3361 | 121.9585 | 0.010941 | 122.0225 | 121.981 | 0.022587 | 0.027864 | 0.18778 | -0.40622 | -0.048247 | 0.30671 | 0.28594 | 0.69216 | 0.054937 | 0.048982 | 122.0507 | 122.0677 | 122.2276 | 121.968 | -0.081342 | 121.9915 | 122.0947 | 122.0888 | 121.5915 | -122.446
1586.625 | 122.2 | -121.9254 | 0.086975 | 1.4211e-13 | 0.00086967 | -0.009936 | -0.027072 | -0.023576 | 0.0039977 | 0.0036627 | -0.012575 | 0.027767 | 0.043302 | 0.0011303 | 0.047219 | 0.097194 | 0.028878 | 0.04653 | 0.11622 | 0.13773 | 0.29306 | 0.023942 | -121.6324 | -0.34762 | -121.6577 | 0.066194 | 0.16938 | 0.16342 | -122.3453 | 121.9493 | 0.02925 | 122.0225 | 121.9719 | 0.022588 | 0.050752 | 0.20608 | -0.41995 | -0.020781 | 0.29297 | 0.26763 | 0.68758 | 0.082404 | 0.076448 | 122.0416 | 122.0631 | 122.2184 | 121.9542 | -0.063033 | 121.9915 | 122.0947 | 122.0888 | 121.5777 | -122.4323
1588.4062 | 122.2 | -121.8933 | 0.09613 | 1.4211e-13 | 0.00044227 | -0.01015 | -0.026644 | -0.023362 | 0.0039977 | 0.0036627 | -0.012788 | 0.027767 | 0.043516 | 0.0013439 | 0.047433 | 0.092615 | 0.033457 | 0.055687 | 0.11622 | 0.13773 | 0.29306 | 0.028521 | -121.6278 | -0.34762 | -121.6531 | 0.075351 | 0.1648 | 0.15884 | -122.3499 | 121.9218 | 0.020095 | 121.9859 | 121.949 | 0.027166 | 0.041597 | 0.19693 | -0.45658 | -0.020779 | 0.26551 | 0.24016 | 0.69674 | 0.06867 | 0.062715 | 122.0095 | 122.031 | 122.1864 | 121.9268 | -0.067609 | 121.9687 | 122.0581 | 122.0522 | 121.5457 | -122.446
1590.1094 | 122.1725 | -121.9345 | 0.091553 | 1.4211e-13 | 0.00065587 | -0.0097224 | -0.026644 | -0.023148 | 0.0037841 | 0.011293 | -0.012148 | 0.02734 | 0.043089 | 0.0013439 | 0.046792 | 0.092615 | 0.028878 | 0.04653 | 0.11622 | 0.13773 | 0.29306 | 0.010206 | -121.637 | -0.34762 | -121.6577 | 0.070773 | 0.1648 | 0.16342 | -122.3545 | 121.9447 | 0.024672 | 122.0271 | 121.981 | 0.036324 | 0.046174 | 0.20151 | -0.41995 | -0.02078 | 0.29755 | 0.27678 | 0.69674 | 0.073247 | 0.07187 | 122.0507 | 122.0722 | 122.2276 | 121.9634 | -0.081347 | 122.0053 | 122.0993 | 122.0979 | 121.5869 | -122.446
1591.8906 | 122.1497 | -121.9391 | 0.086975 | 1.4211e-13 | 0.00086967 | -0.0095086 | -0.027072 | -0.023576 | 0.0039977 | 0.0036627 | -0.012361 | 0.027767 | 0.043516 | 0.0013439 | 0.047219 | 0.092615 | 0.033457 | 0.055687 | 0.1208 | 0.13315 | 0.29306 | 0.028521 | -121.6415 | -0.3522 | -121.6623 | 0.066194 | 0.16022 | 0.15884 | -122.3545 | 121.9676 | 0.033829 | 122.0317 | 121.9948 | 0.027166 | 0.046173 | 0.20608 | -0.41538 | -0.020781 | 0.29755 | 0.27678 | 0.69216 | 0.073247 | 0.07187 | 122.0599 | 122.0722 | 122.2321 | 121.9725 | -0.058454 | 122.0053 | 122.0993 | 122.0979 | 121.5869 | -122.4414
1593.6875 | 122.081 | -121.9711 | 0.12817 | 1.4211e-13 | 0.00086967 | -0.009936 | -0.026858 | -0.023576 | 0.0037841 | 0.0036627 | -0.012575 | 0.027553 | 0.043302 | 0.00091673 | 0.047219 | 0.097194 | 0.038035 | 0.051108 | 0.11165 | 0.14231 | 0.28848 | 0.019363 | -121.6415 | -0.3522 | -121.6669 | 0.066194 | 0.16022 | 0.14969 | -122.359 | 121.9905 | -0.016527 | 122.0683 | 122.0222 | 0.031745 | 0.014132 | 0.16031 | -0.38791 | -0.06198 | 0.32959 | 0.30425 | 0.69216 | 0.032048 | 0.021513 | 122.0828 | 122.1134 | 122.2596 | 122.0092 | -0.10881 | 122.0373 | 122.1314 | 122.1208 | 121.6189 | -122.4872
1595.4062 | 122.2229 | -121.9116 | 0.068665 | 1.4211e-13 | 0.00065587 | -0.009936 | -0.026644 | -0.023576 | 0.0042113 | 0.0036627 | -0.013002 | 0.027981 | 0.043516 | 0.0013439 | 0.046792 | 0.092615 | 0.038035 | 0.041952 | 0.10707 | 0.14231 | 0.28848 | 0.023942 | -121.6507 | -0.33389 | -121.6669 | 0.066194 | 0.1648 | 0.14969 | -122.3682 | 121.9356 | 0.038403 | 122.0042 | 121.9536 | 0.01801 | 0.073641 | 0.21982 | -0.45658 | -0.002471 | 0.26093 | 0.24474 | 0.70132 | 0.096135 | 0.081022 | 122.0187 | 122.0539 | 122.2001 | 121.9497 | -0.044723 | 121.9778 | 122.0764 | 122.0613 | 121.5777 | -122.4369
1597.125 | 122.0947 | -122.0032 | 0.12817 | 1.4211e-13 | 0.00086967 | -0.0097224 | -0.027072 | -0.023576 | 0.0039977 | -0.011598 | -0.012575 | 0.02734 | 0.043516 | 0.0013439 | 0.047433 | 0.092615 | 0.038035 | 0.041952 | 0.11165 | 0.13773 | 0.29306 | 0.028521 | -121.6461 | -0.33847 | -121.6806 | 0.066194 | 0.16022 | 0.16342 | -122.3728 | 122.0317 | -0.016527 | 122.0958 | 122.0451 | 0.013431 | 0.009553 | 0.16489 | -0.36961 | -0.06198 | 0.35706 | 0.32255 | 0.69216 | 0.032048 | 0.035249 | 122.1148 | 122.1409 | 122.2962 | 122.0412 | -0.099653 | 122.0694 | 122.1634 | 122.1666 | 121.6647 | -122.501
1598.9219 | 122.1176 | -121.994 | 0.11444 | 1.4211e-13 | 0.00065587 | -0.009936 | -0.026858 | -0.023576 | 0.0039977 | 0.011293 | -0.012788 | 0.027553 | 0.043089 | 0.0011303 | 0.047006 | 0.092615 | 0.038035 | 0.051108 | 0.1208 | 0.14231 | 0.29764 | 0.023942 | -121.6507 | -0.34304 | -121.676 | 0.052459 | 0.1648 | 0.16342 | -122.3728 | 122.018 | 0.006363 | 122.0866 | 122.0451 | 0.027166 | 0.027865 | 0.1832 | -0.37876 | -0.061982 | 0.34332 | 0.31798 | 0.69674 | 0.050359 | 0.048982 | 122.1148 | 122.1363 | 122.2917 | 122.0321 | -0.090499 | 122.0465 | 122.1588 | 122.1574 | 121.651 | -122.4872
1600.7031 | 122.2275 | -121.9574 | 0.091553 | 1.4211e-13 | 0.00086967 | -0.009936 | -0.026858 | -0.023576 | 0.0037841 | 0.011293 | -0.012575 | 0.027767 | 0.043302 | 0.0013439 | 0.047219 | 0.092615 | 0.033457 | 0.051108 | 0.11622 | 0.13773 | 0.29306 | 0.028521 | -121.6644 | -0.34304 | -121.6898 | 0.061616 | 0.1648 | 0.15427 | -122.3819 | 121.9859 | 0.024672 | 122.05 | 122.0085 | 0.022587 | 0.046174 | 0.20151 | -0.42454 | -0.029937 | 0.29297 | 0.26762 | 0.69216 | 0.073247 | 0.062713 | 122.0736 | 122.0951 | 122.2505 | 121.9909 | -0.063032 | 122.019 | 122.1222 | 122.1117 | 121.6144 | -122.4735
1602.4375 | 122.2366 | -121.9574 | 0.082397 | 1.4211e-13 | 0.0012971 | -0.009936 | -0.027285 | -0.023362 | 0.0037841 | 0.0036627 | -0.012575 | 0.027553 | 0.043516 | 0.0013439 | 0.047006 | 0.088037 | 0.038035 | 0.055687 | 0.10707 | 0.14231 | 0.29764 | 0.028521 | -121.669 | -0.34304 | -121.6898 | 0.061616 | 0.16938 | 0.15884 | -122.3911 | 121.9859 | 0.024671 | 122.0454 | 122.0131 | 0.027166 | 0.059909 | 0.21524 | -0.4337 | -0.020781 | 0.28839 | 0.26762 | 0.70132 | 0.086982 | 0.076448 | 122.0645 | 122.0997 | 122.255 | 121.9954 | -0.053876 | 122.019 | 122.1268 | 122.1162 | 121.6144 | -122.4735
1604.2188 | 122.1725 | -121.9849 | 0.11444 | 1.4211e-13 | 0.00086967 | -0.0097224 | -0.026858 | -0.024003 | 0.0037841 | 0.0036627 | -0.012575 | 0.02734 | 0.043516 | 0.00091673 | 0.046792 | 0.10177 | 0.042614 | 0.04653 | 0.11165 | 0.13773 | 0.29764 | 0.028521 | -121.6644 | -0.3522 | -121.6852 | 0.066194 | 0.16938 | 0.15884 | -122.3774 | 122.0134 | -0.002794 | 122.0866 | 122.0314 | 0.018009 | 0.023286 | 0.1832 | -0.3925 | -0.048247 | 0.32043 | 0.29966 | 0.69216 | 0.054938 | 0.044404 | 122.0965 | 122.1226 | 122.2825 | 122.0275 | -0.08592 | 122.0511 | 122.1542 | 122.1437 | 121.6327 | -122.4918
1606.0156 | 122.2504 | -121.9482 | 0.091553 | 1.4211e-13 | 0.0010833 | -0.0097224 | -0.026858 | -0.023576 | 0.0037841 | 0.0036627 | -0.012788 | 0.027767 | 0.043729 | 0.0011303 | 0.047219 | 0.097194 | 0.042614 | 0.051108 | 0.11165 | 0.14231 | 0.29306 | 0.028521 | -121.669 | -0.34762 | -121.6989 | 0.061616 | 0.1648 | 0.15884 | -122.3819 | 121.9768 | 0.020094 | 122.0454 | 121.9993 | 0.022587 | 0.050753 | 0.20151 | -0.4337 | -0.029937 | 0.27923 | 0.24931 | 0.683 | 0.073247 | 0.067292 | 122.0599 | 122.0905 | 122.2413 | 121.9909 | -0.063032 | 122.0099 | 122.113 | 122.1071 | 121.6006 | -122.4735
1607.7812 | 122.2687 | -121.9437 | 0.064087 | 1.4211e-13 | 0.00065587 | -0.0095086 | -0.027072 | -0.023362 | 0.0037841 | 0.0036627 | -0.012361 | 0.027981 | 0.043302 | 0.00091673 | 0.047433 | 0.092615 | 0.033457 | 0.051108 | 0.11622 | 0.13315 | 0.29764 | 0.028521 | -121.6736 | -0.3522 | -121.7035 | 0.066194 | 0.1648 | 0.15427 | -122.4003 | 121.9722 | 0.052138 | 122.0363 | 121.9948 | 0.022587 | 0.069061 | 0.23355 | -0.45659 | 0.002107 | 0.27008 | 0.24015 | 0.69674 | 0.10071 | 0.090179 | 122.0599 | 122.0768 | 122.2413 | 121.9771 | -0.035566 | 122.0099 | 122.1085 | 122.0979 | 121.5915 | -122.4643
1609.5 | 122.2549 | -121.9528 | 0.082397 | 1.4211e-13 | 0.0010833 | -0.0095086 | -0.027499 | -0.023148 | 0.0039977 | 0.011293 | -0.012361 | 0.027553 | 0.043302 | 0.0011303 | 0.047433 | 0.097194 | 0.038035 | 0.055687 | 0.11165 | 0.13773 | 0.28848 | 0.028521 | -121.6873 | -0.34762 | -121.6989 | 0.066194 | 0.1648 | 0.16342 | -122.4003 | 121.9813 | 0.02925 | 122.05 | 122.0085 | 0.027166 | 0.05533 | 0.20608 | -0.44743 | -0.016203 | 0.2655 | 0.25388 | 0.70132 | 0.082403 | 0.081026 | 122.0645 | 122.0905 | 122.2413 | 121.9909 | -0.053876 | 122.019 | 122.1176 | 122.1162 | 121.6052 | -122.4827
1611.2812 | 122.168 | -122.0078 | 0.10071 | 1.4211e-13 | 0.00086967 | -0.009936 | -0.026858 | -0.023576 | 0.0039977 | 0.0036627 | -0.012361 | 0.02734 | 0.043089 | 0.0013439 | 0.047219 | 0.092615 | 0.028878 | 0.051108 | 0.11165 | 0.13773 | 0.29764 | 0.023942 | -121.6873 | -0.3522 | -121.7035 | 0.057037 | 0.1648 | 0.15427 | -122.4094 | 122.0317 | 0.010939 | 122.1004 | 122.0589 | 0.027166 | 0.037019 | 0.19693 | -0.40166 | -0.043671 | 0.32043 | 0.30424 | 0.7059 | 0.064092 | 0.053558 | 122.1194 | 122.1455 | 122.3054 | 122.0366 | -0.076766 | 122.0648 | 122.1726 | 122.162 | 121.6555 | -122.5101
1613.0781 | 122.2321 | -121.9711 | 0.09613 | 1.4211e-13 | 0.00086967 | -0.0097224 | -0.026644 | -0.023148 | 0.0037841 | 0.011293 | -0.012788 | 0.02734 | 0.043089 | 0.0011303 | 0.047219 | 0.097194 | 0.042614 | 0.051108 | 0.11165 | 0.14231 | 0.29306 | 0.028521 | -121.6919 | -0.35678 | -121.7081 | 0.061616 | 0.16022 | 0.15427 | -122.4094 | 121.9997 | 0.015517 | 122.0683 | 122.0222 | 0.022587 | 0.046176 | 0.19693 | -0.43828 | -0.034514 | 0.27923 | 0.26304 | 0.70132 | 0.064092 | 0.058136 | 122.0828 | 122.1134 | 122.2642 | 122.0137 | -0.067609 | 122.0327 | 122.1314 | 122.1254 | 121.6144 | -122.5055
1614.7969 | 122.1451 | -122.0123 | 0.1236 | 1.4211e-13 | 0.00086967 | -0.0097224 | -0.027072 | -0.023148 | 0.0039977 | 0.0036627 | -0.013002 | 0.027553 | 0.043516 | 0.0013439 | 0.047219 | 0.097194 | 0.038035 | 0.051108 | 0.1208 | 0.12857 | 0.29306 | 0.028521 | -121.6965 | -0.35678 | -121.7081 | 0.061616 | 0.16022 | 0.15427 | -122.4048 | 122.0408 | -0.002792 | 122.1095 | 122.0634 | 0.022587 | 0.004973 | 0.16946 | -0.3925 | -0.06198 | 0.31585 | 0.30424 | 0.69674 | 0.036626 | 0.03067 | 122.1331 | 122.1409 | 122.3054 | 122.0504 | -0.095075 | 122.0739 | 122.1726 | 122.1666 | 121.6555 | -122.5284
1616.5938 | 122.1497 | -122.0261 | 0.10986 | 1.4211e-13 | 0.0010833 | -0.01015 | -0.026858 | -0.023148 | 0.0039977 | 0.011293 | -0.012788 | 0.027767 | 0.043729 | 0.0011303 | 0.047647 | 0.10177 | 0.038035 | 0.051108 | 0.11165 | 0.13315 | 0.29306 | 0.019363 | -121.6965 | -0.35678 | -121.7173 | 0.061616 | 0.1648 | 0.15884 | -122.414 | 122.0454 | 0.001784 | 122.1278 | 122.0772 | 0.031745 | 0.023285 | 0.1832 | -0.38793 | -0.048247 | 0.32958 | 0.30881 | 0.69674 | 0.054937 | 0.048982 | 122.1377 | 122.1592 | 122.3191 | 122.0641 | -0.0905 | 122.0877 | 122.1909 | 122.1849 | 121.6693 | -122.5239
1618.375 | 122.1497 | -122.0306 | 0.10986 | 1.4211e-13 | 0.00086967 | -0.0097224 | -0.027285 | -0.023362 | 0.0039977 | 0.0036627 | -0.012575 | 0.027553 | 0.042875 | 0.0013439 | 0.047219 | 0.088037 | 0.038035 | 0.051108 | 0.11165 | 0.13315 | 0.29764 | 0.019363 | -121.6965 | -0.35678 | -121.7173 | 0.066194 | 0.17396 | 0.14969 | -122.4231 | 122.05 | 0.001784 | 122.1187 | 122.0817 | 0.031745 | 0.023285 | 0.18778 | -0.39251 | -0.043669 | 0.33416 | 0.31339 | 0.7059 | 0.064095 | 0.039824 | 122.1423 | 122.1638 | 122.3283 | 122.0687 | -0.0905 | 122.0968 | 122.2046 | 122.1803 | 121.6739 | -122.533
1620.1562 | 122.1405 | -122.0078 | 0.10986 | 1.4211e-13 | 0.00065587 | -0.0097224 | -0.026858 | -0.023576 | 0.0039977 | 0.0036627 | -0.012575 | 0.027553 | 0.043089 | 0.0011303 | 0.047433 | 0.097194 | 0.033457 | 0.055687 | 0.12538 | 0.13315 | 0.28848 | 0.023942 | -121.7056 | -0.36136 | -121.7218 | 0.061616 | 0.16938 | 0.16342 | -122.414 | 122.0317 | 0.015519 | 122.1049 | 122.0634 | 0.031745 | 0.023285 | 0.17862 | -0.40624 | -0.048247 | 0.30211 | 0.28592 | 0.69216 | 0.059516 | 0.05356 | 122.1331 | 122.1409 | 122.2962 | 122.0412 | -0.085921 | 122.0694 | 122.1771 | 122.1712 | 121.6464 | -122.5239
1621.9375 | 122.1725 | -122.0535 | 0.11444 | 1.4211e-13 | 0.00065587 | -0.009936 | -0.026644 | -0.023362 | 0.0035703 | 0.018923 | -0.012361 | 0.02734 | 0.043302 | 0.0013439 | 0.047433 | 0.092615 | 0.038035 | 0.051108 | 0.11622 | 0.14231 | 0.29306 | 0.028521 | -121.7011 | -0.37052 | -121.731 | 0.066194 | 0.16022 | 0.15427 | -122.4277 | 122.082 | 0.001784 | 122.1461 | 122.1046 | 0.022587 | 0.027865 | 0.17862 | -0.3742 | -0.048247 | 0.35247 | 0.32254 | 0.69674 | 0.045781 | 0.039825 | 122.1698 | 122.1958 | 122.3466 | 122.0916 | -0.08592 | 122.1197 | 122.2138 | 122.2078 | 121.683 | -122.5422
1623.7188 | 122.2641 | -121.9894 | 0.082397 | 1.4211e-13 | 0.00086967 | -0.009936 | -0.027072 | -0.023576 | 0.0039977 | 0.0036627 | -0.012148 | 0.027553 | 0.043302 | 0.0011303 | 0.047433 | 0.092615 | 0.033457 | 0.055687 | 0.1208 | 0.13773 | 0.29764 | 0.023942 | -121.7148 | -0.36594 | -121.731 | 0.061616 | 0.1648 | 0.15884 | -122.4277 | 122.0134 | 0.038407 | 122.0821 | 122.0451 | 0.031745 | 0.05533 | 0.21524 | -0.43829 | -0.020781 | 0.27464 | 0.25845 | 0.69674 | 0.082403 | 0.076448 | 122.1102 | 122.1272 | 122.2871 | 122.0229 | -0.058455 | 122.0511 | 122.1542 | 122.1483 | 121.6235 | -122.5101
1625.4375 | 122.1771 | -122.0352 | 0.10071 | 1.4211e-13 | 0.00086967 | -0.009936 | -0.026858 | -0.023576 | 0.0039977 | 0.0036627 | -0.012788 | 0.027553 | 0.043302 | 0.00091673 | 0.047219 | 0.092615 | 0.033457 | 0.051108 | 0.1208 | 0.13315 | 0.28848 | 0.0331 | -121.7194 | -0.37052 | -121.731 | 0.052459 | 0.1648 | 0.15427 | -122.4323 | 122.0683 | 0.020096 | 122.1278 | 122.0863 | 0.018008 | 0.03244 | 0.18777 | -0.39709 | -0.048249 | 0.31584 | 0.30423 | 0.70132 | 0.064092 | 0.053558 | 122.156 | 122.1684 | 122.3237 | 122.0687 | -0.067608 | 122.0877 | 122.2 | 122.1895 | 121.6647 | -122.533
1627.2344 | 122.2412 | -122.0398 | 0.09613 | 1.4211e-13 | 0.0012971 | -0.0097224 | -0.026858 | -0.023362 | 0.0039977 | 0.0036627 | -0.012148 | 0.027553 | 0.043302 | 0.00091673 | 0.047006 | 0.097194 | 0.033457 | 0.041952 | 0.11622 | 0.14231 | 0.28848 | 0.023942 | -121.7102 | -0.37052 | -121.7447 | 0.066194 | 0.1648 | 0.15427 | -122.4369 | 122.0637 | 0.020095 | 122.137 | 122.0817 | 0.01801 | 0.046176 | 0.19235 | -0.39709 | -0.029936 | 0.32958 | 0.29507 | 0.69216 | 0.06867 | 0.058136 | 122.156 | 122.1821 | 122.3283 | 122.0733 | -0.072188 | 122.106 | 122.2046 | 122.1941 | 121.6693 | -122.533
1629.0312 | 122.3007 | -121.9803 | 0.068665 | 1.4211e-13 | 0.0010833 | -0.009936 | -0.026644 | -0.023362 | 0.0039977 | 0.011293 | -0.012361 | 0.027767 | 0.043516 | 0.0015577 | 0.047006 | 0.097194 | 0.038035 | 0.055687 | 0.11165 | 0.14231 | 0.28848 | 0.023942 | -121.7148 | -0.36594 | -121.7447 | 0.061616 | 0.16022 | 0.15884 | -122.4323 | 122.0042 | 0.042982 | 122.0775 | 122.036 | 0.031745 | 0.073641 | 0.21982 | -0.45202 | -0.007049 | 0.26549 | 0.23556 | 0.68758 | 0.091557 | 0.09018 | 122.0919 | 122.1226 | 122.2688 | 122.0183 | -0.044723 | 122.0419 | 122.1405 | 122.1391 | 121.6143 | -122.501
1630.8125 | 122.3053 | -121.994 | 0.068665 | 1.4211e-13 | 0.0015107 | -0.0095086 | -0.026644 | -0.023362 | 0.0037841 | 0.011293 | -0.012361 | 0.027553 | 0.043302 | 0.0011303 | 0.047219 | 0.092615 | 0.042614 | 0.051108 | 0.11622 | 0.13773 | 0.29764 | 0.028521 | -121.724 | -0.37052 | -121.7493 | 0.066194 | 0.1648 | 0.15884 | -122.446 | 122.0225 | 0.04756 | 122.0866 | 122.0451 | 0.022587 | 0.069062 | 0.22897 | -0.45202 | -0.002471 | 0.27006 | 0.24472 | 0.69674 | 0.096135 | 0.09018 | 122.1102 | 122.1317 | 122.2917 | 122.0366 | -0.040144 | 122.0602 | 122.1588 | 122.1529 | 121.6235 | -122.5147
1632.5469 | 122.2916 | -121.9849 | 0.091553 | 1.4211e-13 | 0.00086967 | -0.0097224 | -0.026644 | -0.023789 | 0.0039977 | 0.011293 | -0.012575 | 0.027553 | 0.043516 | 0.0011303 | 0.047433 | 0.092615 | 0.038035 | 0.055687 | 0.11165 | 0.13773 | 0.29764 | 0.028521 | -121.7194 | -0.37052 | -121.7493 | 0.070773 | 0.1648 | 0.14969 | -122.4506 | 122.0134 | 0.020094 | 122.0775 | 122.0406 | 0.027166 | 0.046174 | 0.20609 | -0.46576 | -0.02078 | 0.26549 | 0.23556 | 0.70132 | 0.073247 | 0.058134 | 122.0965 | 122.1226 | 122.2825 | 122.0229 | -0.063032 | 122.0556 | 122.1497 | 122.1346 | 121.6143 | -122.5422
1634.3281 | 122.2641 | -122.0078 | 0.086975 | 1.4211e-13 | 0.0010833 | -0.009936 | -0.027072 | -0.023789 | 0.0039977 | 0.0036627 | -0.012575 | 0.02734 | 0.043302 | 0.0011303 | 0.047219 | 0.10177 | 0.033457 | 0.060265 | 0.11165 | 0.13315 | 0.2839 | 0.028521 | -121.7285 | -0.37052 | -121.7539 | 0.066194 | 0.16022 | 0.16342 | -122.4506 | 122.0363 | 0.024672 | 122.1095 | 122.068 | 0.031744 | 0.046173 | 0.19693 | -0.44287 | -0.020781 | 0.27922 | 0.25387 | 0.69674 | 0.073247 | 0.076448 | 122.1194 | 122.1409 | 122.2917 | 122.0412 | -0.058454 | 122.0739 | 122.168 | 122.1712 | 121.6372 | -122.5376
1636.1094 | 122.1634 | -122.0444 | 0.11902 | 1.4211e-13 | 0.0010833 | -0.0097224 | -0.026644 | -0.023362 | 0.0039977 | 0.011293 | -0.012575 | 0.02734 | 0.043516 | 0.0011303 | 0.047219 | 0.092615 | 0.047193 | 0.04653 | 0.1208 | 0.13773 | 0.29306 | 0.028521 | -121.7285 | -0.38425 | -121.7539 | 0.061616 | 0.16938 | 0.15884 | -122.4598 | 122.0729 | 0.001785 | 122.137 | 122.0909 | 0.018009 | 0.018708 | 0.17404 | -0.4154 | -0.057403 | 0.31584 | 0.29049 | 0.7059 | 0.05036 | 0.039826 | 122.1652 | 122.1821 | 122.3374 | 122.0916 | -0.090498 | 122.106 | 122.2138 | 122.2032 | 121.6601 | -122.5788
1637.9062 | 122.2733 | -122.0215 | 0.082397 | 1.4211e-13 | 0.00086967 | -0.0097224 | -0.026858 | -0.023789 | 0.0039977 | -0.0039678 | -0.012148 | 0.02734 | 0.043302 | 0.0013439 | 0.047006 | 0.092615 | 0.042614 | 0.055687 | 0.11622 | 0.13773 | 0.29306 | 0.023942 | -121.7331 | -0.38425 | -121.7539 | 0.066194 | 0.16938 | 0.15427 | -122.4598 | 122.0454 | 0.033828 | 122.1141 | 122.0772 | 0.031745 | 0.05533 | 0.21066 | -0.43829 | -0.016203 | 0.28837 | 0.2676 | 0.7059 | 0.086982 | 0.071869 | 122.1377 | 122.1592 | 122.3145 | 122.0641 | -0.058455 | 122.0877 | 122.1909 | 122.1758 | 121.6372 | -122.5422
1639.7031 | 122.3145 | -122.0215 | 0.086975 | 1.4211e-13 | 0.00086967 | -0.01015 | -0.026858 | -0.023789 | 0.0042113 | 0.018923 | -0.012148 | 0.027553 | 0.043516 | 0.0013439 | 0.047433 | 0.097194 | 0.038035 | 0.055687 | 0.1208 | 0.13773 | 0.28848 | 0.028521 | -121.7285 | -0.37967 | -121.7585 | 0.066194 | 0.16022 | 0.15427 | -122.4552 | 122.05 | 0.033829 | 122.1187 | 122.0772 | 0.027166 | 0.050752 | 0.20151 | -0.43371 | -0.020781 | 0.29295 | 0.26302 | 0.69674 | 0.073247 | 0.067291 | 122.1423 | 122.1592 | 122.31 | 122.0595 | -0.058454 | 122.0877 | 122.1817 | 122.1758 | 121.6418 | -122.5422
1641.4219 | 122.319 | -122.0398 | 0.082397 | 1.4211e-13 | 0.0012971 | -0.009936 | -0.026858 | -0.023362 | 0.0039977 | 0.011293 | -0.012575 | 0.027767 | 0.042875 | 0.0011303 | 0.047219 | 0.092615 | 0.038035 | 0.051108 | 0.11165 | 0.13315 | 0.28848 | 0.037679 | -121.7331 | -0.37967 | -121.7585 | 0.061616 | 0.1648 | 0.16342 | -122.4644 | 122.0775 | 0.02925 | 122.1324 | 122.0909 | 0.013429 | 0.050751 | 0.20608 | -0.42456 | -0.020781 | 0.30668 | 0.28134 | 0.7059 | 0.082403 | 0.081026 | 122.1514 | 122.1729 | 122.3283 | 122.0778 | -0.044718 | 122.1014 | 122.2046 | 122.2032 | 121.6601 | -122.5468
1643.2031 | 122.2733 | -122.0764 | 0.091553 | 1.4211e-13 | 0.0010833 | -0.009936 | -0.026858 | -0.023789 | 0.0039977 | 0.0036627 | -0.012575 | 0.027767 | 0.043302 | 0.00091673 | 0.047433 | 0.092615 | 0.038035 | 0.051108 | 0.11165 | 0.13315 | 0.29764 | 0.023942 | -121.7514 | -0.38425 | -121.763 | 0.066194 | 0.16022 | 0.15884 | -122.4735 | 122.1004 | 0.020094 | 122.169 | 122.1275 | 0.027166 | 0.041595 | 0.20609 | -0.3971 | -0.025359 | 0.32499 | 0.31338 | 0.71048 | 0.068669 | 0.067292 | 122.1881 | 122.2096 | 122.3741 | 122.1145 | -0.067611 | 122.1426 | 122.2366 | 122.2353 | 121.6922 | -122.5651
1645 | 122.2092 | -122.0535 | 0.10529 | 1.4211e-13 | 0.00086967 | -0.009295 | -0.026644 | -0.023789 | 0.0042113 | 0.011293 | -0.012575 | 0.027553 | 0.043516 | 0.00048933 | 0.047433 | 0.092615 | 0.038035 | 0.060265 | 0.10707 | 0.13773 | 0.2839 | 0.023942 | -121.7423 | -0.38883 | -121.7722 | 0.066194 | 0.1648 | 0.15884 | -122.4644 | 122.0775 | 0.001782 | 122.1461 | 122.1138 | 0.036323 | 0.032441 | 0.17862 | -0.41083 | -0.039092 | 0.31126 | 0.28133 | 0.69216 | 0.059514 | 0.053559 | 122.1606 | 122.1913 | 122.3374 | 122.0916 | -0.081344 | 122.1197 | 122.2183 | 122.2124 | 121.6647 | -122.5696
1646.7969 | 122.2778 | -122.0444 | 0.073242 | 1.4211e-13 | 0.0010833 | -0.0097224 | -0.026644 | -0.023576 | 0.0037841 | 0.011293 | -0.012361 | 0.027767 | 0.043302 | 0.0013439 | 0.047433 | 0.097194 | 0.042614 | 0.051108 | 0.11165 | 0.13315 | 0.29306 | 0.028521 | -121.7423 | -0.38425 | -121.7722 | 0.061616 | 0.1648 | 0.15427 | -122.4781 | 122.0729 | 0.038405 | 122.1416 | 122.0955 | 0.022587 | 0.059906 | 0.21982 | -0.43372 | -0.011626 | 0.3021 | 0.27218 | 0.7059 | 0.091558 | 0.081024 | 122.156 | 122.1775 | 122.3374 | 122.087 | -0.044721 | 122.106 | 122.2092 | 122.1986 | 121.6601 | -122.5513
1648.5156 | 122.2549 | -122.049 | 0.10071 | 1.4211e-13 | 0.00065587 | -0.0097224 | -0.026644 | -0.023576 | 0.0037841 | 0.0036627 | -0.012575 | 0.027767 | 0.043302 | 0.00091673 | 0.047433 | 0.097194 | 0.042614 | 0.051108 | 0.11622 | 0.14688 | 0.29306 | 0.028521 | -121.7468 | -0.38883 | -121.7814 | 0.066194 | 0.16022 | 0.14969 | -122.4781 | 122.0775 | 0.015517 | 122.1461 | 122.1001 | 0.022587 | 0.046177 | 0.19235 | -0.42914 | -0.034514 | 0.3021 | 0.2676 | 0.69674 | 0.059514 | 0.048979 | 122.1652 | 122.1958 | 122.342 | 122.0916 | -0.072187 | 122.1151 | 122.2092 | 122.1986 | 121.6601 | -122.5788
1650.2812 | 122.3511 | -122.0581 | 0.068665 | 1.4211e-13 | 0.0012971 | -0.0095086 | -0.026644 | -0.023362 | 0.0039977 | 0.0036627 | -0.012361 | 0.027553 | 0.043302 | 0.0011303 | 0.047433 | 0.10177 | 0.033457 | 0.051108 | 0.10707 | 0.13773 | 0.29764 | 0.028521 | -121.7652 | -0.39341 | -121.7768 | 0.061616 | 0.1648 | 0.16342 | -122.4827 | 122.0866 | 0.038403 | 122.1599 | 122.1092 | 0.022587 | 0.069062 | 0.22897 | -0.42457 | -0.007049 | 0.29294 | 0.28133 | 0.7059 | 0.096135 | 0.094758 | 122.1652 | 122.1958 | 122.3557 | 122.0916 | -0.040144 | 122.1197 | 122.2229 | 122.2215 | 121.6647 | -122.5513
1652.0781 | 122.2046 | -122.0673 | 0.10071 | 1.4211e-13 | 0.0010833 | -0.009936 | -0.026858 | -0.023148 | 0.0037841 | 0.0036627 | -0.012575 | 0.027553 | 0.043302 | 0.0011303 | 0.047647 | 0.092615 | 0.038035 | 0.04653 | 0.11622 | 0.13315 | 0.29306 | 0.0331 | -121.756 | -0.38883 | -121.7814 | 0.066194 | 0.1648 | 0.15427 | -122.4873 | 122.1004 | 0.015517 | 122.1599 | 122.1138 | 0.01343 | 0.03244 | 0.19235 | -0.41999 | -0.034514 | 0.31126 | 0.28591 | 0.7059 | 0.064092 | 0.053558 | 122.1835 | 122.2004 | 122.3603 | 122.1053 | -0.067608 | 122.1335 | 122.2321 | 122.2215 | 121.6784 | -122.588
1653.7969 | 122.3465 | -122.0535 | 0.086975 | 1.4211e-13 | 0.0010833 | -0.009295 | -0.026858 | -0.023362 | 0.0037841 | 0.018923 | -0.012788 | 0.027981 | 0.043516 | 0.0013439 | 0.047219 | 0.092615 | 0.038035 | 0.051108 | 0.11165 | 0.13315 | 0.29764 | 0.0331 | -121.7652 | -0.40257 | -121.7859 | 0.061616 | 0.16938 | 0.14969 | -122.4827 | 122.0866 | 0.024672 | 122.1461 | 122.1046 | 0.018008 | 0.046173 | 0.21066 | -0.42914 | -0.025359 | 0.28837 | 0.2676 | 0.69674 | 0.082404 | 0.062712 | 122.1652 | 122.1867 | 122.3512 | 122.0916 | -0.053875 | 122.1151 | 122.2229 | 122.2032 | 121.651 | -122.5696
1655.5781 | 122.2687 | -122.0581 | 0.082397 | 1.4211e-13 | 0.0010833 | -0.0095086 | -0.026858 | -0.023576 | 0.0039977 | 0.018923 | -0.012788 | 0.02734 | 0.043302 | 0.00091673 | 0.047433 | 0.092615 | 0.047193 | 0.051108 | 0.11622 | 0.13315 | 0.29306 | 0.019363 | -121.7606 | -0.39799 | -121.7814 | 0.061616 | 0.16022 | 0.14969 | -122.4827 | 122.0775 | 0.033828 | 122.1507 | 122.1092 | 0.031745 | 0.050751 | 0.21066 | -0.42457 | -0.020781 | 0.29752 | 0.27675 | 0.70132 | 0.077825 | 0.06729 | 122.1743 | 122.1913 | 122.3512 | 122.1053 | -0.063034 | 122.1197 | 122.2183 | 122.2078 | 121.6601 | -122.5651
1657.3594 | 122.2961 | -122.0444 | 0.082397 | 1.4211e-13 | 0.0010833 | -0.009936 | -0.026858 | -0.023362 | 0.0039977 | 0.011293 | -0.012361 | 0.027553 | 0.043729 | 0.00091673 | 0.047006 | 0.10177 | 0.042614 | 0.041952 | 0.11622 | 0.13773 | 0.2839 | 0.028521 | -121.7697 | -0.39799 | -121.7951 | 0.061616 | 0.16022 | 0.14969 | -122.4964 | 122.0729 | 0.033828 | 122.1461 | 122.0863 | 0.013431 | 0.05533 | 0.20151 | -0.45204 | -0.020781 | 0.27463 | 0.24928 | 0.70132 | 0.077825 | 0.06729 | 122.1606 | 122.1821 | 122.3283 | 122.087 | -0.053876 | 122.106 | 122.2046 | 122.1941 | 121.6464 | -122.5788
1659.0781 | 122.3648 | -122.0352 | 0.10529 | 1.4211e-13 | 0.0010833 | -0.0095086 | -0.026644 | -0.023576 | 0.0037841 | 0.0036627 | -0.012148 | 0.027767 | 0.043516 | 0.0011303 | 0.047219 | 0.092615 | 0.042614 | 0.055687 | 0.10707 | 0.13773 | 0.29306 | 0.0331 | -121.7743 | -0.40715 | -121.7951 | 0.066194 | 0.15564 | 0.15884 | -122.4918 | 122.0683 | 0.001782 | 122.1278 | 122.0909 | 0.022587 | 0.032441 | 0.18777 | -0.45661 | -0.039092 | 0.2609 | 0.24013 | 0.69674 | 0.050357 | 0.053559 | 122.1423 | 122.1729 | 122.3283 | 122.0778 | -0.072186 | 122.1014 | 122.1909 | 122.1941 | 121.6281 | -122.5971
1660.8594 | 122.2229 | -122.1039 | 0.11902 | 1.4211e-13 | 0.0012971 | -0.009936 | -0.026858 | -0.023362 | 0.0039977 | 0.0036627 | -0.012575 | 0.027767 | 0.043302 | 0.00091673 | 0.047433 | 0.097194 | 0.038035 | 0.04653 | 0.1208 | 0.13773 | 0.29306 | 0.028521 | -121.7652 | -0.40257 | -121.7951 | 0.061616 | 0.16022 | 0.15884 | -122.5056 | 122.1324 | 0.001785 | 122.2011 | 122.1504 | 0.018009 | 0.018708 | 0.17404 | -0.40168 | -0.057403 | 0.33872 | 0.30879 | 0.71048 | 0.041203 | 0.039826 | 122.2247 | 122.2416 | 122.3969 | 122.1419 | -0.090498 | 122.1655 | 122.2641 | 122.2627 | 121.7013 | -122.6246
1662.6562 | 122.3877 | -122.0947 | 0.086975 | 1.4211e-13 | 0.0010833 | -0.0097224 | -0.026858 | -0.023362 | 0.0039977 | 0.0036627 | -0.012788 | 0.027981 | 0.043516 | 0.00091673 | 0.047006 | 0.097194 | 0.038035 | 0.051108 | 0.11165 | 0.13315 | 0.29764 | 0.0331 | -121.7789 | -0.40715 | -121.7997 | 0.061616 | 0.16938 | 0.14969 | -122.501 | 122.1278 | 0.024672 | 122.1919 | 122.1458 | 0.018008 | 0.046173 | 0.21066 | -0.40626 | -0.025359 | 0.31583 | 0.29506 | 0.70132 | 0.082404 | 0.062712 | 122.2064 | 122.2279 | 122.3924 | 122.1328 | -0.053875 | 122.1563 | 122.2641 | 122.2444 | 121.6876 | -122.588
1664.375 | 122.2961 | -122.0627 | 0.10071 | 1.4211e-13 | 0.0012971 | -0.0097224 | -0.026644 | -0.023148 | 0.0037841 | 0.011293 | -0.012575 | 0.027553 | 0.043302 | 0.0011303 | 0.047219 | 0.092615 | 0.033457 | 0.051108 | 0.11622 | 0.12857 | 0.29306 | 0.028521 | -121.7743 | -0.41173 | -121.7997 | 0.061616 | 0.16938 | 0.14969 | -122.5101 | 122.0912 | 0.015517 | 122.1553 | 122.1138 | 0.022587 | 0.027861 | 0.19235 | -0.44746 | -0.039092 | 0.28836 | 0.26302 | 0.71048 | 0.068671 | 0.048979 | 122.1789 | 122.1913 | 122.3557 | 122.0961 | -0.072187 | 122.1243 | 122.2321 | 122.2124 | 121.651 | -122.6109
1666.1406 | 122.3465 | -122.081 | 0.082397 | 1.4211e-13 | 0.0012971 | -0.0095086 | -0.026644 | -0.023576 | 0.0039977 | 0.0036627 | -0.012361 | 0.02734 | 0.043302 | 0.0011303 | 0.047433 | 0.092615 | 0.042614 | 0.051108 | 0.11622 | 0.13315 | 0.29306 | 0.037679 | -121.7835 | -0.4163 | -121.8042 | 0.061616 | 0.16022 | 0.14969 | -122.5147 | 122.1187 | 0.033828 | 122.1736 | 122.1321 | 0.013429 | 0.050751 | 0.21066 | -0.43373 | -0.020781 | 0.29752 | 0.27675 | 0.71048 | 0.077825 | 0.06729 | 122.1972 | 122.2141 | 122.3741 | 122.1236 | -0.044718 | 122.1426 | 122.2412 | 122.2307 | 121.6647 | -122.5971
1667.8594 | 122.2549 | -122.0947 | 0.09613 | 1.4211e-13 | 0.0012971 | -0.0095086 | -0.026644 | -0.023148 | 0.0042113 | 0.0036627 | -0.012788 | 0.02734 | 0.043516 | 0.0013439 | 0.047219 | 0.092615 | 0.033457 | 0.041952 | 0.10707 | 0.14231 | 0.28848 | 0.0331 | -121.7835 | -0.4163 | -121.7997 | 0.057037 | 0.16938 | 0.14969 | -122.5101 | 122.1278 | 0.010938 | 122.1873 | 122.1367 | 0.008852 | 0.046176 | 0.19235 | -0.41542 | -0.039093 | 0.31125 | 0.29506 | 0.71048 | 0.073249 | 0.053557 | 122.2018 | 122.237 | 122.3832 | 122.1282 | -0.06303 | 122.1518 | 122.2641 | 122.2444 | 121.6784 | -122.6063
1669.6406 | 122.3648 | -122.0627 | 0.091553 | 1.4211e-13 | 0.0012971 | -0.0097224 | -0.026644 | -0.023576 | 0.0037841 | 0.0036627 | -0.012788 | 0.027553 | 0.043089 | 0.00091673 | 0.047219 | 0.092615 | 0.033457 | 0.051108 | 0.11165 | 0.13315 | 0.29306 | 0.028521 | -121.7881 | -0.42546 | -121.8134 | 0.057037 | 0.16938 | 0.15427 | -122.5147 | 122.0912 | 0.020094 | 122.1553 | 122.1138 | 0.022587 | 0.041595 | 0.20151 | -0.45204 | -0.034516 | 0.27463 | 0.24928 | 0.70132 | 0.077826 | 0.062713 | 122.1743 | 122.1958 | 122.3557 | 122.0961 | -0.063032 | 122.1197 | 122.2321 | 122.2169 | 121.6372 | -122.6063
1671.3594 | 122.3282 | -122.0673 | 0.07782 | 1.4211e-13 | 0.0012971 | -0.0090814 | -0.02643 | -0.023362 | 0.0039977 | 0.0036627 | -0.012361 | 0.02734 | 0.043516 | 0.0011303 | 0.047433 | 0.092615 | 0.038035 | 0.055687 | 0.11622 | 0.13315 | 0.28848 | 0.028521 | -121.8018 | -0.41173 | -121.8134 | 0.061616 | 0.16938 | 0.15427 | -122.5193 | 122.0958 | 0.038405 | 122.1599 | 122.1229 | 0.027166 | 0.055328 | 0.21066 | -0.45204 | -0.016204 | 0.26547 | 0.25386 | 0.7059 | 0.091559 | 0.076446 | 122.1835 | 122.2004 | 122.3557 | 122.1053 | -0.049299 | 122.1289 | 122.2366 | 122.2215 | 121.6555 | -122.5971
1673.1406 | 122.2458 | -122.1039 | 0.11902 | 1.4211e-13 | 0.0012971 | -0.01015 | -0.026858 | -0.023576 | 0.0037841 | -0.0039678 | -0.012575 | 0.027767 | 0.043302 | 0.0011303 | 0.047219 | 0.092615 | 0.038035 | 0.051108 | 0.11165 | 0.13315 | 0.29306 | 0.028521 | -121.7926 | -0.42546 | -121.8134 | 0.057037 | 0.1648 | 0.15427 | -122.5193 | 122.1324 | -0.007372 | 122.1965 | 122.155 | 0.022587 | 0.014129 | 0.17404 | -0.41542 | -0.061982 | 0.31125 | 0.29048 | 0.7059 | 0.045781 | 0.035247 | 122.2155 | 122.237 | 122.3969 | 122.1419 | -0.090498 | 122.1609 | 122.2687 | 122.2581 | 121.6784 | -122.6383
1674.8594 | 122.3923 | -122.0764 | 0.064087 | 1.4211e-13 | 0.0015107 | -0.0097224 | -0.026858 | -0.023576 | 0.0042113 | 0.0036627 | -0.012361 | 0.027553 | 0.043729 | 0.0011303 | 0.047433 | 0.083459 | 0.028878 | 0.04653 | 0.11165 | 0.14231 | 0.29306 | 0.023942 | -121.7972 | -0.43004 | -121.818 | 0.057037 | 0.16938 | 0.14511 | -122.5193 | 122.1004 | 0.04756 | 122.1599 | 122.1229 | 0.022588 | 0.078219 | 0.22897 | -0.44289 | -0.00705 | 0.2792 | 0.25843 | 0.70132 | 0.10529 | 0.081022 | 122.1881 | 122.2187 | 122.3695 | 122.1053 | -0.040145 | 122.1335 | 122.2458 | 122.2215 | 121.6464 | -122.5834
1676.6406 | 122.3328 | -122.0947 | 0.086975 | 1.4211e-13 | 0.00086967 | -0.0095086 | -0.02643 | -0.023362 | 0.0044249 | 0.018923 | -0.012361 | 0.027553 | 0.043729 | 0.0013439 | 0.047219 | 0.092615 | 0.033457 | 0.051108 | 0.11622 | 0.13315 | 0.29764 | 0.019363 | -121.8018 | -0.42546 | -121.818 | 0.061616 | 0.16938 | 0.14053 | -122.5285 | 122.1141 | 0.02925 | 122.1873 | 122.1458 | 0.031745 | 0.046173 | 0.21066 | -0.43373 | -0.025359 | 0.29293 | 0.27675 | 0.71048 | 0.082404 | 0.053555 | 122.211 | 122.2279 | 122.3924 | 122.1282 | -0.067612 | 122.1563 | 122.2641 | 122.2353 | 121.6693 | -122.6154
1678.4375 | 122.3923 | -122.0764 | 0.082397 | 1.4211e-13 | 0.0012971 | -0.0097224 | -0.026644 | -0.023789 | 0.0039977 | 0.011293 | -0.012575 | 0.027553 | 0.043302 | 0.0011303 | 0.047219 | 0.10177 | 0.033457 | 0.041952 | 0.10707 | 0.13773 | 0.29306 | 0.019363 | -121.7972 | -0.43462 | -121.8226 | 0.061616 | 0.16938 | 0.15427 | -122.5285 | 122.0958 | 0.024671 | 122.1782 | 122.1184 | 0.022589 | 0.05533 | 0.21066 | -0.45204 | -0.020781 | 0.2792 | 0.25386 | 0.7059 | 0.086982 | 0.071869 | 122.1835 | 122.2141 | 122.3695 | 122.1099 | -0.063034 | 122.138 | 122.2458 | 122.2307 | 121.6418 | -122.6109
1680.2188 | 122.3328 | -122.113 | 0.091553 | 1.4211e-13 | 0.0010833 | -0.0095086 | -0.026644 | -0.023362 | 0.0039977 | 0.011293 | -0.012148 | 0.027553 | 0.043516 | 0.00070293 | 0.047219 | 0.097194 | 0.042614 | 0.051108 | 0.11165 | 0.14231 | 0.30222 | 0.023942 | -121.8018 | -0.43004 | -121.8271 | 0.061616 | 0.1648 | 0.14969 | -122.5376 | 122.137 | 0.020094 | 122.2102 | 122.1641 | 0.027166 | 0.050753 | 0.21066 | -0.42458 | -0.029937 | 0.31124 | 0.2859 | 0.71048 | 0.073247 | 0.058134 | 122.2247 | 122.2553 | 122.4153 | 122.1557 | -0.067611 | 122.1747 | 122.2778 | 122.2627 | 121.683 | -122.6292
1682.0156 | 122.2412 | -122.1313 | 0.10986 | 1.4211e-13 | 0.0017243 | -0.0097224 | -0.026644 | -0.024003 | 0.0037841 | 0.0036627 | -0.012361 | 0.027767 | 0.043729 | 0.0011303 | 0.047219 | 0.097194 | 0.038035 | 0.055687 | 0.11622 | 0.14688 | 0.29306 | 0.023942 | -121.8064 | -0.43462 | -121.8317 | 0.061616 | 0.16938 | 0.14969 | -122.5376 | 122.1553 | 0.006362 | 122.2285 | 122.187 | 0.031745 | 0.037022 | 0.1832 | -0.40627 | -0.048247 | 0.32498 | 0.29963 | 0.7059 | 0.059516 | 0.039824 | 122.2476 | 122.2782 | 122.4244 | 122.1694 | -0.085921 | 122.193 | 122.3007 | 122.281 | 121.6967 | -122.6475
1683.7344 | 122.3923 | -122.0764 | 0.073242 | 1.4211e-13 | 0.0015107 | -0.0095086 | -0.026644 | -0.023148 | 0.0039977 | 0.0036627 | -0.012575 | 0.027553 | 0.043729 | 0.0011303 | 0.047219 | 0.092615 | 0.038035 | 0.055687 | 0.11165 | 0.13773 | 0.28848 | 0.028521 | -121.7972 | -0.4392 | -121.8226 | 0.061616 | 0.16938 | 0.15427 | -122.5422 | 122.1049 | 0.038405 | 122.169 | 122.1321 | 0.027166 | 0.064485 | 0.21524 | -0.46578 | -0.011626 | 0.2792 | 0.25386 | 0.71964 | 0.096137 | 0.081024 | 122.1881 | 122.2141 | 122.3649 | 122.1145 | -0.044721 | 122.138 | 122.2458 | 122.2307 | 121.6372 | -122.6154
1685.5 | 122.3007 | -122.1039 | 0.10071 | 1.4211e-13 | 0.0015107 | -0.01015 | -0.026644 | -0.023362 | 0.0039977 | 0.011293 | -0.012575 | 0.027553 | 0.043516 | 0.0011303 | 0.047219 | 0.097194 | 0.042614 | 0.055687 | 0.11622 | 0.13315 | 0.2839 | 0.023942 | -121.8109 | -0.4392 | -121.8363 | 0.061616 | 0.17396 | 0.15427 | -122.5376 | 122.1278 | 0.015517 | 122.2011 | 122.1596 | 0.031745 | 0.03244 | 0.18319 | -0.43373 | -0.039092 | 0.29293 | 0.26758 | 0.70132 | 0.07325 | 0.053558 | 122.2201 | 122.237 | 122.3878 | 122.1465 | -0.076766 | 122.1655 | 122.2778 | 122.2581 | 121.6647 | -122.6383
1687.2812 | 122.3465 | -122.1176 | 0.082397 | 1.4211e-13 | 0.0012971 | -0.0097224 | -0.027072 | -0.023576 | 0.0039977 | 0.011293 | -0.012361 | 0.027767 | 0.043302 | 0.0013439 | 0.047006 | 0.097194 | 0.038035 | 0.055687 | 0.11165 | 0.13315 | 0.2839 | 0.028521 | -121.8109 | -0.4392 | -121.8363 | 0.070773 | 0.16938 | 0.15884 | -122.5468 | 122.1461 | 0.02925 | 122.2148 | 122.1733 | 0.027166 | 0.050751 | 0.20151 | -0.42916 | -0.011624 | 0.30667 | 0.28132 | 0.71048 | 0.086982 | 0.076448 | 122.2293 | 122.2508 | 122.4015 | 122.1556 | -0.053876 | 122.1884 | 122.287 | 122.2765 | 121.6784 | -122.6292
1689.0625 | 122.2641 | -122.1451 | 0.10986 | 1.4211e-13 | 0.0010833 | -0.0097224 | -0.026644 | -0.023789 | 0.0039977 | 0.011293 | -0.012361 | 0.027767 | 0.043302 | 0.00091673 | 0.047433 | 0.088037 | 0.038035 | 0.055687 | 0.10707 | 0.13315 | 0.2839 | 0.0331 | -121.8109 | -0.4392 | -121.8363 | 0.057037 | 0.1648 | 0.14969 | -122.5468 | 122.1782 | -0.002795 | 122.2331 | 122.2008 | 0.022587 | 0.023285 | 0.17404 | -0.40169 | -0.052826 | 0.33413 | 0.30878 | 0.71048 | 0.054937 | 0.039824 | 122.2521 | 122.2782 | 122.429 | 122.1831 | -0.076763 | 122.2021 | 122.3099 | 122.2948 | 121.7059 | -122.6566
1690.8438 | 122.3328 | -122.1085 | 0.10071 | 1.4211e-13 | 0.0012971 | -0.010363 | -0.027072 | -0.023362 | 0.0039977 | 0.0036627 | -0.012361 | 0.02734 | 0.043302 | 0.00070293 | 0.047219 | 0.092615 | 0.042614 | 0.051108 | 0.11165 | 0.12857 | 0.28848 | 0.0331 | -121.8155 | -0.44378 | -121.8409 | 0.066194 | 0.1648 | 0.14969 | -122.5514 | 122.1416 | 0.010939 | 122.2011 | 122.1596 | 0.018008 | 0.027861 | 0.18777 | -0.4429 | -0.034514 | 0.29293 | 0.26758 | 0.71048 | 0.064092 | 0.048979 | 122.2201 | 122.237 | 122.3969 | 122.1511 | -0.067608 | 122.1747 | 122.2733 | 122.2581 | 121.6647 | -122.6521
1692.5625 | 122.3465 | -122.1222 | 0.082397 | 1.4211e-13 | 0.0012971 | -0.0095086 | -0.026858 | -0.023789 | 0.0042113 | 0.011293 | -0.012575 | 0.027553 | 0.043516 | 0.00091673 | 0.047219 | 0.092615 | 0.042614 | 0.04653 | 0.10707 | 0.13315 | 0.28848 | 0.0331 | -121.8155 | -0.43004 | -121.8409 | 0.061616 | 0.16022 | 0.14969 | -122.5605 | 122.1553 | 0.024671 | 122.2148 | 122.1687 | 0.01343 | 0.050751 | 0.20608 | -0.43832 | -0.020781 | 0.30666 | 0.28132 | 0.71964 | 0.077825 | 0.06729 | 122.2293 | 122.2553 | 122.4107 | 122.1648 | -0.049297 | 122.1838 | 122.2824 | 122.2719 | 121.6922 | -122.6429
1694.3281 | 122.3648 | -122.1085 | 0.091553 | 1.4211e-13 | 0.0010833 | -0.0097224 | -0.027072 | -0.023362 | 0.0039977 | 0.0036627 | -0.012361 | 0.02734 | 0.043516 | 0.00091673 | 0.047647 | 0.088037 | 0.033457 | 0.051108 | 0.11165 | 0.13773 | 0.27932 | 0.028521 | -121.8293 | -0.44378 | -121.8455 | 0.061616 | 0.15564 | 0.15884 | -122.5651 | 122.137 | 0.020094 | 122.1965 | 122.1596 | 0.022587 | 0.046174 | 0.18777 | -0.45663 | -0.029937 | 0.2792 | 0.263 | 0.71963 | 0.06409 | 0.067292 | 122.2201 | 122.2462 | 122.3878 | 122.1419 | -0.063032 | 122.1701 | 122.2641 | 122.2673 | 121.6647 | -122.6566
1696.1094 | 122.2549 | -122.168 | 0.11444 | 1.4211e-13 | 0.0017243 | -0.0097224 | -0.026858 | -0.023576 | 0.0039977 | 0.011293 | -0.012148 | 0.027553 | 0.043302 | 0.00091673 | 0.047433 | 0.092615 | 0.038035 | 0.04653 | 0.11622 | 0.13315 | 0.28848 | 0.028521 | -121.8247 | -0.44836 | -121.8455 | 0.061616 | 0.1648 | 0.15884 | -122.5605 | 122.1965 | 0.001784 | 122.2606 | 122.2145 | 0.018009 | 0.018707 | 0.17404 | -0.39254 | -0.052825 | 0.34328 | 0.32251 | 0.71506 | 0.050359 | 0.044404 | 122.2842 | 122.3011 | 122.4565 | 122.206 | -0.08592 | 122.2296 | 122.3328 | 122.3268 | 121.7196 | -122.675
1697.8906 | 122.3236 | -122.1359 | 0.068665 | 1.4211e-13 | 0.0012971 | -0.0097224 | -0.026644 | -0.023789 | 0.0039977 | 0.0036627 | -0.012575 | 0.027767 | 0.043943 | 0.00091673 | 0.047433 | 0.092615 | 0.038035 | 0.055687 | 0.11622 | 0.13773 | 0.29306 | 0.028521 | -121.8293 | -0.44378 | -121.8546 | 0.057037 | 0.16022 | 0.15884 | -122.5605 | 122.1644 | 0.04756 | 122.2285 | 122.1916 | 0.027166 | 0.069062 | 0.22439 | -0.42459 | -0.011628 | 0.30666 | 0.28131 | 0.7059 | 0.091557 | 0.09018 | 122.2522 | 122.2737 | 122.429 | 122.174 | -0.040144 | 122.193 | 122.2961 | 122.2948 | 121.6921 | -122.6292
1699.6719 | 122.3969 | -122.1222 | 0.086975 | 1.4211e-13 | 0.0012971 | -0.009936 | -0.026644 | -0.024003 | 0.0044249 | -0.0039678 | -0.012361 | 0.027553 | 0.043516 | 0.00091673 | 0.047219 | 0.092615 | 0.033457 | 0.04653 | 0.11622 | 0.12399 | 0.2839 | 0.028521 | -121.8247 | -0.44836 | -121.8546 | 0.061616 | 0.16022 | 0.16342 | -122.5742 | 122.1507 | 0.02925 | 122.2148 | 122.1687 | 0.018009 | 0.037015 | 0.19693 | -0.45206 | -0.025359 | 0.29751 | 0.26758 | 0.71964 | 0.073247 | 0.076448 | 122.2384 | 122.2462 | 122.4061 | 122.1556 | -0.058454 | 122.1838 | 122.2824 | 122.2856 | 121.6738 | -122.6612
1701.4531 | 122.319 | -122.1451 | 0.091553 | 1.4211e-13 | 0.0017243 | -0.0097224 | -0.026644 | -0.023362 | 0.0042113 | 0.011293 | -0.012361 | 0.027553 | 0.043516 | 0.00091673 | 0.047433 | 0.097194 | 0.038035 | 0.055687 | 0.11622 | 0.12857 | 0.2839 | 0.019363 | -121.8384 | -0.44378 | -121.85 | 0.057037 | 0.16938 | 0.14969 | -122.5651 | 122.1644 | 0.024672 | 122.2423 | 122.2008 | 0.036324 | 0.037016 | 0.19235 | -0.42001 | -0.034516 | 0.30666 | 0.29505 | 0.71506 | 0.077826 | 0.058134 | 122.2613 | 122.2737 | 122.429 | 122.1831 | -0.07219 | 122.2021 | 122.3145 | 122.2948 | 121.7013 | -122.6566
1703.1719 | 122.3785 | -122.1405 | 0.09613 | 1.4211e-13 | 0.0017243 | -0.0097224 | -0.026644 | -0.023576 | 0.0039977 | -0.0039678 | -0.012575 | 0.027553 | 0.043729 | 0.00091673 | 0.047647 | 0.097194 | 0.033457 | 0.051108 | 0.11165 | 0.12857 | 0.28848 | 0.028521 | -121.8293 | -0.45293 | -121.8592 | 0.061616 | 0.1648 | 0.15884 | -122.5697 | 122.169 | 0.015517 | 122.2377 | 122.1916 | 0.022587 | 0.032439 | 0.19235 | -0.42917 | -0.034514 | 0.31124 | 0.28131 | 0.71048 | 0.06867 | 0.062715 | 122.2522 | 122.2691 | 122.429 | 122.174 | -0.067609 | 122.2021 | 122.3053 | 122.2993 | 121.6876 | -122.6658
1704.9375 | 122.287 | -122.1817 | 0.1236 | 1.4211e-13 | 0.0015107 | -0.009936 | -0.026644 | -0.023362 | 0.0042113 | 0.0036627 | -0.012575 | 0.027553 | 0.043302 | 0.0011303 | 0.047647 | 0.097194 | 0.042614 | 0.04653 | 0.11165 | 0.13315 | 0.29306 | 0.023942 | -121.8247 | -0.44836 | -121.8546 | 0.066194 | 0.1648 | 0.15427 | -122.5742 | 122.2056 | -0.011949 | 122.2789 | 122.2282 | 0.022588 | 0.009552 | 0.16946 | -0.39255 | -0.057402 | 0.35702 | 0.32709 | 0.71964 | 0.041204 | 0.03067 | 122.2933 | 122.3149 | 122.4748 | 122.2243 | -0.099654 | 122.2479 | 122.3465 | 122.336 | 121.7333 | -122.6978
1706.7188 | 122.4152 | -122.1405 | 0.086975 | 1.4211e-13 | 0.0012971 | -0.009936 | -0.026858 | -0.023576 | 0.0042113 | 0.0036627 | -0.012361 | 0.02734 | 0.043516 | 0.0011303 | 0.047433 | 0.092615 | 0.038035 | 0.04653 | 0.11622 | 0.13315 | 0.29306 | 0.0331 | -121.8384 | -0.44378 | -121.8546 | 0.061616 | 0.1648 | 0.15427 | -122.5788 | 122.1736 | 0.02925 | 122.2331 | 122.187 | 0.01343 | 0.046173 | 0.20608 | -0.43832 | -0.025359 | 0.30208 | 0.28589 | 0.72421 | 0.077825 | 0.067291 | 122.2567 | 122.2737 | 122.4336 | 122.1785 | -0.053875 | 122.2021 | 122.3053 | 122.2948 | 121.6967 | -122.6658
1708.5 | 122.4106 | -122.1268 | 0.09613 | 1.4211e-13 | 0.0017243 | -0.009936 | -0.02643 | -0.023362 | 0.0039977 | 0.0036627 | -0.012361 | 0.027767 | 0.043302 | 0.00091673 | 0.047219 | 0.092615 | 0.038035 | 0.051108 | 0.11165 | 0.13773 | 0.28848 | 0.028521 | -121.8476 | -0.44378 | -121.8592 | 0.066194 | 0.16938 | 0.15884 | -122.5788 | 122.1553 | 0.015517 | 122.2194 | 122.1779 | 0.022587 | 0.041597 | 0.19235 | -0.45206 | -0.029936 | 0.27919 | 0.26758 | 0.71964 | 0.073249 | 0.062715 | 122.2384 | 122.2645 | 122.4153 | 122.1648 | -0.067609 | 122.193 | 122.2961 | 122.2856 | 121.683 | -122.675
1710.2031 | 122.2916 | -122.168 | 0.10071 | 1.4211e-13 | 0.0015107 | -0.009936 | -0.026644 | -0.023362 | 0.0035703 | 0.0036627 | -0.012575 | 0.027553 | 0.043302 | 0.0013439 | 0.047219 | 0.092615 | 0.033457 | 0.055687 | 0.11165 | 0.12857 | 0.2839 | 0.028521 | -121.8384 | -0.45293 | -121.8683 | 0.061616 | 0.16022 | 0.15427 | -122.5834 | 122.1965 | 0.010939 | 122.2606 | 122.2237 | 0.027166 | 0.027861 | 0.18319 | -0.41544 | -0.039092 | 0.32955 | 0.29962 | 0.71506 | 0.059514 | 0.053558 | 122.2796 | 122.2965 | 122.4519 | 122.2014 | -0.072187 | 122.2296 | 122.3282 | 122.3222 | 121.715 | -122.6841
1711.9688 | 122.3053 | -122.168 | 0.11444 | 1.4211e-13 | 0.0012971 | -0.0095086 | -0.026644 | -0.023576 | 0.0039977 | 0.011293 | -0.012575 | 0.027767 | 0.043302 | 0.0013439 | 0.047433 | 0.092615 | 0.042614 | 0.04653 | 0.11622 | 0.13315 | 0.28848 | 0.028521 | -121.843 | -0.45293 | -121.8683 | 0.066194 | 0.15107 | 0.15427 | -122.5834 | 122.1965 | 0.001784 | 122.2606 | 122.2145 | 0.018009 | 0.018707 | 0.17404 | -0.41544 | -0.048247 | 0.32497 | 0.29962 | 0.71506 | 0.036624 | 0.039825 | 122.2842 | 122.3011 | 122.4565 | 122.2106 | -0.08592 | 122.2342 | 122.319 | 122.3222 | 121.715 | -122.6978
1713.7344 | 122.374 | -122.1542 | 0.091553 | 1.4211e-13 | 0.0017243 | -0.009295 | -0.026644 | -0.023789 | 0.0037841 | 0.018923 | -0.012361 | 0.027767 | 0.043516 | 0.0013439 | 0.047219 | 0.092615 | 0.042614 | 0.04653 | 0.11165 | 0.13315 | 0.2839 | 0.0331 | -121.8476 | -0.44836 | -121.8729 | 0.061616 | 0.16022 | 0.14969 | -122.588 | 122.1873 | 0.020094 | 122.2469 | 122.2008 | 0.01343 | 0.041595 | 0.19235 | -0.43375 | -0.029937 | 0.30666 | 0.28131 | 0.71506 | 0.068669 | 0.058134 | 122.2659 | 122.2874 | 122.4381 | 122.1968 | -0.058453 | 122.2159 | 122.3145 | 122.3039 | 121.7059 | -122.6795
1715.5156 | 122.4197 | -122.1313 | 0.073242 | 1.4211e-13 | 0.0012971 | -0.0097224 | -0.026858 | -0.023576 | 0.0042113 | 0.0036627 | -0.012361 | 0.027767 | 0.043729 | 0.00091673 | 0.04786 | 0.092615 | 0.038035 | 0.04653 | 0.11622 | 0.13773 | 0.28848 | 0.028521 | -121.8522 | -0.46209 | -121.8683 | 0.057037 | 0.16938 | 0.15427 | -122.588 | 122.1599 | 0.042983 | 122.224 | 122.1779 | 0.018009 | 0.064485 | 0.21524 | -0.45664 | -0.016205 | 0.27919 | 0.263 | 0.71964 | 0.096137 | 0.081024 | 122.2476 | 122.2691 | 122.4198 | 122.1694 | -0.044721 | 122.1884 | 122.3007 | 122.2856 | 121.6693 | -122.6612
1717.2344 | 122.3053 | -122.168 | 0.11902 | 1.4211e-13 | 0.0010833 | -0.0095086 | -0.026858 | -0.023576 | 0.0039977 | 0.011293 | -0.012575 | 0.027553 | 0.043302 | 0.00091673 | 0.047647 | 0.092615 | 0.038035 | 0.060265 | 0.10707 | 0.12857 | 0.2839 | 0.028521 | -121.8476 | -0.45751 | -121.8683 | 0.057037 | 0.1648 | 0.15884 | -122.5926 | 122.1965 | -0.011951 | 122.2606 | 122.2282 | 0.031744 | 0.00955 | 0.16488 | -0.42459 | -0.061982 | 0.32039 | 0.29962 | 0.72422 | 0.045781 | 0.039826 | 122.275 | 122.2965 | 122.4519 | 122.206 | -0.090498 | 122.225 | 122.3328 | 122.3268 | 121.7105 | -122.7116
1719.0312 | 122.438 | -122.1497 | 0.086975 | 1.4211e-13 | 0.0012971 | -0.009295 | -0.027072 | -0.023789 | 0.0037841 | 0.011293 | -0.012575 | 0.027767 | 0.043089 | 0.00091673 | 0.047006 | 0.092615 | 0.047193 | 0.051108 | 0.11165 | 0.13773 | 0.28848 | 0.028521 | -121.8522 | -0.45293 | -121.8775 | 0.061616 | 0.16022 | 0.15884 | -122.5971 | 122.1782 | 0.024672 | 122.2423 | 122.2008 | 0.022587 | 0.050752 | 0.20151 | -0.44748 | -0.025359 | 0.2975 | 0.27215 | 0.71964 | 0.073247 | 0.07187 | 122.2613 | 122.2874 | 122.4381 | 122.1969 | -0.058454 | 122.2113 | 122.3099 | 122.3085 | 121.6967 | -122.6841
1720.8125 | 122.3007 | -122.1725 | 0.10529 | 1.4211e-13 | 0.0015107 | -0.0097224 | -0.026644 | -0.023789 | 0.0037841 | 0.018923 | -0.012575 | 0.027553 | 0.043516 | 0.00091673 | 0.047219 | 0.088037 | 0.042614 | 0.051108 | 0.11165 | 0.13315 | 0.29764 | 0.037679 | -121.8522 | -0.45751 | -121.8821 | 0.061616 | 0.16022 | 0.15427 | -122.5926 | 122.2102 | 0.006361 | 122.2606 | 122.2237 | 0.013429 | 0.027862 | 0.19235 | -0.42002 | -0.04367 | 0.32039 | 0.29046 | 0.71048 | 0.054936 | 0.04898 | 122.2842 | 122.3057 | 122.4702 | 122.2152 | -0.067607 | 122.2342 | 122.3328 | 122.3268 | 121.715 | -122.6978
1722.5312 | 122.4609 | -122.1405 | 0.073242 | 1.4211e-13 | 0.0012971 | -0.0095086 | -0.02643 | -0.023576 | 0.0042113 | 0.0036627 | -0.012575 | 0.02734 | 0.043516 | 0.0011303 | 0.047647 | 0.092615 | 0.038035 | 0.060265 | 0.11165 | 0.13315 | 0.28848 | 0.042258 | -121.8522 | -0.45751 | -121.8821 | 0.061616 | 0.16022 | 0.14969 | -122.5971 | 122.1828 | 0.038405 | 122.2331 | 122.2008 | 0.018007 | 0.059906 | 0.21524 | -0.45664 | -0.011626 | 0.28834 | 0.25842 | 0.71506 | 0.08698 | 0.076445 | 122.2522 | 122.2737 | 122.429 | 122.1785 | -0.030984 | 122.2021 | 122.3007 | 122.2902 | 121.683 | -122.6704
1724.3125 | 122.2916 | -122.1909 | 0.091553 | 1.4211e-13 | 0.0019381 | -0.0097224 | -0.026858 | -0.023576 | 0.0039977 | 0.011293 | -0.012788 | 0.027767 | 0.043516 | 0.0011303 | 0.047433 | 0.092615 | 0.047193 | 0.04653 | 0.11165 | 0.13315 | 0.27932 | 0.023942 | -121.8567 | -0.48041 | -121.8775 | 0.061616 | 0.16022 | 0.15884 | -122.5971 | 122.2148 | 0.020094 | 122.2835 | 122.2374 | 0.022588 | 0.041595 | 0.18777 | -0.40629 | -0.029937 | 0.33412 | 0.31335 | 0.71964 | 0.068669 | 0.067292 | 122.3025 | 122.324 | 122.4702 | 122.238 | -0.067611 | 122.2525 | 122.3511 | 122.3497 | 121.7105 | -122.6887
1726.0312 | 122.3923 | -122.1588 | 0.09613 | 1.4211e-13 | 0.0017243 | -0.0097224 | -0.026644 | -0.023576 | 0.0039977 | 0.0036627 | -0.012361 | 0.027553 | 0.043516 | 0.0011303 | 0.047433 | 0.097194 | 0.038035 | 0.051108 | 0.11165 | 0.12857 | 0.2839 | 0.028521 | -121.8659 | -0.47125 | -121.8867 | 0.066194 | 0.16022 | 0.15427 | -122.6063 | 122.1873 | 0.015517 | 122.256 | 122.2099 | 0.022587 | 0.032439 | 0.18777 | -0.44749 | -0.029936 | 0.29292 | 0.27215 | 0.71964 | 0.064092 | 0.058136 | 122.2705 | 122.2874 | 122.4427 | 122.1968 | -0.067609 | 122.225 | 122.319 | 122.3131 | 121.6876 | -122.7024
1727.8125 | 122.3282 | -122.2137 | 0.10529 | 1.4211e-13 | 0.0019381 | -0.009936 | -0.026858 | -0.023362 | 0.0042113 | 0.011293 | -0.012788 | 0.027553 | 0.043729 | 0.0011303 | 0.047433 | 0.083459 | 0.038035 | 0.055687 | 0.11622 | 0.12857 | 0.28848 | 0.0331 | -121.8613 | -0.48041 | -121.8958 | 0.066194 | 0.16022 | 0.14969 | -122.6109 | 122.2468 | 0.010939 | 122.2972 | 122.2694 | 0.022587 | 0.023283 | 0.18319 | -0.39713 | -0.039092 | 0.35243 | 0.31793 | 0.71506 | 0.054936 | 0.044401 | 122.33 | 122.3423 | 122.5022 | 122.2518 | -0.072186 | 122.2799 | 122.374 | 122.3634 | 121.7333 | -122.7162
1729.5938 | 122.4472 | -122.1634 | 0.086975 | 1.4211e-13 | 0.0015107 | -0.0097224 | -0.02643 | -0.023576 | 0.0042113 | 0.011293 | -0.012575 | 0.027767 | 0.043516 | 0.00091673 | 0.047219 | 0.088037 | 0.042614 | 0.051108 | 0.11622 | 0.13315 | 0.27932 | 0.028521 | -121.8659 | -0.47583 | -121.8867 | 0.057037 | 0.15564 | 0.14969 | -122.6155 | 122.1919 | 0.02925 | 122.2514 | 122.2145 | 0.022587 | 0.046173 | 0.19235 | -0.45207 | -0.029938 | 0.2975 | 0.27673 | 0.72879 | 0.068668 | 0.062712 | 122.2796 | 122.2965 | 122.4427 | 122.206 | -0.058454 | 122.2204 | 122.319 | 122.3131 | 121.6876 | -122.7024
1731.375 | 122.3145 | -122.1909 | 0.11902 | 1.4211e-13 | 0.0015107 | -0.009936 | -0.026644 | -0.023362 | 0.0039977 | 0.0036627 | -0.012361 | 0.027553 | 0.043516 | 0.00070293 | 0.047433 | 0.092615 | 0.033457 | 0.041952 | 0.11165 | 0.12857 | 0.2839 | 0.028521 | -121.8613 | -0.48041 | -121.8912 | 0.057037 | 0.16022 | 0.15427 | -122.6109 | 122.2194 | -0.007372 | 122.2835 | 122.2328 | 0.013431 | 0.00955 | 0.16488 | -0.42002 | -0.061982 | 0.32954 | 0.29961 | 0.71964 | 0.041203 | 0.035247 | 122.3025 | 122.3194 | 122.4748 | 122.2243 | -0.090498 | 122.2479 | 122.3511 | 122.3451 | 121.7105 | -122.7299
1733.1094 | 122.374 | -122.2 | 0.10986 | 1.4211e-13 | 0.0015107 | -0.0097224 | -0.026644 | -0.023362 | 0.0037841 | 0.011293 | -0.012788 | 0.027767 | 0.043943 | 0.0011303 | 0.047006 | 0.092615 | 0.042614 | 0.051108 | 0.11622 | 0.13315 | 0.28848 | 0.028521 | -121.8751 | -0.48498 | -121.8958 | 0.061616 | 0.1648 | 0.15427 | -122.6063 | 122.2285 | 0.006362 | 122.2926 | 122.2511 | 0.022587 | 0.023285 | 0.17862 | -0.40629 | -0.048247 | 0.32496 | 0.30419 | 0.71048 | 0.054937 | 0.044403 | 122.3162 | 122.3332 | 122.4885 | 122.2426 | -0.081342 | 122.2616 | 122.3648 | 122.3543 | 121.715 | -122.7162
1734.8906 | 122.3236 | -122.168 | 0.091553 | 1.4211e-13 | 0.0012971 | -0.0095086 | -0.026858 | -0.023789 | 0.0042113 | -0.0039678 | -0.012361 | 0.02734 | 0.043089 | 0.0011303 | 0.047433 | 0.092615 | 0.038035 | 0.060265 | 0.1208 | 0.13773 | 0.29306 | 0.023942 | -121.8751 | -0.48041 | -121.9004 | 0.070773 | 0.1648 | 0.14969 | -122.62 | 122.1919 | 0.029251 | 122.2606 | 122.2282 | 0.036323 | 0.046174 | 0.20151 | -0.45207 | -0.02078 | 0.29292 | 0.26757 | 0.71964 | 0.073247 | 0.058134 | 122.2888 | 122.3057 | 122.461 | 122.206 | -0.067611 | 122.2387 | 122.3328 | 122.3177 | 121.6876 | -122.7116
1736.6719 | 122.3053 | -122.2046 | 0.11902 | 1.4211e-13 | 0.0017243 | -0.0097224 | -0.026858 | -0.023789 | 0.0042113 | -0.0039678 | -0.012788 | 0.02734 | 0.043516 | 0.00070293 | 0.047647 | 0.097194 | 0.042614 | 0.055687 | 0.11622 | 0.13315 | 0.28848 | 0.028521 | -121.8751 | -0.48956 | -121.8958 | 0.066194 | 0.16022 | 0.15427 | -122.6155 | 122.2331 | -0.002794 | 122.3018 | 122.2603 | 0.027166 | 0.014129 | 0.16946 | -0.41087 | -0.052825 | 0.32954 | 0.30877 | 0.71964 | 0.041203 | 0.035247 | 122.3208 | 122.3377 | 122.4931 | 122.2472 | -0.090498 | 122.2708 | 122.3648 | 122.3589 | 121.715 | -122.7345
1738.4531 | 122.4243 | -122.1634 | 0.054932 | 1.4211e-13 | 0.0017243 | -0.0095086 | -0.027072 | -0.023789 | 0.0042113 | 0.011293 | -0.012361 | 0.027767 | 0.043302 | 0.00091673 | 0.047647 | 0.092615 | 0.038035 | 0.051108 | 0.10707 | 0.12857 | 0.28848 | 0.028521 | -121.8751 | -0.49414 | -121.9004 | 0.052459 | 0.15564 | 0.14511 | -122.62 | 122.1919 | 0.052136 | 122.256 | 122.2145 | 0.022587 | 0.073637 | 0.23355 | -0.45664 | -0.002473 | 0.28834 | 0.26299 | 0.71964 | 0.10071 | 0.090177 | 122.2705 | 122.292 | 122.4519 | 122.2014 | -0.026411 | 122.2159 | 122.319 | 122.3085 | 121.6692 | -122.675
1740.2188 | 122.4106 | -122.1817 | 0.091553 | 1.4211e-13 | 0.0015107 | -0.0095086 | -0.026644 | -0.023789 | 0.0039977 | 0.0036627 | -0.013002 | 0.02734 | 0.043516 | 0.0011303 | 0.047219 | 0.092615 | 0.033457 | 0.051108 | 0.10249 | 0.13315 | 0.28848 | 0.028521 | -121.8751 | -0.49872 | -121.905 | 0.066194 | 0.15564 | 0.14969 | -122.6246 | 122.2102 | 0.010937 | 122.2743 | 122.2328 | 0.022587 | 0.041595 | 0.19693 | -0.44291 | -0.025359 | 0.30665 | 0.27672 | 0.71964 | 0.06409 | 0.058134 | 122.2842 | 122.3149 | 122.4702 | 122.2152 | -0.063032 | 122.2479 | 122.3373 | 122.3314 | 121.683 | -122.7162
1742 | 122.3282 | -122.2137 | 0.10986 | 1.4211e-13 | 0.0017243 | -0.0097224 | -0.027072 | -0.023576 | 0.0042113 | -0.0039678 | -0.012575 | 0.027553 | 0.043516 | 0.00091673 | 0.047647 | 0.097194 | 0.038035 | 0.051108 | 0.11165 | 0.13315 | 0.29306 | 0.028521 | -121.8842 | -0.49414 | -121.9004 | 0.057037 | 0.15564 | 0.14511 | -122.6292 | 122.2423 | 0.001784 | 122.3109 | 122.2649 | 0.022587 | 0.023285 | 0.1832 | -0.41545 | -0.052826 | 0.32954 | 0.31335 | 0.72879 | 0.04578 | 0.035246 | 122.3254 | 122.3469 | 122.5068 | 122.2518 | -0.081342 | 122.2708 | 122.3694 | 122.3589 | 121.7196 | -122.7391
1743.7188 | 122.4426 | -122.1451 | 0.086975 | 1.4211e-13 | 0.0017243 | -0.0097224 | -0.026644 | -0.023789 | 0.0039977 | 0.011293 | -0.012361 | 0.027126 | 0.043302 | 0.00091673 | 0.047006 | 0.092615 | 0.033457 | 0.051108 | 0.11165 | 0.13315 | 0.2839 | 0.023942 | -121.8842 | -0.50788 | -121.905 | 0.061616 | 0.15564 | 0.14511 | -122.6338 | 122.169 | 0.024672 | 122.2377 | 122.1962 | 0.027166 | 0.046173 | 0.19693 | -0.48869 | -0.025359 | 0.26087 | 0.2401 | 0.72879 | 0.068668 | 0.058134 | 122.2567 | 122.2782 | 122.429 | 122.1785 | -0.063033 | 122.2067 | 122.3007 | 122.2902 | 121.6372 | -122.7207
1745.5156 | 122.4106 | -122.1954 | 0.068665 | 1.4211e-13 | 0.0017243 | -0.009936 | -0.026644 | -0.023362 | 0.0037841 | -0.0039678 | -0.012361 | 0.027553 | 0.043302 | 0.0011303 | 0.047433 | 0.088037 | 0.033457 | 0.04653 | 0.10249 | 0.13315 | 0.27932 | 0.028521 | -121.8796 | -0.50788 | -121.905 | 0.057037 | 0.16022 | 0.14969 | -122.6292 | 122.224 | 0.033825 | 122.2835 | 122.242 | 0.018009 | 0.064483 | 0.21066 | -0.43376 | -0.011628 | 0.3158 | 0.29046 | 0.72422 | 0.091557 | 0.081022 | 122.2979 | 122.3286 | 122.4748 | 122.2289 | -0.040144 | 122.2525 | 122.3557 | 122.3451 | 121.6876 | -122.6979
1747.2344 | 122.3831 | -122.2137 | 0.10071 | 1.4211e-13 | 0.0015107 | -0.009295 | -0.026858 | -0.023362 | 0.0042113 | 0.011293 | -0.012575 | 0.027553 | 0.043516 | 0.0011303 | 0.047433 | 0.092615 | 0.038035 | 0.04653 | 0.11165 | 0.13315 | 0.28848 | 0.0331 | -121.8842 | -0.51246 | -121.905 | 0.066194 | 0.16938 | 0.14969 | -122.6292 | 122.2468 | 0.010939 | 122.3064 | 122.2603 | 0.01343 | 0.03244 | 0.18777 | -0.41545 | -0.034514 | 0.32954 | 0.30877 | 0.72422 | 0.068671 | 0.048979 | 122.3254 | 122.3469 | 122.5022 | 122.2518 | -0.067608 | 122.2799 | 122.3831 | 122.3634 | 121.7013 | -122.7299
1749.0156 | 122.3923 | -122.2092 | 0.09613 | 1.4211e-13 | 0.0019381 | -0.0097224 | -0.026858 | -0.023576 | 0.0044249 | 0.011293 | -0.012575 | 0.027553 | 0.043302 | 0.0011303 | 0.047433 | 0.083459 | 0.042614 | 0.060265 | 0.11165 | 0.12857 | 0.28848 | 0.028521 | -121.8796 | -0.52619 | -121.9096 | 0.057037 | 0.1648 | 0.15427 | -122.6292 | 122.2377 | 0.015517 | 122.2926 | 122.2694 | 0.031744 | 0.032439 | 0.19235 | -0.42003 | -0.039093 | 0.32954 | 0.29961 | 0.71964 | 0.06867 | 0.058136 | 122.3208 | 122.3377 | 122.4976 | 122.2518 | -0.067609 | 122.2662 | 122.374 | 122.3634 | 121.683 | -122.7253
1750.7188 | 122.438 | -122.1588 | 0.07782 | 1.4211e-13 | 0.0015107 | -0.0095086 | -0.026644 | -0.023789 | 0.0042113 | 0.0036627 | -0.012575 | 0.02734 | 0.043302 | 0.0011303 | 0.047433 | 0.088037 | 0.033457 | 0.055687 | 0.10707 | 0.13315 | 0.28848 | 0.028521 | -121.8888 | -0.52161 | -121.9096 | 0.061616 | 0.1648 | 0.15884 | -122.6384 | 122.1873 | 0.029248 | 122.2468 | 122.2145 | 0.027166 | 0.055328 | 0.21066 | -0.47954 | -0.016204 | 0.27003 | 0.24926 | 0.7288 | 0.08698 | 0.081025 | 122.2659 | 122.292 | 122.4473 | 122.1923 | -0.049299 | 122.2204 | 122.3236 | 122.3177 | 121.6372 | -122.7162
1752.5 | 122.438 | -122.1817 | 0.07782 | 1.4211e-13 | 0.0015107 | -0.0095086 | -0.027072 | -0.023789 | 0.0039977 | 0.018923 | -0.012361 | 0.027767 | 0.043302 | 0.00091673 | 0.047433 | 0.088037 | 0.042614 | 0.051108 | 0.11622 | 0.13315 | 0.29306 | 0.0331 | -121.8888 | -0.52619 | -121.9096 | 0.061616 | 0.16022 | 0.15427 | -122.6384 | 122.2148 | 0.038405 | 122.2697 | 122.2328 | 0.018008 | 0.055328 | 0.21524 | -0.45665 | -0.016204 | 0.29292 | 0.27215 | 0.7288 | 0.082402 | 0.076446 | 122.2979 | 122.3149 | 122.4748 | 122.2243 | -0.04472 | 122.2433 | 122.3419 | 122.336 | 121.6555 | -122.7162
1754.2812 | 122.3511 | -122.2183 | 0.11902 | 1.4211e-13 | 0.0021517 | -0.009295 | -0.026858 | -0.023789 | 0.0035703 | 0.011293 | -0.012575 | 0.027553 | 0.043516 | 0.00091673 | 0.047433 | 0.092615 | 0.028878 | 0.04653 | 0.11622 | 0.14231 | 0.2839 | 0.028521 | -121.8888 | -0.52619 | -121.9141 | 0.061616 | 0.16022 | 0.15427 | -122.6384 | 122.2468 | -0.002794 | 122.3109 | 122.2649 | 0.018009 | 0.023287 | 0.16488 | -0.42003 | -0.057403 | 0.32954 | 0.30419 | 0.72422 | 0.041203 | 0.035247 | 122.3345 | 122.3606 | 122.5022 | 122.2472 | -0.090498 | 122.2799 | 122.3785 | 122.3726 | 121.6921 | -122.7574
1756 | 122.3557 | -122.2137 | 0.10986 | 1.4211e-13 | 0.0015107 | -0.0097224 | -0.026858 | -0.023362 | 0.0037841 | 0.0036627 | -0.012361 | 0.027553 | 0.043516 | 0.00091673 | 0.047219 | 0.092615 | 0.038035 | 0.051108 | 0.11622 | 0.13773 | 0.2839 | 0.023942 | -121.8979 | -0.53993 | -121.9187 | 0.061616 | 0.15564 | 0.15427 | -122.6429 | 122.2377 | 0.006362 | 122.3064 | 122.2649 | 0.027166 | 0.027864 | 0.17404 | -0.42919 | -0.048247 | 0.3158 | 0.29503 | 0.72422 | 0.04578 | 0.044403 | 122.33 | 122.3515 | 122.4976 | 122.2518 | -0.085921 | 122.2754 | 122.3694 | 122.368 | 121.6738 | -122.7528
1757.7656 | 122.3831 | -122.2412 | 0.10529 | 1.4211e-13 | 0.0015107 | -0.0097224 | -0.027285 | -0.023789 | 0.0039977 | 0.011293 | -0.012361 | 0.02734 | 0.043516 | 0.0011303 | 0.047006 | 0.088037 | 0.028878 | 0.04653 | 0.10707 | 0.12857 | 0.28848 | 0.028521 | -121.8888 | -0.54909 | -121.9233 | 0.061616 | 0.1648 | 0.15427 | -122.6429 | 122.2697 | 0.001782 | 122.3292 | 122.2877 | 0.018009 | 0.023283 | 0.18319 | -0.40172 | -0.04367 | 0.35242 | 0.31792 | 0.71964 | 0.059514 | 0.04898 | 122.3483 | 122.3698 | 122.5297 | 122.2701 | -0.076765 | 122.3028 | 122.406 | 122.3955 | 121.6921 | -122.7482
1759.5469 | 122.4792 | -122.1771 | 0.068665 | 1.4211e-13 | 0.0015107 | -0.0095086 | -0.02643 | -0.023789 | 0.0042113 | 0.011293 | -0.012788 | 0.02734 | 0.043729 | 0.0011303 | 0.047433 | 0.083459 | 0.038035 | 0.041952 | 0.10707 | 0.13315 | 0.28848 | 0.023942 | -121.8979 | -0.55366 | -121.9233 | 0.052459 | 0.16022 | 0.14969 | -122.6521 | 122.2011 | 0.038403 | 122.2606 | 122.2191 | 0.01801 | 0.064483 | 0.21982 | -0.47496 | -0.016206 | 0.27918 | 0.25383 | 0.7288 | 0.091557 | 0.081022 | 122.2842 | 122.3103 | 122.4656 | 122.2152 | -0.044723 | 122.2296 | 122.3373 | 122.3268 | 121.6235 | -122.7208
1761.3281 | 122.374 | -122.2321 | 0.10986 | 1.4211e-13 | 0.0017243 | -0.009936 | -0.026858 | -0.023789 | 0.0039977 | 0.011293 | -0.013002 | 0.02734 | 0.043516 | 0.00070293 | 0.047433 | 0.097194 | 0.033457 | 0.041952 | 0.10707 | 0.12857 | 0.2839 | 0.028521 | -121.8979 | -0.5674 | -121.9187 | 0.066194 | 0.16022 | 0.15884 | -122.6429 | 122.2606 | -0.002795 | 122.3293 | 122.274 | 0.013431 | 0.018706 | 0.17404 | -0.41087 | -0.043669 | 0.33411 | 0.31334 | 0.72422 | 0.050359 | 0.048982 | 122.3391 | 122.3606 | 122.516 | 122.2655 | -0.081342 | 122.2982 | 122.3923 | 122.3909 | 121.6647 | -122.7528
1763.0469 | 122.3602 | -122.2137 | 0.10529 | 1.4211e-13 | 0.0019381 | -0.0095086 | -0.026644 | -0.024003 | 0.0042113 | 0.011293 | -0.012788 | 0.027553 | 0.043729 | 0.00091673 | 0.047647 | 0.088037 | 0.033457 | 0.051108 | 0.10707 | 0.13315 | 0.28848 | 0.023942 | -121.9117 | -0.57656 | -121.9279 | 0.057037 | 0.16022 | 0.15427 | -122.6521 | 122.2377 | 0.001782 | 122.3018 | 122.2649 | 0.027166 | 0.027862 | 0.18319 | -0.43834 | -0.048249 | 0.30206 | 0.28587 | 0.72422 | 0.054936 | 0.04898 | 122.3208 | 122.3469 | 122.5022 | 122.2472 | -0.081344 | 122.2708 | 122.374 | 122.368 | 121.6372 | -122.7574
1764.8281 | 122.3831 | -122.2504 | 0.10071 | 1.4211e-13 | 0.0017243 | -0.009936 | -0.027072 | -0.023362 | 0.0039977 | 0.011293 | -0.012361 | 0.02734 | 0.043729 | 0.00070293 | 0.047433 | 0.092615 | 0.038035 | 0.055687 | 0.10249 | 0.13773 | 0.2839 | 0.023942 | -121.9025 | -0.59487 | -121.9187 | 0.057037 | 0.16022 | 0.15427 | -122.6567 | 122.2743 | 0.001782 | 122.343 | 122.3061 | 0.031745 | 0.037019 | 0.18319 | -0.4063 | -0.043671 | 0.34784 | 0.33165 | 0.73795 | 0.059514 | 0.053558 | 122.3529 | 122.3881 | 122.5343 | 122.2884 | -0.076766 | 122.3074 | 122.4106 | 122.4046 | 121.6555 | -122.7574
1766.6094 | 122.4106 | -122.2183 | 0.10529 | 1.4211e-13 | 0.0010833 | -0.0097224 | -0.026644 | -0.023576 | 0.0039977 | 0.011293 | -0.012575 | 0.027553 | 0.043943 | 0.00070293 | 0.047433 | 0.083459 | 0.038035 | 0.051108 | 0.11165 | 0.13315 | 0.2839 | 0.0331 | -121.9117 | -0.60861 | -121.9279 | 0.057037 | 0.15107 | 0.15427 | -122.6567 | 122.2514 | 0.006361 | 122.3018 | 122.2694 | 0.018008 | 0.027862 | 0.17862 | -0.43834 | -0.048249 | 0.30664 | 0.29045 | 0.7288 | 0.045779 | 0.04898 | 122.33 | 122.3515 | 122.5022 | 122.2564 | -0.072186 | 122.2754 | 122.3694 | 122.3726 | 121.6097 | -122.762
1768.3906 | 122.4838 | -122.1725 | 0.082397 | 1.4211e-13 | 0.0015107 | -0.0095086 | -0.026858 | -0.023576 | 0.0042113 | 0.011293 | -0.012575 | 0.027767 | 0.043302 | 0.00091673 | 0.047433 | 0.092615 | 0.033457 | 0.051108 | 0.11622 | 0.12399 | 0.27932 | 0.0331 | -121.9071 | -0.62692 | -121.9279 | 0.061616 | 0.15564 | 0.14969 | -122.6612 | 122.2056 | 0.033828 | 122.2652 | 122.2237 | 0.018008 | 0.041593 | 0.19693 | -0.4887 | -0.020781 | 0.26544 | 0.24468 | 0.73337 | 0.073246 | 0.06729 | 122.2888 | 122.2965 | 122.4519 | 122.206 | -0.049297 | 122.2342 | 122.3282 | 122.3222 | 121.5456 | -122.7436
1770.1094 | 122.4838 | -122.2229 | 0.09613 | 1.4211e-13 | 0.0015107 | -0.0097224 | -0.026644 | -0.024003 | 0.0039977 | -0.0039678 | -0.012788 | 0.027981 | 0.043516 | 0.00091673 | 0.047433 | 0.07888 | 0.033457 | 0.04653 | 0.11165 | 0.13773 | 0.27932 | 0.0331 | -121.9117 | -0.64524 | -121.9325 | 0.057037 | 0.1648 | 0.15427 | -122.6612 | 122.256 | 0.015517 | 122.3018 | 122.2694 | 0.01343 | 0.041597 | 0.18319 | -0.43834 | -0.039093 | 0.31122 | 0.29045 | 0.72879 | 0.06867 | 0.058136 | 122.3345 | 122.3606 | 122.5022 | 122.2564 | -0.06303 | 122.2799 | 122.3877 | 122.3772 | 121.5777 | -122.7574
1771.875 | 122.4655 | -122.2 | 0.086975 | 1.4211e-13 | 0.0017243 | -0.0097224 | -0.026858 | -0.023576 | 0.0039977 | 0.011293 | -0.012575 | 0.02734 | 0.043516 | 0.0011303 | 0.047219 | 0.07888 | 0.038035 | 0.055687 | 0.10707 | 0.13315 | 0.28848 | 0.0331 | -121.9071 | -0.66813 | -121.937 | 0.057037 | 0.16022 | 0.14969 | -122.6612 | 122.2331 | 0.020093 | 122.2789 | 122.2557 | 0.022587 | 0.046173 | 0.20151 | -0.46123 | -0.029938 | 0.29291 | 0.26298 | 0.72422 | 0.073247 | 0.062712 | 122.3071 | 122.3332 | 122.4885 | 122.238 | -0.053875 | 122.257 | 122.3602 | 122.3497 | 121.5319 | -122.7482
1773.5938 | 122.493 | -122.2092 | 0.082397 | 1.4211e-13 | 0.0017243 | -0.0097224 | -0.026858 | -0.023789 | 0.0037841 | 0.011293 | -0.012788 | 0.027553 | 0.043729 | 0.0011303 | 0.047647 | 0.097194 | 0.038035 | 0.051108 | 0.10707 | 0.13315 | 0.2839 | 0.023942 | -121.9117 | -0.68187 | -121.9416 | 0.061616 | 0.15564 | 0.15427 | -122.6658 | 122.2331 | 0.024671 | 122.3064 | 122.2603 | 0.027166 | 0.050751 | 0.20151 | -0.45666 | -0.020781 | 0.29749 | 0.26756 | 0.72422 | 0.073246 | 0.071869 | 122.3162 | 122.3423 | 122.4931 | 122.2472 | -0.058455 | 122.2708 | 122.3648 | 122.3634 | 121.5273 | -122.7482
1775.375 | 122.4884 | -122.1909 | 0.09613 | 1.4211e-13 | 0.0017243 | -0.009936 | -0.026858 | -0.023576 | 0.0039977 | 0.011293 | -0.012788 | 0.027553 | 0.043516 | 0.0013439 | 0.047433 | 0.088037 | 0.038035 | 0.051108 | 0.11165 | 0.13315 | 0.2839 | 0.028521 | -121.9117 | -0.7185 | -121.9416 | 0.061616 | 0.15564 | 0.15884 | -122.6658 | 122.2194 | 0.015517 | 122.2789 | 122.242 | 0.022587 | 0.037018 | 0.18777 | -0.47497 | -0.034514 | 0.27918 | 0.24925 | 0.72422 | 0.059513 | 0.062715 | 122.3025 | 122.324 | 122.4748 | 122.2289 | -0.067609 | 122.2525 | 122.3465 | 122.3497 | 121.4724 | -122.762
1777.1562 | 122.4335 | -122.2229 | 0.091553 | 1.4211e-13 | 0.0015107 | -0.0097224 | -0.026644 | -0.023576 | 0.0039977 | 0.018923 | -0.012575 | 0.027767 | 0.043516 | 0.00091673 | 0.047219 | 0.092615 | 0.042614 | 0.051108 | 0.10707 | 0.12857 | 0.2839 | 0.0331 | -121.9117 | -0.73223 | -121.9325 | 0.057037 | 0.16938 | 0.14053 | -122.6704 | 122.256 | 0.015515 | 122.3155 | 122.274 | 0.018008 | 0.037016 | 0.19235 | -0.4475 | -0.034516 | 0.31122 | 0.29045 | 0.73795 | 0.077826 | 0.048977 | 122.33 | 122.3515 | 122.5068 | 122.2655 | -0.058453 | 122.2799 | 122.3923 | 122.3634 | 121.4907 | -122.762
1778.875 | 122.3602 | -122.2366 | 0.12817 | 1.4211e-13 | 0.0015107 | -0.009936 | -0.02643 | -0.023362 | 0.0042113 | 0.0036627 | -0.012361 | 0.027767 | 0.043729 | 0.00070293 | 0.047433 | 0.10177 | 0.038035 | 0.055687 | 0.11165 | 0.13773 | 0.29306 | 0.028521 | -121.9163 | -0.75055 | -121.9462 | 0.061616 | 0.1648 | 0.15427 | -122.6704 | 122.2652 | -0.016527 | 122.3384 | 122.2923 | 0.027166 | 0.009553 | 0.16489 | -0.43377 | -0.066558 | 0.32037 | 0.29045 | 0.72422 | 0.036626 | 0.026092 | 122.3483 | 122.3744 | 122.5297 | 122.2747 | -0.099653 | 122.2982 | 122.4014 | 122.3909 | 121.4861 | -122.7986
1780.6406 | 122.4655 | -122.2321 | 0.091553 | 1.4211e-13 | 0.0017243 | -0.009936 | -0.026858 | -0.023789 | 0.0039977 | 0.011293 | -0.012575 | 0.027981 | 0.043516 | 0.00091673 | 0.047219 | 0.097194 | 0.038035 | 0.051108 | 0.11165 | 0.13315 | 0.2839 | 0.028521 | -121.9208 | -0.77802 | -121.9462 | 0.057037 | 0.16022 | 0.15427 | -122.6658 | 122.2606 | 0.020094 | 122.3293 | 122.2832 | 0.022587 | 0.041595 | 0.19235 | -0.43377 | -0.034516 | 0.31122 | 0.28587 | 0.71964 | 0.068669 | 0.062713 | 122.3437 | 122.3652 | 122.516 | 122.2701 | -0.063032 | 122.2891 | 122.3923 | 122.3863 | 121.454 | -122.7574
1782.4062 | 122.5113 | -122.2 | 0.07782 | 1.4211e-13 | 0.0017243 | -0.0097224 | -0.026644 | -0.023576 | 0.0039977 | 0.011293 | -0.012575 | 0.027553 | 0.044157 | 0.0011303 | 0.047647 | 0.10177 | 0.038035 | 0.051108 | 0.11165 | 0.12857 | 0.28848 | 0.028521 | -121.9254 | -0.81465 | -121.9462 | 0.061616 | 0.15564 | 0.14969 | -122.675 | 122.2285 | 0.033827 | 122.3018 | 122.2511 | 0.022587 | 0.050749 | 0.21066 | -0.47497 | -0.016204 | 0.2746 | 0.25383 | 0.7288 | 0.077823 | 0.071867 | 122.3117 | 122.3286 | 122.4885 | 122.238 | -0.049299 | 122.2616 | 122.3557 | 122.3497 | 121.3854 | -122.7528
1784.1406 | 122.3648 | -122.2641 | 0.1236 | 1.4211e-13 | 0.0017243 | -0.0097224 | -0.026644 | -0.023362 | 0.0039977 | 0.0036627 | -0.012788 | 0.027767 | 0.043516 | 0.0011303 | 0.047219 | 0.10177 | 0.033457 | 0.055687 | 0.11165 | 0.13773 | 0.2839 | 0.028521 | -121.9208 | -0.8467 | -121.9462 | 0.057037 | 0.16022 | 0.15884 | -122.675 | 122.2926 | -0.011949 | 122.3659 | 122.3198 | 0.027166 | 0.014131 | 0.16031 | -0.41088 | -0.066559 | 0.34326 | 0.31791 | 0.7288 | 0.036626 | 0.035249 | 122.3757 | 122.4018 | 122.548 | 122.2976 | -0.095075 | 122.3211 | 122.4243 | 122.4229 | 121.4174 | -122.7986
1785.9062 | 122.3831 | -122.2549 | 0.10529 | 1.4211e-13 | 0.0019381 | -0.009295 | -0.026858 | -0.023576 | 0.0039977 | -0.0039678 | -0.012575 | 0.027553 | 0.043516 | 0.00070293 | 0.047433 | 0.092615 | 0.033457 | 0.04653 | 0.11165 | 0.13315 | 0.28848 | 0.028521 | -121.9163 | -0.90623 | -121.9508 | 0.061616 | 0.15107 | 0.15884 | -122.675 | 122.2835 | 0.006361 | 122.3476 | 122.3015 | 0.018009 | 0.027862 | 0.18319 | -0.42004 | -0.04367 | 0.33868 | 0.30418 | 0.72422 | 0.045779 | 0.053559 | 122.3666 | 122.3881 | 122.5434 | 122.2884 | -0.076765 | 122.3166 | 122.406 | 122.4138 | 121.3487 | -122.7803
1787.6094 | 122.4747 | -122.2183 | 0.082397 | 1.4211e-13 | 0.0015107 | -0.0097224 | -0.026858 | -0.023789 | 0.0037841 | 0.0036627 | -0.012575 | 0.027767 | 0.043516 | 0.0011303 | 0.047433 | 0.097194 | 0.038035 | 0.051108 | 0.10249 | 0.12857 | 0.28848 | 0.0331 | -121.9208 | -0.94743 | -121.9508 | 0.057037 | 0.1648 | 0.15427 | -122.6796 | 122.2514 | 0.020093 | 122.3155 | 122.2694 | 0.018008 | 0.046172 | 0.20608 | -0.46124 | -0.02536 | 0.29748 | 0.26756 | 0.72879 | 0.082403 | 0.071869 | 122.3208 | 122.3469 | 122.5068 | 122.2564 | -0.049297 | 122.2754 | 122.3831 | 122.3726 | 121.2709 | -122.762
1789.3906 | 122.3694 | -122.2824 | 0.09613 | 1.4211e-13 | 0.0017243 | -0.0095086 | -0.026858 | -0.023576 | 0.0037841 | 0.011293 | -0.012788 | 0.027553 | 0.043943 | 0.00091673 | 0.047219 | 0.092615 | 0.033457 | 0.051108 | 0.11165 | 0.12857 | 0.28848 | 0.028521 | -121.9208 | -0.97491 | -121.9462 | 0.061616 | 0.15564 | 0.15427 | -122.6887 | 122.3109 | 0.015517 | 122.375 | 122.3335 | 0.022587 | 0.032439 | 0.19235 | -0.40631 | -0.034514 | 0.36157 | 0.33622 | 0.74253 | 0.059513 | 0.058136 | 122.3941 | 122.411 | 122.5709 | 122.3159 | -0.067609 | 122.344 | 122.4381 | 122.4367 | 121.3075 | -122.7848
1791.1094 | 122.4243 | -122.2641 | 0.086975 | 1.4211e-13 | 0.0017243 | -0.0097224 | -0.026858 | -0.023789 | 0.0037841 | 0.011293 | -0.012788 | 0.027767 | 0.043516 | 0.00070293 | 0.047433 | 0.092615 | 0.042614 | 0.055687 | 0.11165 | 0.13315 | 0.28848 | 0.028521 | -121.93 | -1.0207 | -121.9508 | 0.061616 | 0.15564 | 0.15427 | -122.6796 | 122.2926 | 0.024672 | 122.3567 | 122.3198 | 0.027166 | 0.046173 | 0.20151 | -0.41546 | -0.025359 | 0.3341 | 0.31333 | 0.72879 | 0.068668 | 0.067291 | 122.3757 | 122.3972 | 122.5526 | 122.3067 | -0.058454 | 122.3257 | 122.4197 | 122.4184 | 121.2434 | -122.7665
1792.875 | 122.4197 | -122.2504 | 0.10986 | 1.4211e-13 | 0.0021517 | -0.0095086 | -0.026644 | -0.023362 | 0.0039977 | 0.0036627 | -0.012788 | 0.02734 | 0.043729 | 0.0011303 | 0.047647 | 0.088037 | 0.033457 | 0.051108 | 0.10707 | 0.13315 | 0.2839 | 0.019363 | -121.9208 | -1.0711 | -121.9553 | 0.057037 | 0.16022 | 0.15884 | -122.6841 | 122.2697 | -0.002795 | 122.3384 | 122.3015 | 0.031745 | 0.023285 | 0.17404 | -0.43377 | -0.052826 | 0.32953 | 0.29502 | 0.7288 | 0.050359 | 0.048982 | 122.3574 | 122.3835 | 122.5343 | 122.2838 | -0.0905 | 122.3074 | 122.4106 | 122.4092 | 121.1793 | -122.794
1794.6562 | 122.406 | -122.2595 | 0.10529 | 1.4211e-13 | 0.0017243 | -0.009936 | -0.02643 | -0.023789 | 0.0039977 | 0.0036627 | -0.012575 | 0.027981 | 0.043943 | 0.00091673 | 0.04786 | 0.097194 | 0.038035 | 0.041952 | 0.11622 | 0.13315 | 0.2839 | 0.023942 | -121.9254 | -1.126 | -121.9508 | 0.057037 | 0.15564 | 0.14969 | -122.6887 | 122.2835 | 0.010939 | 122.3567 | 122.3015 | 0.01801 | 0.027862 | 0.17862 | -0.4292 | -0.048249 | 0.3341 | 0.30876 | 0.73795 | 0.050357 | 0.044401 | 122.3757 | 122.3927 | 122.5434 | 122.2976 | -0.081344 | 122.3166 | 122.4152 | 122.4092 | 121.1335 | -122.794
1796.4375 | 122.3877 | -122.2687 | 0.10986 | 1.4211e-13 | 0.0019381 | -0.0095086 | -0.026644 | -0.023576 | 0.0042113 | -0.0039678 | -0.012788 | 0.027767 | 0.043302 | 0.0011303 | 0.047647 | 0.092615 | 0.033457 | 0.051108 | 0.11165 | 0.13773 | 0.28848 | 0.028521 | -121.9254 | -1.1947 | -121.9508 | 0.057037 | 0.15564 | 0.15427 | -122.6887 | 122.2972 | 0.001784 | 122.3613 | 122.3198 | 0.022587 | 0.027864 | 0.17862 | -0.42004 | -0.052826 | 0.34326 | 0.31791 | 0.73795 | 0.04578 | 0.044403 | 122.3803 | 122.4064 | 122.5572 | 122.3021 | -0.081342 | 122.3257 | 122.4243 | 122.4229 | 121.074 | -122.7986
1798.2188 | 122.4701 | -122.2549 | 0.082397 | 1.4211e-13 | 0.0019381 | -0.0097224 | -0.026644 | -0.023576 | 0.0042113 | 0.011293 | -0.012788 | 0.027553 | 0.043729 | 0.00091673 | 0.047647 | 0.092615 | 0.038035 | 0.051108 | 0.10249 | 0.12399 | 0.2839 | 0.028521 | -121.9254 | -1.2496 | -121.9508 | 0.057037 | 0.16022 | 0.14969 | -122.6933 | 122.2835 | 0.020093 | 122.3476 | 122.3061 | 0.022587 | 0.041593 | 0.20151 | -0.43835 | -0.02536 | 0.32953 | 0.30418 | 0.74253 | 0.077825 | 0.06729 | 122.3574 | 122.3789 | 122.5388 | 122.293 | -0.053876 | 122.312 | 122.4152 | 122.4046 | 121.0053 | -122.7757
1800 | 122.374 | -122.2549 | 0.10529 | 1.4211e-13 | 0.0017243 | -0.0095086 | -0.026644 | -0.023789 | 0.0039977 | 0.011293 | -0.012361 | 0.027767 | 0.043729 | 0.00091673 | 0.047647 | 0.097194 | 0.038035 | 0.051108 | 0.10707 | 0.13315 | 0.2839 | 0.023942 | -121.93 | -1.3458 | -121.9508 | 0.057037 | 0.1648 | 0.14511 | -122.6933 | 122.2789 | 0.001782 | 122.3521 | 122.3061 | 0.027166 | 0.027862 | 0.17862 | -0.43835 | -0.048249 | 0.32495 | 0.30418 | 0.74253 | 0.059514 | 0.039823 | 122.362 | 122.3881 | 122.5388 | 122.293 | -0.081344 | 122.312 | 122.4197 | 122.4001 | 120.9092 | -122.7986
1801.7656 | 122.3969 | -122.2687 | 0.10071 | 1.4211e-13 | 0.0015107 | -0.009936 | -0.02643 | -0.023576 | 0.0037841 | 0.011293 | -0.012575 | 0.027553 | 0.043302 | 0.00091673 | 0.047647 | 0.092615 | 0.033457 | 0.04653 | 0.11622 | 0.12857 | 0.28848 | 0.028521 | -121.93 | -1.4099 | -121.9553 | 0.061616 | 0.16022 | 0.14969 | -122.6933 | 122.2972 | 0.015517 | 122.3613 | 122.3152 | 0.018009 | 0.027861 | 0.18777 | -0.42462 | -0.039092 | 0.33868 | 0.31333 | 0.73795 | 0.059514 | 0.048979 | 122.3849 | 122.3972 | 122.5572 | 122.3021 | -0.072187 | 122.3303 | 122.4289 | 122.4184 | 120.8588 | -122.794
1803.5469 | 122.406 | -122.2778 | 0.11902 | 1.4211e-13 | 0.0019381 | -0.0097224 | -0.026217 | -0.023789 | 0.0039977 | 0.0036627 | -0.012361 | 0.02734 | 0.043516 | 0.00091673 | 0.047647 | 0.097194 | 0.033457 | 0.055687 | 0.10707 | 0.12857 | 0.28848 | 0.023942 | -121.9254 | -1.4969 | -121.9508 | 0.061616 | 0.1648 | 0.15427 | -122.7025 | 122.3018 | -0.011951 | 122.375 | 122.3335 | 0.031745 | 0.00955 | 0.16946 | -0.42462 | -0.057403 | 0.35242 | 0.32707 | 0.75169 | 0.045781 | 0.035247 | 122.3849 | 122.4064 | 122.5663 | 122.3113 | -0.095077 | 122.3394 | 122.4426 | 122.4321 | 120.781 | -122.8215
1805.25 | 122.4884 | -122.2321 | 0.091553 | 1.4211e-13 | 0.0019381 | -0.0097224 | -0.02643 | -0.023362 | 0.0039977 | 0.018923 | -0.012788 | 0.027767 | 0.043516 | 0.00091673 | 0.047647 | 0.097194 | 0.038035 | 0.04653 | 0.10249 | 0.13315 | 0.2839 | 0.019363 | -121.93 | -1.5747 | -121.9645 | 0.057037 | 0.1648 | 0.15427 | -122.7025 | 122.2514 | 0.010937 | 122.3293 | 122.2786 | 0.027167 | 0.041595 | 0.19235 | -0.4704 | -0.034516 | 0.30206 | 0.26756 | 0.73795 | 0.073247 | 0.062713 | 122.3345 | 122.3652 | 122.516 | 122.2701 | -0.07219 | 122.2891 | 122.3969 | 122.3863 | 120.6573 | -122.794
1807.0312 | 122.4106 | -122.2778 | 0.12817 | 1.4211e-13 | 0.0019381 | -0.009295 | -0.026644 | -0.023362 | 0.0037841 | 0.011293 | -0.012361 | 0.027767 | 0.043729 | 0.00091673 | 0.047433 | 0.092615 | 0.033457 | 0.055687 | 0.10707 | 0.12857 | 0.2839 | 0.023942 | -121.93 | -1.6754 | -121.9599 | 0.057037 | 0.15564 | 0.14511 | -122.6933 | 122.3018 | -0.021106 | 122.3704 | 122.3335 | 0.031745 | 0.000395 | 0.15573 | -0.41546 | -0.071137 | 0.34784 | 0.31791 | 0.73337 | 0.027469 | 0.016935 | 122.3849 | 122.4064 | 122.5617 | 122.3113 | -0.10423 | 122.3349 | 122.4335 | 122.4229 | 120.6024 | -122.8215
1808.8125 | 122.3831 | -122.2778 | 0.091553 | 1.4211e-13 | 0.0019381 | -0.009936 | -0.026644 | -0.023576 | 0.0042113 | 0.0036627 | -0.012575 | 0.027767 | 0.043516 | 0.00091673 | 0.047219 | 0.092615 | 0.028878 | 0.055687 | 0.11165 | 0.13315 | 0.29306 | 0.028521 | -121.93 | -1.7533 | -121.9599 | 0.052459 | 0.15564 | 0.14511 | -122.707 | 122.3064 | 0.020094 | 122.3704 | 122.3335 | 0.027166 | 0.041595 | 0.20151 | -0.4292 | -0.039094 | 0.34784 | 0.31791 | 0.74711 | 0.06409 | 0.053556 | 122.3895 | 122.411 | 122.5709 | 122.3067 | -0.063032 | 122.3303 | 122.4335 | 122.4229 | 120.5245 | -122.7986
1810.5312 | 122.4289 | -122.287 | 0.1236 | 1.4211e-13 | 0.0021517 | -0.009936 | -0.026644 | -0.023789 | 0.0039977 | 0.018923 | -0.012575 | 0.027553 | 0.043729 | 0.00070293 | 0.047433 | 0.10177 | 0.033457 | 0.04653 | 0.10707 | 0.11941 | 0.27932 | 0.023942 | -121.9254 | -1.8265 | -121.9599 | 0.052459 | 0.15564 | 0.14969 | -122.707 | 122.3109 | -0.016528 | 122.3888 | 122.3335 | 0.022588 | -0.004185 | 0.15573 | -0.42005 | -0.071137 | 0.36157 | 0.32706 | 0.74711 | 0.032047 | 0.026091 | 122.3941 | 122.4064 | 122.5663 | 122.3204 | -0.099654 | 122.3394 | 122.4426 | 122.4367 | 120.4604 | -122.8306
1812.3125 | 122.374 | -122.2916 | 0.10529 | 1.4211e-13 | 0.0019381 | -0.01015 | -0.026644 | -0.023789 | 0.0039977 | 0.0036627 | -0.012788 | 0.027553 | 0.043729 | 0.00070293 | 0.047219 | 0.097194 | 0.038035 | 0.051108 | 0.11165 | 0.12857 | 0.2839 | 0.028521 | -121.9346 | -1.9273 | -121.9691 | 0.057037 | 0.15564 | 0.15427 | -122.707 | 122.3201 | 0.006361 | 122.3888 | 122.3427 | 0.022587 | 0.023283 | 0.17862 | -0.41547 | -0.048249 | 0.35699 | 0.32249 | 0.73795 | 0.050357 | 0.04898 | 122.4032 | 122.4201 | 122.5755 | 122.3296 | -0.076765 | 122.3486 | 122.4472 | 122.4458 | 120.3643 | -122.8123
1814.0938 | 122.4014 | -122.3053 | 0.13275 | 1.4211e-13 | 0.0019381 | -0.0097224 | -0.026644 | -0.023789 | 0.0042113 | 0.011293 | -0.012361 | 0.027553 | 0.043516 | 0.0011303 | 0.047647 | 0.088037 | 0.038035 | 0.04653 | 0.10707 | 0.12857 | 0.2839 | 0.0331 | -121.9254 | -2.0463 | -121.9691 | 0.061616 | 0.16022 | 0.14053 | -122.7116 | 122.3384 | -0.025683 | 122.3933 | 122.3518 | 0.01343 | -0.004182 | 0.15115 | -0.40631 | -0.071135 | 0.37988 | 0.33622 | 0.74253 | 0.027471 | 0.007779 | 122.4124 | 122.4339 | 122.5892 | 122.3433 | -0.099651 | 122.3669 | 122.4655 | 122.4458 | 120.259 | -122.8444
1815.7969 | 122.4518 | -122.2687 | 0.10986 | 1.4211e-13 | 0.0019381 | -0.0097224 | -0.026644 | -0.023576 | 0.0035703 | 0.011293 | -0.012575 | 0.027767 | 0.043729 | 0.00091673 | 0.047647 | 0.10177 | 0.033457 | 0.051108 | 0.10707 | 0.12857 | 0.28848 | 0.028521 | -121.9163 | -2.1699 | -121.9645 | 0.057037 | 0.15564 | 0.14969 | -122.7162 | 122.2972 | -0.002795 | 122.3704 | 122.3198 | 0.022587 | 0.018706 | 0.17862 | -0.44751 | -0.052826 | 0.35242 | 0.30418 | 0.75169 | 0.04578 | 0.039824 | 122.3757 | 122.3972 | 122.5572 | 122.3021 | -0.081342 | 122.3257 | 122.4243 | 122.4184 | 120.0987 | -122.8261
1817.5781 | 122.4609 | -122.2641 | 0.10529 | 1.4211e-13 | 0.0019381 | -0.0097224 | -0.02643 | -0.023789 | 0.0039977 | 0.011293 | -0.012575 | 0.027553 | 0.043516 | 0.00091673 | 0.047647 | 0.092615 | 0.038035 | 0.041952 | 0.10249 | 0.13315 | 0.27932 | 0.0331 | -121.9208 | -2.321 | -121.9645 | 0.061616 | 0.15564 | 0.15884 | -122.7208 | 122.2972 | -0.002796 | 122.3567 | 122.3061 | 0.008852 | 0.027862 | 0.17404 | -0.45667 | -0.04367 | 0.34326 | 0.2996 | 0.75627 | 0.050357 | 0.053559 | 122.3666 | 122.3972 | 122.5434 | 122.3021 | -0.072186 | 122.3257 | 122.4197 | 122.4229 | 119.9431 | -122.8261
1819.3594 | 122.493 | -122.2412 | 0.09613 | 1.4211e-13 | 0.0021517 | -0.0097224 | -0.02643 | -0.023576 | 0.0044249 | 0.026554 | -0.012788 | 0.027767 | 0.043302 | 0.00091673 | 0.047433 | 0.097194 | 0.038035 | 0.04653 | 0.10707 | 0.12857 | 0.2839 | 0.028521 | -121.9254 | -2.4493 | -121.9691 | 0.066194 | 0.15564 | 0.14969 | -122.7162 | 122.2697 | 0.010938 | 122.3384 | 122.2877 | 0.018009 | 0.032439 | 0.18777 | -0.47498 | -0.029936 | 0.31579 | 0.27213 | 0.74711 | 0.059513 | 0.053557 | 122.3483 | 122.3698 | 122.5251 | 122.2792 | -0.067609 | 122.3074 | 122.3969 | 122.3909 | 119.792 | -122.8123
1821.1406 | 122.406 | -122.2961 | 0.13733 | 1.4211e-13 | 0.0021517 | -0.01015 | -0.026644 | -0.023789 | 0.0042113 | 0.011293 | -0.012361 | 0.027553 | 0.043729 | 0.00048933 | 0.047219 | 0.097194 | 0.033457 | 0.04653 | 0.11165 | 0.13315 | 0.28848 | 0.028521 | -121.93 | -2.6187 | -121.9737 | 0.052459 | 0.15564 | 0.15427 | -122.7162 | 122.3247 | -0.025682 | 122.3933 | 122.3427 | 0.018009 | -0.004181 | 0.15115 | -0.42005 | -0.08487 | 0.36615 | 0.32249 | 0.74253 | 0.018314 | 0.016937 | 122.4078 | 122.4293 | 122.5846 | 122.3296 | -0.10881 | 122.3486 | 122.4518 | 122.4504 | 119.6775 | -122.8535
1822.8594 | 122.5342 | -122.2778 | 0.068665 | 1.4211e-13 | 0.0019381 | -0.0097224 | -0.02643 | -0.023362 | 0.0039977 | -0.0039678 | -0.012575 | 0.02734 | 0.043943 | 0.00091673 | 0.047219 | 0.092615 | 0.038035 | 0.051108 | 0.11165 | 0.12857 | 0.28848 | 0.023942 | -121.9254 | -2.7881 | -121.9737 | 0.061616 | 0.15564 | 0.14511 | -122.7162 | 122.3018 | 0.042982 | 122.3704 | 122.3289 | 0.027166 | 0.059904 | 0.21982 | -0.43836 | -0.007049 | 0.35242 | 0.30417 | 0.74253 | 0.086978 | 0.076444 | 122.3895 | 122.4064 | 122.5663 | 122.3159 | -0.044723 | 122.3394 | 122.4335 | 122.4229 | 119.4898 | -122.7849
1824.6406 | 122.3831 | -122.2916 | 0.10986 | 1.4211e-13 | 0.0019381 | -0.0095086 | -0.026644 | -0.023576 | 0.0039977 | 0.0036627 | -0.012361 | 0.027767 | 0.043516 | 0.0011303 | 0.047433 | 0.097194 | 0.033457 | 0.051108 | 0.10707 | 0.11941 | 0.2839 | 0.023942 | -121.93 | -2.9666 | -121.9691 | 0.061616 | 0.16022 | 0.15427 | -122.7162 | 122.3155 | -0.002795 | 122.3888 | 122.3427 | 0.027166 | 0.009548 | 0.17404 | -0.42463 | -0.048247 | 0.36157 | 0.32249 | 0.74711 | 0.050359 | 0.044403 | 122.3986 | 122.411 | 122.5755 | 122.325 | -0.085921 | 122.3532 | 122.4518 | 122.4458 | 119.3249 | -122.8261
1826.4219 | 122.4197 | -122.287 | 0.10529 | 1.4211e-13 | 0.0017243 | -0.0097224 | -0.026858 | -0.023362 | 0.0039977 | 0.0036627 | -0.012575 | 0.027767 | 0.043516 | 0.0011303 | 0.04786 | 0.088037 | 0.047193 | 0.051108 | 0.10707 | 0.12857 | 0.2839 | 0.019363 | -121.9254 | -3.1452 | -121.9737 | 0.057037 | 0.15564 | 0.14969 | -122.7253 | 122.3063 | 0.001782 | 122.375 | 122.3381 | 0.031745 | 0.023283 | 0.17862 | -0.43836 | -0.048249 | 0.36157 | 0.31333 | 0.75169 | 0.050357 | 0.044401 | 122.3941 | 122.4156 | 122.5709 | 122.3342 | -0.085923 | 122.344 | 122.4426 | 122.4367 | 119.1418 | -122.8306
1828.2031 | 122.4243 | -122.2961 | 0.09613 | 1.4211e-13 | 0.0019381 | -0.0097224 | -0.026644 | -0.023576 | 0.0044249 | 0.0036627 | -0.012361 | 0.027553 | 0.043729 | 0.0011303 | 0.047647 | 0.088037 | 0.038035 | 0.051108 | 0.11165 | 0.12857 | 0.2839 | 0.028521 | -121.9208 | -3.3238 | -121.9645 | 0.057037 | 0.16022 | 0.14511 | -122.7208 | 122.3247 | 0.015517 | 122.3842 | 122.3473 | 0.022587 | 0.032439 | 0.18777 | -0.42463 | -0.039093 | 0.3753 | 0.33164 | 0.75627 | 0.064092 | 0.048979 | 122.4078 | 122.4247 | 122.58 | 122.3342 | -0.067609 | 122.3532 | 122.4564 | 122.4413 | 118.9724 | -122.8169
1830 | 122.4289 | -122.2961 | 0.11902 | 1.4211e-13 | 0.0019381 | -0.0095086 | -0.026644 | -0.023789 | 0.0039977 | 0.0036627 | -0.012575 | 0.027553 | 0.043729 | 0.00070293 | 0.047433 | 0.092615 | 0.038035 | 0.04653 | 0.10707 | 0.12857 | 0.27932 | 0.028521 | -121.9163 | -3.5344 | -121.9737 | 0.066194 | 0.15107 | 0.15427 | -122.7299 | 122.3247 | -0.011951 | 122.3888 | 122.3427 | 0.018009 | 0.00955 | 0.16031 | -0.43378 | -0.052825 | 0.37988 | 0.32249 | 0.75627 | 0.032046 | 0.035247 | 122.4032 | 122.4247 | 122.5755 | 122.3342 | -0.090498 | 122.3623 | 122.4472 | 122.4504 | 118.7617 | -122.8489
1831.7812 | 122.4609 | -122.2733 | 0.10529 | 1.4211e-13 | 0.0021517 | -0.009936 | -0.026644 | -0.023576 | 0.0044249 | -0.0039678 | -0.012788 | 0.02734 | 0.043302 | 0.00091673 | 0.04786 | 0.10177 | 0.033457 | 0.04653 | 0.11165 | 0.12399 | 0.28848 | 0.028521 | -121.9208 | -3.7176 | -121.9645 | 0.057037 | 0.16022 | 0.14511 | -122.7208 | 122.3018 | 0.006361 | 122.375 | 122.3198 | 0.018009 | 0.018704 | 0.18319 | -0.44752 | -0.048249 | 0.35242 | 0.30875 | 0.75627 | 0.054936 | 0.039823 | 122.3849 | 122.3972 | 122.5617 | 122.3067 | -0.076765 | 122.3303 | 122.4335 | 122.4184 | 118.5557 | -122.8261
1833.5625 | 122.5342 | -122.2321 | 0.068665 | 1.4211e-13 | 0.0021517 | -0.0097224 | -0.026858 | -0.023576 | 0.0042113 | 0.011293 | -0.012575 | 0.027553 | 0.043516 | 0.00091673 | 0.047219 | 0.097194 | 0.038035 | 0.04653 | 0.10707 | 0.13315 | 0.2839 | 0.037679 | -121.9254 | -3.9007 | -121.9691 | 0.057037 | 0.1648 | 0.15427 | -122.7253 | 122.2697 | 0.038403 | 122.3293 | 122.2786 | 0.008851 | 0.064483 | 0.21524 | -0.49329 | -0.011628 | 0.30664 | 0.26298 | 0.75627 | 0.096135 | 0.085601 | 122.3391 | 122.3652 | 122.516 | 122.2701 | -0.030986 | 122.2891 | 122.3969 | 122.3863 | 118.3314 | -122.794
1835.3438 | 122.4518 | -122.2824 | 0.10986 | 1.4211e-13 | 0.0021517 | -0.0097224 | -0.026644 | -0.023576 | 0.0039977 | 0.011293 | -0.013002 | 0.027767 | 0.043516 | 0.00070293 | 0.047647 | 0.092615 | 0.028878 | 0.051108 | 0.10249 | 0.12399 | 0.28848 | 0.028521 | -121.9208 | -4.1342 | -121.9737 | 0.052459 | 0.15564 | 0.14969 | -122.7345 | 122.3109 | -0.007373 | 122.375 | 122.3335 | 0.022587 | 0.014127 | 0.17862 | -0.4521 | -0.057404 | 0.36157 | 0.30875 | 0.76085 | 0.04578 | 0.039824 | 122.3849 | 122.4064 | 122.5709 | 122.3113 | -0.081342 | 122.3349 | 122.4381 | 122.4321 | 118.1482 | -122.8444
1837.0625 | 122.438 | -122.2824 | 0.10529 | 1.4211e-13 | 0.0019381 | -0.0095086 | -0.026217 | -0.023576 | 0.0042113 | 0.0036627 | -0.012788 | 0.027767 | 0.043729 | 0.0011303 | 0.047433 | 0.088037 | 0.033457 | 0.041952 | 0.10707 | 0.13315 | 0.2839 | 0.023942 | -121.9163 | -4.3632 | -121.9691 | 0.057037 | 0.16022 | 0.15884 | -122.7345 | 122.3064 | 0.001782 | 122.3704 | 122.3244 | 0.01801 | 0.027862 | 0.17862 | -0.4521 | -0.048249 | 0.36615 | 0.31333 | 0.76543 | 0.054936 | 0.053559 | 122.3895 | 122.4156 | 122.5663 | 122.3159 | -0.081344 | 122.3394 | 122.4426 | 122.4413 | 117.9193 | -122.8398
1838.8594 | 122.5479 | -122.2687 | 0.086975 | 1.4211e-13 | 0.0019381 | -0.009936 | -0.026644 | -0.023789 | 0.0042113 | -0.0039678 | -0.012575 | 0.027767 | 0.043943 | 0.00091673 | 0.047647 | 0.097194 | 0.038035 | 0.04653 | 0.11165 | 0.12399 | 0.27932 | 0.028521 | -121.9254 | -4.6287 | -121.9828 | 0.057037 | 0.15107 | 0.15427 | -122.7345 | 122.2972 | 0.024672 | 122.3659 | 122.3152 | 0.018009 | 0.037015 | 0.19235 | -0.46583 | -0.029938 | 0.34326 | 0.28586 | 0.75169 | 0.06409 | 0.067291 | 122.3803 | 122.3927 | 122.548 | 122.3067 | -0.058454 | 122.3257 | 122.4197 | 122.4229 | 117.64 | -122.8215
1840.6406 | 122.4884 | -122.3053 | 0.10986 | 1.4211e-13 | 0.0021517 | -0.009936 | -0.026644 | -0.023576 | 0.0035703 | -0.0039678 | -0.012575 | 0.027553 | 0.043729 | 0.00091673 | 0.047433 | 0.092615 | 0.033457 | 0.04653 | 0.10249 | 0.12857 | 0.27932 | 0.028521 | -121.9208 | -4.8348 | -121.9782 | 0.061616 | 0.15107 | 0.14969 | -122.7345 | 122.3338 | -0.007373 | 122.3979 | 122.3518 | 0.018009 | 0.018706 | 0.16946 | -0.42921 | -0.048247 | 0.38446 | 0.32706 | 0.75627 | 0.041202 | 0.039824 | 122.4078 | 122.4339 | 122.5846 | 122.3388 | -0.081342 | 122.3669 | 122.4564 | 122.455 | 117.4705 | -122.8444
1842.4219 | 122.5616 | -122.2733 | 0.086975 | 1.4211e-13 | 0.0019381 | -0.009936 | -0.026858 | -0.023789 | 0.0039977 | 0.018923 | -0.012361 | 0.027553 | 0.043943 | 0.00091673 | 0.047647 | 0.092615 | 0.028878 | 0.04653 | 0.10249 | 0.13315 | 0.2839 | 0.0331 | -121.9117 | -5.1003 | -121.9782 | 0.057037 | 0.15564 | 0.14969 | -122.7391 | 122.3064 | 0.015515 | 122.3659 | 122.3198 | 0.01343 | 0.046173 | 0.19693 | -0.46583 | -0.029938 | 0.36157 | 0.29502 | 0.76085 | 0.068668 | 0.062712 | 122.3757 | 122.4064 | 122.5572 | 122.3021 | -0.053875 | 122.3303 | 122.4289 | 122.4229 | 117.1729 | -122.8261
1844.1406 | 122.5296 | -122.2824 | 0.10071 | 1.4211e-13 | 0.0021517 | -0.009295 | -0.02643 | -0.023789 | 0.0044249 | -0.0039678 | -0.012361 | 0.027553 | 0.043729 | 0.00048933 | 0.047647 | 0.088037 | 0.038035 | 0.051108 | 0.11622 | 0.12399 | 0.28848 | 0.028521 | -121.9163 | -5.3659 | -121.9737 | 0.061616 | 0.15564 | 0.14053 | -122.7345 | 122.3109 | 0.015517 | 122.3704 | 122.3335 | 0.022587 | 0.023282 | 0.18777 | -0.4521 | -0.039092 | 0.36615 | 0.30875 | 0.76085 | 0.054935 | 0.039822 | 122.3986 | 122.4064 | 122.5709 | 122.3204 | -0.072187 | 122.344 | 122.4381 | 122.4229 | 116.9165 | -122.8352
1845.9062 | 122.5708 | -122.2641 | 0.091553 | 1.4211e-13 | 0.0021517 | -0.009295 | -0.026644 | -0.023576 | 0.0039977 | 0.011293 | -0.012575 | 0.027553 | 0.043516 | 0.00091673 | 0.047647 | 0.088037 | 0.042614 | 0.04653 | 0.10249 | 0.12399 | 0.28848 | 0.023942 | -121.9208 | -5.6452 | -121.9737 | 0.052459 | 0.15564 | 0.14969 | -122.7437 | 122.288 | 0.010937 | 122.3521 | 122.3106 | 0.022588 | 0.032437 | 0.19693 | -0.47956 | -0.039094 | 0.34326 | 0.29044 | 0.77001 | 0.06409 | 0.058134 | 122.3666 | 122.3881 | 122.5526 | 122.3067 | -0.067611 | 122.3166 | 122.4197 | 122.4138 | 116.6189 | -122.8352
1847.6875 | 122.5616 | -122.2733 | 0.054932 | 1.4211e-13 | 0.0019381 | -0.009936 | -0.02643 | -0.023576 | 0.0042113 | 0.011293 | -0.012788 | 0.02734 | 0.043516 | 0.00091673 | 0.047647 | 0.088037 | 0.038035 | 0.051108 | 0.10707 | 0.12399 | 0.27932 | 0.023942 | -121.9208 | -5.9199 | -121.9691 | 0.052459 | 0.15107 | 0.14969 | -122.7437 | 122.2972 | 0.052136 | 122.3613 | 122.3244 | 0.027166 | 0.069058 | 0.22439 | -0.47041 | -0.002473 | 0.35242 | 0.30417 | 0.77458 | 0.096133 | 0.094755 | 122.3803 | 122.3972 | 122.5526 | 122.3113 | -0.03099 | 122.3257 | 122.4243 | 122.4229 | 116.3533 | -122.7986
1849.3906 | 122.5067 | -122.2778 | 0.09613 | 1.4211e-13 | 0.0021517 | -0.0097224 | -0.02643 | -0.023576 | 0.0044249 | 0.0036627 | -0.012575 | 0.027553 | 0.043729 | 0.00048933 | 0.047433 | 0.088037 | 0.038035 | 0.04653 | 0.10249 | 0.12399 | 0.2839 | 0.0331 | -121.9163 | -6.1122 | -121.9737 | 0.052459 | 0.15564 | 0.14969 | -122.7437 | 122.3109 | 0.00636 | 122.3659 | 122.3244 | 0.01343 | 0.02786 | 0.18777 | -0.46583 | -0.043671 | 0.36157 | 0.30417 | 0.77001 | 0.059513 | 0.053557 | 122.3803 | 122.4018 | 122.5617 | 122.3159 | -0.06303 | 122.3303 | 122.4335 | 122.4275 | 116.1656 | -122.8398
1851.1875 | 122.4426 | -122.3236 | 0.11902 | 1.4211e-13 | 0.0021517 | -0.009295 | -0.026858 | -0.023576 | 0.0042113 | 0.0036627 | -0.012788 | 0.027553 | 0.043943 | 0.00048933 | 0.04786 | 0.092615 | 0.033457 | 0.051108 | 0.10707 | 0.12857 | 0.28848 | 0.028521 | -121.9117 | -6.4098 | -121.9737 | 0.066194 | 0.15564 | 0.14969 | -122.7437 | 122.3521 | -0.011951 | 122.4162 | 122.3747 | 0.022587 | 0.00955 | 0.16946 | -0.42006 | -0.052825 | 0.41193 | 0.34995 | 0.77001 | 0.036624 | 0.030668 | 122.4307 | 122.4522 | 122.6121 | 122.3571 | -0.090498 | 122.3898 | 122.4793 | 122.4733 | 115.9138 | -122.8627
1852.9688 | 122.5159 | -122.2961 | 0.07782 | 1.4211e-13 | 0.0019381 | -0.009936 | -0.026858 | -0.023362 | 0.0037841 | 0.0036627 | -0.012575 | 0.027553 | 0.043729 | 0.00070293 | 0.047647 | 0.092615 | 0.028878 | 0.051108 | 0.10249 | 0.11941 | 0.27932 | 0.0331 | -121.9071 | -6.6708 | -121.9737 | 0.057037 | 0.16022 | 0.14053 | -122.7482 | 122.3292 | 0.02467 | 122.3888 | 122.3473 | 0.018008 | 0.041591 | 0.2015 | -0.4521 | -0.020783 | 0.38904 | 0.32249 | 0.77459 | 0.082402 | 0.06271 | 122.3986 | 122.4156 | 122.5755 | 122.325 | -0.04472 | 122.3532 | 122.4564 | 122.4367 | 115.6253 | -122.8261
1854.75 | 122.5891 | -122.2916 | 0.07782 | 1.4211e-13 | 0.0021517 | -0.0095086 | -0.026644 | -0.023576 | 0.0042113 | -0.0039678 | -0.012575 | 0.02734 | 0.043729 | 0.00091673 | 0.047647 | 0.092615 | 0.028878 | 0.04653 | 0.11165 | 0.12399 | 0.27475 | 0.028521 | -121.9071 | -6.9547 | -121.9737 | 0.052459 | 0.15564 | 0.14969 | -122.7482 | 122.3201 | 0.033827 | 122.3842 | 122.3381 | 0.018009 | 0.04617 | 0.19693 | -0.45668 | -0.025361 | 0.38446 | 0.31791 | 0.77459 | 0.077823 | 0.071867 | 122.4032 | 122.4156 | 122.5663 | 122.3204 | -0.049299 | 122.344 | 122.4472 | 122.4413 | 115.3369 | -122.8261
1856.4688 | 122.5662 | -122.2595 | 0.082397 | 1.4211e-13 | 0.0019381 | -0.0097224 | -0.027072 | -0.023789 | 0.0037841 | 0.018923 | -0.012788 | 0.027553 | 0.043302 | 0.00070293 | 0.04786 | 0.088037 | 0.028878 | 0.051108 | 0.10707 | 0.12399 | 0.2839 | 0.0331 | -121.9117 | -7.2844 | -121.9737 | 0.066194 | 0.1648 | 0.14969 | -122.7482 | 122.2926 | 0.024671 | 122.3476 | 122.3106 | 0.018008 | 0.041593 | 0.20151 | -0.48872 | -0.016203 | 0.34784 | 0.28586 | 0.77459 | 0.082403 | 0.06729 | 122.3666 | 122.3835 | 122.5434 | 122.2884 | -0.049297 | 122.3257 | 122.4243 | 122.4092 | 114.9752 | -122.8306
1858.25 | 122.4518 | -122.3373 | 0.10529 | 1.4211e-13 | 0.0015107 | -0.0097224 | -0.026644 | -0.023362 | 0.0042113 | -0.0039678 | -0.012575 | 0.027553 | 0.043516 | 0.00091673 | 0.047647 | 0.092615 | 0.033457 | 0.051108 | 0.10249 | 0.12857 | 0.28848 | 0.028521 | -121.9117 | -7.5179 | -121.9691 | 0.066194 | 0.16022 | 0.14969 | -122.7528 | 122.3659 | -0.002796 | 122.43 | 122.3884 | 0.022587 | 0.023283 | 0.18319 | -0.41548 | -0.039092 | 0.42566 | 0.36826 | 0.78374 | 0.054936 | 0.044401 | 122.4398 | 122.4659 | 122.6258 | 122.3708 | -0.076765 | 122.4035 | 122.4976 | 122.487 | 114.8195 | -122.8581
1860.0469 | 122.5754 | -122.287 | 0.068665 | 1.4211e-13 | 0.0019381 | -0.009936 | -0.026644 | -0.023789 | 0.0044249 | 0.011293 | -0.012788 | 0.027553 | 0.043943 | 0.00091673 | 0.047647 | 0.097194 | 0.038035 | 0.04653 | 0.11622 | 0.13773 | 0.2839 | 0.0331 | -121.9071 | -7.9025 | -121.9737 | 0.057037 | 0.16022 | 0.14053 | -122.7482 | 122.3201 | 0.04756 | 122.3842 | 122.3335 | 0.01343 | 0.069062 | 0.21524 | -0.46126 | -0.011628 | 0.37989 | 0.31333 | 0.77459 | 0.091557 | 0.071865 | 122.4032 | 122.4247 | 122.5709 | 122.325 | -0.035565 | 122.344 | 122.4472 | 122.4275 | 114.3845 | -122.8169
1861.7656 | 122.5388 | -122.2961 | 0.054932 | 1.4211e-13 | 0.0017243 | -0.0095086 | -0.026644 | -0.023789 | 0.0044249 | 0.0036627 | -0.012788 | 0.027553 | 0.043729 | 0.00070293 | 0.04786 | 0.088037 | 0.033457 | 0.051108 | 0.10707 | 0.12857 | 0.28848 | 0.023942 | -121.9025 | -8.2596 | -121.9737 | 0.057037 | 0.15564 | 0.14511 | -122.7528 | 122.3201 | 0.052136 | 122.3842 | 122.3473 | 0.027166 | 0.073637 | 0.23355 | -0.45668 | 0.002105 | 0.39362 | 0.32249 | 0.77916 | 0.10071 | 0.090177 | 122.4032 | 122.4247 | 122.5846 | 122.3296 | -0.03099 | 122.3532 | 122.4518 | 122.4413 | 114.0365 | -122.8078
1863.5469 | 122.58 | -122.2916 | 0.068665 | 1.4211e-13 | 0.0019381 | -0.0097224 | -0.026644 | -0.023789 | 0.0039977 | 0.011293 | -0.012361 | 0.02734 | 0.043516 | 0.00091673 | 0.04786 | 0.092615 | 0.038035 | 0.04653 | 0.11165 | 0.13315 | 0.27932 | 0.028521 | -121.9071 | -8.6397 | -121.9737 | 0.057037 | 0.16022 | 0.14969 | -122.7437 | 122.3201 | 0.042982 | 122.3842 | 122.3381 | 0.018009 | 0.064483 | 0.21066 | -0.4521 | -0.011628 | 0.38446 | 0.31791 | 0.77001 | 0.091557 | 0.081022 | 122.4032 | 122.4247 | 122.5709 | 122.3296 | -0.040144 | 122.3486 | 122.4518 | 122.4413 | 113.6519 | -122.8123
1865.3438 | 122.5754 | -122.3007 | 0.068665 | 1.4211e-13 | 0.0021517 | -0.009936 | -0.026644 | -0.023576 | 0.0042113 | -0.0039678 | -0.012575 | 0.027767 | 0.043516 | 0.00070293 | 0.047433 | 0.088037 | 0.038035 | 0.055687 | 0.10707 | 0.13315 | 0.27475 | 0.028521 | -121.9025 | -9.006 | -121.9737 | 0.052459 | 0.16022 | 0.14969 | -122.7574 | 122.3292 | 0.038403 | 122.3888 | 122.3564 | 0.027166 | 0.064483 | 0.20608 | -0.45668 | -0.016206 | 0.3982 | 0.32706 | 0.78374 | 0.091557 | 0.081022 | 122.4078 | 122.4339 | 122.5755 | 122.3388 | -0.040144 | 122.3532 | 122.4609 | 122.4504 | 113.2948 | -122.8261
1867.0625 | 122.4976 | -122.3282 | 0.10986 | 1.4211e-13 | 0.0019381 | -0.0097224 | -0.026644 | -0.023576 | 0.0039977 | 0.011293 | -0.012575 | 0.02734 | 0.044157 | 0.00091673 | 0.047647 | 0.088037 | 0.033457 | 0.055687 | 0.10707 | 0.12857 | 0.2839 | 0.028521 | -121.9071 | -9.3311 | -121.9645 | 0.057037 | 0.1648 | 0.14053 | -122.7574 | 122.3567 | -0.002795 | 122.4162 | 122.3839 | 0.027166 | 0.018706 | 0.17404 | -0.42921 | -0.052826 | 0.42108 | 0.36369 | 0.7929 | 0.054937 | 0.030667 | 122.4353 | 122.4568 | 122.6121 | 122.3616 | -0.081342 | 122.3852 | 122.493 | 122.4687 | 112.9971 | -122.8673
1868.8438 | 122.4243 | -122.3328 | 0.086975 | 1.4211e-13 | 0.0017243 | -0.009936 | -0.026644 | -0.023789 | 0.0039977 | 0.018923 | -0.012575 | 0.027767 | 0.043729 | 0.00070293 | 0.047647 | 0.097194 | 0.033457 | 0.055687 | 0.11165 | 0.12857 | 0.2839 | 0.028521 | -121.8934 | -9.6607 | -121.9782 | 0.057037 | 0.16022 | 0.14969 | -122.7574 | 122.3613 | 0.024672 | 122.43 | 122.3885 | 0.027166 | 0.041594 | 0.19693 | -0.42464 | -0.029938 | 0.4394 | 0.35453 | 0.77916 | 0.073247 | 0.062712 | 122.4444 | 122.4613 | 122.6167 | 122.3662 | -0.058454 | 122.3898 | 122.493 | 122.4825 | 112.672 | -122.8444
1870.625 | 122.5296 | -122.3007 | 0.086975 | 1.4211e-13 | 0.0015107 | -0.01015 | -0.026644 | -0.023576 | 0.0039977 | 0.0036627 | -0.012361 | 0.027767 | 0.043729 | 0.00091673 | 0.047647 | 0.092615 | 0.038035 | 0.051108 | 0.11165 | 0.12857 | 0.28848 | 0.023942 | -121.8979 | -9.9721 | -121.9782 | 0.057037 | 0.16022 | 0.14053 | -122.7574 | 122.3247 | 0.024672 | 122.3933 | 122.3518 | 0.027166 | 0.041594 | 0.20151 | -0.45668 | -0.029938 | 0.40277 | 0.32248 | 0.77916 | 0.073247 | 0.053555 | 122.4124 | 122.4293 | 122.5892 | 122.3388 | -0.063033 | 122.3578 | 122.4609 | 122.4412 | 112.3286 | -122.8444
1872.3906 | 122.5937 | -122.2504 | 0.064087 | 1.4211e-13 | 0.0019381 | -0.009936 | -0.026644 | -0.023362 | 0.0042113 | 0.0036627 | -0.012361 | 0.027981 | 0.043943 | 0.00091673 | 0.047433 | 0.092615 | 0.033457 | 0.051108 | 0.10707 | 0.13315 | 0.27475 | 0.0331 | -121.8979 | -10.3521 | -121.9691 | 0.061616 | 0.15564 | 0.14511 | -122.762 | 122.2835 | 0.042981 | 122.343 | 122.3015 | 0.018008 | 0.069061 | 0.21066 | -0.51161 | -0.002471 | 0.35242 | 0.28129 | 0.7929 | 0.091556 | 0.081022 | 122.3574 | 122.3835 | 122.5251 | 122.2838 | -0.030987 | 122.312 | 122.406 | 122.3955 | 111.8983 | -122.8261
1874.1719 | 122.5296 | -122.287 | 0.068665 | 1.4211e-13 | 0.0019381 | -0.0095086 | -0.026644 | -0.023789 | 0.0044249 | 0.0036627 | -0.012575 | 0.027553 | 0.043729 | 0.00070293 | 0.047647 | 0.092615 | 0.033457 | 0.055687 | 0.11165 | 0.11941 | 0.2839 | 0.028521 | -121.9025 | -10.6589 | -121.9691 | 0.061616 | 0.16022 | 0.14511 | -122.7574 | 122.3155 | 0.042982 | 122.3796 | 122.3427 | 0.027166 | 0.050746 | 0.21524 | -0.47041 | -0.007049 | 0.38446 | 0.31791 | 0.78832 | 0.091557 | 0.076444 | 122.3986 | 122.4064 | 122.5709 | 122.3204 | -0.040144 | 122.3486 | 122.4472 | 122.4321 | 111.6281 | -122.8261
1875.8906 | 122.6028 | -122.2916 | 0.082397 | 1.4211e-13 | 0.0019381 | -0.0095086 | -0.027072 | -0.023789 | 0.0044249 | 0.011293 | -0.012575 | 0.027553 | 0.043943 | 0.0011303 | 0.04786 | 0.092615 | 0.038035 | 0.04653 | 0.10707 | 0.13315 | 0.27932 | 0.023942 | -121.8934 | -10.9748 | -121.9691 | 0.057037 | 0.16022 | 0.14969 | -122.762 | 122.3155 | 0.024671 | 122.3842 | 122.3381 | 0.022588 | 0.050751 | 0.19693 | -0.47041 | -0.02536 | 0.3982 | 0.32249 | 0.7929 | 0.077825 | 0.06729 | 122.3986 | 122.4247 | 122.5709 | 122.3296 | -0.058455 | 122.3486 | 122.4518 | 122.4413 | 111.3168 | -122.8444
1877.6719 | 122.4655 | -122.3328 | 0.11444 | 1.4211e-13 | 0.0019381 | -0.0097224 | -0.026858 | -0.023362 | 0.0039977 | 0.018923 | -0.012788 | 0.027553 | 0.043729 | 0.00091673 | 0.047647 | 0.092615 | 0.033457 | 0.04653 | 0.10249 | 0.13315 | 0.27932 | 0.019363 | -121.8979 | -11.3319 | -121.9645 | 0.057037 | 0.15564 | 0.14969 | -122.7666 | 122.3521 | -0.011951 | 122.4254 | 122.3793 | 0.027167 | 0.018707 | 0.16488 | -0.43379 | -0.057404 | 0.43482 | 0.36826 | 0.80206 | 0.041202 | 0.035246 | 122.4353 | 122.4659 | 122.6121 | 122.3662 | -0.095078 | 122.3898 | 122.4884 | 122.4825 | 111.0008 | -122.881
1879.4531 | 122.5433 | -122.2778 | 0.082397 | 1.4211e-13 | 0.0017243 | -0.0097224 | -0.027072 | -0.023576 | 0.0042113 | 0.018923 | -0.012575 | 0.02734 | 0.044157 | 0.00091673 | 0.047433 | 0.092615 | 0.033457 | 0.04653 | 0.10249 | 0.13315 | 0.28848 | 0.023942 | -121.8934 | -11.5838 | -121.9599 | 0.061616 | 0.16022 | 0.14511 | -122.762 | 122.3018 | 0.020093 | 122.3704 | 122.3244 | 0.022588 | 0.050751 | 0.20608 | -0.48415 | -0.020781 | 0.38447 | 0.31791 | 0.80206 | 0.077825 | 0.062712 | 122.3803 | 122.411 | 122.5663 | 122.3113 | -0.058455 | 122.3394 | 122.4381 | 122.4229 | 110.6941 | -122.8444
1881.25 | 122.612 | -122.3099 | 0.073242 | 1.4211e-13 | 0.0017243 | -0.009936 | -0.026644 | -0.023789 | 0.0039977 | 0.018923 | -0.012361 | 0.027553 | 0.043943 | 0.00070293 | 0.047433 | 0.083459 | 0.028878 | 0.051108 | 0.10707 | 0.12857 | 0.28848 | 0.028521 | -121.8888 | -11.8631 | -121.9691 | 0.057037 | 0.16022 | 0.15427 | -122.7711 | 122.3384 | 0.033826 | 122.3933 | 122.361 | 0.022587 | 0.055327 | 0.21524 | -0.46126 | -0.016205 | 0.42109 | 0.34079 | 0.80206 | 0.08698 | 0.081024 | 122.4169 | 122.4384 | 122.5984 | 122.3388 | -0.044721 | 122.3669 | 122.4701 | 122.4641 | 110.4468 | -122.8444
1883.0312 | 122.4335 | -122.3557 | 0.1236 | 1.4211e-13 | 0.0017243 | -0.009936 | -0.026217 | -0.023789 | 0.0039977 | 0.011293 | -0.012361 | 0.02734 | 0.043943 | 0.00091673 | 0.04786 | 0.097194 | 0.033457 | 0.051108 | 0.10707 | 0.11941 | 0.27932 | 0.028521 | -121.8934 | -12.266 | -121.9691 | 0.057037 | 0.15564 | 0.14053 | -122.7711 | 122.3842 | -0.016528 | 122.4528 | 122.4068 | 0.022587 | -0.004185 | 0.15573 | -0.41548 | -0.066559 | 0.46229 | 0.38657 | 0.80206 | 0.032047 | 0.016934 | 122.4627 | 122.4751 | 122.635 | 122.3891 | -0.095075 | 122.4127 | 122.5113 | 122.4962 | 110.0896 | -122.8947
1884.8125 | 122.525 | -122.3007 | 0.068665 | 1.4211e-13 | 0.0015107 | -0.009936 | -0.026858 | -0.023148 | 0.0037841 | 0.011293 | -0.012575 | 0.027767 | 0.043516 | 0.00048933 | 0.047647 | 0.083459 | 0.033457 | 0.055687 | 0.10249 | 0.12857 | 0.2839 | 0.037679 | -121.8842 | -12.527 | -121.9599 | 0.061616 | 0.15107 | 0.14053 | -122.7757 | 122.3384 | 0.033825 | 122.3842 | 122.3564 | 0.018008 | 0.059904 | 0.21524 | -0.475 | -0.007049 | 0.41651 | 0.3408 | 0.81579 | 0.0824 | 0.071865 | 122.4032 | 122.4293 | 122.5846 | 122.3342 | -0.030986 | 122.3623 | 122.4518 | 122.4412 | 109.7737 | -122.8444
1886.6094 | 122.5983 | -122.2687 | 0.059509 | 1.4211e-13 | 0.0019381 | -0.009295 | -0.026644 | -0.023789 | 0.0044249 | 0.011293 | -0.012575 | 0.027981 | 0.043943 | 0.00091673 | 0.04786 | 0.092615 | 0.033457 | 0.051108 | 0.10707 | 0.13315 | 0.2839 | 0.0331 | -121.8842 | -12.8338 | -121.9691 | 0.061616 | 0.15107 | 0.14969 | -122.7711 | 122.3018 | 0.047559 | 122.3613 | 122.3198 | 0.018008 | 0.073639 | 0.22439 | -0.50246 | 0.002107 | 0.38447 | 0.2996 | 0.80206 | 0.091556 | 0.090178 | 122.3757 | 122.4018 | 122.5526 | 122.3021 | -0.026409 | 122.3303 | 122.4197 | 122.4184 | 109.4349 | -122.8306
1888.3281 | 122.5571 | -122.3099 | 0.073242 | 1.4211e-13 | 0.0021517 | -0.0095086 | -0.026644 | -0.023576 | 0.0044249 | 0.0036627 | -0.012575 | 0.02734 | 0.04437 | 0.00091673 | 0.047647 | 0.092615 | 0.033457 | 0.051108 | 0.11165 | 0.12399 | 0.2839 | 0.0331 | -121.8842 | -13.136 | -121.9599 | 0.066194 | 0.16022 | 0.14511 | -122.7666 | 122.343 | 0.038405 | 122.4025 | 122.361 | 0.018008 | 0.050748 | 0.21066 | -0.45668 | -0.007048 | 0.42567 | 0.34995 | 0.80664 | 0.08698 | 0.071867 | 122.4215 | 122.4339 | 122.5938 | 122.3433 | -0.040142 | 122.3761 | 122.4701 | 122.455 | 109.1739 | -122.8398
1890.1094 | 122.5525 | -122.3373 | 0.10071 | 1.4211e-13 | 0.0017243 | -0.009936 | -0.026644 | -0.023576 | 0.0044249 | 0.0036627 | -0.012788 | 0.027553 | 0.043729 | 0.00091673 | 0.04786 | 0.092615 | 0.033457 | 0.04653 | 0.11165 | 0.12857 | 0.2839 | 0.028521 | -121.8796 | -13.4061 | -121.9508 | 0.066194 | 0.16022 | 0.14511 | -122.7757 | 122.3659 | 0.010939 | 122.43 | 122.3839 | 0.018009 | 0.027861 | 0.18319 | -0.43838 | -0.034514 | 0.45771 | 0.38658 | 0.82495 | 0.059514 | 0.044401 | 122.449 | 122.4659 | 122.6212 | 122.3708 | -0.072187 | 122.4035 | 122.4976 | 122.4825 | 108.9312 | -122.8764
1891.9062 | 122.5067 | -122.3099 | 0.10986 | 1.4211e-13 | 0.0021517 | -0.009936 | -0.026858 | -0.023362 | 0.0039977 | 0.011293 | -0.012361 | 0.02734 | 0.043729 | 0.00048933 | 0.047647 | 0.088037 | 0.038035 | 0.051108 | 0.10707 | 0.12399 | 0.27932 | 0.0331 | -121.8796 | -13.6991 | -121.9645 | 0.066194 | 0.16022 | 0.15427 | -122.7711 | 122.343 | -0.002795 | 122.3979 | 122.361 | 0.018008 | 0.014127 | 0.16946 | -0.46126 | -0.043669 | 0.43024 | 0.34537 | 0.80664 | 0.050359 | 0.044403 | 122.4169 | 122.4339 | 122.5892 | 122.3479 | -0.076763 | 122.3761 | 122.4701 | 122.4641 | 108.6107 | -122.881
1893.625 | 122.58 | -122.3099 | 0.086975 | 1.4211e-13 | 0.0021517 | -0.01015 | -0.026644 | -0.023789 | 0.0039977 | 0.018923 | -0.012575 | 0.027553 | 0.043729 | 0.00091673 | 0.047433 | 0.092615 | 0.033457 | 0.055687 | 0.10249 | 0.12399 | 0.27932 | 0.0331 | -121.8796 | -14.0105 | -121.9553 | 0.057037 | 0.16022 | 0.14969 | -122.7849 | 122.343 | 0.015515 | 122.4025 | 122.3656 | 0.022587 | 0.037015 | 0.19235 | -0.475 | -0.029938 | 0.43024 | 0.35453 | 0.82953 | 0.073247 | 0.062712 | 122.4124 | 122.4339 | 122.5892 | 122.3433 | -0.053875 | 122.3669 | 122.4701 | 122.4596 | 108.2994 | -122.8718
1895.4062 | 122.5525 | -122.3145 | 0.073242 | 1.4211e-13 | 0.0023653 | -0.0097224 | -0.026858 | -0.023576 | 0.0039977 | 0.011293 | -0.012575 | 0.027767 | 0.043729 | 0.00091673 | 0.048074 | 0.088037 | 0.038035 | 0.041952 | 0.10249 | 0.12857 | 0.28848 | 0.0331 | -121.8659 | -14.3035 | -121.9599 | 0.057037 | 0.16022 | 0.14969 | -122.7803 | 122.3476 | 0.029248 | 122.4025 | 122.3564 | 0.008852 | 0.055327 | 0.21524 | -0.46584 | -0.016205 | 0.44856 | 0.35453 | 0.82037 | 0.08698 | 0.076445 | 122.4169 | 122.443 | 122.6029 | 122.3525 | -0.040142 | 122.3715 | 122.4747 | 122.4641 | 108.0109 | -122.8535
1897.1875 | 122.5021 | -122.3373 | 0.10529 | 1.4211e-13 | 0.0021517 | -0.0095086 | -0.026858 | -0.023576 | 0.0039977 | 0.011293 | -0.012361 | 0.02734 | 0.043516 | 0.00070293 | 0.047647 | 0.088037 | 0.038035 | 0.051108 | 0.10707 | 0.12857 | 0.27932 | 0.0331 | -121.8751 | -14.5737 | -121.9508 | 0.057037 | 0.16022 | 0.15427 | -122.7757 | 122.3704 | 0.001782 | 122.4254 | 122.3884 | 0.018008 | 0.023283 | 0.17404 | -0.43838 | -0.048249 | 0.46229 | 0.38658 | 0.82495 | 0.054936 | 0.04898 | 122.4444 | 122.4659 | 122.6167 | 122.3754 | -0.072186 | 122.3944 | 122.4976 | 122.4916 | 107.7637 | -122.881
1898.9062 | 122.5571 | -122.3557 | 0.091553 | 1.4211e-13 | 0.0021517 | -0.0095086 | -0.027072 | -0.023576 | 0.0042113 | 0.011293 | -0.012361 | 0.02734 | 0.043729 | 0.00091673 | 0.047433 | 0.092615 | 0.033457 | 0.055687 | 0.10707 | 0.12399 | 0.28848 | 0.028521 | -121.8751 | -14.8759 | -121.9553 | 0.061616 | 0.15564 | 0.15884 | -122.7803 | 122.3842 | 0.015515 | 122.4483 | 122.4113 | 0.027166 | 0.032437 | 0.19693 | -0.42464 | -0.029937 | 0.4806 | 0.40031 | 0.82495 | 0.06409 | 0.067292 | 122.4627 | 122.4796 | 122.6441 | 122.3891 | -0.063032 | 122.4173 | 122.5113 | 122.5145 | 107.4798 | -122.8718
1900.6875 | 122.5067 | -122.3282 | 0.091553 | 1.4211e-13 | 0.0023653 | -0.0097224 | -0.026644 | -0.023576 | 0.0044249 | 0.0036627 | -0.012788 | 0.027553 | 0.043943 | 0.00091673 | 0.047433 | 0.097194 | 0.038035 | 0.051108 | 0.11165 | 0.12399 | 0.2839 | 0.028521 | -121.8705 | -15.1735 | -121.9462 | 0.052459 | 0.14649 | 0.14053 | -122.7757 | 122.3567 | 0.020094 | 122.4254 | 122.3793 | 0.022587 | 0.032437 | 0.19235 | -0.44753 | -0.039094 | 0.45771 | 0.382 | 0.82953 | 0.054933 | 0.048977 | 122.4398 | 122.4522 | 122.6121 | 122.3662 | -0.063032 | 122.3806 | 122.4747 | 122.4687 | 107.1547 | -122.8673
1902.4688 | 122.5754 | -122.3236 | 0.068665 | 1.4211e-13 | 0.0023653 | -0.009936 | -0.026644 | -0.023148 | 0.0042113 | 0.026554 | -0.012788 | 0.027553 | 0.043516 | 0.00091673 | 0.047647 | 0.092615 | 0.033457 | 0.055687 | 0.10707 | 0.12857 | 0.27932 | 0.0331 | -121.8659 | -15.4574 | -121.9462 | 0.052459 | 0.15564 | 0.14053 | -122.7849 | 122.3567 | 0.038403 | 122.4162 | 122.3793 | 0.022587 | 0.059904 | 0.21066 | -0.46127 | -0.016206 | 0.45771 | 0.37742 | 0.83869 | 0.086978 | 0.071865 | 122.4307 | 122.4522 | 122.6029 | 122.3571 | -0.035565 | 122.3761 | 122.4793 | 122.4641 | 106.8662 | -122.8535
1904.1875 | 122.5662 | -122.3145 | 0.07782 | 1.4211e-13 | 0.0019381 | -0.01015 | -0.026644 | -0.023362 | 0.0042113 | 0.011293 | -0.012788 | 0.027767 | 0.043302 | 0.00091673 | 0.047647 | 0.088037 | 0.033457 | 0.051108 | 0.10249 | 0.12857 | 0.27932 | 0.042258 | -121.8705 | -15.7916 | -121.9508 | 0.057037 | 0.15564 | 0.14969 | -122.7895 | 122.3567 | 0.02467 | 122.4025 | 122.3656 | 0.00885 | 0.050749 | 0.2015 | -0.475 | -0.020783 | 0.44398 | 0.36369 | 0.83869 | 0.077823 | 0.071867 | 122.4169 | 122.443 | 122.5938 | 122.3479 | -0.035562 | 122.3715 | 122.4701 | 122.4641 | 106.5228 | -122.8673
1905.9688 | 122.5891 | -122.3236 | 0.07782 | 1.4211e-13 | 0.0021517 | -0.0097224 | -0.026644 | -0.023362 | 0.0042113 | 0.011293 | -0.012575 | 0.028194 | 0.044157 | 0.00070293 | 0.04786 | 0.097194 | 0.033457 | 0.051108 | 0.10249 | 0.12857 | 0.2839 | 0.028521 | -121.8613 | -16.19 | -121.9462 | 0.057037 | 0.15564 | 0.14053 | -122.794 | 122.3521 | 0.02467 | 122.4208 | 122.3747 | 0.022587 | 0.050749 | 0.20608 | -0.47042 | -0.020783 | 0.46229 | 0.37742 | 0.84785 | 0.077823 | 0.06271 | 122.4261 | 122.4522 | 122.6075 | 122.3571 | -0.049299 | 122.3806 | 122.4793 | 122.4641 | 106.1336 | -122.8719
1907.75 | 122.612 | -122.3053 | 0.073242 | 1.4211e-13 | 0.0019381 | -0.0097224 | -0.026858 | -0.024217 | 0.0037841 | -0.0039678 | -0.012575 | 0.027767 | 0.043943 | 0.00070293 | 0.047647 | 0.092615 | 0.028878 | 0.041952 | 0.10249 | 0.12857 | 0.2839 | 0.028521 | -121.8659 | -16.5379 | -121.9462 | 0.057037 | 0.15564 | 0.14053 | -122.7849 | 122.3338 | 0.029248 | 122.3979 | 122.3472 | 0.013431 | 0.055327 | 0.21066 | -0.47958 | -0.016205 | 0.4394 | 0.35911 | 0.83869 | 0.082401 | 0.067288 | 122.4078 | 122.4339 | 122.5892 | 122.3342 | -0.044721 | 122.3623 | 122.4609 | 122.4458 | 105.7674 | -122.8581
1909.4688 | 122.5479 | -122.3328 | 0.07782 | 1.4211e-13 | 0.0019381 | -0.0097224 | -0.026858 | -0.023576 | 0.0039977 | -0.0039678 | -0.012575 | 0.027553 | 0.043729 | 0.0011303 | 0.04786 | 0.097194 | 0.028878 | 0.051108 | 0.10707 | 0.12857 | 0.27932 | 0.0331 | -121.8567 | -16.8539 | -121.9462 | 0.04788 | 0.14649 | 0.14511 | -122.7895 | 122.3659 | 0.029248 | 122.43 | 122.3839 | 0.018008 | 0.050749 | 0.2015 | -0.45669 | -0.02994 | 0.47603 | 0.38658 | 0.84327 | 0.068666 | 0.067289 | 122.4398 | 122.4613 | 122.6121 | 122.3616 | -0.04472 | 122.3806 | 122.4792 | 122.4779 | 105.4789 | -122.8673
1911.2656 | 122.6166 | -122.319 | 0.07782 | 1.4211e-13 | 0.0021517 | -0.009936 | -0.026217 | -0.023362 | 0.0037841 | 0.011293 | -0.012361 | 0.027553 | 0.044157 | 0.00070293 | 0.047433 | 0.088037 | 0.038035 | 0.051108 | 0.10249 | 0.12857 | 0.2839 | 0.028521 | -121.8567 | -17.1973 | -121.9462 | 0.057037 | 0.15564 | 0.14969 | -122.794 | 122.3476 | 0.02467 | 122.4071 | 122.3701 | 0.022587 | 0.050749 | 0.20608 | -0.475 | -0.020783 | 0.46229 | 0.37284 | 0.84785 | 0.077823 | 0.071867 | 122.4215 | 122.4476 | 122.6029 | 122.3571 | -0.049299 | 122.3761 | 122.4747 | 122.4687 | 105.1218 | -122.8719
1912.9688 | 122.4747 | -122.3557 | 0.11444 | 1.4211e-13 | 0.0019381 | -0.0097224 | -0.027072 | -0.023362 | 0.0042113 | 0.018923 | -0.012788 | 0.027767 | 0.043729 | 0.00070293 | 0.04786 | 0.092615 | 0.028878 | 0.055687 | 0.11165 | 0.13315 | 0.27932 | 0.0331 | -121.8522 | -17.5407 | -121.9462 | 0.061616 | 0.15564 | 0.14969 | -122.7986 | 122.3888 | -0.002794 | 122.4483 | 122.4113 | 0.022587 | 0.018707 | 0.16488 | -0.44296 | -0.052825 | 0.50349 | 0.40947 | 0.85242 | 0.041202 | 0.035246 | 122.4673 | 122.4888 | 122.635 | 122.3845 | -0.081341 | 122.4173 | 122.5113 | 122.5053 | 104.815 | -122.9131
1914.75 | 122.6074 | -122.2961 | 0.082397 | 1.4211e-13 | 0.0019381 | -0.0097224 | -0.02643 | -0.023789 | 0.0037841 | 0.018923 | -0.012361 | 0.027767 | 0.043516 | 0.00048933 | 0.047647 | 0.092615 | 0.033457 | 0.04653 | 0.11165 | 0.12857 | 0.27932 | 0.0331 | -121.8522 | -17.8429 | -121.9416 | 0.057037 | 0.15564 | 0.15427 | -122.794 | 122.3292 | 0.02925 | 122.3888 | 122.3427 | 0.01343 | 0.046172 | 0.19693 | -0.49789 | -0.02536 | 0.44398 | 0.35454 | 0.85242 | 0.073246 | 0.071869 | 122.4078 | 122.4247 | 122.5755 | 122.3296 | -0.049297 | 122.3532 | 122.4518 | 122.4504 | 104.4533 | -122.8764
1916.5469 | 122.5616 | -122.3282 | 0.064087 | 1.4211e-13 | 0.0021517 | -0.009936 | -0.027072 | -0.023576 | 0.0039977 | 0.0036627 | -0.012361 | 0.027553 | 0.043729 | 0.00070293 | 0.04786 | 0.088037 | 0.033457 | 0.051108 | 0.10249 | 0.13315 | 0.27932 | 0.0331 | -121.8567 | -18.1863 | -121.937 | 0.061616 | 0.15107 | 0.14969 | -122.794 | 122.3613 | 0.038403 | 122.4162 | 122.3793 | 0.018008 | 0.069061 | 0.21524 | -0.46585 | -0.002471 | 0.47145 | 0.39116 | 0.857 | 0.086978 | 0.0856 | 122.4307 | 122.4613 | 122.6075 | 122.3616 | -0.030987 | 122.3898 | 122.4793 | 122.4779 | 104.1419 | -122.8581
1918.2656 | 122.5937 | -122.3282 | 0.073242 | 1.4211e-13 | 0.0019381 | -0.009936 | -0.026644 | -0.023576 | 0.0039977 | 0.011293 | -0.012361 | 0.027767 | 0.043516 | 0.00048933 | 0.04786 | 0.088037 | 0.033457 | 0.060265 | 0.10249 | 0.13773 | 0.27932 | 0.037679 | -121.843 | -18.6167 | -121.937 | 0.057037 | 0.15564 | 0.14053 | -122.7895 | 122.3659 | 0.029248 | 122.4162 | 122.3885 | 0.022586 | 0.064485 | 0.20608 | -0.46127 | -0.016205 | 0.48519 | 0.39116 | 0.85242 | 0.082401 | 0.067288 | 122.4307 | 122.4659 | 122.6075 | 122.3616 | -0.035563 | 122.3852 | 122.4838 | 122.4687 | 103.7115 | -122.8627
1920.0469 | 122.5479 | -122.319 | 0.10986 | 1.4211e-13 | 0.0019381 | -0.0095086 | -0.026858 | -0.023576 | 0.0042113 | 0.011293 | -0.013002 | 0.027767 | 0.043729 | 0.0011303 | 0.04786 | 0.097194 | 0.042614 | 0.051108 | 0.10249 | 0.12857 | 0.27932 | 0.0331 | -121.8384 | -19.0517 | -121.937 | 0.052459 | 0.16022 | 0.14511 | -122.7986 | 122.3521 | -0.007373 | 122.4162 | 122.3701 | 0.018008 | 0.018706 | 0.16946 | -0.47958 | -0.057404 | 0.48061 | 0.382 | 0.86158 | 0.050359 | 0.035246 | 122.4215 | 122.4476 | 122.5984 | 122.3616 | -0.076763 | 122.3715 | 122.4793 | 122.4641 | 103.2674 | -122.9085
1921.8281 | 122.6212 | -122.3282 | 0.064087 | 1.4211e-13 | 0.0019381 | -0.0095086 | -0.026858 | -0.023576 | 0.0044249 | -0.0039678 | -0.012361 | 0.027553 | 0.043729 | 0.00091673 | 0.047647 | 0.092615 | 0.042614 | 0.051108 | 0.10707 | 0.13315 | 0.27932 | 0.0331 | -121.8476 | -19.4775 | -121.9325 | 0.057037 | 0.15564 | 0.14969 | -122.7986 | 122.3613 | 0.042981 | 122.4208 | 122.3793 | 0.018008 | 0.069061 | 0.21524 | -0.47042 | -0.00705 | 0.48061 | 0.39574 | 0.86616 | 0.091556 | 0.0856 | 122.4353 | 122.4613 | 122.6075 | 122.3708 | -0.030987 | 122.3852 | 122.4838 | 122.4779 | 102.8507 | -122.8627
1923.5469 | 122.6028 | -122.3419 | 0.086975 | 1.4211e-13 | 0.0019381 | -0.0097224 | -0.027072 | -0.023576 | 0.0039977 | 0.011293 | -0.012361 | 0.027981 | 0.043729 | 0.00091673 | 0.04786 | 0.088037 | 0.038035 | 0.055687 | 0.10707 | 0.12857 | 0.2839 | 0.023942 | -121.8384 | -19.8621 | -121.9325 | 0.052459 | 0.15107 | 0.15427 | -122.794 | 122.3659 | 0.020093 | 122.43 | 122.3976 | 0.031745 | 0.041594 | 0.19693 | -0.45211 | -0.034516 | 0.5035 | 0.40947 | 0.86158 | 0.06409 | 0.067291 | 122.449 | 122.4705 | 122.6258 | 122.38 | -0.063033 | 122.3944 | 122.493 | 122.4962 | 102.4798 | -122.881
1925.3281 | 122.5937 | -122.3145 | 0.054932 | 1.4211e-13 | 0.0023653 | -0.009295 | -0.026644 | -0.023576 | 0.0042113 | 0.011293 | -0.012361 | 0.02734 | 0.043516 | 0.00070293 | 0.04786 | 0.092615 | 0.047193 | 0.055687 | 0.11165 | 0.12857 | 0.27932 | 0.028521 | -121.8338 | -20.1414 | -121.9325 | 0.052459 | 0.16022 | 0.15427 | -122.8078 | 122.343 | 0.056715 | 122.4071 | 122.3701 | 0.027166 | 0.073637 | 0.22439 | -0.49331 | -0.002473 | 0.48061 | 0.382 | 0.87532 | 0.10529 | 0.099334 | 122.4261 | 122.443 | 122.5938 | 122.3616 | -0.026411 | 122.3669 | 122.4747 | 122.4687 | 102.1731 | -122.8627
1927.125 | 122.5204 | -122.3602 | 0.11902 | 1.4211e-13 | 0.0019381 | -0.009295 | -0.026644 | -0.023789 | 0.0039977 | 0.011293 | -0.012361 | 0.027553 | 0.044157 | 0.00091673 | 0.047647 | 0.092615 | 0.042614 | 0.055687 | 0.11165 | 0.12857 | 0.27475 | 0.023942 | -121.8384 | -20.5947 | -121.9279 | 0.057037 | 0.15107 | 0.15884 | -122.7986 | 122.3842 | -0.007372 | 122.4528 | 122.4159 | 0.031745 | 0.00955 | 0.15573 | -0.43838 | -0.061982 | 0.52181 | 0.43236 | 0.87074 | 0.032046 | 0.039826 | 122.4719 | 122.4888 | 122.635 | 122.4028 | -0.095077 | 122.4173 | 122.5113 | 122.5191 | 101.7656 | -122.9176
1928.8438 | 122.6303 | -122.3282 | 0.064087 | 1.4211e-13 | 0.0021517 | -0.0097224 | -0.026858 | -0.023789 | 0.0039977 | 0.0036627 | -0.012788 | 0.027553 | 0.043302 | 0.00091673 | 0.04786 | 0.088037 | 0.033457 | 0.051108 | 0.11622 | 0.13315 | 0.27932 | 0.0331 | -121.8384 | -20.9243 | -121.9279 | 0.057037 | 0.16022 | 0.15427 | -122.7986 | 122.3613 | 0.052138 | 122.4162 | 122.3793 | 0.018008 | 0.069061 | 0.21524 | -0.47042 | -0.00705 | 0.48976 | 0.40032 | 0.87074 | 0.096135 | 0.090179 | 122.4444 | 122.4613 | 122.6075 | 122.3616 | -0.030987 | 122.3852 | 122.4884 | 122.4825 | 101.4038 | -122.8627
1930.625 | 122.4884 | -122.3328 | 0.10986 | 1.4211e-13 | 0.0021517 | -0.009295 | -0.026644 | -0.023576 | 0.0039977 | 0.0036627 | -0.012575 | 0.02734 | 0.043943 | 0.00070293 | 0.04786 | 0.092615 | 0.028878 | 0.04653 | 0.10249 | 0.12857 | 0.27932 | 0.028521 | -121.8293 | -21.2723 | -121.9279 | 0.052459 | 0.15107 | 0.14969 | -122.8032 | 122.3613 | -0.007373 | 122.4254 | 122.3793 | 0.018009 | 0.018706 | 0.16946 | -0.47043 | -0.057404 | 0.5035 | 0.40489 | 0.87532 | 0.041202 | 0.039824 | 122.4353 | 122.4613 | 122.6121 | 122.3616 | -0.081342 | 122.3852 | 122.4838 | 122.4825 | 101.0604 | -122.9131
1932.3594 | 122.6028 | -122.3236 | 0.059509 | 1.4211e-13 | 0.0021517 | -0.009295 | -0.026858 | -0.024003 | 0.0042113 | 0.011293 | -0.012575 | 0.027553 | 0.043516 | 0.00070293 | 0.048074 | 0.092615 | 0.042614 | 0.04653 | 0.11165 | 0.12857 | 0.27932 | 0.0331 | -121.8247 | -21.6524 | -121.9325 | 0.061616 | 0.16022 | 0.15427 | -122.8032 | 122.3567 | 0.052138 | 122.4162 | 122.3701 | 0.01343 | 0.06906 | 0.21982 | -0.47958 | 0.002107 | 0.49892 | 0.39116 | 0.87074 | 0.10071 | 0.094757 | 122.4353 | 122.4522 | 122.6029 | 122.3662 | -0.026409 | 122.3852 | 122.4838 | 122.4779 | 100.6712 | -122.8627
1934.1406 | 122.5571 | -122.3557 | 0.10529 | 1.4211e-13 | 0.0023653 | -0.0095086 | -0.02643 | -0.023576 | 0.0039977 | 0.011293 | -0.012575 | 0.027767 | 0.043516 | 0.00091673 | 0.04786 | 0.092615 | 0.033457 | 0.051108 | 0.11165 | 0.12857 | 0.27932 | 0.0331 | -121.8247 | -22.0324 | -121.9233 | 0.057037 | 0.15564 | 0.14969 | -122.8078 | 122.3888 | 0.006361 | 122.4483 | 122.4068 | 0.018008 | 0.023283 | 0.17404 | -0.45211 | -0.048249 | 0.53097 | 0.43236 | 0.88447 | 0.050357 | 0.044401 | 122.4673 | 122.4842 | 122.635 | 122.3891 | -0.072186 | 122.4127 | 122.5113 | 122.5053 | 100.3233 | -122.9131
1935.9062 | 122.5388 | -122.3785 | 0.10529 | 1.4211e-13 | 0.0019381 | -0.009936 | -0.026644 | -0.023789 | 0.0039977 | 0.011293 | -0.012575 | 0.027767 | 0.043729 | 0.00070293 | 0.047647 | 0.092615 | 0.028878 | 0.055687 | 0.11165 | 0.12857 | 0.27932 | 0.028521 | -121.8247 | -22.3529 | -121.9233 | 0.057037 | 0.15564 | 0.14969 | -122.8078 | 122.4071 | 0.006361 | 122.4712 | 122.4342 | 0.027166 | 0.023283 | 0.17404 | -0.42923 | -0.048249 | 0.55385 | 0.45525 | 0.88447 | 0.050357 | 0.044401 | 122.4902 | 122.5071 | 122.6579 | 122.4074 | -0.076765 | 122.4356 | 122.5342 | 122.5282 | 100.0256 | -122.9131
1937.6406 | 122.5983 | -122.3236 | 0.082397 | 1.4211e-13 | 0.0023653 | -0.0097224 | -0.026858 | -0.023576 | 0.0037841 | 0.011293 | -0.012575 | 0.027553 | 0.043729 | 0.00091673 | 0.048074 | 0.092615 | 0.038035 | 0.051108 | 0.10249 | 0.12857 | 0.2839 | 0.023942 | -121.8201 | -22.7512 | -121.9141 | 0.057037 | 0.15564 | 0.14511 | -122.8078 | 122.3475 | 0.020093 | 122.4162 | 122.3747 | 0.027166 | 0.046172 | 0.20151 | -0.48416 | -0.02536 | 0.5035 | 0.40947 | 0.89363 | 0.073246 | 0.062712 | 122.4261 | 122.4522 | 122.6075 | 122.3616 | -0.058455 | 122.3806 | 122.4793 | 122.4687 | 99.5724 | -122.8902
1939.4375 | 122.5479 | -122.3694 | 0.091553 | 1.4211e-13 | 0.0023653 | -0.009936 | -0.026858 | -0.023576 | 0.0035703 | 0.018923 | -0.012575 | 0.027767 | 0.043729 | 0.00048933 | 0.048074 | 0.097194 | 0.038035 | 0.04653 | 0.10249 | 0.12857 | 0.2839 | 0.0331 | -121.8155 | -23.1221 | -121.9233 | 0.057037 | 0.15564 | 0.14511 | -122.8169 | 122.4025 | 0.010937 | 122.4666 | 122.4159 | 0.01343 | 0.037016 | 0.19235 | -0.44754 | -0.034516 | 0.55386 | 0.44609 | 0.89363 | 0.06409 | 0.053556 | 122.4719 | 122.498 | 122.6533 | 122.4074 | -0.058453 | 122.4264 | 122.525 | 122.5145 | 99.2473 | -122.9085
1941.1719 | 122.5388 | -122.3877 | 0.10529 | 1.4211e-13 | 0.0021517 | -0.0095086 | -0.026644 | -0.023789 | 0.0044249 | 0.011293 | -0.012575 | 0.027553 | 0.043943 | 0.00048933 | 0.04786 | 0.092615 | 0.033457 | 0.04653 | 0.11165 | 0.12399 | 0.2839 | 0.0331 | -121.8109 | -23.3785 | -121.9187 | 0.052459 | 0.15107 | 0.14511 | -122.8123 | 122.4208 | 0.006361 | 122.4803 | 122.4342 | 0.01343 | 0.018704 | 0.17862 | -0.42465 | -0.052827 | 0.57675 | 0.46898 | 0.89363 | 0.045779 | 0.039823 | 122.4993 | 122.5117 | 122.6716 | 122.4212 | -0.072186 | 122.4402 | 122.5388 | 122.5328 | 99.0092 | -122.9176
1942.9688 | 122.6303 | -122.3419 | 0.09613 | 1.4211e-13 | 0.0021517 | -0.009295 | -0.026644 | -0.023576 | 0.0037841 | 0.011293 | -0.012575 | 0.027767 | 0.043729 | 0.00091673 | 0.048074 | 0.083459 | 0.038035 | 0.051108 | 0.10249 | 0.12399 | 0.2839 | 0.028521 | -121.8018 | -23.7677 | -121.9141 | 0.052459 | 0.16022 | 0.14053 | -122.8078 | 122.3704 | 0.00636 | 122.4254 | 122.393 | 0.022587 | 0.02786 | 0.18777 | -0.46585 | -0.043671 | 0.54013 | 0.42778 | 0.89363 | 0.064092 | 0.0444 | 122.4444 | 122.4659 | 122.6258 | 122.38 | -0.067609 | 122.3944 | 122.5021 | 122.4824 | 98.5742 | -122.9039
1944.6875 | 122.6166 | -122.3282 | 0.068665 | 1.4211e-13 | 0.0023653 | -0.0095086 | -0.026858 | -0.023362 | 0.0044249 | 0.018923 | -0.012575 | 0.027553 | 0.043943 | 0.00091673 | 0.047647 | 0.083459 | 0.042614 | 0.051108 | 0.11165 | 0.12399 | 0.2839 | 0.028521 | -121.7972 | -24.0745 | -121.9141 | 0.057037 | 0.15564 | 0.14969 | -122.8123 | 122.3567 | 0.042982 | 122.4116 | 122.3793 | 0.022587 | 0.055325 | 0.21524 | -0.48416 | -0.011628 | 0.53097 | 0.41405 | 0.89821 | 0.086978 | 0.081022 | 122.4398 | 122.4522 | 122.6121 | 122.3708 | -0.040144 | 122.3852 | 122.4838 | 122.4779 | 98.2537 | -122.881
1946.4688 | 122.5479 | -122.3694 | 0.11444 | 1.4211e-13 | 0.0019381 | -0.009936 | -0.026858 | -0.023789 | 0.0039977 | 0.018923 | -0.012361 | 0.027553 | 0.043516 | 0.00070293 | 0.047433 | 0.092615 | 0.033457 | 0.051108 | 0.10707 | 0.11941 | 0.27932 | 0.023942 | -121.8018 | -24.4728 | -121.9141 | 0.057037 | 0.15564 | 0.14511 | -122.8215 | 122.3933 | -0.007373 | 122.462 | 122.4205 | 0.027166 | 0.00497 | 0.16488 | -0.45212 | -0.057404 | 0.56759 | 0.45525 | 0.90737 | 0.041202 | 0.030668 | 122.4765 | 122.4888 | 122.6487 | 122.4028 | -0.090499 | 122.4264 | 122.525 | 122.5145 | 97.8965 | -122.9359
1948.1875 | 122.5388 | -122.3648 | 0.10529 | 1.4211e-13 | 0.0023653 | -0.0097224 | -0.027072 | -0.023576 | 0.0042113 | 0.011293 | -0.012361 | 0.027767 | 0.043943 | 0.00091673 | 0.048074 | 0.092615 | 0.033457 | 0.041952 | 0.11165 | 0.12857 | 0.2839 | 0.0331 | -121.7972 | -24.7613 | -121.9141 | 0.057037 | 0.15107 | 0.14053 | -122.8215 | 122.3979 | 0.006361 | 122.4574 | 122.4068 | 0.008852 | 0.023283 | 0.17862 | -0.4567 | -0.048249 | 0.56759 | 0.45067 | 0.90737 | 0.045779 | 0.035244 | 122.4765 | 122.4934 | 122.6487 | 122.3983 | -0.072186 | 122.4218 | 122.5159 | 122.5053 | 97.6035 | -122.9268
1949.9688 | 122.5021 | -122.374 | 0.09613 | 1.4211e-13 | 0.0023653 | -0.0095086 | -0.026644 | -0.023362 | 0.0042113 | 0.011293 | -0.012575 | 0.027553 | 0.043729 | 0.00070293 | 0.04786 | 0.088037 | 0.033457 | 0.051108 | 0.10707 | 0.12399 | 0.28848 | 0.0331 | -121.7835 | -25.1413 | -121.9096 | 0.057037 | 0.14649 | 0.14511 | -122.8215 | 122.4071 | 0.010938 | 122.462 | 122.4251 | 0.018008 | 0.02786 | 0.19235 | -0.44754 | -0.039093 | 0.59049 | 0.46441 | 0.91195 | 0.050356 | 0.048979 | 122.481 | 122.498 | 122.6624 | 122.4074 | -0.06303 | 122.431 | 122.5204 | 122.5191 | 97.2326 | -122.9176
1951.75 | 122.4976 | -122.3969 | 0.10986 | 1.4211e-13 | 0.0021517 | -0.009936 | -0.027072 | -0.023362 | 0.0039977 | 0.0036627 | -0.012361 | 0.02734 | 0.043516 | 0.00027553 | 0.048074 | 0.097194 | 0.0243 | 0.055687 | 0.10707 | 0.13315 | 0.27932 | 0.0331 | -121.7835 | -25.5122 | -121.9004 | 0.057037 | 0.15564 | 0.14511 | -122.8215 | 122.43 | -0.002795 | 122.494 | 122.4525 | 0.022587 | 0.023285 | 0.16946 | -0.42465 | -0.052826 | 0.61337 | 0.49645 | 0.92111 | 0.04578 | 0.035246 | 122.5039 | 122.53 | 122.6762 | 122.4212 | -0.076763 | 122.4539 | 122.5525 | 122.542 | 96.8846 | -122.9314
1953.5156 | 122.5479 | -122.3831 | 0.10529 | 1.4211e-13 | 0.0021517 | -0.009295 | -0.02643 | -0.024003 | 0.0039977 | 0.011293 | -0.012788 | 0.027767 | 0.043516 | 0.00091673 | 0.047433 | 0.092615 | 0.038035 | 0.051108 | 0.10707 | 0.12399 | 0.27932 | 0.0331 | -121.7789 | -25.8327 | -121.9096 | 0.061616 | 0.15564 | 0.14969 | -122.8261 | 122.4162 | 0.001782 | 122.4757 | 122.4342 | 0.018008 | 0.018704 | 0.17404 | -0.44297 | -0.04367 | 0.60422 | 0.47356 | 0.91653 | 0.050357 | 0.044401 | 122.4902 | 122.5071 | 122.6624 | 122.4212 | -0.072186 | 122.4447 | 122.5388 | 122.5328 | 96.5504 | -122.9314
1955.2969 | 122.525 | -122.3969 | 0.10529 | 1.4211e-13 | 0.0021517 | -0.0097224 | -0.026858 | -0.023789 | 0.0039977 | 0.018923 | -0.012788 | 0.027553 | 0.043729 | 0.00070293 | 0.047647 | 0.097194 | 0.038035 | 0.051108 | 0.10249 | 0.12857 | 0.2839 | 0.0331 | -121.7743 | -26.2036 | -121.905 | 0.057037 | 0.15564 | 0.14969 | -122.8123 | 122.43 | -0.002796 | 122.494 | 122.448 | 0.018008 | 0.023283 | 0.17862 | -0.4155 | -0.048249 | 0.62253 | 0.49187 | 0.90737 | 0.050357 | 0.044401 | 122.4993 | 122.5254 | 122.6808 | 122.4349 | -0.072186 | 122.4539 | 122.5525 | 122.5465 | 96.1933 | -122.9176
1957.0781 | 122.5113 | -122.3877 | 0.10986 | 1.4211e-13 | 0.0023653 | -0.0097224 | -0.02643 | -0.023789 | 0.0039977 | 0.011293 | -0.012575 | 0.027767 | 0.043943 | 0.00070293 | 0.04786 | 0.083459 | 0.038035 | 0.051108 | 0.10249 | 0.12857 | 0.27932 | 0.0331 | -121.7743 | -26.6615 | -121.9004 | 0.061616 | 0.14649 | 0.14969 | -122.8215 | 122.4208 | -0.007373 | 122.4712 | 122.4388 | 0.018008 | 0.018706 | 0.16946 | -0.43381 | -0.048247 | 0.61337 | 0.4873 | 0.92111 | 0.036623 | 0.039824 | 122.4902 | 122.5163 | 122.667 | 122.4257 | -0.076763 | 122.4493 | 122.5342 | 122.5374 | 95.7262 | -122.9314
1958.8438 | 122.6349 | -122.374 | 0.073242 | 1.4211e-13 | 0.0023653 | -0.009936 | -0.027072 | -0.023362 | 0.0039977 | 0.0036627 | -0.012361 | 0.027553 | 0.043516 | 0.00091673 | 0.047647 | 0.083459 | 0.033457 | 0.055687 | 0.10249 | 0.13315 | 0.27932 | 0.0331 | -121.7652 | -27.1056 | -121.905 | 0.061616 | 0.15564 | 0.14053 | -122.8169 | 122.4071 | 0.029248 | 122.4574 | 122.4296 | 0.022587 | 0.059906 | 0.20608 | -0.44296 | -0.011626 | 0.6088 | 0.46898 | 0.91195 | 0.082401 | 0.067288 | 122.4765 | 122.5071 | 122.6533 | 122.4074 | -0.040142 | 122.4356 | 122.5296 | 122.5145 | 95.2684 | -122.8902
1960.5625 | 122.58 | -122.3557 | 0.086975 | 1.4211e-13 | 0.0019381 | -0.0095086 | -0.026644 | -0.023362 | 0.0042113 | 0.011293 | -0.012575 | 0.027553 | 0.043943 | 0.00070293 | 0.047647 | 0.088037 | 0.033457 | 0.041952 | 0.097912 | 0.12857 | 0.27932 | 0.037679 | -121.7606 | -27.4811 | -121.8958 | 0.052459 | 0.14649 | 0.14969 | -122.8215 | 122.3933 | 0.010937 | 122.4437 | 122.3976 | 0.004273 | 0.041594 | 0.19235 | -0.46585 | -0.034516 | 0.59507 | 0.45983 | 0.92568 | 0.059511 | 0.062712 | 122.4536 | 122.4842 | 122.635 | 122.3891 | -0.049296 | 122.4081 | 122.5021 | 122.5053 | 94.8746 | -122.9085
1962.3438 | 122.5708 | -122.3785 | 0.10986 | 1.4211e-13 | 0.0023653 | -0.009936 | -0.026217 | -0.023789 | 0.0039977 | 0.018923 | -0.012575 | 0.027767 | 0.043729 | 0.0011303 | 0.04786 | 0.092615 | 0.038035 | 0.04653 | 0.10707 | 0.12399 | 0.2839 | 0.0331 | -121.7652 | -27.8107 | -121.8958 | 0.052459 | 0.15107 | 0.14511 | -122.8215 | 122.4116 | -0.002795 | 122.4712 | 122.4251 | 0.01343 | 0.014127 | 0.17404 | -0.44296 | -0.057404 | 0.61338 | 0.48272 | 0.92568 | 0.041202 | 0.035246 | 122.4856 | 122.5025 | 122.6624 | 122.4166 | -0.076763 | 122.431 | 122.5296 | 122.5236 | 94.5678 | -122.9314
1964.0781 | 122.5616 | -122.3694 | 0.091553 | 1.4211e-13 | 0.0021517 | -0.0097224 | -0.02643 | -0.023576 | 0.0039977 | 0.011293 | -0.012361 | 0.027553 | 0.043943 | 0.00091673 | 0.04786 | 0.088037 | 0.038035 | 0.055687 | 0.10249 | 0.12399 | 0.27475 | 0.028521 | -121.7514 | -28.1083 | -121.8912 | 0.061616 | 0.16022 | 0.13595 | -122.8215 | 122.3979 | 0.010937 | 122.4574 | 122.4251 | 0.027166 | 0.032437 | 0.18319 | -0.45212 | -0.029937 | 0.61796 | 0.47814 | 0.93026 | 0.068669 | 0.044399 | 122.4719 | 122.4934 | 122.6441 | 122.4074 | -0.063032 | 122.431 | 122.5296 | 122.5053 | 94.261 | -122.9131
1965.8594 | 122.6349 | -122.3282 | 0.064087 | 1.4211e-13 | 0.0021517 | -0.0095086 | -0.026858 | -0.023789 | 0.0039977 | 0.011293 | -0.012575 | 0.02734 | 0.043516 | 0.00070293 | 0.047647 | 0.097194 | 0.038035 | 0.055687 | 0.11165 | 0.12399 | 0.27475 | 0.028521 | -121.7468 | -28.5113 | -121.8912 | 0.04788 | 0.16022 | 0.14053 | -122.8215 | 122.3567 | 0.04756 | 122.4254 | 122.3839 | 0.027166 | 0.059903 | 0.21066 | -0.49332 | -0.016207 | 0.58134 | 0.43694 | 0.93026 | 0.096135 | 0.076443 | 122.4398 | 122.4522 | 122.6029 | 122.3662 | -0.035566 | 122.3761 | 122.4884 | 122.4687 | 93.8169 | -122.8856
1967.6562 | 122.6166 | -122.3648 | 0.07782 | 1.4211e-13 | 0.0021517 | -0.0097224 | -0.026858 | -0.023789 | 0.0042113 | 0.018923 | -0.012788 | 0.027553 | 0.043729 | 0.00070293 | 0.04786 | 0.088037 | 0.042614 | 0.041952 | 0.10707 | 0.13315 | 0.27932 | 0.028521 | -121.7423 | -28.8409 | -121.8867 | 0.057037 | 0.15564 | 0.14511 | -122.8261 | 122.3933 | 0.029248 | 122.4528 | 122.4068 | 0.013431 | 0.055328 | 0.2015 | -0.46128 | -0.020783 | 0.62254 | 0.47814 | 0.93942 | 0.077823 | 0.067289 | 122.4719 | 122.498 | 122.6441 | 122.4074 | -0.049299 | 122.4218 | 122.5204 | 122.5099 | 93.5239 | -122.9039
1969.3906 | 122.5525 | -122.3969 | 0.09613 | 1.4211e-13 | 0.0021517 | -0.009295 | -0.026644 | -0.023362 | 0.0042113 | -0.0039678 | -0.012575 | 0.02734 | 0.043943 | 0.00070293 | 0.048074 | 0.088037 | 0.038035 | 0.04653 | 0.10707 | 0.12857 | 0.2839 | 0.023942 | -121.7331 | -29.2393 | -121.8821 | 0.052459 | 0.15107 | 0.13595 | -122.8307 | 122.4208 | 0.010938 | 122.4849 | 122.4434 | 0.022588 | 0.032439 | 0.18777 | -0.43381 | -0.043671 | 0.66374 | 0.51477 | 0.94858 | 0.054935 | 0.039822 | 122.5039 | 122.5254 | 122.6808 | 122.4349 | -0.072188 | 122.4493 | 122.5479 | 122.5328 | 93.1576 | -122.9268
1971.1562 | 122.5159 | -122.374 | 0.091553 | 1.4211e-13 | 0.0025791 | -0.009295 | -0.026644 | -0.023576 | 0.0042113 | 0.0036627 | -0.012575 | 0.027553 | 0.043729 | 0.00048933 | 0.048074 | 0.092615 | 0.038035 | 0.051108 | 0.10249 | 0.13315 | 0.27932 | 0.023942 | -121.7285 | -29.7521 | -121.8821 | 0.057037 | 0.14649 | 0.14511 | -122.8307 | 122.3979 | 0.010937 | 122.4666 | 122.4251 | 0.027166 | 0.041595 | 0.18777 | -0.4567 | -0.034516 | 0.64543 | 0.49188 | 0.94858 | 0.054933 | 0.053556 | 122.4765 | 122.5071 | 122.6533 | 122.412 | -0.067611 | 122.431 | 122.5204 | 122.5191 | 92.6219 | -122.9222
1972.9375 | 122.5342 | -122.3923 | 0.086975 | 1.4211e-13 | 0.0021517 | -0.0095086 | -0.026858 | -0.023789 | 0.0042113 | 0.0036627 | -0.012575 | 0.027553 | 0.043729 | 0.00091673 | 0.04786 | 0.10177 | 0.033457 | 0.051108 | 0.10707 | 0.12857 | 0.27932 | 0.028521 | -121.7331 | -30.1917 | -121.8775 | 0.043302 | 0.15564 | 0.14053 | -122.8261 | 122.4208 | 0.020093 | 122.494 | 122.4434 | 0.022587 | 0.041594 | 0.19235 | -0.43381 | -0.043673 | 0.65916 | 0.51477 | 0.94858 | 0.068668 | 0.053555 | 122.4993 | 122.5208 | 122.6716 | 122.4257 | -0.058454 | 122.4356 | 122.5479 | 122.5328 | 92.2006 | -122.9131
1974.7188 | 122.612 | -122.3602 | 0.091553 | 1.4211e-13 | 0.0021517 | -0.0095086 | -0.026858 | -0.023576 | 0.0039977 | -0.0039678 | -0.012788 | 0.027767 | 0.043729 | 0.00070293 | 0.048074 | 0.097194 | 0.038035 | 0.041952 | 0.11165 | 0.12857 | 0.27932 | 0.028521 | -121.7102 | -30.3244 | -121.8775 | 0.057037 | 0.15564 | 0.14053 | -122.8307 | 122.3888 | 0.020094 | 122.4574 | 122.4022 | 0.013431 | 0.037016 | 0.18777 | -0.47043 | -0.034516 | 0.65001 | 0.48272 | 0.95316 | 0.06409 | 0.048977 | 122.4719 | 122.4888 | 122.6396 | 122.3983 | -0.063032 | 122.4173 | 122.5159 | 122.5008 | 92.0358 | -122.9222
1976.4375 | 122.5204 | -122.4014 | 0.091553 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.027072 | -0.023576 | 0.0042113 | 0.011293 | -0.012361 | 0.02734 | 0.043943 | 0.00070293 | 0.048074 | 0.092615 | 0.042614 | 0.051108 | 0.11622 | 0.12399 | 0.27017 | 0.037679 | -121.7148 | -30.6999 | -121.8775 | 0.061616 | 0.14649 | 0.14053 | -122.8352 | 122.4391 | 0.024672 | 122.494 | 122.4525 | 0.013429 | 0.032437 | 0.17861 | -0.43381 | -0.029937 | 0.68663 | 0.52392 | 0.95773 | 0.054933 | 0.048977 | 122.5177 | 122.5254 | 122.6716 | 122.444 | -0.053874 | 122.463 | 122.5479 | 122.542 | 91.7015 | -122.9268
1978.2344 | 122.6395 | -122.3465 | 0.064087 | 1.4211e-13 | 0.0025791 | -0.009295 | -0.026858 | -0.023576 | 0.0039977 | 0.011293 | -0.012361 | 0.027553 | 0.043516 | 0.00027553 | 0.04786 | 0.092615 | 0.038035 | 0.051108 | 0.11165 | 0.11941 | 0.27932 | 0.0331 | -121.7056 | -31.0479 | -121.8683 | 0.057037 | 0.15564 | 0.14053 | -122.8307 | 122.3796 | 0.04756 | 122.4391 | 122.3976 | 0.018008 | 0.055324 | 0.21524 | -0.48416 | -0.00705 | 0.64086 | 0.47815 | 0.96231 | 0.091556 | 0.076443 | 122.4581 | 122.4659 | 122.6258 | 122.3845 | -0.030987 | 122.4035 | 122.5021 | 122.487 | 91.2986 | -122.8947
1980 | 122.6257 | -122.3511 | 0.086975 | 1.4211e-13 | 0.0023653 | -0.0095086 | -0.026644 | -0.023576 | 0.0037841 | 0.0036627 | -0.012361 | 0.027767 | 0.043516 | 0.00070293 | 0.048074 | 0.097194 | 0.038035 | 0.051108 | 0.097912 | 0.12857 | 0.27932 | 0.028521 | -121.7148 | -31.3684 | -121.8729 | 0.057037 | 0.15107 | 0.14969 | -122.8352 | 122.3796 | 0.010937 | 122.4483 | 122.4022 | 0.022587 | 0.041594 | 0.19235 | -0.48417 | -0.029938 | 0.63628 | 0.47815 | 0.96231 | 0.06409 | 0.062712 | 122.449 | 122.4796 | 122.6304 | 122.3891 | -0.058454 | 122.4081 | 122.5021 | 122.5008 | 90.9827 | -122.9222
1981.7656 | 122.6532 | -122.3557 | 0.054932 | 1.4211e-13 | 0.0023653 | -0.0095086 | -0.026858 | -0.023789 | 0.0039977 | 0.011293 | -0.012575 | 0.02734 | 0.043516 | 0.00070293 | 0.047433 | 0.092615 | 0.033457 | 0.055687 | 0.10707 | 0.12857 | 0.28848 | 0.028521 | -121.6965 | -31.5973 | -121.8683 | 0.061616 | 0.15564 | 0.14969 | -122.8352 | 122.3842 | 0.052136 | 122.4483 | 122.4113 | 0.027166 | 0.073637 | 0.23355 | -0.47959 | 0.006684 | 0.65917 | 0.4873 | 0.96689 | 0.10071 | 0.094755 | 122.4627 | 122.4842 | 122.6441 | 122.3891 | -0.026411 | 122.4173 | 122.5113 | 122.5053 | 90.7583 | -122.8902
1983.5625 | 122.5388 | -122.3969 | 0.11444 | 1.4211e-13 | 0.0023653 | -0.0097224 | -0.026858 | -0.023576 | 0.0042113 | -0.0039678 | -0.012788 | 0.027553 | 0.043729 | 0.00091673 | 0.04786 | 0.097194 | 0.047193 | 0.051108 | 0.10707 | 0.13315 | 0.2839 | 0.0331 | -121.6965 | -31.8995 | -121.8638 | 0.052459 | 0.15107 | 0.14511 | -122.8352 | 122.43 | -0.007373 | 122.494 | 122.448 | 0.018008 | 0.018707 | 0.16946 | -0.43839 | -0.061982 | 0.70037 | 0.53308 | 0.97147 | 0.036624 | 0.030668 | 122.5039 | 122.53 | 122.6808 | 122.444 | -0.081341 | 122.4493 | 122.5479 | 122.542 | 90.4973 | -122.9497
1985.2812 | 122.6486 | -122.3648 | 0.064087 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.026644 | -0.023789 | 0.0039977 | 0.0036627 | -0.012148 | 0.027553 | 0.043729 | 0.00091673 | 0.04786 | 0.092615 | 0.038035 | 0.055687 | 0.10707 | 0.12399 | 0.27932 | 0.028521 | -121.6827 | -32.0552 | -121.8592 | 0.061616 | 0.15564 | 0.14053 | -122.8307 | 122.3933 | 0.042981 | 122.4574 | 122.4205 | 0.027166 | 0.059903 | 0.21524 | -0.46585 | -0.002471 | 0.68206 | 0.50562 | 0.97147 | 0.091556 | 0.076443 | 122.4719 | 122.4888 | 122.6441 | 122.4028 | -0.035566 | 122.4264 | 122.5204 | 122.5053 | 90.3096 | -122.8947
1987.0781 | 122.6669 | -122.3694 | 0.064087 | 1.4211e-13 | 0.0023653 | -0.0095086 | -0.027072 | -0.023148 | 0.0042113 | 0.0036627 | -0.013002 | 0.027767 | 0.043943 | 0.00070293 | 0.048074 | 0.097194 | 0.042614 | 0.051108 | 0.097912 | 0.13315 | 0.27475 | 0.0331 | -121.6782 | -32.4764 | -121.8546 | 0.057037 | 0.16022 | 0.14969 | -122.8444 | 122.4025 | 0.033825 | 122.4666 | 122.4205 | 0.018008 | 0.069061 | 0.21066 | -0.47501 | -0.00705 | 0.69122 | 0.51477 | 0.98979 | 0.096135 | 0.0856 | 122.4673 | 122.5025 | 122.6441 | 122.412 | -0.030987 | 122.4264 | 122.5296 | 122.5191 | 89.893 | -122.9085
1988.7812 | 122.5296 | -122.3923 | 0.11444 | 1.4211e-13 | 0.0027927 | -0.0097224 | -0.027072 | -0.023576 | 0.0039977 | 0.011293 | -0.012361 | 0.027767 | 0.043516 | 0.00091673 | 0.04786 | 0.097194 | 0.042614 | 0.060265 | 0.10249 | 0.12857 | 0.27932 | 0.0331 | -121.6827 | -32.6687 | -121.8546 | 0.057037 | 0.15564 | 0.14511 | -122.8352 | 122.4254 | -0.011951 | 122.4895 | 122.4525 | 0.027165 | 0.014128 | 0.16488 | -0.44297 | -0.057404 | 0.70953 | 0.53766 | 0.98063 | 0.041202 | 0.030668 | 122.4948 | 122.5208 | 122.6716 | 122.4349 | -0.081341 | 122.4493 | 122.5479 | 122.5374 | 89.7235 | -122.9497
1990.5625 | 122.5891 | -122.3831 | 0.091553 | 1.4211e-13 | 0.0021517 | -0.0095086 | -0.026858 | -0.023148 | 0.0042113 | 0.011293 | -0.012361 | 0.027981 | 0.043943 | 0.00048933 | 0.048074 | 0.092615 | 0.033457 | 0.051108 | 0.11165 | 0.13315 | 0.27932 | 0.0331 | -121.669 | -33.0305 | -121.8546 | 0.057037 | 0.14191 | 0.14969 | -122.8352 | 122.4162 | 0.020094 | 122.4757 | 122.4342 | 0.018008 | 0.041595 | 0.18777 | -0.45212 | -0.034516 | 0.71411 | 0.52851 | 0.98063 | 0.050354 | 0.058134 | 122.4948 | 122.5163 | 122.6624 | 122.4166 | -0.058453 | 122.4402 | 122.525 | 122.5328 | 89.3527 | -122.9268
1992.2812 | 122.5616 | -122.3923 | 0.10071 | 1.4211e-13 | 0.0023653 | -0.0095086 | -0.027072 | -0.023789 | 0.0044249 | 0.0036627 | -0.012361 | 0.027553 | 0.043516 | 0.00070293 | 0.04786 | 0.097194 | 0.033457 | 0.041952 | 0.11165 | 0.13773 | 0.27932 | 0.0331 | -121.6644 | -33.3693 | -121.85 | 0.066194 | 0.15107 | 0.14511 | -122.8352 | 122.4254 | 0.010939 | 122.4895 | 122.4342 | 0.008852 | 0.037019 | 0.17862 | -0.44297 | -0.034514 | 0.72784 | 0.54224 | 0.98521 | 0.050357 | 0.044401 | 122.5039 | 122.53 | 122.6716 | 122.4257 | -0.067608 | 122.4585 | 122.5433 | 122.5374 | 89.023 | -122.9359
1994.0625 | 122.6486 | -122.374 | 0.086975 | 1.4211e-13 | 0.0023653 | -0.0097224 | -0.026858 | -0.023576 | 0.0039977 | 0.0036627 | -0.012575 | 0.02734 | 0.043729 | 0.00070293 | 0.048288 | 0.092615 | 0.038035 | 0.051108 | 0.10249 | 0.12857 | 0.2839 | 0.028521 | -121.6553 | -33.5799 | -121.8455 | 0.04788 | 0.15564 | 0.14053 | -122.8444 | 122.4025 | 0.015515 | 122.4666 | 122.4251 | 0.022587 | 0.041594 | 0.19693 | -0.47044 | -0.039095 | 0.71869 | 0.52851 | 0.99894 | 0.068668 | 0.053555 | 122.4765 | 122.5025 | 122.6579 | 122.412 | -0.058454 | 122.4218 | 122.5296 | 122.5145 | 88.7941 | -122.9314
1995.8281 | 122.6532 | -122.3923 | 0.082397 | 1.4211e-13 | 0.0023653 | -0.009295 | -0.026858 | -0.023362 | 0.0039977 | 0.0036627 | -0.012148 | 0.02734 | 0.043729 | 0.00091673 | 0.04786 | 0.097194 | 0.038035 | 0.041952 | 0.10707 | 0.12857 | 0.27932 | 0.023942 | -121.6461 | -34.0469 | -121.8409 | 0.052459 | 0.16022 | 0.14511 | -122.8444 | 122.4162 | 0.024671 | 122.4895 | 122.4342 | 0.01801 | 0.046172 | 0.19693 | -0.45212 | -0.029938 | 0.74616 | 0.5514 | 1.0035 | 0.077825 | 0.062712 | 122.4993 | 122.5208 | 122.6716 | 122.4303 | -0.058455 | 122.4447 | 122.5525 | 122.5374 | 88.3453 | -122.9268
1997.5469 | 122.6349 | -122.3602 | 0.07782 | 1.4211e-13 | 0.0023653 | -0.0095086 | -0.026858 | -0.023576 | 0.0039977 | 0.011293 | -0.012788 | 0.027553 | 0.043943 | 0.00070293 | 0.048074 | 0.097194 | 0.038035 | 0.051108 | 0.10707 | 0.11941 | 0.27932 | 0.0331 | -121.6461 | -34.3674 | -121.8363 | 0.057037 | 0.14649 | 0.14969 | -122.8444 | 122.3933 | 0.029248 | 122.4574 | 122.4113 | 0.018008 | 0.041591 | 0.2015 | -0.48417 | -0.020783 | 0.71411 | 0.52393 | 1.0081 | 0.068666 | 0.071867 | 122.4673 | 122.4796 | 122.6396 | 122.3983 | -0.04472 | 122.4173 | 122.5067 | 122.5099 | 87.9928 | -122.9222
1999.3281 | 122.5433 | -122.3969 | 0.1236 | 1.4211e-13 | 0.0021517 | -0.0095086 | -0.026644 | -0.023576 | 0.0042113 | 0.011293 | -0.012575 | 0.02734 | 0.043729 | 0.00048933 | 0.048288 | 0.092615 | 0.047193 | 0.04653 | 0.10707 | 0.13315 | 0.2839 | 0.028521 | -121.6415 | -34.6055 | -121.8317 | 0.061616 | 0.16022 | 0.14053 | -122.8444 | 122.4254 | -0.016528 | 122.4895 | 122.4434 | 0.018009 | 0.009552 | 0.16031 | -0.44755 | -0.06198 | 0.75531 | 0.56513 | 1.0127 | 0.036626 | 0.016934 | 122.5039 | 122.53 | 122.6808 | 122.444 | -0.095075 | 122.4585 | 122.5571 | 122.5374 | 87.7913 | -122.968
2001.0469 | 122.6212 | -122.3923 | 0.07782 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.026858 | -0.023362 | 0.0039977 | 0.011293 | -0.012575 | 0.027553 | 0.043516 | 0.00048933 | 0.04786 | 0.092615 | 0.047193 | 0.041952 | 0.11165 | 0.12399 | 0.27932 | 0.0331 | -121.6278 | -35.1367 | -121.8363 | 0.052459 | 0.16022 | 0.14969 | -122.849 | 122.4254 | 0.033827 | 122.4849 | 122.4342 | 0.008852 | 0.04617 | 0.2015 | -0.4567 | -0.025361 | 0.76447 | 0.55598 | 1.0127 | 0.082402 | 0.071867 | 122.5039 | 122.5163 | 122.6716 | 122.4395 | -0.04472 | 122.4447 | 122.5525 | 122.542 | 87.2556 | -122.9268
2002.8281 | 122.5616 | -122.406 | 0.09613 | 1.4211e-13 | 0.0021517 | -0.009295 | -0.026858 | -0.023362 | 0.0042113 | 0.026554 | -0.012361 | 0.027553 | 0.043943 | 0.00091673 | 0.04786 | 0.097194 | 0.028878 | 0.055687 | 0.10707 | 0.12399 | 0.27932 | 0.0331 | -121.6232 | -35.2237 | -121.8363 | 0.057037 | 0.15107 | 0.14053 | -122.8398 | 122.4391 | 0.010938 | 122.5032 | 122.4617 | 0.022587 | 0.02786 | 0.18319 | -0.43381 | -0.039093 | 0.78278 | 0.56971 | 1.0035 | 0.054935 | 0.0444 | 122.5131 | 122.53 | 122.6853 | 122.4349 | -0.06303 | 122.463 | 122.5571 | 122.5465 | 87.1824 | -122.9359
2004.6094 | 122.6624 | -122.3648 | 0.073242 | 1.4211e-13 | 0.0023653 | -0.0095086 | -0.026644 | -0.024003 | 0.0042113 | 0.0036627 | -0.012361 | 0.027767 | 0.043729 | 0.00070293 | 0.048288 | 0.097194 | 0.038035 | 0.051108 | 0.11165 | 0.12399 | 0.27932 | 0.0331 | -121.6095 | -35.3976 | -121.818 | 0.04788 | 0.15107 | 0.15427 | -122.8444 | 122.3979 | 0.038405 | 122.462 | 122.4159 | 0.018008 | 0.050748 | 0.20608 | -0.47959 | -0.025362 | 0.75532 | 0.54682 | 1.0264 | 0.077823 | 0.081024 | 122.4765 | 122.4888 | 122.6441 | 122.4028 | -0.040142 | 122.4127 | 122.5159 | 122.5191 | 86.9672 | -122.9176
2006.3906 | 122.5388 | -122.406 | 0.11444 | 1.4211e-13 | 0.0021517 | -0.009936 | -0.026644 | -0.023362 | 0.0042113 | 0.0036627 | -0.012575 | 0.027767 | 0.044157 | 0.00048933 | 0.048074 | 0.10177 | 0.042614 | 0.04653 | 0.097912 | 0.12857 | 0.27932 | 0.028521 | -121.6049 | -35.8555 | -121.818 | 0.057037 | 0.15107 | 0.14511 | -122.8444 | 122.4345 | -0.016529 | 122.5078 | 122.4525 | 0.018009 | 0.014128 | 0.16488 | -0.43839 | -0.057404 | 0.8011 | 0.58802 | 1.0264 | 0.036624 | 0.030668 | 122.5039 | 122.5346 | 122.6853 | 122.4486 | -0.08592 | 122.463 | 122.5571 | 122.5511 | 86.5505 | -122.9588
2008.1719 | 122.6166 | -122.3831 | 0.054932 | 1.4211e-13 | 0.0019381 | -0.0097224 | -0.026858 | -0.023576 | 0.0042113 | -0.0039678 | -0.012575 | 0.027767 | 0.044157 | 0.00070293 | 0.048288 | 0.10635 | 0.042614 | 0.04653 | 0.10707 | 0.13315 | 0.27932 | 0.028521 | -121.6003 | -36.0478 | -121.818 | 0.052459 | 0.15564 | 0.14969 | -122.8536 | 122.4116 | 0.052136 | 122.4895 | 122.4296 | 0.018009 | 0.078216 | 0.22439 | -0.47044 | -0.002473 | 0.78279 | 0.56514 | 1.0356 | 0.10071 | 0.094755 | 122.4902 | 122.5163 | 122.6624 | 122.4257 | -0.026411 | 122.4356 | 122.5388 | 122.5328 | 86.3353 | -122.9085
2009.9531 | 122.5708 | -122.3785 | 0.09613 | 1.4211e-13 | 0.0021517 | -0.0097224 | -0.026644 | -0.023362 | 0.0039977 | 0.011293 | -0.011934 | 0.027553 | 0.043516 | 0.00091673 | 0.048074 | 0.097194 | 0.033457 | 0.055687 | 0.10707 | 0.11941 | 0.2839 | 0.0331 | -121.5912 | -36.3546 | -121.8042 | 0.061616 | 0.16022 | 0.14053 | -122.849 | 122.4116 | 0.010938 | 122.4757 | 122.4342 | 0.022587 | 0.023281 | 0.18777 | -0.47044 | -0.034514 | 0.78737 | 0.57429 | 1.0447 | 0.064092 | 0.0444 | 122.4856 | 122.498 | 122.6624 | 122.412 | -0.06303 | 122.4402 | 122.5388 | 122.5191 | 86.0239 | -122.9451
2011.6719 | 122.6669 | -122.374 | 0.059509 | 1.4211e-13 | 0.0021517 | -0.0095086 | -0.026644 | -0.023789 | 0.0039977 | 0.011293 | -0.012361 | 0.027126 | 0.043943 | 0.00091673 | 0.048288 | 0.092615 | 0.033457 | 0.055687 | 0.11165 | 0.12857 | 0.27932 | 0.0331 | -121.5866 | -36.6293 | -121.8088 | 0.052459 | 0.14649 | 0.14511 | -122.8581 | 122.4071 | 0.052138 | 122.4666 | 122.4296 | 0.022587 | 0.06906 | 0.21982 | -0.48417 | -0.00705 | 0.78737 | 0.56514 | 1.0493 | 0.086977 | 0.0856 | 122.4856 | 122.5025 | 122.6533 | 122.4074 | -0.026409 | 122.4264 | 122.5204 | 122.5191 | 85.7446 | -122.9176
2013.4688 | 122.5342 | -122.4197 | 0.11444 | 1.4211e-13 | 0.0023653 | -0.0095086 | -0.026644 | -0.023789 | 0.0044249 | 0.0036627 | -0.012361 | 0.027767 | 0.043943 | 0.00091673 | 0.048288 | 0.097194 | 0.038035 | 0.04653 | 0.10249 | 0.12857 | 0.2839 | 0.028521 | -121.5683 | -36.9773 | -121.7997 | 0.04788 | 0.14649 | 0.14053 | -122.849 | 122.4483 | -0.011951 | 122.5169 | 122.4663 | 0.018009 | 0.014128 | 0.16946 | -0.42924 | -0.066561 | 0.85146 | 0.62007 | 1.0493 | 0.032045 | 0.026089 | 122.5222 | 122.5483 | 122.7036 | 122.4578 | -0.08592 | 122.4676 | 122.5662 | 122.5603 | 85.4424 | -122.9634
2015.1875 | 122.6761 | -122.3694 | 0.059509 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.026217 | -0.023789 | 0.0039977 | 0.011293 | -0.012575 | 0.027767 | 0.043943 | 0.00091673 | 0.048074 | 0.10177 | 0.042614 | 0.055687 | 0.10707 | 0.12857 | 0.2839 | 0.014784 | -121.5637 | -37.1467 | -121.7997 | 0.052459 | 0.15564 | 0.14511 | -122.8581 | 122.3842 | 0.047559 | 122.4712 | 122.4251 | 0.040903 | 0.06906 | 0.22439 | -0.48875 | -0.00705 | 0.80569 | 0.56972 | 1.0585 | 0.096134 | 0.0856 | 122.4765 | 122.498 | 122.6533 | 122.412 | -0.044725 | 122.4218 | 122.525 | 122.5145 | 85.2227 | -122.9176
2016.9531 | 122.5937 | -122.4197 | 0.10529 | 1.4211e-13 | 0.0021517 | -0.0097224 | -0.026858 | -0.023362 | 0.0039977 | 0.0036627 | -0.012361 | 0.027767 | 0.043729 | 0.00070293 | 0.048288 | 0.097194 | 0.038035 | 0.051108 | 0.10707 | 0.12399 | 0.27475 | 0.023942 | -121.5545 | -37.426 | -121.7951 | 0.057037 | 0.16022 | 0.14511 | -122.849 | 122.4437 | 0.001782 | 122.5169 | 122.4708 | 0.027166 | 0.018704 | 0.16946 | -0.42924 | -0.048249 | 0.8652 | 0.62465 | 1.0539 | 0.054936 | 0.039823 | 122.5268 | 122.5437 | 122.6945 | 122.4578 | -0.081344 | 122.4768 | 122.58 | 122.5648 | 84.9937 | -122.9543
2018.7344 | 122.6761 | -122.374 | 0.068665 | 1.4211e-13 | 0.0025791 | -0.009295 | -0.026644 | -0.023576 | 0.0044249 | 0.0036627 | -0.012361 | 0.027553 | 0.044157 | 0.00070293 | 0.048501 | 0.092615 | 0.047193 | 0.055687 | 0.10249 | 0.12857 | 0.27017 | 0.028521 | -121.5454 | -37.7374 | -121.7905 | 0.057037 | 0.15107 | 0.14969 | -122.8536 | 122.4025 | 0.033825 | 122.4666 | 122.4296 | 0.027166 | 0.059904 | 0.2015 | -0.47959 | -0.011628 | 0.82858 | 0.58345 | 1.063 | 0.0824 | 0.081022 | 122.4765 | 122.5025 | 122.6441 | 122.4212 | -0.040144 | 122.431 | 122.525 | 122.5236 | 84.6366 | -122.9222
2020.5156 | 122.612 | -122.374 | 0.086975 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.02643 | -0.023362 | 0.0042113 | 0.011293 | -0.012361 | 0.027553 | 0.044157 | 0.00091673 | 0.048715 | 0.097194 | 0.042614 | 0.04653 | 0.10249 | 0.12857 | 0.27932 | 0.023942 | -121.5408 | -38.0258 | -121.7859 | 0.052459 | 0.15107 | 0.14053 | -122.8536 | 122.3979 | 0.015515 | 122.4712 | 122.4205 | 0.022588 | 0.041594 | 0.19235 | -0.47959 | -0.034516 | 0.83316 | 0.58803 | 1.0676 | 0.06409 | 0.053555 | 122.4765 | 122.5025 | 122.6533 | 122.4166 | -0.063033 | 122.4264 | 122.525 | 122.5145 | 84.3481 | -122.9405
2022.2344 | 122.6257 | -122.3923 | 0.07782 | 1.4211e-13 | 0.0023653 | -0.0095086 | -0.026858 | -0.023362 | 0.0039977 | 0.018923 | -0.012361 | 0.027767 | 0.043516 | 0.00091673 | 0.048074 | 0.097194 | 0.047193 | 0.055687 | 0.10249 | 0.12857 | 0.2839 | 0.014784 | -121.5362 | -38.4059 | -121.7768 | 0.061616 | 0.15564 | 0.14969 | -122.8536 | 122.4071 | 0.02467 | 122.4895 | 122.448 | 0.040903 | 0.050749 | 0.20608 | -0.46128 | -0.016204 | 0.85605 | 0.6155 | 1.0768 | 0.077823 | 0.071867 | 122.4948 | 122.5208 | 122.6762 | 122.4395 | -0.063036 | 122.4539 | 122.5479 | 122.542 | 83.9864 | -122.9314
2024.0312 | 122.6761 | -122.3557 | 0.068665 | 1.4211e-13 | 0.0023653 | -0.0097224 | -0.026858 | -0.023789 | 0.0042113 | 0.011293 | -0.012361 | 0.027553 | 0.043729 | 0.00091673 | 0.048288 | 0.092615 | 0.042614 | 0.055687 | 0.10249 | 0.12399 | 0.27932 | 0.0331 | -121.5362 | -38.8134 | -121.7722 | 0.052459 | 0.15107 | 0.15427 | -122.8581 | 122.3888 | 0.033825 | 122.4483 | 122.4113 | 0.022587 | 0.055325 | 0.21066 | -0.50248 | -0.016206 | 0.81943 | 0.58346 | 1.0859 | 0.0824 | 0.085601 | 122.4581 | 122.4796 | 122.635 | 122.3983 | -0.035565 | 122.4081 | 122.5067 | 122.5099 | 83.5423 | -122.9268
2025.7344 | 122.6166 | -122.374 | 0.068665 | 1.4211e-13 | 0.0023653 | -0.0097224 | -0.026858 | -0.023362 | 0.0039977 | 0.011293 | -0.012575 | 0.02734 | 0.043943 | 0.00091673 | 0.048074 | 0.092615 | 0.038035 | 0.055687 | 0.10249 | 0.12857 | 0.27475 | 0.028521 | -121.5225 | -39.1018 | -121.7768 | 0.052459 | 0.15107 | 0.15427 | -122.8536 | 122.4025 | 0.033825 | 122.4666 | 122.4296 | 0.027166 | 0.059904 | 0.20608 | -0.47959 | -0.016206 | 0.85147 | 0.59719 | 1.0768 | 0.0824 | 0.085601 | 122.4765 | 122.5025 | 122.6487 | 122.412 | -0.040144 | 122.4264 | 122.525 | 122.5282 | 83.2721 | -122.9222
2027.5156 | 122.58 | -122.4243 | 0.10529 | 1.4211e-13 | 0.0023653 | -0.0095086 | -0.026858 | -0.023789 | 0.0037841 | 0.011293 | -0.012361 | 0.027553 | 0.043729 | 0.00091673 | 0.04786 | 0.097194 | 0.033457 | 0.04653 | 0.10707 | 0.12399 | 0.27475 | 0.0331 | -121.5179 | -39.5322 | -121.763 | 0.057037 | 0.15107 | 0.14511 | -122.8581 | 122.4574 | 0.001782 | 122.5215 | 122.4708 | 0.01343 | 0.018704 | 0.16946 | -0.43382 | -0.048249 | 0.9064 | 0.66128 | 1.0951 | 0.045779 | 0.039823 | 122.5314 | 122.5483 | 122.6991 | 122.4578 | -0.072186 | 122.4814 | 122.5754 | 122.5694 | 82.8921 | -122.9634
2029.3281 | 122.6624 | -122.3648 | 0.059509 | 1.4211e-13 | 0.0023653 | -0.0095086 | -0.026858 | -0.023362 | 0.0042113 | 0.011293 | -0.012361 | 0.027553 | 0.043943 | 0.0011303 | 0.048074 | 0.092615 | 0.038035 | 0.051108 | 0.10707 | 0.13315 | 0.27932 | 0.0331 | -121.5088 | -39.7841 | -121.763 | 0.052459 | 0.14649 | 0.14053 | -122.8673 | 122.3979 | 0.047559 | 122.4574 | 122.4159 | 0.018008 | 0.073639 | 0.21982 | -0.50249 | -0.00705 | 0.85605 | 0.60177 | 1.1043 | 0.086977 | 0.081021 | 122.4719 | 122.498 | 122.6441 | 122.4028 | -0.026409 | 122.4173 | 122.5113 | 122.5053 | 82.5808 | -122.9268
2031.0469 | 122.5296 | -122.4243 | 0.10529 | 1.4211e-13 | 0.0023653 | -0.009295 | -0.026858 | -0.024003 | 0.0042113 | 0.0036627 | -0.012575 | 0.027553 | 0.043943 | 0.00048933 | 0.048074 | 0.097194 | 0.038035 | 0.060265 | 0.10249 | 0.13315 | 0.2839 | 0.023942 | -121.5042 | -40.1687 | -121.7493 | 0.04788 | 0.15564 | 0.14969 | -122.8627 | 122.4483 | -0.002796 | 122.5215 | 122.4846 | 0.036323 | 0.027862 | 0.17862 | -0.4384 | -0.057406 | 0.92014 | 0.67501 | 1.1134 | 0.050357 | 0.044401 | 122.5268 | 122.5575 | 122.7082 | 122.4624 | -0.081344 | 122.4722 | 122.58 | 122.574 | 82.2557 | -122.968
2032.8281 | 122.5433 | -122.4197 | 0.10529 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.02643 | -0.023362 | 0.0037841 | 0.011293 | -0.012361 | 0.02734 | 0.043943 | 0.00091673 | 0.048288 | 0.097194 | 0.042614 | 0.051108 | 0.10707 | 0.12399 | 0.2839 | 0.028521 | -121.4859 | -40.741 | -121.7539 | 0.052459 | 0.15107 | 0.13595 | -122.8536 | 122.4483 | 0.001782 | 122.5169 | 122.4708 | 0.022587 | 0.018704 | 0.17862 | -0.43382 | -0.052827 | 0.93388 | 0.66586 | 1.0997 | 0.045779 | 0.030666 | 122.5268 | 122.5437 | 122.7036 | 122.4624 | -0.076765 | 122.4722 | 122.5708 | 122.5557 | 81.6787 | -122.9588
2034.5938 | 122.5433 | -122.4335 | 0.09613 | 1.4211e-13 | 0.0023653 | -0.0097224 | -0.026858 | -0.023789 | 0.0042113 | 0.011293 | -0.012361 | 0.027981 | 0.043943 | 0.00048933 | 0.048074 | 0.092615 | 0.038035 | 0.051108 | 0.11165 | 0.12857 | 0.2839 | 0.028521 | -121.4813 | -40.9928 | -121.7447 | 0.057037 | 0.15564 | 0.14053 | -122.8536 | 122.462 | 0.015517 | 122.5261 | 122.4846 | 0.022587 | 0.032439 | 0.18777 | -0.42008 | -0.039093 | 0.95219 | 0.68875 | 1.1088 | 0.059513 | 0.0444 | 122.5451 | 122.562 | 122.7174 | 122.4715 | -0.067609 | 122.4905 | 122.5891 | 122.574 | 81.4406 | -122.9497
2036.3125 | 122.5433 | -122.438 | 0.1236 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.026644 | -0.023148 | 0.0039977 | 0.0036627 | -0.012361 | 0.027767 | 0.043943 | 0.00048933 | 0.048074 | 0.097194 | 0.038035 | 0.055687 | 0.10249 | 0.12857 | 0.27932 | 0.028521 | -121.4675 | -41.2767 | -121.7447 | 0.057037 | 0.15564 | 0.14969 | -122.8581 | 122.4666 | -0.021106 | 122.5352 | 122.4937 | 0.027166 | 0.004973 | 0.15573 | -0.42009 | -0.066559 | 0.9705 | 0.69333 | 1.1134 | 0.032047 | 0.026091 | 122.5405 | 122.5666 | 122.7174 | 122.4761 | -0.095075 | 122.4951 | 122.5937 | 122.5877 | 81.1613 | -122.9817
2038.0938 | 122.612 | -122.3969 | 0.091553 | 1.4211e-13 | 0.0027927 | -0.0095086 | -0.026644 | -0.023362 | 0.0042113 | -0.0039678 | -0.012575 | 0.02734 | 0.043729 | 0.00070293 | 0.048501 | 0.092615 | 0.033457 | 0.055687 | 0.10249 | 0.12399 | 0.27932 | 0.037679 | -121.4538 | -41.5377 | -121.7356 | 0.052459 | 0.15107 | 0.14511 | -122.8581 | 122.4345 | 0.010937 | 122.4895 | 122.4525 | 0.018008 | 0.032437 | 0.18777 | -0.46128 | -0.039094 | 0.94304 | 0.66129 | 1.1226 | 0.059512 | 0.053556 | 122.4993 | 122.5208 | 122.6762 | 122.4303 | -0.053874 | 122.4493 | 122.5479 | 122.542 | 80.8592 | -122.9497
2039.8125 | 122.5525 | -122.4335 | 0.1236 | 1.4211e-13 | 0.0023653 | -0.0095086 | -0.026644 | -0.023576 | 0.0044249 | 0.011293 | -0.012361 | 0.027767 | 0.043943 | 0.00048933 | 0.048288 | 0.092615 | 0.038035 | 0.051108 | 0.10707 | 0.12857 | 0.27475 | 0.023942 | -121.4447 | -41.8353 | -121.731 | 0.057037 | 0.15564 | 0.14053 | -122.8581 | 122.4574 | -0.016528 | 122.5261 | 122.4846 | 0.027166 | 0.004973 | 0.15115 | -0.42466 | -0.066559 | 0.98882 | 0.70248 | 1.1271 | 0.032047 | 0.016934 | 122.5405 | 122.562 | 122.7082 | 122.4715 | -0.099654 | 122.4905 | 122.5891 | 122.574 | 80.5982 | -122.9817
2041.6094 | 122.5525 | -122.4289 | 0.082397 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.026858 | -0.023576 | 0.0039977 | 0.0036627 | -0.012361 | 0.027553 | 0.044157 | 0.00070293 | 0.048074 | 0.097194 | 0.038035 | 0.060265 | 0.10707 | 0.12857 | 0.27475 | 0.028521 | -121.4401 | -42.3756 | -121.7173 | 0.052459 | 0.15564 | 0.13595 | -122.8673 | 122.4574 | 0.024671 | 122.5261 | 122.4892 | 0.031744 | 0.046172 | 0.19235 | -0.4384 | -0.029938 | 0.98882 | 0.71164 | 1.15 | 0.073246 | 0.053555 | 122.536 | 122.5575 | 122.7036 | 122.4669 | -0.053876 | 122.4814 | 122.5845 | 122.5648 | 80.0533 | -122.9497
2043.3438 | 122.5342 | -122.4243 | 0.11444 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.027285 | -0.023789 | 0.0039977 | 0.0036627 | -0.012575 | 0.027767 | 0.044157 | 0.00091673 | 0.048501 | 0.097194 | 0.033457 | 0.04653 | 0.10249 | 0.12857 | 0.27932 | 0.028521 | -121.4218 | -42.7098 | -121.7173 | 0.061616 | 0.16022 | 0.15427 | -122.8581 | 122.4528 | -0.011951 | 122.5215 | 122.4708 | 0.018009 | 0.014128 | 0.16488 | -0.43382 | -0.052825 | 1.0026 | 0.70707 | 1.1409 | 0.045781 | 0.039825 | 122.5268 | 122.5529 | 122.7036 | 122.4578 | -0.08592 | 122.4859 | 122.5845 | 122.5786 | 79.7145 | -122.9726
2045.1406 | 122.5937 | -122.4289 | 0.091553 | 1.4211e-13 | 0.0025791 | -0.009295 | -0.027072 | -0.023576 | 0.0042113 | 0.0036627 | -0.012148 | 0.027553 | 0.044157 | 0.00091673 | 0.048288 | 0.097194 | 0.038035 | 0.055687 | 0.10249 | 0.12857 | 0.2839 | 0.023942 | -121.4126 | -42.9159 | -121.7081 | 0.052459 | 0.15564 | 0.14969 | -122.8581 | 122.4528 | 0.010937 | 122.5261 | 122.4846 | 0.031745 | 0.037016 | 0.19235 | -0.42924 | -0.039094 | 1.0163 | 0.7208 | 1.15 | 0.06409 | 0.058134 | 122.5314 | 122.5575 | 122.7128 | 122.4669 | -0.067611 | 122.4814 | 122.5845 | 122.5786 | 79.513 | -122.9497
2046.9219 | 122.6807 | -122.3602 | 0.073242 | 1.4211e-13 | 0.0027927 | -0.0097224 | -0.026858 | -0.023576 | 0.0042113 | 0.011293 | -0.011934 | 0.027767 | 0.043729 | 0.00091673 | 0.048288 | 0.097194 | 0.047193 | 0.051108 | 0.10249 | 0.12857 | 0.2839 | 0.0331 | -121.408 | -43.4745 | -121.7081 | 0.052459 | 0.15107 | 0.14969 | -122.8627 | 122.3933 | 0.029248 | 122.4574 | 122.4113 | 0.018008 | 0.055327 | 0.21066 | -0.50248 | -0.020783 | 0.95221 | 0.65214 | 1.1546 | 0.077823 | 0.076445 | 122.4627 | 122.4888 | 122.6441 | 122.4074 | -0.040142 | 122.4127 | 122.5113 | 122.5099 | 78.8857 | -122.936
2048.6875 | 122.6761 | -122.3694 | 0.064087 | 1.4211e-13 | 0.0023653 | -0.0097224 | -0.02643 | -0.023789 | 0.0042113 | 0.018923 | -0.011934 | 0.027767 | 0.043516 | 0.00070293 | 0.048074 | 0.092615 | 0.038035 | 0.04653 | 0.10707 | 0.12399 | 0.2839 | 0.028521 | -121.3897 | -43.6485 | -121.6989 | 0.057037 | 0.1648 | 0.14969 | -122.8581 | 122.3979 | 0.042981 | 122.462 | 122.4159 | 0.018009 | 0.059903 | 0.21982 | -0.48875 | -0.00705 | 0.97968 | 0.67045 | 1.1592 | 0.10071 | 0.0856 | 122.4765 | 122.4934 | 122.6533 | 122.4074 | -0.035566 | 122.4264 | 122.5342 | 122.5191 | 78.7209 | -122.9222
2050.4844 | 122.6486 | -122.4106 | 0.073242 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.026858 | -0.023576 | 0.0042113 | 0.018923 | -0.011934 | 0.027767 | 0.043943 | 0.00091673 | 0.048074 | 0.092615 | 0.033457 | 0.055687 | 0.10707 | 0.12857 | 0.2839 | 0.028521 | -121.376 | -44.0331 | -121.6944 | 0.061616 | 0.1648 | 0.14511 | -122.8627 | 122.4391 | 0.033826 | 122.5032 | 122.4663 | 0.027166 | 0.055327 | 0.21066 | -0.45213 | -0.011626 | 1.0346 | 0.71623 | 1.1684 | 0.091558 | 0.071867 | 122.5177 | 122.5392 | 122.6945 | 122.444 | -0.044721 | 122.4722 | 122.5754 | 122.5557 | 78.3775 | -122.936
2052.2031 | 122.5296 | -122.4426 | 0.10529 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.026858 | -0.023576 | 0.0042113 | 0.011293 | -0.011934 | 0.027981 | 0.043943 | 0.00027553 | 0.048715 | 0.092615 | 0.038035 | 0.051108 | 0.097912 | 0.12857 | 0.28848 | 0.028521 | -121.3577 | -44.175 | -121.676 | 0.052459 | 0.16022 | 0.14511 | -122.8581 | 122.4711 | -0.007374 | 122.5352 | 122.4937 | 0.022587 | 0.023283 | 0.18319 | -0.41551 | -0.052827 | 1.085 | 0.76659 | 1.1821 | 0.054936 | 0.039823 | 122.5405 | 122.5712 | 122.7311 | 122.4807 | -0.076765 | 122.4951 | 122.6028 | 122.5877 | 78.2676 | -122.9634
2053.9844 | 122.5983 | -122.4106 | 0.10529 | 1.4211e-13 | 0.0025791 | -0.0090814 | -0.02643 | -0.023362 | 0.0039977 | 0.011293 | -0.012575 | 0.027553 | 0.043943 | 0.00091673 | 0.048501 | 0.10177 | 0.042614 | 0.051108 | 0.10707 | 0.12857 | 0.27932 | 0.0331 | -121.3531 | -44.5322 | -121.6806 | 0.061616 | 0.15564 | 0.14969 | -122.8719 | 122.4437 | 0.001782 | 122.5124 | 122.4617 | 0.018008 | 0.023283 | 0.17404 | -0.46129 | -0.04367 | 1.0575 | 0.72996 | 1.1912 | 0.050357 | 0.044401 | 122.5177 | 122.5392 | 122.6899 | 122.4532 | -0.072186 | 122.4722 | 122.5662 | 122.5603 | 77.8784 | -122.9772
2055.7344 | 122.6486 | -122.3831 | 0.086975 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.026644 | -0.023576 | 0.0037841 | 0.0036627 | -0.012361 | 0.027553 | 0.043943 | 0.00070293 | 0.048074 | 0.10177 | 0.042614 | 0.055687 | 0.097912 | 0.12399 | 0.27932 | 0.0331 | -121.3302 | -44.9305 | -121.6715 | 0.052459 | 0.15564 | 0.14511 | -122.8673 | 122.4162 | 0.010937 | 122.4849 | 122.4388 | 0.022587 | 0.037015 | 0.19235 | -0.48417 | -0.034516 | 1.0529 | 0.71165 | 1.1958 | 0.068668 | 0.058134 | 122.481 | 122.5071 | 122.6624 | 122.4257 | -0.053875 | 122.4356 | 122.5388 | 122.5282 | 77.4526 | -122.9543
2057.4531 | 122.58 | -122.4289 | 0.11444 | 1.4211e-13 | 0.0027927 | -0.009295 | -0.026858 | -0.023576 | 0.0039977 | 0.0036627 | -0.012575 | 0.027767 | 0.044157 | 0.00091673 | 0.048288 | 0.092615 | 0.038035 | 0.04653 | 0.097912 | 0.12857 | 0.27017 | 0.028521 | -121.3256 | -45.3884 | -121.6715 | 0.052459 | 0.16022 | 0.14969 | -122.8627 | 122.4574 | -0.016529 | 122.5215 | 122.4754 | 0.018009 | 0.014128 | 0.15573 | -0.43382 | -0.061982 | 1.1033 | 0.75743 | 1.1912 | 0.045781 | 0.035246 | 122.5268 | 122.5575 | 122.6991 | 122.4669 | -0.08592 | 122.4814 | 122.5891 | 122.5786 | 77.0405 | -122.9772
2059.25 | 122.5708 | -122.4335 | 0.10986 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.026858 | -0.023789 | 0.0042113 | 0.018923 | -0.012361 | 0.027767 | 0.044157 | 0.00070293 | 0.048288 | 0.097194 | 0.033457 | 0.055687 | 0.10249 | 0.12857 | 0.27932 | 0.028521 | -121.3119 | -45.7226 | -121.6623 | 0.052459 | 0.15107 | 0.15427 | -122.8673 | 122.462 | -0.007373 | 122.5307 | 122.4892 | 0.027166 | 0.018706 | 0.16946 | -0.43382 | -0.057404 | 1.1216 | 0.77117 | 1.205 | 0.041202 | 0.044403 | 122.536 | 122.562 | 122.7128 | 122.4669 | -0.081342 | 122.4859 | 122.5845 | 122.5877 | 76.7108 | -122.9772
2061.0312 | 122.5525 | -122.4518 | 0.10529 | 1.4211e-13 | 0.0025791 | -0.0090814 | -0.026858 | -0.023576 | 0.0037841 | 0.011293 | -0.012361 | 0.027981 | 0.044157 | 0.00070293 | 0.048288 | 0.097194 | 0.042614 | 0.051108 | 0.10707 | 0.11941 | 0.2839 | 0.037679 | -121.289 | -46.0844 | -121.6486 | 0.057037 | 0.16022 | 0.14969 | -122.8673 | 122.4895 | 0.001782 | 122.549 | 122.5029 | 0.013429 | 0.014125 | 0.17862 | -0.41551 | -0.048249 | 1.1628 | 0.80321 | 1.2187 | 0.054936 | 0.044401 | 122.5588 | 122.5712 | 122.7357 | 122.4944 | -0.067607 | 122.5088 | 122.612 | 122.6015 | 76.3674 | -122.9726
2062.7344 | 122.699 | -122.4014 | 0.064087 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.026858 | -0.023362 | 0.0039977 | 0.0036627 | -0.012575 | 0.027553 | 0.04437 | 0.00070293 | 0.048288 | 0.10177 | 0.042614 | 0.051108 | 0.10707 | 0.13315 | 0.2839 | 0.028521 | -121.2798 | -46.5102 | -121.6486 | 0.057037 | 0.16022 | 0.14969 | -122.8627 | 122.4299 | 0.042981 | 122.5032 | 122.4525 | 0.022587 | 0.069061 | 0.21982 | -0.46129 | -0.00705 | 1.1216 | 0.75286 | 1.2141 | 0.096135 | 0.0856 | 122.5085 | 122.5346 | 122.6853 | 122.444 | -0.035566 | 122.4585 | 122.5617 | 122.5511 | 75.8913 | -122.9268
2064.5469 | 122.6395 | -122.3969 | 0.064087 | 1.4211e-13 | 0.0021517 | -0.0097224 | -0.02643 | -0.023789 | 0.0042113 | -0.0039678 | -0.012575 | 0.028194 | 0.044157 | 0.00091673 | 0.048501 | 0.10177 | 0.047193 | 0.051108 | 0.10707 | 0.12857 | 0.27475 | 0.0331 | -121.2569 | -46.8124 | -121.6348 | 0.057037 | 0.1648 | 0.14969 | -122.8765 | 122.43 | 0.042981 | 122.4986 | 122.448 | 0.018008 | 0.064482 | 0.21066 | -0.4796 | -0.00705 | 1.1399 | 0.76202 | 1.2416 | 0.10071 | 0.0856 | 122.5039 | 122.5254 | 122.6716 | 122.444 | -0.030987 | 122.4539 | 122.5617 | 122.5465 | 75.5845 | -122.9405
2066.2812 | 122.6166 | -122.3923 | 0.082397 | 1.4211e-13 | 0.0025791 | -0.009295 | -0.02643 | -0.023576 | 0.0039977 | 0.011293 | -0.012361 | 0.027981 | 0.044157 | 0.00070293 | 0.048715 | 0.092615 | 0.033457 | 0.04653 | 0.11165 | 0.11941 | 0.28848 | 0.028521 | -121.2569 | -47.1741 | -121.6165 | 0.052459 | 0.15107 | 0.14969 | -122.8719 | 122.4208 | 0.02925 | 122.4849 | 122.4388 | 0.018009 | 0.037014 | 0.20608 | -0.4796 | -0.029938 | 1.1353 | 0.77575 | 1.2554 | 0.068668 | 0.06729 | 122.5039 | 122.5117 | 122.6808 | 122.4257 | -0.053876 | 122.4447 | 122.5433 | 122.542 | 75.2182 | -122.9543
2068.0781 | 122.6166 | -122.4426 | 0.10986 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.026858 | -0.023789 | 0.0042113 | 0.011293 | -0.012361 | 0.028194 | 0.04437 | 0.00091673 | 0.048501 | 0.097194 | 0.033457 | 0.055687 | 0.11165 | 0.12857 | 0.27932 | 0.028521 | -121.2386 | -47.6136 | -121.6119 | 0.057037 | 0.15564 | 0.15427 | -122.8719 | 122.4711 | 0.001784 | 122.5398 | 122.4983 | 0.027166 | 0.018706 | 0.16946 | -0.42924 | -0.052826 | 1.204 | 0.83069 | 1.2599 | 0.04578 | 0.044403 | 122.5543 | 122.5712 | 122.722 | 122.4761 | -0.081342 | 122.4997 | 122.5983 | 122.5969 | 74.829 | -122.9817
2069.7812 | 122.5891 | -122.4106 | 0.091553 | 1.4211e-13 | 0.0021517 | -0.0095086 | -0.02643 | -0.023362 | 0.0042113 | 0.011293 | -0.012575 | 0.027981 | 0.043943 | 0.00091673 | 0.048501 | 0.10177 | 0.038035 | 0.055687 | 0.10249 | 0.12857 | 0.27475 | 0.019363 | -121.2249 | -47.8929 | -121.6028 | 0.057037 | 0.15107 | 0.14511 | -122.8765 | 122.4299 | 0.010937 | 122.5124 | 122.4663 | 0.036324 | 0.037016 | 0.18319 | -0.46587 | -0.034516 | 1.1857 | 0.8078 | 1.2737 | 0.059512 | 0.053556 | 122.5131 | 122.5392 | 122.6853 | 122.4486 | -0.07219 | 122.4676 | 122.5616 | 122.5557 | 74.5176 | -122.968
2071.5781 | 122.6624 | -122.4106 | 0.068665 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.026858 | -0.023148 | 0.0042113 | -0.0039678 | -0.012148 | 0.027553 | 0.044157 | 0.00070293 | 0.048501 | 0.097194 | 0.038035 | 0.051108 | 0.10707 | 0.12399 | 0.27017 | 0.028521 | -121.2111 | -48.2455 | -121.5845 | 0.052459 | 0.15107 | 0.14511 | -122.8719 | 122.4391 | 0.038403 | 122.5078 | 122.4617 | 0.022587 | 0.055325 | 0.2015 | -0.46129 | -0.016206 | 1.1994 | 0.82612 | 1.2874 | 0.0824 | 0.076444 | 122.5177 | 122.5346 | 122.6808 | 122.4486 | -0.040144 | 122.463 | 122.5616 | 122.5557 | 74.1651 | -122.9405
2073.3594 | 122.6898 | -122.374 | 0.07782 | 1.4211e-13 | 0.0027927 | -0.0095086 | -0.02643 | -0.023576 | 0.0039977 | 0.018923 | -0.012148 | 0.02734 | 0.043943 | 0.00070293 | 0.048501 | 0.092615 | 0.047193 | 0.051108 | 0.10249 | 0.12857 | 0.2839 | 0.0331 | -121.1882 | -48.6851 | -121.5845 | 0.057037 | 0.15564 | 0.14511 | -122.8719 | 122.4071 | 0.02467 | 122.4666 | 122.4251 | 0.018008 | 0.050749 | 0.20608 | -0.49791 | -0.020783 | 1.1857 | 0.78949 | 1.2874 | 0.077823 | 0.067289 | 122.4765 | 122.5025 | 122.6579 | 122.4212 | -0.04472 | 122.431 | 122.5296 | 122.5191 | 73.6889 | -122.9497
2075.0781 | 122.5616 | -122.4289 | 0.09613 | 1.4211e-13 | 0.0027927 | -0.0095086 | -0.027072 | -0.023362 | 0.0039977 | 0.0036627 | -0.012148 | 0.027767 | 0.043943 | 0.00091673 | 0.048715 | 0.092615 | 0.038035 | 0.051108 | 0.11165 | 0.13315 | 0.27475 | 0.028521 | -121.1699 | -48.9827 | -121.5707 | 0.052459 | 0.15564 | 0.14511 | -122.8765 | 122.4574 | 0.015517 | 122.5215 | 122.48 | 0.022587 | 0.037018 | 0.17862 | -0.44756 | -0.043671 | 1.259 | 0.85816 | 1.3057 | 0.059513 | 0.048979 | 122.5405 | 122.562 | 122.7036 | 122.4669 | -0.067609 | 122.4814 | 122.5845 | 122.574 | 73.4462 | -122.9726
2076.8594 | 122.5754 | -122.4335 | 0.11444 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.026644 | -0.023789 | 0.0039977 | 0.011293 | -0.012361 | 0.027553 | 0.044157 | 0.00091673 | 0.048288 | 0.097194 | 0.042614 | 0.051108 | 0.10707 | 0.13315 | 0.2839 | 0.0331 | -121.1425 | -49.3444 | -121.5616 | 0.057037 | 0.15107 | 0.14053 | -122.8765 | 122.4666 | -0.007373 | 122.5307 | 122.4846 | 0.018008 | 0.018707 | 0.16946 | -0.44298 | -0.057404 | 1.291 | 0.8719 | 1.3149 | 0.036624 | 0.026089 | 122.5405 | 122.5666 | 122.7174 | 122.4761 | -0.081341 | 122.4905 | 122.5845 | 122.574 | 73.0891 | -122.9909
2078.6406 | 122.612 | -122.4289 | 0.10986 | 1.4211e-13 | 0.0027927 | -0.0095086 | -0.026858 | -0.023576 | 0.0042113 | 0.011293 | -0.012361 | 0.027553 | 0.04437 | 0.00070293 | 0.048501 | 0.097194 | 0.038035 | 0.055687 | 0.10707 | 0.12857 | 0.27932 | 0.023942 | -121.1333 | -49.7931 | -121.5524 | 0.057037 | 0.1648 | 0.14969 | -122.8765 | 122.4528 | -0.002795 | 122.5261 | 122.4846 | 0.031745 | 0.018706 | 0.16946 | -0.44756 | -0.052826 | 1.2956 | 0.87648 | 1.324 | 0.054937 | 0.039824 | 122.536 | 122.5575 | 122.7082 | 122.4669 | -0.085921 | 122.4859 | 122.5937 | 122.5786 | 72.6358 | -122.9863
2080.375 | 122.5754 | -122.4564 | 0.10071 | 1.4211e-13 | 0.0023653 | -0.009295 | -0.02643 | -0.023576 | 0.0044249 | 0.0036627 | -0.012148 | 0.027553 | 0.044157 | 0.00070293 | 0.048715 | 0.097194 | 0.042614 | 0.051108 | 0.093333 | 0.13315 | 0.27932 | 0.023942 | -121.1196 | -50.2556 | -121.5387 | 0.052459 | 0.15564 | 0.14053 | -122.8765 | 122.4803 | -0.007375 | 122.5536 | 122.5075 | 0.027166 | 0.03244 | 0.17862 | -0.42009 | -0.048249 | 1.3368 | 0.91768 | 1.3378 | 0.054935 | 0.039822 | 122.5497 | 122.5895 | 122.7357 | 122.499 | -0.076766 | 122.5088 | 122.612 | 122.5969 | 72.2008 | -122.9772
2082.1562 | 122.6715 | -122.4106 | 0.064087 | 1.4211e-13 | 0.0023653 | -0.0097224 | -0.02643 | -0.023576 | 0.0042113 | 0.011293 | -0.012361 | 0.02734 | 0.043516 | 0.00091673 | 0.048501 | 0.097194 | 0.051771 | 0.060265 | 0.10249 | 0.12857 | 0.27932 | 0.028521 | -121.0967 | -50.6448 | -121.5249 | 0.057037 | 0.1648 | 0.14511 | -122.8719 | 122.4391 | 0.038403 | 122.5078 | 122.4708 | 0.031744 | 0.064482 | 0.21524 | -0.46129 | -0.00705 | 1.3139 | 0.88564 | 1.3469 | 0.10071 | 0.081022 | 122.5131 | 122.5392 | 122.6899 | 122.4624 | -0.035566 | 122.4676 | 122.5754 | 122.5557 | 71.7658 | -122.936
2083.9531 | 122.6028 | -122.4243 | 0.086975 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.026644 | -0.023576 | 0.0042113 | 0.011293 | -0.011934 | 0.027981 | 0.044157 | 0.00091673 | 0.048715 | 0.10177 | 0.038035 | 0.055687 | 0.097912 | 0.11941 | 0.27932 | 0.028521 | -121.0784 | -51.1118 | -121.5066 | 0.04788 | 0.16022 | 0.14511 | -122.8765 | 122.4528 | 0.010937 | 122.5261 | 122.48 | 0.027166 | 0.032436 | 0.19235 | -0.45213 | -0.039095 | 1.346 | 0.91769 | 1.3698 | 0.073247 | 0.058134 | 122.5222 | 122.5437 | 122.7036 | 122.4624 | -0.058454 | 122.4722 | 122.5845 | 122.5694 | 71.3125 | -122.9634
2085.6562 | 122.6212 | -122.4197 | 0.086975 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.026644 | -0.023789 | 0.0039977 | 0.018923 | -0.012148 | 0.027767 | 0.04437 | 0.00070293 | 0.048288 | 0.10177 | 0.033457 | 0.055687 | 0.10249 | 0.12857 | 0.27475 | 0.028521 | -121.06 | -51.4323 | -121.5021 | 0.057037 | 0.14649 | 0.14511 | -122.8719 | 122.4483 | 0.015515 | 122.5215 | 122.4754 | 0.027166 | 0.041594 | 0.18777 | -0.45213 | -0.029938 | 1.3597 | 0.91769 | 1.3698 | 0.059511 | 0.058134 | 122.5222 | 122.5483 | 122.6945 | 122.4532 | -0.058454 | 122.4768 | 122.5662 | 122.5648 | 70.9875 | -122.9588
2087.4375 | 122.5479 | -122.438 | 0.091553 | 1.4211e-13 | 0.0025791 | -0.0097224 | -0.026858 | -0.023576 | 0.0042113 | 0.018923 | -0.012148 | 0.027981 | 0.044157 | 0.00070293 | 0.048715 | 0.10177 | 0.051771 | 0.051108 | 0.10707 | 0.12857 | 0.27475 | 0.028521 | -121.028 | -51.8215 | -121.4929 | 0.057037 | 0.16022 | 0.14511 | -122.8765 | 122.4666 | 0.015515 | 122.5398 | 122.4892 | 0.022587 | 0.037016 | 0.18319 | -0.4384 | -0.034516 | 1.4101 | 0.94515 | 1.3836 | 0.068669 | 0.053556 | 122.5451 | 122.5666 | 122.7128 | 122.4898 | -0.063032 | 122.4951 | 122.5983 | 122.5832 | 70.6166 | -122.968
2089.1719 | 122.6852 | -122.4152 | 0.07782 | 1.4211e-13 | 0.0027927 | -0.0090814 | -0.026644 | -0.023576 | 0.0037841 | 0.011293 | -0.012148 | 0.027981 | 0.04437 | 0.00091673 | 0.048929 | 0.097194 | 0.042614 | 0.060265 | 0.10707 | 0.12857 | 0.27017 | 0.0331 | -121.0188 | -52.0092 | -121.4837 | 0.057037 | 0.15107 | 0.15427 | -122.8765 | 122.4483 | 0.029248 | 122.5124 | 122.4754 | 0.027165 | 0.050749 | 0.19235 | -0.46129 | -0.020783 | 1.3963 | 0.93143 | 1.3927 | 0.073245 | 0.076446 | 122.5222 | 122.5437 | 122.6853 | 122.4578 | -0.04472 | 122.4722 | 122.5662 | 122.5694 | 70.406 | -122.9543
2090.9531 | 122.58 | -122.4243 | 0.09613 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.026644 | -0.023789 | 0.0039977 | 0.011293 | -0.012148 | 0.027767 | 0.043943 | 0.00091673 | 0.048715 | 0.092615 | 0.038035 | 0.051108 | 0.097912 | 0.12857 | 0.2839 | 0.028521 | -121.0143 | -52.2565 | -121.4654 | 0.057037 | 0.16022 | 0.14969 | -122.8765 | 122.4528 | 0.001782 | 122.5169 | 122.4754 | 0.022587 | 0.032439 | 0.18777 | -0.45213 | -0.039093 | 1.4101 | 0.95889 | 1.411 | 0.064092 | 0.053557 | 122.5222 | 122.5529 | 122.7082 | 122.4624 | -0.067609 | 122.4814 | 122.5845 | 122.574 | 70.1679 | -122.9726
2092.7344 | 122.6166 | -122.4335 | 0.091553 | 1.4211e-13 | 0.0027927 | -0.0095086 | -0.026644 | -0.023362 | 0.0042113 | 0.0036627 | -0.012148 | 0.027767 | 0.04437 | 0.00091673 | 0.048715 | 0.092615 | 0.047193 | 0.051108 | 0.10249 | 0.12857 | 0.2839 | 0.023942 | -120.9914 | -52.5587 | -121.4517 | 0.057037 | 0.15564 | 0.14969 | -122.8765 | 122.4574 | 0.010937 | 122.5261 | 122.4846 | 0.027166 | 0.037016 | 0.19235 | -0.44298 | -0.034516 | 1.4421 | 0.98179 | 1.4248 | 0.06409 | 0.058134 | 122.536 | 122.562 | 122.7174 | 122.4807 | -0.067611 | 122.4905 | 122.5891 | 122.5832 | 69.8748 | -122.968
2094.5312 | 122.6532 | -122.438 | 0.082397 | 1.4211e-13 | 0.0025791 | -0.009295 | -0.026858 | -0.023789 | 0.0039977 | 0.0036627 | -0.011934 | 0.027981 | 0.043943 | 0.00091673 | 0.048715 | 0.092615 | 0.042614 | 0.060265 | 0.10707 | 0.12857 | 0.27932 | 0.0331 | -120.9639 | -53.0211 | -121.4425 | 0.052459 | 0.15564 | 0.14969 | -122.8765 | 122.4711 | 0.024671 | 122.5307 | 122.4983 | 0.027165 | 0.046172 | 0.19693 | -0.4384 | -0.029938 | 1.4742 | 0.99552 | 1.4339 | 0.073246 | 0.06729 | 122.5451 | 122.5666 | 122.7174 | 122.4807 | -0.049297 | 122.4905 | 122.5937 | 122.5877 | 69.4169 | -122.9588
2096.25 | 122.7036 | -122.3969 | 0.07782 | 1.4211e-13 | 0.0023653 | -0.009295 | -0.026644 | -0.023789 | 0.0044249 | -0.0039678 | -0.012148 | 0.027981 | 0.04437 | 0.00070293 | 0.048501 | 0.092615 | 0.047193 | 0.051108 | 0.10249 | 0.12857 | 0.27932 | 0.028521 | -120.9593 | -53.6575 | -121.4334 | 0.061616 | 0.15107 | 0.15427 | -122.8856 | 122.4254 | 0.02467 | 122.4895 | 122.448 | 0.022587 | 0.050749 | 0.2015 | -0.48876 | -0.016204 | 1.4375 | 0.96348 | 1.4522 | 0.073245 | 0.076446 | 122.4993 | 122.5254 | 122.6762 | 122.444 | -0.049299 | 122.4585 | 122.5479 | 122.5511 | 68.7393 | -122.9634
2098.0312 | 122.699 | -122.3969 | 0.064087 | 1.4211e-13 | 0.0027927 | -0.0090814 | -0.026644 | -0.023362 | 0.0042113 | 0.011293 | -0.012148 | 0.027767 | 0.044157 | 0.00091673 | 0.048715 | 0.097194 | 0.042614 | 0.055687 | 0.10249 | 0.12857 | 0.28848 | 0.037679 | -120.9318 | -53.9552 | -121.4105 | 0.052459 | 0.15107 | 0.14969 | -122.8765 | 122.4345 | 0.038403 | 122.494 | 122.4525 | 0.018008 | 0.064482 | 0.22439 | -0.4796 | -0.011628 | 1.465 | 0.98637 | 1.466 | 0.086978 | 0.0856 | 122.4993 | 122.5254 | 122.6853 | 122.4395 | -0.026408 | 122.4493 | 122.5479 | 122.5465 | 68.4417 | -122.9405
2099.7344 | 122.6349 | -122.406 | 0.082397 | 1.4211e-13 | 0.0027927 | -0.0095086 | -0.026858 | -0.023362 | 0.0044249 | 0.0036627 | -0.012148 | 0.027981 | 0.044157 | 0.00091673 | 0.048501 | 0.097194 | 0.033457 | 0.060265 | 0.10707 | 0.12857 | 0.27475 | 0.028521 | -120.9181 | -54.3489 | -121.4013 | 0.052459 | 0.15564 | 0.14969 | -122.881 | 122.4345 | 0.024671 | 122.5032 | 122.4663 | 0.031744 | 0.046172 | 0.19235 | -0.47502 | -0.029938 | 1.4879 | 1.0047 | 1.4797 | 0.073246 | 0.06729 | 122.5131 | 122.5346 | 122.6808 | 122.4395 | -0.053876 | 122.4585 | 122.5616 | 122.5557 | 68.0571 | -122.9634
2101.5312 | 122.6807 | -122.4014 | 0.064087 | 1.4211e-13 | 0.0023653 | -0.009295 | -0.026644 | -0.023789 | 0.0037841 | 0.018923 | -0.011934 | 0.027767 | 0.044157 | 0.00091673 | 0.048501 | 0.10177 | 0.042614 | 0.055687 | 0.10249 | 0.12399 | 0.2839 | 0.023942 | -120.886 | -54.761 | -121.3876 | 0.057037 | 0.15564 | 0.14969 | -122.8765 | 122.4254 | 0.038403 | 122.5032 | 122.4571 | 0.031745 | 0.059903 | 0.21982 | -0.47502 | -0.00705 | 1.5154 | 1.0138 | 1.4889 | 0.091556 | 0.0856 | 122.5039 | 122.5254 | 122.6853 | 122.444 | -0.040145 | 122.4585 | 122.5571 | 122.5511 | 67.6404 | -122.9405
2103.3125 | 122.699 | -122.4197 | 0.068665 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.026644 | -0.023362 | 0.0037841 | 0.018923 | -0.012148 | 0.027767 | 0.04437 | 0.0011303 | 0.048715 | 0.10177 | 0.038035 | 0.060265 | 0.10707 | 0.11941 | 0.27932 | 0.0331 | -120.8677 | -55.1548 | -121.3693 | 0.061616 | 0.15107 | 0.14053 | -122.8765 | 122.4528 | 0.038403 | 122.5215 | 122.48 | 0.027165 | 0.050746 | 0.21066 | -0.45671 | -0.007049 | 1.552 | 1.0505 | 1.5072 | 0.0824 | 0.071865 | 122.5268 | 122.5392 | 122.6991 | 122.4578 | -0.035565 | 122.4814 | 122.5708 | 122.5603 | 67.265 | -122.9451
2105.0469 | 122.5983 | -122.4472 | 0.07782 | 1.4211e-13 | 0.0027927 | -0.009295 | -0.026644 | -0.023576 | 0.0039977 | 0.011293 | -0.011934 | 0.027981 | 0.044157 | 0.00048933 | 0.049142 | 0.092615 | 0.047193 | 0.060265 | 0.10249 | 0.12857 | 0.27932 | 0.028521 | -120.8403 | -55.4661 | -121.3601 | 0.052459 | 0.14649 | 0.15427 | -122.8856 | 122.4757 | 0.02467 | 122.5398 | 122.5075 | 0.031744 | 0.050749 | 0.2015 | -0.4384 | -0.025361 | 1.6069 | 1.0871 | 1.5255 | 0.068666 | 0.076446 | 122.5497 | 122.5758 | 122.7265 | 122.4944 | -0.049299 | 122.4997 | 122.5937 | 122.6015 | 66.9811 | -122.9634
2106.8125 | 122.699 | -122.4106 | 0.068665 | 1.4211e-13 | 0.0025791 | -0.009295 | -0.026644 | -0.023362 | 0.0039977 | 0.018923 | -0.012148 | 0.027767 | 0.044157 | 0.0011303 | 0.048715 | 0.097194 | 0.042614 | 0.04653 | 0.10249 | 0.12857 | 0.27932 | 0.023942 | -120.8219 | -55.9881 | -121.351 | 0.052459 | 0.15564 | 0.14511 | -122.881 | 122.4345 | 0.033825 | 122.5078 | 122.4571 | 0.022588 | 0.059904 | 0.21066 | -0.47044 | -0.016206 | 1.5886 | 1.0596 | 1.5301 | 0.086978 | 0.076444 | 122.5131 | 122.5392 | 122.6899 | 122.4532 | -0.044723 | 122.463 | 122.5662 | 122.5557 | 66.4225 | -122.9497
2108.5469 | 122.644 | -122.4197 | 0.07782 | 1.4211e-13 | 0.0025791 | -0.009295 | -0.026644 | -0.023789 | 0.0042113 | 0.011293 | -0.012148 | 0.027767 | 0.044157 | 0.00091673 | 0.048929 | 0.097194 | 0.042614 | 0.04653 | 0.11165 | 0.13315 | 0.2839 | 0.037679 | -120.8036 | -56.652 | -121.3235 | 0.057037 | 0.15564 | 0.15427 | -122.881 | 122.4574 | 0.033827 | 122.5169 | 122.4663 | 0.008851 | 0.055328 | 0.20608 | -0.46129 | -0.020783 | 1.6161 | 1.0963 | 1.5575 | 0.077823 | 0.076446 | 122.5314 | 122.5529 | 122.7036 | 122.4624 | -0.040141 | 122.4768 | 122.5754 | 122.574 | 65.7677 | -122.9588
2110.3281 | 122.6303 | -122.4289 | 0.11902 | 1.4211e-13 | 0.0025791 | -0.009295 | -0.026644 | -0.023576 | 0.0042113 | 0.0036627 | -0.012148 | 0.027767 | 0.044157 | 0.00091673 | 0.048715 | 0.10635 | 0.042614 | 0.055687 | 0.10707 | 0.11941 | 0.27932 | 0.028521 | -120.7716 | -56.9313 | -121.3097 | 0.052459 | 0.15107 | 0.14511 | -122.881 | 122.4574 | -0.011951 | 122.5352 | 122.4846 | 0.027166 | 0.000392 | 0.16031 | -0.45213 | -0.06656 | 1.6573 | 1.1191 | 1.5713 | 0.032046 | 0.02609 | 122.536 | 122.5483 | 122.7082 | 122.4715 | -0.090498 | 122.4814 | 122.58 | 122.574 | 65.4976 | -123
2112.1094 | 122.7127 | -122.3785 | 0.059509 | 1.4211e-13 | 0.0025791 | -0.009295 | -0.026858 | -0.023576 | 0.0042113 | -0.0039678 | -0.012361 | 0.027981 | 0.044157 | 0.00091673 | 0.048715 | 0.092615 | 0.042614 | 0.060265 | 0.10249 | 0.12857 | 0.27932 | 0.028521 | -120.767 | -57.5952 | -121.3006 | 0.052459 | 0.15107 | 0.15427 | -122.8948 | 122.4071 | 0.042981 | 122.4712 | 122.4388 | 0.031744 | 0.06906 | 0.21982 | -0.51623 | -0.00705 | 1.6115 | 1.078 | 1.5942 | 0.091556 | 0.094757 | 122.481 | 122.5071 | 122.6579 | 122.4212 | -0.030988 | 122.431 | 122.5296 | 122.5328 | 64.7833 | -122.9543
2113.8125 | 122.644 | -122.4426 | 0.07782 | 1.4211e-13 | 0.0025791 | -0.009295 | -0.027072 | -0.023362 | 0.0042113 | 0.011293 | -0.012148 | 0.027767 | 0.044157 | 0.00048933 | 0.048715 | 0.092615 | 0.047193 | 0.055687 | 0.10707 | 0.12857 | 0.29306 | 0.0331 | -120.7304 | -58.0668 | -121.2869 | 0.061616 | 0.15564 | 0.15427 | -122.881 | 122.4757 | 0.029248 | 122.5352 | 122.4983 | 0.022587 | 0.050749 | 0.21524 | -0.4384 | -0.016204 | 1.7123 | 1.1558 | 1.5942 | 0.077823 | 0.076446 | 122.5497 | 122.5712 | 122.7357 | 122.4898 | -0.04472 | 122.5042 | 122.5983 | 122.5969 | 64.3758 | -122.9588
2115.5938 | 122.5708 | -122.4335 | 0.091553 | 1.4211e-13 | 0.0027927 | -0.0097224 | -0.026644 | -0.023148 | 0.0042113 | 0.0036627 | -0.012148 | 0.027981 | 0.04437 | 0.00091673 | 0.048929 | 0.10177 | 0.047193 | 0.060265 | 0.10249 | 0.12857 | 0.2839 | 0.028521 | -120.7212 | -58.5156 | -121.2869 | 0.061616 | 0.14649 | 0.14053 | -122.881 | 122.462 | 0.010937 | 122.5352 | 122.4937 | 0.031744 | 0.037016 | 0.19235 | -0.44756 | -0.029937 | 1.7123 | 1.1466 | 1.5942 | 0.054933 | 0.048977 | 122.536 | 122.562 | 122.7174 | 122.4807 | -0.063032 | 122.4951 | 122.58 | 122.574 | 63.9179 | -122.9726
2117.375 | 122.6212 | -122.438 | 0.10071 | 1.4211e-13 | 0.0025791 | -0.0097224 | -0.026644 | -0.023576 | 0.0039977 | 0.0036627 | -0.011934 | 0.028194 | 0.044157 | 0.00091673 | 0.049356 | 0.097194 | 0.038035 | 0.055687 | 0.11165 | 0.12857 | 0.27475 | 0.037679 | -120.6937 | -58.7582 | -121.2777 | 0.061616 | 0.15564 | 0.14969 | -122.8765 | 122.4757 | 0.010939 | 122.5352 | 122.4937 | 0.018008 | 0.027861 | 0.17404 | -0.4384 | -0.039092 | 1.7443 | 1.1604 | 1.5988 | 0.054935 | 0.048979 | 122.5497 | 122.5666 | 122.7128 | 122.4761 | -0.063029 | 122.4997 | 122.5937 | 122.5877 | 63.6798 | -122.9772
2119.1719 | 122.6486 | -122.4335 | 0.10986 | 1.4211e-13 | 0.0023653 | -0.0090814 | -0.026858 | -0.023576 | 0.0042113 | -0.0039678 | -0.012361 | 0.027981 | 0.04437 | 0.00091673 | 0.048929 | 0.097194 | 0.042614 | 0.055687 | 0.10707 | 0.12399 | 0.2839 | 0.028521 | -120.6709 | -59.3992 | -121.2548 | 0.057037 | 0.15107 | 0.14969 | -122.881 | 122.462 | -0.002795 | 122.5307 | 122.4892 | 0.027166 | 0.014127 | 0.17404 | -0.44756 | -0.052826 | 1.7626 | 1.1787 | 1.6262 | 0.041202 | 0.039824 | 122.5405 | 122.5575 | 122.7174 | 122.4761 | -0.081342 | 122.4905 | 122.5845 | 122.5832 | 63.0342 | -122.9909
2120.9375 | 122.6166 | -122.4289 | 0.091553 | 1.4211e-13 | 0.0023653 | -0.0095086 | -0.026217 | -0.023362 | 0.0042113 | 0.018923 | -0.012148 | 0.027767 | 0.04437 | 0.00070293 | 0.048929 | 0.097194 | 0.047193 | 0.060265 | 0.11165 | 0.12857 | 0.27932 | 0.0331 | -120.6525 | -59.8663 | -121.2411 | 0.057037 | 0.15564 | 0.14969 | -122.881 | 122.462 | 0.020094 | 122.5261 | 122.4892 | 0.027165 | 0.037016 | 0.18777 | -0.45213 | -0.034516 | 1.7764 | 1.1878 | 1.64 | 0.06409 | 0.058134 | 122.5405 | 122.5575 | 122.7082 | 122.4761 | -0.058453 | 122.4859 | 122.5845 | 122.5786 | 62.5626 | -122.9726
2122.6562 | 122.644 | -122.4197 | 0.054932 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.027072 | -0.023148 | 0.0039977 | 0.0036627 | -0.011934 | 0.027981 | 0.044157 | 0.0011303 | 0.049356 | 0.092615 | 0.042614 | 0.074 | 0.10707 | 0.12857 | 0.2839 | 0.0331 | -120.6159 | -60.2188 | -121.2319 | 0.052459 | 0.15564 | 0.14511 | -122.881 | 122.4528 | 0.052136 | 122.5124 | 122.4937 | 0.0409 | 0.073637 | 0.22897 | -0.46129 | -0.002473 | 1.8038 | 1.1878 | 1.6491 | 0.10071 | 0.090177 | 122.5268 | 122.5483 | 122.7036 | 122.4624 | -0.021832 | 122.4722 | 122.5754 | 122.5648 | 62.2009 | -122.936
2124.4531 | 122.6028 | -122.4518 | 0.10986 | 1.4211e-13 | 0.0027927 | -0.0097224 | -0.026644 | -0.023789 | 0.0042113 | 0.011293 | -0.011934 | 0.028194 | 0.044157 | 0.0011303 | 0.048929 | 0.10635 | 0.038035 | 0.060265 | 0.097912 | 0.13315 | 0.2839 | 0.028521 | -120.5747 | -60.5897 | -121.2228 | 0.057037 | 0.14649 | 0.14969 | -122.8856 | 122.4803 | -0.011951 | 122.5581 | 122.512 | 0.031744 | 0.023285 | 0.17404 | -0.43382 | -0.052826 | 1.8771 | 1.229 | 1.6629 | 0.036623 | 0.039824 | 122.5497 | 122.5849 | 122.7357 | 122.4898 | -0.081342 | 122.5088 | 122.5983 | 122.6015 | 61.8621 | -122.9955
2126.2344 | 122.5571 | -122.4335 | 0.10529 | 1.4211e-13 | 0.0027927 | -0.0095086 | -0.026644 | -0.023789 | 0.0039977 | 0.011293 | -0.011934 | 0.028194 | 0.04437 | 0.0011303 | 0.049142 | 0.097194 | 0.047193 | 0.055687 | 0.10707 | 0.12857 | 0.2839 | 0.0331 | -120.5381 | -61.043 | -121.1953 | 0.061616 | 0.15564 | 0.14053 | -122.8856 | 122.4666 | 0.001782 | 122.5307 | 122.4892 | 0.022587 | 0.023283 | 0.17862 | -0.45213 | -0.04367 | 1.8954 | 1.2382 | 1.6903 | 0.050357 | 0.035244 | 122.5405 | 122.562 | 122.7174 | 122.4807 | -0.072186 | 122.4951 | 122.5891 | 122.574 | 61.3905 | -122.9909
2127.9375 | 122.6761 | -122.4152 | 0.082397 | 1.4211e-13 | 0.0025791 | -0.009295 | -0.02643 | -0.023789 | 0.0042113 | 0.0036627 | -0.01172 | 0.027767 | 0.044157 | 0.00091673 | 0.049356 | 0.097194 | 0.038035 | 0.060265 | 0.10707 | 0.13773 | 0.27932 | 0.0331 | -120.506 | -61.5696 | -121.1815 | 0.057037 | 0.15107 | 0.14969 | -122.881 | 122.4483 | 0.024671 | 122.5124 | 122.4754 | 0.027165 | 0.05533 | 0.19693 | -0.46587 | -0.02536 | 1.9091 | 1.2336 | 1.6995 | 0.068668 | 0.06729 | 122.5222 | 122.5529 | 122.6945 | 122.4532 | -0.049297 | 122.4722 | 122.5662 | 122.5648 | 60.8456 | -122.9634
2129.7344 | 122.699 | -122.3831 | 0.068665 | 1.4211e-13 | 0.0021517 | -0.0095086 | -0.026644 | -0.023576 | 0.0044249 | 0.0036627 | -0.011934 | 0.027981 | 0.044584 | 0.00091673 | 0.048929 | 0.097194 | 0.047193 | 0.055687 | 0.10707 | 0.13315 | 0.2839 | 0.023942 | -120.4785 | -62.4349 | -121.0991 | 0.052459 | 0.15107 | 0.14511 | -122.8765 | 122.4071 | 0.038403 | 122.4803 | 122.4388 | 0.031745 | 0.064483 | 0.21524 | -0.49333 | -0.016206 | 1.9046 | 1.284 | 1.7773 | 0.0824 | 0.076444 | 122.4902 | 122.5163 | 122.667 | 122.4303 | -0.044723 | 122.4356 | 122.5342 | 122.5282 | 59.9482 | -122.9451
2131.5156 | 122.7036 | -122.3877 | 0.07782 | 1.4211e-13 | 0.0025791 | -0.009295 | -0.026858 | -0.023576 | 0.0039977 | 0.018923 | -0.011934 | 0.027981 | 0.043943 | 0.00091673 | 0.049142 | 0.097194 | 0.047193 | 0.064843 | 0.10707 | 0.12857 | 0.27932 | 0.028521 | -120.4373 | -62.8699 | -121.0671 | 0.052459 | 0.15564 | 0.14969 | -122.8856 | 122.4162 | 0.029248 | 122.4849 | 122.4525 | 0.036322 | 0.050749 | 0.2015 | -0.49791 | -0.025361 | 1.9504 | 1.3206 | 1.8185 | 0.077823 | 0.071867 | 122.4948 | 122.5163 | 122.667 | 122.4349 | -0.049299 | 122.4402 | 122.5433 | 122.5374 | 59.5178 | -122.9634
2133.25 | 122.6486 | -122.4289 | 0.07782 | 1.4211e-13 | 0.0027927 | -0.0095086 | -0.026858 | -0.023362 | 0.0039977 | 0.0036627 | -0.01172 | 0.028408 | 0.043943 | 0.0011303 | 0.049356 | 0.092615 | 0.047193 | 0.051108 | 0.10707 | 0.13315 | 0.2839 | 0.0331 | -120.4053 | -63.4422 | -121.0488 | 0.057037 | 0.15107 | 0.14511 | -122.8856 | 122.462 | 0.029248 | 122.5215 | 122.48 | 0.018008 | 0.055328 | 0.20608 | -0.45671 | -0.020783 | 2.0236 | 1.3801 | 1.8368 | 0.073245 | 0.067289 | 122.536 | 122.562 | 122.7128 | 122.4761 | -0.04472 | 122.4859 | 122.58 | 122.574 | 58.9866 | -122.9634
2135.0312 | 122.6028 | -122.4564 | 0.09613 | 1.4211e-13 | 0.0027927 | -0.0097224 | -0.02643 | -0.023576 | 0.0037841 | -0.0039678 | -0.012148 | 0.028194 | 0.04437 | 0.0011303 | 0.049142 | 0.097194 | 0.047193 | 0.055687 | 0.11165 | 0.12857 | 0.2839 | 0.028521 | -120.3687 | -63.9047 | -121.0167 | 0.061616 | 0.15107 | 0.15427 | -122.8856 | 122.4849 | 0.015517 | 122.5536 | 122.512 | 0.027166 | 0.032439 | 0.18777 | -0.42925 | -0.034514 | 2.0877 | 1.4397 | 1.8689 | 0.054935 | 0.058136 | 122.568 | 122.5849 | 122.7403 | 122.5036 | -0.067609 | 122.518 | 122.6074 | 122.6106 | 58.5517 | -122.9817
2136.7344 | 122.6624 | -122.4106 | 0.07782 | 1.4211e-13 | 0.0025791 | -0.009936 | -0.026003 | -0.023789 | 0.0042113 | 0.0036627 | -0.011934 | 0.028194 | 0.04437 | 0.0013439 | 0.049142 | 0.092615 | 0.042614 | 0.060265 | 0.10707 | 0.12399 | 0.2839 | 0.037679 | -120.332 | -64.4816 | -120.9892 | 0.052459 | 0.15564 | 0.15884 | -122.8856 | 122.4483 | 0.029248 | 122.5032 | 122.4708 | 0.022586 | 0.04617 | 0.20608 | -0.47502 | -0.025361 | 2.0786 | 1.4213 | 1.8964 | 0.077823 | 0.081025 | 122.5177 | 122.5346 | 122.6945 | 122.4532 | -0.040141 | 122.463 | 122.5662 | 122.5694 | 57.929 | -122.9634
2138.5156 | 122.644 | -122.4106 | 0.09613 | 1.4211e-13 | 0.0025791 | -0.009936 | -0.026644 | -0.023789 | 0.0042113 | 0.011293 | -0.011934 | 0.028194 | 0.04437 | 0.0013439 | 0.048929 | 0.092615 | 0.051771 | 0.060265 | 0.10707 | 0.12857 | 0.27475 | 0.028521 | -120.2862 | -64.8754 | -120.9526 | 0.057037 | 0.14649 | 0.14969 | -122.881 | 122.4391 | 0.010938 | 122.5032 | 122.4708 | 0.031744 | 0.032439 | 0.17862 | -0.47044 | -0.039093 | 2.1243 | 1.458 | 1.9284 | 0.050356 | 0.053557 | 122.5177 | 122.5392 | 122.6853 | 122.4624 | -0.067609 | 122.4676 | 122.5571 | 122.5603 | 57.5352 | -122.9772
2140.2969 | 122.6028 | -122.438 | 0.10071 | 1.4211e-13 | 0.0027927 | -0.0095086 | -0.026858 | -0.023362 | 0.0042113 | 0.0036627 | -0.011934 | 0.028194 | 0.044584 | 0.0015577 | 0.04957 | 0.092615 | 0.042614 | 0.060265 | 0.11165 | 0.12399 | 0.27932 | 0.028521 | -120.245 | -65.3287 | -120.9206 | 0.061616 | 0.16022 | 0.14969 | -122.881 | 122.4666 | 0.010939 | 122.5307 | 122.4983 | 0.031744 | 0.023282 | 0.17862 | -0.44298 | -0.039092 | 2.193 | 1.5175 | 1.9605 | 0.059514 | 0.048979 | 122.5497 | 122.562 | 122.7174 | 122.4807 | -0.072187 | 122.4997 | 122.5983 | 122.5877 | 57.1094 | -122.9817
2142.0156 | 122.6898 | -122.4014 | 0.07782 | 1.4211e-13 | 0.0027927 | -0.009936 | -0.02643 | -0.023362 | 0.0042113 | 0.0036627 | -0.011934 | 0.028194 | 0.044798 | 0.0011303 | 0.049356 | 0.097194 | 0.047193 | 0.060265 | 0.10249 | 0.12857 | 0.2839 | 0.028521 | -120.1947 | -65.7179 | -120.8885 | 0.052459 | 0.15564 | 0.15427 | -122.8856 | 122.4299 | 0.02467 | 122.4986 | 122.4617 | 0.031744 | 0.050749 | 0.20608 | -0.48418 | -0.025361 | 2.2068 | 1.5129 | 1.9971 | 0.077823 | 0.076446 | 122.5039 | 122.53 | 122.6853 | 122.4486 | -0.049299 | 122.4539 | 122.5571 | 122.5557 | 56.6836 | -122.9634
2143.7812 | 122.6166 | -122.4243 | 0.10529 | 1.4211e-13 | 0.0023653 | -0.009295 | -0.026644 | -0.023576 | 0.0039977 | 0.011293 | -0.01172 | 0.028622 | 0.044584 | 0.0011303 | 0.049356 | 0.097194 | 0.047193 | 0.064843 | 0.10249 | 0.12857 | 0.2839 | 0.0331 | -120.1443 | -66.2078 | -120.8565 | 0.057037 | 0.15107 | 0.14511 | -122.8765 | 122.4574 | -0.002796 | 122.5215 | 122.4892 | 0.031743 | 0.023283 | 0.17862 | -0.45213 | -0.048249 | 2.28 | 1.5679 | 2.02 | 0.045779 | 0.039823 | 122.5268 | 122.5529 | 122.7082 | 122.4715 | -0.072186 | 122.4814 | 122.5754 | 122.5694 | 56.2165 | -122.9817
2145.5 | 122.6257 | -122.438 | 0.10529 | 1.4211e-13 | 0.0027927 | -0.0095086 | -0.026217 | -0.024003 | 0.0042113 | 0.0036627 | -0.011934 | 0.028408 | 0.04437 | 0.0013439 | 0.049783 | 0.092615 | 0.051771 | 0.060265 | 0.10707 | 0.13315 | 0.2839 | 0.0331 | -120.0939 | -66.6061 | -120.829 | 0.057037 | 0.15107 | 0.15884 | -122.881 | 122.4711 | 0.001782 | 122.5307 | 122.4983 | 0.027165 | 0.027862 | 0.17862 | -0.44298 | -0.048249 | 2.3441 | 1.6091 | 2.052 | 0.045779 | 0.053559 | 122.5451 | 122.5712 | 122.722 | 122.4898 | -0.072186 | 122.4951 | 122.5891 | 122.5969 | 55.8319 | -122.9863
2147.2812 | 122.6898 | -122.3923 | 0.07782 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.02643 | -0.023576 | 0.0042113 | 0.011293 | -0.012148 | 0.028408 | 0.04437 | 0.0015577 | 0.049356 | 0.097194 | 0.05635 | 0.055687 | 0.10707 | 0.12857 | 0.27932 | 0.028521 | -120.0298 | -66.9724 | -120.7878 | 0.061616 | 0.15107 | 0.15427 | -122.8856 | 122.4208 | 0.029248 | 122.4895 | 122.448 | 0.027166 | 0.050749 | 0.2015 | -0.49333 | -0.016204 | 2.3624 | 1.6045 | 2.0978 | 0.073245 | 0.076446 | 122.4993 | 122.5208 | 122.6716 | 122.4486 | -0.049299 | 122.4539 | 122.5433 | 122.5465 | 55.4198 | -122.9634
2149 | 122.6349 | -122.4335 | 0.10529 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.026644 | -0.023789 | 0.0046387 | 0.0036627 | -0.011934 | 0.028408 | 0.044584 | 0.0017713 | 0.049783 | 0.092615 | 0.047193 | 0.055687 | 0.11165 | 0.13315 | 0.2839 | 0.028521 | -119.9703 | -67.3662 | -120.7603 | 0.057037 | 0.15107 | 0.14511 | -122.881 | 122.462 | 0.006361 | 122.5261 | 122.4892 | 0.027166 | 0.027862 | 0.17862 | -0.44756 | -0.048249 | 2.4632 | 1.6732 | 2.1207 | 0.045779 | 0.039823 | 122.5451 | 122.5666 | 122.7174 | 122.4807 | -0.076765 | 122.4905 | 122.5845 | 122.5786 | 55.0673 | -122.9863
2150.7656 | 122.5479 | -122.4335 | 0.10986 | 1.4211e-13 | 0.0027927 | -0.0097224 | -0.026644 | -0.023576 | 0.0046387 | 0.018923 | -0.011934 | 0.028194 | 0.04437 | 0.0013439 | 0.049783 | 0.10635 | 0.047193 | 0.055687 | 0.11165 | 0.12399 | 0.27932 | 0.0331 | -119.9016 | -67.5539 | -120.7099 | 0.052459 | 0.15564 | 0.14969 | -122.8902 | 122.4666 | 0.001784 | 122.5398 | 122.4892 | 0.022587 | 0.014127 | 0.16946 | -0.45671 | -0.057404 | 2.5318 | 1.7235 | 2.1803 | 0.04578 | 0.039824 | 122.5451 | 122.5575 | 122.7128 | 122.4807 | -0.076763 | 122.4859 | 122.5891 | 122.5832 | 54.8795 | -123
2152.5469 | 122.6074 | -122.4472 | 0.11444 | 1.4211e-13 | 0.0025791 | -0.0097224 | -0.026217 | -0.023789 | 0.0039977 | 0.0036627 | -0.011293 | 0.028408 | 0.044157 | 0.0017713 | 0.049356 | 0.10177 | 0.047193 | 0.064843 | 0.10249 | 0.13773 | 0.27932 | 0.0331 | -119.8604 | -67.8241 | -120.6825 | 0.057037 | 0.15564 | 0.14969 | -122.8856 | 122.4803 | -0.011951 | 122.549 | 122.512 | 0.031743 | 0.023286 | 0.16488 | -0.4384 | -0.057404 | 2.5868 | 1.7647 | 2.2031 | 0.041202 | 0.035246 | 122.5497 | 122.5849 | 122.7265 | 122.4944 | -0.081341 | 122.5042 | 122.6028 | 122.5969 | 54.6231 | -123
2154.2656 | 122.5891 | -122.4609 | 0.1236 | 1.4211e-13 | 0.0030063 | -0.0097224 | -0.026217 | -0.023789 | 0.0042113 | 0.011293 | -0.011934 | 0.028622 | 0.044798 | 0.0015577 | 0.049997 | 0.092615 | 0.051771 | 0.060265 | 0.11165 | 0.13315 | 0.2839 | 0.028521 | -119.8009 | -67.9935 | -120.6504 | 0.052459 | 0.16022 | 0.14511 | -122.8765 | 122.4895 | -0.011949 | 122.5536 | 122.5212 | 0.031744 | 0.009552 | 0.16031 | -0.41551 | -0.071137 | 2.66 | 1.8105 | 2.226 | 0.036626 | 0.021513 | 122.5726 | 122.5941 | 122.7448 | 122.5127 | -0.095075 | 122.5134 | 122.6212 | 122.606 | 54.4675 | -123
2156.0469 | 122.5983 | -122.4289 | 0.11444 | 1.4211e-13 | 0.0030063 | -0.009295 | -0.02643 | -0.023576 | 0.0039977 | 0.018923 | -0.011293 | 0.028194 | 0.044798 | 0.0011303 | 0.049783 | 0.092615 | 0.051771 | 0.064843 | 0.10707 | 0.12399 | 0.2839 | 0.037679 | -119.7368 | -68.1263 | -120.6092 | 0.066194 | 0.16022 | 0.14969 | -122.881 | 122.4666 | -0.007373 | 122.5215 | 122.4937 | 0.027164 | 0.009549 | 0.16946 | -0.45213 | -0.048247 | 2.6921 | 1.8197 | 2.2718 | 0.045781 | 0.035246 | 122.536 | 122.5529 | 122.7128 | 122.4807 | -0.076762 | 122.4951 | 122.5891 | 122.5786 | 54.3026 | -122.9955
2157.8281 | 122.6166 | -122.4426 | 0.09613 | 1.4211e-13 | 0.0027927 | -0.0095086 | -0.02643 | -0.023362 | 0.0042113 | 0.011293 | -0.011507 | 0.028622 | 0.044584 | 0.0013439 | 0.049783 | 0.10177 | 0.051771 | 0.060265 | 0.10707 | 0.13315 | 0.2839 | 0.037679 | -119.6681 | -68.1675 | -120.5634 | 0.057037 | 0.1648 | 0.15427 | -122.8856 | 122.4803 | 0.010938 | 122.5444 | 122.5029 | 0.022586 | 0.037018 | 0.18777 | -0.44298 | -0.039093 | 2.7745 | 1.8792 | 2.3222 | 0.06867 | 0.058136 | 122.5497 | 122.5758 | 122.7265 | 122.4944 | -0.058451 | 122.4997 | 122.6074 | 122.5969 | 54.2752 | -122.9817
2159.6406 | 122.6028 | -122.4472 | 0.09613 | 1.4211e-13 | 0.0032201 | -0.0097224 | -0.02643 | -0.023789 | 0.0042113 | 0.011293 | -0.011507 | 0.028622 | 0.044584 | 0.0015577 | 0.049997 | 0.10177 | 0.051771 | 0.060265 | 0.1208 | 0.13773 | 0.2839 | 0.028521 | -119.5857 | -68.2087 | -120.5085 | 0.061616 | 0.16938 | 0.14511 | -122.881 | 122.4757 | 0.024674 | 122.549 | 122.5075 | 0.031744 | 0.041597 | 0.18777 | -0.43382 | -0.034514 | 2.8615 | 1.9387 | 2.3726 | 0.073249 | 0.048979 | 122.568 | 122.5849 | 122.7311 | 122.499 | -0.067609 | 122.5088 | 122.6166 | 122.5923 | 54.2385 | -122.9772
2161.4375 | 122.6303 | -122.406 | 0.091553 | 1.4211e-13 | 0.0027927 | -0.0097224 | -0.026644 | -0.023789 | 0.0046387 | 0.011293 | -0.011293 | 0.028408 | 0.044798 | 0.0015577 | 0.050211 | 0.092615 | 0.047193 | 0.069421 | 0.11165 | 0.13315 | 0.2839 | 0.037679 | -119.5216 | -68.3231 | -120.4673 | 0.057037 | 0.1648 | 0.14969 | -122.881 | 122.4437 | 0.020094 | 122.4986 | 122.4754 | 0.031742 | 0.041595 | 0.19235 | -0.47502 | -0.034516 | 2.8844 | 1.9387 | 2.4138 | 0.073247 | 0.058134 | 122.5177 | 122.5392 | 122.6899 | 122.4532 | -0.053874 | 122.463 | 122.5708 | 122.5557 | 54.0829 | -122.9726
2163.1719 | 122.6532 | -122.4106 | 0.091553 | 1.4211e-13 | 0.0030063 | -0.009295 | -0.026644 | -0.023789 | 0.0044249 | 0.011293 | -0.011507 | 0.028622 | 0.044798 | 0.0015577 | 0.049997 | 0.10177 | 0.051771 | 0.064843 | 0.11622 | 0.12857 | 0.28848 | 0.028521 | -119.43 | -68.0942 | -120.4123 | 0.061616 | 0.1648 | 0.15427 | -122.8765 | 122.4391 | 0.024672 | 122.5124 | 122.4754 | 0.036322 | 0.037016 | 0.19693 | -0.46587 | -0.029937 | 2.9806 | 1.9983 | 2.4641 | 0.073247 | 0.062713 | 122.5268 | 122.5392 | 122.6991 | 122.4624 | -0.063032 | 122.4722 | 122.5754 | 122.5648 | 54.3164 | -122.968
2164.9688 | 122.5708 | -122.4335 | 0.11902 | 1.4211e-13 | 0.0027927 | -0.0097224 | -0.026644 | -0.023789 | 0.0042113 | 0.011293 | -0.011507 | 0.028622 | 0.044798 | 0.0019849 | 0.050424 | 0.10177 | 0.051771 | 0.060265 | 0.11165 | 0.13773 | 0.28848 | 0.0331 | -119.4209 | -68.2682 | -120.3894 | 0.057037 | 0.16022 | 0.14511 | -122.8765 | 122.4666 | -0.007372 | 122.5352 | 122.4937 | 0.027165 | 0.018708 | 0.16946 | -0.44298 | -0.061982 | 3.0126 | 2.044 | 2.487 | 0.041203 | 0.02609 | 122.5451 | 122.5712 | 122.722 | 122.4852 | -0.085919 | 122.4905 | 122.5937 | 122.5786 | 54.1653 | -122.9955
2166.6875 | 122.7173 | -122.3831 | 0.07782 | 1.4211e-13 | 0.0025791 | -0.0095086 | -0.026217 | -0.023789 | 0.0037841 | 0.0036627 | -0.011079 | 0.028622 | 0.045011 | 0.0013439 | 0.049783 | 0.10177 | 0.051771 | 0.055687 | 0.11622 | 0.13773 | 0.28848 | 0.037679 | -119.3613 | -68.0118 | -120.3482 | 0.061616 | 0.1648 | 0.14969 | -122.8856 | 122.4208 | 0.038405 | 122.4849 | 122.4388 | 0.018008 | 0.059907 | 0.21066 | -0.50249 | -0.016204 | 3.0218 | 2.0349 | 2.5374 | 0.08698 | 0.071867 | 122.4993 | 122.5208 | 122.6716 | 122.4349 | -0.040141 | 122.4447 | 122.5479 | 122.5328 | 54.3713 | -122.9634
2168.4844 | 122.699 | -122.3694 | 0.10071 | 1.4211e-13 | 0.0030063 | -0.009295 | -0.026644 | -0.023362 | 0.0039977 | 0.0036627 | -0.011507 | 0.028408 | 0.044584 | 0.0017713 | 0.050211 | 0.097194 | 0.047193 | 0.060265 | 0.11622 | 0.12857 | 0.28848 | 0.037679 | -119.3018 | -67.9477 | -120.2979 | 0.061616 | 0.16022 | 0.15884 | -122.8765 | 122.4071 | 0.015517 | 122.4666 | 122.4296 | 0.022586 | 0.027861 | 0.18777 | -0.50707 | -0.039092 | 3.0676 | 2.0715 | 2.5786 | 0.059514 | 0.058137 | 122.4856 | 122.498 | 122.6579 | 122.4166 | -0.063029 | 122.431 | 122.5296 | 122.5282 | 54.4217 | -122.9772
2170.2344 | 122.6898 | -122.3969 | 0.073242 | 1.4211e-13 | 0.0027927 | -0.0095086 | -0.02643 | -0.023362 | 0.0039977 | 0.0036627 | -0.011293 | 0.028622 | 0.04437 | 0.0017713 | 0.050424 | 0.10635 | 0.05635 | 0.064843 | 0.11622 | 0.12857 | 0.28848 | 0.037679 | -119.2377 | -67.9156 | -120.2429 | 0.061616 | 0.16938 | 0.14969 | -122.8719 | 122.4345 | 0.042983 | 122.5032 | 122.4617 | 0.027164 | 0.055327 | 0.21524 | -0.47502 | -0.011626 | 3.1591 | 2.1539 | 2.629 | 0.096137 | 0.076445 | 122.5131 | 122.5254 | 122.6853 | 122.4532 | -0.035563 | 122.4585 | 122.5662 | 122.5465 | 54.4812 | -122.9451
2172.0156 | 122.5708 | -122.4564 | 0.11902 | 1.4211e-13 | 0.0032201 | -0.009295 | -0.026003 | -0.023362 | 0.0042113 | 0.018923 | -0.011293 | 0.028408 | 0.04437 | 0.0015577 | 0.050424 | 0.11093 | 0.051771 | 0.060265 | 0.11622 | 0.13315 | 0.28848 | 0.037679 | -119.169 | -67.8149 | -120.188 | 0.066194 | 0.16022 | 0.14969 | -122.8765 | 122.494 | -0.002794 | 122.5673 | 122.5166 | 0.022586 | 0.014129 | 0.16946 | -0.42009 | -0.052825 | 3.2873 | 2.2684 | 2.6885 | 0.041203 | 0.030668 | 122.5726 | 122.5895 | 122.7448 | 122.5081 | -0.08134 | 122.5226 | 122.6166 | 122.606 | 54.6414 | -122.9955
2173.7812 | 122.5845 | -122.4289 | 0.10529 | 1.4211e-13 | 0.0027927 | -0.0095086 | -0.026217 | -0.023576 | 0.0044249 | 0.011293 | -0.010652 | 0.028622 | 0.044798 | 0.0017713 | 0.050211 | 0.097194 | 0.051771 | 0.064843 | 0.11165 | 0.13773 | 0.2839 | 0.0331 | -119.082 | -67.6913 | -120.133 | 0.066194 | 0.1648 | 0.14511 | -122.881 | 122.462 | 0.006361 | 122.5261 | 122.4937 | 0.031743 | 0.032441 | 0.17862 | -0.45213 | -0.039092 | 3.3469 | 2.2959 | 2.748 | 0.059514 | 0.039823 | 122.5405 | 122.5666 | 122.7128 | 122.4807 | -0.072186 | 122.4951 | 122.5937 | 122.574 | 54.7376 | -122.9863
2175.5 | 122.6074 | -122.4518 | 0.10529 | 1.4211e-13 | 0.0030063 | -0.0095086 | -0.026217 | -0.023576 | 0.0042113 | 0.011293 | -0.011079 | 0.028835 | 0.044584 | 0.0017713 | 0.050424 | 0.10177 | 0.05635 | 0.060265 | 0.11165 | 0.13315 | 0.28848 | 0.0331 | -119.0088 | -67.6089 | -120.0598 | 0.057037 | 0.1648 | 0.14969 | -122.8765 | 122.4849 | 0.006361 | 122.5536 | 122.512 | 0.027165 | 0.027862 | 0.18319 | -0.42467 | -0.048249 | 3.443 | 2.392 | 2.8167 | 0.059514 | 0.044401 | 122.5634 | 122.5849 | 122.7403 | 122.5081 | -0.072186 | 122.5088 | 122.6166 | 122.6015 | 54.8429 | -122.9817
2177.2188 | 122.6944 | -122.3602 | 0.059509 | 1.4211e-13 | 0.0030063 | -0.0095086 | -0.026217 | -0.023576 | 0.0039977 | 0.011293 | -0.011507 | 0.028835 | 0.044798 | 0.0017713 | 0.050424 | 0.10177 | 0.05635 | 0.069421 | 0.11622 | 0.12857 | 0.2839 | 0.0331 | -118.9309 | -67.6409 | -120.0094 | 0.066194 | 0.1648 | 0.15427 | -122.8719 | 122.3933 | 0.056716 | 122.462 | 122.4297 | 0.036321 | 0.06906 | 0.22439 | -0.51164 | 0.006685 | 3.4293 | 2.3508 | 2.8625 | 0.10529 | 0.094757 | 122.4765 | 122.4888 | 122.6441 | 122.4166 | -0.026409 | 122.4264 | 122.525 | 122.5145 | 54.7193 | -122.9314
2179 | 122.5983 | -122.4289 | 0.10529 | 1.4211e-13 | 0.0030063 | -0.0095086 | -0.026217 | -0.023576 | 0.0039977 | 0.0036627 | -0.011079 | 0.028622 | 0.045011 | 0.0019849 | 0.050638 | 0.10177 | 0.05635 | 0.064843 | 0.1208 | 0.14231 | 0.29306 | 0.0331 | -118.8531 | -67.4486 | -119.9407 | 0.061616 | 0.1648 | 0.15427 | -122.8719 | 122.462 | 0.015518 | 122.5307 | 122.4937 | 0.031743 | 0.03702 | 0.18777 | -0.44298 | -0.04367 | 3.5758 | 2.4882 | 2.9312 | 0.059514 | 0.04898 | 122.5497 | 122.5712 | 122.722 | 122.4852 | -0.072186 | 122.4905 | 122.5937 | 122.5832 | 54.9803 | -122.9772
2180.7812 | 122.6624 | -122.4289 | 0.07782 | 1.4211e-13 | 0.0032201 | -0.0095086 | -0.026644 | -0.023362 | 0.0044249 | 0.0036627 | -0.010652 | 0.028622 | 0.045011 | 0.0015577 | 0.050851 | 0.10177 | 0.05635 | 0.064843 | 0.1208 | 0.13773 | 0.28848 | 0.037679 | -118.757 | -67.27 | -119.8858 | 0.061616 | 0.16938 | 0.15427 | -122.881 | 122.4666 | 0.042984 | 122.5307 | 122.4937 | 0.027164 | 0.059907 | 0.21066 | -0.45213 | -0.016204 | 3.6719 | 2.5431 | 2.9953 | 0.091559 | 0.076446 | 122.5497 | 122.5666 | 122.7174 | 122.4852 | -0.040141 | 122.4905 | 122.5983 | 122.5832 | 55.1588 | -122.9588
2182.4844 | 122.5937 | -122.4106 | 0.11902 | 1.4211e-13 | 0.0030063 | -0.0095086 | -0.026217 | -0.023789 | 0.0042113 | 0.011293 | -0.010866 | 0.028408 | 0.044798 | 0.0017713 | 0.050851 | 0.11551 | 0.051771 | 0.069421 | 0.11622 | 0.14231 | 0.2839 | 0.0331 | -118.6745 | -67.2105 | -119.8308 | 0.061616 | 0.16938 | 0.15427 | -122.8765 | 122.4437 | -0.002794 | 122.5261 | 122.48 | 0.036321 | 0.023287 | 0.16488 | -0.46587 | -0.057403 | 3.7361 | 2.5798 | 3.0456 | 0.05036 | 0.035247 | 122.5268 | 122.5529 | 122.6945 | 122.4624 | -0.085919 | 122.4722 | 122.58 | 122.5648 | 55.2001 | -122.9955
2184.2188 | 122.7081 | -122.3969 | 0.064087 | 1.4211e-13 | 0.0030063 | -0.0097224 | -0.026217 | -0.023576 | 0.0037841 | -0.0039678 | -0.010225 | 0.028408 | 0.044798 | 0.0021987 | 0.051065 | 0.10177 | 0.051771 | 0.064843 | 0.11165 | 0.13315 | 0.2839 | 0.028521 | -118.5738 | -67.0228 | -119.7576 | 0.066194 | 0.17396 | 0.16342 | -122.8673 | 122.4254 | 0.04756 | 122.4986 | 122.4617 | 0.036322 | 0.069061 | 0.21982 | -0.47044 | 0.002107 | 3.823 | 2.6393 | 3.1097 | 0.10987 | 0.099336 | 122.5085 | 122.53 | 122.6808 | 122.4486 | -0.035566 | 122.463 | 122.5708 | 122.5603 | 55.3741 | -122.9314
2185.9688 | 122.6715 | -122.3785 | 0.10071 | 1.4211e-13 | 0.0032201 | -0.0095086 | -0.026217 | -0.023362 | 0.0039977 | 0.018923 | -0.010652 | 0.029049 | 0.044584 | 0.0019849 | 0.050638 | 0.10177 | 0.060928 | 0.074 | 0.10707 | 0.12857 | 0.29306 | 0.028521 | -118.4914 | -66.8213 | -119.6889 | 0.066194 | 0.1648 | 0.15884 | -122.8719 | 122.4071 | 0.00636 | 122.4803 | 122.4525 | 0.045479 | 0.027861 | 0.19235 | -0.49333 | -0.034514 | 3.8872 | 2.6897 | 3.183 | 0.064092 | 0.058137 | 122.4856 | 122.5071 | 122.6716 | 122.4395 | -0.072187 | 122.4447 | 122.5433 | 122.5374 | 55.5572 | -122.9726
2187.6875 | 122.6532 | -122.4152 | 0.09613 | 1.4211e-13 | 0.0034337 | -0.0095086 | -0.02643 | -0.023576 | 0.0044249 | 0.011293 | -0.010225 | 0.028835 | 0.044798 | 0.0021987 | 0.051065 | 0.11093 | 0.047193 | 0.074 | 0.11622 | 0.13773 | 0.29306 | 0.037679 | -118.4044 | -66.5649 | -119.6248 | 0.066194 | 0.17396 | 0.16342 | -122.8719 | 122.4528 | 0.020095 | 122.5261 | 122.4892 | 0.036321 | 0.041597 | 0.19693 | -0.45671 | -0.029936 | 4.0108 | 2.7904 | 3.2471 | 0.077828 | 0.067293 | 122.5314 | 122.5529 | 122.7082 | 122.4624 | -0.058451 | 122.4814 | 122.5891 | 122.5786 | 55.8502 | -122.968
2189.4062 | 122.5937 | -122.4014 | 0.082397 | 1.4211e-13 | 0.0030063 | -0.0095086 | -0.026217 | -0.023789 | 0.0039977 | 0.011293 | -0.0097976 | 0.028835 | 0.045011 | 0.0019849 | 0.051492 | 0.10635 | 0.065507 | 0.074 | 0.1208 | 0.14231 | 0.29764 | 0.037679 | -118.322 | -66.5008 | -119.5653 | 0.075351 | 0.1648 | 0.15427 | -122.8673 | 122.4391 | 0.038407 | 122.5078 | 122.4754 | 0.036321 | 0.059909 | 0.21524 | -0.46586 | -0.007046 | 4.0795 | 2.8362 | 3.302 | 0.082403 | 0.071869 | 122.5222 | 122.5437 | 122.6991 | 122.4669 | -0.044718 | 122.4768 | 122.5662 | 122.5557 | 55.9006 | -122.9497
2191.1094 | 122.6074 | -122.4243 | 0.11902 | 1.4211e-13 | 0.0034337 | -0.0095086 | -0.026217 | -0.023148 | 0.0044249 | 0.011293 | -0.0095838 | 0.029049 | 0.044798 | 0.0021987 | 0.051279 | 0.11093 | 0.065507 | 0.064843 | 0.1208 | 0.14231 | 0.30222 | 0.0331 | -118.2396 | -66.2627 | -119.5057 | 0.066194 | 0.16938 | 0.16342 | -122.8673 | 122.4574 | 0.001785 | 122.5352 | 122.4892 | 0.031743 | 0.023287 | 0.1832 | -0.44298 | -0.052825 | 4.1848 | 2.9186 | 3.3616 | 0.05036 | 0.044404 | 122.5451 | 122.5666 | 122.7265 | 122.4898 | -0.085919 | 122.4905 | 122.5937 | 122.5877 | 56.1616 | -122.9863
2192.8438 | 122.58 | -122.4472 | 0.11444 | 1.4211e-13 | 0.0032201 | -0.009295 | -0.026003 | -0.023576 | 0.0044249 | 0.0036627 | -0.010225 | 0.029049 | 0.044584 | 0.0017713 | 0.051279 | 0.11551 | 0.060928 | 0.069421 | 0.1208 | 0.14231 | 0.29764 | 0.0331 | -118.1526 | -66.1757 | -119.4371 | 0.070773 | 0.16938 | 0.16342 | -122.8536 | 122.4803 | 0.006363 | 122.5627 | 122.5166 | 0.036321 | 0.027865 | 0.1832 | -0.40635 | -0.043668 | 4.2946 | 3.0102 | 3.4165 | 0.054938 | 0.048982 | 122.568 | 122.5895 | 122.7448 | 122.5081 | -0.081341 | 122.518 | 122.6166 | 122.6106 | 56.2715 | -122.968
2194.5469 | 122.5433 | -122.4243 | 0.13733 | 1.4211e-13 | 0.0036475 | -0.009295 | -0.026217 | -0.023789 | 0.0042113 | 0.011293 | -0.010011 | 0.028835 | 0.045011 | 0.0024123 | 0.051279 | 0.10635 | 0.070086 | 0.078578 | 0.12538 | 0.13773 | 0.28848 | 0.0331 | -118.0747 | -66.0063 | -119.3684 | 0.070773 | 0.16938 | 0.168 | -122.8627 | 122.4574 | -0.011947 | 122.5307 | 122.5029 | 0.045478 | 0.000398 | 0.15115 | -0.4384 | -0.066556 | 4.3496 | 3.0559 | 3.4943 | 0.03205 | 0.030673 | 122.5497 | 122.562 | 122.7128 | 122.4944 | -0.10423 | 122.4951 | 122.5937 | 122.5923 | 56.418 | -123
2196.25 | 121.907 | -121.6095 | 0.10529 | 1.4211e-13 | 1.2825 | 1.508 | 1.1796 | -0.023576 | 0.0042113 | 0.0036627 | -0.0093702 | 0.029476 | 0.044584 | 0.0021987 | 0.050211 | 19.4546 | 18.7325 | 20.6946 | 21.3142 | 21.155 | 21.405 | 3.971 | -95.2224 | -46.6521 | -96.5206 | 21.5393 | 21.6888 | 21.5547 | -99.7672 | 125.5805 | 21.2089 | 141.0641 | 142.3041 | 16.7236 | 21.0497 | 21.2997 | 21.8423 | 21.434 | 26.3871 | 25.0889 | 3.2465 | 21.5835 | 21.4494 | 142.9237 | 142.7645 | 143.0145 | 140.342 | 3.8657 | 143.1488 | 143.2983 | 143.1642 | 74.9574 | -99.8724
2197.9531 | 122.4609 | -122.2641 | 0.12817 | 1.4211e-13 | 0.015186 | 0.017842 | -0.0061306 | -0.023789 | 0.0042113 | 0.011293 | -0.0091566 | 0.028408 | 0.045225 | 0.0026261 | 0.051065 | 0.11551 | 0.060928 | 0.074 | 0.13912 | 0.14688 | 0.29306 | -0.063057 | -117.7542 | -64.9715 | -119.0936 | 0.070773 | 0.1648 | 0.168 | -122.707 | 122.201 | 0.010943 | 122.3796 | 122.3381 | 0.13706 | 0.018711 | 0.16489 | -0.44293 | -0.057401 | 4.5099 | 3.1704 | 3.6134 | 0.036626 | 0.039828 | 122.4032 | 122.411 | 122.5572 | 122.325 | -0.19123 | 122.3349 | 122.4289 | 122.4321 | 57.2926 | -122.8352
2199.6875 | 122.5296 | -122.2778 | 0.10986 | 1.4211e-13 | 0.013904 | 0.017628 | -0.0057032 | -0.023576 | 0.0037841 | 0.011293 | -0.0095838 | 0.028835 | 0.045011 | 0.0024123 | 0.051706 | 0.11093 | 0.05635 | 0.074 | 0.1208 | 0.14688 | 0.28848 | -0.063057 | -117.7176 | -64.8525 | -119.0708 | 0.061616 | 0.17396 | 0.15884 | -122.7574 | 122.2148 | 0.010941 | 122.3888 | 122.3518 | 0.13706 | 0.037022 | 0.17862 | -0.47957 | -0.048247 | 4.5602 | 3.2071 | 3.6866 | 0.064095 | 0.048982 | 122.3986 | 122.4247 | 122.5663 | 122.3342 | -0.17292 | 122.3394 | 122.4518 | 122.4367 | 57.4253 | -122.8673
2201.3906 | 122.4976 | -122.3328 | 0.1236 | 1.4211e-13 | 0.014117 | 0.017842 | -0.0063442 | -0.023362 | 0.0039977 | 0.011293 | -0.0095838 | 0.028835 | 0.045011 | 0.0026261 | 0.051492 | 0.11093 | 0.051771 | 0.074 | 0.1208 | 0.14231 | 0.29764 | -0.058478 | -117.6489 | -64.8296 | -119.0341 | 0.075351 | 0.16938 | 0.15884 | -122.7803 | 122.2743 | -0.002792 | 122.4437 | 122.4068 | 0.13248 | 0.01871 | 0.17404 | -0.44753 | -0.048245 | 4.6839 | 3.2986 | 3.7462 | 0.045783 | 0.035249 | 122.4536 | 122.4751 | 122.6304 | 122.3845 | -0.18207 | 122.4081 | 122.5021 | 122.4916 | 57.5032 | -122.9039
2203.0938 | 122.5342 | -122.3328 | 0.11444 | 1.4211e-13 | 0.014331 | 0.018483 | -0.0063442 | -0.023789 | 0.0042113 | 0.011293 | -0.0093702 | 0.028835 | 0.044798 | 0.0024123 | 0.05192 | 0.10635 | 0.051771 | 0.069421 | 0.11622 | 0.13773 | 0.28848 | 0.042258 | -117.5848 | -64.6968 | -118.9792 | 0.066194 | 0.17396 | 0.15884 | -122.7849 | 122.375 | 0.001784 | 122.4391 | 122.4022 | 0.027163 | 0.023286 | 0.17404 | -0.45211 | -0.048247 | 4.748 | 3.3536 | 3.8057 | 0.059517 | 0.044404 | 122.449 | 122.4705 | 122.6212 | 122.3845 | -0.072183 | 122.399 | 122.5067 | 122.4916 | 57.636 | -122.8993
2204.8125 | 122.5571 | -122.3282 | 0.10986 | 1.4211e-13 | 0.014331 | 0.018483 | -0.0061306 | -0.023789 | 0.0037841 | 0.011293 | -0.0091566 | 0.029049 | 0.044798 | 0.0026261 | 0.051706 | 0.11551 | 0.060928 | 0.069421 | 0.11622 | 0.13773 | 0.28848 | 0.0331 | -117.5161 | -64.5778 | -118.9288 | 0.066194 | 0.16938 | 0.16342 | -122.7895 | 122.3613 | 0.006362 | 122.4437 | 122.3976 | 0.036321 | 0.027864 | 0.17862 | -0.46127 | -0.043669 | 4.8121 | 3.3994 | 3.8606 | 0.059516 | 0.05356 | 122.4444 | 122.4659 | 122.6167 | 122.3891 | -0.076763 | 122.3944 | 122.4976 | 122.4916 | 57.7504 | -122.8993
2206.6094 | 122.6303 | -122.3328 | 0.082397 | 1.4211e-13 | 0.014117 | 0.018269 | -0.0061306 | -0.023576 | 0.0039977 | 0.011293 | -0.0091566 | 0.028622 | 0.045225 | 0.0024123 | 0.05192 | 0.11551 | 0.05635 | 0.069421 | 0.1208 | 0.14231 | 0.29306 | 0.0331 | -117.4703 | -64.5366 | -118.9059 | 0.066194 | 0.1648 | 0.16342 | -122.7986 | 122.3659 | 0.038407 | 122.4483 | 122.4022 | 0.036321 | 0.059909 | 0.21066 | -0.46585 | -0.016203 | 4.8624 | 3.4268 | 3.8927 | 0.082403 | 0.081026 | 122.4536 | 122.4751 | 122.6258 | 122.3891 | -0.049297 | 122.399 | 122.4976 | 122.4962 | 57.7962 | -122.881
2208.4219 | 122.5204 | -122.3648 | 0.12817 | 1.4211e-13 | 0.014758 | 0.018056 | -0.0057032 | -0.023789 | 0.0039977 | 0.0036627 | -0.008943 | 0.029049 | 0.045011 | 0.0026261 | 0.052347 | 0.11093 | 0.05635 | 0.074 | 0.1208 | 0.14688 | 0.28848 | 0.037679 | -117.42 | -64.4725 | -118.8418 | 0.070773 | 0.1648 | 0.15884 | -122.8078 | 122.4025 | -0.00737 | 122.4757 | 122.4388 | 0.036321 | 0.018711 | 0.16031 | -0.44296 | -0.057401 | 4.9448 | 3.523 | 3.9659 | 0.036626 | 0.030671 | 122.4856 | 122.5117 | 122.6533 | 122.4212 | -0.090495 | 122.4356 | 122.5296 | 122.5237 | 57.8924 | -122.9359
2210.2344 | 122.5616 | -122.374 | 0.10529 | 1.4211e-13 | 0.014545 | 0.017842 | -0.0061306 | -0.023576 | 0.0042113 | 0.018923 | -0.0087294 | 0.028835 | 0.045439 | 0.0026261 | 0.052133 | 0.12009 | 0.05635 | 0.069421 | 0.1208 | 0.14688 | 0.28848 | 0.028521 | -117.3559 | -64.3351 | -118.7869 | 0.066194 | 0.16938 | 0.168 | -122.8078 | 122.4025 | 0.015518 | 122.494 | 122.4434 | 0.0409 | 0.041599 | 0.18319 | -0.4338 | -0.039092 | 5.0181 | 3.5871 | 4.0209 | 0.064093 | 0.062716 | 122.4948 | 122.5208 | 122.6624 | 122.4303 | -0.076765 | 122.4402 | 122.5433 | 122.542 | 58.0389 | -122.9131
2212.0312 | 122.612 | -122.3648 | 0.091553 | 1.4211e-13 | 0.014331 | 0.018483 | -0.0061306 | -0.023362 | 0.0042113 | 0.0036627 | -0.0087294 | 0.029049 | 0.045011 | 0.0028397 | 0.052133 | 0.11093 | 0.051771 | 0.074 | 0.11165 | 0.14688 | 0.29764 | 0.0331 | -117.2963 | -64.271 | -118.7365 | 0.066194 | 0.1648 | 0.15884 | -122.8123 | 122.3979 | 0.020094 | 122.4757 | 122.4388 | 0.0409 | 0.055332 | 0.20609 | -0.44754 | -0.025359 | 5.0685 | 3.6283 | 4.0758 | 0.073247 | 0.067292 | 122.4765 | 122.5117 | 122.6624 | 122.4166 | -0.058453 | 122.431 | 122.5296 | 122.5237 | 58.0938 | -122.9039
2213.8125 | 122.6257 | -122.3373 | 0.091553 | 1.4211e-13 | 0.014758 | 0.018056 | -0.006558 | -0.023362 | 0.0042113 | 0.011293 | -0.0085156 | 0.029263 | 0.045225 | 0.0024123 | 0.052774 | 0.10635 | 0.065507 | 0.074 | 0.1208 | 0.13773 | 0.29306 | 0.042258 | -117.2368 | -64.2756 | -118.677 | 0.075351 | 0.1648 | 0.15884 | -122.8215 | 122.3796 | 0.029251 | 122.4437 | 122.4113 | 0.031742 | 0.046174 | 0.20151 | -0.48416 | -0.016202 | 5.1005 | 3.6604 | 4.1445 | 0.073247 | 0.067292 | 122.4581 | 122.4751 | 122.6304 | 122.4028 | -0.049295 | 122.4127 | 122.5021 | 122.4962 | 58.0618 | -122.9131
2215.625 | 122.5388 | -122.3785 | 0.13733 | 1.4211e-13 | 0.014331 | 0.018056 | -0.0057032 | -0.023362 | 0.0042113 | 0.018923 | -0.0087294 | 0.028835 | 0.045225 | 0.0028397 | 0.05192 | 0.12009 | 0.05635 | 0.078578 | 0.12538 | 0.14688 | 0.29764 | 0.0331 | -117.1681 | -64.2389 | -118.622 | 0.075351 | 0.1648 | 0.168 | -122.8261 | 122.4116 | -0.011947 | 122.4986 | 122.4571 | 0.045478 | 0.009556 | 0.16031 | -0.44754 | -0.061978 | 5.2104 | 3.7565 | 4.204 | 0.027471 | 0.030673 | 122.5039 | 122.5254 | 122.6762 | 122.4349 | -0.10423 | 122.4539 | 122.5433 | 122.5465 | 58.1396 | -122.9634
2217.3594 | 122.5433 | -122.3877 | 0.10529 | 1.4211e-13 | 0.014331 | 0.017842 | -0.0061306 | -0.023789 | 0.0039977 | 0.0036627 | -0.0085156 | 0.028835 | 0.045011 | 0.0028397 | 0.052561 | 0.12009 | 0.05635 | 0.078578 | 0.11622 | 0.14231 | 0.29764 | 0.042258 | -117.104 | -64.1748 | -118.5625 | 0.075351 | 0.1648 | 0.16342 | -122.8307 | 122.43 | 0.010939 | 122.5078 | 122.4663 | 0.03632 | 0.03702 | 0.19235 | -0.44297 | -0.029935 | 5.2837 | 3.8252 | 4.2681 | 0.059514 | 0.058137 | 122.5039 | 122.53 | 122.6853 | 122.444 | -0.063028 | 122.463 | 122.5525 | 122.5511 | 58.2129 | -122.9359
2219.1406 | 122.5388 | -122.3969 | 0.1236 | 1.4211e-13 | 0.014545 | 0.018056 | -0.0061306 | -0.023576 | 0.0042113 | 0.011293 | -0.0085156 | 0.028622 | 0.045011 | 0.0026261 | 0.052133 | 0.11093 | 0.05635 | 0.069421 | 0.11622 | 0.14231 | 0.29764 | 0.0331 | -117.0445 | -64.1519 | -118.4938 | 0.070773 | 0.1648 | 0.16342 | -122.8261 | 122.43 | -0.007371 | 122.5078 | 122.4663 | 0.036321 | 0.01871 | 0.17404 | -0.42923 | -0.052823 | 5.3523 | 3.903 | 4.3322 | 0.041204 | 0.039827 | 122.5131 | 122.5392 | 122.6945 | 122.4532 | -0.090496 | 122.4676 | 122.5617 | 122.5603 | 58.2449 | -122.9497
2220.9219 | 122.5388 | -122.406 | 0.10529 | 1.4211e-13 | 0.014545 | 0.017842 | -0.0057032 | -0.023576 | 0.0042113 | 0.018923 | -0.0087294 | 0.028835 | 0.045225 | 0.0028397 | 0.052133 | 0.11551 | 0.05635 | 0.069421 | 0.12996 | 0.14688 | 0.3068 | 0.0331 | -116.985 | -64.0924 | -118.4389 | 0.070773 | 0.17396 | 0.15884 | -122.8307 | 122.4391 | 0.024674 | 122.5215 | 122.4754 | 0.036321 | 0.041599 | 0.20151 | -0.42466 | -0.034513 | 5.421 | 3.9671 | 4.3918 | 0.068672 | 0.053559 | 122.536 | 122.5529 | 122.7128 | 122.4624 | -0.072186 | 122.4768 | 122.58 | 122.5649 | 58.3136 | -122.9359
2222.7031 | 122.6578 | -122.3602 | 0.09613 | 1.4211e-13 | 0.014331 | 0.018269 | -0.0059168 | -0.023362 | 0.0039977 | 0.011293 | -0.0087294 | 0.029049 | 0.045011 | 0.0030533 | 0.052774 | 0.11093 | 0.060928 | 0.064843 | 0.11622 | 0.14688 | 0.30222 | 0.028521 | -116.9209 | -64.1245 | -118.3885 | 0.070773 | 0.16938 | 0.16342 | -122.8352 | 122.3888 | 0.020095 | 122.4712 | 122.4251 | 0.036322 | 0.050755 | 0.20609 | -0.47501 | -0.025357 | 5.4393 | 3.9717 | 4.4467 | 0.073249 | 0.067293 | 122.4765 | 122.5071 | 122.6624 | 122.4212 | -0.067609 | 122.431 | 122.5296 | 122.5237 | 58.2358 | -122.9314
2224.4844 | 122.6074 | -122.3831 | 0.11902 | 1.4211e-13 | 0.014545 | 0.018056 | -0.0059168 | -0.023789 | 0.0042113 | 0.011293 | -0.008302 | 0.028835 | 0.045225 | 0.0028397 | 0.052774 | 0.11093 | 0.065507 | 0.074 | 0.12538 | 0.13773 | 0.29764 | 0.0331 | -116.8614 | -64.2206 | -118.3244 | 0.075351 | 0.16938 | 0.15884 | -122.8307 | 122.4162 | 0.006363 | 122.494 | 122.4571 | 0.0409 | 0.018708 | 0.17862 | -0.44754 | -0.043668 | 5.5218 | 4.0587 | 4.5062 | 0.05036 | 0.039826 | 122.5085 | 122.5208 | 122.6808 | 122.4486 | -0.085919 | 122.4585 | 122.5525 | 122.542 | 58.1625 | -122.9497
2226.2188 | 122.644 | -122.3694 | 0.09613 | 1.4211e-13 | 0.014545 | 0.018056 | -0.0059168 | -0.023789 | 0.0042113 | -0.0039678 | -0.008302 | 0.029049 | 0.045225 | 0.0030533 | 0.052774 | 0.11551 | 0.060928 | 0.069421 | 0.12538 | 0.14231 | 0.29306 | 0.0331 | -116.8018 | -64.1565 | -118.2649 | 0.07993 | 0.16938 | 0.15884 | -122.8352 | 122.4025 | 0.029252 | 122.4849 | 122.4388 | 0.036321 | 0.046176 | 0.19693 | -0.46586 | -0.0162 | 5.5675 | 4.1045 | 4.5703 | 0.073249 | 0.062715 | 122.4948 | 122.5117 | 122.6624 | 122.4303 | -0.06303 | 122.4493 | 122.5388 | 122.5282 | 58.2129 | -122.9314
2227.9219 | 122.6486 | -122.3877 | 0.086975 | 1.4211e-13 | 0.014758 | 0.018056 | -0.0059168 | -0.023148 | 0.0039977 | 0.011293 | -0.0080884 | 0.029263 | 0.045011 | 0.0032671 | 0.052561 | 0.12009 | 0.060928 | 0.074 | 0.12538 | 0.13773 | 0.29306 | 0.0331 | -116.7423 | -64.271 | -118.2145 | 0.075351 | 0.17396 | 0.16342 | -122.8352 | 122.4208 | 0.038407 | 122.5078 | 122.4617 | 0.0409 | 0.050752 | 0.20608 | -0.44755 | -0.011624 | 5.6454 | 4.1732 | 4.6207 | 0.086983 | 0.076448 | 122.5131 | 122.5254 | 122.6808 | 122.4486 | -0.053875 | 122.463 | 122.5617 | 122.5511 | 58.1167 | -122.9222
2229.6406 | 122.5845 | -122.3831 | 0.11902 | 1.4211e-13 | 0.014331 | 0.018056 | -0.0061306 | -0.023576 | 0.0039977 | 0.011293 | -0.0085156 | 0.029049 | 0.045225 | 0.0030533 | 0.052988 | 0.11551 | 0.065507 | 0.078578 | 0.12538 | 0.15146 | 0.3068 | 0.037679 | -116.6691 | -64.216 | -118.1504 | 0.070773 | 0.1648 | 0.168 | -122.8398 | 122.4208 | 0.006363 | 122.4986 | 122.4617 | 0.040899 | 0.032444 | 0.18778 | -0.4567 | -0.048246 | 5.7141 | 4.2327 | 4.6894 | 0.045781 | 0.048983 | 122.5085 | 122.5346 | 122.6899 | 122.4486 | -0.08134 | 122.4539 | 122.5479 | 122.5511 | 58.1671 | -122.9588
2231.3594 | 122.6532 | -122.3694 | 0.10071 | 1.4211e-13 | 0.014972 | 0.017842 | -0.0057032 | -0.023789 | 0.0042113 | 0.011293 | -0.0078748 | 0.029049 | 0.045225 | 0.0034807 | 0.052988 | 0.11551 | 0.060928 | 0.069421 | 0.11622 | 0.14231 | 0.29764 | 0.037679 | -116.6095 | -64.1657 | -118.0818 | 0.075351 | 0.16938 | 0.16342 | -122.8307 | 122.4071 | 0.015517 | 122.4849 | 122.4388 | 0.031742 | 0.041598 | 0.19693 | -0.46128 | -0.025357 | 5.7599 | 4.2876 | 4.7489 | 0.068671 | 0.062715 | 122.4856 | 122.5117 | 122.667 | 122.4303 | -0.063029 | 122.4447 | 122.5388 | 122.5328 | 58.2037 | -122.9314
2233.1406 | 122.644 | -122.3511 | 0.10071 | 1.4211e-13 | 0.014758 | 0.018269 | -0.0057032 | -0.023362 | 0.0042113 | 0.0036627 | -0.0080884 | 0.029049 | 0.045439 | 0.0030533 | 0.052988 | 0.11551 | 0.065507 | 0.074 | 0.1208 | 0.14231 | 0.30222 | 0.037679 | -116.5317 | -64.1611 | -118.0085 | 0.075351 | 0.17396 | 0.168 | -122.8307 | 122.3888 | 0.020096 | 122.4666 | 122.4251 | 0.036321 | 0.041598 | 0.20151 | -0.47959 | -0.025357 | 5.8194 | 4.3426 | 4.8222 | 0.07325 | 0.067294 | 122.4719 | 122.4934 | 122.6533 | 122.4166 | -0.063029 | 122.4264 | 122.525 | 122.5191 | 58.19 | -122.9314
2234.9219 | 122.5754 | -122.406 | 0.11444 | 1.4211e-13 | 0.014972 | 0.018269 | -0.0059168 | -0.023362 | 0.0042113 | 0.011293 | -0.0080884 | 0.029049 | 0.045439 | 0.0034807 | 0.053202 | 0.11551 | 0.070086 | 0.078578 | 0.1208 | 0.15146 | 0.30222 | 0.037679 | -116.4813 | -64.184 | -117.9444 | 0.075351 | 0.16938 | 0.16342 | -122.8398 | 122.4437 | 0.006363 | 122.5215 | 122.4846 | 0.040899 | 0.037022 | 0.18778 | -0.43381 | -0.03909 | 5.9247 | 4.4616 | 4.8954 | 0.054938 | 0.048982 | 122.5268 | 122.5575 | 122.7082 | 122.4761 | -0.076762 | 122.4814 | 122.5754 | 122.5694 | 58.222 | -122.9543
2236.7188 | 122.6669 | -122.3557 | 0.10071 | 1.4211e-13 | 0.014972 | 0.018269 | -0.0057032 | -0.023576 | 0.0039977 | 0.011293 | -0.0076612 | 0.029049 | 0.045225 | 0.0036943 | 0.053202 | 0.11551 | 0.060928 | 0.074 | 0.1208 | 0.15146 | 0.30222 | 0.037679 | -116.4126 | -64.3076 | -117.8803 | 0.075351 | 0.16938 | 0.16342 | -122.8352 | 122.3933 | 0.020096 | 122.4712 | 122.4297 | 0.036321 | 0.050755 | 0.20151 | -0.47959 | -0.025357 | 5.943 | 4.4754 | 4.9549 | 0.068671 | 0.062715 | 122.4765 | 122.5071 | 122.6579 | 122.4166 | -0.063029 | 122.431 | 122.525 | 122.5191 | 58.048 | -122.9359
2238.5156 | 122.6486 | -122.3694 | 0.09613 | 1.4211e-13 | 0.014758 | 0.018269 | -0.0057032 | -0.023576 | 0.0037841 | 0.026554 | -0.0078748 | 0.029263 | 0.045439 | 0.0030533 | 0.053415 | 0.11551 | 0.065507 | 0.074 | 0.1208 | 0.15604 | 0.29764 | 0.0331 | -116.3394 | -64.2252 | -117.807 | 0.084508 | 0.17396 | 0.15884 | -122.8352 | 122.4025 | 0.024674 | 122.4849 | 122.4434 | 0.0409 | 0.059912 | 0.20151 | -0.46586 | -0.011622 | 6.03 | 4.5624 | 5.0282 | 0.077828 | 0.062715 | 122.4902 | 122.5254 | 122.667 | 122.4349 | -0.06303 | 122.4539 | 122.5433 | 122.5282 | 58.1442 | -122.9314
2240.25 | 122.6715 | -122.3465 | 0.09613 | 1.4211e-13 | 0.015186 | 0.018697 | -0.0054896 | -0.024217 | 0.0039977 | 0.011293 | -0.0076612 | 0.028622 | 0.045652 | 0.0036943 | 0.053202 | 0.11093 | 0.060928 | 0.078578 | 0.12996 | 0.14688 | 0.30222 | 0.037679 | -116.2799 | -64.2664 | -117.7521 | 0.075351 | 0.17396 | 0.16342 | -122.8398 | 122.3842 | 0.03383 | 122.4574 | 122.4251 | 0.040899 | 0.050755 | 0.20609 | -0.49332 | -0.020779 | 6.0666 | 4.5944 | 5.0877 | 0.077828 | 0.067293 | 122.4765 | 122.4934 | 122.6487 | 122.4074 | -0.058451 | 122.4218 | 122.5205 | 122.5099 | 58.0801 | -122.9359
2242.0312 | 122.5937 | -122.406 | 0.11902 | 1.4211e-13 | 0.014972 | 0.018911 | -0.0057032 | -0.023789 | 0.0042113 | 0.011293 | -0.0076612 | 0.028835 | 0.045652 | 0.0036943 | 0.053415 | 0.12009 | 0.070086 | 0.074 | 0.12996 | 0.15146 | 0.30222 | 0.042258 | -116.2112 | -64.1977 | -117.6788 | 0.07993 | 0.16938 | 0.16342 | -122.8352 | 122.4483 | 0.010941 | 122.5261 | 122.48 | 0.031742 | 0.032444 | 0.1832 | -0.42923 | -0.039089 | 6.1948 | 4.7272 | 5.1564 | 0.05036 | 0.044404 | 122.536 | 122.5575 | 122.7082 | 122.4761 | -0.076761 | 122.4859 | 122.5754 | 122.5694 | 58.2083 | -122.9543
2243.7969 | 122.6532 | -122.3465 | 0.10986 | 1.4211e-13 | 0.015399 | 0.018483 | -0.0052758 | -0.023576 | 0.0039977 | 0.0036627 | -0.0074474 | 0.029049 | 0.045225 | 0.0036943 | 0.053629 | 0.12009 | 0.060928 | 0.074 | 0.12538 | 0.16062 | 0.30222 | 0.037679 | -116.1425 | -64.1611 | -117.601 | 0.070773 | 0.17396 | 0.168 | -122.8398 | 122.3842 | 0.015519 | 122.4666 | 122.4205 | 0.036321 | 0.050758 | 0.19235 | -0.49332 | -0.03909 | 6.204 | 4.7455 | 5.2388 | 0.064095 | 0.058139 | 122.4719 | 122.5071 | 122.6487 | 122.4074 | -0.072184 | 122.4173 | 122.5205 | 122.5145 | 58.1854 | -122.9497
2245.5312 | 122.6303 | -122.3694 | 0.09613 | 1.4211e-13 | 0.015399 | 0.018269 | -0.0052758 | -0.023362 | 0.0042113 | 0.0036627 | -0.0072338 | 0.029049 | 0.045652 | 0.0034807 | 0.053415 | 0.12466 | 0.065507 | 0.087735 | 0.1208 | 0.16062 | 0.3068 | 0.037679 | -116.0784 | -64.1474 | -117.5506 | 0.07993 | 0.17396 | 0.17716 | -122.8352 | 122.4071 | 0.024674 | 122.494 | 122.4571 | 0.050056 | 0.064491 | 0.21067 | -0.46586 | -0.0162 | 6.291 | 4.8188 | 5.2846 | 0.077828 | 0.081029 | 122.4902 | 122.53 | 122.6762 | 122.4349 | -0.058451 | 122.4493 | 122.5433 | 122.5465 | 58.222 | -122.9314
2247.3125 | 122.5891 | -122.3694 | 0.13733 | 1.4211e-13 | 0.015399 | 0.017842 | -0.0050622 | -0.023576 | 0.0039977 | -0.0039678 | -0.0076612 | 0.029263 | 0.045225 | 0.0036943 | 0.053629 | 0.12009 | 0.074664 | 0.083156 | 0.12996 | 0.16062 | 0.29764 | 0.037679 | -116.0097 | -64.2252 | -117.4728 | 0.07993 | 0.17854 | 0.168 | -122.8307 | 122.4071 | -0.007369 | 122.4895 | 122.4525 | 0.045477 | 0.023292 | 0.16031 | -0.46128 | -0.057399 | 6.3597 | 4.8966 | 5.3579 | 0.041207 | 0.030673 | 122.4993 | 122.53 | 122.667 | 122.444 | -0.09965 | 122.4493 | 122.5479 | 122.5374 | 58.1442 | -122.968
2249.0938 | 122.612 | -122.3785 | 0.11902 | 1.4211e-13 | 0.015827 | 0.018056 | -0.0048484 | -0.023789 | 0.0044249 | 0.0036627 | -0.0074474 | 0.028835 | 0.045439 | 0.0039081 | 0.053629 | 0.12924 | 0.074664 | 0.087735 | 0.12538 | 0.14688 | 0.31137 | 0.042258 | -115.9319 | -64.3168 | -117.3858 | 0.084508 | 0.18311 | 0.17716 | -122.8169 | 122.4208 | 0.006363 | 122.5078 | 122.4663 | 0.045477 | 0.027866 | 0.19235 | -0.43838 | -0.034511 | 6.4467 | 4.9927 | 5.4311 | 0.064096 | 0.05814 | 122.5039 | 122.5254 | 122.6899 | 122.4532 | -0.076761 | 122.463 | 122.5617 | 122.5557 | 58.0618 | -122.9359
2250.875 | 122.5525 | -122.3969 | 0.14648 | 1.4211e-13 | 0.015613 | 0.018056 | -0.0052758 | -0.023789 | 0.0044249 | 0.018923 | -0.0072338 | 0.029049 | 0.045866 | 0.0036943 | 0.054056 | 0.12466 | 0.074664 | 0.083156 | 0.12996 | 0.16062 | 0.31137 | 0.0331 | -115.8769 | -64.2756 | -117.3125 | 0.089087 | 0.17854 | 0.17258 | -122.8261 | 122.43 | -0.016524 | 122.5215 | 122.48 | 0.050056 | 0.014137 | 0.16489 | -0.42923 | -0.057397 | 6.5199 | 5.0843 | 5.5136 | 0.032052 | 0.026096 | 122.5268 | 122.5575 | 122.7082 | 122.4715 | -0.11338 | 122.4859 | 122.5754 | 122.5694 | 58.1213 | -122.9726
2252.6562 | 122.5891 | -122.3602 | 0.15106 | 1.4211e-13 | 0.015827 | 0.018056 | -0.0050622 | -0.023789 | 0.0039977 | 0.011293 | -0.0072338 | 0.029263 | 0.045439 | 0.0039081 | 0.053843 | 0.12466 | 0.074664 | 0.083156 | 0.12996 | 0.15146 | 0.31137 | 0.042258 | -115.7945 | -64.2801 | -117.2347 | 0.07993 | 0.18311 | 0.168 | -122.8215 | 122.4025 | -0.021102 | 122.4849 | 122.4434 | 0.040898 | 0.000401 | 0.16031 | -0.46128 | -0.071132 | 6.5657 | 5.1255 | 5.5868 | 0.032053 | 0.01694 | 122.4902 | 122.5117 | 122.6716 | 122.4349 | -0.1088 | 122.4402 | 122.5433 | 122.5282 | 58.0801 | -122.9726
2254.3906 | 122.5616 | -122.3648 | 0.14648 | 1.4211e-13 | 0.015613 | 0.017842 | -0.0050622 | -0.023576 | 0.0042113 | 0.018923 | -0.0072338 | 0.029263 | 0.045866 | 0.0039081 | 0.053843 | 0.12466 | 0.070086 | 0.083156 | 0.12996 | 0.15604 | 0.31137 | 0.037679 | -115.7258 | -64.2939 | -117.1706 | 0.089087 | 0.18311 | 0.17258 | -122.8307 | 122.4025 | -0.016524 | 122.4895 | 122.448 | 0.045477 | 0.009558 | 0.16489 | -0.46585 | -0.057397 | 6.639 | 5.1942 | 5.6601 | 0.036631 | 0.026096 | 122.4948 | 122.5208 | 122.6762 | 122.4349 | -0.10881 | 122.4539 | 122.5479 | 122.5374 | 58.0709 | -122.9771
2256.1875 | 122.5891 | -122.3694 | 0.11902 | 1.4211e-13 | 0.015613 | 0.017842 | -0.0052758 | -0.023576 | 0.0042113 | 0.0036627 | -0.0074474 | 0.029476 | 0.045866 | 0.0039081 | 0.054056 | 0.12009 | 0.070086 | 0.078578 | 0.12996 | 0.15604 | 0.31595 | 0.037679 | -115.6434 | -64.3534 | -117.0882 | 0.084508 | 0.18311 | 0.17258 | -122.8169 | 122.4071 | 0.010941 | 122.4895 | 122.448 | 0.040899 | 0.037023 | 0.19693 | -0.44754 | -0.034511 | 6.726 | 5.2812 | 5.7287 | 0.064096 | 0.053561 | 122.4993 | 122.5254 | 122.6853 | 122.4395 | -0.08134 | 122.4539 | 122.5525 | 122.542 | 58.016 | -122.9359
2257.9688 | 122.6669 | -122.3511 | 0.10071 | 1.4211e-13 | 0.015613 | 0.018056 | -0.0046348 | -0.023148 | 0.0044249 | 0.011293 | -0.0072338 | 0.029263 | 0.045652 | 0.0036943 | 0.054056 | 0.12466 | 0.074664 | 0.083156 | 0.12538 | 0.15604 | 0.31137 | 0.042258 | -115.5656 | -64.3626 | -117.0103 | 0.084508 | 0.18311 | 0.17716 | -122.8169 | 122.3933 | 0.024674 | 122.4757 | 122.4342 | 0.040898 | 0.055334 | 0.21067 | -0.46585 | -0.0162 | 6.7855 | 5.3407 | 5.8066 | 0.082407 | 0.076451 | 122.4765 | 122.5071 | 122.6624 | 122.4257 | -0.05845 | 122.4356 | 122.5342 | 122.5282 | 57.9885 | -122.9176
2259.6875 | 122.5937 | -122.3465 | 0.13275 | 1.4211e-13 | 0.01604 | 0.018056 | -0.0048484 | -0.023362 | 0.0039977 | -0.0039678 | -0.0070202 | 0.029263 | 0.045866 | 0.0041217 | 0.05427 | 0.12466 | 0.070086 | 0.092313 | 0.13454 | 0.16062 | 0.31595 | 0.037679 | -115.4923 | -64.4999 | -116.9371 | 0.07993 | 0.18769 | 0.17258 | -122.8123 | 122.3842 | 0.001788 | 122.4712 | 122.4388 | 0.054634 | 0.02787 | 0.1832 | -0.46585 | -0.052821 | 6.8542 | 5.4094 | 5.8753 | 0.054942 | 0.039829 | 122.481 | 122.5071 | 122.6624 | 122.4166 | -0.095072 | 122.4264 | 122.5342 | 122.5191 | 57.8466 | -122.9451
2261.4844 | 122.6166 | -122.3511 | 0.11902 | 1.4211e-13 | 0.016468 | 0.017842 | -0.0048484 | -0.024003 | 0.0042113 | 0.0036627 | -0.0068066 | 0.029263 | 0.045866 | 0.0039081 | 0.05427 | 0.12924 | 0.083821 | 0.096891 | 0.13454 | 0.1652 | 0.31595 | 0.042258 | -115.4191 | -64.4953 | -116.8547 | 0.089087 | 0.20143 | 0.18632 | -122.8169 | 122.3933 | 0.01552 | 122.4803 | 122.448 | 0.054633 | 0.046181 | 0.19693 | -0.46585 | -0.029932 | 6.932 | 5.4964 | 5.9623 | 0.08241 | 0.067297 | 122.4856 | 122.5163 | 122.667 | 122.4349 | -0.076761 | 122.4402 | 122.5525 | 122.5374 | 57.8557 | -122.9359
2263.2031 | 122.5708 | -122.3328 | 0.1236 | 1.4211e-13 | 0.016468 | 0.018056 | -0.0042074 | -0.023576 | 0.0039977 | 0.0036627 | -0.0068066 | 0.029476 | 0.045866 | 0.0041217 | 0.054056 | 0.14298 | 0.083821 | 0.10147 | 0.14827 | 0.17436 | 0.31595 | 0.051416 | -115.3229 | -64.5778 | -116.7768 | 0.098244 | 0.20143 | 0.18174 | -122.8032 | 122.3842 | 0.024678 | 122.4757 | 122.4342 | 0.050053 | 0.050762 | 0.19236 | -0.47043 | -0.025352 | 7.0098 | 5.5559 | 6.0264 | 0.077833 | 0.058142 | 122.481 | 122.5071 | 122.6487 | 122.4166 | -0.07218 | 122.431 | 122.5342 | 122.5145 | 57.755 | -122.9268
2264.9844 | 122.5983 | -122.3099 | 0.15564 | 1.4211e-13 | 0.022237 | 0.021047 | 0.00092099 | -0.023362 | 0.0044249 | 0.011293 | -0.0070202 | 0.029476 | 0.045866 | 0.0043353 | 0.05427 | 0.22081 | 0.16624 | 0.17472 | 0.22153 | 0.25678 | 0.4121 | 0.07431 | -115.1398 | -64.5045 | -116.612 | 0.18524 | 0.28384 | 0.27331 | -122.6979 | 122.3842 | 0.065888 | 122.5307 | 122.4846 | 0.10041 | 0.10114 | 0.25646 | -0.388 | 0.029595 | 7.1701 | 5.6979 | 6.0859 | 0.1282 | 0.11767 | 122.5314 | 122.5667 | 122.722 | 122.4761 | -0.08133 | 122.4951 | 122.5937 | 122.5832 | 57.8054 | -122.8535
2266.7656 | 122.5525 | -121.9528 | 0.4303 | 1.4211e-13 | 0.039117 | 0.028099 | 0.017161 | -0.023362 | 0.0042113 | 0.018923 | -0.0068066 | 0.029263 | 0.045652 | 0.0045491 | 0.054056 | 0.4772 | 0.41348 | 0.43568 | 0.46876 | 0.5132 | 0.66851 | 0.27578 | -114.7597 | -64.3351 | -116.2411 | 0.44621 | 0.55398 | 0.4885 | -122.3957 | 122.2286 | 0.038463 | 122.43 | 122.3885 | 0.1599 | 0.082901 | 0.23821 | -0.44285 | 0.015911 | 7.1931 | 5.7117 | 6.1546 | 0.12368 | 0.058206 | 122.4216 | 122.466 | 122.6213 | 122.3663 | -0.15452 | 122.399 | 122.5068 | 122.4413 | 57.6177 | -122.826
2268.5625 | 120.3781 | -91.1728 | 28.5919 | 1.4211e-13 | 2.2737 | 0.76913 | 2.0713 | -0.023148 | 0.0035703 | 0.011293 | -0.0068066 | 0.030331 | 0.044798 | 0.0041217 | 0.052347 | 27.1326 | 26.3925 | 27.1316 | 27.5362 | 27.5472 | 27.6456 | 8.6918 | -84.7142 | -37.8289 | -86.1315 | 28.1461 | 28.2683 | 28.2486 | -91.9649 | 99.8646 | -1.0557 | 118.3054 | 118.3044 | 18.4398 | -1.0448 | -0.94629 | -0.79206 | -0.44581 | 6.4585 | 5.0413 | 5.8333 | -0.32366 | -0.34335 | 118.709 | 118.72 | 118.8184 | 117.5653 | -19.9001 | 119.3189 | 119.4411 | 119.4214 | 53.3438 | -120.5568
2270.3438 | 119.6548 | -104.686 | 14.6942 | 1.4211e-13 | 1.8609 | 0.35033 | 1.626 | -0.024003 | 0.0033567 | 0.011293 | -0.0068066 | 0.029476 | 0.044584 | 0.0043353 | 0.052347 | 13.4386 | 13.8105 | 14.2529 | 14.6297 | 14.7399 | 14.7706 | 8.266 | -97.2095 | -49.4314 | -98.636 | 15.1066 | 15.1735 | 15.227 | -104.7031 | 112.952 | -0.064499 | 118.1246 | 118.9389 | 5.9869 | 0.045703 | 0.076387 | -0.01715 | 0.41234 | 7.4764 | 6.05 | 6.0671 | 0.47924 | 0.53281 | 119.3157 | 119.4259 | 119.4566 | 118.4964 | -6.4282 | 119.7925 | 119.8594 | 119.913 | 55.2546 | -119.3973
2272.0625 | 119.9066 | -91.0217 | 28.8071 | 1.4211e-13 | 0.023305 | 0.016133 | 0.01075 | -0.023362 | 0.0033567 | 0.011293 | -0.0063794 | 0.02969 | 0.045011 | 0.0043353 | 0.052133 | 0.07888 | 0.028878 | 0.037373 | 0.11165 | 0.11025 | 0.27017 | -0.099689 | -79.1511 | -33.2548 | -80.5867 | 33.3976 | 33.5291 | 33.4407 | -86.4886 | 90.922 | -28.6954 | 91.1006 | 91.0591 | 0.13706 | -28.6968 | -28.5369 | 4.5331 | 4.5906 | 11.8706 | 10.435 | 5.9019 | 4.722 | 4.6336 | 91.1334 | 91.132 | 91.2919 | 91.0506 | -28.9068 | 124.4194 | 124.5508 | 124.4624 | 57.7669 | -115.2957
2273.8438 | 121.0831 | -120.7764 | 0.14191 | 1.4211e-13 | 0.023092 | 0.016346 | 0.010109 | -0.023148 | 0.0044249 | 0.011293 | -0.006593 | 0.02969 | 0.044798 | 0.0045491 | 0.053843 | 0.083459 | 0.0243 | 0.041952 | 0.093333 | 0.11483 | 0.25643 | -0.090531 | -113.1068 | -63.5338 | -114.5882 | 0.20355 | 0.31132 | 0.28704 | -120.99 | 120.6858 | -0.048574 | 120.8598 | 120.8183 | 0.13248 | -0.027075 | 0.11452 | -0.21361 | 0.061642 | 7.6695 | 6.1882 | 6.4018 | 0.16941 | 0.14514 | 120.8697 | 120.8912 | 121.0328 | 120.8007 | -0.23244 | 120.9799 | 121.0877 | 121.0634 | 57.2425 | -121.1319
2275.625 | 121.4172 | -120.9274 | 0.25635 | 1.4211e-13 | 0.022664 | 0.015919 | 0.010109 | -0.023362 | 0.0042113 | 0.011293 | -0.0068066 | 0.02969 | 0.045439 | 0.0045491 | 0.054056 | 0.083459 | 0.028878 | 0.041952 | 0.093333 | 0.11025 | 0.26559 | 0.005627 | -113.4319 | -63.8818 | -114.9316 | 0.20355 | 0.29758 | 0.2962 | -121.4433 | 120.9331 | -0.16302 | 121.0109 | 120.9694 | 0.036325 | -0.1461 | 0.00924 | -0.51585 | -0.052799 | 7.4955 | 5.9958 | 6.5117 | 0.041232 | 0.039855 | 121.0208 | 121.0377 | 121.193 | 120.9563 | -0.25072 | 121.131 | 121.225 | 121.2236 | 57.0456 | -121.6996
2277.4062 | 121.2341 | -120.5933 | 0.60425 | 1.4211e-13 | 0.02181 | 0.016133 | 0.0098956 | -0.023576 | 0.0042113 | 0.011293 | -0.0063794 | 0.02969 | 0.045439 | 0.0045491 | 0.054056 | 0.07888 | 0.0243 | 0.032795 | 0.093333 | 0.10567 | 0.26101 | -0.049321 | -112.9878 | -63.3598 | -114.5104 | 0.51031 | 0.60893 | 0.60297 | -121.0907 | 120.5439 | -0.51092 | 120.6721 | 120.6261 | 0.082116 | -0.49857 | -0.34324 | -0.49745 | -0.09394 | 7.6055 | 6.0829 | 6.5803 | 0.004677 | -0.001279 | 120.6866 | 120.6989 | 120.8543 | 120.6176 | -0.65357 | 121.1036 | 121.2022 | 121.1962 | 57.2334 | -121.695
2279.1875 | 121.4767 | -121.0968 | 0.23804 | 1.4211e-13 | 0.021596 | 0.016133 | 0.0098956 | -0.023362 | 0.0042113 | 0.0036627 | -0.0061656 | 0.029476 | 0.045225 | 0.0047627 | 0.05427 | 0.083459 | 0.0243 | 0.037373 | 0.097912 | 0.1011 | 0.26101 | -0.00811 | -113.3632 | -63.7582 | -114.9041 | 0.19439 | 0.28842 | 0.28247 | -121.5761 | 121.0887 | -0.14012 | 121.1803 | 121.1342 | 0.045483 | -0.13694 | 0.022973 | -0.47926 | -0.043645 | 7.7336 | 6.1927 | 6.6719 | 0.050386 | 0.04443 | 121.1947 | 121.1979 | 121.3578 | 121.1211 | -0.24615 | 121.2912 | 121.3852 | 121.3793 | 57.3386 | -121.8141
2280.8906 | 120.4102 | -119.8791 | 0.46234 | 1.4211e-13 | 0.021596 | 0.015919 | 0.009682 | -0.023576 | 0.0039977 | 0.0036627 | -0.0068066 | 0.029263 | 0.044798 | 0.0047627 | 0.053843 | 0.083459 | 0.033457 | 0.037373 | 0.097912 | 0.10567 | 0.27017 | -0.040163 | -111.7057 | -63.0897 | -113.2512 | 0.51489 | 0.60893 | 0.60755 | -119.8727 | 119.839 | -0.36443 | 119.9626 | 119.9165 | 0.077536 | -0.35667 | -0.19217 | 0.006404 | 0.052546 | 8.1734 | 6.6279 | 6.6215 | 0.14658 | 0.14521 | 119.9771 | 119.9848 | 120.1493 | 119.9126 | -0.5025 | 120.394 | 120.4881 | 120.4867 | 56.7895 | -120.3351
2282.6875 | 120.9915 | -120.6299 | 0.091553 | 1.4211e-13 | 0.021596 | 0.015705 | 0.0098956 | -0.023576 | 0.0042113 | 0.018923 | -0.0068066 | 0.029263 | 0.045439 | 0.0043353 | 0.053843 | 0.083459 | 0.019721 | 0.037373 | 0.084176 | 0.11025 | 0.26559 | -0.026426 | -112.6123 | -63.9139 | -114.1853 | 0.13029 | 0.23806 | 0.19547 | -120.9396 | 120.6035 | -0.007377 | 120.7133 | 120.6673 | 0.063799 | 0.0187 | 0.17403 | -0.30973 | 0.03874 | 8.0176 | 6.4446 | 6.7543 | 0.1465 | 0.10392 | 120.7141 | 120.7401 | 120.8955 | 120.6496 | -0.11798 | 120.7602 | 120.8679 | 120.8254 | 56.716 | -121.0312
2284.4688 | 119.5358 | -117.9291 | 1.5381 | 1.4211e-13 | 0.021169 | 0.015919 | 0.009682 | -0.023362 | 0.0039977 | 0.011293 | -0.0063794 | 0.029476 | 0.04437 | 0.0047627 | 0.053415 | 0.083459 | 0.033457 | 0.037373 | 0.088755 | 0.1011 | 0.26559 | -0.044742 | -110.2268 | -62.2609 | -111.7906 | 1.1742 | 1.282 | 1.2119 | -118.5266 | 117.8843 | -1.4493 | 118.0125 | 117.9665 | 0.082115 | -1.437 | -1.2725 | -0.5975 | -0.3639 | 7.7023 | 6.1385 | 6.736 | -0.25611 | -0.32616 | 118.0178 | 118.0302 | 118.1947 | 117.9625 | -1.5828 | 119.1033 | 119.2111 | 119.141 | 55.6681 | -120.0647
2286.25 | 120.9732 | -120.0119 | 0.77362 | 1.4211e-13 | 0.021169 | 0.015919 | 0.0098956 | -0.023148 | 0.0042113 | -0.0039678 | -0.0063794 | 0.02969 | 0.045011 | 0.0047627 | 0.054056 | 0.07888 | 0.028878 | 0.04653 | 0.088755 | 0.11483 | 0.26101 | -0.003531 | -112.42 | -63.8177 | -114.0159 | 0.36838 | 0.47614 | 0.47019 | -120.9442 | 120.0084 | -0.68487 | 120.0908 | 120.0584 | 0.050061 | -0.65879 | -0.51261 | -0.93229 | -0.40525 | 7.5919 | 5.996 | 6.9283 | -0.29748 | -0.30343 | 120.1007 | 120.1267 | 120.2729 | 120.0408 | -0.77715 | 120.3803 | 120.488 | 120.4821 | 56.1942 | -121.7178
2288.0469 | 120.6482 | -119.9799 | 0.41657 | 1.4211e-13 | 0.021596 | 0.015492 | 0.009682 | -0.023362 | 0.0042113 | 0.011293 | -0.0063794 | 0.029904 | 0.044798 | 0.0047627 | 0.054056 | 0.07888 | 0.019721 | 0.037373 | 0.084176 | 0.11025 | 0.26101 | -0.049321 | -111.2708 | -63.2774 | -112.8849 | 0.89032 | 1.0164 | 0.95552 | -119.8315 | 119.9305 | -0.33239 | 120.0587 | 120.0172 | 0.086694 | -0.30631 | -0.15555 | 0.14832 | 0.47376 | 8.7091 | 7.0949 | 6.9466 | 0.59986 | 0.53896 | 120.064 | 120.0901 | 120.2409 | 119.9996 | -0.46589 | 120.8702 | 120.9963 | 120.9354 | 56.7024 | -120.2481
2289.7656 | 115.3198 | -113.7405 | 1.442 | 1.4211e-13 | 0.021596 | 0.015492 | 0.0094682 | -0.023362 | 0.0035703 | 0.011293 | -0.0063794 | 0.029476 | 0.042661 | 0.0045491 | 0.052133 | 0.083459 | 0.033457 | 0.037373 | 0.088755 | 0.11025 | 0.26559 | -0.067636 | -106.0465 | -59.8251 | -107.6102 | 2.5569 | 2.6418 | 2.645 | -114.4194 | 113.6729 | -1.3532 | 113.824 | 113.7779 | 0.10501 | -1.3317 | -1.1764 | -0.67883 | 1.1149 | 7.6941 | 6.1303 | 6.8091 | 1.1999 | 1.2031 | 113.8293 | 113.8508 | 114.0061 | 113.774 | -1.5096 | 116.2974 | 116.3824 | 116.3856 | 53.9155 | -115.8613
2291.5469 | 117.2104 | -78.7308 | 38.8824 | 1.4211e-13 | 0.021596 | 0.015919 | 0.0094682 | -0.023576 | 0.0033567 | 0.011293 | -0.005952 | 0.030117 | 0.043943 | 0.0047627 | 0.052561 | 0.088037 | 0.038035 | 0.041952 | 0.088755 | 0.11025 | 0.27017 | -0.012689 | -90.6254 | -45.5578 | -92.2395 | 19.1723 | 19.1889 | 19.2516 | -99.0574 | 78.7181 | -38.7937 | 78.8188 | 78.7727 | 0.054641 | -38.7722 | -38.6123 | -20.3267 | -19.7102 | -11.8946 | -13.5087 | 6.8179 | -19.6936 | -19.6308 | 78.8195 | 78.841 | 79.0009 | 78.7688 | -38.8951 | 97.903 | 97.9197 | 97.9824 | 33.173 | -137.9399
2293.2656 | 118.3411 | -78.7857 | 39.1891 | 1.4211e-13 | 0.021596 | 0.015705 | 0.009682 | -0.023362 | 0.0035703 | 0.026554 | -0.0057384 | 0.030117 | 0.044157 | 0.0047627 | 0.052774 | 0.07888 | 0.0243 | 0.032795 | 0.084176 | 0.1011 | 0.25643 | -0.035584 | -92.0631 | -46.5193 | -93.6955 | 17.959 | 18.0351 | 18.107 | -100.6051 | 78.7501 | -39.105 | 78.8646 | 78.8185 | 0.068379 | -39.0881 | -38.9327 | -21.8194 | -21.2302 | -13.2774 | -14.9098 | 6.9095 | -21.1541 | -21.0822 | 78.8699 | 78.8868 | 79.0421 | 78.81 | -39.2247 | 96.7447 | 96.8208 | 96.8927 | 32.2664 | -139.7942
2295.0469 | 119.9799 | -119.8975 | 0.11902 | 1.4211e-13 | 0.021596 | 0.015919 | 0.009682 | -0.023576 | 0.0039977 | 0.011293 | -0.005952 | 0.029904 | 0.045011 | 0.0051901 | 0.053629 | 0.088037 | 0.033457 | 0.037373 | 0.088755 | 0.11025 | 0.26101 | -0.012689 | -111.2845 | -63.4102 | -112.9765 | 0.061616 | 0.15564 | 0.13137 | -120.3032 | 119.8848 | -0.030264 | 119.9855 | 119.9348 | 0.050062 | -0.008766 | 0.14199 | -0.40569 | -0.057403 | 8.613 | 6.921 | 7.3267 | 0.036624 | 0.012354 | 119.9862 | 120.0077 | 120.1585 | 119.9309 | -0.13171 | 119.9591 | 120.0531 | 120.0288 | 56.4873 | -120.4222
2296.8438 | 120.3598 | -120.0851 | 0.068665 | 1.4211e-13 | 0.021382 | 0.015492 | 0.0094682 | -0.023789 | 0.0042113 | 0.011293 | -0.005952 | 0.02969 | 0.045011 | 0.0049765 | 0.054484 | 0.07888 | 0.0243 | 0.041952 | 0.084176 | 0.11483 | 0.25643 | 0.010206 | -111.4219 | -63.5979 | -113.123 | 0.043302 | 0.15107 | 0.13595 | -120.5596 | 120.0953 | 0.015511 | 120.164 | 120.1271 | 0.031746 | 0.046167 | 0.18777 | -0.47442 | -0.025363 | 8.6633 | 6.9621 | 7.4366 | 0.0824 | 0.067287 | 120.1693 | 120.2 | 120.3416 | 120.1094 | -0.058459 | 120.1284 | 120.2362 | 120.2211 | 56.4872 | -120.6282
2298.6406 | 120.4926 | -120.1767 | 0.054932 | 1.4211e-13 | 0.021596 | 0.015705 | 0.009682 | -0.023789 | 0.0044249 | 0.011293 | -0.0055248 | 0.029904 | 0.045225 | 0.0051901 | 0.054484 | 0.083459 | 0.0243 | 0.037373 | 0.093333 | 0.11483 | 0.26559 | 0.010206 | -111.4081 | -63.7811 | -113.1413 | 0.04788 | 0.14649 | 0.14053 | -120.6695 | 120.1869 | 0.038401 | 120.2602 | 120.2141 | 0.027167 | 0.0599 | 0.21066 | -0.49276 | -0.007052 | 8.7686 | 7.0354 | 7.5281 | 0.091554 | 0.085598 | 120.27 | 120.2915 | 120.4423 | 120.201 | -0.044726 | 120.2246 | 120.3232 | 120.3172 | 56.3956 | -120.7244
2300.3594 | 120.5063 | -120.2774 | 0.054932 | 1.4211e-13 | 0.021596 | 0.015705 | 0.0094682 | -0.023362 | 0.0042113 | 0.011293 | -0.005952 | 0.029904 | 0.045225 | 0.0054037 | 0.055125 | 0.083459 | 0.0243 | 0.041952 | 0.084176 | 0.11483 | 0.25643 | 0.023942 | -111.3852 | -64.0558 | -113.1322 | 0.043302 | 0.15107 | 0.14053 | -120.7519 | 120.3013 | 0.029244 | 120.3609 | 120.3194 | 0.01801 | 0.0599 | 0.2015 | -0.47447 | -0.01163 | 8.8922 | 7.1452 | 7.6197 | 0.096133 | 0.085598 | 120.3616 | 120.3922 | 120.5338 | 120.3017 | -0.03099 | 120.3207 | 120.4285 | 120.4179 | 56.2216 | -120.8068
2302.1406 | 120.4742 | -120.3461 | 0.073242 | 1.4211e-13 | 0.021596 | 0.016133 | 0.0094682 | -0.023789 | 0.0046387 | 0.034184 | -0.0061656 | 0.029904 | 0.045439 | 0.0054037 | 0.054911 | 0.083459 | 0.028878 | 0.037373 | 0.084176 | 0.11483 | 0.26559 | 0.014784 | -111.3349 | -64.1199 | -113.0955 | 0.04788 | 0.15107 | 0.13595 | -120.8022 | 120.3609 | 0.010934 | 120.4295 | 120.3834 | 0.022589 | 0.04159 | 0.19235 | -0.45618 | -0.025362 | 9.0112 | 7.2505 | 7.7067 | 0.077823 | 0.06271 | 120.4302 | 120.4609 | 120.6117 | 120.3749 | -0.058458 | 120.3939 | 120.4971 | 120.482 | 56.2262 | -120.8755
2303.8438 | 120.5109 | -120.2225 | 0.21973 | 1.4211e-13 | 0.021382 | 0.015919 | 0.0098956 | -0.023576 | 0.0046387 | 0.011293 | -0.0055248 | 0.030117 | 0.045225 | 0.0054037 | 0.055552 | 0.088037 | 0.033457 | 0.037373 | 0.088755 | 0.11025 | 0.26101 | -0.00811 | -111.138 | -64.1107 | -112.9124 | 0.15776 | 0.26553 | 0.24584 | -120.7152 | 120.2144 | -0.13097 | 120.3105 | 120.2598 | 0.045483 | -0.10947 | 0.041283 | -0.49278 | -0.061963 | 9.0845 | 7.3101 | 7.8029 | 0.045803 | 0.026111 | 120.3112 | 120.3327 | 120.4835 | 120.2559 | -0.22784 | 120.3802 | 120.488 | 120.4683 | 56.1117 | -120.935
2305.6406 | 120.5475 | -120.2728 | 0.25177 | 1.4211e-13 | 0.021596 | 0.015705 | 0.0098956 | -0.023789 | 0.0042113 | 0.011293 | -0.0057384 | 0.029904 | 0.045225 | 0.0056175 | 0.055125 | 0.088037 | 0.033457 | 0.037373 | 0.097912 | 0.11025 | 0.25643 | -0.035584 | -110.9686 | -64.2023 | -112.775 | 0.20813 | 0.30674 | 0.2962 | -120.6786 | 120.2372 | -0.15386 | 120.3609 | 120.3102 | 0.072957 | -0.14152 | 0.004661 | -0.40579 | -0.043643 | 9.3043 | 7.4978 | 7.9036 | 0.054967 | 0.044433 | 120.3707 | 120.3831 | 120.5293 | 120.3063 | -0.28735 | 120.481 | 120.5796 | 120.569 | 56.0705 | -120.9304
2307.3594 | 120.6573 | -120.4605 | 0.068665 | 1.4211e-13 | 0.021596 | 0.015492 | 0.009682 | -0.023789 | 0.0046387 | 0.011293 | -0.0053112 | 0.02969 | 0.045439 | 0.0056175 | 0.055338 | 0.092615 | 0.0243 | 0.04653 | 0.088755 | 0.11025 | 0.26559 | 0.014784 | -111.083 | -64.4267 | -112.8987 | 0.057037 | 0.15564 | 0.14053 | -120.8938 | 120.4753 | 0.02009 | 120.5531 | 120.507 | 0.031746 | 0.041588 | 0.19692 | -0.43331 | -0.011628 | 9.3775 | 7.5619 | 7.9952 | 0.086978 | 0.071865 | 120.5493 | 120.5708 | 120.7261 | 120.4848 | -0.053881 | 120.5175 | 120.6162 | 120.601 | 56.0338 | -120.9625
2309.1406 | 120.6162 | -120.3461 | 0.21515 | 1.4211e-13 | 0.02181 | 0.015492 | 0.009041 | -0.023789 | 0.0044249 | 0.011293 | -0.0055248 | 0.030545 | 0.045652 | 0.0056175 | 0.055552 | 0.088037 | 0.033457 | 0.041952 | 0.093333 | 0.11025 | 0.26559 | 0.019363 | -110.8907 | -64.5823 | -112.7521 | 0.15318 | 0.25179 | 0.23668 | -120.8206 | 120.3654 | -0.12182 | 120.4341 | 120.388 | 0.022589 | -0.1049 | 0.050439 | -0.47449 | -0.061964 | 9.4553 | 7.5939 | 8.0684 | 0.036645 | 0.021532 | 120.4394 | 120.4563 | 120.6117 | 120.3795 | -0.19579 | 120.4993 | 120.5979 | 120.5828 | 55.7637 | -121.0357
2310.9219 | 120.7306 | -120.4926 | 0.054932 | 1.4211e-13 | 0.021382 | 0.015919 | 0.0098956 | -0.024003 | 0.0042113 | 0.011293 | -0.0055248 | 0.030331 | 0.045652 | 0.0058311 | 0.055552 | 0.083459 | 0.0243 | 0.037373 | 0.088755 | 0.11025 | 0.26559 | 0.014784 | -110.909 | -64.88 | -112.8071 | 0.052459 | 0.15107 | 0.14053 | -120.9808 | 120.5073 | 0.033823 | 120.576 | 120.5299 | 0.022589 | 0.055321 | 0.21066 | -0.48826 | -0.002473 | 9.5835 | 7.6855 | 8.1737 | 0.096133 | 0.085598 | 120.5813 | 120.6028 | 120.7581 | 120.5169 | -0.040148 | 120.545 | 120.6436 | 120.6331 | 55.6126 | -121.0358
2312.6406 | 120.7809 | -120.5521 | 0.068665 | 1.4211e-13 | 0.021382 | 0.015705 | 0.0094682 | -0.023789 | 0.0044249 | 0.011293 | -0.0050974 | 0.030117 | 0.045439 | 0.0056175 | 0.055979 | 0.083459 | 0.0243 | 0.032795 | 0.084176 | 0.10567 | 0.26559 | -0.003531 | -110.8175 | -64.9395 | -112.7384 | 0.052459 | 0.15564 | 0.13595 | -121.0174 | 120.5485 | 0.015511 | 120.6355 | 120.5849 | 0.036326 | 0.037009 | 0.19692 | -0.46539 | -0.016206 | 9.7346 | 7.8137 | 8.279 | 0.086978 | 0.067287 | 120.6362 | 120.6577 | 120.8177 | 120.5764 | -0.072196 | 120.6045 | 120.7077 | 120.688 | 55.6126 | -121.0861
2314.4375 | 120.8633 | -120.5933 | 0.07782 | 1.4211e-13 | 0.021169 | 0.015492 | 0.009682 | -0.023789 | 0.0042113 | 0.011293 | -0.0044566 | 0.030117 | 0.045652 | 0.0058311 | 0.055979 | 0.07888 | 0.0243 | 0.041952 | 0.088755 | 0.11025 | 0.26559 | 0.023942 | -110.7305 | -65.173 | -112.6651 | 0.052459 | 0.15564 | 0.14053 | -121.0358 | 120.6172 | 0.010935 | 120.6721 | 120.6352 | 0.01801 | 0.032433 | 0.18777 | -0.4425 | -0.025361 | 9.8628 | 7.9281 | 8.3706 | 0.077823 | 0.06271 | 120.682 | 120.7035 | 120.8588 | 120.6176 | -0.053878 | 120.6457 | 120.7489 | 120.7338 | 55.4203 | -121.1136
2316.1562 | 120.8908 | -120.5841 | 0.064087 | 1.4211e-13 | 0.021382 | 0.015492 | 0.0098956 | -0.023789 | 0.0044249 | 0.011293 | -0.0046702 | 0.030331 | 0.045652 | 0.0058311 | 0.056193 | 0.07888 | 0.0243 | 0.037373 | 0.079598 | 0.11025 | 0.26101 | -0.00811 | -110.6389 | -65.3928 | -112.5827 | 0.043302 | 0.15107 | 0.13137 | -121.0816 | 120.576 | 0.015511 | 120.663 | 120.6215 | 0.045483 | 0.046166 | 0.19692 | -0.49745 | -0.020785 | 9.9452 | 8.0014 | 8.4988 | 0.086978 | 0.067286 | 120.6637 | 120.6944 | 120.8451 | 120.6084 | -0.072197 | 120.6274 | 120.7352 | 120.7155 | 55.1913 | -121.1456
2317.9219 | 120.7169 | -120.0027 | 0.5722 | 1.4211e-13 | 0.021382 | 0.015919 | 0.009682 | -0.023789 | 0.0042113 | 0.011293 | -0.0050974 | 0.030331 | 0.045439 | 0.0060447 | 0.055979 | 0.07888 | 0.028878 | 0.041952 | 0.088755 | 0.10567 | 0.26101 | -0.00811 | -109.8651 | -65.0036 | -111.8318 | 0.58356 | 0.69592 | 0.68996 | -120.4176 | 119.9946 | -0.48345 | 120.0816 | 120.0447 | 0.050062 | -0.46653 | -0.31119 | -0.41488 | 0.011359 | 10.1377 | 8.1709 | 8.5858 | 0.12371 | 0.11776 | 120.0915 | 120.1084 | 120.2638 | 120.0316 | -0.58031 | 120.5863 | 120.6987 | 120.6927 | 54.9992 | -120.9898
2319.7031 | 120.845 | -120.6619 | 0.09613 | 1.4211e-13 | 0.021382 | 0.015705 | 0.0094682 | -0.023362 | 0.0039977 | 0.0036627 | -0.0048838 | 0.030545 | 0.045866 | 0.0060447 | 0.056406 | 0.07888 | 0.028878 | 0.04653 | 0.097912 | 0.11025 | 0.26101 | -0.003531 | -110.4008 | -65.6309 | -112.3858 | 0.043302 | 0.14191 | 0.13595 | -121.1136 | 120.6584 | 0.001782 | 120.7408 | 120.7085 | 0.050061 | 0.014123 | 0.16488 | -0.45168 | -0.052828 | 10.2611 | 8.2761 | 8.7278 | 0.045777 | 0.039822 | 120.7598 | 120.7722 | 120.9229 | 120.6908 | -0.099661 | 120.7052 | 120.8038 | 120.7979 | 55.0311 | -121.2097
2321.4844 | 120.8496 | -120.694 | 0.10986 | 1.4211e-13 | 0.021596 | 0.015705 | 0.009682 | -0.023789 | 0.0042113 | 0.0036627 | -0.0048838 | 0.030545 | 0.045866 | 0.0060447 | 0.05662 | 0.083459 | 0.028878 | 0.037373 | 0.088755 | 0.11025 | 0.26101 | -0.017268 | -110.3092 | -65.8278 | -112.3126 | 0.04788 | 0.15107 | 0.13595 | -121.1502 | 120.6767 | -0.021108 | 120.7774 | 120.7313 | 0.054641 | 0.00039 | 0.15115 | -0.45627 | -0.061983 | 10.3847 | 8.3814 | 8.8377 | 0.041202 | 0.026089 | 120.7827 | 120.8042 | 120.955 | 120.7228 | -0.12713 | 120.7418 | 120.845 | 120.8299 | 54.8662 | -121.2601
2323.25 | 120.845 | -120.7581 | 0.086975 | 1.4211e-13 | 0.021169 | 0.015705 | 0.009682 | -0.023576 | 0.0044249 | 0.011293 | -0.0048838 | 0.030545 | 0.045866 | 0.0064721 | 0.056834 | 0.07888 | 0.028878 | 0.037373 | 0.088755 | 0.11483 | 0.26101 | -0.012689 | -110.1673 | -65.8964 | -112.221 | 0.052459 | 0.15107 | 0.14053 | -121.1731 | 120.7454 | 0.00178 | 120.8369 | 120.7954 | 0.050062 | 0.027857 | 0.17404 | -0.41507 | -0.034516 | 10.5908 | 8.5371 | 8.9521 | 0.06409 | 0.053555 | 120.8468 | 120.8729 | 121.0191 | 120.7869 | -0.099664 | 120.8105 | 120.9091 | 120.8986 | 54.8616 | -121.2601
2324.9844 | 121.0144 | -120.7306 | 0.064087 | 1.4211e-13 | 0.021382 | 0.015705 | 0.0098956 | -0.023576 | 0.0044249 | 0.0036627 | -0.0044566 | 0.030331 | 0.04608 | 0.0062585 | 0.05662 | 0.07888 | 0.028878 | 0.041952 | 0.088755 | 0.11025 | 0.25643 | 0.005627 | -110.0711 | -66.1025 | -112.1432 | 0.052459 | 0.14191 | 0.13595 | -121.1914 | 120.7362 | 0.024668 | 120.8095 | 120.7725 | 0.036325 | 0.046166 | 0.19234 | -0.46085 | -0.011628 | 10.6595 | 8.5874 | 9.0483 | 0.07782 | 0.071865 | 120.8193 | 120.8408 | 120.987 | 120.7595 | -0.05846 | 120.7831 | 120.8725 | 120.8665 | 54.6281 | -121.2555
2326.7656 | 120.9503 | -120.7809 | 0.091553 | 1.4211e-13 | 0.021169 | 0.015705 | 0.0094682 | -0.023362 | 0.0039977 | 0.026554 | -0.0044566 | 0.030331 | 0.046293 | 0.0064721 | 0.05662 | 0.083459 | 0.0243 | 0.041952 | 0.084176 | 0.11025 | 0.26101 | 0.019363 | -109.9521 | -66.4321 | -112.0653 | 0.043302 | 0.14191 | 0.13595 | -121.2143 | 120.8003 | -0.007377 | 120.8644 | 120.8229 | 0.022589 | 0.0187 | 0.16946 | -0.43339 | -0.048251 | 10.8289 | 8.7156 | 9.149 | 0.050354 | 0.044399 | 120.8651 | 120.8912 | 121.042 | 120.8052 | -0.07219 | 120.8242 | 120.9229 | 120.9169 | 54.3488 | -121.3059
2328.5625 | 121.0464 | -120.7397 | 0.086975 | 1.4211e-13 | 0.021382 | 0.015919 | 0.0098956 | -0.023576 | 0.0046387 | 0.011293 | -0.0046702 | 0.030972 | 0.046293 | 0.0064721 | 0.056834 | 0.07888 | 0.0243 | 0.041952 | 0.084176 | 0.11025 | 0.26101 | 0.001048 | -109.8239 | -66.5787 | -111.96 | 0.057037 | 0.14649 | 0.14053 | -121.2327 | 120.7408 | -0.002799 | 120.8186 | 120.7817 | 0.040904 | 0.023278 | 0.17404 | -0.49291 | -0.029938 | 10.9159 | 8.7797 | 9.2726 | 0.059511 | 0.053555 | 120.8239 | 120.85 | 121.0008 | 120.764 | -0.085927 | 120.7968 | 120.8862 | 120.8803 | 54.1611 | -121.3196
2330.2969 | 120.9961 | -120.8038 | 0.10071 | 1.4211e-13 | 0.021382 | 0.015492 | 0.0098956 | -0.023576 | 0.0042113 | 0.011293 | -0.004243 | 0.030758 | 0.045866 | 0.0064721 | 0.057261 | 0.083459 | 0.0243 | 0.041952 | 0.088755 | 0.10567 | 0.26101 | -0.012689 | -109.6774 | -66.7252 | -111.8593 | 0.057037 | 0.15564 | 0.15427 | -121.2372 | 120.7911 | -0.011953 | 120.8873 | 120.8458 | 0.054641 | 0.004966 | 0.1603 | -0.4334 | -0.043671 | 11.1265 | 8.9445 | 9.3779 | 0.054935 | 0.053558 | 120.8926 | 120.9095 | 121.0648 | 120.8281 | -0.1134 | 120.8609 | 120.9595 | 120.9581 | 54.0787 | -121.3379
2332.0781 | 120.9824 | -120.8038 | 0.068665 | 1.4211e-13 | 0.021382 | 0.015919 | 0.0094682 | -0.023789 | 0.0044249 | 0.018923 | -0.0040292 | 0.030758 | 0.046293 | 0.0066857 | 0.057475 | 0.07888 | 0.033457 | 0.04653 | 0.088755 | 0.11025 | 0.26101 | -0.00811 | -109.5446 | -66.7984 | -111.7402 | 0.043302 | 0.13733 | 0.13595 | -121.2601 | 120.7957 | 0.02009 | 120.8827 | 120.8504 | 0.05464 | 0.041588 | 0.19235 | -0.45629 | -0.025363 | 11.2592 | 9.0636 | 9.5199 | 0.068664 | 0.067287 | 120.8926 | 120.9141 | 121.0648 | 120.8373 | -0.076775 | 120.8471 | 120.9412 | 120.9398 | 54.0054 | -121.3288
2333.8594 | 121.0144 | -120.8496 | 0.086975 | 1.4211e-13 | 0.021596 | 0.015919 | 0.0098956 | -0.023576 | 0.0044249 | 0.0036627 | -0.004243 | 0.031185 | 0.046293 | 0.0068995 | 0.057475 | 0.083459 | 0.028878 | 0.041952 | 0.088755 | 0.10567 | 0.25643 | -0.058478 | -109.4484 | -67.1831 | -111.6945 | 0.043302 | 0.14191 | 0.13595 | -121.2968 | 120.7911 | 0.00178 | 120.9331 | 120.8916 | 0.10043 | 0.018699 | 0.16946 | -0.44715 | -0.043673 | 11.4012 | 9.1552 | 9.6023 | 0.054932 | 0.048977 | 120.9384 | 120.9553 | 121.106 | 120.8785 | -0.14545 | 120.8929 | 120.9915 | 120.9856 | 53.6666 | -121.3837
2335.5781 | 121.1197 | -120.8221 | 0.068665 | 1.4211e-13 | 0.021596 | 0.015705 | 0.009682 | -0.023576 | 0.0037841 | 0.011293 | -0.0038156 | 0.030972 | 0.046293 | 0.0068995 | 0.057475 | 0.083459 | 0.0243 | 0.037373 | 0.088755 | 0.11483 | 0.26101 | -0.053899 | -109.2973 | -67.2746 | -111.5846 | 0.04788 | 0.15564 | 0.14053 | -121.3013 | 120.7682 | 0.02009 | 120.9056 | 120.8595 | 0.091272 | 0.046167 | 0.19235 | -0.47919 | -0.020785 | 11.5248 | 9.2376 | 9.7168 | 0.086978 | 0.071865 | 120.9109 | 120.937 | 121.0832 | 120.8464 | -0.12256 | 120.87 | 120.9778 | 120.9627 | 53.5475 | -121.37
2337.3594 | 120.5383 | -120.9183 | 0.10529 | 1.4211e-13 | 0.021382 | 0.015919 | 0.009682 | -0.023789 | 0.0042113 | -0.0039678 | -0.0038156 | 0.030758 | 0.046507 | 0.0068995 | 0.057475 | 0.088037 | 0.028878 | 0.04653 | 0.084176 | 0.11025 | 0.26101 | -0.085952 | -109.1417 | -67.2975 | -111.493 | 0.04788 | 0.15564 | 0.14053 | -121.3334 | 120.8323 | -0.02111 | 121.0063 | 120.9648 | 0.13248 | 0.004967 | 0.15572 | -0.41511 | -0.057406 | 11.7766 | 9.4253 | 9.8404 | 0.050357 | 0.035244 | 121.0024 | 121.0285 | 121.1793 | 120.9472 | -0.19124 | 120.9662 | 121.0739 | 121.0588 | 53.6208 | -121.4387
2339.1406 | 121.1151 | -120.8771 | 0.07782 | 1.4211e-13 | 0.021596 | 0.015705 | 0.0098956 | -0.023576 | 0.0046387 | 0.011293 | -0.0040292 | 0.031185 | 0.046721 | 0.0068995 | 0.057475 | 0.092615 | 0.033457 | 0.037373 | 0.084176 | 0.1011 | 0.26559 | -0.049321 | -109.0318 | -67.412 | -111.3785 | 0.04788 | 0.16022 | 0.13595 | -121.3517 | 120.8278 | 0.006356 | 120.9697 | 120.9144 | 0.086694 | 0.023275 | 0.18777 | -0.47463 | -0.02994 | 11.8453 | 9.4986 | 9.9732 | 0.082402 | 0.058132 | 120.9613 | 120.9782 | 121.1427 | 120.9105 | -0.12714 | 120.925 | 121.0373 | 121.013 | 53.4651 | -121.4295
2340.8594 | 121.1288 | -120.8908 | 0.082397 | 1.4211e-13 | 0.021382 | 0.015492 | 0.009682 | -0.023789 | 0.0044249 | 0.011293 | -0.0038156 | 0.031185 | 0.046934 | 0.0071131 | 0.058329 | 0.092615 | 0.028878 | 0.04653 | 0.084176 | 0.11025 | 0.26101 | -0.067636 | -108.8853 | -67.5631 | -111.3098 | 0.043302 | 0.14191 | 0.13137 | -121.37 | 120.8232 | 0.001779 | 120.9834 | 120.9373 | 0.11417 | 0.027856 | 0.17861 | -0.47921 | -0.039095 | 12.0056 | 9.581 | 10.0602 | 0.05951 | 0.048976 | 120.975 | 121.0011 | 121.1518 | 120.9197 | -0.15003 | 120.9341 | 121.0327 | 121.0222 | 53.3277 | -121.4524
2342.6406 | 121.0693 | -120.9457 | 0.073242 | 1.4211e-13 | 0.021596 | 0.015919 | 0.0098956 | -0.023789 | 0.0042113 | -0.0039678 | -0.0038156 | 0.030972 | 0.046507 | 0.0071131 | 0.057902 | 0.083459 | 0.019721 | 0.041952 | 0.093333 | 0.11483 | 0.26559 | -0.003531 | -108.7433 | -67.6363 | -111.1771 | 0.043302 | 0.15564 | 0.13595 | -121.3883 | 120.9422 | 0.020091 | 121.0292 | 120.9877 | 0.045483 | 0.04159 | 0.19235 | -0.44259 | -0.02994 | 12.2024 | 9.7687 | 10.2113 | 0.082401 | 0.06271 | 121.0391 | 121.0606 | 121.2113 | 120.9655 | -0.076773 | 120.989 | 121.1014 | 121.0817 | 53.3094 | -121.4616
2344.4219 | 121.1838 | -120.9503 | 0.045776 | 1.4211e-13 | 0.021169 | 0.015705 | 0.009682 | -0.023789 | 0.0044249 | 0.011293 | -0.0033884 | 0.031185 | 0.046507 | 0.0071131 | 0.058757 | 0.088037 | 0.0243 | 0.041952 | 0.088755 | 0.11025 | 0.26101 | 0.001048 | -108.6014 | -67.76 | -111.0901 | 0.043302 | 0.13733 | 0.13137 | -121.4158 | 120.9514 | 0.042979 | 121.0384 | 120.9923 | 0.040904 | 0.064477 | 0.21523 | -0.46549 | -0.002474 | 12.3489 | 9.8603 | 10.3257 | 0.091553 | 0.085597 | 121.0391 | 121.0606 | 121.2113 | 120.9746 | -0.044728 | 120.9936 | 121.0876 | 121.0817 | 53.1903 | -121.4616
2346.1406 | 121.0785 | -120.7626 | 0.24261 | 1.4211e-13 | 0.021596 | 0.015919 | 0.0098956 | -0.023789 | 0.0042113 | 0.011293 | -0.0033884 | 0.031399 | 0.046721 | 0.0073269 | 0.059184 | 0.074302 | 0.0243 | 0.032795 | 0.084176 | 0.11025 | 0.26101 | -0.044742 | -108.3908 | -67.8241 | -110.9573 | 0.066194 | 0.16938 | 0.15427 | -121.4021 | 120.7179 | -0.15844 | 120.8369 | 120.7954 | 0.077537 | -0.13236 | 0.018395 | -0.63944 | -0.17642 | 12.3719 | 9.8054 | 10.4448 | -0.073236 | -0.088349 | 120.8468 | 120.8729 | 121.0236 | 120.7869 | -0.28736 | 120.8288 | 120.932 | 120.9169 | 52.9386 | -121.6447
2347.9219 | 121.2753 | -120.9778 | 0.068665 | 1.4211e-13 | 0.021382 | 0.015492 | 0.0098956 | -0.023789 | 0.0039977 | -0.0039678 | -0.0033884 | 0.031185 | 0.047148 | 0.0075405 | 0.05897 | 0.07888 | 0.028878 | 0.037373 | 0.084176 | 0.11025 | 0.26101 | 0.001048 | -108.2992 | -67.9019 | -110.852 | 0.043302 | 0.15107 | 0.13137 | -121.4479 | 120.9788 | 0.015511 | 121.0567 | 121.0152 | 0.036325 | 0.041588 | 0.19235 | -0.47008 | -0.025363 | 12.6786 | 10.1258 | 10.5959 | 0.0824 | 0.062708 | 121.062 | 121.088 | 121.2388 | 121.0067 | -0.067617 | 121.0211 | 121.1288 | 121.1092 | 53.0759 | -121.5165
2349.7031 | 121.1563 | -121.0373 | 0.10986 | 1.4211e-13 | 0.021596 | 0.015492 | 0.009682 | -0.023576 | 0.0042113 | 0.011293 | -0.0031748 | 0.031613 | 0.046721 | 0.0073269 | 0.059184 | 0.088037 | 0.019721 | 0.041952 | 0.088755 | 0.11025 | 0.26101 | 0.0331 | -108.1756 | -67.9477 | -110.7467 | 0.043302 | 0.15107 | 0.13595 | -121.4524 | 121.0704 | -0.021108 | 121.1253 | 121.0792 | 0.008852 | 0.00039 | 0.15115 | -0.41515 | -0.066561 | 12.8617 | 10.2906 | 10.7058 | 0.041202 | 0.026089 | 121.126 | 121.1475 | 121.2983 | 121.057 | -0.076763 | 121.0806 | 121.1884 | 121.1732 | 53.0896 | -121.5623
2351.4219 | 121.2158 | -121.0602 | 0.086975 | 1.4211e-13 | 0.021382 | 0.015705 | 0.009682 | -0.023789 | 0.0042113 | 0.0036627 | -0.0027474 | 0.031399 | 0.046721 | 0.0079679 | 0.059398 | 0.07888 | 0.028878 | 0.037373 | 0.097912 | 0.10567 | 0.26101 | 0.023942 | -108.0428 | -68.1492 | -110.6322 | 0.043302 | 0.14191 | 0.13137 | -121.4799 | 121.0841 | 0.010937 | 121.1391 | 121.0976 | 0.013431 | 0.018699 | 0.17404 | -0.41973 | -0.043673 | 13.0174 | 10.428 | 10.8477 | 0.054932 | 0.044398 | 121.1581 | 121.1659 | 121.3212 | 121.0891 | -0.063033 | 121.1035 | 121.2021 | 121.1916 | 52.911 | -121.5669
2353.2031 | 121.2341 | -121.0602 | 0.091553 | 1.4211e-13 | 0.021596 | 0.015705 | 0.0098956 | -0.023362 | 0.0044249 | 0.011293 | -0.002961 | 0.031399 | 0.047148 | 0.0079679 | 0.059398 | 0.07888 | 0.0243 | 0.041952 | 0.093333 | 0.11025 | 0.26101 | 0.010206 | -107.9237 | -68.3735 | -110.5086 | 0.04788 | 0.15107 | 0.13137 | -121.4982 | 121.0704 | 0.00178 | 121.1391 | 121.1021 | 0.031746 | 0.0187 | 0.16946 | -0.43805 | -0.043673 | 13.1365 | 10.5516 | 10.9897 | 0.059512 | 0.03982 | 121.1535 | 121.1704 | 121.3212 | 121.0845 | -0.081347 | 121.1081 | 121.2112 | 121.1916 | 52.6867 | -121.5898
2354.9062 | 121.2112 | -121.0739 | 0.068665 | 1.4211e-13 | 0.02181 | 0.015705 | 0.009682 | -0.023576 | 0.0042113 | 0.011293 | -0.0027474 | 0.031613 | 0.047148 | 0.0083951 | 0.059611 | 0.083459 | 0.033457 | 0.037373 | 0.088755 | 0.11025 | 0.26101 | 0.023942 | -107.7726 | -68.5246 | -110.3849 | 0.038723 | 0.15107 | 0.13595 | -121.5074 | 121.0979 | 0.02009 | 121.1574 | 121.1113 | 0.013431 | 0.041588 | 0.19235 | -0.43347 | -0.029942 | 13.3013 | 10.689 | 11.1224 | 0.0824 | 0.067287 | 121.1627 | 121.1842 | 121.3349 | 121.1074 | -0.044723 | 121.1126 | 121.225 | 121.2099 | 52.5493 | -121.576
2356.6875 | 121.3715 | -121.051 | 0.054932 | 1.4211e-13 | 0.021596 | 0.015705 | 0.009682 | -0.023576 | 0.0042113 | 0.0036627 | -0.0025338 | 0.031613 | 0.047361 | 0.0079679 | 0.059825 | 0.083459 | 0.033457 | 0.041952 | 0.084176 | 0.11025 | 0.26559 | 0.005627 | -107.6536 | -68.6849 | -110.3117 | 0.04788 | 0.15107 | 0.13595 | -121.5257 | 121.0567 | 0.029244 | 121.1345 | 121.093 | 0.036325 | 0.055321 | 0.21066 | -0.47467 | -0.007052 | 13.3974 | 10.7393 | 11.214 | 0.096133 | 0.08102 | 121.1352 | 121.1613 | 121.3166 | 121.0845 | -0.049305 | 121.0989 | 121.2021 | 121.187 | 52.3662 | -121.5806
2358.4844 | 121.2387 | -121.1105 | 0.091553 | 1.4211e-13 | 0.021382 | 0.015705 | 0.0094682 | -0.023362 | 0.0046387 | -0.0039678 | -0.0025338 | 0.031613 | 0.047148 | 0.0081815 | 0.060039 | 0.088037 | 0.019721 | 0.032795 | 0.093333 | 0.11025 | 0.25643 | 0.010206 | -107.5391 | -68.7169 | -110.1926 | 0.04788 | 0.13733 | 0.13137 | -121.544 | 121.1207 | 0.00178 | 121.1986 | 121.1433 | 0.022589 | 0.0187 | 0.16488 | -0.43348 | -0.043673 | 13.5714 | 10.9179 | 11.3514 | 0.045776 | 0.03982 | 121.2039 | 121.2208 | 121.367 | 121.1303 | -0.081347 | 121.1584 | 121.2479 | 121.2419 | 52.3936 | -121.6356
2360.2031 | 121.344 | -121.0419 | 0.07782 | 1.4211e-13 | 0.02181 | 0.015919 | 0.0094682 | -0.023789 | 0.0044249 | 0.018923 | -0.0027474 | 0.031613 | 0.047148 | 0.0079679 | 0.060039 | 0.083459 | 0.028878 | 0.041952 | 0.084176 | 0.10567 | 0.25643 | 0.005627 | -107.443 | -69.2068 | -110.1102 | 0.052459 | 0.14649 | 0.13595 | -121.5577 | 121.0475 | 0.006356 | 121.1253 | 121.0838 | 0.036325 | 0.027854 | 0.17861 | -0.51588 | -0.025361 | 13.5989 | 10.9316 | 11.4475 | 0.068666 | 0.058132 | 121.126 | 121.1475 | 121.2983 | 121.0707 | -0.072193 | 121.0943 | 121.1884 | 121.1778 | 51.835 | -121.6356
2361.9844 | 121.3074 | -121.1197 | 0.09613 | 1.4211e-13 | 0.021382 | 0.016133 | 0.0098956 | -0.023576 | 0.0044249 | 0.011293 | -0.0021066 | 0.03204 | 0.047361 | 0.0081815 | 0.060039 | 0.083459 | 0.028878 | 0.041952 | 0.088755 | 0.11025 | 0.26101 | -0.026426 | -107.2964 | -69.335 | -109.9683 | 0.04788 | 0.14649 | 0.13595 | -121.5577 | 121.0933 | -0.007375 | 121.2031 | 121.1616 | 0.068378 | 0.014123 | 0.16488 | -0.43806 | -0.04825 | 13.8233 | 11.1514 | 11.5895 | 0.050356 | 0.039822 | 121.2084 | 121.2299 | 121.3807 | 121.1486 | -0.12256 | 121.1676 | 121.2662 | 121.2556 | 51.7846 | -121.6539
2363.7656 | 121.4081 | -121.0831 | 0.068665 | 1.4211e-13 | 0.02181 | 0.015492 | 0.0098956 | -0.023576 | 0.0042113 | 0.018923 | -0.001893 | 0.031826 | 0.047361 | 0.0081815 | 0.060466 | 0.088037 | 0.028878 | 0.041952 | 0.093333 | 0.096516 | 0.26559 | -0.012689 | -107.182 | -69.5182 | -109.8538 | 0.052459 | 0.15564 | 0.14969 | -121.5623 | 121.0704 | 0.024668 | 121.1711 | 121.125 | 0.054641 | 0.027851 | 0.19692 | -0.47926 | -0.016206 | 13.9011 | 11.2293 | 11.7085 | 0.086978 | 0.081022 | 121.1764 | 121.1796 | 121.3487 | 121.1119 | -0.081354 | 121.1355 | 121.2387 | 121.2328 | 51.5649 | -121.631
2365.5469 | 121.2799 | -121.0236 | 0.11444 | 1.4211e-13 | 0.021596 | 0.015705 | 0.0094682 | -0.023148 | 0.0039977 | -0.0039678 | -0.0021066 | 0.031826 | 0.047361 | 0.0083951 | 0.060466 | 0.07888 | 0.028878 | 0.032795 | 0.093333 | 0.11483 | 0.26101 | -0.017268 | -107.0675 | -69.5869 | -109.689 | 0.084508 | 0.17854 | 0.17258 | -121.5165 | 121.0063 | -0.021108 | 121.1024 | 121.0564 | 0.050063 | 0.000391 | 0.14657 | -0.49298 | -0.029933 | 13.9561 | 11.3346 | 11.8276 | 0.064095 | 0.058139 | 121.1169 | 121.1384 | 121.2846 | 121.0524 | -0.13171 | 121.1081 | 121.2021 | 121.1961 | 51.4367 | -121.631
2367.3281 | 119.902 | -119.6732 | 0.064087 | 1.4211e-13 | 0.021596 | 0.015705 | 0.009682 | -0.023576 | 0.0037841 | 0.0036627 | -0.0021066 | 0.031826 | 0.045652 | 0.0083951 | 0.058543 | 0.088037 | 0.0243 | 0.041952 | 0.088755 | 0.11483 | 0.26101 | -0.081373 | -100.639 | -64.8571 | -103.1552 | 3.4726 | 3.6125 | 3.5058 | -114.7216 | 119.5918 | 0.024668 | 119.7612 | 119.7151 | 0.12333 | 0.050745 | 0.19692 | 4.9516 | 3.4085 | 19.0342 | 16.518 | 11.5664 | 3.5484 | 3.4417 | 119.7619 | 119.788 | 119.9342 | 119.6975 | -0.14546 | 123.1458 | 123.2856 | 123.179 | 54.8161 | -114.7857
2369.0469 | 120.8405 | -120.7672 | 0.10071 | 1.4211e-13 | 0.021596 | 0.015919 | 0.009682 | -0.023576 | 0.0039977 | 0.011293 | -0.0021066 | 0.031613 | 0.047361 | 0.0083951 | 0.06068 | 0.07888 | 0.0243 | 0.041952 | 0.097912 | 0.11025 | 0.25643 | 0.010206 | -106.4768 | -69.7792 | -109.1624 | 0.038723 | 0.15107 | 0.13595 | -121.1777 | 120.7774 | -0.002796 | 120.8461 | 120.8092 | 0.031746 | 0.009545 | 0.15572 | -0.4105 | -0.061985 | 14.2904 | 11.6048 | 12.0153 | 0.050357 | 0.035244 | 120.8651 | 120.8775 | 121.0236 | 120.7915 | -0.090502 | 120.8059 | 120.9183 | 120.9032 | 50.988 | -121.2784
2370.8438 | 121.0739 | -120.8038 | 0.068665 | 1.4211e-13 | 0.02181 | 0.015705 | 0.009682 | -0.023576 | 0.0044249 | 0.018923 | -0.001893 | 0.03204 | 0.047148 | 0.0086089 | 0.06068 | 0.083459 | 0.0243 | 0.032795 | 0.088755 | 0.11025 | 0.26101 | 0.023942 | -106.4219 | -69.9944 | -109.1441 | 0.04788 | 0.13733 | 0.13137 | -121.2968 | 120.8278 | 0.02009 | 120.8873 | 120.8366 | 0.008853 | 0.041588 | 0.19235 | -0.49292 | -0.020785 | 14.3819 | 11.6597 | 12.1526 | 0.068664 | 0.062708 | 120.8926 | 120.9141 | 121.0648 | 120.8281 | -0.044723 | 120.8517 | 120.9412 | 120.9352 | 50.8095 | -121.3654
2372.625 | 121.106 | -120.8633 | 0.073242 | 1.4211e-13 | 0.021596 | 0.015705 | 0.010109 | -0.023576 | 0.0042113 | 0.0036627 | -0.001893 | 0.031826 | 0.047361 | 0.0088225 | 0.06068 | 0.083459 | 0.0243 | 0.037373 | 0.088755 | 0.11025 | 0.25643 | 0.001048 | -106.3074 | -70.1226 | -109.0937 | 0.043302 | 0.13733 | 0.14053 | -121.3471 | 120.8644 | 0.015513 | 120.9468 | 120.9007 | 0.036325 | 0.037011 | 0.18319 | -0.48378 | -0.02994 | 14.5559 | 11.7696 | 12.2534 | 0.064087 | 0.067288 | 120.9521 | 120.9736 | 121.1198 | 120.8876 | -0.072194 | 120.9066 | 121.0007 | 121.0039 | 50.7408 | -121.4204
2374.3594 | 121.1563 | -120.9045 | 0.082397 | 1.4211e-13 | 0.022023 | 0.015919 | 0.0098956 | -0.023576 | 0.0046387 | 0.011293 | -0.001893 | 0.03204 | 0.047361 | 0.0090361 | 0.061107 | 0.074302 | 0.028878 | 0.037373 | 0.084176 | 0.11483 | 0.26101 | 0.028521 | -106.2113 | -70.3195 | -108.9884 | 0.043302 | 0.14649 | 0.13595 | -121.3883 | 120.9331 | 0.001779 | 120.9788 | 120.9419 | 0.008852 | 0.032435 | 0.17861 | -0.48379 | -0.039095 | 14.6933 | 11.9161 | 12.3999 | 0.064089 | 0.053555 | 120.9887 | 121.0194 | 121.1656 | 120.9334 | -0.053876 | 120.9478 | 121.051 | 121.0405 | 50.5851 | -121.4707
2376.1406 | 121.2708 | -120.9274 | 0.07782 | 1.4211e-13 | 0.021596 | 0.015705 | 0.009682 | -0.023576 | 0.0042113 | 0.026554 | -0.0016792 | 0.03204 | 0.047789 | 0.0090361 | 0.061107 | 0.083459 | 0.028878 | 0.037373 | 0.093333 | 0.11483 | 0.25185 | 0.005627 | -106.1014 | -70.5347 | -108.874 | 0.043302 | 0.14191 | 0.13595 | -121.4204 | 120.9331 | 0.015513 | 121.0109 | 120.9648 | 0.031746 | 0.037012 | 0.17403 | -0.49296 | -0.034518 | 14.826 | 12.0535 | 12.5464 | 0.064087 | 0.058132 | 121.0208 | 121.0423 | 121.1793 | 120.9563 | -0.072193 | 120.9707 | 121.0693 | 121.0634 | 50.3928 | -121.4982
2377.9219 | 121.1655 | -120.9869 | 0.082397 | 1.4211e-13 | 0.021596 | 0.015705 | 0.0098956 | -0.023576 | 0.0044249 | 0.0036627 | -0.001252 | 0.03204 | 0.048002 | 0.0088225 | 0.061534 | 0.088037 | 0.028878 | 0.051108 | 0.088755 | 0.10567 | 0.26559 | -0.072215 | -105.9778 | -70.6903 | -108.7687 | 0.04788 | 0.14191 | 0.14511 | -121.4479 | 120.9147 | 0.006358 | 121.075 | 121.038 | 0.12332 | 0.023277 | 0.18319 | -0.46092 | -0.034517 | 15.0092 | 12.2183 | 12.6792 | 0.05951 | 0.062712 | 121.0757 | 121.0926 | 121.2525 | 121.0158 | -0.15461 | 121.0348 | 121.1288 | 121.132 | 50.2966 | -121.5303
2379.7188 | 121.3165 | -121.0098 | 0.11444 | 1.4211e-13 | 0.02181 | 0.015492 | 0.009682 | -0.024003 | 0.0042113 | 0.0036627 | -0.001252 | 0.032467 | 0.047789 | 0.0092499 | 0.061961 | 0.083459 | 0.019721 | 0.041952 | 0.097912 | 0.11483 | 0.25643 | -0.076794 | -105.8313 | -70.759 | -108.6267 | 0.04788 | 0.15107 | 0.14053 | -121.4662 | 120.933 | -0.016529 | 121.0933 | 121.0518 | 0.11875 | 0.000391 | 0.14199 | -0.45635 | -0.066561 | 15.1786 | 12.3831 | 12.8395 | 0.036624 | 0.026089 | 121.1077 | 121.1247 | 121.2663 | 121.0295 | -0.19123 | 121.0577 | 121.1609 | 121.1504 | 50.2508 | -121.5806
2381.4375 | 121.1655 | -121.0831 | 0.091553 | 1.4211e-13 | 0.02181 | 0.015705 | 0.009682 | -0.023576 | 0.0042113 | 0.0036627 | -0.0014656 | 0.03204 | 0.048002 | 0.0092499 | 0.061961 | 0.083459 | 0.0243 | 0.037373 | 0.088755 | 0.10567 | 0.26101 | -0.026426 | -105.6756 | -70.9376 | -108.526 | 0.075351 | 0.17854 | 0.17258 | -121.4524 | 121.0566 | -0.002798 | 121.1665 | 121.1204 | 0.063799 | 0.014121 | 0.16946 | -0.36937 | -0.016202 | 15.4075 | 12.5571 | 12.9264 | 0.086983 | 0.081027 | 121.1718 | 121.1887 | 121.3441 | 121.1074 | -0.11798 | 121.1584 | 121.2616 | 121.2556 | 50.1455 | -121.544
2383.2188 | 121.2982 | -121.0876 | 0.082397 | 1.4211e-13 | 0.02181 | 0.015919 | 0.009682 | -0.023576 | 0.0042113 | 0.0036627 | -0.001252 | 0.032467 | 0.047789 | 0.0092499 | 0.062175 | 0.088037 | 0.028878 | 0.041952 | 0.084176 | 0.11025 | 0.25185 | -0.040163 | -105.5794 | -71.0475 | -108.4756 | 0.052459 | 0.14649 | 0.14053 | -121.5165 | 121.0475 | 0.001779 | 121.1757 | 121.1296 | 0.082115 | 0.027856 | 0.16946 | -0.42889 | -0.029938 | 15.5082 | 12.612 | 13.0409 | 0.064089 | 0.058133 | 121.1718 | 121.1979 | 121.3395 | 121.1165 | -0.12256 | 121.1401 | 121.2341 | 121.2282 | 50.0402 | -121.5989
2384.9219 | 121.2387 | -121.0922 | 0.082397 | 1.4211e-13 | 0.021596 | 0.015705 | 0.009682 | -0.023576 | 0.0044249 | 0.011293 | -0.0010384 | 0.032681 | 0.048002 | 0.0090361 | 0.062175 | 0.083459 | 0.028878 | 0.04653 | 0.088755 | 0.10567 | 0.26101 | 0.019363 | -105.4512 | -71.1848 | -108.384 | 0.04788 | 0.14649 | 0.14053 | -121.5349 | 121.1116 | 0.006358 | 121.1757 | 121.1388 | 0.027167 | 0.023277 | 0.17861 | -0.44263 | -0.034517 | 15.641 | 12.7082 | 13.1508 | 0.064089 | 0.058133 | 121.181 | 121.1979 | 121.3532 | 121.1211 | -0.063034 | 121.1401 | 121.2387 | 121.2328 | 49.9074 | -121.6173
2386.7031 | 121.2891 | -121.0648 | 0.09613 | 1.4211e-13 | 0.02181 | 0.015705 | 0.009682 | -0.023789 | 0.0044249 | 0.011293 | -0.00082475 | 0.03204 | 0.048216 | 0.0094635 | 0.062602 | 0.088037 | 0.028878 | 0.041952 | 0.079598 | 0.10567 | 0.26559 | -0.085952 | -105.2681 | -71.313 | -108.2513 | 0.061616 | 0.15564 | 0.14511 | -121.5394 | 120.9788 | -0.016532 | 121.1528 | 121.1067 | 0.1279 | 0.009544 | 0.16946 | -0.47468 | -0.034514 | 15.7967 | 12.8135 | 13.2882 | 0.059513 | 0.048979 | 121.1444 | 121.1704 | 121.3303 | 121.0936 | -0.18208 | 121.1264 | 121.2204 | 121.2099 | 49.7517 | -121.6356
2388.5 | 120.4468 | -120.4056 | 0.10529 | 1.4211e-13 | 0.02181 | 0.015705 | 0.0098956 | -0.023362 | 0.0042113 | 0.0036627 | -0.00082475 | 0.032467 | 0.047361 | 0.0092499 | 0.061961 | 0.083459 | 0.028878 | 0.041952 | 0.084176 | 0.10567 | 0.26101 | 0.014784 | -103.7479 | -70.4294 | -106.7037 | 0.37753 | 0.48988 | 0.46561 | -119.9506 | 120.4204 | -0.02111 | 120.489 | 120.4475 | 0.027168 | 0.000388 | 0.15572 | 0.45499 | 0.27225 | 16.6576 | 13.7019 | 13.2469 | 0.3846 | 0.36033 | 120.4898 | 120.5113 | 120.6666 | 120.4345 | -0.090502 | 120.7831 | 120.8955 | 120.8712 | 49.9762 | -120.0559
2390.2969 | 121.051 | -120.9091 | 0.091553 | 1.4211e-13 | 0.02181 | 0.015919 | 0.009682 | -0.023576 | 0.0044249 | 0.011293 | -0.0010384 | 0.032254 | 0.048002 | 0.0096773 | 0.062816 | 0.083459 | 0.028878 | 0.037373 | 0.084176 | 0.11025 | 0.25185 | 0.019363 | -104.8194 | -71.4046 | -107.8575 | 0.043302 | 0.13733 | 0.13595 | -121.3334 | 120.9285 | -0.007377 | 120.9926 | 120.9465 | 0.01801 | 0.0187 | 0.1603 | -0.42427 | -0.048251 | 16.0898 | 13.0516 | 13.4759 | 0.045776 | 0.044399 | 120.9933 | 121.0194 | 121.161 | 120.938 | -0.07219 | 120.9524 | 121.0464 | 121.0451 | 49.5045 | -121.4249
2392.0625 | 121.1014 | -120.9778 | 0.10071 | 1.4211e-13 | 0.021596 | 0.016133 | 0.0098956 | -0.023576 | 0.0039977 | 0.011293 | -0.00039735 | 0.032467 | 0.048002 | 0.0096773 | 0.062816 | 0.088037 | 0.033457 | 0.041952 | 0.088755 | 0.11025 | 0.25643 | 0.005627 | -104.7369 | -71.487 | -107.798 | 0.038723 | 0.13733 | 0.12679 | -121.4158 | 120.9834 | -0.011953 | 121.0658 | 121.0197 | 0.036325 | 0.009545 | 0.15572 | -0.43802 | -0.061985 | 16.2408 | 13.1798 | 13.6178 | 0.036621 | 0.026086 | 121.0665 | 121.088 | 121.2342 | 121.0112 | -0.095081 | 121.0165 | 121.1151 | 121.1046 | 49.4907 | -121.5165
2393.8594 | 121.2479 | -120.932 | 0.086975 | 1.4211e-13 | 0.02181 | 0.015919 | 0.0094682 | -0.023362 | 0.0042113 | 0.011293 | -0.00018375 | 0.032895 | 0.048216 | 0.0096773 | 0.063243 | 0.07888 | 0.0243 | 0.037373 | 0.088755 | 0.11025 | 0.26101 | -0.00811 | -104.6179 | -71.6748 | -107.7064 | 0.04788 | 0.14649 | 0.14053 | -121.4524 | 120.9239 | 0.00178 | 121.0109 | 120.9694 | 0.045483 | 0.023278 | 0.17404 | -0.52043 | -0.039095 | 16.3141 | 13.2256 | 13.746 | 0.059511 | 0.053555 | 121.0208 | 121.0423 | 121.193 | 120.9563 | -0.095085 | 120.9799 | 121.0785 | 121.0725 | 49.2572 | -121.5394
2395.5938 | 121.1746 | -121.0236 | 0.10986 | 1.4211e-13 | 0.021382 | 0.015705 | 0.009682 | -0.023789 | 0.0039977 | 0.011293 | -0.00018375 | 0.032895 | 0.048216 | 0.0098909 | 0.06303 | 0.074302 | 0.028878 | 0.032795 | 0.088755 | 0.10567 | 0.26559 | -0.017268 | -104.4347 | -71.7297 | -107.5278 | 0.10282 | 0.19685 | 0.19547 | -121.4204 | 121.0063 | -0.021108 | 121.0979 | 121.0564 | 0.050063 | -0.004189 | 0.15573 | -0.39683 | -0.007041 | 16.5888 | 13.4957 | 13.8926 | 0.086988 | 0.08561 | 121.1123 | 121.1292 | 121.2891 | 121.0524 | -0.12713 | 121.1264 | 121.2204 | 121.219 | 49.2939 | -121.5302
2397.375 | 121.2067 | -121.0693 | 0.086975 | 1.4211e-13 | 0.021382 | 0.015705 | 0.009682 | -0.024003 | 0.0042113 | 0.011293 | -0.00018375 | 0.032895 | 0.04843 | 0.0098909 | 0.063457 | 0.088037 | 0.028878 | 0.041952 | 0.084176 | 0.11025 | 0.25643 | 0.023942 | -104.3615 | -72.0777 | -107.5004 | 0.043302 | 0.14191 | 0.14053 | -121.5074 | 121.0933 | -0.002799 | 121.1574 | 121.1113 | 0.01801 | 0.023278 | 0.16946 | -0.43805 | -0.043673 | 16.7079 | 13.569 | 14.007 | 0.054932 | 0.053555 | 121.1535 | 121.1796 | 121.3258 | 121.0982 | -0.063033 | 121.1126 | 121.2112 | 121.2099 | 48.9916 | -121.5944
2399.1719 | 121.2021 | -120.9869 | 0.1831 | 1.4211e-13 | 0.02181 | 0.015705 | 0.0094682 | -0.023576 | 0.0042113 | 0.0036627 | 0.00024345 | 0.032681 | 0.04843 | 0.010318 | 0.063884 | 0.083459 | 0.028878 | 0.037373 | 0.084176 | 0.11025 | 0.26101 | -0.00811 | -104.2195 | -72.2837 | -107.3447 | 0.075351 | 0.17396 | 0.168 | -121.5028 | 120.9788 | -0.098929 | 121.0704 | 121.0243 | 0.045483 | -0.072852 | 0.077905 | -0.51587 | -0.10775 | 16.7674 | 13.6423 | 14.1581 | -0.009147 | -0.015103 | 121.0711 | 121.0972 | 121.2479 | 121.0158 | -0.19121 | 121.0623 | 121.1609 | 121.1549 | 48.7032 | -121.6859
2400.9062 | 121.2387 | -121.1105 | 0.07782 | 1.4211e-13 | 0.02181 | 0.015919 | 0.009682 | -0.023789 | 0.0042113 | 0.018923 | -0.00018375 | 0.033108 | 0.048857 | 0.010105 | 0.063884 | 0.088037 | 0.028878 | 0.041952 | 0.084176 | 0.10567 | 0.26101 | 0.014784 | -104.1463 | -72.6271 | -107.3126 | 0.038723 | 0.14191 | 0.12679 | -121.5532 | 121.1253 | 0.006356 | 121.1986 | 121.1525 | 0.027168 | 0.027854 | 0.18319 | -0.44264 | -0.039097 | 16.9642 | 13.7979 | 14.2405 | 0.064087 | 0.048974 | 121.1947 | 121.2162 | 121.3715 | 121.1394 | -0.063036 | 121.1493 | 121.2524 | 121.2373 | 48.4834 | -121.631
2402.6875 | 121.3715 | -121.0602 | 0.050354 | 1.4211e-13 | 0.021596 | 0.015705 | 0.0098956 | -0.023576 | 0.0044249 | 0.011293 | 2.985e-05 | 0.032681 | 0.048643 | 0.010532 | 0.064312 | 0.088037 | 0.028878 | 0.04653 | 0.088755 | 0.10567 | 0.25185 | 0.005627 | -104.0135 | -72.3753 | -107.1249 | 0.043302 | 0.14191 | 0.13137 | -121.5761 | 121.0658 | 0.038401 | 121.1482 | 121.1067 | 0.040903 | 0.05532 | 0.2015 | -0.51588 | -0.007052 | 17.0467 | 13.9353 | 14.4512 | 0.091553 | 0.081019 | 121.1489 | 121.1659 | 121.312 | 121.0891 | -0.044727 | 121.1035 | 121.2021 | 121.1916 | 48.6849 | -121.6264
2404.4844 | 121.3989 | -121.1288 | 0.073242 | 1.4211e-13 | 0.022023 | 0.015705 | 0.009682 | -0.023576 | 0.0042113 | 0.011293 | 0.00024345 | 0.033108 | 0.048643 | 0.010318 | 0.064312 | 0.083459 | 0.0243 | 0.04653 | 0.079598 | 0.11483 | 0.25643 | 0.001048 | -103.8761 | -72.5539 | -106.983 | 0.038723 | 0.13733 | 0.13137 | -121.5944 | 121.1299 | 0.006356 | 121.2123 | 121.1754 | 0.045482 | 0.04159 | 0.18319 | -0.46554 | -0.034519 | 17.2527 | 14.1459 | 14.6114 | 0.064087 | 0.058131 | 121.2084 | 121.2437 | 121.3853 | 121.1531 | -0.072194 | 121.1676 | 121.2662 | 121.2602 | 48.575 | -121.6676
2406.2031 | 121.2662 | -121.1426 | 0.086975 | 1.4211e-13 | 0.02181 | 0.015492 | 0.009682 | -0.023576 | 0.0039977 | 0.0036627 | 2.985e-05 | 0.032895 | 0.048857 | 0.010746 | 0.064098 | 0.088037 | 0.028878 | 0.04653 | 0.084176 | 0.11025 | 0.26101 | -0.017268 | -103.7388 | -72.5539 | -106.8456 | 0.043302 | 0.14649 | 0.13595 | -121.5944 | 121.1253 | -0.002799 | 121.2306 | 121.1891 | 0.063798 | 0.023278 | 0.17404 | -0.4518 | -0.043673 | 17.4038 | 14.297 | 14.7488 | 0.059511 | 0.048977 | 121.2268 | 121.2528 | 121.4036 | 121.1715 | -0.10424 | 121.1859 | 121.2891 | 121.2785 | 48.5887 | -121.6814
2407.9688 | 121.3623 | -121.1334 | 0.07782 | 1.4211e-13 | 0.021596 | 0.015705 | 0.0094682 | -0.023362 | 0.0048523 | 0.0036627 | 0.00067085 | 0.033536 | 0.048643 | 0.010532 | 0.064739 | 0.083459 | 0.019721 | 0.037373 | 0.088755 | 0.11025 | 0.26101 | 0.014784 | -103.6014 | -72.6088 | -106.7266 | 0.043302 | 0.13733 | 0.14053 | -121.6264 | 121.1482 | 0.010935 | 121.2169 | 121.1708 | 0.022589 | 0.032433 | 0.18319 | -0.49301 | -0.034518 | 17.532 | 14.4069 | 14.8999 | 0.059509 | 0.06271 | 121.2222 | 121.2437 | 121.3944 | 121.1531 | -0.063036 | 121.1767 | 121.2708 | 121.274 | 48.5246 | -121.7043
2409.6875 | 121.344 | -121.1792 | 0.073242 | 1.4211e-13 | 0.021596 | 0.015919 | 0.009682 | -0.023362 | 0.0046387 | 0.018923 | 0.00045725 | 0.033322 | 0.048857 | 0.010532 | 0.064739 | 0.074302 | 0.019721 | 0.041952 | 0.084176 | 0.11025 | 0.26101 | -0.021847 | -103.4595 | -72.5401 | -106.6212 | 0.04788 | 0.14649 | 0.14511 | -121.631 | 121.1574 | 0.010934 | 121.2535 | 121.2212 | 0.063799 | 0.037011 | 0.18777 | -0.45181 | -0.025362 | 17.7197 | 14.558 | 15.0098 | 0.073244 | 0.071867 | 121.2634 | 121.2895 | 121.4402 | 121.1989 | -0.095089 | 121.2271 | 121.3257 | 121.3243 | 48.6391 | -121.7043
2411.4844 | 121.4722 | -121.1563 | 0.064087 | 1.4211e-13 | 0.021382 | 0.015919 | 0.0098956 | -0.023362 | 0.0044249 | 0.0036627 | 0.00045725 | 0.033108 | 0.048857 | 0.010959 | 0.064739 | 0.092615 | 0.0243 | 0.037373 | 0.079598 | 0.11025 | 0.26101 | 0.014784 | -103.3084 | -72.5951 | -106.4839 | 0.057037 | 0.15107 | 0.14511 | -121.631 | 121.1711 | 0.015511 | 121.2489 | 121.1937 | 0.022589 | 0.046166 | 0.19692 | -0.4747 | -0.00705 | 17.8479 | 14.6724 | 15.1471 | 0.086978 | 0.081022 | 121.2359 | 121.2666 | 121.4173 | 121.1806 | -0.049303 | 121.2133 | 121.3074 | 121.3014 | 48.5612 | -121.6951
2413.2656 | 121.344 | -121.2112 | 0.082397 | 1.4211e-13 | 0.021382 | 0.015919 | 0.009682 | -0.023148 | 0.0042113 | 0.011293 | 0.001098 | 0.033108 | 0.048857 | 0.010959 | 0.06538 | 0.07888 | 0.028878 | 0.041952 | 0.084176 | 0.11025 | 0.26101 | -0.021847 | -103.1985 | -72.6958 | -106.3648 | 0.038723 | 0.13733 | 0.14053 | -121.6585 | 121.1894 | 0.001779 | 121.2901 | 121.2532 | 0.063799 | 0.027856 | 0.17861 | -0.44724 | -0.043674 | 18.0127 | 14.8464 | 15.2936 | 0.054932 | 0.058133 | 121.2954 | 121.3215 | 121.4723 | 121.2401 | -0.10424 | 121.25 | 121.3486 | 121.3518 | 48.5154 | -121.7409
2415.0469 | 121.3394 | -121.2341 | 0.10071 | 1.4211e-13 | 0.021596 | 0.015919 | 0.0098956 | -0.023576 | 0.0042113 | 0.0036627 | 0.001098 | 0.033322 | 0.049284 | 0.010959 | 0.06538 | 0.088037 | 0.033457 | 0.051108 | 0.084176 | 0.10567 | 0.26101 | 0.001048 | -103.052 | -72.8194 | -106.2687 | 0.043302 | 0.14191 | 0.13595 | -121.6768 | 121.2352 | -0.016532 | 121.3222 | 121.2852 | 0.05006 | 0.004966 | 0.1603 | -0.44267 | -0.057406 | 18.1822 | 14.9654 | 15.4081 | 0.041199 | 0.035244 | 121.3183 | 121.3398 | 121.4951 | 121.2676 | -0.09966 | 121.2774 | 121.376 | 121.3701 | 48.4147 | -121.7775
2416.75 | 121.4996 | -121.2021 | 0.059509 | 1.4211e-13 | 0.021596 | 0.015919 | 0.009682 | -0.023362 | 0.0048523 | 0.011293 | 0.0015254 | 0.033536 | 0.048643 | 0.011173 | 0.065594 | 0.092615 | 0.033457 | 0.041952 | 0.084176 | 0.1011 | 0.26101 | -0.00811 | -102.9192 | -72.8973 | -106.1588 | 0.038723 | 0.14649 | 0.13137 | -121.686 | 121.194 | 0.024667 | 121.2947 | 121.244 | 0.050062 | 0.041586 | 0.2015 | -0.48387 | -0.020786 | 18.2829 | 15.0433 | 15.5272 | 0.086977 | 0.071864 | 121.2863 | 121.3032 | 121.4631 | 121.2355 | -0.067619 | 121.2408 | 121.3486 | 121.3335 | 48.3048 | -121.7455
2418.5469 | 121.4355 | -121.2387 | 0.086975 | 1.4211e-13 | 0.021596 | 0.015919 | 0.0094682 | -0.023362 | 0.0042113 | 0.011293 | 0.001098 | 0.033322 | 0.049071 | 0.011387 | 0.065807 | 0.088037 | 0.0243 | 0.037373 | 0.088755 | 0.11025 | 0.26559 | -0.003531 | -102.7864 | -73.1766 | -106.0031 | 0.043302 | 0.13275 | 0.13137 | -121.6951 | 121.2352 | 0.00178 | 121.3267 | 121.2761 | 0.040904 | 0.023278 | 0.17861 | -0.45641 | -0.043673 | 18.4523 | 15.2356 | 15.692 | 0.045775 | 0.044398 | 121.3275 | 121.349 | 121.5043 | 121.263 | -0.090506 | 121.282 | 121.3715 | 121.3701 | 48.0621 | -121.7821
2420.3281 | 121.5134 | -121.2296 | 0.07782 | 1.4211e-13 | 0.02181 | 0.015705 | 0.009682 | -0.023362 | 0.0039977 | 0.011293 | 0.0015254 | 0.033322 | 0.049284 | 0.011387 | 0.065807 | 0.088037 | 0.028878 | 0.041952 | 0.093333 | 0.10567 | 0.25643 | 0.010206 | -102.6582 | -73.3139 | -105.8612 | 0.038723 | 0.13275 | 0.13595 | -121.7134 | 121.2398 | 0.015513 | 121.3176 | 121.2715 | 0.031746 | 0.027854 | 0.17861 | -0.48388 | -0.039097 | 18.5713 | 15.3684 | 15.8523 | 0.05493 | 0.058132 | 121.3229 | 121.3352 | 121.486 | 121.2584 | -0.067614 | 121.2683 | 121.3623 | 121.3655 | 47.9156 | -121.7913
2422.0469 | 121.5179 | -121.2296 | 0.059509 | 1.4211e-13 | 0.021382 | 0.015492 | 0.009682 | -0.023576 | 0.0042113 | 0.0036627 | 0.001739 | 0.033536 | 0.049284 | 0.0116 | 0.066021 | 0.083459 | 0.0243 | 0.041952 | 0.084176 | 0.11025 | 0.26101 | 0.019363 | -102.5529 | -73.3872 | -105.733 | 0.043302 | 0.13733 | 0.13595 | -121.718 | 121.2489 | 0.024667 | 121.313 | 121.2715 | 0.022589 | 0.050744 | 0.2015 | -0.48846 | -0.016207 | 18.6767 | 15.4966 | 15.985 | 0.07782 | 0.076443 | 121.3137 | 121.3398 | 121.4906 | 121.2539 | -0.040146 | 121.2729 | 121.3669 | 121.3655 | 47.8423 | -121.7775
2423.8281 | 121.4676 | -121.2708 | 0.10529 | 1.4211e-13 | 0.02181 | 0.015705 | 0.0098956 | -0.023362 | 0.0044249 | 0.0036627 | 0.0015254 | 0.033322 | 0.049498 | 0.011387 | 0.066448 | 0.07888 | 0.019721 | 0.037373 | 0.079598 | 0.11025 | 0.26101 | -0.012689 | -102.411 | -73.3643 | -105.6414 | 0.038723 | 0.13275 | 0.13137 | -121.7317 | 121.2581 | -0.025688 | 121.3496 | 121.3081 | 0.050062 | 0.004967 | 0.15572 | -0.46099 | -0.066563 | 18.8598 | 15.6294 | 16.0903 | 0.027464 | 0.026087 | 121.3504 | 121.381 | 121.5318 | 121.2905 | -0.11798 | 121.3095 | 121.4035 | 121.4021 | 47.9064 | -121.837
2425.5625 | 121.4355 | -121.2982 | 0.10071 | 1.4211e-13 | 0.021596 | 0.015705 | 0.0098956 | -0.023362 | 0.0044249 | 0.011293 | 0.0015254 | 0.033749 | 0.049498 | 0.011814 | 0.066662 | 0.074302 | 0.033457 | 0.037373 | 0.084176 | 0.11025 | 0.26101 | 0.023942 | -102.2782 | -73.1674 | -105.4949 | 0.043302 | 0.13733 | 0.12679 | -121.7501 | 121.3222 | -0.016532 | 121.3725 | 121.3356 | 0.013431 | 0.009545 | 0.1603 | -0.45184 | -0.057406 | 19.02 | 15.8033 | 16.2552 | 0.036621 | 0.026086 | 121.3824 | 121.4085 | 121.5592 | 121.3317 | -0.076766 | 121.3415 | 121.4355 | 121.425 | 48.1308 | -121.8508
2427.3438 | 121.4127 | -121.3028 | 0.091553 | 1.4211e-13 | 0.02181 | 0.015705 | 0.009682 | -0.023576 | 0.0039977 | 0.0036627 | 0.0019526 | 0.033963 | 0.049498 | 0.012028 | 0.066662 | 0.083459 | 0.028878 | 0.041952 | 0.088755 | 0.11025 | 0.25185 | -0.031005 | -102.1271 | -73.4055 | -105.3575 | 0.043302 | 0.13733 | 0.13137 | -121.7501 | 121.2718 | -0.002798 | 121.3863 | 121.3447 | 0.072957 | 0.0187 | 0.1603 | -0.44727 | -0.048251 | 19.1757 | 15.9453 | 16.3925 | 0.045776 | 0.03982 | 121.3916 | 121.413 | 121.5546 | 121.3317 | -0.12256 | 121.3461 | 121.4401 | 121.4342 | 47.8973 | -121.8416
2429.1406 | 121.5179 | -121.2982 | 0.10071 | 1.4211e-13 | 0.02181 | 0.015492 | 0.0094682 | -0.023362 | 0.0039977 | 0.018923 | 0.0021662 | 0.033963 | 0.049712 | 0.011814 | 0.067089 | 0.083459 | 0.028878 | 0.037373 | 0.088755 | 0.10567 | 0.26559 | -0.003531 | -102.0218 | -73.6345 | -105.2476 | 0.043302 | 0.14649 | 0.13595 | -121.773 | 121.2947 | -0.011953 | 121.3817 | 121.3356 | 0.040904 | 0.004966 | 0.16488 | -0.47474 | -0.057406 | 19.2765 | 16.0506 | 16.5253 | 0.045778 | 0.035244 | 121.387 | 121.4039 | 121.5638 | 121.3271 | -0.10424 | 121.3415 | 121.4447 | 121.4342 | 47.6638 | -121.8737
2430.9531 | 121.5042 | -121.3348 | 0.086975 | 1.4211e-13 | 0.021596 | 0.015492 | 0.009682 | -0.023576 | 0.0037841 | 0.011293 | 0.0021662 | 0.033749 | 0.050139 | 0.012028 | 0.066875 | 0.083459 | 0.0243 | 0.051108 | 0.088755 | 0.11025 | 0.25643 | 0.023942 | -101.8386 | -73.5566 | -105.1423 | 0.043302 | 0.13733 | 0.13137 | -121.7821 | 121.3588 | 0.00178 | 121.4183 | 121.3859 | 0.027166 | 0.023278 | 0.16946 | -0.44727 | -0.043673 | 19.4962 | 16.1925 | 16.6398 | 0.050354 | 0.044398 | 121.4236 | 121.4451 | 121.5913 | 121.3591 | -0.063033 | 121.3781 | 121.4722 | 121.4662 | 47.7782 | -121.8691
2432.6719 | 121.5042 | -121.3531 | 0.09613 | 1.4211e-13 | 0.021596 | 0.015919 | 0.009682 | -0.023362 | 0.0044249 | 0.0036627 | 0.0030208 | 0.033749 | 0.049498 | 0.012028 | 0.067089 | 0.083459 | 0.0243 | 0.051108 | 0.084176 | 0.11025 | 0.26559 | 0.019363 | -101.802 | -73.6573 | -105.0416 | 0.043302 | 0.13733 | 0.12679 | -121.7958 | 121.3725 | -0.011954 | 121.4366 | 121.4043 | 0.031745 | 0.014123 | 0.16946 | -0.4427 | -0.052828 | 19.5512 | 16.3116 | 16.7543 | 0.041199 | 0.030664 | 121.4373 | 121.4634 | 121.6187 | 121.3774 | -0.076767 | 121.3965 | 121.4905 | 121.4799 | 47.6958 | -121.892
2434.4688 | 121.55 | -121.3348 | 0.09613 | 1.4211e-13 | 0.021596 | 0.015919 | 0.0094682 | -0.022935 | 0.0044249 | 0.018923 | 0.0023798 | 0.033963 | 0.050139 | 0.012028 | 0.067516 | 0.083459 | 0.0243 | 0.051108 | 0.093333 | 0.10567 | 0.26559 | 0.001048 | -101.6921 | -73.6253 | -104.9225 | 0.043302 | 0.14191 | 0.13137 | -121.8004 | 121.3359 | -0.002797 | 121.4183 | 121.3859 | 0.05006 | 0.009544 | 0.16946 | -0.46559 | -0.052828 | 19.6427 | 16.4123 | 16.8779 | 0.045777 | 0.035243 | 121.4282 | 121.4405 | 121.6004 | 121.3591 | -0.095082 | 121.3781 | 121.4767 | 121.4662 | 47.7095 | -121.8966
2436.2656 | 121.5683 | -121.3394 | 0.082397 | 1.4211e-13 | 0.021596 | 0.015492 | 0.0098956 | -0.023148 | 0.0042113 | 0.018923 | 0.0023798 | 0.033963 | 0.049925 | 0.012241 | 0.067303 | 0.083459 | 0.0243 | 0.037373 | 0.084176 | 0.11025 | 0.26101 | 0.014784 | -101.5547 | -73.7031 | -104.7714 | 0.04788 | 0.14191 | 0.13595 | -121.805 | 121.3542 | 0.001779 | 121.4229 | 121.3768 | 0.022589 | 0.027856 | 0.17861 | -0.46559 | -0.034517 | 19.7847 | 16.568 | 17.0336 | 0.05951 | 0.053555 | 121.4236 | 121.4497 | 121.6004 | 121.3637 | -0.067613 | 121.3873 | 121.4813 | 121.4754 | 47.6363 | -121.8874
2438.0625 | 121.6095 | -121.3211 | 0.059509 | 1.4211e-13 | 0.02181 | 0.015705 | 0.0098956 | -0.023576 | 0.0044249 | 0.011293 | 0.0023798 | 0.03439 | 0.049925 | 0.012241 | 0.06773 | 0.083459 | 0.033457 | 0.04653 | 0.079598 | 0.11025 | 0.25643 | 0.010206 | -101.4632 | -73.8359 | -104.6478 | 0.04788 | 0.14191 | 0.13595 | -121.8187 | 121.3313 | 0.020089 | 121.4046 | 121.3676 | 0.036324 | 0.050744 | 0.19692 | -0.49764 | -0.011629 | 19.8579 | 16.6733 | 17.1709 | 0.082398 | 0.076443 | 121.4007 | 121.4314 | 121.5775 | 121.3546 | -0.049303 | 121.369 | 121.463 | 121.4571 | 47.4852 | -121.8783
2439.8594 | 121.6324 | -121.3577 | 0.073242 | 1.4211e-13 | 0.022023 | 0.015705 | 0.009682 | -0.023789 | 0.0039977 | 0.011293 | 0.0025934 | 0.033963 | 0.049925 | 0.012241 | 0.068371 | 0.083459 | 0.038035 | 0.041952 | 0.088755 | 0.11025 | 0.26559 | -0.026426 | -101.3853 | -73.8222 | -104.515 | 0.038723 | 0.14191 | 0.13595 | -121.8325 | 121.3313 | 0.015513 | 121.4412 | 121.3997 | 0.068378 | 0.037011 | 0.19235 | -0.47475 | -0.034519 | 19.9724 | 16.8427 | 17.3174 | 0.068665 | 0.06271 | 121.4465 | 121.468 | 121.6233 | 121.3958 | -0.099668 | 121.3965 | 121.4996 | 121.4937 | 47.5355 | -121.9057
2441.5781 | 121.5775 | -121.3943 | 0.10071 | 1.4211e-13 | 0.02181 | 0.015705 | 0.0098956 | -0.023576 | 0.0042113 | 0.018923 | 0.0030208 | 0.03439 | 0.049925 | 0.012455 | 0.068371 | 0.083459 | 0.028878 | 0.037373 | 0.088755 | 0.10567 | 0.26101 | -0.017268 | -101.2983 | -73.7993 | -104.3594 | 0.04788 | 0.13733 | 0.13595 | -121.8554 | 121.3771 | -0.011953 | 121.4778 | 121.4317 | 0.054641 | 0.004966 | 0.1603 | -0.46103 | -0.052828 | 20.096 | 17.035 | 17.496 | 0.036621 | 0.035244 | 121.4831 | 121.5 | 121.6554 | 121.4232 | -0.11798 | 121.4422 | 121.5317 | 121.5303 | 47.5951 | -121.9561
2443.3594 | 121.5637 | -121.3943 | 0.091553 | 1.4211e-13 | 0.02181 | 0.015919 | 0.009682 | -0.023362 | 0.0044249 | 0.018923 | 0.0032344 | 0.034177 | 0.050353 | 0.012669 | 0.068157 | 0.07888 | 0.033457 | 0.041952 | 0.084176 | 0.11025 | 0.26101 | 0.005627 | -101.1747 | -73.781 | -104.1899 | 0.043302 | 0.13733 | 0.13137 | -121.8508 | 121.4 | -0.007377 | 121.4732 | 121.4363 | 0.036325 | 0.0187 | 0.16946 | -0.45645 | -0.048251 | 20.2196 | 17.2044 | 17.6608 | 0.045776 | 0.03982 | 121.4785 | 121.5046 | 121.6554 | 121.4278 | -0.085926 | 121.4376 | 121.5317 | 121.5257 | 47.6134 | -121.9423
2445.0938 | 121.5683 | -121.4172 | 0.091553 | 1.4211e-13 | 0.022237 | 0.015705 | 0.0098956 | -0.023362 | 0.0039977 | 0.018923 | 0.0030208 | 0.034177 | 0.050353 | 0.012882 | 0.068585 | 0.083459 | 0.028878 | 0.051108 | 0.088755 | 0.1011 | 0.26101 | -0.017268 | -101.0328 | -73.5566 | -103.9748 | 0.04788 | 0.14191 | 0.13137 | -121.86 | 121.4 | -0.002798 | 121.5007 | 121.4683 | 0.068376 | 0.009542 | 0.16946 | -0.44272 | -0.043673 | 20.3845 | 17.4425 | 17.8852 | 0.050354 | 0.03982 | 121.506 | 121.5183 | 121.6782 | 121.4461 | -0.10882 | 121.4651 | 121.5591 | 121.5486 | 47.8606 | -121.9515
2446.8906 | 121.6187 | -121.4035 | 0.073242 | 1.4211e-13 | 0.02181 | 0.015705 | 0.009682 | -0.023148 | 0.0044249 | 0.0036627 | 0.003448 | 0.03439 | 0.050139 | 0.012669 | 0.069012 | 0.083459 | 0.028878 | 0.041952 | 0.084176 | 0.11025 | 0.26101 | 0.010206 | -100.9458 | -73.5246 | -103.8099 | 0.04788 | 0.14649 | 0.13595 | -121.8645 | 121.4137 | 0.010934 | 121.487 | 121.4455 | 0.031746 | 0.037011 | 0.18777 | -0.46103 | -0.025362 | 20.4577 | 17.5936 | 18.0546 | 0.073244 | 0.06271 | 121.4877 | 121.5138 | 121.6645 | 121.4324 | -0.063036 | 121.4514 | 121.55 | 121.5395 | 47.8789 | -121.9378
2448.6875 | 121.7148 | -121.4127 | 0.091553 | 1.4211e-13 | 0.02181 | 0.015919 | 0.0098956 | -0.023362 | 0.0046387 | 0.011293 | 0.0030208 | 0.033963 | 0.050353 | 0.01331 | 0.069012 | 0.083459 | 0.0243 | 0.041952 | 0.084176 | 0.11025 | 0.26559 | -0.026426 | -100.8542 | -73.5017 | -103.6817 | 0.04788 | 0.15107 | 0.13137 | -121.8783 | 121.3862 | -0.007377 | 121.4961 | 121.4546 | 0.068378 | 0.0187 | 0.17403 | -0.46561 | -0.043673 | 20.5585 | 17.7309 | 18.1966 | 0.059512 | 0.03982 | 121.4968 | 121.5229 | 121.6782 | 121.437 | -0.11798 | 121.4605 | 121.5637 | 121.544 | 47.911 | -121.9698
2450.5 | 121.701 | -121.3898 | 0.054932 | 1.4211e-13 | 0.022237 | 0.015705 | 0.009682 | -0.023148 | 0.0042113 | -0.0039678 | 0.003448 | 0.034177 | 0.050353 | 0.01331 | 0.069226 | 0.088037 | 0.033457 | 0.037373 | 0.088755 | 0.10567 | 0.25643 | -0.053899 | -100.7397 | -73.4009 | -103.5398 | 0.052459 | 0.15107 | 0.14511 | -121.8737 | 121.3359 | 0.033823 | 121.4778 | 121.4271 | 0.091272 | 0.050742 | 0.2015 | -0.48392 | -0.002473 | 20.65 | 17.85 | 18.3339 | 0.096133 | 0.090177 | 121.4785 | 121.4954 | 121.6462 | 121.4232 | -0.10883 | 121.4422 | 121.5408 | 121.5349 | 47.9888 | -121.9286
2452.2969 | 121.5363 | -121.4676 | 0.086975 | 1.4211e-13 | 0.022237 | 0.015919 | 0.009682 | -0.023576 | 0.0044249 | 0.0036627 | 0.003448 | 0.03439 | 0.050353 | 0.01331 | 0.069226 | 0.088037 | 0.033457 | 0.041952 | 0.093333 | 0.10567 | 0.26559 | -0.003531 | -100.6619 | -73.5108 | -103.3337 | 0.04788 | 0.14649 | 0.14053 | -121.8828 | 121.4641 | 0.006358 | 121.5556 | 121.5095 | 0.045483 | 0.018699 | 0.17861 | -0.41526 | -0.039095 | 20.8057 | 18.1339 | 18.5491 | 0.059511 | 0.053555 | 121.5609 | 121.5733 | 121.7332 | 121.501 | -0.090506 | 121.5155 | 121.6141 | 121.6081 | 47.9568 | -121.9698
2454.0938 | 121.6049 | -121.4447 | 0.086975 | 1.4211e-13 | 0.02181 | 0.016133 | 0.0098956 | -0.023576 | 0.0039977 | 0.026554 | 0.0038754 | 0.03439 | 0.050994 | 0.013737 | 0.069653 | 0.083459 | 0.0243 | 0.051108 | 0.084176 | 0.11025 | 0.25643 | -0.012689 | -100.5016 | -73.1537 | -103.0453 | 0.04788 | 0.14191 | 0.14053 | -121.9012 | 121.432 | -0.002799 | 121.5282 | 121.4958 | 0.063797 | 0.023278 | 0.16946 | -0.45646 | -0.039095 | 20.9431 | 18.3994 | 18.8559 | 0.054932 | 0.053555 | 121.5289 | 121.555 | 121.7011 | 121.469 | -0.099664 | 121.4926 | 121.5866 | 121.5852 | 48.291 | -121.9881
2455.8125 | 114.9078 | -105.0705 | 9.9014 | 1.4211e-13 | 0.021596 | 0.015492 | 0.0092546 | -0.022935 | 0.0027157 | 0.011293 | 0.003448 | 0.034177 | 0.048857 | 0.014378 | 0.065166 | 0.088037 | 0.028878 | 0.041952 | 0.088755 | 0.11483 | 0.26101 | -0.063057 | -88.2719 | -62.4441 | -88.9337 | 7.4101 | 7.5272 | 7.4892 | -108.3982 | 105.0074 | -9.8127 | 105.1585 | 105.1124 | 0.10501 | -9.7866 | -9.6404 | -3.3277 | -2.4913 | 16.7986 | 16.1368 | 19.4645 | -2.3742 | -2.4122 | 105.1593 | 105.1853 | 105.3315 | 105.0994 | -9.9645 | 112.4806 | 112.5977 | 112.5597 | 42.6264 | -118.2997
2457.5938 | 121.2662 | -120.9595 | 0.059509 | 1.4211e-13 | 0.02181 | 0.015919 | 0.009682 | -0.023362 | 0.0044249 | 0.0036627 | 0.004089 | 0.03439 | 0.052916 | 0.01566 | 0.069653 | 0.083459 | 0.0243 | 0.037373 | 0.088755 | 0.10567 | 0.26559 | 0.005627 | -99.8789 | -71.6427 | -99.7898 | 0.04788 | 0.13275 | 0.13137 | -121.4524 | 120.9651 | 0.029246 | 121.0429 | 120.9968 | 0.031746 | 0.046165 | 0.20608 | -0.49296 | -0.011629 | 21.0805 | 21.1697 | 21.6626 | 0.073241 | 0.071864 | 121.0482 | 121.0651 | 121.2251 | 120.9838 | -0.053882 | 121.0074 | 121.0922 | 121.0908 | 49.3168 | -121.5119
2459.3125 | 121.257 | -121.0876 | 0.09613 | 1.4211e-13 | 0.02181 | 0.015919 | 0.009682 | -0.023576 | 0.0039977 | 0.0036627 | 0.0038754 | 0.034604 | 0.054626 | 0.016729 | 0.07008 | 0.083459 | 0.0243 | 0.041952 | 0.084176 | 0.1011 | 0.26101 | -0.003531 | -99.8927 | -71.3176 | -98.082 | 0.04788 | 0.13733 | 0.12679 | -121.5532 | 121.0841 | -0.011954 | 121.1711 | 121.1296 | 0.045483 | 0.004965 | 0.16488 | -0.46552 | -0.04825 | 21.195 | 23.0057 | 23.4712 | 0.041199 | 0.030664 | 121.1718 | 121.1887 | 121.3487 | 121.1119 | -0.099661 | 121.1355 | 121.225 | 121.2144 | 49.77 | -121.6493
2461.1094 | 115.7547 | -109.1583 | 6.3904 | 1.4211e-13 | 0.02181 | 0.015064 | 0.009041 | -0.023148 | 0.0027157 | -0.0039678 | 0.003448 | 0.03439 | 0.052489 | 0.01737 | 0.065594 | 0.088037 | 0.028878 | 0.051108 | 0.088755 | 0.10567 | 0.26101 | -0.021847 | -85.9093 | -59.239 | -82.3403 | 9.2369 | 9.3266 | 9.3069 | -106.2782 | 109.1365 | -6.3016 | 109.2464 | 109.2094 | 0.072955 | -6.2847 | -6.1294 | 2.8801 | 2.8465 | 23.249 | 26.818 | 23.9379 | 2.9362 | 2.9165 | 109.2471 | 109.264 | 109.4193 | 109.1872 | -6.4122 | 118.3952 | 118.4849 | 118.4652 | 49.9193 | -112.6686
2462.8281 | 121.0098 | -120.8679 | 0.10071 | 1.4211e-13 | 0.02181 | 0.015705 | 0.009682 | -0.023576 | 0.0039977 | 0.018923 | 0.004089 | 0.03439 | 0.055266 | 0.017797 | 0.070294 | 0.083459 | 0.028878 | 0.041952 | 0.088755 | 0.11025 | 0.26101 | -0.003531 | -99.4577 | -70.6812 | -96.4977 | 0.034145 | 0.14191 | 0.13595 | -121.3059 | 120.8644 | -0.011953 | 120.9514 | 120.9099 | 0.045483 | 0.009545 | 0.1603 | -0.438 | -0.066563 | 21.4102 | 24.3702 | 24.8082 | 0.041199 | 0.035244 | 120.9567 | 120.9782 | 121.1289 | 120.8968 | -0.10424 | 120.9021 | 121.0098 | 121.0039 | 50.1867 | -121.4066
2464.625 | 121.1426 | -120.9915 | 0.091553 | 1.4211e-13 | 0.02181 | 0.015919 | 0.0094682 | -0.023362 | 0.0044249 | 0.011293 | 0.0043026 | 0.03439 | 0.056548 | 0.019079 | 0.070508 | 0.07888 | 0.0243 | 0.04653 | 0.093333 | 0.11025 | 0.25185 | 0.010206 | -99.3936 | -70.0676 | -95.1424 | 0.043302 | 0.14649 | 0.14053 | -121.4204 | 121.0017 | 0.00178 | 121.0704 | 121.038 | 0.036324 | 0.0187 | 0.1603 | -0.42887 | -0.048251 | 21.5979 | 25.8491 | 26.278 | 0.054933 | 0.048977 | 121.0848 | 121.1018 | 121.2434 | 121.0158 | -0.081347 | 121.0348 | 121.138 | 121.132 | 50.9239 | -121.5119
2466.4219 | 121.1517 | -121.0556 | 0.11902 | 1.4211e-13 | 0.02181 | 0.015492 | 0.0098956 | -0.023362 | 0.0042113 | 0.018923 | 0.0043026 | 0.034604 | 0.056335 | 0.019079 | 0.070721 | 0.07888 | 0.0243 | 0.041952 | 0.084176 | 0.11025 | 0.25643 | -0.017268 | -99.1372 | -70.0905 | -95.4721 | 0.04788 | 0.13275 | 0.13595 | -121.4845 | 121.0383 | -0.034843 | 121.1345 | 121.0976 | 0.05922 | -0.008766 | 0.13741 | -0.42889 | -0.071139 | 21.9184 | 25.5835 | 26.0124 | 0.013731 | 0.016933 | 121.1398 | 121.1659 | 121.312 | 121.0799 | -0.13629 | 121.1035 | 121.1884 | 121.1916 | 50.9651 | -121.6035
2468.1562 | 121.3257 | -121.019 | 0.082397 | 1.4211e-13 | 0.02181 | 0.015919 | 0.0094682 | -0.023576 | 0.0044249 | 0.0036627 | 0.0047298 | 0.035459 | 0.056976 | 0.01972 | 0.071789 | 0.083459 | 0.028878 | 0.037373 | 0.093333 | 0.10567 | 0.25643 | 0.010206 | -97.6811 | -69.7471 | -94.5289 | 0.052459 | 0.14191 | 0.13595 | -121.5165 | 121.0292 | 0.010936 | 121.1024 | 121.0564 | 0.027167 | 0.023277 | 0.17403 | -0.49756 | -0.029938 | 23.3378 | 26.4901 | 26.9877 | 0.05951 | 0.053555 | 121.1123 | 121.1247 | 121.2754 | 121.0479 | -0.072191 | 121.0714 | 121.1609 | 121.1549 | 51.2719 | -121.5989
2469.9531 | 121.3028 | -121.0556 | 0.07782 | 1.4211e-13 | 0.02181 | 0.015705 | 0.009682 | -0.023789 | 0.0039977 | 0.0036627 | 0.0047298 | 0.036741 | 0.057189 | 0.019506 | 0.072858 | 0.088037 | 0.019721 | 0.041952 | 0.088755 | 0.11025 | 0.26101 | -0.058478 | -96.1473 | -69.2664 | -94.19 | 0.16692 | 0.27011 | 0.25957 | -121.3975 | 120.9971 | 0.010935 | 121.1436 | 121.0976 | 0.10043 | 0.032433 | 0.18319 | -0.34189 | 0.089101 | 24.9083 | 26.8656 | 27.2074 | 0.19229 | 0.18175 | 121.1444 | 121.1659 | 121.3166 | 121.0753 | -0.1363 | 121.2225 | 121.3257 | 121.3152 | 51.7892 | -121.4753
2471.75 | 120.9824 | -120.6024 | 0.10071 | 1.4211e-13 | 0.022023 | 0.015919 | 0.0094682 | -0.023576 | 0.0042113 | 0.026554 | 0.0051572 | 0.036954 | 0.056976 | 0.019934 | 0.073499 | 0.088037 | 0.028878 | 0.037373 | 0.088755 | 0.11941 | 0.26101 | -0.072215 | -95.4651 | -68.9825 | -93.9748 | 0.098244 | 0.19685 | 0.1909 | -121.0724 | 120.5302 | -0.011953 | 120.6905 | 120.6398 | 0.10959 | 0.018703 | 0.1603 | -0.46998 | -0.002464 | 25.1374 | 26.6276 | 27.0975 | 0.096143 | 0.090187 | 120.6912 | 120.7218 | 120.8634 | 120.6313 | -0.17292 | 120.7007 | 120.7993 | 120.7933 | 51.6199 | -121.1731
2473.5469 | 121.2204 | -120.8862 | 0.082397 | 1.4211e-13 | 0.022023 | 0.015705 | 0.0098956 | -0.023789 | 0.0044249 | 0.018923 | 0.0051572 | 0.039518 | 0.054839 | 0.018011 | 0.075422 | 0.07888 | 0.0243 | 0.032795 | 0.093333 | 0.10567 | 0.26101 | -0.031005 | -91.999 | -69.1839 | -96.2688 | 0.043302 | 0.13733 | 0.14053 | -121.3838 | 120.8552 | 0.010936 | 120.9651 | 120.919 | 0.0638 | 0.023277 | 0.17861 | -0.49752 | -0.039095 | 28.8873 | 24.6174 | 25.115 | 0.054932 | 0.058133 | 120.9796 | 120.9919 | 121.1472 | 120.9105 | -0.1134 | 120.9295 | 121.0236 | 121.0268 | 51.7023 | -121.4662
2475.3281 | 121.0648 | -120.8679 | 0.19684 | 1.4211e-13 | 0.022023 | 0.015919 | 0.009682 | -0.023362 | 0.0039977 | 0.011293 | 0.0051572 | 0.040586 | 0.056121 | 0.019079 | 0.076917 | 0.083459 | 0.0243 | 0.04653 | 0.07502 | 0.10567 | 0.26101 | -0.053899 | -90.2041 | -68.836 | -94.8906 | 0.07993 | 0.17854 | 0.168 | -121.3883 | 120.814 | -0.12182 | 120.9514 | 120.9145 | 0.10043 | -0.091164 | 0.064172 | -0.52041 | -0.11691 | 30.6638 | 25.9773 | 26.4977 | -0.018302 | -0.028836 | 120.9429 | 120.9736 | 121.1289 | 120.8922 | -0.25074 | 120.9479 | 121.0465 | 121.0359 | 52.032 | -121.5852
2477.0469 | 121.1014 | -120.0668 | 0.78278 | 1.4211e-13 | 0.021596 | 0.015919 | 0.0098956 | -0.023362 | 0.0042113 | 0.0036627 | 0.0051572 | 0.045287 | 0.057189 | 0.020361 | 0.080977 | 0.083459 | 0.019721 | 0.041952 | 0.079598 | 0.11025 | 0.25185 | -0.035584 | -83.2719 | -67.7554 | -92.9401 | 0.3638 | 0.46699 | 0.45645 | -121.0358 | 120.0312 | -0.70318 | 120.1503 | 120.1088 | 0.077536 | -0.67252 | -0.53092 | -0.96893 | -0.41898 | 36.7949 | 27.1268 | 28.0957 | -0.31579 | -0.32632 | 120.1464 | 120.1771 | 120.3187 | 120.0866 | -0.81836 | 120.4306 | 120.5338 | 120.5233 | 52.3114 | -121.8185
2478.8281 | 121.3257 | -121.0144 | 0.068665 | 1.4211e-13 | 0.022023 | 0.016133 | 0.009682 | -0.023148 | 0.0042113 | 0.0036627 | 0.0053708 | 0.045501 | 0.056976 | 0.020361 | 0.08119 | 0.07888 | 0.0243 | 0.037373 | 0.088755 | 0.11025 | 0.26559 | -0.053899 | -83.2033 | -68.14 | -93.6406 | 0.052459 | 0.15107 | 0.14511 | -121.4753 | 120.9605 | 0.02009 | 121.0933 | 121.0518 | 0.091272 | 0.041588 | 0.19692 | -0.46093 | -0.016206 | 37.8111 | 27.3738 | 27.8347 | 0.0824 | 0.076444 | 121.1032 | 121.1247 | 121.28 | 121.0387 | -0.12256 | 121.0669 | 121.1655 | 121.1595 | 52.8744 | -121.544
2480.625 | 120.8954 | -119.6503 | 1.2726 | 1.4211e-13 | 0.021596 | 0.015705 | 0.0094682 | -0.023362 | 0.0044249 | 0.018923 | 0.0051572 | 0.046569 | 0.058258 | 0.021857 | 0.082472 | 0.07888 | 0.0243 | 0.04653 | 0.084176 | 0.11025 | 0.25643 | 0.010206 | -80.5476 | -66.629 | -90.7331 | 0.80333 | 0.8928 | 0.896 | -120.5413 | 119.6605 | -1.1884 | 119.7291 | 119.6968 | 0.036324 | -1.1623 | -1.0162 | -0.89098 | -0.46925 | 39.1027 | 28.9171 | 29.8081 | -0.37979 | -0.37658 | 119.7344 | 119.7605 | 119.9067 | 119.6746 | -1.2624 | 120.4536 | 120.5431 | 120.5463 | 53.0212 | -121.8138
2482.3438 | 121.2479 | -120.9595 | 0.15564 | 1.4211e-13 | 0.021596 | 0.015919 | 0.009682 | -0.023362 | 0.0042113 | 0.026554 | 0.0049436 | 0.049346 | 0.059967 | 0.022925 | 0.084822 | 0.074302 | 0.0243 | 0.041952 | 0.084176 | 0.11483 | 0.25643 | -0.021847 | -77.9103 | -66.9679 | -90.2569 | 0.12114 | 0.21974 | 0.21379 | -121.3975 | 120.9376 | -0.071464 | 121.0338 | 121.0014 | 0.063799 | -0.040808 | 0.10079 | -0.43802 | -0.034504 | 43.0492 | 30.7025 | 31.1406 | 0.064104 | 0.058148 | 121.0436 | 121.0743 | 121.2159 | 120.9838 | -0.17749 | 121.0806 | 121.1792 | 121.1733 | 53.9916 | -121.5531
2484.125 | 116.6702 | -116.4001 | 0.22888 | 1.4211e-13 | 0.02181 | 0.015492 | 0.0092546 | -0.023576 | 0.0031431 | 0.011293 | 0.0043026 | 0.051483 | 0.057189 | 0.021857 | 0.083968 | 0.083459 | 0.0243 | 0.04653 | 0.084176 | 0.10567 | 0.27017 | -0.063057 | -70.3875 | -64.3992 | -86.7771 | 0.30428 | 0.40289 | 0.39235 | -117.0385 | 116.3371 | -0.14471 | 116.4836 | 116.4467 | 0.10959 | -0.12321 | 0.041285 | -0.63831 | 0.075394 | 46.0127 | 29.623 | 30.2613 | 0.17401 | 0.16347 | 116.4843 | 116.5058 | 116.6703 | 116.4244 | -0.29194 | 116.7044 | 116.803 | 116.7925 | 52.001 | -117.2673
2485.8594 | 120.3323 | -118.7073 | 1.7303 | 1.4211e-13 | 0.021596 | 0.015919 | 0.009682 | -0.023576 | 0.0039977 | 0.0036627 | 0.0045162 | 0.056183 | 0.059753 | 0.023139 | 0.090591 | 0.088037 | 0.028878 | 0.037373 | 0.088755 | 0.10567 | 0.26101 | -0.053899 | -66.3353 | -65.054 | -87.7524 | 1.3573 | 1.4331 | 1.4454 | -119.5248 | 118.6534 | -1.6416 | 118.7953 | 118.7446 | 0.091272 | -1.6247 | -1.4693 | -0.81748 | -0.37302 | 52.372 | 30.9549 | 31.7724 | -0.29727 | -0.28492 | 118.796 | 118.8129 | 118.9683 | 118.7362 | -1.7842 | 120.0646 | 120.1403 | 120.1527 | 53.6533 | -121.2551
2487.6406 | 120.9 | -120.1721 | 0.55847 | 1.4211e-13 | 0.022237 | 0.015705 | 0.009682 | -0.023576 | 0.0044249 | 0.0036627 | 0.0049436 | 0.056611 | 0.060394 | 0.02378 | 0.091446 | 0.07888 | 0.0243 | 0.037373 | 0.084176 | 0.11483 | 0.26559 | -0.053899 | -66.6192 | -65.7316 | -88.1049 | 0.40958 | 0.5082 | 0.4473 | -120.8022 | 120.1182 | -0.4743 | 120.251 | 120.2095 | 0.091272 | -0.44364 | -0.29288 | -0.63013 | -0.14889 | 53.5529 | 32.0672 | 32.6973 | -0.050276 | -0.11117 | 120.2563 | 120.287 | 120.4377 | 120.1964 | -0.61237 | 120.5817 | 120.6803 | 120.6194 | 54.4405 | -121.3607
2489.4375 | 121.0739 | -120.7169 | 0.16479 | 1.4211e-13 | 0.022023 | 0.016133 | 0.0098956 | -0.023362 | 0.0044249 | 0.011293 | 0.0043026 | 0.060029 | 0.06018 | 0.023993 | 0.09465 | 0.083459 | 0.028878 | 0.04653 | 0.084176 | 0.1011 | 0.26559 | -0.058478 | -61.665 | -65.9605 | -88.3613 | 0.30885 | 0.40289 | 0.3603 | -120.9762 | 120.6584 | -0.080619 | 120.8003 | 120.7634 | 0.10501 | -0.0637 | 0.10079 | -0.25938 | 0.14406 | 59.0518 | 32.3555 | 32.6149 | 0.23809 | 0.19551 | 120.801 | 120.818 | 120.9824 | 120.7457 | -0.22327 | 121.0257 | 121.1197 | 121.0772 | 54.7563 | -121.141
2491.1719 | 120.3049 | -120.0485 | 0.11902 | 1.4211e-13 | 0.022023 | 0.015492 | 0.009682 | -0.023362 | 0.0037841 | 0.026554 | 0.0043026 | 0.060457 | 0.059753 | 0.023993 | 0.094223 | 0.083459 | 0.028878 | 0.037373 | 0.084176 | 0.1011 | 0.26101 | -0.035584 | -59.4306 | -64.5366 | -85.9713 | 0.93611 | 1.0439 | 0.99215 | -118.8608 | 120.0129 | -0.034843 | 120.132 | 120.0859 | 0.072957 | -0.017924 | 0.14199 | 1.1877 | 0.81709 | 60.6179 | 34.0773 | 32.8896 | 0.92487 | 0.87313 | 120.1327 | 120.1496 | 120.3095 | 120.0774 | -0.1546 | 120.9846 | 121.0924 | 121.0407 | 55.512 | -118.9798
2492.9531 | 120.9732 | -120.6894 | 0.068665 | 1.4211e-13 | 0.022237 | 0.016133 | 0.0098956 | -0.023576 | 0.0042113 | 0.0036627 | 0.004089 | 0.061525 | 0.060821 | 0.024207 | 0.095719 | 0.07888 | 0.019721 | 0.037373 | 0.084176 | 0.10567 | 0.25643 | -0.026426 | -59.7832 | -65.6171 | -87.7386 | 0.057037 | 0.15107 | 0.14511 | -121.1457 | 120.663 | 0.015511 | 120.7683 | 120.7268 | 0.063799 | 0.037009 | 0.18777 | -0.45627 | -0.011628 | 60.9062 | 32.9507 | 33.407 | 0.0824 | 0.076444 | 120.7736 | 120.7951 | 120.9458 | 120.7091 | -0.095091 | 120.7464 | 120.8405 | 120.8345 | 55.0723 | -121.2143
2494.6719 | 121.0327 | -120.7489 | 0.09613 | 1.4211e-13 | 0.022023 | 0.015705 | 0.0098956 | -0.023148 | 0.0046387 | 0.0036627 | 0.0045162 | 0.062593 | 0.06189 | 0.024848 | 0.097428 | 0.074302 | 0.028878 | 0.041952 | 0.088755 | 0.11483 | 0.25643 | -0.049321 | -58.3226 | -64.8845 | -86.5757 | 0.066194 | 0.1648 | 0.15884 | -121.2098 | 120.6996 | -0.007375 | 120.8232 | 120.7909 | 0.091273 | 0.018702 | 0.1603 | -0.46086 | -0.029936 | 62.4263 | 34.1732 | 34.6341 | 0.06867 | 0.062715 | 120.8377 | 120.8637 | 121.0053 | 120.7778 | -0.14545 | 120.8151 | 120.9137 | 120.9077 | 55.8644 | -121.3059
2496.4531 | 120.6711 | -120.1401 | 0.35248 | 1.4211e-13 | 0.022023 | 0.016133 | 0.0098956 | -0.023576 | 0.0042113 | 0.011293 | 0.0047298 | 0.065157 | 0.058685 | 0.022925 | 0.099351 | 0.083459 | 0.0243 | 0.037373 | 0.088755 | 0.11025 | 0.25185 | -0.040163 | -54.4398 | -65.434 | -89.1947 | 0.27223 | 0.36626 | 0.3603 | -120.6557 | 120.0999 | -0.26372 | 120.2235 | 120.1774 | 0.077536 | -0.24223 | -0.10063 | -0.51565 | -0.080252 | 65.7003 | 30.9454 | 31.461 | 0.013781 | 0.007825 | 120.2288 | 120.2503 | 120.3919 | 120.1644 | -0.39264 | 120.4123 | 120.5063 | 120.5004 | 54.7061 | -121.0082
2498.25 | 120.8771 | -120.4605 | 0.22888 | 1.4211e-13 | 0.02181 | 0.015919 | 0.009682 | -0.023148 | 0.0042113 | 0.0036627 | 0.0047298 | 0.067294 | 0.059539 | 0.02378 | 0.10106 | 0.07888 | 0.019721 | 0.041952 | 0.084176 | 0.10567 | 0.26101 | -0.053899 | -51.6422 | -65.3241 | -88.5399 | 0.16234 | 0.26095 | 0.25957 | -120.9854 | 120.4066 | -0.14471 | 120.5394 | 120.5025 | 0.095851 | -0.12321 | 0.032128 | -0.52489 | -0.06654 | 68.8183 | 31.9206 | 32.4455 | 0.032069 | 0.030692 | 120.5447 | 120.5662 | 120.7215 | 120.4802 | -0.28278 | 120.6229 | 120.7215 | 120.7201 | 55.1364 | -121.2143
2500.0469 | 120.5521 | -120.2225 | 0.09613 | 1.4211e-13 | 0.022023 | 0.015705 | 0.009682 | -0.023362 | 0.0042113 | 0.011293 | 0.0043026 | 0.066653 | 0.059753 | 0.02378 | 0.10063 | 0.07888 | 0.0243 | 0.037373 | 0.084176 | 0.11483 | 0.26101 | -0.035584 | -52.123 | -64.8571 | -87.5372 | 0.21271 | 0.31132 | 0.30536 | -120.5413 | 120.1869 | -0.011954 | 120.3014 | 120.2598 | 0.072957 | 0.018702 | 0.16488 | -0.31878 | 0.11658 | 68.0995 | 32.6853 | 33.0041 | 0.21519 | 0.20923 | 120.3066 | 120.3373 | 120.4835 | 120.2468 | -0.13171 | 120.4352 | 120.5338 | 120.5278 | 55.3654 | -120.6374
2501.7812 | 120.8221 | -120.5429 | 0.09613 | 1.4211e-13 | 0.022023 | 0.015919 | 0.009682 | -0.023362 | 0.0044249 | 0.018923 | 0.0045162 | 0.068789 | 0.058471 | 0.023139 | 0.10234 | 0.088037 | 0.019721 | 0.037373 | 0.093333 | 0.10567 | 0.26101 | -0.049321 | -49.6963 | -64.7563 | -89.3183 | 0.11656 | 0.21974 | 0.20921 | -120.9259 | 120.4936 | -0.002797 | 120.6309 | 120.5803 | 0.086694 | 0.009544 | 0.16488 | -0.38296 | 0.020427 | 70.8466 | 31.2246 | 31.6076 | 0.12361 | 0.11308 | 120.6362 | 120.6486 | 120.8039 | 120.5626 | -0.14545 | 120.6595 | 120.7627 | 120.7521 | 55.7866 | -121.022
2503.5781 | 120.6985 | -120.1401 | 0.52643 | 1.4211e-13 | 0.022023 | 0.016133 | 0.010109 | -0.023362 | 0.0046387 | 0.0036627 | 0.0047298 | 0.067935 | 0.059112 | 0.023352 | 0.10191 | 0.088037 | 0.0243 | 0.041952 | 0.088755 | 0.10567 | 0.26101 | -0.040163 | -50.7814 | -64.5457 | -88.311 | 0.3409 | 0.43036 | 0.43356 | -120.7198 | 120.0999 | -0.43767 | 120.2281 | 120.182 | 0.082115 | -0.42075 | -0.26542 | -0.57975 | -0.18552 | 69.3587 | 31.8291 | 32.4088 | -0.096069 | -0.092867 | 120.2288 | 120.2457 | 120.4011 | 120.1644 | -0.56659 | 120.481 | 120.5704 | 120.5736 | 55.5944 | -121.2463
2505.3594 | 120.639 | -120.5292 | 0.09613 | 1.4211e-13 | 0.02181 | 0.015919 | 0.0098956 | -0.023362 | 0.0044249 | 0.0036627 | 0.0055844 | 0.066439 | 0.057403 | 0.022925 | 0.10063 | 0.083459 | 0.0243 | 0.051108 | 0.07502 | 0.11025 | 0.26101 | -0.031005 | -52.9014 | -65.5759 | -89.3183 | 0.038723 | 0.12359 | 0.12679 | -120.9213 | 120.4982 | -0.02111 | 120.6126 | 120.5803 | 0.082113 | 0.014123 | 0.16488 | -0.39212 | -0.057407 | 67.6278 | 31.2109 | 31.603 | 0.027463 | 0.030664 | 120.6042 | 120.6394 | 120.7902 | 120.5535 | -0.12713 | 120.5679 | 120.6528 | 120.656 | 54.9533 | -121.0174
2507.1406 | 120.8496 | -120.6482 | 0.073242 | 1.4211e-13 | 0.02181 | 0.015705 | 0.0098956 | -0.023576 | 0.0042113 | 0.011293 | 0.013489 | 0.068362 | 0.049712 | 0.023139 | 0.1032 | 0.083459 | 0.019721 | 0.041952 | 0.088755 | 0.10567 | 0.25643 | -0.017268 | -50.4609 | -66.2582 | -89.3412 | 0.04788 | 0.13733 | 0.13137 | -121.1044 | 120.6309 | 0.015513 | 120.7317 | 120.6901 | 0.05922 | 0.032432 | 0.18319 | -0.45625 | -0.025362 | 70.1873 | 31.307 | 31.7633 | 0.064087 | 0.058131 | 120.7369 | 120.7539 | 120.9046 | 120.6679 | -0.09051 | 120.6961 | 120.7855 | 120.7796 | 54.39 | -121.1777
2508.9375 | 120.7123 | -120.5704 | 0.1236 | 1.4211e-13 | 0.02181 | 0.015919 | 0.009682 | -0.023362 | 0.0042113 | 0.011293 | 0.025025 | 0.069858 | 0.038175 | 0.023566 | 0.10469 | 0.074302 | 0.0243 | 0.037373 | 0.084176 | 0.10567 | 0.26559 | -0.021847 | -47.9838 | -65.5942 | -88.3201 | 0.22186 | 0.30674 | 0.30536 | -120.8526 | 120.5485 | -0.03942 | 120.6447 | 120.6077 | 0.05922 | -0.017922 | 0.14199 | -0.28224 | 0.098267 | 72.5865 | 32.2502 | 32.5325 | 0.18314 | 0.18176 | 120.6546 | 120.676 | 120.836 | 120.5947 | -0.14544 | 120.7922 | 120.8771 | 120.8757 | 54.9761 | -120.9762
2510.6562 | 121.0236 | -120.7214 | 0.068665 | 1.4211e-13 | 0.02181 | 0.015919 | 0.0094682 | -0.023576 | 0.0044249 | 0.011293 | 0.029939 | 0.070285 | 0.032406 | 0.022925 | 0.10491 | 0.083459 | 0.0243 | 0.037373 | 0.088755 | 0.11025 | 0.26101 | -0.012689 | -47.8053 | -65.5347 | -89.5198 | 0.029566 | 0.13733 | 0.12679 | -121.2006 | 120.7087 | 0.02009 | 120.8049 | 120.7588 | 0.050062 | 0.041588 | 0.19235 | -0.47917 | -0.039099 | 72.9162 | 31.2017 | 31.6808 | 0.068664 | 0.058129 | 120.8102 | 120.8317 | 120.9824 | 120.7457 | -0.081354 | 120.751 | 120.8588 | 120.8482 | 55.1867 | -121.2693
2512.4375 | 115.9195 | -115.0864 | 0.48981 | 1.4211e-13 | 0.021596 | 0.015919 | 0.009041 | -0.022721 | 0.0033567 | 0.0036627 | 0.070744 | 0.069858 | 0.061462 | 0.087882 | 0.10491 | 0.07888 | 0.028878 | 0.041952 | 0.079598 | 0.1011 | 0.26101 | -0.072215 | -43.1212 | -39.0606 | 0.57093 | 1.4809 | 1.5796 | 1.5599 | -115.1382 | 115.0142 | -0.41021 | 115.1652 | 115.1283 | 0.11417 | -0.38871 | -0.2288 | -0.051884 | 0.99114 | 71.9651 | 115.6573 | 115.7092 | 1.0898 | 1.0701 | 115.166 | 115.1875 | 115.3474 | 115.1152 | -0.56202 | 116.5673 | 116.666 | 116.6463 | 76.0258 | -115.6281
2514.1562 | 120.8359 | -120.4971 | 0.041199 | 1.4211e-13 | 0.02181 | 0.015919 | 0.0098956 | -0.023576 | 0.0044249 | 0.011293 | 0.073308 | 0.071353 | 0.065308 | 0.091728 | 0.11003 | 0.083459 | 0.0243 | 0.041952 | 0.07502 | 0.10567 | 0.26101 | -0.035584 | -46.5415 | -41.9727 | -0.074666 | 0.024988 | 0.12359 | 0.11764 | -120.9579 | 120.4615 | 0.033821 | 120.5806 | 120.5391 | 0.077536 | 0.064475 | 0.21981 | -0.46079 | -0.016211 | 73.9556 | 120.4225 | 120.8833 | 0.082394 | 0.076438 | 120.5722 | 120.6028 | 120.7581 | 120.5214 | -0.076783 | 120.5221 | 120.6207 | 120.6148 | 78.5245 | -120.9991
2515.9531 | 120.8633 | -120.5795 | 0.10529 | 1.4211e-13 | 0.022237 | 0.015492 | 0.0098956 | -0.022935 | 0.0044249 | 0.011293 | 0.073521 | 0.071567 | 0.066163 | 0.092369 | 0.1111 | 0.083459 | 0.0243 | 0.041952 | 0.093333 | 0.10567 | 0.26101 | -0.040163 | -48.5104 | -43.2227 | -0.010564 | 0.075351 | 0.16938 | 0.16342 | -121.0266 | 120.5394 | -0.011953 | 120.663 | 120.6215 | 0.082115 | 0.000388 | 0.15572 | -0.44708 | -0.029935 | 72.0691 | 120.569 | 121.016 | 0.064093 | 0.058137 | 120.6729 | 120.6852 | 120.8405 | 120.6038 | -0.14545 | 120.6549 | 120.7489 | 120.743 | 77.3569 | -121.1319
2517.7344 | 120.8588 | -120.5566 | 0.21057 | 1.4211e-13 | 0.022023 | 0.015919 | 0.009682 | -0.023362 | 0.0039977 | 0.011293 | 0.072667 | 0.073703 | 0.065949 | 0.092155 | 0.11174 | 0.083459 | 0.0243 | 0.041952 | 0.084176 | 0.096516 | 0.26101 | -0.053899 | -45.9463 | -43.3326 | -0.019721 | 0.061616 | 0.16022 | 0.14969 | -121.0816 | 120.5027 | -0.1264 | 120.6401 | 120.5986 | 0.095851 | -0.11406 | 0.050439 | -0.52491 | -0.14896 | 74.6103 | 120.5369 | 121.0618 | -0.050349 | -0.060884 | 120.6408 | 120.6532 | 120.8177 | 120.5809 | -0.26447 | 120.6183 | 120.7169 | 120.7063 | 77.2241 | -121.2921
2519.5156 | 120.5841 | -120.3598 | 0.064087 | 1.4211e-13 | 0.022451 | 0.016133 | 0.0094682 | -0.023362 | 0.0039977 | 0.018923 | 0.072667 | 0.072208 | 0.065949 | 0.091514 | 0.11174 | 0.07888 | 0.033457 | 0.041952 | 0.088755 | 0.11025 | 0.26559 | 0.019363 | -48.0662 | -45.7547 | -0.06093 | 0.020409 | 0.13733 | 0.11764 | -120.8022 | 120.3792 | 0.024668 | 120.4387 | 120.4018 | 0.022589 | 0.046166 | 0.2015 | -0.44244 | -0.043678 | 72.2936 | 120.2989 | 120.7413 | 0.073242 | 0.05355 | 120.4486 | 120.4701 | 120.6254 | 120.3933 | -0.044724 | 120.3802 | 120.4971 | 120.4774 | 74.6051 | -120.8663
2521.2969 | 120.7947 | -120.5338 | 0.059509 | 1.4211e-13 | 0.022023 | 0.016133 | 0.0098956 | -0.023362 | 0.0042113 | 0.018923 | 0.072453 | 0.070499 | 0.065522 | 0.091514 | 0.10982 | 0.07888 | 0.0243 | 0.041952 | 0.088755 | 0.10567 | 0.25643 | -0.031005 | -49.8291 | -48.4012 | -0.06093 | 0.034145 | 0.12817 | 0.11306 | -120.99 | 120.5027 | 0.029246 | 120.6126 | 120.5757 | 0.072957 | 0.046165 | 0.19692 | -0.45622 | -0.025364 | 70.7047 | 120.4728 | 120.929 | 0.068663 | 0.05355 | 120.6225 | 120.6394 | 120.7902 | 120.5581 | -0.090514 | 120.5679 | 120.6619 | 120.6468 | 72.1326 | -121.0495
2523.0781 | 120.8542 | -120.5978 | 0.07782 | 1.4211e-13 | 0.022237 | 0.015919 | 0.0098956 | -0.023789 | 0.0044249 | 0.011293 | 0.069676 | 0.088019 | 0.062958 | 0.091087 | 0.12478 | 0.083459 | 0.0243 | 0.04653 | 0.088755 | 0.11025 | 0.26101 | 0.001048 | -45.3877 | -119.9023 | -0.06093 | 0.024988 | 0.12817 | 0.11306 | -121.0632 | 120.5989 | 0.010935 | 120.6813 | 120.6444 | 0.045482 | 0.032433 | 0.18319 | -0.4654 | -0.052832 | 75.2101 | 120.5369 | 121.0023 | 0.050352 | 0.035239 | 120.6866 | 120.7081 | 120.8588 | 120.6221 | -0.076772 | 120.6228 | 120.726 | 120.7109 | 0.69552 | -121.1411
2524.8594 | 120.8542 | -120.694 | 0.11444 | 1.4211e-13 | 0.022023 | 0.015492 | 0.009682 | -0.023148 | 0.0042113 | 0.011293 | -0.0053112 | 0.042723 | 0.0089048 | 0.0041217 | 0.016453 | 0.088037 | 0.028878 | 0.041952 | 0.097912 | 0.11483 | 0.25643 | 0.010206 | -120.6159 | -120.0305 | -114.6844 | -8.7566 | -9.0336 | -8.8061 | -121.1548 | 120.7042 | -0.016529 | 120.782 | 120.7359 | 0.031746 | 0.000391 | 0.14199 | -0.46084 | -8.871 | 0.078064 | 6.0096 | 6.4705 | -9.1481 | -8.9205 | 120.7919 | 120.8088 | 120.9504 | 120.7228 | -0.10423 | 111.9374 | 111.6604 | 111.8879 | 0.66345 | -121.2693
2526.6562 | 120.9503 | -120.7214 | 0.07782 | 1.4211e-13 | 0.022023 | 0.015919 | 0.010109 | -0.023362 | 0.0044249 | 0.018923 | -0.0053112 | 0.041868 | 0.0089048 | -0.00036547 | 0.022436 | 0.088037 | 0.028878 | 0.037373 | 0.088755 | 0.11483 | 0.26559 | 0.005627 | -120.8723 | -120.09 | -120.7374 | -8.7611 | -9.029 | -8.8106 | -121.1869 | 120.7271 | 0.010935 | 120.8095 | 120.7588 | 0.031746 | 0.037012 | 0.18777 | -0.46543 | -8.839 | -0.15088 | -0.015971 | 0.44946 | -9.1069 | -8.8885 | 120.8102 | 120.8363 | 120.987 | 120.7503 | -0.072193 | 111.9603 | 111.6924 | 111.9108 | 0.63139 | -121.2647
2528.4375 | 120.8817 | -120.7489 | 0.11902 | 1.4211e-13 | 0.022023 | 0.016133 | 0.009682 | -0.023576 | 0.0037841 | 0.018923 | -0.0050974 | 0.041868 | 0.0091184 | -0.00015167 | 0.022649 | 0.083459 | 0.028878 | 0.04653 | 0.093333 | 0.11025 | 0.26559 | 0.005627 | -120.9089 | -120.1267 | -120.7786 | -8.7611 | -9.0336 | -8.8106 | -121.2281 | 120.7545 | -0.025686 | 120.8324 | 120.7954 | 0.040903 | -0.008766 | 0.14657 | -0.47917 | -8.8802 | -0.16004 | -0.029714 | 0.44946 | -9.1526 | -8.9297 | 120.8422 | 120.8592 | 121.0145 | 120.7778 | -0.11339 | 111.9878 | 111.7153 | 111.9383 | 0.62223 | -121.3471
2530.1562 | 120.9503 | -120.8176 | 0.082397 | 1.4211e-13 | 0.022237 | 0.015705 | 0.009682 | -0.023576 | 0.0042113 | 0.018923 | -0.0048838 | 0.041868 | 0.0089048 | -0.00015167 | 0.022649 | 0.083459 | 0.033457 | 0.041952 | 0.088755 | 0.11025 | 0.26101 | 0.028521 | -120.9364 | -120.1679 | -120.8107 | -8.7611 | -9.0336 | -8.8061 | -121.2555 | 120.8461 | 0.006358 | 120.901 | 120.8595 | 0.013431 | 0.027856 | 0.17861 | -0.43798 | -8.8435 | -0.11885 | 0.0069 | 0.44488 | -9.116 | -8.8885 | 120.9063 | 120.9278 | 121.0786 | 120.851 | -0.053876 | 112.0564 | 111.784 | 112.0115 | 0.64969 | -121.3379
2531.9531 | 121.0419 | -120.8038 | 0.086975 | 1.4211e-13 | 0.022023 | 0.016133 | 0.009682 | -0.023576 | 0.0044249 | 0.011293 | -0.0053112 | 0.042296 | 0.0091184 | -0.00015167 | 0.02329 | 0.088037 | 0.033457 | 0.041952 | 0.084176 | 0.11025 | 0.26559 | 0.019363 | -120.9685 | -120.1999 | -120.8381 | -8.7566 | -9.0336 | -8.8106 | -121.2876 | 120.8232 | -0.002799 | 120.8919 | 120.8458 | 0.022589 | 0.023278 | 0.17861 | -0.48377 | -8.8435 | -0.16463 | -0.034305 | 0.44946 | -9.1206 | -8.8976 | 120.888 | 120.9141 | 121.0694 | 120.8373 | -0.067612 | 112.0473 | 111.7702 | 111.9932 | 0.6039 | -121.3746
2533.7344 | 121.051 | -120.8267 | 0.064087 | 1.4211e-13 | 0.02181 | 0.015919 | 0.009682 | -0.023362 | 0.0044249 | 0.0036627 | -0.0053112 | 0.042082 | 0.0093322 | -0.00015167 | 0.02329 | 0.088037 | 0.033457 | 0.04653 | 0.088755 | 0.11483 | 0.26101 | 0.001048 | -120.9914 | -120.2228 | -120.8656 | -8.7611 | -9.0382 | -8.8106 | -121.3059 | 120.8278 | 0.024668 | 120.9148 | 120.8733 | 0.045482 | 0.050745 | 0.19692 | -0.47919 | -8.8252 | -0.16464 | -0.03889 | 0.4403 | -9.1023 | -8.8747 | 120.9155 | 120.9416 | 121.0877 | 120.8602 | -0.063039 | 112.0656 | 111.7885 | 112.0161 | 0.6039 | -121.37
2535.5312 | 121.0968 | -120.845 | 0.086975 | 1.4211e-13 | 0.02181 | 0.015705 | 0.009682 | -0.023148 | 0.0046387 | 0.0036627 | -0.0050974 | 0.041441 | 0.0089048 | -0.00015167 | 0.023718 | 0.088037 | 0.033457 | 0.041952 | 0.084176 | 0.11941 | 0.26559 | 0.019363 | -121.0188 | -120.2457 | -120.8931 | -8.7611 | -9.0382 | -8.8152 | -121.3288 | 120.8644 | -0.002799 | 120.9331 | 120.887 | 0.022589 | 0.032436 | 0.17861 | -0.48378 | -8.8481 | -0.1738 | -0.048051 | 0.43573 | -9.1252 | -8.9022 | 120.9292 | 120.9644 | 121.1106 | 120.8785 | -0.067612 | 112.0839 | 111.8068 | 112.0298 | 0.59931 | -121.4158
2537.3125 | 121.0373 | -120.8954 | 0.09613 | 1.4211e-13 | 0.022237 | 0.015705 | 0.009682 | -0.023362 | 0.0042113 | 0.011293 | -0.0046702 | 0.041655 | 0.0091184 | -0.00036547 | 0.023931 | 0.097194 | 0.033457 | 0.04653 | 0.088755 | 0.11483 | 0.26101 | 0.014784 | -121.0463 | -120.2732 | -120.9068 | -8.7611 | -9.0382 | -8.8198 | -121.3609 | 120.9102 | -0.007375 | 120.9926 | 120.9419 | 0.031746 | 0.018702 | 0.16488 | -0.46547 | -8.8573 | -0.15092 | -0.011433 | 0.45404 | -9.1343 | -8.9159 | 120.9841 | 121.0102 | 121.1564 | 120.9288 | -0.081346 | 112.1342 | 111.8572 | 112.0756 | 0.6222 | -121.457
2539.0469 | 121.1792 | -120.8542 | 0.073242 | 1.4211e-13 | 0.022237 | 0.015919 | 0.010109 | -0.023789 | 0.0044249 | 0.0036627 | -0.0044566 | 0.042082 | 0.0093322 | -0.00015167 | 0.024572 | 0.088037 | 0.0243 | 0.051108 | 0.097912 | 0.11025 | 0.26559 | 0.019363 | -121.0692 | -120.2915 | -120.9297 | -8.7566 | -9.0473 | -8.8152 | -121.3792 | 120.8735 | 0.02467 | 120.9422 | 120.9053 | 0.031745 | 0.037011 | 0.19235 | -0.52499 | -8.8298 | -0.21501 | -0.075526 | 0.44946 | -9.1206 | -8.8885 | 120.9521 | 120.9644 | 121.1198 | 120.8785 | -0.053879 | 112.0976 | 111.8068 | 112.039 | 0.56268 | -121.4524
2540.8281 | 121.0693 | -120.9366 | 0.09613 | 1.4211e-13 | 0.022237 | 0.015919 | 0.009682 | -0.023576 | 0.0044249 | 0.011293 | -0.0040292 | 0.041441 | 0.0089048 | -0.00015167 | 0.024999 | 0.088037 | 0.0243 | 0.04653 | 0.088755 | 0.11025 | 0.26559 | 0.019363 | -121.0875 | -120.3144 | -120.9572 | -8.7657 | -9.0382 | -8.8106 | -121.3975 | 120.9559 | -0.007375 | 121.0246 | 120.9831 | 0.027167 | 0.014123 | 0.16946 | -0.46091 | -8.8619 | -0.15093 | -0.020601 | 0.44031 | -9.1343 | -8.9068 | 121.0253 | 121.0468 | 121.2022 | 120.9609 | -0.076767 | 112.1709 | 111.8984 | 112.1259 | 0.62218 | -121.4936
2542.6094 | 121.0739 | -120.9549 | 0.11444 | 1.4211e-13 | 0.022237 | 0.015919 | 0.009682 | -0.024003 | 0.0044249 | 0.018923 | -0.0046702 | 0.042082 | 0.0089048 | -0.00036547 | 0.024999 | 0.083459 | 0.033457 | 0.051108 | 0.084176 | 0.11483 | 0.26559 | 0.014784 | -121.1058 | -120.3327 | -120.9801 | -8.7611 | -9.0382 | -8.8106 | -121.4204 | 120.9697 | -0.030265 | 121.0384 | 121.006 | 0.036324 | 0.000391 | 0.15115 | -0.46549 | -8.8756 | -0.15093 | -0.025183 | 0.44031 | -9.1526 | -8.9251 | 121.0391 | 121.0697 | 121.2205 | 120.9884 | -0.099657 | 112.1937 | 111.9167 | 112.1443 | 0.62218 | -121.5348
2544.3906 | 121.1975 | -120.9274 | 0.064087 | 1.4211e-13 | 0.022237 | 0.015919 | 0.009682 | -0.023362 | 0.0044249 | 0.011293 | -0.0044566 | 0.041868 | 0.0089048 | -0.00015167 | 0.025854 | 0.088037 | 0.033457 | 0.04653 | 0.088755 | 0.11025 | 0.25643 | 0.019363 | -121.1196 | -120.3602 | -120.9984 | -8.7611 | -9.029 | -8.8106 | -121.4433 | 120.9468 | 0.024668 | 121.0155 | 120.974 | 0.027167 | 0.046166 | 0.19234 | -0.51585 | -8.8252 | -0.19213 | -0.070964 | 0.44489 | -9.0931 | -8.8747 | 121.0162 | 121.0377 | 121.1839 | 120.9609 | -0.044724 | 112.1663 | 111.8984 | 112.1168 | 0.56724 | -121.5074
2546.1719 | 121.1838 | -120.9869 | 0.09613 | 1.4211e-13 | 0.022023 | 0.016133 | 0.009682 | -0.023576 | 0.0046387 | 0.018923 | -0.0040292 | 0.041655 | 0.0093322 | -0.00036547 | 0.026068 | 0.088037 | 0.019721 | 0.041952 | 0.088755 | 0.11025 | 0.26101 | 0.014784 | -121.1425 | -120.3693 | -121.0167 | -8.7611 | -9.0382 | -8.8106 | -121.457 | 121.0017 | -0.007375 | 121.075 | 121.0289 | 0.027168 | 0.014123 | 0.16488 | -0.47008 | -8.8573 | -0.15552 | -0.02977 | 0.44031 | -9.1343 | -8.9068 | 121.0757 | 121.0972 | 121.2479 | 121.0067 | -0.081346 | 112.2258 | 111.9487 | 112.1763 | 0.61759 | -121.5531
2547.8906 | 121.2891 | -120.9641 | 0.073242 | 1.4211e-13 | 0.022023 | 0.015705 | 0.0098956 | -0.023576 | 0.0044249 | 0.011293 | -0.004243 | 0.041655 | 0.0093322 | -0.00036547 | 0.026068 | 0.092615 | 0.033457 | 0.041952 | 0.088755 | 0.11483 | 0.26559 | -0.003531 | -121.1516 | -120.3922 | -121.0396 | -8.752 | -9.0382 | -8.8152 | -121.4708 | 120.9605 | 0.015513 | 121.0567 | 121.006 | 0.045483 | 0.04159 | 0.19235 | -0.5067 | -8.8252 | -0.18757 | -0.075552 | 0.43115 | -9.1114 | -8.8885 | 121.0528 | 121.0789 | 121.2296 | 120.9975 | -0.076773 | 112.2121 | 111.9259 | 112.1488 | 0.57181 | -121.544
2549.6719 | 121.257 | -121.019 | 0.07782 | 1.4211e-13 | 0.022451 | 0.015919 | 0.009682 | -0.023362 | 0.0042113 | 0.026554 | -0.0046702 | 0.041441 | 0.0089048 | -0.00015167 | 0.026922 | 0.083459 | 0.0243 | 0.037373 | 0.088755 | 0.11025 | 0.26559 | -0.00811 | -121.1608 | -120.406 | -121.0488 | -8.7657 | -9.0336 | -8.8198 | -121.4891 | 121.0109 | 0.010935 | 121.1024 | 121.0564 | 0.045483 | 0.032433 | 0.18777 | -0.47009 | -8.8435 | -0.14179 | -0.029777 | 0.44031 | -9.1114 | -8.8976 | 121.1077 | 121.1292 | 121.2846 | 121.0433 | -0.08593 | 112.2533 | 111.9854 | 112.1992 | 0.61301 | -121.5669
2551.3906 | 121.2296 | -121.0464 | 0.073242 | 1.4211e-13 | 0.022023 | 0.015705 | 0.009682 | -0.023148 | 0.0044249 | -0.0039678 | -0.0040292 | 0.041014 | 0.0093322 | -0.00015167 | 0.026709 | 0.088037 | 0.0243 | 0.037373 | 0.084176 | 0.11025 | 0.26101 | 0.019363 | -121.1562 | -120.4151 | -121.0671 | -8.7566 | -9.0473 | -8.8152 | -121.5074 | 121.0658 | 0.010934 | 121.1345 | 121.0838 | 0.01801 | 0.037011 | 0.18777 | -0.46094 | -8.8298 | -0.10975 | -0.020626 | 0.44031 | -9.1206 | -8.8885 | 121.1306 | 121.1567 | 121.3075 | 121.0707 | -0.053879 | 112.2899 | 111.9991 | 112.2312 | 0.63132 | -121.5806
2553.1719 | 121.2479 | -121.0602 | 0.082397 | 1.4211e-13 | 0.022023 | 0.015919 | 0.0094682 | -0.023789 | 0.0042113 | 0.0036627 | -0.0038156 | 0.040373 | 0.0097594 | -0.00057907 | 0.026495 | 0.088037 | 0.033457 | 0.041952 | 0.079598 | 0.11025 | 0.25643 | 0.010206 | -115.8403 | -120.4426 | -121.0808 | -8.752 | -9.0382 | -8.8244 | -121.5211 | 121.0704 | -0.002799 | 121.1482 | 121.1021 | 0.031746 | 0.027856 | 0.17403 | -0.46094 | -8.8344 | 5.2199 | -0.020629 | 0.44031 | -9.1206 | -8.9068 | 121.1398 | 121.1704 | 121.3166 | 121.0936 | -0.072191 | 112.3082 | 112.022 | 112.2358 | 0.61758 | -121.6035
2554.9688 | 121.2387 | -121.1105 | 0.11444 | 1.4211e-13 | 0.02181 | 0.015705 | 0.0098956 | -0.023362 | 0.0044249 | 0.011293 | -0.0040292 | 0.040586 | 0.0093322 | -0.00036547 | 0.026922 | 0.088037 | 0.0243 | 0.051108 | 0.088755 | 0.11483 | 0.26559 | -0.003531 | -115.8769 | -120.4655 | -121.0945 | -8.752 | -9.0382 | -8.8198 | -121.5303 | 121.107 | -0.025686 | 121.1986 | 121.1616 | 0.054639 | 0.000391 | 0.15115 | -0.41974 | -8.8664 | 5.2336 | 0.015989 | 0.43573 | -9.1526 | -8.9342 | 121.1993 | 121.2254 | 121.3761 | 121.1348 | -0.11797 | 112.3585 | 112.0723 | 112.2907 | 0.64504 | -121.6447
2556.75 | 121.3669 | -121.0693 | 0.082397 | 1.4211e-13 | 0.022451 | 0.015705 | 0.0098956 | -0.023576 | 0.0042113 | 0.018923 | -0.0040292 | 0.041014 | 0.0093322 | -0.00015167 | 0.027136 | 0.092615 | 0.028878 | 0.037373 | 0.084176 | 0.11025 | 0.25643 | 0.023942 | -115.8861 | -120.4701 | -121.1129 | -8.7657 | -9.0382 | -8.8152 | -121.544 | 121.0933 | 0.001779 | 121.162 | 121.1067 | 0.013431 | 0.027856 | 0.17403 | -0.47468 | -8.8481 | 5.1832 | -0.043525 | 0.43115 | -9.1206 | -8.8976 | 121.1535 | 121.1796 | 121.3258 | 121.0982 | -0.058455 | 112.3036 | 112.0311 | 112.2541 | 0.59926 | -121.6264
2558.4688 | 121.3348 | -121.0693 | 0.073242 | 1.4211e-13 | 0.022023 | 0.015705 | 0.010109 | -0.023789 | 0.0042113 | 0.018923 | -0.003602 | 0.041227 | 0.0091184 | -0.00036547 | 0.02735 | 0.088037 | 0.033457 | 0.041952 | 0.093333 | 0.11483 | 0.26559 | 0.023942 | -116.0097 | -120.493 | -121.122 | -8.7566 | -9.0336 | -8.8152 | -121.5623 | 121.0933 | 0.020091 | 121.1574 | 121.1113 | 0.01801 | 0.04159 | 0.19235 | -0.49299 | -8.8298 | 5.0596 | -0.052682 | 0.44031 | -9.1069 | -8.8885 | 121.1627 | 121.1842 | 121.3349 | 121.1028 | -0.0493 | 112.3128 | 112.0357 | 112.2541 | 0.57637 | -121.6356
2560.2344 | 121.2936 | -121.1151 | 0.07782 | 1.4211e-13 | 0.02181 | 0.015919 | 0.009682 | -0.023789 | 0.0042113 | 0.011293 | -0.004243 | 0.041441 | 0.0093322 | -0.00036547 | 0.028204 | 0.097194 | 0.028878 | 0.037373 | 0.084176 | 0.11025 | 0.27017 | 0.001048 | -115.8128 | -120.5113 | -121.1403 | -8.7657 | -9.0336 | -8.8152 | -121.5761 | 121.1162 | 0.006356 | 121.2123 | 121.1525 | 0.036325 | 0.032433 | 0.19235 | -0.46095 | -8.8435 | 5.3023 | -0.025221 | 0.43573 | -9.1114 | -8.893 | 121.1993 | 121.2254 | 121.3853 | 121.144 | -0.076772 | 112.3494 | 112.0815 | 112.2999 | 0.60383 | -121.6539
2562.0312 | 121.2616 | -121.1243 | 0.10529 | 1.4211e-13 | 0.022023 | 0.016133 | 0.0098956 | -0.023576 | 0.0042113 | 0.011293 | -0.0044566 | 0.041655 | 0.0089048 | -0.00036547 | 0.028204 | 0.10177 | 0.028878 | 0.041952 | 0.093333 | 0.11025 | 0.26101 | 0.001048 | -115.7625 | -120.5159 | -121.1495 | -8.7566 | -9.0473 | -8.8198 | -121.5898 | 121.1253 | -0.011953 | 121.226 | 121.1662 | 0.040904 | 0.004967 | 0.15572 | -0.46553 | -8.8619 | 5.3618 | -0.025223 | 0.44031 | -9.1526 | -8.9251 | 121.2176 | 121.2345 | 121.3853 | 121.1531 | -0.10424 | 112.3677 | 112.0769 | 112.3045 | 0.60841 | -121.6951
2563.7969 | 121.3531 | -121.1288 | 0.073242 | 1.4211e-13 | 0.022664 | 0.016133 | 0.010109 | -0.023362 | 0.0042113 | 0.0036627 | -0.0044566 | 0.041655 | 0.0095458 | 6.1934e-05 | 0.028845 | 0.088037 | 0.033457 | 0.037373 | 0.088755 | 0.11025 | 0.26101 | 0.014784 | -115.8037 | -120.5342 | -121.1678 | -8.7657 | -9.0382 | -8.8198 | -121.6035 | 121.1436 | 0.015513 | 121.2169 | 121.1662 | 0.022589 | 0.037011 | 0.18777 | -0.47469 | -8.839 | 5.3252 | -0.03896 | 0.43573 | -9.1114 | -8.893 | 121.2176 | 121.2391 | 121.3899 | 121.1623 | -0.058458 | 112.3631 | 112.0907 | 112.309 | 0.59467 | -121.6768
2565.5312 | 121.3898 | -121.1517 | 0.082397 | 1.4211e-13 | 0.02181 | 0.015919 | 0.009682 | -0.023362 | 0.0046387 | 0.011293 | -0.0044566 | 0.041655 | 0.0091184 | -0.00015167 | 0.028204 | 0.092615 | 0.028878 | 0.041952 | 0.084176 | 0.11941 | 0.26101 | 0.014784 | -115.7899 | -120.5433 | -121.1724 | -8.7703 | -9.029 | -8.8152 | -121.6173 | 121.1665 | 0.001779 | 121.2443 | 121.1937 | 0.027168 | 0.037014 | 0.17861 | -0.46554 | -8.8527 | 5.3618 | -0.020651 | 0.44489 | -9.1114 | -8.8976 | 121.2359 | 121.2711 | 121.4127 | 121.1806 | -0.067613 | 112.3814 | 112.1227 | 112.3365 | 0.6084 | -121.6997
2567.3125 | 121.3623 | -121.1838 | 0.09613 | 1.4211e-13 | 0.022451 | 0.016133 | 0.009682 | -0.023362 | 0.0039977 | 0.0036627 | -0.0044566 | 0.041868 | 0.0091184 | -0.00057907 | 0.028632 | 0.088037 | 0.028878 | 0.037373 | 0.093333 | 0.11483 | 0.26559 | 0.001048 | -115.8037 | -120.5525 | -121.177 | -8.7611 | -9.0336 | -8.8198 | -121.6356 | 121.1848 | -0.002797 | 121.2718 | 121.2212 | 0.036325 | 0.018702 | 0.16946 | -0.45181 | -8.8573 | 5.3801 | 0.006814 | 0.45863 | -9.1297 | -8.9159 | 121.2771 | 121.2986 | 121.4494 | 121.2127 | -0.095082 | 112.4226 | 112.1502 | 112.364 | 0.63128 | -121.7317
2569.0938 | 121.3303 | -121.17 | 0.10529 | 1.4211e-13 | 0.022451 | 0.015919 | 0.0098956 | -0.023362 | 0.0042113 | 0.011293 | -0.0046702 | 0.041655 | 0.0089048 | 0.00027553 | 0.028845 | 0.097194 | 0.038035 | 0.04653 | 0.084176 | 0.11483 | 0.26101 | 0.005627 | -115.4053 | -120.5708 | -121.2044 | -8.7611 | -9.0382 | -8.8244 | -121.6447 | 121.1757 | -0.02111 | 121.2672 | 121.2166 | 0.040903 | 0.009546 | 0.15572 | -0.4747 | -8.8664 | 5.7647 | -0.034391 | 0.44031 | -9.1435 | -8.9297 | 121.2542 | 121.2849 | 121.4311 | 121.2081 | -0.099659 | 112.4089 | 112.1319 | 112.3457 | 0.59924 | -121.75
2570.8125 | 121.3943 | -121.1884 | 0.082397 | 1.4211e-13 | 0.022451 | 0.015919 | 0.0098956 | -0.023362 | 0.0044249 | 0.0036627 | -0.0046702 | 0.041655 | 0.0091184 | -0.00036547 | 0.029273 | 0.07888 | 0.0243 | 0.04653 | 0.093333 | 0.10567 | 0.26101 | 0.010206 | -114.9017 | -120.5937 | -121.2228 | -8.7611 | -9.0382 | -8.8106 | -121.6631 | 121.1986 | 0.010936 | 121.2672 | 121.2349 | 0.036324 | 0.023277 | 0.17861 | -0.47471 | -8.8435 | 6.2867 | -0.034396 | 0.44031 | -9.1206 | -8.893 | 121.2817 | 121.294 | 121.4494 | 121.2127 | -0.072191 | 112.4272 | 112.1502 | 112.3777 | 0.59465 | -121.7455
2572.5938 | 121.3531 | -121.2296 | 0.11444 | 1.4211e-13 | 0.02181 | 0.015919 | 0.009682 | -0.023362 | 0.0042113 | 0.011293 | -0.0048838 | 0.041868 | 0.0091184 | -0.00036547 | 0.028845 | 0.092615 | 0.028878 | 0.041952 | 0.093333 | 0.10567 | 0.26101 | 0.005627 | -114.8284 | -120.5983 | -121.2365 | -8.7657 | -9.0382 | -8.8198 | -121.6631 | 121.2352 | -0.021108 | 121.3222 | 121.2715 | 0.036325 | -0.008767 | 0.14657 | -0.43351 | -8.8802 | 6.4011 | -0.006933 | 0.42658 | -9.1526 | -8.9342 | 121.3229 | 121.3352 | 121.4906 | 121.2584 | -0.10881 | 112.4638 | 112.1914 | 112.4098 | 0.63127 | -121.7775
2574.375 | 121.463 | -121.1929 | 0.068665 | 1.4211e-13 | 0.022451 | 0.015919 | 0.009682 | -0.022935 | 0.0044249 | 0.011293 | -0.004243 | 0.041655 | 0.0089048 | -0.00036547 | 0.030341 | 0.088037 | 0.028878 | 0.037373 | 0.084176 | 0.11025 | 0.26101 | 0.028521 | -114.8559 | -120.6166 | -121.2411 | -8.7611 | -9.0428 | -8.8152 | -121.6814 | 121.2215 | 0.015511 | 121.281 | 121.2303 | 0.008852 | 0.041588 | 0.19235 | -0.48845 | -8.8298 | 6.337 | -0.048133 | 0.44031 | -9.1114 | -8.8839 | 121.2771 | 121.3032 | 121.4539 | 121.2218 | -0.040144 | 112.4318 | 112.1502 | 112.3777 | 0.57634 | -121.75
2576.1562 | 121.4081 | -121.2433 | 0.10529 | 1.4211e-13 | 0.022237 | 0.015919 | 0.009682 | -0.023148 | 0.0044249 | 0.018923 | -0.0046702 | 0.041868 | 0.0091184 | -0.00036547 | 0.029913 | 0.088037 | 0.033457 | 0.041952 | 0.093333 | 0.11483 | 0.26101 | 0.001048 | -114.6544 | -120.6212 | -121.2594 | -8.7566 | -9.0382 | -8.8198 | -121.6951 | 121.2443 | -0.011953 | 121.3313 | 121.2852 | 0.040904 | 0.009546 | 0.15572 | -0.45183 | -8.8619 | 6.5889 | -0.016094 | 0.43574 | -9.1435 | -8.9251 | 121.3366 | 121.3581 | 121.5043 | 121.2767 | -0.10424 | 112.4867 | 112.2051 | 112.4235 | 0.62211 | -121.8004
2577.875 | 121.5408 | -121.1838 | 0.091553 | 1.4211e-13 | 0.022023 | 0.015705 | 0.0098956 | -0.023576 | 0.0044249 | 0.011293 | -0.0044566 | 0.041655 | 0.0089048 | -0.00015167 | 0.030554 | 0.07888 | 0.028878 | 0.041952 | 0.084176 | 0.11025 | 0.27017 | -0.012689 | -114.7048 | -120.6395 | -121.2685 | -8.7611 | -9.0428 | -8.8061 | -121.7134 | 121.1711 | -0.007377 | 121.2627 | 121.2257 | 0.054641 | 0.0187 | 0.17861 | -0.52965 | -8.8527 | 6.479 | -0.08476 | 0.44489 | -9.1343 | -8.8976 | 121.268 | 121.294 | 121.4539 | 121.2127 | -0.10424 | 112.4226 | 112.141 | 112.3777 | 0.54429 | -121.805
2579.6562 | 121.5134 | -121.1975 | 0.073242 | 1.4211e-13 | 0.022237 | 0.015919 | 0.009682 | -0.023789 | 0.0044249 | 0.0036627 | -0.0048838 | 0.042082 | 0.0091184 | -0.00079267 | 0.030768 | 0.083459 | 0.038035 | 0.037373 | 0.088755 | 0.11025 | 0.26559 | -0.003531 | -115.126 | -120.6486 | -121.2823 | -8.7657 | -9.0428 | -8.8198 | -121.7089 | 121.194 | 0.015513 | 121.281 | 121.2349 | 0.040904 | 0.037011 | 0.19235 | -0.51134 | -8.839 | 6.0715 | -0.084763 | 0.42658 | -9.116 | -8.893 | 121.2863 | 121.3078 | 121.4631 | 121.2355 | -0.076773 | 112.4318 | 112.1547 | 112.3777 | 0.54886 | -121.7821
2581.4375 | 121.4127 | -121.2845 | 0.10071 | 1.4211e-13 | 0.022664 | 0.015919 | 0.010109 | -0.023362 | 0.0042113 | 0.011293 | -0.004243 | 0.041868 | 0.0091184 | -0.00036547 | 0.031195 | 0.083459 | 0.028878 | 0.04653 | 0.084176 | 0.11025 | 0.26101 | 0.005627 | -115.4374 | -120.6624 | -121.2914 | -8.7566 | -9.0428 | -8.8198 | -121.7317 | 121.2901 | -0.016532 | 121.3679 | 121.331 | 0.040903 | 0.009545 | 0.1603 | -0.44726 | -8.8573 | 5.8471 | -0.006946 | 0.44031 | -9.1435 | -8.9205 | 121.3687 | 121.3947 | 121.5455 | 121.3134 | -0.095081 | 112.5279 | 112.2417 | 112.4647 | 0.6221 | -121.8325
2583.2344 | 121.4401 | -121.2708 | 0.10071 | 1.4211e-13 | 0.022237 | 0.015919 | 0.009682 | -0.023789 | 0.0044249 | 0.011293 | -0.0046702 | 0.041868 | 0.0091184 | -0.00015167 | 0.030768 | 0.088037 | 0.033457 | 0.04653 | 0.084176 | 0.10567 | 0.26559 | 0.010206 | -113.0656 | -120.6761 | -121.3052 | -8.7611 | -9.0382 | -8.8198 | -121.7363 | 121.281 | -0.016532 | 121.3588 | 121.3173 | 0.036324 | 0.004966 | 0.16488 | -0.46557 | -8.8619 | 8.2051 | -0.034415 | 0.43116 | -9.1389 | -8.9205 | 121.3549 | 121.3764 | 121.5363 | 121.3042 | -0.090502 | 112.5096 | 112.2326 | 112.451 | 0.59463 | -121.837
2585.0312 | 121.55 | -121.2387 | 0.068665 | 1.4211e-13 | 0.022664 | 0.015919 | 0.009682 | -0.023362 | 0.0042113 | 0.011293 | -0.0046702 | 0.041441 | 0.0093322 | -0.00015167 | 0.03205 | 0.088037 | 0.042614 | 0.041952 | 0.084176 | 0.11941 | 0.26559 | 0.019363 | -119.1782 | -120.6944 | -121.3052 | -8.7566 | -9.0428 | -8.8152 | -121.7455 | 121.2581 | 0.015511 | 121.3267 | 121.2807 | 0.022589 | 0.050746 | 0.19692 | -0.50677 | -8.8252 | 2.0605 | -0.066459 | 0.44031 | -9.1114 | -8.8839 | 121.3229 | 121.3581 | 121.5043 | 121.2813 | -0.049302 | 112.4821 | 112.1959 | 112.4235 | 0.54427 | -121.8141
2586.8281 | 121.4813 | -121.3028 | 0.091553 | 1.4211e-13 | 0.022237 | 0.015705 | 0.009682 | -0.023789 | 0.0042113 | 0.011293 | -0.0044566 | 0.041441 | 0.0093322 | -0.00057907 | 0.032905 | 0.088037 | 0.038035 | 0.04653 | 0.084176 | 0.11483 | 0.26559 | -0.031005 | -119.2011 | -120.699 | -121.3281 | -8.7611 | -9.0428 | -8.8152 | -121.7546 | 121.2718 | -0.007377 | 121.3908 | 121.3493 | 0.077535 | 0.023279 | 0.17403 | -0.45184 | -8.8527 | 2.1017 | -0.025265 | 0.42658 | -9.1343 | -8.9068 | 121.387 | 121.4176 | 121.5684 | 121.3408 | -0.12256 | 112.5417 | 112.26 | 112.4876 | 0.60378 | -121.8462
2588.5625 | 121.5729 | -121.2799 | 0.068665 | 1.4211e-13 | 0.022237 | 0.015919 | 0.009682 | -0.023362 | 0.0046387 | 0.0036627 | -0.0068066 | 0.039305 | 0.014246 | -0.00036547 | 0.033759 | 0.092615 | 0.033457 | 0.041952 | 0.093333 | 0.11025 | 0.27017 | 0.028521 | -119.2057 | -120.7082 | -121.3326 | -8.7657 | -9.0336 | -8.8198 | -121.7684 | 121.3084 | 0.024668 | 121.3725 | 121.3219 | 0.013431 | 0.041588 | 0.2015 | -0.48847 | -8.8344 | 2.0742 | -0.052732 | 0.43574 | -9.1023 | -8.8885 | 121.3732 | 121.3902 | 121.5501 | 121.3134 | -0.040144 | 112.5142 | 112.2463 | 112.4601 | 0.57174 | -121.837
2590.3281 | 121.5591 | -121.312 | 0.07782 | 1.4211e-13 | 0.022451 | 0.015919 | 0.0098956 | -0.023362 | 0.0042113 | 0.011293 | -0.0080884 | 0.037809 | 0.016383 | -0.00015167 | 0.0344 | 0.092615 | 0.0243 | 0.037373 | 0.084176 | 0.11025 | 0.26559 | 0.001048 | -119.1736 | -120.7173 | -121.3418 | -8.7611 | -9.0473 | -8.8152 | -121.7775 | 121.313 | 0.006356 | 121.4046 | 121.3493 | 0.036325 | 0.032433 | 0.18777 | -0.46558 | -8.839 | 2.1383 | -0.029845 | 0.43574 | -9.1252 | -8.893 | 121.3961 | 121.4222 | 121.5775 | 121.3363 | -0.076772 | 112.5508 | 112.2646 | 112.4967 | 0.59462 | -121.8554
2592.1094 | 121.5775 | -121.2982 | 0.068665 | 1.4211e-13 | 0.022237 | 0.015705 | 0.0098956 | -0.023789 | 0.0042113 | 0.011293 | -0.0078748 | 0.038023 | 0.01681 | -0.00015167 | 0.033546 | 0.092615 | 0.033457 | 0.04653 | 0.07502 | 0.11025 | 0.26101 | 0.023942 | -119.4941 | -120.7219 | -121.351 | -8.7703 | -9.0382 | -8.8106 | -121.7867 | 121.3222 | 0.006355 | 121.3908 | 121.3447 | 0.022588 | 0.041588 | 0.19235 | -0.48847 | -8.839 | 1.8041 | -0.052736 | 0.43574 | -9.1069 | -8.8793 | 121.3732 | 121.4085 | 121.5592 | 121.3317 | -0.044723 | 112.5279 | 112.26 | 112.4876 | 0.57631 | -121.8554
2593.8125 | 121.5179 | -121.3394 | 0.086975 | 1.4211e-13 | 0.022451 | 0.015919 | 0.0098956 | -0.023789 | 0.0044249 | 0.011293 | -0.0085156 | 0.038023 | 0.01681 | -0.00036547 | 0.033973 | 0.088037 | 0.028878 | 0.041952 | 0.088755 | 0.11025 | 0.26101 | 0.014784 | -119.343 | -120.7356 | -121.3555 | -8.7611 | -9.0473 | -8.8198 | -121.7958 | 121.3542 | 0.00178 | 121.4275 | 121.3814 | 0.027168 | 0.023278 | 0.17404 | -0.45643 | -8.8481 | 1.9964 | -0.016116 | 0.44032 | -9.1343 | -8.9068 | 121.4282 | 121.4497 | 121.6004 | 121.3683 | -0.072191 | 112.5783 | 112.2921 | 112.5196 | 0.60378 | -121.8828
2595.5938 | 121.6415 | -121.3211 | 0.073242 | 1.4211e-13 | 0.022451 | 0.015705 | 0.0094682 | -0.023576 | 0.0044249 | 0.011293 | -0.008302 | 0.038236 | 0.01681 | -0.00036547 | 0.034187 | 0.083459 | 0.028878 | 0.041952 | 0.093333 | 0.11025 | 0.26101 | 0.019363 | -118.9767 | -120.7448 | -121.3738 | -8.7566 | -9.0519 | -8.8244 | -121.805 | 121.3405 | 0.020091 | 121.4046 | 121.3631 | 0.022589 | 0.037011 | 0.18777 | -0.4839 | -8.8298 | 2.3444 | -0.052741 | 0.43116 | -9.1252 | -8.8976 | 121.4144 | 121.4314 | 121.5821 | 121.35 | -0.053879 | 112.5645 | 112.2692 | 112.4967 | 0.57631 | -121.8782
2597.3125 | 121.6278 | -121.3165 | 0.068665 | 1.4211e-13 | 0.022878 | 0.015705 | 0.0098956 | -0.023362 | 0.0042113 | 0.018923 | -0.0085156 | 0.037595 | 0.017023 | -0.00057907 | 0.034614 | 0.088037 | 0.038035 | 0.04653 | 0.084176 | 0.11025 | 0.26559 | -0.012689 | -119.0179 | -120.754 | -121.3738 | -8.7657 | -9.0428 | -8.8198 | -121.8142 | 121.3038 | 0.015511 | 121.4046 | 121.3631 | 0.059219 | 0.041588 | 0.19692 | -0.49764 | -8.8344 | 2.2986 | -0.057319 | 0.44032 | -9.1114 | -8.8885 | 121.4007 | 121.4268 | 121.5821 | 121.3546 | -0.081354 | 112.5508 | 112.2738 | 112.4967 | 0.56257 | -121.8828
2599.0938 | 121.5042 | -121.3806 | 0.09613 | 1.4211e-13 | 0.022664 | 0.015705 | 0.009682 | -0.023362 | 0.0042113 | 0.018923 | -0.0080884 | 0.038023 | 0.016383 | -0.00036547 | 0.034614 | 0.088037 | 0.028878 | 0.041952 | 0.088755 | 0.11483 | 0.26559 | 0.005627 | -118.9676 | -120.7677 | -121.3922 | -8.7703 | -9.0382 | -8.8244 | -121.8325 | 121.3862 | -0.007375 | 121.4687 | 121.4226 | 0.036325 | 0.018702 | 0.16946 | -0.45186 | -8.8664 | 2.413 | -0.011547 | 0.44032 | -9.1343 | -8.9205 | 121.4694 | 121.4954 | 121.6462 | 121.4095 | -0.090503 | 112.6103 | 112.3424 | 112.5562 | 0.61292 | -121.9286
2600.8281 | 121.6644 | -121.3257 | 0.064087 | 1.4211e-13 | 0.022451 | 0.015919 | 0.0098956 | -0.023362 | 0.0042113 | 0.0036627 | -0.0070202 | 0.038664 | 0.014246 | 6.1934e-05 | 0.036109 | 0.088037 | 0.028878 | 0.041952 | 0.088755 | 0.11025 | 0.25643 | 0.014784 | -118.8668 | -120.7768 | -121.3922 | -8.7566 | -9.0428 | -8.8152 | -121.8416 | 121.3405 | 0.024668 | 121.4137 | 121.3676 | 0.027168 | 0.046166 | 0.19234 | -0.51595 | -8.8207 | 2.4588 | -0.066478 | 0.44948 | -9.1069 | -8.8793 | 121.4144 | 121.4359 | 121.5821 | 121.3546 | -0.049303 | 112.5691 | 112.2829 | 112.5105 | 0.54883 | -121.9057
2602.6094 | 121.6507 | -121.3623 | 0.07782 | 1.4211e-13 | 0.022237 | 0.015705 | 0.0098956 | -0.023576 | 0.0044249 | 0.011293 | -0.006593 | 0.039518 | 0.012964 | -0.00036547 | 0.036109 | 0.092615 | 0.033457 | 0.04653 | 0.084176 | 0.10567 | 0.26559 | 0.005627 | -118.6791 | -120.7814 | -121.4013 | -8.7657 | -9.0382 | -8.829 | -121.8508 | 121.3679 | 0.006356 | 121.4549 | 121.4088 | 0.040903 | 0.027854 | 0.18777 | -0.48849 | -8.8435 | 2.6832 | -0.039015 | 0.44948 | -9.116 | -8.9068 | 121.4465 | 121.468 | 121.6279 | 121.3958 | -0.072193 | 112.5966 | 112.3241 | 112.5334 | 0.58088 | -121.9286
2604.4062 | 121.6232 | -121.3577 | 0.082397 | 1.4211e-13 | 0.022664 | 0.015919 | 0.010109 | -0.023362 | 0.0042113 | 0.018923 | -0.0063794 | 0.039945 | 0.01275 | -0.00036547 | 0.03675 | 0.088037 | 0.033457 | 0.041952 | 0.088755 | 0.10567 | 0.25643 | -0.00811 | -118.496 | -120.7906 | -121.4196 | -8.7566 | -9.0382 | -8.8198 | -121.86 | 121.3496 | 0.006358 | 121.4458 | 121.3997 | 0.050062 | 0.023277 | 0.17403 | -0.50223 | -8.839 | 2.8618 | -0.061907 | 0.44032 | -9.1206 | -8.9022 | 121.4465 | 121.4634 | 121.6142 | 121.3912 | -0.090507 | 112.6012 | 112.3195 | 112.5379 | 0.56714 | -121.9423
2606.1406 | 121.6232 | -121.3852 | 0.091553 | 1.4211e-13 | 0.022237 | 0.015705 | 0.009682 | -0.023148 | 0.0044249 | 0.011293 | -0.0061656 | 0.039518 | 0.013391 | -0.00036547 | 0.036323 | 0.088037 | 0.0243 | 0.041952 | 0.084176 | 0.11483 | 0.26101 | 0.023942 | -117.9923 | -120.7997 | -121.4334 | -8.7657 | -9.0473 | -8.8152 | -121.8645 | 121.4091 | -0.007377 | 121.4732 | 121.4271 | 0.01801 | 0.023279 | 0.16946 | -0.47934 | -8.8573 | 3.3929 | -0.048178 | 0.43116 | -9.1389 | -8.9068 | 121.4694 | 121.5 | 121.6462 | 121.4095 | -0.067611 | 112.6195 | 112.3378 | 112.57 | 0.58545 | -121.9561
2607.9219 | 121.5775 | -121.4218 | 0.11444 | 1.4211e-13 | 0.022664 | 0.015919 | 0.0098956 | -0.023789 | 0.0044249 | 0.011293 | -0.0038156 | 0.042509 | 0.0078366 | -0.00057907 | 0.037178 | 0.083459 | 0.028878 | 0.041952 | 0.088755 | 0.11483 | 0.26101 | -0.00811 | -119.4987 | -120.8089 | -121.4379 | -8.7657 | -9.0473 | -8.829 | -121.8691 | 121.4137 | -0.025686 | 121.5053 | 121.4638 | 0.050062 | 0.000391 | 0.14657 | -0.4473 | -8.8802 | 1.9231 | -0.016135 | 0.43116 | -9.1618 | -8.9434 | 121.5106 | 121.5366 | 121.6828 | 121.4507 | -0.12255 | 112.6561 | 112.3745 | 112.5929 | 0.61291 | -121.9836
2609.7031 | 121.6003 | -121.3943 | 0.11444 | 1.4211e-13 | 0.022664 | 0.016133 | 0.0098956 | -0.023576 | 0.0039977 | 0.018923 | -0.0038156 | 0.041868 | 0.0080502 | -0.00036547 | 0.037391 | 0.092615 | 0.0243 | 0.041952 | 0.088755 | 0.10567 | 0.26559 | -0.012689 | -119.3339 | -120.8135 | -121.4334 | -8.7703 | -9.0336 | -8.8244 | -121.8737 | 121.3817 | -0.025686 | 121.487 | 121.4363 | 0.054641 | -0.008767 | 0.15115 | -0.47934 | -8.8847 | 2.0605 | -0.039023 | 0.44032 | -9.1481 | -8.9388 | 121.4831 | 121.5 | 121.6599 | 121.4186 | -0.12713 | 112.624 | 112.3607 | 112.57 | 0.58087 | -121.9881
2611.4844 | 121.5683 | -121.3852 | 0.07782 | 1.4211e-13 | 0.022664 | 0.016346 | 0.009682 | -0.023362 | 0.0044249 | 0.0036627 | -0.0038156 | 0.042082 | 0.0082638 | -0.00036547 | 0.038032 | 0.092615 | 0.028878 | 0.04653 | 0.088755 | 0.1011 | 0.26559 | -0.021847 | -119.1141 | -120.7997 | -121.4242 | -8.7611 | -9.0382 | -8.8244 | -121.8645 | 121.3633 | 0.010935 | 121.4778 | 121.4317 | 0.068377 | 0.023275 | 0.18777 | -0.47934 | -8.839 | 2.2711 | -0.03902 | 0.44032 | -9.116 | -8.9022 | 121.4739 | 121.4863 | 121.6508 | 121.4141 | -0.099667 | 112.624 | 112.347 | 112.5608 | 0.58545 | -121.9424
2613.2656 | 121.6873 | -121.3806 | 0.07782 | 1.4211e-13 | 0.022451 | 0.015919 | 0.009682 | -0.022935 | 0.0044249 | 0.0036627 | -0.0038156 | 0.041868 | 0.0082638 | -0.00057907 | 0.038673 | 0.083459 | 0.028878 | 0.04653 | 0.088755 | 0.11483 | 0.26101 | 0.010206 | -118.5051 | -120.8226 | -121.4471 | -8.7611 | -9.0382 | -8.8198 | -121.8874 | 121.3908 | 0.010935 | 121.4641 | 121.4271 | 0.036324 | 0.037012 | 0.18319 | -0.50681 | -8.839 | 2.8755 | -0.066492 | 0.44032 | -9.116 | -8.8976 | 121.4694 | 121.4954 | 121.6416 | 121.4095 | -0.067614 | 112.6195 | 112.3424 | 112.5608 | 0.55798 | -121.9652
2615.0469 | 121.6232 | -121.431 | 0.10986 | 1.4211e-13 | 0.022451 | 0.015919 | 0.0098956 | -0.023576 | 0.0046387 | 0.011293 | -0.004243 | 0.042082 | 0.0082638 | -0.00036547 | 0.039528 | 0.088037 | 0.033457 | 0.041952 | 0.093333 | 0.11483 | 0.26101 | 0.001048 | -118.1755 | -120.8455 | -121.4608 | -8.7566 | -9.0473 | -8.8198 | -121.8874 | 121.432 | -0.01653 | 121.519 | 121.4729 | 0.040904 | 0.004969 | 0.15115 | -0.45646 | -8.8664 | 3.2555 | -0.029874 | 0.42658 | -9.1572 | -8.9297 | 121.5243 | 121.5458 | 121.692 | 121.4644 | -0.10882 | 112.6744 | 112.3836 | 112.6112 | 0.58544 | -121.9973
2616.7656 | 121.5683 | -121.3989 | 0.10529 | 1.4211e-13 | 0.022451 | 0.015705 | 0.009682 | -0.023576 | 0.0044249 | 0.011293 | -0.0040292 | 0.042509 | 0.0078366 | -0.00057907 | 0.042733 | 0.088037 | 0.019721 | 0.041952 | 0.088755 | 0.10567 | 0.27017 | -0.040163 | -121.3164 | -120.7997 | -121.4196 | -8.7657 | -9.0428 | -8.8198 | -121.8737 | 121.3588 | -0.016531 | 121.487 | 121.4409 | 0.082115 | 0.000388 | 0.16488 | -0.47476 | -8.871 | 0.082477 | -0.020708 | 0.45405 | -9.1481 | -8.9251 | 121.4877 | 121.5046 | 121.6691 | 121.4186 | -0.14545 | 112.6332 | 112.3562 | 112.5791 | 0.59918 | -121.979
2618.5625 | 121.4859 | -121.3669 | 0.11902 | 1.4211e-13 | 0.022664 | 0.016346 | 0.010323 | -0.023362 | 0.0044249 | 0.018923 | -0.003602 | 0.042296 | 0.0078366 | -0.00036547 | 0.044015 | 0.083459 | 0.028878 | 0.04653 | 0.084176 | 0.10567 | 0.27017 | -0.031005 | -121.495 | -120.7677 | -121.383 | -8.7657 | -9.0428 | -8.8244 | -121.8233 | 121.3359 | -0.034843 | 121.4503 | 121.4134 | 0.077535 | -0.013345 | 0.15115 | -0.45644 | -8.8847 | -0.12814 | -0.016123 | 0.44032 | -9.1618 | -8.9434 | 121.4511 | 121.4726 | 121.637 | 121.3958 | -0.15002 | 112.6012 | 112.3241 | 112.5425 | 0.59919 | -121.9423
2620.2812 | 121.4081 | -121.2433 | 0.21057 | 1.4211e-13 | 0.022451 | 0.016133 | 0.0098956 | -0.023576 | 0.0044249 | 0.011293 | -0.0038156 | 0.042723 | 0.007623 | -0.00036547 | 0.043801 | 0.088037 | 0.038035 | 0.041952 | 0.093333 | 0.10567 | 0.26559 | -0.049321 | -121.2981 | -120.5662 | -121.1815 | -8.7703 | -9.0473 | -8.8152 | -121.6264 | 121.194 | -0.11724 | 121.3313 | 121.2852 | 0.091273 | -0.1049 | 0.055017 | -0.38315 | -8.9809 | -0.054848 | 0.061744 | 0.44489 | -9.2579 | -9.0258 | 121.3366 | 121.349 | 121.5089 | 121.2813 | -0.25989 | 112.473 | 112.1959 | 112.4281 | 0.67706 | -121.837
2622.0625 | 115.448 | -111.4197 | 4.1382 | 1.4211e-13 | 0.022451 | 0.015492 | 0.0092546 | -0.022935 | 0.0031431 | 0.0036627 | -0.0038156 | 0.042937 | 0.0074092 | -0.00057907 | 0.039742 | 0.10177 | 0.0243 | 0.051108 | 0.088755 | 0.10567 | 0.25643 | -0.058478 | -109.8468 | -109.1881 | -109.7027 | -8.7611 | -9.0428 | -8.8152 | -110.097 | 111.3612 | -4.0494 | 111.5215 | 111.4708 | 0.10959 | -4.0325 | -3.8818 | 1.3227 | -12.8993 | 1.5729 | 1.717 | 0.39426 | -13.181 | -12.9534 | 111.5084 | 111.5254 | 111.6761 | 111.444 | -4.1967 | 102.6585 | 102.3769 | 102.6045 | 2.2315 | -114.2352
2623.8438 | 121.0281 | -120.7993 | 0.073242 | 1.4211e-13 | 0.022664 | 0.016133 | 0.0098956 | -0.023362 | 0.0042113 | 0.011293 | -0.0033884 | 0.04315 | 0.0065548 | -0.00036547 | 0.044869 | 0.088037 | 0.028878 | 0.04653 | 0.088755 | 0.11025 | 0.26101 | 0.028521 | -120.9364 | -120.1999 | -120.8152 | -8.7657 | -9.0519 | -8.8152 | -121.2601 | 120.8278 | 0.015513 | 120.8873 | 120.8458 | 0.018009 | 0.037011 | 0.18777 | -0.46087 | -8.839 | -0.13716 | -0.01599 | 0.44488 | -9.1252 | -8.8885 | 120.888 | 120.9095 | 121.0603 | 120.8281 | -0.044721 | 112.0335 | 111.7473 | 111.984 | 0.59932 | -121.3334
2625.6406 | 121.1838 | -120.8817 | 0.07782 | 1.4211e-13 | 0.022451 | 0.016346 | 0.010109 | -0.023576 | 0.0044249 | 0.011293 | -0.0025338 | 0.04315 | 0.006341 | -0.00036547 | 0.045937 | 0.088037 | 0.028878 | 0.037373 | 0.088755 | 0.11483 | 0.27017 | -0.021847 | -121.06 | -120.319 | -120.9389 | -8.7611 | -9.0519 | -8.8152 | -121.37 | 120.8598 | 0.010935 | 120.9697 | 120.919 | 0.05922 | 0.037012 | 0.19235 | -0.48837 | -8.839 | -0.17839 | -0.057217 | 0.43115 | -9.1297 | -8.893 | 120.9704 | 120.9965 | 121.1518 | 120.9105 | -0.099667 | 112.1205 | 111.8297 | 112.0664 | 0.56267 | -121.4478
2627.3594 | 121.2341 | -120.9503 | 0.082397 | 1.4211e-13 | 0.022664 | 0.015919 | 0.0098956 | -0.023148 | 0.0039977 | 0.011293 | -0.0023202 | 0.043578 | 0.0048456 | -0.00036547 | 0.046365 | 0.092615 | 0.028878 | 0.04653 | 0.093333 | 0.11483 | 0.26559 | 0.010206 | -121.115 | -120.3785 | -121.003 | -8.7611 | -9.0428 | -8.8152 | -121.4295 | 120.9605 | 0.010936 | 121.0429 | 120.9968 | 0.036324 | 0.032435 | 0.18319 | -0.47923 | -8.8435 | -0.16467 | -0.052655 | 0.42657 | -9.1252 | -8.8976 | 121.0436 | 121.0651 | 121.2159 | 120.9792 | -0.072191 | 112.1892 | 111.9075 | 112.1351 | 0.57182 | -121.5119
2629.1406 | 121.2753 | -120.9457 | 0.073242 | 1.4211e-13 | 0.022451 | 0.015705 | 0.0098956 | -0.023362 | 0.0044249 | 0.018923 | -0.0014656 | 0.044432 | 0.003991 | -0.00057907 | 0.047219 | 0.092615 | 0.028878 | 0.041952 | 0.084176 | 0.11025 | 0.26559 | 0.010206 | -121.1562 | -120.4106 | -121.0259 | -8.7611 | -9.0428 | -8.8244 | -121.4616 | 120.9559 | 0.010934 | 121.0384 | 120.9877 | 0.031746 | 0.037011 | 0.19235 | -0.51586 | -8.8344 | -0.21045 | -0.080125 | 0.43573 | -9.116 | -8.8976 | 121.0299 | 121.056 | 121.2113 | 120.9746 | -0.063036 | 112.1846 | 111.903 | 112.1214 | 0.53519 | -121.5348
2630.8594 | 121.1929 | -121.0144 | 0.11444 | 1.4211e-13 | 0.022664 | 0.015919 | 0.009682 | -0.023576 | 0.0042113 | 0.011293 | -0.0014656 | 0.04486 | 0.0031364 | -0.00079267 | 0.048288 | 0.092615 | 0.0243 | 0.04653 | 0.088755 | 0.11483 | 0.26101 | 0.023942 | -121.1745 | -120.4472 | -121.0488 | -8.7657 | -9.0428 | -8.8198 | -121.4936 | 121.0383 | -0.025686 | 121.107 | 121.0609 | 0.022588 | 0.000391 | 0.14657 | -0.47924 | -8.8802 | -0.16011 | -0.034355 | 0.44489 | -9.1572 | -8.9342 | 121.1032 | 121.1292 | 121.2754 | 121.0387 | -0.090499 | 112.2487 | 111.9716 | 112.1946 | 0.56722 | -121.6081
2632.6406 | 121.2845 | -121.0052 | 0.09613 | 1.4211e-13 | 0.022664 | 0.015919 | 0.0098956 | -0.023148 | 0.0042113 | 0.011293 | -0.00061095 | 0.045287 | 0.0016408 | -0.00057907 | 0.049783 | 0.083459 | 0.0243 | 0.037373 | 0.084176 | 0.11483 | 0.26559 | 0.010206 | -121.1974 | -120.4609 | -121.0762 | -8.7611 | -9.0428 | -8.8244 | -121.512 | 121.0155 | -0.011954 | 121.0887 | 121.0426 | 0.027167 | 0.018702 | 0.16946 | -0.50671 | -8.8573 | -0.19215 | -0.070982 | 0.43573 | -9.1389 | -8.9205 | 121.0894 | 121.1201 | 121.2708 | 121.0295 | -0.085924 | 112.2441 | 111.9625 | 112.1809 | 0.54433 | -121.6081
2634.4219 | 121.3028 | -121.0281 | 0.07782 | 1.4211e-13 | 0.022878 | 0.016133 | 0.0094682 | -0.023362 | 0.0044249 | 0.011293 | -0.00018375 | 0.045928 | 0.00099983 | -0.00036547 | 0.050638 | 0.088037 | 0.028878 | 0.032795 | 0.084176 | 0.11025 | 0.26559 | -0.003531 | -121.2249 | -120.4838 | -121.09 | -8.7703 | -9.0473 | -8.8198 | -121.5303 | 121.0246 | 0.006356 | 121.1162 | 121.0609 | 0.036326 | 0.032433 | 0.18777 | -0.50214 | -8.8481 | -0.19674 | -0.06183 | 0.44031 | -9.1252 | -8.8976 | 121.1123 | 121.1384 | 121.2937 | 121.057 | -0.081351 | 112.2578 | 111.9808 | 112.2083 | 0.54433 | -121.6081
2636.1719 | 121.3623 | -121.0602 | 0.082397 | 1.4211e-13 | 0.022878 | 0.015919 | 0.0098956 | -0.023362 | 0.0039977 | 0.011293 | 2.985e-05 | 0.045928 | 0.00078623 | -0.00057907 | 0.053415 | 0.088037 | 0.0243 | 0.037373 | 0.084176 | 0.10567 | 0.26559 | 0.005627 | -121.2295 | -120.4975 | -121.1083 | -8.7749 | -9.0473 | -8.829 | -121.5486 | 121.0658 | 0.001779 | 121.1482 | 121.0976 | 0.031746 | 0.023277 | 0.18319 | -0.48841 | -8.8573 | -0.16927 | -0.048101 | 0.44031 | -9.1297 | -8.9113 | 121.1444 | 121.1659 | 121.3258 | 121.0845 | -0.07677 | 112.2853 | 112.0128 | 112.2312 | 0.56263 | -121.631
2637.9531 | 121.3623 | -121.0602 | 0.082397 | 1.4211e-13 | 0.022878 | 0.015705 | 0.0094682 | -0.023576 | 0.0044249 | 0.018923 | 0.0013116 | 0.046355 | -0.00092297 | -0.00057907 | 0.054484 | 0.083459 | 0.033457 | 0.041952 | 0.088755 | 0.10567 | 0.27017 | 0.014784 | -121.2432 | -120.5113 | -121.1266 | -8.7611 | -9.0382 | -8.829 | -121.5623 | 121.075 | 0.006358 | 121.1436 | 121.1021 | 0.027168 | 0.023277 | 0.18777 | -0.50215 | -8.8435 | -0.18301 | -0.066416 | 0.43573 | -9.1206 | -8.9113 | 121.1489 | 121.1659 | 121.3303 | 121.0936 | -0.067613 | 112.299 | 112.022 | 112.2312 | 0.5489 | -121.6447
2639.7344 | 121.3806 | -121.1197 | 0.068665 | 1.4211e-13 | 0.022878 | 0.015705 | 0.0094682 | -0.024003 | 0.0044249 | 0.018923 | 0.0030208 | 0.04721 | -0.0034868 | -0.00036547 | 0.055979 | 0.07888 | 0.033457 | 0.041952 | 0.088755 | 0.11025 | 0.26559 | -0.012689 | -121.2523 | -120.525 | -121.1358 | -8.7657 | -9.0336 | -8.8152 | -121.5669 | 121.107 | 0.02009 | 121.1986 | 121.1616 | 0.054641 | 0.041588 | 0.19692 | -0.44722 | -8.8344 | -0.13266 | -0.016064 | 0.43115 | -9.1023 | -8.8839 | 121.2084 | 121.2299 | 121.3853 | 121.1531 | -0.081354 | 112.354 | 112.0861 | 112.3045 | 0.59467 | -121.6356
2641.5156 | 121.1288 | -120.6665 | 0.49896 | 1.4211e-13 | 0.022451 | 0.015705 | 0.0098956 | -0.023148 | 0.0044249 | 0.0036627 | 0.95008 | 0.68733 | -1.602 | 6.1934e-05 | 1.6622 | 0.092615 | 0.028878 | 0.041952 | 0.084176 | 0.11483 | 0.26559 | -0.017268 | -120.2817 | -119.591 | -120.188 | -8.7657 | -9.0382 | -8.8152 | -120.9579 | 120.6492 | -0.41479 | 120.7591 | 120.7085 | 0.05922 | -0.38413 | -0.23337 | -0.29142 | -9.2647 | 0.38484 | 0.47854 | 0.76996 | -9.5372 | -9.3142 | 120.7507 | 120.7813 | 120.9321 | 120.6954 | -0.51623 | 111.9008 | 111.6283 | 111.8513 | 1.0755 | -121.4569
2643.3125 | 121.1746 | -120.8954 | 0.2655 | 1.4211e-13 | 0.022878 | 0.015705 | 0.009682 | -0.023789 | 0.0042113 | 0.011293 | 0.34548 | 0.27796 | -0.59892 | -0.00057907 | 0.63818 | 0.088037 | 0.028878 | 0.04653 | 0.093333 | 0.1011 | 0.26559 | -0.021847 | -120.886 | -120.1725 | -120.7695 | -8.7611 | -9.0428 | -8.8244 | -121.3334 | 120.8735 | -0.17217 | 120.9834 | 120.9419 | 0.068377 | -0.16441 | 8.5e-05 | -0.438 | -9.0266 | 0.009336 | 0.12593 | 0.56393 | -9.3083 | -9.0899 | 120.9887 | 120.9965 | 121.161 | 120.9243 | -0.28735 | 112.1342 | 111.8526 | 112.071 | 0.72293 | -121.5989
2645.0938 | 121.2753 | -120.7718 | 0.27924 | 1.4211e-13 | 0.022664 | 0.016133 | 0.0098956 | -0.023576 | 0.0042113 | 0.0036627 | 0.66444 | 0.51811 | -1.1574 | -0.00015167 | 1.1948 | 0.092615 | 0.033457 | 0.041952 | 0.088755 | 0.11483 | 0.26559 | -0.017268 | -120.5747 | -119.8748 | -120.481 | -8.7566 | -9.0382 | -8.8244 | -121.1502 | 120.7545 | -0.19048 | 120.8644 | 120.8137 | 0.05922 | -0.1644 | -0.013648 | -0.37845 | -9.0358 | 0.19709 | 0.29079 | 0.66924 | -9.3174 | -9.1036 | 120.8605 | 120.8866 | 121.0374 | 120.8052 | -0.2965 | 112.0152 | 111.7336 | 111.9474 | 0.89695 | -121.4295
2646.875 | 121.0831 | -120.2545 | 0.68207 | 1.4211e-13 | 0.022664 | 0.015919 | 0.010109 | -0.023789 | 0.0039977 | 0.011293 | 1.4182 | 1.0448 | -2.4359 | -0.00015167 | 2.5837 | 0.092615 | 0.042614 | 0.04653 | 0.093333 | 0.11025 | 0.26559 | -0.003531 | -119.7643 | -119.0873 | -119.666 | -8.7657 | -9.0473 | -8.8244 | -120.6511 | 120.251 | -0.58874 | 120.3471 | 120.301 | 0.050061 | -0.57181 | -0.41648 | -0.39663 | -9.4478 | 0.49025 | 0.58853 | 0.98516 | -9.7294 | -9.5064 | 120.3479 | 120.3648 | 120.5201 | 120.2971 | -0.6856 | 111.4888 | 111.2072 | 111.4301 | 1.1672 | -121.3332
2648.6719 | 121.3211 | -121.0739 | 0.082397 | 1.4211e-13 | 0.022664 | 0.015919 | 0.009682 | -0.023362 | 0.0042113 | 0.23258 | 0.027803 | 0.0361 | -0.10112 | -0.00057907 | 0.0017113 | 0.07888 | 0.0243 | 0.037373 | 0.088755 | 0.1011 | 0.26101 | -0.044742 | -0.021846 | -0.054586 | -0.092981 | -0.029954 | 0.06865 | 0.062694 | -0.31067 | 121.0292 | 0.006358 | 121.1528 | 121.1113 | 0.082115 | 0.018698 | 0.17861 | 120.7632 | -0.11235 | 121.0521 | 120.9809 | 0.21769 | -0.013747 | -0.019703 | 121.1627 | 121.175 | 121.3349 | 121.0982 | -0.12714 | 121.044 | 121.1426 | 121.1366 | 121.0193 | -0.39307
2650.3906 | 121.2204 | -121.17 | 0.086975 | 1.4211e-13 | 0.023092 | 0.016133 | 0.0098956 | -0.023576 | 0.0042113 | 0.24021 | 0.026735 | 0.035886 | -0.10027 | -0.00057907 | 0.0010705 | 0.083459 | 0.019721 | 0.041952 | 0.093333 | 0.10567 | 0.25643 | -0.003531 | -0.003531 | -0.031692 | -0.070087 | -0.016219 | 0.064071 | 0.067272 | -0.29236 | 121.1665 | 0.006358 | 121.2535 | 121.212 | 0.045483 | 0.018699 | 0.16946 | 120.8777 | -0.10319 | 121.1665 | 121.1 | 0.22227 | -0.022904 | -0.019703 | 121.2634 | 121.2757 | 121.4265 | 121.1898 | -0.090506 | 121.1538 | 121.2341 | 121.2373 | 121.1384 | -0.37933
2652.1875 | 121.3303 | -121.1334 | 0.10071 | 1.4211e-13 | 0.022878 | 0.016133 | 0.009682 | -0.023362 | 0.0044249 | 0.22495 | 0.026735 | 0.036313 | -0.10006 | -0.00057907 | 0.00042948 | 0.07888 | 0.019721 | 0.037373 | 0.07502 | 0.11025 | 0.25643 | -0.053899 | 0.005626 | -0.017956 | -0.06093 | -0.025376 | 0.06865 | 0.067272 | -0.27862 | 121.0795 | -0.025688 | 121.2123 | 121.1708 | 0.091272 | 0.009545 | 0.15572 | 120.8548 | -0.12608 | 121.139 | 121.0725 | 0.21769 | -0.032058 | -0.033436 | 121.2084 | 121.2437 | 121.3899 | 121.1531 | -0.15461 | 121.108 | 121.2021 | 121.2007 | 121.1155 | -0.37933
2653.9844 | 121.3806 | -121.1105 | 0.050354 | 1.4211e-13 | 0.022664 | 0.016133 | 0.009682 | -0.023148 | 0.0044249 | 0.22495 | 0.025453 | 0.036313 | -0.098774 | -0.00057907 | 0.00064308 | 0.083459 | 0.019721 | 0.037373 | 0.079598 | 0.10567 | 0.25643 | -0.040163 | 0.033099 | 0.000359 | -0.038036 | 0.006674 | 0.1007 | 0.099323 | -0.25115 | 121.0704 | 0.029244 | 121.194 | 121.1479 | 0.077536 | 0.05532 | 0.20608 | 120.8594 | -0.04368 | 121.1436 | 121.0725 | 0.21311 | 0.050346 | 0.048969 | 121.1901 | 121.2162 | 121.367 | 121.1303 | -0.090517 | 121.1172 | 121.2112 | 121.2099 | 121.1109 | -0.3015
2655.7031 | 121.3989 | -121.1151 | 0.073242 | 1.4211e-13 | 0.022451 | 0.015919 | 0.009682 | -0.023362 | 0.0042113 | 0.24784 | 0.025666 | 0.035886 | -0.098347 | -0.00079267 | 2.08e-06 | 0.07888 | 0.019721 | 0.037373 | 0.084176 | 0.1011 | 0.25643 | -0.053899 | 0.051413 | 0.009516 | -0.028879 | 0.011252 | 0.10986 | 0.094744 | -0.26946 | 121.0612 | 0.010934 | 121.194 | 121.1525 | 0.091272 | 0.027853 | 0.18319 | 120.8456 | -0.06199 | 121.1665 | 121.0862 | 0.24058 | 0.036615 | 0.021502 | 121.1993 | 121.2162 | 121.3715 | 121.1348 | -0.12714 | 121.1264 | 121.225 | 121.2099 | 121.1246 | -0.3427
2657.4844 | 121.3623 | -121.1563 | 0.068665 | 1.4211e-13 | 0.022664 | 0.016133 | 0.010109 | -0.023576 | 0.0044249 | 0.22495 | 0.025453 | 0.035886 | -0.098347 | -0.00057907 | 0.00021588 | 0.083459 | 0.019721 | 0.032795 | 0.079598 | 0.10567 | 0.25185 | -0.031005 | 0.051413 | 0.014095 | -0.0243 | 0.011252 | 0.10528 | 0.099323 | -0.26488 | 121.1253 | 0.010933 | 121.2398 | 121.1891 | 0.0638 | 0.037009 | 0.18319 | 120.8914 | -0.057413 | 121.2077 | 121.132 | 0.24058 | 0.036614 | 0.030658 | 121.2359 | 121.262 | 121.4082 | 121.176 | -0.09967 | 121.1676 | 121.2616 | 121.2556 | 121.1704 | -0.33355
2659.2656 | 121.4127 | -121.1426 | 0.054932 | 1.4211e-13 | 0.022451 | 0.015919 | 0.0098956 | -0.023148 | 0.0046387 | 0.24784 | 0.025239 | 0.035672 | -0.098133 | -0.00036547 | 0.00042948 | 0.083459 | 0.028878 | 0.037373 | 0.084176 | 0.10567 | 0.24269 | -0.021847 | 0.046835 | 0.009516 | -0.028879 | 0.015831 | 0.10528 | 0.1039 | -0.25115 | 121.1207 | 0.029244 | 121.226 | 121.18 | 0.05922 | 0.050742 | 0.18776 | 120.8914 | -0.039101 | 121.1894 | 121.1137 | 0.22227 | 0.050347 | 0.048969 | 121.2268 | 121.2483 | 121.3853 | 121.1715 | -0.076779 | 121.1584 | 121.2479 | 121.2465 | 121.1521 | -0.30608
2661.0625 | 121.4264 | -121.1517 | 0.050354 | 1.4211e-13 | 0.022878 | 0.016133 | 0.009682 | -0.023362 | 0.0044249 | 0.24021 | 0.025239 | 0.035886 | -0.098133 | -0.00057907 | 2.08e-06 | 0.07888 | 0.0243 | 0.037373 | 0.093333 | 0.10567 | 0.25643 | -0.053899 | 0.042256 | 0.009516 | -0.0243 | 0.020409 | 0.10528 | 0.1039 | -0.25572 | 121.0978 | 0.042979 | 121.2306 | 121.1891 | 0.091272 | 0.05532 | 0.20608 | 120.896 | -0.029945 | 121.194 | 121.1274 | 0.23142 | 0.054925 | 0.053547 | 121.2451 | 121.2574 | 121.4082 | 121.176 | -0.10425 | 121.1721 | 121.257 | 121.2556 | 121.1612 | -0.30608
2662.7812 | 121.4264 | -121.1746 | 0.050354 | 1.4211e-13 | 0.022878 | 0.015919 | 0.0098956 | -0.023789 | 0.0039977 | 0.23258 | 0.024812 | 0.035031 | -0.096637 | -0.00057907 | 0.00021588 | 0.07888 | 0.0243 | 0.032795 | 0.084176 | 0.10567 | 0.26101 | -0.049321 | 0.060571 | 0.027831 | -0.005985 | 0.029566 | 0.12817 | 0.12222 | -0.23283 | 121.1253 | 0.033822 | 121.2535 | 121.2074 | 0.082116 | 0.05532 | 0.21066 | 120.9418 | -0.020788 | 121.2352 | 121.1686 | 0.22685 | 0.077818 | 0.071862 | 121.2588 | 121.2803 | 121.4356 | 121.1989 | -0.099675 | 121.2042 | 121.3028 | 121.2968 | 121.2025 | -0.28319
2664.5781 | 121.3898 | -121.3165 | 0.086975 | 1.4211e-13 | 0.022878 | 0.015919 | 0.0098956 | -0.023576 | 0.0044249 | 0.24021 | 0.025025 | 0.035031 | -0.09621 | -0.00036547 | 2.08e-06 | 0.074302 | 0.010564 | 0.041952 | 0.093333 | 0.10567 | 0.25185 | -0.053899 | 0.069728 | 0.03241 | -0.005985 | 0.029566 | 0.12359 | 0.12222 | -0.23741 | 121.2626 | 0.006358 | 121.3908 | 121.3585 | 0.095851 | 0.018699 | 0.16488 | 121.0791 | -0.057409 | 121.3863 | 121.3105 | 0.23143 | 0.036618 | 0.035241 | 121.4099 | 121.4222 | 121.5684 | 121.3271 | -0.14087 | 121.3461 | 121.4401 | 121.4387 | 121.3489 | -0.32439
2666.2969 | 121.582 | -121.2799 | 0.073242 | 1.4211e-13 | 0.022451 | 0.015919 | 0.0098956 | -0.023362 | 0.0044249 | 0.22495 | 0.024385 | 0.035031 | -0.09621 | -0.00036547 | 0.00021588 | 0.074302 | 0.0243 | 0.032795 | 0.084176 | 0.10567 | 0.25643 | -0.076794 | 0.074307 | 0.036989 | -0.005985 | 0.029566 | 0.12817 | 0.12679 | -0.23741 | 121.2031 | 0.010934 | 121.3542 | 121.3127 | 0.10959 | 0.032432 | 0.18319 | 121.0425 | -0.043676 | 121.3542 | 121.2739 | 0.23143 | 0.05493 | 0.053552 | 121.3641 | 121.3856 | 121.5363 | 121.3042 | -0.15004 | 121.3095 | 121.4081 | 121.4067 | 121.3169 | -0.31065
2668.1094 | 121.5088 | -121.3165 | 0.064087 | 1.4211e-13 | 0.023092 | 0.015919 | 0.0098956 | -0.023362 | 0.0039977 | 0.24784 | 0.024598 | 0.034604 | -0.096424 | -0.00079267 | 0.00064308 | 0.07888 | 0.019721 | 0.037373 | 0.084176 | 0.1011 | 0.25643 | -0.058478 | 0.074307 | 0.03241 | 0.007751 | 0.029566 | 0.12817 | 0.12679 | -0.22825 | 121.2581 | 0.020089 | 121.3954 | 121.3539 | 0.095851 | 0.037008 | 0.19234 | 121.0883 | -0.034521 | 121.3908 | 121.3243 | 0.236 | 0.064085 | 0.062707 | 121.4007 | 121.4176 | 121.573 | 121.3362 | -0.12257 | 121.3461 | 121.4447 | 121.4433 | 121.3489 | -0.29234
2669.8281 | 121.5546 | -121.3394 | 0.059509 | 1.4211e-13 | 0.022664 | 0.016133 | 0.009682 | -0.023148 | 0.0044249 | 0.24021 | 0.024171 | 0.034818 | -0.096424 | -0.00057907 | 0.00042948 | 0.07888 | 0.015142 | 0.032795 | 0.079598 | 0.1011 | 0.25185 | -0.017268 | 0.069728 | 0.036989 | -0.015143 | 0.024988 | 0.12359 | 0.13137 | -0.23283 | 121.3221 | 0.020089 | 121.4183 | 121.3722 | 0.050063 | 0.041586 | 0.19234 | 121.1066 | -0.034521 | 121.4091 | 121.3243 | 0.21769 | 0.064084 | 0.071864 | 121.419 | 121.4405 | 121.5913 | 121.3546 | -0.076777 | 121.3644 | 121.463 | 121.4708 | 121.3764 | -0.29234
2671.6094 | 121.5134 | -121.3211 | 0.09613 | 1.4211e-13 | 0.022664 | 0.015705 | 0.009682 | -0.023362 | 0.0044249 | 0.23258 | 0.024385 | 0.034604 | -0.096851 | -0.00079267 | 0.00042948 | 0.074302 | 0.015142 | 0.032795 | 0.07502 | 0.10567 | 0.24269 | -0.063057 | 0.06515 | 0.03241 | -0.001407 | 0.029566 | 0.12817 | 0.12222 | -0.23283 | 121.258 | -0.02111 | 121.3954 | 121.3539 | 0.095852 | 0.009544 | 0.14657 | 121.0883 | -0.066564 | 121.3863 | 121.3197 | 0.23142 | 0.032042 | 0.026086 | 121.3961 | 121.4268 | 121.5638 | 121.3362 | -0.15919 | 121.3507 | 121.4493 | 121.4433 | 121.3535 | -0.32896
2673.4062 | 121.4813 | -121.3806 | 0.091553 | 1.4211e-13 | 0.023305 | 0.016133 | 0.009682 | -0.023362 | 0.0044249 | 0.22495 | 0.024385 | 0.034818 | -0.096637 | -0.00015167 | 0.00042948 | 0.083459 | 0.019721 | 0.037373 | 0.079598 | 0.1011 | 0.26101 | -0.076794 | 0.06515 | 0.03241 | -0.005985 | 0.029566 | 0.12817 | 0.12222 | -0.22367 | 121.3038 | -0.011955 | 121.4641 | 121.418 | 0.11417 | 0.009542 | 0.16946 | 121.1569 | -0.061987 | 121.4458 | 121.3746 | 0.21769 | 0.036619 | 0.030663 | 121.4602 | 121.4817 | 121.6416 | 121.4003 | -0.16835 | 121.4102 | 121.5088 | 121.5028 | 121.413 | -0.31523
2675.1406 | 121.4813 | -121.3806 | 0.07782 | 1.4211e-13 | 0.022664 | 0.015919 | 0.010109 | -0.023576 | 0.0042113 | 0.22495 | 0.024171 | 0.035031 | -0.096637 | -0.00036547 | 0.00042948 | 0.07888 | 0.0243 | 0.032795 | 0.079598 | 0.096516 | 0.25185 | -0.040163 | 0.069728 | 0.036989 | -0.005985 | 0.038723 | 0.12359 | 0.12222 | -0.22367 | 121.3405 | 0.001778 | 121.4595 | 121.4134 | 0.072958 | 0.018696 | 0.17403 | 121.1569 | -0.039097 | 121.4503 | 121.3746 | 0.21769 | 0.045773 | 0.044396 | 121.4602 | 121.4771 | 121.6325 | 121.4049 | -0.11798 | 121.4193 | 121.5042 | 121.5028 | 121.4176 | -0.30149
2676.9375 | 121.5363 | -121.4218 | 0.091553 | 1.4211e-13 | 0.023092 | 0.016133 | 0.0098956 | -0.023362 | 0.0048523 | 0.24021 | 0.023957 | 0.034818 | -0.096424 | -0.00015167 | 0.00021588 | 0.083459 | 0.028878 | 0.037373 | 0.079598 | 0.10567 | 0.25643 | -0.058478 | 0.074307 | 0.041567 | -0.001407 | 0.038723 | 0.12359 | 0.12679 | -0.22825 | 121.3633 | -0.011955 | 121.5053 | 121.4592 | 0.095851 | 0.014121 | 0.16488 | 121.1936 | -0.05283 | 121.4961 | 121.4204 | 0.22685 | 0.03204 | 0.035241 | 121.5014 | 121.5275 | 121.6782 | 121.4507 | -0.15003 | 121.4605 | 121.5454 | 121.5486 | 121.4634 | -0.31981
2678.7344 | 121.6507 | -121.344 | 0.07782 | 1.4211e-13 | 0.023092 | 0.015919 | 0.0098956 | -0.023789 | 0.0042113 | 0.24021 | 0.023957 | 0.034818 | -0.096424 | -0.00079267 | 0.00021588 | 0.07888 | 0.019721 | 0.037373 | 0.079598 | 0.1011 | 0.25643 | -0.031005 | 0.069728 | 0.03241 | -0.001407 | 0.034145 | 0.13275 | 0.12222 | -0.22367 | 121.313 | 0.001778 | 121.4229 | 121.3814 | 0.068378 | 0.023275 | 0.17861 | 121.1203 | -0.043675 | 121.4137 | 121.3426 | 0.22227 | 0.05493 | 0.044396 | 121.4236 | 121.4451 | 121.6004 | 121.3637 | -0.10883 | 121.3781 | 121.4767 | 121.4662 | 121.3764 | -0.30149
2680.5156 | 121.6919 | -121.4127 | 0.073242 | 1.4211e-13 | 0.022664 | 0.016133 | 0.0098956 | -0.023576 | 0.0042113 | 0.25547 | 0.024171 | 0.034604 | -0.096851 | -0.00036547 | 0.00021588 | 0.088037 | 0.0243 | 0.032795 | 0.079598 | 0.1011 | 0.26101 | -0.00811 | 0.069728 | 0.041567 | 0.003172 | 0.029566 | 0.12817 | 0.12222 | -0.2191 | 121.4045 | 0.006356 | 121.5007 | 121.4455 | 0.040905 | 0.027853 | 0.18777 | 121.1936 | -0.043676 | 121.4824 | 121.4158 | 0.22227 | 0.05493 | 0.048974 | 121.4923 | 121.5138 | 121.6737 | 121.437 | -0.081352 | 121.4422 | 121.5408 | 121.5349 | 121.4542 | -0.29234
2682.25 | 121.6599 | -121.431 | 0.036621 | 1.4211e-13 | 0.022878 | 0.015919 | 0.0098956 | -0.023362 | 0.0044249 | 0.24021 | 0.024385 | 0.034604 | -0.09621 | -0.00057907 | 0.00021588 | 0.07888 | 0.0243 | 0.028217 | 0.088755 | 0.1011 | 0.25185 | -0.021847 | 0.074307 | 0.03241 | -0.001407 | 0.034145 | 0.13275 | 0.11764 | -0.2191 | 121.4091 | 0.052134 | 121.5098 | 121.4592 | 0.050064 | 0.064474 | 0.21523 | 121.2119 | -0.002476 | 121.5053 | 121.4296 | 0.21769 | 0.096129 | 0.081016 | 121.5197 | 121.5321 | 121.6828 | 121.4553 | -0.058468 | 121.4651 | 121.5637 | 121.5486 | 121.4634 | -0.25572
2684.0469 | 121.7285 | -121.4035 | 0.041199 | 1.4211e-13 | 0.023092 | 0.016133 | 0.009682 | -0.023362 | 0.0044249 | 0.22495 | 0.024171 | 0.034818 | -0.096851 | -0.00036547 | 2.08e-06 | 0.074302 | 0.019721 | 0.037373 | 0.084176 | 0.1011 | 0.25643 | -0.053899 | 0.069728 | 0.036989 | -0.005985 | 0.038723 | 0.12817 | 0.12679 | -0.22367 | 121.3496 | 0.042977 | 121.4778 | 121.4409 | 0.091272 | 0.059896 | 0.21523 | 121.1798 | -0.002476 | 121.4732 | 121.3975 | 0.21769 | 0.086973 | 0.085595 | 121.4877 | 121.5046 | 121.6599 | 121.4232 | -0.095098 | 121.4422 | 121.5317 | 121.5303 | 121.4405 | -0.26487
2685.7656 | 121.6415 | -121.4767 | 0.086975 | 1.4211e-13 | 0.022878 | 0.015919 | 0.0098956 | -0.023362 | 0.0042113 | 0.24021 | 0.024598 | 0.035031 | -0.096424 | -0.00057907 | 0.00042948 | 0.07888 | 0.0243 | 0.037373 | 0.079598 | 0.096516 | 0.26101 | -0.053899 | 0.078886 | 0.03241 | 0.003172 | 0.034145 | 0.13275 | 0.12679 | -0.2191 | 121.4228 | -0.007377 | 121.5556 | 121.5141 | 0.091272 | 0.009541 | 0.17404 | 121.2577 | -0.05283 | 121.5556 | 121.4799 | 0.22227 | 0.045775 | 0.039819 | 121.5563 | 121.5733 | 121.7378 | 121.501 | -0.14087 | 121.5109 | 121.6095 | 121.6035 | 121.5092 | -0.30607
2687.5469 | 121.7514 | -121.431 | 0.045776 | 1.4211e-13 | 0.023092 | 0.015919 | 0.0098956 | -0.023576 | 0.0046387 | 0.23258 | 0.024598 | 0.034604 | -0.096424 | -0.00057907 | 2.08e-06 | 0.083459 | 0.015142 | 0.032795 | 0.084176 | 0.1011 | 0.25185 | -0.072215 | 0.06515 | 0.03241 | -0.010564 | 0.024988 | 0.12817 | 0.12679 | -0.21452 | 121.3588 | 0.0384 | 121.5144 | 121.4638 | 0.10501 | 0.055319 | 0.20608 | 121.2165 | -0.020788 | 121.4961 | 121.4204 | 0.20395 | 0.082396 | 0.081018 | 121.5151 | 121.5321 | 121.6828 | 121.4461 | -0.11799 | 121.456 | 121.5591 | 121.5578 | 121.4634 | -0.26029
2689.3438 | 120.9869 | -120.9229 | 0.086975 | 1.4211e-13 | 0.023092 | 0.016133 | 0.009682 | -0.023362 | 0.0044249 | 0.24784 | 0.024385 | 0.034818 | -0.09621 | -0.00079267 | 2.08e-06 | 0.07888 | 0.0243 | 0.028217 | 0.084176 | 0.1011 | 0.25643 | -0.058478 | 0.074307 | 0.036989 | -0.001407 | 0.038723 | 0.12359 | 0.12679 | -0.2191 | 120.8644 | -0.002799 | 121.0017 | 120.9511 | 0.086695 | 0.01412 | 0.16946 | 120.7038 | -0.048252 | 120.9972 | 120.9214 | 0.21769 | 0.036618 | 0.039819 | 121.007 | 121.0239 | 121.1793 | 120.9472 | -0.14545 | 120.9616 | 121.0464 | 121.0496 | 120.9598 | -0.30607
2691.0781 | 121.3806 | -121.1151 | 0.068665 | 1.4211e-13 | 0.022878 | 0.016133 | 0.0094682 | -0.023576 | 0.0044249 | 0.24021 | 0.024171 | 0.034604 | -0.096424 | -0.00079267 | 0.00021588 | 0.074302 | 0.015142 | 0.023639 | 0.07502 | 0.096516 | 0.25185 | -0.081373 | 0.074307 | 0.03241 | -0.001407 | 0.034145 | 0.12817 | 0.12222 | -0.21452 | 121.0337 | 0.006355 | 121.1894 | 121.1388 | 0.10501 | 0.027851 | 0.18319 | 120.9006 | -0.03452 | 121.1894 | 121.1137 | 0.21311 | 0.059507 | 0.053551 | 121.1901 | 121.2116 | 121.367 | 121.1303 | -0.15004 | 121.1493 | 121.2433 | 121.2373 | 121.1475 | -0.28318
2692.8438 | 121.3303 | -121.2387 | 0.091553 | 1.4211e-13 | 0.022878 | 0.015919 | 0.0098956 | -0.023576 | 0.0042113 | 0.22495 | 0.023957 | 0.035031 | -0.096424 | -0.00036547 | 2.08e-06 | 0.07888 | 0.019721 | 0.037373 | 0.07502 | 0.1011 | 0.25643 | -0.031005 | 0.06515 | 0.036989 | -0.001407 | 0.038723 | 0.13275 | 0.12679 | -0.2191 | 121.2077 | -0.016533 | 121.3176 | 121.2761 | 0.068378 | 0.009542 | 0.16488 | 121.0196 | -0.05283 | 121.3039 | 121.2373 | 0.21769 | 0.041197 | 0.035241 | 121.3137 | 121.3398 | 121.4951 | 121.2584 | -0.12256 | 121.2774 | 121.3715 | 121.3655 | 121.2757 | -0.31065
2694.5781 | 121.4951 | -121.2067 | 0.041199 | 1.4211e-13 | 0.022878 | 0.015919 | 0.009682 | -0.023362 | 0.0046387 | 0.23258 | 0.023957 | 0.035031 | -0.096424 | -0.00036547 | 0.00042948 | 0.083459 | 0.015142 | 0.032795 | 0.079598 | 0.1011 | 0.25185 | -0.058478 | 0.074307 | 0.036989 | -0.001407 | 0.034145 | 0.12359 | 0.12222 | -0.21452 | 121.1482 | 0.038399 | 121.2901 | 121.2395 | 0.091273 | 0.059896 | 0.21065 | 120.9921 | -0.007054 | 121.281 | 121.2053 | 0.21311 | 0.082394 | 0.081017 | 121.2863 | 121.3078 | 121.4585 | 121.2218 | -0.099677 | 121.2408 | 121.3303 | 121.3289 | 121.2437 | -0.25572
2696.3594 | 121.0602 | -120.932 | 0.073242 | 1.4211e-13 | 0.022878 | 0.016133 | 0.0098956 | -0.023362 | 0.0044249 | 0.22495 | 0.024171 | 0.034177 | -0.096424 | -0.00036547 | 2.08e-06 | 0.07888 | 0.028878 | 0.037373 | 0.07502 | 0.10567 | 0.25185 | 0.014784 | 0.078886 | 0.036989 | -0.001407 | 0.038723 | 0.12817 | 0.12222 | -0.2191 | 120.9468 | 0.001778 | 121.0109 | 120.9694 | 0.022589 | 0.032432 | 0.17861 | 120.7129 | -0.034519 | 121.0109 | 120.9306 | 0.21769 | 0.05493 | 0.048974 | 121.007 | 121.0377 | 121.1839 | 120.9609 | -0.058458 | 120.9707 | 121.0602 | 121.0542 | 120.969 | -0.29234
2698.0781 | 121.2021 | -121.1472 | 0.10071 | 1.4211e-13 | 0.022664 | 0.015492 | 0.010323 | -0.023576 | 0.0044249 | 0.24021 | 0.024171 | 0.034604 | -0.096424 | -0.00036547 | 0.00042948 | 0.07888 | 0.0243 | 0.037373 | 0.07502 | 0.10567 | 0.26101 | 0.010206 | 0.06515 | 0.03241 | -0.001407 | 0.043302 | 0.13275 | 0.12679 | -0.20994 | 121.1574 | -0.025688 | 121.226 | 121.1845 | 0.027167 | 0.004966 | 0.1603 | 120.9372 | -0.057406 | 121.2123 | 121.1457 | 0.20853 | 0.032042 | 0.026086 | 121.2222 | 121.2528 | 121.4082 | 121.1715 | -0.090502 | 121.1905 | 121.2799 | 121.2739 | 121.1796 | -0.31065
2699.8594 | 121.3028 | -121.1838 | 0.082397 | 1.4211e-13 | 0.022664 | 0.015919 | 0.009682 | -0.023789 | 0.0044249 | 0.23258 | 0.024171 | 0.034177 | -0.09621 | -0.00036547 | 0.00021588 | 0.07888 | 0.028878 | 0.032795 | 0.079598 | 0.10567 | 0.25643 | -0.067636 | 0.069728 | 0.041567 | 0.003172 | 0.024988 | 0.12817 | 0.12679 | -0.20994 | 121.1161 | -0.002799 | 121.2627 | 121.2166 | 0.10043 | 0.023277 | 0.17403 | 120.9738 | -0.057409 | 121.2535 | 121.1869 | 0.21311 | 0.045775 | 0.044397 | 121.2634 | 121.2895 | 121.4402 | 121.2127 | -0.15003 | 121.2088 | 121.3119 | 121.3106 | 121.2253 | -0.29233
2701.6562 | 121.4172 | -121.1792 | 0.050354 | 1.4211e-13 | 0.022664 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.23258 | 0.024385 | 0.034604 | -0.09621 | -0.00079267 | 0.00021588 | 0.07888 | 0.0243 | 0.041952 | 0.079598 | 0.10567 | 0.25643 | -0.049321 | 0.069728 | 0.027831 | -0.001407 | 0.038723 | 0.13733 | 0.12222 | -0.21452 | 121.1299 | 0.029244 | 121.2581 | 121.2212 | 0.091273 | 0.05532 | 0.20608 | 120.9647 | -0.011631 | 121.2489 | 121.1778 | 0.21311 | 0.086975 | 0.071862 | 121.2588 | 121.2849 | 121.4356 | 121.2035 | -0.099675 | 121.2179 | 121.3165 | 121.3014 | 121.207 | -0.26487
2703.4375 | 120.9961 | -120.9 | 0.064087 | 1.4211e-13 | 0.023092 | 0.015919 | 0.009682 | -0.023362 | 0.0044249 | 0.22495 | 0.024598 | 0.035245 | -0.09621 | -0.00079267 | 0.00021588 | 0.083459 | 0.019721 | 0.041952 | 0.079598 | 0.1011 | 0.25185 | -0.017268 | 0.074307 | 0.036989 | -0.001407 | 0.043302 | 0.13733 | 0.12679 | -0.20994 | 120.8827 | 0.015511 | 120.9834 | 120.9419 | 0.05922 | 0.037008 | 0.18777 | 120.69 | -0.020785 | 120.9743 | 120.8986 | 0.20853 | 0.073242 | 0.062707 | 120.9796 | 121.0011 | 121.1518 | 120.9197 | -0.081355 | 120.9433 | 121.0373 | 121.0268 | 120.937 | -0.27402
2705.2344 | 121.1929 | -120.9778 | 0.068665 | 1.4211e-13 | 0.022878 | 0.015919 | 0.010109 | -0.023576 | 0.0046387 | 0.22495 | 0.024385 | 0.034818 | -0.096424 | -0.00079267 | 0.00064308 | 0.069723 | 0.019721 | 0.037373 | 0.079598 | 0.10567 | 0.25643 | -0.053899 | 0.074307 | 0.036989 | -0.005985 | 0.034145 | 0.12359 | 0.12222 | -0.20536 | 120.9239 | 0.010933 | 121.0475 | 121.0152 | 0.091272 | 0.037009 | 0.18777 | 120.7724 | -0.03452 | 121.0521 | 120.9718 | 0.19937 | 0.054928 | 0.053551 | 121.0574 | 121.0835 | 121.2342 | 120.9975 | -0.12256 | 121.0119 | 121.1014 | 121.1 | 121.0148 | -0.27402
2707.0312 | 121.2067 | -121.0968 | 0.09613 | 1.4211e-13 | 0.022878 | 0.015919 | 0.009682 | -0.023789 | 0.0044249 | 0.24021 | 0.024385 | 0.034818 | -0.096637 | -0.00057907 | 0.00021588 | 0.074302 | 0.019721 | 0.041952 | 0.079598 | 0.1011 | 0.25185 | -0.044742 | 0.069728 | 0.041567 | 0.003172 | 0.029566 | 0.12817 | 0.12679 | -0.21452 | 121.0521 | -0.016532 | 121.1711 | 121.1388 | 0.086694 | 0.004965 | 0.15572 | 120.8823 | -0.066564 | 121.1665 | 121.1 | 0.21769 | 0.032042 | 0.030664 | 121.1764 | 121.1979 | 121.3487 | 121.1165 | -0.14087 | 121.1264 | 121.225 | 121.2236 | 121.1384 | -0.31065
2708.75 | 121.3394 | -121.0648 | 0.059509 | 1.4211e-13 | 0.022878 | 0.015919 | 0.009682 | -0.023576 | 0.0042113 | 0.24021 | 0.024385 | 0.034818 | -0.096637 | -0.00057907 | 0.00042948 | 0.074302 | 0.019721 | 0.032795 | 0.079598 | 0.096516 | 0.25643 | -0.021847 | 0.069728 | 0.036989 | -0.001407 | 0.034145 | 0.13275 | 0.12679 | -0.20994 | 121.0429 | 0.020089 | 121.1391 | 121.0976 | 0.054642 | 0.037007 | 0.19692 | 120.8548 | -0.025364 | 121.1345 | 121.0634 | 0.20853 | 0.073241 | 0.067285 | 121.1444 | 121.1613 | 121.3212 | 121.0845 | -0.081356 | 121.0989 | 121.1975 | 121.1916 | 121.1017 | -0.26945
2710.5312 | 121.4264 | -121.1014 | 0.041199 | 1.4211e-13 | 0.022664 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.024598 | 0.034818 | -0.096424 | -0.00036547 | 0.00042948 | 0.07888 | 0.0243 | 0.032795 | 0.079598 | 0.1011 | 0.24727 | -0.076794 | 0.078886 | 0.03241 | -0.005985 | 0.029566 | 0.14191 | 0.12679 | -0.20536 | 121.0246 | 0.038399 | 121.1803 | 121.1342 | 0.10959 | 0.059896 | 0.20608 | 120.896 | -0.011633 | 121.1803 | 121.0954 | 0.19937 | 0.10071 | 0.085595 | 121.181 | 121.2025 | 121.3487 | 121.1257 | -0.11799 | 121.1309 | 121.2433 | 121.2282 | 121.1338 | -0.24656
2712.25 | 120.726 | -120.4971 | 0.11902 | 1.4211e-13 | 0.023092 | 0.016133 | 0.0098956 | -0.023576 | 0.0039977 | 0.25547 | 0.024385 | 0.034818 | -0.096424 | -0.00079267 | 0.00064308 | 0.07888 | 0.019721 | 0.04653 | 0.084176 | 0.1011 | 0.26101 | -0.063057 | 0.069728 | 0.036989 | -0.001407 | 0.034145 | 0.12817 | 0.13137 | -0.20536 | 120.4341 | -0.034843 | 120.576 | 120.5437 | 0.10959 | -0.017924 | 0.14199 | 120.2918 | -0.084874 | 120.5669 | 120.4957 | 0.20395 | 0.009153 | 0.012354 | 120.5813 | 120.5982 | 120.7581 | 120.5169 | -0.18208 | 120.5313 | 120.6253 | 120.6285 | 120.5341 | -0.32438
2714.0312 | 120.9824 | -120.7718 | 0.082397 | 1.4211e-13 | 0.022878 | 0.015705 | 0.009682 | -0.023576 | 0.0042113 | 0.23258 | 0.024385 | 0.034818 | -0.096637 | -0.00036547 | 0.00021588 | 0.083459 | 0.0243 | 0.037373 | 0.079598 | 0.1011 | 0.25185 | -0.031005 | 0.074307 | 0.041567 | -0.001407 | 0.029566 | 0.14191 | 0.12679 | -0.20994 | 120.7408 | -0.002799 | 120.8552 | 120.8092 | 0.068378 | 0.018698 | 0.16946 | 120.5619 | -0.052831 | 120.8461 | 120.7704 | 0.20853 | 0.05951 | 0.044397 | 120.8514 | 120.8729 | 121.0236 | 120.7961 | -0.1134 | 120.8014 | 120.9137 | 120.8986 | 120.8134 | -0.29233
2715.8281 | 121.1105 | -120.6665 | 0.1831 | 1.4211e-13 | 0.023092 | 0.016133 | 0.0098956 | -0.023362 | 0.0044249 | 0.24021 | 0.024385 | 0.034818 | -0.096424 | -0.00079267 | 0.00042948 | 0.07888 | 0.019721 | 0.041952 | 0.084176 | 0.10567 | 0.25185 | -0.063057 | 0.06515 | 0.023253 | -0.001407 | 0.024988 | 0.12359 | 0.12222 | -0.2191 | 120.6034 | -0.098929 | 120.7454 | 120.7085 | 0.10501 | -0.077431 | 0.068747 | 120.4474 | -0.15812 | 120.7317 | 120.6651 | 0.21769 | -0.059512 | -0.060889 | 120.7507 | 120.7722 | 120.9184 | 120.6862 | -0.24616 | 120.6915 | 120.7901 | 120.7887 | 120.6898 | -0.4022
2717.5938 | 121.1243 | -120.7306 | 0.15564 | 1.4211e-13 | 0.023305 | 0.015919 | 0.0098956 | -0.023576 | 0.0044249 | 0.23258 | 0.024385 | 0.034818 | -0.096637 | -0.00079267 | 0.00064308 | 0.083459 | 0.033457 | 0.032795 | 0.07502 | 0.10567 | 0.25185 | -0.044742 | 0.06515 | 0.036989 | -0.015143 | 0.029566 | 0.11901 | 0.12222 | -0.20994 | 120.6858 | -0.08062 | 120.8141 | 120.7634 | 0.077537 | -0.049966 | 0.096212 | 120.5207 | -0.12607 | 120.7957 | 120.7154 | 0.19479 | -0.036626 | -0.033424 | 120.8056 | 120.8363 | 120.9824 | 120.764 | -0.20038 | 120.7602 | 120.8496 | 120.8528 | 120.7676 | -0.36558
2719.3125 | 121.1151 | -120.813 | 0.16022 | 1.4211e-13 | 0.023305 | 0.015919 | 0.010109 | -0.023576 | 0.0044249 | 0.23258 | 0.024598 | 0.035031 | -0.096637 | -0.00057907 | 0.00042948 | 0.074302 | 0.015142 | 0.023639 | 0.079598 | 0.1011 | 0.26559 | -0.058478 | 0.069728 | 0.027831 | -0.005985 | 0.029566 | 0.11901 | 0.11764 | -0.21452 | 120.7545 | -0.080619 | 120.8873 | 120.8366 | 0.082117 | -0.059122 | 0.10537 | 120.5985 | -0.13065 | 120.8827 | 120.807 | 0.20853 | -0.041203 | -0.04258 | 120.8926 | 120.9141 | 121.0786 | 120.8281 | -0.2187 | 120.8426 | 120.932 | 120.9306 | 120.8408 | -0.37473
2721.0469 | 121.1792 | -120.9503 | 0.064087 | 1.4211e-13 | 0.023092 | 0.015919 | 0.0098956 | -0.022935 | 0.0046387 | 0.24021 | 0.024171 | 0.03439 | -0.09621 | -0.00079267 | 0.00042948 | 0.07888 | 0.0243 | 0.032795 | 0.079598 | 0.096516 | 0.25185 | -0.058478 | 0.069728 | 0.03241 | -0.001407 | 0.029566 | 0.12817 | 0.13137 | -0.20994 | 120.8918 | 0.015511 | 121.0292 | 120.9831 | 0.091273 | 0.032429 | 0.18777 | 120.7404 | -0.034521 | 121.02 | 120.9489 | 0.20853 | 0.064085 | 0.067286 | 121.0299 | 121.0468 | 121.2022 | 120.9746 | -0.12257 | 120.9799 | 121.0785 | 121.0817 | 120.9827 | -0.27402
2722.7656 | 121.2067 | -120.9641 | 0.086975 | 1.4211e-13 | 0.023092 | 0.015919 | 0.0098956 | -0.023576 | 0.0046387 | 0.23258 | 0.024598 | 0.034818 | -0.096637 | -0.00057907 | 0.00042948 | 0.074302 | 0.019721 | 0.032795 | 0.084176 | 0.1011 | 0.25185 | -0.012689 | 0.074307 | 0.03241 | -0.005985 | 0.029566 | 0.12817 | 0.12222 | -0.20536 | 120.9514 | -0.002799 | 121.0384 | 120.9968 | 0.045484 | 0.01412 | 0.16488 | 120.7587 | -0.057409 | 121.0384 | 120.9581 | 0.19937 | 0.041197 | 0.035241 | 121.0482 | 121.0651 | 121.2159 | 120.9838 | -0.099664 | 120.9936 | 121.0922 | 121.0863 | 120.9965 | -0.29233
2724.4688 | 121.1426 | -120.9457 | 0.11444 | 1.4211e-13 | 0.023092 | 0.016133 | 0.010109 | -0.023362 | 0.0046387 | 0.23258 | 0.024385 | 0.034818 | -0.096637 | -0.00079267 | 0.00042948 | 0.088037 | 0.019721 | 0.041952 | 0.079598 | 0.10567 | 0.25643 | -0.044742 | 0.069728 | 0.03241 | -0.010564 | 0.024988 | 0.12359 | 0.12679 | -0.21452 | 120.901 | -0.034843 | 121.0338 | 120.9877 | 0.086694 | -0.008767 | 0.14199 | 120.7312 | -0.089453 | 121.0155 | 120.9352 | 0.20395 | 0.009152 | 0.012353 | 121.0253 | 121.0514 | 121.2022 | 120.9655 | -0.15918 | 120.9707 | 121.0693 | 121.0725 | 120.9781 | -0.32896
2726.1719 | 121.2845 | -120.7993 | 0.22888 | 1.4211e-13 | 0.023092 | 0.016346 | 0.009682 | -0.023148 | 0.0046387 | 0.23258 | 0.024385 | 0.034604 | -0.096424 | -0.00057907 | 0.00042948 | 0.083459 | 0.0243 | 0.037373 | 0.079598 | 0.1011 | 0.25185 | -0.063057 | 0.06515 | 0.027831 | -0.005985 | 0.034145 | 0.12817 | 0.11764 | -0.20994 | 120.7362 | -0.14928 | 120.8827 | 120.8366 | 0.10043 | -0.12779 | 0.02297 | 120.5893 | -0.19474 | 120.8644 | 120.7933 | 0.20395 | -0.10071 | -0.11124 | 120.8789 | 120.9004 | 121.0511 | 120.8236 | -0.29194 | 120.8334 | 120.9274 | 120.9169 | 120.8271 | -0.43882
2727.875 | 121.0098 | -120.4697 | 0.48523 | 1.4211e-13 | 0.023092 | 0.015705 | 0.0094682 | -0.023148 | 0.0042113 | 0.24021 | 0.024171 | 0.034818 | -0.096424 | -0.00057907 | 0.00042948 | 0.083459 | 0.019721 | 0.041952 | 0.088755 | 0.087359 | 0.25643 | -0.058478 | 0.06515 | 0.03241 | -0.015143 | 0.024988 | 0.11444 | 0.12222 | -0.2191 | 120.4112 | -0.39647 | 120.5531 | 120.5116 | 0.10043 | -0.39787 | -0.2288 | 120.2506 | -0.46024 | 120.5348 | 120.4545 | 0.20395 | -0.37079 | -0.36301 | 120.5584 | 120.557 | 120.7261 | 120.4894 | -0.54371 | 120.4947 | 120.5841 | 120.5919 | 120.5021 | -0.70432
2729.6094 | 121.0556 | -120.3735 | 0.50812 | 1.4211e-13 | 0.023305 | 0.015919 | 0.0098956 | -0.023576 | 0.0042113 | 0.23258 | 0.023957 | 0.034604 | -0.09621 | -0.00036547 | 2.08e-06 | 0.07888 | 0.0243 | 0.041952 | 0.079598 | 0.10567 | 0.25643 | -0.049321 | 0.046835 | 0.014095 | -0.028879 | 0.011252 | 0.10986 | 0.099323 | -0.22825 | 120.3242 | -0.42852 | 120.4524 | 120.4155 | 0.091273 | -0.40244 | -0.25169 | 120.1453 | -0.49687 | 120.4204 | 120.3447 | 0.19937 | -0.39826 | -0.40879 | 120.4531 | 120.4792 | 120.63 | 120.3978 | -0.55744 | 120.3848 | 120.4834 | 120.4729 | 120.3876 | -0.73637
2731.3438 | 121.2067 | -120.8954 | 0.17853 | 1.4211e-13 | 0.023092 | 0.015919 | 0.009682 | -0.023576 | 0.0044249 | 0.24021 | 0.024171 | 0.034604 | -0.095996 | -0.00079267 | 0.00064308 | 0.07888 | 0.028878 | 0.037373 | 0.07502 | 0.096516 | 0.26559 | -0.053899 | 0.06515 | 0.023253 | -0.005985 | 0.020409 | 0.11901 | 0.11306 | -0.20994 | 120.8415 | -0.10351 | 120.9743 | 120.9328 | 0.091272 | -0.082012 | 0.08706 | 120.6854 | -0.15812 | 120.9605 | 120.8894 | 0.20395 | -0.059514 | -0.065469 | 120.9704 | 120.9919 | 121.161 | 120.9243 | -0.23243 | 120.9158 | 121.0144 | 121.0084 | 120.9186 | -0.38847
2733.0625 | 121.312 | -121.0556 | 0.059509 | 1.4211e-13 | 0.022878 | 0.016346 | 0.0098956 | -0.023148 | 0.0046387 | 0.22495 | 0.024171 | 0.034604 | -0.096424 | -0.00036547 | 0.00021588 | 0.07888 | 0.015142 | 0.037373 | 0.079598 | 0.096516 | 0.26101 | 0.010206 | 0.06515 | 0.027831 | -0.005985 | 0.029566 | 0.12359 | 0.12222 | -0.20994 | 121.0658 | 0.020089 | 121.1345 | 121.093 | 0.027167 | 0.037007 | 0.2015 | 120.8457 | -0.029943 | 121.1208 | 121.0496 | 0.20395 | 0.064084 | 0.062707 | 121.1352 | 121.1521 | 121.3166 | 121.0707 | -0.049303 | 121.0852 | 121.1792 | 121.1778 | 121.0834 | -0.26945
2734.7812 | 121.3898 | -121.0831 | 0.059509 | 1.4211e-13 | 0.023092 | 0.015919 | 0.0094682 | -0.023789 | 0.0044249 | 0.24784 | 0.024171 | 0.034818 | -0.096424 | -0.00079267 | 0.00064308 | 0.07888 | 0.019721 | 0.037373 | 0.07502 | 0.10567 | 0.25643 | -0.026426 | 0.06515 | 0.03241 | -0.010564 | 0.034145 | 0.12817 | 0.12679 | -0.20536 | 121.0566 | 0.015511 | 121.1619 | 121.1204 | 0.063799 | 0.046165 | 0.19692 | 120.8777 | -0.025364 | 121.1482 | 121.0725 | 0.19479 | 0.068663 | 0.067285 | 121.1581 | 121.1887 | 121.3395 | 121.1028 | -0.085935 | 121.1172 | 121.2112 | 121.2099 | 121.1155 | -0.26487
2736.5156 | 121.344 | -121.106 | 0.068665 | 1.4211e-13 | 0.023092 | 0.016346 | 0.010109 | -0.023362 | 0.0044249 | 0.24784 | 0.024171 | 0.03439 | -0.096637 | -0.00079267 | 0.00021588 | 0.074302 | 0.0243 | 0.037373 | 0.084176 | 0.1011 | 0.26101 | -0.035584 | 0.06515 | 0.03241 | -0.001407 | 0.038723 | 0.12359 | 0.12222 | -0.20536 | 121.0704 | 0.015511 | 121.1803 | 121.1433 | 0.072957 | 0.03243 | 0.19235 | 120.9006 | -0.029942 | 121.1711 | 121.1046 | 0.20395 | 0.054928 | 0.053551 | 121.1901 | 121.2071 | 121.367 | 121.1303 | -0.10425 | 121.1447 | 121.2296 | 121.2282 | 121.1384 | -0.27402
2738.25 | 121.3623 | -121.1334 | 0.073242 | 1.4211e-13 | 0.022878 | 0.015919 | 0.009682 | -0.023576 | 0.0044249 | 0.24021 | 0.024385 | 0.03439 | -0.097065 | -0.00079267 | 0.00021588 | 0.088037 | 0.015142 | 0.032795 | 0.070441 | 0.10567 | 0.25185 | -0.049321 | 0.069728 | 0.018674 | -0.005985 | 0.024988 | 0.12817 | 0.12222 | -0.20536 | 121.0841 | -0.002801 | 121.2215 | 121.1662 | 0.082116 | 0.032432 | 0.17861 | 120.9281 | -0.048254 | 121.2032 | 121.1274 | 0.19937 | 0.05493 | 0.048974 | 121.2039 | 121.2391 | 121.3853 | 121.1486 | -0.12256 | 121.1584 | 121.2616 | 121.2556 | 121.1521 | -0.2786
2740 | 121.2799 | -121.1792 | 0.09613 | 1.4211e-13 | 0.022878 | 0.015919 | 0.009682 | -0.023148 | 0.0039977 | 0.24021 | 0.024171 | 0.034604 | -0.096637 | -0.00079267 | 0.00042948 | 0.083459 | 0.019721 | 0.041952 | 0.084176 | 0.10567 | 0.25185 | -0.044742 | 0.06515 | 0.036989 | -0.001407 | 0.034145 | 0.12817 | 0.11764 | -0.20994 | 121.1345 | -0.011954 | 121.2627 | 121.2212 | 0.086694 | 0.009544 | 0.15572 | 120.9693 | -0.061985 | 121.2443 | 121.1778 | 0.20853 | 0.032042 | 0.021507 | 121.2634 | 121.2849 | 121.4311 | 121.1989 | -0.14087 | 121.2133 | 121.3074 | 121.2968 | 121.2162 | -0.30607
2741.6875 | 121.3211 | -121.1746 | 0.09613 | 1.4211e-13 | 0.022878 | 0.016133 | 0.0098956 | -0.023576 | 0.0044249 | 0.22495 | 0.023957 | 0.034604 | -0.096851 | -0.00057907 | 0.00042948 | 0.074302 | 0.015142 | 0.032795 | 0.084176 | 0.10567 | 0.26101 | -0.053899 | 0.069728 | 0.027831 | -0.001407 | 0.024988 | 0.12359 | 0.12222 | -0.20536 | 121.1207 | -0.011954 | 121.2489 | 121.2074 | 0.086694 | 0.009544 | 0.16488 | 120.9693 | -0.071142 | 121.2443 | 121.1732 | 0.20395 | 0.027463 | 0.026086 | 121.2588 | 121.2803 | 121.4356 | 121.1898 | -0.15003 | 121.1996 | 121.2982 | 121.2968 | 121.2025 | -0.30149
2743.3906 | 121.3165 | -121.2021 | 0.09613 | 1.4211e-13 | 0.023092 | 0.016133 | 0.009682 | -0.023789 | 0.0044249 | 0.24021 | 0.024385 | 0.034604 | -0.096424 | -0.00057907 | 0.00021588 | 0.07888 | 0.0243 | 0.041952 | 0.07502 | 0.096516 | 0.25643 | -0.040163 | 0.06515 | 0.023253 | -0.001407 | 0.034145 | 0.13275 | 0.12222 | -0.20536 | 121.1619 | -0.02111 | 121.281 | 121.244 | 0.082115 | 0.000386 | 0.1603 | 120.9967 | -0.061985 | 121.2672 | 121.2007 | 0.20395 | 0.03662 | 0.026086 | 121.2771 | 121.2986 | 121.4585 | 121.2264 | -0.13629 | 121.2362 | 121.3348 | 121.3243 | 121.2253 | -0.30149
2745.0938 | 121.3898 | -121.2021 | 0.10071 | 1.4211e-13 | 0.023519 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.25547 | 0.023957 | 0.035031 | -0.096424 | -0.0010065 | 2.08e-06 | 0.07888 | 0.0243 | 0.037373 | 0.084176 | 0.10567 | 0.26101 | -0.035584 | 0.069728 | 0.027831 | -0.005985 | 0.034145 | 0.12359 | 0.11306 | -0.20536 | 121.1665 | -0.016532 | 121.281 | 121.2395 | 0.072957 | 0.004966 | 0.1603 | 120.9967 | -0.066563 | 121.2718 | 121.1961 | 0.19937 | 0.022885 | 0.012351 | 121.2863 | 121.3078 | 121.4631 | 121.2264 | -0.13629 | 121.2362 | 121.3257 | 121.3151 | 121.2299 | -0.30607
2746.8125 | 121.4172 | -121.2387 | 0.068665 | 1.4211e-13 | 0.023305 | 0.016133 | 0.009682 | -0.023789 | 0.0046387 | 0.22495 | 0.024171 | 0.034818 | -0.096637 | -0.00079267 | 0.00042948 | 0.083459 | 0.0243 | 0.028217 | 0.07502 | 0.096516 | 0.25643 | -0.031005 | 0.069728 | 0.03241 | -0.010564 | 0.034145 | 0.12359 | 0.12222 | -0.20078 | 121.2077 | 0.006355 | 121.3222 | 121.2669 | 0.059222 | 0.027851 | 0.18777 | 121.0379 | -0.03452 | 121.3084 | 121.2281 | 0.19022 | 0.054928 | 0.053551 | 121.3137 | 121.3352 | 121.4951 | 121.263 | -0.09967 | 121.2729 | 121.3623 | 121.3609 | 121.2711 | -0.26944
2748.5156 | 121.4127 | -121.257 | 0.073242 | 1.4211e-13 | 0.023519 | 0.016133 | 0.009682 | -0.023362 | 0.0044249 | 0.24021 | 0.024171 | 0.034818 | -0.09621 | -0.00057907 | 0.00042948 | 0.07888 | 0.019721 | 0.032795 | 0.079598 | 0.1011 | 0.25185 | -0.035584 | 0.069728 | 0.03241 | -0.005985 | 0.038723 | 0.12817 | 0.12222 | -0.21452 | 121.2214 | 0.006356 | 121.3359 | 121.2898 | 0.068379 | 0.027853 | 0.17861 | 121.0425 | -0.034519 | 121.3267 | 121.251 | 0.20853 | 0.05493 | 0.048974 | 121.3366 | 121.3581 | 121.5089 | 121.2767 | -0.10883 | 121.2957 | 121.3852 | 121.3792 | 121.2894 | -0.28776
2750.2344 | 121.4218 | -121.2296 | 0.073242 | 1.4211e-13 | 0.023092 | 0.016346 | 0.0094682 | -0.023576 | 0.0046387 | 0.23258 | 0.024812 | 0.035031 | -0.096637 | -0.0012201 | 0.00042948 | 0.083459 | 0.028878 | 0.032795 | 0.084176 | 0.096516 | 0.25643 | -0.026426 | 0.069728 | 0.027831 | -0.010564 | 0.034145 | 0.12817 | 0.11764 | -0.20536 | 121.2031 | 0.010934 | 121.313 | 121.2623 | 0.059221 | 0.023274 | 0.18319 | 121.0242 | -0.039097 | 121.2993 | 121.219 | 0.19479 | 0.05493 | 0.044395 | 121.3137 | 121.3261 | 121.486 | 121.2584 | -0.099668 | 121.2637 | 121.3577 | 121.3472 | 121.2574 | -0.2786
2751.9844 | 121.4859 | -121.2341 | 0.059509 | 1.4211e-13 | 0.022878 | 0.016133 | 0.0094682 | -0.023362 | 0.0044249 | 0.24021 | 0.024171 | 0.03439 | -0.096637 | -0.00057907 | 0.00042948 | 0.07888 | 0.019721 | 0.037373 | 0.079598 | 0.096516 | 0.25643 | -0.044742 | 0.06515 | 0.036989 | -0.005985 | 0.029566 | 0.13275 | 0.11764 | -0.20536 | 121.1894 | 0.020089 | 121.313 | 121.2715 | 0.082115 | 0.037007 | 0.19692 | 121.0288 | -0.029943 | 121.2993 | 121.2281 | 0.19937 | 0.073241 | 0.058128 | 121.3137 | 121.3306 | 121.4906 | 121.2539 | -0.10425 | 121.2637 | 121.3669 | 121.3518 | 121.2711 | -0.26487
2753.6875 | 121.4539 | -121.2708 | 0.09613 | 1.4211e-13 | 0.023092 | 0.015919 | 0.0094682 | -0.023576 | 0.0042113 | 0.24021 | 0.024385 | 0.034604 | -0.096424 | -0.0010065 | 0.00042948 | 0.083459 | 0.015142 | 0.032795 | 0.084176 | 0.096516 | 0.24269 | 0.001048 | 0.06515 | 0.027831 | -0.005985 | 0.034145 | 0.12817 | 0.12679 | -0.20078 | 121.2718 | -0.011954 | 121.3542 | 121.3035 | 0.031747 | 0.000386 | 0.14657 | 121.07 | -0.061985 | 121.3359 | 121.2648 | 0.19479 | 0.032042 | 0.030664 | 121.3549 | 121.3673 | 121.5134 | 121.2859 | -0.095082 | 121.3049 | 121.3989 | 121.3975 | 121.2986 | -0.29691
2755.3906 | 121.4584 | -121.3028 | 0.086975 | 1.4211e-13 | 0.022878 | 0.015919 | 0.0098956 | -0.023362 | 0.0044249 | 0.22495 | 0.024171 | 0.034818 | -0.09621 | -0.00057907 | 0.00064308 | 0.083459 | 0.019721 | 0.037373 | 0.088755 | 0.10567 | 0.25185 | -0.017268 | 0.069728 | 0.03241 | -0.005985 | 0.029566 | 0.13275 | 0.11306 | -0.20536 | 121.2855 | 0.00178 | 121.3863 | 121.3402 | 0.054641 | 0.018699 | 0.16488 | 121.0974 | -0.057409 | 121.3725 | 121.2968 | 0.19937 | 0.045775 | 0.026084 | 121.3916 | 121.4085 | 121.5546 | 121.3225 | -0.10424 | 121.3324 | 121.4355 | 121.4159 | 121.3352 | -0.29233
2757.125 | 121.4584 | -121.3211 | 0.086975 | 1.4211e-13 | 0.023519 | 0.016346 | 0.010109 | -0.023148 | 0.0046387 | 0.22495 | 0.024171 | 0.035031 | -0.096851 | -0.00057907 | 0.00042948 | 0.07888 | 0.019721 | 0.037373 | 0.084176 | 0.1011 | 0.26559 | -0.003531 | 0.069728 | 0.036989 | -0.001407 | 0.034145 | 0.13275 | 0.11764 | -0.20078 | 121.3176 | -0.002799 | 121.4 | 121.3585 | 0.040904 | 0.01412 | 0.17861 | 121.1203 | -0.05283 | 121.3908 | 121.3197 | 0.19937 | 0.045775 | 0.030662 | 121.4053 | 121.4222 | 121.5867 | 121.3408 | -0.090506 | 121.3553 | 121.4539 | 121.4387 | 121.3581 | -0.28775
2758.875 | 121.4401 | -121.3577 | 0.082397 | 1.4211e-13 | 0.023519 | 0.016133 | 0.0098956 | -0.023576 | 0.0044249 | 0.23258 | 0.024385 | 0.035031 | -0.096424 | -0.00079267 | 0.00042948 | 0.07888 | 0.015142 | 0.028217 | 0.07502 | 0.10567 | 0.24727 | -0.017268 | 0.06515 | 0.027831 | -0.010564 | 0.024988 | 0.12817 | 0.12222 | -0.20078 | 121.3405 | -0.007377 | 121.4366 | 121.3859 | 0.045485 | 0.023277 | 0.16488 | 121.1569 | -0.057409 | 121.4229 | 121.3472 | 0.19022 | 0.045775 | 0.039819 | 121.4327 | 121.4634 | 121.605 | 121.3729 | -0.099665 | 121.3827 | 121.4859 | 121.4799 | 121.3856 | -0.28318
2760.5781 | 121.5271 | -121.3394 | 0.064087 | 1.4211e-13 | 0.023305 | 0.015705 | 0.0098956 | -0.023576 | 0.0046387 | 0.23258 | 0.023957 | 0.035245 | -0.096637 | -0.00079267 | 0.00042948 | 0.083459 | 0.019721 | 0.028217 | 0.088755 | 0.091937 | 0.25643 | -0.031005 | 0.060571 | 0.023253 | -0.001407 | 0.024988 | 0.12359 | 0.11764 | -0.1962 | 121.3084 | 0.024668 | 121.4229 | 121.3676 | 0.059222 | 0.02785 | 0.19234 | 121.1432 | -0.039099 | 121.4 | 121.338 | 0.19479 | 0.059506 | 0.05355 | 121.4282 | 121.4314 | 121.5958 | 121.3591 | -0.095092 | 121.3644 | 121.463 | 121.4571 | 121.3627 | -0.26029
2762.2812 | 121.55 | -121.3394 | 0.068665 | 1.4211e-13 | 0.023305 | 0.016133 | 0.0098956 | -0.023362 | 0.0048523 | 0.23258 | 0.024385 | 0.034604 | -0.096637 | -0.00079267 | 0.00042948 | 0.083459 | 0.019721 | 0.032795 | 0.079598 | 0.1011 | 0.25643 | -0.049321 | 0.074307 | 0.03241 | -0.010564 | 0.029566 | 0.12817 | 0.11306 | -0.20994 | 121.2901 | 0.010933 | 121.4229 | 121.3722 | 0.082116 | 0.03243 | 0.18777 | 121.1295 | -0.039099 | 121.4137 | 121.3289 | 0.19937 | 0.059507 | 0.044394 | 121.419 | 121.4405 | 121.5958 | 121.3591 | -0.11799 | 121.369 | 121.4676 | 121.4525 | 121.3718 | -0.2786
2764.0156 | 121.5729 | -121.3303 | 0.07782 | 1.4211e-13 | 0.023092 | 0.016133 | 0.0098956 | -0.023576 | 0.0042113 | 0.23258 | 0.024385 | 0.03439 | -0.096851 | -0.00079267 | 0.00064308 | 0.074302 | 0.015142 | 0.037373 | 0.079598 | 0.096516 | 0.26101 | -0.053899 | 0.060571 | 0.03241 | -0.010564 | 0.024988 | 0.11901 | 0.11306 | -0.20536 | 121.2764 | 0.001778 | 121.4046 | 121.3676 | 0.091272 | 0.018696 | 0.18319 | 121.1249 | -0.052832 | 121.3908 | 121.3197 | 0.19479 | 0.041194 | 0.035239 | 121.4099 | 121.4268 | 121.5913 | 121.3454 | -0.13172 | 121.3552 | 121.4493 | 121.4433 | 121.3627 | -0.28318
2765.75 | 121.6324 | -121.3486 | 0.045776 | 1.4211e-13 | 0.023519 | 0.015919 | 0.0098956 | -0.023362 | 0.0042113 | 0.24021 | 0.024171 | 0.034818 | -0.096424 | -0.0010065 | 0.00085668 | 0.07888 | 0.019721 | 0.037373 | 0.079598 | 0.1011 | 0.25643 | -0.021847 | 0.06515 | 0.027831 | -0.001407 | 0.034145 | 0.12817 | 0.11764 | -0.20078 | 121.3267 | 0.033822 | 121.4275 | 121.3859 | 0.05922 | 0.055319 | 0.21066 | 121.1478 | -0.011631 | 121.4137 | 121.3472 | 0.19937 | 0.082396 | 0.071861 | 121.4282 | 121.4497 | 121.605 | 121.3683 | -0.067623 | 121.3827 | 121.4767 | 121.4662 | 121.3764 | -0.24656
2767.4531 | 121.5317 | -121.3898 | 0.073242 | 1.4211e-13 | 0.023092 | 0.015919 | 0.009682 | -0.023362 | 0.0042113 | 0.24021 | 0.024171 | 0.035031 | -0.096424 | -0.00079267 | 0.00021588 | 0.083459 | 0.019721 | 0.028217 | 0.084176 | 0.1011 | 0.25185 | -0.053899 | 0.069728 | 0.023253 | -0.001407 | 0.024988 | 0.12359 | 0.11764 | -0.1962 | 121.3359 | 0.010934 | 121.4732 | 121.418 | 0.082116 | 0.027853 | 0.17861 | 121.1936 | -0.048254 | 121.4595 | 121.3884 | 0.19479 | 0.050351 | 0.044395 | 121.4739 | 121.4909 | 121.6416 | 121.4095 | -0.12714 | 121.4148 | 121.5134 | 121.5074 | 121.413 | -0.26944
2769.1562 | 121.5546 | -121.3943 | 0.086975 | 1.4211e-13 | 0.023092 | 0.016133 | 0.0098956 | -0.023789 | 0.0044249 | 0.23258 | 0.024171 | 0.034604 | -0.09621 | -0.0010065 | 0.00042948 | 0.07888 | 0.015142 | 0.032795 | 0.079598 | 0.10567 | 0.25185 | -0.035584 | 0.060571 | 0.027831 | -0.010564 | 0.034145 | 0.12817 | 0.12222 | -0.20536 | 121.3588 | -0.007377 | 121.4732 | 121.4271 | 0.068379 | 0.018699 | 0.16488 | 121.189 | -0.05283 | 121.4549 | 121.3838 | 0.19479 | 0.041197 | 0.035241 | 121.4739 | 121.5 | 121.6462 | 121.4095 | -0.12256 | 121.4285 | 121.5225 | 121.5166 | 121.4222 | -0.29233
2770.9219 | 121.6232 | -121.3806 | 0.059509 | 1.4211e-13 | 0.023092 | 0.016133 | 0.0094682 | -0.023148 | 0.0046387 | 0.23258 | 0.024385 | 0.035031 | -0.096424 | -0.00079267 | 0.00042948 | 0.07888 | 0.019721 | 0.032795 | 0.088755 | 0.096516 | 0.26101 | -0.026426 | 0.069728 | 0.03241 | -0.005985 | 0.034145 | 0.12359 | 0.12222 | -0.20078 | 121.3542 | 0.029246 | 121.4595 | 121.4134 | 0.059221 | 0.037007 | 0.2015 | 121.1798 | -0.025364 | 121.4503 | 121.3746 | 0.19479 | 0.064084 | 0.062707 | 121.4694 | 121.4771 | 121.6416 | 121.4003 | -0.085935 | 121.4148 | 121.5042 | 121.5028 | 121.413 | -0.26029
2772.6562 | 121.6278 | -121.3989 | 0.082397 | 1.4211e-13 | 0.023305 | 0.016133 | 0.0098956 | -0.023362 | 0.0044249 | 0.24021 | 0.023957 | 0.034818 | -0.096637 | -0.0010065 | 0.00064308 | 0.083459 | 0.0243 | 0.028217 | 0.070441 | 0.10567 | 0.25643 | -0.044742 | 0.069728 | 0.027831 | -0.010564 | 0.024988 | 0.12359 | 0.11306 | -0.20536 | 121.3542 | -0.011956 | 121.4824 | 121.4271 | 0.072959 | 0.023277 | 0.17403 | 121.1936 | -0.057409 | 121.4687 | 121.3884 | 0.19479 | 0.041196 | 0.030662 | 121.4694 | 121.5046 | 121.6554 | 121.4232 | -0.12714 | 121.4239 | 121.5225 | 121.512 | 121.4268 | -0.28775
2774.3594 | 121.6782 | -121.4172 | 0.068665 | 1.4211e-13 | 0.023305 | 0.015919 | 0.009682 | -0.023362 | 0.0046387 | 0.24784 | 0.023957 | 0.034177 | -0.096637 | -0.0010065 | 0.00021588 | 0.07888 | 0.015142 | 0.028217 | 0.07502 | 0.10567 | 0.25185 | -0.021847 | 0.060571 | 0.023253 | -0.005985 | 0.024988 | 0.12359 | 0.11306 | -0.20994 | 121.3954 | 0.006355 | 121.4961 | 121.4455 | 0.050064 | 0.037009 | 0.18319 | 121.2073 | -0.043677 | 121.4778 | 121.4113 | 0.20395 | 0.054928 | 0.044394 | 121.4923 | 121.5229 | 121.6691 | 121.4324 | -0.090512 | 121.4422 | 121.5408 | 121.5303 | 121.4405 | -0.2786
2776.0781 | 121.6553 | -121.4264 | 0.073242 | 1.4211e-13 | 0.023305 | 0.016133 | 0.0098956 | -0.023362 | 0.0044249 | 0.24021 | 0.024171 | 0.035031 | -0.096424 | -0.0010065 | 0.00064308 | 0.083459 | 0.0243 | 0.032795 | 0.079598 | 0.10567 | 0.25185 | -0.017268 | 0.06515 | 0.027831 | -0.010564 | 0.024988 | 0.11444 | 0.11306 | -0.20078 | 121.4091 | 0.006356 | 121.5099 | 121.4592 | 0.050063 | 0.032432 | 0.17861 | 121.2256 | -0.048254 | 121.4915 | 121.4158 | 0.19022 | 0.041194 | 0.039817 | 121.506 | 121.5321 | 121.6782 | 121.4507 | -0.09051 | 121.4514 | 121.5408 | 121.5395 | 121.4542 | -0.27402
2777.7812 | 121.5683 | -121.4264 | 0.09613 | 1.4211e-13 | 0.023305 | 0.016133 | 0.009682 | -0.023362 | 0.0046387 | 0.23258 | 0.024171 | 0.035031 | -0.096424 | -0.0010065 | 0.00042948 | 0.083459 | 0.019721 | 0.037373 | 0.079598 | 0.1011 | 0.25185 | -0.026426 | 0.06515 | 0.018674 | -0.010564 | 0.015831 | 0.11444 | 0.10848 | -0.20536 | 121.4 | -0.016532 | 121.5099 | 121.4638 | 0.063799 | 0.004965 | 0.15572 | 121.221 | -0.080299 | 121.4915 | 121.4158 | 0.19479 | 0.018306 | 0.01235 | 121.506 | 121.5275 | 121.6782 | 121.4461 | -0.12256 | 121.4422 | 121.5408 | 121.5349 | 121.4451 | -0.30149
2779.5 | 121.669 | -121.4081 | 0.064087 | 1.4211e-13 | 0.023305 | 0.016133 | 0.009682 | -0.023362 | 0.0044249 | 0.23258 | 0.023957 | 0.03439 | -0.096424 | -0.00079267 | 0.00042948 | 0.074302 | 0.015142 | 0.032795 | 0.07502 | 0.1011 | 0.25643 | -0.017268 | 0.046835 | 0.014095 | -0.0243 | 0.006674 | 0.10986 | 0.10848 | -0.22367 | 121.3908 | 0.010933 | 121.4824 | 121.4409 | 0.050063 | 0.037008 | 0.19234 | 121.1844 | -0.057413 | 121.4549 | 121.3838 | 0.19937 | 0.04577 | 0.044393 | 121.4831 | 121.5092 | 121.6645 | 121.4232 | -0.081355 | 121.4148 | 121.5179 | 121.5166 | 121.4222 | -0.28776
2781.2188 | 121.3211 | -121.0602 | 0.054932 | 1.4211e-13 | 0.023305 | 0.015705 | 0.0094682 | -0.023362 | 0.0048523 | 0.24784 | 0.024598 | 0.03439 | -0.096637 | -0.0012201 | 0.00042948 | 0.07888 | 0.019721 | 0.032795 | 0.07502 | 0.10567 | 0.25185 | -0.053899 | 0.051413 | 0.014095 | -0.015143 | 0.024988 | 0.10528 | 0.1039 | -0.20994 | 121.0063 | 0.020088 | 121.1391 | 121.093 | 0.086694 | 0.050742 | 0.19692 | 120.8502 | -0.029944 | 121.1116 | 121.045 | 0.19479 | 0.050347 | 0.048969 | 121.1352 | 121.1659 | 121.312 | 121.0799 | -0.10883 | 121.0852 | 121.1655 | 121.1641 | 121.0743 | -0.26487
2782.9844 | 121.4172 | -121.2112 | 0.068665 | 1.4211e-13 | 0.023305 | 0.016133 | 0.009682 | -0.023362 | 0.0048523 | 0.24021 | 0.024171 | 0.034604 | -0.095996 | -0.00079267 | 0.00042948 | 0.083459 | 0.019721 | 0.037373 | 0.079598 | 0.1011 | 0.25185 | -0.026426 | 0.055992 | 0.014095 | -0.015143 | 0.020409 | 0.11901 | 0.099323 | -0.20536 | 121.1848 | 0.010933 | 121.2947 | 121.2486 | 0.063799 | 0.03243 | 0.18319 | 121.0059 | -0.048256 | 121.2672 | 121.1961 | 0.19022 | 0.050349 | 0.030658 | 121.2908 | 121.3123 | 121.4631 | 121.231 | -0.095091 | 121.2317 | 121.3303 | 121.3106 | 121.2253 | -0.27402
2784.6875 | 121.4035 | -121.3165 | 0.07782 | 1.4211e-13 | 0.023092 | 0.016133 | 0.0098956 | -0.023576 | 0.0046387 | 0.22495 | 0.024385 | 0.035031 | -0.096637 | -0.0010065 | 0.00064308 | 0.07888 | 0.019721 | 0.028217 | 0.07502 | 0.096516 | 0.25185 | -0.053899 | 0.046835 | 0.014095 | -0.015143 | 0.011252 | 0.11444 | 0.099323 | -0.20994 | 121.2626 | -0.0028 | 121.3954 | 121.3447 | 0.082116 | 0.018696 | 0.17403 | 121.1066 | -0.066568 | 121.3634 | 121.3014 | 0.19479 | 0.036616 | 0.021503 | 121.3915 | 121.413 | 121.5684 | 121.3362 | -0.13172 | 121.3278 | 121.431 | 121.4159 | 121.3306 | -0.28776
2786.3906 | 121.5866 | -121.2982 | 0.041199 | 1.4211e-13 | 0.023519 | 0.016133 | 0.010109 | -0.023362 | 0.0046387 | 0.24021 | 0.023957 | 0.03439 | -0.096424 | -0.00057907 | 0.00042948 | 0.083459 | 0.019721 | 0.032795 | 0.079598 | 0.10567 | 0.25643 | -0.031005 | 0.051413 | 0.009516 | -0.015143 | 0.011252 | 0.12359 | 0.094744 | -0.2191 | 121.2672 | 0.038399 | 121.3817 | 121.331 | 0.0638 | 0.064475 | 0.21523 | 121.0791 | -0.029947 | 121.3496 | 121.2831 | 0.20395 | 0.082394 | 0.053545 | 121.3778 | 121.4039 | 121.5546 | 121.3179 | -0.072204 | 121.3095 | 121.4218 | 121.393 | 121.3077 | -0.26029
2788.1094 | 121.2982 | -121.0373 | 0.059509 | 1.4211e-13 | 0.023519 | 0.015919 | 0.0094682 | -0.023576 | 0.0048523 | 0.24021 | 0.024171 | 0.03439 | -0.09621 | -0.0010065 | 0.00021588 | 0.07888 | 0.019721 | 0.032795 | 0.07502 | 0.11025 | 0.26559 | -0.012689 | 0.051413 | 0.004938 | -0.0243 | 0.011252 | 0.11901 | 0.094744 | -0.2191 | 121.0246 | 0.015511 | 121.1162 | 121.0701 | 0.045484 | 0.050744 | 0.20608 | 120.8182 | -0.048257 | 121.0887 | 121.013 | 0.1948 | 0.059505 | 0.035235 | 121.1123 | 121.1475 | 121.3029 | 121.057 | -0.072198 | 121.0485 | 121.1563 | 121.132 | 121.0422 | -0.2786
2789.8125 | 121.4127 | -121.17 | 0.054932 | 1.4211e-13 | 0.023519 | 0.015919 | 0.010109 | -0.023362 | 0.0046387 | 0.24784 | 0.024171 | 0.034818 | -0.096424 | -0.00079267 | 0.00064308 | 0.07888 | 0.019721 | 0.032795 | 0.079598 | 0.1011 | 0.25643 | -0.040163 | 0.060571 | 0.018674 | -0.0243 | 0.006674 | 0.11444 | 0.099323 | -0.20536 | 121.1299 | 0.024666 | 121.2489 | 121.2028 | 0.072958 | 0.046163 | 0.2015 | 120.9647 | -0.048258 | 121.2306 | 121.1457 | 0.18106 | 0.059504 | 0.044391 | 121.2496 | 121.2711 | 121.4265 | 121.1898 | -0.095095 | 121.1767 | 121.2845 | 121.2694 | 121.1887 | -0.26029
2791.5156 | 121.4035 | -121.2662 | 0.07782 | 1.4211e-13 | 0.023092 | 0.015919 | 0.0098956 | -0.023576 | 0.0046387 | 0.23258 | 0.024171 | 0.03439 | -0.096424 | -0.0010065 | 0.00042948 | 0.07888 | 0.015142 | 0.041952 | 0.079598 | 0.10567 | 0.25643 | -0.021847 | 0.055992 | 0.018674 | -0.019721 | 0.006674 | 0.10986 | 0.094744 | -0.20536 | 121.2443 | 0.001778 | 121.3451 | 121.3081 | 0.063799 | 0.027854 | 0.17861 | 121.0608 | -0.071146 | 121.3222 | 121.2465 | 0.18564 | 0.032037 | 0.016924 | 121.3458 | 121.3718 | 121.5226 | 121.2813 | -0.099667 | 121.2728 | 121.376 | 121.3609 | 121.2848 | -0.28318
2793.2188 | 121.4172 | -121.2845 | 0.10529 | 1.4211e-13 | 0.023305 | 0.016346 | 0.0098956 | -0.023576 | 0.0044249 | 0.25547 | 0.024171 | 0.03439 | -0.096637 | -0.0010065 | 0.00042948 | 0.083459 | 0.015142 | 0.032795 | 0.079598 | 0.1011 | 0.25185 | -0.00811 | 0.051413 | 0.018674 | -0.0243 | 0.011252 | 0.11444 | 0.10848 | -0.21452 | 121.2764 | -0.025688 | 121.3679 | 121.3173 | 0.040905 | -0.004191 | 0.14657 | 121.07 | -0.094034 | 121.3359 | 121.2602 | 0.19022 | 0.00915 | 0.003194 | 121.3641 | 121.3856 | 121.5363 | 121.2996 | -0.1134 | 121.2957 | 121.3989 | 121.393 | 121.3032 | -0.3198
2794.9844 | 121.55 | -121.2891 | 0.041199 | 1.4211e-13 | 0.023519 | 0.016346 | 0.010109 | -0.023148 | 0.0044249 | 0.24021 | 0.024385 | 0.034818 | -0.096424 | -0.0010065 | 0.00042948 | 0.083459 | 0.019721 | 0.032795 | 0.07502 | 0.1011 | 0.25643 | -0.003531 | 0.037677 | 0.009516 | -0.0243 | 0.002095 | 0.1007 | 0.10848 | -0.20994 | 121.2855 | 0.033821 | 121.3725 | 121.3219 | 0.036326 | 0.059896 | 0.21523 | 121.0791 | -0.039104 | 121.3267 | 121.2648 | 0.18564 | 0.059501 | 0.067281 | 121.3641 | 121.3902 | 121.5455 | 121.3088 | -0.04473 | 121.2912 | 121.3898 | 121.3975 | 121.2986 | -0.25114
2796.7188 | 121.5637 | -121.3074 | 0.045776 | 1.4211e-13 | 0.023519 | 0.016133 | 0.0098956 | -0.023576 | 0.0046387 | 0.23258 | 0.024171 | 0.034818 | -0.095996 | -0.0010065 | 0.00042948 | 0.07888 | 0.010564 | 0.037373 | 0.079598 | 0.1011 | 0.25643 | 0.014784 | 0.051413 | 0.014095 | -0.015143 | 0.006674 | 0.11444 | 0.10848 | -0.21452 | 121.3222 | 0.033822 | 121.3863 | 121.3447 | 0.022589 | 0.055319 | 0.21066 | 121.0929 | -0.039102 | 121.3588 | 121.2922 | 0.19937 | 0.06866 | 0.062704 | 121.387 | 121.4085 | 121.5638 | 121.3179 | -0.030992 | 121.314 | 121.4218 | 121.4159 | 121.3215 | -0.26029
2798.4375 | 121.5271 | -121.344 | 0.068665 | 1.4211e-13 | 0.023092 | 0.016133 | 0.010109 | -0.023576 | 0.0042113 | 0.23258 | 0.024385 | 0.035031 | -0.096424 | -0.0012201 | 0.00042948 | 0.083459 | 0.019721 | 0.032795 | 0.079598 | 0.096516 | 0.25643 | -0.021847 | 0.051413 | 0.014095 | -0.019721 | 0.006674 | 0.10528 | 0.099323 | -0.21452 | 121.3221 | 0.010933 | 121.4275 | 121.3768 | 0.054642 | 0.027851 | 0.18777 | 121.1295 | -0.061991 | 121.3954 | 121.3243 | 0.1948 | 0.036614 | 0.030658 | 121.4236 | 121.4405 | 121.6004 | 121.3637 | -0.090512 | 121.3507 | 121.4493 | 121.4433 | 121.3581 | -0.28318
2800.1406 | 121.5042 | -121.3531 | 0.073242 | 1.4211e-13 | 0.023305 | 0.015919 | 0.009682 | -0.023576 | 0.0046387 | 0.24021 | 0.023957 | 0.034604 | -0.096637 | -0.0010065 | 0.00064308 | 0.083459 | 0.010564 | 0.028217 | 0.07502 | 0.1011 | 0.25643 | 0.001048 | 0.051413 | 0.018674 | -0.015143 | 0.011252 | 0.10528 | 0.1039 | -0.20536 | 121.3542 | 0.001778 | 121.4366 | 121.3814 | 0.027169 | 0.027853 | 0.18319 | 121.1478 | -0.06199 | 121.4046 | 121.338 | 0.19022 | 0.032037 | 0.030659 | 121.4282 | 121.4542 | 121.6096 | 121.3637 | -0.072194 | 121.3644 | 121.4584 | 121.457 | 121.3718 | -0.2786
2801.9062 | 121.5729 | -121.3577 | 0.045776 | 1.4211e-13 | 0.023092 | 0.016133 | 0.009682 | -0.023789 | 0.0044249 | 0.24021 | 0.024171 | 0.03439 | -0.096637 | -0.0010065 | 0.00021588 | 0.074302 | 0.019721 | 0.037373 | 0.084176 | 0.1011 | 0.25643 | -0.00811 | 0.051413 | 0.014095 | -0.0243 | 0.002095 | 0.1007 | 0.099323 | -0.21452 | 121.3496 | 0.0384 | 121.432 | 121.3951 | 0.045483 | 0.055319 | 0.21066 | 121.1432 | -0.043681 | 121.4091 | 121.3334 | 0.19022 | 0.054924 | 0.053547 | 121.4419 | 121.4588 | 121.6142 | 121.3774 | -0.053886 | 121.3598 | 121.4584 | 121.457 | 121.3718 | -0.26029
2803.6094 | 121.5408 | -121.4172 | 0.073242 | 1.4211e-13 | 0.023519 | 0.016346 | 0.010109 | -0.023789 | 0.0044249 | 0.23258 | 0.024598 | 0.034818 | -0.096637 | -0.0012201 | 0.00042948 | 0.07888 | 0.0243 | 0.028217 | 0.079598 | 0.1011 | 0.25643 | -0.00811 | 0.055992 | 0.014095 | -0.028879 | 0.006674 | 0.10986 | 0.094744 | -0.21452 | 121.4091 | 0.006356 | 121.4961 | 121.4455 | 0.036327 | 0.027853 | 0.18319 | 121.2027 | -0.066568 | 121.4732 | 121.3884 | 0.18564 | 0.036615 | 0.021502 | 121.4968 | 121.5183 | 121.6737 | 121.4415 | -0.081352 | 121.4239 | 121.5271 | 121.512 | 121.4313 | -0.28776
2805.3125 | 121.6553 | -121.3806 | 0.050354 | 1.4211e-13 | 0.023519 | 0.015919 | 0.009682 | -0.023576 | 0.0044249 | 0.24784 | 0.024171 | 0.03439 | -0.096424 | -0.00079267 | 0.00064308 | 0.083459 | 0.019721 | 0.032795 | 0.079598 | 0.1011 | 0.25643 | -0.035584 | 0.055992 | 0.014095 | -0.028879 | 0.011252 | 0.10528 | 0.1039 | -0.20994 | 121.345 | 0.029244 | 121.4641 | 121.4134 | 0.068379 | 0.050741 | 0.20608 | 121.1707 | -0.039102 | 121.4366 | 121.3517 | 0.18106 | 0.054925 | 0.053547 | 121.4602 | 121.4817 | 121.637 | 121.4003 | -0.085938 | 121.3919 | 121.4859 | 121.4845 | 121.3947 | -0.26029
2807.0156 | 120.7077 | -120.314 | 0.15564 | 1.4211e-13 | 0.023519 | 0.016346 | 0.009682 | -0.023576 | 0.0044249 | 0.24021 | 0.023957 | 0.03439 | -0.095996 | -0.00079267 | 0.00021588 | 0.088037 | 0.019721 | 0.028217 | 0.079598 | 0.1011 | 0.25643 | -0.049321 | 0.02852 | -0.022535 | -0.056351 | -0.016219 | 0.077807 | 0.071851 | -0.23741 | 120.2647 | -0.076042 | 120.4021 | 120.3422 | 0.077538 | -0.054545 | 0.10079 | 120.0766 | -0.17186 | 120.3425 | 120.2577 | 0.18106 | -0.077833 | -0.083789 | 120.3936 | 120.4151 | 120.5705 | 120.3337 | -0.20496 | 120.2978 | 120.3918 | 120.3859 | 120.2915 | -0.39305
2808.7188 | 120.9457 | -120.6665 | 0.064087 | 1.4211e-13 | 0.023305 | 0.01656 | 0.0098956 | -0.022935 | 0.0044249 | 0.24021 | 0.023957 | 0.035031 | -0.09621 | -0.00079267 | 0.00042948 | 0.07888 | 0.019721 | 0.032795 | 0.07502 | 0.1011 | 0.25185 | -0.040163 | 0.010205 | -0.027113 | -0.065509 | -0.039111 | 0.073228 | 0.058115 | -0.24657 | 120.6263 | 0.010933 | 120.7454 | 120.6993 | 0.072958 | 0.037008 | 0.18777 | 120.4199 | -0.1032 | 120.6767 | 120.601 | 0.18106 | 0.009141 | -0.005972 | 120.7415 | 120.7676 | 120.9184 | 120.6862 | -0.10425 | 120.6274 | 120.7397 | 120.7246 | 120.6394 | -0.31065
2810.4219 | 121.0602 | -120.7947 | 0.045776 | 1.4211e-13 | 0.023519 | 0.016133 | 0.010109 | -0.023362 | 0.0046387 | 0.24784 | 0.024385 | 0.034604 | -0.096424 | -0.0012201 | 0.00042948 | 0.083459 | 0.0243 | 0.032795 | 0.07502 | 0.10567 | 0.24727 | -0.026426 | 0.001048 | -0.040849 | -0.074666 | -0.039111 | 0.059493 | 0.048958 | -0.25115 | 120.7683 | 0.029244 | 120.8781 | 120.8275 | 0.059221 | 0.059898 | 0.2015 | 120.5435 | -0.084887 | 120.7957 | 120.72 | 0.17648 | 0.013717 | 0.003182 | 120.8697 | 120.9004 | 121.042 | 120.819 | -0.072202 | 120.7556 | 120.8542 | 120.8436 | 120.7538 | -0.29692
2812.1406 | 121.138 | -120.8588 | 0.050354 | 1.4211e-13 | 0.023305 | 0.016346 | 0.009682 | -0.023148 | 0.0044249 | 0.23258 | 0.024598 | 0.034604 | -0.096424 | -0.0010065 | 0.00064308 | 0.07888 | 0.028878 | 0.032795 | 0.084176 | 0.1011 | 0.25643 | -0.044742 | 0.019362 | -0.022535 | -0.056351 | -0.020797 | 0.077807 | 0.067272 | -0.24199 | 120.814 | 0.033822 | 120.9376 | 120.8916 | 0.077537 | 0.050741 | 0.20608 | 120.6168 | -0.071151 | 120.8781 | 120.8024 | 0.18564 | 0.027453 | 0.016918 | 120.9429 | 120.9599 | 121.1152 | 120.8876 | -0.095096 | 120.838 | 120.9366 | 120.926 | 120.8362 | -0.29234
2813.9062 | 121.1929 | -120.9045 | 0.050354 | 1.4211e-13 | 0.023305 | 0.015919 | 0.0098956 | -0.023148 | 0.0044249 | 0.23258 | 0.023957 | 0.03439 | -0.096637 | -0.00079267 | 0.00042948 | 0.07888 | 0.019721 | 0.041952 | 0.079598 | 0.11025 | 0.25185 | -0.003531 | 0.014784 | -0.027113 | -0.056351 | -0.020797 | 0.06865 | 0.062694 | -0.25115 | 120.901 | 0.029244 | 120.9834 | 120.9465 | 0.045483 | 0.059899 | 0.2015 | 120.6534 | -0.071151 | 120.9193 | 120.8482 | 0.19479 | 0.018296 | 0.01234 | 120.9841 | 121.0148 | 121.1564 | 120.9243 | -0.053885 | 120.8837 | 120.9732 | 120.9672 | 120.8774 | -0.3015
2815.625 | 121.1884 | -120.9503 | 0.045776 | 1.4211e-13 | 0.023733 | 0.01656 | 0.0098956 | -0.023362 | 0.0042113 | 0.24021 | 0.024171 | 0.034818 | -0.09621 | -0.0012201 | 0.00064308 | 0.07888 | 0.019721 | 0.032795 | 0.070441 | 0.11025 | 0.25643 | -0.044742 | 0.010205 | -0.031692 | -0.065509 | -0.020797 | 0.054914 | 0.058115 | -0.24657 | 120.9056 | 0.024665 | 121.0292 | 120.9831 | 0.077537 | 0.064477 | 0.21066 | 120.7037 | -0.066573 | 120.9605 | 120.8848 | 0.18106 | 0.009138 | 0.012339 | 121.0208 | 121.0606 | 121.2067 | 120.97 | -0.090518 | 120.9295 | 121.0052 | 121.0084 | 120.9186 | -0.29234
2817.3438 | 121.1517 | -121.0052 | 0.073242 | 1.4211e-13 | 0.023519 | 0.015919 | 0.0098956 | -0.023362 | 0.0044249 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0010065 | 0.00042948 | 0.07888 | 0.0243 | 0.032795 | 0.07502 | 0.1011 | 0.25185 | -0.031005 | 0.014784 | -0.031692 | -0.065509 | -0.029954 | 0.064071 | 0.053537 | -0.25572 | 120.9742 | 0.001778 | 121.0841 | 121.038 | 0.0638 | 0.027853 | 0.17861 | 120.7495 | -0.1032 | 121.02 | 120.9397 | 0.19022 | -0.009171 | -0.019705 | 121.0803 | 121.1063 | 121.2571 | 121.0295 | -0.10425 | 120.9753 | 121.0693 | 121.0588 | 120.9736 | -0.32897
2819.0781 | 121.2524 | -121.019 | 0.050354 | 1.4211e-13 | 0.023305 | 0.016133 | 0.0094682 | -0.023362 | 0.0042113 | 0.24021 | 0.024385 | 0.034818 | -0.096637 | -0.0014337 | 0.00042948 | 0.083459 | 0.015142 | 0.037373 | 0.079598 | 0.091937 | 0.25185 | -0.049321 | 0.014784 | -0.036271 | -0.070087 | -0.04369 | 0.06865 | 0.058115 | -0.25115 | 120.9697 | 0.029244 | 121.1024 | 121.0564 | 0.086694 | 0.041583 | 0.2015 | 120.7678 | -0.094044 | 121.0338 | 120.9489 | 0.18106 | 0.018296 | 0.007761 | 121.0986 | 121.1109 | 121.2708 | 121.0341 | -0.099675 | 120.9753 | 121.0876 | 121.0771 | 120.9827 | -0.3015
2820.7812 | 121.2982 | -121.0098 | 0.032043 | 1.4211e-13 | 0.023519 | 0.016346 | 0.0094682 | -0.023576 | 0.0044249 | 0.24784 | 0.024171 | 0.034818 | -0.096424 | -0.0012201 | 0.00042948 | 0.07888 | 0.015142 | 0.032795 | 0.079598 | 0.1011 | 0.25643 | -0.049321 | 0.001048 | -0.040849 | -0.074666 | -0.04369 | 0.050335 | 0.048958 | -0.2603 | 120.9605 | 0.047555 | 121.0887 | 121.0426 | 0.082116 | 0.069052 | 0.22439 | 120.7495 | -0.075733 | 121.0109 | 120.9352 | 0.18564 | 0.018292 | 0.016915 | 121.0894 | 121.1109 | 121.2663 | 121.025 | -0.081364 | 120.9661 | 121.0602 | 121.0588 | 120.969 | -0.29235
2822.4844 | 121.3303 | -121.0327 | 0.054932 | 1.4211e-13 | 0.023946 | 0.015919 | 0.009682 | -0.023362 | 0.0048523 | 0.24784 | 0.024385 | 0.034604 | -0.096424 | -0.0012201 | 0.00021588 | 0.088037 | 0.010564 | 0.032795 | 0.084176 | 0.1011 | 0.25643 | -0.072215 | 0.010205 | -0.031692 | -0.070087 | -0.039111 | 0.064071 | 0.053537 | -0.25115 | 120.9605 | 0.029244 | 121.1208 | 121.0655 | 0.10501 | 0.046163 | 0.2015 | 120.7816 | -0.094043 | 121.0429 | 120.9626 | 0.18106 | 0.009139 | -0.001395 | 121.1169 | 121.1338 | 121.2891 | 121.0433 | -0.12715 | 120.9936 | 121.0968 | 121.0863 | 121.001 | -0.30608
2824.1875 | 121.3165 | -121.0968 | 0.054932 | 1.4211e-13 | 0.023733 | 0.015919 | 0.009682 | -0.023362 | 0.0042113 | 0.24021 | 0.024385 | 0.034604 | -0.09621 | -0.0014337 | 0.00085668 | 0.07888 | 0.015142 | 0.041952 | 0.070441 | 0.1011 | 0.25185 | 0.001048 | 0.033099 | -0.008798 | -0.051772 | -0.007062 | 0.082386 | 0.07643 | -0.22825 | 121.0978 | 0.015509 | 121.1757 | 121.1388 | 0.040904 | 0.046163 | 0.19692 | 120.8685 | -0.061994 | 121.1299 | 121.045 | 0.17648 | 0.027454 | 0.021498 | 121.1672 | 121.1979 | 121.3487 | 121.1119 | -0.053884 | 121.0897 | 121.1792 | 121.1732 | 121.088 | -0.28318
2825.9375 | 121.376 | -121.1014 | 0.054932 | 1.4211e-13 | 0.023733 | 0.016133 | 0.009682 | -0.023148 | 0.0046387 | 0.24021 | 0.024598 | 0.034604 | -0.096424 | -0.0014337 | 2.08e-06 | 0.07888 | 0.0243 | 0.041952 | 0.07502 | 0.1011 | 0.25643 | -0.040163 | 0.033099 | -0.017956 | -0.051772 | -0.01164 | 0.086964 | 0.081008 | -0.23283 | 121.0612 | 0.020088 | 121.1803 | 121.1433 | 0.082115 | 0.046163 | 0.2015 | 120.8685 | -0.066572 | 121.1345 | 121.0496 | 0.18106 | 0.032032 | 0.026076 | 121.1764 | 121.2025 | 121.3578 | 121.1257 | -0.095095 | 121.0897 | 121.1883 | 121.1824 | 121.0834 | -0.28776
2827.6406 | 121.3852 | -121.1243 | 0.050354 | 1.4211e-13 | 0.023519 | 0.016133 | 0.0098956 | -0.023148 | 0.0044249 | 0.24021 | 0.024385 | 0.03439 | -0.096424 | -0.0012201 | 0.00021588 | 0.07888 | 0.0243 | 0.032795 | 0.07502 | 0.096516 | 0.25643 | -0.058478 | 0.033099 | -0.008798 | -0.042615 | -0.007062 | 0.082386 | 0.07643 | -0.22367 | 121.0658 | 0.024666 | 121.2031 | 121.1571 | 0.091273 | 0.046162 | 0.20608 | 120.9006 | -0.057416 | 121.1574 | 121.0817 | 0.18106 | 0.032032 | 0.026076 | 121.1993 | 121.2208 | 121.3807 | 121.1486 | -0.10883 | 121.1172 | 121.2067 | 121.2007 | 121.1155 | -0.27403
2829.3594 | 121.2845 | -121.2112 | 0.10529 | 1.4211e-13 | 0.023733 | 0.015919 | 0.010109 | -0.023576 | 0.0046387 | 0.24784 | 0.024171 | 0.035031 | -0.096424 | -0.0012201 | 0.00021588 | 0.07888 | 0.010564 | 0.032795 | 0.079598 | 0.1011 | 0.25643 | -0.035584 | 0.033099 | -0.008798 | -0.042615 | -0.007062 | 0.086964 | 0.07643 | -0.22367 | 121.1757 | -0.025688 | 121.2901 | 121.244 | 0.068379 | -0.004191 | 0.15115 | 120.9876 | -0.11235 | 121.2443 | 121.1686 | 0.18106 | -0.018322 | -0.028856 | 121.2908 | 121.3123 | 121.4677 | 121.2218 | -0.14087 | 121.2042 | 121.2982 | 121.2877 | 121.2024 | -0.32896
2831.0625 | 121.4447 | -121.1792 | 0.054932 | 1.4211e-13 | 0.023733 | 0.016133 | 0.0098956 | -0.023362 | 0.0044249 | 0.23258 | 0.024171 | 0.034818 | -0.09621 | -0.0012201 | 0.00042948 | 0.083459 | 0.015142 | 0.028217 | 0.084176 | 0.1011 | 0.25643 | -0.021847 | 0.037677 | -0.00422 | -0.047194 | -0.01164 | 0.091543 | 0.085587 | -0.22367 | 121.1574 | 0.029244 | 121.2627 | 121.2074 | 0.050064 | 0.046163 | 0.2015 | 120.9555 | -0.066572 | 121.2169 | 121.132 | 0.17648 | 0.036611 | 0.030655 | 121.2634 | 121.2803 | 121.4356 | 121.1943 | -0.076779 | 121.1676 | 121.2707 | 121.2648 | 121.175 | -0.2786
2832.8125 | 121.463 | -121.1975 | 0.045776 | 1.4211e-13 | 0.023519 | 0.016133 | 0.010109 | -0.023362 | 0.0044249 | 0.24021 | 0.024171 | 0.034818 | -0.096424 | -0.0012201 | 0.00064308 | 0.074302 | 0.0243 | 0.032795 | 0.079598 | 0.11025 | 0.24727 | -0.035584 | 0.033099 | -0.008798 | -0.042615 | -0.01164 | 0.091543 | 0.081008 | -0.22825 | 121.1619 | 0.033822 | 121.2718 | 121.2303 | 0.068379 | 0.064477 | 0.2015 | 120.9693 | -0.057416 | 121.2306 | 121.1549 | 0.18564 | 0.045767 | 0.035232 | 121.2771 | 121.3078 | 121.4448 | 121.2218 | -0.08136 | 121.1859 | 121.2891 | 121.2785 | 121.1887 | -0.27403
2834.5156 | 121.4401 | -121.2021 | 0.073242 | 1.4211e-13 | 0.023733 | 0.016133 | 0.010109 | -0.023576 | 0.0048523 | 0.23258 | 0.024171 | 0.03439 | -0.096424 | -0.0014337 | 0.00085668 | 0.07888 | 0.015142 | 0.037373 | 0.084176 | 0.10567 | 0.24727 | 0.019363 | 0.02852 | -0.013377 | -0.047194 | -0.016219 | 0.077807 | 0.085587 | -0.22367 | 121.2215 | 0.010934 | 121.281 | 121.2395 | 0.01801 | 0.032432 | 0.17403 | 120.9784 | -0.089461 | 121.2306 | 121.1549 | 0.17648 | 0.004565 | 0.012345 | 121.2863 | 121.3078 | 121.4494 | 121.2172 | -0.053879 | 121.1859 | 121.2799 | 121.2877 | 121.1887 | -0.29692
2836.2188 | 121.4996 | -121.225 | 0.054932 | 1.4211e-13 | 0.023519 | 0.015919 | 0.009682 | -0.023576 | 0.0048523 | 0.24021 | 0.024171 | 0.034177 | -0.09621 | -0.0012201 | 0.00064308 | 0.083459 | 0.0243 | 0.032795 | 0.07502 | 0.10567 | 0.25185 | -0.012689 | 0.033099 | -0.00422 | -0.047194 | -0.007062 | 0.086964 | 0.07643 | -0.22825 | 121.2123 | 0.020088 | 121.3084 | 121.2578 | 0.045484 | 0.050742 | 0.19692 | 120.9967 | -0.061994 | 121.2581 | 121.1778 | 0.18106 | 0.032032 | 0.021498 | 121.3 | 121.3306 | 121.4768 | 121.2493 | -0.067621 | 121.2179 | 121.3119 | 121.3014 | 121.2208 | -0.28318
2837.9844 | 121.4447 | -121.2662 | 0.059509 | 1.4211e-13 | 0.023519 | 0.015919 | 0.0098956 | -0.023362 | 0.0044249 | 0.23258 | 0.024385 | 0.034604 | -0.096424 | -0.0014337 | 0.00085668 | 0.074302 | 0.019721 | 0.032795 | 0.07502 | 0.096516 | 0.26101 | -0.049321 | 0.033099 | -0.008798 | -0.038036 | -0.007062 | 0.086964 | 0.081008 | -0.22825 | 121.2169 | 0.015511 | 121.3405 | 121.299 | 0.082116 | 0.037007 | 0.2015 | 121.0379 | -0.066571 | 121.2993 | 121.2281 | 0.19022 | 0.027455 | 0.021499 | 121.3412 | 121.3627 | 121.5272 | 121.2859 | -0.10883 | 121.2591 | 121.3531 | 121.3472 | 121.2574 | -0.28776
2839.6875 | 120.5704 | -120.4559 | 0.082397 | 1.4211e-13 | 0.023733 | 0.016346 | 0.0098956 | -0.023362 | 0.0044249 | 0.22495 | 0.024385 | 0.034604 | -0.096424 | -0.0010065 | 0.00064308 | 0.083459 | 0.019721 | 0.037373 | 0.079598 | 0.1011 | 0.24727 | -0.040163 | 0.042256 | -0.00422 | -0.038036 | -0.002483 | 0.096121 | 0.085587 | -0.2191 | 120.4158 | -0.002799 | 120.5394 | 120.4933 | 0.077536 | 0.018698 | 0.16488 | 120.2368 | -0.08488 | 120.4982 | 120.4179 | 0.18106 | 0.013724 | 0.00319 | 120.5355 | 120.557 | 120.7032 | 120.4757 | -0.12256 | 120.4535 | 120.5521 | 120.5415 | 120.4517 | -0.30149
2841.4219 | 120.8221 | -120.6894 | 0.091553 | 1.4211e-13 | 0.023946 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.024598 | 0.034818 | -0.096424 | -0.0014337 | 0.00064308 | 0.083459 | 0.0243 | 0.032795 | 0.079598 | 0.1011 | 0.25185 | -0.026426 | 0.042256 | 0.009516 | -0.0243 | 0.002095 | 0.096121 | 0.094744 | -0.21452 | 120.663 | -0.011955 | 120.7729 | 120.7222 | 0.059221 | 0.009542 | 0.1603 | 120.4749 | -0.089458 | 120.7316 | 120.6651 | 0.19022 | 0.004568 | 0.003191 | 120.769 | 120.7905 | 120.9412 | 120.7137 | -0.11798 | 120.6915 | 120.7855 | 120.7841 | 120.6989 | -0.30607
2843.1406 | 121.0007 | -120.726 | 0.054932 | 1.4211e-13 | 0.023733 | 0.01656 | 0.0098956 | -0.023362 | 0.0044249 | 0.24021 | 0.024812 | 0.034604 | -0.096637 | -0.0014337 | 0.0010705 | 0.088037 | 0.019721 | 0.028217 | 0.07502 | 0.11025 | 0.25185 | -0.031005 | 0.055992 | 0.014095 | -0.0243 | 0.011252 | 0.10528 | 0.094744 | -0.20078 | 120.695 | 0.020088 | 120.814 | 120.7542 | 0.059222 | 0.055321 | 0.19692 | 120.5252 | -0.04368 | 120.782 | 120.7017 | 0.17648 | 0.050347 | 0.039812 | 120.801 | 120.8363 | 120.9779 | 120.7457 | -0.085937 | 120.7373 | 120.8313 | 120.8208 | 120.7401 | -0.25571
2844.9062 | 121.0785 | -120.7993 | 0.045776 | 1.4211e-13 | 0.023946 | 0.015919 | 0.0098956 | -0.023362 | 0.0046387 | 0.23258 | 0.023957 | 0.03439 | -0.095996 | -0.0012201 | 0.00064308 | 0.083459 | 0.015142 | 0.037373 | 0.079598 | 0.096516 | 0.24727 | 0.001048 | 0.046835 | 0.000359 | -0.028879 | 0.011252 | 0.10986 | 0.094744 | -0.20536 | 120.8003 | 0.033822 | 120.8827 | 120.8366 | 0.036325 | 0.05074 | 0.2015 | 120.5939 | -0.034524 | 120.8461 | 120.7704 | 0.17648 | 0.064081 | 0.048968 | 120.8789 | 120.8958 | 121.0465 | 120.8144 | -0.044728 | 120.8105 | 120.9091 | 120.894 | 120.7996 | -0.25113
2846.6094 | 121.0281 | -120.8771 | 0.068665 | 1.4211e-13 | 0.023519 | 0.015919 | 0.010109 | -0.023362 | 0.0044249 | 0.24021 | 0.024385 | 0.034818 | -0.096424 | -0.0012201 | 0.00064308 | 0.074302 | 0.019721 | 0.037373 | 0.07502 | 0.10567 | 0.25643 | -0.049321 | 0.051413 | 0.009516 | -0.0243 | 0.006674 | 0.10528 | 0.099323 | -0.20536 | 120.8278 | 0.006355 | 120.9514 | 120.9144 | 0.086694 | 0.037009 | 0.18777 | 120.6717 | -0.061991 | 120.9285 | 120.8528 | 0.18106 | 0.036614 | 0.030658 | 120.9521 | 120.9827 | 121.1335 | 120.8968 | -0.11799 | 120.8837 | 120.9824 | 120.9764 | 120.8866 | -0.27402
2848.3594 | 121.1655 | -120.8862 | 0.064087 | 1.4211e-13 | 0.023733 | 0.016133 | 0.0098956 | -0.022935 | 0.0044249 | 0.23258 | 0.024385 | 0.034604 | -0.09621 | -0.0012201 | 0.00021588 | 0.074302 | 0.015142 | 0.032795 | 0.07502 | 0.1011 | 0.25643 | -0.035584 | 0.055992 | 0.009516 | -0.028879 | 0.015831 | 0.10528 | 0.099323 | -0.20536 | 120.8506 | 0.010933 | 120.9605 | 120.919 | 0.068379 | 0.037008 | 0.19234 | 120.6809 | -0.048256 | 120.9422 | 120.8574 | 0.17648 | 0.041192 | 0.035236 | 120.9612 | 120.9873 | 121.1427 | 120.9014 | -0.099671 | 120.9021 | 120.9915 | 120.9856 | 120.8957 | -0.26945
2850.0781 | 121.1151 | -120.9366 | 0.07782 | 1.4211e-13 | 0.023733 | 0.016346 | 0.0098956 | -0.023576 | 0.0048523 | 0.24021 | 0.024171 | 0.034604 | -0.096851 | -0.0012201 | 0.00042948 | 0.074302 | 0.019721 | 0.037373 | 0.07502 | 0.1011 | 0.24727 | -0.040163 | 0.055992 | 0.000359 | -0.0243 | 0.006674 | 0.1007 | 0.090166 | -0.20994 | 120.8964 | -0.0028 | 121.0109 | 120.974 | 0.077536 | 0.023275 | 0.16945 | 120.7266 | -0.071146 | 120.9926 | 120.9123 | 0.18564 | 0.02288 | 0.012346 | 121.0116 | 121.0377 | 121.1839 | 120.9563 | -0.11798 | 120.9433 | 121.0373 | 121.0267 | 120.9369 | -0.28776
2851.7812 | 121.1655 | -120.9824 | 0.07782 | 1.4211e-13 | 0.023519 | 0.016346 | 0.010109 | -0.023148 | 0.0046387 | 0.23258 | 0.024171 | 0.034818 | -0.096637 | -0.0014337 | 0.00085668 | 0.083459 | 0.0243 | 0.037373 | 0.084176 | 0.1011 | 0.25643 | -0.035584 | 0.042256 | 0.000359 | -0.033458 | 0.006674 | 0.096121 | 0.090166 | -0.20994 | 120.9468 | 0.006356 | 121.0658 | 121.0197 | 0.072957 | 0.023275 | 0.17861 | 120.7724 | -0.071146 | 121.0246 | 120.9489 | 0.17648 | 0.018301 | 0.012346 | 121.0665 | 121.0835 | 121.2388 | 121.0067 | -0.1134 | 120.989 | 121.0785 | 121.0725 | 120.9827 | -0.28776
2853.4844 | 121.0693 | -120.9686 | 0.045776 | 1.4211e-13 | 0.023946 | 0.016346 | 0.0098956 | -0.023148 | 0.0046387 | 0.24021 | 0.024385 | 0.034818 | -0.096424 | -0.0012201 | 0.00085668 | 0.07888 | 0.0243 | 0.041952 | 0.07502 | 0.1011 | 0.25185 | -0.044742 | 0.033099 | -0.008798 | -0.033458 | 0.002095 | 0.096121 | 0.090166 | -0.21452 | 120.9239 | 0.029244 | 121.0475 | 121.0106 | 0.086694 | 0.055319 | 0.20608 | 120.7541 | -0.043681 | 121.0017 | 120.9352 | 0.18106 | 0.050345 | 0.04439 | 121.0436 | 121.0697 | 121.2205 | 120.9929 | -0.090518 | 120.9707 | 121.0647 | 121.0588 | 120.9598 | -0.26029
2855.1875 | 121.1929 | -121.019 | 0.082397 | 1.4211e-13 | 0.023946 | 0.016133 | 0.0098956 | -0.023362 | 0.0048523 | 0.24021 | 0.024171 | 0.034604 | -0.096424 | -0.0014337 | 0.00021588 | 0.083459 | 0.0243 | 0.032795 | 0.07502 | 0.1011 | 0.25643 | -0.063057 | 0.046835 | 0.004938 | -0.028879 | 0.006674 | 0.096121 | 0.090166 | -0.2191 | 120.9559 | -0.007377 | 121.1024 | 121.0518 | 0.095852 | 0.018698 | 0.17403 | 120.7999 | -0.075723 | 121.0658 | 120.9901 | 0.19022 | 0.013724 | 0.007769 | 121.094 | 121.1201 | 121.2754 | 121.0433 | -0.14545 | 121.0257 | 121.1151 | 121.1091 | 121.0239 | -0.30149
2856.9219 | 121.312 | -121.0144 | 0.045776 | 1.4211e-13 | 0.023946 | 0.015919 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.024171 | 0.03439 | -0.095996 | -0.0012201 | 0.00064308 | 0.074302 | 0.015142 | 0.032795 | 0.084176 | 0.096516 | 0.25643 | -0.053899 | 0.037677 | 0.000359 | -0.033458 | -0.002483 | 0.091543 | 0.090166 | -0.21452 | 120.9605 | 0.0384 | 121.0887 | 121.0472 | 0.086694 | 0.05074 | 0.21066 | 120.7999 | -0.048259 | 121.0521 | 120.9809 | 0.18106 | 0.045767 | 0.04439 | 121.0986 | 121.1109 | 121.2708 | 121.0295 | -0.099675 | 121.0119 | 121.1059 | 121.1046 | 121.0148 | -0.26029
2858.625 | 120.3552 | -120.2225 | 0.059509 | 1.4211e-13 | 0.023733 | 0.016346 | 0.010109 | -0.022935 | 0.0046387 | 0.23258 | 0.024598 | 0.034604 | -0.096637 | -0.0012201 | 0.00064308 | 0.07888 | 0.0243 | 0.041952 | 0.079598 | 0.1011 | 0.26101 | -0.049321 | -0.049318 | -0.086637 | -0.12045 | -0.080318 | 0.004549 | 0.012329 | -0.30151 | 120.1732 | 0.020089 | 120.3014 | 120.2644 | 0.091273 | 0.041586 | 0.2015 | 119.921 | -0.13983 | 120.1732 | 120.102 | 0.18106 | -0.05496 | -0.04718 | 120.3021 | 120.3236 | 120.4835 | 120.2468 | -0.10883 | 120.1422 | 120.227 | 120.2348 | 120.1358 | -0.36102
2860.3594 | 120.8176 | -120.7581 | 0.10986 | 1.4211e-13 | 0.023733 | 0.016346 | 0.009682 | -0.023148 | 0.0048523 | 0.24021 | 0.023957 | 0.034604 | -0.096424 | -0.0014337 | 0.00064308 | 0.083459 | 0.015142 | 0.037373 | 0.07502 | 0.096516 | 0.25643 | -0.031005 | 0.023941 | -0.017956 | -0.051772 | -0.016219 | 0.073228 | 0.067272 | -0.23741 | 120.7271 | -0.034843 | 120.8415 | 120.7954 | 0.068378 | -0.013347 | 0.14657 | 120.5206 | -0.12608 | 120.782 | 120.7063 | 0.18564 | -0.036635 | -0.042591 | 120.8331 | 120.8546 | 121.0145 | 120.7732 | -0.14087 | 120.7418 | 120.8313 | 120.8253 | 120.7401 | -0.34727
2862.0625 | 121.0236 | -120.7581 | 0.068665 | 1.4211e-13 | 0.023733 | 0.016346 | 0.0098956 | -0.023148 | 0.0046387 | 0.24021 | 0.024171 | 0.034604 | -0.09621 | -0.0014337 | 0.00021588 | 0.07888 | 0.015142 | 0.037373 | 0.079598 | 0.10567 | 0.26101 | -0.021847 | 0.02852 | -0.022535 | -0.051772 | -0.01164 | 0.077807 | 0.081008 | -0.22367 | 120.7362 | 0.010933 | 120.8369 | 120.7954 | 0.05922 | 0.037009 | 0.19235 | 120.5344 | -0.080305 | 120.7866 | 120.7063 | 0.1719 | 0.009142 | 0.012343 | 120.8377 | 120.8637 | 121.0191 | 120.7732 | -0.090512 | 120.7464 | 120.8359 | 120.8391 | 120.7355 | -0.29234
2863.7656 | 121.0922 | -120.8221 | 0.068665 | 1.4211e-13 | 0.023519 | 0.016133 | 0.0098956 | -0.023148 | 0.0046387 | 0.24021 | 0.024171 | 0.034818 | -0.09621 | -0.0010065 | 0.00064308 | 0.088037 | 0.019721 | 0.032795 | 0.084176 | 0.10567 | 0.25643 | -0.00811 | 0.014784 | -0.027113 | -0.06093 | -0.029954 | 0.064071 | 0.062694 | -0.24657 | 120.814 | 0.015511 | 120.9102 | 120.8549 | 0.040905 | 0.037009 | 0.18777 | 120.5756 | -0.098619 | 120.8369 | 120.7612 | 0.18564 | -0.004594 | -0.005971 | 120.9063 | 120.9278 | 121.0786 | 120.8419 | -0.076775 | 120.7922 | 120.8862 | 120.8848 | 120.795 | -0.31523
2865.5 | 121.0648 | -120.8862 | 0.086975 | 1.4211e-13 | 0.023946 | 0.015919 | 0.0098956 | -0.023362 | 0.0042113 | 0.24021 | 0.024171 | 0.034818 | -0.09621 | -0.0014337 | 0.00042948 | 0.088037 | 0.0243 | 0.041952 | 0.079598 | 0.10567 | 0.25185 | -0.00811 | 0.023941 | -0.017956 | -0.056351 | -0.020797 | 0.073228 | 0.071851 | -0.23741 | 120.8781 | -0.007377 | 120.9743 | 120.9282 | 0.050062 | 0.018699 | 0.16488 | 120.6488 | -0.10777 | 120.9102 | 120.8299 | 0.18106 | -0.013747 | -0.015124 | 120.9658 | 120.9919 | 121.1381 | 120.9105 | -0.095085 | 120.8654 | 120.9595 | 120.9581 | 120.8683 | -0.32439
2867.2031 | 121.17 | -120.9137 | 0.059509 | 1.4211e-13 | 0.023733 | 0.016346 | 0.0098956 | -0.023148 | 0.0048523 | 0.24784 | 0.024385 | 0.03439 | -0.096424 | -0.0014337 | 0.00064308 | 0.074302 | 0.019721 | 0.04653 | 0.079598 | 0.11025 | 0.25643 | -0.017268 | 0.02852 | -0.017956 | -0.056351 | -0.016219 | 0.073228 | 0.07643 | -0.2191 | 120.8964 | 0.020089 | 120.988 | 120.9602 | 0.063798 | 0.050744 | 0.19692 | 120.6946 | -0.075728 | 120.9422 | 120.8573 | 0.16274 | 0.013719 | 0.016921 | 120.9933 | 121.0239 | 121.1701 | 120.9334 | -0.076777 | 120.8975 | 120.9869 | 120.9901 | 120.8957 | -0.2786
2868.9062 | 121.2021 | -120.9183 | 0.054932 | 1.4211e-13 | 0.023946 | 0.016133 | 0.0098956 | -0.022935 | 0.0044249 | 0.24021 | 0.023957 | 0.034177 | -0.096424 | -0.0014337 | 0.00064308 | 0.074302 | 0.019721 | 0.032795 | 0.07502 | 0.096516 | 0.26101 | -0.017268 | 0.023941 | -0.013377 | -0.051772 | -0.016219 | 0.077807 | 0.07643 | -0.22825 | 120.901 | 0.020088 | 120.9926 | 120.9511 | 0.050063 | 0.041584 | 0.20608 | 120.69 | -0.071151 | 120.9422 | 120.8665 | 0.17648 | 0.022875 | 0.021498 | 120.9933 | 121.0148 | 121.1793 | 120.938 | -0.0722 | 120.9021 | 120.9961 | 120.9947 | 120.9049 | -0.28318
2870.625 | 121.1472 | -120.9915 | 0.082397 | 1.4211e-13 | 0.023733 | 0.016133 | 0.0098956 | -0.023576 | 0.0046387 | 0.24021 | 0.024598 | 0.034604 | -0.095996 | -0.0016475 | 0.00064308 | 0.07888 | 0.0243 | 0.037373 | 0.07502 | 0.10567 | 0.25643 | -0.035584 | 0.02852 | -0.017956 | -0.042615 | -0.007062 | 0.082386 | 0.07643 | -0.22367 | 120.9559 | -0.007377 | 121.0704 | 121.0289 | 0.072957 | 0.023277 | 0.17403 | 120.7678 | -0.089459 | 121.02 | 120.9489 | 0.18106 | -1.1e-05 | -0.005967 | 121.0665 | 121.0972 | 121.2479 | 121.0158 | -0.11798 | 120.9845 | 121.0739 | 121.0679 | 120.9736 | -0.30607
2872.3438 | 119.1605 | -119.133 | 0.091553 | 1.4211e-13 | 0.023519 | 0.015705 | 0.0088272 | -0.023148 | 0.0033567 | 0.24021 | 0.024812 | 0.035245 | -0.097065 | -0.0014337 | 0.00064308 | 0.07888 | 0.0243 | 0.041952 | 0.079598 | 0.1011 | 0.26101 | -0.058478 | -1.281 | -1.2817 | -1.3567 | -1.3028 | -1.2134 | -1.2193 | -1.5195 | 119.0745 | -0.011955 | 119.2119 | 119.1749 | 0.10043 | 0.009542 | 0.16946 | 117.6135 | -1.3943 | 117.852 | 117.7763 | 0.16277 | -1.3049 | -1.3109 | 119.2126 | 119.2341 | 119.394 | 119.1573 | -0.15003 | 117.8302 | 117.9196 | 117.9137 | 117.8513 | -1.611
2874.0625 | 119.5404 | -119.5312 | 0.09613 | 1.4211e-13 | 0.023733 | 0.016346 | 0.009682 | -0.023576 | 0.0042113 | 0.24021 | 0.024171 | 0.034818 | -0.096851 | -0.0014337 | 0.0010705 | 0.083459 | 0.0243 | 0.037373 | 0.084176 | 0.1011 | 0.25643 | -0.058478 | 0.037677 | 0.000359 | -0.019721 | 0.011252 | 0.096121 | 0.1039 | -0.20994 | 119.4728 | -0.011954 | 119.6147 | 119.5686 | 0.095851 | 0.004965 | 0.1603 | 119.3213 | -0.084878 | 119.5689 | 119.5115 | 0.19022 | -9e-06 | 0.007771 | 119.6154 | 119.6323 | 119.7877 | 119.5555 | -0.15461 | 119.5425 | 119.6274 | 119.6352 | 119.5316 | -0.30607
2875.7656 | 120.4697 | -120.3918 | 0.10986 | 1.4211e-13 | 0.023946 | 0.016133 | 0.010109 | -0.023362 | 0.0050659 | 0.24784 | 0.024812 | 0.034604 | -0.096424 | -0.0016475 | 0.00021588 | 0.07888 | 0.019721 | 0.041952 | 0.079598 | 0.1011 | 0.25643 | -0.044742 | 0.055992 | 0.014095 | -0.019721 | 0.011252 | 0.10986 | 0.10848 | -0.20078 | 120.3471 | -0.030265 | 120.4707 | 120.4338 | 0.086694 | -0.008768 | 0.14657 | 120.1911 | -0.098611 | 120.4478 | 120.3721 | 0.18106 | -6e-06 | -0.001383 | 120.4714 | 120.4929 | 120.6483 | 120.4116 | -0.1546 | 120.4031 | 120.5017 | 120.5003 | 120.4059 | -0.31064
2877.4844 | 120.639 | -120.4514 | 0.059509 | 1.4211e-13 | 0.023733 | 0.016133 | 0.009682 | -0.023148 | 0.0046387 | 0.22495 | 0.024171 | 0.034818 | -0.096424 | -0.0014337 | 0.00064308 | 0.083459 | 0.019721 | 0.037373 | 0.07502 | 0.096516 | 0.25185 | -0.040163 | 0.051413 | 0.014095 | -0.015143 | 0.006674 | 0.11444 | 0.10848 | -0.18704 | 120.4112 | 0.015511 | 120.5348 | 120.4887 | 0.077536 | 0.037007 | 0.19234 | 120.2643 | -0.052835 | 120.5028 | 120.4362 | 0.1719 | 0.054927 | 0.048971 | 120.5264 | 120.5479 | 120.7032 | 120.4711 | -0.099672 | 120.458 | 120.5658 | 120.5598 | 120.4655 | -0.24655
2879.2031 | 120.7947 | -120.52 | 0.064087 | 1.4211e-13 | 0.023733 | 0.016133 | 0.009682 | -0.023576 | 0.0048523 | 0.23258 | 0.023957 | 0.034604 | -0.096424 | -0.0016475 | 0.00085668 | 0.07888 | 0.0243 | 0.032795 | 0.07502 | 0.1011 | 0.25643 | -0.026426 | 0.055992 | 0.009516 | -0.019721 | 0.011252 | 0.10986 | 0.10848 | -0.1962 | 120.4936 | 0.010933 | 120.5989 | 120.5528 | 0.059221 | 0.037008 | 0.19234 | 120.3238 | -0.052835 | 120.576 | 120.5003 | 0.17648 | 0.04577 | 0.044393 | 120.595 | 120.6211 | 120.7765 | 120.5443 | -0.090513 | 120.5313 | 120.6299 | 120.6285 | 120.5295 | -0.26029
2880.9062 | 120.813 | -120.5887 | 0.068665 | 1.4211e-13 | 0.02416 | 0.016346 | 0.010109 | -0.023148 | 0.0046387 | 0.23258 | 0.024385 | 0.03439 | -0.09621 | -0.0010065 | 0.00042948 | 0.074302 | 0.0243 | 0.032795 | 0.084176 | 0.096516 | 0.25185 | -0.035584 | 0.060571 | 0.014095 | -0.019721 | 0.020409 | 0.11901 | 0.11306 | -0.1962 | 120.5531 | 0.015511 | 120.663 | 120.6215 | 0.068379 | 0.027851 | 0.18319 | 120.3925 | -0.048256 | 120.6493 | 120.569 | 0.17648 | 0.050349 | 0.044394 | 120.6729 | 120.6852 | 120.8405 | 120.613 | -0.10425 | 120.6091 | 120.7077 | 120.7017 | 120.6028 | -0.26487
2882.625 | 120.8359 | -120.5978 | 0.054932 | 1.4211e-13 | 0.023519 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.22495 | 0.024385 | 0.03439 | -0.096424 | -0.0014337 | 0.00042948 | 0.074302 | 0.015142 | 0.028217 | 0.07502 | 0.1011 | 0.25185 | 0.001048 | 0.06515 | 0.014095 | -0.019721 | 0.024988 | 0.10986 | 0.1039 | -0.18246 | 120.5989 | 0.020088 | 120.6721 | 120.6261 | 0.027169 | 0.046163 | 0.19692 | 120.4154 | -0.029944 | 120.663 | 120.5781 | 0.16274 | 0.054925 | 0.048969 | 120.6729 | 120.6989 | 120.8497 | 120.613 | -0.053884 | 120.6228 | 120.7077 | 120.7017 | 120.6119 | -0.2374
2884.3906 | 120.8221 | -120.7077 | 0.09613 | 1.4211e-13 | 0.023733 | 0.01656 | 0.0098956 | -0.023148 | 0.0046387 | 0.23258 | 0.024385 | 0.034604 | -0.096424 | -0.0016475 | 0.00042948 | 0.07888 | 0.019721 | 0.037373 | 0.07502 | 0.11025 | 0.24727 | 0.001048 | 0.06515 | 0.009516 | -0.019721 | 0.011252 | 0.11901 | 0.1039 | -0.19162 | 120.7088 | -0.02111 | 120.7866 | 120.7451 | 0.036325 | 0.014123 | 0.15114 | 120.5161 | -0.084878 | 120.7729 | 120.688 | 0.1719 | 0.022884 | 0.007771 | 120.7827 | 120.818 | 120.955 | 120.7274 | -0.095082 | 120.719 | 120.8267 | 120.8116 | 120.7172 | -0.28775
2886.0938 | 120.9503 | -120.6894 | 0.068665 | 1.4211e-13 | 0.023519 | 0.016133 | 0.0098956 | -0.023576 | 0.0048523 | 0.22495 | 0.024385 | 0.034604 | -0.096424 | -0.0012201 | 2.08e-06 | 0.074302 | 0.0243 | 0.032795 | 0.084176 | 0.10567 | 0.25643 | -0.026426 | 0.06515 | 0.014095 | -0.010564 | 0.015831 | 0.11901 | 0.1039 | -0.19162 | 120.663 | 0.015511 | 120.7637 | 120.7222 | 0.059221 | 0.037009 | 0.18777 | 120.4978 | -0.052834 | 120.7545 | 120.6788 | 0.18106 | 0.050349 | 0.035236 | 120.7736 | 120.7951 | 120.9458 | 120.7137 | -0.095091 | 120.7052 | 120.8084 | 120.7933 | 120.7035 | -0.26029
2887.8281 | 120.8679 | -120.7855 | 0.10529 | 1.4211e-13 | 0.023733 | 0.015919 | 0.009682 | -0.023148 | 0.0050659 | 0.24784 | 0.023957 | 0.03439 | -0.096424 | -0.0014337 | 0.00064308 | 0.083459 | 0.0243 | 0.037373 | 0.079598 | 0.10567 | 0.25643 | -0.026426 | 0.055992 | 0.014095 | -0.015143 | 0.020409 | 0.11901 | 0.10848 | -0.1962 | 120.7591 | -0.025688 | 120.869 | 120.8229 | 0.063799 | 0.000388 | 0.15115 | 120.5893 | -0.084877 | 120.8415 | 120.7704 | 0.18106 | 0.013728 | 0.003194 | 120.8651 | 120.8912 | 121.042 | 120.8098 | -0.13171 | 120.8059 | 120.9045 | 120.894 | 120.7996 | -0.30149
2889.5469 | 120.9183 | -120.7855 | 0.082397 | 1.4211e-13 | 0.023733 | 0.016346 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034604 | -0.09621 | -0.0012201 | 0.00042948 | 0.07888 | 0.028878 | 0.032795 | 0.07502 | 0.1011 | 0.25185 | -0.040163 | 0.055992 | 0.009516 | -0.015143 | 0.020409 | 0.12359 | 0.1039 | -0.19162 | 120.7454 | -0.007377 | 120.8644 | 120.8183 | 0.072958 | 0.018698 | 0.16946 | 120.5939 | -0.061988 | 120.8415 | 120.7704 | 0.17648 | 0.041196 | 0.021504 | 120.8605 | 120.8866 | 121.0374 | 120.8144 | -0.12256 | 120.8059 | 120.9091 | 120.8894 | 120.795 | -0.27402
2891.25 | 120.9961 | -120.813 | 0.086975 | 1.4211e-13 | 0.023733 | 0.015919 | 0.010109 | -0.023362 | 0.0046387 | 0.21732 | 0.024385 | 0.034604 | -0.096424 | -0.0016475 | 0.00042948 | 0.083459 | 0.015142 | 0.032795 | 0.079598 | 0.10567 | 0.25185 | -0.063057 | 0.060571 | 0.014095 | -0.015143 | 0.015831 | 0.11901 | 0.10848 | -0.18246 | 120.7499 | -0.007377 | 120.8964 | 120.8458 | 0.095852 | 0.018699 | 0.16488 | 120.6305 | -0.071144 | 120.8736 | 120.7978 | 0.16732 | 0.032039 | 0.021505 | 120.8926 | 120.9187 | 121.0648 | 120.8281 | -0.15003 | 120.8288 | 120.932 | 120.9215 | 120.8271 | -0.26944
2892.9531 | 121.0098 | -120.8542 | 0.068665 | 1.4211e-13 | 0.02416 | 0.016133 | 0.010109 | -0.023362 | 0.0044249 | 0.24784 | 0.024171 | 0.034604 | -0.096424 | -0.0014337 | 0.00064308 | 0.083459 | 0.019721 | 0.041952 | 0.07502 | 0.1011 | 0.24727 | -0.044742 | 0.055992 | 0.018674 | -0.015143 | 0.020409 | 0.11901 | 0.1039 | -0.18246 | 120.8094 | 0.006355 | 120.9376 | 120.8961 | 0.086694 | 0.03243 | 0.17861 | 120.6717 | -0.048256 | 120.9102 | 120.839 | 0.16732 | 0.050349 | 0.035236 | 120.9292 | 120.9553 | 121.1015 | 120.8739 | -0.11341 | 120.8746 | 120.9732 | 120.9581 | 120.8729 | -0.25113
2894.6719 | 121.0739 | -120.8588 | 0.07782 | 1.4211e-13 | 0.02416 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.024598 | 0.034604 | -0.096424 | -0.0014337 | 0.00042948 | 0.083459 | 0.019721 | 0.032795 | 0.079598 | 0.1011 | 0.25643 | -0.053899 | 0.06515 | 0.014095 | -0.005985 | 0.020409 | 0.11901 | 0.10848 | -0.18704 | 120.8049 | 0.001778 | 120.9422 | 120.8916 | 0.086694 | 0.023275 | 0.17861 | 120.6717 | -0.057411 | 120.9239 | 120.8528 | 0.18106 | 0.041194 | 0.03066 | 120.9384 | 120.9599 | 121.1152 | 120.8785 | -0.13172 | 120.8792 | 120.9778 | 120.9672 | 120.8729 | -0.26486
2896.375 | 121.138 | -120.8862 | 0.045776 | 1.4211e-13 | 0.023733 | 0.016346 | 0.009682 | -0.023148 | 0.0046387 | 0.24784 | 0.024171 | 0.034604 | -0.096851 | -0.0016475 | 0.00042948 | 0.088037 | 0.028878 | 0.032795 | 0.079598 | 0.1011 | 0.25643 | -0.044742 | 0.06515 | 0.014095 | -0.010564 | 0.020409 | 0.11901 | 0.11306 | -0.18246 | 120.8415 | 0.033822 | 120.9743 | 120.919 | 0.077537 | 0.055319 | 0.21066 | 120.7038 | -0.025367 | 120.9514 | 120.8757 | 0.1719 | 0.073238 | 0.067283 | 120.9658 | 120.9873 | 121.1427 | 120.9151 | -0.090518 | 120.9066 | 121.0052 | 120.9993 | 120.9003 | -0.22824
2898.0781 | 121.1014 | -120.8862 | 0.041199 | 1.4211e-13 | 0.023946 | 0.01656 | 0.010109 | -0.023576 | 0.0046387 | 0.24784 | 0.024385 | 0.034818 | -0.096637 | -0.0016475 | 0.00042948 | 0.07888 | 0.015142 | 0.028217 | 0.079598 | 0.10567 | 0.24727 | -0.031005 | 0.037677 | 0.009516 | -0.028879 | 0.006674 | 0.096121 | 0.094744 | -0.1962 | 120.8552 | 0.038399 | 120.9651 | 120.9144 | 0.059222 | 0.064475 | 0.20608 | 120.69 | -0.034525 | 120.9239 | 120.8574 | 0.16732 | 0.054922 | 0.053545 | 120.9658 | 120.9919 | 121.1335 | 120.9014 | -0.072204 | 120.8929 | 120.9824 | 120.981 | 120.8957 | -0.2374
2899.7812 | 120.6848 | -120.5704 | 0.07782 | 1.4211e-13 | 0.02416 | 0.015919 | 0.0098956 | -0.023576 | 0.0046387 | 0.24021 | 0.024812 | 0.03439 | -0.096637 | -0.0016475 | 0.00021588 | 0.083459 | 0.015142 | 0.041952 | 0.07502 | 0.10567 | 0.25185 | -0.044742 | 0.051413 | 0.014095 | -0.015143 | 0.015831 | 0.1007 | 0.094744 | -0.20078 | 120.5256 | -0.0028 | 120.6538 | 120.6123 | 0.086694 | 0.027854 | 0.17403 | 120.3696 | -0.061989 | 120.6218 | 120.5552 | 0.18564 | 0.02288 | 0.016924 | 120.6454 | 120.676 | 120.8222 | 120.5855 | -0.12256 | 120.5862 | 120.6711 | 120.6651 | 120.5845 | -0.2786
2901.5 | 120.4056 | -120.163 | 0.050354 | 1.4211e-13 | 0.02416 | 0.016133 | 0.0098956 | -0.023148 | 0.0044249 | 0.23258 | 0.024171 | 0.034818 | -0.096424 | -0.0016475 | 0.00085668 | 0.07888 | 0.015142 | 0.032795 | 0.07502 | 0.1011 | 0.25185 | -0.012689 | 0.046835 | 0.014095 | -0.0243 | 0.006674 | 0.10528 | 0.1039 | -0.20536 | 120.1503 | 0.024666 | 120.2418 | 120.1958 | 0.045484 | 0.050741 | 0.2015 | 119.9576 | -0.04368 | 120.2098 | 120.1387 | 0.18106 | 0.054925 | 0.053547 | 120.238 | 120.2641 | 120.4148 | 120.1781 | -0.063043 | 120.1696 | 120.2682 | 120.2669 | 120.1771 | -0.25571
2903.2188 | 120.5704 | -120.3323 | 0.15564 | 1.4211e-13 | 0.02416 | 0.016133 | 0.010537 | -0.023362 | 0.0042113 | 0.24784 | 0.024385 | 0.03439 | -0.096637 | -0.0018611 | 0.00042948 | 0.07888 | 0.019721 | 0.037373 | 0.079598 | 0.1011 | 0.25185 | -0.058478 | 0.02852 | 0.000359 | -0.038036 | -0.002483 | 0.096121 | 0.085587 | -0.20994 | 120.2739 | -0.076042 | 120.4112 | 120.3697 | 0.095851 | -0.054545 | 0.096212 | 120.1224 | -0.15812 | 120.3609 | 120.2943 | 0.1719 | -0.059519 | -0.070053 | 120.4119 | 120.4334 | 120.5842 | 120.3521 | -0.21412 | 120.3299 | 120.4285 | 120.4179 | 120.3327 | -0.36558
2904.9844 | 120.7764 | -120.488 | 0.073242 | 1.4211e-13 | 0.023733 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.024385 | 0.034818 | -0.096424 | -0.0016475 | 0.00042948 | 0.083459 | 0.015142 | 0.041952 | 0.079598 | 0.1011 | 0.26101 | -0.021847 | 0.02852 | -0.017956 | -0.047194 | -0.01164 | 0.082386 | 0.071851 | -0.2191 | 120.4661 | 0.006356 | 120.5714 | 120.5299 | 0.063799 | 0.027853 | 0.18777 | 120.2689 | -0.084882 | 120.5165 | 120.4408 | 0.1719 | 0.009144 | -0.001391 | 120.5676 | 120.5891 | 120.749 | 120.5031 | -0.095089 | 120.4763 | 120.5704 | 120.5598 | 120.47 | -0.29234
2906.6875 | 119.3985 | -119.133 | 0.086975 | 1.4211e-13 | 0.023733 | 0.015919 | 0.0094682 | -0.022721 | 0.0042113 | 0.24021 | 0.024171 | 0.034604 | -0.096851 | -0.0016475 | 0.00085668 | 0.074302 | 0.019721 | 0.037373 | 0.079598 | 0.1011 | 0.25643 | -0.049321 | 0.037677 | 0.000359 | -0.038036 | 0.002095 | 0.091543 | 0.090166 | -0.20994 | 119.0837 | -0.007377 | 119.2073 | 119.1704 | 0.086694 | 0.01412 | 0.16946 | 118.9231 | -0.08488 | 119.1707 | 119.095 | 0.1719 | 0.004568 | 0.003191 | 119.2126 | 119.2341 | 119.3894 | 119.1527 | -0.1363 | 119.1351 | 119.2245 | 119.2232 | 119.1334 | -0.29691
2908.4219 | 120.5933 | -120.3781 | 0.050354 | 1.4211e-13 | 0.023946 | 0.016133 | 0.0098956 | -0.023576 | 0.0048523 | 0.23258 | 0.023957 | 0.034604 | -0.09621 | -0.0016475 | 0.00042948 | 0.07888 | 0.0243 | 0.032795 | 0.07502 | 0.096516 | 0.26101 | -0.063057 | 0.051413 | 0.009516 | -0.033458 | 0.006674 | 0.1007 | 0.094744 | -0.1962 | 120.3151 | 0.024666 | 120.457 | 120.4109 | 0.095852 | 0.046162 | 0.21066 | 120.1819 | -0.04368 | 120.4295 | 120.3447 | 0.16274 | 0.050346 | 0.04439 | 120.4531 | 120.4746 | 120.6391 | 120.4024 | -0.11341 | 120.3848 | 120.4788 | 120.4729 | 120.3876 | -0.24655
2910.1562 | 120.6985 | -120.4559 | 0.068665 | 1.4211e-13 | 0.023946 | 0.015919 | 0.010323 | -0.023362 | 0.0048523 | 0.24021 | 0.023957 | 0.034604 | -0.09621 | -0.0014337 | 0.00085668 | 0.074302 | 0.019721 | 0.032795 | 0.07502 | 0.096516 | 0.25185 | -0.053899 | 0.033099 | -0.00422 | -0.033458 | -0.01164 | 0.1007 | 0.081008 | -0.21452 | 120.402 | 0.006355 | 120.5302 | 120.4887 | 0.086694 | 0.027851 | 0.18319 | 120.2414 | -0.080305 | 120.489 | 120.4225 | 0.18106 | 0.032035 | 0.012343 | 120.531 | 120.5524 | 120.7078 | 120.4757 | -0.12256 | 120.4443 | 120.5566 | 120.5369 | 120.4517 | -0.28318
2911.9219 | 120.2179 | -120.0714 | 0.09613 | 1.4211e-13 | 0.02416 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.23258 | 0.024598 | 0.035031 | -0.096424 | -0.0016475 | 0.00064308 | 0.069723 | 0.019721 | 0.037373 | 0.079598 | 0.1011 | 0.25185 | -0.012689 | 0.060571 | 0.023253 | -0.010564 | 0.015831 | 0.12359 | 0.10848 | -0.18704 | 120.0587 | -0.016532 | 120.1411 | 120.1088 | 0.050062 | 0.004965 | 0.15572 | 119.8844 | -0.080299 | 120.132 | 120.0608 | 0.17648 | 0.027463 | 0.01235 | 120.151 | 120.1725 | 120.3233 | 120.0911 | -0.10882 | 120.0872 | 120.195 | 120.1799 | 120.0947 | -0.28317
2913.625 | 120.3552 | -120.2591 | 0.10071 | 1.4211e-13 | 0.023733 | 0.016346 | 0.0094682 | -0.023148 | 0.0046387 | 0.23258 | 0.024171 | 0.034604 | -0.095996 | -0.0016475 | 0.00064308 | 0.083459 | 0.019721 | 0.032795 | 0.079598 | 0.096516 | 0.25185 | -0.049321 | 0.042256 | 0.009516 | -0.033458 | 0.006674 | 0.1007 | 0.099323 | -0.1962 | 120.2098 | -0.02111 | 120.3426 | 120.2919 | 0.082116 | -0.004192 | 0.15114 | 120.0629 | -0.094034 | 120.3013 | 120.2256 | 0.16274 | -8e-06 | -0.001385 | 120.3387 | 120.3556 | 120.5109 | 120.2788 | -0.15003 | 120.2658 | 120.3598 | 120.3584 | 120.2686 | -0.29691
2915.3438 | 120.4559 | -120.2133 | 0.032043 | 1.4211e-13 | 0.023946 | 0.015919 | 0.009682 | -0.023148 | 0.0046387 | 0.24021 | 0.024598 | 0.034604 | -0.096637 | -0.0014337 | 0.00064308 | 0.07888 | 0.015142 | 0.032795 | 0.084176 | 0.11025 | 0.25185 | -0.026426 | 0.06515 | 0.018674 | -0.015143 | 0.020409 | 0.11901 | 0.11306 | -0.18246 | 120.1869 | 0.052133 | 120.2922 | 120.2461 | 0.059221 | 0.07821 | 0.21981 | 120.0309 | -0.011634 | 120.2785 | 120.1982 | 0.16732 | 0.086971 | 0.081016 | 120.2975 | 120.3236 | 120.4652 | 120.2285 | -0.058469 | 120.2337 | 120.3323 | 120.3264 | 120.232 | -0.21451
2917.0469 | 120.4788 | -120.3461 | 0.059509 | 1.4211e-13 | 0.02416 | 0.016346 | 0.009682 | -0.023362 | 0.0048523 | 0.24021 | 0.024598 | 0.034604 | -0.096637 | -0.0014337 | 0.00064308 | 0.074302 | 0.0243 | 0.032795 | 0.079598 | 0.1011 | 0.25643 | -0.049321 | 0.060571 | 0.014095 | -0.015143 | 0.015831 | 0.11444 | 0.1039 | -0.19162 | 120.2967 | 0.020089 | 120.4204 | 120.3789 | 0.082116 | 0.041586 | 0.19692 | 120.1544 | -0.043678 | 120.4066 | 120.3309 | 0.17648 | 0.054927 | 0.044392 | 120.4257 | 120.4472 | 120.6025 | 120.3704 | -0.10883 | 120.3619 | 120.4605 | 120.45 | 120.3602 | -0.25113
2918.75 | 120.6848 | -120.3644 | 0.045776 | 1.4211e-13 | 0.02416 | 0.016133 | 0.0098956 | -0.023148 | 0.0046387 | 0.24021 | 0.024385 | 0.034818 | -0.096851 | -0.0016475 | 0.00064308 | 0.07888 | 0.019721 | 0.032795 | 0.079598 | 0.10567 | 0.25643 | -0.040163 | 0.060571 | 0.009516 | -0.015143 | 0.020409 | 0.11901 | 0.1039 | -0.18704 | 120.3242 | 0.033822 | 120.4433 | 120.3972 | 0.072958 | 0.059898 | 0.21066 | 120.1773 | -0.025367 | 120.425 | 120.3492 | 0.1719 | 0.073238 | 0.058125 | 120.444 | 120.4701 | 120.6208 | 120.3841 | -0.085939 | 120.3848 | 120.4834 | 120.4683 | 120.3739 | -0.23282
2920.4531 | 120.726 | -120.4193 | 0.054932 | 1.4211e-13 | 0.02416 | 0.015919 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034818 | -0.096424 | -0.0012201 | 0.00021588 | 0.07888 | 0.015142 | 0.037373 | 0.07502 | 0.091937 | 0.25643 | -0.067636 | 0.055992 | 0.014095 | -0.0243 | 0.011252 | 0.11444 | 0.10848 | -0.18246 | 120.3517 | 0.020088 | 120.4982 | 120.4567 | 0.10501 | 0.037005 | 0.2015 | 120.2368 | -0.04368 | 120.4753 | 120.395 | 0.15816 | 0.059504 | 0.053548 | 120.4943 | 120.5112 | 120.6757 | 120.4345 | -0.12257 | 120.4306 | 120.5337 | 120.5278 | 120.4334 | -0.2374
2922.1719 | 120.6802 | -120.4971 | 0.082397 | 1.4211e-13 | 0.023946 | 0.015919 | 0.010109 | -0.023362 | 0.0048523 | 0.24784 | 0.024385 | 0.034818 | -0.096637 | -0.0014337 | 0.00042948 | 0.074302 | 0.0243 | 0.037373 | 0.079598 | 0.096516 | 0.25185 | -0.058478 | 0.060571 | 0.023253 | -0.010564 | 0.015831 | 0.11901 | 0.1039 | -0.18246 | 120.4387 | -0.002799 | 120.5714 | 120.5345 | 0.095851 | 0.014119 | 0.16946 | 120.3147 | -0.066566 | 120.5577 | 120.4866 | 0.1719 | 0.036617 | 0.021504 | 120.5767 | 120.5936 | 120.749 | 120.5214 | -0.14088 | 120.513 | 120.6161 | 120.601 | 120.5204 | -0.26486
2923.9375 | 120.726 | -120.52 | 0.073242 | 1.4211e-13 | 0.02416 | 0.016346 | 0.009682 | -0.023576 | 0.0044249 | 0.23258 | 0.024171 | 0.034604 | -0.096424 | -0.0014337 | 0.00042948 | 0.07888 | 0.0243 | 0.037373 | 0.070441 | 0.1011 | 0.25643 | -0.040163 | 0.051413 | 0.023253 | -0.010564 | 0.024988 | 0.11901 | 0.1039 | -0.18246 | 120.4799 | -0.002801 | 120.5989 | 120.5574 | 0.077536 | 0.027853 | 0.18319 | 120.3376 | -0.048254 | 120.5714 | 120.5095 | 0.1719 | 0.045772 | 0.030659 | 120.5905 | 120.6211 | 120.7765 | 120.5443 | -0.11341 | 120.545 | 120.639 | 120.6239 | 120.5433 | -0.25571
2925.6562 | 120.1584 | -119.8929 | 0.041199 | 1.4211e-13 | 0.02416 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.25547 | 0.024385 | 0.034604 | -0.096851 | -0.0014337 | 0.00064308 | 0.07888 | 0.0243 | 0.032795 | 0.079598 | 0.096516 | 0.24727 | -0.003531 | 0.055992 | 0.023253 | -0.019721 | 0.006674 | 0.11444 | 0.1039 | -0.18704 | 119.8894 | 0.038399 | 119.9718 | 119.9257 | 0.036326 | 0.055317 | 0.20608 | 119.7058 | -0.034525 | 119.9489 | 119.8732 | 0.16732 | 0.073237 | 0.062702 | 119.9725 | 119.9894 | 120.1402 | 119.9172 | -0.04473 | 119.8996 | 120.0073 | 119.9968 | 119.9161 | -0.22824
2927.3906 | 120.4193 | -120.282 | 0.09613 | 1.4211e-13 | 0.02416 | 0.016346 | 0.0098956 | -0.023148 | 0.0044249 | 0.23258 | 0.024385 | 0.034604 | -0.096637 | -0.0014337 | 0.00085668 | 0.07888 | 0.019721 | 0.032795 | 0.070441 | 0.10567 | 0.25185 | -0.053899 | 0.06515 | 0.014095 | -0.010564 | 0.020409 | 0.11901 | 0.11306 | -0.17788 | 120.2281 | -0.025689 | 120.3609 | 120.3148 | 0.086694 | 0.009544 | 0.15572 | 120.1041 | -0.075721 | 120.3471 | 120.2714 | 0.16732 | 0.022884 | 0.016929 | 120.3524 | 120.3877 | 120.5338 | 120.3017 | -0.15003 | 120.3024 | 120.401 | 120.395 | 120.2961 | -0.27402
2929.1094 | 120.4559 | -120.401 | 0.10529 | 1.4211e-13 | 0.023946 | 0.016133 | 0.010109 | -0.023148 | 0.0048523 | 0.23258 | 0.024598 | 0.034818 | -0.09621 | -0.0016475 | 0.00064308 | 0.088037 | 0.019721 | 0.032795 | 0.070441 | 0.1011 | 0.25643 | -0.040163 | 0.06515 | 0.018674 | -0.005985 | 0.015831 | 0.11901 | 0.11764 | -0.18246 | 120.3608 | -0.034845 | 120.489 | 120.4338 | 0.072958 | -0.004191 | 0.15115 | 120.2185 | -0.089455 | 120.4662 | 120.395 | 0.17648 | 0.013728 | 0.012351 | 120.4714 | 120.5021 | 120.6574 | 120.4207 | -0.14545 | 120.4168 | 120.52 | 120.5186 | 120.4197 | -0.28775
2930.8125 | 120.6528 | -120.4742 | 0.073242 | 1.4211e-13 | 0.023733 | 0.016346 | 0.009682 | -0.023148 | 0.0048523 | 0.22495 | 0.024385 | 0.034818 | -0.096637 | -0.0014337 | 0.00064308 | 0.083459 | 0.028878 | 0.041952 | 0.079598 | 0.091937 | 0.25643 | -0.044742 | 0.060571 | 0.014095 | -0.010564 | 0.015831 | 0.11444 | 0.10848 | -0.17331 | 120.4295 | 0.006356 | 120.5577 | 120.5162 | 0.086694 | 0.018695 | 0.18319 | 120.3009 | -0.057411 | 120.5348 | 120.4637 | 0.16274 | 0.041194 | 0.035238 | 120.5538 | 120.5662 | 120.7307 | 120.5031 | -0.11798 | 120.4901 | 120.5887 | 120.5827 | 120.4883 | -0.24655
2932.5156 | 120.8176 | -120.1767 | 0.48523 | 1.4211e-13 | 0.02416 | 0.016346 | 0.010109 | -0.023362 | 0.0044249 | 0.24784 | 0.024598 | 0.034818 | -0.096637 | -0.0016475 | 0.00064308 | 0.074302 | 0.0243 | 0.028217 | 0.079598 | 0.096516 | 0.25643 | -0.044742 | 0.055992 | 0.004938 | -0.033458 | -0.002483 | 0.10986 | 0.090166 | -0.20536 | 120.132 | -0.40563 | 120.251 | 120.2049 | 0.072959 | -0.38871 | -0.2288 | 119.9713 | -0.48771 | 120.2327 | 120.1432 | 0.1719 | -0.37537 | -0.39506 | 120.2563 | 120.2732 | 120.4331 | 120.201 | -0.52997 | 120.1742 | 120.2866 | 120.2669 | 120.1816 | -0.69059
2934.2188 | 119.7372 | -8.6838 | 111.1084 | 1.4211e-13 | 0.023946 | 0.016346 | 0.010109 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.034818 | -0.096851 | -0.0014337 | 0.00064308 | 0.05141 | -0.012329 | 0.005325 | 0.052128 | 0.073622 | 0.21522 | -0.11342 | 0.051413 | 0.004938 | -0.0243 | 0.006674 | 0.1007 | -0.001407 | -0.1962 | 8.5704 | -111.0563 | 8.7352 | 8.6891 | 0.11875 | -111.0348 | -110.8932 | 8.4876 | -111.1017 | 8.7352 | 8.6595 | 0.1719 | -111.0077 | -111.1098 | 8.7359 | 8.7574 | 8.899 | 8.6714 | -111.2218 | 8.6905 | 8.7845 | 8.6824 | 8.6887 | -111.3046
2935.9844 | 120.2591 | -44.1422 | 75.7324 | 1.4211e-13 | 0.02416 | 0.016346 | 0.010109 | -0.023362 | 0.0046387 | 0.24021 | 0.024171 | 0.035031 | -0.096637 | -0.0018611 | 0.00085668 | 0.037675 | -0.016908 | 0.000747 | 0.047549 | 0.064464 | 0.2198 | -0.090531 | 0.051413 | 0.004938 | -0.0243 | 0.006674 | 0.096121 | -0.010564 | -0.19162 | 44.0516 | -75.6849 | 44.1798 | 44.1429 | 0.091278 | -75.668 | -75.5126 | 43.9505 | -75.7257 | 44.1936 | 44.1179 | 0.16732 | -75.6363 | -75.743 | 44.1897 | 44.2066 | 44.362 | 44.1252 | -75.823 | 44.1488 | 44.2383 | 44.1316 | 44.1471 | -75.924
2937.6875 | 120.1675 | -76.5015 | 43.9407 | 1.4211e-13 | 0.024587 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.024598 | 0.03439 | -0.09621 | -0.0018611 | 0.00042948 | 0.055988 | -0.016908 | 0.000747 | 0.065863 | 0.078201 | 0.23354 | -0.099689 | 0.055992 | 0.004938 | -0.015143 | 0.015831 | 0.10986 | 0.021486 | -0.18246 | 76.4018 | -43.8749 | 76.5575 | 76.5022 | 0.10044 | -43.8625 | -43.7072 | 76.319 | -43.9249 | 76.5575 | 76.4863 | 0.16732 | -43.8309 | -43.9192 | 76.5673 | 76.5797 | 76.735 | 76.4846 | -44.0404 | 76.5173 | 76.6113 | 76.523 | 76.5064 | -44.1232
2939.4219 | 120.3598 | -119.9799 | 0.073242 | 1.4211e-13 | 0.024374 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.24784 | 0.024171 | 0.034604 | -0.096424 | -0.0014337 | 0.00042948 | 0.07888 | 0.019721 | 0.032795 | 0.079598 | 0.1011 | 0.25185 | -0.031005 | 0.069728 | 0.027831 | -0.001407 | 0.029566 | 0.12359 | 0.044379 | -0.17331 | 119.9489 | 0.006356 | 120.0587 | 120.0127 | 0.0638 | 0.027853 | 0.17861 | 119.8066 | -0.043676 | 120.0496 | 119.9785 | 0.1719 | 0.050351 | -0.028863 | 120.0595 | 120.081 | 120.2317 | 119.9996 | -0.10425 | 120.0094 | 120.1035 | 120.0242 | 120.0077 | -0.24655
2941.125 | 120.282 | -119.8791 | 0.1236 | 1.4211e-13 | 0.02416 | 0.016133 | 0.0094682 | -0.023576 | 0.0044249 | 0.23258 | 0.024385 | 0.035031 | -0.096851 | -0.0016475 | 0.00064308 | 0.07888 | 0.0243 | 0.028217 | 0.084176 | 0.1011 | 0.26101 | -0.044742 | 0.060571 | 0.018674 | -0.001407 | 0.024988 | 0.11901 | 0.026065 | -0.17788 | 119.8344 | -0.03942 | 119.958 | 119.9074 | 0.072959 | -0.022501 | 0.13741 | 119.7013 | -0.098608 | 119.9397 | 119.8777 | 0.17648 | -0.004582 | -0.097531 | 119.9633 | 119.9802 | 120.1402 | 119.9034 | -0.16834 | 119.9041 | 119.9982 | 119.9052 | 119.8978 | -0.30148
2942.8906 | 120.3873 | -120.1126 | 0.13275 | 1.4211e-13 | 0.024587 | 0.015919 | 0.010109 | -0.023362 | 0.0052797 | 0.23258 | 0.024171 | 0.034818 | -0.096424 | -0.0018611 | 0.00042948 | 0.07888 | 0.015142 | 0.032795 | 0.070441 | 0.091937 | 0.25185 | -0.067636 | 0.06515 | 0.014095 | -0.010564 | 0.020409 | 0.12817 | 0.026065 | -0.17788 | 120.045 | -0.06231 | 120.1915 | 120.1454 | 0.10043 | -0.040814 | 0.1191 | 119.9347 | -0.11234 | 120.1778 | 120.102 | 0.16732 | -0.004579 | -0.10669 | 120.1831 | 120.2045 | 120.3645 | 120.1278 | -0.20039 | 120.133 | 120.2408 | 120.1387 | 120.1267 | -0.31064
2944.5938 | 120.2225 | -119.9982 | 0.14648 | 1.4211e-13 | 0.023946 | 0.015919 | 0.0098956 | -0.022935 | 0.0046387 | 0.23258 | 0.024598 | 0.034177 | -0.096424 | -0.0016475 | 0.00042948 | 0.07888 | 0.019721 | 0.032795 | 0.07502 | 0.1011 | 0.25643 | -0.058478 | 0.060571 | 0.023253 | -0.001407 | 0.020409 | 0.12817 | 0.021486 | -0.18246 | 119.9397 | -0.071464 | 120.077 | 120.031 | 0.091273 | -0.045389 | 0.10995 | 119.8157 | -0.12607 | 120.0587 | 119.9968 | 0.18106 | -0.018312 | -0.125 | 120.0732 | 120.0993 | 120.2546 | 120.0179 | -0.20496 | 120.0186 | 120.1263 | 120.0197 | 120.0214 | -0.32895
2946.3125 | 120.3964 | -120.1309 | 0.10529 | 1.4211e-13 | 0.02416 | 0.016133 | 0.009682 | -0.023362 | 0.0046387 | 0.24784 | 0.024171 | 0.034818 | -0.096424 | -0.0018611 | 0.00042948 | 0.07888 | 0.019721 | 0.041952 | 0.07502 | 0.1011 | 0.24727 | -0.035584 | 0.069728 | 0.014095 | -0.005985 | 0.024988 | 0.11901 | 0.030644 | -0.17331 | 120.0953 | -0.030266 | 120.2098 | 120.1729 | 0.077536 | -0.004191 | 0.14199 | 119.9576 | -0.080298 | 120.2006 | 120.1249 | 0.16732 | 0.013728 | -0.074642 | 120.2059 | 120.232 | 120.3782 | 120.1506 | -0.14087 | 120.1559 | 120.2499 | 120.1616 | 120.145 | -0.27859
2948.0312 | 120.5017 | -119.9432 | 0.28839 | 1.4211e-13 | 0.024374 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.024385 | 0.03439 | -0.096637 | -0.0016475 | 0.00064308 | 0.083459 | 0.015142 | 0.037373 | 0.070441 | 0.096516 | 0.24727 | -0.058478 | 0.055992 | 0.004938 | -0.015143 | 0.006674 | 0.11901 | 0.012329 | -0.18704 | 119.8848 | -0.21795 | 120.0267 | 119.9806 | 0.095851 | -0.19188 | -0.041117 | 119.7562 | -0.28172 | 119.9992 | 119.9281 | 0.1719 | -0.16938 | -0.27606 | 120.0137 | 120.0398 | 120.1905 | 119.9584 | -0.34687 | 119.9499 | 120.0623 | 119.9556 | 119.9482 | -0.47543
2949.75 | 120.314 | -119.5633 | 0.65918 | 1.4211e-13 | 0.024374 | 0.015919 | 0.0098956 | -0.023362 | 0.0046387 | 0.24784 | 0.024385 | 0.035459 | -0.096637 | -0.0016475 | 0.00042948 | 0.083459 | 0.019721 | 0.041952 | 0.079598 | 0.096516 | 0.26101 | -0.063057 | 0.060571 | 0.014095 | -0.015143 | 0.011252 | 0.11444 | 0.016908 | -0.18246 | 119.5002 | -0.57958 | 119.6468 | 119.6052 | 0.10501 | -0.56266 | -0.39817 | 119.3808 | -0.64793 | 119.6239 | 119.5482 | 0.16732 | -0.54474 | -0.64227 | 119.6429 | 119.6598 | 119.8243 | 119.583 | -0.72224 | 119.5745 | 119.6777 | 119.5802 | 119.5774 | -0.84164
2951.5 | 120.3049 | -119.7968 | 0.032043 | 1.4211e-13 | 0.024374 | 0.016346 | 0.009682 | -0.023148 | 0.0044249 | 0.23258 | 0.024171 | 0.034604 | -0.096637 | -0.0018611 | 0.00064308 | 0.07888 | 0.015142 | 0.028217 | 0.084176 | 0.10567 | 0.25185 | -0.00811 | 0.060571 | 0.023253 | -0.010564 | 0.015831 | 0.10986 | 0.016908 | -0.17788 | 119.7886 | 0.052133 | 119.8756 | 119.825 | 0.036327 | 0.073631 | 0.21981 | 119.6189 | -0.016212 | 119.8573 | 119.7862 | 0.16732 | 0.077814 | -0.015135 | 119.8809 | 119.9024 | 120.0486 | 119.8119 | -0.040153 | 119.8126 | 119.9066 | 119.8137 | 119.82 | -0.20993
2953.25 | 120.4376 | -120.2179 | 0.10071 | 1.4211e-13 | 0.024587 | 0.016133 | 0.010109 | -0.023362 | 0.0046387 | 0.23258 | 0.024385 | 0.034604 | -0.09621 | -0.0018611 | 0.00042948 | 0.083459 | 0.015142 | 0.041952 | 0.07502 | 0.096516 | 0.25185 | -0.003531 | 0.055992 | 0.023253 | -0.015143 | 0.011252 | 0.11444 | 0.021486 | -0.18704 | 120.2144 | -0.025688 | 120.3014 | 120.2598 | 0.045483 | -0.004192 | 0.15114 | 120.0309 | -0.089456 | 120.2739 | 120.2028 | 0.1719 | 0.013728 | -0.079222 | 120.2929 | 120.3144 | 120.4697 | 120.233 | -0.10424 | 120.2291 | 120.3323 | 120.2394 | 120.2411 | -0.28775
2955.0312 | 120.4971 | -120.3461 | 0.09613 | 1.4211e-13 | 0.024587 | 0.016346 | 0.0098956 | -0.022935 | 0.0048523 | 0.23258 | 0.024385 | 0.034604 | -0.096637 | -0.0018611 | 0.00042948 | 0.07888 | 0.0243 | 0.028217 | 0.079598 | 0.1011 | 0.25643 | -0.049321 | 0.060571 | 0.014095 | -0.015143 | 0.006674 | 0.11901 | 0.012329 | -0.18704 | 120.2967 | -0.016532 | 120.4249 | 120.3743 | 0.077538 | 0.004965 | 0.1603 | 120.159 | -0.089456 | 120.4066 | 120.3309 | 0.1719 | 0.022884 | -0.083801 | 120.4257 | 120.4472 | 120.6025 | 120.3704 | -0.14545 | 120.3527 | 120.4651 | 120.3584 | 120.3602 | -0.28317
2956.7344 | 120.5292 | -120.3964 | 0.082397 | 1.4211e-13 | 0.024374 | 0.016346 | 0.010109 | -0.023362 | 0.0046387 | 0.23258 | 0.024598 | 0.03439 | -0.096637 | -0.0016475 | 0.00042948 | 0.088037 | 0.019721 | 0.037373 | 0.084176 | 0.10567 | 0.26101 | -0.026426 | 0.069728 | 0.009516 | -0.015143 | 0.015831 | 0.11901 | 0.016908 | -0.17788 | 120.37 | 0.001779 | 120.4845 | 120.4338 | 0.063799 | 0.023277 | 0.17861 | 120.2185 | -0.066566 | 120.4662 | 120.3813 | 0.16274 | 0.036617 | -0.065489 | 120.4806 | 120.5021 | 120.6574 | 120.4161 | -0.10882 | 120.4123 | 120.5154 | 120.4133 | 120.4059 | -0.26028
2958.5 | 120.6665 | -120.314 | 0.12817 | 1.4211e-13 | 0.024374 | 0.016346 | 0.010109 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034818 | -0.096424 | -0.0020749 | 0.00064308 | 0.07888 | 0.019721 | 0.041952 | 0.07502 | 0.1011 | 0.25185 | -0.063057 | 0.055992 | 0.009516 | -0.019721 | 0.020409 | 0.11901 | 0.007751 | -0.18246 | 120.251 | -0.053154 | 120.3929 | 120.356 | 0.10501 | -0.027079 | 0.12368 | 120.1316 | -0.10777 | 120.37 | 120.2943 | 0.16274 | -0.00916 | -0.12042 | 120.389 | 120.4151 | 120.5659 | 120.3337 | -0.19123 | 120.3344 | 120.433 | 120.3218 | 120.3235 | -0.31064
2960.2188 | 120.7352 | -120.401 | 0.045776 | 1.4211e-13 | 0.024374 | 0.016346 | 0.009682 | -0.023362 | 0.0046387 | 0.23258 | 0.024171 | 0.034604 | -0.09621 | -0.0018611 | 0.00042948 | 0.083459 | 0.0243 | 0.037373 | 0.084176 | 0.1011 | 0.24727 | -0.035584 | 0.060571 | 0.009516 | -0.019721 | 0.015831 | 0.11901 | 0.016908 | -0.18246 | 120.3654 | 0.0384 | 120.4845 | 120.4384 | 0.072957 | 0.055319 | 0.2015 | 120.2185 | -0.029945 | 120.4616 | 120.3813 | 0.16274 | 0.073238 | -0.028868 | 120.4852 | 120.5021 | 120.6483 | 120.4253 | -0.08136 | 120.4168 | 120.52 | 120.4179 | 120.4105 | -0.22824
2962.0156 | 120.6299 | -120.4742 | 0.09613 | 1.4211e-13 | 0.024374 | 0.016133 | 0.0098956 | -0.023148 | 0.0046387 | 0.23258 | 0.024812 | 0.034818 | -0.096851 | -0.0016475 | 0.00021588 | 0.069723 | 0.0243 | 0.023639 | 0.07502 | 0.11025 | 0.25185 | -0.044742 | 0.06515 | 0.014095 | -0.010564 | 0.011252 | 0.12817 | 0.012329 | -0.17788 | 120.4295 | -0.02111 | 120.544 | 120.4979 | 0.068381 | 0.014123 | 0.15572 | 120.2964 | -0.084878 | 120.5394 | 120.4637 | 0.16732 | 0.032042 | -0.083801 | 120.5493 | 120.5845 | 120.7261 | 120.4985 | -0.14087 | 120.4855 | 120.6024 | 120.4866 | 120.4883 | -0.27402
2963.7188 | 115.361 | -12.8586 | 92.3538 | 1.4211e-13 | 0.024587 | 0.016133 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024598 | 0.034818 | -0.096851 | -0.0018611 | 0.00085668 | 0.055988 | 0.001407 | 0.005325 | 0.047549 | 0.078201 | 0.22438 | -0.090531 | 0.051413 | 0.000359 | -0.019721 | 0.006674 | 0.10986 | -0.010564 | -0.19162 | 12.7681 | -92.3063 | 12.9146 | 12.8639 | 0.095856 | -92.2756 | -92.1294 | 12.667 | -92.3471 | 12.91 | 12.8389 | 0.1719 | -92.244 | -92.3644 | 12.9061 | 12.9368 | 13.083 | 12.86 | -92.4444 | 12.8653 | 12.9684 | 12.848 | 12.8589 | -92.5454
2965.4375 | 96.9452 | -0.10529 | 96.0434 | 1.4211e-13 | 0.024374 | 0.016133 | 0.009682 | -0.023148 | 0.0046387 | 0.23258 | 0.024598 | 0.03439 | -0.096637 | -0.0018611 | 0.00064308 | 0.046831 | -0.021486 | -0.008409 | 0.038393 | 0.059885 | 0.21522 | -0.10427 | 0.037677 | -0.00422 | -0.033458 | -0.002483 | 0.091543 | -0.028878 | -0.20536 | 0.001018 | -96.005 | 0.15212 | 0.096877 | 0.095859 | -95.9835 | -95.8282 | -0.10007 | -96.0459 | 0.14296 | 0.071828 | 0.1719 | -95.9519 | -96.0723 | 0.14368 | 0.16517 | 0.32051 | 0.0838 | -96.1477 | 0.1028 | 0.19683 | 0.076408 | 0.10107 | -96.2488
2967.1562 | 120.5704 | -2.861 | 116.8716 | 1.4211e-13 | 0.023946 | 0.016346 | 0.0098956 | -0.023362 | 0.0044249 | 0.24784 | 0.024598 | 0.034818 | -0.096637 | -0.0016475 | 0.00042948 | 0.042253 | -0.021486 | -0.003831 | 0.038393 | 0.055306 | 0.21522 | -0.09511 | 0.042256 | 0.000359 | -0.033458 | 0.002095 | 0.096121 | -0.060928 | -0.19162 | 2.7659 | -116.8333 | 2.9033 | 2.8572 | 0.091279 | -116.8163 | -116.6564 | 2.6694 | -116.8695 | 2.9033 | 2.8276 | 0.15816 | -116.7755 | -116.9326 | 2.8994 | 2.9163 | 3.0762 | 2.8395 | -116.9668 | 2.8631 | 2.9571 | 2.8001 | 2.8614 | -117.0633
2968.9375 | 120.694 | -4.0604 | 116.1667 | 1.4211e-13 | 0.02416 | 0.016346 | 0.009682 | -0.023148 | 0.0044249 | 0.24784 | 0.024598 | 0.034818 | -0.096851 | -0.0016475 | 0.00064308 | 0.037675 | -0.026065 | -0.003831 | 0.042971 | 0.059885 | 0.21522 | -0.09511 | 0.042256 | 0.000359 | -0.033458 | -0.002483 | 0.096121 | -0.047193 | -0.19162 | 3.9653 | -116.1237 | 4.098 | 4.0565 | 0.091279 | -116.1068 | -115.9515 | 3.8687 | -116.1692 | 4.1026 | 4.0269 | 0.15816 | -116.0706 | -116.2139 | 4.1033 | 4.1202 | 4.2756 | 4.0343 | -116.2618 | 4.0579 | 4.1565 | 4.0132 | 4.0607 | -116.3583
2970.6875 | 115.9927 | -60.6995 | 54.8126 | 1.4211e-13 | 0.024587 | 0.016133 | 0.009682 | -0.023148 | 0.0044249 | 0.22495 | 0.023957 | 0.034604 | -0.096637 | -0.0016475 | 0.00042948 | 0.037675 | -0.016908 | -0.003831 | 0.038393 | 0.064464 | 0.20607 | -0.10427 | 0.046835 | 0.004938 | -0.028879 | 0.002095 | 0.096121 | -0.033457 | -0.19162 | 60.5952 | -54.7742 | 60.7371 | 60.6956 | 0.10044 | -54.7482 | -54.6066 | 60.5078 | -54.8105 | 60.7463 | 60.6706 | 0.16274 | -54.7165 | -54.8461 | 60.7379 | 60.7639 | 60.9055 | 60.6826 | -54.9169 | 60.7016 | 60.7956 | 60.666 | 60.7044 | -55.0042
2972.3906 | 120.5566 | -91.2415 | 25.3372 | 1.4211e-13 | 0.024374 | 0.016133 | 0.009682 | -0.023576 | 0.0044249 | 0.22495 | 0.024385 | 0.034604 | -0.096424 | -0.0020749 | 0.00085668 | 0.055988 | 0.001407 | 0.01906 | 0.065863 | 0.08278 | 0.23354 | -0.076794 | 0.055992 | 0.009516 | -0.028879 | 0.011252 | 0.10986 | 0.016908 | -0.18246 | 91.1647 | -25.2714 | 91.2974 | 91.2605 | 0.095854 | -25.2544 | -25.1037 | 91.059 | -25.326 | 91.2974 | 91.2126 | 0.15358 | -25.2274 | -25.3203 | 91.3073 | 91.3242 | 91.475 | 91.2429 | -25.414 | 91.2527 | 91.3513 | 91.2584 | 91.251 | -25.5197
2974.0938 | 120.5017 | -14.9826 | 104.8782 | 1.4211e-13 | 0.024374 | 0.016346 | 0.009682 | -0.023362 | 0.0044249 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0020749 | 0.00042948 | 0.037675 | -0.021486 | -0.003831 | 0.038393 | 0.064464 | 0.21522 | -0.09511 | 0.042256 | -0.00422 | -0.028879 | 0.002095 | 0.1007 | -0.033457 | -0.1962 | 14.8875 | -104.8398 | 15.0203 | 14.9788 | 0.091279 | -104.8138 | -104.663 | 14.7864 | -104.8761 | 15.0249 | 14.9537 | 0.16732 | -104.7775 | -104.9117 | 15.021 | 15.0471 | 15.1978 | 14.9611 | -104.9733 | 14.9847 | 15.0833 | 14.9491 | 14.9784 | -105.0744
2975.7969 | 119.8975 | -12.4786 | 107.1625 | 1.4211e-13 | 0.024374 | 0.015919 | 0.010109 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.034604 | -0.09621 | -0.0018611 | 0.00021588 | 0.042253 | -0.016908 | -0.003831 | 0.052128 | 0.059885 | 0.21064 | -0.09511 | 0.046835 | 0.004938 | -0.0243 | -0.002483 | 0.096121 | -0.051771 | -0.19162 | 12.3835 | -107.1103 | 12.5209 | 12.4748 | 0.091279 | -107.1026 | -106.9518 | 12.287 | -107.165 | 12.5255 | 12.4543 | 0.16732 | -107.0664 | -107.2142 | 12.5308 | 12.5385 | 12.6893 | 12.4617 | -107.2576 | 12.4762 | 12.5748 | 12.4269 | 12.4836 | -107.3541
2977.5 | 92.6651 | -0.13275 | 94.693 | 1.4211e-13 | 0.024587 | 0.015919 | 0.0098956 | -0.023576 | 0.0046387 | 0.23258 | 0.023957 | 0.034604 | -0.09621 | -0.0020749 | 0.00042948 | 0.042253 | -0.026065 | 0.005325 | 0.042971 | 0.064464 | 0.21522 | -0.10885 | 0.037677 | 0.009516 | -0.028879 | -0.002483 | 0.096121 | -0.047193 | -0.19162 | 0.023904 | -94.65 | 0.175 | 0.13808 | 0.11417 | -94.6285 | -94.4778 | -0.058871 | -94.6955 | 0.17043 | 0.10387 | 0.16274 | -94.5969 | -94.7402 | 0.17572 | 0.19722 | 0.34798 | 0.10669 | -94.8018 | 0.13027 | 0.22887 | 0.085558 | 0.14227 | -94.8846
2979.2188 | 99.8062 | -2.6642 | 86.6455 | 1.4211e-13 | 0.024587 | 0.016346 | 0.010109 | -0.023576 | 0.0048523 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0016475 | 0.00064308 | 0.046831 | -0.021486 | -0.008409 | 0.042971 | 0.059885 | 0.2198 | -0.118 | 0.051413 | 0.009516 | -0.0243 | 0.002095 | 0.1007 | 0.012329 | -0.19162 | 2.5462 | -86.6025 | 2.711 | 2.6558 | 0.10959 | -86.5856 | -86.4257 | 2.4726 | -86.6434 | 2.7156 | 2.6399 | 0.16732 | -86.5448 | -86.6332 | 2.7072 | 2.7241 | 2.884 | 2.6427 | -86.7635 | 2.6663 | 2.7649 | 2.6765 | 2.6737 | -86.8371
2980.9844 | 120.6528 | -3.9642 | 115.9103 | 1.4211e-13 | 0.024374 | 0.016346 | 0.009682 | -0.022935 | 0.0044249 | 0.23258 | 0.024385 | 0.03439 | -0.096851 | -0.0018611 | 0.00064308 | 0.037675 | -0.026065 | -0.003831 | 0.038393 | 0.059885 | 0.21064 | -0.099689 | 0.051413 | 0.004938 | -0.0243 | 0.002095 | 0.1007 | -0.010564 | -0.19162 | 3.8645 | -115.8719 | 4.0019 | 3.9604 | 0.095858 | -115.8505 | -115.6997 | 3.7726 | -115.9082 | 4.0156 | 3.9399 | 0.16732 | -115.8096 | -115.9209 | 4.0026 | 4.0241 | 4.1749 | 3.9382 | -116.01 | 3.9663 | 4.0649 | 3.9537 | 3.9692 | -116.102
2982.6875 | 119.6548 | -106.5445 | 12.6892 | 1.4211e-13 | 0.024374 | 0.015919 | 0.010109 | -0.023148 | 0.0042113 | 0.22495 | 0.024171 | 0.03439 | -0.096424 | -0.0018611 | 0.0010705 | 0.065145 | 0.005985 | 0.028217 | 0.07502 | 0.087359 | 0.24727 | -0.058478 | 0.069728 | 0.023253 | -0.005985 | 0.020409 | 0.12359 | 0.039801 | -0.17788 | 106.486 | -12.6142 | 106.6096 | 106.5727 | 0.086695 | -12.6019 | -12.4419 | 106.3666 | -12.6688 | 106.6142 | 106.5385 | 0.1719 | -12.5656 | -12.6494 | 106.6195 | 106.6319 | 106.7918 | 106.5505 | -12.7477 | 106.5649 | 106.6681 | 106.5843 | 106.5677 | -12.8671
2984.4688 | 120.6253 | -106.4117 | 13.7238 | 1.4211e-13 | 0.024587 | 0.01656 | 0.010109 | -0.022935 | 0.0046387 | 0.23258 | 0.024385 | 0.034604 | -0.096637 | -0.0018611 | 0.00064308 | 0.074302 | 0.015142 | 0.028217 | 0.070441 | 0.1011 | 0.25185 | -0.031005 | 0.074307 | 0.023253 | -0.001407 | 0.029566 | 0.12359 | 0.030644 | -0.16415 | 106.3807 | -13.6533 | 106.486 | 106.44 | 0.059222 | -13.6227 | -13.4719 | 106.2476 | -13.6942 | 106.4861 | 106.4103 | 0.16274 | -13.6002 | -13.6931 | 106.4822 | 106.5128 | 106.6636 | 106.4269 | -13.7548 | 106.4413 | 106.5353 | 106.4424 | 106.435 | -13.8879
2986.1719 | 120.5109 | -105.7663 | 14.1495 | 1.4211e-13 | 0.024587 | 0.016346 | 0.010109 | -0.022721 | 0.0048523 | 0.24021 | 0.024598 | 0.035031 | -0.096637 | -0.0022885 | 0.00042948 | 0.07888 | 0.015142 | 0.037373 | 0.065863 | 0.1011 | 0.24269 | -0.021847 | 0.069728 | 0.027831 | 0.003172 | 0.034145 | 0.13275 | 0.026065 | -0.16415 | 105.7444 | -14.0836 | 105.8452 | 105.8037 | 0.05922 | -14.0484 | -13.9068 | 105.6021 | -14.1153 | 105.836 | 105.7695 | 0.16732 | -14.0167 | -14.1234 | 105.8322 | 105.8674 | 106.009 | 105.7814 | -14.1713 | 105.8004 | 105.899 | 105.7924 | 105.7941 | -14.3136
2987.9375 | 115.2969 | -47.9233 | 66.5451 | 1.4211e-13 | 0.024374 | 0.016133 | 0.0094682 | -0.022721 | 0.0037841 | 0.24021 | 0.024385 | 0.034604 | -0.09621 | -0.0020749 | 0.00064308 | 0.042253 | -0.012329 | 0.005325 | 0.052128 | 0.064464 | 0.22438 | -0.10885 | 0.069728 | 0.018674 | -0.015143 | 0.015831 | 0.12359 | 0.007751 | -0.17788 | 47.8144 | -66.493 | 47.9655 | 47.9286 | 0.11417 | -66.4806 | -66.3207 | 47.7454 | -66.5293 | 47.993 | 47.9081 | 0.16274 | -66.4215 | -66.5374 | 47.9754 | 47.9877 | 48.1477 | 47.9109 | -66.654 | 47.9391 | 48.0469 | 47.931 | 47.942 | -66.723
2989.6406 | 120.4102 | -0.38452 | 119.3115 | 1.4211e-13 | 0.024374 | 0.016133 | 0.0094682 | -0.023576 | 0.0046387 | 0.23258 | 0.024385 | 0.03439 | -0.096424 | -0.0022885 | 0.00042948 | 0.037675 | -0.026065 | -0.003831 | 0.038393 | 0.055306 | 0.20607 | -0.10427 | 0.046835 | 0.004938 | -0.033458 | 0.002095 | 0.1007 | -0.051771 | -0.18704 | 0.28025 | -119.2731 | 0.4222 | 0.38069 | 0.10044 | -119.2562 | -119.1055 | 0.19748 | -119.3094 | 0.43136 | 0.35106 | 0.15358 | -119.2108 | -119.3633 | 0.42291 | 0.43983 | 0.59059 | 0.35846 | -119.4158 | 0.38662 | 0.48522 | 0.33275 | 0.38946 | -119.4986
2991.3438 | 119.8196 | -0.737 | 118.309 | 1.4211e-13 | 0.024374 | 0.016133 | 0.0098956 | -0.023362 | 0.0048523 | 0.23258 | 0.024171 | 0.034604 | -0.096637 | -0.0020749 | 0.00042948 | 0.042253 | -0.021486 | -0.003831 | 0.047549 | 0.064464 | 0.21522 | -0.09511 | 0.046835 | 0.009516 | -0.028879 | 0.002095 | 0.10528 | -0.019721 | -0.1962 | 0.64189 | -118.2615 | 0.77925 | 0.73317 | 0.091279 | -118.2446 | -118.0938 | 0.5408 | -118.3069 | 0.78383 | 0.70812 | 0.16732 | -118.2037 | -118.3287 | 0.78455 | 0.80146 | 0.95222 | 0.71551 | -118.4041 | 0.73909 | 0.84228 | 0.71728 | 0.74652 | -118.5052
2993.0781 | 120.4193 | -0.54932 | 119.3619 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023148 | 0.0044249 | 0.22495 | 0.024385 | 0.034604 | -0.096637 | -0.0016475 | 0.00064308 | 0.037675 | -0.021486 | -0.012988 | 0.038393 | 0.059885 | 0.21522 | -0.11342 | 0.046835 | 0.000359 | -0.028879 | 0.002095 | 0.096121 | -0.005985 | -0.1962 | 0.43589 | -119.3235 | 0.58699 | 0.53633 | 0.10044 | -119.302 | -119.1467 | 0.35312 | -119.3598 | 0.59615 | 0.52044 | 0.16732 | -119.2658 | -119.3679 | 0.58771 | 0.6092 | 0.76454 | 0.52783 | -119.4753 | 0.55141 | 0.64544 | 0.54333 | 0.54968 | -119.5581
2994.7812 | 120.1584 | -1.2955 | 118.8538 | 1.4211e-13 | 0.024587 | 0.016346 | 0.0098956 | -0.023362 | 0.0048523 | 0.22495 | 0.024385 | 0.034604 | -0.096424 | -0.0018611 | 0.00064308 | 0.037675 | -0.021486 | -0.012988 | 0.047549 | 0.059885 | 0.20607 | -0.10885 | 0.037677 | -0.00422 | -0.0243 | 0.002095 | 0.1007 | -0.033457 | -0.18704 | 1.1866 | -118.8062 | 1.3331 | 1.2825 | 0.095859 | -118.7939 | -118.6477 | 1.1084 | -118.8517 | 1.3331 | 1.2712 | 0.16274 | -118.7531 | -118.8872 | 1.343 | 1.3554 | 1.5015 | 1.274 | -118.9626 | 1.2976 | 1.3962 | 1.262 | 1.2913 | -119.0408
2996.5156 | 120.3918 | -1.3824 | 119.0689 | 1.4211e-13 | 0.02416 | 0.01656 | 0.0098956 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.034604 | -0.096424 | -0.0018611 | 0.00085668 | 0.042253 | -0.026065 | -0.003831 | 0.038393 | 0.059885 | 0.21522 | -0.10885 | 0.042256 | 0.000359 | -0.033458 | 0.006674 | 0.1007 | -0.015142 | -0.19162 | 1.2736 | -119.0305 | 1.4247 | 1.3786 | 0.10502 | -119.009 | -118.8537 | 1.1908 | -119.0622 | 1.4247 | 1.349 | 0.15816 | -118.9682 | -119.0841 | 1.4208 | 1.4423 | 1.5977 | 1.3564 | -119.1778 | 1.3891 | 1.4831 | 1.3673 | 1.3828 | -119.2605
2998.25 | 120.4468 | -0.58136 | 119.3298 | 1.4211e-13 | 0.024374 | 0.016346 | 0.009682 | -0.023362 | 0.0048523 | 0.24021 | 0.024171 | 0.034818 | -0.096424 | -0.0022885 | 0.00085668 | 0.042253 | -0.026065 | -0.012988 | 0.042971 | 0.055306 | 0.20607 | -0.10885 | 0.042256 | 0.000359 | -0.0243 | 0.002095 | 0.086964 | -0.015142 | -0.1962 | 0.47251 | -119.2869 | 0.62361 | 0.56837 | 0.095859 | -119.2745 | -119.1238 | 0.38516 | -119.3277 | 0.62362 | 0.55706 | 0.1719 | -119.2429 | -119.345 | 0.62433 | 0.63667 | 0.78743 | 0.55529 | -119.4387 | 0.58345 | 0.66832 | 0.56622 | 0.58172 | -119.526
3000 | 120.5841 | -0.74158 | 119.5358 | 1.4211e-13 | 0.024587 | 0.015919 | 0.009682 | -0.023362 | 0.0046387 | 0.24021 | 0.024385 | 0.034818 | -0.096424 | -0.0016475 | 0.00085668 | 0.037675 | -0.021486 | -0.008409 | 0.042971 | 0.055306 | 0.20607 | -0.099689 | 0.046835 | 0.000359 | -0.033458 | 0.006674 | 0.096121 | -0.001407 | -0.18704 | 0.64189 | -119.4929 | 0.77925 | 0.73317 | 0.09128 | -119.4805 | -119.3298 | 0.55453 | -119.5292 | 0.78841 | 0.70812 | 0.15358 | -119.4397 | -119.5372 | 0.78455 | 0.79688 | 0.94764 | 0.72009 | -119.6355 | 0.74825 | 0.8377 | 0.74017 | 0.74194 | -119.7229
3001.7031 | 120.6116 | -0.82855 | 119.5587 | 1.4211e-13 | 0.02416 | 0.015919 | 0.010109 | -0.023362 | 0.0042113 | 0.23258 | 0.024385 | 0.034818 | -0.09621 | -0.0020749 | 0.00021588 | 0.037675 | -0.026065 | -0.012988 | 0.033814 | 0.069043 | 0.21064 | -0.099689 | 0.033099 | 0.009516 | -0.033458 | 0.002095 | 0.096121 | -0.033457 | -0.19162 | 0.72886 | -119.5249 | 0.86623 | 0.81556 | 0.086701 | -119.4897 | -119.3481 | 0.63693 | -119.5566 | 0.86165 | 0.79509 | 0.15816 | -119.4626 | -119.5922 | 0.86237 | 0.89759 | 1.0392 | 0.80249 | -119.6584 | 0.83065 | 0.92467 | 0.79509 | 0.83807 | -119.7503
3003.4062 | 119.6411 | -1.0757 | 119.0872 | 1.4211e-13 | 0.024374 | 0.016346 | 0.009682 | -0.023362 | 0.0046387 | 0.23258 | 0.024171 | 0.034818 | -0.096424 | -0.0016475 | 0.00064308 | 0.042253 | -0.021486 | -0.017566 | 0.042971 | 0.064464 | 0.21522 | -0.099689 | 0.037677 | 0.009516 | -0.028879 | 0.002095 | 0.096121 | -0.042614 | -0.19162 | 0.97606 | -119.0442 | 1.118 | 1.0582 | 0.082123 | -119.0228 | -118.872 | 0.88412 | -119.0851 | 1.1134 | 1.0469 | 0.16274 | -118.9911 | -119.1298 | 1.1187 | 1.1402 | 1.291 | 1.0543 | -119.1869 | 1.0778 | 1.1719 | 1.0331 | 1.0853 | -119.2788
3005.1406 | 120.2087 | -1.1261 | 119.2017 | 1.4211e-13 | 0.024587 | 0.016774 | 0.0098956 | -0.022935 | 0.0046387 | 0.24021 | 0.024598 | 0.034818 | -0.096424 | -0.0016475 | 0.00042948 | 0.037675 | -0.016908 | -0.003831 | 0.047549 | 0.059885 | 0.2198 | -0.099689 | 0.042256 | 0.004938 | -0.033458 | -0.002483 | 0.096121 | -0.051771 | -0.18246 | 1.0264 | -119.1541 | 1.1638 | 1.1223 | 0.095858 | -119.1418 | -118.9819 | 0.94364 | -119.2041 | 1.1684 | 1.0926 | 0.14901 | -119.1055 | -119.2534 | 1.1736 | 1.186 | 1.3459 | 1.1092 | -119.3013 | 1.1236 | 1.2222 | 1.0743 | 1.131 | -119.3841
3006.8438 | 119.5679 | -102.4475 | 16.4429 | 1.4211e-13 | 0.02416 | 0.016133 | 0.0098956 | -0.023148 | 0.0042113 | 0.22495 | 0.023957 | 0.034604 | -0.09621 | -0.0018611 | 0.00085668 | 0.065145 | 0.005985 | 0.014482 | 0.065863 | 0.087359 | 0.22896 | -0.081373 | 0.06515 | 0.023253 | -0.010564 | 0.024988 | 0.12817 | 0.012329 | -0.16873 | 102.3661 | -16.377 | 102.5127 | 102.462 | 0.095855 | -16.3555 | -16.2139 | 102.2788 | -16.4179 | 102.5127 | 102.4369 | 0.15816 | -16.3147 | -16.4305 | 102.5134 | 102.5349 | 102.6765 | 102.4535 | -16.5242 | 102.4725 | 102.5757 | 102.4598 | 102.4708 | -16.6116
3008.5469 | 120.4468 | -2.7191 | 117.5262 | 1.4211e-13 | 0.024374 | 0.016346 | 0.010109 | -0.023148 | 0.0044249 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0020749 | 0.00021588 | 0.037675 | -0.026065 | -0.008409 | 0.038393 | 0.064464 | 0.20607 | -0.099689 | 0.042256 | -0.00422 | -0.033458 | 0.002095 | 0.091543 | -0.05635 | -0.18246 | 2.6194 | -117.4879 | 2.7568 | 2.7107 | 0.09128 | -117.4618 | -117.3202 | 2.5367 | -117.5242 | 2.7614 | 2.6857 | 0.14901 | -117.4347 | -117.5826 | 2.7575 | 2.7836 | 2.9252 | 2.6931 | -117.6259 | 2.7212 | 2.8107 | 2.6628 | 2.7149 | -117.7087
3010.2812 | 88.4857 | -0.11902 | 86.2976 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023576 | 0.0048523 | 0.24784 | 0.024385 | 0.03439 | -0.096424 | -0.0018611 | 0.00042948 | 0.042253 | -0.026065 | -0.008409 | 0.042971 | 0.059885 | 0.21064 | -0.099689 | 0.055992 | 0.009516 | -0.019721 | 0.011252 | 0.10528 | -0.019721 | -0.18246 | 0.01933 | -86.2546 | 0.16127 | 0.11061 | 0.09128 | -86.2377 | -86.087 | -0.063445 | -86.2864 | 0.17501 | 0.099298 | 0.16274 | -86.1923 | -86.3173 | 0.16199 | 0.1789 | 0.32966 | 0.092954 | -86.3973 | 0.13027 | 0.2243 | 0.099298 | 0.12854 | -86.4801
3011.9844 | 111.7355 | -2.4765 | 89.6027 | 1.4211e-13 | 0.024374 | 0.016346 | 0.0094682 | -0.023148 | 0.0044249 | 0.24021 | 0.024171 | 0.034818 | -0.096424 | -0.0018611 | 0.00042948 | 0.033096 | -0.026065 | -0.012988 | 0.038393 | 0.059885 | 0.21522 | -0.10427 | 0.046835 | 0.004938 | -0.0243 | 0.002095 | 0.096121 | -0.0243 | -0.1962 | 2.3722 | -89.5643 | 2.5096 | 2.4635 | 0.09128 | -89.5428 | -89.3874 | 2.2803 | -89.6006 | 2.5233 | 2.4522 | 0.1719 | -89.5065 | -89.627 | 2.5149 | 2.5364 | 2.6917 | 2.4504 | -89.7069 | 2.4786 | 2.5726 | 2.4522 | 2.4814 | -89.7989
3013.7031 | 120.3369 | -81.4133 | 40.3427 | 1.4211e-13 | 0.025015 | 0.016346 | 0.0098956 | -0.023362 | 0.0044249 | 0.24021 | 0.024171 | 0.034177 | -0.096637 | -0.0018611 | 0.00064308 | 0.069723 | 0.001407 | 0.032795 | 0.065863 | 0.096516 | 0.23354 | -0.067636 | 0.074307 | 0.023253 | -0.005985 | 0.024988 | 0.12359 | 0.030644 | -0.16415 | 81.3456 | -40.2768 | 81.483 | 81.4461 | 0.10043 | -40.2462 | -40.1092 | 81.2491 | -40.3177 | 81.4876 | 81.4073 | 0.15816 | -40.2191 | -40.3121 | 81.4791 | 81.5098 | 81.6468 | 81.4147 | -40.4103 | 81.4383 | 81.5369 | 81.4439 | 81.4365 | -40.5069
3015.4219 | 120.5612 | -108.6411 | 11.2793 | 1.4211e-13 | 0.024801 | 0.01656 | 0.010109 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.03439 | -0.09621 | -0.0020749 | 0.00064308 | 0.074302 | 0.019721 | 0.028217 | 0.070441 | 0.1011 | 0.25185 | -0.081373 | 0.078886 | 0.027831 | 0.003172 | 0.038723 | 0.13275 | 0.030644 | -0.15957 | 108.5597 | -11.2089 | 108.7154 | 108.6693 | 0.10959 | -11.1782 | -11.0274 | 108.4815 | -11.2406 | 108.7199 | 108.6442 | 0.16274 | -11.1465 | -11.2487 | 108.7115 | 108.7421 | 108.8929 | 108.6608 | -11.3607 | 108.6798 | 108.7738 | 108.6717 | 108.6689 | -11.4389
3017.125 | 119.9432 | -0.14648 | 119.8883 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.23258 | 0.024812 | 0.034818 | -0.096637 | -0.0016475 | 0.00042948 | 0.033096 | -0.021486 | -0.012988 | 0.038393 | 0.059885 | 0.21522 | -0.099689 | 0.051413 | 0.000359 | -0.038036 | 0.011252 | 0.096121 | -0.028878 | -0.1962 | 0.046795 | -119.8499 | 0.17958 | 0.1335 | 0.086701 | -119.8284 | -119.6731 | -0.049716 | -119.8771 | 0.1979 | 0.10845 | 0.15816 | -119.7922 | -119.9172 | 0.18488 | 0.20637 | 0.36171 | 0.125 | -119.988 | 0.15774 | 0.24261 | 0.11761 | 0.14684 | -120.0845
3018.875 | 119.9615 | -0.16479 | 119.4168 | 1.4211e-13 | 0.024587 | 0.016133 | 0.0098956 | -0.022935 | 0.0046387 | 0.24021 | 0.024812 | 0.03439 | -0.09621 | -0.0016475 | 0.00064308 | 0.033096 | -0.030644 | -0.008409 | 0.024657 | 0.055306 | 0.21522 | -0.099689 | 0.060571 | 0.004938 | -0.033458 | 0.002095 | 0.096121 | -0.079243 | -0.19162 | 0.065106 | -119.3922 | 0.19789 | 0.15639 | 0.09128 | -119.3615 | -119.2016 | -0.026827 | -119.4147 | 0.22537 | 0.13134 | 0.15816 | -119.3207 | -119.4961 | 0.18945 | 0.2201 | 0.38002 | 0.13415 | -119.5165 | 0.16689 | 0.26092 | 0.085552 | 0.16973 | -119.6084
3020.5938 | 119.8471 | -0.022888 | 116.1575 | 1.4211e-13 | 0.024374 | 0.016133 | 0.009682 | -0.023148 | 0.0044249 | 0.24021 | 0.024171 | 0.034604 | -0.096637 | -0.0020749 | 0.00064308 | 0.033096 | -0.021486 | -0.008409 | 0.038393 | 0.055306 | 0.20607 | -0.099689 | 0.046835 | 0.000359 | -0.028879 | 0.011252 | 0.096121 | -0.051771 | -0.18704 | -0.076801 | -116.1191 | 0.055984 | 0.014479 | 0.09128 | -116.1022 | -115.9515 | -0.16415 | -116.1463 | 0.069723 | -0.005991 | 0.15816 | -116.0614 | -116.2093 | 0.061281 | 0.078194 | 0.22895 | 0.001402 | -116.2572 | 0.03414 | 0.11901 | -0.028883 | 0.023247 | -116.3446
3022.2969 | 120.4834 | -0.17395 | 119.7739 | 1.4211e-13 | 0.024374 | 0.016346 | 0.009682 | -0.023362 | 0.0048523 | 0.23258 | 0.024385 | 0.034604 | -0.096424 | -0.0018611 | 0.00085668 | 0.037675 | -0.026065 | -0.008409 | 0.042971 | 0.050727 | 0.21064 | -0.099689 | 0.042256 | 0.000359 | -0.0243 | 0.002095 | 0.10528 | -0.019721 | -0.19162 | 0.074261 | -119.7309 | 0.21163 | 0.16554 | 0.09128 | -119.7231 | -119.5632 | -0.017672 | -119.7718 | 0.21621 | 0.14965 | 0.16732 | -119.6686 | -119.7936 | 0.21692 | 0.22468 | 0.3846 | 0.14788 | -119.8736 | 0.17605 | 0.27923 | 0.15423 | 0.17431 | -119.9655
3024.0156 | 119.9844 | -0.15106 | 119.1879 | 1.4211e-13 | 0.024587 | 0.01656 | 0.010109 | -0.023576 | 0.0048523 | 0.24021 | 0.024598 | 0.034604 | -0.096424 | -0.0018611 | 0.00064308 | 0.033096 | -0.021486 | -0.003831 | 0.038393 | 0.064464 | 0.21064 | -0.099689 | 0.055992 | 0.004938 | -0.033458 | -0.002483 | 0.1007 | -0.047193 | -0.19162 | 0.051373 | -119.1495 | 0.18416 | 0.14723 | 0.095858 | -119.1235 | -118.9773 | -0.04056 | -119.1904 | 0.20705 | 0.1176 | 0.15816 | -119.0872 | -119.2351 | 0.18945 | 0.21553 | 0.36171 | 0.12958 | -119.2876 | 0.14858 | 0.25176 | 0.10387 | 0.156 | -119.3795
3025.7188 | 89.8773 | -46.376 | 72.3495 | 1.4211e-13 | 0.024374 | 0.016133 | 0.009682 | -0.023362 | 0.0046387 | 0.24021 | 0.024598 | 0.034818 | -0.096637 | -0.0020749 | 0.00064308 | 0.060567 | 0.001407 | 0.009904 | 0.056706 | 0.08278 | 0.23354 | -0.076794 | 0.055992 | 0.018674 | -0.010564 | 0.015831 | 0.12359 | 0.003172 | -0.16873 | 46.2992 | -72.2928 | 46.4366 | 46.3859 | 0.086698 | -72.2668 | -72.116 | 46.2073 | -72.3337 | 46.432 | 46.3655 | 0.15816 | -72.226 | -72.3464 | 46.4327 | 46.4588 | 46.6096 | 46.3774 | -72.4263 | 46.3919 | 46.4996 | 46.3792 | 46.3947 | -72.5183
3027.4531 | 119.5038 | -3.6255 | 87.6709 | 1.4211e-13 | 0.024587 | 0.015919 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024598 | 0.034177 | -0.096424 | -0.0020749 | 0.00042948 | 0.037675 | -0.021486 | -0.003831 | 0.029236 | 0.059885 | 0.21064 | -0.10427 | 0.046835 | 0.004938 | -0.028879 | 0.002095 | 0.091543 | -0.028878 | -0.18246 | 3.5212 | -87.6417 | 3.6632 | 3.6217 | 0.10044 | -87.611 | -87.4603 | 3.443 | -87.6688 | 3.6723 | 3.5966 | 0.15358 | -87.5794 | -87.6998 | 3.6547 | 3.6854 | 3.8361 | 3.604 | -87.7752 | 3.6276 | 3.717 | 3.5966 | 3.6304 | -87.8534
3029.1719 | 111.3785 | -21.0571 | 97.8882 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023148 | 0.0050659 | 0.23258 | 0.024385 | 0.034604 | -0.096424 | -0.0020749 | 0.00042948 | 0.042253 | -0.007751 | -0.003831 | 0.042971 | 0.064464 | 0.22896 | -0.099689 | 0.046835 | 0.009516 | -0.019721 | 0.011252 | 0.1007 | -0.010564 | -0.18246 | 20.9574 | -97.8452 | 21.0994 | 21.0533 | 0.095858 | -97.8237 | -97.6592 | 20.8747 | -97.8769 | 21.104 | 21.0374 | 0.16274 | -97.7875 | -97.8987 | 21.1001 | 21.1216 | 21.2861 | 21.0494 | -97.9879 | 21.0684 | 21.1578 | 21.0466 | 21.0666 | -98.0706
3030.9375 | 120.3094 | -117.3615 | 2.623 | 1.4211e-13 | 0.024587 | 0.015919 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.024812 | 0.034818 | -0.096637 | -0.0020749 | 0.00021588 | 0.07888 | 0.019721 | 0.028217 | 0.07502 | 0.1011 | 0.24727 | -0.053899 | 0.078886 | 0.027831 | 0.007751 | 0.043302 | 0.12817 | 0.035222 | -0.15499 | 117.3076 | -2.548 | 117.4403 | 117.3897 | 0.082116 | -2.5219 | -2.3757 | 117.2065 | -2.5797 | 117.4403 | 117.3692 | 0.16274 | -2.4948 | -2.5878 | 117.4365 | 117.4625 | 117.6087 | 117.3812 | -2.6769 | 117.4048 | 117.4896 | 117.3967 | 117.3893 | -2.778
3032.6406 | 118.634 | -6.8024 | 95.3384 | 1.4211e-13 | 0.024374 | 0.016133 | 0.0098956 | -0.023362 | 0.0044249 | 0.24021 | 0.024385 | 0.034604 | -0.09621 | -0.0022885 | 0.00085668 | 0.042253 | -0.016908 | 0.000747 | 0.042971 | 0.064464 | 0.2198 | -0.10885 | 0.051413 | 0.009516 | -0.028879 | 0.011252 | 0.10986 | -0.001407 | -0.18246 | 6.6935 | -95.2955 | 6.8446 | 6.8031 | 0.10959 | -95.274 | -95.1186 | 6.6199 | -95.3272 | 6.8538 | 6.7735 | 0.15358 | -95.2286 | -95.3398 | 6.8453 | 6.8668 | 7.0222 | 6.7855 | -95.4473 | 6.8136 | 6.9122 | 6.801 | 6.8119 | -95.5209
3034.3594 | 94.6335 | -0.32959 | 85.5606 | 1.4211e-13 | 0.024587 | 0.016133 | 0.0098956 | -0.023362 | 0.0048523 | 0.24784 | 0.024171 | 0.034818 | -0.096424 | -0.0016475 | 0.00085668 | 0.042253 | -0.026065 | 0.000747 | 0.042971 | 0.064464 | 0.21522 | -0.090531 | 0.046835 | 0.000359 | -0.028879 | 0.002095 | 0.096121 | -0.033457 | -0.18246 | 0.23906 | -85.5176 | 0.37184 | 0.33034 | 0.091278 | -85.4961 | -85.3454 | 0.14713 | -85.5585 | 0.37643 | 0.30071 | 0.15358 | -85.4645 | -85.5941 | 0.37256 | 0.39405 | 0.54481 | 0.30352 | -85.6511 | 0.33169 | 0.42571 | 0.29613 | 0.32995 | -85.7431
3036.0781 | 120.0989 | -7.4249 | 111.9141 | 1.4211e-13 | 0.024374 | 0.016346 | 0.0098956 | -0.023576 | 0.0044249 | 0.23258 | 0.024385 | 0.034818 | -0.09621 | -0.0020749 | 0.00085668 | 0.037675 | -0.021486 | -0.003831 | 0.038393 | 0.059885 | 0.21522 | -0.09511 | 0.046835 | 0.000359 | -0.028879 | -0.002483 | 0.1007 | -0.038035 | -0.18704 | 7.3298 | -111.8757 | 7.4626 | 7.4211 | 0.091279 | -111.8542 | -111.6988 | 7.2379 | -111.9165 | 7.4718 | 7.396 | 0.15816 | -111.8134 | -111.9521 | 7.4633 | 7.4848 | 7.6402 | 7.4034 | -112.0092 | 7.4224 | 7.5256 | 7.3869 | 7.4253 | -112.1011
3037.7812 | 120.5933 | -6.752 | 112.9074 | 1.4211e-13 | 0.024587 | 0.015919 | 0.009682 | -0.023362 | 0.0044249 | 0.24021 | 0.024598 | 0.035245 | -0.096424 | -0.0018611 | 0.00064308 | 0.042253 | -0.012329 | -0.003831 | 0.042971 | 0.059885 | 0.22438 | -0.090531 | 0.051413 | 0.004938 | -0.019721 | 0.002095 | 0.1007 | -0.0243 | -0.18704 | 6.6615 | -112.8644 | 6.7943 | 6.7482 | 0.0867 | -112.8475 | -112.683 | 6.565 | -112.9053 | 6.8034 | 6.7323 | 0.16732 | -112.8067 | -112.9317 | 6.795 | 6.8119 | 6.9764 | 6.7397 | -112.9979 | 6.7541 | 6.8527 | 6.7277 | 6.757 | -113.0945
3039.5 | 119.5862 | -35.0601 | 84.3658 | 1.4211e-13 | 0.025015 | 0.016346 | 0.009682 | -0.022935 | 0.0044249 | 0.24021 | 0.024171 | 0.034604 | -0.096424 | -0.0022885 | 0.00042948 | 0.060567 | -0.012329 | 0.009904 | 0.047549 | 0.073622 | 0.22438 | -0.085952 | 0.06515 | 0.014095 | -0.010564 | 0.020409 | 0.11444 | 0.016908 | -0.17331 | 34.9742 | -84.3183 | 35.1207 | 35.07 | 0.095856 | -84.2922 | -84.1415 | 34.8868 | -84.3454 | 35.1253 | 35.0496 | 0.16274 | -84.2514 | -84.3489 | 35.1077 | 35.1337 | 35.2845 | 35.0478 | -84.4518 | 35.0805 | 35.1746 | 35.077 | 35.0742 | -84.5392
3041.2344 | 120.2774 | -20.1828 | 99.8016 | 1.4211e-13 | 0.024374 | 0.016346 | 0.0098956 | -0.023362 | 0.0044249 | 0.24021 | 0.024385 | 0.034818 | -0.096851 | -0.0020749 | 0.00085668 | 0.046831 | -0.012329 | 0.005325 | 0.038393 | 0.064464 | 0.21522 | -0.090531 | 0.051413 | 0.004938 | -0.0243 | 0.006674 | 0.10528 | -0.019721 | -0.18246 | 20.0923 | -99.7632 | 20.2296 | 20.1881 | 0.095856 | -99.7372 | -99.5864 | 20.0003 | -99.795 | 20.2342 | 20.1585 | 0.15816 | -99.6964 | -99.8214 | 20.2212 | 20.2473 | 20.398 | 20.1705 | -99.8922 | 20.1895 | 20.2881 | 20.1631 | 20.1877 | -99.9841
3042.9844 | 120.3506 | -39.6194 | 80.3696 | 1.4211e-13 | 0.024374 | 0.016133 | 0.0094682 | -0.023148 | 0.0046387 | 0.24784 | 0.024598 | 0.034604 | -0.096637 | -0.0018611 | 0.00042948 | 0.05141 | -0.007751 | 0.009904 | 0.047549 | 0.073622 | 0.22438 | -0.090531 | 0.055992 | 0.004938 | -0.019721 | 0.011252 | 0.10528 | 0.007751 | -0.17331 | 39.5289 | -80.322 | 39.6709 | 39.6294 | 0.10043 | -80.2959 | -80.1452 | 39.4461 | -80.3583 | 39.6754 | 39.5997 | 0.15358 | -80.2643 | -80.3618 | 39.667 | 39.6931 | 39.8438 | 39.6117 | -80.4601 | 39.6307 | 39.7247 | 39.6272 | 39.6244 | -80.5429
3044.6875 | 115.0726 | -24.4492 | 95.7916 | 1.4211e-13 | 0.024587 | 0.016346 | 0.0094682 | -0.022935 | 0.0046387 | 0.23258 | 0.024598 | 0.03439 | -0.09621 | -0.0022885 | 0.00064308 | 0.05141 | -0.016908 | -0.003831 | 0.047549 | 0.069043 | 0.22438 | -0.09511 | 0.051413 | 0.000359 | -0.019721 | 0.006674 | 0.1007 | 0.016908 | -0.17788 | 24.354 | -95.7441 | 24.5006 | 24.4453 | 0.091279 | -95.7226 | -95.5672 | 24.2713 | -95.785 | 24.5006 | 24.4294 | 0.15816 | -95.6909 | -95.7747 | 24.4967 | 24.5182 | 24.6735 | 24.4322 | -95.8867 | 24.4558 | 24.5499 | 24.4661 | 24.4495 | -95.9695
3046.4062 | 105.8441 | -22.9477 | 97.1512 | 1.4211e-13 | 0.025015 | 0.016346 | 0.009682 | -0.023576 | 0.0048523 | 0.22495 | 0.024385 | 0.034818 | -0.096637 | -0.0020749 | 0.00085668 | 0.037675 | -0.012329 | 0.005325 | 0.047549 | 0.069043 | 0.2198 | -0.090531 | 0.051413 | 0.004938 | -0.028879 | 0.002095 | 0.10986 | 0.003172 | -0.18246 | 22.8572 | -97.1036 | 22.9854 | 22.953 | 0.095856 | -97.0821 | -96.9314 | 22.7652 | -97.1491 | 22.9991 | 22.9188 | 0.15358 | -97.0413 | -97.148 | 22.9952 | 23.0167 | 23.1675 | 22.9354 | -97.2417 | 22.9498 | 23.0576 | 22.9509 | 22.9526 | -97.3336
3048.1094 | 120.1996 | -6.4178 | 113.1088 | 1.4211e-13 | 0.024587 | 0.016133 | 0.0098956 | -0.023789 | 0.0048523 | 0.23258 | 0.024385 | 0.035031 | -0.096424 | -0.0020749 | 0.00085668 | 0.037675 | -0.021486 | 0.000747 | 0.042971 | 0.059885 | 0.21064 | -0.090531 | 0.042256 | 0.004938 | -0.033458 | -0.002483 | 0.096121 | -0.001407 | -0.18704 | 6.3273 | -113.0659 | 6.4555 | 6.4186 | 0.091278 | -113.0489 | -112.8982 | 6.2308 | -113.1113 | 6.4601 | 6.3844 | 0.15358 | -113.0127 | -113.1102 | 6.4608 | 6.4777 | 6.6285 | 6.3964 | -113.1994 | 6.4154 | 6.514 | 6.4164 | 6.4228 | -113.2959
3049.875 | 120.5063 | -5.983 | 114.1205 | 1.4211e-13 | 0.024587 | 0.016346 | 0.0098956 | -0.023148 | 0.0046387 | 0.23258 | 0.024385 | 0.034604 | -0.096424 | -0.0020749 | 0.00064308 | 0.042253 | -0.016908 | -0.003831 | 0.047549 | 0.059885 | 0.2198 | -0.099689 | 0.042256 | 0.000359 | -0.028879 | -0.002483 | 0.091543 | -0.019721 | -0.19162 | 5.8833 | -114.0729 | 6.0252 | 5.9791 | 0.095858 | -114.0606 | -113.9007 | 5.7913 | -114.123 | 6.0252 | 5.9541 | 0.16274 | -114.0289 | -114.1402 | 6.0305 | 6.0429 | 6.2028 | 5.9661 | -114.2202 | 5.9805 | 6.0745 | 5.9633 | 5.9833 | -114.3121
3051.5781 | 119.9799 | -6.4407 | 113.9053 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.035031 | -0.09621 | -0.0025021 | 0.00042948 | 0.033096 | -0.026065 | -0.003831 | 0.042971 | 0.055306 | 0.2198 | -0.10885 | 0.042256 | 0.000359 | -0.0243 | -0.002483 | 0.096121 | -0.042614 | -0.18704 | 6.3319 | -113.8624 | 6.4738 | 6.4369 | 0.10502 | -113.85 | -113.6855 | 6.2537 | -113.9078 | 6.483 | 6.4164 | 0.16274 | -113.8092 | -113.9479 | 6.4837 | 6.496 | 6.6605 | 6.4147 | -114.0142 | 6.4383 | 6.5369 | 6.3981 | 6.4411 | -114.0924
3053.2969 | 120.5933 | -4.7012 | 115.2054 | 1.4211e-13 | 0.024587 | 0.016133 | 0.009682 | -0.023362 | 0.0050659 | 0.23258 | 0.024385 | 0.034604 | -0.096424 | -0.0020749 | 0.00021588 | 0.033096 | -0.021486 | 0.000747 | 0.038393 | 0.059885 | 0.21064 | -0.090531 | 0.046835 | -0.008798 | -0.028879 | 0.002095 | 0.1007 | -0.038035 | -0.18704 | 4.6107 | -115.167 | 4.7343 | 4.702 | 0.091278 | -115.1455 | -114.9947 | 4.5142 | -115.2033 | 4.7481 | 4.6724 | 0.15816 | -115.1047 | -115.2434 | 4.7396 | 4.7611 | 4.9119 | 4.6797 | -115.2959 | 4.7033 | 4.8019 | 4.6632 | 4.6924 | -115.3924
3055.0156 | 120.6253 | -38.7589 | 81.3812 | 1.4211e-13 | 0.024801 | 0.016346 | 0.009682 | -0.022935 | 0.0050659 | 0.24021 | 0.024598 | 0.034604 | -0.096424 | -0.0018611 | 0.00042948 | 0.046831 | -0.016908 | 0.000747 | 0.038393 | 0.064464 | 0.2198 | -0.118 | 0.051413 | -0.00422 | -0.0243 | -0.002483 | 0.1007 | -0.033457 | -0.17788 | 38.6408 | -81.3428 | 38.8057 | 38.7596 | 0.11875 | -81.3168 | -81.1614 | 38.581 | -81.3837 | 38.8103 | 38.7346 | 0.15358 | -81.2805 | -81.4147 | 38.7972 | 38.8233 | 38.9787 | 38.7419 | -81.4992 | 38.7564 | 38.8596 | 38.7254 | 38.7546 | -81.5591
3056.7344 | 120.5978 | -3.4607 | 117.009 | 1.4211e-13 | 0.024374 | 0.016133 | 0.0094682 | -0.022935 | 0.0046387 | 0.23258 | 0.024598 | 0.034604 | -0.096424 | -0.0020749 | 0.00042948 | 0.033096 | -0.016908 | -0.008409 | 0.042971 | 0.055306 | 0.21522 | -0.11342 | 0.037677 | -0.00422 | -0.028879 | -0.007062 | 0.1007 | -0.070086 | -0.18704 | 3.3473 | -116.966 | 3.4938 | 3.4523 | 0.10502 | -116.9537 | -116.7937 | 3.2736 | -117.016 | 3.4984 | 3.4318 | 0.15816 | -116.9083 | -117.0791 | 3.5037 | 3.516 | 3.6759 | 3.4438 | -117.1224 | 3.4536 | 3.5614 | 3.3906 | 3.4565 | -117.196
3058.4844 | 120.0623 | -119.6457 | 0.064087 | 1.4211e-13 | 0.025015 | 0.016346 | 0.010109 | -0.023148 | 0.0044249 | 0.24021 | 0.024171 | 0.034818 | -0.096851 | -0.0022885 | 0.00064308 | 0.074302 | 0.019721 | 0.028217 | 0.070441 | 0.1011 | 0.24727 | -0.044742 | 0.097201 | 0.036989 | 0.007751 | 0.043302 | 0.13733 | 0.039801 | -0.14583 | 119.6009 | 0.006354 | 119.72 | 119.6739 | 0.072959 | 0.037008 | 0.18319 | 119.4999 | -0.020785 | 119.7429 | 119.6534 | 0.15358 | 0.073242 | -0.024286 | 119.7161 | 119.7468 | 119.893 | 119.6654 | -0.10883 | 119.689 | 119.783 | 119.6855 | 119.6827 | -0.20992
3060.1875 | 120.4422 | -120.0531 | 0.064087 | 1.4211e-13 | 0.024587 | 0.01656 | 0.010109 | -0.023148 | 0.0050659 | 0.23258 | 0.024598 | 0.03439 | -0.096637 | -0.0022885 | 0.00042948 | 0.07888 | 0.019721 | 0.037373 | 0.07502 | 0.1011 | 0.24727 | -0.035584 | 0.088043 | 0.046146 | 0.007751 | 0.038723 | 0.14191 | 0.039801 | -0.15041 | 120.0175 | 0.010933 | 120.132 | 120.0905 | 0.072957 | 0.037008 | 0.18319 | 119.9027 | -0.025364 | 120.1411 | 120.0609 | 0.15816 | 0.07782 | -0.024286 | 120.1281 | 120.1542 | 120.3004 | 120.0728 | -0.099671 | 120.0918 | 120.195 | 120.0929 | 120.0992 | -0.2145
3061.9375 | 120.5246 | -120.2042 | 0.10071 | 1.4211e-13 | 0.024801 | 0.016346 | 0.009682 | -0.023148 | 0.0044249 | 0.22495 | 0.024385 | 0.034818 | -0.096424 | -0.0020749 | 0.0010705 | 0.07888 | 0.019721 | 0.028217 | 0.07502 | 0.096516 | 0.25185 | -0.072215 | 0.078886 | 0.027831 | 0.003172 | 0.043302 | 0.13733 | 0.048958 | -0.15499 | 120.1319 | -0.025688 | 120.283 | 120.2324 | 0.10043 | -0.004192 | 0.15114 | 120.0492 | -0.057406 | 120.283 | 120.2073 | 0.15816 | 0.036621 | -0.05175 | 120.2792 | 120.3007 | 120.456 | 120.2239 | -0.17292 | 120.2475 | 120.3415 | 120.2531 | 120.232 | -0.2557
3063.6875 | 120.4193 | -120.195 | 0.21515 | 1.4211e-13 | 0.024801 | 0.016346 | 0.010109 | -0.023362 | 0.0042113 | 0.24021 | 0.024385 | 0.03439 | -0.096424 | -0.0020749 | 0.00064308 | 0.083459 | 0.0243 | 0.028217 | 0.07502 | 0.10567 | 0.25185 | -0.040163 | 0.088043 | 0.036989 | 0.01233 | 0.043302 | 0.13733 | 0.039801 | -0.14125 | 120.1548 | -0.14013 | 120.2785 | 120.2232 | 0.06838 | -0.10948 | 0.036703 | 120.0538 | -0.17185 | 120.2831 | 120.2073 | 0.15358 | -0.07782 | -0.17535 | 120.27 | 120.3007 | 120.4469 | 120.2193 | -0.25531 | 120.2383 | 120.3323 | 120.2348 | 120.232 | -0.3564
3065.4062 | 119.9158 | -119.4122 | 0.10529 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.022935 | 0.0048523 | 0.24784 | 0.024385 | 0.034818 | -0.096637 | -0.0020749 | 0.00064308 | 0.074302 | 0.010564 | 0.028217 | 0.084176 | 0.1011 | 0.25643 | -0.053899 | 0.083464 | 0.036989 | 0.01233 | 0.034145 | 0.13733 | 0.035222 | -0.15041 | 119.3583 | -0.02111 | 119.4865 | 119.4404 | 0.082116 | -0.004191 | 0.15115 | 119.2618 | -0.071141 | 119.4957 | 119.4246 | 0.16274 | 0.032043 | -0.070064 | 119.4964 | 119.5133 | 119.6687 | 119.4228 | -0.15919 | 119.4464 | 119.5496 | 119.4475 | 119.4492 | -0.2557
3067.1094 | 120.0714 | -119.6503 | 0.20142 | 1.4211e-13 | 0.025015 | 0.016346 | 0.010323 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.034604 | -0.096637 | -0.0020749 | 0.00085668 | 0.074302 | 0.015142 | 0.032795 | 0.079598 | 0.10567 | 0.25643 | -0.044742 | 0.078886 | 0.036989 | 0.003172 | 0.038723 | 0.14191 | 0.035222 | -0.15041 | 119.6055 | -0.12182 | 119.7246 | 119.6831 | 0.077537 | -0.095742 | 0.055015 | 119.4999 | -0.16269 | 119.7292 | 119.6534 | 0.15358 | -0.059509 | -0.16619 | 119.7299 | 119.7559 | 119.9067 | 119.6654 | -0.24616 | 119.689 | 119.7922 | 119.6855 | 119.6873 | -0.35183
3068.875 | 119.8975 | -119.4901 | 0.068665 | 1.4211e-13 | 0.024587 | 0.016346 | 0.009682 | -0.023362 | 0.0048523 | 0.24021 | 0.024171 | 0.034604 | -0.096424 | -0.0025021 | 0.00064308 | 0.07888 | 0.019721 | 0.028217 | 0.070441 | 0.10567 | 0.25185 | -0.072215 | 0.078886 | 0.03241 | 0.007751 | 0.038723 | 0.13733 | 0.044379 | -0.15041 | 119.4178 | 0.001776 | 119.5689 | 119.5183 | 0.10043 | 0.037009 | 0.18319 | 119.3396 | -0.029942 | 119.5689 | 119.4978 | 0.15816 | 0.068664 | -0.024286 | 119.5605 | 119.5957 | 119.7419 | 119.5098 | -0.14088 | 119.5288 | 119.6274 | 119.5344 | 119.5225 | -0.21908
3070.5781 | 120.2911 | -119.9341 | 0.091553 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.022935 | 0.0046387 | 0.24021 | 0.024385 | 0.034818 | -0.096424 | -0.0025021 | 0.00064308 | 0.083459 | 0.019721 | 0.037373 | 0.070441 | 0.1011 | 0.26101 | -0.053899 | 0.083464 | 0.036989 | 0.003172 | 0.034145 | 0.13733 | 0.035222 | -0.14583 | 119.8802 | -0.021112 | 120.0175 | 119.9715 | 0.091272 | 0.009542 | 0.16946 | 119.7882 | -0.057408 | 120.0175 | 119.9373 | 0.149 | 0.045776 | -0.056331 | 120.0045 | 120.0352 | 120.1951 | 119.9538 | -0.14545 | 119.9682 | 120.0714 | 119.9693 | 119.9711 | -0.23739
3072.2812 | 120.2866 | -120.0485 | 0.15106 | 1.4211e-13 | 0.024801 | 0.016346 | 0.010109 | -0.023148 | 0.0042113 | 0.24784 | 0.024385 | 0.034604 | -0.096637 | -0.0025021 | 0.00064308 | 0.07888 | 0.019721 | 0.037373 | 0.079598 | 0.1011 | 0.25643 | -0.049321 | 0.078886 | 0.027831 | 0.003172 | 0.043302 | 0.13275 | 0.035222 | -0.15499 | 119.9992 | -0.071464 | 120.1274 | 120.0859 | 0.086694 | -0.049967 | 0.10537 | 119.8935 | -0.10776 | 120.1274 | 120.0517 | 0.15816 | -0.018312 | -0.11584 | 120.1281 | 120.1496 | 120.305 | 120.0682 | -0.20038 | 120.0918 | 120.1813 | 120.0837 | 120.0764 | -0.30605
3074 | 120.3781 | -120.0668 | 0.059509 | 1.4211e-13 | 0.024587 | 0.016133 | 0.010109 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.034604 | -0.096424 | -0.0022885 | 0.00064308 | 0.074302 | 0.015142 | 0.037373 | 0.079598 | 0.1011 | 0.24269 | -0.044742 | 0.083464 | 0.027831 | 0.007751 | 0.043302 | 0.13733 | 0.039801 | -0.15041 | 120.0221 | 0.020089 | 120.1411 | 120.1042 | 0.082115 | 0.041586 | 0.18319 | 119.9164 | -0.016207 | 120.1503 | 120.0746 | 0.15816 | 0.07782 | -0.019708 | 120.1464 | 120.1679 | 120.3095 | 120.082 | -0.10425 | 120.1101 | 120.2042 | 120.1066 | 120.0947 | -0.20992
3075.7344 | 120.4285 | -119.8837 | 0.27924 | 1.4211e-13 | 0.024374 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.22495 | 0.024598 | 0.034604 | -0.096424 | -0.0022885 | 0.00042948 | 0.07888 | 0.028878 | 0.041952 | 0.079598 | 0.096516 | 0.25185 | -0.021847 | 0.074307 | 0.027831 | -0.001407 | 0.029566 | 0.13275 | 0.026065 | -0.15041 | 119.8619 | -0.19964 | 119.9626 | 119.9257 | 0.063799 | -0.18272 | -0.027384 | 119.7333 | -0.24967 | 119.958 | 119.8823 | 0.149 | -0.14649 | -0.25317 | 119.9633 | 119.9802 | 120.1356 | 119.9126 | -0.30108 | 119.9133 | 120.0165 | 119.9098 | 119.9116 | -0.42965
3077.6562 | 119.165 | -118.6615 | 0.19684 | 1.4211e-13 | 0.024374 | 0.016133 | 0.009682 | -0.023148 | 0.0039977 | 0.21732 | 0.024171 | 0.034818 | -0.096851 | -0.0020749 | 0.00085668 | 0.060567 | 0.001407 | 0.009904 | 0.056706 | 0.087359 | 0.23812 | -0.072215 | 0.042256 | 0.004938 | -0.028879 | 0.002095 | 0.1007 | -0.042614 | -0.17331 | 118.5893 | -0.14013 | 118.7221 | 118.6714 | 0.082119 | -0.10948 | 0.041279 | 118.4882 | -0.19474 | 118.7038 | 118.6326 | 0.14443 | -0.096138 | -0.23945 | 118.7182 | 118.7489 | 118.8996 | 118.6629 | -0.26905 | 118.6636 | 118.7622 | 118.6189 | 118.6664 | -0.37014
3079.5 | 120.3415 | -120.0943 | 0.091553 | 1.4211e-13 | 0.024587 | 0.016133 | 0.010109 | -0.023362 | 0.0048523 | 0.24784 | 0.024598 | 0.034818 | -0.096637 | -0.0025021 | 0.00064308 | 0.07888 | 0.015142 | 0.041952 | 0.084176 | 0.10567 | 0.25185 | -0.058478 | 0.083464 | 0.027831 | 0.003172 | 0.038723 | 0.13275 | 0.039801 | -0.15041 | 120.0358 | -0.007377 | 120.1732 | 120.1363 | 0.10043 | 0.014121 | 0.1603 | 119.9439 | -0.05283 | 120.1778 | 120.0975 | 0.15358 | 0.041197 | -0.051752 | 120.1785 | 120.2 | 120.3462 | 120.1094 | -0.15003 | 120.133 | 120.227 | 120.1341 | 120.1221 | -0.24196
3081.2344 | 120.488 | -120.1538 | 0.07782 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.023362 | 0.0048523 | 0.23258 | 0.024598 | 0.034604 | -0.096637 | -0.0022885 | 0.00085668 | 0.074302 | 0.0243 | 0.032795 | 0.07502 | 0.096516 | 0.25185 | -0.035584 | 0.078886 | 0.03241 | 0.003172 | 0.034145 | 0.12359 | 0.035222 | -0.15957 | 120.1182 | -0.0028 | 120.2281 | 120.1866 | 0.068379 | 0.018696 | 0.17403 | 119.9942 | -0.043675 | 120.2327 | 120.157 | 0.16274 | 0.045773 | -0.042598 | 120.2288 | 120.2503 | 120.4057 | 120.1781 | -0.1134 | 120.188 | 120.2774 | 120.189 | 120.1862 | -0.23739
3083.0156 | 120.5109 | -120.2179 | 0.091553 | 1.4211e-13 | 0.024801 | 0.016346 | 0.009682 | -0.023362 | 0.0048523 | 0.24021 | 0.024598 | 0.034604 | -0.095996 | -0.0022885 | 0.00064308 | 0.07888 | 0.0243 | 0.041952 | 0.07502 | 0.096516 | 0.24727 | -0.026426 | 0.078886 | 0.023253 | 0.003172 | 0.034145 | 0.12817 | 0.030644 | -0.14125 | 120.1915 | -0.016533 | 120.2968 | 120.2598 | 0.068378 | 0.004963 | 0.15572 | 120.0766 | -0.057408 | 120.2968 | 120.2211 | 0.14443 | 0.036619 | -0.060909 | 120.2929 | 120.3144 | 120.4652 | 120.2422 | -0.11798 | 120.252 | 120.3461 | 120.2485 | 120.2411 | -0.23281
3084.8125 | 120.4376 | -120.2957 | 0.10529 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.023362 | 0.0046387 | 0.24021 | 0.024598 | 0.034604 | -0.096637 | -0.0020749 | 0.00064308 | 0.074302 | 0.019721 | 0.032795 | 0.070441 | 0.1011 | 0.24727 | -0.00811 | 0.078886 | 0.023253 | 0.007751 | 0.034145 | 0.12359 | 0.026065 | -0.15041 | 120.2876 | -0.034845 | 120.37 | 120.3285 | 0.040905 | -0.004191 | 0.14199 | 120.1453 | -0.071141 | 120.3746 | 120.3035 | 0.15816 | 0.018307 | -0.079221 | 120.3662 | 120.3968 | 120.543 | 120.3154 | -0.1134 | 120.3299 | 120.4193 | 120.3218 | 120.319 | -0.2557
3086.625 | 120.5475 | -120.3186 | 0.07782 | 1.4211e-13 | 0.025015 | 0.015919 | 0.0098956 | -0.023362 | 0.0048523 | 0.24021 | 0.024598 | 0.034604 | -0.096637 | -0.0022885 | 0.00064308 | 0.088037 | 0.015142 | 0.041952 | 0.079598 | 0.096516 | 0.25643 | -0.026426 | 0.078886 | 0.03241 | 0.007751 | 0.034145 | 0.13275 | 0.030644 | -0.15041 | 120.2922 | 0.001778 | 120.4066 | 120.3606 | 0.068378 | 0.018696 | 0.17861 | 120.1682 | -0.043675 | 120.3975 | 120.3264 | 0.15816 | 0.05493 | -0.047176 | 120.3982 | 120.4151 | 120.575 | 120.3337 | -0.10425 | 120.3527 | 120.4514 | 120.3492 | 120.351 | -0.22823
3088.3438 | 120.6299 | -120.3278 | 0.050354 | 1.4211e-13 | 0.024801 | 0.016133 | 0.009682 | -0.023148 | 0.0050659 | 0.22495 | 0.024598 | 0.034604 | -0.096424 | -0.0020749 | 0.00064308 | 0.069723 | 0.015142 | 0.041952 | 0.084176 | 0.10567 | 0.25185 | -0.053899 | 0.078886 | 0.036989 | -0.001407 | 0.024988 | 0.11901 | 0.035222 | -0.14583 | 120.2739 | 0.033822 | 120.3975 | 120.3697 | 0.095851 | 0.05532 | 0.2015 | 120.1819 | -0.025366 | 120.4066 | 120.3264 | 0.14443 | 0.06866 | -0.015132 | 120.4119 | 120.4334 | 120.5796 | 120.3429 | -0.10425 | 120.3527 | 120.4468 | 120.363 | 120.3647 | -0.19619
3090.125 | 120.5841 | -120.3918 | 0.09613 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023576 | 0.0046387 | 0.24021 | 0.024385 | 0.03439 | -0.096851 | -0.0025021 | 0.00064308 | 0.07888 | 0.019721 | 0.037373 | 0.079598 | 0.1011 | 0.25643 | -0.058478 | 0.078886 | 0.027831 | -0.001407 | 0.034145 | 0.13733 | 0.035222 | -0.14583 | 120.3334 | -0.016532 | 120.4707 | 120.4292 | 0.095851 | 0.004965 | 0.1603 | 120.246 | -0.061985 | 120.4707 | 120.3904 | 0.14443 | 0.041199 | -0.060908 | 120.4714 | 120.4929 | 120.6483 | 120.4116 | -0.15461 | 120.426 | 120.5292 | 120.4271 | 120.4197 | -0.24196
3091.9062 | 120.6162 | -120.433 | 0.068665 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.022721 | 0.0048523 | 0.24784 | 0.024385 | 0.034818 | -0.096424 | -0.0022885 | 0.00042948 | 0.07888 | 0.015142 | 0.037373 | 0.07502 | 0.096516 | 0.25643 | -0.021847 | 0.078886 | 0.03241 | 0.007751 | 0.034145 | 0.13275 | 0.030644 | -0.15041 | 120.4112 | 0.006355 | 120.5119 | 120.4704 | 0.05922 | 0.027851 | 0.18777 | 120.2826 | -0.03452 | 120.5119 | 120.4408 | 0.15816 | 0.064085 | -0.038021 | 120.5081 | 120.5296 | 120.6895 | 120.4482 | -0.090512 | 120.4672 | 120.5658 | 120.4637 | 120.4655 | -0.21908
3093.6406 | 120.5841 | -120.4422 | 0.07782 | 1.4211e-13 | 0.024374 | 0.01656 | 0.010109 | -0.023362 | 0.0046387 | 0.23258 | 0.024598 | 0.034818 | -0.096851 | -0.0022885 | 0.00064308 | 0.07888 | 0.028878 | 0.041952 | 0.07502 | 0.091937 | 0.25185 | -0.026426 | 0.078886 | 0.03241 | 0.007751 | 0.029566 | 0.13733 | 0.026065 | -0.15041 | 120.4158 | -0.0028 | 120.5211 | 120.4842 | 0.068378 | 0.014117 | 0.17403 | 120.2918 | -0.048254 | 120.5211 | 120.45 | 0.15816 | 0.059509 | -0.051755 | 120.5172 | 120.5341 | 120.6941 | 120.4711 | -0.10425 | 120.4718 | 120.5795 | 120.4683 | 120.4746 | -0.22823
3095.3906 | 120.6024 | -120.488 | 0.10529 | 1.4211e-13 | 0.024587 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.23258 | 0.024598 | 0.034818 | -0.096424 | -0.0027159 | 0.00064308 | 0.07888 | 0.019721 | 0.032795 | 0.079598 | 0.096516 | 0.25185 | -0.017268 | 0.083464 | 0.027831 | -0.001407 | 0.038723 | 0.12817 | 0.035222 | -0.14583 | 120.4707 | -0.025688 | 120.5669 | 120.5208 | 0.050063 | -0.00877 | 0.14657 | 120.3421 | -0.066563 | 120.5714 | 120.4866 | 0.14443 | 0.022886 | -0.070064 | 120.5676 | 120.5845 | 120.7398 | 120.5077 | -0.12255 | 120.5267 | 120.6161 | 120.5232 | 120.5158 | -0.25112
3097.1875 | 120.6162 | -120.5154 | 0.10986 | 1.4211e-13 | 0.024801 | 0.015705 | 0.009682 | -0.023576 | 0.0048523 | 0.24021 | 0.024598 | 0.034818 | -0.096424 | -0.0022885 | 0.00064308 | 0.07888 | 0.019721 | 0.037373 | 0.070441 | 0.096516 | 0.24727 | -0.031005 | 0.074307 | 0.027831 | 0.003172 | 0.034145 | 0.13275 | 0.030644 | -0.14583 | 120.4844 | -0.039422 | 120.5943 | 120.5528 | 0.068378 | -0.013347 | 0.13741 | 120.3696 | -0.075718 | 120.5897 | 120.5186 | 0.149 | 0.022887 | -0.079219 | 120.5859 | 120.612 | 120.7627 | 120.5352 | -0.14087 | 120.5496 | 120.6482 | 120.5461 | 120.5433 | -0.2557
3098.9688 | 120.7535 | -120.4834 | 0.082397 | 1.4211e-13 | 0.024587 | 0.015919 | 0.010109 | -0.023148 | 0.0046387 | 0.23258 | 0.024598 | 0.034604 | -0.09621 | -0.0025021 | 0.00064308 | 0.083459 | 0.0243 | 0.028217 | 0.07502 | 0.096516 | 0.25185 | -0.044742 | 0.083464 | 0.03241 | -0.001407 | 0.034145 | 0.12817 | 0.021486 | -0.15041 | 120.4387 | -0.007377 | 120.5669 | 120.5116 | 0.072959 | 0.014119 | 0.16946 | 120.333 | -0.048252 | 120.5669 | 120.482 | 0.149 | 0.045775 | -0.060911 | 120.5584 | 120.5799 | 120.7352 | 120.5077 | -0.12714 | 120.5175 | 120.6116 | 120.5049 | 120.5158 | -0.23281
3100.7031 | 120.7993 | -120.5109 | 0.073242 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023148 | 0.0048523 | 0.23258 | 0.024598 | 0.034818 | -0.096637 | -0.0020749 | 0.00085668 | 0.07888 | 0.015142 | 0.037373 | 0.070441 | 0.1011 | 0.25185 | -0.044742 | 0.078886 | 0.03241 | -0.001407 | 0.029566 | 0.12817 | 0.030644 | -0.14583 | 120.4661 | -0.002801 | 120.5897 | 120.5482 | 0.082115 | 0.027853 | 0.17861 | 120.365 | -0.043676 | 120.5897 | 120.5095 | 0.14443 | 0.05493 | -0.042598 | 120.5813 | 120.612 | 120.7627 | 120.526 | -0.11798 | 120.5404 | 120.639 | 120.5415 | 120.5433 | -0.21907
3102.5156 | 120.8084 | -120.5063 | 0.064087 | 1.4211e-13 | 0.025015 | 0.01656 | 0.0098956 | -0.022935 | 0.0046387 | 0.24021 | 0.024385 | 0.03439 | -0.096424 | -0.0025021 | 0.00064308 | 0.07888 | 0.019721 | 0.037373 | 0.07502 | 0.096516 | 0.24727 | -0.044742 | 0.074307 | 0.03241 | 0.007751 | 0.038723 | 0.12817 | 0.039801 | -0.14583 | 120.4615 | 0.010933 | 120.5852 | 120.5437 | 0.082115 | 0.032429 | 0.18319 | 120.3605 | -0.025364 | 120.5806 | 120.514 | 0.15358 | 0.064085 | -0.024286 | 120.5813 | 120.6028 | 120.7536 | 120.526 | -0.10883 | 120.545 | 120.6345 | 120.5461 | 120.5387 | -0.20992
3104.25 | 120.7214 | -120.575 | 0.10529 | 1.4211e-13 | 0.024587 | 0.016346 | 0.010109 | -0.022935 | 0.0046387 | 0.24021 | 0.024171 | 0.03439 | -0.09621 | -0.0025021 | 0.00085668 | 0.07888 | 0.015142 | 0.037373 | 0.079598 | 0.11025 | 0.24727 | -0.044742 | 0.078886 | 0.027831 | 0.007751 | 0.024988 | 0.12817 | 0.035222 | -0.14583 | 120.5302 | -0.025688 | 120.6538 | 120.6123 | 0.082115 | 0.004967 | 0.14199 | 120.4291 | -0.080298 | 120.6538 | 120.5827 | 0.15358 | 0.022886 | -0.070064 | 120.6545 | 120.6852 | 120.8222 | 120.5901 | -0.15003 | 120.5999 | 120.7031 | 120.6102 | 120.6028 | -0.25112
3105.9688 | 120.7031 | -120.5933 | 0.09613 | 1.4211e-13 | 0.024374 | 0.016346 | 0.009682 | -0.023148 | 0.0046387 | 0.24784 | 0.024385 | 0.034818 | -0.096637 | -0.0022885 | 0.00064308 | 0.088037 | 0.0243 | 0.032795 | 0.07502 | 0.10567 | 0.25185 | -0.035584 | 0.074307 | 0.03241 | 0.003172 | 0.034145 | 0.13275 | 0.030644 | -0.15041 | 120.5577 | -0.02111 | 120.6813 | 120.6261 | 0.068379 | 0.009544 | 0.15572 | 120.4428 | -0.061985 | 120.6676 | 120.5964 | 0.15358 | 0.03662 | -0.065486 | 120.6683 | 120.6989 | 120.8451 | 120.6176 | -0.13171 | 120.6274 | 120.726 | 120.6239 | 120.6257 | -0.24654
3107.75 | 120.8633 | -120.5658 | 0.07782 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.22495 | 0.024171 | 0.034818 | -0.096424 | -0.0020749 | 0.0012841 | 0.092615 | 0.015142 | 0.037373 | 0.084176 | 0.1011 | 0.25185 | -0.031005 | 0.074307 | 0.036989 | 0.003172 | 0.034145 | 0.13275 | 0.026065 | -0.14125 | 120.5348 | 0.006356 | 120.6584 | 120.6032 | 0.068378 | 0.023275 | 0.17403 | 120.4245 | -0.043675 | 120.6401 | 120.569 | 0.14443 | 0.05493 | -0.051755 | 120.65 | 120.6669 | 120.8176 | 120.5809 | -0.10883 | 120.5999 | 120.6985 | 120.5919 | 120.6028 | -0.21907
3109.5469 | 120.8084 | -120.6436 | 0.082397 | 1.4211e-13 | 0.024801 | 0.01656 | 0.009682 | -0.023148 | 0.0046387 | 0.24021 | 0.024598 | 0.034604 | -0.09621 | -0.0020749 | 0.00064308 | 0.07888 | 0.0243 | 0.032795 | 0.07502 | 0.1011 | 0.25643 | -0.040163 | 0.074307 | 0.027831 | 0.007751 | 0.038723 | 0.13733 | 0.039801 | -0.15041 | 120.6035 | -0.007377 | 120.7225 | 120.6764 | 0.072958 | 0.018698 | 0.17403 | 120.4932 | -0.043674 | 120.7179 | 120.6514 | 0.15816 | 0.054932 | -0.042596 | 120.7186 | 120.7447 | 120.9 | 120.6679 | -0.12256 | 120.6823 | 120.7809 | 120.6834 | 120.6714 | -0.23281
3111.2812 | 115.5579 | -77.8152 | 37.587 | 1.4211e-13 | 0.024374 | 0.016133 | 0.0092546 | -0.022721 | 0.0042113 | 0.24021 | 0.024385 | 0.03439 | -0.09621 | -0.0025021 | 0.0010705 | 0.065145 | 0.005985 | 0.01906 | 0.065863 | 0.091937 | 0.23812 | -0.076794 | 0.06515 | 0.018674 | -0.015143 | 0.024988 | 0.11901 | 0.026065 | -0.16873 | 77.7385 | -37.5211 | 77.8804 | 77.8343 | 0.095854 | -37.495 | -37.3489 | 77.6465 | -37.562 | 77.8804 | 77.8001 | 0.15358 | -37.468 | -37.5609 | 77.8811 | 77.9072 | 78.0534 | 77.8212 | -37.6638 | 77.8402 | 77.9343 | 77.8413 | 77.8339 | -37.7557
3113.0781 | 120.6299 | -120.2728 | 0.082397 | 1.4211e-13 | 0.024587 | 0.016346 | 0.0098956 | -0.023148 | 0.0044249 | 0.24021 | 0.024385 | 0.034604 | -0.096424 | -0.0025021 | 0.00042948 | 0.083459 | 0.019721 | 0.037373 | 0.07502 | 0.1011 | 0.25185 | -0.044742 | 0.074307 | 0.023253 | -0.001407 | 0.029566 | 0.13733 | 0.035222 | -0.15041 | 120.2281 | -0.007377 | 120.3563 | 120.3102 | 0.082115 | 0.018698 | 0.16946 | 120.1224 | -0.052831 | 120.3471 | 120.2714 | 0.149 | 0.054932 | -0.047175 | 120.3478 | 120.3739 | 120.5247 | 120.2925 | -0.12714 | 120.3024 | 120.4102 | 120.308 | 120.2961 | -0.23281
3114.8125 | 120.726 | -120.4056 | 0.073242 | 1.4211e-13 | 0.024587 | 0.015919 | 0.009682 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034818 | -0.095996 | -0.0025021 | 0.00042948 | 0.074302 | 0.0243 | 0.028217 | 0.084176 | 0.1011 | 0.25185 | -0.053899 | 0.078886 | 0.023253 | -0.005985 | 0.038723 | 0.13733 | 0.035222 | -0.14583 | 120.3517 | 0.010934 | 120.4799 | 120.4338 | 0.082116 | 0.027853 | 0.17861 | 120.2597 | -0.034519 | 120.4845 | 120.3996 | 0.13985 | 0.064087 | -0.03802 | 120.4898 | 120.5067 | 120.6574 | 120.4299 | -0.12714 | 120.4443 | 120.5429 | 120.4408 | 120.4288 | -0.21907
3116.5938 | 120.7626 | -120.488 | 0.041199 | 1.4211e-13 | 0.024587 | 0.016346 | 0.009682 | -0.023148 | 0.0046387 | 0.24021 | 0.024385 | 0.034177 | -0.096424 | -0.0025021 | 0.00042948 | 0.07888 | 0.015142 | 0.041952 | 0.084176 | 0.1011 | 0.24727 | -0.058478 | 0.078886 | 0.023253 | 0.007751 | 0.034145 | 0.12817 | 0.030644 | -0.14583 | 120.4295 | 0.042977 | 120.5669 | 120.5299 | 0.10043 | 0.059896 | 0.20608 | 120.3421 | -0.007054 | 120.5669 | 120.4957 | 0.15358 | 0.086973 | -0.010555 | 120.5722 | 120.5891 | 120.7353 | 120.5031 | -0.099677 | 120.5221 | 120.6161 | 120.5186 | 120.5112 | -0.18703
3118.3906 | 120.7993 | -120.5566 | 0.082397 | 1.4211e-13 | 0.024374 | 0.016133 | 0.010109 | -0.023148 | 0.0048523 | 0.24784 | 0.024385 | 0.034818 | -0.096424 | -0.0025021 | 0.00064308 | 0.07888 | 0.010564 | 0.032795 | 0.07502 | 0.096516 | 0.25643 | -0.040163 | 0.078886 | 0.027831 | 0.007751 | 0.029566 | 0.13275 | 0.030644 | -0.15041 | 120.5165 | -0.007377 | 120.6355 | 120.5894 | 0.072958 | 0.014119 | 0.17403 | 120.4062 | -0.052831 | 120.6355 | 120.5644 | 0.15816 | 0.050353 | -0.051753 | 120.6317 | 120.6532 | 120.8131 | 120.5672 | -0.12256 | 120.5862 | 120.6894 | 120.5873 | 120.5845 | -0.23281
3120.1875 | 120.8771 | -120.5612 | 0.059509 | 1.4211e-13 | 0.024587 | 0.016133 | 0.0098956 | -0.022935 | 0.0048523 | 0.24784 | 0.024598 | 0.03439 | -0.096637 | -0.0025021 | 0.00085668 | 0.083459 | 0.0243 | 0.041952 | 0.07502 | 0.096516 | 0.25643 | -0.026426 | 0.078886 | 0.027831 | -0.005985 | 0.034145 | 0.13733 | 0.030644 | -0.14583 | 120.5348 | 0.015511 | 120.6447 | 120.6032 | 0.068378 | 0.037007 | 0.19692 | 120.4154 | -0.025364 | 120.6401 | 120.5552 | 0.13985 | 0.07782 | -0.028865 | 120.6362 | 120.6577 | 120.8176 | 120.5855 | -0.085935 | 120.5954 | 120.6985 | 120.5919 | 120.589 | -0.20534
3121.9062 | 120.7718 | -120.6116 | 0.11902 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.023148 | 0.0048523 | 0.24021 | 0.024598 | 0.035245 | -0.096424 | -0.0027159 | 0.00042948 | 0.083459 | 0.019721 | 0.032795 | 0.07502 | 0.096516 | 0.25185 | -0.026426 | 0.078886 | 0.03241 | 0.007751 | 0.034145 | 0.13275 | 0.035222 | -0.15041 | 120.5851 | -0.043999 | 120.695 | 120.6444 | 0.059221 | -0.022503 | 0.13283 | 120.4612 | -0.084874 | 120.6905 | 120.6193 | 0.15816 | 0.013731 | -0.083797 | 120.6866 | 120.7081 | 120.8634 | 120.6313 | -0.14544 | 120.6457 | 120.7443 | 120.6468 | 120.644 | -0.26943
3123.6875 | 120.7901 | -120.6665 | 0.11902 | 1.4211e-13 | 0.024801 | 0.01656 | 0.009682 | -0.023362 | 0.0046387 | 0.24021 | 0.024171 | 0.03439 | -0.096424 | -0.0025021 | 0.00064308 | 0.07888 | 0.015142 | 0.037373 | 0.079598 | 0.1011 | 0.25185 | -0.049321 | 0.074307 | 0.027831 | 0.007751 | 0.038723 | 0.13275 | 0.035222 | -0.15041 | 120.6172 | -0.039421 | 120.7454 | 120.7039 | 0.086694 | -0.017924 | 0.13283 | 120.5161 | -0.080296 | 120.7408 | 120.6743 | 0.15816 | 0.013731 | -0.083797 | 120.7461 | 120.7676 | 120.9184 | 120.6816 | -0.16834 | 120.7052 | 120.7993 | 120.7017 | 120.6943 | -0.26943
3125.4688 | 120.2087 | -119.9615 | 0.068665 | 1.4211e-13 | 0.024587 | 0.016346 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024171 | 0.035031 | -0.096424 | -0.0025021 | 0.00064308 | 0.083459 | 0.015142 | 0.037373 | 0.070441 | 0.096516 | 0.25185 | -0.035584 | 0.088043 | 0.03241 | 0.007751 | 0.034145 | 0.14191 | 0.039801 | -0.14583 | 119.926 | 0.001776 | 120.045 | 119.9989 | 0.072957 | 0.027851 | 0.18319 | 119.8157 | -0.03452 | 120.0496 | 119.9693 | 0.15358 | 0.073242 | -0.028864 | 120.032 | 120.0581 | 120.2134 | 119.9767 | -0.10425 | 119.9957 | 120.1035 | 120.0013 | 119.994 | -0.2145
3127.2656 | 120.575 | -120.3232 | 0.091553 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.023362 | 0.0044249 | 0.24021 | 0.024385 | 0.034818 | -0.09621 | -0.0025021 | 0.00064308 | 0.07888 | 0.019721 | 0.032795 | 0.07502 | 0.10567 | 0.24727 | -0.031005 | 0.088043 | 0.03241 | 0.003172 | 0.038723 | 0.12817 | 0.044379 | -0.14583 | 120.2922 | -0.016533 | 120.4021 | 120.356 | 0.0638 | 0.014121 | 0.15572 | 120.1773 | -0.05283 | 120.4112 | 120.3264 | 0.149 | 0.036619 | -0.047174 | 120.3982 | 120.4289 | 120.5705 | 120.3429 | -0.12256 | 120.3619 | 120.4514 | 120.3676 | 120.3556 | -0.23739
3129.0469 | 120.6757 | -120.4422 | 0.082397 | 1.4211e-13 | 0.024801 | 0.015919 | 0.010109 | -0.023148 | 0.0048523 | 0.24021 | 0.024171 | 0.035031 | -0.096424 | -0.0027159 | 0.00064308 | 0.083459 | 0.019721 | 0.028217 | 0.07502 | 0.1011 | 0.25185 | -0.026426 | 0.083464 | 0.03241 | 0.003172 | 0.043302 | 0.12817 | 0.039801 | -0.14125 | 120.4158 | -0.007377 | 120.5257 | 120.4704 | 0.054643 | 0.018698 | 0.16946 | 120.3009 | -0.039095 | 120.5257 | 120.4454 | 0.14443 | 0.045775 | -0.042596 | 120.5172 | 120.5433 | 120.6941 | 120.4619 | -0.10882 | 120.4855 | 120.5704 | 120.482 | 120.4746 | -0.22365
3130.7812 | 120.7993 | -120.488 | 0.054932 | 1.4211e-13 | 0.024587 | 0.01656 | 0.010109 | -0.022935 | 0.0046387 | 0.23258 | 0.024171 | 0.035031 | -0.096424 | -0.0022885 | 0.00064308 | 0.074302 | 0.015142 | 0.023639 | 0.079598 | 0.10567 | 0.25643 | -0.053899 | 0.078886 | 0.03241 | 0.007751 | 0.034145 | 0.14191 | 0.035222 | -0.14583 | 120.4341 | 0.024666 | 120.5623 | 120.5116 | 0.077538 | 0.050742 | 0.2015 | 120.3421 | -0.020787 | 120.5669 | 120.4957 | 0.15358 | 0.086975 | -0.01971 | 120.5676 | 120.5936 | 120.7444 | 120.5031 | -0.10883 | 120.5221 | 120.6299 | 120.5232 | 120.5204 | -0.20076
3132.5781 | 120.7489 | -120.5658 | 0.059509 | 1.4211e-13 | 0.025015 | 0.01656 | 0.0098956 | -0.023148 | 0.0048523 | 0.22495 | 0.023957 | 0.035245 | -0.096637 | -0.0020749 | 0.00064308 | 0.07888 | 0.0243 | 0.037373 | 0.079598 | 0.1011 | 0.25185 | -0.053899 | 0.088043 | 0.03241 | -0.005985 | 0.034145 | 0.13275 | 0.030644 | -0.14583 | 120.5119 | 0.020089 | 120.6447 | 120.6032 | 0.091272 | 0.041586 | 0.19234 | 120.42 | -0.025364 | 120.6538 | 120.5598 | 0.13985 | 0.073241 | -0.028865 | 120.6454 | 120.6669 | 120.8176 | 120.5901 | -0.11341 | 120.5999 | 120.6985 | 120.5964 | 120.5982 | -0.20534
3134.375 | 120.8359 | -120.5658 | 0.059509 | 1.4211e-13 | 0.024587 | 0.016133 | 0.010109 | -0.022935 | 0.0048523 | 0.24021 | 0.023744 | 0.035245 | -0.096424 | -0.0027159 | 0.00085668 | 0.083459 | 0.015142 | 0.037373 | 0.07502 | 0.1011 | 0.24727 | -0.00811 | 0.078886 | 0.03241 | 0.007751 | 0.038723 | 0.13733 | 0.030644 | -0.14583 | 120.5577 | 0.015511 | 120.6493 | 120.6032 | 0.045483 | 0.041586 | 0.18776 | 120.42 | -0.020786 | 120.6447 | 120.5735 | 0.15358 | 0.07782 | -0.028865 | 120.6408 | 120.6669 | 120.8131 | 120.5809 | -0.067619 | 120.6045 | 120.7031 | 120.5964 | 120.5982 | -0.20534
3136.1719 | 120.8221 | -120.5704 | 0.13733 | 1.4211e-13 | 0.024801 | 0.016346 | 0.009682 | -0.022935 | 0.0048523 | 0.23258 | 0.023957 | 0.034818 | -0.09621 | -0.0025021 | 0.00021588 | 0.083459 | 0.0243 | 0.041952 | 0.07502 | 0.091937 | 0.25643 | -0.040163 | 0.074307 | 0.03241 | 0.01233 | 0.034145 | 0.13733 | 0.035222 | -0.14125 | 120.5302 | -0.062309 | 120.6538 | 120.6123 | 0.082115 | -0.045392 | 0.1191 | 120.4291 | -0.10318 | 120.6447 | 120.5827 | 0.15358 | 0 | -0.10211 | 120.6454 | 120.6623 | 120.8268 | 120.5947 | -0.17749 | 120.6045 | 120.7077 | 120.6056 | 120.6028 | -0.27858
3137.875 | 120.7672 | -120.6528 | 0.082397 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023148 | 0.0046387 | 0.24021 | 0.024385 | 0.035031 | -0.096637 | -0.0022885 | 0.00064308 | 0.083459 | 0.019721 | 0.037373 | 0.07502 | 0.1011 | 0.25643 | -0.035584 | 0.083464 | 0.027831 | 0.003172 | 0.034145 | 0.13275 | 0.035222 | -0.15041 | 120.6172 | -0.007377 | 120.7362 | 120.6901 | 0.072957 | 0.018698 | 0.17403 | 120.5024 | -0.048252 | 120.7362 | 120.6559 | 0.15358 | 0.050353 | -0.047175 | 120.7278 | 120.7539 | 120.9092 | 120.6725 | -0.11798 | 120.6869 | 120.7855 | 120.688 | 120.6806 | -0.23281
3139.6562 | 120.7993 | -120.5658 | 0.16022 | 1.4211e-13 | 0.024374 | 0.016774 | 0.009682 | -0.023148 | 0.0046387 | 0.23258 | 0.024171 | 0.034818 | -0.096637 | -0.0022885 | 0.00042948 | 0.083459 | 0.0243 | 0.032795 | 0.079598 | 0.1011 | 0.25185 | -0.053899 | 0.083464 | 0.027831 | 0.003172 | 0.034145 | 0.13275 | 0.039801 | -0.13668 | 120.5119 | -0.080619 | 120.6493 | 120.5986 | 0.086694 | -0.059122 | 0.091635 | 120.4291 | -0.12607 | 120.6493 | 120.569 | 0.13985 | -0.027467 | -0.12042 | 120.6454 | 120.6669 | 120.8176 | 120.5901 | -0.21412 | 120.5999 | 120.6985 | 120.6056 | 120.5936 | -0.29689
3141.4531 | 120.8862 | -120.6573 | 0.11902 | 1.4211e-13 | 0.025015 | 0.016346 | 0.0098956 | -0.023362 | 0.0044249 | 0.24784 | 0.024598 | 0.035031 | -0.096851 | -0.0029295 | 0.00064308 | 0.07888 | 0.015142 | 0.037373 | 0.079598 | 0.1011 | 0.25643 | -0.044742 | 0.078886 | 0.027831 | 0.003172 | 0.024988 | 0.12359 | 0.039801 | -0.14583 | 120.6126 | -0.039421 | 120.7362 | 120.6947 | 0.082115 | -0.017924 | 0.13741 | 120.5115 | -0.094031 | 120.7362 | 120.6605 | 0.149 | 0.004574 | -0.079218 | 120.7369 | 120.7584 | 120.9138 | 120.6725 | -0.16376 | 120.6823 | 120.7809 | 120.6971 | 120.6852 | -0.26485
3143.2344 | 120.845 | -120.7169 | 0.10986 | 1.4211e-13 | 0.025228 | 0.016346 | 0.009682 | -0.023148 | 0.0046387 | 0.24021 | 0.024171 | 0.035031 | -0.096424 | -0.0025021 | 0.00042948 | 0.07888 | 0.019721 | 0.037373 | 0.070441 | 0.1011 | 0.24727 | -0.044742 | 0.078886 | 0.027831 | -0.005985 | 0.034145 | 0.12817 | 0.035222 | -0.14125 | 120.6721 | -0.039422 | 120.7957 | 120.7542 | 0.082115 | -0.008768 | 0.13741 | 120.5756 | -0.075718 | 120.7957 | 120.7109 | 0.13527 | 0.018309 | -0.074641 | 120.7873 | 120.818 | 120.9641 | 120.7366 | -0.1546 | 120.751 | 120.845 | 120.7521 | 120.7447 | -0.25112
3145.0156 | 120.6116 | -120.2774 | 0.050354 | 1.4211e-13 | 0.024587 | 0.016346 | 0.009682 | -0.023148 | 0.0048523 | 0.23258 | 0.024171 | 0.035031 | -0.096637 | -0.0025021 | 0.00042948 | 0.088037 | 0.019721 | 0.028217 | 0.079598 | 0.11025 | 0.25185 | -0.044742 | 0.083464 | 0.03241 | 0.007751 | 0.038723 | 0.13275 | 0.035222 | -0.14125 | 120.2327 | 0.029244 | 120.3654 | 120.3056 | 0.072959 | 0.059899 | 0.2015 | 120.1362 | -0.011631 | 120.3609 | 120.2852 | 0.14901 | 0.082396 | -0.015132 | 120.357 | 120.3877 | 120.5293 | 120.2971 | -0.095096 | 120.3161 | 120.4102 | 120.3126 | 120.3098 | -0.19161
3146.8125 | 120.8084 | -120.5566 | 0.064087 | 1.4211e-13 | 0.024374 | 0.01656 | 0.0098956 | -0.023148 | 0.0046387 | 0.22495 | 0.025025 | 0.035031 | -0.096637 | -0.0022885 | 0.00064308 | 0.083459 | 0.019721 | 0.032795 | 0.079598 | 0.1011 | 0.25185 | -0.053899 | 0.078886 | 0.027831 | 0.007751 | 0.038723 | 0.13733 | 0.053537 | -0.14583 | 120.5027 | 0.015511 | 120.6401 | 120.5894 | 0.086694 | 0.037008 | 0.18777 | 120.4108 | -0.025364 | 120.6355 | 120.5644 | 0.15358 | 0.073242 | -0.01055 | 120.6362 | 120.6577 | 120.8085 | 120.5764 | -0.11799 | 120.5954 | 120.694 | 120.6102 | 120.5845 | -0.20992
3148.5469 | 120.7993 | -120.6573 | 0.082397 | 1.4211e-13 | 0.024587 | 0.016346 | 0.0098956 | -0.023362 | 0.0048523 | 0.24021 | 0.024171 | 0.034818 | -0.096424 | -0.0029295 | 0.00085668 | 0.07888 | 0.019721 | 0.041952 | 0.07502 | 0.096516 | 0.25185 | -0.035584 | 0.078886 | 0.03241 | 0.007751 | 0.038723 | 0.12817 | 0.030644 | -0.14125 | 120.6218 | -0.007377 | 120.7362 | 120.6993 | 0.077536 | 0.014119 | 0.16946 | 120.5161 | -0.043674 | 120.7362 | 120.6651 | 0.14901 | 0.045775 | -0.051753 | 120.7324 | 120.7539 | 120.9092 | 120.6771 | -0.11798 | 120.6961 | 120.7855 | 120.688 | 120.6898 | -0.22365
3150.3438 | 120.8633 | -120.6757 | 0.10071 | 1.4211e-13 | 0.024801 | 0.01656 | 0.0098956 | -0.023362 | 0.0044249 | 0.24021 | 0.024171 | 0.035031 | -0.096424 | -0.0027159 | 0.00064308 | 0.07888 | 0.0243 | 0.032795 | 0.079598 | 0.1011 | 0.25643 | -0.021847 | 0.088043 | 0.027831 | 0.003172 | 0.038723 | 0.13275 | 0.044379 | -0.14125 | 120.6538 | -0.02111 | 120.7545 | 120.7085 | 0.054642 | 0.000387 | 0.15572 | 120.5344 | -0.061985 | 120.7637 | 120.6788 | 0.14443 | 0.032042 | -0.056329 | 120.7553 | 120.7768 | 120.9321 | 120.7 | -0.12255 | 120.7144 | 120.8084 | 120.72 | 120.7035 | -0.24196
3152.125 | 120.8588 | -120.7169 | 0.10529 | 1.4211e-13 | 0.025228 | 0.016346 | 0.009682 | -0.022935 | 0.0048523 | 0.23258 | 0.024171 | 0.034818 | -0.096424 | -0.0022885 | 0.00064308 | 0.083459 | 0.019721 | 0.037373 | 0.07502 | 0.1011 | 0.24269 | -0.017268 | 0.088043 | 0.03241 | 0.007751 | 0.038723 | 0.13275 | 0.030644 | -0.13668 | 120.6996 | -0.030266 | 120.8003 | 120.7542 | 0.054641 | -0.004191 | 0.13741 | 120.5802 | -0.066563 | 120.8049 | 120.7246 | 0.14443 | 0.027464 | -0.074642 | 120.7919 | 120.818 | 120.9596 | 120.7366 | -0.12255 | 120.7556 | 120.8496 | 120.7475 | 120.7493 | -0.24196
3153.8438 | 120.8633 | -120.7077 | 0.086975 | 1.4211e-13 | 0.024587 | 0.016346 | 0.010109 | -0.023576 | 0.0048523 | 0.24784 | 0.024385 | 0.034818 | -0.096424 | -0.0022885 | 0.00085668 | 0.07888 | 0.019721 | 0.032795 | 0.079598 | 0.1011 | 0.26559 | -0.040163 | 0.092622 | 0.023253 | 0.003172 | 0.038723 | 0.13275 | 0.039801 | -0.14125 | 120.6675 | -0.007377 | 120.7866 | 120.7405 | 0.072958 | 0.01412 | 0.17861 | 120.5664 | -0.048252 | 120.8003 | 120.7109 | 0.14443 | 0.045775 | -0.047174 | 120.7873 | 120.8088 | 120.9733 | 120.7274 | -0.12714 | 120.7464 | 120.8405 | 120.7475 | 120.731 | -0.22823
3155.625 | 121.0098 | -120.7535 | 0.064087 | 1.4211e-13 | 0.024587 | 0.016346 | 0.010323 | -0.023148 | 0.0046387 | 0.23258 | 0.024598 | 0.034818 | -0.09621 | -0.0025021 | 0.00042948 | 0.083459 | 0.019721 | 0.032795 | 0.079598 | 0.1011 | 0.24727 | -0.049321 | 0.078886 | 0.03241 | -0.001407 | 0.038723 | 0.12817 | 0.044379 | -0.14583 | 120.7042 | 0.015511 | 120.8369 | 120.7863 | 0.082116 | 0.037008 | 0.18319 | 120.6076 | -0.025364 | 120.8324 | 120.7521 | 0.14443 | 0.064085 | -0.019708 | 120.8331 | 120.8546 | 121.0008 | 120.7732 | -0.11341 | 120.7922 | 120.8817 | 120.7979 | 120.7859 | -0.20992
3157.4375 | 120.9183 | -120.7764 | 0.091553 | 1.4211e-13 | 0.024801 | 0.01656 | 0.010109 | -0.023576 | 0.0048523 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0025021 | 0.00064308 | 0.083459 | 0.019721 | 0.037373 | 0.079598 | 0.091937 | 0.24727 | -0.003531 | 0.088043 | 0.036989 | 0.003172 | 0.029566 | 0.13733 | 0.035222 | -0.14125 | 120.7728 | -0.011955 | 120.8598 | 120.8137 | 0.040904 | 0.000384 | 0.15572 | 120.6351 | -0.061987 | 120.8644 | 120.7795 | 0.14443 | 0.045776 | -0.056331 | 120.856 | 120.8683 | 121.0236 | 120.7961 | -0.095084 | 120.8059 | 120.9137 | 120.8116 | 120.8134 | -0.23281
3159.1719 | 120.9183 | -120.6207 | 0.27466 | 1.4211e-13 | 0.025015 | 0.01656 | 0.0098956 | -0.023576 | 0.0046387 | 0.23258 | 0.024598 | 0.034818 | -0.096424 | -0.0025021 | 0.00064308 | 0.083459 | 0.019721 | 0.032795 | 0.070441 | 0.096516 | 0.24727 | -0.021847 | 0.088043 | 0.036989 | 0.007751 | 0.034145 | 0.13275 | 0.035222 | -0.1321 | 120.5989 | -0.20422 | 120.7042 | 120.6535 | 0.054642 | -0.17814 | -0.027384 | 120.4886 | -0.24051 | 120.7088 | 120.6285 | 0.13985 | -0.14191 | -0.23944 | 120.6912 | 120.7172 | 120.868 | 120.6404 | -0.29651 | 120.6549 | 120.7535 | 120.656 | 120.6577 | -0.40675
3160.9531 | 121.138 | -120.7581 | 0.064087 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023362 | 0.0050659 | 0.24784 | 0.024171 | 0.034818 | -0.096851 | -0.0022885 | 0.00085668 | 0.069723 | 0.019721 | 0.028217 | 0.079598 | 0.1011 | 0.25185 | -0.040163 | 0.083464 | 0.03241 | 0.003172 | 0.043302 | 0.13275 | 0.035222 | -0.14125 | 120.7179 | 0.015511 | 120.8278 | 120.7863 | 0.06838 | 0.037008 | 0.18777 | 120.6168 | -0.020785 | 120.8415 | 120.7612 | 0.14443 | 0.068663 | -0.028865 | 120.8377 | 120.8592 | 121.0099 | 120.7778 | -0.10425 | 120.8014 | 120.8908 | 120.7933 | 120.7905 | -0.20534
3162.6875 | 120.9229 | -120.6619 | 0.21515 | 1.4211e-13 | 0.025015 | 0.016133 | 0.010109 | -0.023362 | 0.0048523 | 0.22495 | 0.024171 | 0.034604 | -0.096637 | -0.0027159 | 0.00064308 | 0.083459 | 0.019721 | 0.041952 | 0.079598 | 0.096516 | 0.25643 | -0.058478 | 0.083464 | 0.03241 | 0.01233 | 0.038723 | 0.13275 | 0.035222 | -0.14125 | 120.6034 | -0.13555 | 120.7454 | 120.7039 | 0.10043 | -0.11863 | 0.041282 | 120.5207 | -0.17643 | 120.7454 | 120.6743 | 0.15358 | -0.082399 | -0.17993 | 120.7415 | 120.7584 | 120.9184 | 120.6816 | -0.27363 | 120.7006 | 120.7947 | 120.6971 | 120.6943 | -0.3564
3164.4844 | 121.0648 | -120.7031 | 0.073242 | 1.4211e-13 | 0.024801 | 0.01656 | 0.0098956 | -0.023362 | 0.0048523 | 0.23258 | 0.024171 | 0.034604 | -0.09621 | -0.0022885 | 0.00042948 | 0.083459 | 0.019721 | 0.028217 | 0.079598 | 0.096516 | 0.25643 | -0.076794 | 0.083464 | 0.027831 | 0.003172 | 0.038723 | 0.13275 | 0.039801 | -0.13668 | 120.6263 | 0.006356 | 120.7866 | 120.7313 | 0.10501 | 0.023274 | 0.18319 | 120.5664 | -0.034519 | 120.7866 | 120.7063 | 0.13985 | 0.059508 | -0.033441 | 120.7827 | 120.7996 | 120.9596 | 120.7228 | -0.15004 | 120.7418 | 120.8359 | 120.7429 | 120.731 | -0.20992
3166.2188 | 121.0144 | -120.8542 | 0.10529 | 1.4211e-13 | 0.025015 | 0.016133 | 0.0098956 | -0.023362 | 0.0050659 | 0.22495 | 0.023957 | 0.035031 | -0.096424 | -0.0025021 | 0.00085668 | 0.083459 | 0.0243 | 0.041952 | 0.07502 | 0.10567 | 0.24727 | -0.053899 | 0.078886 | 0.027831 | -0.001407 | 0.038723 | 0.13275 | 0.039801 | -0.14125 | 120.8003 | -0.030266 | 120.9376 | 120.8961 | 0.095851 | 0.000388 | 0.14199 | 120.7129 | -0.066563 | 120.9331 | 120.8528 | 0.13985 | 0.027464 | -0.065485 | 120.9292 | 120.9599 | 121.1015 | 120.8785 | -0.15919 | 120.8929 | 120.9869 | 120.894 | 120.882 | -0.24654
3168.0156 | 120.8725 | -120.0211 | 0.073242 | 1.4211e-13 | 0.025015 | 0.016133 | 0.009682 | -0.023362 | 0.0046387 | 0.24021 | 0.024385 | 0.034818 | -0.096851 | -0.0025021 | 0.00042948 | 0.083459 | 0.015142 | 0.032795 | 0.079598 | 0.1011 | 0.24727 | 0.037679 | 0.078886 | 0.027831 | 0.007751 | 0.034145 | 0.12817 | 0.048958 | 0.041898 | 120.0587 | 0.006356 | 120.1045 | 120.0539 | -0.004884 | 0.027853 | 0.17403 | 120.063 | -0.039097 | 120.0999 | 120.0288 | -0.034147 | 0.05493 | -0.024284 | 120.1007 | 120.1222 | 120.2683 | 120.0362 | -0.035563 | 120.0552 | 120.1492 | 120.07 | 120.0489 | -0.031344
3169.7344 | 121.0281 | -120.6894 | 0.054932 | 1.4211e-13 | 0.024587 | 0.015919 | 0.010109 | -0.022935 | 0.0046387 | 0.24784 | 0.024171 | 0.034818 | -0.09621 | -0.0025021 | 0.00042948 | 0.088037 | 0.015142 | 0.037373 | 0.07502 | 0.096516 | 0.25185 | -0.021847 | 0.078886 | 0.027831 | 0.003172 | 0.038723 | 0.13275 | 0.039801 | -0.14125 | 120.6675 | 0.020088 | 120.7774 | 120.7268 | 0.05922 | 0.041584 | 0.19692 | 120.5481 | -0.016209 | 120.7683 | 120.6926 | 0.14443 | 0.077818 | -0.015131 | 120.7644 | 120.7859 | 120.9412 | 120.7045 | -0.076779 | 120.7281 | 120.8221 | 120.7292 | 120.7172 | -0.19619
3171.5312 | 121.0281 | -120.7764 | 0.059509 | 1.4211e-13 | 0.025015 | 0.016774 | 0.009682 | -0.022935 | 0.0052797 | 0.24021 | 0.024171 | 0.034818 | -0.09621 | -0.0025021 | 0.00021588 | 0.07888 | 0.019721 | 0.032795 | 0.07502 | 0.096516 | 0.24727 | -0.044742 | 0.078886 | 0.036989 | -0.001407 | 0.034145 | 0.12817 | 0.030644 | -0.14125 | 120.7316 | 0.015511 | 120.8552 | 120.8092 | 0.077537 | 0.037007 | 0.18776 | 120.6351 | -0.025364 | 120.8553 | 120.775 | 0.13985 | 0.068663 | -0.028865 | 120.8514 | 120.8729 | 121.0236 | 120.7961 | -0.10425 | 120.8105 | 120.9045 | 120.807 | 120.8134 | -0.20076
3173.3281 | 121.0236 | -120.7947 | 0.082397 | 1.4211e-13 | 0.024587 | 0.016346 | 0.0098956 | -0.023362 | 0.0052797 | 0.24021 | 0.024385 | 0.034818 | -0.096637 | -0.0027159 | 0.00085668 | 0.088037 | 0.0243 | 0.032795 | 0.07502 | 0.1011 | 0.25643 | -0.067636 | 0.083464 | 0.036989 | -0.001407 | 0.034145 | 0.12817 | 0.039801 | -0.15041 | 120.727 | -0.007377 | 120.8827 | 120.8275 | 0.10043 | 0.018698 | 0.17403 | 120.6443 | -0.048252 | 120.8781 | 120.7933 | 0.149 | 0.045775 | -0.042596 | 120.8697 | 120.8958 | 121.0511 | 120.819 | -0.15003 | 120.8288 | 120.9229 | 120.8345 | 120.8317 | -0.23281
3175.125 | 121.1151 | -120.7855 | 0.064087 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.022935 | 0.0046387 | 0.24021 | 0.024598 | 0.034818 | -0.096637 | -0.0025021 | 0.00042948 | 0.083459 | 0.015142 | 0.032795 | 0.07502 | 0.1011 | 0.25185 | -0.081373 | 0.078886 | 0.023253 | 0.007751 | 0.038723 | 0.13275 | 0.039801 | -0.14125 | 120.7041 | 0.010933 | 120.869 | 120.8183 | 0.11417 | 0.037008 | 0.18777 | 120.6443 | -0.025364 | 120.8644 | 120.7933 | 0.14901 | 0.068663 | -0.024286 | 120.8605 | 120.8866 | 121.0374 | 120.8007 | -0.14546 | 120.8242 | 120.9183 | 120.8253 | 120.8088 | -0.20534
3176.9531 | 121.1426 | -120.8405 | 0.068665 | 1.4211e-13 | 0.025015 | 0.016346 | 0.009682 | -0.023362 | 0.0048523 | 0.22495 | 0.024598 | 0.034818 | -0.096424 | -0.0022885 | 0.00064308 | 0.092615 | 0.019721 | 0.037373 | 0.070441 | 0.1011 | 0.24727 | -0.026426 | 0.078886 | 0.03241 | 0.007751 | 0.029566 | 0.12359 | 0.035222 | -0.15041 | 120.814 | 0.001776 | 120.9331 | 120.8778 | 0.063799 | 0.03243 | 0.17861 | 120.69 | -0.039099 | 120.9193 | 120.8482 | 0.15816 | 0.054928 | -0.033443 | 120.9109 | 120.9415 | 121.0877 | 120.8602 | -0.095091 | 120.87 | 120.964 | 120.8757 | 120.8729 | -0.21908
3178.6875 | 121.0739 | -120.8817 | 0.064087 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.023362 | 0.0046387 | 0.22495 | 0.024385 | 0.034818 | -0.096637 | -0.0025021 | 0.00064308 | 0.083459 | 0.0243 | 0.04653 | 0.070441 | 0.1011 | 0.25643 | -0.049321 | 0.074307 | 0.018674 | 0.003172 | 0.034145 | 0.12359 | 0.039801 | -0.14125 | 120.8323 | 0.006354 | 120.9651 | 120.9282 | 0.095851 | 0.037008 | 0.19234 | 120.7404 | -0.029942 | 120.956 | 120.8848 | 0.14443 | 0.059506 | -0.024286 | 120.9521 | 120.9827 | 121.1381 | 120.906 | -0.11341 | 120.9158 | 121.0052 | 120.9215 | 120.9003 | -0.20534
3180.4219 | 121.138 | -120.8633 | 0.073242 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.023148 | 0.0050659 | 0.23258 | 0.024812 | 0.034818 | -0.096424 | -0.0027159 | 0.00064308 | 0.083459 | 0.015142 | 0.028217 | 0.070441 | 0.1011 | 0.25643 | -0.012689 | 0.074307 | 0.027831 | 0.003172 | 0.029566 | 0.12817 | 0.030644 | -0.14125 | 120.8507 | -0.002801 | 120.9468 | 120.8916 | 0.040906 | 0.027853 | 0.18319 | 120.7221 | -0.043676 | 120.9376 | 120.8665 | 0.14443 | 0.05493 | -0.042598 | 120.9338 | 120.9644 | 121.1198 | 120.8785 | -0.085931 | 120.8929 | 120.9915 | 120.894 | 120.8912 | -0.2145
3182.1562 | 121.1884 | -120.8908 | 0.082397 | 1.4211e-13 | 0.024801 | 0.016346 | 0.009682 | -0.023148 | 0.0050659 | 0.23258 | 0.024171 | 0.035031 | -0.096851 | -0.0027159 | 0.00042948 | 0.07888 | 0.015142 | 0.037373 | 0.070441 | 0.10567 | 0.24727 | -0.026426 | 0.074307 | 0.027831 | -0.001407 | 0.038723 | 0.13275 | 0.026065 | -0.14125 | 120.8644 | -0.011956 | 120.9697 | 120.9282 | 0.063799 | 0.023277 | 0.16488 | 120.7496 | -0.043674 | 120.9651 | 120.8894 | 0.13985 | 0.050353 | -0.056332 | 120.9612 | 120.9965 | 121.1381 | 120.906 | -0.10882 | 120.9295 | 121.0236 | 120.9169 | 120.9186 | -0.22365
3183.9531 | 121.2387 | -120.8908 | 0.059509 | 1.4211e-13 | 0.025015 | 0.016346 | 0.0098956 | -0.023148 | 0.0044249 | 0.24021 | 0.024171 | 0.034818 | -0.096637 | -0.0027159 | 0.0012841 | 0.07888 | 0.015142 | 0.041952 | 0.079598 | 0.096516 | 0.25185 | -0.040163 | 0.069728 | 0.023253 | -0.001407 | 0.038723 | 0.12359 | 0.048958 | -0.13668 | 120.8506 | 0.020089 | 120.9697 | 120.9328 | 0.082115 | 0.037007 | 0.19234 | 120.7541 | -0.020786 | 120.9605 | 120.8894 | 0.13527 | 0.064084 | -0.010551 | 120.9704 | 120.9873 | 121.1427 | 120.906 | -0.099672 | 120.9295 | 121.0144 | 120.9398 | 120.9141 | -0.19618
3185.6719 | 121.1563 | -120.9091 | 0.054932 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023362 | 0.0048523 | 0.23258 | 0.024598 | 0.034818 | -0.096851 | -0.0020749 | 0.00064308 | 0.074302 | 0.019721 | 0.023639 | 0.07502 | 0.1011 | 0.25643 | -0.035584 | 0.074307 | 0.023253 | -0.001407 | 0.029566 | 0.13275 | 0.030644 | -0.14125 | 120.8735 | 0.020088 | 120.9834 | 120.9328 | 0.059223 | 0.046163 | 0.2015 | 120.7679 | -0.025366 | 120.9834 | 120.9077 | 0.13985 | 0.077818 | -0.024288 | 120.9841 | 121.0102 | 121.1656 | 120.9288 | -0.090516 | 120.9387 | 121.0419 | 120.9398 | 120.9324 | -0.19619
3187.4531 | 121.2296 | -120.8954 | 0.054932 | 1.4211e-13 | 0.025228 | 0.01656 | 0.010109 | -0.023148 | 0.0046387 | 0.24021 | 0.024171 | 0.035031 | -0.097065 | -0.0027159 | 0.00021588 | 0.083459 | 0.015142 | 0.032795 | 0.07502 | 0.1011 | 0.25185 | -0.040163 | 0.083464 | 0.027831 | 0.003172 | 0.034145 | 0.12817 | 0.021486 | -0.14125 | 120.8552 | 0.020088 | 120.9788 | 120.9282 | 0.072958 | 0.046163 | 0.19692 | 120.7541 | -0.020787 | 120.9789 | 120.8986 | 0.14443 | 0.07324 | -0.033446 | 120.9704 | 120.9965 | 121.1472 | 120.9105 | -0.095095 | 120.9295 | 121.0236 | 120.9169 | 120.9232 | -0.19619
3189.1562 | 121.2524 | -120.9366 | 0.050354 | 1.4211e-13 | 0.025015 | 0.015919 | 0.0098956 | -0.023148 | 0.0046387 | 0.23258 | 0.024385 | 0.034818 | -0.09621 | -0.0029295 | 0.00064308 | 0.07888 | 0.0243 | 0.037373 | 0.070441 | 0.096516 | 0.25185 | -0.053899 | 0.078886 | 0.027831 | 0.003172 | 0.034145 | 0.12817 | 0.039801 | -0.14125 | 120.8827 | 0.020087 | 121.0155 | 120.974 | 0.091272 | 0.046162 | 0.2015 | 120.7953 | -0.016209 | 121.0155 | 120.9398 | 0.14443 | 0.077818 | -0.010553 | 121.007 | 121.0331 | 121.1884 | 120.9609 | -0.10425 | 120.9707 | 121.0648 | 120.9764 | 120.9644 | -0.19161
3190.875 | 121.0922 | -120.9915 | 0.07782 | 1.4211e-13 | 0.025015 | 0.016133 | 0.010109 | -0.023576 | 0.0048523 | 0.24784 | 0.024385 | 0.034818 | -0.096851 | -0.0025021 | 0.00064308 | 0.07888 | 0.0243 | 0.037373 | 0.070441 | 0.1011 | 0.25185 | -0.012689 | 0.078886 | 0.027831 | 0.007751 | 0.043302 | 0.11901 | 0.030644 | -0.14125 | 120.9788 | -0.007379 | 121.0704 | 121.0289 | 0.050062 | 0.023275 | 0.17403 | 120.8503 | -0.034518 | 121.0704 | 120.9993 | 0.14901 | 0.041194 | -0.047176 | 121.062 | 121.0926 | 121.2434 | 121.0158 | -0.090509 | 121.0348 | 121.1105 | 121.0222 | 121.0193 | -0.21907
3192.5938 | 121.1746 | -121.0052 | 0.10986 | 1.4211e-13 | 0.025228 | 0.016346 | 0.0098956 | -0.023148 | 0.0046387 | 0.24784 | 0.024385 | 0.035031 | -0.096424 | -0.0027159 | 0.00064308 | 0.074302 | 0.015142 | 0.032795 | 0.079598 | 0.096516 | 0.24269 | -0.031005 | 0.078886 | 0.023253 | -0.001407 | 0.029566 | 0.12817 | 0.035222 | -0.14583 | 120.9742 | -0.030265 | 121.0796 | 121.038 | 0.0638 | -0.013347 | 0.13283 | 120.8594 | -0.080297 | 121.0841 | 121.0038 | 0.14443 | 0.018309 | -0.074641 | 121.0848 | 121.1018 | 121.2479 | 121.0204 | -0.14087 | 121.0348 | 121.1334 | 121.0405 | 121.0285 | -0.2557
3194.3281 | 121.2662 | -120.9686 | 0.086975 | 1.4211e-13 | 0.025015 | 0.016346 | 0.010323 | -0.023148 | 0.0046387 | 0.24021 | 0.024171 | 0.034818 | -0.096851 | -0.0022885 | 0.00064308 | 0.07888 | 0.019721 | 0.032795 | 0.07502 | 0.10567 | 0.24269 | -0.076794 | 0.078886 | 0.027831 | 0.007751 | 0.038723 | 0.12359 | 0.044379 | -0.14583 | 120.8918 | -0.011955 | 121.0475 | 121.0014 | 0.10959 | 0.018699 | 0.15572 | 120.8228 | -0.048252 | 121.0475 | 120.9764 | 0.15358 | 0.036618 | -0.042596 | 121.0436 | 121.0743 | 121.2113 | 120.9883 | -0.16377 | 121.0074 | 121.0922 | 121.013 | 120.9965 | -0.23281
3196.0469 | 121.1792 | -120.9732 | 0.13733 | 1.4211e-13 | 0.025015 | 0.016133 | 0.010109 | -0.022721 | 0.0046387 | 0.23258 | 0.024385 | 0.035031 | -0.097065 | -0.0022885 | 0.00085668 | 0.07888 | 0.015142 | 0.032795 | 0.07502 | 0.1011 | 0.25185 | -0.067636 | 0.078886 | 0.036989 | 0.01233 | 0.034145 | 0.12817 | 0.044379 | -0.14125 | 120.9056 | -0.062309 | 121.0521 | 121.006 | 0.10043 | -0.036234 | 0.11452 | 120.832 | -0.10318 | 121.0521 | 120.9855 | 0.15358 | -0.009157 | -0.09295 | 121.0482 | 121.0743 | 121.2251 | 120.9883 | -0.20497 | 121.0074 | 121.1014 | 121.0176 | 121.0102 | -0.27858
3197.75 | 121.225 | -121.0236 | 0.073242 | 1.4211e-13 | 0.025015 | 0.016346 | 0.010109 | -0.023148 | 0.0042113 | 0.24021 | 0.024598 | 0.035031 | -0.096424 | -0.0025021 | 0.00064308 | 0.07888 | 0.015142 | 0.037373 | 0.070441 | 0.096516 | 0.24727 | -0.044742 | 0.078886 | 0.03241 | 0.003172 | 0.034145 | 0.11901 | 0.044379 | -0.14583 | 120.9788 | -0.002801 | 121.1024 | 121.0609 | 0.082115 | 0.023274 | 0.17403 | 120.8777 | -0.039097 | 121.1024 | 121.0267 | 0.149 | 0.045772 | -0.028863 | 121.094 | 121.1201 | 121.2708 | 121.0387 | -0.11798 | 121.0577 | 121.1426 | 121.0679 | 121.056 | -0.21907
3199.4688 | 121.225 | -121.0098 | 0.059509 | 1.4211e-13 | 0.024801 | 0.016346 | 0.010109 | -0.022935 | 0.0046387 | 0.24021 | 0.024385 | 0.035245 | -0.096424 | -0.0025021 | 0.00064308 | 0.083459 | 0.0243 | 0.037373 | 0.079598 | 0.1011 | 0.25185 | -0.063057 | 0.078886 | 0.027831 | 0.007751 | 0.034145 | 0.12359 | 0.048958 | -0.13668 | 120.9468 | 0.020089 | 121.0933 | 121.0472 | 0.10043 | 0.041586 | 0.19234 | 120.8732 | -0.025364 | 121.0887 | 121.0176 | 0.14443 | 0.064084 | -0.010551 | 121.0894 | 121.1109 | 121.2617 | 121.0341 | -0.12257 | 121.044 | 121.1334 | 121.0588 | 121.0377 | -0.19618
3201.2031 | 121.1975 | -121.051 | 0.091553 | 1.4211e-13 | 0.025015 | 0.015919 | 0.010323 | -0.023148 | 0.0046387 | 0.22495 | 0.024385 | 0.034818 | -0.096637 | -0.0025021 | 0.00064308 | 0.069723 | 0.019721 | 0.032795 | 0.079598 | 0.1011 | 0.24269 | -0.040163 | 0.083464 | 0.03241 | 0.003172 | 0.029566 | 0.12817 | 0.030644 | -0.14583 | 121.0109 | -0.011955 | 121.1207 | 121.0838 | 0.072958 | 0.009542 | 0.15114 | 120.9052 | -0.061987 | 121.1345 | 121.0542 | 0.149 | 0.036619 | -0.060909 | 121.1306 | 121.1521 | 121.2937 | 121.0707 | -0.13172 | 121.0806 | 121.1792 | 121.0817 | 121.0834 | -0.23739
3202.9688 | 121.2433 | -121.0602 | 0.064087 | 1.4211e-13 | 0.025015 | 0.016346 | 0.010109 | -0.023148 | 0.0050659 | 0.23258 | 0.024385 | 0.034818 | -0.096424 | -0.0029295 | 0.00042948 | 0.07888 | 0.019721 | 0.037373 | 0.079598 | 0.096516 | 0.25185 | -0.063057 | 0.074307 | 0.03241 | -0.001407 | 0.029566 | 0.12359 | 0.039801 | -0.14583 | 120.9971 | 0.015511 | 121.1391 | 121.0976 | 0.10043 | 0.032429 | 0.18777 | 120.9143 | -0.034521 | 121.1345 | 121.0588 | 0.14443 | 0.059506 | -0.024286 | 121.1398 | 121.1567 | 121.312 | 121.0799 | -0.12714 | 121.0897 | 121.1838 | 121.1 | 121.0926 | -0.20992
3204.6875 | 121.3165 | -120.9824 | 0.059509 | 1.4211e-13 | 0.024801 | 0.015919 | 0.010109 | -0.023362 | 0.0046387 | 0.24021 | 0.024171 | 0.034818 | -0.096851 | -0.0025021 | 0.00064308 | 0.07888 | 0.010564 | 0.028217 | 0.07502 | 0.10567 | 0.24727 | -0.081373 | 0.078886 | 0.023253 | 0.003172 | 0.029566 | 0.12817 | 0.030644 | -0.14125 | 120.901 | 0.015511 | 121.0612 | 121.0106 | 0.10959 | 0.046165 | 0.18776 | 120.8411 | -0.029943 | 121.0612 | 120.9855 | 0.14443 | 0.068663 | -0.028865 | 121.0574 | 121.088 | 121.2296 | 120.9929 | -0.14088 | 121.0119 | 121.1105 | 121.013 | 121.0056 | -0.20076
3206.4062 | 121.3806 | -120.9961 | 0.086975 | 1.4211e-13 | 0.025228 | 0.01656 | 0.010323 | -0.023362 | 0.0046387 | 0.23258 | 0.024385 | 0.034818 | -0.096637 | -0.0027159 | 0.00042948 | 0.083459 | 0.015142 | 0.037373 | 0.079598 | 0.1011 | 0.25643 | -0.072215 | 0.078886 | 0.023253 | -0.001407 | 0.034145 | 0.13733 | 0.035222 | -0.14125 | 120.9239 | -0.007377 | 121.0796 | 121.0335 | 0.10959 | 0.01412 | 0.16946 | 120.8548 | -0.05283 | 121.075 | 120.9947 | 0.13985 | 0.050354 | -0.051753 | 121.0757 | 121.0972 | 121.2525 | 121.0112 | -0.15919 | 121.0302 | 121.1334 | 121.0313 | 121.0193 | -0.22823
3208.125 | 121.4035 | -121.0373 | 0.07782 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010323 | -0.023362 | 0.0048523 | 0.23258 | 0.024171 | 0.034818 | -0.096851 | -0.0025021 | 0.00042948 | 0.083459 | 0.015142 | 0.041952 | 0.07502 | 0.096516 | 0.24269 | -0.063057 | 0.083464 | 0.027831 | -0.001407 | 0.029566 | 0.13275 | 0.035222 | -0.15041 | 120.9742 | -0.0028 | 121.1208 | 121.0792 | 0.10501 | 0.018696 | 0.16487 | 120.8869 | -0.048254 | 121.1208 | 121.0359 | 0.149 | 0.05493 | -0.042598 | 121.1123 | 121.1338 | 121.28 | 121.0524 | -0.14088 | 121.0669 | 121.17 | 121.0725 | 121.0651 | -0.22823
3209.8906 | 121.3211 | -121.0419 | 0.068665 | 1.4211e-13 | 0.024801 | 0.015919 | 0.009682 | -0.023362 | 0.0048523 | 0.23258 | 0.024385 | 0.034818 | -0.096851 | -0.0022885 | 0.00064308 | 0.07888 | 0.019721 | 0.037373 | 0.07502 | 0.1011 | 0.25185 | -0.053899 | 0.074307 | 0.03241 | 0.003172 | 0.034145 | 0.12817 | 0.026065 | -0.14125 | 120.988 | 0.006355 | 121.1208 | 121.0792 | 0.091272 | 0.03243 | 0.18319 | 120.9006 | -0.03452 | 121.1162 | 121.045 | 0.14443 | 0.059507 | -0.0426 | 121.1169 | 121.143 | 121.2937 | 121.0616 | -0.12256 | 121.076 | 121.17 | 121.0679 | 121.0743 | -0.20992
3211.6094 | 121.2616 | -121.0968 | 0.086975 | 1.4211e-13 | 0.024587 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.23258 | 0.024171 | 0.035031 | -0.096851 | -0.0022885 | 0.00085668 | 0.07888 | 0.015142 | 0.037373 | 0.07502 | 0.096516 | 0.25643 | -0.031005 | 0.083464 | 0.03241 | 0.01233 | 0.038723 | 0.12359 | 0.048958 | -0.14125 | 121.0658 | -0.011955 | 121.1757 | 121.1342 | 0.068378 | 0.009541 | 0.16946 | 120.9555 | -0.048252 | 121.1803 | 121.1091 | 0.15358 | 0.036618 | -0.038017 | 121.1718 | 121.1933 | 121.3532 | 121.1119 | -0.11798 | 121.1355 | 121.2204 | 121.1458 | 121.1292 | -0.22823
3213.3125 | 121.2799 | -121.138 | 0.10071 | 1.4211e-13 | 0.024801 | 0.016133 | 0.009682 | -0.023362 | 0.0046387 | 0.24021 | 0.024385 | 0.034604 | -0.096851 | -0.0027159 | 0.00064308 | 0.074302 | 0.019721 | 0.037373 | 0.07502 | 0.096516 | 0.25643 | -0.035584 | 0.088043 | 0.03241 | 0.007751 | 0.034145 | 0.12817 | 0.044379 | -0.14125 | 121.1024 | -0.025688 | 121.2123 | 121.1754 | 0.072957 | -0.004192 | 0.15572 | 120.9967 | -0.066563 | 121.226 | 121.1458 | 0.14901 | 0.027464 | -0.056329 | 121.213 | 121.2345 | 121.3944 | 121.1577 | -0.13629 | 121.1721 | 121.2662 | 121.1824 | 121.1704 | -0.24196
3215.0312 | 121.2433 | -121.0922 | 0.12817 | 1.4211e-13 | 0.025015 | 0.016133 | 0.010109 | -0.023362 | 0.0048523 | 0.24021 | 0.024598 | 0.034604 | -0.096637 | -0.0025021 | 0.00042948 | 0.07888 | 0.019721 | 0.041952 | 0.079598 | 0.096516 | 0.25185 | -0.063057 | 0.083464 | 0.027831 | 0.003172 | 0.038723 | 0.12817 | 0.039801 | -0.14125 | 121.0292 | -0.048576 | 121.1711 | 121.1342 | 0.10501 | -0.031658 | 0.12368 | 120.951 | -0.089451 | 121.1757 | 121.0954 | 0.14443 | -2e-06 | -0.088373 | 121.1718 | 121.1887 | 121.3441 | 121.1119 | -0.19123 | 121.1309 | 121.2204 | 121.132 | 121.1201 | -0.26943
3216.7344 | 121.3211 | -121.0327 | 0.10986 | 1.4211e-13 | 0.025015 | 0.016774 | 0.009682 | -0.023148 | 0.0046387 | 0.24784 | 0.024171 | 0.035031 | -0.096424 | -0.0027159 | 0.00064308 | 0.083459 | 0.019721 | 0.032795 | 0.065863 | 0.1011 | 0.25185 | -0.035584 | 0.078886 | 0.027831 | 0.007751 | 0.034145 | 0.13275 | 0.039801 | -0.14125 | 120.9971 | -0.044 | 121.1162 | 121.0655 | 0.068379 | -0.008768 | 0.14199 | 120.8915 | -0.075718 | 121.1116 | 121.0405 | 0.14901 | 0.022887 | -0.070062 | 121.0986 | 121.1338 | 121.2846 | 121.0524 | -0.14545 | 121.0669 | 121.1655 | 121.0725 | 121.0605 | -0.25112
3218.5 | 120.3323 | -8.6517 | 112.0651 | 1.4211e-13 | 0.024801 | 0.016346 | 0.009682 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.034818 | -0.096637 | -0.0022885 | 0.00085668 | 0.037675 | -0.021486 | -0.008409 | 0.038393 | 0.059885 | 0.21064 | -0.090531 | 0.033099 | -0.00422 | -0.033458 | -0.01164 | 0.086964 | -0.065507 | -0.18246 | 8.5612 | -112.0267 | 8.6894 | 8.6433 | 0.082122 | -112.0052 | -111.8545 | 8.4693 | -112.0768 | 8.6848 | 8.6183 | 0.14901 | -111.9782 | -112.1306 | 8.6901 | 8.7116 | 8.8624 | 8.6302 | -112.1557 | 8.6401 | 8.7387 | 8.5862 | 8.6475 | -112.2476
3220.2031 | 120.3873 | -9.2148 | 111.1816 | 1.4211e-13 | 0.025228 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.22495 | 0.024385 | 0.034818 | -0.096637 | -0.0025021 | 0.00064308 | 0.042253 | -0.016908 | -0.003831 | 0.042971 | 0.055306 | 0.21522 | -0.12258 | 0.037677 | -0.008798 | -0.033458 | -0.007062 | 0.091543 | -0.0884 | -0.17788 | 9.0922 | -111.1387 | 9.257 | 9.211 | 0.11875 | -111.1263 | -110.9664 | 9.0369 | -111.1887 | 9.2525 | 9.1813 | 0.14443 | -111.0901 | -111.27 | 9.2578 | 9.2701 | 9.43 | 9.1979 | -111.3042 | 9.2077 | 9.3063 | 9.1264 | 9.206 | -111.3595
3221.9062 | 121.2433 | -6.2164 | 114.8392 | 1.4211e-13 | 0.025228 | 0.016774 | 0.0098956 | -0.023362 | 0.0044249 | 0.23258 | 0.024171 | 0.034604 | -0.096424 | -0.0025021 | 0.00064308 | 0.05141 | -0.026065 | 0.000747 | 0.038393 | 0.059885 | 0.21522 | -0.099689 | 0.033099 | -0.008798 | -0.038036 | -0.007062 | 0.086964 | -0.074664 | -0.18246 | 6.1167 | -114.8008 | 6.2678 | 6.2172 | 0.10044 | -114.7793 | -114.6239 | 6.034 | -114.8462 | 6.2495 | 6.1784 | 0.14443 | -114.7522 | -114.9138 | 6.2548 | 6.2763 | 6.4317 | 6.1904 | -114.9389 | 6.2094 | 6.3034 | 6.1418 | 6.2076 | -115.0216
3223.6094 | 121.2479 | -4.7012 | 116.423 | 1.4211e-13 | 0.024801 | 0.016346 | 0.009682 | -0.022935 | 0.0046387 | 0.23258 | 0.024385 | 0.034818 | -0.096424 | -0.0022885 | 0.00064308 | 0.037675 | -0.026065 | -0.008409 | 0.042971 | 0.059885 | 0.21522 | -0.10885 | 0.046835 | 0.000359 | -0.033458 | -0.007062 | 0.086964 | -0.074664 | -0.18704 | 4.5924 | -116.3801 | 4.7389 | 4.6928 | 0.10044 | -116.3632 | -116.2078 | 4.5142 | -116.4301 | 4.7481 | 4.6678 | 0.15358 | -116.3361 | -116.4977 | 4.7442 | 4.7611 | 4.9165 | 4.6752 | -116.5319 | 4.6942 | 4.7882 | 4.6266 | 4.7016 | -116.6101
3225.3906 | 121.1609 | -5.9143 | 114.592 | 1.4211e-13 | 0.025015 | 0.016774 | 0.0098956 | -0.022935 | 0.0046387 | 0.24021 | 0.024385 | 0.034604 | -0.096424 | -0.0027159 | 0.00064308 | 0.046831 | -0.021486 | -0.003831 | 0.033814 | 0.059885 | 0.20607 | -0.10427 | 0.033099 | -0.00422 | -0.038036 | -0.007062 | 0.091543 | -0.070086 | -0.18246 | 5.81 | -114.5582 | 5.9611 | 5.9105 | 0.10044 | -114.5321 | -114.3859 | 5.7318 | -114.599 | 5.9474 | 5.8763 | 0.14443 | -114.5004 | -114.6621 | 5.9481 | 5.9742 | 6.1204 | 5.8928 | -114.6962 | 5.9072 | 6.0058 | 5.8442 | 5.9101 | -114.7744
3227.1094 | 121.2021 | -3.3142 | 117.7368 | 1.4211e-13 | 0.024801 | 0.016346 | 0.010109 | -0.023362 | 0.0050659 | 0.22495 | 0.024385 | 0.034604 | -0.096424 | -0.0025021 | 0.00064308 | 0.037675 | -0.016908 | 0.000747 | 0.033814 | 0.055306 | 0.21064 | -0.10427 | 0.033099 | -0.00422 | -0.033458 | -0.01164 | 0.091543 | -0.10214 | -0.17788 | 3.2099 | -117.703 | 3.3519 | 3.315 | 0.10501 | -117.6815 | -117.5262 | 3.1363 | -117.7485 | 3.3473 | 3.2808 | 0.14443 | -117.6453 | -117.839 | 3.348 | 3.3695 | 3.5249 | 3.2973 | -117.8411 | 3.3026 | 3.4058 | 3.2121 | 3.31 | -117.9147
3228.8438 | 121.2112 | -3.1174 | 118.1259 | 1.4211e-13 | 0.024801 | 0.01656 | 0.0098956 | -0.023148 | 0.0046387 | 0.23258 | 0.024385 | 0.034818 | -0.096851 | -0.0027159 | 0.00064308 | 0.037675 | -0.021486 | -0.003831 | 0.042971 | 0.055306 | 0.21064 | -0.10885 | 0.042256 | -0.008798 | -0.042615 | -0.007062 | 0.091543 | -0.079243 | -0.18704 | 3.0085 | -118.0829 | 3.155 | 3.1135 | 0.10502 | -118.0706 | -117.9153 | 2.9303 | -118.133 | 3.1596 | 3.0748 | 0.14443 | -118.0344 | -118.2052 | 3.1603 | 3.1727 | 3.328 | 3.0959 | -118.2348 | 3.1103 | 3.2089 | 3.0381 | 3.1086 | -118.313
3230.5625 | 121.3303 | -3.7765 | 117.5079 | 1.4211e-13 | 0.024801 | 0.016346 | 0.009682 | -0.023362 | 0.0046387 | 0.24021 | 0.024598 | 0.035031 | -0.096851 | -0.0027159 | 0.00085668 | 0.042253 | -0.021486 | -0.008409 | 0.042971 | 0.055306 | 0.20607 | -0.11342 | 0.033099 | -0.00422 | -0.038036 | -0.002483 | 0.086964 | -0.070086 | -0.17788 | 3.6631 | -117.465 | 3.8188 | 3.7681 | 0.10502 | -117.4526 | -117.3019 | 3.5987 | -117.5104 | 3.8096 | 3.7385 | 0.13985 | -117.421 | -117.578 | 3.8195 | 3.8319 | 3.9826 | 3.7551 | -117.6214 | 3.7741 | 3.8635 | 3.7065 | 3.7723 | -117.6858
3232.2812 | 121.3028 | -9.1782 | 111.9232 | 1.4211e-13 | 0.024801 | 0.01656 | 0.0098956 | -0.023362 | 0.0046387 | 0.24784 | 0.024171 | 0.03439 | -0.096637 | -0.0025021 | 0.00085668 | 0.037675 | -0.021486 | -0.012988 | 0.038393 | 0.059885 | 0.21064 | -0.10427 | 0.033099 | -0.00422 | -0.047194 | -0.007062 | 0.086964 | -0.074664 | -0.18704 | 9.0739 | -111.8848 | 9.2158 | 9.1652 | 0.09128 | -111.8633 | -111.7126 | 8.9911 | -111.9303 | 9.2113 | 9.131 | 0.13985 | -111.8363 | -111.9979 | 9.2166 | 9.238 | 9.3888 | 9.1567 | -112.0275 | 9.1711 | 9.2651 | 9.1035 | 9.1739 | -112.1103
3234.0156 | 121.1517 | -5.0629 | 115.6494 | 1.4211e-13 | 0.024801 | 0.016346 | 0.009682 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.034818 | -0.096424 | -0.0022885 | 0.00064308 | 0.037675 | -0.016908 | -0.003831 | 0.042971 | 0.059885 | 0.21064 | -0.099689 | 0.046835 | -0.013377 | -0.038036 | -0.01164 | 0.086964 | -0.079243 | -0.17788 | 4.9632 | -115.6064 | 5.1005 | 5.059 | 0.095858 | -115.5895 | -115.4388 | 4.885 | -115.6611 | 5.1097 | 5.0248 | 0.13985 | -115.5624 | -115.7287 | 5.1058 | 5.1228 | 5.2735 | 5.046 | -115.7491 | 5.0512 | 5.1498 | 4.9836 | 5.0495 | -115.8273
3235.7344 | 121.3303 | -4.3488 | 116.89 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023148 | 0.0046387 | 0.24021 | 0.024598 | 0.034818 | -0.096637 | -0.0025021 | 0.00085668 | 0.037675 | -0.016908 | -0.003831 | 0.038393 | 0.055306 | 0.21064 | -0.10885 | 0.042256 | 0.000359 | -0.038036 | -0.002483 | 0.082386 | -0.028878 | -0.17788 | 4.2399 | -116.8516 | 4.3864 | 4.3449 | 0.10502 | -116.8346 | -116.6793 | 4.1709 | -116.8924 | 4.391 | 4.3107 | 0.13985 | -116.8076 | -116.9188 | 4.3871 | 4.4041 | 4.5594 | 4.3318 | -116.9988 | 4.3463 | 4.4311 | 4.3199 | 4.3491 | -117.0678
3237.4531 | 121.376 | -4.9942 | 115.535 | 1.4211e-13 | 0.024587 | 0.01656 | 0.0094682 | -0.023362 | 0.0046387 | 0.24021 | 0.024812 | 0.034818 | -0.096851 | -0.0027159 | 0.00042948 | 0.037675 | -0.016908 | -0.008409 | 0.042971 | 0.064464 | 0.21064 | -0.099689 | 0.042256 | -0.00422 | -0.033458 | -0.01164 | 0.086964 | -0.0884 | -0.17788 | 4.8945 | -115.492 | 5.0319 | 4.9858 | 0.09128 | -115.4705 | -115.3243 | 4.8163 | -115.5466 | 5.0365 | 4.9607 | 0.14443 | -115.448 | -115.6234 | 5.0372 | 5.0587 | 5.2048 | 4.9773 | -115.6347 | 4.9826 | 5.0812 | 4.9058 | 4.99 | -115.7129
3239.1875 | 121.4539 | -113.4567 | 7.4615 | 1.4211e-13 | 0.025015 | 0.016133 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024598 | 0.035031 | -0.096851 | -0.0027159 | 0.00085668 | 0.074302 | 0.010564 | 0.032795 | 0.07502 | 0.10567 | 0.25185 | -0.063057 | 0.069728 | 0.023253 | 0.003172 | 0.029566 | 0.12359 | 0.035222 | -0.14583 | 113.3937 | -7.3865 | 113.531 | 113.4895 | 0.095852 | -7.3559 | -7.2097 | 113.3109 | -7.432 | 113.5265 | 113.4599 | 0.149 | -7.338 | -7.4263 | 113.5317 | 113.5624 | 113.7086 | 113.4673 | -7.5246 | 113.4863 | 113.5803 | 113.4919 | 113.48 | -7.6074
3240.9688 | 121.4584 | -120.9732 | 0.16479 | 1.4211e-13 | 0.025228 | 0.016346 | 0.009682 | -0.023148 | 0.0046387 | 0.24021 | 0.024812 | 0.034818 | -0.096637 | -0.0027159 | 0.00085668 | 0.07888 | 0.019721 | 0.041952 | 0.07502 | 0.096516 | 0.24727 | -0.058478 | 0.078886 | 0.03241 | 0.007751 | 0.034145 | 0.12817 | 0.026065 | -0.1321 | 120.9147 | -0.089775 | 121.0521 | 121.0152 | 0.10043 | -0.068279 | 0.082479 | 120.8411 | -0.13065 | 121.0521 | 120.981 | 0.13985 | -0.036623 | -0.13873 | 121.0482 | 121.0697 | 121.2205 | 120.9929 | -0.22327 | 121.0074 | 121.1014 | 120.9993 | 121.0056 | -0.29689
3242.6875 | 121.4447 | -120.8496 | 0.30212 | 1.4211e-13 | 0.024374 | 0.016346 | 0.009682 | -0.023362 | 0.0048523 | 0.24021 | 0.024171 | 0.034604 | -0.096637 | -0.0025021 | 0.00085668 | 0.07888 | 0.015142 | 0.041952 | 0.07502 | 0.096516 | 0.25185 | -0.031005 | 0.083464 | 0.027831 | -0.001407 | 0.034145 | 0.12359 | 0.044379 | -0.14125 | 120.8186 | -0.2271 | 120.9285 | 120.8916 | 0.072957 | -0.20561 | -0.050272 | 120.7084 | -0.26798 | 120.9331 | 120.8482 | 0.13985 | -0.17853 | -0.25775 | 120.9246 | 120.9461 | 121.1015 | 120.8648 | -0.33313 | 120.8838 | 120.9732 | 120.894 | 120.8774 | -0.44338
3244.4688 | 121.4035 | -120.5704 | 0.6546 | 1.4211e-13 | 0.024587 | 0.016346 | 0.010109 | -0.023148 | 0.0046387 | 0.22495 | 0.024385 | 0.03439 | -0.096637 | -0.0027159 | 0.00085668 | 0.088037 | 0.0243 | 0.037373 | 0.079598 | 0.096516 | 0.24727 | -0.049321 | 0.083464 | 0.03241 | 0.003172 | 0.034145 | 0.11901 | 0.035222 | -0.14125 | 120.5211 | -0.575 | 120.6584 | 120.6077 | 0.086694 | -0.55809 | -0.40733 | 120.4291 | -0.62046 | 120.6538 | 120.5735 | 0.14443 | -0.53559 | -0.61938 | 120.65 | 120.6669 | 120.8176 | 120.5947 | -0.70392 | 120.6045 | 120.6894 | 120.6056 | 120.6028 | -0.79586
3246.1719 | 121.344 | -120.8176 | 0.41199 | 1.4211e-13 | 0.024587 | 0.016346 | 0.0098956 | -0.023148 | 0.0044249 | 0.24784 | 0.024171 | 0.034604 | -0.096424 | -0.0025021 | 0.00064308 | 0.088037 | 0.019721 | 0.037373 | 0.079598 | 0.1011 | 0.25185 | -0.049321 | 0.074307 | 0.03241 | 0.003172 | 0.034145 | 0.12817 | 0.044379 | -0.13668 | 120.7682 | -0.33239 | 120.9056 | 120.8549 | 0.086694 | -0.31089 | -0.16013 | 120.6809 | -0.37784 | 120.8919 | 120.8207 | 0.13985 | -0.28381 | -0.36761 | 120.8972 | 120.9187 | 121.0694 | 120.8373 | -0.46131 | 120.8517 | 120.9457 | 120.8619 | 120.85 | -0.54866
3247.9375 | 121.4401 | -120.8771 | 0.36621 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.022935 | 0.0050659 | 0.24021 | 0.024385 | 0.035031 | -0.096637 | -0.0029295 | 0.00042948 | 0.07888 | 0.019721 | 0.037373 | 0.070441 | 0.10567 | 0.24727 | -0.053899 | 0.074307 | 0.03241 | 0.003172 | 0.029566 | 0.13275 | 0.035222 | -0.1321 | 120.8232 | -0.29577 | 120.956 | 120.9144 | 0.091272 | -0.26054 | -0.11894 | 120.745 | -0.33665 | 120.9514 | 120.8802 | 0.13527 | -0.23346 | -0.33099 | 120.9475 | 120.9827 | 121.1243 | 120.8968 | -0.42011 | 120.9066 | 121.0098 | 120.9123 | 120.9095 | -0.49831
3249.6406 | 121.3394 | -120.8221 | 0.44861 | 1.4211e-13 | 0.025015 | 0.016133 | 0.010109 | -0.022935 | 0.0044249 | 0.23258 | 0.024385 | 0.034604 | -0.096851 | -0.0029295 | 0.00064308 | 0.088037 | 0.0243 | 0.032795 | 0.07502 | 0.1011 | 0.25643 | -0.049321 | 0.083464 | 0.027831 | 0.003172 | 0.038723 | 0.12359 | 0.039801 | -0.14125 | 120.7728 | -0.37359 | 120.9102 | 120.8549 | 0.082116 | -0.34751 | -0.19218 | 120.6809 | -0.40988 | 120.9056 | 120.8253 | 0.14443 | -0.32501 | -0.40881 | 120.8972 | 120.9232 | 121.0786 | 120.8464 | -0.49793 | 120.8609 | 120.9457 | 120.8619 | 120.85 | -0.58986
3251.3438 | 121.4539 | -120.9595 | 0.27008 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023148 | 0.0050659 | 0.23258 | 0.024598 | 0.034818 | -0.096424 | -0.0022885 | 0.00064308 | 0.083459 | 0.019721 | 0.028217 | 0.079598 | 0.1011 | 0.25185 | -0.063057 | 0.078886 | 0.027831 | 0.007751 | 0.034145 | 0.13275 | 0.030644 | -0.14125 | 120.8964 | -0.19048 | 121.0429 | 120.9877 | 0.091274 | -0.16899 | -0.018229 | 120.8182 | -0.23594 | 121.0384 | 120.9672 | 0.14901 | -0.13733 | -0.23944 | 121.0391 | 121.0606 | 121.2113 | 120.9792 | -0.33314 | 120.9936 | 121.0922 | 120.9901 | 120.9873 | -0.41134
3253.0781 | 121.4722 | -120.9366 | 0.32959 | 1.4211e-13 | 0.024587 | 0.01656 | 0.0098956 | -0.023148 | 0.0048523 | 0.23258 | 0.023957 | 0.03439 | -0.096424 | -0.0027159 | 0.00064308 | 0.07888 | 0.019721 | 0.032795 | 0.07502 | 0.10567 | 0.24727 | -0.031005 | 0.078886 | 0.036989 | 0.003172 | 0.034145 | 0.12359 | 0.044379 | -0.14125 | 120.9056 | -0.25457 | 121.0155 | 120.9694 | 0.0638 | -0.22392 | -0.082316 | 120.7953 | -0.29545 | 121.0155 | 120.9398 | 0.14443 | -0.206 | -0.28521 | 121.0116 | 121.0423 | 121.1839 | 120.9563 | -0.36059 | 120.9707 | 121.0602 | 120.981 | 120.9736 | -0.47084
3254.7969 | 121.4355 | -120.8542 | 0.36621 | 1.4211e-13 | 0.025015 | 0.01656 | 0.010109 | -0.023148 | 0.0050659 | 0.23258 | 0.024385 | 0.034604 | -0.096637 | -0.0025021 | 0.00085668 | 0.07888 | 0.015142 | 0.037373 | 0.07502 | 0.1011 | 0.24727 | -0.063057 | 0.069728 | 0.027831 | 0.003172 | 0.034145 | 0.11901 | 0.035222 | -0.14583 | 120.7911 | -0.29119 | 120.9331 | 120.8916 | 0.10043 | -0.26512 | -0.11894 | 120.7084 | -0.33207 | 120.9239 | 120.8574 | 0.149 | -0.2472 | -0.33099 | 120.9292 | 120.9553 | 121.1015 | 120.8693 | -0.42927 | 120.8883 | 120.9732 | 120.8894 | 120.882 | -0.51204
3256.5156 | 121.4859 | -120.9503 | 0.32044 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0025021 | 0.00064308 | 0.07888 | 0.019721 | 0.032795 | 0.070441 | 0.1011 | 0.25185 | -0.017268 | 0.078886 | 0.023253 | 0.003172 | 0.038723 | 0.12817 | 0.039801 | -0.14125 | 120.933 | -0.24999 | 121.0292 | 120.9831 | 0.050063 | -0.21934 | -0.068583 | 120.8091 | -0.28171 | 121.0292 | 120.9535 | 0.14443 | -0.19226 | -0.28063 | 121.0208 | 121.0514 | 121.2022 | 120.97 | -0.3377 | 120.989 | 121.0785 | 120.9901 | 120.9736 | -0.46169
3258.2188 | 121.312 | -119.3939 | 1.918 | 1.4211e-13 | 0.025015 | 0.016346 | 0.0098956 | -0.023362 | 0.0048523 | 0.23258 | 0.024385 | 0.034604 | -0.096424 | -0.0029295 | 0.00064308 | 0.07888 | 0.019721 | 0.032795 | 0.07502 | 0.10567 | 0.25185 | -0.040163 | 0.078886 | 0.027831 | 0.003172 | 0.034145 | 0.12817 | 0.039801 | -0.13668 | 119.3538 | -1.843 | 119.4728 | 119.4267 | 0.072958 | -1.8124 | -1.6662 | 119.2572 | -1.8839 | 119.4728 | 119.3971 | 0.13985 | -1.7899 | -1.8782 | 119.4689 | 119.4996 | 119.6458 | 119.4136 | -1.9582 | 119.4281 | 119.5221 | 119.4337 | 119.4218 | -2.0547
3260 | 121.4355 | -121.138 | 0.2243 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023148 | 0.0046387 | 0.24784 | 0.024385 | 0.035031 | -0.096637 | -0.0025021 | 0.00085668 | 0.07888 | 0.019721 | 0.037373 | 0.07502 | 0.1011 | 0.25185 | -0.058478 | 0.088043 | 0.03241 | 0.003172 | 0.029566 | 0.13275 | 0.039801 | -0.13668 | 121.0795 | -0.14928 | 121.2169 | 121.1754 | 0.095851 | -0.12321 | 0.027548 | 121.0013 | -0.19474 | 121.226 | 121.1412 | 0.13985 | -0.091554 | -0.1845 | 121.213 | 121.2391 | 121.3899 | 121.1577 | -0.28278 | 121.1676 | 121.2708 | 121.1778 | 121.1704 | -0.36098
3261.7031 | 121.4218 | -119.7464 | 1.6113 | 1.4211e-13 | 0.024801 | 0.016346 | 0.009682 | -0.023362 | 0.0046387 | 0.23258 | 0.024171 | 0.034604 | -0.096424 | -0.0025021 | 0.0010705 | 0.07888 | 0.019721 | 0.028217 | 0.079598 | 0.096516 | 0.24727 | -0.058478 | 0.074307 | 0.023253 | 0.003172 | 0.034145 | 0.12359 | 0.035222 | -0.1321 | 119.6879 | -1.5317 | 119.8253 | 119.7746 | 0.086695 | -1.5148 | -1.3641 | 119.6143 | -1.5772 | 119.8207 | 119.7496 | 0.13527 | -1.4877 | -1.5761 | 119.826 | 119.8429 | 119.9937 | 119.7661 | -1.6698 | 119.7805 | 119.87 | 119.7816 | 119.7697 | -1.7434
3263.4688 | 121.1563 | -117.2699 | 4.0833 | 1.4211e-13 | 0.024587 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.21732 | 0.024598 | 0.034604 | -0.096424 | -0.0025021 | 0.00085668 | 0.083459 | 0.0243 | 0.032795 | 0.070441 | 0.096516 | 0.24269 | -0.053899 | 0.078886 | 0.018674 | -0.001407 | 0.034145 | 0.13733 | 0.048958 | -0.14125 | 117.216 | -4.0128 | 117.3534 | 117.3027 | 0.086694 | -3.9867 | -3.8406 | 117.1286 | -4.0491 | 117.3488 | 117.2685 | 0.13985 | -3.9459 | -4.0343 | 117.3403 | 117.3664 | 117.5126 | 117.2942 | -4.1372 | 117.304 | 117.4072 | 117.3189 | 117.2886 | -4.2245
3265.1875 | 121.4539 | -119.9066 | 1.4053 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023576 | 0.0048523 | 0.24021 | 0.024598 | 0.034818 | -0.096424 | -0.0027159 | 0.0010705 | 0.07888 | 0.019721 | 0.037373 | 0.079598 | 0.096516 | 0.24727 | -0.072215 | 0.083464 | 0.036989 | 0.003172 | 0.038723 | 0.12817 | 0.030644 | -0.14125 | 119.8344 | -1.3257 | 119.9855 | 119.944 | 0.10959 | -1.3088 | -1.1581 | 119.7654 | -1.3666 | 119.9901 | 119.9098 | 0.14443 | -1.2772 | -1.3747 | 119.9862 | 120.0031 | 120.1539 | 119.9263 | -1.4775 | 119.9453 | 120.0348 | 119.9373 | 119.9436 | -1.5466
3266.9531 | 121.3303 | -118.7805 | 2.4857 | 1.4211e-13 | 0.025015 | 0.016346 | 0.009682 | -0.023362 | 0.0046387 | 0.24021 | 0.024385 | 0.034818 | -0.096851 | -0.0025021 | 0.00042948 | 0.07888 | 0.015142 | 0.037373 | 0.07502 | 0.091937 | 0.26559 | -0.012689 | 0.078886 | 0.027831 | -0.001407 | 0.029566 | 0.13275 | 0.030644 | -0.13668 | 118.7678 | -2.4106 | 118.8594 | 118.8179 | 0.050062 | -2.3937 | -2.2201 | 118.6438 | -2.4561 | 118.8594 | 118.7791 | 0.13527 | -2.3529 | -2.455 | 118.8555 | 118.8725 | 119.0461 | 118.7957 | -2.4983 | 118.8101 | 118.9133 | 118.8112 | 118.8083 | -2.6223
3268.6719 | 121.4859 | -121.0693 | 0.26093 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034604 | -0.096424 | -0.0025021 | 0.00042948 | 0.083459 | 0.015142 | 0.037373 | 0.070441 | 0.1011 | 0.25185 | -0.058478 | 0.083464 | 0.03241 | 0.003172 | 0.029566 | 0.13275 | 0.030644 | -0.1321 | 121.0109 | -0.19048 | 121.1528 | 121.1067 | 0.095851 | -0.15983 | -0.009073 | 120.9372 | -0.23136 | 121.1528 | 121.0725 | 0.13527 | -0.12818 | -0.23028 | 121.1398 | 121.1704 | 121.3212 | 121.0845 | -0.3194 | 121.0989 | 121.2021 | 121.1 | 121.1017 | -0.39302
3270.3906 | 120.163 | -119.8929 | 0.10071 | 1.4211e-13 | 0.024801 | 0.016346 | 0.009682 | -0.023148 | 0.0046387 | 0.22495 | 0.024385 | 0.034818 | -0.096637 | -0.0027159 | 0.00085668 | 0.07888 | 0.010564 | 0.028217 | 0.07502 | 0.091937 | 0.23812 | -0.076794 | 0.074307 | 0.023253 | 0.003172 | 0.029566 | 0.12817 | 0.044379 | -0.13668 | 119.8161 | -0.025688 | 119.9718 | 119.9211 | 0.10501 | -0.008771 | 0.13741 | 119.7562 | -0.071142 | 119.9672 | 119.8961 | 0.13985 | 0.027464 | -0.056329 | 119.9679 | 119.9848 | 120.131 | 119.9034 | -0.1775 | 119.9224 | 120.0211 | 119.9373 | 119.9161 | -0.23738
3272.1094 | 120.0256 | -120.6345 | 0.10071 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.023148 | 0.0046387 | 0.23258 | 0.024171 | 0.034604 | -0.096851 | -0.0025021 | 0.00064308 | 0.083459 | 0.015142 | 0.037373 | 0.07502 | 0.1011 | 0.25185 | -0.044742 | 0.078886 | 0.03241 | 0.007751 | 0.038723 | 0.13275 | 0.026065 | -0.14125 | 120.5897 | -0.025688 | 120.7179 | 120.6718 | 0.082115 | 0.000387 | 0.15114 | 120.4932 | -0.061985 | 120.7133 | 120.6422 | 0.14901 | 0.032042 | -0.074643 | 120.7095 | 120.7356 | 120.8863 | 120.6496 | -0.14545 | 120.6732 | 120.7672 | 120.6605 | 120.6669 | -0.24196
3273.875 | 120.7947 | -120.3598 | 0.32501 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.022935 | 0.0046387 | 0.24784 | 0.024385 | 0.034604 | -0.096424 | -0.0029295 | 0.00042948 | 0.083459 | 0.015142 | 0.032795 | 0.079598 | 0.087359 | 0.25185 | -0.053899 | 0.083464 | 0.036989 | 0.007751 | 0.034145 | 0.13733 | 0.030644 | -0.12752 | 120.3059 | -0.24541 | 120.4433 | 120.3926 | 0.086694 | -0.23765 | -0.07316 | 120.2323 | -0.29087 | 120.4433 | 120.3676 | 0.13527 | -0.18768 | -0.29437 | 120.4394 | 120.4472 | 120.6117 | 120.3749 | -0.37891 | 120.3939 | 120.4971 | 120.3904 | 120.3968 | -0.45253
3275.5781 | 121.0327 | -120.6802 | 0.10986 | 1.4211e-13 | 0.024801 | 0.015919 | 0.0094682 | -0.023362 | 0.0048523 | 0.23258 | 0.024171 | 0.034818 | -0.096424 | -0.0029295 | 0.00064308 | 0.083459 | 0.019721 | 0.028217 | 0.079598 | 0.11025 | 0.24727 | -0.044742 | 0.083464 | 0.023253 | 0.003172 | 0.038723 | 0.12359 | 0.035222 | -0.13668 | 120.6355 | -0.030265 | 120.7637 | 120.7085 | 0.072959 | 0.00039 | 0.13741 | 120.5436 | -0.07114 | 120.7637 | 120.6834 | 0.13985 | 0.01373 | -0.074641 | 120.7598 | 120.7905 | 120.9275 | 120.7 | -0.1546 | 120.719 | 120.8038 | 120.7155 | 120.7035 | -0.24654
3277.2969 | 121.0373 | -120.7947 | 0.091553 | 1.4211e-13 | 0.025015 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.23258 | 0.024598 | 0.035031 | -0.096851 | -0.0029295 | 0.00064308 | 0.083459 | 0.019721 | 0.032795 | 0.07502 | 0.087359 | 0.25185 | -0.058478 | 0.078886 | 0.027831 | 0.007751 | 0.034145 | 0.13733 | 0.044379 | -0.13668 | 120.7362 | -0.016533 | 120.8781 | 120.8275 | 0.091273 | -0.004194 | 0.1603 | 120.658 | -0.057408 | 120.8736 | 120.8024 | 0.14443 | 0.045776 | -0.047174 | 120.8697 | 120.882 | 121.0465 | 120.8144 | -0.15003 | 120.8288 | 120.932 | 120.8391 | 120.8225 | -0.22823
3279 | 121.0693 | -120.6207 | 0.23804 | 1.4211e-13 | 0.025015 | 0.016346 | 0.0098956 | -0.023148 | 0.0048523 | 0.22495 | 0.023957 | 0.034604 | -0.096424 | -0.0027159 | 0.00085668 | 0.07888 | 0.015142 | 0.032795 | 0.07502 | 0.096516 | 0.26101 | -0.058478 | 0.083464 | 0.03241 | 0.003172 | 0.038723 | 0.13275 | 0.035222 | -0.14125 | 120.5623 | -0.16302 | 120.6996 | 120.6535 | 0.091273 | -0.14152 | 0.022973 | 120.4795 | -0.19931 | 120.7042 | 120.6239 | 0.14443 | -0.10529 | -0.20281 | 120.6957 | 120.7172 | 120.8817 | 120.6359 | -0.29651 | 120.6595 | 120.7535 | 120.656 | 120.6531 | -0.37929
3280.7188 | 121.1746 | -120.8176 | 0.054932 | 1.4211e-13 | 0.025015 | 0.016133 | 0.009682 | -0.023362 | 0.0048523 | 0.22495 | 0.024598 | 0.034818 | -0.096637 | -0.0027159 | 0.00064308 | 0.083459 | 0.015142 | 0.037373 | 0.084176 | 0.1011 | 0.24727 | -0.040163 | 0.092622 | 0.027831 | 0.003172 | 0.034145 | 0.13733 | 0.058115 | -0.1321 | 120.7774 | 0.029244 | 120.901 | 120.8549 | 0.077536 | 0.046163 | 0.19234 | 120.6855 | -0.020787 | 120.9102 | 120.8207 | 0.13527 | 0.082397 | 0.003183 | 120.9017 | 120.9187 | 121.0648 | 120.8327 | -0.095095 | 120.8517 | 120.9549 | 120.8757 | 120.8454 | -0.18703
3282.4531 | 121.0785 | -120.9183 | 0.09613 | 1.4211e-13 | 0.024801 | 0.016346 | 0.010109 | -0.023362 | 0.0044249 | 0.23258 | 0.024385 | 0.034818 | -0.096424 | -0.0025021 | 0.00042948 | 0.069723 | 0.015142 | 0.028217 | 0.07502 | 0.091937 | 0.24269 | -0.063057 | 0.088043 | 0.027831 | 0.003172 | 0.029566 | 0.13733 | 0.035222 | -0.14125 | 120.8552 | -0.02111 | 120.988 | 120.9465 | 0.091274 | -0.004193 | 0.14657 | 120.777 | -0.066564 | 121.0063 | 120.9214 | 0.14443 | 0.041199 | -0.060908 | 120.9933 | 121.0102 | 121.161 | 120.9334 | -0.15919 | 120.9478 | 121.0556 | 120.9535 | 120.9461 | -0.23738
3284.1562 | 121.2204 | -120.6894 | 0.24261 | 1.4211e-13 | 0.025015 | 0.016133 | 0.009682 | -0.023362 | 0.0048523 | 0.24021 | 0.024171 | 0.034818 | -0.096637 | -0.0025021 | 0.00085668 | 0.083459 | 0.019721 | 0.028217 | 0.07502 | 0.096516 | 0.25185 | -0.053899 | 0.078886 | 0.03241 | 0.003172 | 0.038723 | 0.12817 | 0.030644 | -0.14125 | 120.6355 | -0.16759 | 120.7729 | 120.7176 | 0.082116 | -0.1461 | 0.009237 | 120.5481 | -0.20389 | 120.7683 | 120.6926 | 0.14443 | -0.11444 | -0.21197 | 120.7644 | 120.7859 | 120.9412 | 120.7091 | -0.29651 | 120.7281 | 120.8176 | 120.72 | 120.7218 | -0.38387
3285.9062 | 121.2845 | -120.9229 | 0.054932 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.022935 | 0.0046387 | 0.23258 | 0.024385 | 0.034818 | -0.096424 | -0.0022885 | 0.00064308 | 0.083459 | 0.019721 | 0.037373 | 0.084176 | 0.091937 | 0.25185 | -0.044742 | 0.069728 | 0.027831 | -0.001407 | 0.038723 | 0.13275 | 0.035222 | -0.13668 | 120.8781 | 0.029244 | 121.0063 | 120.9602 | 0.082115 | 0.037005 | 0.19692 | 120.7862 | -0.016209 | 120.9926 | 120.9214 | 0.13527 | 0.077818 | -0.01971 | 121.007 | 121.0148 | 121.1747 | 120.9426 | -0.099674 | 120.9616 | 121.0556 | 120.9581 | 120.9507 | -0.19161
3287.625 | 121.1746 | -121.0007 | 0.068665 | 1.4211e-13 | 0.025015 | 0.016346 | 0.009682 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.035031 | -0.096424 | -0.0025021 | 0.00064308 | 0.07888 | 0.019721 | 0.032795 | 0.084176 | 0.1011 | 0.25185 | -0.035584 | 0.078886 | 0.023253 | -0.001407 | 0.029566 | 0.13275 | 0.044379 | -0.1321 | 120.9651 | 0.015511 | 121.0796 | 121.0335 | 0.068379 | 0.03243 | 0.18319 | 120.8686 | -0.039099 | 121.0796 | 120.9993 | 0.13069 | 0.064085 | -0.024286 | 121.0848 | 121.1018 | 121.2525 | 121.0204 | -0.10425 | 121.0302 | 121.1334 | 121.0451 | 121.0239 | -0.20076
3289.4062 | 121.1746 | -121.019 | 0.10071 | 1.4211e-13 | 0.025015 | 0.016346 | 0.009682 | -0.023148 | 0.0046387 | 0.23258 | 0.024598 | 0.034818 | -0.096424 | -0.0025021 | 0.00064308 | 0.083459 | 0.0243 | 0.037373 | 0.079598 | 0.096516 | 0.25185 | -0.049321 | 0.088043 | 0.03241 | 0.007751 | 0.024988 | 0.12817 | 0.039801 | -0.1321 | 120.9697 | -0.02111 | 121.1024 | 121.0564 | 0.086694 | -0.004192 | 0.15114 | 120.8869 | -0.07572 | 121.107 | 121.0267 | 0.13985 | 0.027464 | -0.060907 | 121.0986 | 121.1155 | 121.2708 | 121.0433 | -0.15003 | 121.044 | 121.1472 | 121.0588 | 121.0514 | -0.2328
3291.125 | 121.2296 | -121.0327 | 0.09613 | 1.4211e-13 | 0.024801 | 0.01656 | 0.010323 | -0.023148 | 0.0044249 | 0.22495 | 0.024171 | 0.034604 | -0.096637 | -0.0022885 | 0.00064308 | 0.07888 | 0.028878 | 0.041952 | 0.07502 | 0.1011 | 0.25185 | -0.044742 | 0.078886 | 0.03241 | 0.007751 | 0.038723 | 0.14191 | 0.048958 | -0.1321 | 120.988 | -0.02111 | 121.1116 | 121.0747 | 0.086694 | 0.004965 | 0.15572 | 120.9006 | -0.057407 | 121.1116 | 121.0405 | 0.13985 | 0.045777 | -0.047172 | 121.1077 | 121.1338 | 121.2846 | 121.0616 | -0.14087 | 121.0714 | 121.1746 | 121.0817 | 121.0651 | -0.22823
3292.8438 | 121.3028 | -121.0556 | 0.068665 | 1.4211e-13 | 0.024801 | 0.015919 | 0.0098956 | -0.023148 | 0.0046387 | 0.23258 | 0.024385 | 0.03439 | -0.09621 | -0.0027159 | 0.00064308 | 0.088037 | 0.015142 | 0.037373 | 0.079598 | 0.096516 | 0.25185 | -0.053899 | 0.078886 | 0.027831 | 0.007751 | 0.029566 | 0.13275 | 0.039801 | -0.13668 | 121.0017 | 0.010933 | 121.1436 | 121.093 | 0.091272 | 0.027851 | 0.18319 | 120.9189 | -0.039099 | 121.1345 | 121.0634 | 0.14443 | 0.064085 | -0.028864 | 121.1352 | 121.1521 | 121.3075 | 121.0707 | -0.12256 | 121.0852 | 121.1884 | 121.0954 | 121.0834 | -0.20534
3294.5469 | 121.2753 | -121.0556 | 0.086975 | 1.4211e-13 | 0.024587 | 0.016346 | 0.010109 | -0.023148 | 0.0046387 | 0.23258 | 0.024385 | 0.034604 | -0.096637 | -0.0025021 | 0.0010705 | 0.083459 | 0.019721 | 0.032795 | 0.070441 | 0.096516 | 0.25185 | -0.031005 | 0.074307 | 0.03241 | 0.007751 | 0.029566 | 0.13733 | 0.039801 | -0.14125 | 121.0246 | -0.016534 | 121.1391 | 121.0884 | 0.0638 | 0.009541 | 0.16488 | 120.9143 | -0.057409 | 121.1299 | 121.0634 | 0.14901 | 0.050354 | -0.047174 | 121.126 | 121.1521 | 121.3075 | 121.0753 | -0.11798 | 121.0852 | 121.1929 | 121.0954 | 121.088 | -0.22823
3296.2812 | 121.2479 | -121.0602 | 0.07782 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034818 | -0.096851 | -0.0027159 | 0.00064308 | 0.083459 | 0.0243 | 0.041952 | 0.079598 | 0.10567 | 0.25643 | -0.053899 | 0.083464 | 0.03241 | 0.01233 | 0.034145 | 0.12817 | 0.035222 | -0.13668 | 121.0063 | 0.001778 | 121.1436 | 121.1021 | 0.095851 | 0.027854 | 0.17861 | 120.9235 | -0.043675 | 121.1436 | 121.0725 | 0.14901 | 0.050352 | -0.042598 | 121.1398 | 121.1659 | 121.3166 | 121.0845 | -0.13172 | 121.0943 | 121.1884 | 121.0954 | 121.0926 | -0.2145
3297.9844 | 121.3669 | -121.0648 | 0.059509 | 1.4211e-13 | 0.024587 | 0.01656 | 0.010109 | -0.023148 | 0.0046387 | 0.23258 | 0.024598 | 0.034604 | -0.096637 | -0.0025021 | 0.00064308 | 0.088037 | 0.019721 | 0.032795 | 0.07502 | 0.096516 | 0.24727 | -0.031005 | 0.083464 | 0.027831 | 0.003172 | 0.034145 | 0.13733 | 0.030644 | -0.13668 | 121.0338 | 0.015511 | 121.1528 | 121.0976 | 0.0638 | 0.037007 | 0.18776 | 120.9281 | -0.025364 | 121.1482 | 121.0679 | 0.13985 | 0.07782 | -0.028865 | 121.1398 | 121.1613 | 121.312 | 121.0845 | -0.090514 | 121.0989 | 121.2021 | 121.0954 | 121.0926 | -0.19618
3299.7031 | 121.3531 | -121.0831 | 0.064087 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.023148 | 0.0048523 | 0.23258 | 0.024812 | 0.034818 | -0.096851 | -0.0025021 | 0.00042948 | 0.083459 | 0.015142 | 0.032795 | 0.070441 | 0.10567 | 0.26101 | -0.017268 | 0.083464 | 0.027831 | 0.003172 | 0.029566 | 0.13733 | 0.030644 | -0.13668 | 121.0658 | 0.006354 | 121.1665 | 121.1159 | 0.050063 | 0.041587 | 0.19692 | 120.9464 | -0.034521 | 121.1665 | 121.0862 | 0.13985 | 0.073242 | -0.033443 | 121.1535 | 121.1887 | 121.3441 | 121.0982 | -0.081355 | 121.1126 | 121.2204 | 121.1137 | 121.1109 | -0.20076
3301.4688 | 121.3806 | -121.0968 | 0.07782 | 1.4211e-13 | 0.025228 | 0.016133 | 0.009682 | -0.023148 | 0.0046387 | 0.24784 | 0.024598 | 0.034604 | -0.096637 | -0.0029295 | 0.00085668 | 0.07888 | 0.015142 | 0.037373 | 0.070441 | 0.1011 | 0.24727 | -0.049321 | 0.083464 | 0.036989 | 0.003172 | 0.029566 | 0.13275 | 0.039801 | -0.14125 | 121.0475 | -0.007379 | 121.1757 | 121.1342 | 0.086694 | 0.023275 | 0.16945 | 120.9555 | -0.048254 | 121.1803 | 121.1 | 0.14443 | 0.05493 | -0.038019 | 121.1672 | 121.1979 | 121.3441 | 121.1119 | -0.12714 | 121.1264 | 121.2296 | 121.1366 | 121.1338 | -0.21907
3303.1875 | 121.4218 | -121.0968 | 0.054932 | 1.4211e-13 | 0.024801 | 0.01656 | 0.010109 | -0.023362 | 0.0046387 | 0.24784 | 0.023957 | 0.034604 | -0.096424 | -0.0025021 | 0.00064308 | 0.083459 | 0.019721 | 0.028217 | 0.070441 | 0.1011 | 0.24727 | -0.035584 | 0.074307 | 0.03241 | 0.003172 | 0.029566 | 0.14191 | 0.039801 | -0.13668 | 121.0612 | 0.015509 | 121.1803 | 121.125 | 0.063801 | 0.046163 | 0.19234 | 120.9601 | -0.025366 | 121.1711 | 121.1 | 0.13985 | 0.086975 | -0.015131 | 121.1672 | 121.1979 | 121.3441 | 121.1165 | -0.090516 | 121.1264 | 121.2387 | 121.1366 | 121.1292 | -0.19161
3304.9531 | 121.3623 | -121.1563 | 0.10071 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023362 | 0.0048523 | 0.23258 | 0.024171 | 0.034604 | -0.096637 | -0.0027159 | 0.00085668 | 0.083459 | 0.019721 | 0.032795 | 0.07502 | 0.096516 | 0.24727 | -0.053899 | 0.078886 | 0.03241 | 0.01233 | 0.034145 | 0.13275 | 0.044379 | -0.13668 | 121.1024 | -0.025688 | 121.2398 | 121.1891 | 0.086694 | -0.004192 | 0.14657 | 121.0196 | -0.066563 | 121.2352 | 121.1686 | 0.14901 | 0.032042 | -0.056329 | 121.2313 | 121.2528 | 121.4036 | 121.176 | -0.15461 | 121.1905 | 121.2891 | 121.2007 | 121.1887 | -0.23738
3306.6562 | 121.4172 | -121.1426 | 0.082397 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.023362 | 0.0046387 | 0.24021 | 0.024598 | 0.035031 | -0.096851 | -0.0025021 | 0.00064308 | 0.07888 | 0.0243 | 0.037373 | 0.079598 | 0.096516 | 0.25643 | -0.049321 | 0.083464 | 0.03241 | -0.001407 | 0.038723 | 0.13275 | 0.030644 | -0.13668 | 121.0933 | -0.002799 | 121.2215 | 121.18 | 0.086694 | 0.014119 | 0.17403 | 121.0059 | -0.043674 | 121.226 | 121.1412 | 0.13527 | 0.050353 | -0.051753 | 121.2222 | 121.2391 | 121.399 | 121.1669 | -0.13172 | 121.1813 | 121.2753 | 121.1732 | 121.175 | -0.21907
3308.3594 | 121.3531 | -121.1838 | 0.054932 | 1.4211e-13 | 0.024801 | 0.015919 | 0.010109 | -0.022935 | 0.0046387 | 0.24021 | 0.024171 | 0.03439 | -0.097065 | -0.0025021 | 0.00085668 | 0.07888 | 0.015142 | 0.032795 | 0.07502 | 0.10567 | 0.25185 | -0.040163 | 0.078886 | 0.027831 | 0.003172 | 0.034145 | 0.13733 | 0.035222 | -0.14125 | 121.1436 | 0.020088 | 121.2627 | 121.2166 | 0.072958 | 0.050742 | 0.19692 | 121.0425 | -0.020787 | 121.2627 | 121.1869 | 0.14443 | 0.082397 | -0.01971 | 121.2588 | 121.2895 | 121.4356 | 121.1989 | -0.095095 | 121.2179 | 121.3211 | 121.219 | 121.2116 | -0.19619
3310.0938 | 121.2982 | -121.2021 | 0.12817 | 1.4211e-13 | 0.025015 | 0.016133 | 0.0098956 | -0.023148 | 0.0046387 | 0.24784 | 0.024598 | 0.03439 | -0.097065 | -0.0027159 | 0.00064308 | 0.083459 | 0.0243 | 0.032795 | 0.070441 | 0.10567 | 0.25185 | -0.049321 | 0.083464 | 0.03241 | 0.007751 | 0.034145 | 0.12817 | 0.044379 | -0.13668 | 121.1528 | -0.057733 | 121.2855 | 121.2349 | 0.082116 | -0.0225 | 0.12368 | 121.0654 | -0.094029 | 121.2856 | 121.2098 | 0.14443 | -2e-06 | -0.083795 | 121.2725 | 121.3078 | 121.4539 | 121.2264 | -0.1775 | 121.2362 | 121.3303 | 121.2465 | 121.2345 | -0.26485
3311.7969 | 121.4264 | -121.1517 | 0.11444 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023362 | 0.0048523 | 0.24021 | 0.024171 | 0.034818 | -0.097065 | -0.0027159 | 0.00085668 | 0.07888 | 0.0243 | 0.032795 | 0.070441 | 0.096516 | 0.25185 | -0.035584 | 0.083464 | 0.023253 | -0.001407 | 0.043302 | 0.13275 | 0.026065 | -0.12752 | 121.1161 | -0.044 | 121.2306 | 121.1845 | 0.068379 | -0.017925 | 0.13741 | 121.0242 | -0.071139 | 121.2352 | 121.1503 | 0.12611 | 0.018309 | -0.088376 | 121.2222 | 121.2482 | 121.4036 | 121.176 | -0.15002 | 121.195 | 121.2845 | 121.1778 | 121.175 | -0.24196
3313.5 | 121.4172 | -121.1838 | 0.09613 | 1.4211e-13 | 0.025015 | 0.016346 | 0.0098956 | -0.023576 | 0.0048523 | 0.24784 | 0.024385 | 0.034604 | -0.096851 | -0.0027159 | 0.00064308 | 0.07888 | 0.019721 | 0.028217 | 0.07502 | 0.1011 | 0.25185 | -0.035584 | 0.088043 | 0.027831 | 0.003172 | 0.038723 | 0.12359 | 0.026065 | -0.1321 | 121.1482 | -0.02111 | 121.2627 | 121.212 | 0.063801 | 0.004965 | 0.15572 | 121.0517 | -0.057407 | 121.2718 | 121.1869 | 0.13527 | 0.027463 | -0.070065 | 121.2588 | 121.2849 | 121.4356 | 121.2035 | -0.13171 | 121.2225 | 121.3074 | 121.2098 | 121.2116 | -0.22823
3315.2188 | 121.3898 | -121.2112 | 0.10986 | 1.4211e-13 | 0.024801 | 0.016346 | 0.010537 | -0.023576 | 0.0046387 | 0.23258 | 0.024385 | 0.034818 | -0.096637 | -0.0025021 | 0.00042948 | 0.07888 | 0.015142 | 0.037373 | 0.079598 | 0.1011 | 0.25185 | -0.003531 | 0.083464 | 0.027831 | 0.007751 | 0.038723 | 0.12359 | 0.035222 | -0.1321 | 121.2077 | -0.030265 | 121.2901 | 121.2486 | 0.040904 | -0.008768 | 0.14199 | 121.0791 | -0.07114 | 121.2947 | 121.219 | 0.13985 | 0.01373 | -0.074641 | 121.2908 | 121.3123 | 121.4631 | 121.2264 | -0.11339 | 121.25 | 121.3348 | 121.2465 | 121.2391 | -0.24196
3316.9844 | 115.3519 | -72.7341 | 42.6773 | 1.4211e-13 | 0.025228 | 0.016133 | 0.0094682 | -0.022935 | 0.0039977 | 0.23258 | 0.024385 | 0.035031 | -0.096851 | -0.0025021 | 0.0010705 | 0.069723 | 0.010564 | 0.028217 | 0.070441 | 0.078201 | 0.23354 | -0.053899 | 0.060571 | 0.009516 | -0.010564 | 0.015831 | 0.10986 | 0.016908 | -0.15041 | 72.6802 | -42.6069 | 72.8038 | 72.7623 | 0.082116 | -42.5991 | -42.4438 | 72.5837 | -42.6615 | 72.7946 | 72.7235 | 0.13985 | -42.5675 | -42.6604 | 72.8045 | 72.8123 | 72.9676 | 72.7446 | -42.7312 | 72.7499 | 72.8439 | 72.751 | 72.7436 | -42.8277
3318.7031 | 120.7855 | -120.2545 | 0.068665 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.023362 | 0.0048523 | 0.22495 | 0.024385 | 0.034818 | -0.096424 | -0.0029295 | 0.00064308 | 0.07888 | 0.019721 | 0.032795 | 0.07502 | 0.096516 | 0.25185 | -0.00811 | 0.074307 | 0.03241 | -0.001407 | 0.034145 | 0.12359 | 0.039801 | -0.1321 | 120.2464 | 0.006355 | 120.3334 | 120.2873 | 0.040905 | 0.027851 | 0.18319 | 120.1224 | -0.03452 | 120.3288 | 120.2531 | 0.13069 | 0.054928 | -0.028864 | 120.3295 | 120.351 | 120.5064 | 120.2742 | -0.076775 | 120.2887 | 120.3781 | 120.2943 | 120.2869 | -0.20076
3320.4688 | 120.5109 | -119.87 | 0.17395 | 1.4211e-13 | 0.024801 | 0.015919 | 0.010109 | -0.023148 | 0.0050659 | 0.24021 | 0.024812 | 0.035031 | -0.096851 | -0.0027159 | 0.0010705 | 0.07888 | 0.019721 | 0.037373 | 0.07502 | 0.1011 | 0.24727 | -0.063057 | 0.078886 | 0.027831 | 0.003172 | 0.034145 | 0.12817 | 0.035222 | -0.13668 | 119.8069 | -0.09893 | 119.9489 | 119.9074 | 0.10043 | -0.072855 | 0.073324 | 119.7333 | -0.1398 | 119.9489 | 119.8732 | 0.13985 | -0.045778 | -0.13873 | 119.945 | 119.9711 | 120.1173 | 119.8897 | -0.23701 | 119.9041 | 119.9982 | 119.9052 | 119.8978 | -0.31063
3322.1875 | 120.7672 | -120.4376 | 0.07782 | 1.4211e-13 | 0.024801 | 0.015919 | 0.0098956 | -0.023362 | 0.0050659 | 0.23258 | 0.024171 | 0.034604 | -0.096637 | -0.0025021 | 0.00085668 | 0.083459 | 0.0243 | 0.028217 | 0.07502 | 0.096516 | 0.24727 | -0.012689 | 0.074307 | 0.023253 | 0.003172 | 0.034145 | 0.12817 | 0.030644 | -0.13668 | 120.4249 | -0.0028 | 120.5211 | 120.4658 | 0.040906 | 0.018696 | 0.16945 | 120.3009 | -0.043675 | 120.5119 | 120.4408 | 0.13985 | 0.050352 | -0.047176 | 120.5126 | 120.5341 | 120.6849 | 120.4619 | -0.090509 | 120.4718 | 120.5658 | 120.4683 | 120.4609 | -0.2145
3323.9531 | 120.8359 | -120.0806 | 0.36621 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.22495 | 0.024385 | 0.03439 | -0.09621 | -0.0027159 | 0.00042948 | 0.083459 | 0.0243 | 0.028217 | 0.079598 | 0.10567 | 0.25185 | -0.063057 | 0.078886 | 0.027831 | 0.003172 | 0.034145 | 0.12817 | 0.035222 | -0.13668 | 120.0175 | -0.28661 | 120.164 | 120.1088 | 0.091274 | -0.26054 | -0.11436 | 119.9439 | -0.33207 | 120.1595 | 120.0837 | 0.13985 | -0.23804 | -0.33099 | 120.1602 | 120.1862 | 120.3324 | 120.1049 | -0.42927 | 120.1147 | 120.2087 | 120.1158 | 120.1084 | -0.50289
3325.6562 | 120.5063 | -118.7714 | 1.561 | 1.4211e-13 | 0.025015 | 0.015919 | 0.0098956 | -0.023148 | 0.0046387 | 0.24021 | 0.024812 | 0.033963 | -0.095783 | -0.0027159 | 0.00042948 | 0.074302 | 0.019721 | 0.041952 | 0.07502 | 0.096516 | 0.25185 | -0.063057 | 0.074307 | 0.023253 | -0.001407 | 0.034145 | 0.12359 | 0.026065 | -0.13668 | 118.7083 | -1.486 | 118.8457 | 118.8133 | 0.10501 | -1.4645 | -1.3091 | 118.6347 | -1.5268 | 118.8457 | 118.77 | 0.13527 | -1.4374 | -1.5349 | 118.8464 | 118.8679 | 119.0232 | 118.7911 | -1.624 | 118.8055 | 118.895 | 118.7974 | 118.7946 | -1.6977
3327.3906 | 120.9045 | -120.5109 | 0.1236 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023148 | 0.0046387 | 0.23258 | 0.024385 | 0.034604 | -0.096637 | -0.0025021 | 0.00085668 | 0.074302 | 0.0243 | 0.023639 | 0.07502 | 0.096516 | 0.25185 | -0.058478 | 0.078886 | 0.023253 | 0.007751 | 0.029566 | 0.12817 | 0.039801 | -0.13668 | 120.4524 | -0.048576 | 120.5852 | 120.5345 | 0.082117 | -0.02708 | 0.12826 | 120.3742 | -0.09403 | 120.5897 | 120.5186 | 0.14443 | 0.004576 | -0.083795 | 120.5859 | 120.6074 | 120.7627 | 120.5352 | -0.18207 | 120.5404 | 120.639 | 120.5507 | 120.5341 | -0.26027
3329.0938 | 120.8908 | -120.6345 | 0.07782 | 1.4211e-13 | 0.024801 | 0.015705 | 0.010323 | -0.023362 | 0.0046387 | 0.23258 | 0.024171 | 0.034604 | -0.09621 | -0.0029295 | 0.00042948 | 0.083459 | 0.019721 | 0.032795 | 0.070441 | 0.1011 | 0.25185 | -0.067636 | 0.078886 | 0.018674 | 0.007751 | 0.024988 | 0.11901 | 0.035222 | -0.13668 | 120.5668 | -0.007379 | 120.7179 | 120.6673 | 0.10043 | 0.023275 | 0.17403 | 120.4978 | -0.052832 | 120.7133 | 120.6422 | 0.14443 | 0.041194 | -0.042598 | 120.7049 | 120.7356 | 120.8863 | 120.6542 | -0.14546 | 120.6594 | 120.7535 | 120.6697 | 120.6531 | -0.2145
3330.8125 | 120.607 | -120.1035 | 0.39368 | 1.4211e-13 | 0.024801 | 0.015919 | 0.0098956 | -0.023576 | 0.0046387 | 0.23258 | 0.024598 | 0.03439 | -0.096637 | -0.0029295 | 0.00064308 | 0.083459 | 0.019721 | 0.037373 | 0.07502 | 0.10567 | 0.25185 | -0.026426 | 0.078886 | 0.023253 | 0.007751 | 0.034145 | 0.12359 | 0.030644 | -0.1321 | 120.077 | -0.31866 | 120.1869 | 120.1408 | 0.063799 | -0.288 | -0.14182 | 119.9714 | -0.35953 | 120.1823 | 120.1112 | 0.13985 | -0.27008 | -0.36303 | 120.1785 | 120.2091 | 120.3553 | 120.1232 | -0.4201 | 120.1376 | 120.227 | 120.1341 | 120.1267 | -0.52577
3332.5469 | 120.607 | -120.1859 | 0.37537 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.023148 | 0.0048523 | 0.23258 | 0.024598 | 0.03439 | -0.096424 | -0.0027159 | 0.00064308 | 0.07888 | 0.019721 | 0.037373 | 0.07502 | 0.096516 | 0.25185 | -0.053899 | 0.078886 | 0.03241 | -0.001407 | 0.029566 | 0.12817 | 0.026065 | -0.13668 | 120.132 | -0.30035 | 120.2647 | 120.2232 | 0.091272 | -0.27885 | -0.12351 | 120.0492 | -0.3458 | 120.2647 | 120.1844 | 0.13527 | -0.24719 | -0.3493 | 120.2609 | 120.2824 | 120.4377 | 120.2056 | -0.42927 | 120.2154 | 120.314 | 120.2119 | 120.2183 | -0.51204
3334.25 | 120.7855 | -120.6116 | 0.1236 | 1.4211e-13 | 0.024374 | 0.016346 | 0.0098956 | -0.023148 | 0.0044249 | 0.24021 | 0.024598 | 0.034818 | -0.096637 | -0.0022885 | 0.00064308 | 0.074302 | 0.019721 | 0.023639 | 0.07502 | 0.096516 | 0.24727 | -0.063057 | 0.074307 | 0.027831 | -0.001407 | 0.034145 | 0.12359 | 0.039801 | -0.1321 | 120.5485 | -0.048576 | 120.6859 | 120.6352 | 0.086696 | -0.02708 | 0.12368 | 120.4795 | -0.089451 | 120.6859 | 120.6102 | 0.13069 | -3e-06 | -0.083795 | 120.6866 | 120.7081 | 120.8588 | 120.6313 | -0.18665 | 120.6457 | 120.7352 | 120.6514 | 120.6394 | -0.25569
3335.9844 | 120.7901 | -120.1172 | 0.4303 | 1.4211e-13 | 0.025015 | 0.015919 | 0.0098956 | -0.023148 | 0.0042113 | 0.23258 | 0.024598 | 0.034818 | -0.096637 | -0.0020749 | 0.00085668 | 0.07888 | 0.0243 | 0.032795 | 0.07502 | 0.1011 | 0.24269 | -0.058478 | 0.083464 | 0.03241 | 0.003172 | 0.034145 | 0.12817 | 0.030644 | -0.14125 | 120.0587 | -0.35528 | 120.1961 | 120.15 | 0.091273 | -0.3292 | -0.1876 | 119.9759 | -0.39615 | 120.2007 | 120.1204 | 0.14443 | -0.30213 | -0.39965 | 120.1922 | 120.2183 | 120.3599 | 120.1415 | -0.48878 | 120.1513 | 120.2454 | 120.1478 | 120.1496 | -0.57155
3337.6875 | 120.6619 | -119.9661 | 0.67749 | 1.4211e-13 | 0.025015 | 0.016346 | 0.0098956 | -0.023148 | 0.0052797 | 0.24784 | 0.023957 | 0.034818 | -0.096637 | -0.0025021 | 0.00085668 | 0.083459 | 0.019721 | 0.037373 | 0.070441 | 0.096516 | 0.26101 | -0.063057 | 0.074307 | 0.027831 | 0.007751 | 0.038723 | 0.12359 | 0.039801 | -0.13668 | 119.9031 | -0.60705 | 120.0496 | 120.0035 | 0.10043 | -0.58097 | -0.41648 | 119.8294 | -0.63877 | 120.0404 | 119.9739 | 0.14443 | -0.5539 | -0.63769 | 120.0366 | 120.0626 | 120.2271 | 119.9858 | -0.74055 | 120.0048 | 120.0897 | 120.0059 | 119.994 | -0.81417
3339.4375 | 120.9503 | -120.5841 | 0.068665 | 1.4211e-13 | 0.024801 | 0.016133 | 0.009682 | -0.023148 | 0.0046387 | 0.24021 | 0.024385 | 0.034604 | -0.096424 | -0.0025021 | 0.00042948 | 0.083459 | 0.019721 | 0.032795 | 0.07502 | 0.10567 | 0.25643 | -0.063057 | 0.078886 | 0.027831 | -0.001407 | 0.034145 | 0.12817 | 0.044379 | -0.12752 | 120.521 | 0.006355 | 120.6676 | 120.6169 | 0.095852 | 0.037009 | 0.18777 | 120.4566 | -0.03452 | 120.663 | 120.5827 | 0.12611 | 0.059507 | -0.024286 | 120.6591 | 120.6898 | 120.8405 | 120.6038 | -0.13172 | 120.6183 | 120.7123 | 120.6285 | 120.6119 | -0.19618
3341.1562 | 120.845 | -120.4742 | 0.27466 | 1.4211e-13 | 0.025228 | 0.015919 | 0.0098956 | -0.023362 | 0.0046387 | 0.24784 | 0.024598 | 0.034604 | -0.096637 | -0.0025021 | 0.00064308 | 0.07888 | 0.0243 | 0.028217 | 0.07502 | 0.1011 | 0.24727 | -0.067636 | 0.088043 | 0.03241 | -0.001407 | 0.029566 | 0.12817 | 0.035222 | -0.13668 | 120.4066 | -0.19964 | 120.5531 | 120.5025 | 0.095853 | -0.17356 | -0.027384 | 120.3376 | -0.24509 | 120.5623 | 120.4728 | 0.13527 | -0.14649 | -0.23944 | 120.5493 | 120.5753 | 120.7215 | 120.4985 | -0.34229 | 120.5038 | 120.6024 | 120.5095 | 120.5067 | -0.41133
3342.9219 | 120.9869 | -120.7169 | 0.059509 | 1.4211e-13 | 0.024801 | 0.015705 | 0.010323 | -0.023148 | 0.0048523 | 0.24021 | 0.024598 | 0.034604 | -0.096424 | -0.0027159 | 0.00085668 | 0.088037 | 0.015142 | 0.028217 | 0.070441 | 0.1011 | 0.24727 | -0.053899 | 0.078886 | 0.03241 | 0.003172 | 0.038723 | 0.12359 | 0.039801 | -0.13668 | 120.663 | 0.010932 | 120.8049 | 120.7451 | 0.082116 | 0.041586 | 0.18776 | 120.5802 | -0.020786 | 120.7957 | 120.72 | 0.13985 | 0.064084 | -0.019708 | 120.7873 | 120.818 | 120.9641 | 120.732 | -0.11341 | 120.7556 | 120.8405 | 120.7567 | 120.7493 | -0.19618
3344.6406 | 120.9137 | -120.7672 | 0.068665 | 1.4211e-13 | 0.025015 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.024171 | 0.034818 | -0.096424 | -0.0025021 | 0.00064308 | 0.07888 | 0.019721 | 0.032795 | 0.079598 | 0.1011 | 0.24727 | -0.076794 | 0.078886 | 0.023253 | 0.003172 | 0.034145 | 0.13275 | 0.044379 | -0.1321 | 120.6904 | 0.010933 | 120.8461 | 120.8 | 0.10959 | 0.03243 | 0.17861 | 120.6351 | -0.03452 | 120.8461 | 120.7704 | 0.13527 | 0.064085 | -0.024286 | 120.8468 | 120.8683 | 121.0145 | 120.7869 | -0.14546 | 120.8014 | 120.9 | 120.8116 | 120.7905 | -0.20076
3346.3594 | 120.8954 | -120.0485 | 0.65918 | 1.4211e-13 | 0.025015 | 0.015919 | 0.0098956 | -0.023148 | 0.0050659 | 0.24021 | 0.024598 | 0.035031 | -0.096424 | -0.0027159 | 0.00064308 | 0.07888 | 0.015142 | 0.032795 | 0.07502 | 0.10567 | 0.25185 | -0.063057 | 0.083464 | 0.023253 | 0.007751 | 0.034145 | 0.12817 | 0.035222 | -0.1321 | 119.9855 | -0.58416 | 120.1274 | 120.0813 | 0.095852 | -0.55351 | -0.40733 | 119.9164 | -0.62504 | 120.132 | 120.0563 | 0.13985 | -0.53101 | -0.62396 | 120.1235 | 120.1542 | 120.3004 | 120.0637 | -0.72224 | 120.0827 | 120.1767 | 120.0837 | 120.0718 | -0.79128
3348.0938 | 120.7535 | -120.7764 | 0.073242 | 1.4211e-13 | 0.024801 | 0.015919 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024598 | 0.034818 | -0.096424 | -0.0027159 | 0.00064308 | 0.074302 | 0.0243 | 0.028217 | 0.07502 | 0.1011 | 0.24727 | -0.081373 | 0.083464 | 0.023253 | 0.007751 | 0.034145 | 0.13275 | 0.035222 | -0.1321 | 120.695 | 0.001778 | 120.8507 | 120.8046 | 0.10959 | 0.027853 | 0.17403 | 120.6443 | -0.039097 | 120.8598 | 120.7841 | 0.13985 | 0.059508 | -0.03802 | 120.8514 | 120.8775 | 121.0236 | 120.8007 | -0.15462 | 120.8105 | 120.9091 | 120.8116 | 120.7996 | -0.20534
3349.8125 | 116.2628 | -82.8964 | 33.0368 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0094682 | -0.022294 | 0.0037841 | 0.24021 | 0.024385 | 0.035031 | -0.096637 | -0.0025021 | 0.00064308 | 0.065145 | 0.010564 | 0.023639 | 0.061284 | 0.08278 | 0.23812 | -0.076794 | 0.060571 | 0.014095 | -0.005985 | 0.020409 | 0.11444 | 0.007751 | -0.15041 | 82.8196 | -32.9755 | 82.9616 | 82.9201 | 0.10043 | -32.954 | -32.7987 | 82.746 | -33.0164 | 82.957 | 82.8904 | 0.14443 | -32.9224 | -33.0291 | 82.9577 | 82.9792 | 83.1345 | 82.907 | -33.1136 | 82.9168 | 83.0109 | 82.9042 | 82.9105 | -33.1872
3351.5312 | 120.6848 | -120.1492 | 0.24261 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.024171 | 0.034818 | -0.096424 | -0.0027159 | 0.00064308 | 0.083459 | 0.0243 | 0.032795 | 0.079598 | 0.1011 | 0.25185 | -0.053899 | 0.078886 | 0.027831 | 0.003172 | 0.034145 | 0.12359 | 0.030644 | -0.12752 | 120.0953 | -0.16302 | 120.2327 | 120.182 | 0.086694 | -0.14152 | 0.009237 | 120.0217 | -0.20847 | 120.2281 | 120.1524 | 0.13069 | -0.11902 | -0.21197 | 120.2288 | 120.2503 | 120.4011 | 120.1735 | -0.29651 | 120.1834 | 120.2728 | 120.1799 | 120.1771 | -0.37013
3353.25 | 120.163 | -119.8654 | 0.10529 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.023362 | 0.0044249 | 0.24784 | 0.024385 | 0.034604 | -0.096637 | -0.0025021 | 0.00085668 | 0.074302 | 0.019721 | 0.037373 | 0.079598 | 0.1011 | 0.25185 | -0.031005 | 0.078886 | 0.03241 | 0.007751 | 0.038723 | 0.12359 | 0.035222 | -0.1321 | 119.8344 | -0.025688 | 119.9397 | 119.9028 | 0.068378 | -0.004191 | 0.14657 | 119.7333 | -0.066563 | 119.9443 | 119.8732 | 0.13985 | 0.018307 | -0.070064 | 119.945 | 119.9665 | 120.1173 | 119.8851 | -0.13629 | 119.9041 | 119.989 | 119.9006 | 119.8978 | -0.23738
3355 | 120.5566 | -120.1721 | 0.086975 | 1.4211e-13 | 0.024801 | 0.016346 | 0.010323 | -0.023148 | 0.0046387 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0025021 | 0.00085668 | 0.074302 | 0.019721 | 0.028217 | 0.07502 | 0.11025 | 0.24269 | -0.063057 | 0.083464 | 0.027831 | 0.01233 | 0.034145 | 0.13275 | 0.030644 | -0.1321 | 120.1091 | -0.011955 | 120.2464 | 120.2003 | 0.091274 | 0.023278 | 0.15572 | 120.04 | -0.05283 | 120.2556 | 120.1844 | 0.14443 | 0.045775 | -0.056331 | 120.2471 | 120.2824 | 120.4148 | 120.1918 | -0.15003 | 120.2063 | 120.3049 | 120.2028 | 120.2 | -0.21907
3356.7031 | 120.639 | -120.4422 | 0.07782 | 1.4211e-13 | 0.024374 | 0.016133 | 0.010109 | -0.023362 | 0.0050659 | 0.23258 | 0.024171 | 0.034818 | -0.09621 | -0.0029295 | 0.00064308 | 0.083459 | 0.015142 | 0.032795 | 0.07502 | 0.1011 | 0.25185 | -0.044742 | 0.078886 | 0.03241 | 0.003172 | 0.038723 | 0.12817 | 0.039801 | -0.13668 | 120.3975 | -0.0028 | 120.5257 | 120.475 | 0.077537 | 0.023275 | 0.17403 | 120.3055 | -0.039097 | 120.5211 | 120.4454 | 0.13985 | 0.050352 | -0.038019 | 120.5172 | 120.5433 | 120.6941 | 120.4573 | -0.12256 | 120.4809 | 120.5704 | 120.482 | 120.4746 | -0.2145
3358.4062 | 120.6665 | -120.4605 | 0.068665 | 1.4211e-13 | 0.024587 | 0.016346 | 0.009682 | -0.022935 | 0.0046387 | 0.23258 | 0.024385 | 0.034818 | -0.096637 | -0.0022885 | 0.00064308 | 0.07888 | 0.019721 | 0.032795 | 0.084176 | 0.096516 | 0.24269 | -0.049321 | 0.078886 | 0.036989 | 0.003172 | 0.034145 | 0.13275 | 0.026065 | -0.12752 | 120.4112 | 0.015511 | 120.5394 | 120.4933 | 0.082116 | 0.027851 | 0.17403 | 120.333 | -0.03452 | 120.5394 | 120.4637 | 0.13069 | 0.064085 | -0.0426 | 120.5447 | 120.557 | 120.7032 | 120.4802 | -0.11799 | 120.4947 | 120.5933 | 120.4866 | 120.4975 | -0.19618
3360.125 | 120.7626 | -120.5017 | 0.073242 | 1.4211e-13 | 0.024587 | 0.016133 | 0.0098956 | -0.023148 | 0.0048523 | 0.24784 | 0.024598 | 0.034818 | -0.096637 | -0.0027159 | 0.00064308 | 0.07888 | 0.0243 | 0.032795 | 0.079598 | 0.096516 | 0.24727 | -0.067636 | 0.088043 | 0.03241 | 0.003172 | 0.038723 | 0.13275 | 0.035222 | -0.1321 | 120.4341 | 0.006356 | 120.5806 | 120.5345 | 0.10043 | 0.023274 | 0.17403 | 120.3696 | -0.034519 | 120.5898 | 120.5049 | 0.13527 | 0.059508 | -0.03802 | 120.5813 | 120.5982 | 120.749 | 120.526 | -0.14088 | 120.5404 | 120.6345 | 120.5369 | 120.5341 | -0.20534
3361.8281 | 120.7901 | -120.5292 | 0.086975 | 1.4211e-13 | 0.025015 | 0.015919 | 0.009682 | -0.023576 | 0.0046387 | 0.24021 | 0.024598 | 0.034604 | -0.096424 | -0.0025021 | 0.00085668 | 0.083459 | 0.019721 | 0.032795 | 0.07502 | 0.096516 | 0.24727 | -0.044742 | 0.083464 | 0.027831 | 0.003172 | 0.034145 | 0.13275 | 0.021486 | -0.1321 | 120.4844 | -0.011955 | 120.6126 | 120.562 | 0.077537 | 0.009541 | 0.1603 | 120.3971 | -0.05283 | 120.6126 | 120.5323 | 0.13527 | 0.045775 | -0.065489 | 120.6042 | 120.6257 | 120.7764 | 120.5489 | -0.13172 | 120.5633 | 120.6619 | 120.5507 | 120.557 | -0.21907
3363.5469 | 120.7123 | -120.2866 | 0.33417 | 1.4211e-13 | 0.025015 | 0.015919 | 0.010323 | -0.022935 | 0.0050659 | 0.24021 | 0.024385 | 0.034604 | -0.096851 | -0.0027159 | 0.00064308 | 0.07888 | 0.019721 | 0.037373 | 0.065863 | 0.1011 | 0.24727 | -0.053899 | 0.078886 | 0.03241 | 0.007751 | 0.034145 | 0.13275 | 0.035222 | -0.13668 | 120.2327 | -0.2683 | 120.3654 | 120.3239 | 0.091272 | -0.23307 | -0.086893 | 120.1499 | -0.30002 | 120.3654 | 120.2943 | 0.14443 | -0.20142 | -0.29895 | 120.3524 | 120.3877 | 120.5338 | 120.3063 | -0.38807 | 120.3207 | 120.4193 | 120.3218 | 120.319 | -0.47084
3365.2812 | 119.7784 | -119.2474 | 0.21515 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.24784 | 0.024385 | 0.034604 | -0.096424 | -0.0027159 | 0.00064308 | 0.074302 | 0.0243 | 0.028217 | 0.070441 | 0.096516 | 0.24727 | -0.058478 | 0.078886 | 0.027831 | 0.007751 | 0.038723 | 0.13733 | 0.039801 | -0.13668 | 119.189 | -0.14471 | 119.3217 | 119.2757 | 0.086695 | -0.11863 | 0.032125 | 119.1108 | -0.17643 | 119.3263 | 119.2552 | 0.14443 | -0.07782 | -0.17535 | 119.3179 | 119.344 | 119.4947 | 119.2717 | -0.27363 | 119.2862 | 119.3848 | 119.2872 | 119.2753 | -0.35182
3366.9844 | 120.1492 | -119.8151 | 0.18768 | 1.4211e-13 | 0.024374 | 0.016133 | 0.0098956 | -0.023362 | 0.0044249 | 0.24021 | 0.024385 | 0.034818 | -0.096637 | -0.0027159 | 0.00064308 | 0.083459 | 0.019721 | 0.032795 | 0.070441 | 0.096516 | 0.25643 | -0.067636 | 0.078886 | 0.023253 | -0.001407 | 0.038723 | 0.13275 | 0.030644 | -0.12752 | 119.7474 | -0.11724 | 119.8985 | 119.8479 | 0.10043 | -0.091167 | 0.068748 | 119.6875 | -0.14896 | 119.8939 | 119.8137 | 0.12611 | -0.054933 | -0.15704 | 119.8855 | 119.9116 | 120.0715 | 119.8348 | -0.25532 | 119.8538 | 119.9478 | 119.8457 | 119.8383 | -0.3152
3368.7188 | 120.2362 | -120.0073 | 0.14191 | 1.4211e-13 | 0.025015 | 0.016133 | 0.0098956 | -0.023362 | 0.0048523 | 0.24784 | 0.024385 | 0.034604 | -0.096424 | -0.0025021 | 0.00064308 | 0.088037 | 0.0243 | 0.037373 | 0.07502 | 0.1011 | 0.24269 | -0.049321 | 0.083464 | 0.03241 | 0.003172 | 0.038723 | 0.13275 | 0.030644 | -0.1321 | 119.958 | -0.066887 | 120.0954 | 120.0447 | 0.086694 | -0.040812 | 0.10079 | 119.8752 | -0.10318 | 120.0908 | 120.0105 | 0.13527 | -0.009157 | -0.11126 | 120.0823 | 120.1084 | 120.25 | 120.0316 | -0.19123 | 120.046 | 120.1401 | 120.038 | 120.0397 | -0.274
3370.4531 | 120.2499 | -119.9295 | 0.27008 | 1.4211e-13 | 0.025015 | 0.016346 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034818 | -0.096424 | -0.0022885 | 0.00085668 | 0.07888 | 0.015142 | 0.032795 | 0.07502 | 0.1011 | 0.25185 | -0.063057 | 0.083464 | 0.03241 | 0.003172 | 0.029566 | 0.11901 | 0.030644 | -0.13668 | 119.8664 | -0.19506 | 120.0084 | 119.9623 | 0.095852 | -0.16899 | -0.018229 | 119.7928 | -0.24052 | 120.013 | 119.9327 | 0.13985 | -0.15107 | -0.23944 | 120.0045 | 120.0306 | 120.1814 | 119.9446 | -0.33314 | 119.9591 | 120.0485 | 119.9601 | 119.9619 | -0.40676
3372.1719 | 120.1584 | -119.5358 | 0.45319 | 1.4211e-13 | 0.025015 | 0.015919 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.024598 | 0.03439 | -0.096637 | -0.0022885 | 0.00064308 | 0.083459 | 0.019721 | 0.037373 | 0.070441 | 0.1011 | 0.25185 | -0.063057 | 0.083464 | 0.027831 | -0.001407 | 0.038723 | 0.12817 | 0.035222 | -0.1321 | 119.4728 | -0.38275 | 119.6193 | 119.5732 | 0.10043 | -0.35209 | -0.20133 | 119.4037 | -0.41446 | 119.6193 | 119.5344 | 0.13069 | -0.32501 | -0.41796 | 119.6063 | 119.6369 | 119.7877 | 119.5555 | -0.51624 | 119.5746 | 119.664 | 119.571 | 119.5637 | -0.58528
3373.875 | 120.3506 | -119.8929 | 0.32501 | 1.4211e-13 | 0.025228 | 0.016346 | 0.009682 | -0.023362 | 0.0046387 | 0.24784 | 0.024598 | 0.035245 | -0.096851 | -0.0025021 | 0.00064308 | 0.07888 | 0.0243 | 0.032795 | 0.070441 | 0.091937 | 0.25185 | -0.053899 | 0.083464 | 0.027831 | 0.003172 | 0.034145 | 0.12817 | 0.035222 | -0.12752 | 119.839 | -0.25457 | 119.9718 | 119.9257 | 0.086694 | -0.23308 | -0.07316 | 119.7654 | -0.29087 | 119.9763 | 119.8961 | 0.13069 | -0.19684 | -0.28979 | 119.9633 | 119.9848 | 120.1447 | 119.9172 | -0.37891 | 119.927 | 120.0211 | 119.9281 | 119.9207 | -0.45253
3375.6094 | 120.488 | -120.1859 | 0.068665 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.023576 | 0.0044249 | 0.24021 | 0.024171 | 0.034604 | -0.096424 | -0.0027159 | 0.00085668 | 0.07888 | 0.019721 | 0.028217 | 0.07502 | 0.1011 | 0.25185 | -0.044742 | 0.078886 | 0.027831 | -0.001407 | 0.034145 | 0.13275 | 0.030644 | -0.13668 | 120.1411 | 0.006355 | 120.2647 | 120.2141 | 0.072959 | 0.03243 | 0.18319 | 120.0492 | -0.03452 | 120.2647 | 120.1844 | 0.13527 | 0.064085 | -0.038021 | 120.2609 | 120.2869 | 120.4377 | 120.2056 | -0.11341 | 120.22 | 120.3186 | 120.2165 | 120.2137 | -0.20534
3377.3281 | 120.3918 | -120.0531 | 0.28839 | 1.4211e-13 | 0.024587 | 0.016133 | 0.0098956 | -0.023576 | 0.0046387 | 0.24021 | 0.024812 | 0.035031 | -0.096637 | -0.0031431 | 0.00085668 | 0.083459 | 0.019721 | 0.032795 | 0.070441 | 0.096516 | 0.24727 | -0.063057 | 0.083464 | 0.027831 | -0.001407 | 0.034145 | 0.13733 | 0.035222 | -0.1321 | 119.99 | -0.21795 | 120.1366 | 120.0859 | 0.095852 | -0.19188 | -0.041117 | 119.921 | -0.25425 | 120.1366 | 120.0517 | 0.13069 | -0.15106 | -0.25317 | 120.1235 | 120.1496 | 120.3004 | 120.0728 | -0.35145 | 120.0872 | 120.1904 | 120.0883 | 120.0809 | -0.42049
3379.0469 | 120.5933 | -120.3186 | 0.050354 | 1.4211e-13 | 0.024587 | 0.015919 | 0.010109 | -0.023362 | 0.0046387 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0027159 | 0.00042948 | 0.074302 | 0.0243 | 0.037373 | 0.07502 | 0.1011 | 0.25185 | -0.044742 | 0.078886 | 0.023253 | 0.003172 | 0.029566 | 0.13275 | 0.030644 | -0.13668 | 120.2739 | 0.024666 | 120.3929 | 120.356 | 0.082115 | 0.050741 | 0.2015 | 120.1819 | -0.020788 | 120.3975 | 120.3218 | 0.13985 | 0.082396 | -0.01971 | 120.3936 | 120.4197 | 120.5705 | 120.3429 | -0.095096 | 120.3482 | 120.4514 | 120.3492 | 120.3419 | -0.18703
3380.75 | 120.5246 | -120.1355 | 0.068665 | 1.4211e-13 | 0.024587 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.023957 | 0.034604 | -0.096851 | -0.0025021 | 0.00085668 | 0.074302 | 0.015142 | 0.032795 | 0.079598 | 0.1011 | 0.24727 | -0.063057 | 0.078886 | 0.03241 | 0.007751 | 0.038723 | 0.13275 | 0.026065 | -0.12752 | 120.0724 | 0.010933 | 120.2098 | 120.1683 | 0.095852 | 0.03243 | 0.17861 | 120.008 | -0.029942 | 120.2144 | 120.1432 | 0.13527 | 0.064085 | -0.0426 | 120.2151 | 120.2366 | 120.3828 | 120.1506 | -0.13172 | 120.1742 | 120.2682 | 120.1616 | 120.1679 | -0.19618
3382.4531 | 120.5383 | -120.3964 | 0.09613 | 1.4211e-13 | 0.02416 | 0.016133 | 0.0098956 | -0.023148 | 0.0046387 | 0.23258 | 0.024385 | 0.034818 | -0.096424 | -0.0025021 | 0.00064308 | 0.083459 | 0.019721 | 0.028217 | 0.07502 | 0.096516 | 0.25185 | -0.053899 | 0.074307 | 0.027831 | 0.003172 | 0.034145 | 0.12817 | 0.026065 | -0.12752 | 120.3425 | -0.02111 | 120.4799 | 120.4246 | 0.082116 | 0.000386 | 0.15572 | 120.2689 | -0.061985 | 120.4707 | 120.3996 | 0.13069 | 0.032042 | -0.070065 | 120.4714 | 120.4929 | 120.6483 | 120.4161 | -0.15003 | 120.4306 | 120.5246 | 120.4225 | 120.4243 | -0.22365
3384.1719 | 120.6573 | -120.369 | 0.054932 | 1.4211e-13 | 0.024374 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.024171 | 0.034604 | -0.09621 | -0.0027159 | 0.0010705 | 0.07888 | 0.015142 | 0.023639 | 0.07502 | 0.1011 | 0.25185 | -0.049321 | 0.078886 | 0.023253 | 0.003172 | 0.034145 | 0.12817 | 0.030644 | -0.1321 | 120.3196 | 0.020088 | 120.4478 | 120.3926 | 0.07296 | 0.046163 | 0.19692 | 120.2369 | -0.020787 | 120.4478 | 120.3721 | 0.13527 | 0.07324 | -0.024288 | 120.444 | 120.4701 | 120.6208 | 120.3841 | -0.10425 | 120.4031 | 120.4971 | 120.3996 | 120.3922 | -0.18703
3385.8906 | 120.6345 | -120.4193 | 0.07782 | 1.4211e-13 | 0.024801 | 0.01656 | 0.009682 | -0.023576 | 0.0042113 | 0.24021 | 0.024385 | 0.034604 | -0.096424 | -0.0027159 | 0.00085668 | 0.074302 | 0.019721 | 0.028217 | 0.070441 | 0.1011 | 0.25185 | -0.058478 | 0.078886 | 0.027831 | 0.007751 | 0.038723 | 0.13275 | 0.030644 | -0.1321 | 120.3608 | -0.007379 | 120.4936 | 120.4475 | 0.086695 | 0.023275 | 0.17403 | 120.2872 | -0.039097 | 120.4982 | 120.4271 | 0.13985 | 0.05493 | -0.047176 | 120.4898 | 120.5204 | 120.6712 | 120.439 | -0.1363 | 120.458 | 120.5521 | 120.45 | 120.4471 | -0.20992
3387.625 | 120.6436 | -120.4468 | 0.07782 | 1.4211e-13 | 0.024801 | 0.015919 | 0.0098956 | -0.023362 | 0.0052797 | 0.25547 | 0.024171 | 0.034604 | -0.096851 | -0.0027159 | 0.00042948 | 0.074302 | 0.0243 | 0.023639 | 0.079598 | 0.1011 | 0.25185 | -0.053899 | 0.078886 | 0.027831 | -0.001407 | 0.034145 | 0.12817 | 0.030644 | -0.1321 | 120.3929 | 0.001778 | 120.5211 | 120.4704 | 0.077538 | 0.023275 | 0.17403 | 120.3147 | -0.043675 | 120.5257 | 120.4454 | 0.13069 | 0.050352 | -0.047176 | 120.5264 | 120.5479 | 120.6986 | 120.4711 | -0.13172 | 120.4809 | 120.5749 | 120.4774 | 120.4746 | -0.20992
3389.3906 | 120.5292 | -119.8196 | 0.5127 | 1.4211e-13 | 0.024587 | 0.016133 | 0.009682 | -0.023362 | 0.0044249 | 0.24784 | 0.024598 | 0.034177 | -0.096424 | -0.0025021 | 0.00085668 | 0.083459 | 0.0243 | 0.032795 | 0.07502 | 0.10567 | 0.25185 | -0.044742 | 0.083464 | 0.023253 | 0.003172 | 0.029566 | 0.12817 | 0.039801 | -0.1321 | 119.7749 | -0.43768 | 119.9031 | 119.8524 | 0.077537 | -0.40702 | -0.26084 | 119.6875 | -0.48313 | 119.9031 | 119.8228 | 0.13527 | -0.38452 | -0.47289 | 119.8947 | 119.9253 | 120.0715 | 119.8439 | -0.55744 | 119.8492 | 119.9478 | 119.8594 | 119.8429 | -0.64479
3391.1094 | 120.5109 | -119.5312 | 0.85144 | 1.4211e-13 | 0.024587 | 0.015919 | 0.010109 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.03439 | -0.096637 | -0.0027159 | 0.00064308 | 0.074302 | 0.0243 | 0.032795 | 0.07502 | 0.1011 | 0.24727 | -0.063057 | 0.078886 | 0.023253 | 0.003172 | 0.029566 | 0.12817 | 0.030644 | -0.1321 | 119.4682 | -0.77642 | 119.6056 | 119.564 | 0.095852 | -0.75034 | -0.60417 | 119.3992 | -0.82187 | 119.6101 | 119.5344 | 0.13527 | -0.72327 | -0.8208 | 119.6063 | 119.6323 | 119.7785 | 119.5555 | -0.9145 | 119.5608 | 119.6594 | 119.5619 | 119.5545 | -0.98354
3392.8281 | 120.7581 | -120.433 | 0.091553 | 1.4211e-13 | 0.024587 | 0.016133 | 0.010109 | -0.022935 | 0.0048523 | 0.22495 | 0.024598 | 0.034818 | -0.096424 | -0.0027159 | 0.0010705 | 0.07888 | 0.015142 | 0.037373 | 0.07502 | 0.1011 | 0.25185 | -0.058478 | 0.074307 | 0.027831 | -0.001407 | 0.043302 | 0.13733 | 0.030644 | -0.12752 | 120.3746 | -0.016533 | 120.5119 | 120.4704 | 0.095851 | 0.009542 | 0.1603 | 120.3055 | -0.048251 | 120.5074 | 120.4316 | 0.12611 | 0.045776 | -0.060909 | 120.5081 | 120.5341 | 120.6849 | 120.4482 | -0.15003 | 120.4763 | 120.5704 | 120.4637 | 120.4609 | -0.21907
3394.5469 | 120.5383 | -119.4168 | 0.88806 | 1.4211e-13 | 0.024587 | 0.016133 | 0.010109 | -0.023148 | 0.0046387 | 0.23258 | 0.023957 | 0.034604 | -0.096424 | -0.0029295 | 0.00064308 | 0.083459 | 0.015142 | 0.028217 | 0.07502 | 0.096516 | 0.24727 | -0.035584 | 0.074307 | 0.023253 | 0.007751 | 0.038723 | 0.12359 | 0.030644 | -0.12752 | 119.3812 | -0.81304 | 119.5003 | 119.445 | 0.063801 | -0.79155 | -0.64079 | 119.2893 | -0.84934 | 119.4911 | 119.4246 | 0.13527 | -0.76447 | -0.85742 | 119.4918 | 119.5133 | 119.6641 | 119.432 | -0.92365 | 119.4555 | 119.5404 | 119.4475 | 119.4401 | -1.0156
3396.3125 | 120.7031 | -120.4056 | 0.082397 | 1.4211e-13 | 0.024374 | 0.016346 | 0.0098956 | -0.022935 | 0.0048523 | 0.23258 | 0.024171 | 0.034604 | -0.09621 | -0.0025021 | 0.00064308 | 0.07888 | 0.010564 | 0.028217 | 0.070441 | 0.1011 | 0.24269 | -0.058478 | 0.083464 | 0.03241 | 0.007751 | 0.029566 | 0.12817 | 0.021486 | -0.12752 | 120.3471 | -0.011956 | 120.4845 | 120.4338 | 0.086695 | 0.018698 | 0.1603 | 120.2781 | -0.052831 | 120.489 | 120.4133 | 0.13527 | 0.045775 | -0.060911 | 120.476 | 120.5067 | 120.6483 | 120.4161 | -0.14088 | 120.4351 | 120.5338 | 120.4271 | 120.438 | -0.20991
3398.0938 | 120.5521 | -119.8837 | 0.70953 | 1.4211e-13 | 0.024587 | 0.016346 | 0.0098956 | -0.023148 | 0.0048523 | 0.24784 | 0.024171 | 0.03439 | -0.096637 | -0.0025021 | 0.00042948 | 0.07888 | 0.0243 | 0.032795 | 0.07502 | 0.1011 | 0.25643 | -0.058478 | 0.083464 | 0.027831 | 0.003172 | 0.038723 | 0.12817 | 0.035222 | -0.12752 | 119.8253 | -0.63451 | 119.9626 | 119.9165 | 0.091273 | -0.60844 | -0.4531 | 119.7562 | -0.67081 | 119.9672 | 119.8869 | 0.13069 | -0.58136 | -0.67431 | 119.9587 | 119.9848 | 120.1402 | 119.908 | -0.76801 | 119.9225 | 120.0119 | 119.919 | 119.9116 | -0.83705
3399.8438 | 120.8267 | -120.4788 | 0.10529 | 1.4211e-13 | 0.02416 | 0.016346 | 0.010109 | -0.023148 | 0.0048523 | 0.24021 | 0.024171 | 0.034818 | -0.096424 | -0.0027159 | 0.00064308 | 0.07888 | 0.019721 | 0.041952 | 0.084176 | 0.1011 | 0.25185 | -0.021847 | 0.083464 | 0.03241 | 0.003172 | 0.034145 | 0.13733 | 0.026065 | -0.1321 | 120.457 | -0.02111 | 120.5577 | 120.5208 | 0.063799 | -0.004191 | 0.14657 | 120.3467 | -0.071141 | 120.5623 | 120.482 | 0.13527 | 0.032043 | -0.079221 | 120.563 | 120.5799 | 120.7307 | 120.4985 | -0.12713 | 120.513 | 120.6161 | 120.5049 | 120.5112 | -0.23738
3401.6406 | 120.7718 | -120.5566 | 0.082397 | 1.4211e-13 | 0.024374 | 0.016346 | 0.010109 | -0.023362 | 0.0048523 | 0.23258 | 0.024385 | 0.034604 | -0.096637 | -0.0027159 | 0.00064308 | 0.083459 | 0.019721 | 0.028217 | 0.07502 | 0.1011 | 0.25185 | -0.040163 | 0.078886 | 0.036989 | 0.003172 | 0.038723 | 0.12359 | 0.039801 | -0.12752 | 120.5165 | -0.007377 | 120.6401 | 120.5849 | 0.06838 | 0.018698 | 0.16946 | 120.4291 | -0.043674 | 120.6355 | 120.5598 | 0.13069 | 0.041196 | -0.042596 | 120.6317 | 120.6577 | 120.8085 | 120.5764 | -0.12256 | 120.5954 | 120.6802 | 120.5964 | 120.5936 | -0.20991
3403.4375 | 120.7947 | -120.6207 | 0.091553 | 1.4211e-13 | 0.025015 | 0.016346 | 0.0098956 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.034818 | -0.096637 | -0.0029295 | 0.00064308 | 0.074302 | 0.015142 | 0.028217 | 0.07502 | 0.1011 | 0.25185 | -0.053899 | 0.074307 | 0.027831 | 0.003172 | 0.024988 | 0.12359 | 0.039801 | -0.13668 | 120.5668 | -0.016533 | 120.695 | 120.6489 | 0.082116 | 0.009542 | 0.1603 | 120.4841 | -0.066565 | 120.695 | 120.6239 | 0.13985 | 0.03204 | -0.051752 | 120.6957 | 120.7218 | 120.8726 | 120.6359 | -0.14545 | 120.6457 | 120.7443 | 120.6605 | 120.6486 | -0.22823
3405.1875 | 120.7764 | -120.6619 | 0.086975 | 1.4211e-13 | 0.024587 | 0.016346 | 0.0098956 | -0.023148 | 0.0044249 | 0.22495 | 0.024385 | 0.034818 | -0.096851 | -0.0029295 | 0.00042948 | 0.07888 | 0.019721 | 0.028217 | 0.07502 | 0.1011 | 0.24727 | -0.058478 | 0.083464 | 0.03241 | 0.007751 | 0.034145 | 0.12359 | 0.035222 | -0.12752 | 120.6034 | -0.011955 | 120.7408 | 120.6901 | 0.086695 | 0.01412 | 0.1603 | 120.5344 | -0.05283 | 120.7454 | 120.6697 | 0.13527 | 0.036618 | -0.051753 | 120.7369 | 120.763 | 120.9092 | 120.6816 | -0.14545 | 120.6961 | 120.7855 | 120.6971 | 120.6943 | -0.21449
3406.9844 | 120.7535 | -120.3506 | 0.32501 | 1.4211e-13 | 0.025015 | 0.016346 | 0.0098956 | -0.023148 | 0.0046387 | 0.24021 | 0.024598 | 0.034604 | -0.096424 | -0.0025021 | 0.00085668 | 0.083459 | 0.015142 | 0.023639 | 0.070441 | 0.096516 | 0.25185 | -0.049321 | 0.069728 | 0.03241 | 0.003172 | 0.034145 | 0.14191 | 0.039801 | -0.12752 | 120.3013 | -0.25457 | 120.4341 | 120.3743 | 0.07296 | -0.2285 | -0.07316 | 120.2231 | -0.29087 | 120.4204 | 120.3538 | 0.13069 | -0.18311 | -0.28521 | 120.4211 | 120.4472 | 120.6025 | 120.3658 | -0.37433 | 120.3848 | 120.4926 | 120.3904 | 120.3831 | -0.45253
3408.7812 | 120.9595 | -120.6116 | 0.082397 | 1.4211e-13 | 0.024587 | 0.016133 | 0.010323 | -0.023362 | 0.0048523 | 0.24021 | 0.024812 | 0.034818 | -0.096424 | -0.0025021 | 0.00085668 | 0.074302 | 0.019721 | 0.032795 | 0.079598 | 0.10567 | 0.25185 | -0.044742 | 0.078886 | 0.023253 | -0.001407 | 0.043302 | 0.13733 | 0.030644 | -0.1321 | 120.5668 | -0.002799 | 120.6859 | 120.6444 | 0.077537 | 0.023277 | 0.16946 | 120.4795 | -0.039095 | 120.6905 | 120.6102 | 0.13069 | 0.054932 | -0.051753 | 120.6912 | 120.7172 | 120.8634 | 120.6313 | -0.12714 | 120.6549 | 120.7489 | 120.6422 | 120.6348 | -0.21449
3410.5781 | 120.8588 | -120.6573 | 0.10986 | 1.4211e-13 | 0.02416 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.024598 | 0.03439 | -0.096637 | -0.0029295 | 0.00085668 | 0.07888 | 0.0243 | 0.028217 | 0.07502 | 0.091937 | 0.25185 | -0.058478 | 0.078886 | 0.03241 | -0.001407 | 0.034145 | 0.14191 | 0.039801 | -0.12294 | 120.5989 | -0.034843 | 120.7362 | 120.6856 | 0.086695 | -0.017926 | 0.14199 | 120.5344 | -0.075718 | 120.7362 | 120.6559 | 0.12153 | 0.032044 | -0.070062 | 120.7324 | 120.7493 | 120.9092 | 120.6816 | -0.16834 | 120.6915 | 120.7993 | 120.6971 | 120.6898 | -0.2328
3412.3125 | 120.9457 | -120.5612 | 0.14191 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023148 | 0.0044249 | 0.22495 | 0.024385 | 0.03439 | -0.096637 | -0.0027159 | 0.00085668 | 0.074302 | 0.019721 | 0.037373 | 0.07502 | 0.1011 | 0.25185 | -0.058478 | 0.083464 | 0.027831 | 0.007751 | 0.029566 | 0.13275 | 0.030644 | -0.12294 | 120.5027 | -0.066887 | 120.6355 | 120.5986 | 0.095851 | -0.040812 | 0.10995 | 120.4383 | -0.11234 | 120.6447 | 120.569 | 0.13069 | -0.009157 | -0.11126 | 120.6362 | 120.6623 | 120.8131 | 120.5809 | -0.20039 | 120.5908 | 120.694 | 120.5919 | 120.589 | -0.26485
3414.0938 | 120.8633 | -120.7031 | 0.09613 | 1.4211e-13 | 0.024374 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.23258 | 0.024598 | 0.034818 | -0.096424 | -0.0027159 | 0.00085668 | 0.07888 | 0.019721 | 0.041952 | 0.07502 | 0.096516 | 0.24727 | -0.053899 | 0.078886 | 0.027831 | 0.007751 | 0.034145 | 0.13733 | 0.039801 | -0.1321 | 120.6492 | -0.02111 | 120.782 | 120.7451 | 0.095851 | 0.000386 | 0.15114 | 120.571 | -0.061985 | 120.782 | 120.7109 | 0.13985 | 0.041199 | -0.056329 | 120.7781 | 120.7996 | 120.9504 | 120.7228 | -0.15003 | 120.7373 | 120.8405 | 120.7429 | 120.731 | -0.22823
3415.8125 | 120.8405 | -120.7031 | 0.11902 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.023576 | 0.0046387 | 0.23258 | 0.024598 | 0.034604 | -0.096637 | -0.0027159 | 0.00064308 | 0.07888 | 0.010564 | 0.028217 | 0.070441 | 0.1011 | 0.25643 | -0.049321 | 0.083464 | 0.036989 | 0.003172 | 0.034145 | 0.13733 | 0.030644 | -0.1321 | 120.6538 | -0.048578 | 120.782 | 120.7313 | 0.077538 | -0.017924 | 0.13741 | 120.571 | -0.084874 | 120.7866 | 120.7063 | 0.13527 | 0.01831 | -0.088375 | 120.7736 | 120.8042 | 120.9596 | 120.7137 | -0.16834 | 120.7373 | 120.8405 | 120.7338 | 120.7401 | -0.25112
3417.625 | 120.9137 | -120.7581 | 0.10529 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010323 | -0.023576 | 0.0048523 | 0.24784 | 0.024171 | 0.034604 | -0.096424 | -0.0020749 | 0.00042948 | 0.074302 | 0.019721 | 0.037373 | 0.07502 | 0.096516 | 0.25185 | -0.031005 | 0.083464 | 0.03241 | 0.007751 | 0.04788 | 0.14191 | 0.026065 | -0.12752 | 120.7271 | -0.030266 | 120.8324 | 120.7954 | 0.068378 | -0.00877 | 0.14657 | 120.6305 | -0.057406 | 120.8415 | 120.7658 | 0.13527 | 0.036621 | -0.079221 | 120.8331 | 120.8546 | 121.0099 | 120.7778 | -0.13629 | 120.8059 | 120.9 | 120.7841 | 120.7905 | -0.2328
3419.4219 | 121.0007 | -120.7626 | 0.054932 | 1.4211e-13 | 0.024801 | 0.015919 | 0.0098956 | -0.022935 | 0.0044249 | 0.24021 | 0.024171 | 0.034604 | -0.096424 | -0.0027159 | 0.00085668 | 0.083459 | 0.019721 | 0.032795 | 0.07502 | 0.10567 | 0.25185 | -0.067636 | 0.078886 | 0.027831 | 0.003172 | 0.034145 | 0.13275 | 0.035222 | -0.12294 | 120.695 | 0.020088 | 120.8461 | 120.7954 | 0.10043 | 0.050742 | 0.19692 | 120.6397 | -0.020787 | 120.8415 | 120.7658 | 0.12611 | 0.077818 | -0.01971 | 120.8377 | 120.8683 | 121.0145 | 120.7824 | -0.12257 | 120.7968 | 120.8954 | 120.7979 | 120.7905 | -0.17787
3421.2188 | 119.8471 | -77.3666 | 42.3614 | 1.4211e-13 | 0.024801 | 0.01656 | 0.010109 | -0.022721 | 0.0046387 | 0.23258 | 0.024598 | 0.034604 | -0.096424 | -0.0022885 | 0.00064308 | 0.060567 | 0.001407 | 0.01906 | 0.061284 | 0.08278 | 0.23354 | -0.085952 | 0.069728 | 0.014095 | -0.010564 | 0.015831 | 0.11444 | 0.026065 | -0.14583 | 77.2807 | -42.3002 | 77.4272 | 77.3857 | 0.10501 | -42.2787 | -42.1279 | 77.2208 | -42.3456 | 77.4364 | 77.3561 | 0.13527 | -42.247 | -42.3354 | 77.4279 | 77.4494 | 77.6002 | 77.368 | -42.4474 | 77.3825 | 77.4811 | 77.3927 | 77.3807 | -42.5073
3422.9375 | 120.7169 | -118.2266 | 2.0462 | 1.4211e-13 | 0.024374 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.24784 | 0.024598 | 0.034818 | -0.096424 | -0.0027159 | 0.00064308 | 0.074302 | 0.019721 | 0.01906 | 0.065863 | 0.1011 | 0.25185 | -0.021847 | 0.074307 | 0.027831 | -0.001407 | 0.029566 | 0.13275 | 0.021486 | -0.1321 | 118.2048 | -1.9803 | 118.3009 | 118.2457 | 0.040907 | -1.9451 | -1.7944 | 118.0945 | -2.0166 | 118.3009 | 118.2252 | 0.13069 | -1.9135 | -2.0247 | 118.2925 | 118.3277 | 118.4785 | 118.2463 | -2.0681 | 118.2562 | 118.3594 | 118.2481 | 118.2545 | -2.1783
3424.7188 | 121.7606 | -67.5339 | 50.6516 | 1.4211e-13 | 0.024801 | 0.01656 | 0.010109 | -0.023362 | 0.0048523 | 0.25547 | 0.024171 | 0.034818 | -0.096637 | -0.0025021 | 0.00064308 | 0.060567 | -0.003172 | 0.014482 | 0.056706 | 0.087359 | 0.22896 | -0.085952 | 0.060571 | 0.014095 | -0.015143 | 0.015831 | 0.12359 | 0.021486 | -0.15041 | 67.4479 | -50.5948 | 67.5944 | 67.5484 | 0.10043 | -50.5642 | -50.4226 | 67.3835 | -50.6357 | 67.5944 | 67.5187 | 0.13527 | -50.528 | -50.6301 | 67.5906 | 67.6212 | 67.7628 | 67.5307 | -50.7375 | 67.5497 | 67.6575 | 67.5554 | 67.548 | -50.802
3426.4375 | 120.8588 | -119.3985 | 1.0941 | 1.4211e-13 | 0.024801 | 0.01656 | 0.009682 | -0.023362 | 0.0044249 | 0.24021 | 0.024385 | 0.03439 | -0.096851 | -0.0025021 | 0.00064308 | 0.07888 | 0.019721 | 0.028217 | 0.070441 | 0.1011 | 0.25185 | -0.058478 | 0.078886 | 0.03241 | 0.01233 | 0.024988 | 0.13275 | 0.026065 | -0.1321 | 119.34 | -1.0236 | 119.4774 | 119.4267 | 0.086695 | -0.99296 | -0.8422 | 119.2664 | -1.0691 | 119.4774 | 119.4108 | 0.14443 | -0.9613 | -1.068 | 119.4689 | 119.4996 | 119.6504 | 119.4182 | -1.1525 | 119.4235 | 119.5312 | 119.4246 | 119.4309 | -1.2262
3428.2188 | 120.8771 | -114.6652 | 4.3625 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023148 | 0.0046387 | 0.24784 | 0.024385 | 0.034604 | -0.096424 | -0.0029295 | 0.00085668 | 0.083459 | 0.0243 | 0.028217 | 0.079598 | 0.096516 | 0.25643 | -0.040163 | 0.083464 | 0.027831 | 0.003172 | 0.029566 | 0.13275 | 0.030644 | -0.1321 | 114.6251 | -4.2829 | 114.7487 | 114.6934 | 0.06838 | -4.266 | -4.1061 | 114.5331 | -4.3329 | 114.7487 | 114.6684 | 0.13527 | -4.2297 | -4.3318 | 114.7448 | 114.7617 | 114.9217 | 114.6895 | -4.4027 | 114.6948 | 114.798 | 114.6959 | 114.6931 | -4.4946
3430.0156 | 120.8313 | -119.8929 | 0.84228 | 1.4211e-13 | 0.024374 | 0.016346 | 0.0098956 | -0.023362 | 0.0044249 | 0.23258 | 0.024385 | 0.034604 | -0.096637 | -0.0027159 | 0.00064308 | 0.07888 | 0.019721 | 0.032795 | 0.07502 | 0.096516 | 0.24727 | -0.058478 | 0.078886 | 0.027831 | 0.003172 | 0.038723 | 0.12817 | 0.044379 | -0.12752 | 119.8344 | -0.76726 | 119.9718 | 119.9257 | 0.091273 | -0.74577 | -0.59501 | 119.7654 | -0.80356 | 119.9718 | 119.8961 | 0.13069 | -0.71411 | -0.79791 | 119.9679 | 119.9894 | 120.1402 | 119.9126 | -0.90076 | 119.9316 | 120.0211 | 119.9373 | 119.9207 | -0.9698
3431.7344 | 120.9457 | -119.8425 | 0.85144 | 1.4211e-13 | 0.024374 | 0.01656 | 0.0098956 | -0.023148 | 0.0046387 | 0.24021 | 0.024598 | 0.034604 | -0.096424 | -0.0027159 | 0.00064308 | 0.083459 | 0.019721 | 0.037373 | 0.079598 | 0.1011 | 0.25185 | -0.053899 | 0.083464 | 0.027831 | 0.003172 | 0.029566 | 0.12359 | 0.026065 | -0.12752 | 119.7886 | -0.77184 | 119.926 | 119.8799 | 0.091272 | -0.75034 | -0.59959 | 119.715 | -0.82187 | 119.926 | 119.8457 | 0.13069 | -0.72785 | -0.82537 | 119.9221 | 119.9436 | 120.0944 | 119.8623 | -0.90534 | 119.8721 | 119.9661 | 119.8686 | 119.8704 | -0.97896
3433.5156 | 120.8817 | -120.0073 | 0.81482 | 1.4211e-13 | 0.024374 | 0.016133 | 0.009682 | -0.023576 | 0.0050659 | 0.24021 | 0.024598 | 0.03439 | -0.096424 | -0.0025021 | 0.00085668 | 0.07888 | 0.019721 | 0.028217 | 0.07502 | 0.10567 | 0.24727 | -0.044742 | 0.078886 | 0.03241 | 0.003172 | 0.029566 | 0.12359 | 0.035222 | -0.13668 | 119.9626 | -0.7398 | 120.0862 | 120.0355 | 0.072959 | -0.70914 | -0.56754 | 119.8706 | -0.78525 | 120.0862 | 120.0105 | 0.13985 | -0.69123 | -0.7796 | 120.0823 | 120.113 | 120.2546 | 120.027 | -0.85956 | 120.0369 | 120.1309 | 120.0425 | 120.0397 | -0.95149
3435.3125 | 120.9961 | -120.1035 | 0.63629 | 1.4211e-13 | 0.024587 | 0.016133 | 0.0098956 | -0.023362 | 0.0048523 | 0.23258 | 0.024385 | 0.034177 | -0.096851 | -0.0027159 | 0.00064308 | 0.07888 | 0.0243 | 0.032795 | 0.070441 | 0.1011 | 0.25185 | -0.053899 | 0.083464 | 0.03241 | -0.001407 | 0.024988 | 0.11901 | 0.030644 | -0.12752 | 120.0496 | -0.56585 | 120.1823 | 120.1362 | 0.086694 | -0.5352 | -0.38444 | 119.9759 | -0.6113 | 120.1869 | 120.102 | 0.12611 | -0.51728 | -0.60565 | 120.1739 | 120.2045 | 120.3553 | 120.1278 | -0.69019 | 120.1284 | 120.2225 | 120.1341 | 120.1359 | -0.76381
3437.0469 | 121.051 | -120.1401 | 0.61798 | 1.4211e-13 | 0.025015 | 0.016346 | 0.010109 | -0.023362 | 0.0046387 | 0.24021 | 0.024598 | 0.034818 | -0.096424 | -0.0025021 | 0.00064308 | 0.083459 | 0.0243 | 0.032795 | 0.070441 | 0.10567 | 0.24727 | -0.058478 | 0.078886 | 0.027831 | -0.001407 | 0.029566 | 0.12817 | 0.030644 | -0.13668 | 120.0816 | -0.54754 | 120.2235 | 120.1729 | 0.091273 | -0.51231 | -0.37071 | 120.0034 | -0.58842 | 120.219 | 120.1387 | 0.13527 | -0.48981 | -0.58734 | 120.2105 | 120.2457 | 120.3873 | 120.1644 | -0.67646 | 120.1696 | 120.2682 | 120.1707 | 120.1679 | -0.75466
3438.8281 | 121.0556 | -119.4946 | 1.2817 | 1.4211e-13 | 0.024801 | 0.016346 | 0.009682 | -0.023362 | 0.0048523 | 0.23258 | 0.024171 | 0.035031 | -0.096424 | -0.0025021 | 0.00064308 | 0.074302 | 0.019721 | 0.037373 | 0.079598 | 0.1011 | 0.25185 | -0.058478 | 0.074307 | 0.027831 | 0.003172 | 0.038723 | 0.13275 | 0.035222 | -0.1321 | 119.4362 | -1.2021 | 119.5689 | 119.532 | 0.095851 | -1.1806 | -1.0299 | 119.3625 | -1.243 | 119.5689 | 119.4978 | 0.13527 | -1.149 | -1.2465 | 119.5742 | 119.5957 | 119.7465 | 119.5144 | -1.3402 | 119.5334 | 119.6274 | 119.5299 | 119.5225 | -1.4138
3440.5469 | 120.9961 | -120.3598 | 0.50812 | 1.4211e-13 | 0.024801 | 0.016346 | 0.010109 | -0.023362 | 0.0048523 | 0.23258 | 0.023957 | 0.034604 | -0.096851 | -0.0027159 | 0.00064308 | 0.074302 | 0.0243 | 0.032795 | 0.070441 | 0.096516 | 0.25185 | -0.017268 | 0.088043 | 0.03241 | 0.007751 | 0.029566 | 0.13275 | 0.035222 | -0.12752 | 120.3425 | -0.43768 | 120.4341 | 120.3926 | 0.050063 | -0.4116 | -0.25627 | 120.2323 | -0.47855 | 120.4478 | 120.3676 | 0.13527 | -0.37537 | -0.4729 | 120.4302 | 120.4563 | 120.6117 | 120.3841 | -0.52539 | 120.3894 | 120.4926 | 120.395 | 120.3922 | -0.63564
3442.2812 | 120.9549 | -119.0598 | 1.7212 | 1.4211e-13 | 0.024374 | 0.016346 | 0.010109 | -0.022935 | 0.0046387 | 0.24021 | 0.024812 | 0.034604 | -0.096424 | -0.0027159 | 0.00085668 | 0.074302 | 0.015142 | 0.028217 | 0.07502 | 0.096516 | 0.24727 | -0.040163 | 0.083464 | 0.03241 | 0.01233 | 0.029566 | 0.12817 | 0.030644 | -0.12752 | 119.0196 | -1.6462 | 119.1341 | 119.088 | 0.06838 | -1.6247 | -1.4739 | 118.9322 | -1.6916 | 119.1432 | 119.0721 | 0.13985 | -1.593 | -1.6905 | 119.1348 | 119.1563 | 119.307 | 119.0749 | -1.7614 | 119.0893 | 119.1879 | 119.0904 | 119.0922 | -1.8487
3444.0625 | 120.9824 | -120.4651 | 0.44861 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023362 | 0.0044249 | 0.23258 | 0.024598 | 0.034818 | -0.096424 | -0.0025021 | 0.00064308 | 0.07888 | 0.019721 | 0.032795 | 0.07502 | 0.096516 | 0.24727 | -0.040163 | 0.083464 | 0.03241 | 0.003172 | 0.038723 | 0.12817 | 0.035222 | -0.12752 | 120.4249 | -0.37359 | 120.544 | 120.4979 | 0.072958 | -0.35209 | -0.20133 | 120.3376 | -0.40988 | 120.5486 | 120.4683 | 0.13069 | -0.32044 | -0.41339 | 120.5401 | 120.5616 | 120.7124 | 120.4848 | -0.48877 | 120.5038 | 120.5933 | 120.5003 | 120.4975 | -0.57613
3445.8438 | 120.9366 | -118.5196 | 2.4124 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.023362 | 0.0048523 | 0.23258 | 0.024812 | 0.034818 | -0.096424 | -0.0027159 | 0.0010705 | 0.07888 | 0.019721 | 0.037373 | 0.07502 | 0.091937 | 0.24269 | -0.067636 | 0.074307 | 0.03241 | 0.007751 | 0.029566 | 0.12817 | 0.026065 | -0.12752 | 118.452 | -2.3374 | 118.5985 | 118.557 | 0.10501 | -2.3205 | -2.1697 | 118.3921 | -2.3828 | 118.5939 | 118.5273 | 0.13527 | -2.2842 | -2.3864 | 118.5946 | 118.6115 | 118.7623 | 118.5393 | -2.4801 | 118.5492 | 118.6478 | 118.5457 | 118.552 | -2.5399
3447.5938 | 121.1014 | -119.8654 | 1.0666 | 1.4211e-13 | 0.024587 | 0.016346 | 0.0098956 | -0.023148 | 0.0048523 | 0.23258 | 0.024598 | 0.034604 | -0.096637 | -0.0025021 | 0.00064308 | 0.07888 | 0.0243 | 0.032795 | 0.070441 | 0.1011 | 0.24727 | -0.040163 | 0.078886 | 0.023253 | 0.003172 | 0.034145 | 0.13275 | 0.035222 | -0.1321 | 119.8253 | -0.99615 | 119.9443 | 119.8982 | 0.072958 | -0.96549 | -0.81932 | 119.7333 | -1.0324 | 119.9443 | 119.8686 | 0.13527 | -0.93384 | -1.0314 | 119.9359 | 119.9665 | 120.1127 | 119.8897 | -1.1068 | 119.8996 | 119.9982 | 119.9006 | 119.8887 | -1.1987
3449.375 | 121.1197 | -120.3049 | 0.60883 | 1.4211e-13 | 0.024801 | 0.016346 | 0.010109 | -0.023148 | 0.0046387 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0025021 | 0.00042948 | 0.088037 | 0.015142 | 0.032795 | 0.070441 | 0.1011 | 0.25185 | -0.035584 | 0.074307 | 0.03241 | 0.003172 | 0.038723 | 0.12359 | 0.026065 | -0.12752 | 120.2693 | -0.53839 | 120.3929 | 120.3377 | 0.068379 | -0.50773 | -0.35697 | 120.1774 | -0.5701 | 120.3792 | 120.308 | 0.13069 | -0.48523 | -0.58276 | 120.3753 | 120.406 | 120.5567 | 120.32 | -0.64441 | 120.3436 | 120.4285 | 120.3309 | 120.3373 | -0.73634
3451.1719 | 121.0648 | -120.1172 | 0.82398 | 1.4211e-13 | 0.025015 | 0.016133 | 0.010109 | -0.023148 | 0.0046387 | 0.24021 | 0.024171 | 0.034604 | -0.096851 | -0.0025021 | 0.00085668 | 0.07888 | 0.019721 | 0.032795 | 0.07502 | 0.1011 | 0.24727 | -0.067636 | 0.083464 | 0.027831 | 0.007751 | 0.034145 | 0.12817 | 0.039801 | -0.1321 | 120.0496 | -0.74896 | 120.1961 | 120.15 | 0.10043 | -0.72288 | -0.5767 | 119.9851 | -0.78983 | 120.2007 | 120.1249 | 0.13985 | -0.6958 | -0.78417 | 120.1922 | 120.2183 | 120.3645 | 120.1369 | -0.89161 | 120.1513 | 120.2454 | 120.157 | 120.145 | -0.95607
3452.9062 | 121.0876 | -120.0302 | 0.94299 | 1.4211e-13 | 0.024587 | 0.016133 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024171 | 0.034818 | -0.096637 | -0.0027159 | 0.00064308 | 0.083459 | 0.019721 | 0.037373 | 0.070441 | 0.096516 | 0.25643 | -0.072215 | 0.069728 | 0.03241 | 0.003172 | 0.038723 | 0.11901 | 0.035222 | -0.12752 | 119.958 | -0.87255 | 120.1137 | 120.0676 | 0.10959 | -0.84648 | -0.68656 | 119.9027 | -0.90427 | 120.0999 | 120.0334 | 0.13069 | -0.82398 | -0.90777 | 120.1007 | 120.1267 | 120.2866 | 120.0499 | -1.0152 | 120.0689 | 120.1492 | 120.0654 | 120.0626 | -1.0705
3454.7031 | 121.1884 | -120.0394 | 0.90637 | 1.4211e-13 | 0.024801 | 0.01656 | 0.0098956 | -0.023362 | 0.0046387 | 0.23258 | 0.024385 | 0.035031 | -0.096424 | -0.0025021 | 0.00064308 | 0.074302 | 0.0243 | 0.032795 | 0.07502 | 0.096516 | 0.25643 | -0.063057 | 0.078886 | 0.018674 | -0.001407 | 0.029566 | 0.12359 | 0.035222 | -0.12752 | 119.9763 | -0.83135 | 120.1137 | 120.0722 | 0.095852 | -0.80986 | -0.64994 | 119.9119 | -0.87681 | 120.1183 | 120.038 | 0.12611 | -0.78278 | -0.87115 | 120.1144 | 120.1359 | 120.2958 | 120.0637 | -0.96943 | 120.0689 | 120.163 | 120.0746 | 120.058 | -1.0339
3456.4375 | 121.17 | -120.4605 | 0.41657 | 1.4211e-13 | 0.025015 | 0.016133 | 0.010109 | -0.023362 | 0.0050659 | 0.23258 | 0.024598 | 0.034818 | -0.09621 | -0.0029295 | 0.00064308 | 0.083459 | 0.0243 | 0.032795 | 0.07502 | 0.096516 | 0.24269 | -0.085952 | 0.078886 | 0.023253 | -0.001407 | 0.029566 | 0.12817 | 0.030644 | -0.1321 | 120.3746 | -0.34154 | 120.544 | 120.4933 | 0.11875 | -0.32005 | -0.17387 | 120.3284 | -0.387 | 120.5394 | 120.4591 | 0.13069 | -0.28839 | -0.38592 | 120.5355 | 120.557 | 120.7032 | 120.4848 | -0.50252 | 120.4901 | 120.5887 | 120.4912 | 120.4838 | -0.54866
3458.25 | 121.0693 | -120.5429 | 0.47607 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023362 | 0.0048523 | 0.23258 | 0.024598 | 0.034604 | -0.096424 | -0.0022885 | 0.00021588 | 0.07888 | 0.019721 | 0.037373 | 0.07502 | 0.096516 | 0.25185 | -0.067636 | 0.083464 | 0.03241 | 0.007751 | 0.034145 | 0.13275 | 0.035222 | -0.12752 | 120.4753 | -0.40105 | 120.6218 | 120.5803 | 0.10501 | -0.37956 | -0.22422 | 120.4154 | -0.44193 | 120.6264 | 120.5507 | 0.13527 | -0.34332 | -0.44085 | 120.6179 | 120.6394 | 120.7948 | 120.5626 | -0.54371 | 120.5771 | 120.6757 | 120.5781 | 120.5753 | -0.60359
3460.0469 | 121.0602 | -120.6024 | 0.43488 | 1.4211e-13 | 0.024587 | 0.016133 | 0.010109 | -0.023362 | 0.0046387 | 0.22495 | 0.024385 | 0.034818 | -0.096637 | -0.0029295 | 0.00064308 | 0.088037 | 0.0243 | 0.028217 | 0.070441 | 0.096516 | 0.25185 | -0.058478 | 0.078886 | 0.027831 | 0.01233 | 0.043302 | 0.12817 | 0.026065 | -0.1321 | 120.5439 | -0.36443 | 120.6905 | 120.6306 | 0.086695 | -0.33836 | -0.18302 | 120.4703 | -0.39157 | 120.6813 | 120.6147 | 0.14443 | -0.3067 | -0.40881 | 120.6729 | 120.6989 | 120.8543 | 120.6267 | -0.49335 | 120.6457 | 120.7306 | 120.6285 | 120.6302 | -0.56697
3461.7812 | 121.1838 | -120.52 | 0.45776 | 1.4211e-13 | 0.024801 | 0.015705 | 0.010323 | -0.023362 | 0.0050659 | 0.24784 | 0.024385 | 0.035031 | -0.096424 | -0.0022885 | 0.00085668 | 0.069723 | 0.019721 | 0.028217 | 0.070441 | 0.096516 | 0.25643 | -0.067636 | 0.074307 | 0.027831 | -0.001407 | 0.029566 | 0.13733 | 0.035222 | -0.12752 | 120.4524 | -0.38732 | 120.5897 | 120.5482 | 0.095853 | -0.36125 | -0.20133 | 120.3925 | -0.4282 | 120.5943 | 120.5186 | 0.12611 | -0.32044 | -0.42254 | 120.5905 | 120.6165 | 120.7765 | 120.5397 | -0.5254 | 120.5496 | 120.6573 | 120.5552 | 120.5479 | -0.58528
3463.5625 | 121.1105 | -120.4971 | 0.50812 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.023362 | 0.0046387 | 0.23258 | 0.024598 | 0.034604 | -0.096637 | -0.0025021 | 0.00085668 | 0.07888 | 0.015142 | 0.041952 | 0.070441 | 0.096516 | 0.25185 | -0.085952 | 0.074307 | 0.027831 | 0.003172 | 0.029566 | 0.12817 | 0.035222 | -0.12752 | 120.4112 | -0.43768 | 120.576 | 120.5391 | 0.1279 | -0.4116 | -0.25627 | 120.3696 | -0.47855 | 120.5714 | 120.5003 | 0.13069 | -0.37995 | -0.4729 | 120.5676 | 120.5936 | 120.749 | 120.5123 | -0.59407 | 120.5267 | 120.6253 | 120.5324 | 120.525 | -0.63564
3465.375 | 121.1746 | -120.5566 | 0.52185 | 1.4211e-13 | 0.024587 | 0.016133 | 0.009682 | -0.023148 | 0.0050659 | 0.24784 | 0.024385 | 0.03439 | -0.096424 | -0.0022885 | 0.00064308 | 0.074302 | 0.010564 | 0.032795 | 0.07502 | 0.096516 | 0.25185 | -0.049321 | 0.083464 | 0.023253 | 0.007751 | 0.034145 | 0.13733 | 0.039801 | -0.12752 | 120.5073 | -0.44683 | 120.6309 | 120.5894 | 0.082116 | -0.42533 | -0.27 | 120.4291 | -0.48771 | 120.6401 | 120.5644 | 0.13527 | -0.38452 | -0.48205 | 120.6317 | 120.6532 | 120.8085 | 120.5672 | -0.57117 | 120.5908 | 120.694 | 120.5964 | 120.5799 | -0.64937
3467.125 | 121.1746 | -120.4834 | 0.55847 | 1.4211e-13 | 0.024587 | 0.015919 | 0.009682 | -0.023362 | 0.0050659 | 0.23258 | 0.024385 | 0.034604 | -0.096637 | -0.0025021 | 0.00064308 | 0.074302 | 0.0243 | 0.028217 | 0.065863 | 0.1011 | 0.25185 | -0.053899 | 0.083464 | 0.027831 | 0.007751 | 0.029566 | 0.13275 | 0.039801 | -0.13668 | 120.4295 | -0.49261 | 120.5577 | 120.5116 | 0.082116 | -0.45738 | -0.30662 | 120.3467 | -0.52891 | 120.5669 | 120.4911 | 0.14443 | -0.42572 | -0.51867 | 120.5493 | 120.5845 | 120.7352 | 120.5077 | -0.61237 | 120.513 | 120.6161 | 120.5232 | 120.5112 | -0.69515
3468.9062 | 121.2021 | -120.5795 | 0.46234 | 1.4211e-13 | 0.024587 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.024171 | 0.035031 | -0.096424 | -0.0025021 | 0.00064308 | 0.07888 | 0.019721 | 0.032795 | 0.070441 | 0.096516 | 0.23812 | -0.063057 | 0.078886 | 0.036989 | 0.003172 | 0.024988 | 0.13275 | 0.044379 | -0.12752 | 120.5165 | -0.3919 | 120.6584 | 120.6123 | 0.095852 | -0.36583 | -0.22422 | 120.452 | -0.43735 | 120.6584 | 120.5827 | 0.13069 | -0.32959 | -0.41796 | 120.65 | 120.676 | 120.8176 | 120.5992 | -0.5254 | 120.6045 | 120.7123 | 120.6239 | 120.6165 | -0.58986
3470.6875 | 121.1014 | -120.0806 | 0.86517 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.023148 | 0.0046387 | 0.22495 | 0.024171 | 0.034604 | -0.096424 | -0.0025021 | 0.00064308 | 0.074302 | 0.019721 | 0.032795 | 0.07502 | 0.091937 | 0.24269 | -0.072215 | 0.083464 | 0.03241 | 0.01233 | 0.029566 | 0.12817 | 0.026065 | -0.12294 | 120.0084 | -0.79015 | 120.1549 | 120.1134 | 0.10501 | -0.77324 | -0.62248 | 119.9576 | -0.83561 | 120.164 | 120.0929 | 0.13527 | -0.737 | -0.83911 | 120.1556 | 120.1725 | 120.3233 | 120.1003 | -0.93739 | 120.1101 | 120.2087 | 120.1066 | 120.113 | -0.98811
3472.4844 | 121.2158 | -120.4376 | 0.72327 | 1.4211e-13 | 0.025015 | 0.016133 | 0.010109 | -0.023148 | 0.0050659 | 0.24021 | 0.024812 | 0.034604 | -0.096424 | -0.0027159 | 0.00042948 | 0.07888 | 0.019721 | 0.037373 | 0.065863 | 0.096516 | 0.24269 | -0.067636 | 0.088043 | 0.027831 | 0.007751 | 0.029566 | 0.13275 | 0.026065 | -0.12294 | 120.37 | -0.6574 | 120.5165 | 120.475 | 0.10501 | -0.62675 | -0.48057 | 120.3147 | -0.6937 | 120.5257 | 120.4454 | 0.13069 | -0.59052 | -0.6972 | 120.5035 | 120.5341 | 120.6803 | 120.4573 | -0.7909 | 120.4672 | 120.5704 | 120.4637 | 120.4655 | -0.84621
3474.2188 | 121.3394 | -120.5017 | 0.57678 | 1.4211e-13 | 0.024374 | 0.016346 | 0.0094682 | -0.023362 | 0.0046387 | 0.24784 | 0.024385 | 0.034604 | -0.096637 | -0.0029295 | 0.00064308 | 0.07888 | 0.015142 | 0.032795 | 0.07502 | 0.096516 | 0.25185 | -0.067636 | 0.083464 | 0.027831 | 0.007751 | 0.038723 | 0.13733 | 0.044379 | -0.12752 | 120.4341 | -0.50176 | 120.5806 | 120.5345 | 0.10043 | -0.48027 | -0.32493 | 120.3742 | -0.53806 | 120.5852 | 120.5095 | 0.13527 | -0.43945 | -0.5324 | 120.5767 | 120.5982 | 120.7536 | 120.5169 | -0.64442 | 120.5404 | 120.639 | 120.5461 | 120.5295 | -0.7043
3476.0156 | 121.1975 | -120.6482 | 0.47607 | 1.4211e-13 | 0.024587 | 0.016346 | 0.010109 | -0.023362 | 0.0046387 | 0.23258 | 0.024598 | 0.034818 | -0.096424 | -0.0025021 | 0.00064308 | 0.083459 | 0.019721 | 0.037373 | 0.07502 | 0.1011 | 0.25185 | -0.072215 | 0.083464 | 0.027831 | 0.01233 | 0.034145 | 0.12817 | 0.039801 | -0.12752 | 120.576 | -0.40105 | 120.7317 | 120.6856 | 0.10959 | -0.37498 | -0.22422 | 120.5207 | -0.44193 | 120.7317 | 120.6605 | 0.13985 | -0.3479 | -0.43627 | 120.7232 | 120.7493 | 120.9 | 120.6679 | -0.54829 | 120.6823 | 120.7764 | 120.688 | 120.676 | -0.60359
3477.75 | 119.632 | -9.8923 | 109.5886 | 1.4211e-13 | 0.024801 | 0.015492 | 0.0092546 | -0.023148 | 0.0035703 | 0.24021 | 0.024385 | 0.035031 | -0.096637 | -0.0025021 | 0.00085668 | 0.046831 | -0.007751 | 0.009904 | 0.052128 | 0.08278 | 0.23354 | -0.090531 | 0.055992 | 0.004938 | -0.015143 | 0.011252 | 0.11444 | 0.012329 | -0.15041 | 9.8017 | -109.5365 | 9.9391 | 9.9022 | 0.10043 | -109.5058 | -109.3551 | 9.7419 | -109.5774 | 9.9483 | 9.8771 | 0.13527 | -109.4742 | -109.5763 | 9.9444 | 9.9751 | 10.1258 | 9.8845 | -109.6792 | 9.9035 | 10.0067 | 9.9046 | 9.8972 | -109.739
3479.5312 | 120.6619 | -13.9389 | 106.7459 | 1.4211e-13 | 0.024587 | 0.016133 | 0.0098956 | -0.023362 | 0.0044249 | 0.23258 | 0.024385 | 0.035031 | -0.096637 | -0.0029295 | 0.00042948 | 0.046831 | -0.016908 | 0.000747 | 0.038393 | 0.064464 | 0.21522 | -0.09511 | 0.042256 | 0.000359 | -0.033458 | 0.002095 | 0.091543 | -0.060928 | -0.17331 | 13.8438 | -106.7075 | 13.9857 | 13.9397 | 0.095857 | -106.6814 | -106.5307 | 13.7656 | -106.7438 | 13.9812 | 13.9054 | 0.13985 | -106.6544 | -106.8068 | 13.9773 | 14.0034 | 14.1541 | 13.922 | -106.841 | 13.941 | 14.0304 | 13.878 | 13.9393 | -106.9192
3481.2656 | 108.6502 | -54.6753 | 66.0233 | 1.4211e-13 | 0.024587 | 0.016133 | 0.0098956 | -0.022935 | 0.0044249 | 0.23258 | 0.024385 | 0.034177 | -0.096851 | -0.0027159 | 0.00085668 | 0.069723 | 0.010564 | 0.01906 | 0.065863 | 0.078201 | 0.24269 | -0.090531 | 0.06515 | 0.023253 | -0.005985 | 0.020409 | 0.10986 | 0.021486 | -0.13668 | 54.5848 | -65.9574 | 54.745 | 54.6944 | 0.10959 | -65.9451 | -65.7806 | 54.5386 | -66.0028 | 54.7404 | 54.6693 | 0.13069 | -65.9134 | -66.0018 | 54.7412 | 54.7535 | 54.918 | 54.6859 | -66.1138 | 54.6957 | 54.7852 | 54.6968 | 54.6985 | -66.1599
3483.0625 | 121.3486 | -117.6041 | 3.392 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.023148 | 0.0050659 | 0.23258 | 0.024171 | 0.034818 | -0.096424 | -0.0022885 | 0.00085668 | 0.065145 | 0.001407 | 0.014482 | 0.065863 | 0.08278 | 0.23812 | -0.09511 | 0.069728 | 0.018674 | -0.001407 | 0.015831 | 0.12359 | 0.030644 | -0.1321 | 117.509 | -3.3262 | 117.6692 | 117.6185 | 0.10959 | -3.3092 | -3.1539 | 117.472 | -3.3762 | 117.6738 | 117.6027 | 0.13069 | -3.2684 | -3.3614 | 117.6699 | 117.6868 | 117.8422 | 117.6055 | -3.4871 | 117.6199 | 117.7277 | 117.6347 | 117.6227 | -3.5241
3484.8594 | 121.2753 | -118.8309 | 2.0416 | 1.4211e-13 | 0.024374 | 0.016133 | 0.010109 | -0.023148 | 0.0050659 | 0.23258 | 0.024385 | 0.034818 | -0.096424 | -0.0022885 | 0.00085668 | 0.074302 | 0.028878 | 0.028217 | 0.079598 | 0.096516 | 0.25185 | -0.058478 | 0.083464 | 0.027831 | -0.001407 | 0.034145 | 0.13733 | 0.030644 | -0.13668 | 118.7724 | -1.962 | 118.9052 | 118.8591 | 0.086695 | -1.9451 | -1.7898 | 118.6942 | -2.0075 | 118.9143 | 118.8295 | 0.13527 | -1.9043 | -2.011 | 118.9105 | 118.9274 | 119.0827 | 118.8598 | -2.1001 | 118.865 | 118.9682 | 118.8615 | 118.8587 | -2.1783
3486.6562 | 121.2158 | -119.1605 | 1.8082 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023362 | 0.0048523 | 0.24784 | 0.024598 | 0.035031 | -0.096424 | -0.0027159 | 0.00042948 | 0.07888 | 0.019721 | 0.028217 | 0.079598 | 0.1011 | 0.25185 | -0.067636 | 0.083464 | 0.03241 | 0.01233 | 0.034145 | 0.12359 | 0.053537 | -0.1321 | 119.0928 | -1.7286 | 119.2393 | 119.1887 | 0.095853 | -1.7071 | -1.5563 | 119.0284 | -1.774 | 119.2439 | 119.1728 | 0.14443 | -1.6846 | -1.7546 | 119.2401 | 119.2616 | 119.4123 | 119.1802 | -1.8758 | 119.1946 | 119.2841 | 119.214 | 119.1929 | -1.9403
3488.3906 | 121.3165 | -120.3827 | 0.54016 | 1.4211e-13 | 0.025015 | 0.016346 | 0.010109 | -0.022935 | 0.0048523 | 0.23258 | 0.024598 | 0.034818 | -0.096851 | -0.0029295 | 0.00064308 | 0.074302 | 0.010564 | 0.023639 | 0.070441 | 0.091937 | 0.25643 | -0.063057 | 0.074307 | 0.023253 | 0.003172 | 0.029566 | 0.13733 | 0.026065 | -0.14125 | 120.3196 | -0.46972 | 120.457 | 120.4063 | 0.086696 | -0.44822 | -0.28373 | 120.2414 | -0.5106 | 120.457 | 120.3859 | 0.14443 | -0.40283 | -0.5141 | 120.4531 | 120.4746 | 120.6391 | 120.3933 | -0.60322 | 120.4123 | 120.52 | 120.4088 | 120.4059 | -0.68142
3490.1875 | 121.3486 | -120.0806 | 0.91095 | 1.4211e-13 | 0.024801 | 0.016346 | 0.009682 | -0.023362 | 0.0044249 | 0.24784 | 0.024385 | 0.034177 | -0.096637 | -0.0025021 | 0.00085668 | 0.07888 | 0.019721 | 0.028217 | 0.070441 | 0.096516 | 0.24727 | -0.063057 | 0.078886 | 0.027831 | 0.003172 | 0.034145 | 0.12817 | 0.026065 | -0.12294 | 120.0175 | -0.84051 | 120.1594 | 120.1088 | 0.091274 | -0.81443 | -0.66368 | 119.9576 | -0.87681 | 120.1595 | 120.0837 | 0.12611 | -0.78278 | -0.88489 | 120.151 | 120.1771 | 120.3278 | 120.1003 | -0.97401 | 120.1147 | 120.2087 | 120.1066 | 120.1084 | -1.0339
3491.9688 | 121.3348 | -103.7521 | 17.0929 | 1.4211e-13 | 0.024587 | 0.016133 | 0.010109 | -0.023362 | 0.0044249 | 0.23258 | 0.024598 | 0.034818 | -0.097065 | -0.0029295 | 0.00085668 | 0.069723 | 0.010564 | 0.023639 | 0.070441 | 0.091937 | 0.24727 | -0.076794 | 0.069728 | 0.023253 | -0.010564 | 0.020409 | 0.11444 | 0.021486 | -0.14125 | 103.6753 | -17.0225 | 103.8219 | 103.7758 | 0.10043 | -17.001 | -16.8456 | 103.6109 | -17.0725 | 103.8219 | 103.7416 | 0.13069 | -16.9785 | -17.0714 | 103.8226 | 103.8441 | 103.9994 | 103.7627 | -17.1697 | 103.7725 | 103.8666 | 103.7736 | 103.7754 | -17.2342
3493.75 | 121.4447 | -119.9295 | 1.0345 | 1.4211e-13 | 0.024587 | 0.01656 | 0.0098956 | -0.023148 | 0.0046387 | 0.23258 | 0.024385 | 0.03439 | -0.096637 | -0.0029295 | 0.00042948 | 0.07888 | 0.015142 | 0.023639 | 0.079598 | 0.10567 | 0.25185 | -0.058478 | 0.083464 | 0.027831 | 0.01233 | 0.029566 | 0.12359 | 0.026065 | -0.1321 | 119.871 | -0.95495 | 120.0084 | 119.9531 | 0.082117 | -0.92887 | -0.78269 | 119.7974 | -1.005 | 120.013 | 119.9418 | 0.14443 | -0.91095 | -1.0085 | 120.0091 | 120.0352 | 120.1814 | 119.9446 | -1.093 | 119.9591 | 120.0531 | 119.9556 | 119.9573 | -1.1666
3495.4688 | 121.3943 | -119.5633 | 1.5289 | 1.4211e-13 | 0.024801 | 0.016346 | 0.009682 | -0.023362 | 0.0048523 | 0.23258 | 0.024598 | 0.034604 | -0.096851 | -0.0027159 | 0.00064308 | 0.074302 | 0.015142 | 0.032795 | 0.070441 | 0.096516 | 0.24269 | -0.063057 | 0.074307 | 0.027831 | 0.007751 | 0.034145 | 0.13733 | 0.030644 | -0.1321 | 119.5002 | -1.4585 | 119.6376 | 119.5961 | 0.095852 | -1.4324 | -1.2862 | 119.4312 | -1.4948 | 119.6376 | 119.571 | 0.13985 | -1.3916 | -1.4983 | 119.6337 | 119.6598 | 119.806 | 119.5784 | -1.592 | 119.5974 | 119.7006 | 119.5939 | 119.5911 | -1.661
3497.25 | 121.344 | -119.6182 | 1.4648 | 1.4211e-13 | 0.025015 | 0.016346 | 0.009682 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.03439 | -0.096424 | -0.0029295 | 0.00042948 | 0.07888 | 0.019721 | 0.032795 | 0.070441 | 0.096516 | 0.25643 | -0.063057 | 0.078886 | 0.03241 | 0.003172 | 0.024988 | 0.13275 | 0.030644 | -0.12752 | 119.5552 | -1.3944 | 119.6971 | 119.651 | 0.095852 | -1.3683 | -1.2084 | 119.4907 | -1.4399 | 119.6971 | 119.6214 | 0.13069 | -1.3321 | -1.4342 | 119.6887 | 119.7147 | 119.8747 | 119.6379 | -1.5279 | 119.6432 | 119.751 | 119.6489 | 119.6506 | -1.5924
3499.0312 | 120.2042 | -120.0073 | 0.13733 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.023148 | 0.0046387 | 0.23258 | 0.024385 | 0.034604 | -0.096424 | -0.0027159 | 0.00085668 | 0.069723 | 0.019721 | 0.032795 | 0.070441 | 0.1011 | 0.25185 | -0.063057 | 0.083464 | 0.03241 | 0.003172 | 0.029566 | 0.12817 | 0.026065 | -0.12752 | 119.9443 | -0.066888 | 120.077 | 120.0401 | 0.095852 | -0.036234 | 0.11452 | 119.8798 | -0.10776 | 120.0908 | 120.0105 | 0.13069 | -0.009157 | -0.11126 | 120.0778 | 120.1084 | 120.2592 | 120.027 | -0.20039 | 120.0369 | 120.1355 | 120.0334 | 120.0397 | -0.26485
3500.8281 | 120.9824 | -120.6573 | 0.059509 | 1.4211e-13 | 0.024374 | 0.016346 | 0.0098956 | -0.023576 | 0.0044249 | 0.23258 | 0.024385 | 0.034818 | -0.096637 | -0.0025021 | 0.00085668 | 0.074302 | 0.015142 | 0.032795 | 0.07502 | 0.096516 | 0.25643 | -0.053899 | 0.083464 | 0.03241 | 0.003172 | 0.038723 | 0.12817 | 0.026065 | -0.1321 | 120.6034 | 0.015511 | 120.7317 | 120.6901 | 0.086694 | 0.037007 | 0.19692 | 120.5253 | -0.020786 | 120.7408 | 120.6605 | 0.13527 | 0.068663 | -0.033444 | 120.7324 | 120.7539 | 120.9138 | 120.6725 | -0.11341 | 120.6961 | 120.7855 | 120.6834 | 120.6898 | -0.19161
3502.6406 | 121.0968 | -120.7489 | 0.059509 | 1.4211e-13 | 0.024374 | 0.016346 | 0.0098956 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.034818 | -0.09621 | -0.0025021 | 0.00085668 | 0.083459 | 0.010564 | 0.032795 | 0.070441 | 0.10567 | 0.25185 | -0.044742 | 0.078886 | 0.027831 | 0.007751 | 0.034145 | 0.12817 | 0.035222 | -0.12752 | 120.7042 | 0.010932 | 120.8324 | 120.7817 | 0.077537 | 0.046165 | 0.19234 | 120.6214 | -0.025364 | 120.8278 | 120.7567 | 0.13527 | 0.068663 | -0.024287 | 120.8193 | 120.8546 | 121.0008 | 120.7595 | -0.10425 | 120.783 | 120.8771 | 120.7841 | 120.7767 | -0.18703
3504.4219 | 121.051 | -120.8542 | 0.086975 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023362 | 0.0050659 | 0.23258 | 0.024598 | 0.034818 | -0.09621 | -0.0022885 | 0.00085668 | 0.083459 | 0.019721 | 0.028217 | 0.07502 | 0.091937 | 0.25185 | -0.058478 | 0.083464 | 0.027831 | 0.003172 | 0.029566 | 0.12817 | 0.030644 | -0.1321 | 120.7957 | -0.011955 | 120.9376 | 120.8824 | 0.086695 | 0.004962 | 0.16488 | 120.7221 | -0.057409 | 120.9377 | 120.8574 | 0.13527 | 0.041197 | -0.056331 | 120.9292 | 120.9461 | 121.106 | 120.8739 | -0.14545 | 120.8838 | 120.9824 | 120.8848 | 120.882 | -0.21907
3506.1562 | 121.1884 | -120.8359 | 0.07782 | 1.4211e-13 | 0.024374 | 0.016133 | 0.010109 | -0.023362 | 0.0046387 | 0.23258 | 0.024385 | 0.034818 | -0.09621 | -0.0020749 | 0.00021588 | 0.074302 | 0.015142 | 0.032795 | 0.070441 | 0.1011 | 0.24727 | -0.053899 | 0.078886 | 0.027831 | 0.007751 | 0.034145 | 0.12817 | 0.030644 | -0.11836 | 120.782 | -0.007379 | 120.9102 | 120.8687 | 0.086694 | 0.023275 | 0.16945 | 120.7175 | -0.043675 | 120.9148 | 120.8436 | 0.12611 | 0.050352 | -0.047176 | 120.9063 | 120.937 | 121.0832 | 120.851 | -0.13172 | 120.87 | 120.964 | 120.8665 | 120.8637 | -0.19618
3507.9531 | 120.8633 | -120.9091 | 0.1236 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.023576 | 0.0048523 | 0.24784 | 0.024171 | 0.034604 | -0.096424 | -0.0027159 | 0.00085668 | 0.07888 | 0.0243 | 0.037373 | 0.07502 | 0.096516 | 0.24727 | -0.053899 | 0.088043 | 0.023253 | 0.01233 | 0.034145 | 0.12817 | 0.039801 | -0.12294 | 120.8552 | -0.048576 | 120.988 | 120.9465 | 0.091272 | -0.02708 | 0.12368 | 120.7862 | -0.089451 | 120.9972 | 120.9214 | 0.13527 | 0.004576 | -0.083795 | 120.9841 | 121.0056 | 121.1564 | 120.9334 | -0.1775 | 120.9433 | 121.0373 | 120.9489 | 120.9324 | -0.24654
3509.7344 | 121.2341 | -120.8954 | 0.073242 | 1.4211e-13 | 0.024587 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.23258 | 0.024598 | 0.034604 | -0.096424 | -0.0022885 | 0.00064308 | 0.07888 | 0.019721 | 0.028217 | 0.070441 | 0.096516 | 0.25185 | -0.053899 | 0.083464 | 0.036989 | 0.007751 | 0.034145 | 0.12817 | 0.035222 | -0.12752 | 120.8415 | -0.002801 | 120.9743 | 120.9236 | 0.082116 | 0.023274 | 0.17861 | 120.7679 | -0.039097 | 120.9789 | 120.9031 | 0.13527 | 0.05493 | -0.03802 | 120.9658 | 120.9919 | 121.1472 | 120.9151 | -0.12714 | 120.9295 | 121.0236 | 120.9306 | 120.9324 | -0.20076
3511.4531 | 121.2296 | -120.9091 | 0.064087 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.023576 | 0.0048523 | 0.24021 | 0.024598 | 0.034818 | -0.096424 | -0.0025021 | 0.00064308 | 0.07888 | 0.015142 | 0.032795 | 0.07502 | 0.096516 | 0.25185 | -0.049321 | 0.078886 | 0.027831 | 0.003172 | 0.029566 | 0.12817 | 0.030644 | -0.12752 | 120.8598 | 0.010933 | 120.988 | 120.9419 | 0.082116 | 0.032429 | 0.18777 | 120.7816 | -0.034521 | 120.988 | 120.9123 | 0.13069 | 0.064085 | -0.033443 | 120.9841 | 121.0056 | 121.161 | 120.9243 | -0.11341 | 120.9387 | 121.0373 | 120.9398 | 120.937 | -0.1916
3513.25 | 121.2524 | -120.9595 | 0.059509 | 1.4211e-13 | 0.024587 | 0.016346 | 0.009682 | -0.023362 | 0.0048523 | 0.24021 | 0.024385 | 0.034604 | -0.096851 | -0.0027159 | 0.00085668 | 0.07888 | 0.028878 | 0.037373 | 0.084176 | 0.10567 | 0.24727 | -0.044742 | 0.074307 | 0.023253 | 0.007751 | 0.029566 | 0.12359 | 0.026065 | -0.12294 | 120.9147 | 0.024667 | 121.0384 | 120.9968 | 0.082115 | 0.046165 | 0.18776 | 120.8365 | -0.029943 | 121.0338 | 120.9672 | 0.13069 | 0.064084 | -0.033444 | 121.0436 | 121.0651 | 121.2067 | 120.9884 | -0.10425 | 120.989 | 121.0831 | 120.9855 | 120.9827 | -0.18245
3515.0469 | 121.2387 | -120.9778 | 0.054932 | 1.4211e-13 | 0.024587 | 0.016133 | 0.0098956 | -0.023362 | 0.0048523 | 0.23258 | 0.024385 | 0.03439 | -0.096424 | -0.0027159 | 0.00064308 | 0.074302 | 0.019721 | 0.023639 | 0.070441 | 0.096516 | 0.24727 | -0.053899 | 0.083464 | 0.027831 | -0.001407 | 0.034145 | 0.13275 | 0.030644 | -0.12752 | 120.9239 | 0.015509 | 121.0521 | 121.0014 | 0.077538 | 0.041584 | 0.19234 | 120.8503 | -0.020787 | 121.0612 | 120.9764 | 0.12611 | 0.077818 | -0.024288 | 121.0482 | 121.0743 | 121.2251 | 120.9975 | -0.10883 | 121.0119 | 121.1105 | 121.0084 | 121.0056 | -0.18245
3516.7656 | 121.2845 | -121.0007 | 0.054932 | 1.4211e-13 | 0.024374 | 0.016133 | 0.0098956 | -0.023148 | 0.0050659 | 0.24021 | 0.024385 | 0.034604 | -0.096424 | -0.0022885 | 0.00085668 | 0.07888 | 0.0243 | 0.032795 | 0.07502 | 0.10567 | 0.24727 | -0.058478 | 0.078886 | 0.03241 | 0.003172 | 0.034145 | 0.12817 | 0.035222 | -0.12294 | 120.9422 | 0.020088 | 121.0796 | 121.0335 | 0.091273 | 0.050742 | 0.19234 | 120.8777 | -0.020787 | 121.0796 | 121.0038 | 0.12611 | 0.07324 | -0.01971 | 121.0757 | 121.1063 | 121.2479 | 121.025 | -0.11341 | 121.0348 | 121.1288 | 121.0359 | 121.0331 | -0.17787
3518.5625 | 121.2616 | -121.0236 | 0.082397 | 1.4211e-13 | 0.024587 | 0.016346 | 0.010109 | -0.023362 | 0.0050659 | 0.24021 | 0.024598 | 0.034604 | -0.096424 | -0.0025021 | 0.00085668 | 0.069723 | 0.019721 | 0.023639 | 0.07502 | 0.096516 | 0.25185 | -0.058478 | 0.083464 | 0.027831 | 0.003172 | 0.034145 | 0.12817 | 0.048958 | -0.12752 | 120.9651 | -0.007377 | 121.0933 | 121.0472 | 0.082117 | 0.014119 | 0.16946 | 120.896 | -0.048252 | 121.107 | 121.0267 | 0.13069 | 0.045775 | -0.033439 | 121.0986 | 121.1201 | 121.2754 | 121.0433 | -0.14088 | 121.0577 | 121.1517 | 121.0725 | 121.0514 | -0.20991
3520.3125 | 121.2753 | -121.0373 | 0.073242 | 1.4211e-13 | 0.024801 | 0.015705 | 0.0098956 | -0.023148 | 0.0050659 | 0.24021 | 0.024385 | 0.034818 | -0.09621 | -0.0027159 | 0.00042948 | 0.07888 | 0.0243 | 0.028217 | 0.065863 | 0.1011 | 0.26101 | -0.063057 | 0.074307 | 0.027831 | 0.003172 | 0.034145 | 0.13275 | 0.035222 | -0.12294 | 120.9742 | -0.007379 | 121.1162 | 121.0655 | 0.091274 | 0.027853 | 0.18777 | 120.9144 | -0.039097 | 121.1116 | 121.0405 | 0.12611 | 0.059508 | -0.03802 | 121.1032 | 121.1384 | 121.2983 | 121.0616 | -0.1363 | 121.0714 | 121.17 | 121.0725 | 121.0651 | -0.19618
3522.0469 | 120.9549 | -121.019 | 0.10529 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.023789 | 0.0044249 | 0.24021 | 0.025025 | 0.034604 | -0.096851 | -0.0022885 | 0.00042948 | 0.083459 | 0.019721 | 0.028217 | 0.070441 | 0.091937 | 0.24269 | -0.049321 | 0.078886 | 0.018674 | 0.003172 | 0.038723 | 0.12817 | 0.039801 | -0.12752 | 120.9697 | -0.034845 | 121.1024 | 121.0472 | 0.077538 | -0.013349 | 0.13741 | 120.8915 | -0.066563 | 121.0979 | 121.0222 | 0.13069 | 0.022886 | -0.065485 | 121.0894 | 121.1109 | 121.2617 | 121.0387 | -0.15461 | 121.0577 | 121.1472 | 121.0588 | 121.0377 | -0.2328
3523.8281 | 121.3348 | -121.0831 | 0.059509 | 1.4211e-13 | 0.025015 | 0.016133 | 0.010109 | -0.022935 | 0.0046387 | 0.22495 | 0.024598 | 0.034604 | -0.096424 | -0.0029295 | 0.00064308 | 0.083459 | 0.019721 | 0.028217 | 0.070441 | 0.096516 | 0.25185 | -0.058478 | 0.078886 | 0.027831 | 0.003172 | 0.029566 | 0.12817 | 0.035222 | -0.12752 | 121.0246 | 0.010932 | 121.1665 | 121.1113 | 0.086695 | 0.037007 | 0.19234 | 120.9556 | -0.029943 | 121.162 | 121.0862 | 0.13069 | 0.068663 | -0.024287 | 121.1535 | 121.1796 | 121.3349 | 121.1028 | -0.11799 | 121.1126 | 121.2112 | 121.1183 | 121.1109 | -0.18703
3525.625 | 120.8267 | -120.5978 | 0.082397 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.023362 | 0.0044249 | 0.24784 | 0.024598 | 0.034818 | -0.096851 | -0.0022885 | 0.00064308 | 0.07888 | 0.015142 | 0.028217 | 0.07502 | 0.1011 | 0.24727 | -0.053899 | 0.083464 | 0.027831 | -0.005985 | 0.029566 | 0.12359 | 0.035222 | -0.11836 | 120.5439 | -0.007377 | 120.6767 | 120.6261 | 0.082116 | 0.018698 | 0.16488 | 120.4795 | -0.052831 | 120.6813 | 120.5919 | 0.11238 | 0.041196 | -0.047175 | 120.6729 | 120.6989 | 120.8451 | 120.613 | -0.1363 | 120.6274 | 120.7214 | 120.6331 | 120.6257 | -0.20076
3527.4531 | 121.2891 | -121.1105 | 0.10071 | 1.4211e-13 | 0.024374 | 0.015919 | 0.009682 | -0.023576 | 0.0048523 | 0.24784 | 0.024385 | 0.03439 | -0.096637 | -0.0020749 | 0.00064308 | 0.074302 | 0.0243 | 0.023639 | 0.065863 | 0.087359 | 0.26101 | -0.058478 | 0.078886 | 0.03241 | 0.007751 | 0.034145 | 0.12817 | 0.030644 | -0.11836 | 121.0521 | -0.034845 | 121.1848 | 121.1342 | 0.082117 | -0.013349 | 0.1603 | 120.9922 | -0.066563 | 121.1894 | 121.1183 | 0.12611 | 0.027464 | -0.070064 | 121.1764 | 121.1979 | 121.3715 | 121.1348 | -0.15919 | 121.1447 | 121.2387 | 121.1412 | 121.1429 | -0.21907
3529.2344 | 121.2067 | -121.0922 | 0.10986 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.034604 | -0.09621 | -0.0025021 | 0.00042948 | 0.07888 | 0.019721 | 0.028217 | 0.070441 | 0.087359 | 0.25643 | -0.063057 | 0.083464 | 0.027831 | 0.007751 | 0.029566 | 0.12359 | 0.035222 | -0.11836 | 121.0292 | -0.039422 | 121.1711 | 121.1204 | 0.091274 | -0.022504 | 0.14657 | 120.9739 | -0.080297 | 121.1757 | 121.1 | 0.12611 | 0.01373 | -0.074641 | 121.1627 | 121.1796 | 121.3487 | 121.1119 | -0.17292 | 121.1218 | 121.2158 | 121.1274 | 121.1201 | -0.22822
3530.9844 | 121.3715 | -121.0876 | 0.07782 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.023362 | 0.0046387 | 0.23258 | 0.024812 | 0.03439 | -0.096424 | -0.0025021 | 0.00064308 | 0.074302 | 0.019721 | 0.037373 | 0.070441 | 0.1011 | 0.25643 | -0.040163 | 0.078886 | 0.03241 | 0.003172 | 0.024988 | 0.13733 | 0.026065 | -0.12752 | 121.0475 | -0.007379 | 121.1619 | 121.125 | 0.077536 | 0.023275 | 0.17861 | 120.9601 | -0.052832 | 121.1665 | 121.0908 | 0.13069 | 0.059509 | -0.051755 | 121.1581 | 121.1887 | 121.3441 | 121.1074 | -0.11798 | 121.1126 | 121.225 | 121.1137 | 121.1201 | -0.20534
3532.7812 | 121.4172 | -121.0602 | 0.068665 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.022935 | 0.0044249 | 0.24784 | 0.024171 | 0.034604 | -0.09621 | -0.0025021 | 0.00064308 | 0.07888 | 0.019721 | 0.032795 | 0.07502 | 0.096516 | 0.24727 | -0.053899 | 0.078886 | 0.027831 | -0.005985 | 0.029566 | 0.12359 | 0.030644 | -0.12294 | 121.0063 | 0.006355 | 121.1391 | 121.093 | 0.086694 | 0.027851 | 0.17861 | 120.9372 | -0.039099 | 121.1391 | 121.0542 | 0.11695 | 0.054928 | -0.038021 | 121.1352 | 121.1567 | 121.3075 | 121.0799 | -0.12256 | 121.0897 | 121.1838 | 121.0908 | 121.088 | -0.1916
3534.5781 | 121.4127 | -121.1334 | 0.082397 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.023148 | 0.0048523 | 0.23258 | 0.024812 | 0.03439 | -0.096637 | -0.0029295 | 0.00064308 | 0.074302 | 0.019721 | 0.028217 | 0.070441 | 0.091937 | 0.25185 | -0.067636 | 0.078886 | 0.027831 | 0.007751 | 0.038723 | 0.12817 | 0.030644 | -0.11836 | 121.0658 | -0.011956 | 121.2077 | 121.1616 | 0.095853 | 0.00954 | 0.16946 | 121.0151 | -0.043674 | 121.2123 | 121.1412 | 0.12611 | 0.045775 | -0.051753 | 121.2039 | 121.2254 | 121.3853 | 121.1531 | -0.15003 | 121.1721 | 121.2616 | 121.1641 | 121.1613 | -0.20076
3536.3594 | 121.4264 | -121.1243 | 0.064087 | 1.4211e-13 | 0.025015 | 0.015705 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0027159 | 0.00064308 | 0.083459 | 0.019721 | 0.028217 | 0.070441 | 0.096516 | 0.24269 | -0.063057 | 0.083464 | 0.027831 | 0.007751 | 0.034145 | 0.12359 | 0.030644 | -0.12294 | 121.0612 | 0.006354 | 121.2077 | 121.1525 | 0.091274 | 0.032429 | 0.17861 | 121.0013 | -0.029942 | 121.2077 | 121.132 | 0.13069 | 0.059506 | -0.033443 | 121.1947 | 121.2208 | 121.367 | 121.144 | -0.12714 | 121.1584 | 121.2479 | 121.1549 | 121.1521 | -0.18703
3538.0938 | 116.2445 | -77.2659 | 38.7039 | 1.4211e-13 | 0.02416 | 0.016133 | 0.0094682 | -0.022721 | 0.0039977 | 0.23258 | 0.024812 | 0.03439 | -0.096851 | -0.0025021 | 0.00064308 | 0.065145 | 0.005985 | 0.023639 | 0.070441 | 0.087359 | 0.24269 | -0.067636 | 0.069728 | 0.023253 | -0.001407 | 0.029566 | 0.12817 | 0.026065 | -0.1321 | 77.1983 | -38.6335 | 77.3311 | 77.2896 | 0.091275 | -38.6166 | -38.4612 | 77.1338 | -38.6744 | 77.3357 | 77.2645 | 0.13069 | -38.5757 | -38.6779 | 77.3364 | 77.3533 | 77.5086 | 77.2719 | -38.7716 | 77.2955 | 77.3941 | 77.292 | 77.2892 | -38.836
3539.875 | 121.1014 | -5.3329 | 114.6698 | 1.4211e-13 | 0.024587 | 0.015919 | 0.010109 | -0.023148 | 0.0046387 | 0.22495 | 0.024385 | 0.034818 | -0.096637 | -0.0027159 | 0.0010705 | 0.042253 | -0.026065 | -0.017566 | 0.033814 | 0.064464 | 0.20607 | -0.10427 | 0.046835 | 0.000359 | -0.038036 | -0.002483 | 0.086964 | -0.042614 | -0.15499 | 5.2287 | -114.636 | 5.3752 | 5.3154 | 0.086702 | -114.6053 | -114.4637 | 5.178 | -114.6723 | 5.3798 | 5.2949 | 0.11695 | -114.5828 | -114.7124 | 5.3668 | 5.3974 | 5.539 | 5.3069 | -114.7741 | 5.3305 | 5.4199 | 5.2903 | 5.3333 | -114.8248
3541.6094 | 121.0831 | -3.9597 | 116.3361 | 1.4211e-13 | 0.024587 | 0.015919 | 0.010109 | -0.023576 | 0.0044249 | 0.23258 | 0.025025 | 0.034604 | -0.096851 | -0.0025021 | 0.00085668 | 0.037675 | -0.026065 | -0.008409 | 0.038393 | 0.069043 | 0.20607 | -0.099689 | 0.037677 | -0.00422 | -0.038036 | -0.002483 | 0.091543 | -0.05635 | -0.16415 | 3.86 | -116.2977 | 3.9973 | 3.9512 | 0.09128 | -116.267 | -116.13 | 3.7955 | -116.3385 | 3.9973 | 3.9216 | 0.12611 | -116.2445 | -116.3924 | 3.998 | 4.0287 | 4.1657 | 3.9336 | -116.4357 | 3.9572 | 4.0512 | 3.9033 | 3.9554 | -116.5002
3543.4062 | 121.1792 | -4.0009 | 108.2565 | 1.4211e-13 | 0.024587 | 0.015919 | 0.010323 | -0.023148 | 0.0048523 | 0.24021 | 0.024812 | 0.03439 | -0.096424 | -0.0025021 | 0.00064308 | 0.042253 | -0.016908 | -0.008409 | 0.038393 | 0.064464 | 0.21522 | -0.099689 | 0.037677 | -0.013377 | -0.033458 | -0.007062 | 0.086964 | -0.042614 | -0.16873 | 3.9012 | -108.2181 | 4.0431 | 3.9924 | 0.09128 | -108.1921 | -108.0413 | 3.8321 | -108.2636 | 4.0385 | 3.9674 | 0.13527 | -108.1696 | -108.2991 | 4.0392 | 4.0653 | 4.2161 | 3.9839 | -108.3562 | 3.9938 | 4.0878 | 3.9582 | 3.9875 | -108.4253
3545.2031 | 120.8862 | -2.9755 | 111.3693 | 1.4211e-13 | 0.024374 | 0.015919 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024171 | 0.034604 | -0.096637 | -0.0027159 | 0.00085668 | 0.033096 | -0.021486 | -0.008409 | 0.038393 | 0.050727 | 0.2198 | -0.10427 | 0.042256 | -0.017956 | -0.033458 | -0.007062 | 0.086964 | -0.038035 | -0.16873 | 2.8712 | -111.3309 | 3.0086 | 2.9671 | 0.095859 | -111.3186 | -111.1495 | 2.8067 | -111.3764 | 3.0177 | 2.942 | 0.13527 | -111.2824 | -111.4074 | 3.0139 | 3.0262 | 3.1953 | 2.954 | -111.4736 | 2.9684 | 3.0624 | 2.9374 | 2.9575 | -111.5381
3546.9219 | 121.3211 | -3.7674 | 116.8304 | 1.4211e-13 | 0.024587 | 0.016133 | 0.0098956 | -0.023148 | 0.0046387 | 0.24784 | 0.024385 | 0.034604 | -0.09621 | -0.0025021 | 0.00064308 | 0.033096 | -0.026065 | -0.008409 | 0.033814 | 0.059885 | 0.20607 | -0.099689 | 0.037677 | -0.017956 | -0.038036 | -0.002483 | 0.086964 | -0.010564 | -0.16415 | 3.6677 | -116.7966 | 3.8005 | 3.759 | 0.09128 | -116.7706 | -116.6244 | 3.6032 | -116.8329 | 3.8051 | 3.7294 | 0.12611 | -116.7435 | -116.841 | 3.8012 | 3.8273 | 3.9735 | 3.7413 | -116.9301 | 3.7649 | 3.8544 | 3.7568 | 3.7494 | -116.9946
3548.7188 | 121.2341 | -4.129 | 117.0731 | 1.4211e-13 | 0.024587 | 0.016346 | 0.0098956 | -0.023148 | 0.0046387 | 0.23258 | 0.024598 | 0.034604 | -0.09621 | -0.0022885 | 0.00085668 | 0.037675 | -0.021486 | -0.008409 | 0.042971 | 0.059885 | 0.20607 | -0.099689 | 0.042256 | -0.008798 | -0.033458 | -0.002483 | 0.091543 | -0.070086 | -0.16873 | 4.0293 | -117.0301 | 4.1667 | 4.1206 | 0.09128 | -117.0132 | -116.867 | 3.9603 | -117.0755 | 4.1713 | 4.0956 | 0.13527 | -116.9815 | -117.1431 | 4.172 | 4.1889 | 4.3351 | 4.1075 | -117.1727 | 4.1265 | 4.2206 | 4.0589 | 4.1202 | -117.2418
3550.5156 | 102.5116 | -45.6619 | 75.4623 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010323 | -0.023148 | 0.0048523 | 0.23258 | 0.024598 | 0.034604 | -0.096851 | -0.0025021 | 0.00064308 | 0.055988 | -0.003172 | 0.009904 | 0.056706 | 0.073622 | 0.22896 | -0.072215 | 0.055992 | 0.014095 | -0.010564 | 0.011252 | 0.10528 | -0.0243 | -0.15041 | 45.5897 | -75.4056 | 45.7179 | 45.6718 | 0.082119 | -75.3887 | -75.2334 | 45.5115 | -75.4511 | 45.7179 | 45.6514 | 0.13985 | -75.3571 | -75.4866 | 45.7186 | 45.7355 | 45.8909 | 45.6588 | -75.5346 | 45.6732 | 45.7672 | 45.6376 | 45.676 | -75.6128
3552.25 | 120.9595 | -115.7822 | 4.7424 | 1.4211e-13 | 0.025015 | 0.015919 | 0.0098956 | -0.023362 | 0.0048523 | 0.24021 | 0.024812 | 0.034818 | -0.096424 | -0.0027159 | 0.00085668 | 0.069723 | 0.015142 | 0.023639 | 0.065863 | 0.087359 | 0.24727 | -0.063057 | 0.074307 | 0.023253 | 0.007751 | 0.029566 | 0.11901 | 0.026065 | -0.12752 | 115.7191 | -4.6766 | 115.8519 | 115.8058 | 0.086696 | -4.6551 | -4.4952 | 115.6546 | -4.7129 | 115.8565 | 115.7899 | 0.13527 | -4.6234 | -4.7164 | 115.848 | 115.8695 | 116.0294 | 115.7973 | -4.8055 | 115.8117 | 115.9012 | 115.8082 | 115.8054 | -4.87
3554.0469 | 121.2708 | -113.5941 | 7.251 | 1.4211e-13 | 0.024801 | 0.015919 | 0.0094682 | -0.023148 | 0.0050659 | 0.24021 | 0.024598 | 0.03439 | -0.096637 | -0.0022885 | 0.00064308 | 0.074302 | 0.015142 | 0.037373 | 0.07502 | 0.1011 | 0.25185 | -0.040163 | 0.078886 | 0.027831 | -0.001407 | 0.034145 | 0.12359 | 0.026065 | -0.12294 | 113.5539 | -7.176 | 113.6684 | 113.6314 | 0.077536 | -7.1499 | -6.9991 | 113.4711 | -7.2168 | 113.6729 | 113.5926 | 0.12153 | -7.1274 | -7.2249 | 113.6691 | 113.6951 | 113.8459 | 113.6092 | -7.2911 | 113.6282 | 113.7176 | 113.6201 | 113.6219 | -7.3739
3555.7656 | 121.3028 | -97.4167 | 23.2681 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.023148 | 0.0046387 | 0.24021 | 0.024385 | 0.03439 | -0.09621 | -0.0025021 | 0.00064308 | 0.065145 | 0.010564 | 0.028217 | 0.065863 | 0.087359 | 0.24269 | -0.058478 | 0.069728 | 0.018674 | -0.010564 | 0.020409 | 0.11901 | 0.021486 | -0.1321 | 97.3582 | -23.2023 | 97.4818 | 97.4449 | 0.086695 | -23.1808 | -23.0254 | 97.2846 | -23.2477 | 97.4864 | 97.4061 | 0.12153 | -23.1491 | -23.2466 | 97.4825 | 97.504 | 97.6594 | 97.4273 | -23.3266 | 97.4371 | 97.5357 | 97.4382 | 97.4354 | -23.4002
3557.5469 | 120.5429 | -115.3839 | 4.9072 | 1.4211e-13 | 0.024801 | 0.016346 | 0.010109 | -0.022935 | 0.0044249 | 0.24784 | 0.024171 | 0.034818 | -0.096637 | -0.0029295 | 0.00042948 | 0.07888 | 0.019721 | 0.028217 | 0.07502 | 0.091937 | 0.25185 | -0.067636 | 0.078886 | 0.027831 | -0.001407 | 0.029566 | 0.13275 | 0.035222 | -0.12752 | 115.3163 | -4.8322 | 115.4628 | 115.4121 | 0.095853 | -4.8153 | -4.6554 | 115.2564 | -4.8777 | 115.4628 | 115.3825 | 0.12611 | -4.7745 | -4.872 | 115.4589 | 115.4758 | 115.6358 | 115.4036 | -4.9749 | 115.4135 | 115.5167 | 115.4191 | 115.4117 | -5.0347
3559.3438 | 120.9229 | -115.3976 | 5.2551 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023148 | 0.0046387 | 0.24021 | 0.024598 | 0.034604 | -0.096424 | -0.0025021 | 0.0010705 | 0.074302 | 0.010564 | 0.032795 | 0.070441 | 0.096516 | 0.25185 | -0.063057 | 0.083464 | 0.03241 | 0.003172 | 0.024988 | 0.12817 | 0.039801 | -0.1321 | 115.3346 | -5.1847 | 115.4719 | 115.4304 | 0.095852 | -5.1586 | -5.0033 | 115.2655 | -5.2301 | 115.4811 | 115.4008 | 0.13527 | -5.127 | -5.2153 | 115.4681 | 115.4942 | 115.6495 | 115.4082 | -5.3182 | 115.4226 | 115.5258 | 115.4374 | 115.4301 | -5.3872
3561.125 | 121.0098 | -114.2807 | 6.2942 | 1.4211e-13 | 0.024801 | 0.015919 | 0.010109 | -0.023148 | 0.0044249 | 0.24021 | 0.024385 | 0.035031 | -0.096637 | -0.0027159 | 0.00042948 | 0.069723 | 0.015142 | 0.032795 | 0.070441 | 0.1011 | 0.24727 | -0.063057 | 0.083464 | 0.023253 | -0.001407 | 0.034145 | 0.12817 | 0.026065 | -0.12752 | 114.2176 | -6.2238 | 114.3504 | 114.3135 | 0.095852 | -6.1932 | -6.047 | 114.1532 | -6.2601 | 114.3642 | 114.2793 | 0.12611 | -6.1661 | -6.2682 | 114.3511 | 114.3818 | 114.528 | 114.2958 | -6.3573 | 114.3148 | 114.4089 | 114.3068 | 114.304 | -6.4218
3562.9062 | 120.9366 | -116.2903 | 4.5044 | 1.4211e-13 | 0.025228 | 0.016133 | 0.009682 | -0.023362 | 0.0046387 | 0.23258 | 0.024385 | 0.03439 | -0.09621 | -0.0020749 | 0.00064308 | 0.07888 | 0.019721 | 0.023639 | 0.07502 | 0.087359 | 0.25643 | -0.049321 | 0.074307 | 0.023253 | 0.007751 | 0.038723 | 0.13275 | 0.030644 | -0.12752 | 116.241 | -4.4294 | 116.3692 | 116.3139 | 0.07296 | -4.417 | -4.248 | 116.1628 | -4.4657 | 116.3646 | 116.298 | 0.13527 | -4.3716 | -4.4738 | 116.3653 | 116.3776 | 116.5467 | 116.31 | -4.5537 | 116.329 | 116.423 | 116.3209 | 116.3135 | -4.6319
3564.6406 | 121.019 | -118.4967 | 2.3666 | 1.4211e-13 | 0.025015 | 0.016346 | 0.010109 | -0.023148 | 0.0044249 | 0.24784 | 0.024598 | 0.034818 | -0.096424 | -0.0025021 | 0.00085668 | 0.07888 | 0.019721 | 0.028217 | 0.079598 | 0.1011 | 0.24727 | -0.053899 | 0.078886 | 0.03241 | 0.003172 | 0.029566 | 0.13275 | 0.039801 | -0.12294 | 118.4428 | -2.287 | 118.5756 | 118.5249 | 0.082116 | -2.2655 | -2.1194 | 118.3738 | -2.3371 | 118.5756 | 118.4999 | 0.12611 | -2.2339 | -2.3268 | 118.5763 | 118.5978 | 118.744 | 118.5164 | -2.4205 | 118.5263 | 118.6295 | 118.5365 | 118.5291 | -2.4896
3566.4531 | 121.1105 | -117.3889 | 3.3188 | 1.4211e-13 | 0.024587 | 0.016133 | 0.009682 | -0.023148 | 0.0048523 | 0.23258 | 0.024812 | 0.034818 | -0.096637 | -0.0029295 | 0.00042948 | 0.07888 | 0.019721 | 0.023639 | 0.07502 | 0.096516 | 0.25185 | -0.053899 | 0.074307 | 0.03241 | 0.003172 | 0.038723 | 0.13275 | 0.030644 | -0.12752 | 117.335 | -3.2438 | 117.4678 | 117.4126 | 0.077538 | -3.2223 | -3.0669 | 117.2614 | -3.2801 | 117.4632 | 117.3921 | 0.13069 | -3.186 | -3.2881 | 117.4639 | 117.4854 | 117.6408 | 117.4086 | -3.3727 | 117.4276 | 117.5217 | 117.4196 | 117.4213 | -3.4463
3568.25 | 121.1288 | -114.7751 | 6.0379 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023362 | 0.0048523 | 0.24021 | 0.024385 | 0.034604 | -0.096424 | -0.0025021 | 0.0010705 | 0.07888 | 0.015142 | 0.023639 | 0.07502 | 0.096516 | 0.24727 | -0.058478 | 0.074307 | 0.027831 | -0.005985 | 0.034145 | 0.13733 | 0.021486 | -0.1321 | 114.7166 | -5.9629 | 114.854 | 114.7987 | 0.082117 | -5.9414 | -5.7906 | 114.643 | -6.0038 | 114.8494 | 114.7691 | 0.12611 | -5.9006 | -6.0164 | 114.8501 | 114.8716 | 115.0224 | 114.7902 | -6.0964 | 114.8092 | 114.9124 | 114.7966 | 114.8029 | -6.17
3570.0469 | 120.9961 | -114.4226 | 6.3538 | 1.4211e-13 | 0.025228 | 0.016346 | 0.010109 | -0.023362 | 0.0044249 | 0.24021 | 0.024385 | 0.03439 | -0.096424 | -0.0022885 | 0.00085668 | 0.074302 | 0.019721 | 0.028217 | 0.070441 | 0.1011 | 0.24727 | -0.063057 | 0.078886 | 0.027831 | 0.003172 | 0.029566 | 0.12817 | 0.030644 | -0.12752 | 114.3595 | -6.2833 | 114.4969 | 114.4508 | 0.091274 | -6.2527 | -6.1065 | 114.2951 | -6.3242 | 114.5015 | 114.4258 | 0.13069 | -6.2256 | -6.3231 | 114.493 | 114.5237 | 114.6699 | 114.4423 | -6.4168 | 114.4522 | 114.5508 | 114.4533 | 114.4504 | -6.4813
3571.8281 | 121.0052 | -116.5878 | 4.3121 | 1.4211e-13 | 0.025015 | 0.016346 | 0.010109 | -0.022721 | 0.0046387 | 0.24784 | 0.024598 | 0.033963 | -0.096424 | -0.0022885 | 0.00042948 | 0.07888 | 0.019721 | 0.023639 | 0.07502 | 0.1011 | 0.25185 | -0.058478 | 0.074307 | 0.023253 | -0.001407 | 0.029566 | 0.12817 | 0.030644 | -0.12752 | 116.5294 | -4.2371 | 116.6667 | 116.6115 | 0.082117 | -4.211 | -4.0603 | 116.4603 | -4.2826 | 116.6621 | 116.5864 | 0.12611 | -4.184 | -4.2815 | 116.6628 | 116.6889 | 116.8397 | 116.6076 | -4.3706 | 116.6174 | 116.716 | 116.6185 | 116.6111 | -4.4397
3573.625 | 121.0281 | -117.6682 | 3.2593 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.23258 | 0.024812 | 0.034177 | -0.096637 | -0.0025021 | 0.00085668 | 0.074302 | 0.015142 | 0.028217 | 0.07502 | 0.1011 | 0.25185 | -0.053899 | 0.074307 | 0.036989 | -0.001407 | 0.029566 | 0.12817 | 0.030644 | -0.12294 | 117.6143 | -3.1843 | 117.7425 | 117.6964 | 0.082116 | -3.1582 | -3.0074 | 117.5452 | -3.2297 | 117.7425 | 117.6667 | 0.12153 | -3.1311 | -3.2286 | 117.7432 | 117.7692 | 117.92 | 117.6833 | -3.3132 | 117.6977 | 117.7963 | 117.6988 | 117.7051 | -3.3822
3575.375 | 121.0602 | -116.6519 | 4.2892 | 1.4211e-13 | 0.024374 | 0.016346 | 0.010109 | -0.023362 | 0.0046387 | 0.23258 | 0.024598 | 0.034177 | -0.096424 | -0.0027159 | 0.00085668 | 0.074302 | 0.0243 | 0.01906 | 0.07502 | 0.096516 | 0.25185 | -0.063057 | 0.078886 | 0.027831 | -0.001407 | 0.029566 | 0.12817 | 0.039801 | -0.12752 | 116.5889 | -4.2142 | 116.7262 | 116.671 | 0.082117 | -4.1927 | -4.0374 | 116.5244 | -4.2597 | 116.7308 | 116.6505 | 0.12611 | -4.1611 | -4.2494 | 116.7269 | 116.7484 | 116.9038 | 116.6762 | -4.3523 | 116.6815 | 116.7801 | 116.6917 | 116.6797 | -4.4168
3577.1719 | 121.1334 | -117.7231 | 3.1357 | 1.4211e-13 | 0.024587 | 0.015919 | 0.009682 | -0.023576 | 0.0048523 | 0.23258 | 0.024598 | 0.034604 | -0.09621 | -0.0027159 | 0.00064308 | 0.07888 | 0.010564 | 0.01906 | 0.07502 | 0.091937 | 0.25643 | -0.044742 | 0.074307 | 0.027831 | 0.003172 | 0.034145 | 0.13733 | 0.026065 | -0.12752 | 117.6783 | -3.0607 | 117.802 | 117.7421 | 0.063802 | -3.0437 | -2.8792 | 117.5956 | -3.1015 | 117.7974 | 117.7263 | 0.13069 | -2.9984 | -3.1096 | 117.7981 | 117.815 | 117.9795 | 117.7336 | -3.1804 | 117.7572 | 117.8604 | 117.7491 | 117.7509 | -3.2632
3578.9062 | 121.1014 | -115.416 | 5.4474 | 1.4211e-13 | 0.024587 | 0.016133 | 0.009682 | -0.023148 | 0.0048523 | 0.23258 | 0.024598 | 0.03439 | -0.096424 | -0.0027159 | 0.00064308 | 0.074302 | 0.019721 | 0.01906 | 0.070441 | 0.1011 | 0.24269 | -0.067636 | 0.074307 | 0.027831 | 0.003172 | 0.024988 | 0.12359 | 0.026065 | -0.12294 | 115.3483 | -5.3769 | 115.4903 | 115.435 | 0.086696 | -5.3463 | -5.2047 | 115.293 | -5.4224 | 115.4903 | 115.4191 | 0.12611 | -5.3238 | -5.4213 | 115.4864 | 115.517 | 115.6586 | 115.4357 | -5.515 | 115.4409 | 115.5395 | 115.442 | 115.4438 | -5.5703
3580.7031 | 121.1243 | -117.9108 | 2.9617 | 1.4211e-13 | 0.025228 | 0.016346 | 0.009682 | -0.023362 | 0.0046387 | 0.23258 | 0.024598 | 0.03439 | -0.096424 | -0.0025021 | 0.00085668 | 0.07888 | 0.0243 | 0.023639 | 0.07502 | 0.096516 | 0.24727 | -0.063057 | 0.074307 | 0.023253 | 0.003172 | 0.029566 | 0.12817 | 0.026065 | -0.12752 | 117.8477 | -2.8867 | 117.9896 | 117.9344 | 0.086696 | -2.8652 | -2.7145 | 117.7832 | -2.9322 | 117.9851 | 117.9139 | 0.13069 | -2.8336 | -2.9357 | 117.9858 | 118.0073 | 118.158 | 117.9351 | -3.0248 | 117.9403 | 118.0389 | 117.9368 | 117.934 | -3.0892
3582.5156 | 121.2799 | -116.4368 | 4.4312 | 1.4211e-13 | 0.024801 | 0.016346 | 0.009682 | -0.023148 | 0.0048523 | 0.24021 | 0.024598 | 0.03439 | -0.095996 | -0.0029295 | 0.00085668 | 0.07888 | 0.019721 | 0.028217 | 0.070441 | 0.1011 | 0.25185 | -0.063057 | 0.083464 | 0.023253 | 0.003172 | 0.024988 | 0.12359 | 0.030644 | -0.12294 | 116.3737 | -4.3607 | 116.5156 | 116.465 | 0.091274 | -4.3301 | -4.1793 | 116.3138 | -4.4062 | 116.5202 | 116.4399 | 0.12611 | -4.3076 | -4.4005 | 116.5072 | 116.5379 | 116.6886 | 116.4565 | -4.4942 | 116.4618 | 116.5604 | 116.4674 | 116.46 | -4.5541
3584.2656 | 121.3486 | -120.1675 | 0.80109 | 1.4211e-13 | 0.024587 | 0.016133 | 0.010109 | -0.022935 | 0.0046387 | 0.23258 | 0.024812 | 0.03439 | -0.096424 | -0.0025021 | 0.00021588 | 0.07888 | 0.0243 | 0.028217 | 0.070441 | 0.091937 | 0.24727 | -0.063057 | 0.078886 | 0.023253 | 0.003172 | 0.034145 | 0.13275 | 0.030644 | -0.1321 | 120.1045 | -0.73064 | 120.2464 | 120.1958 | 0.091274 | -0.70915 | -0.55381 | 120.0354 | -0.76694 | 120.2464 | 120.1707 | 0.13527 | -0.66834 | -0.77044 | 120.238 | 120.2595 | 120.4148 | 120.1918 | -0.86414 | 120.2017 | 120.3003 | 120.1982 | 120.1908 | -0.93318
3586.0625 | 121.1838 | -120.1355 | 0.96588 | 1.4211e-13 | 0.025015 | 0.016133 | 0.010109 | -0.023148 | 0.0046387 | 0.24784 | 0.024598 | 0.034604 | -0.096851 | -0.0022885 | 0.00085668 | 0.083459 | 0.019721 | 0.028217 | 0.070441 | 0.10567 | 0.25643 | -0.049321 | 0.083464 | 0.027831 | 0.007751 | 0.029566 | 0.13275 | 0.039801 | -0.12752 | 120.0862 | -0.89544 | 120.219 | 120.1637 | 0.077538 | -0.86021 | -0.70945 | 120.008 | -0.93632 | 120.219 | 120.1432 | 0.13527 | -0.83313 | -0.92608 | 120.2059 | 120.2412 | 120.3919 | 120.1552 | -1.0152 | 120.1651 | 120.2682 | 120.1753 | 120.1633 | -1.0934
3587.7812 | 121.3257 | -120.3094 | 0.7782 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023148 | 0.0046387 | 0.23258 | 0.024598 | 0.035031 | -0.095996 | -0.0027159 | 0.00042948 | 0.07888 | 0.0243 | 0.028217 | 0.070441 | 0.1011 | 0.24727 | -0.053899 | 0.078886 | 0.03241 | 0.003172 | 0.034145 | 0.12359 | 0.035222 | -0.1321 | 120.2555 | -0.70776 | 120.3883 | 120.3377 | 0.082116 | -0.6771 | -0.53092 | 120.1774 | -0.74405 | 120.3883 | 120.3126 | 0.13527 | -0.6546 | -0.74298 | 120.3799 | 120.4105 | 120.5567 | 120.3337 | -0.8321 | 120.3436 | 120.433 | 120.3447 | 120.3419 | -0.91029
3589.5938 | 121.2433 | -119.4489 | 1.6663 | 1.4211e-13 | 0.025015 | 0.01656 | 0.010109 | -0.023148 | 0.0044249 | 0.22495 | 0.024812 | 0.034818 | -0.096424 | -0.0027159 | 0.00042948 | 0.088037 | 0.019721 | 0.032795 | 0.07502 | 0.091937 | 0.24727 | -0.053899 | 0.078886 | 0.03241 | -0.005985 | 0.029566 | 0.12817 | 0.030644 | -0.12294 | 119.395 | -1.5912 | 119.5369 | 119.4816 | 0.086694 | -1.5743 | -1.419 | 119.3259 | -1.6367 | 119.5277 | 119.4429 | 0.11695 | -1.5381 | -1.6356 | 119.5239 | 119.5408 | 119.6961 | 119.4686 | -1.7202 | 119.4784 | 119.577 | 119.4795 | 119.4813 | -1.7892
3591.3438 | 121.3486 | -120.5887 | 0.52185 | 1.4211e-13 | 0.024587 | 0.016133 | 0.010109 | -0.023362 | 0.0046387 | 0.24021 | 0.024385 | 0.034604 | -0.09621 | -0.0025021 | 0.00085668 | 0.07888 | 0.015142 | 0.028217 | 0.070441 | 0.091937 | 0.24727 | -0.076794 | 0.078886 | 0.027831 | 0.003172 | 0.034145 | 0.13275 | 0.026065 | -0.12294 | 120.5119 | -0.45141 | 120.6676 | 120.6169 | 0.10501 | -0.42991 | -0.27458 | 120.4657 | -0.48771 | 120.6676 | 120.5919 | 0.12611 | -0.3891 | -0.49579 | 120.6591 | 120.6806 | 120.836 | 120.6038 | -0.59864 | 120.6228 | 120.7214 | 120.6147 | 120.6165 | -0.64479
3593.1406 | 121.2982 | -120.2179 | 0.86975 | 1.4211e-13 | 0.025015 | 0.016133 | 0.0098956 | -0.023148 | 0.0046387 | 0.24784 | 0.024598 | 0.034818 | -0.096637 | -0.0022885 | 0.00042948 | 0.07888 | 0.015142 | 0.028217 | 0.065863 | 0.096516 | 0.24727 | -0.063057 | 0.083464 | 0.027831 | 0.003172 | 0.029566 | 0.11901 | 0.035222 | -0.12294 | 120.1548 | -0.80389 | 120.2968 | 120.2461 | 0.091274 | -0.77324 | -0.62248 | 120.095 | -0.84019 | 120.3014 | 120.2211 | 0.12611 | -0.75074 | -0.83453 | 120.2838 | 120.3144 | 120.4652 | 120.233 | -0.93281 | 120.2475 | 120.3369 | 120.2531 | 120.2457 | -0.99269
3594.9531 | 121.2524 | -120.7489 | 0.40283 | 1.4211e-13 | 0.025015 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.23258 | 0.024598 | 0.03439 | -0.09621 | -0.0025021 | 0.00064308 | 0.074302 | 0.0243 | 0.023639 | 0.07502 | 0.096516 | 0.24727 | -0.053899 | 0.083464 | 0.027831 | 0.003172 | 0.029566 | 0.12817 | 0.035222 | -0.12752 | 120.695 | -0.32781 | 120.8232 | 120.7725 | 0.077538 | -0.30632 | -0.15556 | 120.6214 | -0.37327 | 120.8324 | 120.7521 | 0.13069 | -0.27466 | -0.36761 | 120.8239 | 120.8454 | 120.9962 | 120.7732 | -0.45673 | 120.7785 | 120.8771 | 120.7841 | 120.7767 | -0.53035
3596.7344 | 121.3394 | -120.7443 | 0.4303 | 1.4211e-13 | 0.024374 | 0.015919 | 0.009682 | -0.023576 | 0.0046387 | 0.24021 | 0.024598 | 0.03439 | -0.09621 | -0.0027159 | 0.00085668 | 0.083459 | 0.019721 | 0.023639 | 0.070441 | 0.1011 | 0.25185 | -0.067636 | 0.078886 | 0.027831 | 0.003172 | 0.038723 | 0.13275 | 0.026065 | -0.12294 | 120.6767 | -0.35986 | 120.8278 | 120.768 | 0.091275 | -0.3292 | -0.17845 | 120.6214 | -0.39158 | 120.8232 | 120.7475 | 0.12611 | -0.29755 | -0.40423 | 120.8148 | 120.8454 | 120.9962 | 120.764 | -0.49793 | 120.783 | 120.8771 | 120.7704 | 120.7722 | -0.55324
3598.4688 | 121.3806 | -120.6848 | 0.47607 | 1.4211e-13 | 0.024801 | 0.016346 | 0.009682 | -0.023362 | 0.0048523 | 0.23258 | 0.024598 | 0.034604 | -0.096424 | -0.0022885 | 0.00064308 | 0.074302 | 0.019721 | 0.023639 | 0.070441 | 0.1011 | 0.25185 | -0.063057 | 0.083464 | 0.03241 | 0.007751 | 0.034145 | 0.12359 | 0.030644 | -0.12294 | 120.6218 | -0.40563 | 120.7591 | 120.7085 | 0.086696 | -0.37498 | -0.22422 | 120.5619 | -0.44193 | 120.7683 | 120.6926 | 0.13069 | -0.35248 | -0.44543 | 120.7553 | 120.7859 | 120.9367 | 120.7045 | -0.53913 | 120.719 | 120.8084 | 120.7155 | 120.7172 | -0.59901
3600.2656 | 121.2982 | -118.0847 | 3.1082 | 1.4211e-13 | 0.024587 | 0.016346 | 0.009682 | -0.023148 | 0.0048523 | 0.23258 | 0.024812 | 0.034604 | -0.096424 | -0.0025021 | 0.00085668 | 0.07888 | 0.010564 | 0.032795 | 0.070441 | 0.1011 | 0.24727 | -0.063057 | 0.074307 | 0.018674 | 0.007751 | 0.034145 | 0.12817 | 0.026065 | -0.12752 | 118.0217 | -3.0378 | 118.1636 | 118.1175 | 0.095852 | -3.0071 | -2.8609 | 117.9572 | -3.0741 | 118.159 | 118.0925 | 0.13527 | -2.98 | -3.0821 | 118.1552 | 118.1858 | 118.332 | 118.0953 | -3.1713 | 118.1189 | 118.2129 | 118.1108 | 118.1034 | -3.2357
3602.0625 | 121.3852 | -120.7809 | 0.37994 | 1.4211e-13 | 0.025015 | 0.016346 | 0.0098956 | -0.023362 | 0.0050659 | 0.25547 | 0.024598 | 0.034604 | -0.096851 | -0.0025021 | 0.00085668 | 0.083459 | 0.015142 | 0.023639 | 0.07502 | 0.1011 | 0.24269 | -0.058478 | 0.078886 | 0.027831 | 0.007751 | 0.029566 | 0.13733 | 0.026065 | -0.12294 | 120.7225 | -0.30492 | 120.8644 | 120.8046 | 0.082117 | -0.27885 | -0.13725 | 120.658 | -0.35038 | 120.8598 | 120.7887 | 0.13069 | -0.24261 | -0.35388 | 120.856 | 120.882 | 121.0236 | 120.7961 | -0.43842 | 120.8105 | 120.9183 | 120.807 | 120.8088 | -0.50288
3603.7812 | 121.3943 | -120.7352 | 0.39368 | 1.4211e-13 | 0.025228 | 0.016133 | 0.009682 | -0.023576 | 0.0050659 | 0.24021 | 0.024812 | 0.034818 | -0.096851 | -0.0025021 | 0.00085668 | 0.069723 | 0.015142 | 0.028217 | 0.07502 | 0.096516 | 0.24727 | -0.063057 | 0.083464 | 0.03241 | 0.01233 | 0.034145 | 0.12817 | 0.026065 | -0.12294 | 120.6721 | -0.31866 | 120.8049 | 120.7634 | 0.091274 | -0.29716 | -0.1464 | 120.6122 | -0.35953 | 120.8186 | 120.7475 | 0.13527 | -0.2655 | -0.36761 | 120.8102 | 120.8317 | 120.9824 | 120.7503 | -0.45673 | 120.7693 | 120.8633 | 120.7612 | 120.7676 | -0.51662
3605.5781 | 119.87 | -116.629 | 2.8839 | 1.4211e-13 | 0.024801 | 0.016133 | 0.009682 | -0.022935 | 0.0046387 | 0.23258 | 0.024598 | 0.034604 | -0.096424 | -0.0022885 | 0.00085668 | 0.069723 | 0.010564 | 0.01906 | 0.061284 | 0.091937 | 0.24269 | -0.063057 | 0.074307 | 0.023253 | -0.001407 | 0.029566 | 0.11901 | 0.026065 | -0.1321 | 116.566 | -2.8226 | 116.6988 | 116.6481 | 0.082117 | -2.792 | -2.6412 | 116.4969 | -2.8543 | 116.7033 | 116.6276 | 0.13069 | -2.7649 | -2.8578 | 116.6903 | 116.721 | 116.8717 | 116.6396 | -2.947 | 116.6586 | 116.748 | 116.6551 | 116.6523 | -3.016
3607.3906 | 120.8496 | -119.3527 | 1.2222 | 1.4211e-13 | 0.025228 | 0.016346 | 0.010109 | -0.023362 | 0.0044249 | 0.24784 | 0.024385 | 0.034604 | -0.096424 | -0.0025021 | 0.00064308 | 0.07888 | 0.019721 | 0.028217 | 0.070441 | 0.096516 | 0.25643 | -0.049321 | 0.078886 | 0.027831 | 0.007751 | 0.034145 | 0.12359 | 0.030644 | -0.12294 | 119.3034 | -1.1518 | 119.4316 | 119.3809 | 0.077538 | -1.1257 | -0.9658 | 119.2298 | -1.1881 | 119.4316 | 119.3605 | 0.13069 | -1.0986 | -1.1916 | 119.4232 | 119.4492 | 119.6092 | 119.3724 | -1.2715 | 119.3869 | 119.4763 | 119.3834 | 119.3806 | -1.3452
3609.1719 | 121.0327 | -119.7144 | 0.96588 | 1.4211e-13 | 0.025015 | 0.016346 | 0.0098956 | -0.023362 | 0.0052797 | 0.24021 | 0.024385 | 0.034604 | -0.096424 | -0.0025021 | 0.00085668 | 0.07888 | 0.015142 | 0.014482 | 0.070441 | 0.087359 | 0.25185 | -0.044742 | 0.083464 | 0.023253 | 0.007751 | 0.038723 | 0.12359 | 0.030644 | -0.12752 | 119.6696 | -0.89544 | 119.7932 | 119.7288 | 0.059224 | -0.87852 | -0.71403 | 119.5868 | -0.92716 | 119.7978 | 119.7221 | 0.13527 | -0.84229 | -0.93524 | 119.7848 | 119.8017 | 119.9662 | 119.7295 | -1.0106 | 119.7531 | 119.8379 | 119.745 | 119.7376 | -1.0934
3610.9688 | 120.9686 | -120.195 | 0.6546 | 1.4211e-13 | 0.024801 | 0.01656 | 0.0094682 | -0.023362 | 0.0044249 | 0.24021 | 0.024598 | 0.034604 | -0.096637 | -0.0022885 | 0.00085668 | 0.074302 | 0.015142 | 0.023639 | 0.065863 | 0.1011 | 0.24727 | -0.058478 | 0.074307 | 0.03241 | 0.003172 | 0.029566 | 0.11901 | 0.030644 | -0.12294 | 120.1365 | -0.58874 | 120.2693 | 120.2186 | 0.082117 | -0.55351 | -0.40733 | 120.0721 | -0.62504 | 120.2693 | 120.1982 | 0.12611 | -0.53559 | -0.62396 | 120.2609 | 120.2961 | 120.4423 | 120.2101 | -0.71308 | 120.2246 | 120.314 | 120.2257 | 120.2274 | -0.77754
3612.75 | 121.019 | -120.314 | 0.5722 | 1.4211e-13 | 0.024587 | 0.016133 | 0.010323 | -0.023362 | 0.0044249 | 0.24021 | 0.024171 | 0.034604 | -0.097065 | -0.0025021 | 0.00085668 | 0.07888 | 0.015142 | 0.032795 | 0.065863 | 0.1011 | 0.25185 | -0.063057 | 0.083464 | 0.036989 | 0.003172 | 0.034145 | 0.11901 | 0.026065 | -0.12294 | 120.251 | -0.50634 | 120.3929 | 120.3468 | 0.095852 | -0.47111 | -0.32035 | 120.1911 | -0.53806 | 120.3975 | 120.3172 | 0.12611 | -0.45319 | -0.54614 | 120.3799 | 120.4151 | 120.5659 | 120.3292 | -0.63526 | 120.3482 | 120.433 | 120.3401 | 120.351 | -0.69514
3614.5469 | 121.0556 | -120.488 | 0.46234 | 1.4211e-13 | 0.024801 | 0.016133 | 0.009682 | -0.023362 | 0.0048523 | 0.24784 | 0.024812 | 0.034604 | -0.096637 | -0.0020749 | 0.00042948 | 0.07888 | 0.0243 | 0.023639 | 0.070441 | 0.091937 | 0.25185 | -0.053899 | 0.078886 | 0.023253 | 0.007751 | 0.034145 | 0.12817 | 0.035222 | -0.12752 | 120.4341 | -0.3919 | 120.5669 | 120.5116 | 0.077538 | -0.3704 | -0.21049 | 120.3605 | -0.4282 | 120.5669 | 120.4957 | 0.13527 | -0.33417 | -0.42712 | 120.5584 | 120.5799 | 120.7398 | 120.5123 | -0.51624 | 120.5221 | 120.6161 | 120.5232 | 120.5112 | -0.58986
3616.2812 | 121.1609 | -120.4147 | 0.49439 | 1.4211e-13 | 0.025015 | 0.016133 | 0.009682 | -0.023362 | 0.0046387 | 0.22495 | 0.024385 | 0.034604 | -0.096424 | -0.0025021 | 0.00064308 | 0.07888 | 0.0243 | 0.023639 | 0.07502 | 0.096516 | 0.24727 | -0.058478 | 0.083464 | 0.023253 | -0.001407 | 0.029566 | 0.12359 | 0.026065 | -0.11836 | 120.3563 | -0.41936 | 120.4936 | 120.4384 | 0.082117 | -0.39787 | -0.24711 | 120.2964 | -0.46482 | 120.4982 | 120.4133 | 0.11695 | -0.37079 | -0.46832 | 120.4898 | 120.5112 | 120.662 | 120.439 | -0.55286 | 120.4443 | 120.5383 | 120.4408 | 120.438 | -0.61275
3618.0781 | 121.1792 | -120.4926 | 0.43945 | 1.4211e-13 | 0.024587 | 0.016133 | 0.0098956 | -0.022935 | 0.0050659 | 0.23258 | 0.024812 | 0.034604 | -0.096637 | -0.0025021 | 0.00085668 | 0.083459 | 0.019721 | 0.032795 | 0.07502 | 0.091937 | 0.25185 | -0.067636 | 0.078886 | 0.036989 | 0.007751 | 0.034145 | 0.12817 | 0.039801 | -0.12294 | 120.4249 | -0.36443 | 120.576 | 120.5253 | 0.10043 | -0.34752 | -0.1876 | 120.3696 | -0.40531 | 120.5714 | 120.5003 | 0.13069 | -0.31128 | -0.39965 | 120.5676 | 120.5845 | 120.7444 | 120.5123 | -0.50709 | 120.5267 | 120.6207 | 120.5324 | 120.5295 | -0.56239
3619.875 | 121.1609 | -120.5246 | 0.43945 | 1.4211e-13 | 0.024801 | 0.016133 | 0.009682 | -0.022935 | 0.0048523 | 0.23258 | 0.024598 | 0.034818 | -0.096424 | -0.0022885 | 0.00064308 | 0.074302 | 0.015142 | 0.028217 | 0.079598 | 0.096516 | 0.24727 | -0.067636 | 0.078886 | 0.027831 | -0.001407 | 0.029566 | 0.12359 | 0.030644 | -0.12294 | 120.457 | -0.35985 | 120.5989 | 120.5528 | 0.095853 | -0.34294 | -0.19218 | 120.4017 | -0.40989 | 120.6035 | 120.5232 | 0.12153 | -0.31586 | -0.40881 | 120.6042 | 120.6211 | 120.7719 | 120.5397 | -0.50709 | 120.5542 | 120.6482 | 120.5552 | 120.5524 | -0.56239
3621.6562 | 121.2021 | -120.5246 | 0.45319 | 1.4211e-13 | 0.025015 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.23258 | 0.024385 | 0.034604 | -0.096424 | -0.0027159 | 0.00085668 | 0.083459 | 0.019721 | 0.032795 | 0.07502 | 0.091937 | 0.24269 | -0.040163 | 0.074307 | 0.027831 | 0.007751 | 0.029566 | 0.12359 | 0.026065 | -0.12752 | 120.4844 | -0.37817 | 120.6081 | 120.5574 | 0.072958 | -0.36125 | -0.21049 | 120.3971 | -0.42362 | 120.5989 | 120.5323 | 0.13527 | -0.32959 | -0.42712 | 120.5996 | 120.6165 | 120.7673 | 120.5443 | -0.49335 | 120.5542 | 120.6482 | 120.5507 | 120.5524 | -0.5807
3623.4531 | 121.1746 | -120.7397 | 0.29297 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.022935 | 0.0046387 | 0.23258 | 0.024598 | 0.034818 | -0.096637 | -0.0025021 | 0.00064308 | 0.074302 | 0.019721 | 0.01906 | 0.079598 | 0.096516 | 0.25643 | -0.058478 | 0.074307 | 0.023253 | 0.01233 | 0.04788 | 0.12359 | 0.030644 | -0.12294 | 120.6813 | -0.21337 | 120.814 | 120.7588 | 0.077538 | -0.19645 | -0.036538 | 120.6168 | -0.24509 | 120.8141 | 120.7521 | 0.13527 | -0.16938 | -0.26232 | 120.8193 | 120.8363 | 120.9962 | 120.7595 | -0.35145 | 120.7876 | 120.8633 | 120.7704 | 120.763 | -0.41591
3625.1875 | 121.1792 | -120.7535 | 0.3067 | 1.4211e-13 | 0.025015 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.25547 | 0.024598 | 0.034818 | -0.096637 | -0.0022885 | 0.00042948 | 0.07888 | 0.0243 | 0.023639 | 0.07502 | 0.1011 | 0.25185 | -0.063057 | 0.069728 | 0.027831 | 0.007751 | 0.043302 | 0.12359 | 0.030644 | -0.12294 | 120.6904 | -0.23168 | 120.8324 | 120.7771 | 0.086696 | -0.20561 | -0.05485 | 120.6305 | -0.2634 | 120.8232 | 120.7612 | 0.13069 | -0.18311 | -0.27606 | 120.8285 | 120.8546 | 121.0053 | 120.7778 | -0.36976 | 120.7968 | 120.8771 | 120.7841 | 120.7813 | -0.42964
3626.9688 | 121.1792 | -120.6253 | 0.44403 | 1.4211e-13 | 0.025015 | 0.015919 | 0.009682 | -0.023148 | 0.0046387 | 0.24021 | 0.024598 | 0.034818 | -0.096851 | -0.0029295 | 0.00064308 | 0.07888 | 0.019721 | 0.028217 | 0.065863 | 0.1011 | 0.25185 | -0.067636 | 0.078886 | 0.03241 | 0.007751 | 0.043302 | 0.12359 | 0.035222 | -0.12752 | 120.5577 | -0.37817 | 120.7042 | 120.6535 | 0.095853 | -0.34294 | -0.19218 | 120.4978 | -0.40073 | 120.7042 | 120.6331 | 0.13527 | -0.32044 | -0.40881 | 120.6912 | 120.7264 | 120.8772 | 120.645 | -0.51167 | 120.6686 | 120.7489 | 120.6605 | 120.6577 | -0.57155
3628.75 | 121.2982 | -120.7077 | 0.34332 | 1.4211e-13 | 0.025015 | 0.016346 | 0.010109 | -0.023148 | 0.0046387 | 0.24784 | 0.024171 | 0.034818 | -0.096637 | -0.0025021 | 0.00064308 | 0.083459 | 0.015142 | 0.023639 | 0.079598 | 0.096516 | 0.24727 | -0.049321 | 0.069728 | 0.03241 | 0.003172 | 0.043302 | 0.12359 | 0.035222 | -0.12752 | 120.6584 | -0.26372 | 120.7912 | 120.7313 | 0.07296 | -0.24681 | -0.096049 | 120.5802 | -0.30002 | 120.7774 | 120.7109 | 0.13069 | -0.21973 | -0.3081 | 120.7873 | 120.8042 | 120.955 | 120.7228 | -0.39264 | 120.751 | 120.8313 | 120.7429 | 120.7401 | -0.47084
3630.4844 | 121.2662 | -120.7306 | 0.39368 | 1.4211e-13 | 0.025015 | 0.016133 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024598 | 0.034604 | -0.096851 | -0.0025021 | 0.00085668 | 0.083459 | 0.019721 | 0.023639 | 0.070441 | 0.096516 | 0.24727 | -0.058478 | 0.083464 | 0.03241 | 0.007751 | 0.038723 | 0.12359 | 0.021486 | -0.11836 | 120.6721 | -0.32324 | 120.8141 | 120.7542 | 0.082117 | -0.29716 | -0.1464 | 120.6122 | -0.35495 | 120.8141 | 120.7383 | 0.12611 | -0.27008 | -0.37219 | 120.801 | 120.8271 | 120.9779 | 120.7503 | -0.45215 | 120.7693 | 120.8542 | 120.7521 | 120.763 | -0.51204
3632.2812 | 121.2936 | -120.7947 | 0.29755 | 1.4211e-13 | 0.024801 | 0.01656 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.025239 | 0.034604 | -0.096851 | -0.0027159 | 0.00064308 | 0.083459 | 0.015142 | 0.023639 | 0.070441 | 0.1011 | 0.24727 | -0.058478 | 0.069728 | 0.018674 | 0.003172 | 0.043302 | 0.13275 | 0.026065 | -0.11836 | 120.7362 | -0.2271 | 120.8781 | 120.8183 | 0.082117 | -0.19645 | -0.050272 | 120.6763 | -0.25424 | 120.8644 | 120.7979 | 0.12153 | -0.1648 | -0.27148 | 120.8651 | 120.8958 | 121.042 | 120.8098 | -0.35602 | 120.838 | 120.9274 | 120.8207 | 120.8134 | -0.41591
3634.0781 | 121.3165 | -120.6757 | 0.40741 | 1.4211e-13 | 0.025015 | 0.016133 | 0.009682 | -0.023362 | 0.0046387 | 0.24784 | 0.024812 | 0.034818 | -0.096637 | -0.0022885 | 0.00064308 | 0.088037 | 0.019721 | 0.01906 | 0.070441 | 0.1011 | 0.24727 | -0.063057 | 0.088043 | 0.03241 | 0.007751 | 0.038723 | 0.13733 | 0.030644 | -0.11836 | 120.6126 | -0.33697 | 120.7637 | 120.6947 | 0.082117 | -0.30632 | -0.16014 | 120.5573 | -0.36869 | 120.7637 | 120.6834 | 0.12611 | -0.27008 | -0.37677 | 120.7461 | 120.7768 | 120.9229 | 120.6954 | -0.47047 | 120.7144 | 120.813 | 120.7063 | 120.7081 | -0.52577
3635.7969 | 121.3806 | -120.8313 | 0.49896 | 1.4211e-13 | 0.025442 | 0.016133 | 0.010109 | -0.023576 | 0.0046387 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0027159 | 0.00042948 | 0.083459 | 0.015142 | 0.023639 | 0.07502 | 0.1011 | 0.24269 | -0.072215 | 0.088043 | 0.027831 | 0.003172 | 0.038723 | 0.13275 | 0.035222 | -0.11836 | 120.7591 | -0.42394 | 120.9148 | 120.8549 | 0.095854 | -0.39787 | -0.25627 | 120.7129 | -0.46024 | 120.9193 | 120.8345 | 0.12153 | -0.36621 | -0.46374 | 120.9063 | 120.9324 | 121.074 | 120.8464 | -0.57118 | 120.87 | 120.964 | 120.8665 | 120.8591 | -0.61732
3637.5938 | 121.2296 | -121.0007 | 0.17395 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.024598 | 0.034604 | -0.096851 | -0.0027159 | 0.00042948 | 0.074302 | 0.0243 | 0.023639 | 0.070441 | 0.096516 | 0.24727 | -0.072215 | 0.083464 | 0.027831 | 0.003172 | 0.04788 | 0.12817 | 0.039801 | -0.12752 | 120.9285 | -0.10351 | 121.075 | 121.0243 | 0.095854 | -0.077434 | 0.073324 | 120.8732 | -0.12607 | 121.0841 | 121.0038 | 0.13069 | -0.045778 | -0.13415 | 121.0711 | 121.0972 | 121.2479 | 121.025 | -0.24616 | 121.0486 | 121.1288 | 121.0405 | 121.0285 | -0.30147
3639.3281 | 121.3028 | -120.9641 | 0.13733 | 1.4211e-13 | 0.024801 | 0.016346 | 0.010109 | -0.023148 | 0.0046387 | 0.24784 | 0.024598 | 0.034604 | -0.096637 | -0.0027159 | 0.00042948 | 0.07888 | 0.010564 | 0.023639 | 0.070441 | 0.1011 | 0.25185 | -0.063057 | 0.074307 | 0.018674 | 0.003172 | 0.043302 | 0.13733 | 0.030644 | -0.12294 | 120.901 | -0.066888 | 121.0429 | 120.9877 | 0.086696 | -0.036234 | 0.11452 | 120.8411 | -0.094027 | 121.0384 | 120.9672 | 0.12611 | 0 | -0.10669 | 121.0345 | 121.0651 | 121.2159 | 120.9746 | -0.20039 | 121.0074 | 121.1014 | 120.9947 | 120.9827 | -0.26027
3641.125 | 121.2799 | -120.7214 | 0.46692 | 1.4211e-13 | 0.025015 | 0.016346 | 0.010109 | -0.022935 | 0.0044249 | 0.23258 | 0.024385 | 0.034604 | -0.096851 | -0.0027159 | 0.00042948 | 0.083459 | 0.028878 | 0.023639 | 0.065863 | 0.091937 | 0.24727 | -0.081373 | 0.078886 | 0.03241 | 0.003172 | 0.043302 | 0.12817 | 0.030644 | -0.12294 | 120.6401 | -0.40106 | 120.8049 | 120.7451 | 0.10501 | -0.37498 | -0.21964 | 120.5985 | -0.42362 | 120.8003 | 120.7246 | 0.12611 | -0.33875 | -0.43627 | 120.7873 | 120.8134 | 120.9687 | 120.7503 | -0.54829 | 120.7647 | 120.8496 | 120.7521 | 120.7538 | -0.58986
3642.8438 | 120.5383 | -15.303 | 98.7579 | 1.4211e-13 | 0.025015 | 0.01656 | 0.009682 | -0.023362 | 0.0046387 | 0.23258 | 0.024598 | 0.034818 | -0.096637 | -0.0027159 | 0.0010705 | 0.05141 | -0.016908 | -0.012988 | 0.042971 | 0.069043 | 0.21522 | -0.10885 | 0.051413 | 0.004938 | -0.028879 | 0.006674 | 0.096121 | 0.007751 | -0.15499 | 15.1942 | -98.715 | 15.3544 | 15.2901 | 0.095859 | -98.6889 | -98.5427 | 15.148 | -98.7513 | 15.3545 | 15.2742 | 0.12611 | -98.6618 | -98.7502 | 15.346 | 15.3721 | 15.5183 | 15.2861 | -98.8668 | 15.3097 | 15.3992 | 15.3108 | 15.308 | -98.9129
3644.6406 | 121.1746 | -95.723 | 24.9023 | 1.4211e-13 | 0.025015 | 0.016346 | 0.010109 | -0.023362 | 0.0050659 | 0.23258 | 0.024385 | 0.034818 | -0.096851 | -0.0027159 | 0.00064308 | 0.074302 | 0.015142 | 0.009904 | 0.065863 | 0.08278 | 0.24269 | -0.072215 | 0.074307 | 0.018674 | -0.005985 | 0.043302 | 0.12359 | 0.021486 | -0.12752 | 95.6507 | -24.8365 | 95.7973 | 95.7329 | 0.082119 | -24.8196 | -24.6596 | 95.5954 | -24.859 | 95.7973 | 95.717 | 0.12153 | -24.7788 | -24.8809 | 95.7888 | 95.8057 | 95.9657 | 95.7381 | -24.9746 | 95.7663 | 95.8466 | 95.7444 | 95.7416 | -25.0299
3646.3906 | 121.2616 | -95.8008 | 24.9527 | 1.4211e-13 | 0.025015 | 0.016133 | 0.0098956 | -0.022935 | 0.0050659 | 0.24021 | 0.024171 | 0.035031 | -0.096851 | -0.0029295 | 0.00085668 | 0.069723 | 0.010564 | 0.009904 | 0.065863 | 0.087359 | 0.24269 | -0.063057 | 0.069728 | 0.018674 | -0.001407 | 0.029566 | 0.12359 | 0.021486 | -0.1321 | 95.7377 | -24.8868 | 95.8705 | 95.8107 | 0.072961 | -24.8653 | -24.71 | 95.6687 | -24.9231 | 95.8705 | 95.7994 | 0.13069 | -24.8291 | -24.9312 | 95.8666 | 95.8881 | 96.0435 | 95.8113 | -25.0158 | 95.8303 | 95.9244 | 95.8223 | 95.8195 | -25.0848
3648.1875 | 121.2296 | -95.8786 | 25.0122 | 1.4211e-13 | 0.025442 | 0.016133 | 0.0098956 | -0.023148 | 0.0050659 | 0.23258 | 0.024385 | 0.034604 | -0.096851 | -0.0025021 | 0.00085668 | 0.065145 | 0.010564 | 0.014482 | 0.065863 | 0.087359 | 0.23812 | -0.072215 | 0.074307 | 0.027831 | -0.001407 | 0.034145 | 0.11444 | 0.021486 | -0.12752 | 95.8064 | -24.9463 | 95.9437 | 95.8931 | 0.086697 | -24.9248 | -24.7741 | 95.7511 | -24.9781 | 95.9529 | 95.8772 | 0.12611 | -24.8978 | -24.9907 | 95.9445 | 95.966 | 96.1167 | 95.8892 | -25.0844 | 95.9127 | 95.993 | 95.9001 | 95.9064 | -25.1397
3649.9062 | 121.1838 | -95.9747 | 25.0214 | 1.4211e-13 | 0.025015 | 0.01656 | 0.010323 | -0.023362 | 0.0046387 | 0.23258 | 0.024812 | 0.034818 | -0.096637 | -0.0025021 | 0.00064308 | 0.065145 | 0.019721 | 0.01906 | 0.056706 | 0.08278 | 0.24269 | -0.063057 | 0.074307 | 0.009516 | -0.001407 | 0.038723 | 0.11901 | 0.030644 | -0.12752 | 95.9117 | -24.9647 | 96.0399 | 95.9938 | 0.082117 | -24.9386 | -24.7787 | 95.8472 | -24.9826 | 96.049 | 95.9733 | 0.12611 | -24.9023 | -24.9907 | 96.0314 | 96.0575 | 96.2174 | 95.9945 | -25.0844 | 96.0135 | 96.0937 | 96.0054 | 95.9842 | -25.1489
3651.6875 | 121.17 | -95.929 | 25.1129 | 1.4211e-13 | 0.025228 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.23258 | 0.024598 | 0.034604 | -0.096424 | -0.0025021 | 0.00042948 | 0.069723 | 0.015142 | 0.014482 | 0.065863 | 0.08278 | 0.23812 | -0.067636 | 0.06515 | 0.023253 | 0.003172 | 0.034145 | 0.12359 | 0.026065 | -0.12752 | 95.8613 | -25.0471 | 95.9987 | 95.9434 | 0.082118 | -25.0301 | -24.8748 | 95.8014 | -25.0788 | 95.9941 | 95.9321 | 0.13069 | -24.9893 | -25.0869 | 95.9948 | 96.0117 | 96.1671 | 95.9441 | -25.1806 | 95.9631 | 96.0525 | 95.955 | 95.9522 | -25.2404
3653.4844 | 121.3028 | -96.4188 | 24.5728 | 1.4211e-13 | 0.025228 | 0.01656 | 0.010109 | -0.023362 | 0.0048523 | 0.24021 | 0.024385 | 0.035031 | -0.096637 | -0.0027159 | 0.00064308 | 0.065145 | 0.010564 | 0.023639 | 0.061284 | 0.091937 | 0.24727 | -0.067636 | 0.069728 | 0.018674 | -0.001407 | 0.029566 | 0.12359 | 0.026065 | -0.12752 | 96.3511 | -24.5115 | 96.4839 | 96.4424 | 0.091275 | -24.4808 | -24.3255 | 96.2912 | -24.5432 | 96.4885 | 96.4174 | 0.12611 | -24.4492 | -24.5467 | 96.48 | 96.5107 | 96.666 | 96.4293 | -24.6404 | 96.4483 | 96.5424 | 96.4448 | 96.4374 | -24.7003
3655.2656 | 121.2341 | -96.9818 | 24.1104 | 1.4211e-13 | 0.025228 | 0.016346 | 0.009682 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034604 | -0.097065 | -0.0027159 | 0.00064308 | 0.069723 | 0.015142 | 0.014482 | 0.061284 | 0.096516 | 0.24269 | -0.067636 | 0.074307 | 0.023253 | -0.005985 | 0.038723 | 0.11901 | 0.026065 | -0.1321 | 96.9142 | -24.0491 | 97.0515 | 96.9963 | 0.082118 | -24.0139 | -23.8677 | 96.8497 | -24.0717 | 97.0561 | 96.9758 | 0.12611 | -23.9914 | -24.0843 | 97.0431 | 97.0783 | 97.2245 | 96.997 | -24.178 | 97.0205 | 97.1008 | 97.0079 | 97.0051 | -24.2425
3657 | 121.3486 | -21.7575 | 99.1882 | 1.4211e-13 | 0.025228 | 0.016774 | 0.0098956 | -0.023148 | 0.0048523 | 0.23258 | 0.024812 | 0.034818 | -0.096851 | -0.0022885 | 0.00021588 | 0.037675 | -0.021486 | -0.017566 | 0.038393 | 0.055306 | 0.20149 | -0.099689 | 0.046835 | -0.013377 | -0.028879 | 0.015831 | 0.091543 | -0.042614 | -0.15957 | 21.6578 | -99.1498 | 21.7952 | 21.7399 | 0.082123 | -99.1329 | -98.9867 | 21.5979 | -99.1724 | 21.8043 | 21.7286 | 0.13069 | -99.0967 | -99.2308 | 21.7959 | 21.8128 | 21.959 | 21.736 | -99.2879 | 21.7733 | 21.8491 | 21.7149 | 21.7441 | -99.3478
3658.7812 | 121.2616 | -3.804 | 117.1326 | 1.4211e-13 | 0.025015 | 0.01656 | 0.0098956 | -0.023148 | 0.0046387 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0029295 | 0.00064308 | 0.037675 | -0.026065 | -0.022144 | 0.024657 | 0.055306 | 0.21064 | -0.09511 | 0.037677 | 0.000359 | -0.042615 | 0.002095 | 0.091543 | -0.060928 | -0.15957 | 3.7089 | -117.1079 | 3.8417 | 3.7819 | 0.072966 | -117.0773 | -116.9219 | 3.6444 | -117.1305 | 3.8417 | 3.7614 | 0.11695 | -117.041 | -117.1935 | 3.8287 | 3.8593 | 4.0147 | 3.778 | -117.2277 | 3.8061 | 3.8956 | 3.7431 | 3.8044 | -117.2921
3660.5781 | 121.2845 | -4.7562 | 116.0843 | 1.4211e-13 | 0.025015 | 0.016133 | 0.009682 | -0.023148 | 0.0048523 | 0.22495 | 0.024598 | 0.034818 | -0.096851 | -0.0025021 | 0.00064308 | 0.042253 | -0.021486 | -0.012988 | 0.042971 | 0.055306 | 0.20607 | -0.099689 | 0.042256 | -0.008798 | -0.042615 | 0.002095 | 0.077807 | -0.060928 | -0.15957 | 4.6565 | -116.0413 | 4.7984 | 4.7432 | 0.086701 | -116.029 | -115.8782 | 4.5966 | -116.0822 | 4.7984 | 4.7136 | 0.11695 | -116.0065 | -116.1452 | 4.7991 | 4.8115 | 4.9622 | 4.7347 | -116.184 | 4.7583 | 4.834 | 4.6952 | 4.7474 | -116.2439
3662.3125 | 121.2296 | -5.7037 | 115.0314 | 1.4211e-13 | 0.025228 | 0.016133 | 0.010323 | -0.023362 | 0.0044249 | 0.24021 | 0.024812 | 0.034604 | -0.096851 | -0.0029295 | 0.00064308 | 0.033096 | -0.016908 | -0.012988 | 0.038393 | 0.055306 | 0.21064 | -0.11342 | 0.046835 | 0.000359 | -0.038036 | 0.011252 | 0.091543 | -0.038035 | -0.15499 | 5.5903 | -114.993 | 5.7368 | 5.6907 | 0.10044 | -114.9761 | -114.8208 | 5.5487 | -115.0202 | 5.7506 | 5.6657 | 0.11695 | -114.9399 | -115.0695 | 5.7421 | 5.759 | 5.9144 | 5.6868 | -115.1449 | 5.715 | 5.7953 | 5.6657 | 5.7041 | -115.1864
3664.1094 | 121.2708 | -4.1748 | 117.1371 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.022935 | 0.0048523 | 0.24784 | 0.024171 | 0.034818 | -0.096851 | -0.0025021 | 0.0010705 | 0.042253 | -0.012329 | -0.017566 | 0.038393 | 0.059885 | 0.20607 | -0.12716 | 0.046835 | 0.000359 | -0.033458 | 0.006674 | 0.082386 | -0.042614 | -0.15957 | 4.0476 | -117.0988 | 4.2171 | 4.1572 | 0.1096 | -117.0773 | -116.9311 | 4.0152 | -117.1305 | 4.2216 | 4.1413 | 0.12611 | -117.0548 | -117.1798 | 4.2132 | 4.2347 | 4.3809 | 4.1625 | -117.2643 | 4.1815 | 4.2572 | 4.1322 | 4.1752 | -117.2967
3665.9062 | 121.431 | -4.8203 | 116.7206 | 1.4211e-13 | 0.025015 | 0.016346 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034818 | -0.096424 | -0.0027159 | 0.00064308 | 0.037675 | -0.026065 | -0.017566 | 0.042971 | 0.064464 | 0.20607 | -0.118 | 0.042256 | -0.008798 | -0.038036 | 0.002095 | 0.082386 | -0.074664 | -0.15957 | 4.7022 | -116.6776 | 4.8579 | 4.8027 | 0.10044 | -116.6561 | -116.5145 | 4.6607 | -116.7185 | 4.8625 | 4.7822 | 0.12153 | -116.6382 | -116.7952 | 4.8632 | 4.8847 | 5.0263 | 4.7942 | -116.8386 | 4.8223 | 4.9026 | 4.7456 | 4.8115 | -116.8802
3667.6875 | 121.3989 | -112.9028 | 8.1894 | 1.4211e-13 | 0.025228 | 0.016133 | 0.0098956 | -0.022935 | 0.0050659 | 0.23258 | 0.024385 | 0.034604 | -0.096637 | -0.0025021 | 0.00042948 | 0.074302 | 0.019721 | 0.01906 | 0.070441 | 0.096516 | 0.26101 | -0.063057 | 0.078886 | 0.03241 | 0.003172 | 0.043302 | 0.12359 | 0.030644 | -0.12752 | 112.8398 | -8.119 | 112.9771 | 112.9219 | 0.082117 | -8.0929 | -7.9284 | 112.7753 | -8.1461 | 112.9817 | 112.906 | 0.13069 | -8.0658 | -8.1587 | 112.9733 | 112.9993 | 113.1638 | 112.9226 | -8.2524 | 112.9461 | 113.0264 | 112.9335 | 112.9352 | -8.3169
3669.4844 | 121.5088 | -114.2212 | 6.839 | 1.4211e-13 | 0.025228 | 0.015919 | 0.009682 | -0.023362 | 0.0048523 | 0.24784 | 0.024385 | 0.034604 | -0.096851 | -0.0025021 | 0.00021588 | 0.069723 | 0.019721 | 0.01906 | 0.070441 | 0.096516 | 0.24727 | -0.063057 | 0.069728 | 0.027831 | -0.001407 | 0.043302 | 0.12359 | 0.026065 | -0.12294 | 114.1581 | -6.7685 | 114.2909 | 114.2403 | 0.082117 | -6.7425 | -6.5917 | 114.0983 | -6.7957 | 114.2909 | 114.2198 | 0.12153 | -6.7154 | -6.8129 | 114.2916 | 114.3177 | 114.4685 | 114.2409 | -6.902 | 114.2645 | 114.3448 | 114.2473 | 114.249 | -6.9619
3671.2656 | 121.4951 | -114.5599 | 6.6055 | 1.4211e-13 | 0.025228 | 0.016346 | 0.0098956 | -0.023148 | 0.0050659 | 0.23258 | 0.024385 | 0.03439 | -0.096851 | -0.0029295 | 0.00064308 | 0.074302 | 0.010564 | 0.01906 | 0.065863 | 0.091937 | 0.24727 | -0.049321 | 0.078886 | 0.023253 | 0.003172 | 0.038723 | 0.12817 | 0.030644 | -0.12752 | 114.5106 | -6.5397 | 114.6342 | 114.579 | 0.068381 | -6.5136 | -6.3583 | 114.4324 | -6.5668 | 114.6388 | 114.5631 | 0.13069 | -6.4774 | -6.5749 | 114.6258 | 114.6519 | 114.8072 | 114.5705 | -6.6549 | 114.5987 | 114.6881 | 114.5906 | 114.5832 | -6.733
3673 | 121.4951 | -114.8163 | 6.3675 | 1.4211e-13 | 0.025228 | 0.016133 | 0.0094682 | -0.023362 | 0.0046387 | 0.24021 | 0.024385 | 0.034604 | -0.096424 | -0.0029295 | 0.00064308 | 0.069723 | 0.019721 | 0.01906 | 0.07502 | 0.1011 | 0.24727 | -0.053899 | 0.074307 | 0.027831 | 0.003172 | 0.038723 | 0.12359 | 0.021486 | -0.11836 | 114.7624 | -6.2925 | 114.886 | 114.8353 | 0.072959 | -6.2664 | -6.1202 | 114.6979 | -6.3288 | 114.8906 | 114.8195 | 0.12153 | -6.2439 | -6.346 | 114.8913 | 114.9174 | 115.0636 | 114.836 | -6.4214 | 114.855 | 114.9399 | 114.8378 | 114.8441 | -6.4859
3674.7812 | 121.4081 | -116.0522 | 5.2231 | 1.4211e-13 | 0.025228 | 0.016133 | 0.0098956 | -0.023362 | 0.0044249 | 0.23258 | 0.024385 | 0.034818 | -0.096637 | -0.0025021 | 0.00042948 | 0.07888 | 0.015142 | 0.014482 | 0.065863 | 0.091937 | 0.25185 | -0.063057 | 0.074307 | 0.023253 | 0.007751 | 0.034145 | 0.12359 | 0.030644 | -0.11378 | 115.9892 | -5.1572 | 116.1311 | 116.0667 | 0.077539 | -5.1311 | -4.9712 | 115.9385 | -5.1889 | 116.1266 | 116.06 | 0.12153 | -5.0995 | -5.1924 | 116.1181 | 116.1442 | 116.3041 | 116.0674 | -5.2861 | 116.0864 | 116.1758 | 116.0829 | 116.0755 | -5.3369
3676.5938 | 121.4218 | -116.0019 | 5.3238 | 1.4211e-13 | 0.025442 | 0.016346 | 0.0098956 | -0.023148 | 0.0046387 | 0.23258 | 0.024598 | 0.034604 | -0.096637 | -0.0027159 | 0.00042948 | 0.069723 | 0.015142 | 0.023639 | 0.070441 | 0.1011 | 0.25185 | -0.058478 | 0.074307 | 0.03241 | 0.003172 | 0.052459 | 0.12817 | 0.035222 | -0.12294 | 115.9434 | -5.2534 | 116.0716 | 116.0255 | 0.082117 | -5.2227 | -5.0719 | 115.879 | -5.2713 | 116.0762 | 116.0051 | 0.12611 | -5.1956 | -5.2886 | 116.0723 | 116.103 | 116.2537 | 116.017 | -5.3823 | 116.0544 | 116.1301 | 116.0371 | 116.0343 | -5.4467
3678.3281 | 121.3806 | -115.5533 | 5.7724 | 1.4211e-13 | 0.025442 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.24784 | 0.024385 | 0.034604 | -0.096424 | -0.0031431 | 0.00042948 | 0.07888 | 0.015142 | 0.023639 | 0.070441 | 0.091937 | 0.24727 | -0.053899 | 0.078886 | 0.027831 | -0.010564 | 0.04788 | 0.12359 | 0.030644 | -0.12294 | 115.4994 | -5.702 | 115.6322 | 115.5769 | 0.077538 | -5.6805 | -5.5251 | 115.4303 | -5.7245 | 115.6322 | 115.5427 | 0.11238 | -5.6488 | -5.7418 | 115.6237 | 115.6452 | 115.8006 | 115.5684 | -5.8263 | 115.6012 | 115.6769 | 115.5839 | 115.5811 | -5.8953
3680.1094 | 121.3852 | -116.4825 | 4.8111 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023148 | 0.0046387 | 0.24021 | 0.024385 | 0.034818 | -0.096424 | -0.0027159 | 0.00085668 | 0.07888 | 0.019721 | 0.01906 | 0.07502 | 0.091937 | 0.24727 | -0.053899 | 0.074307 | 0.03241 | 0.007751 | 0.034145 | 0.12359 | 0.035222 | -0.12294 | 116.4286 | -4.7361 | 116.5614 | 116.5016 | 0.072959 | -4.7192 | -4.5638 | 116.3596 | -4.777 | 116.5569 | 116.4903 | 0.13069 | -4.6875 | -4.7759 | 116.5576 | 116.5745 | 116.7298 | 116.5023 | -4.865 | 116.5167 | 116.6061 | 116.5178 | 116.515 | -4.934
3681.9062 | 121.3852 | -117.3615 | 3.9734 | 1.4211e-13 | 0.025228 | 0.01656 | 0.0098956 | -0.023148 | 0.0048523 | 0.23258 | 0.024598 | 0.034818 | -0.096424 | -0.0029295 | 0.00064308 | 0.083459 | 0.019721 | 0.032795 | 0.070441 | 0.1011 | 0.24269 | -0.053899 | 0.078886 | 0.03241 | 0.003172 | 0.038723 | 0.11901 | 0.003172 | -0.12294 | 117.3076 | -3.9029 | 117.4449 | 117.3942 | 0.086694 | -3.8723 | -3.7307 | 117.2385 | -3.9347 | 117.4403 | 117.3646 | 0.12611 | -3.8544 | -3.9702 | 117.4319 | 117.4625 | 117.6041 | 117.3812 | -4.0273 | 117.4002 | 117.4805 | 117.3646 | 117.3939 | -4.0963
3683.7031 | 121.4035 | -117.6178 | 3.7354 | 1.4211e-13 | 0.025228 | 0.015919 | 0.010109 | -0.023148 | 0.0046387 | 0.24021 | 0.024385 | 0.034818 | -0.096637 | -0.0027159 | 0.00042948 | 0.07888 | 0.015142 | 0.01906 | 0.079598 | 0.10567 | 0.24269 | -0.049321 | 0.074307 | 0.027831 | 0.007751 | 0.04788 | 0.12817 | 0.035222 | -0.12294 | 117.5685 | -3.6558 | 117.6967 | 117.6369 | 0.068381 | -3.6297 | -3.4927 | 117.4949 | -3.6875 | 117.6921 | 117.6255 | 0.13069 | -3.6072 | -3.7001 | 117.6974 | 117.7235 | 117.8605 | 117.6329 | -3.7847 | 117.6657 | 117.746 | 117.653 | 117.6456 | -3.8583
3685.5 | 121.5363 | -118.1168 | 3.1265 | 1.4211e-13 | 0.025442 | 0.015919 | 0.0098956 | -0.023148 | 0.0046387 | 0.24021 | 0.024171 | 0.034604 | -0.096424 | -0.0025021 | 0.00085668 | 0.074302 | 0.019721 | 0.014482 | 0.084176 | 0.096516 | 0.24269 | -0.053899 | 0.074307 | 0.023253 | 0.003172 | 0.038723 | 0.11444 | 0.030644 | -0.12752 | 118.0629 | -3.0424 | 118.1911 | 118.1312 | 0.068381 | -3.03 | -2.8838 | 117.9892 | -3.0878 | 118.1911 | 118.1199 | 0.13069 | -3.0121 | -3.0959 | 118.2009 | 118.2133 | 118.3595 | 118.1365 | -3.1804 | 118.1555 | 118.2312 | 118.1474 | 118.14 | -3.254
3687.2344 | 121.4493 | -118.3548 | 3.0075 | 1.4211e-13 | 0.025442 | 0.016133 | 0.009682 | -0.023362 | 0.0046387 | 0.24021 | 0.024598 | 0.034818 | -0.096851 | -0.0029295 | 0.00085668 | 0.07888 | 0.019721 | 0.028217 | 0.07502 | 0.1011 | 0.25185 | -0.058478 | 0.074307 | 0.027831 | 0.007751 | 0.038723 | 0.12359 | 0.026065 | -0.11836 | 118.2963 | -2.9325 | 118.4337 | 118.383 | 0.086695 | -2.9064 | -2.7557 | 118.2364 | -2.9688 | 118.4291 | 118.3625 | 0.12611 | -2.8839 | -2.9814 | 118.4298 | 118.4559 | 118.6066 | 118.3745 | -3.066 | 118.3935 | 118.4784 | 118.3809 | 118.3826 | -3.1259
3689.0312 | 121.4127 | -118.4463 | 2.9114 | 1.4211e-13 | 0.025015 | 0.016133 | 0.010109 | -0.023362 | 0.0048523 | 0.23258 | 0.024385 | 0.034818 | -0.096424 | -0.0025021 | 0.00064308 | 0.083459 | 0.0243 | 0.01906 | 0.079598 | 0.096516 | 0.25185 | -0.058478 | 0.078886 | 0.023253 | 0.003172 | 0.043302 | 0.12817 | 0.044379 | -0.12294 | 118.3879 | -2.8318 | 118.5298 | 118.4654 | 0.077538 | -2.8149 | -2.6595 | 118.3234 | -2.8681 | 118.5252 | 118.4495 | 0.12611 | -2.7832 | -2.867 | 118.5259 | 118.5429 | 118.6982 | 118.4706 | -2.9699 | 118.4897 | 118.5745 | 118.4907 | 118.4696 | -3.0343
3690.8281 | 121.4905 | -118.5837 | 2.6962 | 1.4211e-13 | 0.025228 | 0.016133 | 0.010109 | -0.023362 | 0.0046387 | 0.24021 | 0.024812 | 0.035031 | -0.096424 | -0.0027159 | 0.00064308 | 0.07888 | 0.015142 | 0.023639 | 0.070441 | 0.096516 | 0.24727 | -0.058478 | 0.078886 | 0.027831 | 0.003172 | 0.043302 | 0.12359 | 0.030644 | -0.12294 | 118.5252 | -2.6258 | 118.6626 | 118.6073 | 0.082117 | -2.5997 | -2.449 | 118.4607 | -2.6529 | 118.6626 | 118.5869 | 0.12611 | -2.5726 | -2.6656 | 118.6541 | 118.6802 | 118.831 | 118.5988 | -2.7547 | 118.627 | 118.7073 | 118.6143 | 118.6115 | -2.8192
3692.625 | 121.4996 | -118.634 | 2.6733 | 1.4211e-13 | 0.025228 | 0.01656 | 0.0098956 | -0.023362 | 0.0046387 | 0.23258 | 0.024812 | 0.03439 | -0.096637 | -0.0029295 | 0.00064308 | 0.074302 | 0.019721 | 0.023639 | 0.065863 | 0.091937 | 0.24727 | -0.063057 | 0.078886 | 0.027831 | 0.003172 | 0.04788 | 0.12359 | 0.021486 | -0.12752 | 118.571 | -2.6075 | 118.7083 | 118.6577 | 0.086696 | -2.5814 | -2.4261 | 118.5065 | -2.6255 | 118.7129 | 118.6372 | 0.13069 | -2.5497 | -2.6519 | 118.6999 | 118.726 | 118.8813 | 118.6538 | -2.7364 | 118.6819 | 118.7576 | 118.6555 | 118.6619 | -2.8009
3694.3594 | 121.4722 | -118.6935 | 2.6642 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.023362 | 0.0044249 | 0.24021 | 0.024598 | 0.03439 | -0.097065 | -0.0025021 | 0.00064308 | 0.07888 | 0.0243 | 0.023639 | 0.07502 | 0.087359 | 0.24727 | -0.044742 | 0.083464 | 0.036989 | 0.007751 | 0.04788 | 0.12359 | 0.035222 | -0.12294 | 118.6488 | -2.5892 | 118.7724 | 118.7172 | 0.068381 | -2.5768 | -2.4169 | 118.5706 | -2.6163 | 118.777 | 118.7013 | 0.13069 | -2.5406 | -2.629 | 118.7686 | 118.7809 | 118.9408 | 118.7178 | -2.7089 | 118.7414 | 118.8171 | 118.7288 | 118.7305 | -2.7871
3696.1562 | 121.55 | -118.7164 | 2.5955 | 1.4211e-13 | 0.025442 | 0.016346 | 0.009682 | -0.023148 | 0.0046387 | 0.23258 | 0.024385 | 0.034604 | -0.096424 | -0.0029295 | 0.00064308 | 0.088037 | 0.019721 | 0.023639 | 0.070441 | 0.096516 | 0.26101 | -0.053899 | 0.078886 | 0.023253 | 0.003172 | 0.043302 | 0.12359 | 0.030644 | -0.12294 | 118.6625 | -2.5251 | 118.8045 | 118.7401 | 0.077538 | -2.499 | -2.3345 | 118.5935 | -2.5522 | 118.7953 | 118.7196 | 0.12611 | -2.4719 | -2.5649 | 118.7869 | 118.8129 | 118.9774 | 118.7362 | -2.6494 | 118.7597 | 118.84 | 118.7471 | 118.7397 | -2.7185
3697.9375 | 121.4401 | -119.0323 | 2.3712 | 1.4211e-13 | 0.025015 | 0.015705 | 0.010109 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034604 | -0.096851 | -0.0031431 | 0.00064308 | 0.07888 | 0.010564 | 0.028217 | 0.07502 | 0.096516 | 0.24727 | -0.049321 | 0.078886 | 0.027831 | 0.003172 | 0.043302 | 0.12817 | 0.030644 | -0.12752 | 118.983 | -2.2962 | 119.1112 | 119.0605 | 0.077538 | -2.2747 | -2.1239 | 118.9048 | -2.3279 | 119.1112 | 119.0355 | 0.13069 | -2.243 | -2.3406 | 119.1073 | 119.1288 | 119.2796 | 119.0429 | -2.4205 | 119.0756 | 119.1605 | 119.0629 | 119.0601 | -2.4987
3699.7188 | 121.4447 | -119.0231 | 2.3987 | 1.4211e-13 | 0.025015 | 0.016346 | 0.009682 | -0.023148 | 0.0046387 | 0.22495 | 0.024598 | 0.034604 | -0.096637 | -0.0025021 | 0.00064308 | 0.07888 | 0.019721 | 0.01906 | 0.07502 | 0.096516 | 0.24727 | -0.058478 | 0.078886 | 0.023253 | 0.007751 | 0.043302 | 0.12359 | 0.030644 | -0.12294 | 118.9647 | -2.3237 | 119.102 | 119.0422 | 0.077538 | -2.3022 | -2.1514 | 118.9002 | -2.3554 | 119.102 | 119.0309 | 0.13069 | -2.2751 | -2.368 | 119.0982 | 119.1196 | 119.2704 | 119.0429 | -2.4572 | 119.0664 | 119.1467 | 119.0538 | 119.0464 | -2.5216
3701.5312 | 121.4996 | -119.0002 | 2.3758 | 1.4211e-13 | 0.025228 | 0.016346 | 0.0098956 | -0.023362 | 0.0048523 | 0.24021 | 0.024171 | 0.034604 | -0.096424 | -0.0027159 | 0.00064308 | 0.07888 | 0.019721 | 0.023639 | 0.07502 | 0.096516 | 0.24269 | -0.053899 | 0.074307 | 0.023253 | 0.01233 | 0.043302 | 0.13275 | 0.030644 | -0.11378 | 118.9463 | -2.3008 | 119.0791 | 119.0239 | 0.077538 | -2.2793 | -2.1331 | 118.8865 | -2.3325 | 119.0746 | 119.0126 | 0.12611 | -2.243 | -2.3451 | 119.0753 | 119.0968 | 119.2429 | 119.02 | -2.4297 | 119.0435 | 119.133 | 119.0309 | 119.0235 | -2.4896
3703.2656 | 121.4996 | -119.0323 | 2.3529 | 1.4211e-13 | 0.025228 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.024171 | 0.034604 | -0.096424 | -0.0027159 | 0.00064308 | 0.083459 | 0.019721 | 0.023639 | 0.065863 | 0.096516 | 0.25185 | -0.049321 | 0.074307 | 0.023253 | 0.007751 | 0.04788 | 0.12359 | 0.030644 | -0.12294 | 118.983 | -2.287 | 119.1157 | 119.0559 | 0.07296 | -2.2564 | -2.1011 | 118.9093 | -2.305 | 119.1066 | 119.04 | 0.13069 | -2.2293 | -2.3223 | 119.0982 | 119.1288 | 119.2841 | 119.052 | -2.4022 | 119.0802 | 119.1559 | 119.0629 | 119.0555 | -2.4758
3705.0625 | 121.4905 | -119.0872 | 2.3254 | 1.4211e-13 | 0.025228 | 0.015919 | 0.0098956 | -0.022721 | 0.0044249 | 0.24021 | 0.024812 | 0.034604 | -0.096637 | -0.0025021 | 0.00085668 | 0.083459 | 0.015142 | 0.028217 | 0.079598 | 0.096516 | 0.24727 | -0.067636 | 0.078886 | 0.027831 | 0.007751 | 0.038723 | 0.12359 | 0.044379 | -0.12294 | 119.0196 | -2.2458 | 119.1707 | 119.1154 | 0.095853 | -2.2289 | -2.0782 | 118.9643 | -2.2867 | 119.1661 | 119.095 | 0.13069 | -2.2018 | -2.2811 | 119.1668 | 119.1837 | 119.3345 | 119.1024 | -2.3931 | 119.1259 | 119.2108 | 119.1316 | 119.1151 | -2.4484
3706.8594 | 121.5454 | -119.101 | 2.3071 | 1.4211e-13 | 0.025015 | 0.016346 | 0.0098956 | -0.023148 | 0.0050659 | 0.23258 | 0.024598 | 0.034604 | -0.096851 | -0.0025021 | 0.00021588 | 0.074302 | 0.0243 | 0.028217 | 0.065863 | 0.096516 | 0.25185 | -0.063057 | 0.078886 | 0.041567 | 0.01233 | 0.038723 | 0.13275 | 0.035222 | -0.12752 | 119.0379 | -2.2413 | 119.1753 | 119.1292 | 0.091274 | -2.2106 | -2.0553 | 118.9734 | -2.2684 | 119.1798 | 119.1133 | 0.13985 | -2.1744 | -2.2719 | 119.1668 | 119.1975 | 119.3528 | 119.1253 | -2.3702 | 119.1397 | 119.2337 | 119.1362 | 119.1425 | -2.4346
3708.6562 | 121.5408 | -119.1284 | 2.2705 | 1.4211e-13 | 0.025228 | 0.016346 | 0.0098956 | -0.023362 | 0.0044249 | 0.23258 | 0.024598 | 0.034604 | -0.096851 | -0.0025021 | 0.00042948 | 0.07888 | 0.019721 | 0.032795 | 0.079598 | 0.10567 | 0.24727 | -0.058478 | 0.083464 | 0.03241 | 0.007751 | 0.043302 | 0.12359 | 0.026065 | -0.12752 | 119.0699 | -2.1909 | 119.2073 | 119.1612 | 0.091273 | -2.1648 | -2.0232 | 119.0009 | -2.2272 | 119.2119 | 119.1362 | 0.13527 | -2.1469 | -2.2444 | 119.208 | 119.2341 | 119.3757 | 119.1481 | -2.329 | 119.1717 | 119.252 | 119.1545 | 119.1608 | -2.398
3710.3906 | 121.6324 | -119.1788 | 2.2247 | 1.4211e-13 | 0.025015 | 0.015919 | 0.009682 | -0.023362 | 0.0046387 | 0.23258 | 0.024385 | 0.034604 | -0.096851 | -0.0027159 | 0.00064308 | 0.074302 | 0.019721 | 0.023639 | 0.07502 | 0.1011 | 0.24727 | -0.049321 | 0.078886 | 0.03241 | 0.003172 | 0.052459 | 0.12359 | 0.035222 | -0.11836 | 119.1295 | -2.1497 | 119.2531 | 119.2024 | 0.07296 | -2.1236 | -1.9775 | 119.0604 | -2.1723 | 119.2577 | 119.1819 | 0.12153 | -2.1011 | -2.1895 | 119.2538 | 119.2799 | 119.426 | 119.1985 | -2.2741 | 119.2312 | 119.3024 | 119.214 | 119.2112 | -2.3431
3712.1875 | 121.4722 | -119.2383 | 2.2247 | 1.4211e-13 | 0.025228 | 0.015919 | 0.0098956 | -0.023362 | 0.0046387 | 0.23258 | 0.024385 | 0.034604 | -0.096851 | -0.0027159 | 0.00064308 | 0.07888 | 0.019721 | 0.023639 | 0.07502 | 0.096516 | 0.24269 | -0.035584 | 0.078886 | 0.03241 | 0.003172 | 0.043302 | 0.12817 | 0.030644 | -0.12752 | 119.2027 | -2.1497 | 119.3172 | 119.2619 | 0.059223 | -2.1282 | -1.982 | 119.1108 | -2.1814 | 119.3172 | 119.2415 | 0.13069 | -2.0966 | -2.1941 | 119.3133 | 119.3348 | 119.481 | 119.258 | -2.2603 | 119.2816 | 119.3665 | 119.2689 | 119.2707 | -2.3522
3713.9688 | 121.637 | -119.2062 | 2.1606 | 1.4211e-13 | 0.025015 | 0.016346 | 0.009682 | -0.023148 | 0.0046387 | 0.23258 | 0.024598 | 0.034604 | -0.096851 | -0.0027159 | 0.00064308 | 0.07888 | 0.019721 | 0.028217 | 0.07502 | 0.096516 | 0.24727 | -0.058478 | 0.074307 | 0.03241 | 0.007751 | 0.043302 | 0.13275 | 0.030644 | -0.12294 | 119.1478 | -2.0856 | 119.2851 | 119.2345 | 0.086695 | -2.0641 | -1.9134 | 119.0833 | -2.1173 | 119.2805 | 119.214 | 0.13069 | -2.0279 | -2.13 | 119.2813 | 119.3028 | 119.4535 | 119.226 | -2.2191 | 119.2495 | 119.339 | 119.2369 | 119.2386 | -2.2836
3715.75 | 121.5958 | -119.2703 | 2.1652 | 1.4211e-13 | 0.025228 | 0.015919 | 0.010109 | -0.023362 | 0.0048523 | 0.24021 | 0.024385 | 0.035245 | -0.096424 | -0.0027159 | 0.00064308 | 0.07888 | 0.019721 | 0.032795 | 0.065863 | 0.091937 | 0.25643 | -0.053899 | 0.083464 | 0.03241 | 0.007751 | 0.04788 | 0.12817 | 0.030644 | -0.12752 | 119.2164 | -2.0994 | 119.3492 | 119.3031 | 0.086694 | -2.0733 | -1.9088 | 119.1428 | -2.1173 | 119.3538 | 119.2781 | 0.13527 | -2.037 | -2.1346 | 119.3362 | 119.3623 | 119.5268 | 119.29 | -2.2191 | 119.3182 | 119.3985 | 119.301 | 119.3027 | -2.2927
3717.5625 | 121.669 | -119.3939 | 2.0462 | 1.4211e-13 | 0.025015 | 0.016133 | 0.010109 | -0.023576 | 0.0048523 | 0.24021 | 0.024385 | 0.034818 | -0.096424 | -0.0029295 | 0.00064308 | 0.083459 | 0.019721 | 0.023639 | 0.07502 | 0.10567 | 0.25185 | -0.058478 | 0.078886 | 0.036989 | 0.003172 | 0.038723 | 0.12359 | 0.030644 | -0.11836 | 119.3354 | -1.9712 | 119.4774 | 119.4176 | 0.082117 | -1.9405 | -1.7944 | 119.2756 | -2.0075 | 119.4728 | 119.3971 | 0.12153 | -1.9226 | -2.0156 | 119.4689 | 119.4996 | 119.6458 | 119.4136 | -2.1047 | 119.4326 | 119.5175 | 119.4246 | 119.4309 | -2.1646
3719.2969 | 121.6141 | -119.4168 | 2.0142 | 1.4211e-13 | 0.025015 | 0.015705 | 0.0098956 | -0.023789 | 0.0046387 | 0.24784 | 0.024598 | 0.035031 | -0.096424 | -0.0027159 | 0.0010705 | 0.083459 | 0.015142 | 0.028217 | 0.070441 | 0.10567 | 0.24727 | -0.058478 | 0.074307 | 0.027831 | 0.003172 | 0.04788 | 0.12817 | 0.021486 | -0.12294 | 119.3583 | -1.9437 | 119.5003 | 119.445 | 0.086695 | -1.9085 | -1.7669 | 119.2939 | -1.9663 | 119.4911 | 119.42 | 0.12611 | -1.886 | -1.9927 | 119.4873 | 119.5225 | 119.6641 | 119.432 | -2.0726 | 119.4647 | 119.545 | 119.4383 | 119.4446 | -2.1371
3721.0781 | 121.6644 | -119.4992 | 1.9089 | 1.4211e-13 | 0.025228 | 0.016346 | 0.009682 | -0.023362 | 0.0048523 | 0.24021 | 0.024598 | 0.034818 | -0.096424 | -0.0027159 | 0.00064308 | 0.069723 | 0.019721 | 0.032795 | 0.07502 | 0.091937 | 0.24727 | -0.040163 | 0.074307 | 0.036989 | -0.001407 | 0.043302 | 0.12817 | 0.026065 | -0.12294 | 119.459 | -1.8339 | 119.5689 | 119.532 | 0.072958 | -1.8169 | -1.6616 | 119.3763 | -1.8656 | 119.5735 | 119.4978 | 0.12153 | -1.7807 | -1.8828 | 119.5742 | 119.5911 | 119.7465 | 119.5189 | -1.949 | 119.5425 | 119.6274 | 119.5253 | 119.5362 | -2.0318
3722.7969 | 121.637 | -119.6411 | 1.8082 | 1.4211e-13 | 0.025442 | 0.016133 | 0.010109 | -0.023148 | 0.0044249 | 0.24021 | 0.024812 | 0.03439 | -0.096424 | -0.0027159 | 0.00064308 | 0.074302 | 0.019721 | 0.028217 | 0.084176 | 0.091937 | 0.24727 | -0.063057 | 0.074307 | 0.027831 | 0.003172 | 0.043302 | 0.12817 | 0.035222 | -0.12294 | 119.5781 | -1.724 | 119.7154 | 119.6693 | 0.091274 | -1.7162 | -1.5609 | 119.5182 | -1.7649 | 119.7154 | 119.6443 | 0.12611 | -1.68 | -1.7729 | 119.7253 | 119.7331 | 119.8884 | 119.6608 | -1.8712 | 119.6844 | 119.7693 | 119.6763 | 119.6689 | -1.9311
3724.5938 | 121.55 | -119.7372 | 1.7807 | 1.4211e-13 | 0.025442 | 0.016346 | 0.009682 | -0.023362 | 0.0048523 | 0.24021 | 0.024385 | 0.03439 | -0.09621 | -0.0027159 | 0.00042948 | 0.083459 | 0.019721 | 0.028217 | 0.07502 | 0.1011 | 0.24727 | -0.058478 | 0.078886 | 0.027831 | -0.001407 | 0.052459 | 0.11901 | 0.030644 | -0.11836 | 119.6788 | -1.7057 | 119.8207 | 119.7655 | 0.086695 | -1.6796 | -1.5334 | 119.6189 | -1.7282 | 119.8161 | 119.7358 | 0.11695 | -1.6617 | -1.7501 | 119.8123 | 119.8383 | 119.9845 | 119.757 | -1.8392 | 119.7897 | 119.8563 | 119.7679 | 119.7651 | -1.8991
3726.3281 | 121.6095 | -119.8425 | 1.6434 | 1.4211e-13 | 0.025228 | 0.016346 | 0.0098956 | -0.023362 | 0.0050659 | 0.24021 | 0.024598 | 0.034604 | -0.096424 | -0.0025021 | 0.0010705 | 0.074302 | 0.0243 | 0.028217 | 0.065863 | 0.091937 | 0.25185 | -0.053899 | 0.074307 | 0.03241 | 0.003172 | 0.043302 | 0.12359 | 0.030644 | -0.12294 | 119.7886 | -1.5775 | 119.9168 | 119.8707 | 0.082116 | -1.5514 | -1.3915 | 119.7196 | -1.6001 | 119.9168 | 119.8457 | 0.12611 | -1.5198 | -1.6127 | 119.9084 | 119.9345 | 120.0944 | 119.8668 | -1.6973 | 119.8858 | 119.9661 | 119.8732 | 119.8749 | -1.7663
3728.1094 | 121.5591 | -119.9524 | 1.5747 | 1.4211e-13 | 0.025442 | 0.016346 | 0.0098956 | -0.023148 | 0.0046387 | 0.24021 | 0.024812 | 0.03439 | -0.096424 | -0.0029295 | 0.00042948 | 0.074302 | 0.019721 | 0.028217 | 0.079598 | 0.096516 | 0.25185 | -0.040163 | 0.078886 | 0.03241 | 0.007751 | 0.043302 | 0.12359 | 0.026065 | -0.12752 | 119.9122 | -1.4951 | 120.0267 | 119.9806 | 0.06838 | -1.4782 | -1.3229 | 119.8249 | -1.5314 | 120.0313 | 119.9601 | 0.13527 | -1.4511 | -1.5486 | 120.032 | 120.0489 | 120.2042 | 119.9721 | -1.6149 | 119.9957 | 120.076 | 119.9785 | 119.9848 | -1.7022
3729.8906 | 121.6187 | -120.0302 | 1.506 | 1.4211e-13 | 0.025228 | 0.015919 | 0.010109 | -0.022935 | 0.0046387 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0031431 | 0.00042948 | 0.083459 | 0.019721 | 0.014482 | 0.07502 | 0.1011 | 0.25185 | -0.063057 | 0.078886 | 0.023253 | 0.003172 | 0.043302 | 0.12359 | 0.030644 | -0.12752 | 119.9672 | -1.431 | 120.1137 | 120.0447 | 0.077539 | -1.4049 | -1.2542 | 119.9027 | -1.4627 | 120.1091 | 120.0334 | 0.13069 | -1.3824 | -1.4754 | 120.1052 | 120.1313 | 120.2821 | 120.0499 | -1.5691 | 120.0735 | 120.1538 | 120.0609 | 120.0535 | -1.6336
3731.7031 | 121.6873 | -120.1309 | 1.3458 | 1.4211e-13 | 0.025656 | 0.016133 | 0.010109 | -0.023148 | 0.0046387 | 0.24021 | 0.024598 | 0.034818 | -0.096424 | -0.0027159 | 0.0010705 | 0.07888 | 0.0243 | 0.028217 | 0.07502 | 0.091937 | 0.24727 | -0.058478 | 0.078886 | 0.036989 | 0.007751 | 0.043302 | 0.12359 | 0.016908 | -0.11836 | 120.0724 | -1.2708 | 120.2098 | 120.1591 | 0.086695 | -1.2539 | -1.0986 | 120.0126 | -1.3025 | 120.2098 | 120.1387 | 0.12611 | -1.2222 | -1.3289 | 120.2059 | 120.2229 | 120.3782 | 120.1552 | -1.4043 | 120.1742 | 120.2545 | 120.1478 | 120.1679 | -1.4642
3733.5 | 121.6324 | -120.2866 | 1.2497 | 1.4211e-13 | 0.025442 | 0.016133 | 0.009682 | -0.023148 | 0.0046387 | 0.22495 | 0.024385 | 0.03439 | -0.096637 | -0.0027159 | 0.00085668 | 0.083459 | 0.015142 | 0.01906 | 0.07502 | 0.096516 | 0.25185 | -0.058478 | 0.074307 | 0.023253 | 0.01233 | 0.038723 | 0.11901 | 0.044379 | -0.11378 | 120.2281 | -1.1747 | 120.37 | 120.3056 | 0.077538 | -1.1532 | -0.99784 | 120.1728 | -1.211 | 120.3609 | 120.2989 | 0.12611 | -1.1307 | -1.2053 | 120.3616 | 120.3831 | 120.5384 | 120.3017 | -1.3082 | 120.3253 | 120.4056 | 120.3309 | 120.3098 | -1.3635
3735.2344 | 121.7422 | -120.3552 | 1.1215 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.023148 | 0.0046387 | 0.24021 | 0.024812 | 0.034604 | -0.096424 | -0.0029295 | 0.00064308 | 0.074302 | 0.0243 | 0.028217 | 0.065863 | 0.1011 | 0.24727 | -0.044742 | 0.078886 | 0.023253 | 0.003172 | 0.043302 | 0.11901 | 0.030644 | -0.11836 | 120.3105 | -1.0557 | 120.4295 | 120.3834 | 0.072959 | -1.0204 | -0.87425 | 120.2369 | -1.0782 | 120.4341 | 120.3584 | 0.12153 | -1.0025 | -1.0909 | 120.4211 | 120.4563 | 120.6025 | 120.3795 | -1.1663 | 120.3985 | 120.4742 | 120.3859 | 120.3785 | -1.2399
3737.0469 | 121.7285 | -120.4742 | 1.062 | 1.4211e-13 | 0.025015 | 0.016133 | 0.0094682 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034818 | -0.096424 | -0.0033569 | 0.00021588 | 0.074302 | 0.015142 | 0.028217 | 0.070441 | 0.1011 | 0.25185 | -0.053899 | 0.078886 | 0.03241 | 0.003172 | 0.038723 | 0.13275 | 0.039801 | -0.12752 | 120.4203 | -0.99157 | 120.5485 | 120.5025 | 0.082116 | -0.96092 | -0.81016 | 120.3467 | -1.0233 | 120.5531 | 120.4774 | 0.13069 | -0.92926 | -1.0222 | 120.5447 | 120.5753 | 120.7261 | 120.4894 | -1.1159 | 120.513 | 120.607 | 120.514 | 120.5067 | -1.1895
3738.8438 | 121.7331 | -120.4376 | 1.0529 | 1.4211e-13 | 0.025015 | 0.016774 | 0.0098956 | -0.023362 | 0.0044249 | 0.22495 | 0.024171 | 0.034818 | -0.096851 | -0.0027159 | 0.00042948 | 0.083459 | 0.0243 | 0.028217 | 0.07502 | 0.1011 | 0.24727 | -0.044742 | 0.083464 | 0.027831 | 0.003172 | 0.04788 | 0.13275 | 0.030644 | -0.12294 | 120.3929 | -0.97784 | 120.5211 | 120.4658 | 0.072959 | -0.95176 | -0.80558 | 120.3147 | -1.005 | 120.5211 | 120.4408 | 0.12611 | -0.92011 | -1.0222 | 120.5126 | 120.5387 | 120.6849 | 120.4619 | -1.0976 | 120.4855 | 120.5704 | 120.4683 | 120.4655 | -1.1758
3740.6406 | 121.6553 | -120.5063 | 1.0483 | 1.4211e-13 | 0.025442 | 0.01656 | 0.0098956 | -0.023362 | 0.0046387 | 0.23258 | 0.024385 | 0.034604 | -0.096637 | -0.0029295 | 0.00042948 | 0.074302 | 0.015142 | 0.028217 | 0.07502 | 0.091937 | 0.24727 | -0.044742 | 0.083464 | 0.036989 | 0.003172 | 0.038723 | 0.12359 | 0.026065 | -0.12294 | 120.4615 | -0.97326 | 120.5806 | 120.5345 | 0.072959 | -0.95634 | -0.801 | 120.3833 | -1.0096 | 120.5898 | 120.5095 | 0.12611 | -0.92469 | -1.0222 | 120.5813 | 120.5982 | 120.7536 | 120.5214 | -1.093 | 120.545 | 120.6299 | 120.5324 | 120.5433 | -1.1712
3742.3906 | 121.6187 | -120.3094 | 1.2405 | 1.4211e-13 | 0.025015 | 0.015919 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034818 | -0.097065 | -0.0031431 | 0.00085668 | 0.07888 | 0.0243 | 0.023639 | 0.079598 | 0.1011 | 0.24727 | -0.053899 | 0.069728 | 0.027831 | 0.007751 | 0.043302 | 0.12359 | 0.026065 | -0.12752 | 120.2555 | -1.1609 | 120.3883 | 120.3331 | 0.077538 | -1.1394 | -0.99327 | 120.1819 | -1.1972 | 120.3792 | 120.3172 | 0.13527 | -1.1169 | -1.2145 | 120.389 | 120.4105 | 120.5567 | 120.3337 | -1.2944 | 120.3528 | 120.433 | 120.3355 | 120.3373 | -1.3681
3744.1875 | 121.6141 | -120.2545 | 1.3367 | 1.4211e-13 | 0.025228 | 0.01656 | 0.010109 | -0.023362 | 0.0050659 | 0.24021 | 0.024812 | 0.034604 | -0.096851 | -0.0029295 | 0.00042948 | 0.083459 | 0.0243 | 0.028217 | 0.07502 | 0.096516 | 0.24727 | -0.053899 | 0.078886 | 0.03241 | 0.003172 | 0.038723 | 0.13733 | 0.026065 | -0.12294 | 120.2006 | -1.2616 | 120.338 | 120.2827 | 0.082116 | -1.2402 | -1.0894 | 120.1316 | -1.2979 | 120.3334 | 120.2577 | 0.12611 | -1.1993 | -1.3106 | 120.3295 | 120.351 | 120.5018 | 120.2788 | -1.3906 | 120.2932 | 120.3918 | 120.2806 | 120.2869 | -1.4596
3745.9844 | 121.7148 | -120.2454 | 1.3412 | 1.4211e-13 | 0.025228 | 0.015919 | 0.010109 | -0.023362 | 0.0048523 | 0.23258 | 0.024171 | 0.034818 | -0.096424 | -0.0031431 | 0.00064308 | 0.07888 | 0.019721 | 0.028217 | 0.061284 | 0.096516 | 0.25185 | -0.053899 | 0.074307 | 0.027831 | -0.001407 | 0.043302 | 0.13733 | 0.026065 | -0.11836 | 120.1915 | -1.28 | 120.3242 | 120.2736 | 0.082116 | -1.2447 | -1.0894 | 120.127 | -1.2979 | 120.3197 | 120.244 | 0.11695 | -1.2039 | -1.3152 | 120.3066 | 120.3419 | 120.4972 | 120.2651 | -1.3951 | 120.2887 | 120.3827 | 120.2714 | 120.2732 | -1.4596
3747.7656 | 121.6644 | -120.1447 | 1.4557 | 1.4211e-13 | 0.025442 | 0.016346 | 0.0098956 | -0.023576 | 0.0046387 | 0.23258 | 0.024385 | 0.034818 | -0.096424 | -0.0029295 | 0.00085668 | 0.07888 | 0.010564 | 0.023639 | 0.07502 | 0.096516 | 0.24269 | -0.063057 | 0.078886 | 0.027831 | 0.003172 | 0.043302 | 0.13733 | 0.035222 | -0.12294 | 120.0816 | -1.3807 | 120.2235 | 120.1683 | 0.086696 | -1.3592 | -1.213 | 120.0217 | -1.4124 | 120.2235 | 120.1478 | 0.12611 | -1.3184 | -1.4205 | 120.2197 | 120.2412 | 120.3873 | 120.1552 | -1.5187 | 120.188 | 120.282 | 120.1799 | 120.1725 | -1.5786
3749.5625 | 121.6873 | -120.0577 | 1.4877 | 1.4211e-13 | 0.025442 | 0.016133 | 0.0098956 | -0.023576 | 0.0046387 | 0.23258 | 0.024598 | 0.034604 | -0.096851 | -0.0027159 | 0.00085668 | 0.07888 | 0.0243 | 0.028217 | 0.07502 | 0.10567 | 0.25185 | -0.063057 | 0.074307 | 0.023253 | 0.003172 | 0.043302 | 0.12817 | 0.030644 | -0.11378 | 119.9946 | -1.4127 | 120.1366 | 120.0859 | 0.091274 | -1.3821 | -1.2359 | 119.9439 | -1.4444 | 120.132 | 120.0609 | 0.11695 | -1.3596 | -1.4571 | 120.1327 | 120.1634 | 120.3095 | 120.082 | -1.5508 | 120.101 | 120.1859 | 120.0883 | 120.0809 | -1.6015
3751.3438 | 121.6553 | -119.9478 | 1.6388 | 1.4211e-13 | 0.025015 | 0.016133 | 0.009682 | -0.023148 | 0.0046387 | 0.24021 | 0.024171 | 0.034818 | -0.096851 | -0.0029295 | 0.00085668 | 0.074302 | 0.019721 | 0.01906 | 0.07502 | 0.096516 | 0.24727 | -0.063057 | 0.078886 | 0.027831 | 0.003172 | 0.04788 | 0.13275 | 0.048958 | -0.12752 | 119.8848 | -1.5638 | 120.0221 | 119.9669 | 0.082117 | -1.5423 | -1.3915 | 119.8203 | -1.5909 | 120.0267 | 119.951 | 0.13069 | -1.506 | -1.5898 | 120.0228 | 120.0443 | 120.1951 | 119.9675 | -1.7019 | 119.9957 | 120.0806 | 119.9968 | 119.9756 | -1.7663
3753.0781 | 121.7148 | -120.0531 | 1.5381 | 1.4211e-13 | 0.025442 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.24784 | 0.024385 | 0.034604 | -0.096851 | -0.0029295 | 0.00064308 | 0.07888 | 0.019721 | 0.028217 | 0.070441 | 0.096516 | 0.24727 | -0.049321 | 0.078886 | 0.023253 | -0.001407 | 0.043302 | 0.12817 | 0.035222 | -0.12752 | 120.0038 | -1.4676 | 120.132 | 120.0813 | 0.077538 | -1.4416 | -1.2908 | 119.9256 | -1.4948 | 120.132 | 120.0517 | 0.12611 | -1.4099 | -1.5029 | 120.1235 | 120.1496 | 120.3004 | 120.0728 | -1.5874 | 120.0964 | 120.1813 | 120.0883 | 120.0764 | -1.6656
3754.8438 | 121.7697 | -120.0623 | 1.4969 | 1.4211e-13 | 0.025228 | 0.016133 | 0.009682 | -0.023576 | 0.0048523 | 0.24021 | 0.024812 | 0.034818 | -0.096424 | -0.0025021 | 0.00064308 | 0.074302 | 0.019721 | 0.023639 | 0.065863 | 0.1011 | 0.24727 | -0.035584 | 0.074307 | 0.027831 | -0.001407 | 0.038723 | 0.12817 | 0.030644 | -0.12294 | 120.0267 | -1.431 | 120.1366 | 120.0859 | 0.059223 | -1.3958 | -1.2496 | 119.9393 | -1.4582 | 120.1366 | 120.0608 | 0.12153 | -1.3687 | -1.4662 | 120.1281 | 120.1634 | 120.3095 | 120.082 | -1.5325 | 120.101 | 120.1904 | 120.0929 | 120.0901 | -1.6198
3756.6562 | 121.7926 | -120.1126 | 1.4465 | 1.4211e-13 | 0.025228 | 0.016133 | 0.009682 | -0.023362 | 0.0046387 | 0.23258 | 0.024812 | 0.034818 | -0.096424 | -0.0029295 | 0.00064308 | 0.07888 | 0.019721 | 0.023639 | 0.070441 | 0.11025 | 0.24269 | -0.044742 | 0.074307 | 0.023253 | 0.01233 | 0.043302 | 0.12359 | 0.030644 | -0.12294 | 120.0679 | -1.3761 | 120.1915 | 120.1362 | 0.068381 | -1.3363 | -1.2038 | 119.9897 | -1.4032 | 120.1869 | 120.1249 | 0.13527 | -1.3229 | -1.4159 | 120.1831 | 120.2229 | 120.3553 | 120.1323 | -1.4913 | 120.1559 | 120.2362 | 120.1433 | 120.1359 | -1.5695
3758.4531 | 121.8018 | -120.1401 | 1.4008 | 1.4211e-13 | 0.025442 | 0.016346 | 0.009682 | -0.023148 | 0.0048523 | 0.24784 | 0.025025 | 0.034604 | -0.096637 | -0.0027159 | 0.00064308 | 0.07888 | 0.015142 | 0.023639 | 0.07502 | 0.091937 | 0.24727 | -0.049321 | 0.078886 | 0.027831 | -0.001407 | 0.043302 | 0.11901 | 0.026065 | -0.12294 | 120.0908 | -1.3257 | 120.219 | 120.1637 | 0.07296 | -1.3088 | -1.1535 | 120.0171 | -1.3575 | 120.219 | 120.1387 | 0.12153 | -1.2817 | -1.3747 | 120.2151 | 120.232 | 120.3873 | 120.1552 | -1.4501 | 120.1834 | 120.2591 | 120.1661 | 120.1679 | -1.5237
3760.2031 | 121.669 | -120.2316 | 1.3916 | 1.4211e-13 | 0.025015 | 0.016346 | 0.0094682 | -0.023362 | 0.0048523 | 0.24021 | 0.024385 | 0.034818 | -0.096424 | -0.0029295 | 0.00064308 | 0.07888 | 0.010564 | 0.023639 | 0.079598 | 0.096516 | 0.25185 | -0.044742 | 0.074307 | 0.027831 | 0.007751 | 0.043302 | 0.12359 | 0.030644 | -0.12294 | 120.1869 | -1.312 | 120.3105 | 120.2553 | 0.068381 | -1.2951 | -1.1398 | 120.1087 | -1.3483 | 120.3059 | 120.2394 | 0.13069 | -1.268 | -1.361 | 120.3112 | 120.3281 | 120.4835 | 120.2422 | -1.4363 | 120.2749 | 120.3552 | 120.2623 | 120.2595 | -1.5145
3762 | 121.7285 | -120.2957 | 1.3412 | 1.4211e-13 | 0.025228 | 0.016133 | 0.0098956 | -0.023148 | 0.0046387 | 0.24021 | 0.024385 | 0.03439 | -0.096637 | -0.0031431 | 0.00064308 | 0.083459 | 0.010564 | 0.023639 | 0.079598 | 0.091937 | 0.25185 | -0.035584 | 0.083464 | 0.027831 | 0.007751 | 0.043302 | 0.11901 | 0.039801 | -0.12294 | 120.2601 | -1.2616 | 120.3792 | 120.3194 | 0.059223 | -1.2493 | -1.0894 | 120.1728 | -1.2979 | 120.3792 | 120.3035 | 0.13069 | -1.2222 | -1.3014 | 120.3753 | 120.3877 | 120.5476 | 120.3063 | -1.3768 | 120.339 | 120.4147 | 120.3355 | 120.3235 | -1.4642
3763.7812 | 121.8063 | -120.3049 | 1.2543 | 1.4211e-13 | 0.025228 | 0.016133 | 0.009682 | -0.023148 | 0.0046387 | 0.23258 | 0.024171 | 0.034604 | -0.096851 | -0.0031431 | 0.00085668 | 0.069723 | 0.019721 | 0.028217 | 0.070441 | 0.096516 | 0.24727 | -0.053899 | 0.074307 | 0.027831 | 0.003172 | 0.034145 | 0.11901 | 0.035222 | -0.11836 | 120.251 | -1.1838 | 120.3746 | 120.3331 | 0.082116 | -1.1578 | -1.007 | 120.1865 | -1.2201 | 120.3792 | 120.308 | 0.12153 | -1.1353 | -1.219 | 120.3753 | 120.4014 | 120.5521 | 120.3246 | -1.3082 | 120.339 | 120.4239 | 120.3401 | 120.3327 | -1.3726
3765.5156 | 121.7468 | -120.3506 | 1.2726 | 1.4211e-13 | 0.025015 | 0.016346 | 0.009682 | -0.023362 | 0.0044249 | 0.24021 | 0.024598 | 0.034604 | -0.096424 | -0.0031431 | 0.00085668 | 0.07888 | 0.015142 | 0.023639 | 0.07502 | 0.091937 | 0.25185 | -0.063057 | 0.083464 | 0.03241 | 0.003172 | 0.04788 | 0.12817 | 0.026065 | -0.11836 | 120.2876 | -1.1976 | 120.4295 | 120.3743 | 0.086696 | -1.1806 | -1.0207 | 120.2323 | -1.2247 | 120.4341 | 120.3538 | 0.12153 | -1.1444 | -1.2465 | 120.4257 | 120.4426 | 120.6025 | 120.3658 | -1.3356 | 120.3985 | 120.4788 | 120.3767 | 120.3831 | -1.3909
3768.625 | 121.8201 | -120.3827 | 1.2131 | 1.4211e-13 | 0.025442 | 0.016133 | 0.0098956 | -0.023148 | 0.0050659 | 0.24021 | 0.024598 | 0.034604 | -0.096637 | -0.0031431 | 0.00064308 | 0.074302 | 0.019721 | 0.028217 | 0.07502 | 0.1011 | 0.25185 | -0.058478 | 0.074307 | 0.027831 | 0.003172 | 0.043302 | 0.12359 | 0.048958 | -0.11836 | 120.3242 | -1.1381 | 120.457 | 120.4109 | 0.086695 | -1.112 | -0.96122 | 120.2643 | -1.1698 | 120.457 | 120.3859 | 0.12153 | -1.0895 | -1.1641 | 120.4577 | 120.4838 | 120.6345 | 120.4024 | -1.2716 | 120.426 | 120.5063 | 120.4316 | 120.4105 | -1.3314
3772.7188 | 121.6873 | -118.7576 | 2.8976 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0098956 | -0.022935 | 0.0048523 | 0.24021 | 0.024385 | 0.034818 | -0.096637 | -0.0027159 | 0.00042948 | 0.07888 | 0.015142 | 0.01906 | 0.070441 | 0.096516 | 0.25185 | -0.053899 | 0.083464 | 0.023253 | 0.003172 | 0.04788 | 0.12359 | 0.030644 | -0.11836 | 118.7037 | -2.8272 | 118.8365 | 118.7767 | 0.072959 | -2.8011 | -2.6458 | 118.6393 | -2.8498 | 118.8411 | 118.7608 | 0.12153 | -2.7741 | -2.867 | 118.8281 | 118.8541 | 119.0095 | 118.7728 | -2.9515 | 118.8055 | 118.8812 | 118.7883 | 118.7809 | -3.016
3778.875 | 121.8155 | -118.1305 | 3.4058 | 1.4211e-13 | 0.025228 | 0.016133 | 0.009682 | -0.023362 | 0.0050659 | 0.24021 | 0.024812 | 0.035031 | -0.096851 | -0.0029295 | 0.00042948 | 0.074302 | 0.010564 | 0.01906 | 0.065863 | 0.096516 | 0.25643 | -0.026426 | 0.078886 | 0.023253 | -0.001407 | 0.038723 | 0.12359 | 0.026065 | -0.11836 | 118.1041 | -3.3399 | 118.2048 | 118.1496 | 0.045486 | -3.3092 | -3.1493 | 118.0121 | -3.367 | 118.2094 | 118.1291 | 0.11695 | -3.2822 | -3.3797 | 118.1964 | 118.227 | 118.3869 | 118.1411 | -3.4322 | 118.1692 | 118.2541 | 118.1566 | 118.1537 | -3.5241
3780.8281 | 121.6782 | -118.6066 | 3.0533 | 1.4211e-13 | 0.025015 | 0.016346 | 0.0098956 | -0.023148 | 0.0046387 | 0.23258 | 0.024598 | 0.034818 | -0.096851 | -0.0031431 | 0.00064308 | 0.074302 | 0.010564 | 0.014482 | 0.070441 | 0.096516 | 0.24269 | -0.063057 | 0.074307 | 0.027831 | 0.007751 | 0.038723 | 0.11901 | 0.026065 | -0.11378 | 118.5435 | -2.9828 | 118.6809 | 118.621 | 0.077539 | -2.9568 | -2.8106 | 118.4928 | -3.0146 | 118.6809 | 118.6143 | 0.12153 | -2.9343 | -3.0272 | 118.677 | 118.7031 | 118.8493 | 118.6171 | -3.1163 | 118.6453 | 118.7256 | 118.6326 | 118.6344 | -3.1671
3782.6562 | 121.6873 | -119.2474 | 2.3529 | 1.4211e-13 | 0.025228 | 0.016133 | 0.0094682 | -0.023362 | 0.0048523 | 0.24021 | 0.024812 | 0.035031 | -0.096851 | -0.0033569 | 0.00064308 | 0.07888 | 0.015142 | 0.028217 | 0.070441 | 0.091937 | 0.24727 | -0.053899 | 0.074307 | 0.027831 | 0.003172 | 0.043302 | 0.11901 | 0.030644 | -0.12294 | 119.1935 | -2.2825 | 119.3263 | 119.2757 | 0.082116 | -2.261 | -2.1056 | 119.1245 | -2.3096 | 119.3217 | 119.2506 | 0.12611 | -2.2339 | -2.3223 | 119.3179 | 119.3394 | 119.4947 | 119.2626 | -2.4068 | 119.2907 | 119.3665 | 119.2781 | 119.2753 | -2.4758
3784.4531 | 121.7651 | -118.7256 | 2.8061 | 1.4211e-13 | 0.025656 | 0.015919 | 0.0098956 | -0.023148 | 0.0046387 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0029295 | 0.00085668 | 0.07888 | 0.019721 | 0.028217 | 0.07502 | 0.091937 | 0.24727 | -0.035584 | 0.078886 | 0.023253 | -0.001407 | 0.04788 | 0.12359 | 0.030644 | -0.11836 | 118.69 | -2.7311 | 118.8045 | 118.7538 | 0.063801 | -2.7142 | -2.5588 | 118.6072 | -2.7582 | 118.8045 | 118.7242 | 0.11695 | -2.6825 | -2.7754 | 118.8006 | 118.8175 | 118.9729 | 118.7453 | -2.8417 | 118.7735 | 118.8492 | 118.7562 | 118.7488 | -2.9245
3786.1875 | 121.6507 | -119.8883 | 1.7715 | 1.4211e-13 | 0.025228 | 0.016346 | 0.010109 | -0.023362 | 0.0050659 | 0.24021 | 0.024598 | 0.034604 | -0.096851 | -0.0031431 | 0.00085668 | 0.07888 | 0.0243 | 0.028217 | 0.070441 | 0.091937 | 0.24727 | -0.044742 | 0.078886 | 0.027831 | 0.003172 | 0.043302 | 0.13275 | 0.026065 | -0.12752 | 119.8436 | -1.7011 | 119.9672 | 119.9165 | 0.072959 | -1.6796 | -1.5243 | 119.7608 | -1.7282 | 119.9672 | 119.8915 | 0.13069 | -1.6388 | -1.7455 | 119.9587 | 119.9802 | 120.1356 | 119.9126 | -1.8163 | 119.9316 | 120.0211 | 119.9144 | 119.9161 | -1.8991
3787.9688 | 121.7377 | -120.282 | 1.3596 | 1.4211e-13 | 0.025015 | 0.015919 | 0.009682 | -0.023362 | 0.0048523 | 0.23258 | 0.024812 | 0.034818 | -0.096637 | -0.0031431 | 0.0010705 | 0.074302 | 0.015142 | 0.023639 | 0.070441 | 0.087359 | 0.24727 | -0.053899 | 0.074307 | 0.027831 | 0.007751 | 0.043302 | 0.11901 | 0.030644 | -0.12294 | 120.2281 | -1.2891 | 120.3563 | 120.3056 | 0.077538 | -1.2722 | -1.1123 | 120.159 | -1.3163 | 120.3563 | 120.2897 | 0.13069 | -1.2405 | -1.3289 | 120.3524 | 120.3693 | 120.5293 | 120.2971 | -1.4135 | 120.3253 | 120.401 | 120.3126 | 120.3098 | -1.4825
3789.7656 | 121.8475 | -120.6757 | 0.93842 | 1.4211e-13 | 0.025442 | 0.01656 | 0.009682 | -0.023148 | 0.0050659 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0029295 | 0.00042948 | 0.07888 | 0.019721 | 0.01906 | 0.07502 | 0.091937 | 0.25185 | -0.035584 | 0.074307 | 0.018674 | -0.001407 | 0.043302 | 0.12359 | 0.021486 | -0.11836 | 120.6401 | -0.8634 | 120.7545 | 120.6947 | 0.054644 | -0.84648 | -0.68656 | 120.5573 | -0.89511 | 120.75 | 120.6743 | 0.11695 | -0.81482 | -0.91693 | 120.7507 | 120.7676 | 120.9275 | 120.6954 | -0.974 | 120.719 | 120.7993 | 120.6971 | 120.6943 | -1.0568
3791.5 | 121.7834 | -120.3964 | 1.2451 | 1.4211e-13 | 0.025015 | 0.016133 | 0.009682 | -0.023362 | 0.0046387 | 0.23258 | 0.024598 | 0.035031 | -0.096637 | -0.0029295 | 0.00085668 | 0.07888 | 0.019721 | 0.023639 | 0.065863 | 0.091937 | 0.24727 | -0.058478 | 0.078886 | 0.023253 | -0.001407 | 0.043302 | 0.13275 | 0.026065 | -0.12294 | 120.3379 | -1.1793 | 120.4753 | 120.4201 | 0.082117 | -1.1532 | -0.99784 | 120.2735 | -1.2018 | 120.4753 | 120.395 | 0.12153 | -1.1124 | -1.2191 | 120.4623 | 120.4884 | 120.6437 | 120.4161 | -1.3036 | 120.4397 | 120.5292 | 120.4225 | 120.4197 | -1.3681
3793.2344 | 121.7331 | -119.4443 | 2.2018 | 1.4211e-13 | 0.025228 | 0.016133 | 0.0098956 | -0.023362 | 0.0044249 | 0.23258 | 0.024812 | 0.034604 | -0.096637 | -0.0031431 | 0.00085668 | 0.074302 | 0.019721 | 0.032795 | 0.07502 | 0.096516 | 0.24727 | -0.044742 | 0.074307 | 0.027831 | 0.007751 | 0.043302 | 0.12359 | 0.030644 | -0.11836 | 119.3995 | -2.1268 | 119.5186 | 119.4771 | 0.077537 | -2.1053 | -1.9546 | 119.3259 | -2.1585 | 119.5186 | 119.452 | 0.12611 | -2.0783 | -2.1712 | 119.5193 | 119.5408 | 119.6915 | 119.464 | -2.2466 | 119.4876 | 119.5679 | 119.4749 | 119.4721 | -2.3202
3794.9688 | 121.8063 | -118.9224 | 2.6276 | 1.4211e-13 | 0.025656 | 0.01656 | 0.009682 | -0.023362 | 0.0046387 | 0.24021 | 0.024598 | 0.034604 | -0.096424 | -0.0033569 | 0.00085668 | 0.07888 | 0.015142 | 0.023639 | 0.070441 | 0.1011 | 0.24727 | -0.044742 | 0.083464 | 0.023253 | -0.001407 | 0.043302 | 0.12359 | 0.026065 | -0.1321 | 118.8777 | -2.5571 | 119.0013 | 118.9461 | 0.068381 | -2.5265 | -2.3803 | 118.7903 | -2.5843 | 119.0059 | 118.921 | 0.13069 | -2.504 | -2.6015 | 118.9929 | 119.0235 | 119.1697 | 118.9376 | -2.6723 | 118.9657 | 119.046 | 118.9485 | 118.9457 | -2.7597
3796.75 | 121.6278 | -118.5471 | 3.0762 | 1.4211e-13 | 0.025228 | 0.015705 | 0.0098956 | -0.023576 | 0.0046387 | 0.24784 | 0.024598 | 0.03439 | -0.096637 | -0.0027159 | 0.00064308 | 0.07888 | 0.015142 | 0.028217 | 0.07502 | 0.096516 | 0.24727 | -0.063057 | 0.074307 | 0.027831 | 0.003172 | 0.043302 | 0.11901 | 0.026065 | -0.12294 | 118.484 | -3.0012 | 118.6259 | 118.5753 | 0.091274 | -2.9797 | -2.8289 | 118.4241 | -3.0329 | 118.6214 | 118.5502 | 0.12611 | -2.9572 | -3.0501 | 118.6221 | 118.6436 | 118.7943 | 118.5622 | -3.1392 | 118.5904 | 118.6661 | 118.5731 | 118.5749 | -3.1991
3798.4844 | 121.6873 | -117.4988 | 4.0146 | 1.4211e-13 | 0.025228 | 0.016346 | 0.0098956 | -0.023148 | 0.0048523 | 0.24784 | 0.023957 | 0.034604 | -0.096637 | -0.0027159 | 0.0010705 | 0.069723 | 0.019721 | 0.01906 | 0.070441 | 0.091937 | 0.24727 | -0.053899 | 0.074307 | 0.027831 | 0.003172 | 0.043302 | 0.12817 | 0.030644 | -0.11836 | 117.4449 | -3.9441 | 117.5685 | 117.5178 | 0.072959 | -3.9226 | -3.7673 | 117.3804 | -3.9713 | 117.5731 | 117.502 | 0.12153 | -3.8864 | -3.9839 | 117.5692 | 117.5907 | 117.7461 | 117.5185 | -4.0685 | 117.5421 | 117.627 | 117.5294 | 117.5266 | -4.1329
3800.2344 | 121.8338 | -118.7119 | 2.861 | 1.4211e-13 | 0.025656 | 0.016133 | 0.009682 | -0.023148 | 0.0046387 | 0.25547 | 0.024171 | 0.035031 | -0.096637 | -0.0033569 | 0.00064308 | 0.074302 | 0.019721 | 0.023639 | 0.070441 | 0.1011 | 0.24269 | -0.063057 | 0.074307 | 0.027831 | 0.003172 | 0.052459 | 0.12359 | 0.026065 | -0.11836 | 118.6488 | -2.7906 | 118.7862 | 118.7355 | 0.086696 | -2.7599 | -2.6183 | 118.5935 | -2.8086 | 118.7862 | 118.715 | 0.12153 | -2.7374 | -2.835 | 118.7823 | 118.8129 | 118.9545 | 118.7316 | -2.9241 | 118.7643 | 118.8354 | 118.7379 | 118.7397 | -2.9794
3801.9688 | 121.6782 | -119.3481 | 2.1744 | 1.4211e-13 | 0.025228 | 0.01656 | 0.009682 | -0.023362 | 0.0048523 | 0.24784 | 0.024385 | 0.034818 | -0.096637 | -0.0029295 | 0.00085668 | 0.074302 | 0.019721 | 0.01906 | 0.07502 | 0.096516 | 0.24727 | -0.067636 | 0.074307 | 0.027831 | -0.001407 | 0.043302 | 0.12359 | 0.026065 | -0.11378 | 119.2805 | -2.0994 | 119.4224 | 119.3672 | 0.086696 | -2.0779 | -1.9271 | 119.2344 | -2.1311 | 119.4225 | 119.3467 | 0.11237 | -2.0508 | -2.1483 | 119.4232 | 119.4447 | 119.5954 | 119.3679 | -2.242 | 119.3914 | 119.4717 | 119.3742 | 119.376 | -2.2882
3803.7656 | 121.8063 | -118.9224 | 2.5406 | 1.4211e-13 | 0.025442 | 0.016346 | 0.009682 | -0.023362 | 0.0048523 | 0.22495 | 0.024171 | 0.034604 | -0.097065 | -0.0031431 | 0.00064308 | 0.083459 | 0.019721 | 0.023639 | 0.07502 | 0.091937 | 0.25185 | -0.063057 | 0.074307 | 0.023253 | 0.003172 | 0.038723 | 0.12359 | 0.044379 | -0.11378 | 118.8594 | -2.4656 | 119.0059 | 118.9461 | 0.086696 | -2.4487 | -2.2887 | 118.8086 | -2.5019 | 118.9967 | 118.9256 | 0.11695 | -2.417 | -2.4962 | 118.9974 | 119.0144 | 119.1743 | 118.9421 | -2.6036 | 118.9611 | 119.046 | 118.9668 | 118.9457 | -2.6544
3805.5625 | 121.7606 | -121.312 | 0.3891 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0094682 | -0.023576 | 0.0046387 | 0.24021 | 0.024385 | 0.034604 | -0.096851 | -0.0029295 | 0.0010705 | 0.07888 | 0.019721 | 0.01906 | 0.07502 | 0.091937 | 0.24269 | -0.049321 | 0.074307 | 0.027831 | -0.001407 | 0.038723 | 0.12359 | 0.039801 | -0.11836 | 121.2626 | -0.31408 | 121.3908 | 121.331 | 0.068381 | -0.29716 | -0.1464 | 121.1936 | -0.35038 | 121.3863 | 121.3105 | 0.11695 | -0.26551 | -0.3493 | 121.387 | 121.4039 | 121.5546 | 121.3317 | -0.43842 | 121.3507 | 121.4355 | 121.3518 | 121.3398 | -0.50746
3807.3594 | 121.8018 | -121.2891 | 0.3891 | 1.4211e-13 | 0.025228 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.024385 | 0.034604 | -0.096851 | -0.0029295 | 0.00064308 | 0.07888 | 0.015142 | 0.01906 | 0.070441 | 0.096516 | 0.24727 | -0.049321 | 0.074307 | 0.027831 | 0.01233 | 0.043302 | 0.12359 | 0.030644 | -0.11836 | 121.2397 | -0.31866 | 121.3679 | 121.3081 | 0.068381 | -0.29258 | -0.14182 | 121.1707 | -0.3458 | 121.3634 | 121.3014 | 0.13069 | -0.26551 | -0.35845 | 121.3595 | 121.3856 | 121.5363 | 121.3042 | -0.43842 | 121.3324 | 121.4127 | 121.3197 | 121.3169 | -0.50746
3809.1719 | 121.8109 | -121.2936 | 0.39368 | 1.4211e-13 | 0.025228 | 0.015919 | 0.010109 | -0.022935 | 0.0048523 | 0.22495 | 0.024171 | 0.035031 | -0.096851 | -0.0033569 | 0.00042948 | 0.07888 | 0.019721 | 0.023639 | 0.07502 | 0.096516 | 0.24727 | -0.058478 | 0.078886 | 0.03241 | 0.007751 | 0.038723 | 0.12359 | 0.030644 | -0.11378 | 121.2352 | -0.31866 | 121.3725 | 121.3173 | 0.082117 | -0.29716 | -0.1464 | 121.1799 | -0.35495 | 121.3725 | 121.3014 | 0.12153 | -0.27008 | -0.36303 | 121.3687 | 121.3902 | 121.5409 | 121.3134 | -0.45215 | 121.3324 | 121.4172 | 121.3243 | 121.326 | -0.50746
3810.9688 | 121.8796 | -121.2753 | 0.3479 | 1.4211e-13 | 0.025228 | 0.016133 | 0.0098956 | -0.022935 | 0.0046387 | 0.24021 | 0.024385 | 0.035031 | -0.096637 | -0.0033569 | 0.00085668 | 0.083459 | 0.0243 | 0.028217 | 0.07502 | 0.096516 | 0.25185 | -0.040163 | 0.078886 | 0.03241 | 0.007751 | 0.038723 | 0.11901 | 0.030644 | -0.12294 | 121.2352 | -0.27288 | 121.3588 | 121.3035 | 0.06838 | -0.25138 | -0.096048 | 121.1524 | -0.30918 | 121.3542 | 121.2831 | 0.13069 | -0.22889 | -0.31726 | 121.3503 | 121.3718 | 121.5272 | 121.2996 | -0.38806 | 121.3141 | 121.3943 | 121.306 | 121.3077 | -0.47084
3812.75 | 121.8887 | -121.2753 | 0.37079 | 1.4211e-13 | 0.025228 | 0.016346 | 0.009682 | -0.023576 | 0.0046387 | 0.24784 | 0.024385 | 0.034604 | -0.096424 | -0.0031431 | 0.00064308 | 0.083459 | 0.019721 | 0.023639 | 0.070441 | 0.1011 | 0.24269 | -0.049321 | 0.083464 | 0.03241 | 0.003172 | 0.043302 | 0.11901 | 0.026065 | -0.11378 | 121.226 | -0.30035 | 121.3588 | 121.299 | 0.07296 | -0.26969 | -0.12809 | 121.1615 | -0.32749 | 121.3588 | 121.2785 | 0.11695 | -0.25177 | -0.34472 | 121.3458 | 121.3764 | 121.518 | 121.2951 | -0.42011 | 121.3186 | 121.3943 | 121.3014 | 121.3077 | -0.48457
3814.5469 | 121.8613 | -121.2845 | 0.40741 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.23258 | 0.024385 | 0.035031 | -0.096851 | -0.0029295 | 0.00064308 | 0.07888 | 0.015142 | 0.023639 | 0.065863 | 0.091937 | 0.25643 | -0.035584 | 0.078886 | 0.027831 | 0.007751 | 0.04788 | 0.12359 | 0.021486 | -0.12752 | 121.2489 | -0.34155 | 121.3634 | 121.3081 | 0.059223 | -0.31547 | -0.15098 | 121.157 | -0.35953 | 121.3634 | 121.2922 | 0.13527 | -0.28382 | -0.38592 | 121.3503 | 121.3764 | 121.5409 | 121.2996 | -0.44299 | 121.3324 | 121.4081 | 121.306 | 121.3123 | -0.53493
3816.2812 | 121.9208 | -121.2936 | 0.37994 | 1.4211e-13 | 0.025015 | 0.016346 | 0.009682 | -0.023362 | 0.0048523 | 0.24021 | 0.024385 | 0.034818 | -0.096851 | -0.0029295 | 0.00085668 | 0.083459 | 0.019721 | 0.023639 | 0.07502 | 0.091937 | 0.24269 | -0.044742 | 0.078886 | 0.023253 | -0.001407 | 0.043302 | 0.11444 | 0.039801 | -0.11378 | 121.2489 | -0.30492 | 121.3771 | 121.3173 | 0.068381 | -0.28801 | -0.13725 | 121.1799 | -0.33664 | 121.3725 | 121.2922 | 0.11237 | -0.26551 | -0.34014 | 121.3687 | 121.3856 | 121.5363 | 121.3134 | -0.42469 | 121.3369 | 121.4081 | 121.3334 | 121.3169 | -0.49373
3818.0156 | 121.875 | -121.2982 | 0.41657 | 1.4211e-13 | 0.025228 | 0.016133 | 0.009682 | -0.023576 | 0.0044249 | 0.24021 | 0.024598 | 0.034604 | -0.096851 | -0.0031431 | 0.00021588 | 0.07888 | 0.015142 | 0.023639 | 0.07502 | 0.1011 | 0.26101 | -0.053899 | 0.074307 | 0.03241 | 0.003172 | 0.038723 | 0.11901 | 0.026065 | -0.12294 | 121.2443 | -0.34154 | 121.3771 | 121.3219 | 0.077538 | -0.31547 | -0.15555 | 121.1753 | -0.37784 | 121.3725 | 121.3014 | 0.12611 | -0.29755 | -0.3905 | 121.3732 | 121.3993 | 121.5592 | 121.3134 | -0.47046 | 121.3369 | 121.4172 | 121.3243 | 121.3306 | -0.5395
3819.75 | 121.9025 | -121.2708 | 0.40283 | 1.4211e-13 | 0.025442 | 0.016346 | 0.009682 | -0.023148 | 0.0050659 | 0.23258 | 0.024598 | 0.034818 | -0.096637 | -0.0031431 | 0.00085668 | 0.083459 | 0.019721 | 0.01906 | 0.07502 | 0.1011 | 0.24727 | -0.058478 | 0.078886 | 0.027831 | 0.016908 | 0.038723 | 0.12359 | 0.026065 | -0.11836 | 121.2123 | -0.32781 | 121.3542 | 121.2898 | 0.077538 | -0.30174 | -0.15556 | 121.1524 | -0.36411 | 121.3496 | 121.2877 | 0.13527 | -0.27924 | -0.37677 | 121.3458 | 121.3718 | 121.518 | 121.2905 | -0.46131 | 121.3095 | 121.3943 | 121.2968 | 121.2986 | -0.52119
3821.4844 | 121.7102 | -118.1259 | 3.5431 | 1.4211e-13 | 0.025656 | 0.015919 | 0.0098956 | -0.023362 | 0.0048523 | 0.24021 | 0.023957 | 0.034818 | -0.096851 | -0.0031431 | 0.00064308 | 0.07888 | 0.015142 | 0.01906 | 0.065863 | 0.1011 | 0.24727 | -0.072215 | 0.069728 | 0.027831 | 0.003172 | 0.038723 | 0.12359 | 0.035222 | -0.11378 | 118.0537 | -3.4772 | 118.2048 | 118.145 | 0.091275 | -3.442 | -3.2958 | 118.0121 | -3.5044 | 118.1956 | 118.1291 | 0.11695 | -3.4195 | -3.5079 | 118.1918 | 118.227 | 118.3732 | 118.1411 | -3.6153 | 118.1646 | 118.2495 | 118.1611 | 118.1537 | -3.6569
3823.2812 | 121.788 | -118.0573 | 3.598 | 1.4211e-13 | 0.025228 | 0.016133 | 0.0098956 | -0.022935 | 0.0050659 | 0.23258 | 0.024385 | 0.034604 | -0.096637 | -0.0033569 | 0.00064308 | 0.074302 | 0.019721 | 0.023639 | 0.07502 | 0.1011 | 0.24727 | -0.053899 | 0.069728 | 0.023253 | 0.003172 | 0.043302 | 0.12359 | 0.039801 | -0.12294 | 118.0034 | -3.523 | 118.1316 | 118.0809 | 0.077538 | -3.4969 | -3.3507 | 117.9343 | -3.5547 | 118.127 | 118.0604 | 0.12611 | -3.4744 | -3.5582 | 118.1323 | 118.1583 | 118.3045 | 118.077 | -3.6519 | 118.1006 | 118.1808 | 118.0971 | 118.0805 | -3.721
3825 | 121.7926 | -121.3989 | 0.28839 | 1.4211e-13 | 0.025015 | 0.016133 | 0.010323 | -0.023148 | 0.0046387 | 0.24021 | 0.024598 | 0.034818 | -0.096424 | -0.0031431 | 0.00064308 | 0.088037 | 0.019721 | 0.023639 | 0.07502 | 0.1011 | 0.25185 | -0.012689 | 0.078886 | 0.027831 | 0.01233 | 0.043302 | 0.12359 | 0.035222 | -0.11836 | 121.3862 | -0.21337 | 121.487 | 121.4226 | 0.036328 | -0.1873 | -0.036539 | 121.2806 | -0.24509 | 121.4778 | 121.4113 | 0.13069 | -0.1648 | -0.25317 | 121.4739 | 121.5 | 121.6508 | 121.4186 | -0.30108 | 121.4422 | 121.5225 | 121.4341 | 121.4268 | -0.40675
3826.7812 | 121.7834 | -121.4401 | 0.31128 | 1.4211e-13 | 0.025228 | 0.015919 | 0.010109 | -0.023362 | 0.0046387 | 0.24784 | 0.024598 | 0.034818 | -0.096424 | -0.0035705 | 0.00064308 | 0.074302 | 0.0243 | 0.01906 | 0.070441 | 0.096516 | 0.24269 | -0.049321 | 0.074307 | 0.023253 | 0.007751 | 0.038723 | 0.12359 | 0.030644 | -0.11378 | 121.3908 | -0.24084 | 121.5144 | 121.4592 | 0.068381 | -0.21476 | -0.068584 | 121.3263 | -0.27256 | 121.5144 | 121.4479 | 0.12153 | -0.18769 | -0.28063 | 121.5106 | 121.5366 | 121.6828 | 121.4644 | -0.3606 | 121.4788 | 121.5637 | 121.4708 | 121.4634 | -0.42506
3828.5781 | 121.8842 | -121.4035 | 0.25635 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.023362 | 0.0050659 | 0.23258 | 0.024171 | 0.035031 | -0.097278 | -0.0035705 | 0.00064308 | 0.088037 | 0.015142 | 0.023639 | 0.07502 | 0.096516 | 0.25185 | -0.021847 | 0.083464 | 0.027831 | 0.003172 | 0.038723 | 0.11901 | 0.026065 | -0.11836 | 121.3817 | -0.18133 | 121.4915 | 121.4271 | 0.045486 | -0.15983 | -0.004496 | 121.2851 | -0.21763 | 121.487 | 121.4067 | 0.12153 | -0.13733 | -0.23028 | 121.4785 | 121.5 | 121.6554 | 121.4186 | -0.2782 | 121.4422 | 121.5225 | 121.4296 | 121.4313 | -0.37471
3830.375 | 121.843 | -121.4584 | 0.31128 | 1.4211e-13 | 0.025015 | 0.015919 | 0.0098956 | -0.022935 | 0.0050659 | 0.23258 | 0.024385 | 0.035031 | -0.096637 | -0.0031431 | 0.00085668 | 0.07888 | 0.019721 | 0.023639 | 0.065863 | 0.10567 | 0.24727 | -0.035584 | 0.074307 | 0.027831 | 0.007751 | 0.034145 | 0.12359 | 0.035222 | -0.11836 | 121.4229 | -0.24542 | 121.5373 | 121.4821 | 0.059223 | -0.2056 | -0.064005 | 121.3401 | -0.27713 | 121.5327 | 121.4662 | 0.12611 | -0.18769 | -0.27606 | 121.5243 | 121.5641 | 121.7057 | 121.4782 | -0.34686 | 121.4926 | 121.582 | 121.4937 | 121.4863 | -0.42964
3832.1094 | 121.9391 | -121.4355 | 0.2655 | 1.4211e-13 | 0.025015 | 0.015919 | 0.010323 | -0.023362 | 0.0048523 | 0.22495 | 0.024812 | 0.034177 | -0.096424 | -0.0029295 | 0.00085668 | 0.069723 | 0.019721 | 0.023639 | 0.070441 | 0.1011 | 0.24727 | -0.063057 | 0.083464 | 0.023253 | -0.001407 | 0.043302 | 0.13275 | 0.030644 | -0.11378 | 121.3725 | -0.19506 | 121.5053 | 121.4592 | 0.086696 | -0.16441 | -0.018229 | 121.3218 | -0.2222 | 121.519 | 121.4341 | 0.11237 | -0.13275 | -0.23486 | 121.506 | 121.5366 | 121.6828 | 121.4553 | -0.32856 | 121.4788 | 121.5683 | 121.4662 | 121.4588 | -0.37928
3833.8906 | 121.9528 | -121.4447 | 0.25635 | 1.4211e-13 | 0.025228 | 0.016346 | 0.0098956 | -0.023362 | 0.0050659 | 0.24021 | 0.024598 | 0.034818 | -0.096424 | -0.0035705 | 0.00064308 | 0.07888 | 0.010564 | 0.01906 | 0.070441 | 0.096516 | 0.24269 | -0.053899 | 0.078886 | 0.03241 | 0.003172 | 0.029566 | 0.13275 | 0.030644 | -0.12294 | 121.3908 | -0.18591 | 121.5236 | 121.4638 | 0.072959 | -0.15983 | -0.013653 | 121.3218 | -0.22678 | 121.5236 | 121.4479 | 0.12611 | -0.1236 | -0.2257 | 121.5151 | 121.5412 | 121.6874 | 121.4553 | -0.31025 | 121.4743 | 121.5775 | 121.4753 | 121.4771 | -0.37929
3835.6406 | 121.9528 | -121.4493 | 0.25635 | 1.4211e-13 | 0.025228 | 0.016133 | 0.0098956 | -0.022935 | 0.0044249 | 0.23258 | 0.024598 | 0.035031 | -0.096637 | -0.0033569 | 0.00064308 | 0.07888 | 0.019721 | 0.023639 | 0.070441 | 0.1011 | 0.24727 | -0.035584 | 0.078886 | 0.023253 | 0.003172 | 0.038723 | 0.12817 | 0.021486 | -0.11836 | 121.4137 | -0.18591 | 121.5282 | 121.4729 | 0.059223 | -0.15525 | -0.009074 | 121.3309 | -0.21763 | 121.5282 | 121.4525 | 0.12153 | -0.12818 | -0.23486 | 121.5197 | 121.5504 | 121.6966 | 121.469 | -0.29193 | 121.488 | 121.5775 | 121.4708 | 121.4725 | -0.37471
3837.4375 | 121.8887 | -121.4859 | 0.28839 | 1.4211e-13 | 0.025442 | 0.016346 | 0.010109 | -0.022935 | 0.0046387 | 0.23258 | 0.024598 | 0.034818 | -0.096851 | -0.0035705 | 0.00085668 | 0.083459 | 0.0243 | 0.023639 | 0.065863 | 0.096516 | 0.24269 | -0.063057 | 0.078886 | 0.023253 | 0.007751 | 0.038723 | 0.12359 | 0.026065 | -0.11836 | 121.4228 | -0.22253 | 121.5694 | 121.5095 | 0.086696 | -0.19188 | -0.045696 | 121.3675 | -0.24967 | 121.5648 | 121.4937 | 0.12611 | -0.1648 | -0.26233 | 121.5518 | 121.5824 | 121.7286 | 121.5102 | -0.35145 | 121.5246 | 121.6095 | 121.512 | 121.5092 | -0.40675
3839.2344 | 121.9116 | -121.4722 | 0.25635 | 1.4211e-13 | 0.025228 | 0.016346 | 0.009682 | -0.023148 | 0.0048523 | 0.24021 | 0.024171 | 0.034818 | -0.096424 | -0.0031431 | 0.0010705 | 0.083459 | 0.0243 | 0.01906 | 0.07502 | 0.096516 | 0.25185 | -0.035584 | 0.074307 | 0.03241 | 0.003172 | 0.043302 | 0.12359 | 0.021486 | -0.1092 | 121.4366 | -0.18133 | 121.5556 | 121.4912 | 0.054644 | -0.15983 | -0.004496 | 121.363 | -0.21305 | 121.5465 | 121.4753 | 0.11237 | -0.13276 | -0.23486 | 121.5472 | 121.5687 | 121.724 | 121.4965 | -0.29193 | 121.5155 | 121.5958 | 121.4937 | 121.5046 | -0.36555
3841.0312 | 121.9437 | -121.4401 | 0.28381 | 1.4211e-13 | 0.025015 | 0.016346 | 0.009682 | -0.023362 | 0.0046387 | 0.24784 | 0.024812 | 0.034604 | -0.097065 | -0.0029295 | 0.00042948 | 0.07888 | 0.019721 | 0.023639 | 0.07502 | 0.091937 | 0.24727 | -0.053899 | 0.078886 | 0.027831 | -0.001407 | 0.04788 | 0.12817 | 0.035222 | -0.11378 | 121.3862 | -0.20879 | 121.519 | 121.4638 | 0.077538 | -0.19188 | -0.036539 | 121.3263 | -0.23593 | 121.519 | 121.4387 | 0.11237 | -0.15564 | -0.24859 | 121.5151 | 121.5321 | 121.6874 | 121.4598 | -0.33771 | 121.488 | 121.5683 | 121.4753 | 121.468 | -0.39759
3842.8125 | 121.9574 | -121.4035 | 0.31128 | 1.4211e-13 | 0.025228 | 0.016133 | 0.009682 | -0.023148 | 0.0048523 | 0.23258 | 0.024598 | 0.034604 | -0.096851 | -0.0033569 | 0.00085668 | 0.083459 | 0.019721 | 0.028217 | 0.070441 | 0.10567 | 0.25185 | -0.063057 | 0.083464 | 0.023253 | 0.007751 | 0.04788 | 0.12359 | 0.026065 | -0.1092 | 121.3404 | -0.24084 | 121.487 | 121.4317 | 0.091274 | -0.2056 | -0.059427 | 121.2943 | -0.2634 | 121.487 | 121.4113 | 0.11695 | -0.18769 | -0.28521 | 121.4739 | 121.5092 | 121.6554 | 121.4232 | -0.37434 | 121.4514 | 121.5271 | 121.4296 | 121.4268 | -0.42048
3844.5469 | 121.9299 | -121.4127 | 0.32501 | 1.4211e-13 | 0.025015 | 0.015919 | 0.009682 | -0.023362 | 0.0044249 | 0.24021 | 0.025025 | 0.034604 | -0.096637 | -0.0033569 | 0.00064308 | 0.07888 | 0.028878 | 0.023639 | 0.070441 | 0.091937 | 0.24269 | -0.026426 | 0.074307 | 0.027831 | 0.007751 | 0.043302 | 0.11901 | 0.026065 | -0.11836 | 121.3862 | -0.25457 | 121.4915 | 121.4363 | 0.050065 | -0.23308 | -0.082317 | 121.2943 | -0.28171 | 121.487 | 121.4204 | 0.12611 | -0.206 | -0.29895 | 121.4831 | 121.5046 | 121.6554 | 121.4415 | -0.35144 | 121.456 | 121.5317 | 121.4387 | 121.4405 | -0.44337
3846.3438 | 121.8521 | -121.4447 | 0.37994 | 1.4211e-13 | 0.025442 | 0.016133 | 0.009682 | -0.023576 | 0.0046387 | 0.23258 | 0.024598 | 0.035031 | -0.096851 | -0.0033569 | 0.00064308 | 0.083459 | 0.015142 | 0.023639 | 0.070441 | 0.10567 | 0.25185 | -0.035584 | 0.074307 | 0.027831 | 0.007751 | 0.043302 | 0.12359 | 0.021486 | -0.11378 | 121.4091 | -0.3095 | 121.5282 | 121.4683 | 0.059223 | -0.27427 | -0.12809 | 121.3309 | -0.33664 | 121.519 | 121.4525 | 0.12153 | -0.25635 | -0.35846 | 121.5151 | 121.5504 | 121.6966 | 121.4598 | -0.41553 | 121.488 | 121.5683 | 121.4662 | 121.4725 | -0.49373
3848.1406 | 121.9803 | -121.3989 | 0.33417 | 1.4211e-13 | 0.025442 | 0.015919 | 0.010109 | -0.023148 | 0.0048523 | 0.23258 | 0.024598 | 0.035031 | -0.096424 | -0.0029295 | 0.00042948 | 0.07888 | 0.015142 | 0.023639 | 0.079598 | 0.1011 | 0.24727 | -0.026426 | 0.069728 | 0.023253 | 0.007751 | 0.043302 | 0.12817 | 0.026065 | -0.11378 | 121.3725 | -0.25457 | 121.4778 | 121.4226 | 0.050065 | -0.23307 | -0.086893 | 121.2851 | -0.29086 | 121.4687 | 121.4067 | 0.12153 | -0.20599 | -0.3081 | 121.4785 | 121.5 | 121.6462 | 121.4141 | -0.36059 | 121.4422 | 121.5271 | 121.425 | 121.4222 | -0.44795
3849.9375 | 121.9528 | -121.4218 | 0.35706 | 1.4211e-13 | 0.024801 | 0.015919 | 0.009682 | -0.023148 | 0.0050659 | 0.24021 | 0.024598 | 0.034818 | -0.096637 | -0.0033569 | 0.00064308 | 0.069723 | 0.015142 | 0.028217 | 0.070441 | 0.096516 | 0.24727 | -0.026426 | 0.088043 | 0.027831 | 0.003172 | 0.052459 | 0.12359 | 0.026065 | -0.11378 | 121.3954 | -0.28661 | 121.4915 | 121.45 | 0.054643 | -0.26054 | -0.10978 | 121.308 | -0.3046 | 121.5099 | 121.425 | 0.11695 | -0.23346 | -0.33099 | 121.4923 | 121.5183 | 121.6691 | 121.437 | -0.38348 | 121.4743 | 121.5454 | 121.4479 | 121.4496 | -0.47084
3851.6719 | 121.8613 | -121.4493 | 0.40741 | 1.4211e-13 | 0.025228 | 0.016346 | 0.0098956 | -0.023148 | 0.0050659 | 0.23258 | 0.024385 | 0.034818 | -0.096851 | -0.0033569 | 0.00064308 | 0.083459 | 0.015142 | 0.01906 | 0.07502 | 0.10567 | 0.24269 | -0.031005 | 0.074307 | 0.023253 | 0.01233 | 0.038723 | 0.12359 | 0.035222 | -0.11836 | 121.4183 | -0.33239 | 121.5327 | 121.4683 | 0.050065 | -0.30174 | -0.16472 | 121.3309 | -0.36869 | 121.5236 | 121.4616 | 0.13069 | -0.28382 | -0.37219 | 121.5243 | 121.555 | 121.692 | 121.4644 | -0.43841 | 121.488 | 121.5729 | 121.4845 | 121.4725 | -0.52577
3853.4688 | 121.9757 | -121.3943 | 0.37079 | 1.4211e-13 | 0.025228 | 0.016133 | 0.009682 | -0.023362 | 0.0048523 | 0.24784 | 0.024385 | 0.035031 | -0.096424 | -0.0031431 | 0.00064308 | 0.088037 | 0.015142 | 0.023639 | 0.070441 | 0.1011 | 0.23812 | -0.00811 | 0.074307 | 0.023253 | 0.007751 | 0.043302 | 0.11901 | 0.021486 | -0.11836 | 121.3862 | -0.30035 | 121.4824 | 121.418 | 0.031749 | -0.26969 | -0.13267 | 121.276 | -0.32749 | 121.4687 | 121.4021 | 0.12611 | -0.25177 | -0.3493 | 121.4648 | 121.4954 | 121.6325 | 121.4095 | -0.3789 | 121.4376 | 121.5134 | 121.4158 | 121.4176 | -0.48915
3855.2031 | 121.8613 | -121.4355 | 0.3891 | 1.4211e-13 | 0.025015 | 0.01656 | 0.009682 | -0.023362 | 0.0050659 | 0.24021 | 0.024812 | 0.034604 | -0.096424 | -0.0031431 | 0.00064308 | 0.088037 | 0.010564 | 0.01906 | 0.07502 | 0.091937 | 0.26101 | -0.044742 | 0.074307 | 0.03241 | 0.007751 | 0.038723 | 0.11444 | 0.026065 | -0.12294 | 121.3908 | -0.31408 | 121.5236 | 121.4546 | 0.063802 | -0.29716 | -0.12809 | 121.3126 | -0.35038 | 121.5099 | 121.4433 | 0.13069 | -0.27466 | -0.36303 | 121.5106 | 121.5275 | 121.6966 | 121.4461 | -0.43384 | 121.4743 | 121.55 | 121.4616 | 121.468 | -0.51204
3857 | 121.9208 | -121.4447 | 0.3891 | 1.4211e-13 | 0.025228 | 0.016133 | 0.0098956 | -0.023148 | 0.0044249 | 0.24021 | 0.024598 | 0.03439 | -0.096851 | -0.0033569 | 0.00085668 | 0.074302 | 0.019721 | 0.023639 | 0.061284 | 0.091937 | 0.24727 | -0.021847 | 0.083464 | 0.03241 | 0.007751 | 0.04788 | 0.11901 | 0.030644 | -0.12294 | 121.4229 | -0.32781 | 121.519 | 121.4683 | 0.045486 | -0.29716 | -0.14182 | 121.3218 | -0.34122 | 121.5282 | 121.4525 | 0.13069 | -0.27008 | -0.35845 | 121.506 | 121.5366 | 121.692 | 121.4644 | -0.41095 | 121.4926 | 121.5637 | 121.4753 | 121.4771 | -0.51204
3858.7969 | 121.9345 | -121.4447 | 0.37079 | 1.4211e-13 | 0.025228 | 0.016133 | 0.010109 | -0.023148 | 0.0048523 | 0.22495 | 0.024171 | 0.034604 | -0.096851 | -0.0037841 | 0.00085668 | 0.074302 | 0.019721 | 0.023639 | 0.07502 | 0.091937 | 0.24727 | -0.040163 | 0.083464 | 0.036989 | -0.001407 | 0.04788 | 0.12359 | 0.021486 | -0.11836 | 121.4045 | -0.29577 | 121.519 | 121.4683 | 0.063802 | -0.27885 | -0.12351 | 121.3263 | -0.32291 | 121.5282 | 121.4433 | 0.11695 | -0.2472 | -0.3493 | 121.5197 | 121.5366 | 121.692 | 121.4644 | -0.41095 | 121.4926 | 121.5683 | 121.4662 | 121.4817 | -0.48915
3860.5625 | 121.9574 | -121.4401 | 0.39825 | 1.4211e-13 | 0.025228 | 0.015919 | 0.0098956 | -0.023362 | 0.0052797 | 0.23258 | 0.024812 | 0.03439 | -0.096637 | -0.0031431 | 0.00064308 | 0.074302 | 0.0243 | 0.023639 | 0.070441 | 0.096516 | 0.25185 | -0.044742 | 0.078886 | 0.023253 | 0.003172 | 0.04788 | 0.11901 | 0.030644 | -0.11378 | 121.3954 | -0.32781 | 121.5144 | 121.4638 | 0.068381 | -0.30174 | -0.1464 | 121.3263 | -0.35037 | 121.519 | 121.4433 | 0.11695 | -0.27924 | -0.36761 | 121.5106 | 121.5366 | 121.692 | 121.4644 | -0.443 | 121.488 | 121.5591 | 121.4708 | 121.4634 | -0.51204
3862.3594 | 121.9208 | -121.4218 | 0.39825 | 1.4211e-13 | 0.025228 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.24784 | 0.024598 | 0.034604 | -0.096637 | -0.0035705 | 0.00085668 | 0.07888 | 0.019721 | 0.028217 | 0.065863 | 0.096516 | 0.24727 | -0.031005 | 0.083464 | 0.027831 | 0.007751 | 0.038723 | 0.11444 | 0.026065 | -0.12294 | 121.3908 | -0.33239 | 121.5007 | 121.45 | 0.059222 | -0.30174 | -0.15098 | 121.2989 | -0.35953 | 121.5053 | 121.4296 | 0.13069 | -0.28382 | -0.37219 | 121.4877 | 121.5183 | 121.6691 | 121.4415 | -0.42926 | 121.4605 | 121.5362 | 121.4479 | 121.4496 | -0.52119
3864.0781 | 121.9986 | -121.4081 | 0.38452 | 1.4211e-13 | 0.025228 | 0.016133 | 0.009682 | -0.023362 | 0.0048523 | 0.23258 | 0.024598 | 0.035031 | -0.096637 | -0.0029295 | 0.00042948 | 0.07888 | 0.015142 | 0.028217 | 0.070441 | 0.091937 | 0.25643 | -0.053899 | 0.078886 | 0.023253 | 0.01233 | 0.043302 | 0.11901 | 0.030644 | -0.1092 | 121.3542 | -0.31408 | 121.487 | 121.4363 | 0.082116 | -0.29258 | -0.12809 | 121.2989 | -0.34122 | 121.487 | 121.4204 | 0.12153 | -0.26551 | -0.35388 | 121.4785 | 121.5 | 121.6645 | 121.4232 | -0.43842 | 121.4514 | 121.5271 | 121.4387 | 121.4313 | -0.49372
3865.8594 | 121.9345 | -121.4539 | 0.40283 | 1.4211e-13 | 0.025015 | 0.016133 | 0.010109 | -0.023362 | 0.0048523 | 0.23258 | 0.024385 | 0.034818 | -0.096424 | -0.0031431 | 0.00085668 | 0.083459 | 0.019721 | 0.01906 | 0.07502 | 0.096516 | 0.24727 | -0.00811 | 0.083464 | 0.03241 | 0.01233 | 0.038723 | 0.12817 | 0.030644 | -0.11836 | 121.4457 | -0.32781 | 121.5373 | 121.4729 | 0.02717 | -0.30632 | -0.15556 | 121.3355 | -0.36411 | 121.5373 | 121.4662 | 0.13069 | -0.27466 | -0.37219 | 121.5289 | 121.5504 | 121.7011 | 121.4736 | -0.41094 | 121.4926 | 121.582 | 121.4845 | 121.4863 | -0.52119
3867.6562 | 121.9894 | -121.431 | 0.37994 | 1.4211e-13 | 0.025015 | 0.016346 | 0.009682 | -0.022721 | 0.0044249 | 0.23258 | 0.024598 | 0.034818 | -0.096851 | -0.0031431 | 0.00064308 | 0.07888 | 0.019721 | 0.014482 | 0.079598 | 0.1011 | 0.25185 | -0.040163 | 0.083464 | 0.03241 | 0.007751 | 0.043302 | 0.12359 | 0.026065 | -0.11836 | 121.3908 | -0.30035 | 121.5098 | 121.4455 | 0.054645 | -0.27885 | -0.12809 | 121.3126 | -0.33664 | 121.5144 | 121.4387 | 0.12611 | -0.25635 | -0.35388 | 121.5106 | 121.5321 | 121.6828 | 121.4507 | -0.42011 | 121.4743 | 121.5546 | 121.457 | 121.4634 | -0.4983
3869.3906 | 121.9574 | -121.4264 | 0.39825 | 1.4211e-13 | 0.024801 | 0.016133 | 0.009682 | -0.023148 | 0.0046387 | 0.24021 | 0.024812 | 0.03439 | -0.096637 | -0.0033569 | 0.00064308 | 0.07888 | 0.019721 | 0.028217 | 0.070441 | 0.091937 | 0.25185 | -0.026426 | 0.078886 | 0.023253 | 0.007751 | 0.038723 | 0.12817 | 0.039801 | -0.12294 | 121.4 | -0.32781 | 121.5053 | 121.4546 | 0.054643 | -0.30632 | -0.1464 | 121.3035 | -0.35953 | 121.5053 | 121.4341 | 0.13069 | -0.27008 | -0.35845 | 121.4968 | 121.5183 | 121.6782 | 121.4461 | -0.42468 | 121.4651 | 121.5546 | 121.4662 | 121.4496 | -0.52119
3871.1875 | 121.9666 | -121.431 | 0.36621 | 1.4211e-13 | 0.025015 | 0.016133 | 0.009682 | -0.023148 | 0.0046387 | 0.24021 | 0.024171 | 0.035031 | -0.096851 | -0.0033569 | 0.00064308 | 0.07888 | 0.028878 | 0.023639 | 0.065863 | 0.096516 | 0.25185 | -0.049321 | 0.078886 | 0.023253 | 0.003172 | 0.052459 | 0.12817 | 0.026065 | -0.11836 | 121.3816 | -0.30035 | 121.5098 | 121.4546 | 0.07296 | -0.2697 | -0.11436 | 121.3126 | -0.31375 | 121.5099 | 121.4341 | 0.12153 | -0.23804 | -0.34015 | 121.4968 | 121.5275 | 121.6828 | 121.4598 | -0.41553 | 121.4834 | 121.5591 | 121.457 | 121.4542 | -0.48457
3872.9844 | 122.0306 | -121.4127 | 0.37079 | 1.4211e-13 | 0.025015 | 0.01656 | 0.0098956 | -0.022935 | 0.0046387 | 0.22495 | 0.024385 | 0.034604 | -0.096637 | -0.0031431 | 0.00085668 | 0.07888 | 0.015142 | 0.028217 | 0.065863 | 0.1011 | 0.25185 | -0.040163 | 0.078886 | 0.023253 | 0.007751 | 0.038723 | 0.11901 | 0.026065 | -0.11836 | 121.3725 | -0.30493 | 121.4915 | 121.4409 | 0.06838 | -0.26969 | -0.11894 | 121.2943 | -0.33207 | 121.4915 | 121.4204 | 0.12611 | -0.25177 | -0.34472 | 121.4785 | 121.5138 | 121.6645 | 121.4278 | -0.41095 | 121.4514 | 121.5317 | 121.4387 | 121.4359 | -0.48915
3874.7031 | 122.0535 | -121.431 | 0.36163 | 1.4211e-13 | 0.025015 | 0.01656 | 0.010323 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.034604 | -0.096637 | -0.0033569 | 0.00064308 | 0.07888 | 0.015142 | 0.014482 | 0.07502 | 0.10567 | 0.25185 | -0.044742 | 0.078886 | 0.027831 | 0.003172 | 0.038723 | 0.11444 | 0.026065 | -0.11836 | 121.3862 | -0.28661 | 121.5098 | 121.4455 | 0.059224 | -0.25596 | -0.10978 | 121.3126 | -0.32291 | 121.5099 | 121.4341 | 0.12153 | -0.2472 | -0.33557 | 121.506 | 121.5366 | 121.6828 | 121.4461 | -0.40637 | 121.4697 | 121.5454 | 121.457 | 121.4588 | -0.47999
3876.5 | 121.9208 | -121.4813 | 0.39368 | 1.4211e-13 | 0.024801 | 0.016133 | 0.010109 | -0.023576 | 0.0048523 | 0.23258 | 0.024171 | 0.034604 | -0.096424 | -0.0033569 | 0.00064308 | 0.07888 | 0.019721 | 0.023639 | 0.07502 | 0.091937 | 0.24727 | -0.035584 | 0.069728 | 0.027831 | 0.003172 | 0.038723 | 0.11901 | 0.030644 | -0.12294 | 121.4457 | -0.31866 | 121.5602 | 121.505 | 0.059223 | -0.30174 | -0.1464 | 121.3584 | -0.35495 | 121.5511 | 121.4845 | 0.12611 | -0.27466 | -0.36303 | 121.5563 | 121.5733 | 121.7286 | 121.501 | -0.42926 | 121.52 | 121.6003 | 121.512 | 121.5092 | -0.51662
3878.2969 | 122.0352 | -121.4172 | 0.37537 | 1.4211e-13 | 0.024801 | 0.016133 | 0.009682 | -0.023148 | 0.0050659 | 0.22495 | 0.024812 | 0.03439 | -0.096424 | -0.0033569 | 0.00085668 | 0.074302 | 0.015142 | 0.023639 | 0.065863 | 0.096516 | 0.25185 | -0.031005 | 0.083464 | 0.027831 | 0.007751 | 0.038723 | 0.11901 | 0.021486 | -0.11378 | 121.3862 | -0.3095 | 121.4915 | 121.4409 | 0.054644 | -0.27885 | -0.12351 | 121.3035 | -0.33664 | 121.5007 | 121.425 | 0.12153 | -0.25635 | -0.35388 | 121.4831 | 121.5138 | 121.6691 | 121.4324 | -0.40637 | 121.456 | 121.5363 | 121.4387 | 121.4451 | -0.48915
3880.0156 | 122.0444 | -121.4355 | 0.3891 | 1.4211e-13 | 0.025015 | 0.016133 | 0.010109 | -0.023362 | 0.0048523 | 0.23258 | 0.024385 | 0.034604 | -0.096637 | -0.0037841 | 0.00042948 | 0.07888 | 0.015142 | 0.023639 | 0.065863 | 0.1011 | 0.25185 | -0.053899 | 0.078886 | 0.023253 | 0.007751 | 0.034145 | 0.12359 | 0.026065 | -0.11836 | 121.3816 | -0.32324 | 121.5144 | 121.4592 | 0.077538 | -0.288 | -0.13725 | 121.3172 | -0.35495 | 121.5144 | 121.4433 | 0.12611 | -0.26551 | -0.36303 | 121.5014 | 121.5366 | 121.6874 | 121.4507 | -0.443 | 121.4697 | 121.5591 | 121.4616 | 121.4588 | -0.50746
3881.7969 | 121.9299 | -121.4584 | 0.41199 | 1.4211e-13 | 0.024801 | 0.016346 | 0.0094682 | -0.023148 | 0.0046387 | 0.23258 | 0.024385 | 0.034818 | -0.096851 | -0.0037841 | 0.00085668 | 0.083459 | 0.019721 | 0.023639 | 0.070441 | 0.10567 | 0.24727 | -0.067636 | 0.074307 | 0.027831 | 0.003172 | 0.04788 | 0.12359 | 0.035222 | -0.12294 | 121.3908 | -0.34155 | 121.5419 | 121.4821 | 0.091275 | -0.30631 | -0.16471 | 121.3355 | -0.36411 | 121.5327 | 121.4616 | 0.12611 | -0.28839 | -0.37677 | 121.5289 | 121.5641 | 121.7057 | 121.4782 | -0.47962 | 121.5063 | 121.582 | 121.4937 | 121.4863 | -0.53493
3883.5938 | 121.8567 | -119.6182 | 2.2202 | 1.4211e-13 | 0.025015 | 0.015919 | 0.009682 | -0.022935 | 0.0048523 | 0.22495 | 0.024171 | 0.034604 | -0.096424 | -0.0033569 | 0.00085668 | 0.074302 | 0.019721 | 0.01906 | 0.070441 | 0.091937 | 0.24269 | -0.049321 | 0.074307 | 0.023253 | 0.003172 | 0.038723 | 0.11901 | 0.026065 | -0.11836 | 119.5689 | -2.1497 | 119.6925 | 119.6373 | 0.068381 | -2.1282 | -1.9775 | 119.4999 | -2.1814 | 119.6925 | 119.6214 | 0.12153 | -2.1011 | -2.1941 | 119.6887 | 119.7102 | 119.8609 | 119.6379 | -2.2695 | 119.6569 | 119.7372 | 119.6443 | 119.6415 | -2.3385
3885.4062 | 121.9894 | -116.2079 | 5.5527 | 1.4211e-13 | 0.025015 | 0.016133 | 0.009682 | -0.022935 | 0.0046387 | 0.22495 | 0.024598 | 0.035031 | -0.096637 | -0.0031431 | 0.00064308 | 0.07888 | 0.010564 | 0.01906 | 0.079598 | 0.091937 | 0.23812 | -0.063057 | 0.074307 | 0.027831 | 0.003172 | 0.043302 | 0.11901 | 0.021486 | -0.11836 | 116.1448 | -5.4731 | 116.2868 | 116.2269 | 0.082117 | -5.4607 | -5.3146 | 116.0895 | -5.5094 | 116.2822 | 116.2111 | 0.12153 | -5.4337 | -5.5312 | 116.2875 | 116.2998 | 116.446 | 116.2185 | -5.6157 | 116.2512 | 116.3269 | 116.2294 | 116.2357 | -5.671
3887.1406 | 122.0261 | -116.2811 | 5.5115 | 1.4211e-13 | 0.025228 | 0.016346 | 0.0098956 | -0.023148 | 0.0048523 | 0.23258 | 0.024598 | 0.034604 | -0.096637 | -0.0033569 | 0.00064308 | 0.07888 | 0.0243 | 0.01906 | 0.061284 | 0.096516 | 0.24727 | -0.044742 | 0.074307 | 0.027831 | 0.003172 | 0.043302 | 0.12817 | 0.026065 | -0.11836 | 116.2364 | -5.4502 | 116.36 | 116.3002 | 0.063802 | -5.415 | -5.2642 | 116.1628 | -5.4682 | 116.3554 | 116.2843 | 0.12153 | -5.3833 | -5.4854 | 116.3424 | 116.3776 | 116.5284 | 116.3054 | -5.5562 | 116.3244 | 116.4093 | 116.3072 | 116.309 | -5.6298
3888.9219 | 122.0078 | -118.4463 | 3.3966 | 1.4211e-13 | 0.024801 | 0.015919 | 0.0098956 | -0.022935 | 0.0046387 | 0.21732 | 0.024598 | 0.035245 | -0.096851 | -0.0033569 | 0.0010705 | 0.074302 | 0.015142 | 0.023639 | 0.07502 | 0.096516 | 0.25185 | -0.053899 | 0.074307 | 0.023253 | -0.001407 | 0.038723 | 0.11444 | 0.030644 | -0.12294 | 118.3925 | -3.3216 | 118.5207 | 118.47 | 0.077538 | -3.3001 | -3.1448 | 118.3234 | -3.3579 | 118.5207 | 118.4449 | 0.12153 | -3.2822 | -3.366 | 118.5214 | 118.5429 | 118.6982 | 118.4615 | -3.4505 | 118.4851 | 118.5608 | 118.477 | 118.4696 | -3.5195
3890.7188 | 121.9574 | -118.5928 | 3.2867 | 1.4211e-13 | 0.025015 | 0.016133 | 0.010109 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.034604 | -0.096851 | -0.0037841 | 0.00085668 | 0.07888 | 0.0243 | 0.023639 | 0.07502 | 0.096516 | 0.25185 | -0.031005 | 0.078886 | 0.03241 | 0.003172 | 0.04788 | 0.12359 | 0.016908 | -0.1092 | 118.5618 | -3.2117 | 118.6717 | 118.6165 | 0.054644 | -3.1902 | -3.0349 | 118.4836 | -3.2389 | 118.6717 | 118.596 | 0.11237 | -3.1631 | -3.2698 | 118.6679 | 118.6893 | 118.8447 | 118.6171 | -3.3177 | 118.6407 | 118.7164 | 118.6097 | 118.6252 | -3.3959
3892.5156 | 122.0993 | -119.5679 | 2.2385 | 1.4211e-13 | 0.025228 | 0.015919 | 0.009682 | -0.023148 | 0.0046387 | 0.24021 | 0.024385 | 0.034818 | -0.096424 | -0.0035705 | 0.00064308 | 0.074302 | 0.019721 | 0.023639 | 0.070441 | 0.096516 | 0.24727 | -0.049321 | 0.074307 | 0.027831 | 0.003172 | 0.043302 | 0.12817 | 0.026065 | -0.12294 | 119.5185 | -2.168 | 119.6422 | 119.5915 | 0.07296 | -2.1419 | -1.9912 | 119.4449 | -2.1952 | 119.6422 | 119.571 | 0.12611 | -2.1103 | -2.2124 | 119.6383 | 119.6644 | 119.8151 | 119.5876 | -2.2878 | 119.6112 | 119.696 | 119.5939 | 119.5957 | -2.3614
3894.2344 | 122.1313 | -119.5541 | 2.2751 | 1.4211e-13 | 0.024801 | 0.015919 | 0.0098956 | -0.023148 | 0.0046387 | 0.22495 | 0.024598 | 0.034604 | -0.096637 | -0.0031431 | 0.00064308 | 0.07888 | 0.015142 | 0.023639 | 0.070441 | 0.096516 | 0.24727 | -0.049321 | 0.078886 | 0.023253 | 0.007751 | 0.043302 | 0.11901 | 0.030644 | -0.11378 | 119.5048 | -2.2046 | 119.633 | 119.5778 | 0.07296 | -2.1786 | -2.0278 | 119.4404 | -2.2318 | 119.633 | 119.5619 | 0.12153 | -2.1561 | -2.2444 | 119.6246 | 119.6507 | 119.8014 | 119.5693 | -2.3244 | 119.5974 | 119.6732 | 119.5848 | 119.5774 | -2.3889
3896.0312 | 122.081 | -119.664 | 2.1606 | 1.4211e-13 | 0.025228 | 0.016133 | 0.0098956 | -0.023148 | 0.0046387 | 0.24021 | 0.024598 | 0.035031 | -0.096637 | -0.0033569 | 0.0010705 | 0.074302 | 0.019721 | 0.023639 | 0.07502 | 0.091937 | 0.24727 | -0.040163 | 0.078886 | 0.027831 | -0.005985 | 0.038723 | 0.11444 | 0.030644 | -0.11836 | 119.6238 | -2.0856 | 119.7383 | 119.6876 | 0.063802 | -2.0687 | -1.9134 | 119.5456 | -2.1219 | 119.7429 | 119.658 | 0.11238 | -2.0462 | -2.13 | 119.739 | 119.7559 | 119.9113 | 119.6837 | -2.2008 | 119.7027 | 119.7784 | 119.6946 | 119.6918 | -2.279
3897.7656 | 122.0352 | -119.7784 | 2.1057 | 1.4211e-13 | 0.025015 | 0.016346 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.024598 | 0.034818 | -0.096851 | -0.0031431 | 0.00021588 | 0.07888 | 0.0243 | 0.023639 | 0.070441 | 0.096516 | 0.25185 | -0.031005 | 0.074307 | 0.027831 | 0.007751 | 0.043302 | 0.11901 | 0.035222 | -0.11836 | 119.7474 | -2.0353 | 119.8573 | 119.8021 | 0.054644 | -2.0092 | -1.8539 | 119.6601 | -2.0624 | 119.8527 | 119.7862 | 0.12611 | -1.9867 | -2.0705 | 119.8489 | 119.875 | 120.0303 | 119.8027 | -2.1367 | 119.8217 | 119.8975 | 119.8137 | 119.8063 | -2.2241
3899.5625 | 122.0718 | -119.7006 | 2.179 | 1.4211e-13 | 0.024801 | 0.015919 | 0.010109 | -0.023362 | 0.0050659 | 0.24021 | 0.024598 | 0.034818 | -0.096637 | -0.0037841 | 0.00085668 | 0.07888 | 0.019721 | 0.023639 | 0.065863 | 0.10567 | 0.25643 | -0.031005 | 0.074307 | 0.027831 | -0.001407 | 0.038723 | 0.12359 | 0.026065 | -0.1092 | 119.6696 | -2.1131 | 119.7795 | 119.7243 | 0.054644 | -2.0733 | -1.9225 | 119.5914 | -2.1402 | 119.7749 | 119.6992 | 0.1078 | -2.0554 | -2.1529 | 119.7665 | 119.8063 | 119.9571 | 119.7203 | -2.21 | 119.7393 | 119.8242 | 119.7267 | 119.7285 | -2.2882
3901.3438 | 122.0764 | -119.6686 | 2.211 | 1.4211e-13 | 0.024801 | 0.01656 | 0.009682 | -0.023148 | 0.0050659 | 0.22495 | 0.024385 | 0.034604 | -0.096851 | -0.0037841 | 0.0010705 | 0.07888 | 0.019721 | 0.01906 | 0.070441 | 0.096516 | 0.24269 | -0.063057 | 0.078886 | 0.027831 | 0.007751 | 0.043302 | 0.12359 | 0.026065 | -0.11378 | 119.6055 | -2.1406 | 119.7475 | 119.6876 | 0.082117 | -2.1145 | -1.9683 | 119.5548 | -2.1677 | 119.7475 | 119.6763 | 0.12153 | -2.0874 | -2.1849 | 119.739 | 119.7651 | 119.9113 | 119.6883 | -2.2741 | 119.7119 | 119.7922 | 119.6946 | 119.6964 | -2.3248
3903.0781 | 121.9803 | -119.8288 | 2.1149 | 1.4211e-13 | 0.024587 | 0.015919 | 0.009682 | -0.023148 | 0.0046387 | 0.23258 | 0.024171 | 0.034604 | -0.096851 | -0.0033569 | 0.00085668 | 0.074302 | 0.0243 | 0.028217 | 0.070441 | 0.096516 | 0.24269 | -0.049321 | 0.083464 | 0.027831 | 0.007751 | 0.043302 | 0.12359 | 0.030644 | -0.11378 | 119.7795 | -2.0444 | 119.9031 | 119.857 | 0.077538 | -2.0184 | -1.8722 | 119.715 | -2.0716 | 119.9123 | 119.8365 | 0.12153 | -1.9913 | -2.0842 | 119.8992 | 119.9253 | 120.0715 | 119.8531 | -2.1642 | 119.8721 | 119.9524 | 119.8594 | 119.8566 | -2.2287
3904.8594 | 122.0673 | -119.6732 | 2.2568 | 1.4211e-13 | 0.025015 | 0.016346 | 0.0098956 | -0.023148 | 0.0046387 | 0.23258 | 0.024812 | 0.034818 | -0.096637 | -0.0033569 | 0.00064308 | 0.065145 | 0.019721 | 0.01906 | 0.07502 | 0.091937 | 0.24727 | -0.076794 | 0.078886 | 0.027831 | -0.001407 | 0.043302 | 0.12359 | 0.030644 | -0.11836 | 119.5964 | -2.1818 | 119.7383 | 119.6922 | 0.095854 | -2.1648 | -2.0095 | 119.5548 | -2.2135 | 119.752 | 119.6718 | 0.11695 | -2.1332 | -2.2261 | 119.7482 | 119.7651 | 119.9204 | 119.6929 | -2.3336 | 119.7165 | 119.7968 | 119.7038 | 119.701 | -2.3751
3906.6562 | 122.0581 | -119.5999 | 2.2751 | 1.4211e-13 | 0.024587 | 0.016133 | 0.0098956 | -0.022935 | 0.0048523 | 0.23258 | 0.024385 | 0.035031 | -0.096851 | -0.0033569 | 0.00085668 | 0.07888 | 0.019721 | 0.028217 | 0.065863 | 0.096516 | 0.24727 | -0.049321 | 0.074307 | 0.023253 | -0.001407 | 0.043302 | 0.12359 | 0.021486 | -0.11378 | 119.5506 | -2.2092 | 119.6788 | 119.6281 | 0.077538 | -2.1786 | -2.0278 | 119.4861 | -2.2318 | 119.6742 | 119.5985 | 0.11237 | -2.1515 | -2.2536 | 119.6658 | 119.6964 | 119.8472 | 119.6196 | -2.3244 | 119.6432 | 119.7235 | 119.6214 | 119.6232 | -2.3889
3908.3906 | 122.1497 | -119.8883 | 1.9638 | 1.4211e-13 | 0.025228 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.024385 | 0.034818 | -0.096637 | -0.0033569 | 0.00042948 | 0.07888 | 0.019721 | 0.028217 | 0.070441 | 0.1011 | 0.24727 | -0.067636 | 0.069728 | 0.023253 | 0.007751 | 0.043302 | 0.12359 | 0.030644 | -0.11836 | 119.8207 | -1.8934 | 119.9672 | 119.9165 | 0.095853 | -1.8627 | -1.7165 | 119.7699 | -1.9205 | 119.958 | 119.8961 | 0.12611 | -1.8402 | -1.9332 | 119.9587 | 119.9894 | 120.1356 | 119.908 | -2.0314 | 119.9316 | 120.0119 | 119.9189 | 119.9116 | -2.0822
3910.1719 | 122.1268 | -120.0027 | 1.8448 | 1.4211e-13 | 0.024587 | 0.015919 | 0.0098956 | -0.022935 | 0.0046387 | 0.23258 | 0.024385 | 0.034818 | -0.096424 | -0.0033569 | 0.00085668 | 0.083459 | 0.019721 | 0.023639 | 0.07502 | 0.096516 | 0.24727 | -0.026426 | 0.083464 | 0.036989 | 0.003172 | 0.038723 | 0.12817 | 0.030644 | -0.11378 | 119.9763 | -1.7698 | 120.0862 | 120.0264 | 0.050065 | -1.7483 | -1.5975 | 119.889 | -1.8061 | 120.0862 | 120.0059 | 0.11695 | -1.7166 | -1.8141 | 120.0778 | 120.0993 | 120.25 | 120.0225 | -1.8712 | 120.0415 | 120.1309 | 120.0334 | 120.0397 | -1.9586
3911.8906 | 122.1359 | -120.1126 | 1.767 | 1.4211e-13 | 0.025015 | 0.015919 | 0.010109 | -0.023362 | 0.0048523 | 0.23258 | 0.024598 | 0.035031 | -0.096424 | -0.0035705 | 0.00042948 | 0.07888 | 0.019721 | 0.028217 | 0.070441 | 0.096516 | 0.24727 | -0.035584 | 0.083464 | 0.03241 | 0.007751 | 0.04788 | 0.12817 | 0.030644 | -0.12294 | 120.077 | -1.6965 | 120.1915 | 120.1408 | 0.063801 | -1.6705 | -1.5197 | 119.9897 | -1.7191 | 120.1961 | 120.1204 | 0.13069 | -1.6388 | -1.7363 | 120.1831 | 120.2091 | 120.3599 | 120.1323 | -1.8026 | 120.1605 | 120.2408 | 120.1433 | 120.145 | -1.8899
3913.6875 | 122.113 | -120.0989 | 1.7715 | 1.4211e-13 | 0.024801 | 0.016133 | 0.009682 | -0.022935 | 0.0048523 | 0.24021 | 0.024598 | 0.034604 | -0.096851 | -0.0037841 | 0.00064308 | 0.074302 | 0.010564 | 0.023639 | 0.070441 | 0.096516 | 0.25185 | -0.035584 | 0.083464 | 0.023253 | -0.001407 | 0.038723 | 0.11901 | 0.026065 | -0.12294 | 120.0633 | -1.7011 | 120.1732 | 120.1225 | 0.059223 | -1.675 | -1.5197 | 119.9759 | -1.7328 | 120.1823 | 120.0975 | 0.12153 | -1.6525 | -1.7455 | 120.1693 | 120.1954 | 120.3507 | 120.1094 | -1.8071 | 120.1376 | 120.2179 | 120.1249 | 120.1221 | -1.8945
3915.4844 | 122.1039 | -120.0394 | 1.8631 | 1.4211e-13 | 0.024801 | 0.015919 | 0.010109 | -0.023148 | 0.0050659 | 0.24021 | 0.024598 | 0.034818 | -0.096424 | -0.0033569 | 0.00085668 | 0.074302 | 0.015142 | 0.01906 | 0.070441 | 0.096516 | 0.24727 | -0.049321 | 0.078886 | 0.027831 | -0.001407 | 0.043302 | 0.12817 | 0.026065 | -0.11378 | 119.99 | -1.7927 | 120.1137 | 120.0584 | 0.068381 | -1.7666 | -1.6158 | 119.9256 | -1.8198 | 120.1183 | 120.038 | 0.11237 | -1.7349 | -1.837 | 120.1098 | 120.1359 | 120.2866 | 120.0545 | -1.9124 | 120.0827 | 120.1675 | 120.0654 | 120.0672 | -1.9769
3917.2969 | 121.9803 | -120.0989 | 1.8951 | 1.4211e-13 | 0.025015 | 0.01656 | 0.0098956 | -0.023362 | 0.0044249 | 0.23258 | 0.024598 | 0.034604 | -0.096637 | -0.0035705 | 0.00085668 | 0.07888 | 0.0243 | 0.023639 | 0.061284 | 0.096516 | 0.24269 | -0.040163 | 0.078886 | 0.027831 | 0.007751 | 0.04788 | 0.12359 | 0.030644 | -0.11836 | 120.0587 | -1.8339 | 120.1778 | 120.1225 | 0.063802 | -1.7986 | -1.6524 | 119.9805 | -1.8473 | 120.1778 | 120.1066 | 0.12611 | -1.7715 | -1.8645 | 120.1602 | 120.1954 | 120.3416 | 120.1232 | -1.9353 | 120.1468 | 120.2225 | 120.1295 | 120.1267 | -2.0135
3919.0156 | 122.0444 | -120.1401 | 1.8539 | 1.4211e-13 | 0.024374 | 0.016346 | 0.0098956 | -0.022935 | 0.0048523 | 0.23258 | 0.024812 | 0.034604 | -0.096851 | -0.0035705 | 0.00064308 | 0.074302 | 0.019721 | 0.028217 | 0.065863 | 0.096516 | 0.24727 | -0.044742 | 0.074307 | 0.036989 | 0.01233 | 0.043302 | 0.11901 | 0.026065 | -0.11836 | 120.0953 | -1.7881 | 120.2144 | 120.1683 | 0.072959 | -1.7574 | -1.6067 | 120.0217 | -1.8106 | 120.2144 | 120.1524 | 0.13069 | -1.7349 | -1.8279 | 120.2059 | 120.2366 | 120.3873 | 120.1598 | -1.8987 | 120.1834 | 120.2591 | 120.1661 | 120.1771 | -1.9723
3920.7969 | 122.0535 | -119.957 | 2.0004 | 1.4211e-13 | 0.024801 | 0.015919 | 0.0098956 | -0.023148 | 0.0046387 | 0.23258 | 0.024385 | 0.034604 | -0.096637 | -0.0037841 | 0.00042948 | 0.069723 | 0.015142 | 0.023639 | 0.070441 | 0.091937 | 0.25185 | -0.040163 | 0.083464 | 0.03241 | 0.007751 | 0.038723 | 0.11901 | 0.026065 | -0.11836 | 119.9168 | -1.93 | 120.0267 | 119.9806 | 0.063802 | -1.9085 | -1.7486 | 119.8386 | -1.9617 | 120.0404 | 119.9647 | 0.12611 | -1.8814 | -1.9744 | 120.0274 | 120.0489 | 120.2088 | 119.9721 | -2.0406 | 119.9957 | 120.076 | 119.983 | 119.9894 | -2.1188
3922.5469 | 122.0856 | -119.7739 | 2.1378 | 1.4211e-13 | 0.024587 | 0.015919 | 0.009682 | -0.023148 | 0.0046387 | 0.24021 | 0.024385 | 0.034818 | -0.097065 | -0.0035705 | 0.00085668 | 0.074302 | 0.019721 | 0.01906 | 0.070441 | 0.096516 | 0.24727 | -0.053899 | 0.083464 | 0.03241 | 0.007751 | 0.038723 | 0.11901 | 0.026065 | -0.12294 | 119.72 | -2.0673 | 119.8482 | 119.7929 | 0.072959 | -2.0412 | -1.8905 | 119.6509 | -2.099 | 119.8573 | 119.7816 | 0.13069 | -2.0187 | -2.1117 | 119.8443 | 119.8704 | 120.0211 | 119.7936 | -2.1917 | 119.8126 | 119.8929 | 119.7999 | 119.8063 | -2.2607
3924.3438 | 122.1359 | -119.9799 | 1.9043 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024598 | 0.034818 | -0.096637 | -0.0037841 | 0.00064308 | 0.074302 | 0.019721 | 0.01906 | 0.065863 | 0.087359 | 0.24727 | -0.053899 | 0.06515 | 0.023253 | 0.003172 | 0.043302 | 0.12359 | 0.030644 | -0.11378 | 119.926 | -1.8384 | 120.0542 | 119.9989 | 0.072959 | -1.8169 | -1.657 | 119.8661 | -1.861 | 120.045 | 119.983 | 0.11695 | -1.7807 | -1.8737 | 120.0457 | 120.0672 | 120.2271 | 119.9996 | -1.9582 | 120.0232 | 120.1035 | 120.0105 | 120.0031 | -2.0181
3926.0625 | 122.0764 | -119.8746 | 2.0554 | 1.4211e-13 | 0.024374 | 0.015919 | 0.010109 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0031431 | 0.00085668 | 0.074302 | 0.019721 | 0.023639 | 0.07502 | 0.096516 | 0.25185 | -0.063057 | 0.074307 | 0.027831 | 0.007751 | 0.038723 | 0.11901 | 0.035222 | -0.11378 | 119.8115 | -1.9803 | 119.9489 | 119.8982 | 0.086696 | -1.9588 | -1.8035 | 119.7608 | -2.0166 | 119.9489 | 119.8823 | 0.12153 | -1.9363 | -2.0201 | 119.9496 | 119.9711 | 120.1264 | 119.8943 | -2.1184 | 119.9133 | 119.9936 | 119.9098 | 119.9024 | -2.1691
3927.8438 | 122.3648 | -119.6136 | 2.3163 | 1.4211e-13 | 0.024587 | 0.015919 | 0.009682 | -0.023362 | 0.0044249 | 0.24021 | 0.024385 | 0.034818 | -0.096637 | -0.0033569 | 0.00042948 | 0.074302 | 0.015142 | 0.01906 | 0.070441 | 0.091937 | 0.24269 | -0.044742 | 0.074307 | 0.023253 | -0.001407 | 0.043302 | 0.11901 | 0.030644 | -0.11836 | 119.5689 | -2.2458 | 119.6879 | 119.6327 | 0.063802 | -2.2243 | -2.0736 | 119.4953 | -2.273 | 119.688 | 119.6122 | 0.11695 | -2.1973 | -2.2856 | 119.6841 | 119.7056 | 119.8563 | 119.6288 | -2.361 | 119.6569 | 119.7327 | 119.6443 | 119.6369 | -2.4346
3929.5625 | 121.962 | -119.9661 | 2.0233 | 1.4211e-13 | 0.025015 | 0.016346 | 0.0098956 | -0.023576 | 0.0048523 | 0.23258 | 0.024385 | 0.034818 | -0.096637 | -0.0033569 | 0.00085668 | 0.083459 | 0.015142 | 0.023639 | 0.061284 | 0.096516 | 0.25643 | -0.058478 | 0.074307 | 0.023253 | 0.003172 | 0.038723 | 0.11901 | 0.026065 | -0.1092 | 119.9076 | -1.962 | 120.0496 | 119.9898 | 0.082117 | -1.9268 | -1.7669 | 119.8569 | -1.9846 | 120.0404 | 119.9693 | 0.11237 | -1.9043 | -1.9973 | 120.0274 | 120.0626 | 120.2226 | 119.9813 | -2.0818 | 120.0048 | 120.0851 | 119.9922 | 119.9894 | -2.1325
3931.3594 | 122.1725 | -119.5908 | 2.3346 | 1.4211e-13 | 0.024801 | 0.016133 | 0.009682 | -0.023576 | 0.0048523 | 0.23258 | 0.024385 | 0.034604 | -0.096851 | -0.0035705 | 0.00085668 | 0.083459 | 0.0243 | 0.01906 | 0.07502 | 0.091937 | 0.25185 | -0.072215 | 0.069728 | 0.027831 | 0.003172 | 0.029566 | 0.13275 | 0.021486 | -0.11836 | 119.5185 | -2.2596 | 119.6742 | 119.6098 | 0.091275 | -2.2427 | -2.0827 | 119.4724 | -2.305 | 119.6605 | 119.5939 | 0.12153 | -2.2018 | -2.3131 | 119.6658 | 119.6827 | 119.8426 | 119.6151 | -2.4068 | 119.6203 | 119.7235 | 119.6122 | 119.6186 | -2.453
3933.0781 | 122.0078 | -114.3677 | 7.489 | 1.4211e-13 | 0.024374 | 0.016133 | 0.010109 | -0.023576 | 0.0050659 | 0.23258 | 0.024812 | 0.034818 | -0.096851 | -0.0035705 | 0.00085668 | 0.074302 | 0.010564 | 0.014482 | 0.07502 | 0.096516 | 0.24727 | -0.076794 | 0.074307 | 0.027831 | -0.005985 | 0.043302 | 0.13275 | 0.026065 | -0.10462 | 114.2909 | -7.414 | 114.442 | 114.3822 | 0.091276 | -7.3925 | -7.2417 | 114.2631 | -7.4457 | 114.442 | 114.3617 | 0.098639 | -7.3563 | -7.4629 | 114.4427 | 114.4642 | 114.615 | 114.3782 | -7.5658 | 114.411 | 114.5004 | 114.3937 | 114.3955 | -7.5936
3934.8594 | 121.5729 | -13.4445 | 108.3252 | 1.4211e-13 | 0.024801 | 0.016133 | 0.009682 | -0.023576 | 0.0050659 | 0.22495 | 0.024598 | 0.034604 | -0.096851 | -0.0035705 | 0.00064308 | 0.046831 | -0.012329 | -0.012988 | 0.042971 | 0.069043 | 0.22438 | -0.085952 | 0.055992 | 0.004938 | -0.028879 | 0.006674 | 0.10986 | -0.051771 | -0.13668 | 13.3586 | -108.2822 | 13.4913 | 13.4315 | 0.072964 | -108.2562 | -108.1008 | 13.3078 | -108.3185 | 13.5005 | 13.4156 | 0.1078 | -108.2153 | -108.377 | 13.4875 | 13.5136 | 13.6689 | 13.4322 | -108.4111 | 13.4512 | 13.5544 | 13.3927 | 13.4495 | -108.4619
3936.6562 | 121.9849 | -84.2056 | 37.3627 | 1.4211e-13 | 0.025015 | 0.016133 | 0.010109 | -0.023148 | 0.0046387 | 0.24021 | 0.024385 | 0.034818 | -0.096637 | -0.0033569 | 0.00064308 | 0.055988 | -0.007751 | -0.003831 | 0.052128 | 0.069043 | 0.21522 | -0.09511 | 0.051413 | 0.004938 | -0.0243 | 0.020409 | 0.096121 | -0.0243 | -0.12294 | 84.1105 | -37.3105 | 84.2616 | 84.2018 | 0.091279 | -37.2936 | -37.1474 | 84.0827 | -37.3423 | 84.257 | 84.1813 | 0.098639 | -37.2666 | -37.387 | 84.2578 | 84.2747 | 84.4209 | 84.1979 | -37.4578 | 84.226 | 84.3017 | 84.1813 | 84.2106 | -37.4856
3938.4375 | 121.7331 | -5.4108 | 116.5192 | 1.4211e-13 | 0.024801 | 0.016133 | 0.009682 | -0.023576 | 0.0046387 | 0.23258 | 0.024812 | 0.034604 | -0.096851 | -0.0037841 | 0.00085668 | 0.037675 | -0.021486 | -0.017566 | 0.029236 | 0.055306 | 0.20149 | -0.099689 | 0.042256 | -0.00422 | -0.033458 | 0.002095 | 0.082386 | -0.10214 | -0.15041 | 5.3111 | -116.4899 | 5.4484 | 5.3932 | 0.082123 | -116.4639 | -116.3177 | 5.2604 | -116.5171 | 5.453 | 5.3773 | 0.11695 | -116.4368 | -116.6213 | 5.44 | 5.4661 | 5.6123 | 5.3893 | -116.6189 | 5.4129 | 5.4932 | 5.3086 | 5.4065 | -116.6696
3940.2344 | 122.0352 | -4.6005 | 117.3248 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.023148 | 0.0044249 | 0.24021 | 0.024171 | 0.035031 | -0.096637 | -0.0035705 | 0.00085668 | 0.037675 | -0.026065 | -0.012988 | 0.033814 | 0.059885 | 0.21522 | -0.10885 | 0.042256 | -0.008798 | -0.038036 | 0.002095 | 0.077807 | -0.070086 | -0.14583 | 4.4917 | -117.291 | 4.6382 | 4.5875 | 0.095859 | -117.2649 | -117.1096 | 4.4547 | -117.3227 | 4.6428 | 4.5625 | 0.1078 | -117.247 | -117.3949 | 4.6343 | 4.6604 | 4.8157 | 4.5745 | -117.4337 | 4.6026 | 4.6783 | 4.5304 | 4.5917 | -117.4707
3941.9688 | 121.9528 | -4.3442 | 117.691 | 1.4211e-13 | 0.024801 | 0.016133 | 0.009682 | -0.023576 | 0.0048523 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0033569 | 0.00064308 | 0.042253 | -0.016908 | -0.017566 | 0.033814 | 0.055306 | 0.21064 | -0.090531 | 0.042256 | -0.00422 | -0.033458 | 0.002095 | 0.077807 | -0.083821 | -0.14583 | 4.2536 | -117.6572 | 4.3864 | 4.3266 | 0.072965 | -117.6357 | -117.4804 | 4.1983 | -117.6889 | 4.3864 | 4.3107 | 0.11237 | -117.6132 | -117.7749 | 4.378 | 4.3995 | 4.5548 | 4.3273 | -117.7816 | 4.3463 | 4.422 | 4.2604 | 4.34 | -117.8369
3943.75 | 121.9528 | -4.1656 | 117.865 | 1.4211e-13 | 0.025015 | 0.015919 | 0.0098956 | -0.023148 | 0.0042113 | 0.24021 | 0.024385 | 0.034818 | -0.096637 | -0.0037841 | 0.00085668 | 0.037675 | -0.021486 | -0.022144 | 0.033814 | 0.055306 | 0.20607 | -0.09511 | 0.037677 | -0.008798 | -0.042615 | 0.006674 | 0.082386 | -0.0884 | -0.15041 | 4.0705 | -117.8312 | 4.2033 | 4.1435 | 0.072966 | -117.8097 | -117.6589 | 4.0152 | -117.8583 | 4.2033 | 4.123 | 0.1078 | -117.7826 | -117.9534 | 4.1995 | 4.221 | 4.3717 | 4.1442 | -117.9601 | 4.1723 | 4.248 | 4.0772 | 4.1569 | -118.0154
3945.5625 | 122.0306 | -3.9322 | 118.1168 | 1.4211e-13 | 0.024801 | 0.016133 | 0.009682 | -0.023148 | 0.0048523 | 0.23258 | 0.024598 | 0.035031 | -0.096424 | -0.0033569 | 0.00085668 | 0.046831 | -0.026065 | -0.022144 | 0.038393 | 0.055306 | 0.20607 | -0.099689 | 0.033099 | -0.017956 | -0.033458 | -0.007062 | 0.077807 | -0.10671 | -0.15957 | 3.8325 | -118.0784 | 3.979 | 3.91 | 0.077545 | -118.0615 | -117.9107 | 3.7726 | -118.1238 | 3.9653 | 3.8987 | 0.12611 | -118.039 | -118.2235 | 3.9706 | 3.9875 | 4.1383 | 3.9061 | -118.2164 | 3.9251 | 4.01 | 3.8255 | 3.9142 | -118.2763
3947.375 | 121.9803 | -3.7857 | 118.2587 | 1.4211e-13 | 0.024374 | 0.016133 | 0.0094682 | -0.023362 | 0.0044249 | 0.24784 | 0.024385 | 0.034604 | -0.096851 | -0.0035705 | 0.00064308 | 0.037675 | -0.016908 | -0.022144 | 0.029236 | 0.050727 | 0.21064 | -0.10885 | 0.037677 | -0.008798 | -0.033458 | 0.002095 | 0.082386 | -0.097557 | -0.15041 | 3.6769 | -118.2294 | 3.8234 | 3.7636 | 0.086703 | -118.2079 | -118.048 | 3.6353 | -118.2566 | 3.8234 | 3.7522 | 0.11695 | -118.1763 | -118.3562 | 3.8149 | 3.8364 | 3.9964 | 3.7688 | -118.3675 | 3.7878 | 3.8681 | 3.6881 | 3.7769 | -118.4091
3949.1562 | 122.0123 | -3.7308 | 118.3136 | 1.4211e-13 | 0.024801 | 0.015705 | 0.009682 | -0.023362 | 0.0048523 | 0.23258 | 0.024598 | 0.034818 | -0.096851 | -0.0039979 | 0.00064308 | 0.042253 | -0.026065 | -0.017566 | 0.033814 | 0.050727 | 0.20607 | -0.099689 | 0.037677 | -0.008798 | -0.038036 | 0.002095 | 0.086964 | -0.083821 | -0.15499 | 3.6311 | -118.2798 | 3.773 | 3.7132 | 0.082123 | -118.2629 | -118.1075 | 3.5758 | -118.3115 | 3.7685 | 3.6927 | 0.11695 | -118.2266 | -118.3974 | 3.7646 | 3.7815 | 3.9368 | 3.7047 | -118.4133 | 3.7329 | 3.8177 | 3.647 | 3.722 | -118.4686
3950.875 | 122.0078 | -3.6896 | 118.3319 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.023148 | 0.0046387 | 0.24784 | 0.024598 | 0.034818 | -0.096637 | -0.0037841 | 0.00042948 | 0.042253 | -0.021486 | -0.022144 | 0.033814 | 0.059885 | 0.21064 | -0.099689 | 0.042256 | -0.013377 | -0.033458 | 0.002095 | 0.086964 | -0.10214 | -0.15957 | 3.5899 | -118.2981 | 3.7318 | 3.6674 | 0.077545 | -118.272 | -118.1213 | 3.53 | -118.3298 | 3.7318 | 3.6561 | 0.12611 | -118.2449 | -118.434 | 3.7234 | 3.7495 | 3.9002 | 3.6681 | -118.4316 | 3.6917 | 3.7765 | 3.5874 | 3.6762 | -118.4915
3952.6719 | 122.049 | -3.6255 | 118.4052 | 1.4211e-13 | 0.024801 | 0.015919 | 0.0098956 | -0.023362 | 0.0046387 | 0.23258 | 0.024385 | 0.034818 | -0.097065 | -0.0035705 | 0.00064308 | 0.046831 | -0.021486 | -0.012988 | 0.033814 | 0.059885 | 0.20607 | -0.099689 | 0.042256 | -0.013377 | -0.038036 | -0.007062 | 0.086964 | -0.10671 | -0.15499 | 3.5258 | -118.3713 | 3.6723 | 3.6125 | 0.086701 | -118.3453 | -118.1991 | 3.4705 | -118.4122 | 3.6677 | 3.5875 | 0.11695 | -118.3182 | -118.5119 | 3.6593 | 3.6854 | 3.8316 | 3.604 | -118.5048 | 3.6184 | 3.7125 | 3.5188 | 3.6121 | -118.5601
3954.4688 | 122.1268 | -3.4836 | 118.4555 | 1.4211e-13 | 0.024587 | 0.015919 | 0.009682 | -0.023576 | 0.0048523 | 0.24784 | 0.024598 | 0.034604 | -0.096637 | -0.0033569 | 0.0010705 | 0.037675 | -0.021486 | -0.017566 | 0.038393 | 0.064464 | 0.21064 | -0.10427 | 0.046835 | -0.013377 | -0.038036 | -0.002483 | 0.082386 | -0.0884 | -0.15041 | 3.3793 | -118.4171 | 3.5213 | 3.466 | 0.086702 | -118.391 | -118.2449 | 3.3332 | -118.458 | 3.5304 | 3.4455 | 0.11238 | -118.3731 | -118.5439 | 3.522 | 3.548 | 3.6942 | 3.4621 | -118.5598 | 3.4811 | 3.566 | 3.3952 | 3.4702 | -118.6059
3956.2031 | 121.9894 | -41.803 | 79.8843 | 1.4211e-13 | 0.024374 | 0.015705 | 0.0098956 | -0.023576 | 0.0048523 | 0.24784 | 0.024385 | 0.03439 | -0.096637 | -0.0035705 | 0.00085668 | 0.046831 | -0.003172 | -0.003831 | 0.052128 | 0.073622 | 0.22438 | -0.09511 | 0.046835 | 0.000359 | -0.019721 | 0.006674 | 0.10528 | -0.070086 | -0.14125 | 41.7079 | -79.8322 | 41.8498 | 41.7991 | 0.091279 | -79.8107 | -79.66 | 41.6617 | -79.8777 | 41.8498 | 41.7833 | 0.12153 | -79.7791 | -79.9544 | 41.8551 | 41.8766 | 42.0274 | 41.7998 | -79.9794 | 41.8097 | 41.9083 | 41.7329 | 41.8033 | -80.0256
3958 | 121.8292 | -5.0583 | 117.0181 | 1.4211e-13 | 0.024587 | 0.015919 | 0.009682 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.034818 | -0.096637 | -0.0033569 | 0.0010705 | 0.037675 | -0.021486 | -0.012988 | 0.024657 | 0.055306 | 0.21522 | -0.09511 | 0.042256 | 0.000359 | -0.033458 | -0.002483 | 0.091543 | -0.10214 | -0.15041 | 4.9632 | -116.9935 | 5.096 | 5.0453 | 0.082122 | -116.9628 | -116.8029 | 4.9079 | -117.0206 | 5.1005 | 5.0248 | 0.11695 | -116.9266 | -117.1203 | 5.0829 | 5.1136 | 5.2735 | 5.0368 | -117.1132 | 5.0558 | 5.1498 | 4.9562 | 5.0586 | -117.1685
3959.7969 | 122.0078 | -4.7333 | 117.3203 | 1.4211e-13 | 0.024587 | 0.015919 | 0.0098956 | -0.023148 | 0.0048523 | 0.22495 | 0.024598 | 0.034604 | -0.096851 | -0.0035705 | 0.00042948 | 0.037675 | -0.021486 | -0.017566 | 0.029236 | 0.059885 | 0.21064 | -0.099689 | 0.037677 | -0.017956 | -0.033458 | -0.002483 | 0.082386 | -0.11129 | -0.15041 | 4.6336 | -117.291 | 4.771 | 4.7157 | 0.082123 | -117.2604 | -117.1096 | 4.5829 | -117.3227 | 4.771 | 4.6998 | 0.11695 | -117.2379 | -117.4315 | 4.7625 | 4.7932 | 4.9439 | 4.7118 | -117.4199 | 4.7308 | 4.8157 | 4.622 | 4.7153 | -117.4707
3961.5469 | 122.0169 | -4.9576 | 117.1051 | 1.4211e-13 | 0.024587 | 0.016133 | 0.010109 | -0.023148 | 0.0044249 | 0.24784 | 0.024598 | 0.034818 | -0.097065 | -0.0035705 | 0.00085668 | 0.037675 | -0.021486 | -0.017566 | 0.033814 | 0.064464 | 0.20607 | -0.099689 | 0.033099 | -0.00422 | -0.038036 | -0.002483 | 0.086964 | -0.097557 | -0.15041 | 4.8579 | -117.0713 | 4.9953 | 4.94 | 0.082123 | -117.0406 | -116.899 | 4.8072 | -117.1076 | 4.9907 | 4.9195 | 0.11238 | -117.0181 | -117.2027 | 4.9914 | 5.022 | 5.1636 | 4.9361 | -117.2048 | 4.9551 | 5.0445 | 4.86 | 4.9534 | -117.2555
3963.3594 | 122.1634 | -5.0034 | 116.9128 | 1.4211e-13 | 0.024374 | 0.016133 | 0.010109 | -0.023362 | 0.0048523 | 0.24021 | 0.024598 | 0.034818 | -0.096851 | -0.0037841 | 0.00064308 | 0.042253 | -0.026065 | -0.022144 | 0.038393 | 0.055306 | 0.21064 | -0.10427 | 0.037677 | -0.008798 | -0.033458 | 0.002095 | 0.091543 | -0.10214 | -0.14583 | 4.8991 | -116.8744 | 5.0456 | 4.9812 | 0.082124 | -116.8575 | -116.7022 | 4.8575 | -116.9107 | 5.041 | 4.9699 | 0.11237 | -116.8213 | -117.015 | 5.0418 | 5.0587 | 5.214 | 4.9773 | -117.0171 | 5.0055 | 5.0949 | 4.9012 | 4.9946 | -117.0587
3965.1562 | 122.0032 | -4.4312 | 117.6224 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.023362 | 0.0044249 | 0.23258 | 0.024385 | 0.034818 | -0.096637 | -0.0037841 | 0.00042948 | 0.042253 | -0.021486 | -0.012988 | 0.038393 | 0.059885 | 0.21064 | -0.099689 | 0.042256 | -0.008798 | -0.028879 | -0.002483 | 0.091543 | -0.10214 | -0.15499 | 4.3315 | -117.584 | 4.4734 | 4.4182 | 0.086701 | -117.5625 | -117.4117 | 4.2762 | -117.6249 | 4.4734 | 4.4023 | 0.12611 | -117.5308 | -117.7245 | 4.4695 | 4.491 | 4.6418 | 4.4097 | -117.7221 | 4.4287 | 4.5227 | 4.329 | 4.4224 | -117.7774
3966.9531 | 122.0718 | -4.3625 | 117.7094 | 1.4211e-13 | 0.024801 | 0.015919 | 0.0094682 | -0.023148 | 0.0050659 | 0.24784 | 0.024598 | 0.034604 | -0.096637 | -0.0037841 | 0.00064308 | 0.037675 | -0.021486 | -0.017566 | 0.029236 | 0.055306 | 0.20607 | -0.09511 | 0.042256 | -0.00422 | -0.033458 | -0.002483 | 0.082386 | -0.11129 | -0.15041 | 4.2674 | -117.6801 | 4.4002 | 4.3449 | 0.077544 | -117.654 | -117.5033 | 4.2121 | -117.7118 | 4.4047 | 4.329 | 0.11695 | -117.627 | -117.8206 | 4.3917 | 4.4178 | 4.5686 | 4.341 | -117.8045 | 4.36 | 4.4449 | 4.2512 | 4.3583 | -117.8598
3968.6719 | 122.0352 | -4.248 | 117.8101 | 1.4211e-13 | 0.024801 | 0.015919 | 0.010109 | -0.023576 | 0.0046387 | 0.24021 | 0.024598 | 0.034818 | -0.096424 | -0.0033569 | 0.00085668 | 0.037675 | -0.021486 | -0.017566 | 0.038393 | 0.055306 | 0.20607 | -0.10427 | 0.042256 | -0.008798 | -0.038036 | -0.01164 | 0.086964 | -0.097557 | -0.15041 | 4.1438 | -117.7717 | 4.2857 | 4.2305 | 0.086702 | -117.7548 | -117.604 | 4.0976 | -117.8217 | 4.2903 | 4.21 | 0.11238 | -117.7231 | -117.9076 | 4.2864 | 4.3034 | 4.4541 | 4.2266 | -117.9143 | 4.2364 | 4.335 | 4.1505 | 4.2392 | -117.9605
3970.4688 | 122.1771 | -4.2572 | 117.746 | 1.4211e-13 | 0.024587 | 0.016133 | 0.010109 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.034818 | -0.096851 | -0.0033569 | 0.00085668 | 0.042253 | -0.026065 | -0.017566 | 0.038393 | 0.055306 | 0.20149 | -0.099689 | 0.037677 | -0.008798 | -0.038036 | -0.002483 | 0.077807 | -0.092979 | -0.15041 | 4.1575 | -117.7076 | 4.2995 | 4.2396 | 0.082123 | -117.6907 | -117.5445 | 4.1068 | -117.7485 | 4.2949 | 4.2192 | 0.11238 | -117.6682 | -117.839 | 4.2956 | 4.3125 | 4.4587 | 4.2311 | -117.8457 | 4.2547 | 4.335 | 4.1642 | 4.2484 | -117.8964
3972.2656 | 122.0535 | -4.0192 | 118.0847 | 1.4211e-13 | 0.024374 | 0.016133 | 0.0098956 | -0.023362 | 0.0044249 | 0.22495 | 0.024385 | 0.034818 | -0.096637 | -0.0037841 | 0.00085668 | 0.037675 | -0.026065 | -0.017566 | 0.042971 | 0.055306 | 0.21064 | -0.09511 | 0.037677 | -0.008798 | -0.033458 | 0.002095 | 0.073228 | -0.092979 | -0.15957 | 3.9241 | -118.0417 | 4.0568 | 4.0016 | 0.077544 | -118.0294 | -117.8741 | 3.8596 | -118.0826 | 4.0568 | 3.9857 | 0.12611 | -118.0115 | -118.1777 | 4.0621 | 4.0745 | 4.2298 | 3.9931 | -118.1798 | 4.0213 | 4.0924 | 3.9262 | 4.0104 | -118.2443
3974 | 122.1817 | -4.0649 | 117.8787 | 1.4211e-13 | 0.024801 | 0.016346 | 0.009682 | -0.023362 | 0.0048523 | 0.24021 | 0.024385 | 0.034604 | -0.09621 | -0.0033569 | 0.00064308 | 0.037675 | -0.016908 | -0.012988 | 0.033814 | 0.055306 | 0.21064 | -0.099689 | 0.042256 | -0.00422 | -0.038036 | 0.002095 | 0.086964 | -0.10214 | -0.15041 | 3.9653 | -117.8449 | 4.1026 | 4.052 | 0.086701 | -117.8234 | -117.6681 | 3.9145 | -117.8766 | 4.1072 | 4.0269 | 0.11238 | -117.7918 | -117.9809 | 4.0988 | 4.1202 | 4.2756 | 4.048 | -117.9784 | 4.067 | 4.1519 | 3.9628 | 4.0607 | -118.0291
3975.7969 | 122.0627 | -4.1245 | 117.952 | 1.4211e-13 | 0.024587 | 0.016346 | 0.010109 | -0.022721 | 0.0046387 | 0.23258 | 0.024812 | 0.03439 | -0.096637 | -0.0033569 | 0.00085668 | 0.028518 | -0.030644 | -0.012988 | 0.033814 | 0.059885 | 0.21522 | -0.09511 | 0.037677 | -0.00422 | -0.033458 | -0.002483 | 0.082386 | -0.10214 | -0.15041 | 4.0293 | -117.9182 | 4.153 | 4.1115 | 0.082122 | -117.8921 | -117.7367 | 3.974 | -117.9544 | 4.1621 | 4.091 | 0.11695 | -117.8696 | -118.0541 | 4.1583 | 4.1843 | 4.3397 | 4.0938 | -118.0471 | 4.122 | 4.2068 | 4.0223 | 4.1202 | -118.1024
3977.6094 | 122.0627 | -4.0558 | 118.0115 | 1.4211e-13 | 0.024587 | 0.015919 | 0.0098956 | -0.023148 | 0.0050659 | 0.23258 | 0.024171 | 0.034604 | -0.096424 | -0.0033569 | 0.00064308 | 0.042253 | -0.021486 | -0.012988 | 0.038393 | 0.055306 | 0.21064 | -0.09511 | 0.037677 | -0.00422 | -0.033458 | 0.002095 | 0.091543 | -0.0884 | -0.15957 | 3.9607 | -117.9731 | 4.098 | 4.0428 | 0.082122 | -117.9562 | -117.8008 | 3.8962 | -118.0094 | 4.0935 | 4.0223 | 0.12611 | -117.9199 | -118.0999 | 4.0942 | 4.1111 | 4.2664 | 4.0343 | -118.1066 | 4.0579 | 4.1473 | 3.9674 | 4.0516 | -118.171
3979.4062 | 122.0215 | -4.0466 | 118.0252 | 1.4211e-13 | 0.024587 | 0.015919 | 0.0098956 | -0.023148 | 0.0046387 | 0.23258 | 0.024171 | 0.034604 | -0.096637 | -0.0037841 | 0.00064308 | 0.037675 | -0.016908 | -0.017566 | 0.033814 | 0.059885 | 0.20607 | -0.09511 | 0.042256 | -0.008798 | -0.033458 | 0.006674 | 0.086964 | -0.097557 | -0.15041 | 3.9515 | -117.9914 | 4.0843 | 4.0291 | 0.077544 | -117.9653 | -117.8191 | 3.8962 | -118.0185 | 4.0889 | 4.0132 | 0.11695 | -117.9382 | -118.1228 | 4.0804 | 4.1065 | 4.2527 | 4.0297 | -118.1203 | 4.0533 | 4.1336 | 3.9491 | 4.0378 | -118.1756
3981.125 | 122.168 | -4.01 | 118.0161 | 1.4211e-13 | 0.024801 | 0.01656 | 0.0098956 | -0.023576 | 0.0046387 | 0.24021 | 0.024598 | 0.035031 | -0.096851 | -0.0033569 | 0.00064308 | 0.042253 | -0.030644 | -0.012988 | 0.038393 | 0.055306 | 0.21064 | -0.09511 | 0.037677 | -0.008798 | -0.047194 | 0.002095 | 0.082386 | -0.10214 | -0.15957 | 3.9149 | -117.9777 | 4.0523 | 3.997 | 0.082122 | -117.9607 | -117.8054 | 3.8504 | -118.014 | 4.0477 | 3.9628 | 0.11238 | -117.9337 | -118.1182 | 4.0484 | 4.0653 | 4.2207 | 3.9794 | -118.1112 | 4.0121 | 4.0924 | 3.9079 | 4.0012 | -118.1756
3982.9219 | 122.1085 | -3.9322 | 118.1168 | 1.4211e-13 | 0.024587 | 0.016346 | 0.009682 | -0.023362 | 0.0046387 | 0.24021 | 0.024385 | 0.034818 | -0.096851 | -0.0037841 | 0.00064308 | 0.042253 | -0.026065 | -0.012988 | 0.033814 | 0.059885 | 0.21522 | -0.099689 | 0.033099 | -0.00422 | -0.033458 | 0.002095 | 0.091543 | -0.097557 | -0.15499 | 3.8325 | -118.0829 | 3.9744 | 3.9192 | 0.086701 | -118.0569 | -117.9015 | 3.7772 | -118.1147 | 3.9653 | 3.8987 | 0.12153 | -118.0252 | -118.2143 | 3.966 | 3.9921 | 4.1474 | 3.9061 | -118.2164 | 3.9343 | 4.0237 | 3.8346 | 3.928 | -118.2718
3984.6875 | 122.1863 | -3.8269 | 118.1808 | 1.4211e-13 | 0.024587 | 0.015919 | 0.009682 | -0.022935 | 0.0048523 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0035705 | 0.00085668 | 0.046831 | -0.021486 | -0.012988 | 0.033814 | 0.055306 | 0.21064 | -0.099689 | 0.037677 | -0.00422 | -0.033458 | 0.011252 | 0.082386 | -0.097557 | -0.15041 | 3.7272 | -118.147 | 3.8737 | 3.8139 | 0.086701 | -118.1255 | -117.9702 | 3.6765 | -118.1696 | 3.8646 | 3.7934 | 0.11695 | -118.0985 | -118.2784 | 3.8607 | 3.8822 | 4.0375 | 3.8054 | -118.2805 | 3.8382 | 3.9093 | 3.7293 | 3.8227 | -118.3313
3986.5 | 122.0718 | -3.9917 | 118.071 | 1.4211e-13 | 0.024587 | 0.016346 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034818 | -0.096851 | -0.0033569 | 0.0010705 | 0.037675 | -0.026065 | -0.022144 | 0.033814 | 0.064464 | 0.20607 | -0.090531 | 0.037677 | -0.008798 | -0.038036 | 0.006674 | 0.082386 | -0.10214 | -0.15957 | 3.9012 | -118.0372 | 4.0294 | 3.9696 | 0.068387 | -118.0065 | -117.8649 | 3.8321 | -118.0643 | 4.0294 | 3.9537 | 0.12153 | -117.9886 | -118.1731 | 4.0255 | 4.0562 | 4.1978 | 3.9656 | -118.1615 | 3.9984 | 4.0741 | 3.8896 | 3.9829 | -118.2306
3988.2188 | 122.1588 | -3.9047 | 118.103 | 1.4211e-13 | 0.024374 | 0.015919 | 0.0098956 | -0.023362 | 0.0048523 | 0.24021 | 0.024812 | 0.034818 | -0.096637 | -0.0033569 | 0.00064308 | 0.042253 | -0.021486 | -0.017566 | 0.042971 | 0.059885 | 0.21522 | -0.099689 | 0.042256 | -0.00422 | -0.033458 | 0.002095 | 0.082386 | -0.097557 | -0.15957 | 3.805 | -118.0601 | 3.947 | 3.8872 | 0.082123 | -118.0431 | -117.8878 | 3.7452 | -118.1009 | 3.947 | 3.8713 | 0.12611 | -118.0206 | -118.2006 | 3.9477 | 3.9646 | 4.1199 | 3.8832 | -118.2027 | 3.9068 | 3.9871 | 3.8072 | 3.9005 | -118.2626
3990 | 122.081 | -4.1702 | 117.9337 | 1.4211e-13 | 0.024587 | 0.016133 | 0.010109 | -0.023362 | 0.0046387 | 0.24021 | 0.024385 | 0.034818 | -0.096637 | -0.0037841 | 0.00064308 | 0.037675 | -0.016908 | -0.012988 | 0.042971 | 0.059885 | 0.21522 | -0.099689 | 0.033099 | -0.00422 | -0.038036 | 0.002095 | 0.091543 | -0.092979 | -0.15499 | 4.0705 | -117.8907 | 4.2079 | 4.1572 | 0.086701 | -117.8738 | -117.7184 | 4.0152 | -117.9316 | 4.2033 | 4.1322 | 0.11695 | -117.8421 | -118.0266 | 4.2132 | 4.2301 | 4.3855 | 4.1533 | -118.0333 | 4.1723 | 4.2618 | 4.0772 | 4.166 | -118.0886
3991.7031 | 122.0627 | -4.1611 | 117.9108 | 1.4211e-13 | 0.024587 | 0.016346 | 0.009682 | -0.023362 | 0.0048523 | 0.23258 | 0.024385 | 0.034818 | -0.096637 | -0.0037841 | 0.00064308 | 0.033096 | -0.030644 | -0.012988 | 0.038393 | 0.059885 | 0.21064 | -0.10427 | 0.037677 | -0.013377 | -0.038036 | 0.006674 | 0.077807 | -0.10214 | -0.15041 | 4.0568 | -117.8724 | 4.1942 | 4.1481 | 0.09128 | -117.8509 | -117.7001 | 4.0107 | -117.9041 | 4.1987 | 4.123 | 0.11238 | -117.833 | -118.0129 | 4.1995 | 4.221 | 4.3717 | 4.1304 | -118.015 | 4.1677 | 4.2389 | 4.0589 | 4.1477 | -118.0612
3993.4688 | 122.081 | -4.216 | 117.9245 | 1.4211e-13 | 0.024587 | 0.016133 | 0.009682 | -0.023148 | 0.0046387 | 0.23258 | 0.024598 | 0.034604 | -0.096851 | -0.0037841 | 0.00064308 | 0.042253 | -0.026065 | -0.017566 | 0.038393 | 0.055306 | 0.20149 | -0.099689 | 0.037677 | -0.008798 | -0.038036 | 0.002095 | 0.077807 | -0.097557 | -0.15499 | 4.1163 | -117.8861 | 4.2583 | 4.1984 | 0.082123 | -117.8692 | -117.723 | 4.061 | -117.9224 | 4.2537 | 4.178 | 0.11695 | -117.8467 | -118.0221 | 4.2544 | 4.2713 | 4.4175 | 4.1899 | -118.0242 | 4.2181 | 4.2938 | 4.1184 | 4.2072 | -118.0795
3995.1719 | 122.1451 | -4.1611 | 117.9062 | 1.4211e-13 | 0.024374 | 0.015919 | 0.009682 | -0.023148 | 0.0046387 | 0.24021 | 0.024598 | 0.034818 | -0.096637 | -0.0035705 | 0.00064308 | 0.042253 | -0.021486 | -0.017566 | 0.042971 | 0.055306 | 0.21064 | -0.099689 | 0.037677 | -0.00422 | -0.042615 | 0.006674 | 0.082386 | -0.10214 | -0.15957 | 4.0614 | -117.8632 | 4.2033 | 4.1435 | 0.082123 | -117.8509 | -117.6955 | 4.0015 | -117.8995 | 4.1987 | 4.1185 | 0.11695 | -117.8238 | -118.0083 | 4.204 | 4.2164 | 4.3717 | 4.1396 | -118.0059 | 4.1677 | 4.2435 | 4.0589 | 4.1569 | -118.0658
3996.9531 | 122.168 | -4.0237 | 117.9749 | 1.4211e-13 | 0.024374 | 0.015919 | 0.009682 | -0.023362 | 0.0048523 | 0.23258 | 0.024598 | 0.034818 | -0.096851 | -0.0033569 | 0.00064308 | 0.033096 | -0.021486 | -0.012988 | 0.038393 | 0.050727 | 0.21522 | -0.099689 | 0.033099 | -0.008798 | -0.033458 | -0.002483 | 0.091543 | -0.10671 | -0.15499 | 3.9241 | -117.9365 | 4.0568 | 4.0108 | 0.086701 | -117.9241 | -117.7596 | 3.8688 | -117.9773 | 4.0568 | 3.9903 | 0.12153 | -117.8833 | -118.0816 | 4.0621 | 4.0745 | 4.239 | 4.0023 | -118.0745 | 4.0213 | 4.1153 | 3.917 | 4.0149 | -118.1298
3998.6719 | 122.168 | -4.1931 | 117.8192 | 1.4211e-13 | 0.024587 | 0.016133 | 0.009682 | -0.023148 | 0.0048523 | 0.22495 | 0.024171 | 0.035245 | -0.096851 | -0.0035705 | 0.00064308 | 0.037675 | -0.016908 | -0.017566 | 0.038393 | 0.059885 | 0.21064 | -0.099689 | 0.033099 | -0.013377 | -0.038036 | 0.002095 | 0.077807 | -0.10214 | -0.15957 | 4.0934 | -117.7808 | 4.2308 | 4.1755 | 0.082123 | -117.7593 | -117.6086 | 4.0335 | -117.8171 | 4.2262 | 4.1551 | 0.12153 | -117.7414 | -117.9214 | 4.2315 | 4.253 | 4.4038 | 4.1762 | -117.9189 | 4.1952 | 4.2709 | 4.091 | 4.1797 | -117.9788
4000.3906 | 122.1039 | -4.1199 | 117.9749 | 1.4211e-13 | 0.024374 | 0.016133 | 0.010109 | -0.023362 | 0.0048523 | 0.23258 | 0.024171 | 0.034818 | -0.096637 | -0.0037841 | 0.00085668 | 0.037675 | -0.030644 | -0.017566 | 0.033814 | 0.059885 | 0.20607 | -0.099689 | 0.037677 | -0.008798 | -0.038036 | 0.006674 | 0.086964 | -0.10214 | -0.15499 | 4.0202 | -117.941 | 4.1575 | 4.1023 | 0.082123 | -117.915 | -117.7688 | 3.9649 | -117.9682 | 4.1576 | 4.0818 | 0.11695 | -117.8879 | -118.077 | 4.1537 | 4.1798 | 4.3259 | 4.0892 | -118.0745 | 4.1265 | 4.2068 | 4.0177 | 4.1111 | -118.1298
4002.1562 | 122.0856 | -4.0512 | 118.0801 | 1.4211e-13 | 0.024587 | 0.015919 | 0.009682 | -0.023362 | 0.0048523 | 0.24784 | 0.024598 | 0.034818 | -0.096424 | -0.0035705 | 0.00064308 | 0.033096 | -0.026065 | -0.022144 | 0.029236 | 0.055306 | 0.20607 | -0.10427 | 0.033099 | -0.00422 | -0.038036 | 0.002095 | 0.086964 | -0.083821 | -0.15957 | 3.9469 | -118.0509 | 4.0843 | 4.0291 | 0.082124 | -118.0248 | -117.8741 | 3.8916 | -118.078 | 4.0843 | 4.0132 | 0.12153 | -117.9932 | -118.164 | 4.0804 | 4.1065 | 4.2573 | 4.0251 | -118.1844 | 4.0533 | 4.1382 | 3.9674 | 4.047 | -118.2397
4004.0156 | 122.0627 | -5.983 | 116.1209 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.023148 | 0.0046387 | 0.22495 | 0.024598 | 0.035031 | -0.097065 | -0.0039979 | 0.0010705 | 0.037675 | -0.021486 | -0.017566 | 0.038393 | 0.059885 | 0.21064 | -0.10427 | 0.037677 | -0.008798 | -0.033458 | -0.002483 | 0.086964 | -0.10671 | -0.15499 | 5.8787 | -116.0825 | 6.0206 | 5.9654 | 0.086702 | -116.061 | -115.9103 | 5.828 | -116.1234 | 6.0206 | 5.9495 | 0.12153 | -116.0339 | -116.2276 | 6.0214 | 6.0429 | 6.1936 | 5.9615 | -116.2252 | 5.9805 | 6.0699 | 5.8763 | 5.9742 | -116.2759
4005.7188 | 122.1405 | -6.6925 | 115.3473 | 1.4211e-13 | 0.024374 | 0.016133 | 0.010109 | -0.023148 | 0.0046387 | 0.23258 | 0.024598 | 0.034604 | -0.096424 | -0.0037841 | 0.00042948 | 0.037675 | -0.016908 | -0.008409 | 0.033814 | 0.059885 | 0.21064 | -0.09511 | 0.042256 | -0.013377 | -0.042615 | 0.002095 | 0.086964 | -0.097557 | -0.15499 | 6.5974 | -115.3135 | 6.7302 | 6.6841 | 0.086701 | -115.2874 | -115.1366 | 6.5375 | -115.3452 | 6.7348 | 6.6499 | 0.11238 | -115.2603 | -115.4448 | 6.7263 | 6.7524 | 6.9032 | 6.6756 | -115.4424 | 6.6946 | 6.7795 | 6.5949 | 6.6791 | -115.5023
4007.4219 | 122.1222 | -5.7449 | 116.2903 | 1.4211e-13 | 0.02416 | 0.015919 | 0.0098956 | -0.023148 | 0.0048523 | 0.22495 | 0.024385 | 0.034818 | -0.096424 | -0.0035705 | 0.00085668 | 0.042253 | -0.021486 | -0.008409 | 0.038393 | 0.046148 | 0.21522 | -0.099689 | 0.042256 | -0.008798 | -0.038036 | 0.006674 | 0.06865 | -0.097557 | -0.15041 | 5.6452 | -116.2519 | 5.7872 | 5.7365 | 0.09128 | -116.2441 | -116.0751 | 5.5945 | -116.2836 | 5.7872 | 5.7069 | 0.11238 | -116.2216 | -116.3878 | 5.7833 | 5.7911 | 5.9602 | 5.7234 | -116.39 | 5.7516 | 5.8136 | 5.6474 | 5.7361 | -116.4407
4009.1406 | 121.3943 | -4.248 | 117.8833 | 1.4211e-13 | 0.024374 | 0.015919 | 0.009682 | -0.022935 | 0.0046387 | 0.24021 | 0.024385 | 0.035031 | -0.096851 | -0.0033569 | 0.00064308 | 0.037675 | -0.016908 | -0.012988 | 0.033814 | 0.055306 | 0.21522 | -0.099689 | 0.02852 | -0.008798 | -0.028879 | -0.002483 | 0.082386 | -0.10214 | -0.15041 | 4.1484 | -117.8495 | 4.2857 | 4.2351 | 0.086701 | -117.828 | -117.6681 | 4.0976 | -117.8858 | 4.2766 | 4.2192 | 0.12153 | -117.8009 | -117.9854 | 4.2819 | 4.3034 | 4.4633 | 4.2311 | -117.983 | 4.2456 | 4.3304 | 4.1459 | 4.2392 | -118.0337
4010.8594 | 121.7056 | -5.0583 | 117.0639 | 1.4211e-13 | 0.024374 | 0.016346 | 0.009682 | -0.022935 | 0.0048523 | 0.24021 | 0.024385 | 0.034818 | -0.09621 | -0.0035705 | 0.0010705 | 0.033096 | -0.016908 | -0.017566 | 0.042971 | 0.064464 | 0.21064 | -0.09511 | 0.033099 | -0.008798 | -0.033458 | 0.006674 | 0.091543 | -0.097557 | -0.15499 | 4.9632 | -117.0209 | 5.0914 | 5.0407 | 0.077544 | -116.9994 | -116.8533 | 4.9033 | -117.0572 | 5.0914 | 5.0248 | 0.12153 | -116.9724 | -117.1615 | 5.1013 | 5.1228 | 5.2689 | 5.0414 | -117.159 | 5.065 | 5.1498 | 4.9607 | 5.0495 | -117.2189
4012.5781 | 121.5775 | -6.514 | 115.6265 | 1.4211e-13 | 0.02416 | 0.016133 | 0.0094682 | -0.022935 | 0.0048523 | 0.23258 | 0.024171 | 0.034818 | -0.096851 | -0.0033569 | 0.00064308 | 0.042253 | -0.016908 | -0.012988 | 0.033814 | 0.055306 | 0.21064 | -0.10885 | 0.046835 | -0.008798 | -0.038036 | 0.002095 | 0.077807 | -0.097557 | -0.15499 | 6.4051 | -115.5927 | 6.5562 | 6.501 | 0.095859 | -115.5712 | -115.4159 | 6.359 | -115.6244 | 6.5608 | 6.4759 | 0.11695 | -115.5487 | -115.7241 | 6.5478 | 6.5693 | 6.7246 | 6.4971 | -115.7354 | 6.5161 | 6.5918 | 6.4164 | 6.5052 | -115.7815
4014.2969 | 122.1451 | -4.2297 | 117.8421 | 1.4211e-13 | 0.024587 | 0.015919 | 0.0094682 | -0.023148 | 0.0046387 | 0.24021 | 0.024598 | 0.034604 | -0.096851 | -0.0037841 | 0.00042948 | 0.042253 | -0.016908 | -0.012988 | 0.033814 | 0.059885 | 0.20607 | -0.10427 | 0.02852 | -0.00422 | -0.033458 | -0.002483 | 0.091543 | -0.10214 | -0.15499 | 4.1255 | -117.8083 | 4.272 | 4.2167 | 0.09128 | -117.7822 | -117.636 | 4.0747 | -117.8446 | 4.2583 | 4.1963 | 0.12153 | -117.7506 | -117.9442 | 4.2635 | 4.2896 | 4.4358 | 4.2128 | -117.9464 | 4.2273 | 4.3213 | 4.1276 | 4.2255 | -117.9971
4016.0156 | 122.0764 | -4.7562 | 117.3706 | 1.4211e-13 | 0.024587 | 0.015919 | 0.009682 | -0.023362 | 0.0046387 | 0.23258 | 0.024385 | 0.034604 | -0.096851 | -0.0035705 | 0.00064308 | 0.037675 | -0.021486 | -0.017566 | 0.033814 | 0.050727 | 0.21064 | -0.099689 | 0.037677 | -0.017956 | -0.038036 | 0.002095 | 0.086964 | -0.097557 | -0.15499 | 4.6565 | -117.3368 | 4.7938 | 4.7386 | 0.082123 | -117.3199 | -117.16 | 4.6012 | -117.3685 | 4.7938 | 4.7181 | 0.11695 | -117.2836 | -117.4682 | 4.79 | 4.8069 | 4.9668 | 4.7347 | -117.4703 | 4.7583 | 4.8431 | 4.6586 | 4.7382 | -117.5256
4017.7188 | 122.1817 | -4.8294 | 117.1509 | 1.4211e-13 | 0.024374 | 0.015705 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.024171 | 0.034818 | -0.096424 | -0.0035705 | 0.00085668 | 0.037675 | -0.026065 | -0.017566 | 0.042971 | 0.059885 | 0.21064 | -0.11342 | 0.037677 | -0.008798 | -0.038036 | -0.002483 | 0.082386 | -0.10671 | -0.15041 | 4.716 | -117.1079 | 4.8671 | 4.8118 | 0.095859 | -117.091 | -116.9402 | 4.679 | -117.1534 | 4.8671 | 4.7914 | 0.11238 | -117.0685 | -117.2576 | 4.8724 | 4.8893 | 5.0401 | 4.8033 | -117.2643 | 4.8269 | 4.9118 | 4.7227 | 4.8206 | -117.3013
4019.4844 | 121.7789 | -4.303 | 117.5446 | 1.4211e-13 | 0.024587 | 0.015919 | 0.009682 | -0.023362 | 0.0048523 | 0.24021 | 0.024385 | 0.035031 | -0.096851 | -0.0039979 | 0.0010705 | 0.037675 | -0.021486 | -0.012988 | 0.033814 | 0.059885 | 0.20607 | -0.099689 | 0.037677 | -0.008798 | -0.047194 | 0.006674 | 0.077807 | -0.092979 | -0.15499 | 4.2033 | -117.5107 | 4.3407 | 4.29 | 0.086701 | -117.4847 | -117.3385 | 4.148 | -117.5379 | 4.3407 | 4.2558 | 0.1078 | -117.4667 | -117.6375 | 4.3368 | 4.3629 | 4.509 | 4.2815 | -117.6442 | 4.3097 | 4.3808 | 4.21 | 4.2942 | -117.6995
4021.1875 | 122.0993 | -4.628 | 117.54 | 1.4211e-13 | 0.024374 | 0.016133 | 0.009682 | -0.023362 | 0.0046387 | 0.24021 | 0.024812 | 0.034818 | -0.096851 | -0.0042115 | 0.00085668 | 0.037675 | -0.026065 | -0.012988 | 0.033814 | 0.059885 | 0.21064 | -0.09511 | 0.042256 | -0.008798 | -0.038036 | 0.002095 | 0.077807 | -0.0884 | -0.14583 | 4.5329 | -117.5062 | 4.6657 | 4.615 | 0.082122 | -117.4801 | -117.3293 | 4.4822 | -117.5379 | 4.6702 | 4.59 | 0.1078 | -117.4622 | -117.6284 | 4.6618 | 4.6879 | 4.8386 | 4.6019 | -117.6351 | 4.6301 | 4.7058 | 4.5396 | 4.6192 | -117.6858
4022.9688 | 121.701 | -3.0167 | 119.1696 | 1.4211e-13 | 0.024374 | 0.016133 | 0.0098956 | -0.023789 | 0.0050659 | 0.23258 | 0.025025 | 0.034818 | -0.096637 | -0.0037841 | 0.00085668 | 0.037675 | -0.021486 | -0.017566 | 0.033814 | 0.050727 | 0.21064 | -0.099689 | 0.033099 | -0.013377 | -0.042615 | 0.006674 | 0.082386 | -0.097557 | -0.15499 | 2.917 | -119.1358 | 3.0543 | 2.9991 | 0.082123 | -119.1189 | -118.959 | 2.8617 | -119.1629 | 3.0498 | 2.974 | 0.11238 | -119.0872 | -119.2672 | 3.0505 | 3.0674 | 3.2273 | 2.9952 | -119.2693 | 3.0233 | 3.099 | 2.9191 | 3.0033 | -119.3246
4024.6875 | 122.1268 | -4.9026 | 117.1967 | 1.4211e-13 | 0.024374 | 0.016133 | 0.0094682 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0035705 | 0.00042948 | 0.037675 | -0.021486 | -0.008409 | 0.038393 | 0.064464 | 0.2198 | -0.09511 | 0.033099 | -0.00422 | -0.038036 | 0.002095 | 0.082386 | -0.097557 | -0.15499 | 4.8075 | -117.1583 | 4.9403 | 4.8942 | 0.086701 | -117.1322 | -116.9769 | 4.7477 | -117.1946 | 4.9357 | 4.8646 | 0.11695 | -117.1143 | -117.2942 | 4.941 | 4.9671 | 5.1225 | 4.8812 | -117.2918 | 4.9047 | 4.985 | 4.8051 | 4.8984 | -117.3516
4026.4531 | 122.168 | -4.0237 | 118.0573 | 1.4211e-13 | 0.024587 | 0.016133 | 0.009682 | -0.023148 | 0.0046387 | 0.23258 | 0.024812 | 0.034818 | -0.096637 | -0.0035705 | 0.00021588 | 0.037675 | -0.030644 | -0.012988 | 0.038393 | 0.059885 | 0.21522 | -0.09511 | 0.037677 | -0.008798 | -0.042615 | -0.007062 | 0.082386 | -0.10214 | -0.15041 | 3.9286 | -118.0189 | 4.0614 | 4.0108 | 0.082122 | -117.9974 | -117.842 | 3.8733 | -118.0643 | 4.0614 | 3.9811 | 0.1078 | -117.9749 | -118.1594 | 4.0621 | 4.0836 | 4.239 | 3.9931 | -118.1524 | 4.0167 | 4.1061 | 3.9216 | 4.0149 | -118.2077
4028.1562 | 122.287 | -3.7308 | 118.309 | 1.4211e-13 | 0.024374 | 0.015492 | 0.0098956 | -0.023148 | 0.0052797 | 0.24021 | 0.024598 | 0.034818 | -0.096637 | -0.0039979 | 0.00085668 | 0.033096 | -0.016908 | -0.017566 | 0.033814 | 0.064464 | 0.21064 | -0.13174 | 0.037677 | -0.00422 | -0.033458 | -0.002483 | 0.077807 | -0.10214 | -0.15957 | 3.599 | -118.2752 | 3.7639 | 3.7132 | 0.11417 | -118.2446 | -118.0984 | 3.5712 | -118.3115 | 3.7685 | 3.6973 | 0.12611 | -118.2312 | -118.4112 | 3.7646 | 3.7952 | 3.9414 | 3.7139 | -118.4408 | 3.7283 | 3.8086 | 3.6286 | 3.7266 | -118.4686
4029.875 | 121.3165 | -120.9869 | 0.10986 | 1.4211e-13 | 0.024374 | 0.016133 | 0.009682 | -0.023148 | 0.0044249 | 0.24784 | 0.024385 | 0.034818 | -0.096637 | -0.0037841 | 0.00085668 | 0.074302 | 0.019721 | 0.01906 | 0.07502 | 0.1011 | 0.25185 | -0.063057 | 0.078886 | 0.018674 | -0.001407 | 0.034145 | 0.12359 | 0.016908 | -0.12752 | 120.9239 | -0.034843 | 121.0612 | 121.006 | 0.082117 | -0.008768 | 0.14199 | 120.8594 | -0.075718 | 121.0658 | 120.9855 | 0.12611 | 0.01373 | -0.092955 | 121.062 | 121.088 | 121.2388 | 121.0067 | -0.17292 | 121.0211 | 121.1105 | 121.0038 | 121.0056 | -0.23738
4031.5781 | 121.3303 | -120.1904 | 1.1261 | 1.4211e-13 | 0.024374 | 0.016133 | 0.009682 | -0.023362 | 0.0042113 | 0.22495 | 0.024385 | 0.034818 | -0.096424 | -0.0037841 | 0.00085668 | 0.083459 | 0.015142 | 0.01906 | 0.070441 | 0.096516 | 0.24727 | -0.058478 | 0.074307 | 0.018674 | 0.003172 | 0.038723 | 0.11444 | 0.026065 | -0.11836 | 120.132 | -1.0557 | 120.2739 | 120.2095 | 0.077538 | -1.0296 | -0.87882 | 120.0721 | -1.0874 | 120.2647 | 120.1936 | 0.12153 | -1.0117 | -1.1 | 120.2609 | 120.2869 | 120.4377 | 120.2056 | -1.1846 | 120.2292 | 120.3049 | 120.2165 | 120.2091 | -1.2445
4033.2969 | 121.3852 | -6.3995 | 114.2578 | 1.4211e-13 | 0.024587 | 0.015919 | 0.010109 | -0.023362 | 0.0052797 | 0.24021 | 0.024812 | 0.035031 | -0.096424 | -0.0035705 | 0.00042948 | 0.042253 | -0.016908 | -0.017566 | 0.033814 | 0.059885 | 0.21064 | -0.10427 | 0.042256 | -0.008798 | -0.033458 | 0.002095 | 0.082386 | -0.092979 | -0.15041 | 6.2953 | -114.224 | 6.4418 | 6.382 | 0.086702 | -114.1979 | -114.0472 | 6.2491 | -114.2557 | 6.4418 | 6.3661 | 0.11695 | -114.1754 | -114.3508 | 6.4333 | 6.4594 | 6.6102 | 6.3826 | -114.3621 | 6.4016 | 6.4819 | 6.3066 | 6.3907 | -114.4082
4035.0156 | 121.2479 | -8.6517 | 105.8533 | 1.4211e-13 | 0.024587 | 0.015919 | 0.010109 | -0.023576 | 0.0044249 | 0.23258 | 0.024598 | 0.034604 | -0.096637 | -0.0035705 | 0.00064308 | 0.037675 | -0.012329 | -0.012988 | 0.038393 | 0.059885 | 0.21522 | -0.099689 | 0.037677 | 0.000359 | -0.033458 | 0.011252 | 0.082386 | -0.10214 | -0.15499 | 8.552 | -105.8149 | 8.6894 | 8.6387 | 0.086701 | -105.7934 | -105.638 | 8.4967 | -105.842 | 8.6894 | 8.6183 | 0.12153 | -105.7709 | -105.9554 | 8.6901 | 8.7116 | 8.867 | 8.6394 | -105.953 | 8.663 | 8.7341 | 8.5496 | 8.6521 | -106.0083
4036.7656 | 121.1151 | -8.8852 | 112.1613 | 1.4211e-13 | 0.024374 | 0.016346 | 0.0098956 | -0.023362 | 0.0048523 | 0.23258 | 0.024812 | 0.034818 | -0.096637 | -0.0037841 | 0.00064308 | 0.046831 | -0.021486 | -0.012988 | 0.038393 | 0.059885 | 0.21522 | -0.09511 | 0.037677 | -0.013377 | -0.028879 | -0.002483 | 0.086964 | -0.097557 | -0.15041 | 8.7901 | -112.1229 | 8.932 | 8.8722 | 0.082122 | -112.1014 | -111.946 | 8.7348 | -112.1637 | 8.9229 | 8.8563 | 0.12153 | -112.0743 | -112.2588 | 8.9236 | 8.9451 | 9.1004 | 8.8637 | -112.2564 | 8.8827 | 8.9722 | 8.7876 | 8.8718 | -112.3117
4038.4844 | 121.3486 | -6.5277 | 114.473 | 1.4211e-13 | 0.024587 | 0.016133 | 0.0094682 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.03439 | -0.096851 | -0.0037841 | 0.00064308 | 0.037675 | -0.021486 | -0.017566 | 0.038393 | 0.059885 | 0.21064 | -0.099689 | 0.033099 | -0.008798 | -0.038036 | 0.002095 | 0.086964 | -0.10671 | -0.15041 | 6.428 | -114.4346 | 6.5654 | 6.5101 | 0.082123 | -114.4131 | -114.2623 | 6.3773 | -114.4709 | 6.5608 | 6.4897 | 0.11238 | -114.386 | -114.5797 | 6.5661 | 6.5876 | 6.7384 | 6.5062 | -114.5726 | 6.5298 | 6.6147 | 6.421 | 6.5189 | -114.6234
4040.2031 | 121.7514 | -107.9269 | 13.3255 | 1.4211e-13 | 0.024587 | 0.016346 | 0.009682 | -0.023362 | 0.0048523 | 0.24021 | 0.024812 | 0.035031 | -0.097065 | -0.0035705 | 0.00064308 | 0.074302 | 0.005985 | 0.009904 | 0.061284 | 0.091937 | 0.23812 | -0.058478 | 0.069728 | 0.014095 | 0.003172 | 0.038723 | 0.11901 | 0.012329 | -0.11378 | 107.8685 | -13.2642 | 108.0012 | 107.9368 | 0.068382 | -13.2336 | -13.0874 | 107.8132 | -13.2868 | 107.9967 | 107.9301 | 0.11695 | -13.2065 | -13.3132 | 107.9882 | 108.0189 | 108.1651 | 107.9329 | -13.384 | 107.9657 | 108.046 | 107.9393 | 107.941 | -13.4393
4041.9688 | 121.3394 | -42.3431 | 78.9917 | 1.4211e-13 | 0.024587 | 0.015919 | 0.0094682 | -0.022935 | 0.0048523 | 0.21732 | 0.024598 | 0.034818 | -0.096851 | -0.0037841 | 0.00064308 | 0.05141 | -0.012329 | -0.003831 | 0.042971 | 0.064464 | 0.22438 | -0.09511 | 0.060571 | 0.004938 | -0.015143 | 0.011252 | 0.1007 | -0.10214 | -0.14125 | 42.248 | -78.9487 | 42.3945 | 42.3393 | 0.091279 | -78.9272 | -78.7673 | 42.2019 | -78.9804 | 42.4037 | 42.328 | 0.12611 | -78.891 | -79.0938 | 42.3861 | 42.4076 | 42.5675 | 42.3308 | -79.0868 | 42.3544 | 42.4438 | 42.241 | 42.3481 | -79.133
4043.7188 | 121.3943 | -22.0184 | 99.4583 | 1.4211e-13 | 0.024587 | 0.015705 | 0.009682 | -0.023362 | 0.0050659 | 0.23258 | 0.024385 | 0.034604 | -0.096851 | -0.0042115 | 0.00085668 | 0.046831 | -0.016908 | -0.003831 | 0.042971 | 0.059885 | 0.21064 | -0.099689 | 0.046835 | -0.00422 | -0.028879 | 0.011252 | 0.082386 | -0.10214 | -0.13668 | 21.9187 | -99.4153 | 22.0653 | 22.0146 | 0.095858 | -99.3984 | -99.2477 | 21.8818 | -99.4471 | 22.0653 | 21.9896 | 0.1078 | -99.3759 | -99.5604 | 22.0614 | 22.0783 | 22.2291 | 22.0015 | -99.558 | 22.0297 | 22.1008 | 21.9163 | 22.0142 | -99.595
4045.4375 | 121.1655 | -13.9755 | 107.1716 | 1.4211e-13 | 0.024374 | 0.016133 | 0.009682 | -0.022935 | 0.0048523 | 0.24021 | 0.024598 | 0.034818 | -0.096424 | -0.0037841 | 0.00085668 | 0.037675 | -0.016908 | -0.008409 | 0.042971 | 0.064464 | 0.21522 | -0.090531 | 0.042256 | -0.008798 | -0.038036 | 0.002095 | 0.086964 | -0.10214 | -0.14583 | 13.885 | -107.1287 | 14.0132 | 13.9671 | 0.082122 | -107.1072 | -106.9564 | 13.8297 | -107.1695 | 14.0178 | 13.9375 | 0.1078 | -107.0847 | -107.2738 | 14.0185 | 14.04 | 14.1907 | 13.9586 | -107.2622 | 13.9776 | 14.0625 | 13.8734 | 13.9667 | -107.3175
4047.1562 | 120.8908 | -7.8369 | 113.0173 | 1.4211e-13 | 0.024587 | 0.015919 | 0.0094682 | -0.023148 | 0.0050659 | 0.23258 | 0.024385 | 0.034818 | -0.096637 | -0.0035705 | 0.00085668 | 0.042253 | -0.016908 | -0.017566 | 0.033814 | 0.055306 | 0.20607 | -0.099689 | 0.046835 | -0.00422 | -0.033458 | -0.002483 | 0.082386 | -0.10214 | -0.15499 | 7.7372 | -112.9835 | 7.8792 | 7.8193 | 0.082123 | -112.962 | -112.8112 | 7.6819 | -113.0198 | 7.8837 | 7.8035 | 0.12153 | -112.9349 | -113.1194 | 7.8707 | 7.8922 | 8.043 | 7.82 | -113.117 | 7.8344 | 7.9193 | 7.7348 | 7.8327 | -113.1723
4048.9219 | 98.8861 | -8.0933 | 113.5437 | 1.4211e-13 | 0.024587 | 0.015919 | 0.0098956 | -0.023148 | 0.0050659 | 0.24021 | 0.024385 | 0.034818 | -0.096424 | -0.0037841 | 0.00085668 | 0.042253 | -0.016908 | -0.017566 | 0.042971 | 0.059885 | 0.21522 | -0.099689 | 0.046835 | -0.013377 | -0.028879 | -0.002483 | 0.086964 | -0.097557 | -0.15041 | 7.9936 | -113.5007 | 8.1355 | 8.0757 | 0.082123 | -113.4838 | -113.3285 | 7.9428 | -113.5462 | 8.1401 | 8.0644 | 0.12153 | -113.4567 | -113.6413 | 8.1362 | 8.1531 | 8.3085 | 8.0764 | -113.6434 | 8.0908 | 8.1802 | 7.9957 | 8.0799 | -113.6941
4050.6406 | 100.0397 | -21.1533 | 74.5056 | 1.4211e-13 | 0.024587 | 0.015919 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034818 | -0.096424 | -0.0037841 | 0.00064308 | 0.046831 | -0.007751 | -0.008409 | 0.042971 | 0.069043 | 0.2198 | -0.090531 | 0.051413 | 0.004938 | -0.0243 | 0.011252 | 0.096121 | -0.065507 | -0.15041 | 21.0627 | -74.4626 | 21.2001 | 21.1448 | 0.082122 | -74.4366 | -74.2858 | 21.0028 | -74.4944 | 21.2047 | 21.129 | 0.12611 | -74.4095 | -74.5711 | 21.1962 | 21.2223 | 21.3731 | 21.1455 | -74.5961 | 21.1645 | 21.2494 | 21.0878 | 21.1582 | -74.656
4052.3594 | 121.1014 | -16.8961 | 103.8483 | 1.4211e-13 | 0.024587 | 0.01656 | 0.0098956 | -0.022935 | 0.0048523 | 0.24021 | 0.024385 | 0.03439 | -0.096424 | -0.0039979 | 0.00085668 | 0.046831 | -0.012329 | -0.017566 | 0.033814 | 0.064464 | 0.21522 | -0.09511 | 0.042256 | -0.00422 | -0.033458 | 0.006674 | 0.091543 | -0.097557 | -0.15041 | 16.8009 | -103.8145 | 16.9429 | 16.8785 | 0.077544 | -103.7838 | -103.633 | 16.7456 | -103.8416 | 16.9383 | 16.8626 | 0.11695 | -103.7567 | -103.9458 | 16.9299 | 16.9605 | 17.1113 | 16.8837 | -103.9434 | 16.9027 | 16.9876 | 16.7985 | 16.8918 | -103.9987
4054.0781 | 111.3235 | -15.9668 | 100.5066 | 1.4211e-13 | 0.024587 | 0.016346 | 0.009682 | -0.023148 | 0.0046387 | 0.24784 | 0.024598 | 0.035031 | -0.096851 | -0.0037841 | 0.00085668 | 0.042253 | -0.021486 | -0.008409 | 0.033814 | 0.064464 | 0.2198 | -0.09511 | 0.042256 | 0.000359 | -0.033458 | 0.002095 | 0.077807 | -0.10214 | -0.15041 | 15.8717 | -100.4728 | 16.009 | 15.9584 | 0.086701 | -100.4421 | -100.2868 | 15.8164 | -100.5045 | 16.0091 | 15.9333 | 0.11695 | -100.4288 | -100.6087 | 16.0006 | 16.0313 | 16.1866 | 15.9453 | -100.6017 | 15.9689 | 16.0446 | 15.8647 | 15.9672 | -100.657
4055.7812 | 121.0098 | -14.1357 | 106.3477 | 1.4211e-13 | 0.024374 | 0.015705 | 0.0092546 | -0.023148 | 0.0048523 | 0.24021 | 0.024598 | 0.034818 | -0.096637 | -0.0037841 | 0.00064308 | 0.037675 | -0.016908 | -0.012988 | 0.033814 | 0.059885 | 0.20607 | -0.099689 | 0.037677 | -0.00422 | -0.028879 | 0.006674 | 0.086964 | -0.083821 | -0.15041 | 14.0361 | -106.3138 | 14.1734 | 14.1228 | 0.086701 | -106.2878 | -106.1416 | 13.9853 | -106.341 | 14.1734 | 14.1069 | 0.12153 | -106.2607 | -106.4315 | 14.1696 | 14.1956 | 14.3418 | 14.1188 | -106.4473 | 14.1424 | 14.2227 | 14.0519 | 14.1315 | -106.4981
4057.4844 | 121.907 | -87.6801 | 33.7234 | 1.4211e-13 | 0.024374 | 0.015919 | 0.0094682 | -0.023148 | 0.0048523 | 0.24784 | 0.024598 | 0.034818 | -0.096637 | -0.0037841 | 0.00085668 | 0.055988 | -0.003172 | 0.000747 | 0.052128 | 0.069043 | 0.22896 | -0.085952 | 0.046835 | 0.004938 | -0.0243 | 0.011252 | 0.1007 | -0.079243 | -0.14125 | 87.5941 | -33.6713 | 87.736 | 87.6808 | 0.086699 | -33.6544 | -33.4945 | 87.5388 | -33.7122 | 87.7269 | 87.6558 | 0.11695 | -33.6227 | -33.8027 | 87.7322 | 87.7491 | 87.909 | 87.6769 | -33.8094 | 87.6913 | 87.7808 | 87.6008 | 87.685 | -33.8647
4059.1875 | 121.8338 | -59.9808 | 61.4731 | 1.4211e-13 | 0.024374 | 0.015919 | 0.009682 | -0.023148 | 0.0048523 | 0.24021 | 0.024812 | 0.034177 | -0.096637 | -0.0037841 | 0.00042948 | 0.055988 | -0.012329 | 0.000747 | 0.042971 | 0.073622 | 0.22896 | -0.081373 | 0.051413 | 0.009516 | -0.0243 | 0.011252 | 0.1007 | -0.0884 | -0.14125 | 59.8994 | -61.4301 | 60.0368 | 59.9815 | 0.08212 | -61.3995 | -61.2441 | 59.8395 | -61.4618 | 60.0322 | 59.9565 | 0.11695 | -61.3724 | -61.5615 | 60.0237 | 60.0544 | 60.2097 | 59.9684 | -61.5545 | 59.992 | 60.0815 | 59.8924 | 59.9903 | -61.6143
4060.8906 | 112.6923 | -9.343 | 86.2152 | 1.4211e-13 | 0.024587 | 0.016346 | 0.009682 | -0.023362 | 0.0048523 | 0.24784 | 0.024171 | 0.03439 | -0.096424 | -0.0035705 | 0.00042948 | 0.042253 | -0.021486 | -0.017566 | 0.038393 | 0.069043 | 0.20607 | -0.099689 | 0.037677 | -0.00422 | -0.038036 | 0.006674 | 0.082386 | -0.10214 | -0.15041 | 9.2433 | -86.1768 | 9.3852 | 9.3254 | 0.082123 | -86.1462 | -86.0091 | 9.1925 | -86.2085 | 9.3806 | 9.3049 | 0.11238 | -86.1328 | -86.3173 | 9.3813 | 9.412 | 9.549 | 9.3215 | -86.3149 | 9.3496 | 9.4253 | 9.2408 | 9.3387 | -86.3656
4062.625 | 121.8292 | -9.2239 | 111.5524 | 1.4211e-13 | 0.024374 | 0.016133 | 0.009682 | -0.023362 | 0.0046387 | 0.23258 | 0.024598 | 0.034818 | -0.096637 | -0.0035705 | 0.00064308 | 0.037675 | -0.021486 | -0.012988 | 0.038393 | 0.055306 | 0.21064 | -0.099689 | 0.037677 | -0.00422 | -0.038036 | 0.002095 | 0.077807 | -0.10214 | -0.15041 | 9.1242 | -111.514 | 9.2616 | 9.211 | 0.086701 | -111.4971 | -111.3418 | 9.0735 | -111.5503 | 9.2616 | 9.1859 | 0.11238 | -111.4746 | -111.6546 | 9.2623 | 9.2792 | 9.4346 | 9.2025 | -111.6521 | 9.226 | 9.3017 | 9.1218 | 9.2197 | -111.7028
4064.3281 | 121.431 | -11.5997 | 109.845 | 1.4211e-13 | 0.024374 | 0.015705 | 0.0094682 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034818 | -0.096851 | -0.0035705 | 0.00064308 | 0.037675 | -0.016908 | -0.008409 | 0.038393 | 0.059885 | 0.21522 | -0.09511 | 0.042256 | -0.013377 | -0.033458 | 0.002095 | 0.086964 | -0.074664 | -0.15499 | 11.5046 | -109.8066 | 11.6374 | 11.5913 | 0.086701 | -109.7851 | -109.6297 | 11.4447 | -109.8429 | 11.642 | 11.5663 | 0.12153 | -109.758 | -109.9196 | 11.6381 | 11.6596 | 11.815 | 11.5828 | -109.9401 | 11.6018 | 11.6867 | 11.5251 | 11.5864 | -110
4066.0469 | 121.3577 | -10.0113 | 110.9253 | 1.4211e-13 | 0.024374 | 0.015919 | 0.0094682 | -0.023148 | 0.0048523 | 0.22495 | 0.024385 | 0.034818 | -0.096637 | -0.0035705 | 0.00085668 | 0.042253 | -0.021486 | -0.008409 | 0.038393 | 0.064464 | 0.21522 | -0.090531 | 0.042256 | -0.00422 | -0.038036 | 0.006674 | 0.086964 | -0.10214 | -0.15499 | 9.9208 | -110.8869 | 10.0535 | 10.0029 | 0.082122 | -110.8608 | -110.7101 | 9.8563 | -110.9186 | 10.0535 | 9.9733 | 0.11695 | -110.8383 | -111.0274 | 10.0497 | 10.0758 | 10.2265 | 9.9898 | -111.0158 | 10.018 | 10.0983 | 9.9092 | 10.0071 | -111.0803
4067.75 | 121.8613 | -8.8806 | 111.9736 | 1.4211e-13 | 0.02416 | 0.015705 | 0.0098956 | -0.023148 | 0.0050659 | 0.24021 | 0.024598 | 0.034818 | -0.096424 | -0.0039979 | 0.00085668 | 0.037675 | -0.021486 | -0.012988 | 0.038393 | 0.059885 | 0.21064 | -0.09511 | 0.042256 | -0.013377 | -0.033458 | 0.002095 | 0.077807 | -0.092979 | -0.15499 | 8.7855 | -111.9352 | 8.9183 | 8.8676 | 0.082122 | -111.9137 | -111.7629 | 8.7256 | -111.9715 | 8.9229 | 8.8472 | 0.12153 | -111.8958 | -112.0666 | 8.919 | 8.9405 | 9.0913 | 8.8591 | -112.0687 | 8.8827 | 8.9584 | 8.7876 | 8.8672 | -112.1286
4069.4531 | 121.0556 | -10.5377 | 111.1496 | 1.4211e-13 | 0.02416 | 0.016133 | 0.0094682 | -0.022935 | 0.0048523 | 0.23258 | 0.024385 | 0.035245 | -0.09621 | -0.0035705 | 0.00042948 | 0.042253 | -0.016908 | -0.017566 | 0.047549 | 0.055306 | 0.21064 | -0.099689 | 0.037677 | -0.008798 | -0.038036 | 0.006674 | 0.086964 | -0.10214 | -0.15499 | 10.438 | -111.102 | 10.58 | 10.5202 | 0.082123 | -111.0943 | -110.939 | 10.3827 | -111.1429 | 10.5754 | 10.4997 | 0.11695 | -111.0626 | -111.2517 | 10.5853 | 10.593 | 10.7484 | 10.5208 | -111.2493 | 10.5444 | 10.6247 | 10.4356 | 10.5289 | -111.3046
4071.1562 | 101.3535 | -9.407 | 92.157 | 1.4211e-13 | 0.024801 | 0.016133 | 0.0098956 | -0.023148 | 0.0050659 | 0.24784 | 0.024598 | 0.034818 | -0.096424 | -0.0042115 | 0.0010705 | 0.05141 | -0.016908 | -0.017566 | 0.038393 | 0.059885 | 0.21522 | -0.09511 | 0.042256 | -0.00422 | -0.028879 | 0.006674 | 0.073228 | -0.092979 | -0.15041 | 9.3119 | -92.1186 | 9.4585 | 9.3895 | 0.077544 | -92.0971 | -91.9418 | 9.2566 | -92.1503 | 9.4493 | 9.3782 | 0.12153 | -92.0838 | -92.25 | 9.4454 | 9.4669 | 9.6223 | 9.3901 | -92.2521 | 9.4137 | 9.4803 | 9.3141 | 9.4028 | -92.3074
4072.8906 | 121.4264 | -10.2219 | 110.8704 | 1.4211e-13 | 0.024587 | 0.016133 | 0.009682 | -0.023362 | 0.0046387 | 0.24784 | 0.024385 | 0.034818 | -0.096637 | -0.0042115 | 0.00085668 | 0.042253 | -0.016908 | -0.003831 | 0.038393 | 0.059885 | 0.21522 | -0.090531 | 0.042256 | -0.00422 | -0.033458 | -0.007062 | 0.086964 | -0.097557 | -0.15499 | 10.1313 | -110.832 | 10.2641 | 10.218 | 0.0867 | -110.8105 | -110.6551 | 10.0669 | -110.8774 | 10.2641 | 10.1884 | 0.12153 | -110.7834 | -110.9679 | 10.2603 | 10.2817 | 10.4371 | 10.205 | -110.9609 | 10.2148 | 10.3088 | 10.1243 | 10.2176 | -111.0254
4074.6562 | 121.4813 | -9.9426 | 111.0489 | 1.4211e-13 | 0.02416 | 0.016133 | 0.009682 | -0.023148 | 0.0048523 | 0.23258 | 0.024598 | 0.034604 | -0.096637 | -0.0037841 | 0.00042948 | 0.033096 | -0.016908 | -0.017566 | 0.038393 | 0.064464 | 0.21522 | -0.09511 | 0.037677 | -0.008798 | -0.038036 | 0.002095 | 0.086964 | -0.097557 | -0.15041 | 9.8475 | -111.0105 | 9.9757 | 9.9251 | 0.077544 | -110.9844 | -110.8337 | 9.7922 | -111.0468 | 9.9803 | 9.9046 | 0.11238 | -110.9619 | -111.1464 | 9.981 | 10.0071 | 10.1579 | 9.9257 | -111.144 | 9.9447 | 10.0296 | 9.8451 | 9.9338 | -111.1993
4076.375 | 121.257 | -10.6339 | 110.5362 | 1.4211e-13 | 0.024374 | 0.015919 | 0.009682 | -0.023148 | 0.0050659 | 0.24784 | 0.024171 | 0.035031 | -0.096851 | -0.0037841 | 0.00042948 | 0.046831 | -0.016908 | -0.012988 | 0.033814 | 0.059885 | 0.21064 | -0.099689 | 0.033099 | -0.008798 | -0.038036 | 0.011252 | 0.082386 | -0.10214 | -0.15957 | 10.5342 | -110.5024 | 10.6807 | 10.6209 | 0.086701 | -110.4763 | -110.3255 | 10.4743 | -110.5249 | 10.6669 | 10.5958 | 0.12153 | -110.4538 | -110.6383 | 10.6677 | 10.6937 | 10.8445 | 10.6169 | -110.6359 | 10.6451 | 10.7162 | 10.5317 | 10.6251 | -110.6958
4078.0781 | 121.4401 | -10.2219 | 111.3052 | 1.4211e-13 | 0.024801 | 0.016133 | 0.009682 | -0.022935 | 0.0050659 | 0.24021 | 0.024171 | 0.034818 | -0.09621 | -0.0035705 | 0.00064308 | 0.037675 | -0.016908 | -0.008409 | 0.033814 | 0.059885 | 0.21522 | -0.090531 | 0.042256 | 0.000359 | -0.038036 | -0.002483 | 0.086964 | -0.10214 | -0.15499 | 10.1313 | -111.2714 | 10.2595 | 10.2135 | 0.082122 | -111.2454 | -111.09 | 10.0669 | -111.3077 | 10.2641 | 10.1838 | 0.11695 | -111.2183 | -111.4074 | 10.2557 | 10.2817 | 10.4371 | 10.205 | -111.3958 | 10.2194 | 10.3088 | 10.1197 | 10.2222 | -111.4602
4079.7812 | 121.4264 | -9.9884 | 111.5433 | 1.4211e-13 | 0.02416 | 0.016133 | 0.0098956 | -0.022935 | 0.0048523 | 0.22495 | 0.024385 | 0.034818 | -0.096424 | -0.0037841 | 0.00085668 | 0.033096 | -0.016908 | -0.012988 | 0.038393 | 0.055306 | 0.21522 | -0.09511 | 0.042256 | -0.008798 | -0.038036 | -0.002483 | 0.082386 | -0.10214 | -0.15041 | 9.8933 | -111.5049 | 10.0215 | 9.9754 | 0.082122 | -111.488 | -111.328 | 9.838 | -111.5458 | 10.0307 | 9.9504 | 0.11238 | -111.4609 | -111.6454 | 10.0268 | 10.0437 | 10.2036 | 9.9715 | -111.6384 | 9.9859 | 10.0708 | 9.8863 | 9.9796 | -111.6937
4081.4844 | 121.1792 | -7.7408 | 112.9532 | 1.4211e-13 | 0.024374 | 0.016346 | 0.0098956 | -0.023362 | 0.0048523 | 0.24021 | 0.024385 | 0.034604 | -0.096851 | -0.0035705 | 0.00085668 | 0.037675 | -0.016908 | -0.008409 | 0.033814 | 0.055306 | 0.21064 | -0.090531 | 0.037677 | -0.013377 | -0.038036 | -0.002483 | 0.091543 | -0.10671 | -0.15499 | 7.6503 | -112.9194 | 7.7785 | 7.7324 | 0.082122 | -112.8979 | -112.7425 | 7.5858 | -112.9557 | 7.7785 | 7.7027 | 0.11695 | -112.8616 | -113.0599 | 7.7746 | 7.7961 | 7.9514 | 7.7239 | -113.0437 | 7.7383 | 7.8323 | 7.6341 | 7.7274 | -113.1082
4083.2031 | 121.1746 | -7.7591 | 113.2233 | 1.4211e-13 | 0.024374 | 0.01656 | 0.009682 | -0.022935 | 0.0050659 | 0.24784 | 0.024385 | 0.034818 | -0.096851 | -0.0039979 | 0.00042948 | 0.042253 | -0.021486 | -0.017566 | 0.038393 | 0.059885 | 0.20607 | -0.09511 | 0.037677 | -0.013377 | -0.038036 | 0.006674 | 0.082386 | -0.10214 | -0.15499 | 7.664 | -113.1849 | 7.8013 | 7.7415 | 0.077544 | -113.1634 | -113.0172 | 7.6041 | -113.2166 | 7.7968 | 7.7211 | 0.11695 | -113.1409 | -113.3254 | 7.7975 | 7.819 | 7.9652 | 7.7376 | -113.3184 | 7.7658 | 7.8415 | 7.657 | 7.7457 | -113.3783
4084.9688 | 104.4525 | -7.6813 | 113.0676 | 1.4211e-13 | 0.024374 | 0.016346 | 0.009682 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.034604 | -0.096424 | -0.0037841 | 0.00064308 | 0.042253 | -0.016908 | -0.017566 | 0.033814 | 0.064464 | 0.21522 | -0.09511 | 0.037677 | -0.008798 | -0.038036 | -0.002483 | 0.082386 | -0.079243 | -0.15041 | 7.5862 | -113.0338 | 7.7235 | 7.6637 | 0.077544 | -113.0032 | -112.8524 | 7.5309 | -113.0701 | 7.719 | 7.6432 | 0.11238 | -112.9852 | -113.1469 | 7.7151 | 7.7457 | 7.8965 | 7.6644 | -113.1627 | 7.6788 | 7.7637 | 7.602 | 7.6725 | -113.218
4086.6719 | 92.1661 | -8.194 | 86.3892 | 1.4211e-13 | 0.023946 | 0.016133 | 0.0098956 | -0.022935 | 0.0048523 | 0.23258 | 0.024598 | 0.034818 | -0.096424 | -0.0035705 | 0.0010705 | 0.037675 | -0.016908 | -0.012988 | 0.033814 | 0.059885 | 0.20607 | -0.099689 | 0.033099 | -0.00422 | -0.033458 | 0.006674 | 0.086964 | -0.10214 | -0.15499 | 8.0943 | -86.3553 | 8.2316 | 8.181 | 0.086701 | -86.3293 | -86.1831 | 8.039 | -86.3825 | 8.2271 | 8.1605 | 0.12153 | -86.3022 | -86.4913 | 8.2278 | 8.2539 | 8.4 | 8.1771 | -86.4888 | 8.2006 | 8.2809 | 8.0918 | 8.1898 | -86.5442
4088.4062 | 103.5507 | -7.9147 | 97.0413 | 1.4211e-13 | 0.024587 | 0.016133 | 0.0094682 | -0.023148 | 0.0050659 | 0.23258 | 0.024385 | 0.034818 | -0.096851 | -0.0037841 | 0.00064308 | 0.046831 | -0.007751 | -0.012988 | 0.038393 | 0.064464 | 0.21064 | -0.09511 | 0.037677 | -0.008798 | -0.033458 | -0.002483 | 0.082386 | -0.10214 | -0.15499 | 7.8196 | -97.0029 | 7.9616 | 7.9017 | 0.082122 | -96.9769 | -96.8307 | 7.7597 | -97.0438 | 7.9524 | 7.8813 | 0.12153 | -96.9589 | -97.1435 | 7.9531 | 7.9792 | 8.1254 | 7.907 | -97.1364 | 7.9123 | 7.9971 | 7.8126 | 7.9059 | -97.1963
4090.1094 | 110.8475 | -7.9834 | 113.5345 | 1.4211e-13 | 0.02416 | 0.016346 | 0.0092546 | -0.023148 | 0.0046387 | 0.24021 | 0.024598 | 0.034818 | -0.096424 | -0.0033569 | 0.00064308 | 0.037675 | -0.007751 | -0.012988 | 0.029236 | 0.055306 | 0.21064 | -0.099689 | 0.042256 | -0.013377 | -0.033458 | -0.002483 | 0.082386 | -0.11129 | -0.15499 | 7.8837 | -113.5053 | 8.0211 | 7.9704 | 0.086701 | -113.4792 | -113.3239 | 7.8284 | -113.537 | 8.0257 | 7.9499 | 0.12153 | -113.4522 | -113.6458 | 8.0126 | 8.0387 | 8.194 | 7.9756 | -113.6342 | 7.9809 | 8.0658 | 7.8721 | 7.97 | -113.6895
4091.8438 | 121.4996 | -8.5464 | 112.5458 | 1.4211e-13 | 0.02416 | 0.016133 | 0.0098956 | -0.023362 | 0.0052797 | 0.23258 | 0.024385 | 0.035031 | -0.096851 | -0.0035705 | 0.00064308 | 0.042253 | -0.021486 | -0.012988 | 0.038393 | 0.059885 | 0.21064 | -0.090531 | 0.037677 | -0.008798 | -0.038036 | 0.002095 | 0.091543 | -0.097557 | -0.15041 | 8.4559 | -112.5074 | 8.5887 | 8.5335 | 0.077543 | -112.4859 | -112.3351 | 8.396 | -112.5437 | 8.5841 | 8.5084 | 0.11238 | -112.4542 | -112.6433 | 8.5848 | 8.6063 | 8.7571 | 8.525 | -112.6363 | 8.5485 | 8.638 | 8.4489 | 8.5376 | -112.6962
4093.5625 | 104.6265 | -8.844 | 94.1071 | 1.4211e-13 | 0.024374 | 0.015919 | 0.009682 | -0.022935 | 0.0050659 | 0.24021 | 0.024171 | 0.035031 | -0.096851 | -0.0037841 | 0.00064308 | 0.042253 | -0.021486 | -0.022144 | 0.042971 | 0.059885 | 0.20607 | -0.099689 | 0.033099 | -0.008798 | -0.038036 | 0.002095 | 0.086964 | -0.10214 | -0.15957 | 8.7443 | -94.0641 | 8.8862 | 8.8218 | 0.077545 | -94.0472 | -93.901 | 8.6844 | -94.105 | 8.8771 | 8.806 | 0.12153 | -94.0201 | -94.2092 | 8.887 | 8.9039 | 9.0501 | 8.8225 | -94.2067 | 8.8461 | 8.931 | 8.7419 | 8.8352 | -94.2666
4095.2969 | 121.5454 | -8.7433 | 112.3032 | 1.4211e-13 | 0.023946 | 0.015919 | 0.0092546 | -0.023148 | 0.0046387 | 0.23258 | 0.024812 | 0.034818 | -0.096851 | -0.0039979 | 0.00064308 | 0.046831 | -0.021486 | -0.017566 | 0.033814 | 0.059885 | 0.20607 | -0.099689 | 0.037677 | -0.013377 | -0.033458 | 0.002095 | 0.086964 | -0.092979 | -0.15041 | 8.6436 | -112.2693 | 8.7901 | 8.7257 | 0.082123 | -112.2433 | -112.0971 | 8.5929 | -112.3011 | 8.781 | 8.7098 | 0.11695 | -112.2162 | -112.3961 | 8.7771 | 8.8032 | 8.9494 | 8.7218 | -112.4029 | 8.7454 | 8.8302 | 8.6503 | 8.7299 | -112.4536
4097.0312 | 121.5454 | -8.8028 | 112.6648 | 1.4211e-13 | 0.02416 | 0.015919 | 0.0098956 | -0.023362 | 0.0048523 | 0.24021 | 0.024598 | 0.034604 | -0.09621 | -0.0037841 | 0.00064308 | 0.042253 | -0.021486 | -0.012988 | 0.038393 | 0.064464 | 0.21522 | -0.09511 | 0.033099 | -0.00422 | -0.033458 | 0.006674 | 0.091543 | -0.097557 | -0.15499 | 8.7077 | -112.6264 | 8.845 | 8.7898 | 0.082122 | -112.6003 | -112.4496 | 8.6478 | -112.6581 | 8.8359 | 8.7693 | 0.12153 | -112.5733 | -112.7624 | 8.8412 | 8.8673 | 9.018 | 8.7813 | -112.7599 | 8.8095 | 8.8943 | 8.7052 | 8.7986 | -112.8198
4098.7344 | 121.2387 | -15.4175 | 101.8982 | 1.4211e-13 | 0.024374 | 0.016133 | 0.0098956 | -0.023148 | 0.0048523 | 0.23258 | 0.024598 | 0.034604 | -0.096851 | -0.0039979 | 0.00085668 | 0.05141 | -0.007751 | -0.012988 | 0.038393 | 0.064464 | 0.21064 | -0.09511 | 0.042256 | -0.008798 | -0.038036 | 0.011252 | 0.086964 | -0.10214 | -0.14583 | 15.3224 | -101.8598 | 15.4689 | 15.4045 | 0.082122 | -101.8337 | -101.6875 | 15.2716 | -101.8869 | 15.4597 | 15.3794 | 0.1078 | -101.8112 | -102.0003 | 15.4559 | 15.4819 | 15.6281 | 15.4097 | -101.9933 | 15.4287 | 15.5044 | 15.3153 | 15.4087 | -102.044
4100.4688 | 121.9482 | -8.9081 | 111.8134 | 1.4211e-13 | 0.024587 | 0.016346 | 0.0098956 | -0.023576 | 0.0046387 | 0.24021 | 0.024385 | 0.03439 | -0.096851 | -0.0035705 | 0.00064308 | 0.042253 | -0.021486 | -0.012988 | 0.038393 | 0.059885 | 0.21064 | -0.10427 | 0.042256 | -0.00422 | -0.042615 | 0.002095 | 0.082386 | -0.097557 | -0.14583 | 8.8038 | -111.775 | 8.9503 | 8.8951 | 0.09128 | -111.7535 | -111.6027 | 8.7622 | -111.8113 | 8.9503 | 8.8655 | 0.10322 | -111.731 | -111.9109 | 8.9465 | 8.968 | 9.1187 | 8.8866 | -111.9176 | 8.9102 | 8.9905 | 8.8105 | 8.9039 | -111.9592
4102.1719 | 121.9803 | -95.018 | 26.3809 | 1.4211e-13 | 0.024374 | 0.015919 | 0.0098956 | -0.023148 | 0.0048523 | 0.23258 | 0.024598 | 0.034604 | -0.096637 | -0.0037841 | 0.00085668 | 0.074302 | 0.005985 | 0.009904 | 0.061284 | 0.087359 | 0.24269 | -0.044742 | 0.060571 | 0.004938 | -0.010564 | 0.020409 | 0.11444 | -0.083821 | -0.1321 | 94.9733 | -26.3196 | 95.0923 | 95.0279 | 0.054646 | -26.2936 | -26.1382 | 94.8859 | -26.3605 | 95.0786 | 95.0074 | 0.12153 | -26.2665 | -26.4647 | 95.0793 | 95.1054 | 95.2607 | 95.024 | -26.4257 | 95.0384 | 95.1324 | 94.9342 | 95.0229 | -26.513
4103.9375 | 121.5454 | -9.3109 | 112.4359 | 1.4211e-13 | 0.02416 | 0.01656 | 0.0094682 | -0.023148 | 0.0050659 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0037841 | 0.00085668 | 0.037675 | -0.021486 | -0.012988 | 0.029236 | 0.064464 | 0.21064 | -0.090531 | 0.033099 | -0.013377 | -0.038036 | 0.006674 | 0.086964 | -0.10214 | -0.15499 | 9.2204 | -112.4067 | 9.3486 | 9.2979 | 0.077543 | -112.3714 | -112.2253 | 9.1559 | -112.4292 | 9.344 | 9.2729 | 0.11695 | -112.3489 | -112.538 | 9.3401 | 9.3754 | 9.5216 | 9.2894 | -112.5264 | 9.3176 | 9.3979 | 9.2088 | 9.2975 | -112.5909
4105.6562 | 121.9299 | -8.5648 | 112.5137 | 1.4211e-13 | 0.023946 | 0.015705 | 0.0098956 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.035031 | -0.096637 | -0.0037841 | 0.00085668 | 0.037675 | -0.016908 | -0.022144 | 0.033814 | 0.059885 | 0.21064 | -0.09511 | 0.033099 | -0.00422 | -0.038036 | -0.002483 | 0.082386 | -0.097557 | -0.15957 | 8.4696 | -112.4799 | 8.6024 | 8.5426 | 0.072966 | -112.4538 | -112.3031 | 8.4052 | -112.5162 | 8.5979 | 8.5267 | 0.12153 | -112.4313 | -112.6113 | 8.5986 | 8.6246 | 8.7754 | 8.5478 | -112.6088 | 8.5623 | 8.6471 | 8.4672 | 8.5605 | -112.6733
4107.375 | 108.2108 | -9.2011 | 102.5253 | 1.4211e-13 | 0.02416 | 0.015919 | 0.009682 | -0.023362 | 0.0048523 | 0.24021 | 0.024171 | 0.035031 | -0.09621 | -0.0037841 | 0.00085668 | 0.037675 | -0.016908 | -0.012988 | 0.033814 | 0.055306 | 0.21064 | -0.090531 | 0.037677 | -0.00422 | -0.033458 | 0.002095 | 0.086964 | -0.097557 | -0.15041 | 9.1105 | -102.4915 | 9.2387 | 9.1881 | 0.077543 | -102.47 | -102.3147 | 9.0506 | -102.5232 | 9.2387 | 9.1676 | 0.11695 | -102.4384 | -102.6229 | 9.2349 | 9.2564 | 9.4117 | 9.1841 | -102.6159 | 9.2031 | 9.288 | 9.1035 | 9.1968 | -102.6757
4109.125 | 121.1792 | -8.3817 | 113.4338 | 1.4211e-13 | 0.02416 | 0.015919 | 0.009682 | -0.022935 | 0.0048523 | 0.22495 | 0.024385 | 0.034818 | -0.096637 | -0.0033569 | 0.00064308 | 0.037675 | -0.016908 | -0.022144 | 0.029236 | 0.064464 | 0.21064 | -0.099689 | 0.037677 | -0.008798 | -0.033458 | -0.002483 | 0.082386 | -0.097557 | -0.14583 | 8.282 | -113.4046 | 8.4193 | 8.3595 | 0.077545 | -113.3694 | -113.2232 | 8.2358 | -113.4363 | 8.4193 | 8.3482 | 0.11237 | -113.3515 | -113.5314 | 8.4109 | 8.4461 | 8.5923 | 8.3647 | -113.5335 | 8.3792 | 8.464 | 8.2841 | 8.3729 | -113.5797
4110.8438 | 100.8774 | -14.1769 | 92.8757 | 1.4211e-13 | 0.023946 | 0.015919 | 0.009682 | -0.023576 | 0.0048523 | 0.23258 | 0.024385 | 0.034604 | -0.096851 | -0.0033569 | 0.00042948 | 0.042253 | -0.016908 | -0.012988 | 0.042971 | 0.064464 | 0.21064 | -0.09511 | 0.046835 | 0.000359 | -0.038036 | 0.002095 | 0.086964 | -0.097557 | -0.14125 | 14.0818 | -92.8327 | 14.2192 | 14.164 | 0.082122 | -92.8112 | -92.665 | 14.0357 | -92.8736 | 14.2238 | 14.1389 | 0.10322 | -92.7887 | -92.9732 | 14.2199 | 14.2414 | 14.3876 | 14.16 | -92.9708 | 14.179 | 14.2639 | 14.0794 | 14.1773 | -93.0169
4112.5781 | 121.2341 | -8.2535 | 113.0264 | 1.4211e-13 | 0.024374 | 0.015705 | 0.0094682 | -0.023148 | 0.0050659 | 0.24021 | 0.024385 | 0.034818 | -0.096637 | -0.0035705 | 0.00064308 | 0.037675 | -0.021486 | -0.012988 | 0.038393 | 0.059885 | 0.21064 | -0.09511 | 0.037677 | -0.013377 | -0.047194 | 0.006674 | 0.082386 | -0.10671 | -0.15499 | 8.1584 | -112.988 | 8.2912 | 8.2405 | 0.082122 | -112.9665 | -112.8158 | 8.0985 | -113.0198 | 8.2912 | 8.2063 | 0.1078 | -112.944 | -113.1331 | 8.2919 | 8.3134 | 8.4641 | 8.232 | -113.1215 | 8.2602 | 8.3359 | 8.1468 | 8.2401 | -113.1814
4114.3125 | 115.0177 | -8.0887 | 104.4754 | 1.4211e-13 | 0.02416 | 0.015919 | 0.009682 | -0.023576 | 0.0048523 | 0.24784 | 0.024598 | 0.035031 | -0.096424 | -0.0037841 | 0.00042948 | 0.042253 | -0.016908 | -0.017566 | 0.033814 | 0.050727 | 0.21064 | -0.099689 | 0.042256 | -0.008798 | -0.042615 | -0.007062 | 0.086964 | -0.10214 | -0.14583 | 7.989 | -104.4416 | 8.1309 | 8.0711 | 0.082123 | -104.4247 | -104.2648 | 7.9429 | -104.4825 | 8.1309 | 8.0461 | 0.10322 | -104.3884 | -104.5775 | 8.1225 | 8.1394 | 8.2993 | 8.0718 | -104.5751 | 8.0816 | 8.1756 | 7.9865 | 8.0799 | -104.6212
4116.0469 | 121.4905 | -7.7316 | 113.4476 | 1.4211e-13 | 0.02416 | 0.015919 | 0.0098956 | -0.023362 | 0.0050659 | 0.24784 | 0.024385 | 0.03439 | -0.096424 | -0.0039979 | 0.00064308 | 0.042253 | -0.026065 | -0.017566 | 0.029236 | 0.050727 | 0.21064 | -0.099689 | 0.033099 | -0.008798 | -0.042615 | 0.002095 | 0.077807 | -0.097557 | -0.14583 | 7.6319 | -113.4183 | 7.7739 | 7.7141 | 0.082123 | -113.3968 | -113.2369 | 7.5858 | -113.4455 | 7.7647 | 7.689 | 0.10322 | -113.3698 | -113.5451 | 7.7609 | 7.7824 | 7.9423 | 7.7056 | -113.5473 | 7.7337 | 7.8094 | 7.6341 | 7.7228 | -113.5934
4117.75 | 121.6827 | -7.5302 | 111.7264 | 1.4211e-13 | 0.02416 | 0.016346 | 0.009682 | -0.023576 | 0.0048523 | 0.23258 | 0.024598 | 0.034818 | -0.096424 | -0.0037841 | 0.00042948 | 0.037675 | -0.021486 | -0.008409 | 0.033814 | 0.059885 | 0.21064 | -0.099689 | 0.037677 | -0.013377 | -0.033458 | -0.002483 | 0.082386 | -0.083821 | -0.15499 | 7.4305 | -111.6926 | 7.5679 | 7.5218 | 0.09128 | -111.6665 | -111.5157 | 7.3752 | -111.7289 | 7.5679 | 7.4968 | 0.12153 | -111.644 | -111.8102 | 7.564 | 7.5901 | 7.7409 | 7.5087 | -111.8261 | 7.5277 | 7.6126 | 7.4464 | 7.5168 | -111.8814
4119.4844 | 121.8613 | -7.5577 | 113.6581 | 1.4211e-13 | 0.024374 | 0.015919 | 0.0094682 | -0.023362 | 0.0046387 | 0.24784 | 0.024812 | 0.034818 | -0.096637 | -0.0035705 | 0.00085668 | 0.037675 | -0.021486 | -0.017566 | 0.042971 | 0.059885 | 0.21064 | -0.090531 | 0.037677 | -0.00422 | -0.038036 | 0.002095 | 0.082386 | -0.083821 | -0.15041 | 7.4671 | -113.6152 | 7.5954 | 7.5401 | 0.072965 | -113.5983 | -113.4475 | 7.4073 | -113.656 | 7.5954 | 7.5196 | 0.11238 | -113.5758 | -113.742 | 7.6006 | 7.6176 | 7.7683 | 7.5362 | -113.7487 | 7.5598 | 7.6401 | 7.4739 | 7.5535 | -113.8086
4121.2188 | 121.2067 | -119.2429 | 1.6022 | 1.4211e-13 | 0.02416 | 0.015492 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024598 | 0.035031 | -0.096637 | -0.0039979 | 0.00064308 | 0.069723 | 0.015142 | 0.014482 | 0.056706 | 0.096516 | 0.24727 | -0.035584 | 0.078886 | 0.023253 | 0.007751 | 0.038723 | 0.11901 | 0.021486 | -0.11836 | 119.2073 | -1.5455 | 119.3126 | 119.2573 | 0.050066 | -1.5057 | -1.3549 | 119.1245 | -1.5635 | 119.3217 | 119.2506 | 0.12611 | -1.4832 | -1.5807 | 119.2996 | 119.3394 | 119.4901 | 119.258 | -1.6378 | 119.2816 | 119.3619 | 119.2643 | 119.2661 | -1.7205
4123 | 121.5637 | -120.0119 | 1.3596 | 1.4211e-13 | 0.024374 | 0.015705 | 0.009682 | -0.023148 | 0.0048523 | 0.23258 | 0.024171 | 0.034604 | -0.096637 | -0.0037841 | 0.0010705 | 0.07888 | 0.015142 | 0.023639 | 0.070441 | 0.096516 | 0.24727 | -0.058478 | 0.074307 | 0.023253 | 0.003172 | 0.038723 | 0.11901 | 0.021486 | -0.11378 | 119.9534 | -1.2891 | 120.0908 | 120.0355 | 0.082117 | -1.263 | -1.1123 | 119.8981 | -1.3208 | 120.0862 | 120.0151 | 0.11695 | -1.2405 | -1.3381 | 120.0823 | 120.1084 | 120.2592 | 120.027 | -1.418 | 120.0506 | 120.1309 | 120.0334 | 120.0352 | -1.4733
4124.7031 | 121.6095 | -120.163 | 1.3046 | 1.4211e-13 | 0.023946 | 0.016346 | 0.0094682 | -0.023576 | 0.0046387 | 0.23258 | 0.024385 | 0.034818 | -0.096424 | -0.0039979 | 0.00085668 | 0.07888 | 0.015142 | 0.023639 | 0.065863 | 0.096516 | 0.24269 | -0.031005 | 0.078886 | 0.018674 | 0.003172 | 0.043302 | 0.11444 | 0.026065 | -0.11836 | 120.132 | -1.2388 | 120.2418 | 120.1866 | 0.054644 | -1.2081 | -1.0619 | 120.0446 | -1.2613 | 120.2418 | 120.1661 | 0.12153 | -1.1902 | -1.2786 | 120.2288 | 120.2595 | 120.4057 | 120.1781 | -1.3356 | 120.2063 | 120.2774 | 120.189 | 120.1816 | -1.423
4126.4688 | 121.756 | -120.6573 | 0.82398 | 1.4211e-13 | 0.02416 | 0.015705 | 0.009682 | -0.023148 | 0.0048523 | 0.24021 | 0.024598 | 0.034818 | -0.096637 | -0.0039979 | 0.00042948 | 0.074302 | 0.019721 | 0.023639 | 0.065863 | 0.096516 | 0.24727 | -0.026426 | 0.069728 | 0.023253 | -0.001407 | 0.034145 | 0.11901 | 0.021486 | -0.11836 | 120.6309 | -0.75811 | 120.7317 | 120.681 | 0.050065 | -0.72746 | -0.5767 | 120.539 | -0.78983 | 120.7271 | 120.6559 | 0.11695 | -0.70496 | -0.80249 | 120.7232 | 120.7539 | 120.9046 | 120.6771 | -0.8504 | 120.6915 | 120.7764 | 120.6788 | 120.6806 | -0.94234
4128.1719 | 121.7926 | -120.7169 | 0.80566 | 1.4211e-13 | 0.024374 | 0.015705 | 0.009682 | -0.023362 | 0.0046387 | 0.23258 | 0.024385 | 0.034818 | -0.09621 | -0.0035705 | 0.00021588 | 0.074302 | 0.015142 | 0.01906 | 0.07502 | 0.1011 | 0.25185 | -0.053899 | 0.074307 | 0.023253 | 0.003172 | 0.034145 | 0.12359 | 0.016908 | -0.11378 | 120.663 | -0.73064 | 120.7912 | 120.7359 | 0.072959 | -0.70457 | -0.55381 | 120.6031 | -0.77152 | 120.7912 | 120.72 | 0.11695 | -0.68207 | -0.78876 | 120.7919 | 120.818 | 120.9687 | 120.732 | -0.85956 | 120.751 | 120.8405 | 120.7338 | 120.7401 | -0.91945
4129.9375 | 121.6232 | -120.9824 | 0.6546 | 1.4211e-13 | 0.024374 | 0.015919 | 0.009682 | -0.023148 | 0.0048523 | 0.22495 | 0.024171 | 0.034818 | -0.096637 | -0.0039979 | 0.00042948 | 0.07888 | 0.005985 | 0.014482 | 0.07502 | 0.096516 | 0.24269 | -0.021847 | 0.078886 | 0.027831 | -0.001407 | 0.038723 | 0.12359 | 0.021486 | -0.11378 | 120.9605 | -0.57958 | 121.0612 | 120.9968 | 0.036329 | -0.55809 | -0.41191 | 120.8686 | -0.61588 | 121.0612 | 120.981 | 0.11237 | -0.53101 | -0.63312 | 121.0574 | 121.0789 | 121.2251 | 120.9883 | -0.67645 | 121.0211 | 121.106 | 121.0038 | 121.0102 | -0.76838
4131.6406 | 121.7239 | -120.9503 | 0.62714 | 1.4211e-13 | 0.023946 | 0.015919 | 0.009682 | -0.023362 | 0.0048523 | 0.24021 | 0.024598 | 0.034818 | -0.096851 | -0.0035705 | 0.00064308 | 0.069723 | 0.015142 | 0.023639 | 0.070441 | 0.096516 | 0.25185 | -0.063057 | 0.069728 | 0.027831 | -0.005985 | 0.034145 | 0.10528 | 0.026065 | -0.11836 | 120.8873 | -0.5567 | 121.02 | 120.974 | 0.086696 | -0.53062 | -0.37528 | 120.832 | -0.59299 | 121.02 | 120.9443 | 0.11238 | -0.52186 | -0.60107 | 121.0208 | 121.0468 | 121.2022 | 120.9655 | -0.69019 | 120.9845 | 121.0556 | 120.9764 | 120.9781 | -0.7455
4133.375 | 121.7834 | -120.9686 | 0.59509 | 1.4211e-13 | 0.02416 | 0.015919 | 0.009682 | -0.023148 | 0.0050659 | 0.23258 | 0.024598 | 0.034818 | -0.096637 | -0.0042115 | 0.0010705 | 0.07888 | 0.010564 | 0.023639 | 0.079598 | 0.091937 | 0.24727 | -0.053899 | 0.074307 | 0.023253 | 0.003172 | 0.038723 | 0.11444 | 0.021486 | -0.11378 | 120.9147 | -0.5155 | 121.0475 | 120.9923 | 0.077538 | -0.50316 | -0.34782 | 120.8548 | -0.55637 | 121.0429 | 120.9718 | 0.11695 | -0.48066 | -0.57361 | 121.0482 | 121.0606 | 121.2159 | 120.9792 | -0.64899 | 121.0074 | 121.0831 | 120.9901 | 120.9919 | -0.70887
4135.1094 | 121.7377 | -120.9045 | 0.72784 | 1.4211e-13 | 0.02416 | 0.016133 | 0.009682 | -0.023148 | 0.0048523 | 0.24021 | 0.024812 | 0.035031 | -0.096851 | -0.0035705 | 0.00064308 | 0.07888 | 0.0243 | 0.023639 | 0.065863 | 0.096516 | 0.25185 | -0.040163 | 0.083464 | 0.023253 | -0.001407 | 0.038723 | 0.11901 | 0.021486 | -0.11836 | 120.8644 | -0.66198 | 120.9834 | 120.9282 | 0.063802 | -0.63133 | -0.47599 | 120.7862 | -0.68912 | 120.988 | 120.9031 | 0.11695 | -0.60883 | -0.70636 | 120.9704 | 121.0011 | 121.1564 | 120.9288 | -0.76801 | 120.9433 | 121.0236 | 120.926 | 120.9278 | -0.84621
4136.8125 | 121.6736 | -121.0236 | 0.63171 | 1.4211e-13 | 0.023946 | 0.015919 | 0.009682 | -0.023789 | 0.0048523 | 0.22495 | 0.024598 | 0.034818 | -0.096424 | -0.0039979 | 0.00064308 | 0.088037 | 0.015142 | 0.023639 | 0.07502 | 0.1011 | 0.24727 | -0.053899 | 0.078886 | 0.023253 | 0.003172 | 0.034145 | 0.10986 | 0.021486 | -0.11836 | 120.9697 | -0.55669 | 121.1116 | 121.0472 | 0.077538 | -0.53062 | -0.38444 | 120.9052 | -0.59757 | 121.1024 | 121.0267 | 0.12153 | -0.52186 | -0.61023 | 121.0986 | 121.1247 | 121.2708 | 121.0387 | -0.68561 | 121.0577 | 121.1334 | 121.045 | 121.0468 | -0.75008
4138.5938 | 121.8109 | -120.9549 | 0.62256 | 1.4211e-13 | 0.02416 | 0.015705 | 0.009682 | -0.023148 | 0.0052797 | 0.23258 | 0.024385 | 0.034818 | -0.096637 | -0.0037841 | 0.00064308 | 0.07888 | 0.019721 | 0.014482 | 0.070441 | 0.1011 | 0.24269 | -0.067636 | 0.069728 | 0.027831 | -0.005985 | 0.034145 | 0.11901 | 0.030644 | -0.10462 | 120.8873 | -0.55212 | 121.0338 | 120.9694 | 0.082118 | -0.52146 | -0.37986 | 120.8503 | -0.58841 | 121.0246 | 120.9489 | 0.098639 | -0.50355 | -0.59191 | 121.0253 | 121.056 | 121.1976 | 120.9746 | -0.6902 | 120.989 | 121.0739 | 120.9855 | 120.9827 | -0.72718
4140.3281 | 121.8201 | -120.8542 | 0.737 | 1.4211e-13 | 0.023946 | 0.016133 | 0.009682 | -0.023148 | 0.0046387 | 0.24021 | 0.024385 | 0.034818 | -0.096637 | -0.0037841 | 0.00064308 | 0.069723 | 0.015142 | 0.01906 | 0.07502 | 0.091937 | 0.24727 | -0.063057 | 0.06515 | 0.023253 | 0.003172 | 0.038723 | 0.12359 | 0.003172 | -0.11378 | 120.7911 | -0.66198 | 120.9239 | 120.8732 | 0.082117 | -0.64506 | -0.48973 | 120.7404 | -0.69828 | 120.9193 | 120.8574 | 0.11695 | -0.61341 | -0.73383 | 120.9292 | 120.9461 | 121.1015 | 120.8693 | -0.80006 | 120.8929 | 120.9778 | 120.8574 | 120.8774 | -0.85078
4142.0625 | 121.7972 | -120.3278 | 1.2451 | 1.4211e-13 | 0.023946 | 0.016133 | 0.009682 | -0.023362 | 0.0048523 | 0.23258 | 0.024598 | 0.034604 | -0.096424 | -0.0037841 | 0.00064308 | 0.069723 | 0.0243 | 0.028217 | 0.070441 | 0.1011 | 0.23812 | -0.058478 | 0.078886 | 0.018674 | -0.005985 | 0.034145 | 0.12817 | 0.016908 | -0.11378 | 120.2693 | -1.1747 | 120.3975 | 120.356 | 0.086695 | -1.144 | -1.007 | 120.214 | -1.211 | 120.4066 | 120.3218 | 0.1078 | -1.1169 | -1.2282 | 120.3982 | 120.4289 | 120.5659 | 120.3521 | -1.3036 | 120.3619 | 120.4559 | 120.3447 | 120.3464 | -1.3589
4143.7812 | 121.9574 | -120.9183 | 0.68207 | 1.4211e-13 | 0.02416 | 0.015919 | 0.009041 | -0.023148 | 0.0048523 | 0.22495 | 0.024385 | 0.034604 | -0.096424 | -0.0037841 | 0.00064308 | 0.07888 | 0.015142 | 0.023639 | 0.07502 | 0.1011 | 0.24727 | -0.044742 | 0.078886 | 0.027831 | 0.003172 | 0.038723 | 0.12359 | 0.016908 | -0.11378 | 120.8735 | -0.60705 | 120.9972 | 120.9419 | 0.068381 | -0.58097 | -0.43479 | 120.8045 | -0.64335 | 120.9972 | 120.9214 | 0.11695 | -0.55848 | -0.66516 | 120.9933 | 121.0194 | 121.1655 | 120.9334 | -0.72681 | 120.957 | 121.0419 | 120.9352 | 120.9461 | -0.79585
4145.5 | 117.1097 | -67.6254 | 48.0927 | 1.4211e-13 | 0.023946 | 0.015492 | 0.0094682 | -0.022721 | 0.0039977 | 0.24021 | 0.024171 | 0.034604 | -0.096424 | -0.0037841 | 0.00085668 | 0.055988 | 0.001407 | 0.005325 | 0.052128 | 0.087359 | 0.23354 | -0.081373 | 0.060571 | 0.014095 | -0.015143 | 0.024988 | 0.10528 | -0.028878 | -0.1321 | 67.5441 | -48.0405 | 67.6814 | 67.6308 | 0.086698 | -48.0053 | -47.8591 | 67.4933 | -48.0677 | 67.686 | 67.6103 | 0.11695 | -47.9874 | -48.1215 | 67.6776 | 67.7128 | 67.859 | 67.6268 | -48.174 | 67.6504 | 67.7307 | 67.5965 | 67.6395 | -48.2247
4147.2031 | 116.2445 | -66.0278 | 51.1459 | 1.4211e-13 | 0.023946 | 0.015705 | 0.0092546 | -0.023148 | 0.0042113 | 0.24021 | 0.024598 | 0.034818 | -0.096637 | -0.0037841 | 0.00064308 | 0.069723 | 0.010564 | 0.009904 | 0.061284 | 0.096516 | 0.23812 | -0.053899 | 0.078886 | 0.018674 | -0.001407 | 0.038723 | 0.11444 | -0.001407 | -0.11836 | 65.9739 | -51.0847 | 66.0976 | 66.0377 | 0.063803 | -51.0494 | -50.9078 | 65.9095 | -51.1072 | 66.1067 | 66.0264 | 0.11695 | -51.0315 | -51.1473 | 66.0891 | 66.1243 | 66.2659 | 66.0384 | -51.1998 | 66.0666 | 66.1423 | 66.0264 | 66.0465 | -51.2643
4148.9375 | 120.9183 | -98.1445 | 22.3755 | 1.4211e-13 | 0.023946 | 0.015919 | 0.009682 | -0.023362 | 0.0046387 | 0.23258 | 0.024385 | 0.034604 | -0.096637 | -0.0037841 | 0.00064308 | 0.065145 | 0.015142 | 0.023639 | 0.061284 | 0.091937 | 0.23354 | -0.063057 | 0.074307 | 0.014095 | -0.005985 | 0.034145 | 0.11901 | 0.016908 | -0.11836 | 98.0815 | -22.3142 | 98.2097 | 98.1682 | 0.086696 | -22.2836 | -22.142 | 98.0262 | -22.3413 | 98.2188 | 98.1385 | 0.11238 | -22.2565 | -22.3586 | 98.2058 | 98.2365 | 98.3781 | 98.1597 | -22.4385 | 98.1787 | 98.2635 | 98.1614 | 98.1586 | -22.4938
4150.7188 | 121.1243 | -119.7052 | 1.0025 | 1.4211e-13 | 0.02416 | 0.016346 | 0.0094682 | -0.023362 | 0.0046387 | 0.24784 | 0.024171 | 0.034604 | -0.096851 | -0.0031431 | 0.00064308 | 0.074302 | 0.019721 | 0.023639 | 0.065863 | 0.087359 | 0.24727 | -0.067636 | 0.069728 | 0.023253 | 0.007751 | 0.043302 | 0.11444 | 0.026065 | -0.11836 | 119.6376 | -0.93664 | 119.7795 | 119.7288 | 0.091275 | -0.91514 | -0.75523 | 119.5868 | -0.9592 | 119.7749 | 119.713 | 0.12611 | -0.88807 | -0.97644 | 119.7711 | 119.7926 | 119.9525 | 119.7249 | -1.0701 | 119.7485 | 119.8196 | 119.7313 | 119.7285 | -1.1209
4152.4844 | 120.4788 | -105.2719 | 14.0762 | 1.4211e-13 | 0.023946 | 0.016133 | 0.0094682 | -0.023362 | 0.0046387 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0039979 | 0.00042948 | 0.074302 | 0.015142 | 0.01906 | 0.065863 | 0.091937 | 0.24727 | -0.076794 | 0.074307 | 0.018674 | -0.001407 | 0.038723 | 0.11901 | 0.003172 | -0.12294 | 105.1951 | -14.0104 | 105.3462 | 105.291 | 0.095854 | -13.9843 | -13.829 | 105.149 | -14.0375 | 105.3462 | 105.2705 | 0.12153 | -13.9572 | -14.0731 | 105.3378 | 105.3638 | 105.5192 | 105.2871 | -14.153 | 105.3106 | 105.3909 | 105.2751 | 105.2906 | -14.1992
4154.2188 | 120.6802 | -119.2703 | 0.91095 | 1.4211e-13 | 0.02416 | 0.015919 | 0.0094682 | -0.023148 | 0.0044249 | 0.24021 | 0.024171 | 0.034818 | -0.096637 | -0.0039979 | 0.00021588 | 0.065145 | 0.019721 | 0.023639 | 0.070441 | 0.091937 | 0.24727 | -0.044742 | 0.069728 | 0.014095 | -0.001407 | 0.038723 | 0.11444 | -0.001407 | -0.11836 | 119.2256 | -0.84051 | 119.3355 | 119.294 | 0.068381 | -0.81901 | -0.66368 | 119.152 | -0.87223 | 119.3401 | 119.2689 | 0.11695 | -0.79651 | -0.91236 | 119.3408 | 119.3623 | 119.5176 | 119.29 | -0.95569 | 119.309 | 119.3848 | 119.2689 | 119.2844 | -1.0293
4155.9844 | 120.2316 | -46.55 | 72.8027 | 1.4211e-13 | 0.023946 | 0.015919 | 0.0092546 | -0.023148 | 0.0042113 | 0.23258 | 0.024385 | 0.034818 | -0.096637 | -0.0037841 | 0.00064308 | 0.060567 | 0.010564 | 0.014482 | 0.061284 | 0.078201 | 0.23812 | -0.081373 | 0.055992 | 0.009516 | -0.010564 | 0.029566 | 0.10528 | -0.028878 | -0.1321 | 46.4686 | -72.7415 | 46.6106 | 46.5645 | 0.095855 | -72.7245 | -72.5646 | 46.4179 | -72.7732 | 46.606 | 46.5394 | 0.12153 | -72.6975 | -72.8316 | 46.6113 | 46.6282 | 46.7881 | 46.5606 | -72.8841 | 46.5796 | 46.6553 | 46.5211 | 46.5595 | -72.9348
4157.6875 | 120.5063 | -119.3893 | 0.59509 | 1.4211e-13 | 0.023946 | 0.015705 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0039979 | 0.00064308 | 0.065145 | 0.005985 | 0.01906 | 0.065863 | 0.087359 | 0.24727 | -0.021847 | 0.074307 | 0.023253 | 0.003172 | 0.034145 | 0.12359 | -0.005985 | -0.11378 | 119.3675 | -0.52923 | 119.4545 | 119.4084 | 0.040907 | -0.50773 | -0.34782 | 119.2756 | -0.56095 | 119.4637 | 119.3925 | 0.11695 | -0.4715 | -0.60108 | 119.4552 | 119.4767 | 119.6366 | 119.3953 | -0.61694 | 119.4235 | 119.5129 | 119.3834 | 119.4126 | -0.70887
4159.4062 | 120.6711 | -119.3802 | 0.82398 | 1.4211e-13 | 0.024374 | 0.015919 | 0.0094682 | -0.023148 | 0.0048523 | 0.24021 | 0.024598 | 0.034604 | -0.096851 | -0.0039979 | 0.00042948 | 0.07888 | 0.015142 | 0.01906 | 0.070441 | 0.091937 | 0.24727 | -0.040163 | 0.069728 | 0.018674 | -0.005985 | 0.038723 | 0.11901 | 0.012329 | -0.12294 | 119.34 | -0.75353 | 119.4591 | 119.3992 | 0.059223 | -0.73204 | -0.5767 | 119.2572 | -0.78525 | 119.4499 | 119.3742 | 0.11695 | -0.70496 | -0.81165 | 119.4506 | 119.4721 | 119.6275 | 119.3953 | -0.86414 | 119.4189 | 119.4992 | 119.3925 | 119.3989 | -0.94691
4161.1406 | 120.7718 | -120.0485 | 0.5127 | 1.4211e-13 | 0.02416 | 0.015705 | 0.009682 | -0.023148 | 0.0046387 | 0.24021 | 0.024598 | 0.03439 | -0.096637 | -0.0037841 | 0.00064308 | 0.069723 | 0.015142 | 0.023639 | 0.070441 | 0.096516 | 0.24727 | -0.00811 | 0.074307 | 0.023253 | -0.001407 | 0.029566 | 0.11444 | 0.021486 | -0.11836 | 120.0404 | -0.44225 | 120.1182 | 120.0722 | 0.031749 | -0.41618 | -0.26542 | 119.9302 | -0.48313 | 120.1228 | 120.0471 | 0.11695 | -0.39826 | -0.49121 | 120.119 | 120.145 | 120.2958 | 120.0637 | -0.5208 | 120.0781 | 120.163 | 120.07 | 120.0718 | -0.63106
4162.9531 | 116.8396 | -70.6467 | 45.7718 | 1.4211e-13 | 0.02416 | 0.015705 | 0.0094682 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.035031 | -0.096424 | -0.0037841 | 0.00042948 | 0.065145 | 0.010564 | 0.01906 | 0.065863 | 0.096516 | 0.24269 | -0.072215 | 0.069728 | 0.009516 | -0.001407 | 0.029566 | 0.10986 | 0.007751 | -0.12294 | 70.5745 | -45.7059 | 70.7118 | 70.6657 | 0.091275 | -45.6753 | -45.5291 | 70.5237 | -45.7422 | 70.7164 | 70.6453 | 0.12153 | -45.6619 | -45.764 | 70.7125 | 70.7432 | 70.8894 | 70.6572 | -45.844 | 70.6762 | 70.7565 | 70.6544 | 70.6562 | -45.8947
4164.6875 | 119.8242 | -96.4188 | 22.9431 | 1.4211e-13 | 0.023946 | 0.015919 | 0.0094682 | -0.023362 | 0.0046387 | 0.24021 | 0.024171 | 0.034818 | -0.096851 | -0.0037841 | 0.00042948 | 0.069723 | 0.005985 | -0.003831 | 0.065863 | 0.091937 | 0.23812 | -0.058478 | 0.069728 | 0.027831 | -0.010564 | 0.029566 | 0.11444 | 0.016908 | -0.11836 | 96.3603 | -22.8773 | 96.4885 | 96.4149 | 0.054647 | -22.8512 | -22.705 | 96.3004 | -22.9135 | 96.4885 | 96.4082 | 0.1078 | -22.8287 | -22.9262 | 96.4846 | 96.5107 | 96.6569 | 96.4247 | -23.0016 | 96.4483 | 96.5332 | 96.4357 | 96.4466 | -23.0615
4166.4219 | 120.7214 | -119.87 | 0.56305 | 1.4211e-13 | 0.024374 | 0.015919 | 0.0092546 | -0.023789 | 0.0046387 | 0.23258 | 0.024598 | 0.035031 | -0.096637 | -0.0035705 | 0.00042948 | 0.07888 | 0.015142 | 0.009904 | 0.07502 | 0.096516 | 0.25185 | -0.026426 | 0.083464 | 0.018674 | -0.001407 | 0.034145 | 0.12359 | 0.026065 | -0.11836 | 119.8436 | -0.48803 | 119.9489 | 119.8799 | 0.03633 | -0.46653 | -0.3112 | 119.7516 | -0.5289 | 119.9535 | 119.8686 | 0.11695 | -0.43946 | -0.53698 | 119.945 | 119.9665 | 120.1218 | 119.8851 | -0.58947 | 119.9041 | 119.9936 | 119.8961 | 119.8887 | -0.68141
4168.1562 | 120.7672 | -120.0577 | 0.54932 | 1.4211e-13 | 0.023946 | 0.016133 | 0.0094682 | -0.023362 | 0.0048523 | 0.24021 | 0.024171 | 0.034604 | -0.096851 | -0.0031431 | 0.00085668 | 0.069723 | 0.015142 | 0.005325 | 0.070441 | 0.091937 | 0.25643 | -0.040163 | 0.074307 | 0.023253 | 0.007751 | 0.038723 | 0.12817 | 0.016908 | -0.11836 | 120.0175 | -0.47888 | 120.1274 | 120.063 | 0.045488 | -0.45738 | -0.29289 | 119.9393 | -0.51059 | 120.132 | 120.0654 | 0.12611 | -0.42114 | -0.53241 | 120.1281 | 120.1496 | 120.3141 | 120.0728 | -0.58948 | 120.0964 | 120.1859 | 120.0746 | 120.0809 | -0.66768
4169.9219 | 120.1218 | -119.1101 | 0.60883 | 1.4211e-13 | 0.023733 | 0.015919 | 0.0092546 | -0.023148 | 0.0046387 | 0.22495 | 0.024598 | 0.03439 | -0.096637 | -0.0035705 | 0.0010705 | 0.069723 | 0.019721 | 0.000747 | 0.061284 | 0.091937 | 0.24269 | -0.058478 | 0.074307 | 0.014095 | -0.001407 | 0.034145 | 0.12359 | 0.012329 | -0.12294 | 119.0516 | -0.54754 | 119.1798 | 119.1109 | 0.059225 | -0.51689 | -0.36613 | 118.9872 | -0.57468 | 119.1844 | 119.1087 | 0.12153 | -0.48523 | -0.5965 | 119.1714 | 119.202 | 119.3528 | 119.1298 | -0.6673 | 119.1443 | 119.2337 | 119.1224 | 119.1242 | -0.73176
4171.625 | 120.2866 | -117.9474 | 1.8356 | 1.4211e-13 | 0.02416 | 0.015705 | 0.0098956 | -0.023148 | 0.0044249 | 0.24021 | 0.024385 | 0.034818 | -0.096637 | -0.0039979 | 0.00064308 | 0.074302 | 0.019721 | 0.005325 | 0.07502 | 0.096516 | 0.24727 | -0.035584 | 0.074307 | 0.027831 | -0.001407 | 0.038723 | 0.12359 | 0.003172 | -0.11378 | 117.9118 | -1.7606 | 118.0217 | 117.9527 | 0.040909 | -1.7391 | -1.5884 | 117.8336 | -1.7969 | 118.0217 | 117.946 | 0.11237 | -1.712 | -1.8325 | 118.0224 | 118.0439 | 118.1947 | 117.9671 | -1.8712 | 117.9861 | 118.071 | 117.9506 | 117.9752 | -1.9494
4173.3438 | 120.6436 | -115.8646 | 4.4312 | 1.4211e-13 | 0.023733 | 0.015919 | 0.009682 | -0.023362 | 0.0044249 | 0.22495 | 0.024171 | 0.034818 | -0.096851 | -0.0039979 | 0.00064308 | 0.074302 | 0.015142 | 0.005325 | 0.07502 | 0.091937 | 0.24727 | -0.063057 | 0.069728 | 0.023253 | 0.003172 | 0.043302 | 0.12359 | 0.026065 | -0.12294 | 115.8015 | -4.3561 | 115.9389 | 115.8699 | 0.068382 | -4.3392 | -4.1839 | 115.7416 | -4.3879 | 115.9343 | 115.8677 | 0.12611 | -4.3076 | -4.4051 | 115.9396 | 115.9565 | 116.1118 | 115.8797 | -4.4942 | 115.9079 | 115.9882 | 115.8906 | 115.8878 | -4.5541
4175.0625 | 120.7626 | -116.3361 | 4.0924 | 1.4211e-13 | 0.024374 | 0.016133 | 0.009682 | -0.023576 | 0.0048523 | 0.24021 | 0.024598 | 0.034604 | -0.096637 | -0.0035705 | 0.00042948 | 0.07888 | 0.0243 | 0.014482 | 0.061284 | 0.091937 | 0.25185 | -0.026426 | 0.074307 | 0.027831 | -0.001407 | 0.038723 | 0.11901 | 0.016908 | -0.12294 | 116.3096 | -4.0311 | 116.4149 | 116.3505 | 0.040908 | -4.0005 | -3.8406 | 116.2131 | -4.0537 | 116.4104 | 116.3347 | 0.12153 | -3.9734 | -4.0755 | 116.3973 | 116.428 | 116.5879 | 116.3604 | -4.1188 | 116.3748 | 116.4551 | 116.353 | 116.3639 | -4.2153
4176.7812 | 120.8542 | -118.0664 | 2.4353 | 1.4211e-13 | 0.023519 | 0.015705 | 0.0098956 | -0.023362 | 0.0046387 | 0.24021 | 0.024385 | 0.034818 | -0.096851 | -0.0037841 | 0.00042948 | 0.074302 | 0.0243 | 0.014482 | 0.070441 | 0.096516 | 0.25185 | -0.017268 | 0.078886 | 0.014095 | 0.003172 | 0.034145 | 0.12359 | -0.005985 | -0.11378 | 118.0491 | -2.3649 | 118.1407 | 118.0809 | 0.03175 | -2.3388 | -2.1835 | 117.9526 | -2.4012 | 118.1453 | 118.0696 | 0.11695 | -2.3117 | -2.4413 | 118.1368 | 118.1629 | 118.3183 | 118.0907 | -2.4526 | 118.1006 | 118.19 | 118.0604 | 118.0805 | -2.5491
4178.5 | 120.8954 | -118.0481 | 2.4353 | 1.4211e-13 | 0.023946 | 0.016133 | 0.0094682 | -0.023148 | 0.0048523 | 0.23258 | 0.024598 | 0.035031 | -0.096424 | -0.0037841 | 0.00064308 | 0.07888 | 0.015142 | 0.005325 | 0.065863 | 0.096516 | 0.24727 | -0.049321 | 0.078886 | 0.018674 | 0.007751 | 0.038723 | 0.11901 | -0.047193 | -0.11378 | 117.9988 | -2.3694 | 118.127 | 118.0534 | 0.054646 | -2.3388 | -2.188 | 117.9343 | -2.3966 | 118.127 | 118.0558 | 0.12153 | -2.3163 | -2.4825 | 118.114 | 118.1446 | 118.2954 | 118.0632 | -2.4846 | 118.0868 | 118.1671 | 118.0009 | 118.0668 | -2.5491
4180.2188 | 120.9915 | -118.3502 | 2.2156 | 1.4211e-13 | 0.023946 | 0.015919 | 0.009682 | -0.023362 | 0.0046387 | 0.23258 | 0.024171 | 0.035031 | -0.096851 | -0.0037841 | 0.00064308 | 0.083459 | 0.015142 | 0.009904 | 0.07502 | 0.091937 | 0.25185 | -0.044742 | 0.074307 | 0.027831 | 0.003172 | 0.034145 | 0.12817 | 0.021486 | -0.11836 | 118.3055 | -2.1406 | 118.4337 | 118.3601 | 0.054646 | -2.1236 | -1.9637 | 118.2319 | -2.1814 | 118.4245 | 118.3534 | 0.12153 | -2.0874 | -2.1941 | 118.4252 | 118.4422 | 118.6021 | 118.3654 | -2.2603 | 118.3844 | 118.4784 | 118.3717 | 118.3781 | -2.3339
4181.9844 | 120.8817 | -118.5699 | 2.092 | 1.4211e-13 | 0.02416 | 0.015919 | 0.0098956 | -0.023148 | 0.0050659 | 0.23258 | 0.024385 | 0.034818 | -0.096851 | -0.0039979 | 0.00085668 | 0.07888 | 0.015142 | 0.005325 | 0.070441 | 0.096516 | 0.24269 | -0.031005 | 0.069728 | 0.027831 | -0.001407 | 0.029566 | 0.11444 | 0.021486 | -0.11378 | 118.5389 | -2.0215 | 118.6488 | 118.5753 | 0.03633 | -1.9955 | -1.8493 | 118.4562 | -2.0624 | 118.6397 | 118.5685 | 0.11237 | -1.9775 | -2.0705 | 118.6404 | 118.6665 | 118.8126 | 118.5851 | -2.123 | 118.5995 | 118.6844 | 118.5914 | 118.5978 | -2.2058
4183.6875 | 120.9091 | -118.959 | 1.7349 | 1.4211e-13 | 0.023946 | 0.015919 | 0.0094682 | -0.023362 | 0.0048523 | 0.22495 | 0.024385 | 0.034604 | -0.096637 | -0.0037841 | 0.00085668 | 0.074302 | 0.015142 | 0.000747 | 0.07502 | 0.091937 | 0.24727 | -0.040163 | 0.074307 | 0.023253 | -0.001407 | 0.038723 | 0.11901 | 0.016908 | -0.11836 | 118.9189 | -1.6599 | 119.0333 | 118.9598 | 0.04091 | -1.643 | -1.4876 | 118.8407 | -1.6962 | 119.0334 | 118.9576 | 0.11695 | -1.6159 | -1.718 | 119.0341 | 119.051 | 119.2063 | 118.9742 | -1.7751 | 118.9978 | 119.0781 | 118.976 | 118.9823 | -1.8533
4185.4531 | 120.9137 | -118.5104 | 2.1423 | 1.4211e-13 | 0.02416 | 0.016346 | 0.0098956 | -0.023362 | 0.0048523 | 0.24021 | 0.024598 | 0.034818 | -0.096851 | -0.0037841 | 0.00021588 | 0.069723 | 0.015142 | 0.009904 | 0.061284 | 0.096516 | 0.24269 | -0.044742 | 0.074307 | 0.018674 | -0.005985 | 0.034145 | 0.11444 | 0.016908 | -0.11378 | 118.4657 | -2.081 | 118.5802 | 118.5203 | 0.054646 | -2.0458 | -1.8996 | 118.3967 | -2.1082 | 118.5847 | 118.5045 | 0.1078 | -2.0279 | -2.1254 | 118.5717 | 118.607 | 118.7531 | 118.5256 | -2.1871 | 118.5446 | 118.6249 | 118.5273 | 118.5291 | -2.2561
4187.2344 | 120.9961 | -119.4077 | 1.3458 | 1.4211e-13 | 0.02416 | 0.015919 | 0.0094682 | -0.023362 | 0.0046387 | 0.23258 | 0.024385 | 0.034818 | -0.096637 | -0.0035705 | 0.00042948 | 0.074302 | 0.015142 | 0.000747 | 0.065863 | 0.08278 | 0.25185 | -0.026426 | 0.069728 | 0.027831 | -0.001407 | 0.038723 | 0.12359 | 0.012329 | -0.12752 | 119.3812 | -1.28 | 119.482 | 119.4084 | 0.027173 | -1.263 | -1.094 | 119.2801 | -1.3071 | 119.4774 | 119.4062 | 0.12611 | -1.2222 | -1.3335 | 119.4735 | 119.4904 | 119.6595 | 119.4228 | -1.3723 | 119.4464 | 119.5312 | 119.42 | 119.4355 | -1.4733
4188.9688 | 120.7809 | -118.4189 | 2.0966 | 1.4211e-13 | 0.02416 | 0.015705 | 0.0094682 | -0.023362 | 0.0050659 | 0.23258 | 0.024171 | 0.034604 | -0.096637 | -0.0039979 | 0.00042948 | 0.074302 | 0.015142 | 0.009904 | 0.061284 | 0.091937 | 0.25185 | -0.081373 | 0.078886 | 0.018674 | -0.001407 | 0.038723 | 0.12817 | 0.021486 | -0.1092 | 118.3375 | -2.0353 | 118.4932 | 118.4288 | 0.091277 | -2.0046 | -1.8447 | 118.3097 | -2.0578 | 118.4978 | 118.4175 | 0.1078 | -1.9684 | -2.0751 | 118.4802 | 118.5108 | 118.6707 | 118.434 | -2.1779 | 118.4576 | 118.5471 | 118.4404 | 118.4376 | -2.2058
4190.75 | 120.8405 | -117.778 | 2.9709 | 1.4211e-13 | 0.02416 | 0.016346 | 0.0098956 | -0.023148 | 0.0048523 | 0.24784 | 0.024385 | 0.034604 | -0.09621 | -0.0037841 | 0.00085668 | 0.069723 | 0.015142 | 0.005325 | 0.065863 | 0.096516 | 0.24727 | -0.031005 | 0.069728 | 0.023253 | 0.003172 | 0.038723 | 0.11901 | -0.001407 | -0.11378 | 117.747 | -2.905 | 117.8477 | 117.7833 | 0.03633 | -2.8744 | -2.7236 | 117.6642 | -2.9322 | 117.8477 | 117.7812 | 0.11695 | -2.8519 | -2.9723 | 117.8439 | 117.8745 | 118.0253 | 117.7932 | -3.0019 | 117.8167 | 117.897 | 117.7766 | 117.8013 | -3.0847
4192.4844 | 120.9366 | -118.8858 | 1.7578 | 1.4211e-13 | 0.023733 | 0.015919 | 0.0094682 | -0.023362 | 0.0046387 | 0.23258 | 0.024385 | 0.034604 | -0.096637 | -0.0033569 | 0.00064308 | 0.07888 | 0.019721 | 0.005325 | 0.07502 | 0.096516 | 0.24727 | -0.053899 | 0.078886 | 0.023253 | -0.005985 | 0.038723 | 0.12359 | 0.016908 | -0.1092 | 118.8319 | -1.6828 | 118.9647 | 118.8911 | 0.059224 | -1.6613 | -1.5105 | 118.7766 | -1.7191 | 118.9647 | 118.8798 | 0.10322 | -1.6342 | -1.7409 | 118.9608 | 118.9823 | 119.1331 | 118.9055 | -1.8117 | 118.9245 | 119.0094 | 118.9027 | 118.9091 | -1.867
4194.25 | 120.9549 | -119.1101 | 1.6067 | 1.4211e-13 | 0.02416 | 0.015705 | 0.009682 | -0.023362 | 0.0046387 | 0.23258 | 0.024171 | 0.035031 | -0.096637 | -0.0037841 | 0.00064308 | 0.07888 | 0.015142 | 0.005325 | 0.070441 | 0.1011 | 0.24727 | -0.053899 | 0.069728 | 0.036989 | 0.003172 | 0.043302 | 0.12359 | 0.016908 | -0.1092 | 119.0562 | -1.5363 | 119.189 | 119.1154 | 0.059224 | -1.5057 | -1.3595 | 119.0009 | -1.5634 | 119.1798 | 119.1133 | 0.11237 | -1.4832 | -1.5898 | 119.1805 | 119.2112 | 119.3574 | 119.1252 | -1.6606 | 119.1534 | 119.2337 | 119.127 | 119.1471 | -1.716
4196.0156 | 120.9595 | -114.7156 | 3.8315 | 1.4211e-13 | 0.023946 | 0.015705 | 0.009682 | -0.023362 | 0.0044249 | 0.23258 | 0.024385 | 0.034604 | -0.096637 | -0.0042115 | 0.00064308 | 0.069723 | 0.015142 | 0.005325 | 0.065863 | 0.091937 | 0.24269 | -0.031005 | 0.074307 | 0.027831 | -0.001407 | 0.034145 | 0.10986 | 0.007751 | -0.11836 | 114.6846 | -3.7656 | 114.7853 | 114.7209 | 0.03633 | -3.7395 | -3.5888 | 114.5972 | -3.7973 | 114.7899 | 114.7142 | 0.11695 | -3.7216 | -3.8237 | 114.7814 | 114.8075 | 114.9583 | 114.7307 | -3.8625 | 114.7497 | 114.8254 | 114.7233 | 114.7434 | -3.9498
4197.7188 | 121.0373 | -119.2932 | 1.4191 | 1.4211e-13 | 0.023946 | 0.015705 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034818 | -0.096424 | -0.0039979 | 0.0010705 | 0.07888 | 0.0243 | 0.014482 | 0.070441 | 0.10567 | 0.24727 | -0.035584 | 0.06515 | 0.018674 | -0.010564 | 0.034145 | 0.12359 | 0.026065 | -0.11378 | 119.2576 | -1.3486 | 119.3721 | 119.3077 | 0.050066 | -1.3134 | -1.1718 | 119.1794 | -1.3849 | 119.3584 | 119.2826 | 0.10322 | -1.2955 | -1.393 | 119.3637 | 119.3989 | 119.5405 | 119.3175 | -1.4547 | 119.3274 | 119.4168 | 119.3193 | 119.3119 | -1.5328
4199.4844 | 121.0831 | -117.6132 | 3.1036 | 1.4211e-13 | 0.023946 | 0.016133 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.035031 | -0.096851 | -0.0035705 | 0.00064308 | 0.069723 | 0.015142 | 0.009904 | 0.061284 | 0.091937 | 0.23812 | -0.021847 | 0.074307 | 0.023253 | 0.003172 | 0.038723 | 0.12359 | -0.005985 | -0.11836 | 117.5914 | -3.0424 | 117.6829 | 117.6231 | 0.031751 | -3.0117 | -2.8655 | 117.4949 | -3.0649 | 117.6875 | 117.6164 | 0.12153 | -2.98 | -3.1096 | 117.6745 | 117.7052 | 117.8513 | 117.6284 | -3.1255 | 117.6519 | 117.7368 | 117.6072 | 117.6365 | -3.222
4201.2031 | 121.0831 | -119.4077 | 1.3687 | 1.4211e-13 | 0.023519 | 0.015919 | 0.009682 | -0.023576 | 0.0050659 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0037841 | 0.00042948 | 0.074302 | 0.015142 | 0.005325 | 0.065863 | 0.096516 | 0.25185 | -0.053899 | 0.074307 | 0.027831 | -0.001407 | 0.038723 | 0.11901 | -0.001407 | -0.11836 | 119.3538 | -1.3029 | 119.482 | 119.413 | 0.059224 | -1.2722 | -1.1169 | 119.2893 | -1.33 | 119.482 | 119.4062 | 0.11695 | -1.2497 | -1.3701 | 119.4735 | 119.5042 | 119.6595 | 119.4228 | -1.4226 | 119.4464 | 119.5267 | 119.4062 | 119.4355 | -1.4871
4203 | 120.9732 | -119.2383 | 1.6113 | 1.4211e-13 | 0.023519 | 0.015919 | 0.009682 | -0.023148 | 0.0050659 | 0.24021 | 0.024385 | 0.034818 | -0.096851 | -0.0035705 | 0.00042948 | 0.074302 | 0.015142 | 0.009904 | 0.061284 | 0.091937 | 0.24727 | -0.035584 | 0.074307 | 0.018674 | -0.005985 | 0.038723 | 0.12359 | 0.021486 | -0.12294 | 119.2027 | -1.55 | 119.3126 | 119.2482 | 0.045488 | -1.5194 | -1.3641 | 119.1153 | -1.5726 | 119.3126 | 119.2323 | 0.11695 | -1.4877 | -1.5898 | 119.2996 | 119.3302 | 119.4856 | 119.2534 | -1.6469 | 119.277 | 119.3619 | 119.2598 | 119.257 | -1.7343
4204.75 | 121.0693 | -119.8013 | 1.062 | 1.4211e-13 | 0.023733 | 0.015919 | 0.009682 | -0.023576 | 0.0048523 | 0.22495 | 0.024385 | 0.034604 | -0.096424 | -0.0037841 | 0.00021588 | 0.069723 | 0.019721 | 0.000747 | 0.065863 | 0.091937 | 0.25185 | -0.026426 | 0.069728 | 0.018674 | -0.010564 | 0.043302 | 0.11901 | 0.007751 | -0.11836 | 119.7749 | -0.99615 | 119.8711 | 119.8021 | 0.027173 | -0.97007 | -0.81016 | 119.683 | -1.0187 | 119.8711 | 119.7908 | 0.1078 | -0.943 | -1.0543 | 119.8672 | 119.8933 | 120.0532 | 119.8211 | -1.0884 | 119.8446 | 119.9203 | 119.8091 | 119.82 | -1.1804
4206.5 | 120.9686 | -119.902 | 1.0117 | 1.4211e-13 | 0.023733 | 0.015919 | 0.009682 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.034604 | -0.096637 | -0.0035705 | 0.00064308 | 0.074302 | 0.019721 | 0.005325 | 0.065863 | 0.087359 | 0.24727 | -0.035584 | 0.074307 | 0.03241 | -0.001407 | 0.034145 | 0.11901 | 0.016908 | -0.11836 | 119.8665 | -0.94579 | 119.9763 | 119.9074 | 0.040909 | -0.9243 | -0.76438 | 119.7837 | -0.97751 | 119.9763 | 119.9006 | 0.11695 | -0.89264 | -0.99475 | 119.9679 | 119.9894 | 120.1493 | 119.9218 | -1.0472 | 119.9362 | 120.0211 | 119.9189 | 119.9344 | -1.13
4208.2656 | 121.0144 | -119.0323 | 1.9363 | 1.4211e-13 | 0.023733 | 0.016133 | 0.009682 | -0.023362 | 0.0050659 | 0.24021 | 0.024385 | 0.034604 | -0.096851 | -0.0039979 | 0.00064308 | 0.069723 | 0.015142 | 0.009904 | 0.070441 | 0.096516 | 0.24727 | -0.040163 | 0.074307 | 0.027831 | -0.001407 | 0.034145 | 0.11901 | 0.003172 | -0.1092 | 118.9921 | -1.8659 | 119.102 | 119.0422 | 0.050067 | -1.8398 | -1.6891 | 118.9231 | -1.9022 | 119.1066 | 119.0309 | 0.1078 | -1.8173 | -1.9332 | 119.1027 | 119.1288 | 119.2796 | 119.0474 | -1.9765 | 119.0664 | 119.1513 | 119.0355 | 119.0601 | -2.0455
4210.0156 | 121.0098 | -119.7235 | 1.2634 | 1.4211e-13 | 0.023946 | 0.015919 | 0.0094682 | -0.023576 | 0.0048523 | 0.24021 | 0.024385 | 0.035031 | -0.096851 | -0.0037841 | 0.00064308 | 0.07888 | 0.010564 | 0.009904 | 0.065863 | 0.091937 | 0.24727 | -0.031005 | 0.074307 | 0.027831 | 0.007751 | 0.038723 | 0.11901 | 0.035222 | -0.11836 | 119.6925 | -1.1976 | 119.8024 | 119.7334 | 0.040909 | -1.1715 | -1.0162 | 119.6052 | -1.2247 | 119.7978 | 119.7313 | 0.12611 | -1.1444 | -1.2282 | 119.7894 | 119.8154 | 119.9708 | 119.7341 | -1.2944 | 119.7622 | 119.8425 | 119.7587 | 119.7513 | -1.3818
4211.7656 | 121.1243 | -119.7739 | 1.1536 | 1.4211e-13 | 0.023519 | 0.016346 | 0.0094682 | -0.023362 | 0.0044249 | 0.24021 | 0.024385 | 0.034818 | -0.096424 | -0.0035705 | 0.00085668 | 0.074302 | 0.015142 | 0.000747 | 0.070441 | 0.1011 | 0.24727 | -0.026426 | 0.074307 | 0.023253 | 0.003172 | 0.038723 | 0.11901 | 0.026065 | -0.12752 | 119.7474 | -1.0831 | 119.8482 | 119.7746 | 0.027173 | -1.0525 | -0.90629 | 119.6463 | -1.1148 | 119.8482 | 119.777 | 0.13069 | -1.0346 | -1.1275 | 119.8443 | 119.875 | 120.0211 | 119.789 | -1.18 | 119.8126 | 119.8929 | 119.7999 | 119.7971 | -1.2811
4213.4844 | 121.0419 | -119.902 | 1.0162 | 1.4211e-13 | 0.023946 | 0.015705 | 0.009682 | -0.023362 | 0.0046387 | 0.24784 | 0.024385 | 0.034818 | -0.096851 | -0.0037841 | 0.00085668 | 0.07888 | 0.015142 | 0.000747 | 0.070441 | 0.096516 | 0.24269 | -0.053899 | 0.069728 | 0.023253 | -0.001407 | 0.034145 | 0.11901 | 0.026065 | -0.11836 | 119.8481 | -0.94579 | 119.9809 | 119.9028 | 0.054646 | -0.91972 | -0.77354 | 119.7837 | -0.98209 | 119.9718 | 119.9006 | 0.11695 | -0.89722 | -0.99017 | 119.9725 | 119.9986 | 120.1447 | 119.9172 | -1.0701 | 119.9362 | 120.0211 | 119.9281 | 119.9253 | -1.1346
4215.2344 | 121.0922 | -120.1218 | 0.82398 | 1.4211e-13 | 0.023519 | 0.015705 | 0.009682 | -0.023576 | 0.0048523 | 0.22495 | 0.024171 | 0.035031 | -0.096851 | -0.0035705 | 0.00085668 | 0.069723 | 0.0243 | 0.005325 | 0.061284 | 0.1011 | 0.24727 | -0.044742 | 0.069728 | 0.027831 | -0.001407 | 0.038723 | 0.11444 | -0.001407 | -0.11378 | 120.077 | -0.76269 | 120.1915 | 120.1271 | 0.050067 | -0.72288 | -0.5767 | 120.008 | -0.78525 | 120.1915 | 120.1204 | 0.11237 | -0.70954 | -0.82538 | 120.183 | 120.2229 | 120.369 | 120.1461 | -0.86872 | 120.1605 | 120.2362 | 120.1204 | 120.1496 | -0.93776
4217 | 121.1517 | -119.8929 | 1.0574 | 1.4211e-13 | 0.023733 | 0.016133 | 0.009682 | -0.024003 | 0.0046387 | 0.22495 | 0.024385 | 0.034818 | -0.097065 | -0.0037841 | 0.00085668 | 0.074302 | 0.019721 | 0.005325 | 0.070441 | 0.1011 | 0.24269 | -0.00811 | 0.074307 | 0.027831 | -0.005985 | 0.029566 | 0.11901 | 0.016908 | -0.12294 | 119.8848 | -0.98699 | 119.9672 | 119.8982 | 0.013435 | -0.95634 | -0.81474 | 119.7699 | -1.0279 | 119.9672 | 119.8869 | 0.11695 | -0.93842 | -1.0405 | 119.9633 | 119.994 | 120.1356 | 119.9126 | -1.0655 | 119.9224 | 120.0119 | 119.9098 | 119.9207 | -1.1804
4218.7812 | 121.1288 | -120.3644 | 0.61798 | 1.4211e-13 | 0.023305 | 0.016346 | 0.0098956 | -0.022935 | 0.0046387 | 0.24021 | 0.024171 | 0.034818 | -0.096851 | -0.0037841 | 0.00064308 | 0.069723 | 0.015142 | 0.000747 | 0.070441 | 0.1011 | 0.24269 | -0.035584 | 0.074307 | 0.027831 | -0.001407 | 0.043302 | 0.11901 | 0.003172 | -0.11378 | 120.3288 | -0.54754 | 120.4341 | 120.3651 | 0.036331 | -0.51689 | -0.37529 | 120.2506 | -0.57468 | 120.4387 | 120.363 | 0.11237 | -0.49897 | -0.61481 | 120.4348 | 120.4655 | 120.6071 | 120.3795 | -0.65356 | 120.4077 | 120.4834 | 120.3676 | 120.3922 | -0.73176
4220.5625 | 121.051 | -120.4742 | 0.57678 | 1.4211e-13 | 0.023733 | 0.016346 | 0.010109 | -0.023789 | 0.0050659 | 0.24021 | 0.024171 | 0.034818 | -0.096851 | -0.0037841 | 0.00085668 | 0.074302 | 0.015142 | 0.005325 | 0.070441 | 0.1011 | 0.24269 | -0.044742 | 0.06515 | 0.027831 | 0.003172 | 0.038723 | 0.11901 | -0.001407 | -0.12294 | 120.4295 | -0.50634 | 120.5485 | 120.4796 | 0.050067 | -0.47569 | -0.33409 | 120.3513 | -0.53806 | 120.5394 | 120.4774 | 0.12611 | -0.45777 | -0.57819 | 120.5447 | 120.5753 | 120.7169 | 120.4894 | -0.62152 | 120.513 | 120.5933 | 120.4728 | 120.5021 | -0.69972
4222.3438 | 121.2524 | -120.1675 | 0.72784 | 1.4211e-13 | 0.023946 | 0.016346 | 0.0094682 | -0.023576 | 0.0046387 | 0.24784 | 0.024385 | 0.034604 | -0.096424 | -0.0039979 | 0.00085668 | 0.074302 | 0.019721 | 0.005325 | 0.070441 | 0.096516 | 0.24727 | -0.031005 | 0.069728 | 0.018674 | -0.005985 | 0.038723 | 0.11901 | 0.026065 | -0.11836 | 120.1365 | -0.6574 | 120.2418 | 120.1729 | 0.03633 | -0.63133 | -0.48057 | 120.0492 | -0.68912 | 120.2373 | 120.1616 | 0.11238 | -0.60883 | -0.70178 | 120.238 | 120.2641 | 120.4148 | 120.1873 | -0.75885 | 120.2063 | 120.2866 | 120.1936 | 120.1862 | -0.84621
4224.125 | 121.1243 | -120.3918 | 0.66834 | 1.4211e-13 | 0.023305 | 0.016346 | 0.0092546 | -0.023576 | 0.0048523 | 0.23258 | 0.024385 | 0.034604 | -0.096424 | -0.0039979 | 0.00064308 | 0.065145 | 0.015142 | 0.005325 | 0.065863 | 0.091937 | 0.25643 | -0.063057 | 0.074307 | 0.023253 | -0.001407 | 0.034145 | 0.12359 | 0.007751 | -0.1092 | 120.3288 | -0.60247 | 120.457 | 120.3972 | 0.068382 | -0.5764 | -0.4119 | 120.2826 | -0.63419 | 120.4662 | 120.3904 | 0.1078 | -0.54474 | -0.66058 | 120.4577 | 120.4838 | 120.6483 | 120.407 | -0.73139 | 120.426 | 120.5154 | 120.3996 | 120.4151 | -0.77754
4225.8594 | 121.2112 | -120.2911 | 0.70496 | 1.4211e-13 | 0.023946 | 0.015919 | 0.0094682 | -0.023362 | 0.0048523 | 0.23258 | 0.024385 | 0.034818 | -0.09621 | -0.0039979 | 0.00064308 | 0.069723 | 0.010564 | 0.005325 | 0.065863 | 0.1011 | 0.24727 | -0.053899 | 0.060571 | 0.018674 | -0.001407 | 0.038723 | 0.12359 | 0.030644 | -0.11378 | 120.2372 | -0.63909 | 120.3609 | 120.2965 | 0.059224 | -0.60386 | -0.45768 | 120.1774 | -0.66623 | 120.3517 | 120.2897 | 0.11237 | -0.58136 | -0.67431 | 120.357 | 120.3922 | 120.5384 | 120.3017 | -0.75886 | 120.3299 | 120.4147 | 120.3218 | 120.3098 | -0.81874
4227.625 | 121.2616 | -119.2383 | 1.6617 | 1.4211e-13 | 0.023946 | 0.015919 | 0.009682 | -0.023362 | 0.0046387 | 0.23258 | 0.024385 | 0.035031 | -0.096637 | -0.0039979 | 0.00085668 | 0.074302 | 0.015142 | 0.009904 | 0.065863 | 0.096516 | 0.23812 | -0.031005 | 0.069728 | 0.018674 | -0.001407 | 0.034145 | 0.11444 | 0.021486 | -0.11378 | 119.2073 | -1.5958 | 119.3126 | 119.2482 | 0.040909 | -1.5652 | -1.4236 | 119.1245 | -1.6275 | 119.308 | 119.2369 | 0.11237 | -1.5472 | -1.6402 | 119.3041 | 119.3348 | 119.4764 | 119.2534 | -1.6927 | 119.2724 | 119.3527 | 119.2598 | 119.257 | -1.7755
4229.3906 | 121.1563 | -119.2062 | 1.8951 | 1.4211e-13 | 0.023733 | 0.015705 | 0.0094682 | -0.023362 | 0.0048523 | 0.23258 | 0.024598 | 0.034818 | -0.096637 | -0.0039979 | 0.00064308 | 0.074302 | 0.019721 | 0.005325 | 0.070441 | 0.091937 | 0.24727 | -0.058478 | 0.078886 | 0.023253 | -0.001407 | 0.034145 | 0.12359 | 0.003172 | -0.1092 | 119.1478 | -1.8247 | 119.2805 | 119.2116 | 0.063803 | -1.8032 | -1.6479 | 119.097 | -1.861 | 119.2851 | 119.2048 | 0.1078 | -1.7715 | -1.892 | 119.2767 | 119.2982 | 119.4535 | 119.226 | -1.9536 | 119.2404 | 119.3298 | 119.2094 | 119.2295 | -2.0043
4231.125 | 120.0485 | -74.9222 | 44.8105 | 1.4211e-13 | 0.023519 | 0.016133 | 0.009041 | -0.023148 | 0.0046387 | 0.23258 | 0.024385 | 0.035031 | -0.096637 | -0.0039979 | 0.00064308 | 0.060567 | 0.001407 | -0.017566 | 0.056706 | 0.078201 | 0.2198 | -0.085952 | 0.055992 | 0.004938 | -0.019721 | 0.015831 | 0.10528 | -0.05635 | -0.1321 | 74.8362 | -44.7538 | 74.9827 | 74.9046 | 0.068386 | -44.7323 | -44.5907 | 74.7901 | -44.7947 | 74.9782 | 74.9025 | 0.11238 | -44.7052 | -44.8668 | 74.9789 | 75.0004 | 75.142 | 74.9236 | -44.8964 | 74.938 | 75.0275 | 74.8658 | 74.9271 | -44.9426
4232.875 | 104.7043 | -5.4291 | 90.8478 | 1.4211e-13 | 0.023519 | 0.016133 | 0.0094682 | -0.022935 | 0.0048523 | 0.23258 | 0.024171 | 0.034818 | -0.096637 | -0.0039979 | 0.00085668 | 0.05141 | 0.001407 | -0.017566 | 0.056706 | 0.073622 | 0.22896 | -0.09511 | 0.055992 | 0.004938 | -0.019721 | 0.015831 | 0.1007 | -0.05635 | -0.14125 | 5.334 | -90.7911 | 5.4805 | 5.4115 | 0.077544 | -90.7742 | -90.6188 | 5.2878 | -90.8319 | 5.4851 | 5.4094 | 0.12153 | -90.7471 | -90.9041 | 5.4858 | 5.5027 | 5.658 | 5.4305 | -90.9429 | 5.4449 | 5.5298 | 5.3727 | 5.434 | -90.989
4234.625 | 120.2682 | -96.0938 | 23.8586 | 1.4211e-13 | 0.023305 | 0.015705 | 0.009682 | -0.023148 | 0.0046387 | 0.23258 | 0.024385 | 0.034604 | -0.096851 | -0.0037841 | 0.00085668 | 0.060567 | 0.005985 | -0.008409 | 0.061284 | 0.08278 | 0.22896 | -0.081373 | 0.06515 | 0.014095 | -0.005985 | 0.024988 | 0.10986 | -0.028878 | -0.11836 | 96.0124 | -23.7974 | 96.1543 | 96.0853 | 0.072964 | -23.7759 | -23.6297 | 95.9754 | -23.8337 | 96.1589 | 96.0878 | 0.11238 | -23.7488 | -23.8875 | 96.155 | 96.1765 | 96.3227 | 96.0997 | -23.94 | 96.1187 | 96.2036 | 96.0649 | 96.1078 | -23.977
4236.375 | 120.4285 | -95.9244 | 24.1699 | 1.4211e-13 | 0.023733 | 0.015919 | 0.009682 | -0.022935 | 0.0046387 | 0.23258 | 0.024171 | 0.034818 | -0.096424 | -0.0039979 | 0.00042948 | 0.05141 | -0.003172 | -0.012988 | 0.056706 | 0.078201 | 0.22438 | -0.076794 | 0.055992 | 0.009516 | -0.019721 | 0.015831 | 0.1007 | -0.042614 | -0.1321 | 95.8476 | -24.1132 | 95.9758 | 95.9114 | 0.063806 | -24.0917 | -23.9455 | 95.7923 | -24.1541 | 95.9804 | 95.9047 | 0.11238 | -24.0692 | -24.2125 | 95.9811 | 96.0026 | 96.1488 | 95.9212 | -24.2467 | 95.9402 | 96.0251 | 95.8818 | 95.9339 | -24.302
4238.1406 | 120.2911 | -95.842 | 23.9273 | 1.4211e-13 | 0.023519 | 0.015705 | 0.009682 | -0.023148 | 0.0042113 | 0.24021 | 0.023957 | 0.034818 | -0.096637 | -0.0037841 | 0.00085668 | 0.069723 | 0.010564 | 0.000747 | 0.065863 | 0.087359 | 0.23812 | -0.072215 | 0.060571 | 0.018674 | -0.010564 | 0.029566 | 0.10986 | -0.005985 | -0.11836 | 95.7698 | -23.8614 | 95.9117 | 95.8427 | 0.072962 | -23.8399 | -23.6892 | 95.7236 | -23.8977 | 95.9026 | 95.8314 | 0.1078 | -23.8174 | -23.9333 | 95.9078 | 95.9293 | 96.0801 | 95.8525 | -23.9995 | 95.8715 | 95.9518 | 95.836 | 95.8607 | -24.0457
4239.8594 | 117.2104 | -68.2709 | 45.7306 | 1.4211e-13 | 0.023519 | 0.015705 | 0.009682 | -0.023362 | 0.0050659 | 0.24784 | 0.024385 | 0.034818 | -0.096637 | -0.0035705 | 0.00085668 | 0.065145 | 0.015142 | 0.000747 | 0.061284 | 0.091937 | 0.24269 | -0.053899 | 0.06515 | 0.014095 | -0.010564 | 0.029566 | 0.10528 | -0.010564 | -0.12294 | 68.217 | -45.6693 | 68.336 | 68.2716 | 0.054646 | -45.6387 | -45.4879 | 68.1479 | -45.701 | 68.336 | 68.2603 | 0.11238 | -45.6253 | -45.7412 | 68.3322 | 68.3628 | 68.5136 | 68.286 | -45.7845 | 68.3004 | 68.3762 | 68.2603 | 68.285 | -45.8535
4241.6094 | 104.3701 | -63.5742 | 55.5267 | 1.4211e-13 | 0.023733 | 0.015492 | 0.0094682 | -0.023148 | 0.0048523 | 0.22495 | 0.024385 | 0.035031 | -0.096851 | -0.0039979 | 0.00085668 | 0.060567 | 0.005985 | 0.000747 | 0.056706 | 0.08278 | 0.24269 | -0.076794 | 0.060571 | 0.014095 | -0.005985 | 0.024988 | 0.1007 | -0.015142 | -0.1321 | 63.4974 | -55.47 | 63.6348 | 63.575 | 0.077541 | -55.444 | -55.284 | 63.4421 | -55.5017 | 63.6348 | 63.5682 | 0.12611 | -55.426 | -55.5419 | 63.6309 | 63.657 | 63.8169 | 63.5802 | -55.6035 | 63.5992 | 63.6749 | 63.5591 | 63.5883 | -55.6588
4243.3281 | 120.2774 | -105.0751 | 16.8091 | 1.4211e-13 | 0.023733 | 0.016346 | 0.0094682 | -0.023576 | 0.0046387 | 0.24021 | 0.024171 | 0.034818 | -0.096637 | -0.0037841 | 0.00064308 | 0.069723 | 0.010564 | 0.005325 | 0.065863 | 0.091937 | 0.23812 | -0.035584 | 0.074307 | 0.023253 | -0.005985 | 0.043302 | 0.11444 | 0.007751 | -0.11836 | 105.0395 | -16.7432 | 105.1448 | 105.0804 | 0.040909 | -16.7171 | -16.571 | 104.9567 | -16.7658 | 105.1494 | 105.0691 | 0.11238 | -16.6946 | -16.8013 | 105.1409 | 105.167 | 105.3132 | 105.0856 | -16.8447 | 105.1184 | 105.1895 | 105.0828 | 105.0983 | -16.9274
4245.0625 | 120.5612 | -25.3738 | 89.1769 | 1.4211e-13 | 0.023733 | 0.015919 | 0.009682 | -0.023148 | 0.0046387 | 0.22495 | 0.024171 | 0.034604 | -0.097065 | -0.0039979 | 0.00085668 | 0.046831 | -0.016908 | -0.022144 | 0.038393 | 0.059885 | 0.21522 | -0.09511 | 0.042256 | -0.00422 | -0.0243 | -0.002483 | 0.082386 | -0.097557 | -0.15041 | 25.2787 | -89.1385 | 25.4207 | 25.3517 | 0.072966 | -89.1171 | -88.9617 | 25.2234 | -89.1794 | 25.4161 | 25.3495 | 0.12611 | -89.0946 | -89.2745 | 25.4122 | 25.4337 | 25.5891 | 25.3569 | -89.2721 | 25.3714 | 25.4562 | 25.2763 | 25.3696 | -89.3274
4246.7812 | 89.5615 | -0.10986 | 82.8415 | 1.4211e-13 | 0.023305 | 0.016133 | 0.009682 | -0.023148 | 0.0048523 | 0.23258 | 0.024171 | 0.034818 | -0.096851 | -0.0039979 | 0.00085668 | 0.037675 | -0.021486 | -0.031301 | 0.033814 | 0.046148 | 0.21522 | -0.099689 | 0.033099 | -0.00422 | -0.0243 | 0.002095 | 0.077807 | -0.10671 | -0.15041 | 0.010174 | -82.8077 | 0.14754 | 0.078562 | 0.068388 | -82.7953 | -82.6263 | -0.040549 | -82.8394 | 0.14296 | 0.085563 | 0.12611 | -82.7637 | -82.9482 | 0.14368 | 0.15601 | 0.32509 | 0.088377 | -82.9412 | 0.11196 | 0.18767 | 0.003149 | 0.10564 | -82.9919
4248.5 | 110.6461 | -7.8461 | 88.2385 | 1.4211e-13 | 0.023733 | 0.016133 | 0.0098956 | -0.023789 | 0.0046387 | 0.23258 | 0.024171 | 0.034818 | -0.096637 | -0.0037841 | 0.0010705 | 0.033096 | -0.012329 | -0.026723 | 0.033814 | 0.059885 | 0.21522 | -0.090531 | 0.037677 | -0.00422 | -0.038036 | 0.006674 | 0.082386 | -0.10214 | -0.15041 | 7.7555 | -88.2047 | 7.8792 | 7.8193 | 0.063808 | -88.1786 | -88.0233 | 7.6957 | -88.2319 | 7.8837 | 7.808 | 0.11238 | -88.1561 | -88.3407 | 7.8799 | 7.906 | 8.0613 | 7.8337 | -88.3291 | 7.8527 | 7.9285 | 7.7439 | 7.8418 | -88.3889
4250.3281 | 120.1767 | -10.5835 | 109.4421 | 1.4211e-13 | 0.023733 | 0.015919 | 0.0094682 | -0.023148 | 0.0048523 | 0.23258 | 0.024171 | 0.035031 | -0.097065 | -0.0035705 | 0.00085668 | 0.037675 | -0.012329 | -0.031301 | 0.038393 | 0.064464 | 0.21064 | -0.099689 | 0.037677 | -0.008798 | -0.038036 | 0.006674 | 0.086964 | -0.097557 | -0.15041 | 10.4838 | -109.4037 | 10.6212 | 10.5522 | 0.068388 | -109.3777 | -109.2315 | 10.4331 | -109.4355 | 10.6212 | 10.5455 | 0.11238 | -109.3552 | -109.5397 | 10.6219 | 10.648 | 10.7941 | 10.5712 | -109.5418 | 10.5902 | 10.6705 | 10.4859 | 10.5747 | -109.5926
4252.1094 | 119.8837 | -117.1555 | 2.211 | 1.4211e-13 | 0.023519 | 0.015919 | 0.0092546 | -0.023362 | 0.0044249 | 0.22495 | 0.024385 | 0.035031 | -0.096637 | -0.0035705 | 0.00064308 | 0.069723 | 0.010564 | 0.000747 | 0.065863 | 0.091937 | 0.23354 | -0.072215 | 0.06515 | 0.018674 | -0.010564 | 0.029566 | 0.10986 | -0.015142 | -0.11378 | 117.0832 | -2.1451 | 117.2252 | 117.1562 | 0.072962 | -2.1191 | -1.9775 | 117.0417 | -2.1814 | 117.2206 | 117.1449 | 0.10322 | -2.1011 | -2.2261 | 117.2213 | 117.2474 | 117.389 | 117.166 | -2.2832 | 117.185 | 117.2653 | 117.1403 | 117.1741 | -2.3248
4253.8906 | 120.2637 | -119.0277 | 0.78278 | 1.4211e-13 | 0.023946 | 0.015919 | 0.009682 | -0.023148 | 0.0048523 | 0.24021 | 0.023957 | 0.035031 | -0.096424 | -0.0037841 | 0.00042948 | 0.074302 | 0.015142 | 0.000747 | 0.056706 | 0.091937 | 0.23812 | -0.058478 | 0.074307 | 0.018674 | -0.005985 | 0.029566 | 0.11901 | 0.007751 | -0.11836 | 118.9692 | -0.72607 | 119.102 | 119.0285 | 0.059225 | -0.69084 | -0.54466 | 118.9093 | -0.75321 | 119.102 | 119.0217 | 0.11238 | -0.66376 | -0.77503 | 119.0844 | 119.1196 | 119.2658 | 119.0429 | -0.84125 | 119.0573 | 119.1467 | 119.0355 | 119.0464 | -0.90114
4255.6094 | 120.6665 | -119.6091 | 0.70953 | 1.4211e-13 | 0.023519 | 0.016133 | 0.009682 | -0.023362 | 0.0044249 | 0.24021 | 0.023957 | 0.034818 | -0.096424 | -0.0037841 | 0.00064308 | 0.074302 | 0.015142 | 0.005325 | 0.070441 | 0.096516 | 0.24727 | -0.053899 | 0.074307 | 0.027831 | -0.005985 | 0.038723 | 0.11444 | 0.026065 | -0.11836 | 119.5552 | -0.63909 | 119.6834 | 119.6144 | 0.059224 | -0.61302 | -0.46226 | 119.4907 | -0.67081 | 119.6834 | 119.6031 | 0.11238 | -0.5951 | -0.68347 | 119.6795 | 119.7056 | 119.8563 | 119.6242 | -0.76343 | 119.6478 | 119.7235 | 119.6351 | 119.6369 | -0.8279
4257.3906 | 120.488 | -119.5908 | 0.66376 | 1.4211e-13 | 0.023733 | 0.015705 | 0.009682 | -0.023362 | 0.0046387 | 0.22495 | 0.024171 | 0.034818 | -0.096424 | -0.0037841 | 0.00042948 | 0.069723 | 0.019721 | 0.009904 | 0.065863 | 0.096516 | 0.25185 | -0.053899 | 0.078886 | 0.023253 | -0.001407 | 0.038723 | 0.11444 | 0.016908 | -0.11378 | 119.5369 | -0.59789 | 119.6605 | 119.6007 | 0.063803 | -0.56724 | -0.41191 | 119.477 | -0.62503 | 119.6696 | 119.5894 | 0.11237 | -0.54932 | -0.64685 | 119.6566 | 119.6873 | 119.8426 | 119.6105 | -0.71766 | 119.6295 | 119.7052 | 119.6077 | 119.614 | -0.77754
4259.1406 | 119.8105 | -119.101 | 0.32044 | 1.4211e-13 | 0.023305 | 0.016133 | 0.0094682 | -0.023362 | 0.0046387 | 0.24784 | 0.024171 | 0.034818 | -0.096424 | -0.0037841 | 0.00064308 | 0.083459 | 0.010564 | 0.005325 | 0.065863 | 0.087359 | 0.24269 | -0.053899 | 0.06515 | 0.014095 | -0.001407 | 0.029566 | 0.11444 | 0.003172 | -0.11378 | 119.0471 | -0.25457 | 119.1844 | 119.1063 | 0.059224 | -0.23308 | -0.07774 | 118.9872 | -0.29087 | 119.1661 | 119.0995 | 0.11237 | -0.206 | -0.31726 | 119.1668 | 119.1883 | 119.3436 | 119.1115 | -0.37433 | 119.1305 | 119.2154 | 119.1041 | 119.115 | -0.43422
4260.8438 | 120.4971 | -119.7418 | 0.37994 | 1.4211e-13 | 0.023305 | 0.016133 | 0.0098956 | -0.023148 | 0.0050659 | 0.22495 | 0.023957 | 0.035245 | -0.096424 | -0.0037841 | 0.00064308 | 0.069723 | 0.010564 | 0.009904 | 0.070441 | 0.1011 | 0.25185 | -0.049321 | 0.074307 | 0.018674 | 0.007751 | 0.029566 | 0.11444 | 0.026065 | -0.11836 | 119.6925 | -0.3095 | 119.8115 | 119.7517 | 0.059225 | -0.27885 | -0.12809 | 119.6235 | -0.35038 | 119.8161 | 119.7496 | 0.12611 | -0.26551 | -0.35388 | 119.8123 | 119.8429 | 119.9937 | 119.7524 | -0.42927 | 119.7714 | 119.8563 | 119.7679 | 119.7605 | -0.4983
4262.5625 | 120.5338 | -120.0119 | 0.33417 | 1.4211e-13 | 0.023519 | 0.015705 | 0.0094682 | -0.023148 | 0.0044249 | 0.24784 | 0.024598 | 0.034604 | -0.096424 | -0.0037841 | 0.00064308 | 0.065145 | 0.015142 | 0.009904 | 0.065863 | 0.096516 | 0.25185 | -0.049321 | 0.069728 | 0.023253 | -0.001407 | 0.038723 | 0.12359 | 0.026065 | -0.11378 | 119.9626 | -0.2683 | 120.077 | 120.0218 | 0.059225 | -0.23765 | -0.082315 | 119.8981 | -0.29544 | 120.0816 | 120.0105 | 0.11237 | -0.21057 | -0.3081 | 120.0778 | 120.1084 | 120.2638 | 120.027 | -0.38349 | 120.0506 | 120.1355 | 120.038 | 120.0352 | -0.44795
4264.2969 | 120.639 | -120.108 | 0.27466 | 1.4211e-13 | 0.023519 | 0.016133 | 0.009682 | -0.023362 | 0.0048523 | 0.24021 | 0.024171 | 0.034818 | -0.096637 | -0.0039979 | 0.00042948 | 0.074302 | 0.019721 | 0.005325 | 0.065863 | 0.096516 | 0.24727 | -0.053899 | 0.078886 | 0.018674 | -0.001407 | 0.038723 | 0.11444 | 0.021486 | -0.11836 | 120.0541 | -0.2088 | 120.1823 | 120.1134 | 0.059224 | -0.17814 | -0.027384 | 119.9897 | -0.23594 | 120.1869 | 120.1066 | 0.11695 | -0.16022 | -0.25317 | 120.1739 | 120.2045 | 120.3553 | 120.1278 | -0.32856 | 120.1468 | 120.2225 | 120.1295 | 120.1267 | -0.39302
4266 | 120.6345 | -120.1904 | 0.29755 | 1.4211e-13 | 0.023946 | 0.015705 | 0.009682 | -0.023148 | 0.0046387 | 0.23258 | 0.024385 | 0.034177 | -0.096851 | -0.0035705 | 0.00085668 | 0.07888 | 0.010564 | 0.005325 | 0.070441 | 0.096516 | 0.25185 | -0.063057 | 0.074307 | 0.018674 | 0.003172 | 0.038723 | 0.11901 | 0.021486 | -0.11836 | 120.1274 | -0.2271 | 120.2693 | 120.1958 | 0.068382 | -0.20103 | -0.045694 | 120.0721 | -0.25882 | 120.2647 | 120.1936 | 0.12153 | -0.17853 | -0.27606 | 120.2609 | 120.2869 | 120.4423 | 120.201 | -0.3606 | 120.2292 | 120.3094 | 120.2119 | 120.2091 | -0.41591
4267.7656 | 120.6116 | -120.3049 | 0.31586 | 1.4211e-13 | 0.023733 | 0.015492 | 0.0092546 | -0.023576 | 0.0050659 | 0.24021 | 0.024171 | 0.034604 | -0.096637 | -0.0039979 | 0.00042948 | 0.069723 | 0.015142 | 0.005325 | 0.07502 | 0.091937 | 0.24269 | -0.044742 | 0.074307 | 0.023253 | -0.005985 | 0.034145 | 0.11901 | 0.016908 | -0.11378 | 120.2601 | -0.24084 | 120.3746 | 120.3102 | 0.050067 | -0.22392 | -0.073162 | 120.1911 | -0.28171 | 120.3792 | 120.2989 | 0.1078 | -0.19684 | -0.29895 | 120.3799 | 120.3968 | 120.5476 | 120.32 | -0.3606 | 120.339 | 120.4239 | 120.3218 | 120.3281 | -0.42964
4269.4844 | 120.6757 | -120.1996 | 0.33875 | 1.4211e-13 | 0.023733 | 0.015919 | 0.0094682 | -0.023148 | 0.0048523 | 0.23258 | 0.024171 | 0.034604 | -0.096424 | -0.0039979 | 0.00064308 | 0.069723 | 0.0243 | 0.000747 | 0.07502 | 0.096516 | 0.25643 | -0.058478 | 0.069728 | 0.023253 | -0.001407 | 0.038723 | 0.11444 | 0.021486 | -0.11378 | 120.1411 | -0.26372 | 120.2693 | 120.2003 | 0.059225 | -0.24223 | -0.082314 | 120.0858 | -0.30002 | 120.2693 | 120.1982 | 0.11237 | -0.22431 | -0.31726 | 120.2746 | 120.2961 | 120.456 | 120.2239 | -0.39722 | 120.2383 | 120.314 | 120.2211 | 120.2228 | -0.45253
4271.2031 | 120.6573 | -120.2499 | 0.35248 | 1.4211e-13 | 0.023519 | 0.015705 | 0.0092546 | -0.023789 | 0.0046387 | 0.23258 | 0.024171 | 0.034818 | -0.096424 | -0.0037841 | 0.00064308 | 0.07888 | 0.0243 | 0.005325 | 0.070441 | 0.087359 | 0.25185 | -0.035584 | 0.074307 | 0.023253 | 0.003172 | 0.038723 | 0.11444 | 0.026065 | -0.11836 | 120.2144 | -0.28204 | 120.3288 | 120.2553 | 0.040909 | -0.26512 | -0.10063 | 120.1316 | -0.31376 | 120.3242 | 120.2531 | 0.12153 | -0.23804 | -0.32641 | 120.3204 | 120.3373 | 120.5018 | 120.2742 | -0.38806 | 120.2887 | 120.3644 | 120.276 | 120.2732 | -0.47084
4272.9219 | 120.7214 | -120.1904 | 0.42572 | 1.4211e-13 | 0.023092 | 0.016133 | 0.0094682 | -0.023362 | 0.0046387 | 0.24021 | 0.024385 | 0.034818 | -0.096637 | -0.0035705 | 0.00042948 | 0.07888 | 0.015142 | 0.009904 | 0.070441 | 0.091937 | 0.25185 | -0.021847 | 0.078886 | 0.014095 | -0.001407 | 0.034145 | 0.11901 | 0.021486 | -0.11378 | 120.1686 | -0.35528 | 120.2693 | 120.2003 | 0.031751 | -0.33378 | -0.17387 | 120.0766 | -0.39158 | 120.2693 | 120.189 | 0.11237 | -0.30671 | -0.40423 | 120.2609 | 120.2824 | 120.4423 | 120.2056 | -0.44757 | 120.2246 | 120.3094 | 120.2119 | 120.2045 | -0.5395
4274.6406 | 120.7031 | -120.3003 | 0.35248 | 1.4211e-13 | 0.023733 | 0.015705 | 0.009682 | -0.023148 | 0.0046387 | 0.22495 | 0.023957 | 0.034818 | -0.096851 | -0.0037841 | 0.00064308 | 0.069723 | 0.015142 | 0.014482 | 0.065863 | 0.091937 | 0.24269 | -0.026426 | 0.078886 | 0.023253 | -0.001407 | 0.038723 | 0.11444 | 0.030644 | -0.11378 | 120.2739 | -0.28662 | 120.37 | 120.3148 | 0.040908 | -0.26054 | -0.10978 | 120.1865 | -0.31376 | 120.3792 | 120.2989 | 0.11237 | -0.23804 | -0.32183 | 120.3662 | 120.3922 | 120.543 | 120.3154 | -0.3789 | 120.339 | 120.4147 | 120.3309 | 120.3235 | -0.46626
4276.4219 | 120.7947 | -120.2866 | 0.36163 | 1.4211e-13 | 0.023305 | 0.015492 | 0.0094682 | -0.023148 | 0.0050659 | 0.24021 | 0.024385 | 0.034818 | -0.096851 | -0.0035705 | 0.00021588 | 0.074302 | 0.015142 | 0.000747 | 0.07502 | 0.091937 | 0.24727 | -0.049321 | 0.078886 | 0.023253 | 0.003172 | 0.038723 | 0.11901 | 0.026065 | -0.11378 | 120.2372 | -0.28661 | 120.3609 | 120.2873 | 0.050068 | -0.2697 | -0.11436 | 120.1728 | -0.32291 | 120.3654 | 120.2897 | 0.11695 | -0.24262 | -0.33557 | 120.3616 | 120.3785 | 120.5338 | 120.3017 | -0.41095 | 120.3253 | 120.4056 | 120.3126 | 120.3098 | -0.47541
4278.1562 | 120.7535 | -120.4285 | 0.29755 | 1.4211e-13 | 0.023305 | 0.016346 | 0.0092546 | -0.023148 | 0.0048523 | 0.24021 | 0.024385 | 0.034604 | -0.096424 | -0.0035705 | 0.00064308 | 0.065145 | 0.010564 | 0.009904 | 0.061284 | 0.1011 | 0.24727 | -0.053899 | 0.069728 | 0.018674 | -0.001407 | 0.038723 | 0.11901 | 0.016908 | -0.11836 | 120.3746 | -0.23626 | 120.4936 | 120.4384 | 0.063803 | -0.19645 | -0.050272 | 120.3101 | -0.25882 | 120.4982 | 120.4271 | 0.11695 | -0.17853 | -0.28064 | 120.4898 | 120.5296 | 120.6757 | 120.439 | -0.35145 | 120.4672 | 120.5475 | 120.4454 | 120.4471 | -0.41591
4279.875 | 120.8359 | -120.3735 | 0.30212 | 1.4211e-13 | 0.023733 | 0.015705 | 0.0092546 | -0.023362 | 0.0048523 | 0.23258 | 0.024171 | 0.03439 | -0.096637 | -0.0042115 | 0.00064308 | 0.069723 | 0.010564 | 0.000747 | 0.065863 | 0.096516 | 0.24727 | -0.049321 | 0.069728 | 0.027831 | -0.001407 | 0.034145 | 0.11901 | 0.016908 | -0.11378 | 120.3242 | -0.23626 | 120.4433 | 120.3743 | 0.050068 | -0.20561 | -0.05485 | 120.2598 | -0.26798 | 120.4433 | 120.3721 | 0.11237 | -0.18311 | -0.28522 | 120.4394 | 120.4701 | 120.6208 | 120.3841 | -0.35145 | 120.4077 | 120.4925 | 120.3904 | 120.4014 | -0.41591
4281.6406 | 120.8633 | -120.3232 | 0.36621 | 1.4211e-13 | 0.023519 | 0.015919 | 0.0092546 | -0.023362 | 0.0050659 | 0.24784 | 0.024385 | 0.035245 | -0.096637 | -0.0037841 | 0.00042948 | 0.069723 | 0.010564 | 0.014482 | 0.070441 | 0.096516 | 0.24727 | -0.040163 | 0.078886 | 0.018674 | 0.003172 | 0.038723 | 0.12359 | 0.021486 | -0.11836 | 120.283 | -0.29577 | 120.3929 | 120.3377 | 0.054645 | -0.2697 | -0.11894 | 120.2048 | -0.32749 | 120.4021 | 120.3264 | 0.12153 | -0.24262 | -0.34473 | 120.3936 | 120.4197 | 120.5705 | 120.3337 | -0.40637 | 120.3619 | 120.4468 | 120.3447 | 120.3419 | -0.48457
4283.3906 | 120.9091 | -120.4285 | 0.2655 | 1.4211e-13 | 0.023305 | 0.016133 | 0.0094682 | -0.023148 | 0.0046387 | 0.24784 | 0.024385 | 0.034604 | -0.096424 | -0.0035705 | 0.00042948 | 0.074302 | 0.015142 | 0.005325 | 0.065863 | 0.096516 | 0.24727 | -0.053899 | 0.074307 | 0.018674 | -0.001407 | 0.034145 | 0.12359 | 0.026065 | -0.11836 | 120.3746 | -0.19964 | 120.5028 | 120.4338 | 0.059224 | -0.16899 | -0.018229 | 120.3101 | -0.23136 | 120.5028 | 120.4271 | 0.11695 | -0.14191 | -0.23944 | 120.4943 | 120.525 | 120.6757 | 120.4436 | -0.3194 | 120.4626 | 120.5521 | 120.4545 | 120.4471 | -0.38386
4285.125 | 120.845 | -120.5017 | 0.29297 | 1.4211e-13 | 0.023519 | 0.016133 | 0.0094682 | -0.023362 | 0.0050659 | 0.23258 | 0.024598 | 0.03439 | -0.096851 | -0.0037841 | 0.00064308 | 0.074302 | 0.010564 | 0.009904 | 0.065863 | 0.096516 | 0.24269 | -0.049321 | 0.069728 | 0.023253 | 0.003172 | 0.029566 | 0.12359 | 0.016908 | -0.11378 | 120.4524 | -0.22711 | 120.576 | 120.5116 | 0.059225 | -0.19645 | -0.050274 | 120.3879 | -0.2634 | 120.5714 | 120.5049 | 0.11695 | -0.16938 | -0.27606 | 120.5676 | 120.5982 | 120.7444 | 120.5123 | -0.34229 | 120.5313 | 120.6253 | 120.5186 | 120.525 | -0.40675
4286.875 | 120.9503 | -120.4559 | 0.27924 | 1.4211e-13 | 0.023733 | 0.016133 | 0.0092546 | -0.023362 | 0.0046387 | 0.24784 | 0.024171 | 0.035031 | -0.09621 | -0.0035705 | 0.00064308 | 0.069723 | 0.010564 | 0.009904 | 0.070441 | 0.091937 | 0.24269 | -0.053899 | 0.069728 | 0.023253 | -0.001407 | 0.034145 | 0.11901 | 0.016908 | -0.11836 | 120.402 | -0.20879 | 120.5257 | 120.4658 | 0.063803 | -0.1873 | -0.036541 | 120.3376 | -0.24509 | 120.5257 | 120.4545 | 0.11695 | -0.16022 | -0.26233 | 120.5264 | 120.5479 | 120.6986 | 120.4665 | -0.33313 | 120.4901 | 120.5749 | 120.4728 | 120.4792 | -0.3976
4288.6406 | 120.9091 | -120.4971 | 0.28839 | 1.4211e-13 | 0.023733 | 0.016133 | 0.0092546 | -0.023362 | 0.0046387 | 0.24784 | 0.024171 | 0.034818 | -0.097065 | -0.0037841 | 0.00064308 | 0.069723 | 0.015142 | 0.009904 | 0.065863 | 0.091937 | 0.25185 | -0.058478 | 0.069728 | 0.03241 | -0.001407 | 0.038723 | 0.12359 | 0.021486 | -0.11378 | 120.4387 | -0.22253 | 120.5669 | 120.507 | 0.068382 | -0.19645 | -0.036539 | 120.3833 | -0.24967 | 120.5669 | 120.4957 | 0.11237 | -0.1648 | -0.26691 | 120.563 | 120.5891 | 120.749 | 120.5123 | -0.34687 | 120.5359 | 120.6207 | 120.5186 | 120.5295 | -0.40217
4290.3594 | 121.0602 | -120.3644 | 0.40283 | 1.4211e-13 | 0.023305 | 0.015919 | 0.0094682 | -0.023148 | 0.0050659 | 0.24784 | 0.024171 | 0.034818 | -0.096851 | -0.0039979 | 0.00085668 | 0.074302 | 0.015142 | 0.005325 | 0.070441 | 0.096516 | 0.24269 | -0.063057 | 0.069728 | 0.023253 | -0.001407 | 0.043302 | 0.12359 | 0.021486 | -0.11378 | 120.3013 | -0.33239 | 120.4387 | 120.3697 | 0.068382 | -0.30632 | -0.16014 | 120.2506 | -0.35953 | 120.4341 | 120.363 | 0.11237 | -0.27924 | -0.38135 | 120.4348 | 120.4609 | 120.6071 | 120.3795 | -0.46589 | 120.4077 | 120.488 | 120.3859 | 120.3876 | -0.51661
4292.0938 | 120.9412 | -120.5109 | 0.28839 | 1.4211e-13 | 0.023519 | 0.016133 | 0.0094682 | -0.023362 | 0.0048523 | 0.22495 | 0.024171 | 0.034604 | -0.096851 | -0.0042115 | 0.00064308 | 0.074302 | 0.019721 | 0.009904 | 0.07502 | 0.11025 | 0.24269 | -0.053899 | 0.074307 | 0.018674 | 0.003172 | 0.038723 | 0.12359 | 0.030644 | -0.11836 | 120.457 | -0.21337 | 120.5852 | 120.5208 | 0.063803 | -0.17814 | -0.045696 | 120.3925 | -0.24967 | 120.5852 | 120.514 | 0.12153 | -0.1648 | -0.25775 | 120.5859 | 120.6211 | 120.7536 | 120.5306 | -0.34229 | 120.5496 | 120.6345 | 120.5415 | 120.5295 | -0.40675
4293.8125 | 120.9274 | -120.5521 | 0.27008 | 1.4211e-13 | 0.023305 | 0.015919 | 0.0094682 | -0.023789 | 0.0048523 | 0.24021 | 0.024812 | 0.034818 | -0.096637 | -0.0037841 | 0.00064308 | 0.074302 | 0.015142 | 0.009904 | 0.065863 | 0.096516 | 0.25643 | -0.058478 | 0.074307 | 0.027831 | -0.001407 | 0.038723 | 0.11901 | 0.026065 | -0.12294 | 120.4936 | -0.20422 | 120.6264 | 120.562 | 0.068382 | -0.17357 | -0.01365 | 120.4291 | -0.23136 | 120.6264 | 120.5507 | 0.12153 | -0.15107 | -0.24402 | 120.6179 | 120.6486 | 120.8085 | 120.5672 | -0.32856 | 120.5908 | 120.6711 | 120.5781 | 120.5799 | -0.39302
4295.5469 | 120.8588 | -118.8629 | 1.6617 | 1.4211e-13 | 0.023305 | 0.015919 | 0.0094682 | -0.023362 | 0.0046387 | 0.24021 | 0.024812 | 0.034818 | -0.096424 | -0.0035705 | 0.00064308 | 0.074302 | 0.005985 | 0.014482 | 0.065863 | 0.1011 | 0.25185 | -0.067636 | 0.06515 | 0.023253 | -0.001407 | 0.043302 | 0.11901 | 0.026065 | -0.11378 | 118.7953 | -1.5958 | 118.9372 | 118.8774 | 0.082118 | -1.5606 | -1.4098 | 118.7491 | -1.6184 | 118.9281 | 118.8615 | 0.11237 | -1.5427 | -1.6356 | 118.9288 | 118.964 | 119.1148 | 118.8689 | -1.7293 | 118.9062 | 118.9819 | 118.889 | 118.8862 | -1.7755
4297.2812 | 120.2591 | -94.3405 | 25.3738 | 1.4211e-13 | 0.023305 | 0.016346 | 0.009682 | -0.023148 | 0.0048523 | 0.24784 | 0.024171 | 0.034818 | -0.097065 | -0.0033569 | 0.00064308 | 0.065145 | 0.005985 | 0.005325 | 0.061284 | 0.08278 | 0.23812 | -0.099689 | 0.060571 | 0.018674 | -0.010564 | 0.029566 | 0.11901 | 0.016908 | -0.1321 | 94.2408 | -25.3126 | 94.4057 | 94.3458 | 0.10501 | -25.2911 | -25.1357 | 94.2084 | -25.3443 | 94.4011 | 94.33 | 0.12153 | -25.2548 | -25.3569 | 94.4018 | 94.4233 | 94.5786 | 94.3465 | -25.4735 | 94.3701 | 94.4595 | 94.3574 | 94.3592 | -25.5059
4299 | 120.7626 | -113.887 | 6.3583 | 1.4211e-13 | 0.023305 | 0.015919 | 0.0094682 | -0.022935 | 0.0050659 | 0.24021 | 0.024171 | 0.035031 | -0.096424 | -0.0037841 | 0.00064308 | 0.074302 | 0.010564 | 0.009904 | 0.065863 | 0.087359 | 0.25185 | -0.063057 | 0.069728 | 0.018674 | -0.001407 | 0.034145 | 0.11901 | 0.021486 | -0.11836 | 113.824 | -6.2925 | 113.9613 | 113.8969 | 0.072961 | -6.271 | -6.1065 | 113.7687 | -6.3242 | 113.9568 | 113.8856 | 0.11695 | -6.2393 | -6.3369 | 113.9529 | 113.9744 | 114.1389 | 113.8976 | -6.4214 | 113.9212 | 114.006 | 113.9085 | 113.9057 | -6.4767
4300.7188 | 120.8038 | -109.8633 | 10.4965 | 1.4211e-13 | 0.023305 | 0.015919 | 0.010109 | -0.023576 | 0.0048523 | 0.22495 | 0.024385 | 0.034604 | -0.096424 | -0.0035705 | 0.00064308 | 0.065145 | 0.005985 | -0.003831 | 0.070441 | 0.091937 | 0.24727 | -0.063057 | 0.06515 | 0.014095 | -0.001407 | 0.034145 | 0.11444 | 0.007751 | -0.12752 | 109.8002 | -10.4261 | 109.9284 | 109.8594 | 0.059226 | -10.4046 | -10.2492 | 109.7358 | -10.4624 | 109.9284 | 109.8619 | 0.12611 | -10.3821 | -10.4888 | 109.9337 | 109.9552 | 110.1106 | 109.8693 | -10.5596 | 109.8974 | 109.9777 | 109.871 | 109.8774 | -10.624
4302.4531 | 116.7709 | -93.2281 | 23.5336 | 1.4211e-13 | 0.023305 | 0.015705 | 0.009041 | -0.022935 | 0.0044249 | 0.24021 | 0.024385 | 0.034604 | -0.096637 | -0.0033569 | 0.00064308 | 0.065145 | 0.010564 | 0.005325 | 0.061284 | 0.08278 | 0.24727 | -0.090531 | 0.06515 | 0.023253 | -0.010564 | 0.034145 | 0.11444 | 0.007751 | -0.12294 | 93.1376 | -23.4723 | 93.2933 | 93.2335 | 0.095856 | -23.4508 | -23.2864 | 93.1052 | -23.4995 | 93.2933 | 93.2176 | 0.11238 | -23.4192 | -23.5259 | 93.2894 | 93.3109 | 93.4754 | 93.2387 | -23.6242 | 93.2623 | 93.3426 | 93.2359 | 93.2514 | -23.6566
4304.1875 | 120.4788 | -94.6609 | 25.1541 | 1.4211e-13 | 0.023519 | 0.015919 | 0.0094682 | -0.023362 | 0.0046387 | 0.22495 | 0.024598 | 0.034818 | -0.096637 | -0.0035705 | 0.00064308 | 0.065145 | 0.015142 | -0.003831 | 0.052128 | 0.087359 | 0.23812 | -0.067636 | 0.055992 | 0.018674 | -0.010564 | 0.034145 | 0.11901 | 0.016908 | -0.11836 | 94.5933 | -25.102 | 94.7261 | 94.6571 | 0.063805 | -25.0668 | -24.916 | 94.5426 | -25.12 | 94.7169 | 94.6504 | 0.1078 | -25.0351 | -25.1372 | 94.7131 | 94.7483 | 94.8991 | 94.6761 | -25.2218 | 94.6951 | 94.78 | 94.6779 | 94.6796 | -25.2725
4305.9062 | 120.6162 | -94.4824 | 25.7767 | 1.4211e-13 | 0.023305 | 0.016346 | 0.009682 | -0.023362 | 0.0046387 | 0.22495 | 0.024171 | 0.035031 | -0.096851 | -0.0033569 | 0.00064308 | 0.065145 | 0.005985 | 0.005325 | 0.061284 | 0.091937 | 0.24269 | -0.058478 | 0.06515 | 0.014095 | -0.005985 | 0.034145 | 0.11444 | -0.001407 | -0.12294 | 94.4239 | -25.7154 | 94.5476 | 94.4877 | 0.063803 | -25.6847 | -25.534 | 94.3595 | -25.7425 | 94.5476 | 94.4764 | 0.11695 | -25.6622 | -25.7781 | 94.5437 | 94.5744 | 94.7251 | 94.4884 | -25.8352 | 94.5166 | 94.5969 | 94.481 | 94.4965 | -25.8996
4307.6406 | 120.8038 | -111.763 | 8.4961 | 1.4211e-13 | 0.023733 | 0.016133 | 0.0098956 | -0.023362 | 0.0046387 | 0.23258 | 0.023957 | 0.034818 | -0.096637 | -0.0033569 | 0.00042948 | 0.07888 | 0.005985 | 0.009904 | 0.065863 | 0.08278 | 0.25185 | -0.058478 | 0.069728 | 0.023253 | -0.010564 | 0.029566 | 0.10986 | 0.021486 | -0.11378 | 111.7045 | -8.4302 | 111.8419 | 111.7729 | 0.068382 | -8.4133 | -8.2442 | 111.6492 | -8.4665 | 111.8327 | 111.7524 | 0.10322 | -8.3862 | -8.4746 | 111.8289 | 111.8458 | 112.0149 | 111.769 | -8.5546 | 111.7926 | 111.8729 | 111.7845 | 111.7863 | -8.6099
4309.3906 | 120.8588 | -111.8454 | 8.551 | 1.4211e-13 | 0.023305 | 0.016133 | 0.009682 | -0.023362 | 0.0046387 | 0.24784 | 0.024171 | 0.034604 | -0.096424 | -0.0033569 | 0.00085668 | 0.074302 | 0.010564 | 0.000747 | 0.056706 | 0.087359 | 0.24269 | -0.058478 | 0.06515 | 0.018674 | -0.010564 | 0.034145 | 0.11444 | -0.010564 | -0.11836 | 111.7869 | -8.4943 | 111.9197 | 111.8461 | 0.059225 | -8.4637 | -8.3083 | 111.727 | -8.5169 | 111.9105 | 111.8348 | 0.1078 | -8.4366 | -8.5616 | 111.9021 | 111.9328 | 112.0881 | 111.856 | -8.6095 | 111.8795 | 111.9598 | 111.8348 | 111.8641 | -8.6694
4311.125 | 120.932 | -112.9257 | 7.4524 | 1.4211e-13 | 0.023519 | 0.016133 | 0.009682 | -0.023362 | 0.0044249 | 0.23258 | 0.024385 | 0.035031 | -0.096637 | -0.0035705 | 0.00085668 | 0.065145 | 0.015142 | 0.009904 | 0.065863 | 0.1011 | 0.25185 | -0.053899 | 0.069728 | 0.018674 | -0.001407 | 0.038723 | 0.11901 | 0.021486 | -0.11836 | 112.8718 | -7.3865 | 112.9909 | 112.9356 | 0.063803 | -7.3513 | -7.2005 | 112.8074 | -7.4137 | 112.9954 | 112.9243 | 0.11695 | -7.3334 | -7.4309 | 112.9916 | 113.0268 | 113.1776 | 112.9409 | -7.5063 | 112.9644 | 113.0447 | 112.9472 | 112.9444 | -7.5708
4312.8594 | 120.9274 | -113.7634 | 6.7062 | 1.4211e-13 | 0.023733 | 0.016346 | 0.0094682 | -0.023148 | 0.0048523 | 0.24021 | 0.024171 | 0.034604 | -0.096424 | -0.0035705 | 0.00042948 | 0.074302 | 0.015142 | 0.009904 | 0.061284 | 0.087359 | 0.24269 | -0.058478 | 0.074307 | 0.023253 | -0.001407 | 0.043302 | 0.11444 | 0.016908 | -0.12294 | 113.705 | -6.645 | 113.8377 | 113.7733 | 0.068382 | -6.6189 | -6.4635 | 113.6405 | -6.6629 | 113.8377 | 113.762 | 0.12153 | -6.5918 | -6.6893 | 113.8247 | 113.8508 | 114.0061 | 113.7786 | -6.7647 | 113.8067 | 113.8779 | 113.7803 | 113.7867 | -6.8292
4314.625 | 120.9778 | -114.2395 | 6.2622 | 1.4211e-13 | 0.023305 | 0.016346 | 0.0094682 | -0.022935 | 0.0048523 | 0.24784 | 0.024171 | 0.034818 | -0.096637 | -0.0037841 | 0.00064308 | 0.074302 | 0.005985 | 0.000747 | 0.07502 | 0.1011 | 0.24727 | -0.053899 | 0.069728 | 0.023253 | -0.005985 | 0.029566 | 0.12359 | 0.016908 | -0.12294 | 114.1856 | -6.1872 | 114.3138 | 114.2402 | 0.054646 | -6.1611 | -6.0149 | 114.1166 | -6.2326 | 114.3092 | 114.2335 | 0.11695 | -6.1386 | -6.2453 | 114.3145 | 114.3406 | 114.4868 | 114.2455 | -6.3161 | 114.2691 | 114.3631 | 114.2564 | 114.2628 | -6.3851
4316.3594 | 120.4056 | -117.4301 | 2.623 | 1.4211e-13 | 0.023305 | 0.016133 | 0.0094682 | -0.023148 | 0.0044249 | 0.24021 | 0.024385 | 0.034818 | -0.096637 | -0.0037841 | 0.00064308 | 0.074302 | 0.019721 | 0.014482 | 0.070441 | 0.096516 | 0.25185 | -0.058478 | 0.069728 | 0.023253 | -0.005985 | 0.038723 | 0.11444 | 0.016908 | -0.11378 | 117.3716 | -2.5525 | 117.5044 | 117.4446 | 0.07296 | -2.5265 | -2.3711 | 117.3163 | -2.5843 | 117.4998 | 117.4241 | 0.1078 | -2.5086 | -2.6061 | 117.5006 | 117.5266 | 117.682 | 117.4498 | -2.6815 | 117.4688 | 117.5446 | 117.447 | 117.4534 | -2.7368
4318.0938 | 120.9641 | -116.2903 | 4.2526 | 1.4211e-13 | 0.023519 | 0.015705 | 0.009682 | -0.023148 | 0.0050659 | 0.24784 | 0.024171 | 0.034818 | -0.096637 | -0.0035705 | 0.00064308 | 0.069723 | 0.015142 | 0.000747 | 0.065863 | 0.091937 | 0.24727 | -0.067636 | 0.06515 | 0.018674 | 0.003172 | 0.034145 | 0.11901 | 0.021486 | -0.11836 | 116.2226 | -4.1868 | 116.36 | 116.291 | 0.068383 | -4.1607 | -4.0054 | 116.1719 | -4.2185 | 116.3554 | 116.2935 | 0.12153 | -4.1336 | -4.2311 | 116.3561 | 116.3822 | 116.5376 | 116.3054 | -4.3203 | 116.3244 | 116.4093 | 116.3118 | 116.309 | -4.371
4319.8125 | 120.726 | -118.895 | 1.5793 | 1.4211e-13 | 0.023305 | 0.016346 | 0.0094682 | -0.023362 | 0.0048523 | 0.24784 | 0.024171 | 0.034818 | -0.09621 | -0.0035705 | 0.00042948 | 0.074302 | 0.019721 | 0.005325 | 0.070441 | 0.091937 | 0.24269 | -0.044742 | 0.078886 | 0.027831 | -0.001407 | 0.034145 | 0.10986 | 0.026065 | -0.12294 | 118.8502 | -1.5088 | 118.9693 | 118.9003 | 0.050067 | -1.4873 | -1.3366 | 118.772 | -1.5451 | 118.9738 | 118.8936 | 0.12153 | -1.4694 | -1.5532 | 118.9654 | 118.9869 | 119.1377 | 118.9147 | -1.624 | 118.9291 | 119.0048 | 118.921 | 118.9228 | -1.7022
4321.5312 | 120.6802 | -117.865 | 2.5955 | 1.4211e-13 | 0.023092 | 0.016133 | 0.0094682 | -0.023148 | 0.0046387 | 0.22495 | 0.024385 | 0.034604 | -0.096851 | -0.0035705 | 0.00064308 | 0.074302 | 0.0243 | 0.009904 | 0.065863 | 0.096516 | 0.24727 | -0.026426 | 0.074307 | 0.023253 | -0.001407 | 0.034145 | 0.11444 | 0.021486 | -0.11836 | 117.8386 | -2.5297 | 117.9393 | 117.8749 | 0.03633 | -2.499 | -2.3482 | 117.7466 | -2.5614 | 117.9393 | 117.8636 | 0.11695 | -2.4811 | -2.574 | 117.9309 | 117.9615 | 118.1123 | 117.8893 | -2.6219 | 117.8991 | 117.9794 | 117.8865 | 117.8882 | -2.7139
4323.25 | 120.7855 | -119.0277 | 1.4511 | 1.4211e-13 | 0.023092 | 0.016133 | 0.0094682 | -0.023148 | 0.0048523 | 0.24021 | 0.024171 | 0.035031 | -0.096424 | -0.0039979 | 0.00064308 | 0.074302 | 0.010564 | 0.009904 | 0.07502 | 0.091937 | 0.24269 | -0.067636 | 0.074307 | 0.027831 | -0.001407 | 0.038723 | 0.12359 | 0.026065 | -0.11378 | 118.9601 | -1.3761 | 119.102 | 119.0376 | 0.07754 | -1.3592 | -1.2084 | 118.9139 | -1.4124 | 119.102 | 119.0263 | 0.11237 | -1.3275 | -1.425 | 119.1027 | 119.1196 | 119.2704 | 119.0383 | -1.5187 | 119.0664 | 119.1513 | 119.0538 | 119.0555 | -1.5649
4325 | 120.8679 | -114.9811 | 5.5893 | 1.4211e-13 | 0.023519 | 0.015919 | 0.009682 | -0.022935 | 0.0046387 | 0.22495 | 0.023957 | 0.035031 | -0.096637 | -0.0033569 | 0.00085668 | 0.069723 | 0.010564 | 0.005325 | 0.056706 | 0.096516 | 0.24727 | -0.067636 | 0.069728 | 0.018674 | 0.003172 | 0.029566 | 0.10986 | 0.021486 | -0.11836 | 114.9134 | -5.5326 | 115.0508 | 114.9864 | 0.072961 | -5.4928 | -5.342 | 114.8627 | -5.5597 | 115.0508 | 114.9843 | 0.12153 | -5.4794 | -5.5678 | 115.0378 | 115.0776 | 115.2284 | 114.9916 | -5.6569 | 115.0106 | 115.0909 | 115.0026 | 114.9998 | -5.7077
4326.7344 | 120.0027 | -118.4509 | 1.3046 | 1.4211e-13 | 0.023305 | 0.015705 | 0.0092546 | -0.022935 | 0.0046387 | 0.24021 | 0.024385 | 0.034818 | -0.096637 | -0.0035705 | 0.00064308 | 0.065145 | 0.015142 | 0.005325 | 0.079598 | 0.091937 | 0.23812 | -0.067636 | 0.06515 | 0.027831 | -0.001407 | 0.038723 | 0.10986 | 0.026065 | -0.12294 | 118.3833 | -1.225 | 118.5161 | 118.4563 | 0.072961 | -1.2127 | -1.0665 | 118.328 | -1.2659 | 118.5161 | 118.4495 | 0.12153 | -1.1948 | -1.2786 | 118.5305 | 118.5429 | 118.689 | 118.4661 | -1.3723 | 118.4897 | 118.5608 | 118.477 | 118.4788 | -1.4276
4328.4531 | 120.0119 | -112.2437 | 7.1823 | 1.4211e-13 | 0.023519 | 0.015705 | 0.0094682 | -0.023148 | 0.0048523 | 0.24021 | 0.023957 | 0.034818 | -0.096424 | -0.0035705 | 0.00085668 | 0.065145 | 0.005985 | 0.000747 | 0.061284 | 0.091937 | 0.24269 | -0.044742 | 0.069728 | 0.023253 | -0.005985 | 0.034145 | 0.10986 | 0.012329 | -0.12294 | 112.1989 | -7.121 | 112.3088 | 112.2444 | 0.045489 | -7.0904 | -6.9396 | 112.1207 | -7.1482 | 112.3134 | 112.2377 | 0.11695 | -7.0725 | -7.17 | 112.3049 | 112.3356 | 112.4863 | 112.2496 | -7.2271 | 112.2778 | 112.3535 | 112.256 | 112.2669 | -7.3053
4330.1875 | 119.7464 | -114.1434 | 5.3192 | 1.4211e-13 | 0.023519 | 0.015919 | 0.0092546 | -0.023362 | 0.0044249 | 0.24784 | 0.023957 | 0.034604 | -0.096637 | -0.0039979 | 0.00042948 | 0.069723 | 0.010564 | 0.009904 | 0.065863 | 0.091937 | 0.23812 | -0.076794 | 0.069728 | 0.018674 | -0.001407 | 0.024988 | 0.11901 | 0.026065 | -0.11836 | 114.0666 | -5.2534 | 114.2131 | 114.1533 | 0.086698 | -5.2273 | -5.0811 | 114.025 | -5.2942 | 114.2131 | 114.142 | 0.11695 | -5.2002 | -5.2931 | 114.2092 | 114.2353 | 114.3815 | 114.1539 | -5.396 | 114.1684 | 114.2624 | 114.1694 | 114.162 | -5.4376
4331.9688 | 118.3594 | -65.7669 | 49.8688 | 1.4211e-13 | 0.023305 | 0.015919 | 0.009041 | -0.023362 | 0.0044249 | 0.24021 | 0.024171 | 0.035031 | -0.096424 | -0.0037841 | 0.00064308 | 0.074302 | 0.015142 | 0.000747 | 0.061284 | 0.091937 | 0.24727 | -0.063057 | 0.069728 | 0.018674 | 0.003172 | 0.034145 | 0.11444 | 0.021486 | -0.12294 | 65.7039 | -49.8075 | 65.8412 | 65.7677 | 0.063804 | -49.7768 | -49.6215 | 65.644 | -49.8346 | 65.8366 | 65.7701 | 0.12611 | -49.7543 | -49.8473 | 65.8282 | 65.8588 | 66.0142 | 65.782 | -49.9318 | 65.8011 | 65.8813 | 65.7884 | 65.7856 | -49.9917
4333.6875 | 118.2953 | -116.8625 | 2.4536 | 1.4211e-13 | 0.023305 | 0.015919 | 0.009682 | -0.023362 | 0.0046387 | 0.24021 | 0.024171 | 0.034604 | -0.096851 | -0.0035705 | 0.00064308 | 0.065145 | 0.015142 | 0.005325 | 0.065863 | 0.096516 | 0.24269 | -0.049321 | 0.069728 | 0.014095 | 0.003172 | 0.034145 | 0.11444 | 0.030644 | -0.12294 | 116.8132 | -2.3877 | 116.9276 | 116.8678 | 0.054646 | -2.3571 | -2.2109 | 116.7395 | -2.4195 | 116.9322 | 116.8657 | 0.12611 | -2.3392 | -2.423 | 116.9284 | 116.959 | 117.1052 | 116.8776 | -2.5029 | 116.8966 | 116.9769 | 116.8931 | 116.8766 | -2.5766
4335.4688 | 119.989 | -117.8833 | 1.7212 | 1.4211e-13 | 0.023946 | 0.015705 | 0.0098956 | -0.023362 | 0.0048523 | 0.23258 | 0.024385 | 0.035031 | -0.096851 | -0.0033569 | 0.00064308 | 0.074302 | 0.015142 | 0.009904 | 0.07502 | 0.091937 | 0.24269 | -0.058478 | 0.069728 | 0.023253 | 0.003172 | 0.038723 | 0.11444 | 0.021486 | -0.11378 | 117.8248 | -1.6462 | 117.9576 | 117.8932 | 0.068382 | -1.6293 | -1.4785 | 117.7695 | -1.6825 | 117.953 | 117.8865 | 0.11695 | -1.6068 | -1.6997 | 117.9583 | 117.9752 | 118.126 | 117.8984 | -1.7797 | 117.922 | 117.9977 | 117.9048 | 117.9066 | -1.835
4337.1875 | 116.4688 | -86.5997 | 29.393 | 1.4211e-13 | 0.023733 | 0.016133 | 0.0094682 | -0.023362 | 0.0048523 | 0.23258 | 0.024171 | 0.034818 | -0.09621 | -0.0035705 | 0.00021588 | 0.069723 | 0.019721 | 0.005325 | 0.070441 | 0.1011 | 0.24727 | -0.081373 | 0.074307 | 0.023253 | 0.003172 | 0.034145 | 0.11901 | 0.026065 | -0.1092 | 86.5184 | -29.3226 | 86.6695 | 86.6051 | 0.086698 | -29.2919 | -29.1457 | 86.4905 | -29.3589 | 86.674 | 86.6029 | 0.11237 | -29.274 | -29.3669 | 86.6702 | 86.7008 | 86.847 | 86.6195 | -29.4744 | 86.6339 | 86.7187 | 86.6258 | 86.623 | -29.5022
4338.9688 | 119.6182 | -118.8171 | 0.60883 | 1.4211e-13 | 0.023733 | 0.015705 | 0.009682 | -0.023362 | 0.0046387 | 0.23258 | 0.024171 | 0.034818 | -0.096637 | -0.0033569 | 0.00085668 | 0.074302 | 0.010564 | 0.005325 | 0.07502 | 0.1011 | 0.24727 | -0.049321 | 0.06515 | 0.023253 | 0.003172 | 0.034145 | 0.11444 | 0.016908 | -0.12294 | 118.7678 | -0.53381 | 118.8914 | 118.8225 | 0.054646 | -0.50773 | -0.36155 | 118.6942 | -0.57468 | 118.8823 | 118.8203 | 0.12611 | -0.49439 | -0.59192 | 118.8922 | 118.9182 | 119.0644 | 118.8277 | -0.65815 | 118.8513 | 118.9316 | 118.834 | 118.8404 | -0.73176
4340.7031 | 120.1218 | -119.577 | 0.21515 | 1.4211e-13 | 0.023733 | 0.015919 | 0.009682 | -0.023148 | 0.0048523 | 0.24021 | 0.024171 | 0.034604 | -0.096851 | -0.0037841 | 0.00064308 | 0.074302 | 0.015142 | 0.009904 | 0.065863 | 0.091937 | 0.24727 | -0.044742 | 0.069728 | 0.018674 | 0.003172 | 0.043302 | 0.11901 | 0.021486 | -0.11836 | 119.5323 | -0.14929 | 119.6513 | 119.5869 | 0.054646 | -0.12321 | 0.032125 | 119.4587 | -0.17185 | 119.6468 | 119.5802 | 0.12153 | -0.096135 | -0.19366 | 119.6429 | 119.669 | 119.8243 | 119.5922 | -0.25989 | 119.6203 | 119.696 | 119.5985 | 119.5957 | -0.33351
4342.4531 | 120.2408 | -119.696 | 0.21515 | 1.4211e-13 | 0.023305 | 0.015705 | 0.0094682 | -0.023362 | 0.0050659 | 0.24021 | 0.024171 | 0.034604 | -0.096851 | -0.0037841 | 0.00085668 | 0.069723 | 0.010564 | 0.005325 | 0.065863 | 0.096516 | 0.24727 | -0.058478 | 0.06515 | 0.027831 | 0.003172 | 0.034145 | 0.12359 | 0.030644 | -0.11836 | 119.6376 | -0.14929 | 119.7658 | 119.7014 | 0.063803 | -0.11863 | 0.032125 | 119.5777 | -0.181 | 119.7612 | 119.6992 | 0.12153 | -0.091556 | -0.18451 | 119.7619 | 119.7926 | 119.9433 | 119.7066 | -0.27363 | 119.7302 | 119.8196 | 119.7267 | 119.7239 | -0.33351
4344.3438 | 120.3873 | -119.8471 | 0.21973 | 1.4211e-13 | 0.023519 | 0.015919 | 0.009682 | -0.023148 | 0.0048523 | 0.22495 | 0.024385 | 0.035031 | -0.096637 | -0.0037841 | 0.00021588 | 0.074302 | 0.015142 | 0.005325 | 0.07502 | 0.091937 | 0.24269 | -0.049321 | 0.069728 | 0.023253 | 0.003172 | 0.043302 | 0.11901 | 0.030644 | -0.11378 | 119.7978 | -0.14471 | 119.9214 | 119.8524 | 0.054646 | -0.12779 | 0.022968 | 119.7333 | -0.17642 | 119.9168 | 119.8503 | 0.11695 | -0.10071 | -0.18908 | 119.9221 | 119.939 | 120.0898 | 119.8622 | -0.26905 | 119.8904 | 119.9661 | 119.8778 | 119.8704 | -0.33351
4346.1562 | 119.989 | -119.4534 | 0.25177 | 1.4211e-13 | 0.023305 | 0.015919 | 0.009682 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.035245 | -0.096637 | -0.0035705 | 0.00064308 | 0.069723 | 0.015142 | 0.014482 | 0.065863 | 0.1011 | 0.24727 | -0.067636 | 0.069728 | 0.023253 | 0.003172 | 0.038723 | 0.11901 | 0.021486 | -0.11836 | 119.3858 | -0.18591 | 119.5232 | 119.4679 | 0.082118 | -0.15068 | -0.004496 | 119.3351 | -0.21305 | 119.5232 | 119.4566 | 0.12153 | -0.13276 | -0.23028 | 119.5193 | 119.5545 | 119.7007 | 119.4686 | -0.31941 | 119.4922 | 119.5724 | 119.4749 | 119.4767 | -0.37013
4347.9688 | 120.3644 | -119.8151 | 0.1831 | 1.4211e-13 | 0.023305 | 0.016133 | 0.0094682 | -0.023148 | 0.0050659 | 0.24021 | 0.024385 | 0.034818 | -0.096424 | -0.0037841 | 0.00085668 | 0.069723 | 0.019721 | 0.000747 | 0.065863 | 0.096516 | 0.25185 | -0.026426 | 0.074307 | 0.027831 | 0.003172 | 0.038723 | 0.10986 | 0.021486 | -0.1092 | 119.7886 | -0.11724 | 119.8848 | 119.8158 | 0.027173 | -0.086589 | 0.068747 | 119.7059 | -0.14438 | 119.8894 | 119.8182 | 0.11237 | -0.073248 | -0.16162 | 119.8809 | 119.9116 | 120.0669 | 119.8348 | -0.20953 | 119.8538 | 119.9249 | 119.8365 | 119.8429 | -0.29231
4349.7812 | 120.4468 | -119.8746 | 0.20599 | 1.4211e-13 | 0.023305 | 0.015919 | 0.009682 | -0.023148 | 0.0048523 | 0.23258 | 0.024385 | 0.034818 | -0.096637 | -0.0037841 | 0.00085668 | 0.07888 | 0.015142 | 0.014482 | 0.070441 | 0.096516 | 0.25185 | -0.044742 | 0.078886 | 0.018674 | 0.003172 | 0.038723 | 0.11444 | 0.012329 | -0.11378 | 119.8298 | -0.13555 | 119.9535 | 119.8891 | 0.059224 | -0.10948 | 0.045858 | 119.7608 | -0.16727 | 119.9535 | 119.8777 | 0.11695 | -0.091558 | -0.19367 | 119.945 | 119.9711 | 120.1264 | 119.8897 | -0.25074 | 119.9133 | 119.989 | 119.8869 | 119.8932 | -0.31978
4351.6094 | 120.3735 | -119.9936 | 0.31586 | 1.4211e-13 | 0.023519 | 0.016133 | 0.009682 | -0.023148 | 0.0050659 | 0.23258 | 0.024171 | 0.034818 | -0.09621 | -0.0035705 | 0.00042948 | 0.074302 | 0.015142 | 0.014482 | 0.07502 | 0.096516 | 0.24727 | -0.044742 | 0.06515 | 0.014095 | -0.001407 | 0.034145 | 0.11444 | 0.012329 | -0.11378 | 119.9488 | -0.24084 | 120.0679 | 120.0081 | 0.059224 | -0.21934 | -0.068583 | 119.8798 | -0.28171 | 120.0587 | 119.9922 | 0.11237 | -0.20142 | -0.30353 | 120.0686 | 120.0901 | 120.2409 | 120.0087 | -0.3606 | 120.0277 | 120.108 | 120.0059 | 120.0077 | -0.42964
4353.4219 | 120.3918 | -119.9753 | 0.37079 | 1.4211e-13 | 0.023519 | 0.015705 | 0.0094682 | -0.023362 | 0.0048523 | 0.23258 | 0.024385 | 0.034818 | -0.096851 | -0.0035705 | 0.00042948 | 0.074302 | 0.015142 | 0.009904 | 0.07502 | 0.096516 | 0.25185 | -0.063057 | 0.069728 | 0.03241 | 0.007751 | 0.038723 | 0.11901 | 0.016908 | -0.11378 | 119.9122 | -0.29577 | 120.0496 | 119.9852 | 0.072961 | -0.27427 | -0.11894 | 119.8615 | -0.33207 | 120.045 | 119.983 | 0.12153 | -0.25177 | -0.35388 | 120.0503 | 120.0718 | 120.2271 | 119.9904 | -0.43385 | 120.014 | 120.0943 | 119.9922 | 120.0077 | -0.48457
4355.1562 | 120.4834 | -120.0897 | 0.25177 | 1.4211e-13 | 0.023305 | 0.016346 | 0.0094682 | -0.023362 | 0.0048523 | 0.22495 | 0.024385 | 0.035031 | -0.096424 | -0.0035705 | 0.00042948 | 0.069723 | 0.010564 | 0.005325 | 0.065863 | 0.091937 | 0.24727 | -0.049321 | 0.069728 | 0.03241 | -0.001407 | 0.038723 | 0.12359 | 0.021486 | -0.11378 | 120.0404 | -0.18591 | 120.1594 | 120.095 | 0.054646 | -0.15983 | -0.004496 | 119.9759 | -0.21305 | 120.1594 | 120.0883 | 0.11237 | -0.12818 | -0.23028 | 120.1556 | 120.1817 | 120.337 | 120.1003 | -0.30109 | 120.1284 | 120.2133 | 120.1112 | 120.1221 | -0.36555
4356.9531 | 120.5521 | -120.0623 | 0.26093 | 1.4211e-13 | 0.023305 | 0.016133 | 0.009682 | -0.022935 | 0.0050659 | 0.22495 | 0.023957 | 0.034818 | -0.096637 | -0.0033569 | 0.00042948 | 0.065145 | 0.010564 | 0.009904 | 0.070441 | 0.1011 | 0.25185 | -0.021847 | 0.069728 | 0.018674 | 0.003172 | 0.043302 | 0.11901 | 0.016908 | -0.11836 | 120.0404 | -0.19048 | 120.1274 | 120.0722 | 0.031751 | -0.15983 | -0.009073 | 119.9439 | -0.21762 | 120.132 | 120.0654 | 0.12153 | -0.14191 | -0.24402 | 120.1327 | 120.1634 | 120.3141 | 120.0728 | -0.28277 | 120.1056 | 120.1813 | 120.0792 | 120.0809 | -0.37929
4358.75 | 120.2682 | -119.783 | 0.24261 | 1.4211e-13 | 0.023519 | 0.015919 | 0.0098956 | -0.023576 | 0.0046387 | 0.24021 | 0.024171 | 0.034818 | -0.096424 | -0.0033569 | 0.00064308 | 0.069723 | 0.015142 | 0.005325 | 0.065863 | 0.1011 | 0.24269 | -0.040163 | 0.074307 | 0.023253 | -0.001407 | 0.038723 | 0.11901 | 0.016908 | -0.12294 | 119.7429 | -0.17675 | 119.8527 | 119.7883 | 0.045488 | -0.14152 | 8e-05 | 119.6601 | -0.20389 | 119.8573 | 119.7816 | 0.12153 | -0.1236 | -0.22571 | 119.8489 | 119.8841 | 120.0257 | 119.7982 | -0.28278 | 119.8217 | 119.902 | 119.7999 | 119.8063 | -0.36555
4360.5781 | 120.4376 | -120.0668 | 0.27466 | 1.4211e-13 | 0.023305 | 0.015919 | 0.0098956 | -0.023148 | 0.0048523 | 0.24021 | 0.024171 | 0.034818 | -0.096851 | -0.0037841 | 0.00064308 | 0.074302 | 0.019721 | 0.005325 | 0.070441 | 0.096516 | 0.24727 | -0.053899 | 0.074307 | 0.018674 | -0.005985 | 0.038723 | 0.12359 | 0.021486 | -0.11378 | 120.0129 | -0.20422 | 120.1411 | 120.0722 | 0.059224 | -0.17814 | -0.027384 | 119.9531 | -0.23594 | 120.1411 | 120.0608 | 0.1078 | -0.15107 | -0.25317 | 120.1373 | 120.1633 | 120.3141 | 120.0866 | -0.32856 | 120.1056 | 120.1904 | 120.0883 | 120.0855 | -0.38844
4362.375 | 120.575 | -120.1218 | 0.23804 | 1.4211e-13 | 0.023519 | 0.016133 | 0.0094682 | -0.023362 | 0.0048523 | 0.23258 | 0.024171 | 0.035031 | -0.096637 | -0.0035705 | 0.00064308 | 0.069723 | 0.015142 | 0.005325 | 0.065863 | 0.091937 | 0.25185 | -0.049321 | 0.078886 | 0.023253 | 0.003172 | 0.029566 | 0.12359 | 0.016908 | -0.1092 | 120.0724 | -0.17217 | 120.1915 | 120.1271 | 0.054646 | -0.1461 | 0.013815 | 120.0126 | -0.20847 | 120.2007 | 120.1249 | 0.11237 | -0.11444 | -0.22113 | 120.1876 | 120.2137 | 120.3736 | 120.1369 | -0.28736 | 120.1513 | 120.2454 | 120.1387 | 120.145 | -0.34724
4364.1719 | 120.4926 | -120.2042 | 0.27466 | 1.4211e-13 | 0.023519 | 0.015919 | 0.0094682 | -0.023362 | 0.0048523 | 0.24021 | 0.024171 | 0.034818 | -0.096637 | -0.0035705 | 0.00064308 | 0.074302 | 0.019721 | 0.005325 | 0.070441 | 0.091937 | 0.24727 | -0.049321 | 0.060571 | 0.023253 | 0.003172 | 0.038723 | 0.11444 | 0.021486 | -0.11378 | 120.1548 | -0.20422 | 120.2785 | 120.2095 | 0.054646 | -0.18272 | -0.027384 | 120.0904 | -0.23594 | 120.2647 | 120.2073 | 0.11695 | -0.16022 | -0.25317 | 120.2746 | 120.2961 | 120.4514 | 120.2239 | -0.32398 | 120.2429 | 120.3186 | 120.2256 | 120.2274 | -0.38844
4365.9219 | 120.5658 | -120.1904 | 0.24261 | 1.4211e-13 | 0.023519 | 0.015919 | 0.0094682 | -0.023362 | 0.0050659 | 0.22495 | 0.024171 | 0.034604 | -0.096637 | -0.0033569 | 0.00064308 | 0.074302 | 0.0243 | 0.014482 | 0.065863 | 0.096516 | 0.24727 | -0.031005 | 0.074307 | 0.027831 | -0.001407 | 0.043302 | 0.11444 | 0.012329 | -0.12752 | 120.1594 | -0.17675 | 120.2647 | 120.2049 | 0.045487 | -0.1461 | 0.004659 | 120.0629 | -0.19931 | 120.2647 | 120.189 | 0.12611 | -0.12818 | -0.23029 | 120.2563 | 120.2869 | 120.4377 | 120.2147 | -0.27362 | 120.2337 | 120.3049 | 120.2028 | 120.2183 | -0.37013
4367.7188 | 120.5933 | -120.2179 | 0.27008 | 1.4211e-13 | 0.023519 | 0.015705 | 0.0092546 | -0.023362 | 0.0048523 | 0.23258 | 0.024598 | 0.034604 | -0.096637 | -0.0037841 | 0.00085668 | 0.074302 | 0.015142 | 0.009904 | 0.065863 | 0.096516 | 0.24269 | -0.063057 | 0.069728 | 0.023253 | -0.001407 | 0.034145 | 0.12359 | 0.021486 | -0.1092 | 120.1548 | -0.20422 | 120.2922 | 120.2278 | 0.072961 | -0.17357 | -0.027386 | 120.1087 | -0.23594 | 120.2876 | 120.2165 | 0.1078 | -0.14649 | -0.2486 | 120.2838 | 120.3144 | 120.4606 | 120.233 | -0.33314 | 120.252 | 120.3415 | 120.2394 | 120.2411 | -0.37928
4369.5156 | 120.5429 | -120.2591 | 0.28839 | 1.4211e-13 | 0.023519 | 0.015919 | 0.0098956 | -0.023362 | 0.0048523 | 0.24784 | 0.024385 | 0.034818 | -0.096637 | -0.0035705 | 0.00064308 | 0.065145 | 0.019721 | 0.009904 | 0.065863 | 0.091937 | 0.25185 | -0.026426 | 0.074307 | 0.027831 | -0.001407 | 0.038723 | 0.11444 | 0.016908 | -0.12752 | 120.2327 | -0.22253 | 120.3242 | 120.269 | 0.03633 | -0.19645 | -0.036539 | 120.1316 | -0.24967 | 120.3334 | 120.2577 | 0.12611 | -0.17396 | -0.27148 | 120.325 | 120.351 | 120.5109 | 120.2788 | -0.31482 | 120.2978 | 120.3735 | 120.276 | 120.2869 | -0.41591
4371.2656 | 120.5704 | -120.3094 | 0.25635 | 1.4211e-13 | 0.023092 | 0.015705 | 0.0092546 | -0.023576 | 0.0048523 | 0.23258 | 0.023744 | 0.034818 | -0.096637 | -0.0035705 | 0.00042948 | 0.07888 | 0.015142 | 0.005325 | 0.065863 | 0.096516 | 0.25185 | -0.031005 | 0.06515 | 0.027831 | -0.001407 | 0.043302 | 0.11901 | 0.012329 | -0.11378 | 120.2784 | -0.19049 | 120.3883 | 120.3148 | 0.03633 | -0.15983 | -0.004496 | 120.1957 | -0.21305 | 120.3746 | 120.308 | 0.11237 | -0.13733 | -0.24402 | 120.3753 | 120.406 | 120.5613 | 120.3246 | -0.28735 | 120.3528 | 120.4285 | 120.3218 | 120.3373 | -0.37013
4373.0625 | 120.6436 | -120.2866 | 0.26093 | 1.4211e-13 | 0.023305 | 0.015705 | 0.009682 | -0.023362 | 0.0048523 | 0.21732 | 0.024385 | 0.034604 | -0.096424 | -0.0039979 | 0.00042948 | 0.074302 | 0.019721 | 0.009904 | 0.065863 | 0.091937 | 0.25185 | -0.044742 | 0.069728 | 0.023253 | -0.001407 | 0.038723 | 0.11901 | 0.026065 | -0.12294 | 120.2418 | -0.19506 | 120.3609 | 120.2965 | 0.054646 | -0.16899 | -0.009073 | 120.1636 | -0.2222 | 120.3563 | 120.2852 | 0.12153 | -0.14191 | -0.23486 | 120.3524 | 120.3785 | 120.5384 | 120.3063 | -0.30567 | 120.3253 | 120.4056 | 120.3126 | 120.3098 | -0.38386
4374.7969 | 120.607 | -120.3232 | 0.2655 | 1.4211e-13 | 0.023519 | 0.015705 | 0.009682 | -0.023148 | 0.0046387 | 0.22495 | 0.024171 | 0.03439 | -0.096424 | -0.0037841 | 0.00064308 | 0.069723 | 0.015142 | 0.005325 | 0.065863 | 0.091937 | 0.25185 | -0.040163 | 0.074307 | 0.023253 | -0.001407 | 0.034145 | 0.11901 | 0.021486 | -0.11378 | 120.283 | -0.19964 | 120.3929 | 120.3285 | 0.045488 | -0.17357 | -0.013651 | 120.2094 | -0.23136 | 120.3975 | 120.3218 | 0.11237 | -0.14649 | -0.24402 | 120.389 | 120.4151 | 120.575 | 120.3383 | -0.30567 | 120.3573 | 120.4422 | 120.3447 | 120.3464 | -0.37928
4376.5938 | 120.7489 | -120.3369 | 0.25177 | 1.4211e-13 | 0.023305 | 0.015919 | 0.009682 | -0.023362 | 0.0046387 | 0.22495 | 0.024385 | 0.035031 | -0.096637 | -0.0035705 | 0.00064308 | 0.069723 | 0.019721 | 0.005325 | 0.065863 | 0.091937 | 0.25643 | -0.035584 | 0.078886 | 0.018674 | 0.003172 | 0.034145 | 0.11444 | 0.021486 | -0.12294 | 120.3013 | -0.18591 | 120.4066 | 120.3422 | 0.040909 | -0.15983 | 0.004661 | 120.214 | -0.21762 | 120.4158 | 120.3401 | 0.12611 | -0.13733 | -0.23028 | 120.4028 | 120.4289 | 120.5933 | 120.3566 | -0.28735 | 120.3711 | 120.4513 | 120.3584 | 120.3556 | -0.37471
4378.3906 | 120.6573 | -120.3781 | 0.27008 | 1.4211e-13 | 0.023519 | 0.016133 | 0.0094682 | -0.023362 | 0.0046387 | 0.24021 | 0.023957 | 0.034604 | -0.096424 | -0.0037841 | 0.00042948 | 0.07888 | 0.015142 | 0.014482 | 0.065863 | 0.096516 | 0.24727 | -0.012689 | 0.078886 | 0.023253 | -0.005985 | 0.034145 | 0.11444 | -0.010564 | -0.12294 | 120.3654 | -0.20422 | 120.457 | 120.3926 | 0.027171 | -0.17357 | -0.022807 | 120.2552 | -0.23594 | 120.457 | 120.3721 | 0.11695 | -0.15565 | -0.28065 | 120.444 | 120.4746 | 120.6254 | 120.3933 | -0.28277 | 120.4123 | 120.4925 | 120.3675 | 120.4014 | -0.39302
4380.2188 | 120.7169 | -120.3644 | 0.23804 | 1.4211e-13 | 0.023092 | 0.015705 | 0.009682 | -0.023362 | 0.0048523 | 0.24021 | 0.024598 | 0.035031 | -0.096424 | -0.0037841 | 0.00064308 | 0.074302 | 0.015142 | 0.014482 | 0.070441 | 0.1011 | 0.25185 | -0.049321 | 0.078886 | 0.023253 | -0.001407 | 0.038723 | 0.12817 | -0.001407 | -0.11378 | 120.3151 | -0.1676 | 120.4387 | 120.3789 | 0.063803 | -0.13694 | 0.013815 | 120.2506 | -0.19931 | 120.4433 | 120.363 | 0.11237 | -0.10986 | -0.23944 | 120.4348 | 120.4655 | 120.6162 | 120.3795 | -0.28736 | 120.4031 | 120.4926 | 120.363 | 120.3876 | -0.35182

## Thermal Data
Fire Time | B Position - Tray - Middle | B Position - Conduit - 3' | B Position - Conduit - Middle | B Position - Conduit - 7' | D Position - 3' | D Position - Middle | D Position - 7'
-0.9646 | 6.7734 | 6.6106 | 6.7024 | 6.6163 | 6.6406 | 6.8873 | 6.9225
0.0354 | 6.7705 | 6.6132 | 6.7065 | 6.617 | 6.6387 | 6.8852 | 6.9306
1.0354 | 6.776 | 6.6125 | 6.7187 | 6.6172 | 6.6379 | 6.8832 | 6.9253
2.0354 | 6.7807 | 6.6153 | 6.7122 | 6.6164 | 6.6441 | 6.9001 | 6.9315
3.0354 | 6.7901 | 6.6149 | 6.7146 | 6.6242 | 6.6506 | 6.8945 | 6.9297
4.0354 | 6.7955 | 6.6141 | 6.7155 | 6.6214 | 6.6617 | 6.9011 | 6.9327
5.0354 | 6.7789 | 6.6175 | 6.7159 | 6.6151 | 6.6592 | 6.906 | 6.9225
6.0354 | 6.7853 | 6.6194 | 6.7137 | 6.6278 | 6.6616 | 6.9052 | 6.9407
7.0354 | 6.8108 | 6.6234 | 6.7179 | 6.6353 | 6.6622 | 6.9248 | 6.9446
8.0354 | 7.0075 | 6.6307 | 6.928 | 6.668 | 6.6896 | 7.2115 | 6.9584
9.0354 | 7.329 | 6.6411 | 7.1972 | 6.8052 | 6.8573 | 7.6941 | 7.5834
10.0354 | 8.0886 | 6.892 | 7.2569 | 6.8966 | 7.7673 | 8.5786 | 8.7952
11.0354 | 10.1484 | 6.8515 | 7.5328 | 6.9671 | 8.6993 | 10.3667 | 10.4745
12.0354 | 12.2551 | 6.8238 | 7.4262 | 7.1107 | 10.7566 | 13.223 | 12.185
13.0354 | 14.4135 | 6.8062 | 7.6616 | 7.3149 | 13.0535 | 16.4711 | 13.8645
14.0354 | 17.2405 | 6.8714 | 7.9566 | 7.5401 | 15.6463 | 20.9416 | 17.2234
15.0354 | 20.7646 | 6.9193 | 8.1931 | 7.6368 | 17.6273 | 25.7265 | 19.5288
16.0354 | 25.5875 | 6.9491 | 8.1911 | 7.7444 | 20.8978 | 30.6265 | 21.9667
17.0354 | 28.5832 | 7.0523 | 8.3494 | 7.74 | 23.7355 | 34.3161 | 23.7792
18.0354 | 33.6705 | 7.094 | 8.6253 | 7.967 | 26.3768 | 37.9511 | 27.2212
19.0354 | 37.3049 | 7.1538 | 8.8749 | 8.0491 | 29.9889 | 43.0952 | 31.0688
20.0354 | 40.5163 | 7.3008 | 9.1489 | 8.589 | 33.3845 | 49.7825 | 34.1204
21.0354 | 42.7969 | 7.2911 | 9.2259 | 8.4896 | 37.6394 | 55.2711 | 37.6197
22.0354 | 45.1197 | 7.5154 | 10.1147 | 8.5551 | 39.668 | 56.6639 | 40.8542
23.0354 | 49.0544 | 7.4145 | 10.4701 | 8.8179 | 41.6608 | 59.7382 | 43.7539
24.0354 | 52.941 | 7.5714 | 10.4166 | 8.7574 | 45.1685 | 66.1676 | 48.6474
25.0354 | 55.7159 | 7.5919 | 10.5123 | 9.0086 | 48.8339 | 68.6845 | 53.0789
26.0354 | 57.9326 | 7.7776 | 10.6032 | 9.0587 | 52.4955 | 72.3989 | 56.1847
27.0354 | 59.8348 | 7.8462 | 11.2183 | 9.0069 | 55.6501 | 76.4267 | 59.3524
28.0354 | 62.5858 | 7.8494 | 11.0847 | 9.2534 | 57.132 | 80.9033 | 61.4627
29.0354 | 65.0332 | 7.9377 | 11.5388 | 9.4792 | 59.1813 | 84.1895 | 63.7638
30.0354 | 67.9443 | 8.0546 | 11.7526 | 9.7219 | 61.8994 | 87.3122 | 66.494
31.0354 | 70.2127 | 8.0804 | 12.059 | 9.7773 | 64.1896 | 89.3774 | 69.5733
32.0354 | 71.5543 | 8.2228 | 12.1895 | 9.9393 | 66.8049 | 91.7391 | 72.1596
33.0354 | 74.4736 | 8.3108 | 12.6182 | 10.0075 | 68.5093 | 94.4608 | 74.8498
34.0354 | 77.1899 | 8.4782 | 13.0681 | 10.3965 | 69.0819 | 97.8568 | 78.5564
35.0354 | 79.9674 | 8.5596 | 13.0252 | 10.1837 | 71.5216 | 101.7058 | 81.6432
36.0354 | 81.8209 | 8.8212 | 13.3025 | 10.5409 | 72.786 | 104.8127 | 83.9866
37.0354 | 84.2056 | 8.8071 | 13.4677 | 10.6292 | 74.15 | 108.1631 | 86.6115
38.0354 | 86.6215 | 9.0518 | 13.6223 | 10.5425 | 75.5625 | 115.0107 | 90.5184
39.0354 | 88.6851 | 9.1525 | 14.0642 | 10.7497 | 76.937 | 119.5597 | 92.835
40.0354 | 91.1794 | 9.156 | 14.1041 | 10.8538 | 77.9703 | 124.2813 | 95.6698
41.0354 | 91.9549 | 9.2348 | 14.0196 | 10.8874 | 79.204 | 127.241 | 98.3208
42.0354 | 92.7585 | 9.2377 | 14.2973 | 10.943 | 79.9542 | 129.7016 | 99.2463
43.0354 | 92.7789 | 9.2933 | 14.5305 | 11.1111 | 81.0335 | 132.1673 | 99.8557
44.0354 | 93.3356 | 9.473 | 14.6432 | 11.2599 | 82.5745 | 135.0679 | 101.0471
45.0354 | 94.6667 | 9.5044 | 15.0357 | 11.4604 | 83.5097 | 137.4888 | 102.1073
46.0354 | 96.4374 | 9.5951 | 15.171 | 11.4942 | 83.8989 | 139.1049 | 103.529
47.0354 | 97.7139 | 9.9003 | 15.3009 | 11.522 | 85.675 | 140.6698 | 105.9531
48.0354 | 98.6874 | 10.116 | 15.8749 | 11.6786 | 87.2573 | 142.1176 | 106.8191
49.0354 | 100.2736 | 10.2263 | 16.0343 | 12.3632 | 88.2669 | 143.2206 | 107.5446
50.0354 | 103.2493 | 10.1314 | 16.0759 | 12.2371 | 90.0882 | 145.5203 | 108.2561
51.0354 | 104.918 | 10.0892 | 16.6625 | 12.4002 | 92.3929 | 147.2506 | 109.0673
52.0354 | 106.5822 | 10.2687 | 16.7268 | 12.5745 | 94.984 | 148.4193 | 110.7018
53.0354 | 109.4081 | 10.3751 | 17.2088 | 12.835 | 96.7564 | 149.2397 | 111.8971
54.0354 | 111.3457 | 10.5073 | 17.3533 | 12.8977 | 99.1983 | 150.1836 | 113.2497
55.0354 | 112.6403 | 10.5495 | 17.254 | 12.877 | 103.0808 | 152.3962 | 114.1984
56.0354 | 114.3119 | 10.5454 | 17.4218 | 13.34 | 103.91 | 153.281 | 114.7736
57.0354 | 115.9559 | 11.0245 | 17.8999 | 13.4284 | 106.1408 | 154.5556 | 115.5808
58.0354 | 117.2895 | 11.0467 | 17.9912 | 13.711 | 107.9727 | 155.0706 | 116.2853
59.0354 | 117.9481 | 11.166 | 18.0394 | 13.7598 | 109.8962 | 155.1095 | 117.1107
60.0354 | 118.0875 | 11.242 | 18.2654 | 13.9974 | 111.6456 | 155.6642 | 117.7899
61.0354 | 119.4958 | 11.2918 | 18.5713 | 14.1961 | 112.773 | 155.3412 | 118.7349
62.0354 | 120.2122 | 11.3095 | 18.8349 | 14.6099 | 113.8198 | 155.1456 | 119.352
63.0354 | 121.2887 | 11.4695 | 19.0653 | 15.0434 | 116.1148 | 156.0492 | 120.0664
64.0354 | 121.3671 | 11.6181 | 19.3839 | 15.2478 | 116.923 | 156.3055 | 120.3129
65.0354 | 122.2595 | 11.8677 | 19.8527 | 15.4297 | 118.7625 | 156.4227 | 121.564
66.0354 | 121.5709 | 11.9132 | 20.5351 | 15.6749 | 118.8118 | 155.1654 | 121.5178
67.0354 | 122.3243 | 12.077 | 21.254 | 15.7896 | 118.1134 | 154.031 | 121.4551
68.0354 | 121.5343 | 11.9144 | 21.2596 | 15.868 | 118.2802 | 153.0397 | 121.3322
69.0354 | 122.3719 | 11.9957 | 23.2236 | 15.8772 | 118.0166 | 152.8527 | 121.8865
70.0354 | 122.4425 | 11.9034 | 22.3662 | 16.2096 | 118.6526 | 152.5555 | 122.5459
71.0354 | 122.8717 | 11.9934 | 22.5935 | 16.3251 | 118.8767 | 151.508 | 122.2704
72.0354 | 124.2104 | 12.1847 | 23.5572 | 16.5421 | 119.959 | 151.7918 | 122.9499
73.0354 | 125.0872 | 12.5014 | 24.6362 | 16.7772 | 120.7999 | 152.5694 | 123.8428
74.0354 | 125.4959 | 12.4608 | 24.8452 | 16.9798 | 121.7127 | 151.7278 | 123.9243
75.0354 | 125.2955 | 12.4444 | 24.8618 | 17.1483 | 121.5756 | 152.0565 | 124.6186
76.0354 | 125.2278 | 12.6165 | 26.7895 | 17.3372 | 121.6919 | 150.8031 | 124.8104
77.0354 | 126.025 | 12.5048 | 26.3722 | 17.5334 | 121.0974 | 150.4274 | 125.0473
78.0354 | 126.4602 | 12.6477 | 26.7024 | 17.6716 | 121.8482 | 149.7226 | 125.1214
79.0354 | 126.5932 | 12.8929 | 27.0705 | 17.951 | 121.7992 | 149.6002 | 125.6948
80.0354 | 126.8967 | 13.2715 | 28.0184 | 17.929 | 121.4769 | 148.5581 | 125.669
81.0354 | 127.1173 | 13.6128 | 29.0428 | 18.1419 | 121.7229 | 148.3424 | 125.7402
82.0354 | 127.4914 | 13.6895 | 29.3088 | 18.2226 | 122.2324 | 148.1598 | 126.4242
83.0354 | 127.7114 | 13.6929 | 29.9378 | 18.4314 | 121.5856 | 147.3278 | 126.2036
84.0354 | 128.5854 | 13.8429 | 30.1854 | 18.5873 | 121.1197 | 146.3124 | 125.8741
85.0354 | 128.3453 | 14.041 | 31.4962 | 18.8062 | 121.0334 | 146.2005 | 126.2947
86.0354 | 127.7018 | 14.0344 | 31.8261 | 19.0427 | 121.0986 | 145.0417 | 126.1607
87.0354 | 127.6376 | 14.095 | 32.7002 | 18.9591 | 120.5365 | 144.5322 | 126.266
88.0354 | 127.5525 | 14.1499 | 33.022 | 19.158 | 120.4979 | 143.9743 | 125.9722
89.0354 | 128.2823 | 14.4249 | 32.9403 | 19.1903 | 120.2015 | 142.8059 | 125.5985
90.0354 | 128.1746 | 14.494 | 33.0635 | 19.3478 | 119.7275 | 142.8005 | 125.8265
91.0354 | 128.4146 | 14.729 | 34.3698 | 19.5454 | 119.1505 | 142.3252 | 125.8776
92.0354 | 128.133 | 14.8386 | 34.6163 | 19.8137 | 119.1358 | 141.6487 | 125.9798
93.0354 | 128.4526 | 14.8636 | 35.1937 | 20.0805 | 118.9928 | 140.8524 | 125.9574
94.0354 | 128.6716 | 15.336 | 35.2514 | 20.0522 | 119.3597 | 140.9177 | 126.6253
95.0354 | 129.4647 | 15.4841 | 36.3374 | 20.1974 | 120.3073 | 141.7089 | 127.9551
96.0354 | 130.8156 | 15.5897 | 36.6534 | 20.7095 | 121.3989 | 142.2943 | 128.8064
97.0354 | 131.7787 | 15.6075 | 37.5292 | 20.6155 | 121.6569 | 142.6566 | 129.3784
98.0354 | 131.9391 | 15.3257 | 38.9587 | 20.645 | 121.3906 | 142.1619 | 129.4735
99.0354 | 132.3881 | 15.4746 | 38.1271 | 20.7815 | 121.2136 | 141.5926 | 129.5976
100.0354 | 132.5319 | 15.6821 | 39.1491 | 20.9152 | 121.1587 | 141.6146 | 130.5706
101.0354 | 132.5168 | 15.7077 | 39.7072 | 21.0621 | 121.3776 | 141.7564 | 131.1033
102.0354 | 132.9534 | 16.0642 | 39.8761 | 21.1541 | 122.6043 | 143.1658 | 132.0495
103.0354 | 133.5924 | 16.0864 | 42.1231 | 21.5154 | 123.244 | 144.0078 | 133.1281
104.0354 | 133.0255 | 16.2353 | 42.6789 | 21.7912 | 123.4901 | 144.5693 | 134.3391
105.0354 | 134.6953 | 16.4293 | 42.1027 | 21.9496 | 124.6001 | 145.4526 | 134.9397
106.0354 | 135.3356 | 16.8433 | 43.1948 | 22.0176 | 125.374 | 146.4598 | 135.9752
107.0354 | 136.0847 | 16.8898 | 43.7472 | 22.1571 | 125.9384 | 148.0295 | 136.9262
108.0354 | 136.9107 | 16.7739 | 43.7358 | 22.279 | 126.6679 | 149.2235 | 138.378
109.0354 | 137.3476 | 16.939 | 44.7698 | 22.1165 | 126.7537 | 150.0611 | 139.6296
110.0354 | 137.0366 | 17.0885 | 44.8753 | 22.2934 | 126.4464 | 150.307 | 140.0874
111.0354 | 136.957 | 17.2894 | 45.5161 | 22.6115 | 127.4611 | 151.1274 | 140.9334
112.0354 | 137.0814 | 17.3335 | 46.0047 | 22.7027 | 127.7731 | 151.6648 | 142.1332
113.0354 | 137.5971 | 17.5286 | 46.1392 | 22.7961 | 128.3702 | 152.5512 | 143.8544
114.0354 | 138.1856 | 17.7279 | 47.8128 | 23.1071 | 130.3483 | 154.7512 | 145.2339
115.0354 | 138.953 | 17.9564 | 47.4536 | 23.2324 | 131.3761 | 155.6034 | 146.1584
116.0354 | 139.1293 | 17.8052 | 48.2069 | 23.2489 | 132.3285 | 156.8147 | 147.1132
117.0354 | 140.2405 | 17.7902 | 48.3266 | 23.7377 | 133.0043 | 157.2093 | 148.1837
118.0354 | 141.5838 | 17.8389 | 48.9895 | 23.7859 | 134.8416 | 157.5577 | 149.1548
119.0354 | 141.6456 | 18.1234 | 50.079 | 23.8529 | 136.8956 | 159.6625 | 150.9335
120.0354 | 142.512 | 18.1018 | 49.9805 | 23.9054 | 138.34 | 161.9577 | 153.6491
121.0354 | 143.4841 | 18.2549 | 50.2764 | 23.8755 | 139.7477 | 163.314 | 155.9977
122.0354 | 144.35 | 18.4509 | 51.4138 | 24.1631 | 140.1515 | 165.1343 | 157.6187
123.0354 | 146.0058 | 18.6684 | 52.0135 | 24.3657 | 140.6838 | 166.3326 | 158.6602
124.0354 | 148.3684 | 18.7555 | 53.197 | 24.5157 | 140.7592 | 168.1703 | 160.9483
125.0354 | 150.3369 | 18.9256 | 53.4033 | 24.9167 | 141.1284 | 169.4103 | 161.6821
126.0354 | 151.1865 | 19.067 | 53.5231 | 25.2671 | 140.7707 | 170.184 | 162.2349
127.0354 | 150.9043 | 19.1047 | 53.9902 | 25.37 | 142.5953 | 170.8134 | 162.168
128.0354 | 151.1593 | 19.4731 | 54.2247 | 25.5187 | 141.9947 | 170.0774 | 161.9378
129.0354 | 151.3744 | 19.4233 | 54.442 | 25.4678 | 143.2442 | 171.2145 | 163.0423
130.0354 | 152.3614 | 19.5155 | 54.7209 | 25.4713 | 143.3987 | 173.5689 | 163.9196
131.0354 | 152.8367 | 19.6098 | 55.0805 | 25.6828 | 144.4052 | 174.525 | 164.0421
132.0354 | 154.0151 | 19.6516 | 56.2904 | 26.0914 | 145.1447 | 175.6234 | 165.4852
133.0354 | 153.9634 | 19.6985 | 56.0645 | 26.305 | 146.2599 | 177.4566 | 167.2562
134.0354 | 154.3374 | 20.0596 | 56.5523 | 26.3896 | 146.4459 | 177.5959 | 167.9878
135.0354 | 154.2308 | 20.2535 | 57.9726 | 26.4169 | 146.4309 | 177.7202 | 168.4335
136.0354 | 153.3901 | 20.3267 | 58.9341 | 26.733 | 145.4599 | 175.8987 | 168.1782
137.0354 | 151.8027 | 20.4365 | 59.7024 | 26.9115 | 144.1124 | 175.1189 | 167.1453
138.0354 | 151.5362 | 20.492 | 59.563 | 26.9726 | 144.7489 | 175.3204 | 168.073
139.0354 | 151.9509 | 20.5978 | 59.5595 | 27.1424 | 145.4561 | 177.9898 | 169.6111
140.0354 | 152.1692 | 20.933 | 60.4614 | 27.3678 | 146.208 | 178.6218 | 169.2084
141.0354 | 152.5187 | 21.004 | 60.7276 | 27.6044 | 147.256 | 179.5595 | 169.6753
142.0354 | 153.2248 | 21.1282 | 61.3578 | 27.6209 | 147.7632 | 180.2167 | 169.92
143.0354 | 152.7185 | 21.1163 | 61.4455 | 27.6731 | 147.7082 | 181.1713 | 171.5309
144.0354 | 152.562 | 21.3613 | 62.5118 | 27.9083 | 147.1667 | 182.2883 | 172.9241
145.0354 | 153.0074 | 21.5668 | 62.7833 | 27.9708 | 147.7442 | 184.1316 | 174.6967
146.0354 | 153.1102 | 21.6757 | 63.2387 | 28.1717 | 148.1677 | 185.246 | 175.7451
147.0354 | 153.5617 | 21.7283 | 64.0233 | 28.4527 | 148.9586 | 184.3199 | 175.8264
148.0354 | 153.611 | 21.7734 | 64.3257 | 28.5944 | 147.6743 | 183.6959 | 175.273
149.0354 | 152.8661 | 22.0475 | 65.7403 | 28.6832 | 148.3936 | 183.3361 | 174.1013
150.0354 | 152.4414 | 22.5846 | 66.646 | 28.9513 | 148.6178 | 182.3068 | 173.2482
151.0354 | 152.1324 | 22.4884 | 66.3982 | 29.3581 | 148.0704 | 181.368 | 171.8656
152.0354 | 152.2222 | 22.5196 | 66.7826 | 29.6134 | 147.7076 | 180.5677 | 171.0848
153.0354 | 152.0067 | 22.6377 | 67.1231 | 29.4559 | 147.568 | 180.741 | 170.2975
154.0354 | 151.0222 | 22.7503 | 67.8653 | 29.5702 | 149.1838 | 180.9584 | 170.2062
155.0354 | 150.9752 | 22.7719 | 68.1788 | 29.6508 | 150.3254 | 181.6668 | 170.7433
156.0354 | 151.1529 | 23.1018 | 68.8884 | 29.7404 | 151.2087 | 181.8096 | 170.7144
157.0354 | 150.0594 | 23.5897 | 68.7303 | 29.8099 | 150.5062 | 181.0779 | 170.6637
158.0354 | 149.8785 | 23.5766 | 69.2646 | 29.9877 | 150.0638 | 180.584 | 171.3723
159.0354 | 149.6418 | 23.6312 | 69.7948 | 30.2414 | 149.1538 | 179.5617 | 171.7342
160.0354 | 150.0195 | 23.9712 | 70.9121 | 30.3939 | 148.7632 | 180.1021 | 171.9968
161.0354 | 150.3218 | 24.3145 | 71.9162 | 30.6337 | 147.7114 | 180.7389 | 172.1669
162.0354 | 149.9934 | 24.5067 | 71.9912 | 30.8707 | 146.9688 | 180.7956 | 172.187
163.0354 | 150.9 | 24.416 | 74.3328 | 31.0714 | 146.8617 | 180.5175 | 171.869
164.0354 | 150.8482 | 24.5317 | 74.2839 | 31.1848 | 147.4479 | 180.6759 | 171.6257
165.0354 | 150.9028 | 24.6993 | 73.8411 | 31.3122 | 147.9612 | 180.7256 | 172.1033
166.0354 | 150.4698 | 24.8597 | 74.1083 | 31.4167 | 148.3741 | 181.0608 | 172.7418
167.0354 | 150.2661 | 24.8945 | 74.9266 | 31.5363 | 148.2329 | 180.4741 | 172.5025
168.0354 | 150.0426 | 25.4061 | 76.3467 | 31.8142 | 148.6334 | 182.0649 | 173.178
169.0354 | 150.0853 | 25.4472 | 76.3846 | 31.9724 | 148.2656 | 181.1758 | 172.3715
170.0354 | 149.8879 | 25.7509 | 76.8017 | 32.1347 | 147.4242 | 180.731 | 172.893
171.0354 | 150.2713 | 25.8805 | 77.0038 | 32.4994 | 147.7251 | 179.9355 | 172.5287
172.0354 | 150.5817 | 25.8011 | 79.0234 | 32.5054 | 147.702 | 179.4745 | 172.0017
173.0354 | 150.7014 | 25.9094 | 79.5961 | 32.607 | 147.2906 | 179.41 | 172.0873
174.0354 | 150.7183 | 26.2467 | 80.3204 | 32.7457 | 147.1801 | 178.1071 | 171.7067
175.0354 | 151.4262 | 26.5113 | 80.6312 | 32.8456 | 147.1949 | 178.1801 | 172.3837
176.0354 | 151.6138 | 26.4266 | 80.4998 | 32.8765 | 147.9436 | 178.5538 | 172.9522
177.0354 | 151.4855 | 26.9697 | 80.3563 | 33.0254 | 147.9001 | 178.4911 | 172.809
178.0354 | 151.4828 | 26.9659 | 82.0799 | 33.0625 | 147.7023 | 179.5492 | 172.9308
179.0354 | 151.7318 | 26.8751 | 83.0233 | 33.2286 | 147.7173 | 179.324 | 173.7214
180.0354 | 151.6482 | 27.0385 | 82.7293 | 33.3865 | 148.4509 | 180.8268 | 174.8089
181.0354 | 151.6935 | 27.1687 | 83.2201 | 33.3807 | 148.4173 | 180.0956 | 175.2919
182.0354 | 151.9266 | 27.3665 | 84.2347 | 33.5162 | 148.0889 | 180.5984 | 176.0135
183.0354 | 152.0191 | 27.4653 | 84.2856 | 33.6337 | 148.5507 | 181.1499 | 176.6512
184.0354 | 153.0268 | 27.6384 | 85.5315 | 33.9694 | 149.1011 | 180.623 | 177.5645
185.0354 | 153.4589 | 27.8983 | 86.682 | 34.0191 | 148.5028 | 179.8312 | 177.2432
186.0354 | 153.7193 | 28.1607 | 86.5351 | 34.2468 | 148.3925 | 179.7369 | 177.3417
187.0354 | 153.8216 | 28.3776 | 86.2701 | 34.2754 | 148.6122 | 179.2724 | 176.8806
188.0354 | 153.3694 | 28.4073 | 87.5901 | 34.4739 | 149.3615 | 179.0178 | 176.3571
189.0354 | 153.1687 | 28.4779 | 87.3541 | 34.5113 | 149.2885 | 179.0161 | 176.4286
190.0354 | 153.5319 | 28.5957 | 88.0212 | 34.624 | 149.9471 | 180.2343 | 176.5375
191.0354 | 153.1306 | 28.5955 | 89.823 | 34.853 | 149.6117 | 181.4184 | 178.4429
192.0354 | 153.4193 | 28.7817 | 89.5874 | 34.9376 | 149.4117 | 179.9228 | 177.147
193.0354 | 153.184 | 28.9547 | 89.2595 | 35.0417 | 148.7137 | 179.4137 | 176.726
194.0354 | 152.5264 | 29.0701 | 91.9378 | 35.2827 | 149.7542 | 179.673 | 176.7867
195.0354 | 152.1526 | 29.3565 | 92.1762 | 35.4028 | 149.4974 | 178.6923 | 176.4206
196.0354 | 152.0147 | 29.2494 | 92.8804 | 35.5149 | 149.3494 | 178.423 | 176.2627
197.0354 | 152.2934 | 29.2896 | 93.1724 | 35.615 | 150.455 | 178.5345 | 176.2443
198.0354 | 152.8083 | 29.44 | 93.9825 | 35.7913 | 151.0169 | 178.8094 | 176.1673
199.0354 | 153.4277 | 29.8277 | 94.3362 | 35.973 | 150.7553 | 179.2901 | 175.8514
200.0354 | 154.1579 | 30.0587 | 95.0036 | 35.9664 | 151.9015 | 179.348 | 176.5497
201.0354 | 154.3447 | 30.1371 | 94.3944 | 36.0794 | 151.435 | 179.5827 | 175.8545
202.0354 | 154.252 | 30.2401 | 95.2611 | 36.3164 | 152.289 | 180.0971 | 177.0776
203.0354 | 154.0478 | 30.4643 | 96.6686 | 36.4049 | 153.4834 | 179.7227 | 177.8448
204.0354 | 154.2875 | 30.7671 | 97.4292 | 36.6998 | 153.6061 | 179.7973 | 178.1331
205.0354 | 154.1721 | 30.5922 | 98.1099 | 36.793 | 152.3516 | 177.9739 | 177.2675
206.0354 | 153.7408 | 30.7272 | 98.6718 | 36.9051 | 151.5161 | 177.8137 | 177.1763
207.0354 | 154.0455 | 30.8927 | 99.3595 | 37.0903 | 152.2213 | 177.6873 | 177.1261
208.0354 | 153.5062 | 31.0835 | 99.6596 | 37.1983 | 152.2344 | 176.9046 | 176.0263
209.0354 | 153.5481 | 31.3679 | 99.6577 | 37.2207 | 151.9362 | 176.6401 | 175.1707
210.0354 | 153.4909 | 31.3871 | 100.4033 | 37.4276 | 151.9618 | 176.73 | 175.1124
211.0354 | 153.1359 | 31.4476 | 101.5141 | 37.4904 | 152.3939 | 176.8816 | 175.6226
212.0354 | 153.7068 | 31.612 | 102.8803 | 37.8005 | 153.7778 | 177.621 | 176.1757
213.0354 | 154.6536 | 31.5939 | 102.6062 | 38.3973 | 154.8256 | 177.8279 | 176.707
214.0354 | 154.2519 | 31.8124 | 104.3248 | 38.0587 | 154.5764 | 177.2572 | 176.0882
215.0354 | 154.1807 | 32.0916 | 104.9047 | 38.2757 | 154.4035 | 177.6854 | 176.1562
216.0354 | 154.4373 | 32.1903 | 104.6367 | 38.317 | 154.7132 | 177.824 | 176.5151
217.0354 | 154.9797 | 32.4268 | 105.2658 | 38.4777 | 156.0709 | 178.835 | 177.6184
218.0354 | 155.3171 | 32.5346 | 105.7656 | 38.6242 | 156.8658 | 180.2224 | 178.3372
219.0354 | 155.659 | 32.5443 | 107.4873 | 38.8249 | 157.2629 | 180.3915 | 178.8971
220.0354 | 156.2857 | 32.686 | 107.8321 | 38.9903 | 155.9247 | 180.7706 | 178.9486
221.0354 | 156.3783 | 32.7137 | 108.2598 | 39.1116 | 156.1331 | 179.9573 | 179.2762
222.0354 | 156.494 | 32.7604 | 109.7413 | 39.1187 | 156.6581 | 180.6566 | 179.5691
223.0354 | 156.6034 | 32.9095 | 110.3561 | 39.3255 | 156.4778 | 181.6169 | 180.0264
224.0354 | 156.3334 | 33.149 | 110.2448 | 39.4623 | 156.5841 | 181.9643 | 180.0405
225.0354 | 156.6599 | 33.3269 | 111.0686 | 39.5371 | 156.6267 | 180.6508 | 178.8367
226.0354 | 155.779 | 33.5089 | 111.1819 | 39.5972 | 156.5931 | 180.42 | 178.1919
227.0354 | 156.4672 | 33.5494 | 111.1983 | 39.7675 | 158.3498 | 181.0118 | 178.8652
228.0354 | 157.0612 | 33.8684 | 111.9043 | 39.8874 | 159.1784 | 182.0571 | 178.6733
229.0354 | 157.8798 | 33.858 | 112.4158 | 40.047 | 161.1986 | 182.951 | 180.1533
230.0354 | 158.9599 | 33.8834 | 113.6021 | 40.4583 | 161.0116 | 183.2999 | 179.9066
231.0354 | 160.0426 | 34.0382 | 114.4578 | 40.4456 | 160.8297 | 182.9128 | 180.345
232.0354 | 161.0248 | 34.3306 | 115.1163 | 40.5287 | 161.6795 | 183.751 | 180.9648
233.0354 | 161.0669 | 34.4403 | 115.4892 | 40.66 | 161.0426 | 183.5296 | 181.14
234.0354 | 161.2443 | 34.6164 | 115.4074 | 40.8215 | 160.3133 | 183.6619 | 180.6331
235.0354 | 161.2909 | 34.5682 | 116.9096 | 40.9476 | 160.4709 | 183.9351 | 180.8927
236.0354 | 161.9515 | 34.7189 | 118.695 | 41.1267 | 160.521 | 183.9551 | 180.6701
237.0354 | 162.6952 | 35.0202 | 118.266 | 41.3223 | 160.8499 | 184.0123 | 180.5834
238.0354 | 162.4755 | 35.1237 | 119.3864 | 41.5319 | 160.7991 | 183.9038 | 181.6991
239.0354 | 161.8343 | 35.5537 | 119.8044 | 41.6704 | 159.6189 | 184.2171 | 180.925
240.0354 | 161.3829 | 35.5707 | 120.5953 | 41.8428 | 160.4193 | 184.4751 | 181.1734
241.0354 | 161.3284 | 35.72 | 119.7149 | 41.9973 | 160.9236 | 185.0237 | 181.9314
242.0354 | 160.5583 | 35.6956 | 119.9223 | 42.1209 | 161.8229 | 185.1109 | 182.6701
243.0354 | 160.8916 | 35.7615 | 120.3198 | 42.51 | 162.6029 | 185.5333 | 182.246
244.0354 | 161.3026 | 35.7529 | 121.8437 | 42.6824 | 163.555 | 185.9125 | 182.6759
245.0354 | 161.6973 | 35.8527 | 123.159 | 42.8371 | 165.4331 | 187.4437 | 183.3995
246.0354 | 160.835 | 35.9773 | 123.1456 | 42.7325 | 164.3764 | 186.4938 | 183.0887
247.0354 | 161.2685 | 36.1068 | 123.9101 | 42.9017 | 164.8947 | 186.5087 | 183.35
248.0354 | 161.274 | 36.1201 | 124.8258 | 43.0977 | 164.8412 | 187.3429 | 183.5391
249.0354 | 161.3113 | 36.3387 | 125.4032 | 43.4453 | 165.058 | 187.5845 | 183.0689
250.0354 | 160.9992 | 36.571 | 125.8447 | 43.5653 | 165.7491 | 187.6756 | 183.8387
251.0354 | 160.6418 | 36.7758 | 125.5915 | 43.6923 | 165.5536 | 186.6008 | 184.03
252.0354 | 161.1683 | 36.8143 | 126.6903 | 43.7867 | 164.8457 | 187.2913 | 184.8065
253.0354 | 162.2511 | 36.9512 | 128.1634 | 43.9872 | 164.4735 | 187.9388 | 185.4044
254.0354 | 161.9453 | 36.9328 | 128.0961 | 43.985 | 163.2326 | 187.5576 | 185.0763
255.0354 | 161.5526 | 37.1905 | 129.4526 | 44.224 | 162.9356 | 187.6909 | 184.5855
256.0354 | 162.2816 | 37.3884 | 129.1927 | 44.6002 | 164.6966 | 189.1432 | 185.5754
257.0354 | 161.8594 | 37.5202 | 131.0591 | 44.5614 | 165.3317 | 188.7785 | 186.1756
258.0354 | 162.1903 | 37.545 | 131.7789 | 44.8671 | 164.5963 | 189.1491 | 186.442
259.0354 | 163.1696 | 37.7415 | 132.9053 | 45.0091 | 163.636 | 189.7703 | 187.6959
260.0354 | 163.6561 | 37.7835 | 131.7986 | 45.0163 | 163.2825 | 190.731 | 187.4861
261.0354 | 163.931 | 37.8643 | 133.7756 | 45.4233 | 162.5636 | 190.4627 | 186.7909
262.0354 | 163.4857 | 38.1804 | 132.9348 | 45.4823 | 162.3911 | 189.6224 | 186.7161
263.0354 | 162.9622 | 38.7192 | 133.0692 | 45.7356 | 161.8353 | 188.3238 | 185.6415
264.0354 | 162.8852 | 38.5662 | 134.5563 | 45.8107 | 162.5228 | 188.6936 | 186.2614
265.0354 | 163.6962 | 38.4584 | 135.5313 | 45.9619 | 163.7512 | 189.9454 | 187.7127
266.0354 | 163.9416 | 38.5427 | 135.8659 | 46.1227 | 164.3471 | 190.7233 | 187.1872
267.0354 | 165.213 | 38.6651 | 136.7533 | 46.2907 | 164.4456 | 191.9308 | 187.3963
268.0354 | 165.7094 | 38.6666 | 138.1551 | 46.5029 | 165.8023 | 192.3567 | 188.3498
269.0354 | 165.8157 | 38.8353 | 138.1055 | 46.5966 | 164.6409 | 191.9804 | 188.3535
270.0354 | 165.1819 | 38.9558 | 138.3968 | 46.7027 | 165.2922 | 191.1746 | 187.9336
271.0354 | 164.7118 | 39.1648 | 138.647 | 46.8331 | 164.6663 | 190.836 | 187.2489
272.0354 | 163.6395 | 39.4308 | 139.5736 | 46.9483 | 163.4228 | 189.7085 | 186.1582
273.0354 | 163.231 | 39.7596 | 140.2578 | 47.2007 | 162.7537 | 189.3791 | 185.3687
274.0354 | 162.6337 | 39.9925 | 140.2885 | 47.3343 | 163.0372 | 188.9228 | 184.5052
275.0354 | 161.8747 | 40.1216 | 140.4462 | 47.3734 | 162.5218 | 188.005 | 183.9321
276.0354 | 161.7796 | 40.2621 | 141.2174 | 47.5396 | 163.2003 | 189.2542 | 183.5828
277.0354 | 162.1743 | 40.2107 | 142.615 | 47.6553 | 162.654 | 188.8652 | 183.2674
278.0354 | 162.1832 | 40.3207 | 142.8535 | 47.9883 | 161.8174 | 187.3372 | 182.5613
279.0354 | 162.6598 | 40.4333 | 142.8107 | 48.1235 | 162.0746 | 187.5979 | 182.8896
280.0354 | 163.5608 | 40.6183 | 144.1556 | 48.3324 | 162.4805 | 189.1299 | 183.4673
281.0354 | 163.9445 | 40.746 | 145.5285 | 48.5521 | 162.3571 | 188.5689 | 184.3254
282.0354 | 164.6087 | 40.7835 | 146.3017 | 48.8432 | 161.4942 | 188.6558 | 183.9726
283.0354 | 165.3659 | 40.7102 | 145.4922 | 48.8847 | 162.7858 | 189.4903 | 184.6214
284.0354 | 165.7386 | 40.6845 | 146.0916 | 49.0075 | 162.1571 | 188.2876 | 184.991
285.0354 | 165.4072 | 40.8058 | 147.8897 | 49.0989 | 162.17 | 188.5374 | 185.4903
286.0354 | 165.3974 | 41.1497 | 149.5971 | 49.2952 | 161.8146 | 187.482 | 186.2105
287.0354 | 164.7653 | 41.2587 | 149.3306 | 49.4822 | 161.1093 | 186.9408 | 186.4085
288.0354 | 164.4419 | 41.4502 | 149.7432 | 49.664 | 160.5989 | 186.535 | 186.32
289.0354 | 164.0444 | 41.682 | 149.4191 | 49.9858 | 160.3689 | 186.0938 | 186.517
290.0354 | 163.7367 | 41.6741 | 150.3188 | 49.9076 | 161.925 | 188.4745 | 188.0874
291.0354 | 163.5148 | 41.6759 | 150.0127 | 50.1489 | 163.4738 | 189.5094 | 188.6429
292.0354 | 163.0906 | 41.863 | 150.4523 | 50.1768 | 163.8879 | 189.7013 | 188.9872
293.0354 | 162.9834 | 42.1336 | 151.5639 | 50.7039 | 164.2294 | 188.611 | 188.9871
294.0354 | 162.6166 | 42.4687 | 152.2282 | 50.7761 | 163.058 | 187.871 | 189.2514
295.0354 | 163.1079 | 42.6177 | 152.1964 | 50.8193 | 162.9365 | 187.6905 | 189.2213
296.0354 | 163.1939 | 42.7056 | 153.368 | 50.974 | 162.7354 | 187.9783 | 189.0494
297.0354 | 163.7854 | 42.8632 | 154.5424 | 51.1889 | 161.9611 | 187.8857 | 188.5547
298.0354 | 163.6857 | 43.0885 | 155.1058 | 51.3924 | 161.8899 | 188.0676 | 189.3007
299.0354 | 163.5489 | 43.1322 | 156.0438 | 51.5878 | 161.554 | 187.146 | 189.048
300.0354 | 165.1537 | 43.2027 | 157.3753 | 52.0345 | 160.6572 | 185.4494 | 188.7893
301.0354 | 164.8443 | 43.3105 | 158.738 | 51.9791 | 160.36 | 186.3014 | 188.9736
302.0354 | 164.1712 | 43.5111 | 157.7959 | 52.07 | 160.6603 | 186.4331 | 189.6575
303.0354 | 164.0366 | 44.009 | 157.1891 | 52.285 | 160.445 | 185.6586 | 189.0946
304.0354 | 163.4614 | 44.1651 | 157.8413 | 52.4913 | 160.449 | 185.2058 | 188.9597
305.0354 | 163.1898 | 44.0785 | 158.2914 | 52.6516 | 159.8314 | 184.0685 | 188.4861
306.0354 | 161.9596 | 44.2383 | 158.5645 | 52.8015 | 159.2149 | 184.1345 | 188.2454
307.0354 | 161.7533 | 44.6104 | 160.8288 | 52.8462 | 159.3561 | 184.1181 | 189.1388
308.0354 | 162.2915 | 44.5823 | 161.2294 | 53.13 | 159.5099 | 184.3502 | 188.75
309.0354 | 162.2514 | 44.7543 | 162.6805 | 53.2613 | 159.0496 | 184.8237 | 188.7541
310.0354 | 162.5583 | 44.8861 | 161.6747 | 53.3313 | 158.8589 | 185.6308 | 189.0286
311.0354 | 161.9857 | 45.0278 | 163.1485 | 53.3998 | 158.6118 | 184.4245 | 188.799
312.0354 | 161.8034 | 45.1575 | 163.9036 | 53.5316 | 157.6943 | 184.1176 | 188.6208
313.0354 | 161.4339 | 45.3628 | 163.8161 | 53.9816 | 157.0416 | 183.8067 | 188.1416
314.0354 | 161.791 | 45.6368 | 164.8996 | 53.902 | 157.1381 | 183.6152 | 188.1191
315.0354 | 161.4425 | 45.6361 | 164.7537 | 54.2253 | 157.2326 | 183.2558 | 188.2498
316.0354 | 160.5418 | 45.9086 | 164.4132 | 54.2748 | 156.7942 | 183.3603 | 187.9653
317.0354 | 160.9222 | 46.1884 | 165.7446 | 54.5553 | 156.3918 | 182.7541 | 187.2724
318.0354 | 161.2181 | 46.5215 | 166.1235 | 54.6917 | 156.4176 | 182.2177 | 188.0219
319.0354 | 160.7368 | 46.4922 | 167.3763 | 54.8288 | 156.3748 | 182.371 | 187.9625
320.0354 | 160.2419 | 46.5189 | 168.8763 | 54.8759 | 155.8253 | 182.398 | 187.7923
321.0354 | 159.9219 | 46.6958 | 169.0478 | 55.033 | 155.2747 | 183.3997 | 188.0058
322.0354 | 160.583 | 46.7396 | 171.2228 | 55.1937 | 154.8715 | 182.7596 | 188.0025
323.0354 | 162.2261 | 46.7426 | 170.9144 | 55.3847 | 154.8704 | 182.2618 | 187.4646
324.0354 | 162.1182 | 46.9053 | 171.4178 | 55.2958 | 154.6206 | 183.5865 | 187.3937
325.0354 | 161.9982 | 47.0055 | 171.8327 | 55.4978 | 155.273 | 182.6963 | 187.0612
326.0354 | 161.6481 | 47.5232 | 171.6763 | 55.6104 | 155.2119 | 183.1286 | 187.0406
327.0354 | 161.0854 | 47.6217 | 173.8092 | 55.7536 | 155.3416 | 182.5751 | 186.2672
328.0354 | 160.7741 | 47.7995 | 174.2789 | 55.7817 | 155.2649 | 182.5297 | 185.8695
329.0354 | 161.6382 | 47.7397 | 174.255 | 55.9669 | 154.7005 | 182.3088 | 185.7597
330.0354 | 161.3127 | 47.8048 | 173.6125 | 56.1992 | 154.748 | 181.7586 | 184.7944
331.0354 | 160.3414 | 47.7805 | 174.0716 | 56.2069 | 155.114 | 181.0595 | 184.1132
332.0354 | 160.4868 | 47.9725 | 174.3427 | 56.5394 | 155.6884 | 181.9697 | 183.8701
333.0354 | 160.7786 | 48.3986 | 174.4322 | 56.6476 | 156.365 | 181.9536 | 184.0803
334.0354 | 161.063 | 48.5967 | 174.8153 | 56.7966 | 156.681 | 183.728 | 184.4526
335.0354 | 161.4582 | 48.6226 | 176.0759 | 56.794 | 157.4408 | 184.9493 | 184.4963
336.0354 | 161.358 | 48.7345 | 176.0578 | 56.948 | 157.8608 | 185.9048 | 184.4779
337.0354 | 162.828 | 48.677 | 176.7548 | 57.2311 | 159.9269 | 187.7109 | 184.4982
338.0354 | 163.2891 | 48.7187 | 176.3067 | 57.3845 | 162.2393 | 189.7468 | 186.2411
339.0354 | 163.2927 | 48.8997 | 177.2803 | 57.4345 | 164.9634 | 190.8446 | 187.7956
340.0354 | 163.9498 | 49.0177 | 178.4868 | 57.8107 | 164.8574 | 192.1209 | 188.0949
341.0354 | 165.0037 | 49.5016 | 178.196 | 58.1657 | 164.9358 | 191.6837 | 188.3817
342.0354 | 166.4089 | 49.6229 | 179.0835 | 58.0669 | 165.6994 | 191.8483 | 188.2675
343.0354 | 166.6322 | 49.7948 | 181.0006 | 58.1235 | 165.7668 | 191.4346 | 188.2002
344.0354 | 167.3607 | 49.8748 | 182.6109 | 58.306 | 165.2641 | 190.6656 | 187.7083
345.0354 | 167.5365 | 49.9216 | 182.3213 | 58.5371 | 165.8995 | 191.1287 | 188.1053
346.0354 | 167.4095 | 50.0123 | 183.1316 | 58.6212 | 166.2562 | 191.33 | 188.256
347.0354 | 167.3812 | 50.2005 | 183.7094 | 58.852 | 166.5667 | 192.4554 | 189.3752
348.0354 | 167.5948 | 50.3407 | 184.2759 | 58.9711 | 166.8178 | 193.0134 | 189.8958
349.0354 | 168.8603 | 50.3106 | 185.929 | 59.167 | 166.4357 | 193.6056 | 190.0974
350.0354 | 168.567 | 50.4663 | 185.4827 | 59.2289 | 165.3149 | 192.7572 | 189.5452
351.0354 | 169.4047 | 50.5177 | 186.1784 | 59.7294 | 165.2841 | 192.7972 | 189.5462
352.0354 | 169.5432 | 50.6477 | 187.8917 | 59.9681 | 166.9141 | 193.4906 | 191.1215
353.0354 | 170.0032 | 50.877 | 188.163 | 60.0009 | 166.508 | 193.6354 | 191.886
354.0354 | 170.3666 | 51.0681 | 189.035 | 59.9973 | 166.5705 | 193.4667 | 191.9075
355.0354 | 170.1477 | 51.4649 | 190.5454 | 60.0992 | 167.1965 | 194.6328 | 192.1586
356.0354 | 170.3028 | 51.8294 | 190.2029 | 60.6197 | 166.5412 | 194.4427 | 192.4055
357.0354 | 170.9442 | 51.8378 | 191.3398 | 60.6795 | 167.7071 | 195.6712 | 192.6428
358.0354 | 171.4609 | 51.8549 | 192.5724 | 60.8218 | 167.5928 | 196.9044 | 193.2073
359.0354 | 171.03 | 52.0414 | 191.8462 | 60.8479 | 168.313 | 198.7623 | 193.7939
360.0354 | 171.1147 | 52.0667 | 192.4557 | 61.0778 | 170.8372 | 200.2734 | 195.0183
361.0354 | 172.4126 | 52.2433 | 192.9689 | 61.2853 | 172.3067 | 200.8358 | 196.2397
362.0354 | 173.2409 | 52.3511 | 193.5595 | 61.3457 | 173.0881 | 200.3449 | 195.6346
363.0354 | 172.9656 | 52.7393 | 193.7467 | 61.5149 | 172.2375 | 199.041 | 194.8759
364.0354 | 172.842 | 52.9858 | 194.2497 | 62.1439 | 171.2595 | 198.4972 | 194.1171
365.0354 | 172.3939 | 53.0472 | 194.7388 | 61.9514 | 170.6023 | 196.9674 | 193.2506
366.0354 | 171.533 | 53.0653 | 194.7704 | 62.1387 | 169.7693 | 195.8487 | 192.0078
367.0354 | 170.976 | 52.9898 | 195.6975 | 62.2694 | 168.9771 | 195.283 | 191.4594
368.0354 | 170.5377 | 52.9771 | 195.9165 | 62.2972 | 168.995 | 194.6704 | 191.4305
369.0354 | 170.5443 | 53.4872 | 196.1807 | 62.5144 | 168.5226 | 193.4826 | 190.8823
370.0354 | 171.0267 | 53.7879 | 197.5921 | 62.7605 | 168.2289 | 193.1387 | 190.4503
371.0354 | 170.0701 | 53.8523 | 197.6722 | 62.9451 | 167.8429 | 192.2951 | 189.6244
372.0354 | 170.6563 | 53.6742 | 197.8477 | 63.279 | 167.0053 | 190.9091 | 188.5626
373.0354 | 170.7946 | 54.0863 | 197.6873 | 63.368 | 166.574 | 190.7988 | 187.8299
374.0354 | 171.1113 | 54.2029 | 198.6704 | 63.5069 | 166.0657 | 190.0095 | 187.097
375.0354 | 171.3283 | 54.1777 | 199.8784 | 63.9725 | 166.8746 | 190.0498 | 186.927
376.0354 | 171.4194 | 54.4303 | 199.3964 | 64.3766 | 167.3701 | 189.6657 | 186.384
377.0354 | 172.0323 | 54.4577 | 199.3357 | 64.4628 | 168.416 | 188.9166 | 186.0923
378.0354 | 171.6878 | 54.5866 | 200.2378 | 64.4271 | 169.2067 | 189.1811 | 185.7457
379.0354 | 170.8784 | 54.5287 | 200.9037 | 64.5111 | 169.4801 | 189.691 | 186.1852
380.0354 | 171.2309 | 54.8973 | 201.4856 | 64.7832 | 169.9004 | 190.2277 | 186.5404
381.0354 | 171.8445 | 55.1554 | 203.9613 | 64.9926 | 170.0225 | 191.136 | 186.8598
382.0354 | 171.5724 | 54.9906 | 203.3524 | 65.0627 | 170.7622 | 191.8458 | 187.6203
383.0354 | 171.2277 | 55.27 | 202.761 | 65.1003 | 171.5952 | 192.3628 | 188.9816
384.0354 | 171.7024 | 55.4452 | 203.5879 | 65.4149 | 175.174 | 193.7436 | 189.3271
385.0354 | 171.884 | 55.3355 | 203.8002 | 65.6239 | 178.7123 | 195.2653 | 190.1511
386.0354 | 171.9935 | 55.4065 | 203.6592 | 65.745 | 180.6983 | 197.9424 | 192.3213
387.0354 | 171.6531 | 55.3422 | 203.8054 | 65.7791 | 180.5465 | 199.3532 | 193.991
388.0354 | 171.5612 | 55.3168 | 204.2263 | 65.9867 | 179.4453 | 199.6339 | 194.9908
389.0354 | 171.7219 | 55.5147 | 205.2006 | 66.2282 | 180.6021 | 199.9812 | 195.0309
390.0354 | 172.9672 | 55.7778 | 205.556 | 66.5444 | 181.2725 | 200.8631 | 195.9901
391.0354 | 173.6877 | 55.7142 | 206.0508 | 67.2808 | 183.0282 | 200.9669 | 196.2844
392.0354 | 173.2359 | 55.7996 | 207.4242 | 67.0583 | 184.2597 | 200.5896 | 195.9708
393.0354 | 173.7573 | 55.9138 | 208.2874 | 67.0603 | 184.5414 | 200.2085 | 195.9194
394.0354 | 174.1508 | 56.0405 | 207.1693 | 67.2281 | 184.3687 | 199.9605 | 196.4481
395.0354 | 174.6686 | 56.1213 | 207.6653 | 67.3372 | 184.7378 | 198.965 | 195.8297
396.0354 | 174.9128 | 56.0653 | 208.0343 | 67.6054 | 185.4254 | 198.8634 | 195.3595
397.0354 | 175.1023 | 56.1526 | 208.1754 | 67.6033 | 186.6275 | 200.0636 | 196.157
398.0354 | 174.7624 | 56.3263 | 208.0054 | 67.7358 | 185.7952 | 200.6903 | 196.8774
399.0354 | 174.8931 | 56.5319 | 208.3624 | 68.1083 | 187.8906 | 201.3385 | 195.8516
400.0354 | 174.2757 | 56.5756 | 208.0297 | 68.1365 | 188.803 | 201.4789 | 196.2105
401.0354 | 174.2308 | 56.5993 | 208.4561 | 68.3527 | 188.4541 | 201.0992 | 195.1456
402.0354 | 174.1923 | 56.5846 | 208.434 | 68.6236 | 187.5799 | 200.9674 | 194.5774
403.0354 | 174.4081 | 56.791 | 208.4872 | 68.8157 | 187.6258 | 201.5472 | 193.6723
404.0354 | 176.0759 | 57.0031 | 209.0383 | 68.9919 | 187.8597 | 201.0313 | 192.5162
405.0354 | 176.9808 | 57.0656 | 210.4787 | 69.176 | 187.6814 | 201.6986 | 192.7136
406.0354 | 176.9583 | 57.1161 | 210.7841 | 69.4667 | 189.1924 | 203.6387 | 195.6443
407.0354 | 177.4277 | 57.2139 | 210.844 | 69.7324 | 189.8948 | 204.8961 | 196.7703
408.0354 | 178.981 | 57.3762 | 210.7194 | 69.6559 | 191.2407 | 205.9334 | 197.6751
409.0354 | 180.0458 | 57.6747 | 210.4806 | 69.7942 | 191.3467 | 207.5264 | 198.6108
410.0354 | 181.3653 | 57.6789 | 211.0227 | 70.2198 | 191.6332 | 207.74 | 198.4082
411.0354 | 182.6318 | 57.6621 | 211.0259 | 70.339 | 192.6821 | 209.0507 | 198.7883
412.0354 | 184.3705 | 57.8678 | 211.4005 | 70.7575 | 193.1793 | 209.5907 | 199.5077
413.0354 | 186.4154 | 57.9987 | 211.3634 | 71.3523 | 193.5784 | 210.5738 | 199.1339
414.0354 | 187.288 | 57.9997 | 213.0264 | 71.3826 | 195.0074 | 211.4637 | 199.0126
415.0354 | 187.4305 | 58.0654 | 212.3375 | 71.4913 | 194.8804 | 212.578 | 198.1947
416.0354 | 186.7826 | 58.5072 | 212.2544 | 72.0376 | 195.9759 | 213.5847 | 198.6766
417.0354 | 186.3483 | 58.5974 | 213.2709 | 71.9815 | 196.0593 | 213.2685 | 198.909
418.0354 | 187.0469 | 58.8703 | 213.4902 | 72.2535 | 196.2549 | 212.7553 | 198.8933
419.0354 | 188.8088 | 58.9948 | 214.2383 | 72.4163 | 195.7623 | 211.8262 | 198.2131
420.0354 | 188.6295 | 59.1625 | 215.4301 | 72.5141 | 194.3622 | 210.9544 | 197.52
421.0354 | 188.5745 | 59.3822 | 215.4265 | 72.6337 | 193.2618 | 209.6418 | 196.7206
422.0354 | 189.0522 | 59.3152 | 217.024 | 73.0824 | 192.6644 | 209.6844 | 197.0675
423.0354 | 190.1621 | 59.3942 | 217.5861 | 73.3147 | 192.1983 | 210.5911 | 198.0886
424.0354 | 190.6301 | 59.5688 | 216.595 | 74.7518 | 193.1216 | 211.2271 | 197.6771
425.0198 | 192.5026 | 59.8276 | 218.4134 | 74.2193 | 192.3688 | 210.7074 | 197.11
426.0198 | 192.5028 | 60.2069 | 217.856 | 74.0016 | 192.2497 | 210.6655 | 197.3694
427.0198 | 191.832 | 60.3207 | 217.1378 | 74.5488 | 191.595 | 209.7147 | 197.63
428.0354 | 190.2756 | 60.5825 | 217.603 | 74.4544 | 190.1829 | 208.1723 | 196.9665
429.0354 | 190.1353 | 60.761 | 218.136 | 74.9676 | 189.338 | 206.9855 | 196.2054
430.0354 | 190.2125 | 60.8686 | 219.1005 | 75.4609 | 188.001 | 207.4109 | 195.897
431.0354 | 191.2396 | 60.9678 | 220.3421 | 75.327 | 188.7248 | 206.9762 | 195.1594
432.0354 | 190.4125 | 61.1088 | 220.9013 | 75.5724 | 188.7178 | 206.891 | 195.5345
433.0354 | 190.5849 | 61.4903 | 220.6259 | 75.6296 | 188.2536 | 206.8919 | 195.7493
434.0354 | 190.4612 | 61.7157 | 220.2189 | 75.803 | 190.4288 | 208.0434 | 197.3416
435.0354 | 189.9172 | 61.6168 | 221.0641 | 75.8837 | 191.0744 | 208.6011 | 197.7256
436.0354 | 190.2627 | 61.4162 | 221.7108 | 76.1257 | 191.1352 | 209.2406 | 198.4563
437.0354 | 190.4145 | 61.5755 | 222.0063 | 76.2315 | 192.0296 | 210.2031 | 200.1037
438.0198 | 190.0839 | 61.7529 | 222.0095 | 76.5027 | 193.426 | 211.9916 | 201.2552
439.0198 | 188.8795 | 61.6929 | 223.3066 | 76.7819 | 193.6115 | 213.2486 | 203.2828
440.0198 | 188.6283 | 61.7081 | 223.3975 | 77.1083 | 194.1347 | 212.3276 | 202.7315
441.0198 | 190.1727 | 61.6959 | 223.3143 | 77.1015 | 195.1603 | 212.4073 | 202.1822
442.0198 | 190.4914 | 61.7232 | 223.7431 | 77.3679 | 195.5672 | 212.7404 | 201.8176
443.0198 | 190.434 | 61.885 | 224.993 | 77.5595 | 195.135 | 211.3419 | 201.5285
444.0198 | 192.3063 | 62.1434 | 226.031 | 77.8114 | 194.466 | 211.331 | 201.7017
445.0354 | 192.465 | 62.225 | 226.1892 | 78.1239 | 194.0348 | 211.938 | 201.8634
446.0354 | 192.4823 | 62.4795 | 225.6901 | 78.14 | 193.9755 | 212.3168 | 202.1294
447.0354 | 193.1246 | 62.6692 | 225.9438 | 78.7176 | 194.558 | 212.2888 | 202.5487
448.0354 | 193.0504 | 62.8975 | 225.5455 | 78.774 | 194.0014 | 212.4939 | 202.2877
449.0354 | 194.8236 | 62.9925 | 226.3575 | 79.1853 | 194.3589 | 214.1595 | 202.7816
450.0354 | 195.3131 | 63.0294 | 226.3088 | 79.5152 | 194.9467 | 215.2102 | 203.3819
451.0354 | 195.7922 | 62.8166 | 227.0378 | 79.622 | 196.5675 | 216.819 | 203.9629
452.0354 | 195.7662 | 62.9881 | 227.2763 | 79.8863 | 198.3674 | 217.7144 | 204.8824
453.0354 | 196.9441 | 62.938 | 228.3475 | 80.1098 | 199.0895 | 217.9595 | 204.314
454.0354 | 196.3983 | 62.9072 | 228.1501 | 80.2762 | 199.1824 | 218.2188 | 204.8576
455.0354 | 196.0571 | 63.1501 | 228.6056 | 80.9815 | 199.8656 | 219.6418 | 205.9847
456.0354 | 195.7288 | 63.5837 | 228.3062 | 81.3843 | 199.691 | 219.1368 | 206.1132
457.0354 | 196.8234 | 63.6569 | 228.512 | 81.8461 | 199.4943 | 218.7046 | 206.3289
458.0354 | 197.6903 | 63.6261 | 228.3381 | 82.2825 | 199.7939 | 218.804 | 206.6949
459.0354 | 198.2422 | 63.9797 | 228.6427 | 82.3557 | 198.9572 | 218.1794 | 205.6765
460.0354 | 198.7606 | 63.9664 | 228.5666 | 82.8814 | 198.9577 | 217.4086 | 205.269
461.0354 | 200.1286 | 64.3369 | 229.1622 | 83.5661 | 198.844 | 215.4273 | 204.2649
462.0354 | 199.9143 | 64.717 | 229.2236 | 83.1957 | 197.9796 | 214.2779 | 203.2846
463.0354 | 199.2009 | 64.756 | 230.1212 | 83.3781 | 196.8273 | 213.272 | 202.3572
464.0354 | 199.1986 | 64.702 | 230.4772 | 83.8841 | 196.3135 | 212.5457 | 201.5698
465.0354 | 198.9078 | 64.7062 | 230.8221 | 83.8722 | 196.2354 | 212.2344 | 200.7597
466.0354 | 199.2444 | 64.817 | 230.8783 | 85.1328 | 195.8221 | 212.2841 | 200.4738
467.0354 | 200.5707 | 64.9565 | 231.2531 | 85.549 | 195.0152 | 213.0005 | 200.068
468.0354 | 202.6241 | 65.1634 | 231.5974 | 84.7913 | 195.6014 | 211.9412 | 199.4639
469.0354 | 203.1115 | 65.2705 | 233.0237 | 84.917 | 197.0863 | 213.0157 | 199.2988
470.0354 | 204.1934 | 65.4176 | 232.9517 | 85.4315 | 199.9233 | 215.4465 | 201.0702
471.0354 | 204.133 | 65.69 | 232.8652 | 85.9471 | 201.6332 | 216.4893 | 202.3097
472.0354 | 205.7772 | 65.7277 | 234.4967 | 85.8721 | 203.5744 | 218.0252 | 203.5591
473.0354 | 206.6887 | 65.5997 | 233.3869 | 86.1005 | 205.3548 | 219.6867 | 205.5017
474.0354 | 206.3332 | 65.8318 | 232.9542 | 86.279 | 205.7814 | 221.2274 | 206.83
475.0354 | 205.6165 | 65.745 | 233.3881 | 86.4807 | 206.3437 | 221.4005 | 207.3556
476.0354 | 204.8586 | 65.8167 | 235.0501 | 86.7673 | 208.0201 | 223.2121 | 207.6024
477.0354 | 205.3155 | 65.9044 | 236.0109 | 86.8493 | 209.5959 | 224.3492 | 208.8519
478.0354 | 206.4954 | 66.1918 | 236.7802 | 87.1425 | 208.9608 | 225.0843 | 209.7455
479.0354 | 206.8172 | 66.2171 | 237.999 | 87.4645 | 208.7796 | 225.5764 | 211.322
480.0354 | 206.3422 | 66.4924 | 237.1387 | 87.915 | 208.6104 | 225.8161 | 211.4274
481.0354 | 207.4385 | 66.4245 | 237.3441 | 88.3463 | 211.1875 | 225.6221 | 211.3035
482.0354 | 208.5329 | 66.7054 | 237.7999 | 88.7787 | 211.7293 | 225.1844 | 210.4858
483.0354 | 209.157 | 66.7064 | 238.5267 | 88.5386 | 210.0882 | 224.0881 | 209.4692
484.0354 | 209.1383 | 66.9372 | 239.1703 | 88.7461 | 209.6189 | 224.2857 | 209.518
485.0354 | 208.5112 | 67.0565 | 238.6983 | 88.8849 | 209.9762 | 224.6078 | 210.4177
486.0354 | 208.1614 | 67.0558 | 238.4288 | 88.9898 | 211.3156 | 226.3315 | 212.4685
487.0354 | 208.6387 | 67.0782 | 239.3471 | 89.182 | 211.2101 | 227.4878 | 213.3667
488.0354 | 208.8681 | 67.097 | 239.6761 | 89.4921 | 211.3397 | 228.558 | 215.4867
489.0354 | 208.8874 | 67.327 | 241.8107 | 89.8945 | 210.8819 | 228.8394 | 216.3809
490.0354 | 209.6433 | 67.5814 | 241.0326 | 90.1911 | 209.2036 | 227.808 | 216.6219
491.0354 | 210.4253 | 67.5686 | 240.2773 | 90.5236 | 208.7832 | 227.7318 | 215.8307
492.0354 | 210.7734 | 67.6194 | 240.2963 | 90.8623 | 210.3756 | 229.36 | 216.1733
493.0354 | 210.4957 | 67.6523 | 240.5093 | 90.7859 | 211.1047 | 231.4829 | 216.3599
494.0354 | 209.712 | 67.7141 | 240.9184 | 90.8458 | 211.7207 | 232.774 | 216.9311
495.0354 | 208.3017 | 67.8372 | 241.1304 | 90.9781 | 212.8609 | 233.9266 | 217.4717
496.0354 | 207.2702 | 67.8988 | 241.1247 | 91.453 | 212.5323 | 234.2793 | 216.7815
497.0354 | 207.713 | 68.0892 | 241.6908 | 91.6059 | 212.3419 | 234.1249 | 216.2752
498.0354 | 208.705 | 68.1934 | 241.9327 | 91.9275 | 212.6202 | 236.0487 | 216.5397
499.0354 | 209.9807 | 68.4447 | 242.2988 | 92.1135 | 213.9755 | 237.9308 | 217.5916
500.0354 | 211.0738 | 68.6064 | 242.4316 | 92.4666 | 214.6461 | 238.2532 | 218.4566
501.0354 | 211.4521 | 68.6712 | 243.1506 | 92.6668 | 215.7193 | 239.5324 | 220.3579
502.0354 | 211.2869 | 68.7877 | 243.676 | 93.0614 | 215.4094 | 238.3534 | 220.9781
503.0354 | 210.8154 | 68.9617 | 244.2358 | 93.1608 | 215.0638 | 237.579 | 220.7653
504.0354 | 209.4449 | 69.0573 | 244.695 | 93.2668 | 215.631 | 238.1091 | 221.3282
505.051 | 208.9491 | 68.9713 | 244.3973 | 93.3852 | 217.0722 | 239.2632 | 222.7166
506.0354 | 209.4191 | 69.3415 | 244.3341 | 93.5419 | 218.9172 | 239.6752 | 222.5765
507.0354 | 208.8032 | 69.4909 | 244.5454 | 93.8661 | 220.7726 | 241.6067 | 223.2893
508.0354 | 209.2872 | 69.6823 | 245.8625 | 94.0276 | 220.3271 | 241.6267 | 223.4336
509.0354 | 209.1921 | 69.7599 | 245.681 | 94.2592 | 220.9569 | 242.1128 | 224.2889
510.0354 | 209.758 | 69.7938 | 245.7959 | 94.5506 | 223.0919 | 242.3844 | 224.5247
511.0354 | 209.8528 | 69.9099 | 246.0281 | 94.6591 | 226.5017 | 244.0331 | 225.9462
512.0354 | 209.7225 | 70.0346 | 245.6936 | 94.7857 | 226.8636 | 245.6396 | 225.5749
513.0354 | 209.3693 | 70.2469 | 246.1162 | 95.1819 | 226.9954 | 245.8709 | 224.9832
514.0354 | 210.076 | 70.4139 | 246.4103 | 95.7665 | 228.577 | 247.4122 | 226.344
515.0354 | 210.3783 | 70.5863 | 246.0467 | 96.0069 | 228.4604 | 247.923 | 227.4389
516.0354 | 210.6543 | 70.6984 | 246.3608 | 96.0772 | 230.0471 | 248.2171 | 227.7759
517.0354 | 210.5575 | 70.7211 | 246.1949 | 96.3025 | 228.8278 | 247.7254 | 226.6005
518.0354 | 211.3294 | 70.9712 | 246.1252 | 96.6075 | 228.685 | 248.7137 | 225.9089
519.0354 | 211.627 | 71.0936 | 246.1506 | 96.7557 | 227.9766 | 247.8659 | 225.2859
520.0354 | 211.8779 | 71.0689 | 246.1894 | 97.5442 | 228.6858 | 248.2445 | 225.4119
521.0354 | 212.0737 | 71.0081 | 246.4735 | 97.4344 | 228.5423 | 248.87 | 224.4245
522.0354 | 212.2964 | 71.161 | 247.4362 | 97.6246 | 228.283 | 248.8628 | 224.924
523.0354 | 213.0544 | 71.4661 | 247.1545 | 97.9409 | 228.1941 | 248.8744 | 225.7206
524.0354 | 213.0184 | 71.392 | 247.1973 | 98.2587 | 228.9104 | 248.7407 | 225.2908
525.0354 | 212.815 | 71.3451 | 246.8764 | 98.1046 | 228.1583 | 249.0601 | 225.3156
526.0354 | 212.8582 | 71.5609 | 247.2058 | 98.3599 | 227.3886 | 248.5461 | 224.3392
527.0354 | 211.9679 | 71.8039 | 247.5663 | 98.9226 | 227.9312 | 249.2086 | 224.5826
528.0354 | 212.5784 | 71.8362 | 248.0415 | 99.7145 | 229.9236 | 249.1053 | 225.3278
529.0354 | 213.4856 | 72.0092 | 247.9157 | 99.6207 | 230.1061 | 247.3995 | 224.2812
530.0354 | 214.9243 | 72.1623 | 248.047 | 99.7792 | 232.2972 | 247.8211 | 224.4779
531.0354 | 215.2087 | 72.0642 | 248.0599 | 99.9547 | 233.0453 | 248.4987 | 224.5648
532.0354 | 215.0722 | 72.1027 | 247.9785 | 100.0348 | 233.5714 | 248.9831 | 225.1744
533.0354 | 215.8693 | 72.305 | 248.2067 | 100.3342 | 233.821 | 248.7461 | 225.1065
534.0354 | 216.3594 | 72.4982 | 248.1288 | 100.5352 | 233.8447 | 249.7396 | 225.4964
535.0354 | 216.0456 | 72.5238 | 248.6409 | 100.8701 | 233.1744 | 248.486 | 224.4074
536.0354 | 216.3445 | 72.5375 | 248.8707 | 101.1715 | 234.2647 | 248.854 | 224.5038
537.0354 | 216.0914 | 72.6001 | 249.1101 | 101.5395 | 233.9253 | 249.1637 | 225.3479
538.0354 | 216.1435 | 72.6784 | 249.1625 | 101.644 | 233.4963 | 250.9448 | 225.7397
539.0354 | 215.5366 | 72.9669 | 249.1902 | 102.2964 | 232.953 | 251.9111 | 226.0175
540.0354 | 215.1116 | 73.0803 | 249.1867 | 102.6406 | 233.4243 | 253.4292 | 226.7756
541.0354 | 216.4838 | 73.198 | 248.9386 | 103.3223 | 234.413 | 253.73 | 226.3674
542.0354 | 217.1762 | 73.4935 | 248.9747 | 103.1979 | 234.5141 | 254.3262 | 227.3712
543.0354 | 218.4378 | 73.5701 | 249.3006 | 104.1063 | 235.2419 | 255.4735 | 227.0934
544.0354 | 220.405 | 73.6755 | 250.096 | 104.8396 | 234.354 | 255.7551 | 228.5136
545.0354 | 222.2885 | 73.8619 | 249.8184 | 104.9449 | 234.4431 | 256.4512 | 228.8103
546.0354 | 222.615 | 74.1128 | 250.0377 | 104.7074 | 234.3308 | 256.4795 | 228.6355
547.0354 | 223.1298 | 74.1551 | 249.9583 | 105.7075 | 233.7955 | 257.5423 | 229.8251
548.0354 | 224.0366 | 74.2867 | 250.4516 | 106.4146 | 235.7529 | 257.8508 | 229.7989
549.0354 | 224.8285 | 74.5231 | 250.3137 | 106.9574 | 236.0423 | 259.1617 | 230.5274
550.0354 | 225.4479 | 74.7628 | 250.4047 | 107.2082 | 235.944 | 259.2819 | 231.0472
551.0354 | 226.306 | 74.8208 | 250.1097 | 106.9519 | 236.2949 | 260.0254 | 230.3206
552.0354 | 226.5632 | 74.9546 | 250.4171 | 106.9372 | 238.3009 | 262.23 | 232.3263
553.0354 | 228.3425 | 75.166 | 252.0271 | 107.1655 | 237.4592 | 263.1478 | 233.6012
554.0354 | 227.2118 | 75.1782 | 252.1058 | 107.5458 | 237.2523 | 263.8861 | 235.0091
555.0354 | 227.6532 | 75.1492 | 251.6916 | 107.8171 | 236.6423 | 264.1882 | 235.6505
556.0354 | 227.8386 | 75.4206 | 252.1726 | 108.1928 | 238.0456 | 264.5607 | 237.4929
557.0354 | 229.0538 | 75.2876 | 252.1533 | 108.6137 | 240.1486 | 265.9641 | 239.6694
558.0354 | 229.6576 | 75.3659 | 253.2445 | 108.9047 | 239.3681 | 264.665 | 239.3138
559.0354 | 231.1494 | 75.5165 | 253.1501 | 109.2678 | 239.6729 | 264.0773 | 239.422
560.0354 | 232.1802 | 75.8291 | 252.9877 | 109.259 | 238.8363 | 263.4836 | 238.6393
561.0354 | 231.3186 | 75.8308 | 252.9326 | 109.5857 | 238.8183 | 264.2257 | 239.8979
562.0354 | 231.4624 | 75.775 | 253.1379 | 109.9096 | 238.5795 | 264.6215 | 240.4223
563.0354 | 230.8659 | 75.8446 | 252.6879 | 110.5115 | 240.2653 | 265.3094 | 241.0599
564.0354 | 231.8818 | 75.9695 | 253.3376 | 110.8423 | 239.8491 | 265.7217 | 242.097
565.0354 | 232.1591 | 76.0941 | 254.0454 | 111.6276 | 239.99 | 266.9753 | 242.8794
566.0354 | 231.9109 | 76.3889 | 253.3482 | 112.1345 | 240.7033 | 266.4737 | 243.1882
567.0354 | 232.9946 | 76.6185 | 253.8802 | 111.874 | 241.0542 | 266.0469 | 243.6414
568.0354 | 233.3411 | 76.6112 | 254.1717 | 112.3187 | 240.5223 | 265.954 | 243.0911
569.0354 | 234.3261 | 76.9222 | 254.0869 | 112.6335 | 241.0753 | 264.5954 | 242.7741
570.0354 | 234.232 | 76.9942 | 254.522 | 113.3151 | 240.4801 | 265.5211 | 243.6709
571.0354 | 236.1783 | 77.1834 | 254.9138 | 113.3987 | 240.6364 | 264.8854 | 243.6143
572.0354 | 236.1899 | 77.2614 | 254.7388 | 113.8369 | 240.8387 | 264.733 | 243.7225
573.0354 | 236.8614 | 77.4821 | 255.2104 | 114.4285 | 239.9469 | 265.1158 | 243.7395
574.0354 | 237.4323 | 77.4181 | 254.8577 | 114.5608 | 239.5232 | 264.3093 | 242.3309
575.0354 | 236.4346 | 77.7551 | 255.0436 | 115.8842 | 239.3719 | 263.0401 | 240.9831
576.0354 | 236.3481 | 77.9817 | 255.145 | 116.7731 | 240.0946 | 262.5833 | 240.9033
577.0354 | 235.5378 | 78.0818 | 254.5402 | 117.0256 | 240.8377 | 261.6993 | 239.331
578.0354 | 233.672 | 77.9135 | 254.7345 | 117.2309 | 240.3058 | 261.5476 | 237.7717
579.0354 | 233.2683 | 78.0996 | 254.9651 | 116.8002 | 241.7143 | 261.3341 | 238.5029
580.0354 | 232.345 | 78.364 | 255.3048 | 117.6899 | 240.5869 | 260.5225 | 238.0548
581.0354 | 231.7759 | 78.4272 | 255.3583 | 117.958 | 240.4491 | 259.2885 | 237.2063
582.0354 | 231.1471 | 78.2491 | 255.0964 | 118.3583 | 240.2464 | 258.4912 | 236.6539
583.0354 | 231.9122 | 78.4028 | 255.5159 | 118.4615 | 239.9537 | 258.1295 | 236.1105
584.0354 | 232.4407 | 78.4123 | 255.4737 | 118.5898 | 240.0475 | 259.0467 | 236.1917
585.0354 | 232.0669 | 78.3785 | 255.883 | 118.8941 | 240.1282 | 259.7483 | 235.7868
586.0354 | 232.4234 | 78.5032 | 255.8657 | 119.0804 | 239.3193 | 259.738 | 235.7172
587.0354 | 231.7591 | 78.6353 | 256.051 | 119.5383 | 239.3363 | 260.7673 | 236.0056
588.0354 | 230.5649 | 78.837 | 256.0252 | 119.8199 | 239.2137 | 260.9376 | 235.7313
589.0354 | 231.0609 | 79.1122 | 255.9367 | 120.1345 | 239.9599 | 261.4449 | 235.2199
590.0354 | 231.0505 | 79.1433 | 256.0751 | 120.8732 | 239.4908 | 260.8079 | 234.1061
591.0354 | 231.0103 | 79.122 | 256.6338 | 121.3458 | 240.634 | 261.3651 | 233.2568
592.0354 | 230.9192 | 79.3538 | 256.4017 | 121.5392 | 240.8934 | 262.8479 | 234.9458
593.0354 | 230.3796 | 79.4984 | 256.093 | 121.5168 | 240.6138 | 262.157 | 234.5559
594.0354 | 229.7916 | 79.5637 | 256.1136 | 121.9147 | 240.5093 | 261.2255 | 234.1029
595.0354 | 228.833 | 79.6745 | 256.0495 | 122.547 | 240.3775 | 260.1784 | 232.8682
596.0354 | 228.3028 | 79.9441 | 256.103 | 123.6573 | 239.5022 | 259.4101 | 232.2981
597.0354 | 229.1082 | 79.8922 | 256.8596 | 123.5075 | 240.4599 | 258.857 | 230.7671
598.0354 | 230.9119 | 80.0533 | 257.2835 | 123.7455 | 241.9708 | 259.7305 | 230.7186
599.0354 | 231.988 | 80.2431 | 257.2403 | 124.248 | 243.1726 | 260.8443 | 231.272
600.0354 | 231.6831 | 80.3981 | 257.0154 | 125.6672 | 242.9068 | 260.2658 | 231.1149
601.0354 | 231.3881 | 80.4911 | 256.83 | 125.579 | 244.3847 | 262.5984 | 232.182
602.0354 | 230.7183 | 80.5275 | 257.0506 | 125.6292 | 245.3271 | 262.3621 | 232.9404
603.0354 | 230.063 | 80.4149 | 257.0819 | 126.0455 | 243.8792 | 261.8782 | 233.6604
604.0354 | 229.7174 | 80.5602 | 257.023 | 127.8173 | 244.064 | 261.4256 | 233.1931
605.0354 | 229.2426 | 80.8418 | 257.1791 | 127.7183 | 244.4089 | 261.6781 | 234.2987
606.0354 | 230.1169 | 81.0156 | 257.3178 | 128.2777 | 244.0414 | 260.7145 | 233.1888
607.0354 | 229.7743 | 81.1335 | 257.215 | 129.3306 | 244.3138 | 259.9816 | 231.7341
608.0354 | 229.1069 | 81.3445 | 257.3485 | 128.5938 | 244.3396 | 260.1298 | 232.9457
609.0354 | 229.1846 | 81.3838 | 257.2447 | 129.4327 | 243.3832 | 260.4701 | 233.5318
610.0354 | 228.6602 | 81.4154 | 257.1525 | 130.5462 | 243.9158 | 261.4933 | 234.8233
611.0354 | 227.8598 | 81.7448 | 257.3867 | 130.2025 | 246.1541 | 262.2965 | 235.8452
612.0354 | 227.0862 | 81.784 | 257.4758 | 130.7344 | 245.3193 | 262.0302 | 236.955
613.0354 | 227.0232 | 81.8568 | 257.8609 | 131.4451 | 245.3051 | 262.7428 | 235.9159
614.0354 | 226.8711 | 81.917 | 257.707 | 131.7318 | 246.9504 | 263.472 | 237.1901
615.0354 | 227.2725 | 81.9096 | 257.7832 | 132.2661 | 247.2286 | 263.2896 | 237.3775
616.0354 | 226.8166 | 82.0779 | 257.6258 | 132.2209 | 245.3505 | 263.2102 | 236.6052
617.0354 | 226.7648 | 81.952 | 257.8932 | 132.5912 | 245.4685 | 262.2148 | 236.0813
618.0354 | 226.1442 | 82.1619 | 257.5264 | 133.4567 | 245.5538 | 261.8006 | 235.1537
619.0354 | 225.4384 | 82.3158 | 257.6884 | 133.7137 | 245.6563 | 260.3426 | 233.9908
620.0354 | 225.9218 | 82.3693 | 258.1537 | 133.8963 | 246.908 | 260.1888 | 233.4283
621.0354 | 227.3939 | 82.4434 | 258.1695 | 133.948 | 248.3406 | 261.133 | 233.6524
622.0354 | 227.6463 | 82.7292 | 258.2503 | 134.3926 | 250.1418 | 262.0416 | 234.3016
623.0354 | 227.1742 | 82.8787 | 258.1837 | 135.1177 | 251.5739 | 262.5975 | 236.1627
624.0354 | 226.7131 | 83.0144 | 258.0607 | 135.4956 | 252.9165 | 263.023 | 236.0376
625.0354 | 226.3333 | 82.9804 | 258.2612 | 135.7212 | 253.9998 | 263.7265 | 236.4744
626.0354 | 226.1118 | 82.9 | 258.0982 | 136.3337 | 252.2151 | 263.2907 | 235.7347
627.0354 | 225.9115 | 82.9295 | 258.2243 | 136.429 | 253.5848 | 263.1042 | 235.9652
628.0354 | 226.2294 | 83.05 | 258.3742 | 137.0065 | 253.499 | 263.274 | 235.2908
629.0354 | 227.0622 | 83.2801 | 259.0775 | 137.1681 | 253.2333 | 264.3028 | 236.6409
630.0354 | 227.2938 | 83.2456 | 258.8976 | 137.7909 | 252.6612 | 264.393 | 236.7713
631.0354 | 228.5507 | 83.6064 | 259.4213 | 139.0621 | 252.2406 | 264.3254 | 236.5581
632.0354 | 229.1406 | 83.8861 | 259.0632 | 138.8865 | 251.7531 | 264.9857 | 236.2331
633.0354 | 229.3945 | 83.8409 | 259.0102 | 139.8836 | 250.3881 | 265.6707 | 235.8002
634.0354 | 229.1606 | 83.8407 | 259.0826 | 139.57 | 249.6896 | 265.4707 | 234.8714
635.0354 | 228.5392 | 84.1277 | 259.0767 | 140.0043 | 251.6681 | 266.7019 | 236.5455
636.0354 | 227.7054 | 84.224 | 258.9102 | 139.7672 | 252.2172 | 266.7081 | 237.1517
637.0354 | 226.8884 | 84.2781 | 259.0721 | 140.1936 | 250.6293 | 265.4113 | 236.6371
638.0354 | 225.7631 | 84.5436 | 258.9316 | 140.7323 | 249.7965 | 264.4981 | 235.5153
639.0354 | 225.7903 | 84.486 | 259.118 | 141.5939 | 249.17 | 263.192 | 234.797
640.0354 | 225.45 | 84.3871 | 259.0379 | 141.6251 | 249.0002 | 262.6432 | 234.7325
641.0354 | 226.0425 | 84.4653 | 259.6578 | 141.7126 | 249.6726 | 263.6868 | 235.5245
642.0354 | 226.8804 | 84.5102 | 259.8148 | 142.15 | 248.3338 | 263.5007 | 235.3097
643.0354 | 228.7014 | 84.7708 | 260.3762 | 142.5751 | 249.7567 | 264.401 | 235.321
644.0354 | 229.5195 | 84.7208 | 260.6624 | 142.8399 | 250.5759 | 266.2345 | 235.805
645.0354 | 228.6553 | 84.7024 | 260.4371 | 143.1616 | 250.9442 | 266.9881 | 235.947
646.0354 | 228.7995 | 85.1187 | 260.3778 | 144.6167 | 251.062 | 266.8858 | 237.7527
647.0354 | 228.6736 | 85.1606 | 259.9388 | 145.1544 | 250.0497 | 266.9398 | 237.8655
648.0354 | 227.8304 | 85.2695 | 260.0926 | 145.3284 | 251.082 | 267.664 | 238.8567
649.0354 | 228.1163 | 85.5846 | 260.6854 | 144.8998 | 250.3086 | 267.1059 | 239.458
650.0354 | 228.2787 | 85.6024 | 261.4439 | 145.3357 | 249.5621 | 266.771 | 239.4982
651.0354 | 229.217 | 85.5271 | 260.7742 | 146.1954 | 250.4723 | 267.6492 | 240.7268
652.0354 | 229.5605 | 85.7132 | 260.6567 | 146.3306 | 252.5623 | 269.3316 | 241.8959
653.0354 | 229.7016 | 85.7892 | 260.8105 | 146.8499 | 252.244 | 269.3342 | 242.3329
654.0354 | 229.2264 | 86.0933 | 261.1493 | 147.5529 | 251.8191 | 268.4501 | 241.5708
655.0354 | 228.6096 | 86.312 | 261.1923 | 147.9281 | 251.1258 | 267.7885 | 241.4832
656.0354 | 228.2991 | 86.506 | 261.3053 | 148.6054 | 250.3036 | 267.1631 | 241.3172
657.0354 | 227.9988 | 86.2984 | 261.0412 | 148.2643 | 251.3381 | 268.3789 | 241.0282
658.0354 | 227.8236 | 86.2042 | 261.1676 | 148.8557 | 251.1948 | 268.7417 | 241.2366
659.0354 | 227.6549 | 86.2151 | 260.8703 | 148.8711 | 250.6314 | 269.1918 | 240.6347
660.0354 | 227.829 | 86.1652 | 261.1212 | 149.4739 | 250.4276 | 268.3611 | 239.9192
661.0354 | 227.9088 | 86.5526 | 261.1819 | 149.4496 | 251.4765 | 267.6815 | 240.4748
662.0354 | 227.4762 | 86.5982 | 261.2799 | 149.9707 | 252.7272 | 268.3809 | 241.6078
663.0354 | 227.101 | 86.7349 | 261.3719 | 150.3178 | 251.4822 | 267.9573 | 242.3749
664.0354 | 226.9646 | 87.0598 | 261.4223 | 150.658 | 251.8036 | 267.5442 | 241.7107
665.0354 | 227.5112 | 87.087 | 261.7034 | 151.1247 | 250.1022 | 266.9966 | 241.32
666.0354 | 227.503 | 87.1176 | 261.9851 | 151.6778 | 249.2987 | 266.058 | 240.2019
667.0354 | 227.6291 | 87.2121 | 261.5954 | 151.5965 | 248.3114 | 265.1153 | 239.8453
668.0354 | 227.1399 | 87.4045 | 261.6428 | 151.9581 | 247.1126 | 264.9507 | 238.7458
669.0354 | 227.3174 | 87.4104 | 261.4666 | 152.3979 | 247.4647 | 264.1894 | 238.3116
670.0354 | 226.7074 | 87.4467 | 261.7951 | 153.2315 | 247.5376 | 263.8172 | 237.1629
671.0354 | 226.5461 | 87.6678 | 261.6169 | 153.5473 | 247.1457 | 263.1918 | 237.3596
672.0354 | 226.966 | 87.5617 | 261.961 | 153.6819 | 245.9848 | 260.9219 | 236.0783
673.0354 | 227.4326 | 87.5577 | 262.3039 | 153.5928 | 245.0041 | 260.5026 | 235.7725
674.0354 | 227.0898 | 87.5966 | 261.7424 | 153.7383 | 243.7367 | 260.5686 | 235.2723
675.0354 | 226.5013 | 87.6407 | 261.6048 | 154.3134 | 243.3414 | 260.2647 | 235.0406
676.0354 | 225.945 | 87.7881 | 262.067 | 154.6873 | 243.0793 | 259.7438 | 234.6324
677.0354 | 226.685 | 87.8376 | 263.1256 | 154.7804 | 244.4199 | 259.9621 | 234.9565
678.0354 | 226.6267 | 88.1302 | 262.7023 | 155.1557 | 246.0208 | 260.6568 | 235.2064
679.0354 | 227.1964 | 88.091 | 262.316 | 155.8448 | 247.024 | 261.6655 | 236.3315
680.0354 | 227.3948 | 88.3252 | 262.5903 | 156.0023 | 246.4786 | 261.3681 | 235.2402
681.0354 | 228.252 | 88.3079 | 262.5439 | 156.2901 | 246.5382 | 260.6684 | 234.875
682.0354 | 227.9675 | 88.3377 | 262.4797 | 156.3325 | 247.3148 | 260.9598 | 234.1983
683.0354 | 228.0468 | 88.8049 | 262.2163 | 157.0447 | 247.9135 | 260.9187 | 233.2245
684.0354 | 227.5367 | 88.9202 | 262.5311 | 157.3106 | 248.126 | 261.0444 | 232.7307
685.0354 | 227.2532 | 89.0707 | 262.4292 | 157.3819 | 248.2663 | 260.7407 | 232.6108
686.0354 | 226.5402 | 89.2826 | 262.5786 | 157.8202 | 247.8457 | 260.2402 | 231.9725
687.0354 | 226.3668 | 89.4733 | 262.7002 | 158.2429 | 247.5339 | 259.8995 | 232.0743
688.0354 | 225.6587 | 89.5427 | 262.6284 | 158.5543 | 247.9764 | 259.6566 | 231.5079
689.0354 | 224.7247 | 89.5515 | 262.5366 | 158.8437 | 247.4889 | 259.3917 | 230.9337
690.0354 | 224.1035 | 89.7524 | 262.6136 | 159.5987 | 247.4807 | 259.6943 | 230.3502
691.0354 | 224.3516 | 89.5315 | 262.8351 | 159.6363 | 246.8429 | 259.5239 | 230.193
692.0354 | 224.4793 | 89.8009 | 262.632 | 160.0821 | 246.5738 | 258.8696 | 229.8417
693.0354 | 224.372 | 89.8124 | 262.4149 | 160.1528 | 246.7974 | 258.9421 | 229.5477
694.0354 | 224.0675 | 90.0133 | 262.6721 | 160.4569 | 246.667 | 258.4079 | 228.7979
695.0354 | 224.0668 | 90.0623 | 262.8251 | 161.1448 | 246.1394 | 258.5571 | 228.863
696.0354 | 224.718 | 90.2798 | 263.4832 | 160.7202 | 246.1018 | 257.5571 | 228.183
697.0354 | 224.5769 | 90.3697 | 263.2813 | 161.1534 | 245.5619 | 258.578 | 228.613
698.0354 | 225.654 | 90.4691 | 263.188 | 161.8978 | 245.0755 | 259.2277 | 229.0338
699.0354 | 226.2918 | 90.4652 | 263.4864 | 161.9693 | 245.3832 | 260.6382 | 229.4287
700.0354 | 227.2124 | 90.4129 | 263.4494 | 162.056 | 246.0325 | 262.1204 | 230.0266
701.0354 | 226.989 | 90.7161 | 263.558 | 162.3077 | 248.5839 | 262.4188 | 231.9094
702.0354 | 227.64 | 90.9224 | 264.1412 | 162.8079 | 249.8579 | 262.8234 | 233.4679
703.0354 | 228.1746 | 90.8846 | 263.7278 | 163.6861 | 249.7221 | 263.1451 | 233.775
704.0354 | 228.5362 | 91.0088 | 264.0666 | 163.8174 | 249.0603 | 263.9959 | 233.551
705.0354 | 227.7386 | 91.1161 | 264.4822 | 164.4147 | 248.9245 | 263.9693 | 233.5078
706.0354 | 227.775 | 91.1002 | 264.1929 | 164.7468 | 250.1116 | 265.2674 | 234.6997
707.0354 | 227.8712 | 91.4365 | 265.2336 | 164.6155 | 251.6097 | 266.1101 | 235.9293
708.0354 | 227.9833 | 91.6479 | 264.9429 | 164.7354 | 251.6403 | 266.5902 | 236.7816
709.0354 | 228.8309 | 91.7008 | 265.0005 | 165.4365 | 251.2518 | 267.0235 | 238.3035
710.0354 | 230.8978 | 91.6918 | 265.0748 | 166.085 | 251.6759 | 265.8052 | 237.7441
711.0354 | 231.8747 | 91.7957 | 264.609 | 165.8487 | 251.9711 | 265.3703 | 238.1099
712.0354 | 231.9487 | 91.9527 | 264.3492 | 166.9567 | 253.1806 | 265.3571 | 238.4642
713.0354 | 231.3777 | 92.0868 | 264.7436 | 166.7284 | 253.4001 | 265.2027 | 238.7947
714.0354 | 230.6617 | 92.1722 | 264.2769 | 167.0267 | 251.9978 | 264.6369 | 238.5
715.0354 | 229.9224 | 92.1693 | 264.4045 | 167.4245 | 250.8101 | 263.8846 | 237.1824
716.0354 | 230.1993 | 92.0215 | 264.6439 | 167.4533 | 250.0766 | 263.1146 | 235.9313
717.0354 | 229.534 | 92.3503 | 264.609 | 167.6826 | 250.5627 | 263.2614 | 236.0547
718.0354 | 229.4023 | 92.4209 | 264.7257 | 168.2709 | 249.727 | 262.6067 | 236.6434
719.0354 | 229.4839 | 92.5819 | 264.7638 | 168.648 | 250.0054 | 262.3057 | 235.6909
720.0354 | 228.7442 | 92.6788 | 265.2788 | 169.4835 | 249.3142 | 262.6407 | 236.6752
721.0354 | 228.9782 | 92.8691 | 265.4288 | 169.7576 | 250.0595 | 261.856 | 236.0909
722.0354 | 229.8243 | 92.8064 | 265.2516 | 170.7162 | 250.3429 | 262.5571 | 236.8735
723.0354 | 229.7176 | 92.8675 | 265.0789 | 170.8848 | 250.1014 | 263.6716 | 236.157
724.0354 | 229.6578 | 93.0139 | 266.4925 | 171.2164 | 249.6852 | 263.5661 | 236.8478
725.0354 | 229.2883 | 93.0499 | 265.4636 | 171.1903 | 250.3479 | 264.8432 | 236.4691
726.0354 | 229.91 | 93.2066 | 265.5378 | 171.5072 | 250.193 | 264.4068 | 235.8785
727.0354 | 230.6347 | 93.1851 | 265.69 | 171.7384 | 249.6133 | 264.6452 | 235.1012
728.0354 | 230.2875 | 93.1748 | 265.8695 | 172.3344 | 250.6471 | 264.4306 | 236.8977
729.0354 | 229.5869 | 93.1897 | 265.3187 | 172.5655 | 252.2287 | 265.7243 | 238.3701
730.0354 | 228.6767 | 93.2662 | 265.2224 | 173.6878 | 252.3701 | 264.6144 | 237.7307
731.0354 | 228.1633 | 93.4367 | 265.1726 | 174.0438 | 251.8096 | 263.4151 | 236.6234
732.0354 | 228.0704 | 93.7487 | 265.63 | 173.8328 | 250.9169 | 262.6553 | 235.3632
733.0354 | 228.6566 | 93.6906 | 265.5703 | 174.0827 | 250.6728 | 263.001 | 235.7076
734.0354 | 229.5924 | 93.6327 | 266.0022 | 174.6038 | 250.1634 | 262.8062 | 235.6296
735.0354 | 229.3634 | 93.9845 | 266.0273 | 174.581 | 251.5809 | 263.3826 | 237.0301
736.0354 | 230.2574 | 93.9663 | 265.9185 | 174.7942 | 253.2078 | 265.936 | 239.321
737.0354 | 230.0539 | 94.2231 | 266.1573 | 175.0396 | 252.3758 | 266.6933 | 240.7792
738.0354 | 229.417 | 94.4224 | 266.015 | 175.3464 | 252.151 | 265.9529 | 240.7458
739.0354 | 229.0876 | 94.4071 | 266.1649 | 175.5825 | 251.5562 | 264.9317 | 240.562
740.0354 | 228.6898 | 94.3613 | 266.2384 | 176.0461 | 251.2966 | 264.4349 | 239.5274
741.0354 | 228.8029 | 94.5265 | 265.9103 | 177.0163 | 251.6216 | 264.1231 | 238.3078
742.0354 | 229.0521 | 94.5329 | 265.8916 | 177.0707 | 252.1276 | 264.3497 | 238.2731
743.0354 | 228.8806 | 94.7098 | 266.3562 | 177.881 | 252.5321 | 263.8699 | 237.6081
744.0354 | 229.2576 | 94.7524 | 266.1019 | 177.7264 | 252.6939 | 263.8786 | 237.1974
745.0354 | 228.9834 | 94.9262 | 265.8978 | 177.5678 | 252.2729 | 263.7768 | 237.0405
746.0354 | 229.1774 | 95.0087 | 265.8804 | 178.1119 | 251.5625 | 263.3228 | 236.0337
747.0354 | 228.8846 | 94.9187 | 265.8578 | 178.0297 | 251.521 | 262.3754 | 234.9676
748.0354 | 228.5371 | 95.0839 | 266.2267 | 178.5703 | 250.9808 | 261.2913 | 233.9784
749.0354 | 229.5978 | 95.37 | 266.4372 | 178.9395 | 251.8621 | 261.6576 | 233.6211
750.0354 | 229.9081 | 95.302 | 266.8806 | 179.2167 | 251.7992 | 263.1656 | 234.7877
751.0354 | 230.6474 | 95.2281 | 267.4243 | 179.1246 | 252.1717 | 265.4154 | 237.2098
752.0354 | 231.4226 | 95.5074 | 267.9594 | 179.4383 | 251.6676 | 266.8322 | 239.4865
753.0354 | 231.7873 | 95.5972 | 267.5487 | 180.0508 | 250.6834 | 268.6319 | 241.4231
754.0354 | 231.4289 | 95.5148 | 267.1213 | 180.7526 | 250.8958 | 269.3334 | 242.0551
755.0354 | 230.7786 | 95.593 | 267.3824 | 180.5718 | 251.0025 | 269.7332 | 242.2851
756.0354 | 230.6391 | 95.7478 | 267.3435 | 181.0623 | 250.9474 | 269.1019 | 243.0781
757.0354 | 230.8058 | 95.842 | 267.7027 | 181.4414 | 251.8185 | 269.6046 | 243.4829
758.0354 | 231.1549 | 95.9977 | 267.3294 | 181.997 | 250.8594 | 267.8459 | 242.7001
759.0354 | 230.699 | 96.2634 | 267.7805 | 181.5893 | 250.0977 | 266.7486 | 241.6674
760.0354 | 231.9251 | 96.2533 | 268.1145 | 182.0656 | 248.6716 | 265.7295 | 240.4838
761.0354 | 232.8705 | 96.323 | 269.6409 | 182.1402 | 248.687 | 264.2419 | 239.9856
762.0354 | 233.9807 | 96.4369 | 269.456 | 182.3111 | 248.4829 | 263.7055 | 238.9884
763.0354 | 233.9389 | 96.8526 | 269.4104 | 183.8659 | 247.1911 | 262.2213 | 237.8951
764.0354 | 233.7325 | 97.0642 | 269.3131 | 183.3762 | 247.3488 | 261.5884 | 236.6902
765.0354 | 234.1442 | 97.1475 | 269.5319 | 183.5147 | 246.5012 | 261.3433 | 235.5888
766.0354 | 235.2568 | 97.2605 | 269.0531 | 183.8777 | 247.3186 | 262.0071 | 234.9959
767.0354 | 234.4056 | 97.3405 | 269.0141 | 184.5693 | 245.914 | 260.3332 | 234.0933
768.0354 | 233.7767 | 97.2702 | 269.269 | 184.8288 | 246.723 | 259.154 | 233.086
769.0354 | 234.7096 | 97.4799 | 269.6875 | 184.8272 | 247.7881 | 257.7986 | 232.0318
770.0354 | 235.6459 | 97.6492 | 270.3062 | 185.7404 | 247.4546 | 257.3788 | 230.9381
771.0354 | 236.7132 | 97.8144 | 269.9156 | 185.7166 | 248.6085 | 258.216 | 230.8464
772.0354 | 236.8611 | 97.9383 | 270.2998 | 185.7214 | 248.3231 | 258.5603 | 231.3509
773.0354 | 237.1136 | 98.0853 | 270.1785 | 186.0337 | 248.889 | 259.1518 | 231.2684
774.0354 | 236.512 | 98.0634 | 270.4375 | 186.087 | 250.3528 | 259.4061 | 231.8293
775.0354 | 236.8767 | 98.0696 | 271.1037 | 186.8056 | 250.2993 | 258.0939 | 231.6874
776.0354 | 237.141 | 98.1348 | 270.6457 | 187.7457 | 250.5457 | 257.802 | 231.8171
777.0354 | 237.7489 | 98.4083 | 271.1113 | 187.7966 | 251.0813 | 258.6505 | 231.3991
778.0354 | 236.6549 | 98.5324 | 270.8539 | 187.9022 | 250.3721 | 257.1518 | 231.2113
779.0354 | 236.0163 | 98.5609 | 271.3348 | 188.3358 | 250.0388 | 256.8426 | 231.4286
780.0354 | 236.1095 | 98.6717 | 271.6067 | 188.5216 | 249.4802 | 256.4081 | 231.0027
781.0354 | 235.9795 | 98.7674 | 272.0793 | 188.4891 | 249.1117 | 255.3168 | 230.4292
782.0354 | 236.3001 | 98.6784 | 272.1047 | 188.5168 | 249.1052 | 255.3799 | 230.6007
783.0354 | 235.8629 | 98.8885 | 271.9816 | 188.4919 | 248.7025 | 256.6081 | 231.4507
784.0354 | 235.1612 | 98.7967 | 271.713 | 188.7818 | 248.1821 | 258.0263 | 232.6277
785.0354 | 234.9081 | 98.7405 | 271.3786 | 189.0574 | 248.2075 | 259.0395 | 232.928
786.0354 | 235.0439 | 98.8223 | 271.8357 | 189.4293 | 248.1391 | 259.2776 | 232.4225
787.0354 | 234.4862 | 98.867 | 272.1239 | 189.6336 | 248.4258 | 260.5052 | 233.4185
788.0354 | 233.8588 | 99.1491 | 271.7696 | 190.1253 | 248.174 | 259.6371 | 233.8283
789.0354 | 233.6904 | 99.2092 | 271.9547 | 190.6707 | 248.3921 | 259.9914 | 234.5723
790.0354 | 232.9875 | 99.2302 | 271.8179 | 191.2265 | 247.2957 | 259.6055 | 235.7723
791.0354 | 232.1475 | 99.4022 | 272.1568 | 191.4716 | 247.9296 | 261.2417 | 236.5713
792.0354 | 232.231 | 99.603 | 272.2595 | 191.9975 | 247.7823 | 261.7873 | 237.4895
793.0354 | 232.2672 | 99.5791 | 272.1509 | 191.5591 | 248.6912 | 262.2517 | 237.4173
794.0354 | 232.0287 | 99.881 | 272.3895 | 191.9286 | 247.8259 | 262.2746 | 237.3881
795.0354 | 232.7946 | 99.6767 | 272.5319 | 191.9231 | 247.5695 | 262.668 | 237.1353
796.0354 | 233.3249 | 99.6519 | 272.3708 | 192.4832 | 247.5666 | 263.1618 | 237.2693
797.0354 | 233.063 | 99.9837 | 272.1477 | 192.5337 | 248.6227 | 261.6742 | 236.9153
798.0354 | 232.5481 | 100.1718 | 272.6529 | 192.985 | 248.1002 | 261.7045 | 236.7518
799.0354 | 232.8105 | 100.2212 | 272.94 | 192.9996 | 249.7366 | 262.1662 | 236.6129
800.0354 | 231.946 | 100.1332 | 272.7015 | 193.1348 | 249.9393 | 261.7982 | 237.1528
801.0354 | 232.4476 | 100.1938 | 272.8249 | 193.3212 | 249.9803 | 262.7435 | 237.009
802.0354 | 232.5833 | 100.1364 | 272.5224 | 193.5052 | 249.5322 | 262.7033 | 237.1252
803.0354 | 232.6519 | 100.3219 | 272.5422 | 194.0887 | 249.4309 | 262.8389 | 237.5138
804.0354 | 232.0739 | 100.4278 | 272.886 | 194.3155 | 249.2419 | 262.5522 | 236.8902
805.0354 | 231.9582 | 100.731 | 272.9908 | 194.7027 | 250.1324 | 262.9599 | 237.0765
806.0354 | 231.7015 | 100.8797 | 273.4352 | 194.5178 | 249.3901 | 262.842 | 237.2252
807.0354 | 231.5266 | 100.7474 | 273.5767 | 194.5177 | 249.7774 | 263.2963 | 239.0952
808.0354 | 232.0212 | 100.7835 | 273.9213 | 194.6966 | 250.7903 | 264.6606 | 239.7259
809.0354 | 232.1485 | 100.8599 | 273.5612 | 195.0008 | 249.6656 | 265.1252 | 241.0074
810.0354 | 233.0715 | 101.0709 | 273.5661 | 195.8174 | 249.8978 | 265.9187 | 240.815
811.0354 | 232.9751 | 101.1549 | 273.7817 | 195.5298 | 251.0909 | 265.5447 | 240.957
812.0354 | 232.8225 | 101.3468 | 274.1006 | 195.834 | 251.0489 | 265.0238 | 241.2201
813.0354 | 233.6884 | 101.4893 | 273.635 | 195.8557 | 249.7662 | 265.636 | 241.1545
814.0354 | 233.3761 | 101.6128 | 273.6741 | 196.0501 | 249.4128 | 265.086 | 240.6112
815.0354 | 233.2866 | 101.6691 | 273.6257 | 196.3573 | 248.9711 | 264.681 | 239.7103
816.0354 | 232.6143 | 101.7515 | 273.5403 | 196.4423 | 248.6636 | 263.7555 | 238.5714
817.0354 | 232.0377 | 102.0062 | 273.7595 | 196.8844 | 248.364 | 263.533 | 238.2804
818.0354 | 232.5023 | 101.9398 | 274.5937 | 198.3167 | 249.8027 | 264.0567 | 238.0363
819.0354 | 232.4517 | 102.1157 | 275.023 | 198.9803 | 249.5816 | 263.8954 | 239.1227
820.0354 | 232.9 | 102.2138 | 274.8136 | 198.2611 | 249.7145 | 263.928 | 238.5878
821.0354 | 232.5274 | 102.2102 | 274.548 | 198.1784 | 249.383 | 264.5954 | 240.1493
822.0354 | 231.7181 | 102.1371 | 274.571 | 199.2683 | 251.2766 | 265.0103 | 241.0107
823.0354 | 231.5262 | 102.2275 | 274.3549 | 199.5254 | 252.8731 | 264.183 | 240.4016
824.0354 | 230.8251 | 102.1798 | 274.3589 | 199.7639 | 253.1197 | 263.4279 | 240.7812
825.0354 | 230.1825 | 102.2529 | 274.7078 | 200.2233 | 253.5438 | 263.653 | 239.5939
826.0354 | 230.4181 | 102.5825 | 274.4513 | 200.4491 | 255.0923 | 264.0419 | 239.9127
827.0354 | 229.9634 | 102.6841 | 274.8045 | 201.1027 | 256.7535 | 264.4911 | 241.0098
828.0354 | 229.554 | 102.9514 | 274.6407 | 201.2918 | 256.9773 | 264.1497 | 241.8754
829.0354 | 229.7224 | 103.0251 | 274.538 | 201.4566 | 256.1085 | 263.2957 | 241.5539
830.0354 | 229.3486 | 103.0526 | 274.9502 | 201.398 | 256.2119 | 263.114 | 241.4224
831.0354 | 230.029 | 103.0463 | 274.944 | 201.5298 | 254.8591 | 263.0618 | 241.6793
832.0354 | 230.0927 | 103.193 | 275.1407 | 201.779 | 254.4116 | 262.5845 | 240.8727
833.0354 | 230.5766 | 103.2127 | 274.9669 | 201.8906 | 253.7609 | 261.5417 | 240.135
834.0354 | 230.5344 | 103.4672 | 274.8665 | 202.0038 | 253.3012 | 261.4972 | 239.1295
835.0354 | 229.545 | 103.6555 | 274.9116 | 202.0608 | 251.8519 | 260.3436 | 238.0153
836.0354 | 229.2214 | 103.7009 | 274.8978 | 202.2902 | 250.8608 | 259.0634 | 237.4343
837.0354 | 228.6152 | 103.7685 | 274.6796 | 202.3043 | 250.1756 | 258.4542 | 236.3446
838.0354 | 227.9488 | 103.7794 | 274.8917 | 202.6089 | 249.679 | 258.1971 | 235.8818
839.0354 | 227.1009 | 103.836 | 274.7905 | 203.2566 | 250.3871 | 259.0012 | 236.1403
840.0354 | 226.5242 | 103.9387 | 275.1708 | 203.4948 | 249.579 | 257.9721 | 235.1078
841.0354 | 226.792 | 103.7811 | 274.9595 | 203.4049 | 249.0298 | 256.996 | 234.1919
842.0354 | 227.0464 | 103.7983 | 275.6356 | 203.9802 | 248.8294 | 256.9164 | 233.0322
843.0354 | 227.0506 | 103.9047 | 275.2587 | 204.0873 | 249.3137 | 257.7857 | 234.0309
844.0354 | 227.6841 | 104.0676 | 275.4842 | 205.2509 | 248.7462 | 257.6841 | 234.5807
845.0354 | 227.8052 | 104.1649 | 275.6712 | 205.5654 | 249.8812 | 257.7365 | 233.8435
846.0354 | 228.4327 | 104.4441 | 275.5176 | 205.6088 | 249.1894 | 257.3757 | 233.4095
847.0354 | 227.647 | 104.2847 | 275.3102 | 206.0439 | 249.2917 | 257.8704 | 232.7787
848.0354 | 227.7451 | 104.1905 | 275.3096 | 205.8057 | 248.658 | 259.0578 | 234.0967
849.0354 | 227.4485 | 104.6055 | 275.2828 | 205.8397 | 248.1891 | 258.618 | 233.4704
850.0354 | 227.4944 | 104.5316 | 275.1731 | 206.1992 | 247.6193 | 259.7961 | 233.218
851.0354 | 227.4007 | 104.3922 | 275.5467 | 206.2511 | 247.7012 | 259.8826 | 233.6192
852.0354 | 228.002 | 104.5651 | 275.6578 | 206.3581 | 247.8101 | 259.8917 | 233.5756
853.0354 | 228.8054 | 104.8186 | 275.7018 | 206.7322 | 247.7218 | 260.221 | 233.8529
854.0354 | 228.7494 | 104.7403 | 275.3923 | 207.0423 | 247.8014 | 261.1059 | 233.6206
855.0354 | 229.8033 | 104.9785 | 276.247 | 207.5979 | 247.5785 | 261.4387 | 233.8847
856.0354 | 229.7385 | 105.1278 | 276.5347 | 207.5904 | 248.904 | 261.7704 | 234.6303
857.0354 | 229.9467 | 105.3765 | 276.1476 | 208.1516 | 250.2388 | 261.9401 | 234.6898
858.0354 | 229.179 | 105.5297 | 275.9169 | 208.2831 | 251.2397 | 261.2421 | 234.4455
859.0354 | 229.372 | 105.4486 | 276.0204 | 209.3726 | 251.1317 | 261.0992 | 235.4019
860.0354 | 229.5035 | 105.6169 | 275.9744 | 209.7275 | 250.62 | 259.9562 | 234.7482
861.0354 | 229.618 | 105.7476 | 276.3314 | 209.2398 | 250.5683 | 259.799 | 234.0228
862.0354 | 229.1627 | 105.6502 | 276.3984 | 209.2479 | 250.2748 | 259.6237 | 233.9465
863.0354 | 229.0377 | 105.9429 | 276.4769 | 209.7072 | 249.2661 | 259.1777 | 234.004
864.0354 | 230.1634 | 105.9969 | 276.3903 | 210.4837 | 249.3844 | 259.4697 | 234.5166
865.0354 | 230.9577 | 106.1377 | 277.6805 | 209.9095 | 249.3991 | 259.4171 | 234.7783
866.0354 | 232.6569 | 106.2791 | 279.2822 | 210.049 | 249.5653 | 260.3242 | 235.2198
867.0354 | 234.4841 | 106.5348 | 279.1465 | 210.0841 | 248.4026 | 259.6414 | 234.5359
868.0354 | 235.119 | 106.7449 | 279.8088 | 210.4706 | 247.5419 | 259.5529 | 234.5978
869.0354 | 234.4473 | 106.7629 | 280.5646 | 210.5507 | 247.3965 | 259.5636 | 234.7844
870.0354 | 235.2255 | 106.9339 | 279.9071 | 211.1549 | 247.6096 | 260.7542 | 235.5535
871.0354 | 235.2322 | 106.9461 | 280.6427 | 211.5826 | 247.9162 | 261.3294 | 235.2525
872.0354 | 235.8099 | 106.8247 | 279.1703 | 211.921 | 249.0857 | 262.3142 | 236.0192
873.0354 | 235.4645 | 106.9774 | 278.8881 | 211.7602 | 249.0221 | 261.8105 | 236.152
874.0354 | 234.5672 | 107.0437 | 278.9773 | 211.7869 | 250.0937 | 262.7919 | 236.8167
875.0354 | 234.2933 | 107.2977 | 278.6473 | 211.8065 | 249.7366 | 262.6942 | 236.6194
876.0354 | 233.2584 | 107.3492 | 278.8367 | 212.6128 | 248.8858 | 261.7267 | 235.8696
877.0354 | 232.8306 | 107.1976 | 279.0858 | 212.2677 | 249.3752 | 261.0679 | 235.8364
878.0354 | 232.9589 | 107.1721 | 279.4892 | 212.8292 | 248.0313 | 260.5895 | 236.4532
879.0354 | 233.2727 | 107.4167 | 279.3628 | 213.097 | 247.8281 | 260.2891 | 236.851
880.0354 | 233.1813 | 107.5083 | 280.2835 | 212.9873 | 247.2996 | 260.0671 | 237.4244
881.0354 | 232.7862 | 107.4194 | 280.0568 | 212.9742 | 248.222 | 260.2898 | 237.8157
882.0354 | 232.325 | 107.5651 | 280.9245 | 213.1005 | 247.276 | 260.7137 | 238.9369
883.0354 | 231.3097 | 107.8568 | 280.5566 | 213.6082 | 247.1865 | 261.0037 | 238.9058
884.0354 | 230.3641 | 107.9731 | 280.6942 | 213.7583 | 246.6952 | 260.4377 | 238.755
885.0354 | 230.6788 | 108.1716 | 281.5607 | 213.777 | 245.7584 | 260.7437 | 238.8065
886.0354 | 231.522 | 108.0602 | 281.8257 | 213.9184 | 245.6215 | 260.054 | 238.8574
887.0354 | 230.9835 | 108.0945 | 281.4487 | 214.1003 | 245.2851 | 259.7542 | 238.5166
888.0354 | 231.6909 | 108.2522 | 281.2354 | 214.6792 | 244.3366 | 259.1279 | 238.485
889.0354 | 231.8795 | 108.2011 | 282.0259 | 215.0496 | 243.6011 | 259.2759 | 238.1626
890.0354 | 231.35 | 108.3907 | 282.5009 | 215.2759 | 244.2523 | 259.1913 | 236.9777
891.0354 | 233.0933 | 108.3715 | 282.7639 | 214.8088 | 244.2633 | 258.5488 | 235.5499
892.0354 | 233.3151 | 108.407 | 283.3205 | 214.8133 | 243.4986 | 258.8333 | 235.6672
893.0354 | 234.1159 | 108.6054 | 284.2546 | 215.2238 | 243.2926 | 257.8256 | 235.7533
894.0354 | 234.7887 | 108.674 | 283.7247 | 215.4481 | 242.6997 | 257.1956 | 235.488
895.0354 | 234.7403 | 108.9074 | 283.7506 | 215.7297 | 242.7991 | 256.7471 | 234.7163
896.0354 | 234.2856 | 109.0681 | 283.4794 | 215.9107 | 241.966 | 255.5884 | 234.5536
897.0354 | 233.731 | 109.2555 | 283.6736 | 216.3139 | 241.6761 | 254.7688 | 234.9243
898.0354 | 233.2134 | 109.4013 | 283.7083 | 216.5027 | 241.8226 | 254.8371 | 236.3486
899.0354 | 232.496 | 109.3135 | 283.8358 | 216.4011 | 240.3661 | 255.3997 | 237.1807
900.0354 | 232.7943 | 109.2111 | 284.3642 | 216.964 | 240.2684 | 256.969 | 239.289
901.0354 | 232.8174 | 109.525 | 284.1329 | 217.1763 | 240.9491 | 257.704 | 238.9496
902.0354 | 233.1723 | 109.4753 | 284.2096 | 217.2059 | 241.6292 | 257.952 | 238.5367
903.0354 | 233.6358 | 109.4007 | 284.0988 | 217.5304 | 242.2816 | 258.2961 | 238.5709
904.0354 | 233.5828 | 109.468 | 284.3352 | 217.2597 | 241.8688 | 259.9364 | 240.4431
905.0354 | 234.1852 | 109.5389 | 284.3685 | 217.5989 | 243.1455 | 260.9636 | 240.192
906.0354 | 234.1168 | 109.9437 | 284.4305 | 218.2328 | 243.3791 | 261.8933 | 240.8836
907.0354 | 235.2572 | 110.0242 | 284.7868 | 218.4133 | 244.453 | 262.9685 | 240.5929
908.0354 | 236.3069 | 110.1642 | 284.661 | 219.161 | 245.745 | 264.9626 | 242.8123
909.0354 | 237.3585 | 110.31 | 285.2865 | 219.2243 | 248.7262 | 267.1838 | 244.7108
910.0354 | 237.6502 | 110.4093 | 285.6039 | 219.1988 | 251.802 | 267.6697 | 245.8993
911.0354 | 238.4601 | 110.5819 | 285.5302 | 219.4173 | 253.9432 | 267.9764 | 246.8484
912.0354 | 239.0367 | 110.4411 | 286.5275 | 219.9655 | 255.2461 | 268.367 | 247.1912
913.0354 | 240.8355 | 110.6421 | 286.4461 | 219.7094 | 257.6089 | 269.8033 | 248.8509
914.0354 | 241.7611 | 110.7601 | 286.6251 | 220.0835 | 259.3198 | 270.245 | 248.972
915.0354 | 243.7575 | 110.8119 | 286.7268 | 220.4193 | 260.2405 | 271.8351 | 250.1624
916.0354 | 244.5565 | 111.0392 | 287.1687 | 220.2835 | 262.2142 | 273.1371 | 251.1392
917.0354 | 244.9157 | 110.949 | 287.0369 | 221.535 | 263.1488 | 273.9347 | 251.5289
918.0354 | 245.1893 | 110.9683 | 286.9023 | 221.198 | 264.4641 | 274.8757 | 252.0307
919.0354 | 245.8427 | 111.0184 | 287.0443 | 221.1467 | 264.0842 | 275.4826 | 253.2125
920.0354 | 246.404 | 111.0907 | 287.9052 | 221.2947 | 264.2035 | 276.7419 | 253.248
921.0354 | 247.8398 | 111.0666 | 287.9567 | 222.0524 | 263.8723 | 279.0534 | 254.4506
922.0354 | 248.8904 | 111.3209 | 288.1246 | 222.7795 | 264.927 | 279.954 | 255.3296
923.0354 | 249.3147 | 111.4568 | 287.7195 | 222.6939 | 266.4054 | 281.3408 | 255.1487
924.0354 | 249.3032 | 111.3642 | 288.0495 | 222.6555 | 267.1983 | 280.8857 | 254.6659
925.0354 | 249.6635 | 111.3752 | 287.7563 | 223.2815 | 267.6989 | 281.2088 | 253.7813
926.0354 | 249.9136 | 111.6629 | 288.6427 | 222.9 | 268.3965 | 281.2563 | 254.0752
927.0354 | 250.1458 | 111.74 | 288.8362 | 223.132 | 268.6313 | 281.5447 | 254.5006
928.0354 | 250.9243 | 111.9463 | 289.4441 | 223.6163 | 268.2583 | 282.5494 | 255.0601
929.0354 | 251.9862 | 111.9987 | 289.3631 | 224.4789 | 270.5318 | 284.1956 | 257.8103
930.0354 | 252.5183 | 112.2507 | 289.2967 | 224.7515 | 271.729 | 285.0592 | 257.8572
931.0354 | 253.6714 | 112.2102 | 290.3838 | 224.673 | 272.266 | 285.6277 | 259.5289
932.0354 | 255.979 | 112.437 | 292.9131 | 224.8164 | 271.2413 | 286.6032 | 259.6454
933.0354 | 257.8807 | 112.323 | 292.6869 | 224.712 | 271.5626 | 287.9284 | 260.4307
934.0354 | 258.3686 | 112.3604 | 292.177 | 225.069 | 271.7975 | 287.376 | 260.5745
935.0354 | 258.7496 | 112.6117 | 291.4551 | 225.3435 | 271.4429 | 287.1128 | 260.6774
936.0354 | 258.9687 | 112.6778 | 291.3575 | 226.5946 | 271.8968 | 286.8767 | 260.7455
937.0354 | 258.8932 | 113.1067 | 291.4214 | 227.309 | 275.7612 | 288.8994 | 262.1105
938.0354 | 258.6659 | 113.2462 | 291.7103 | 226.6099 | 277.9934 | 290.9237 | 263.6722
939.0354 | 258.6083 | 113.3896 | 291.9193 | 226.5804 | 277.2387 | 291.5205 | 265.0219
940.0354 | 259.7186 | 113.2409 | 292.0048 | 227.1439 | 277.7334 | 292.0077 | 265.7727
941.0354 | 258.9288 | 113.3711 | 292.2373 | 227.225 | 277.7254 | 292.7962 | 265.8743
942.0354 | 259.1075 | 113.5899 | 292.1172 | 227.3564 | 277.3298 | 292.6213 | 266.2139
943.0354 | 258.9441 | 113.6137 | 292.6473 | 227.8148 | 277.0179 | 292.4616 | 265.897
944.0354 | 259.1082 | 113.8022 | 293.3113 | 227.7101 | 276.3123 | 293.8292 | 267.1703
945.0354 | 259.9287 | 113.9891 | 293.3782 | 228.5253 | 274.9884 | 294.7373 | 267.3673
946.0354 | 259.5242 | 114.0597 | 292.8569 | 229.4552 | 277.3069 | 295.6932 | 266.9531
947.0354 | 259.6207 | 114.2075 | 292.9175 | 229.8787 | 277.3393 | 294.9164 | 265.4392
948.0354 | 259.0227 | 114.2923 | 293.1772 | 229.7747 | 277.0511 | 293.5502 | 264.6332
949.0354 | 258.6315 | 114.304 | 293.6475 | 229.605 | 276.8491 | 293.4798 | 263.4106
950.0354 | 259.0074 | 114.5873 | 293.9277 | 230.1507 | 277.5642 | 294.1459 | 263.1711
951.0354 | 259.1921 | 114.8662 | 293.9945 | 231.2826 | 277.7125 | 295.2017 | 263.0519
952.0354 | 259.2878 | 115.0066 | 294.182 | 231.7305 | 278.0878 | 294.4086 | 262.7845
953.0354 | 260.0362 | 115.0121 | 294.1676 | 232.5023 | 278.5672 | 293.3637 | 262.7838
954.0354 | 259.3273 | 115.1278 | 294.1564 | 232.2664 | 278.255 | 293.8288 | 262.2539
955.0354 | 258.7732 | 115.2209 | 294.4142 | 232.3093 | 278.0063 | 292.7927 | 262.8328
956.0354 | 257.959 | 114.9992 | 294.4452 | 232.2201 | 278.9173 | 292.2143 | 262.3673
957.0354 | 257.4665 | 115.3156 | 294.173 | 232.2049 | 280.873 | 292.7524 | 263.248
958.0354 | 256.304 | 115.5593 | 294.4508 | 232.4405 | 279.6072 | 291.8271 | 261.8987
959.0354 | 255.8988 | 115.6903 | 294.4258 | 232.6154 | 278.8539 | 291.7666 | 261.6716
960.0354 | 255.6535 | 115.8772 | 294.6333 | 232.9024 | 278.1761 | 291.5284 | 261.3413
961.0354 | 255.3282 | 115.9015 | 294.7276 | 233.6433 | 277.3387 | 291.4514 | 260.8703
962.0354 | 255.633 | 115.8121 | 294.7806 | 234.2356 | 277.6951 | 291.0134 | 259.5748
963.0354 | 255.1838 | 115.6705 | 294.908 | 234.5348 | 277.08 | 290.4948 | 259.3042
964.0354 | 255.4829 | 115.7701 | 295.6652 | 234.5271 | 279.4108 | 291.5311 | 259.8316
965.0354 | 255.0136 | 116.1991 | 295.7956 | 235.1747 | 280.5347 | 292.8215 | 260.3928
966.0354 | 254.4342 | 116.2994 | 295.3513 | 235.8663 | 280.9188 | 293.2917 | 260.6671
967.0354 | 253.899 | 116.2052 | 295.2053 | 236.1131 | 281.4775 | 293.9394 | 261.4931
968.0354 | 253.0327 | 116.1524 | 295.4388 | 236.7523 | 282.1288 | 293.8857 | 260.6258
969.0354 | 252.8355 | 116.074 | 295.6254 | 236.9943 | 282.2954 | 293.4165 | 260.9572
970.0198 | 253.6401 | 116.1635 | 296.0336 | 237.2252 | 281.6586 | 292.9462 | 260.4394
971.0354 | 253.9587 | 116.6118 | 296.3875 | 237.827 | 282.9965 | 293.5568 | 261.6046
972.0354 | 255.4717 | 116.5437 | 296.1235 | 237.8879 | 283.7751 | 295.291 | 263.6599
973.0354 | 255.9969 | 116.6994 | 296.0742 | 239.1567 | 285.0521 | 297.0688 | 265.6342
974.0354 | 255.7641 | 117.0115 | 296.2789 | 239.2678 | 285.1024 | 297.2807 | 265.6942
975.0354 | 256.564 | 117.1917 | 296.9894 | 239.771 | 285.6617 | 297.2904 | 267.6205
976.0354 | 256.5932 | 117.271 | 296.857 | 240.0016 | 284.094 | 296.5589 | 266.784
977.0354 | 257.6423 | 117.3939 | 296.9364 | 240.5269 | 285.2415 | 297.0871 | 267.1098
978.0354 | 258.1241 | 117.5647 | 297.7049 | 241.6776 | 286.9939 | 297.6331 | 268.3592
979.0354 | 258.3375 | 117.6711 | 297.216 | 241.6226 | 287.456 | 296.9586 | 267.0535
980.0354 | 260.8306 | 117.8621 | 298.0028 | 242.5639 | 288.1693 | 297.042 | 266.749
981.0354 | 261.0303 | 117.8658 | 297.7761 | 242.4434 | 287.8483 | 295.7059 | 265.0982
982.0354 | 262.2071 | 117.9666 | 298.0862 | 242.3797 | 287.1617 | 296.8459 | 264.2259
983.0354 | 262.8548 | 117.9841 | 298.8078 | 242.9667 | 287.4324 | 298.1265 | 264.2211
984.0354 | 263.8683 | 118.2856 | 301.0404 | 242.9368 | 289.0884 | 299.6903 | 264.7091
985.0354 | 265.0351 | 118.5286 | 302.3458 | 243.4151 | 289.1126 | 299.5793 | 266.0257
986.0354 | 267.1515 | 118.4591 | 301.8421 | 243.3701 | 289.6979 | 300.385 | 265.699
987.0354 | 267.8732 | 118.6453 | 300.5614 | 244.1735 | 289.9507 | 301.8879 | 266.5612
988.0354 | 269.3731 | 118.7576 | 300.7745 | 244.4815 | 289.7328 | 303.0619 | 266.7779
989.0354 | 270.5044 | 118.6342 | 300.5729 | 244.5105 | 290.1565 | 303.0215 | 267.1731
990.0354 | 270.8802 | 118.7299 | 300.2687 | 244.8131 | 291.181 | 303.6247 | 267.4976
991.0354 | 270.7627 | 118.7962 | 300.6003 | 245.6931 | 292.1873 | 303.4376 | 266.903
992.0354 | 270.5904 | 118.9219 | 301.7974 | 245.6812 | 293.2566 | 305.221 | 269.5781
993.0354 | 271.0694 | 118.9251 | 301.6971 | 246.0276 | 291.958 | 305.8688 | 269.8688
994.0354 | 271.2486 | 119.2565 | 302.4722 | 246.5063 | 291.7787 | 306.1 | 270.3457
995.0354 | 271.4033 | 119.3415 | 302.0117 | 246.6812 | 291.1724 | 306.6222 | 270.3468
996.0354 | 271.3421 | 119.2669 | 301.6886 | 247.0785 | 290.7356 | 306.8847 | 270.155
997.0354 | 271.5484 | 119.5617 | 302.1594 | 247.2451 | 290.1715 | 307.1293 | 270.2883
998.0354 | 271.9174 | 119.848 | 302.2654 | 248.4695 | 290.154 | 307.0541 | 271.657
999.0354 | 271.9361 | 119.84 | 302.1217 | 249.848 | 291.1888 | 308.0117 | 272.1655
1000.0354 | 272.1829 | 119.8934 | 302.7892 | 249.6728 | 291.9602 | 307.2851 | 272.0171
1001.0354 | 271.4892 | 119.7636 | 302.7913 | 249.4785 | 290.7685 | 306.8472 | 271.3505
1002.0354 | 271.1785 | 119.8208 | 303.2291 | 250.1656 | 291.7087 | 306.7976 | 272.0974
1003.0354 | 271.4581 | 120.2123 | 302.7959 | 250.5784 | 293.1201 | 307.2289 | 272.998
1004.0354 | 271.6793 | 120.3596 | 303.7956 | 250.1529 | 293.4934 | 307.3122 | 273.1389
1005.0354 | 271.8557 | 120.3979 | 304.2654 | 250.8012 | 294.4406 | 309.0257 | 275.6505
1006.0354 | 271.6237 | 120.6133 | 303.6657 | 251.8403 | 294.1177 | 309.1443 | 274.6776
1007.0354 | 271.8117 | 120.5964 | 304.1657 | 251.8676 | 296.6047 | 311.4623 | 277.0207
1008.0354 | 271.9645 | 120.837 | 304.2807 | 252.5153 | 297.362 | 310.7733 | 277.4119
1009.0354 | 271.9108 | 120.8451 | 304.3583 | 253.4654 | 298.6038 | 310.5747 | 277.9933
1010.0354 | 271.1202 | 120.9285 | 304.0609 | 254.1224 | 298.8611 | 310.5823 | 277.69
1011.0354 | 269.7598 | 121.0214 | 304.414 | 253.9515 | 298.7235 | 309.4117 | 277.6286
1012.0198 | 268.9043 | 121.0121 | 304.4625 | 254.2563 | 297.2761 | 308.5167 | 276.8385
1013.0354 | 268.338 | 121.2853 | 304.2464 | 254.8435 | 297.1067 | 309.1256 | 277.6101
1014.0354 | 268.2609 | 121.3007 | 304.4195 | 254.8368 | 296.2975 | 308.9412 | 276.7436
1015.0354 | 267.8561 | 121.4267 | 304.9329 | 254.5693 | 296.4032 | 308.9454 | 277.1677
1016.0354 | 268.0773 | 121.4645 | 305.0727 | 255.8436 | 295.7026 | 308.124 | 277.1079
1017.0354 | 269.3714 | 121.4106 | 305.469 | 256.4416 | 295.4191 | 306.9733 | 276.5142
1018.0354 | 268.493 | 121.7694 | 305.1835 | 256.2562 | 296.3715 | 305.9097 | 276.1184
1019.0354 | 267.7899 | 121.9371 | 304.8731 | 256.6374 | 296.904 | 305.8529 | 276.1085
1020.0354 | 266.8005 | 121.8923 | 305.5616 | 257.4691 | 297.3593 | 304.3216 | 274.5212
1021.0354 | 266.3375 | 121.9102 | 305.4097 | 258.0503 | 297.5189 | 304.4723 | 275.6394
1022.0354 | 265.8735 | 122.1127 | 305.5722 | 257.9588 | 298.4482 | 304.997 | 275.7182
1023.0354 | 265.1706 | 122.2737 | 306.1856 | 258.3821 | 297.5839 | 306.1637 | 274.8438
1024.0354 | 265.6762 | 122.0963 | 306.74 | 258.3772 | 297.6999 | 306.2044 | 274.7733
1025.0354 | 265.914 | 122.1328 | 306.0893 | 258.6276 | 297.2022 | 306.28 | 273.7652
1026.0354 | 265.6787 | 122.195 | 306.7365 | 259.6889 | 297.0773 | 307.0199 | 274.377
1027.0354 | 267.0352 | 122.5738 | 306.6627 | 260.0532 | 297.1635 | 307.2907 | 274.9478
1028.0354 | 266.7693 | 122.6102 | 306.3367 | 260.0338 | 296.2349 | 306.6438 | 274.1582
1029.0354 | 266.5825 | 122.8757 | 306.4227 | 261.5272 | 296.5139 | 306.5667 | 273.392
1030.0354 | 266.4704 | 122.9326 | 306.1667 | 262.5923 | 296.3556 | 305.2442 | 272.0365
1031.0354 | 265.4926 | 123.0998 | 306.5964 | 263.8874 | 296.8403 | 304.977 | 271.3998
1032.0354 | 264.5028 | 123.323 | 306.4728 | 263.5785 | 296.3035 | 303.5491 | 270.6983
1033.0354 | 263.6354 | 123.5374 | 306.3099 | 262.8975 | 295.8316 | 303.6384 | 271.5084
1034.0354 | 264.5874 | 123.6363 | 307.0746 | 264.1371 | 295.6959 | 304.1681 | 270.1693
1035.0354 | 265.9277 | 123.642 | 307.0444 | 264.1646 | 298.8857 | 305.7572 | 271.6189
1036.0354 | 265.791 | 123.8895 | 307.2032 | 264.4195 | 297.8193 | 307.6879 | 272.447
1037.0354 | 267.2888 | 123.7545 | 308.5318 | 265.6478 | 299.203 | 308.4759 | 273.8259
1038.0354 | 268.8178 | 123.9459 | 309.8294 | 265.7838 | 298.7393 | 307.4786 | 273.4232
1039.0354 | 269.9418 | 123.9427 | 309.6066 | 265.2579 | 298.129 | 308.366 | 273.4171
1040.0354 | 272.1105 | 123.9472 | 309.555 | 265.5812 | 299.2227 | 309.9048 | 275.5947
1041.0354 | 272.9936 | 124.2413 | 309.1078 | 265.9563 | 299.1499 | 309.4242 | 275.8684
1042.0354 | 273.892 | 124.121 | 309.3955 | 266.3494 | 298.6409 | 310.0776 | 276.9652
1043.0354 | 274.776 | 124.3655 | 309.5322 | 266.5392 | 299.5685 | 310.4426 | 277.0266
1044.0354 | 275.3747 | 124.4551 | 310.2676 | 266.9821 | 299.5297 | 312.5374 | 277.8147
1045.0354 | 276.187 | 124.5233 | 310.6897 | 267.4613 | 299.916 | 311.9914 | 277.6962
1046.0354 | 275.9846 | 124.9494 | 309.5409 | 267.8931 | 300.2771 | 312.3965 | 277.4441
1047.0354 | 276.0817 | 125.0802 | 309.5611 | 267.9658 | 299.8987 | 311.4602 | 276.6758
1048.0354 | 275.5277 | 125.2411 | 309.9256 | 268.4078 | 300.4512 | 311.6868 | 276.7421
1049.0354 | 275.1671 | 125.2406 | 310.4908 | 268.6149 | 300.8549 | 311.7181 | 276.4241
1050.0354 | 275.3707 | 125.362 | 310.52 | 269.3082 | 299.7704 | 311.445 | 276.8585
1051.0354 | 275.8482 | 125.4861 | 310.4018 | 269.4782 | 299.716 | 311.5619 | 277.0949
1052.0354 | 275.2423 | 125.6379 | 310.2452 | 270.33 | 299.9745 | 311.2924 | 276.9959
1053.0354 | 274.4095 | 125.7803 | 310.6592 | 270.3829 | 299.8635 | 310.4802 | 276.8207
1054.0354 | 273.965 | 125.8216 | 311.2069 | 270.9 | 298.7733 | 310.3427 | 276.9248
1055.0354 | 274.2468 | 125.9554 | 311.0627 | 271.1049 | 298.9902 | 310.5338 | 277.56
1056.0354 | 274.9839 | 125.9728 | 311.1865 | 271.2542 | 298.3093 | 310.2982 | 277.7437
1057.0354 | 276.427 | 126.1034 | 311.9269 | 271.1547 | 297.881 | 310.3371 | 278.6479
1058.0354 | 277.1587 | 126.2129 | 311.5362 | 272.0952 | 297.8782 | 311.0831 | 279.2987
1059.0354 | 277.5881 | 126.2713 | 312.0149 | 272.304 | 298.3876 | 312.282 | 279.5109
1060.0354 | 278.2046 | 126.5331 | 311.5328 | 272.648 | 298.8224 | 311.582 | 279.0807
1061.0354 | 278.2393 | 126.5703 | 311.9536 | 272.878 | 299.0949 | 310.8952 | 278.5111
1062.0354 | 278.0274 | 126.7939 | 311.7591 | 273.6896 | 300.0757 | 311.4422 | 278.123
1063.0354 | 277.7734 | 127.0007 | 311.7534 | 273.5319 | 299.2489 | 311.986 | 277.8292
1064.0354 | 277.7394 | 127.1509 | 311.6715 | 273.8725 | 298.991 | 312.6692 | 277.8726
1065.0354 | 276.5987 | 127.0424 | 311.8039 | 274.9184 | 299.1521 | 312.9706 | 277.4861
1066.0354 | 276.244 | 127.2775 | 312.1629 | 275.0854 | 299.6961 | 311.8625 | 276.2968
1067.0354 | 276.0267 | 127.4433 | 312.5083 | 275.2244 | 299.2561 | 310.9821 | 275.8039
1068.0354 | 276.3478 | 127.5643 | 312.5121 | 276.0064 | 299.9444 | 311.0277 | 276.0736
1069.0354 | 275.3421 | 127.6952 | 312.3173 | 277.0418 | 300.1861 | 310.7435 | 275.4728
1070.0354 | 274.5466 | 127.5617 | 312.1976 | 277.8402 | 301.4419 | 310.7295 | 275.926
1071.0354 | 275.1075 | 127.7475 | 312.855 | 277.7202 | 302.5361 | 310.5414 | 275.2763
1072.0354 | 274.6491 | 127.6595 | 313.8052 | 278.1469 | 302.2593 | 309.7919 | 275.5262
1073.0354 | 274.9196 | 127.8491 | 314.1066 | 277.4674 | 301.5918 | 311.8447 | 276.7244
1074.0354 | 275.7353 | 127.7815 | 313.8432 | 278.8224 | 302.319 | 314.5494 | 278.3023
1075.0354 | 276.1445 | 128.1321 | 314.2478 | 278.9382 | 304.5422 | 316.7136 | 280.7911
1076.0354 | 277.7638 | 128.2378 | 314.4611 | 279.2722 | 305.2433 | 317.961 | 282.5104
1077.0354 | 278.8983 | 128.2258 | 314.5713 | 279.8853 | 305.3429 | 318.1593 | 282.4518
1078.0354 | 279.6844 | 128.2028 | 315.2041 | 280.4197 | 308.2476 | 318.0017 | 282.3694
1079.0354 | 280.0626 | 128.485 | 314.8922 | 281.0968 | 310.181 | 320.3106 | 284.2565
1080.0354 | 281.6389 | 128.6101 | 314.5543 | 281.6889 | 310.6841 | 319.7883 | 284.8038
1081.0354 | 282.3085 | 128.5301 | 314.4578 | 282.2884 | 311.5246 | 319.6614 | 284.8543
1082.0354 | 283.1495 | 128.5405 | 314.5472 | 282.4882 | 312.081 | 319.2588 | 283.9069
1083.0354 | 283.7591 | 128.9754 | 314.5751 | 282.864 | 311.8868 | 318.1462 | 283.4112
1084.0354 | 283.7613 | 129.0203 | 315.1016 | 283.5206 | 311.555 | 317.4984 | 282.6225
1085.0354 | 284.7551 | 129.0577 | 315.2969 | 283.5154 | 310.8706 | 317.0698 | 283.1153
1086.0354 | 285.787 | 129.2864 | 314.9895 | 284.0146 | 310.8101 | 317.6586 | 282.5811
1087.0354 | 286.2981 | 129.3734 | 315.2304 | 284.8912 | 311.2209 | 317.4589 | 281.7013
1088.0354 | 286.3191 | 129.4986 | 315.6441 | 285.5359 | 311.95 | 317.7413 | 280.7672
1089.0354 | 285.4992 | 129.7484 | 315.6089 | 285.2081 | 312.1876 | 318.2015 | 280.3593
1090.0354 | 285.5385 | 129.9219 | 315.6018 | 285.656 | 311.3074 | 317.456 | 280.0962
1091.0354 | 285.113 | 129.9843 | 316.442 | 286.1987 | 311.9063 | 317.5918 | 279.7766
1092.0354 | 284.6603 | 130.2016 | 315.8747 | 287.4218 | 311.6387 | 319.174 | 281.0802
1093.0354 | 284.3751 | 130.2836 | 316.0062 | 287.542 | 311.4498 | 318.7888 | 280.3292
1094.0354 | 283.8849 | 130.2697 | 316.0909 | 287.8208 | 311.2063 | 317.9094 | 281.0511
1095.0354 | 283.6837 | 130.394 | 316.0043 | 287.9129 | 310.7523 | 316.9534 | 279.6857
1096.0354 | 283.0513 | 130.5382 | 315.9843 | 288.3377 | 309.5506 | 316.1229 | 279.0817
1097.0354 | 282.6478 | 130.79 | 316.5393 | 288.4082 | 309.3798 | 315.7223 | 278.6633
1098.0354 | 283.2195 | 130.9386 | 317.2888 | 288.7384 | 308.1174 | 315.9492 | 278.8417
1099.0354 | 284.1792 | 131.0351 | 318.4089 | 289.3773 | 308.1202 | 315.7692 | 279.4608
1100.0354 | 284.6799 | 130.8727 | 317.5019 | 289.3308 | 308.0383 | 316.5027 | 280.8988
1101.0354 | 285.2543 | 130.8685 | 317.9057 | 289.7298 | 307.0358 | 316.5946 | 280.8832
1102.0354 | 285.7976 | 130.998 | 318.2223 | 290.3156 | 307.2334 | 317.244 | 281.1401
1103.0354 | 286.4774 | 131.1295 | 318.7151 | 290.7983 | 307.7573 | 317.873 | 282.1725
1104.0354 | 285.9845 | 131.396 | 318.1717 | 291.5896 | 308.0018 | 318.4376 | 283.5186
1105.0354 | 286.4226 | 131.5491 | 318.7508 | 291.401 | 308.3948 | 318.1136 | 282.887
1106.0354 | 286.8773 | 131.6705 | 318.1981 | 292.8224 | 308.4415 | 319.0493 | 282.4907
1107.0354 | 286.7468 | 131.7076 | 318.4512 | 292.847 | 308.184 | 319.041 | 282.8097
1108.0354 | 286.3218 | 131.8525 | 318.9908 | 292.9313 | 308.9416 | 318.5301 | 283.3644
1109.0354 | 287.043 | 132.1197 | 318.6189 | 293.5633 | 309.6874 | 319.2898 | 285.1463
1110.0354 | 286.4516 | 131.9288 | 319.1651 | 293.8805 | 308.461 | 319.4676 | 285.9607
1111.0354 | 286.9267 | 132.2206 | 319.0351 | 294.476 | 308.2529 | 319.7951 | 286.0854
1112.0354 | 286.7852 | 132.3575 | 318.9044 | 294.7247 | 307.2452 | 320.7757 | 287.0294
1113.0354 | 287.5395 | 132.2654 | 319.5882 | 294.7478 | 306.8441 | 320.3178 | 286.8283
1114.0354 | 287.2512 | 132.2433 | 320.0379 | 294.9542 | 306.3391 | 320.6578 | 287.204
1115.0354 | 286.1582 | 132.3007 | 320.1785 | 295.7744 | 306.3321 | 320.7865 | 288.4652
1116.0354 | 285.796 | 132.537 | 320.1394 | 296.1669 | 306.6399 | 320.8191 | 289.1036
1117.0354 | 286.3382 | 132.7145 | 320.9499 | 297.0926 | 306.7961 | 321.3099 | 290.4607
1118.0354 | 286.4279 | 132.7002 | 321.0767 | 296.9538 | 307.0778 | 320.6774 | 290.7017
1119.0354 | 287.1908 | 132.8432 | 321.1974 | 296.9691 | 306.322 | 322.4269 | 292.4101
1120.0354 | 288.729 | 132.8796 | 321.0977 | 297.2326 | 306.4491 | 323.1373 | 293.1649
1121.0354 | 289.5229 | 133.0039 | 321.4952 | 298.0681 | 305.8983 | 324.9969 | 293.6141
1122.0354 | 290.1273 | 133.0392 | 321.6888 | 297.8442 | 306.351 | 325.7798 | 293.6578
1123.0354 | 290.2585 | 133.3647 | 321.8385 | 298.0573 | 307.7755 | 326.0667 | 293.7909
1124.0354 | 291.2084 | 133.407 | 321.9458 | 298.3755 | 309.1757 | 327.0019 | 295.2475
1125.0354 | 293.6256 | 133.4789 | 322.1493 | 298.9826 | 308.5298 | 327.8125 | 296.3136
1126.0354 | 293.801 | 133.5936 | 322.5674 | 298.7525 | 308.6005 | 328.3786 | 296.4371
1127.0354 | 294.1952 | 133.7063 | 323.7421 | 299.5113 | 308.3025 | 329.0268 | 297.9633
1128.0354 | 295.1005 | 133.856 | 324.2745 | 299.6295 | 309.2635 | 328.9215 | 299.2385
1129.0354 | 295.751 | 133.9059 | 324.1726 | 299.9961 | 311.1286 | 330.1728 | 300.4115
1130.0354 | 297.822 | 133.9624 | 324.161 | 300.0484 | 311.6098 | 331.9864 | 302.9369
1131.0354 | 298.333 | 134.045 | 325.53 | 300.4157 | 311.8539 | 332.1295 | 304.2131
1132.0354 | 299.2493 | 134.3604 | 326.3921 | 300.6528 | 311.4951 | 332.9304 | 304.8971
1133.0354 | 299.7508 | 134.4424 | 327.6422 | 301.0026 | 311.1425 | 332.7289 | 305.8278
1134.0354 | 301.1479 | 134.723 | 328.1645 | 301.5076 | 311.4016 | 333.2008 | 306.1944
1135.0354 | 302.5275 | 134.9276 | 328.0926 | 301.718 | 311.1868 | 333.0793 | 305.5188
1136.0354 | 304.3343 | 135.1819 | 328.0435 | 302.4484 | 311.8237 | 333.5846 | 306.3106
1137.0354 | 305.0303 | 135.4355 | 327.699 | 302.3126 | 311.3344 | 333.7391 | 305.8603
1138.0354 | 305.5768 | 135.4904 | 329.3705 | 302.504 | 310.4274 | 332.8538 | 304.2763
1139.0354 | 306.2272 | 135.5779 | 329.6833 | 302.8536 | 311.1046 | 333.1807 | 304.6608
1140.0354 | 306.6229 | 135.8444 | 330.8824 | 303.1754 | 311.8123 | 334.1954 | 303.9137
1141.0354 | 308.4812 | 136.0109 | 331.556 | 303.6408 | 312.0843 | 336.5913 | 304.825
1142.0354 | 310.4795 | 135.9816 | 331.0674 | 303.3658 | 312.5311 | 337.775 | 306.2674
1143.0354 | 309.9965 | 136.0364 | 331.3981 | 303.9594 | 311.34 | 337.7241 | 306.5096
1144.0354 | 309.9546 | 136.2545 | 331.1979 | 305.0026 | 310.0823 | 336.6952 | 304.8855
1145.0354 | 310.1375 | 136.5907 | 331.6781 | 305.2534 | 310.3997 | 336.4934 | 304.1287
1146.0354 | 311.1302 | 136.6047 | 332.3264 | 306.4708 | 310.846 | 335.1247 | 302.4583
1147.0354 | 312.3144 | 136.7683 | 334.2337 | 306.2264 | 310.8155 | 334.5127 | 300.8962
1148.0354 | 313.0715 | 136.8158 | 334.9198 | 306.1531 | 311.4129 | 333.9815 | 299.8141
1149.0354 | 314.0507 | 137.1528 | 334.6486 | 306.0894 | 312.678 | 335.1003 | 299.3482
1150.0354 | 313.8331 | 137.1707 | 335.622 | 305.973 | 312.6233 | 336.3573 | 300.2883
1151.0354 | 315.1518 | 137.2279 | 337.7688 | 307.0722 | 312.9534 | 338.6975 | 302.4595
1152.0354 | 318.2174 | 137.3761 | 337.9694 | 307.0839 | 313.9548 | 340.7281 | 303.3125
1153.0354 | 318.7009 | 137.5809 | 337.3401 | 307.1423 | 315.51 | 341.6581 | 303.8951
1154.0354 | 319.9352 | 137.7413 | 337.8818 | 307.8794 | 315.361 | 342.7307 | 303.7212
1155.0354 | 320.4197 | 137.8364 | 338.0231 | 307.9404 | 316.9687 | 342.7004 | 304.417
1156.0354 | 322.9047 | 137.9546 | 339.3358 | 308.0905 | 317.1582 | 343.8986 | 304.3008
1157.0354 | 324.4185 | 138.1473 | 339.4391 | 308.102 | 318.8574 | 345.1574 | 305.4249
1158.0354 | 324.6065 | 138.2169 | 339.1791 | 308.2045 | 318.5848 | 346.4647 | 306.1053
1159.0354 | 326.5265 | 138.4476 | 339.6861 | 308.3874 | 320.8917 | 348.9097 | 307.8464
1160.0354 | 327.5611 | 138.4484 | 340.2434 | 308.9838 | 323.5149 | 352.3875 | 310.4545
1161.0354 | 328.1842 | 138.4157 | 341.1152 | 309.4056 | 326.2443 | 354.0824 | 311.5992
1162.0354 | 328.7622 | 138.6719 | 341.3676 | 309.8511 | 326.7134 | 355.8603 | 313.6771
1163.0354 | 329.0487 | 138.903 | 341.6585 | 310.6044 | 327.1766 | 358.208 | 317.2405
1164.0354 | 330.2371 | 138.985 | 341.9684 | 310.3314 | 329.1565 | 358.6219 | 318.4018
1165.0354 | 332.7173 | 139.1545 | 342.5142 | 310.6408 | 329.572 | 358.3516 | 318.195
1166.0354 | 334.3005 | 139.4066 | 344.2009 | 310.6941 | 330.4866 | 360.3204 | 320.3051
1167.0354 | 336.892 | 139.395 | 346.3269 | 311.1656 | 332.345 | 361.5226 | 321.3105
1168.0354 | 337.9434 | 139.3344 | 347.2157 | 311.4081 | 332.4315 | 362.1975 | 321.9406
1169.0354 | 339.3154 | 139.4258 | 346.2896 | 311.5989 | 331.4502 | 361.0719 | 322.6514
1170.0354 | 337.95 | 139.707 | 346.0552 | 312.2336 | 330.9909 | 360.6806 | 322.8199
1171.0354 | 339.4427 | 140.0278 | 345.5086 | 312.1122 | 332.8234 | 361.7109 | 323.9976
1172.0354 | 340.3246 | 139.9964 | 346.8216 | 312.6382 | 332.3273 | 362.2449 | 323.1109
1173.0354 | 342.856 | 140.2368 | 347.2816 | 314.2195 | 333.9291 | 364.025 | 324.3174
1174.0354 | 344.4537 | 140.4187 | 347.0292 | 315.7334 | 333.7207 | 362.819 | 323.0962
1175.0354 | 344.0868 | 140.5857 | 349.0602 | 314.4573 | 333.6135 | 361.9995 | 322.3818
1176.0354 | 347.6413 | 140.6819 | 349.5749 | 314.6548 | 333.5548 | 361.9952 | 321.4178
1177.0354 | 351.521 | 140.8867 | 349.671 | 316.3598 | 334.1285 | 362.5282 | 321.1912
1178.0354 | 352.9315 | 140.9829 | 349.1738 | 316.4307 | 334.7434 | 361.7666 | 319.9619
1179.0354 | 356.1511 | 141.0431 | 349.6542 | 316.1566 | 334.4985 | 360.3589 | 318.9979
1180.0354 | 355.6246 | 141.295 | 351.6245 | 316.1648 | 334.4024 | 361.3626 | 318.6296
1181.0354 | 354.9861 | 141.1579 | 351.4647 | 316.7684 | 336.0167 | 362.6743 | 320.2447
1182.0354 | 356.4809 | 141.32 | 353.6422 | 316.6772 | 336.0735 | 361.4792 | 319.5605
1183.0354 | 358.5831 | 141.6644 | 355.3023 | 317.5122 | 336.0593 | 363.9376 | 319.7657
1184.0354 | 358.8817 | 141.9098 | 355.3314 | 318.7845 | 336.6952 | 365.7615 | 320.7847
1185.0354 | 360.9875 | 142.0764 | 356.8641 | 318.6128 | 336.2243 | 366.3506 | 321.2068
1186.0354 | 363.7831 | 142.2723 | 358.5862 | 318.5378 | 336.8389 | 367.0403 | 321.7462
1187.0354 | 364.1722 | 142.312 | 358.2142 | 318.846 | 336.7234 | 367.7085 | 323.0901
1188.0354 | 364.5854 | 142.3345 | 358.0249 | 319.2171 | 336.8643 | 367.4532 | 322.6913
1189.0354 | 365.9599 | 142.3372 | 357.673 | 319.4876 | 338.5991 | 369.1633 | 324.4581
1190.0354 | 367.8753 | 142.6028 | 358.0129 | 319.9633 | 339.3137 | 370.3729 | 325.7314
1191.0354 | 367.6983 | 142.6095 | 358.3957 | 320.2673 | 339.6266 | 372.2975 | 325.2751
1192.0354 | 367.5689 | 142.636 | 359.0485 | 320.2321 | 340.3242 | 372.5863 | 325.0855
1193.0354 | 367.8182 | 142.8175 | 360.6151 | 320.3506 | 340.2227 | 373.9566 | 326.5028
1194.0354 | 369.1198 | 143.042 | 360.7502 | 320.8676 | 342.1199 | 373.8575 | 327.6566
1195.0354 | 368.5927 | 143.2449 | 360.9737 | 320.9813 | 341.7617 | 373.1841 | 326.7628
1196.0354 | 367.8324 | 143.4694 | 361.8024 | 321.076 | 342.8621 | 373.5442 | 328.5413
1197.0354 | 369.8386 | 143.4461 | 362.8542 | 321.3736 | 345.3822 | 373.2002 | 329.2178
1198.0354 | 374.0605 | 143.5825 | 364.1912 | 321.9022 | 346.8458 | 376.539 | 330.2885
1199.0354 | 375.3456 | 143.639 | 364.1501 | 322.7395 | 347.3017 | 377.1931 | 332.6344
1200.0354 | 381.5474 | 143.9303 | 364.8391 | 323.3892 | 346.2345 | 377.2735 | 332.889
1201.0354 | 381.4859 | 144.2761 | 364.2353 | 323.3976 | 345.4562 | 377.7833 | 333.3077
1202.0354 | 383.2972 | 144.3806 | 365.3944 | 323.6797 | 345.3078 | 377.1728 | 333.0159
1203.0354 | 389.547 | 144.7805 | 366.2021 | 324.1834 | 346.024 | 377.9187 | 333.9005
1204.0354 | 394.7414 | 144.9228 | 368.1297 | 324.7052 | 346.9845 | 379.9744 | 335.4449
1205.0354 | 397.4974 | 145.0298 | 369.2086 | 324.7143 | 346.6546 | 380.9173 | 334.1705
1206.0354 | 399.7701 | 145.1702 | 369.602 | 325.1958 | 346.8326 | 382.1886 | 334.4969
1207.0354 | 399.2316 | 145.3003 | 369.029 | 325.5624 | 348.0436 | 382.363 | 334.8147
1208.0354 | 398.0465 | 145.3065 | 370.1745 | 325.992 | 350.1708 | 383.1735 | 336.8367
1209.0354 | 402.2565 | 145.3498 | 369.4694 | 325.7449 | 351.9109 | 384.0315 | 338.5055
1210.0354 | 402.5024 | 145.4096 | 369.7399 | 326.3612 | 352.4034 | 384.8067 | 337.2338
1211.0354 | 403.8406 | 145.5532 | 372.1434 | 326.823 | 354.2527 | 386.1106 | 338.3795
1212.0354 | 409.0516 | 145.7168 | 373.3458 | 327.4565 | 355.21 | 386.8055 | 339.0038
1213.0354 | 411.3797 | 145.8788 | 374.6659 | 327.332 | 354.0849 | 386.8607 | 338.1304
1214.0354 | 411.1627 | 145.9546 | 373.7995 | 328.2243 | 353.5546 | 387.4963 | 340.044
1215.0354 | 410.4419 | 146.0926 | 373.6897 | 328.6243 | 353.7349 | 388.1748 | 340.8857
1216.0354 | 408.962 | 146.2019 | 374.2712 | 328.3894 | 354.6892 | 390.7276 | 340.7011
1217.0354 | 408.4371 | 146.4956 | 375.4072 | 328.6813 | 357.1741 | 391.1272 | 341.748
1218.0354 | 416.1294 | 146.6782 | 375.9552 | 329.0139 | 358.804 | 391.4915 | 342.2267
1219.0354 | 420.3391 | 146.6915 | 376.2814 | 329.2904 | 359.8224 | 392.706 | 344.5455
1220.0354 | 420.3184 | 146.7766 | 376.1303 | 330.4231 | 359.6992 | 394.962 | 345.2703
1221.0354 | 420.8104 | 146.8829 | 376.3163 | 330.7133 | 361.0846 | 395.5925 | 345.4024
1222.0354 | 425.0342 | 146.9803 | 376.5768 | 331.2579 | 361.3967 | 396.6876 | 344.6569
1223.0354 | 426.4506 | 147.1149 | 377.1296 | 331.9614 | 362.4799 | 395.533 | 343.9466
1224.0354 | 436.3999 | 147.2166 | 377.7531 | 331.4312 | 362.9946 | 396.3963 | 342.868
1225.0354 | 438.4571 | 147.2998 | 378.2166 | 331.4054 | 364.1284 | 399.6576 | 343.0598
1226.0354 | 445.3664 | 147.4808 | 378.7675 | 331.7917 | 364.2287 | 402.3756 | 344.2401
1227.0354 | 456.6029 | 147.8113 | 379.718 | 332.4967 | 364.5073 | 404.3274 | 344.2521
1228.0354 | 453.4369 | 147.9991 | 380.3148 | 333.0007 | 364.2424 | 405.0486 | 344.8062
1229.0354 | 453.8502 | 148.2039 | 380.9988 | 333.6224 | 367.1705 | 406.5375 | 345.8611
1230.0354 | 459.2371 | 148.5044 | 381.3036 | 334.0081 | 369.1713 | 406.8699 | 346.427
1231.0354 | 454.7899 | 148.7346 | 381.0788 | 334.81 | 370.7022 | 407.1506 | 346.5988
1232.0354 | 452.4741 | 148.8551 | 381.307 | 334.9143 | 372.9133 | 409.2343 | 345.9613
1233.0354 | 449.7746 | 149.1047 | 381.3542 | 336.3654 | 373.8363 | 410.6062 | 346.9393
1234.0354 | 467.2531 | 149.2675 | 381.9833 | 335.9708 | 374.5247 | 409.9822 | 347.431
1235.0354 | 466.3253 | 149.4617 | 382.3279 | 336.3446 | 374.4617 | 410.0519 | 347.6419
1236.0354 | 470.6484 | 149.4719 | 382.8008 | 336.5416 | 376.0451 | 409.9884 | 348.4994
1237.0354 | 469.8704 | 149.4304 | 382.9162 | 337.5672 | 375.1344 | 410.5409 | 348.0521
1238.0354 | 466.4278 | 149.6348 | 383.0562 | 338.0517 | 375.2531 | 410.3791 | 347.811
1239.0354 | 476.1458 | 149.7856 | 383.2041 | 338.3591 | 374.7972 | 409.6263 | 346.649
1240.0354 | 476.5595 | 150.0395 | 384.3077 | 338.8835 | 375.4299 | 409.9752 | 346.4516
1241.0354 | 493.5531 | 150.0055 | 384.5621 | 338.9878 | 375.196 | 409.9996 | 347.1736
1242.0354 | 488.4283 | 150.1451 | 385.7119 | 338.9327 | 374.7596 | 410.3321 | 348.0521
1243.0354 | 507.0421 | 150.3977 | 385.7699 | 339.9184 | 375.4641 | 410.9346 | 348.6548
1244.0354 | 520.208 | 150.3729 | 385.7373 | 341.3009 | 376.1427 | 412.0856 | 349.8839
1245.0354 | 528.8278 | 150.4724 | 385.5205 | 341.4183 | 376.2247 | 411.6328 | 349.7577
1246.0354 | 546.8916 | 150.6556 | 385.8892 | 342.4519 | 375.9862 | 409.8993 | 348.8291
1247.0354 | 547.7395 | 150.8267 | 386.2651 | 342.7745 | 376.9042 | 410.324 | 348.8685
1248.0354 | 562.9662 | 150.9115 | 387.0684 | 343.0934 | 376.7458 | 410.3872 | 348.6181
1249.0354 | 579.6504 | 151.0613 | 388.4905 | 342.7317 | 376.7016 | 411.2846 | 349.0951
1250.0354 | 590.4047 | 151.3939 | 390.6393 | 343.1819 | 377.3847 | 412.3249 | 350.5287
1251.0354 | 583.8155 | 151.5359 | 390.7787 | 343.5954 | 378.2502 | 413.8543 | 353.4297
1252.0354 | 595.1695 | 151.7496 | 390.461 | 343.9791 | 379.4589 | 414.6647 | 355.3099
1253.0354 | 607.2474 | 151.745 | 392.1229 | 344.4564 | 380.6865 | 416.0175 | 356.834
1254.0354 | 626.9186 | 152.0091 | 393.3564 | 344.7994 | 381.8397 | 417.5903 | 357.8065
1255.0354 | 655.229 | 152.276 | 393.288 | 345.4751 | 382.2747 | 418.0901 | 359.0204
1256.0354 | 670.6556 | 152.2265 | 392.9757 | 345.3911 | 381.3042 | 420.8906 | 361.1588
1257.0354 | 655.0271 | 152.3053 | 393.5039 | 345.9321 | 380.9767 | 421.6848 | 361.9856
1258.0354 | 671.9063 | 152.4746 | 393.6995 | 346.4838 | 383.6683 | 422.386 | 363.0814
1259.0354 | 671.1804 | 152.6338 | 393.8306 | 346.8857 | 383.682 | 423.5363 | 363.4266
1260.0354 | 682.2522 | 152.9549 | 394.4478 | 347.005 | 383.8816 | 423.9946 | 362.642
1261.0354 | 661.6716 | 153.1475 | 394.4562 | 347.5334 | 383.5972 | 423.9676 | 362.2794
1262.0354 | 645.4172 | 153.1194 | 395.8023 | 348.0679 | 384.4023 | 425.699 | 363.1752
1263.0354 | 653.1224 | 153.3612 | 397.6639 | 348.3346 | 386.2807 | 427.0138 | 364.6509
1264.0354 | 646.4928 | 153.4861 | 397.6783 | 348.4188 | 385.4844 | 425.5239 | 366.0099
1265.0354 | 630.3244 | 153.7113 | 397.1843 | 348.8011 | 384.0547 | 425.0285 | 365.798
1266.0354 | 638.9981 | 153.9385 | 396.8129 | 349.7583 | 385.322 | 425.6381 | 367.1511
1267.0354 | 661.161 | 154.0851 | 397.7246 | 349.694 | 385.7339 | 428.2863 | 367.9258
1268.0354 | 666.7388 | 154.2409 | 398.8387 | 349.8803 | 385.6861 | 429.2337 | 368.8561
1269.0354 | 645.7498 | 154.3937 | 398.7326 | 350.7243 | 386.9444 | 429.0742 | 370.5229
1270.0354 | 621.2515 | 154.7122 | 399.0765 | 351.6237 | 388.5873 | 427.7617 | 370.6373
1271.0354 | 600.8712 | 154.8387 | 399.3936 | 351.8535 | 389.287 | 427.5803 | 370.0736
1272.0354 | 584.8668 | 154.9416 | 400.0049 | 352.5633 | 391.1601 | 428.7022 | 369.8835
1273.0354 | 590.2059 | 155.1447 | 400.2002 | 352.537 | 392.1379 | 428.9848 | 370.8614
1274.0354 | 588.0475 | 155.3312 | 400.8223 | 353.2157 | 393.4572 | 428.8772 | 371.4267
1275.0354 | 577.1731 | 155.3931 | 401.3721 | 353.1966 | 392.5657 | 427.6249 | 371.4711
1276.0354 | 587.172 | 155.6192 | 402.3477 | 353.9476 | 391.8254 | 426.5826 | 370.7534
1277.0354 | 583.3872 | 155.9073 | 401.5698 | 354.7169 | 391.1454 | 427.4042 | 370.6703
1278.0354 | 591.5625 | 156.0932 | 402.8632 | 355.1139 | 391.3532 | 427.8426 | 370.0886
1279.0354 | 602.8408 | 156.2543 | 404.2045 | 354.9459 | 391.8582 | 425.5741 | 368.4448
1280.0354 | 615.4367 | 156.4202 | 403.3752 | 355.4923 | 390.5695 | 424.3395 | 368.4057
1281.0354 | 616.2204 | 156.5509 | 403.3656 | 356.7593 | 390.9438 | 424.6351 | 367.7254
1282.0354 | 607.8349 | 156.7296 | 403.3122 | 357.5443 | 390.0415 | 423.3406 | 366.9099
1283.0354 | 594.6106 | 156.8116 | 403.9292 | 357.1671 | 391.0892 | 422.9604 | 365.6844
1284.0354 | 585.1203 | 156.9411 | 404.0613 | 357.4456 | 390.0132 | 421.0593 | 363.578
1285.0354 | 573.3291 | 157.0397 | 403.9234 | 357.9098 | 392.0183 | 422.4857 | 362.6858
1286.0354 | 577.2638 | 157.2012 | 404.5849 | 358.3107 | 392.9322 | 422.3534 | 362.3172
1287.0354 | 591.0049 | 157.4525 | 405.0382 | 358.52 | 393.836 | 421.9303 | 361.1709
1288.0354 | 587.3963 | 157.6043 | 406.5871 | 359.006 | 394.2788 | 422.2763 | 361.9494
1289.0354 | 585.2694 | 157.7083 | 406.026 | 360.0707 | 394.5753 | 420.5948 | 362.4118
1290.0354 | 585.7946 | 157.7762 | 406.1618 | 362.4187 | 394.2737 | 418.6202 | 361.0738
1291.0354 | 588.7874 | 157.8755 | 405.9481 | 362.9496 | 392.9514 | 417.805 | 359.4053
1292.0354 | 565.472 | 158.0539 | 405.8637 | 362.5987 | 391.848 | 416.189 | 358.5613
1293.0354 | 568.305 | 158.3069 | 406.8671 | 362.7232 | 392.625 | 415.5054 | 358.4426
1294.0354 | 562.8496 | 158.5413 | 407.081 | 363.1334 | 393.8951 | 415.5755 | 359.1127
1295.0354 | 561.4482 | 158.6893 | 408.4706 | 363.4453 | 393.6606 | 415.4403 | 359.7763
1296.0354 | 555.4908 | 158.5344 | 407.9174 | 363.5454 | 392.7778 | 413.9032 | 358.3474
1297.0354 | 557.169 | 158.8063 | 408.1332 | 365.0004 | 392.8443 | 414.311 | 359.2904
1298.0354 | 560.4267 | 158.9958 | 407.8744 | 365.7731 | 393.5974 | 413.3654 | 358.9643
1299.0354 | 554.7241 | 159.2196 | 408.4338 | 366.8424 | 394.3282 | 413.4505 | 358.6075
1300.0354 | 568.0711 | 159.1327 | 408.7752 | 366.6616 | 395.4127 | 413.005 | 357.3936
1301.0354 | 563.1643 | 159.3737 | 409.2588 | 366.6584 | 395.2782 | 413.7613 | 357.9895
1302.0354 | 549.3554 | 159.4567 | 409.1157 | 366.7757 | 395.224 | 414.1186 | 358.8712
1303.0354 | 543.0416 | 159.479 | 409.3892 | 367.8986 | 396.2301 | 413.4613 | 358.9553
1304.0354 | 544.3634 | 159.7798 | 410.3607 | 368.1297 | 398.1629 | 415.002 | 359.333
1305.0354 | 555.794 | 159.8135 | 410.8803 | 368.8014 | 397.3735 | 414.5554 | 359.5273
1306.0354 | 564.7078 | 159.8609 | 410.833 | 369.0613 | 396.9431 | 416.271 | 360.158
1307.0354 | 563.5538 | 160.1017 | 411.8845 | 369.3742 | 395.7353 | 416.8029 | 360.7704
1308.0354 | 555.2557 | 160.1878 | 411.5944 | 370.04 | 394.3866 | 417.6677 | 361.1371
1309.0354 | 559.7249 | 160.3358 | 411.4002 | 370.5339 | 395.0729 | 419.0674 | 362.7442
1310.0354 | 553.0335 | 160.4183 | 412.1637 | 370.6064 | 395.4584 | 417.6719 | 363.1034
1311.0354 | 567.1381 | 160.6169 | 412.0059 | 371.3694 | 395.5909 | 417.717 | 362.9253
1312.0354 | 567.2123 | 160.643 | 412.2861 | 372.364 | 394.758 | 418.2031 | 362.6181
1313.0354 | 571.4797 | 160.7669 | 412.7928 | 371.9237 | 394.6545 | 419.5062 | 363.2107
1314.0354 | 580.5136 | 161.1703 | 413.0292 | 372.1183 | 393.8043 | 421.5008 | 363.975
1315.0354 | 573.7562 | 161.3041 | 412.7868 | 372.9029 | 392.7887 | 423.2637 | 363.4143
1316.0354 | 573.1893 | 161.3988 | 413.9068 | 373.1616 | 392.4952 | 424.2327 | 364.944
1317.0354 | 559.6864 | 161.5328 | 413.4867 | 374.6292 | 392.0171 | 424.6381 | 364.8044
1318.0354 | 558.6818 | 161.8527 | 413.7311 | 375.3739 | 391.9883 | 425.4954 | 363.5853
1319.0354 | 545.4648 | 162.0085 | 413.7318 | 374.9533 | 392.8703 | 423.4652 | 362.2389
1320.0354 | 539.8342 | 162.0367 | 413.8219 | 375.585 | 392.403 | 422.1915 | 361.1492
1321.0354 | 542.1666 | 162.0291 | 414.3985 | 376.5251 | 392.457 | 422.2285 | 361.3756
1322.0354 | 537.9279 | 162.0699 | 414.2543 | 375.9674 | 393.1369 | 420.699 | 360.896
1323.0354 | 522.3136 | 162.1764 | 415.333 | 376.4712 | 394.2803 | 420.6588 | 361.999
1324.0354 | 526.4043 | 162.3547 | 415.9772 | 377.15 | 394.0281 | 419.7771 | 362.4908
1325.0354 | 523.1283 | 162.7 | 415.7098 | 377.6772 | 394.5094 | 419.5645 | 362.762
1326.0354 | 515.4442 | 162.8889 | 415.3763 | 378.4186 | 393.7956 | 419.1578 | 362.2412
1327.0354 | 500.0019 | 163.1915 | 415.888 | 378.7185 | 393.7869 | 418.559 | 362.2818
1328.0354 | 500.4293 | 163.0909 | 415.9797 | 379.0094 | 394.2665 | 418.9002 | 363.1827
1329.0354 | 499.5664 | 163.0756 | 416.4513 | 379.1924 | 396.0449 | 419.8265 | 363.4382
1330.0354 | 501.6465 | 163.1363 | 416.3448 | 379.7607 | 394.9373 | 420.9362 | 363.24
1331.0354 | 506.1624 | 163.2351 | 416.5035 | 380.0296 | 395.1096 | 420.8682 | 363.1489
1332.0354 | 524.4279 | 163.5346 | 417.8755 | 380.8819 | 396.3539 | 421.1243 | 363.4569
1333.0354 | 523.7422 | 163.7349 | 418.8613 | 381.5241 | 395.3641 | 420.7764 | 362.2654
1334.0354 | 535.2337 | 163.98 | 419.1804 | 381.8604 | 395.464 | 420.4405 | 363.438
1335.0354 | 527.6838 | 164.2395 | 420.0202 | 381.7828 | 394.3609 | 420.1033 | 364.3064
1336.0354 | 518.1228 | 164.2814 | 419.8832 | 382.0738 | 393.2986 | 419.1292 | 364.7518
1337.0354 | 506.6756 | 164.3792 | 421.0362 | 382.6236 | 393.2258 | 419.2027 | 365.0682
1338.0354 | 496.3442 | 164.7332 | 422.0239 | 382.9662 | 392.7123 | 418.3466 | 363.95
1339.0354 | 486.5273 | 164.9825 | 421.6042 | 383.6098 | 393.6766 | 418.6327 | 363.7181
1340.0354 | 479.5807 | 165.1914 | 423.6608 | 383.5992 | 393.6491 | 419.3888 | 364.6525
1341.0354 | 471.7253 | 165.2181 | 423.1842 | 384.1134 | 393.3966 | 418.6574 | 364.3476
1342.0354 | 466.2055 | 165.1545 | 422.3694 | 384.5934 | 393.877 | 418.516 | 364.6026
1343.0354 | 460.3517 | 165.374 | 423.7003 | 384.9109 | 393.5132 | 418.3628 | 363.7385
1344.0354 | 454.3027 | 165.5774 | 423.6463 | 385.2673 | 395.1916 | 417.5733 | 364.1917
1345.0354 | 449.2142 | 165.7722 | 424.1838 | 386.0556 | 394.3929 | 416.4179 | 363.956
1346.0354 | 443.1783 | 166.0956 | 425.4364 | 385.8034 | 394.7265 | 415.8053 | 363.793
1347.0354 | 437.5518 | 165.9625 | 424.7228 | 386.3883 | 393.3656 | 415.3791 | 363.2287
1348.0354 | 435.6789 | 166.1327 | 424.54 | 386.7296 | 393.5607 | 416.6856 | 363.1319
1349.0354 | 433.5947 | 166.3502 | 424.892 | 387.2184 | 392.5967 | 417.0434 | 363.0951
1350.0354 | 430.513 | 166.4184 | 425.8058 | 387.0704 | 392.7418 | 417.3336 | 363.4102
1351.0354 | 428.9863 | 166.5571 | 426.5493 | 387.7102 | 392.1695 | 416.4886 | 363.3187
1352.0354 | 427.3486 | 166.7427 | 426.0626 | 388.25 | 393.5202 | 419.0929 | 364.5657
1353.0354 | 425.3062 | 166.9865 | 425.8514 | 388.4525 | 393.9101 | 419.8206 | 363.9271
1354.0354 | 424.99 | 167.0107 | 426.9201 | 389.1174 | 394.1576 | 420.1123 | 363.0555
1355.0354 | 422.6755 | 167.0053 | 427.1281 | 389.4359 | 393.7946 | 420.6725 | 363.1513
1356.0354 | 423.0778 | 167.2345 | 427.8548 | 389.3751 | 393.2615 | 420.7118 | 363.0039
1357.0354 | 422.1416 | 167.4267 | 427.6904 | 389.821 | 392.7461 | 420.1601 | 364.1121
1358.0354 | 418.7464 | 167.5752 | 427.8669 | 390.5349 | 392.1401 | 418.9957 | 364.6678
1359.0354 | 416.4974 | 167.8005 | 428.4173 | 391.2254 | 391.4807 | 417.6954 | 364.2396
1360.0354 | 415.9364 | 167.9956 | 429.3305 | 391.3358 | 391.9044 | 416.9893 | 363.947
1361.0354 | 414.4069 | 168.1934 | 429.6066 | 391.5869 | 391.3741 | 416.2799 | 364.1518
1362.0354 | 412.6805 | 168.3214 | 429.709 | 392.0068 | 390.7813 | 415.8458 | 364.1394
1363.0354 | 412.5764 | 168.4288 | 430.2629 | 392.1406 | 390.3178 | 415.0618 | 363.387
1364.0354 | 410.6193 | 168.6208 | 430.0288 | 392.217 | 390.5394 | 415.5078 | 363.7752
1365.0354 | 409.2949 | 168.8595 | 430.8321 | 392.7071 | 390.2023 | 414.9754 | 364.2366
1366.0354 | 409.1927 | 168.9469 | 432.1855 | 392.8431 | 391.67 | 415.1407 | 365.3634
1367.0354 | 411.0512 | 168.9837 | 431.9475 | 393.2715 | 390.7082 | 415.612 | 365.0048
1368.0354 | 410.5372 | 169.236 | 431.9897 | 393.9631 | 391.1697 | 415.9145 | 365.6916
1369.0354 | 408.4566 | 169.1539 | 432.2754 | 394.5193 | 392.12 | 415.5291 | 366.4019
1370.0354 | 408.5382 | 169.3695 | 433.0407 | 394.3082 | 392.3145 | 416.3227 | 366.6891
1371.0354 | 408.3801 | 169.4935 | 434.9803 | 394.7184 | 391.301 | 416.4107 | 366.7023
1372.0354 | 407.923 | 169.5745 | 434.5047 | 395.2481 | 391.8093 | 416.1205 | 366.9616
1373.0354 | 408.5945 | 169.7533 | 433.999 | 396.0728 | 392.171 | 416.3172 | 367.6489
1374.0354 | 407.949 | 169.8078 | 435.9895 | 396.5259 | 391.7346 | 415.5495 | 366.6242
1375.0354 | 407.8898 | 170.0231 | 435.8939 | 396.377 | 391.9899 | 414.0981 | 365.2231
1376.0354 | 407.921 | 170.2279 | 435.9353 | 396.2236 | 392.4111 | 414.8363 | 365.4106
1377.0354 | 409.7658 | 170.3615 | 435.6773 | 396.359 | 393.1619 | 415.8076 | 366.9201
1378.0354 | 409.354 | 170.528 | 436.6977 | 396.8588 | 393.2357 | 418.4486 | 367.1813
1379.0354 | 409.9774 | 170.9257 | 437.2818 | 397.3339 | 393.3643 | 418.0819 | 368.237
1380.0354 | 409.6059 | 171.8383 | 438.4039 | 397.4362 | 392.8043 | 416.2934 | 365.4569
1381.0354 | 409.8716 | 171.266 | 438.4861 | 398.1014 | 392.5895 | 415.5866 | 366.0649
1382.0354 | 411.0158 | 171.8072 | 438.5786 | 398.1989 | 392.5075 | 415.8487 | 366.51
1383.0354 | 410.5835 | 171.2981 | 438.3596 | 398.2261 | 392.0005 | 416.443 | 368.0993
1384.0354 | 408.8513 | 171.3241 | 438.0347 | 398.7391 | 391.3412 | 418.0509 | 368.3559
1385.0354 | 407.1125 | 171.5782 | 438.2129 | 398.7975 | 391.1673 | 419.2638 | 367.6269
1386.0354 | 408.0817 | 171.8227 | 438.5546 | 399.3989 | 391.2113 | 419.3591 | 366.3804
1387.0354 | 407.613 | 172.0035 | 438.6711 | 400.1372 | 391.3456 | 419.1615 | 367.1481
1388.0354 | 406.0105 | 172.1413 | 439.4148 | 400.0653 | 390.483 | 418.2276 | 367.3649
1389.0354 | 405.0735 | 172.241 | 440.03 | 400.194 | 390.248 | 417.3095 | 366.5244
1390.0354 | 403.6366 | 172.8452 | 439.8759 | 400.5127 | 391.2355 | 416.549 | 366.5871
1391.0354 | 403.032 | 172.768 | 440.4558 | 401.4921 | 390.5252 | 415.8871 | 365.0696
1392.0354 | 402.4951 | 172.5712 | 441.7218 | 400.9722 | 390.6907 | 416.2285 | 363.9496
1393.0354 | 401.3247 | 172.6991 | 442.4491 | 400.9638 | 391.35 | 416.1496 | 364.104
1394.0354 | 400.9546 | 172.914 | 442.5219 | 401.4359 | 391.738 | 416.4165 | 364.902
1395.0354 | 400.6581 | 172.9031 | 441.9591 | 402.1055 | 391.5913 | 416.0647 | 365.4109
1396.0354 | 400.6611 | 173.0329 | 442.7508 | 401.8229 | 391.6473 | 416.2988 | 366.4007
1397.0354 | 402.1657 | 173.1205 | 443.8638 | 402.1457 | 390.1614 | 416.8722 | 367.2128
1398.0354 | 402.4356 | 173.1924 | 444.0616 | 402.531 | 388.6577 | 416.295 | 367.779
1399.0354 | 402.0306 | 173.2358 | 443.8806 | 402.8819 | 387.7451 | 414.8083 | 367.7132
1400.0354 | 401.3024 | 173.6836 | 445.0475 | 403.0587 | 387.3256 | 414.479 | 367.232
1401.0354 | 400.5706 | 173.7385 | 445.7692 | 402.8948 | 387.0018 | 413.5986 | 367.2067
1402.0354 | 399.8509 | 174.0335 | 445.7146 | 403.022 | 387.2782 | 412.936 | 367.0527
1403.0354 | 399.0896 | 174.0898 | 445.7982 | 404.0808 | 386.1438 | 411.472 | 366.367
1404.0354 | 399.8473 | 174.1923 | 445.8503 | 403.8695 | 385.6135 | 410.9445 | 366.2262
1405.0354 | 399.8746 | 174.2633 | 446.3712 | 404.2566 | 385.6008 | 410.5423 | 365.4494
1406.0354 | 401.2313 | 174.3666 | 446.5071 | 404.0445 | 386.4133 | 410.8242 | 366.141
1407.0354 | 400.1008 | 174.4251 | 446.4391 | 404.4303 | 385.3851 | 410.949 | 366.4222
1408.0354 | 398.4377 | 174.5272 | 447.0464 | 404.4977 | 384.9885 | 412.3873 | 366.2701
1409.0354 | 396.5583 | 174.6825 | 446.9573 | 404.5027 | 384.1801 | 412.335 | 365.6538
1410.0354 | 394.7779 | 174.8572 | 446.914 | 404.7079 | 383.4633 | 411.2173 | 364.7642
1411.0354 | 392.7169 | 175.1357 | 447.263 | 405.7532 | 383.2144 | 409.8476 | 362.8574
1412.0354 | 391.3811 | 175.2638 | 449.7129 | 405.3255 | 382.6696 | 409.1644 | 362.5536
1413.0354 | 391.3871 | 175.3235 | 449.1374 | 405.3787 | 382.8294 | 408.9919 | 362.8779
1414.0354 | 392.103 | 175.4935 | 449.502 | 405.4762 | 381.8998 | 409.2437 | 363.1435
1415.0354 | 391.5907 | 175.8976 | 449.4232 | 405.6201 | 381.3135 | 409.4543 | 363.1435
1416.0354 | 392.8785 | 176.1273 | 449.0487 | 405.6865 | 381.5347 | 410.9737 | 363.034
1417.0354 | 393.1844 | 176.2098 | 449.6097 | 405.8955 | 380.6361 | 412.1206 | 363.5099
1418.0354 | 391.9202 | 176.4055 | 450.4345 | 406.1205 | 380.3514 | 412.6056 | 363.625
1419.0354 | 391.0634 | 176.3487 | 450.1691 | 406.2033 | 379.8483 | 412.4489 | 363.2803
1420.0354 | 391.7806 | 176.5335 | 449.952 | 406.1194 | 379.1497 | 411.3672 | 361.833
1421.0354 | 390.2009 | 176.7327 | 449.9589 | 406.9495 | 379.5102 | 411.7688 | 360.5931
1422.0354 | 389.4811 | 176.9337 | 450.4245 | 406.5977 | 380.2829 | 412.7554 | 360.5946
1423.0354 | 388.5619 | 177.0473 | 450.6502 | 406.5691 | 379.7378 | 412.0197 | 359.8212
1424.0354 | 386.4075 | 177.3499 | 451.6577 | 407.0286 | 379.7451 | 411.4874 | 359.4372
1425.0354 | 386.5998 | 177.5323 | 451.3166 | 407.1814 | 378.7975 | 411.2079 | 359.5237
1426.0354 | 385.3401 | 177.2833 | 452.0485 | 407.6184 | 378.1467 | 411.4203 | 359.5158
1427.0354 | 383.9741 | 177.3032 | 451.5677 | 407.2882 | 378.4686 | 410.6006 | 359.5852
1428.0354 | 383.4355 | 177.51 | 452.1604 | 407.3049 | 377.9645 | 409.8686 | 359.8388
1429.0354 | 383.9195 | 177.5737 | 452.3817 | 407.4462 | 377.824 | 408.5225 | 358.9774
1430.0354 | 383.715 | 177.838 | 453.3232 | 407.6435 | 378.99 | 408.2801 | 359.2108
1431.0354 | 383.5075 | 177.8592 | 452.9901 | 408.3875 | 378.8166 | 406.9619 | 359.6911
1432.0354 | 382.3027 | 177.8724 | 452.0569 | 407.9289 | 378.9461 | 405.8854 | 359.2649
1433.0354 | 381.2794 | 178.1785 | 451.9922 | 408.6764 | 377.7954 | 404.5927 | 357.536
1434.0354 | 380.6047 | 178.326 | 452.3235 | 408.1962 | 377.0885 | 403.3599 | 356.7864
1435.0354 | 378.5524 | 178.35 | 451.9361 | 409.0177 | 376.4949 | 401.8736 | 355.8851
1436.0354 | 377.5039 | 178.7013 | 452.1118 | 408.9972 | 375.6462 | 400.7207 | 354.552
1437.0354 | 375.69 | 178.8508 | 451.845 | 409.0037 | 376.9661 | 399.383 | 353.8142
1438.0354 | 374.4624 | 179.0048 | 451.8475 | 410.2487 | 377.4907 | 397.9377 | 351.9275
1439.0354 | 373.0009 | 179.0359 | 452.4179 | 409.7145 | 376.9277 | 397.8716 | 350.7629
1440.0354 | 372.0005 | 179.0594 | 453.3312 | 410.1426 | 377.4555 | 397.8527 | 350.1057
1441.0354 | 371.7759 | 179.1682 | 453.721 | 410.6388 | 379.0386 | 398.4107 | 351.1237
1442.0354 | 371.7388 | 179.2506 | 453.2467 | 411.2054 | 379.393 | 398.9613 | 351.4993
1443.0354 | 370.9894 | 179.4656 | 453.101 | 412.0403 | 380.5794 | 399.0658 | 352.8086
1444.0354 | 370.153 | 179.7501 | 453.0116 | 411.3157 | 379.6288 | 398.7114 | 353.013
1445.0354 | 369.9361 | 179.7451 | 453.2273 | 410.9789 | 378.9533 | 398.1141 | 352.9614
1446.0354 | 370.6974 | 180.0276 | 453.5198 | 411.3364 | 379.0439 | 397.5474 | 352.3133
1447.0354 | 370.6723 | 179.9773 | 452.8915 | 412.2979 | 379.4942 | 397.4276 | 352.5914
1448.0354 | 370.864 | 180.1228 | 452.601 | 412.4321 | 380.4146 | 397.6504 | 351.9202
1449.0354 | 371.076 | 180.3468 | 452.8002 | 412.3433 | 380.6329 | 395.9451 | 350.7422
1450.0354 | 370.9972 | 180.4886 | 453.0585 | 412.8001 | 381.1928 | 395.0476 | 349.7379
1451.0354 | 369.9672 | 180.5547 | 452.6385 | 412.8419 | 380.8492 | 395.09 | 349.0464
1452.0354 | 369.5838 | 180.8208 | 453.6637 | 414.2216 | 380.8045 | 394.5004 | 348.2147
1453.0354 | 368.0015 | 180.8606 | 453.8139 | 413.4973 | 382.0675 | 394.7287 | 347.9873
1454.0354 | 368.8973 | 180.9089 | 454.5645 | 413.3943 | 383.3113 | 395.1538 | 348.7976
1455.0354 | 369.9117 | 180.966 | 454.0264 | 413.4415 | 382.6692 | 396.2541 | 349.954
1456.0354 | 369.6211 | 181.0673 | 453.9244 | 413.8166 | 381.6285 | 396.3292 | 349.1959
1457.0354 | 369.4769 | 181.1765 | 453.6352 | 413.7805 | 381.0261 | 395.7332 | 348.6097
1458.0354 | 370.0927 | 181.3835 | 455.0646 | 414.3644 | 380.977 | 395.0545 | 348.2335
1459.0354 | 371.0491 | 181.7208 | 456.6635 | 414.0549 | 380.6223 | 396.0019 | 349.2238
1460.0354 | 372.7943 | 181.7926 | 456.738 | 414.2171 | 381.9458 | 398.065 | 351.3993
1461.0354 | 374.3854 | 181.9486 | 456.0431 | 414.5337 | 381.2883 | 399.8945 | 354.0407
1462.0354 | 376.8034 | 182.0786 | 457.1251 | 414.733 | 381.9078 | 401.1016 | 355.9064
1463.0354 | 377.7994 | 182.2448 | 456.8078 | 414.8324 | 381.8013 | 401.6122 | 356.7573
1464.0354 | 378.8736 | 182.2736 | 456.6342 | 415.0724 | 382.2416 | 402.7051 | 357.3445
1465.0354 | 379.8823 | 182.4062 | 457.0393 | 415.195 | 383.2523 | 403.0568 | 358.5863
1466.0354 | 381.8255 | 182.4949 | 457.681 | 415.6567 | 382.9789 | 403.2304 | 359.1264
1467.0354 | 382.2089 | 182.6735 | 457.9004 | 415.9579 | 383.1849 | 403.3476 | 358.9285
1468.0354 | 383.5947 | 182.8797 | 458.7276 | 416.705 | 383.1561 | 403.6659 | 358.7266
1469.0354 | 384.9565 | 183.027 | 459.7981 | 416.1958 | 383.1837 | 403.7535 | 358.6372
1470.0354 | 386.4791 | 183.0259 | 459.9536 | 416.1765 | 383.6737 | 404.2368 | 359.5675
1471.0354 | 387.9947 | 183.1274 | 460.5015 | 416.6862 | 383.8069 | 403.5465 | 358.8366
1472.0354 | 389.9227 | 183.364 | 461.5225 | 416.6279 | 383.1575 | 403.6892 | 358.8667
1473.0354 | 391.2299 | 183.7357 | 460.3186 | 416.4861 | 383.9412 | 404.5851 | 359.8738
1474.0354 | 391.8825 | 183.6399 | 459.9053 | 416.8162 | 385.5246 | 405.8107 | 360.548
1475.0354 | 393.1117 | 183.7068 | 460.1527 | 416.9362 | 384.7284 | 407.0538 | 361.2395
1476.0354 | 393.3076 | 183.8563 | 460.2285 | 417.4908 | 385.4403 | 407.6075 | 361.2232
1477.0354 | 393.9531 | 184.059 | 460.7774 | 417.8961 | 387.6443 | 407.7308 | 361.5144
1478.0354 | 393.9628 | 184.1043 | 460.0709 | 417.733 | 387.7891 | 408.1371 | 360.9596
1479.0354 | 393.4629 | 184.5149 | 460.476 | 417.612 | 388.2966 | 408.7733 | 361.532
1480.0354 | 394.4165 | 184.2626 | 461.1334 | 417.9353 | 387.3238 | 410.3246 | 361.5973
1481.0354 | 393.6214 | 184.4099 | 460.7525 | 417.7958 | 387.0104 | 410.3821 | 360.8236
1482.0354 | 393.3937 | 184.8132 | 460.6091 | 418.7124 | 387.0919 | 410.1906 | 360.0279
1483.0354 | 394.4257 | 184.8563 | 462.8332 | 418.3702 | 387.2733 | 409.3322 | 359.2375
1484.0354 | 393.7265 | 184.999 | 463.8835 | 418.3952 | 386.7966 | 408.9779 | 359.8723
1485.0354 | 395.2027 | 185.0333 | 463.7761 | 418.5648 | 386.574 | 408.4469 | 360.79
1486.0354 | 394.7548 | 185.27 | 462.6452 | 419.2085 | 385.6773 | 408.2943 | 361.6267
1487.0354 | 395.1166 | 185.2951 | 462.2493 | 419.1768 | 384.6686 | 408.0065 | 361.1534
1488.0354 | 394.4813 | 185.3686 | 462.2015 | 419.3765 | 384.75 | 408.3149 | 360.1039
1489.0354 | 391.819 | 185.4587 | 462.4052 | 419.4901 | 384.787 | 407.3599 | 359.326
1490.0354 | 391.6836 | 185.6452 | 463.7824 | 419.9415 | 384.8647 | 407.1672 | 359.7241
1491.0354 | 391.5484 | 185.6777 | 462.7735 | 419.741 | 384.8039 | 407.5881 | 359.7809
1492.0354 | 390.6376 | 185.8341 | 462.3172 | 420.1232 | 384.2865 | 408.2697 | 359.8865
1493.0354 | 390.955 | 186.025 | 462.3982 | 419.9377 | 384.5132 | 408.1375 | 359.1245
1494.0354 | 390.2928 | 186.1624 | 462.7861 | 420.3086 | 385.887 | 407.2901 | 358.0178
1495.0354 | 389.6027 | 186.3623 | 462.4766 | 420.7013 | 386.2255 | 406.8404 | 357.9099
1496.0354 | 388.9301 | 186.5684 | 462.3138 | 421.4298 | 385.9158 | 405.5287 | 357.816
1497.0354 | 387.9288 | 186.5441 | 462.6557 | 421.4007 | 385.6385 | 404.0428 | 357.1739
1498.0354 | 387.2836 | 186.5108 | 462.9168 | 421.9333 | 385.3703 | 403.3699 | 356.6517
1499.0354 | 387.2 | 186.7585 | 462.9256 | 422.6681 | 385.4826 | 404.3076 | 357.3816
1500.0354 | 385.5702 | 186.7605 | 464.0116 | 423.3729 | 385.1974 | 403.2022 | 357.8073
1501.0354 | 384.5318 | 186.9677 | 463.6601 | 422.4608 | 384.6402 | 403.014 | 356.411
1502.0354 | 383.6683 | 186.9603 | 463.9127 | 422.0996 | 384.6699 | 402.8769 | 356.202
1503.0354 | 383.6646 | 187.0309 | 463.766 | 422.6036 | 384.3888 | 402.4085 | 356.0664
1504.0354 | 382.8433 | 187.2412 | 463.9684 | 423.227 | 383.869 | 402.3121 | 356.2541
1505.0354 | 383.0877 | 187.3584 | 464.2691 | 423.4614 | 383.9888 | 402.1182 | 356.3105
1506.0354 | 383.6558 | 187.4548 | 464.3273 | 423.107 | 383.8714 | 402.5728 | 356.3166
1507.0354 | 382.5615 | 187.5211 | 464.9468 | 423.1522 | 383.6776 | 402.827 | 356.7933
1508.0354 | 381.9691 | 187.6032 | 464.2433 | 423.2831 | 383.5945 | 402.4478 | 356.8963
1509.0354 | 380.4341 | 187.7814 | 465.0142 | 423.3913 | 383.2703 | 401.6399 | 356.5476
1510.0354 | 380.9825 | 187.967 | 466.2045 | 423.65 | 382.9912 | 402.3928 | 357.1317
1511.0354 | 381.9714 | 188.0333 | 465.4052 | 423.8994 | 382.3812 | 402.1341 | 357.3995
1512.0354 | 382.7438 | 188.1692 | 464.9584 | 424.3704 | 382.1245 | 402.631 | 357.963
1513.0354 | 382.2524 | 188.4026 | 465.1972 | 424.5259 | 381.4936 | 401.7916 | 357.0635
1514.0354 | 382.5783 | 188.4894 | 465.5042 | 424.9241 | 381.2522 | 401.7416 | 357.4616
1515.0354 | 381.6843 | 188.479 | 464.8231 | 424.6521 | 381.2644 | 401.2857 | 357.364
1516.0354 | 381.0879 | 188.5632 | 464.6491 | 424.9168 | 381.1116 | 402.0517 | 356.4491
1517.0354 | 379.6383 | 188.6145 | 464.5746 | 424.9758 | 381.803 | 402.5409 | 356.732
1518.0354 | 378.4768 | 188.9024 | 464.2267 | 425.3293 | 381.3951 | 400.7985 | 355.6139
1519.0354 | 377.0906 | 189.165 | 464.1538 | 426.2223 | 380.7986 | 398.0863 | 353.5679
1520.0354 | 375.9179 | 189.2344 | 464.2804 | 425.8286 | 380.5573 | 396.2442 | 352.6085
1521.0354 | 375.0542 | 189.2835 | 465.5991 | 425.4941 | 380.8131 | 396.168 | 352.3384
1522.0354 | 373.6183 | 189.2944 | 465.1487 | 425.9097 | 380.8603 | 396.586 | 353.2906
1523.0354 | 372.336 | 189.3985 | 466.1889 | 425.8076 | 380.1256 | 396.3514 | 353.7096
1524.0354 | 372.4005 | 189.5029 | 465.987 | 425.8054 | 380.3779 | 396.4274 | 353.8216
1525.0354 | 371.164 | 189.572 | 465.2148 | 426.2419 | 380.8104 | 396.3012 | 354.3645
1526.0354 | 372.0187 | 189.9751 | 465.2379 | 426.4035 | 381.5797 | 396.1711 | 354.3149
1527.0354 | 373.0883 | 190.1196 | 465.8809 | 426.9526 | 381.0792 | 396.1589 | 353.5583
1528.0354 | 373.5749 | 190.1002 | 465.4615 | 426.9615 | 380.8299 | 396.7465 | 353.9676
1529.0354 | 374.1707 | 190.3612 | 465.1286 | 426.776 | 380.7746 | 396.87 | 353.2227
1530.0354 | 375.2474 | 190.5689 | 465.1868 | 426.6435 | 381.3608 | 398.0975 | 353.0845
1531.0354 | 375.8032 | 190.5015 | 465.4547 | 427.7476 | 381.3799 | 398.3097 | 353.5019
1532.0354 | 374.7558 | 190.6111 | 465.0335 | 429.0853 | 381.088 | 397.1498 | 353.5657
1533.0354 | 374.7255 | 190.6883 | 464.5883 | 428.1905 | 380.8283 | 396.9127 | 353.4084
1534.0354 | 374.172 | 190.846 | 465.0383 | 427.9519 | 380.7629 | 397.4673 | 352.8978
1535.0354 | 373.2078 | 190.9506 | 465.5788 | 427.8653 | 380.6427 | 396.741 | 352.6109
1536.0354 | 373.4041 | 191.1503 | 465.4972 | 427.7584 | 380.2315 | 397.1312 | 352.8505
1537.0354 | 373.8553 | 191.1888 | 465.8575 | 428.2624 | 380.1278 | 396.5828 | 353.3482
1538.0354 | 377.5455 | 191.314 | 466.5404 | 428.4954 | 379.6287 | 396.2473 | 353.4539
1539.0354 | 379.4241 | 191.562 | 466.7246 | 428.4093 | 379.2767 | 397.1654 | 354.6253
1540.0354 | 380.8416 | 191.6899 | 466.5588 | 428.3918 | 379.0866 | 396.7663 | 354.6194
1541.0354 | 382.1608 | 191.7161 | 466.7753 | 428.5663 | 379.0015 | 396.5489 | 355.7222
1542.0354 | 383.7761 | 191.8159 | 466.6231 | 429.1832 | 378.5009 | 396.9447 | 355.866
1543.0354 | 384.2037 | 191.9461 | 467.8226 | 429.7769 | 378.6944 | 397.0579 | 356.1013
1544.0354 | 384.8542 | 192.0169 | 468.5433 | 429.1389 | 378.799 | 398.145 | 355.4896
1545.0354 | 386.5968 | 192.1949 | 468.9709 | 429.0973 | 378.2977 | 398.9641 | 355.6727
1546.0354 | 388.3804 | 192.3152 | 467.437 | 429.0139 | 378.3871 | 398.9733 | 356.2519
1547.0354 | 389.6549 | 192.5344 | 469.3061 | 429.7157 | 378.0822 | 398.0985 | 355.5891
1548.0354 | 391.0409 | 192.4907 | 469.405 | 429.7043 | 378.9173 | 398.942 | 356.7022
1549.0354 | 392.5264 | 192.589 | 469.5735 | 429.8204 | 379.1187 | 398.4484 | 356.4304
1550.0354 | 393.0268 | 192.8045 | 469.0257 | 429.9793 | 379.8687 | 398.0505 | 355.6343
1551.0354 | 393.62 | 193.066 | 468.913 | 429.6774 | 380.8108 | 398.0403 | 356.0557
1552.0354 | 394.1712 | 193.0408 | 469.4882 | 430.3228 | 380.8947 | 399.014 | 357.4389
1553.0354 | 393.5944 | 193.0469 | 468.6609 | 429.9158 | 380.6548 | 398.8368 | 358.0714
1554.0354 | 392.4967 | 193.2067 | 468.3757 | 430.0843 | 380.1096 | 398.3717 | 357.3688
1555.0354 | 391.8402 | 193.2607 | 468.9588 | 430.4374 | 379.7196 | 397.1752 | 356.2752
1556.0354 | 392.5915 | 193.5476 | 469.7223 | 430.0989 | 379.7571 | 396.9264 | 356.1391
1557.0354 | 394.5451 | 193.6448 | 469.3887 | 430.0822 | 378.9629 | 397.8554 | 356.4888
1558.0354 | 396.5852 | 193.6675 | 469.3095 | 430.5137 | 378.7168 | 398.9387 | 356.7739
1559.0354 | 399.7556 | 193.7113 | 469.2844 | 430.0238 | 379.0013 | 400.7895 | 356.2198
1560.0354 | 398.6323 | 193.7124 | 470.2874 | 429.9902 | 378.9647 | 402.899 | 356.6966
1561.0354 | 400.2832 | 194.101 | 472.0032 | 430.3353 | 378.9691 | 403.617 | 357.4154
1562.0354 | 401.3384 | 194.239 | 471.9288 | 431.0616 | 378.6242 | 403.3096 | 357.6394
1563.0354 | 399.9776 | 194.3105 | 472.2181 | 431.0821 | 378.3253 | 402.7688 | 357.3882
1564.0354 | 402.0579 | 194.5701 | 471.9229 | 430.8901 | 377.7296 | 402.2358 | 356.7885
1565.0354 | 402.8942 | 194.7536 | 472.0941 | 430.8333 | 377.4672 | 401.8253 | 357.2618
1566.0354 | 402.9271 | 194.7814 | 471.5168 | 430.8269 | 377.2628 | 401.2114 | 357.7517
1567.0354 | 404.2074 | 194.7327 | 471.0205 | 431.3998 | 377.3435 | 402.656 | 358.3562
1568.0354 | 408.1116 | 194.9038 | 470.6024 | 431.0476 | 378.7556 | 403.0123 | 358.3567
1569.0354 | 413.2463 | 195.0753 | 470.6522 | 432.1777 | 381.1233 | 403.608 | 358.2864
1570.0354 | 430.5992 | 195.0683 | 471.3987 | 432.5596 | 381.6771 | 403.5542 | 357.3378
1571.0354 | 429.234 | 195.3055 | 471.3025 | 432.1651 | 382.4916 | 404.0994 | 356.809
1572.0354 | 427.5391 | 195.4937 | 470.9598 | 431.971 | 383.0843 | 404.2356 | 356.2335
1573.0354 | 431.0582 | 195.6382 | 470.7222 | 431.82 | 383.1246 | 403.6965 | 355.6776
1574.0354 | 434.3293 | 195.705 | 471.1451 | 432.702 | 383.5554 | 402.999 | 355.8553
1575.0354 | 432.6716 | 195.6899 | 472.0876 | 432.3342 | 384.5483 | 403.4462 | 355.6111
1576.0354 | 430.9108 | 195.7104 | 471.8693 | 431.9265 | 383.7846 | 403.0388 | 355.3623
1577.0354 | 431.1111 | 195.9302 | 471.3283 | 432.7731 | 382.9429 | 403.805 | 355.5314
1578.0354 | 429.0068 | 196.1708 | 472.6968 | 432.2321 | 383.4251 | 403.1331 | 354.6661
1579.0354 | 428.8853 | 196.4466 | 472.0351 | 432.0835 | 383.0462 | 403.1117 | 354.6287
1580.0354 | 428.0983 | 196.6257 | 471.9593 | 432.5669 | 381.8732 | 403.3634 | 355.2749
1581.0354 | 429.4499 | 196.6658 | 473.4054 | 432.8444 | 380.8045 | 403.7677 | 355.2819
1582.0354 | 428.6227 | 196.7067 | 473.7126 | 432.8177 | 380.5946 | 403.5081 | 356.4544
1583.0354 | 427.2262 | 196.8277 | 473.9408 | 433.0967 | 381.0531 | 403.1316 | 356.1852
1584.0354 | 426.2354 | 196.8519 | 473.4563 | 433.2635 | 381.0955 | 403.206 | 357.0449
1585.0354 | 425.8728 | 196.9984 | 472.4755 | 432.9273 | 380.7295 | 403.9669 | 356.7723
1586.0354 | 424.1334 | 197.2072 | 472.9184 | 433.3082 | 380.6759 | 405.4539 | 356.4937
1587.0354 | 422.051 | 197.3014 | 472.7788 | 433.5139 | 381.3573 | 406.9305 | 356.4879
1588.0354 | 425.1421 | 197.2778 | 473.3259 | 434.0648 | 382.3568 | 407.1515 | 355.7862
1589.0354 | 425.8129 | 197.3113 | 472.6431 | 434.2576 | 383.7541 | 407.7541 | 356.3039
1590.0354 | 430.8704 | 197.4267 | 474.3802 | 434.2688 | 383.7084 | 407.8674 | 357.2939
1591.0354 | 437.3549 | 197.6081 | 474.5729 | 435.1472 | 383.7807 | 408.5341 | 358.023
1592.0354 | 440.3099 | 197.7895 | 473.6721 | 434.3057 | 383.6296 | 408.6663 | 358.1552
1593.0354 | 443.8078 | 197.8775 | 474.1176 | 434.817 | 384.6325 | 409.0238 | 357.816
1594.0354 | 445.3626 | 198.1866 | 475.3912 | 434.831 | 383.9168 | 409.3775 | 357.5971
1595.0354 | 446.249 | 198.0948 | 474.6483 | 434.6739 | 383.4822 | 408.6338 | 357.4104
1596.0354 | 445.0682 | 198.1903 | 476.0315 | 434.8278 | 384.3193 | 408.9615 | 357.6614
1597.0354 | 451.9275 | 198.3208 | 475.9447 | 434.9365 | 384.5259 | 409.2342 | 358.9248
1598.0354 | 454.6982 | 198.6011 | 476.1154 | 435.0299 | 384.716 | 409.6714 | 360.2728
1599.0354 | 455.6984 | 198.5744 | 475.1235 | 435.23 | 385.1589 | 410.2904 | 361.5
1600.0354 | 459.2832 | 198.8214 | 475.5517 | 435.538 | 385.9315 | 412.4974 | 362.3818
1601.0354 | 461.9859 | 199.047 | 476.4193 | 435.4428 | 386.419 | 412.7104 | 363.1576
1602.0354 | 466.5995 | 198.9648 | 476.1915 | 435.5051 | 385.7032 | 411.9477 | 362.3413
1603.0354 | 469.8208 | 199.166 | 476.5336 | 435.4095 | 385.4318 | 412.5142 | 362.9216
1604.0354 | 468.599 | 199.37 | 477.6267 | 435.7449 | 385.3218 | 413.4084 | 364.1553
1605.0354 | 467.2814 | 199.4231 | 477.5449 | 435.6699 | 385.8835 | 414.1571 | 365.1189
1606.0354 | 465.1639 | 199.5749 | 477.381 | 435.5804 | 385.705 | 414.2966 | 365.4317
1607.0354 | 463.0874 | 199.6742 | 477.114 | 435.377 | 385.4273 | 415.0557 | 365.5896
1608.0354 | 468.7999 | 199.8598 | 476.9732 | 435.8727 | 385.4684 | 415.884 | 365.2788
1609.0354 | 467.9719 | 199.8974 | 476.5775 | 436.3052 | 385.4292 | 416.6004 | 363.9272
1610.0354 | 480.0058 | 199.8585 | 477.5762 | 437.5439 | 386.3037 | 416.9766 | 363.7895
1611.0354 | 480.4838 | 200.0144 | 477.0779 | 437.2899 | 386.9314 | 417.2787 | 364.1291
1612.0354 | 489.0835 | 200.1622 | 476.8414 | 437.3962 | 387.7514 | 417.5769 | 365.524
1613.0354 | 502.371 | 200.4114 | 476.5562 | 436.5436 | 388.1394 | 417.9205 | 366.6003
1614.0354 | 508.7026 | 200.5305 | 476.9511 | 436.7139 | 388.0235 | 419.0549 | 367.2998
1615.0354 | 508.0934 | 200.6596 | 476.9077 | 437.2552 | 387.8993 | 419.4565 | 367.1578
1616.0354 | 508.0675 | 200.6962 | 477.0364 | 438.0969 | 388.0267 | 418.828 | 366.912
1617.0354 | 510.9483 | 200.8605 | 476.7221 | 438.068 | 389.0152 | 417.9842 | 366.985
1618.0354 | 522.0472 | 201.0168 | 476.7391 | 437.2205 | 389.0242 | 418.3354 | 366.6963
1619.0354 | 518.9699 | 201.2968 | 477.8432 | 437.2163 | 389.5606 | 417.8193 | 366.5511
1620.0354 | 515.1837 | 201.2318 | 477.6195 | 437.151 | 389.1179 | 418.7426 | 367.2742
1621.0354 | 518.8771 | 201.3094 | 477.7343 | 437.6504 | 388.5163 | 420.9391 | 367.076
1622.0354 | 512.0546 | 201.4217 | 478.0223 | 437.3573 | 388.4346 | 422.1015 | 368.0195
1623.0354 | 510.7344 | 201.4289 | 477.4591 | 437.7204 | 388.2799 | 421.1771 | 367.9856
1624.0354 | 524.9142 | 201.569 | 478.0892 | 437.6352 | 388.0701 | 421.2861 | 367.6109
1625.0354 | 525.724 | 201.6859 | 478.4946 | 437.6096 | 387.7426 | 422.0259 | 368.0223
1626.0354 | 531.0708 | 201.896 | 478.3763 | 437.9254 | 386.3132 | 422.1606 | 367.4256
1627.0354 | 526.0601 | 201.9275 | 479.5501 | 438.3357 | 385.6869 | 422.521 | 367.7613
1628.0354 | 526.997 | 202.0329 | 479.3006 | 438.3263 | 385.8904 | 423.4283 | 368.1802
1629.0354 | 530.304 | 202.1384 | 479.5523 | 438.1909 | 385.7151 | 424.2629 | 368.2216
1630.0354 | 527.4886 | 202.2211 | 479.272 | 438.6196 | 386.5168 | 424.2197 | 368.6151
1631.0354 | 520.2234 | 202.2514 | 479.2978 | 438.6994 | 386.6528 | 424.6946 | 368.7969
1632.0354 | 521.3597 | 202.4386 | 479.6812 | 438.7728 | 387.5574 | 423.9582 | 367.9981
1633.0354 | 516.7683 | 202.6279 | 479.5644 | 438.9606 | 387.7798 | 423.402 | 368.5179
1634.0354 | 529.7409 | 202.7266 | 478.2989 | 439.0453 | 387.5023 | 423.7322 | 368.9132
1635.0354 | 539.9238 | 202.8047 | 478.2477 | 439.6243 | 387.5663 | 424.63 | 368.569
1636.0354 | 553.0269 | 202.8386 | 479.2658 | 439.2773 | 388.5427 | 423.5046 | 368.5741
1637.0354 | 560.5819 | 203.0357 | 479.8397 | 439.6995 | 388.7899 | 423.2112 | 368.1178
1638.0354 | 572.2828 | 203.1258 | 479.5107 | 439.1097 | 388.4667 | 422.1947 | 367.8551
1639.0354 | 563.6667 | 203.2538 | 480.4038 | 438.9569 | 387.6027 | 425.0933 | 369.1103
1640.0354 | 567.7036 | 203.6011 | 481.0277 | 438.9067 | 387.0407 | 426.5719 | 370.3435
1641.0354 | 565.3226 | 203.7063 | 480.489 | 439.4753 | 387.2463 | 426.9427 | 371.7105
1642.0354 | 558.3574 | 203.6746 | 479.8456 | 439.2784 | 387.046 | 426.9385 | 371.5085
1643.0354 | 549.206 | 203.7107 | 479.7887 | 439.3956 | 386.7706 | 427.7613 | 370.7697
1644.0354 | 552.682 | 203.9354 | 481.1291 | 439.274 | 387.3245 | 428.4662 | 369.5482
1645.0354 | 549.0742 | 204.0828 | 480.6084 | 439.6297 | 387.6078 | 428.3918 | 369.9556
1646.0354 | 539.6568 | 204.1255 | 480.197 | 439.5498 | 387.6115 | 429.9145 | 370.0905
1647.0354 | 534.9927 | 204.274 | 480.6364 | 439.7252 | 387.3744 | 428.9388 | 369.8999
1648.0354 | 529.9089 | 204.3957 | 480.4766 | 439.6831 | 387.4017 | 427.9405 | 369.3065
1649.0354 | 545.1674 | 204.5248 | 481.5767 | 439.5253 | 387.0576 | 428.8456 | 369.2131
1650.0354 | 537.0067 | 204.5831 | 481.4628 | 439.7049 | 386.9035 | 429.6422 | 369.1945
1651.0354 | 547.9874 | 204.7258 | 482.1027 | 440.4045 | 386.3322 | 430.1843 | 369.1401
1652.0354 | 563.064 | 204.833 | 482.7741 | 440.0515 | 385.6514 | 429.9039 | 370.0421
1653.0354 | 574.6912 | 205.1175 | 483.9187 | 439.8288 | 385.1017 | 429.6092 | 369.9119
1654.0354 | 565.0313 | 205.2944 | 483.958 | 439.7407 | 384.2544 | 428.3557 | 370.2793
1655.0354 | 557.3572 | 205.4442 | 483.4765 | 439.7449 | 384.3647 | 428.8654 | 372.1107
1656.0354 | 548.1546 | 205.4896 | 483.2819 | 439.9262 | 383.9887 | 427.9249 | 371.8655
1657.0354 | 538.8977 | 205.46 | 483.2547 | 440.5275 | 383.5884 | 426.8786 | 371.6701
1658.0354 | 534.41 | 205.4592 | 483.1129 | 440.4839 | 383.2895 | 426.1503 | 371.3655
1659.0354 | 536.4825 | 205.6078 | 483.0801 | 440.6187 | 383.8957 | 426.0557 | 371.7358
1660.0354 | 548.8364 | 205.757 | 482.9014 | 440.2489 | 384.4334 | 426.0577 | 371.6438
1661.0354 | 540.7094 | 205.9409 | 483.3739 | 439.9541 | 385.0967 | 426.2153 | 371.0572
1662.0354 | 550.9336 | 206.1167 | 483.5346 | 440.0296 | 384.5322 | 425.9888 | 371.5769
1663.0354 | 566.6676 | 206.4036 | 483.2158 | 440.6994 | 384.0673 | 426.073 | 370.9479
1664.0354 | 551.6858 | 206.3471 | 483.5955 | 440.6977 | 383.7307 | 425.167 | 370.2724
1665.0354 | 543.9062 | 206.3835 | 483.0209 | 440.7848 | 383.8373 | 423.5214 | 369.4658
1666.0354 | 536.7948 | 206.3939 | 482.6428 | 440.632 | 384.1362 | 422.0472 | 368.6701
1667.0354 | 524.6441 | 206.458 | 483.5661 | 441.3148 | 384.6387 | 420.1468 | 367.1561
1668.0354 | 516.2489 | 206.5904 | 483.9217 | 440.6338 | 385.3325 | 419.2832 | 366.0854
1669.0354 | 508.1324 | 206.8775 | 484.1062 | 441.0585 | 386.055 | 420.3759 | 367.4586
1670.0354 | 501.2426 | 206.9038 | 484.8157 | 440.6773 | 386.9833 | 420.1327 | 368.0001
1671.0354 | 516.949 | 206.9713 | 484.3458 | 440.634 | 386.3376 | 419.9174 | 367.7727
1672.0354 | 503.8883 | 207.2602 | 484.2568 | 440.9377 | 387.0971 | 420.4546 | 367.6652
1673.0354 | 494.2412 | 207.4523 | 485.6339 | 440.7183 | 387.1781 | 420.0842 | 368.393
1674.0354 | 491.351 | 207.4233 | 485.293 | 441.02 | 387.2782 | 420.235 | 368.616
1675.0354 | 485.1318 | 207.5393 | 485.1563 | 440.7369 | 387.0979 | 419.435 | 369.3968
1676.0354 | 479.5551 | 207.5888 | 484.8359 | 441.1969 | 387.2491 | 418.884 | 369.5452
1677.0354 | 477.7569 | 207.6378 | 484.8098 | 441.491 | 386.9163 | 417.6247 | 369.4335
1678.0354 | 471.2333 | 207.8663 | 484.2427 | 441.3108 | 387.5439 | 418.8611 | 370.2047
1679.0354 | 467.6854 | 207.9683 | 484.6592 | 441.3518 | 387.1339 | 418.9007 | 369.3112
1680.0354 | 463.6564 | 207.9591 | 484.9359 | 441.5018 | 387.8248 | 419.4495 | 370.1489
1681.0354 | 464.8862 | 207.9139 | 484.2553 | 440.8912 | 387.8583 | 419.641 | 369.4502
1682.0354 | 461.8957 | 207.9968 | 484.2863 | 441.1387 | 387.7173 | 421.1641 | 369.0764
1683.0354 | 461.4322 | 208.1606 | 485.2491 | 441.9086 | 387.5505 | 420.4439 | 368.1799
1684.0354 | 467.1442 | 208.2737 | 484.4927 | 441.8929 | 387.9409 | 421.6268 | 368.7291
1685.0354 | 469.6454 | 208.3991 | 484.468 | 442.5043 | 387.9622 | 422.5936 | 368.6242
1686.0354 | 466.339 | 208.4311 | 484.1803 | 442.3926 | 387.9678 | 420.8725 | 367.9576
1687.0354 | 460.8478 | 208.5299 | 484.3194 | 442.1568 | 388.0723 | 419.8936 | 367.3761
1688.0354 | 456.8434 | 208.6594 | 485.0386 | 441.8976 | 387.8839 | 418.7764 | 367.4018
1689.0354 | 453.9541 | 208.7738 | 485.4174 | 442.0114 | 387.8089 | 417.5219 | 367.3781
1690.0354 | 450.57 | 208.9164 | 484.4573 | 442.3013 | 388.1692 | 417.4703 | 368.1137
1691.0354 | 449.3403 | 208.9801 | 484.6966 | 442.5661 | 387.5462 | 415.8507 | 368.0598
1692.0354 | 445.5716 | 208.9974 | 484.4085 | 442.5151 | 386.9192 | 415.0784 | 367.8873
1693.0354 | 441.5004 | 209.0361 | 484.1081 | 442.5669 | 387.1446 | 415.9192 | 366.4717
1694.0354 | 441.8191 | 209.2755 | 484.7609 | 442.802 | 386.5031 | 414.053 | 365.2855
1695.0354 | 439.6239 | 209.4882 | 485.6078 | 443.1187 | 386.6846 | 414.0277 | 365.7136
1696.0354 | 437.4924 | 209.4526 | 484.8262 | 443.1993 | 386.9116 | 413.3941 | 365.2976
1697.0354 | 435.2441 | 209.4751 | 485.995 | 442.7817 | 387.2311 | 412.5932 | 365.2505
1698.0354 | 433.4981 | 209.7083 | 486.0665 | 443.0059 | 387.712 | 412.1858 | 365.2539
1699.0354 | 431.7926 | 209.8652 | 485.2597 | 443.2597 | 387.2481 | 412.5299 | 365.7756
1700.0354 | 431.3392 | 209.8776 | 485.3283 | 443.1923 | 386.9288 | 412.4343 | 365.6197
1701.0354 | 430.2625 | 210.0863 | 486.54 | 443.2629 | 386.8606 | 412.1553 | 365.1452
1702.0354 | 429.1493 | 210.238 | 486.5528 | 443.1559 | 386.1828 | 411.6968 | 365.2158
1703.0354 | 429.7317 | 210.3748 | 486.2033 | 443.3596 | 385.8102 | 412.1653 | 365.3843
1704.0354 | 429.169 | 210.3875 | 486.7784 | 443.5213 | 386.0799 | 413.0097 | 366.1951
1705.0354 | 428.2503 | 210.4674 | 486.1449 | 444.0978 | 386.4149 | 412.2473 | 366.3959
1706.0354 | 427.2559 | 210.5502 | 486.8354 | 443.6888 | 386.4026 | 413.3268 | 366.9488
1707.0354 | 426.3021 | 210.7066 | 487.5618 | 443.6737 | 386.288 | 413.043 | 366.981
1708.0354 | 425.8869 | 210.7332 | 486.7184 | 443.5148 | 386.2137 | 413.2231 | 367.5102
1709.0354 | 426.4847 | 210.8318 | 487.3895 | 444.1883 | 385.9521 | 413.5591 | 366.9195
1710.0354 | 425.6222 | 211.014 | 486.4451 | 444.4527 | 385.596 | 412.8452 | 367.0607
1711.0354 | 426.7717 | 211.1445 | 489.0979 | 444.1211 | 385.6159 | 412.1473 | 367.3263
1712.0354 | 428.5864 | 211.4024 | 488.8421 | 444.0784 | 385.9394 | 413.5539 | 368.2765
1713.0354 | 428.084 | 211.5473 | 488.374 | 444.36 | 385.7079 | 413.3489 | 368.3141
1714.0354 | 428.4258 | 211.5833 | 488.7308 | 444.5978 | 385.4931 | 412.2469 | 367.4203
1715.0354 | 430.4723 | 211.6469 | 488.1521 | 446.1669 | 386.425 | 412.0993 | 367.508
1716.0354 | 433.2402 | 211.8459 | 488.1926 | 445.157 | 387.1573 | 412.0361 | 366.9349
1717.0354 | 433.4728 | 211.8601 | 488.4587 | 445.1449 | 387.3358 | 412.1068 | 366.3908
1718.0354 | 431.0378 | 211.8251 | 488.7691 | 446.0452 | 388.4465 | 413.4037 | 367.5326
1719.0354 | 431.282 | 211.9953 | 488.3563 | 446.1181 | 388.9782 | 413.3011 | 368.3263
1720.0354 | 434.2779 | 212.1483 | 488.6619 | 445.6914 | 389.0527 | 412.6678 | 367.5074
1721.0354 | 436.3991 | 212.2643 | 489.5305 | 445.8111 | 389.2181 | 413.3365 | 367.4267
1722.0354 | 436.4326 | 212.5237 | 490.1799 | 446.6711 | 389.2326 | 414.9661 | 368.3547
1723.0354 | 435.6274 | 212.7829 | 490.6957 | 446.6868 | 389.6584 | 416.3326 | 368.9783
1724.0354 | 438.9846 | 212.7886 | 491.105 | 446.7976 | 390.0116 | 416.7092 | 368.2837
1725.0354 | 441.9178 | 212.8919 | 490.673 | 446.5175 | 390.0275 | 417.9535 | 368.4236
1726.0354 | 440.791 | 212.9567 | 490.8703 | 446.5599 | 390.3521 | 417.5048 | 368.8507
1727.0354 | 440.0795 | 213.0656 | 490.6057 | 446.6978 | 390.2566 | 417.4011 | 368.7924
1728.0354 | 439.979 | 213.2148 | 490.9659 | 446.582 | 390.0997 | 417.5045 | 369.1058
1729.0354 | 439.254 | 213.2849 | 490.9341 | 446.974 | 390.285 | 418.5451 | 369.0341
1730.0354 | 441.5676 | 213.4609 | 492.6012 | 447.3839 | 390.7272 | 418.9763 | 369.552
1731.0354 | 441.6273 | 213.7483 | 492.3015 | 447.2776 | 391.672 | 419.3357 | 370.3044
1732.0354 | 442.6043 | 213.7275 | 491.8467 | 447.6163 | 392.1091 | 419.4098 | 370.6763
1733.0354 | 448.0883 | 213.8273 | 492.018 | 447.2226 | 392.3669 | 419.8399 | 370.8691
1734.0354 | 449.6653 | 213.9142 | 491.5972 | 447.4699 | 392.4145 | 420.7419 | 371.3928
1735.0354 | 454.3409 | 213.99 | 491.9153 | 447.3625 | 393.0631 | 421.4499 | 371.6741
1736.0354 | 458.4557 | 214.1798 | 492.5392 | 447.3109 | 394.0545 | 423.6071 | 372.5882
1737.0354 | 461.894 | 214.2118 | 493.2202 | 447.6123 | 394.2604 | 425.9275 | 373.8809
1738.0354 | 461.9279 | 214.3192 | 492.3628 | 447.4438 | 394.3865 | 427.5152 | 374.8807
1739.0354 | 482.1864 | 214.3592 | 492.1987 | 447.3147 | 394.5494 | 430.9946 | 376.6123
1740.0354 | 484.511 | 214.6006 | 493.433 | 448.2817 | 394.7947 | 434.5619 | 378.2684
1741.0354 | 484.1324 | 214.7927 | 493.9449 | 449.0428 | 395.0213 | 434.6233 | 378.5758
1742.0354 | 487.7948 | 214.9028 | 493.3635 | 448.9642 | 395.5751 | 435.1325 | 378.0227
1743.0354 | 493.8125 | 215.1428 | 493.2931 | 448.5846 | 396.1196 | 434.6072 | 377.6058
1744.0354 | 490.806 | 215.2305 | 492.8791 | 448.7947 | 396.2189 | 433.774 | 377.4802
1745.0354 | 490.433 | 215.17 | 492.8176 | 448.098 | 396.6824 | 434.6393 | 377.7195
1746.0354 | 488.2533 | 215.4072 | 494.0571 | 448.1857 | 397.9041 | 435.4449 | 377.5935
1747.0354 | 483.9546 | 215.5565 | 493.8799 | 448.6267 | 398.0266 | 436.5056 | 377.4503
1748.0354 | 481.7021 | 215.6271 | 494.4625 | 449.6686 | 398.5306 | 436.1313 | 377.5388
1749.0354 | 478.7751 | 215.7053 | 495.0957 | 449.8345 | 399.0689 | 436.1038 | 377.9449
1750.0354 | 478.8038 | 215.8763 | 495.2022 | 449.9466 | 399.8567 | 434.9028 | 377.6939
1751.0354 | 478.283 | 216.09 | 495.4588 | 449.831 | 399.9803 | 434.6396 | 377.4351
1752.0354 | 476.1076 | 216.2034 | 495.8469 | 449.7276 | 400.0338 | 432.9853 | 377.7871
1753.0354 | 475.1711 | 216.274 | 495.74 | 450.1198 | 399.8942 | 431.0523 | 377.5103
1754.0354 | 479.9208 | 216.4677 | 495.9879 | 450.8225 | 400.2984 | 430.638 | 376.9111
1755.0354 | 485.0756 | 216.6768 | 496.2958 | 450.6646 | 400.469 | 430.8461 | 375.798
1756.0354 | 491.1818 | 217.0066 | 498.7771 | 450.5456 | 400.6987 | 430.1781 | 375.1976
1757.0354 | 490.0043 | 217.1326 | 497.3772 | 449.9756 | 400.1415 | 427.5925 | 373.8424
1758.0354 | 486.5561 | 216.9953 | 496.8553 | 450.2462 | 399.9836 | 427.6154 | 374.5764
1759.0354 | 485.4135 | 217.0956 | 496.194 | 450.5485 | 399.8478 | 428.8986 | 374.4974
1760.0354 | 484.7779 | 217.1683 | 496.0237 | 450.8038 | 400.1502 | 432.1617 | 376.0541
1761.0354 | 482.1438 | 217.2377 | 496.7235 | 450.7403 | 400.1948 | 432.8532 | 376.1059
1762.0354 | 480.7353 | 217.4701 | 496.7979 | 450.9482 | 399.9092 | 432.0238 | 376.3131
1763.0354 | 478.6558 | 217.5684 | 496.6432 | 450.5925 | 400.3885 | 433.0817 | 376.9422
1764.0354 | 477.9692 | 217.6134 | 496.2932 | 451.0016 | 401.3582 | 434.2026 | 377.0743
1765.0354 | 477.7513 | 217.7601 | 496.4896 | 451.2017 | 402.1386 | 434.0966 | 377.0348
1766.0354 | 478.0433 | 217.7851 | 496.5482 | 451.4677 | 402.6634 | 433.1662 | 376.3357
1767.0354 | 475.7091 | 217.8817 | 496.7243 | 451.4531 | 403.4629 | 433.9278 | 376.5577
1768.0354 | 472.1607 | 218.0235 | 496.7053 | 451.3332 | 403.8244 | 433.023 | 376.4798
1769.0354 | 472.7962 | 218.2034 | 496.4471 | 451.4948 | 403.0703 | 430.3364 | 375.1154
1770.0354 | 473.799 | 218.3493 | 498.6276 | 452.2231 | 402.6819 | 430.1923 | 375.0439
1771.0354 | 475.3933 | 218.5649 | 500.2259 | 452.2452 | 403.0299 | 431.5018 | 375.6034
1772.0354 | 474.9033 | 218.5964 | 498.0345 | 451.5619 | 403.8622 | 431.9407 | 375.5317
1773.0354 | 473.5248 | 218.9214 | 500.0131 | 452.2614 | 403.3947 | 431.4568 | 375.4656
1774.0354 | 473.9558 | 219.195 | 499.3595 | 452.2821 | 402.8685 | 431.838 | 376.5365
1775.0354 | 472.1028 | 219.1577 | 498.8454 | 452.6545 | 402.5059 | 430.5226 | 376.6274
1776.0354 | 475.23 | 219.2102 | 498.8756 | 452.2819 | 402.7354 | 430.9604 | 376.9871
1777.0354 | 476.6213 | 219.2289 | 498.3093 | 452.2015 | 403.4738 | 433.7046 | 377.4032
1778.0354 | 486.1237 | 219.2702 | 499.6655 | 452.6487 | 404.1622 | 438.1999 | 379.4326
1779.0354 | 484.9967 | 219.6212 | 500.8186 | 452.8453 | 404.9958 | 438.9913 | 380.5664
1780.0354 | 483.8824 | 219.8031 | 502.0376 | 452.9653 | 405.3301 | 439.6336 | 381.9206
1781.0354 | 484.0463 | 220.1278 | 502.8275 | 453.0072 | 405.1007 | 439.426 | 383.1338
1782.0354 | 484.7073 | 220.3029 | 502.4362 | 453.303 | 404.4132 | 438.8124 | 383.7925
1783.0354 | 485.0044 | 220.3623 | 501.9133 | 454.0633 | 404.6772 | 440.0794 | 384.7218
1784.0354 | 486.6838 | 220.4403 | 502.0172 | 454.076 | 405.1658 | 440.1773 | 385.4315
1785.0354 | 487.8845 | 220.4318 | 502.2322 | 453.829 | 405.4772 | 439.7372 | 385.2881
1786.0354 | 490.737 | 220.7711 | 501.4427 | 454.0272 | 405.8242 | 441.0146 | 386.0052
1787.0354 | 493.1776 | 220.7206 | 501.0488 | 453.399 | 406.5346 | 442.2098 | 386.192
1788.0354 | 503.8034 | 220.7556 | 501.009 | 453.0643 | 407.7513 | 450.2046 | 389.0177
1789.0354 | 506.9906 | 220.8712 | 501.0322 | 453.5261 | 409.0286 | 454.7626 | 390.5601
1790.0354 | 507.6785 | 220.9683 | 501.6053 | 453.9888 | 410.1369 | 458.0665 | 390.0609
1791.0354 | 506.3531 | 221.0568 | 501.0704 | 454.652 | 410.8195 | 459.6484 | 390.0892
1792.0354 | 506.5495 | 221.2225 | 501.0361 | 455.0697 | 411.6609 | 459.9942 | 389.8405
1793.0354 | 510.5271 | 221.4488 | 501.3577 | 455.1128 | 412.5927 | 460.1856 | 390.8
1794.0354 | 510.991 | 221.7019 | 503.1846 | 455.2458 | 413.2208 | 457.9058 | 390.6125
1795.0354 | 508.3141 | 221.782 | 503.3426 | 455.6844 | 413.7324 | 456.5068 | 390.1739
1796.0354 | 503.7828 | 221.9023 | 502.877 | 455.819 | 413.7818 | 454.4706 | 390.0011
1797.0354 | 500.8893 | 222.1063 | 504.1759 | 455.5134 | 413.696 | 452.6305 | 389.4317
1798.0354 | 499.8666 | 222.3279 | 503.5038 | 455.1841 | 413.3865 | 452.0828 | 389.6559
1799.0354 | 497.8249 | 222.4248 | 503.5607 | 455.3024 | 413.2814 | 451.9828 | 390.1547
1800.0354 | 495.3641 | 222.4536 | 502.8762 | 456.1487 | 412.7229 | 450.7219 | 389.9337
1801.0354 | 506.7067 | 222.7122 | 503.6422 | 456.2162 | 412.5572 | 449.2214 | 389.9115
1802.0354 | 506.5876 | 222.6783 | 504.1945 | 456.7381 | 412.6871 | 448.3161 | 390.0247
1803.0354 | 506.4661 | 222.9532 | 504.7398 | 456.5714 | 412.4063 | 446.9391 | 388.665
1804.0354 | 504.3068 | 223.1276 | 504.6761 | 456.3347 | 412.3815 | 445.9721 | 388.1331
1805.0354 | 508.1026 | 223.3013 | 505.1126 | 456.6762 | 412.1979 | 445.6 | 388.9592
1806.0354 | 507.1704 | 223.3886 | 506.8083 | 456.7863 | 412.4744 | 446.6796 | 390.3258
1807.0354 | 507.2531 | 223.5388 | 507.2604 | 457.0119 | 412.2755 | 445.9777 | 390.0616
1808.0354 | 506.6023 | 223.7931 | 507.147 | 457.0727 | 412.0465 | 445.1469 | 389.6969
1809.0354 | 508.7172 | 224.0928 | 507.9123 | 457.1269 | 411.3563 | 444.6738 | 389.7859
1810.0354 | 507.9027 | 224.3078 | 508.9584 | 458.3372 | 410.6279 | 444.4947 | 390.9198
1811.0354 | 507.9209 | 224.4718 | 511.2588 | 457.9258 | 410.156 | 444.9596 | 392.5053
1812.0354 | 507.9729 | 224.5203 | 511.1084 | 457.8169 | 409.6839 | 444.6542 | 391.9259
1813.0354 | 506.8464 | 224.6522 | 509.1689 | 458.2051 | 409.5646 | 443.4163 | 391.3146
1814.0354 | 503.7484 | 224.8519 | 508.2618 | 458.7184 | 409.2987 | 442.943 | 390.6125
1815.0354 | 506.8148 | 224.9027 | 507.9383 | 458.3854 | 409.368 | 442.4451 | 389.5684
1816.0354 | 510.4162 | 224.9802 | 508.801 | 457.9636 | 410.2945 | 445.538 | 390.3922
1817.0354 | 508.8133 | 225.0336 | 509.0857 | 457.8925 | 411.245 | 448.2041 | 390.982
1818.0354 | 509.1458 | 225.1123 | 508.5388 | 458.001 | 412.0402 | 452.1489 | 392.3517
1819.0354 | 510.9411 | 225.1188 | 508.2705 | 458.7347 | 413.1654 | 456.7286 | 392.8451
1820.0354 | 508.7202 | 225.4892 | 508.2838 | 458.5217 | 414.66 | 458.7535 | 392.8579
1821.0354 | 507.6422 | 225.677 | 508.2871 | 458.8758 | 416.2138 | 458.9848 | 393.0931
1822.0354 | 507.9628 | 225.7075 | 508.2299 | 459.3787 | 417.3009 | 458.0741 | 392.1592
1823.0354 | 504.1092 | 225.7927 | 508.1625 | 459.318 | 418.827 | 457.8604 | 392.4614
1824.0354 | 503.5594 | 226.1255 | 509.0246 | 458.5209 | 419.2568 | 457.0267 | 391.9063
1825.0354 | 502.0285 | 226.1178 | 509.2834 | 458.9276 | 419.7548 | 457.9447 | 392.0979
1826.0354 | 502.9699 | 226.2581 | 509.1563 | 459.3882 | 419.3253 | 456.7704 | 391.9959
1827.0354 | 515.5624 | 226.4152 | 510.0255 | 459.5269 | 420.467 | 459.6104 | 392.8788
1828.0354 | 524.7264 | 226.5081 | 510.1296 | 459.6494 | 420.8143 | 460.8485 | 395.0869
1829.0354 | 523.8464 | 226.718 | 511.0095 | 459.6385 | 420.913 | 461.391 | 396.059
1830.0354 | 522.5674 | 226.8982 | 512.3423 | 459.8991 | 421.1592 | 460.8591 | 396.8452
1831.0354 | 521.096 | 227.1313 | 511.5205 | 460.0117 | 420.7669 | 460.731 | 397.1683
1832.0354 | 516.2743 | 227.0627 | 510.2225 | 459.9918 | 420.9805 | 460.5308 | 397.7321
1833.0354 | 516.7508 | 227.2345 | 511.2474 | 460.1802 | 420.6751 | 459.654 | 397.6991
1834.0354 | 513.7692 | 227.3873 | 511.3153 | 460.6555 | 420.621 | 459.0539 | 397.8358
1835.0354 | 509.6216 | 227.6282 | 510.7765 | 460.6388 | 420.0914 | 458.4241 | 398.2654
1836.0354 | 505.5992 | 227.6175 | 510.4165 | 461.1389 | 419.7385 | 456.8419 | 397.7103
1837.0354 | 503.7699 | 227.7178 | 511.3551 | 461.7011 | 420.0682 | 455.9011 | 397.007
1838.0354 | 502.2668 | 228.022 | 513.1624 | 461.0702 | 419.9235 | 456.0704 | 397.6563
1839.0354 | 500.249 | 228.1759 | 512.5121 | 461.843 | 420.2303 | 456.1062 | 398.1239
1840.0354 | 498.7788 | 228.2962 | 510.9949 | 461.3444 | 420.6088 | 457.3253 | 397.4628
1841.0354 | 495.4087 | 228.376 | 511.2775 | 460.9553 | 420.9082 | 458.7593 | 397.9287
1842.0354 | 494.4152 | 228.5846 | 510.6271 | 461.6532 | 420.9331 | 457.8659 | 396.759
1843.0354 | 492.8815 | 228.859 | 511.9109 | 461.5054 | 420.7838 | 456.4703 | 395.6407
1844.0354 | 490.0485 | 228.7918 | 511.0929 | 461.2334 | 420.3046 | 457.493 | 395.5957
1845.0354 | 485.1165 | 228.7255 | 510.7983 | 461.3908 | 420.1709 | 456.7476 | 395.4265
1846.0354 | 481.2686 | 228.8394 | 510.9018 | 461.4814 | 419.5383 | 454.671 | 393.8302
1847.0354 | 478.4632 | 228.8203 | 510.8052 | 461.4242 | 419.2271 | 452.7193 | 392.5538
1848.0354 | 484.613 | 229.0579 | 511.0922 | 461.8763 | 419.5463 | 452.3937 | 392.1729
1849.0354 | 481.8455 | 229.0896 | 510.8241 | 461.9156 | 420.7189 | 451.6774 | 392.1793
1850.0354 | 480.428 | 229.3465 | 510.7791 | 462.2209 | 420.8142 | 451.1647 | 391.5995
1851.0354 | 478.2768 | 229.4193 | 511.3119 | 462.003 | 420.7203 | 452.1271 | 390.8904
1852.0354 | 474.2036 | 229.4978 | 510.9501 | 461.5997 | 420.6329 | 452.3225 | 391.2709
1853.0354 | 472.3524 | 229.6097 | 510.5744 | 461.5569 | 419.8465 | 451.967 | 391.4644
1854.0354 | 468.6766 | 229.6727 | 510.0669 | 461.7669 | 419.5095 | 451.6073 | 390.4452
1855.0354 | 464.1626 | 229.8384 | 509.8232 | 461.775 | 418.8463 | 450.8896 | 389.2738
1856.0354 | 462.1738 | 230.0227 | 509.5292 | 461.8662 | 418.5648 | 449.5152 | 388.464
1857.0354 | 462.9115 | 230.2009 | 509.4603 | 462.1623 | 418.8379 | 450.4686 | 388.4764
1858.0354 | 461.6982 | 230.3595 | 509.2749 | 462.9552 | 420.9705 | 452.1899 | 388.3182
1859.0354 | 459.8558 | 230.4093 | 509.4553 | 462.938 | 422.5449 | 452.0889 | 387.6018
1860.0354 | 459.837 | 230.476 | 509.3222 | 463.6077 | 422.6003 | 450.5382 | 387.0244
1861.0354 | 456.5626 | 230.5758 | 508.963 | 462.6992 | 423.0378 | 449.3554 | 386.1538
1862.0198 | 454.7918 | 230.6262 | 508.691 | 462.944 | 423.7583 | 447.9606 | 385.6002
1863.0354 | 453.6163 | 230.6922 | 508.5666 | 462.8861 | 424.327 | 445.9122 | 384.5354
1864.0354 | 452.728 | 230.7555 | 508.5217 | 463.5096 | 424.1199 | 444.7481 | 383.8605
1865.0354 | 453.0891 | 231.0634 | 508.2633 | 463.9225 | 424.0118 | 443.7191 | 383.7957
1866.0354 | 459.0142 | 231.1722 | 508.1118 | 464.3162 | 424.0738 | 442.9248 | 383.702
1867.0354 | 456.8758 | 231.0997 | 507.7492 | 464.2412 | 425.1227 | 443.2341 | 383.8117
1868.0354 | 454.3261 | 231.275 | 507.5837 | 464.7957 | 425.3173 | 441.8835 | 383.4841
1869.0354 | 451.6652 | 231.4151 | 507.3261 | 464.8061 | 425.3768 | 440.5762 | 382.3302
1870.0354 | 448.411 | 231.4161 | 507.1797 | 464.0459 | 424.8965 | 438.4519 | 381.5173
1871.0354 | 445.725 | 231.5775 | 507.4284 | 464.2621 | 424.374 | 437.612 | 381.1597
1872.0354 | 442.1604 | 231.6923 | 508.3006 | 464.7682 | 423.4554 | 436.9132 | 380.927
1873.0354 | 439.7163 | 231.7955 | 508.2613 | 464.4877 | 422.8022 | 436.7452 | 381.2274
1874.0354 | 437.8778 | 231.9713 | 506.9026 | 464.7601 | 422.4234 | 436.0201 | 380.6747
1875.0354 | 435.9139 | 232.0151 | 506.8009 | 464.6621 | 421.7502 | 434.1831 | 379.5565
1876.0354 | 435.08 | 232.2175 | 507.0357 | 464.2951 | 421.0975 | 432.5569 | 378.7685
1877.0354 | 435.2387 | 232.2567 | 507.1494 | 464.1368 | 421.0151 | 432.3704 | 378.3559
1878.0354 | 433.5783 | 232.3494 | 506.656 | 464.8873 | 420.7176 | 432.9875 | 378.0248
1879.0354 | 432.7375 | 232.4372 | 506.1919 | 465.5489 | 420.8242 | 433.4386 | 378.2984
1880.0354 | 432.4007 | 232.5117 | 506.1365 | 466.2949 | 420.6417 | 432.4595 | 377.8527
1881.0354 | 431.8082 | 232.6123 | 505.8616 | 466.2198 | 421.1546 | 432.0603 | 377.4456
1882.0354 | 431.006 | 232.6715 | 506.9577 | 465.4944 | 421.5325 | 431.7712 | 377.2219
1883.0354 | 431.3637 | 232.9208 | 506.4437 | 465.6012 | 421.1263 | 431.7139 | 377.5159
1884.0354 | 432.6093 | 232.9544 | 506.3603 | 465.5711 | 420.945 | 432.0262 | 378.5146
1885.0354 | 433.8658 | 233.0667 | 506.4793 | 465.9447 | 420.8189 | 433.0311 | 378.5607
1886.0354 | 433.883 | 233.2336 | 507.8787 | 465.9064 | 420.033 | 434.1464 | 379.7341
1887.0354 | 433.6208 | 233.5062 | 508.0262 | 465.9173 | 419.7917 | 434.4357 | 380.9633
1888.0354 | 435.4569 | 233.5665 | 506.7699 | 466.1781 | 419.6356 | 434.5465 | 381.6106
1889.0354 | 437.186 | 233.7767 | 510.2113 | 466.1798 | 420.3474 | 435.4537 | 382.9801
1890.0354 | 440.7082 | 233.7566 | 509.615 | 466.3647 | 420.3408 | 437.194 | 383.4831
1891.0354 | 442.3507 | 233.734 | 508.0975 | 466.4122 | 420.2954 | 438.6255 | 384.5499
1892.0354 | 442.1772 | 234.0694 | 509.3603 | 466.6937 | 419.8047 | 438.3102 | 385.4495
1893.0354 | 442.3733 | 234.3035 | 509.0551 | 466.6263 | 419.1651 | 439.0095 | 385.3567
1894.0354 | 444.9985 | 234.5016 | 507.8996 | 466.5048 | 419.6963 | 441.6258 | 386.6601
1895.0354 | 454.7411 | 234.5232 | 507.9921 | 467.0786 | 420.2085 | 445.4193 | 388.1433
1896.0354 | 453.7607 | 234.5532 | 507.9401 | 466.7338 | 420.7946 | 445.8038 | 389.2138
1897.0354 | 452.5891 | 234.5201 | 508.2888 | 467.1929 | 420.9308 | 445.1739 | 389.113
1898.0354 | 455.634 | 234.8958 | 508.7177 | 466.9775 | 421.0793 | 448.1801 | 390.3678
1899.0354 | 455.8821 | 234.7939 | 508.0634 | 467.7853 | 421.078 | 450.989 | 391.5766
1900.0354 | 455.9214 | 234.8482 | 508.043 | 468.0651 | 421.3279 | 449.8783 | 391.4454
1901.0354 | 456.9007 | 234.9239 | 508.1739 | 468.2608 | 422.1398 | 449.2647 | 391.3274
1902.0354 | 457.9285 | 235.0562 | 508.2833 | 467.9729 | 422.4218 | 449.0396 | 391.0625
1903.0354 | 458.9053 | 235.1999 | 508.7562 | 467.6255 | 422.8123 | 448.985 | 392.0692
1904.0354 | 457.9214 | 235.2802 | 508.9285 | 467.5136 | 423.1268 | 449.0862 | 393.0203
1905.0354 | 457.2454 | 235.4281 | 509.7144 | 467.761 | 423.1911 | 449.738 | 394.1602
1906.0354 | 457.8692 | 235.4495 | 508.8641 | 467.5954 | 423.0563 | 450.2699 | 395.5287
1907.0354 | 459.8713 | 235.6161 | 509.7141 | 467.9394 | 423.0085 | 451.5938 | 397.023
1908.0354 | 460.6542 | 235.7892 | 509.1417 | 468.2765 | 423.0124 | 455.8809 | 397.3616
1909.0354 | 458.6748 | 235.8684 | 508.6845 | 468.7704 | 423.279 | 455.021 | 397.3918
1910.0354 | 458.9572 | 236.045 | 509.2543 | 469.6303 | 423.5422 | 453.7383 | 396.7484
1911.0354 | 459.8156 | 236.2287 | 509.9892 | 468.7772 | 423.4017 | 452.5295 | 395.2474
1912.0354 | 459.9759 | 236.3157 | 509.2755 | 468.9896 | 423.782 | 452.067 | 394.7349
1913.0354 | 459.1024 | 236.4531 | 509.3274 | 469.1563 | 423.8744 | 451.0134 | 394.138
1914.0354 | 456.6725 | 236.5602 | 509.7102 | 469.0571 | 423.6749 | 450.3066 | 393.5777
1915.0354 | 456.1584 | 236.6425 | 509.0631 | 469.3293 | 423.4815 | 450.1702 | 394.0623
1916.0354 | 455.3535 | 236.8612 | 509.397 | 469.1432 | 423.419 | 450.0683 | 394.0271
1917.0354 | 455.4625 | 237.0228 | 509.7971 | 469.465 | 423.9882 | 449.7175 | 394.5762
1918.0354 | 455.2187 | 236.9933 | 509.1184 | 469.957 | 423.7679 | 448.5294 | 393.927
1919.0354 | 452.666 | 237.1351 | 509.4933 | 470.4118 | 423.3354 | 447.769 | 393.3098
1920.0354 | 452.4229 | 237.1735 | 509.3245 | 469.7718 | 423.8003 | 448.7624 | 394.1993
1921.0354 | 452.0654 | 237.4457 | 510.2632 | 469.8552 | 423.3769 | 449.626 | 394.6854
1922.0354 | 450.3329 | 237.587 | 509.5046 | 470.7338 | 424.2991 | 450.4169 | 396.7193
1923.0354 | 449.5478 | 237.6005 | 509.0689 | 470.3667 | 424.5237 | 449.5945 | 397.0595
1924.0354 | 452.0393 | 237.7302 | 508.8537 | 471.015 | 424.5014 | 450.1256 | 397.3975
1925.0354 | 451.2558 | 237.8987 | 509.7373 | 470.7918 | 425.5488 | 448.8555 | 397.8027
1926.0354 | 452.059 | 238.0844 | 509.3077 | 470.3653 | 425.2068 | 447.3788 | 396.3632
1927.0354 | 451.2164 | 238.1364 | 508.6371 | 470.4144 | 425.8317 | 448.4225 | 395.4287
1928.0354 | 450.4278 | 238.2967 | 509.168 | 470.5916 | 425.4169 | 448.591 | 395.0141
1929.0354 | 450.5842 | 238.2547 | 509.3007 | 470.3635 | 425.2855 | 448.5764 | 394.7872
1930.0354 | 451.1025 | 238.202 | 508.5872 | 470.3923 | 424.7401 | 448.7921 | 394.5849
1931.0354 | 450.254 | 238.2701 | 509.0794 | 470.544 | 424.1136 | 447.8362 | 394.5491
1932.0354 | 448.9455 | 238.5959 | 509.8374 | 470.8731 | 423.6169 | 447.4001 | 394.5201
1933.0354 | 445.7471 | 238.7577 | 509.1265 | 471.5929 | 423.7991 | 446.4825 | 394.9798
1934.0354 | 447.8018 | 238.8721 | 509.4041 | 471.9074 | 423.2199 | 444.9299 | 393.6205
1935.0354 | 448.6841 | 238.8767 | 509.4114 | 470.9681 | 423.1966 | 444.812 | 393.9816
1936.0354 | 448.8423 | 239.0413 | 509.7541 | 471.4474 | 423.7689 | 445.4523 | 394.3578
1937.0354 | 446.0838 | 239.2003 | 509.7791 | 471.972 | 423.8003 | 445.0837 | 394.6189
1938.0354 | 445.0818 | 239.3791 | 508.7793 | 471.6804 | 423.4837 | 444.1353 | 394.4953
1939.0354 | 443.2866 | 239.3301 | 509.6341 | 471.2275 | 424.0477 | 443.8897 | 394.638
1940.0354 | 443.663 | 239.3189 | 509.5084 | 471.2516 | 423.5137 | 442.719 | 394.1344
1941.0354 | 444.5277 | 239.4631 | 510.3829 | 471.2232 | 422.5865 | 442.5625 | 393.8349
1942.0354 | 444.6811 | 239.5832 | 509.7221 | 472.0126 | 422.3181 | 441.7547 | 394.0383
1943.0354 | 445.632 | 239.6057 | 511.1954 | 471.8775 | 422.379 | 440.9163 | 394.4792
1944.0354 | 447.3316 | 239.7206 | 511.937 | 471.7886 | 421.8648 | 441.4986 | 394.9095
1945.0354 | 447.3798 | 240.0393 | 511.5807 | 471.4789 | 421.8925 | 441.8227 | 395.8777
1946.0354 | 447.722 | 240.0882 | 510.9016 | 471.6024 | 421.1906 | 441.134 | 395.9525
1947.0354 | 449.1827 | 240.1677 | 510.5601 | 471.5213 | 420.2638 | 441.116 | 395.9029
1948.0354 | 448.8363 | 240.2269 | 509.6775 | 471.5929 | 420.3373 | 442.5568 | 395.8019
1949.0354 | 446.3661 | 240.3469 | 509.8879 | 471.892 | 420.5603 | 441.7917 | 394.7172
1950.0354 | 445.7935 | 240.4903 | 510.0337 | 471.4961 | 422.5785 | 442.4293 | 393.9498
1951.0354 | 444.1052 | 240.4262 | 509.5583 | 471.7184 | 422.5181 | 442.7176 | 393.5536
1952.0354 | 443.5406 | 240.5363 | 509.4185 | 471.68 | 423.2589 | 442.591 | 392.6398
1953.0354 | 443.4679 | 240.6411 | 509.7311 | 471.5963 | 423.4959 | 443.3366 | 391.9531
1954.0354 | 442.0913 | 240.6766 | 510.5147 | 472.0492 | 424.3814 | 443.7763 | 391.6454
1955.0354 | 441.5542 | 240.8025 | 509.9563 | 471.6486 | 424.6105 | 444.9171 | 391.6351
1956.0354 | 442.0709 | 241.0685 | 509.4291 | 471.4457 | 424.8586 | 446.7688 | 392.5174
1957.0354 | 444.5508 | 241.3129 | 510.3145 | 471.9244 | 425.1447 | 447.912 | 392.5638
1958.0354 | 446.3626 | 241.4033 | 512.799 | 472.4213 | 426.4705 | 449.5309 | 393.5722
1959.0354 | 448.3259 | 241.4873 | 513.3441 | 472.5692 | 425.8545 | 448.9797 | 393.5168
1960.0354 | 448.626 | 241.5018 | 511.3815 | 472.332 | 425.6582 | 447.8739 | 393.516
1961.0354 | 449.0536 | 241.721 | 511.3314 | 472.6968 | 425.3523 | 445.5889 | 392.3842
1962.0354 | 450.871 | 241.8271 | 513.0719 | 472.9574 | 425.157 | 444.5055 | 392.2129
1963.0354 | 455.5325 | 241.9841 | 513.5352 | 472.8705 | 426.6434 | 445.7688 | 392.0326
1964.0354 | 459.2782 | 242.0498 | 512.4497 | 473.634 | 427.4717 | 447.0235 | 392.1078
1965.0354 | 459.6051 | 242.3936 | 512.3514 | 472.7319 | 427.0516 | 445.0204 | 391.314
1966.0354 | 460.2273 | 242.421 | 513.6307 | 472.8557 | 426.4524 | 444.5466 | 390.7199
1967.0354 | 461.8997 | 242.8054 | 514.7692 | 472.8487 | 426.836 | 445.2997 | 392.588
1968.0354 | 463.2123 | 242.6965 | 514.4949 | 473.0549 | 426.3838 | 445.1108 | 393.0451
1969.0354 | 463.534 | 242.8283 | 513.9909 | 472.9844 | 426.3357 | 444.8036 | 393.5991
1970.0354 | 464.376 | 242.9664 | 515.306 | 473.0321 | 426.033 | 445.0563 | 393.902
1971.0354 | 466.3997 | 243.0164 | 514.8052 | 472.7025 | 425.7577 | 445.8807 | 395.2478
1972.0354 | 468.1471 | 243.0901 | 514.6014 | 472.9726 | 426.316 | 446.2585 | 396.1008
1973.0354 | 469.0142 | 243.0742 | 513.9567 | 472.9908 | 426.5768 | 446.8499 | 396.9158
1974.0354 | 469.097 | 243.0588 | 514.1978 | 472.9698 | 426.0345 | 447.0841 | 396.5801
1975.0354 | 469.0308 | 243.2487 | 514.411 | 473.4437 | 427.2122 | 447.2877 | 397.0214
1976.0354 | 469.4127 | 243.3837 | 514.5287 | 474.1589 | 428.1941 | 446.9052 | 397.219
1977.0354 | 468.4085 | 243.5098 | 515.2319 | 474.3193 | 428.0632 | 446.6399 | 397.0945
1978.0354 | 468.8048 | 243.5217 | 515.6581 | 474.186 | 427.9959 | 446.7441 | 396.9118
1979.0354 | 468.8645 | 243.7453 | 516.8631 | 474.0769 | 427.4596 | 446.2457 | 396.7575
1980.0354 | 468.8687 | 243.8589 | 515.9894 | 473.6839 | 427.3191 | 446.0404 | 396.2853
1981.0354 | 468.8966 | 243.8732 | 515.4373 | 473.9132 | 427.8204 | 445.8211 | 396.893
1982.0354 | 471.0004 | 244.0174 | 515.38 | 473.9979 | 427.5094 | 448.5705 | 398.0372
1983.0354 | 472.5129 | 244.185 | 515.3784 | 474.3199 | 427.2714 | 450.8795 | 398.8743
1984.0354 | 471.191 | 244.2519 | 514.9794 | 474.2544 | 427.2686 | 450.4573 | 398.4269
1985.0354 | 470.8694 | 244.456 | 514.9375 | 474.6748 | 428.2502 | 450.7772 | 398.6296
1986.0354 | 475.3393 | 244.382 | 514.8872 | 474.1205 | 429.457 | 449.1804 | 397.2522
1987.0354 | 473.295 | 244.4553 | 515.3223 | 475.0004 | 431.9111 | 449.6154 | 396.8305
1988.0354 | 472.1599 | 244.5833 | 515.616 | 474.9187 | 432.8936 | 449.2052 | 396.329
1989.0354 | 471.2203 | 244.6246 | 515.5144 | 474.9578 | 433.2629 | 448.4472 | 395.4006
1990.0354 | 470.2112 | 244.8012 | 515.3988 | 475.0287 | 433.3099 | 448.1684 | 395.4766
1991.0354 | 471.3676 | 244.9025 | 515.9923 | 475.3151 | 432.969 | 447.5786 | 395.1647
1992.0354 | 471.4106 | 245.0058 | 516.1106 | 475.0345 | 432.8425 | 448.5842 | 396.4781
1993.0354 | 469.8298 | 245.1505 | 515.8973 | 475.158 | 432.6046 | 448.3247 | 396.8796
1994.0354 | 469.5905 | 245.2656 | 515.8717 | 474.9951 | 432.9793 | 449.3616 | 397.2783
1995.0354 | 470.5824 | 245.3897 | 516.5821 | 475.2386 | 432.3203 | 450.115 | 397.5717
1996.0354 | 472.831 | 245.4519 | 516.957 | 475.761 | 432.8111 | 450.3692 | 398.3365
1997.0354 | 473.0165 | 245.4837 | 516.4427 | 475.4633 | 433.1068 | 449.3142 | 398.8055
1998.0354 | 474.0278 | 245.7746 | 517.8513 | 475.7873 | 432.5684 | 448.8997 | 399.1038
1999.0354 | 475.05 | 245.9087 | 517.4804 | 476.021 | 432.4467 | 448.2588 | 398.828
2000.0354 | 478.0295 | 246.1168 | 518.668 | 476.2493 | 431.7505 | 449.1755 | 399.491
2001.0354 | 480.6768 | 246.3543 | 520.3478 | 476.1003 | 432.139 | 451.9952 | 401.4019
2002.0354 | 479.4528 | 246.4105 | 518.72 | 476.1607 | 431.8884 | 453.4276 | 402.2029
2003.0354 | 477.0766 | 246.5743 | 517.5763 | 476.3569 | 432.3112 | 453.1113 | 401.8202
2004.0354 | 477.162 | 246.5967 | 517.7511 | 476.6383 | 433.5293 | 451.8654 | 400.7958
2005.0354 | 479.7509 | 246.6832 | 518.4526 | 478.2957 | 433.2012 | 451.6222 | 400.9337
2006.0354 | 479.2279 | 246.7497 | 518.5837 | 477.9298 | 432.9405 | 450.0911 | 400.7358
2007.0354 | 481.1771 | 246.8652 | 518.6751 | 477.0156 | 432.8344 | 449.3352 | 400.2833
2008.0354 | 480.334 | 246.9992 | 518.4901 | 476.9836 | 432.7581 | 450.4638 | 400.5091
2009.0354 | 479.1242 | 247.1357 | 518.1162 | 476.9817 | 432.8688 | 453.1696 | 401.5631
2010.0354 | 476.5843 | 247.3397 | 518.2223 | 477.4461 | 433.3208 | 455.0036 | 402.1423
2011.0354 | 474.8033 | 247.4227 | 518.3702 | 477.4146 | 434.0298 | 454.5197 | 401.7962
2012.0354 | 474.3858 | 247.4639 | 518.2039 | 477.7812 | 434.4509 | 455.0213 | 402.4834
2013.0354 | 472.6957 | 247.4669 | 517.6825 | 477.0373 | 435.0021 | 456.5676 | 402.2489
2014.0354 | 478.84 | 247.5046 | 517.5693 | 476.9121 | 436.5424 | 457.1046 | 401.3961
2015.0354 | 478.4886 | 247.6039 | 518.0353 | 478.0073 | 439.0659 | 458.5848 | 401.5222
2016.0354 | 476.8497 | 247.7973 | 518.0945 | 477.6449 | 439.9328 | 457.8909 | 401.1601
2017.0354 | 475.4456 | 247.9384 | 518.766 | 477.5486 | 440.3766 | 458.9733 | 401.4645
2018.0354 | 475.2073 | 247.9964 | 518.1522 | 477.8061 | 442.3152 | 462.333 | 401.5995
2019.0354 | 474.0024 | 248.1413 | 517.8479 | 478.3292 | 442.9461 | 463.2729 | 402.3578
2020.0354 | 472.1286 | 248.2664 | 519.0771 | 478.0371 | 444.0973 | 462.4083 | 402.6824
2021.0354 | 473.4722 | 248.4362 | 520.0718 | 478.2031 | 442.7938 | 461.8555 | 402.8324
2022.0354 | 472.383 | 248.4839 | 518.6418 | 478.4034 | 441.8313 | 461.9317 | 403.2898
2023.0354 | 473.4281 | 248.503 | 518.8849 | 478.4942 | 442.0022 | 461.6728 | 404.226
2024.0354 | 474.0529 | 248.6055 | 518.686 | 478.4324 | 441.8365 | 460.477 | 403.8864
2025.0354 | 473.307 | 248.688 | 518.5499 | 478.8874 | 441.4763 | 459.6702 | 403.4733
2026.0354 | 472.9974 | 248.8716 | 519.7301 | 479.293 | 441.7235 | 458.6876 | 403.2851
2027.0354 | 471.9885 | 248.9474 | 518.9159 | 478.8734 | 441.7341 | 457.6584 | 403.6803
2028.0354 | 475.5164 | 248.9789 | 519.2114 | 480.0777 | 441.7243 | 456.8143 | 404.8023
2029.0354 | 478.5425 | 249.1334 | 519.4637 | 480.346 | 442.4452 | 457.7158 | 405.1556
2030.0354 | 477.7227 | 249.2222 | 519.2587 | 480.0631 | 442.5977 | 457.3573 | 404.6255
2031.0354 | 478.6981 | 249.349 | 518.9805 | 479.8825 | 442.9629 | 457.0446 | 404.6017
2032.0354 | 481.5559 | 249.3853 | 518.407 | 479.8326 | 444.0884 | 463.3283 | 405.6437
2033.0354 | 483.834 | 249.489 | 518.8929 | 480.1639 | 444.6902 | 467.819 | 406.3181
2034.0354 | 483.5858 | 249.7204 | 520.3322 | 480.2319 | 445.2835 | 467.2444 | 406.3411
2035.0354 | 482.2727 | 249.7901 | 519.3223 | 480.2039 | 445.3941 | 465.9186 | 405.8594
2036.0354 | 480.427 | 249.7012 | 519.3617 | 480.5837 | 444.7025 | 465.4023 | 406.0635
2037.0354 | 478.804 | 249.9258 | 518.9799 | 481.1412 | 444.2234 | 463.6971 | 404.7868
2038.0354 | 479.3587 | 250.1492 | 518.4404 | 481.8837 | 444.1293 | 461.6254 | 403.4174
2039.0354 | 480.3812 | 250.2649 | 518.682 | 481.0292 | 444.1449 | 462.8968 | 403.517
2040.0354 | 481.6727 | 250.3144 | 518.5435 | 481.1067 | 445.9966 | 465.5413 | 404.2224
2041.0354 | 481.8364 | 250.3574 | 518.4218 | 481.142 | 447.6974 | 469.357 | 404.9251
2042.0354 | 479.8846 | 250.4195 | 518.4006 | 480.9015 | 447.4522 | 469.3891 | 403.8689
2043.0354 | 479.4949 | 250.5417 | 518.7524 | 480.9483 | 446.893 | 468.0341 | 403.3028
2044.0354 | 480.3126 | 250.6439 | 519.0311 | 481.6309 | 446.3414 | 466.7181 | 403.0384
2045.0354 | 480.1485 | 250.8088 | 519.1054 | 482.3747 | 445.8121 | 465.5738 | 402.7573
2046.0354 | 481.2665 | 251.091 | 519.3037 | 481.7925 | 446.0996 | 464.7298 | 403.0165
2047.0354 | 483.8705 | 251.2208 | 520.0301 | 481.342 | 445.9249 | 465.0168 | 403.5042
2048.0354 | 484.7038 | 251.3557 | 520.577 | 482.4928 | 445.7422 | 465.0931 | 404.5963
2049.0354 | 484.1387 | 251.2999 | 520.2421 | 482.1948 | 445.422 | 464.3045 | 404.3194
2050.0354 | 486.0696 | 251.4467 | 520.1119 | 481.9353 | 445.6978 | 463.6119 | 404.7761
2051.0354 | 484.9153 | 251.3913 | 518.977 | 482.4896 | 445.158 | 463.4072 | 404.5304
2052.0354 | 483.2111 | 251.5827 | 518.884 | 482.3347 | 446.2525 | 463.9591 | 404.724
2053.0354 | 483.5879 | 251.5946 | 520.2165 | 482.1698 | 446.1335 | 462.9647 | 404.682
2054.0354 | 483.9048 | 251.8177 | 519.9214 | 482.6254 | 446.7055 | 464.5267 | 405.2933
2055.0354 | 483.9376 | 251.8953 | 519.9256 | 483.2003 | 446.7455 | 465.3097 | 405.3863
2056.0354 | 483.638 | 252.0746 | 519.3804 | 483.226 | 445.8812 | 465.221 | 405.8749
2057.0354 | 486.4744 | 252.0751 | 519.6512 | 483.0331 | 445.9954 | 465.6786 | 406.57
2058.0354 | 490.7383 | 252.052 | 519.0776 | 482.8104 | 446.6745 | 470.9155 | 408.6083
2059.0354 | 495.4019 | 252.2697 | 518.9634 | 483.0924 | 448.9171 | 476.7478 | 410.3888
2060.0354 | 499.9775 | 252.5734 | 519.9682 | 483.5586 | 451.7079 | 481.2613 | 412.6098
2061.0354 | 498.5322 | 252.5628 | 518.9258 | 483.4582 | 453.2878 | 481.4132 | 412.6931
2062.0354 | 498.737 | 252.7701 | 518.9762 | 483.4795 | 453.2914 | 480.1137 | 412.3995
2063.0354 | 500.2129 | 252.9134 | 519.9999 | 484.12 | 454.7267 | 480.4132 | 411.654
2064.0354 | 501.3727 | 252.8649 | 520.3701 | 484.8031 | 454.0116 | 479.4126 | 411.1261
2065.0354 | 501.7815 | 252.9016 | 519.7196 | 483.6026 | 453.6697 | 477.8749 | 409.3294
2066.0354 | 502.1836 | 252.9076 | 519.7703 | 483.6568 | 453.5652 | 477.5413 | 409.5851
2067.0354 | 500.7231 | 253.0769 | 519.1585 | 483.5497 | 452.9482 | 478.1527 | 409.5207
2068.0354 | 497.872 | 253.2002 | 519.3591 | 483.7132 | 451.9254 | 476.6733 | 409.5114
2069.0354 | 497.6566 | 253.4335 | 519.4356 | 483.4191 | 451.895 | 476.1399 | 409.5801
2070.051 | 498.6442 | 253.5405 | 519.7493 | 483.4623 | 454.165 | 480.3202 | 410.0652
2071.0354 | 502.8626 | 253.642 | 519.4816 | 483.7771 | 457.6633 | 485.7536 | 411.8577
2072.0354 | 502.459 | 253.7978 | 520.2047 | 483.7067 | 459.088 | 492.4214 | 414.0191
2073.0354 | 500.1368 | 253.9033 | 519.7257 | 483.4854 | 459.9607 | 498.6543 | 415.861
2074.0354 | 499.9431 | 253.9636 | 519.0052 | 483.7862 | 458.6587 | 499.5594 | 414.9934
2075.0354 | 498.0716 | 253.9763 | 518.5663 | 483.7623 | 459.4659 | 502.0672 | 414.1146
2076.0354 | 495.6178 | 254.0172 | 519.9463 | 483.7925 | 462.5004 | 504.6012 | 414.7123
2077.0354 | 493.2495 | 254.0847 | 520.4562 | 483.5577 | 463.3666 | 504.6184 | 416.1571
2078.0354 | 494.4433 | 254.1783 | 519.2541 | 483.7131 | 462.9915 | 503.3271 | 416.408
2079.0354 | 494.6961 | 254.6056 | 519.2285 | 483.667 | 464.521 | 505.4105 | 417.0558
2080.0354 | 492.2007 | 254.7058 | 519.6994 | 483.3483 | 464.5475 | 504.0476 | 416.4161
2081.0354 | 492.9075 | 254.9161 | 519.4697 | 483.7049 | 463.1199 | 502.4343 | 416.7137
2082.0354 | 494.3767 | 255.0142 | 520.3422 | 483.2073 | 463.8796 | 512.9676 | 418.7786
2083.0354 | 495.1115 | 255.0074 | 521.5989 | 483.6277 | 465.0419 | 517.0151 | 421.2795
2084.0354 | 496.4608 | 255.1871 | 521.1919 | 483.7356 | 465.4669 | 517.2303 | 421.916
2085.0354 | 496.0495 | 255.2826 | 520.5593 | 483.7159 | 464.3348 | 517.3953 | 422.0951
2086.0354 | 498.4281 | 255.6317 | 520.9246 | 483.0819 | 463.5168 | 519.9138 | 422.5244
2087.0354 | 499.9116 | 255.7148 | 521.2785 | 483.6347 | 463.2259 | 521.6964 | 423.587
2088.0354 | 499.9274 | 255.6885 | 520.9807 | 483.495 | 461.5721 | 521.7981 | 423.8782
2089.0354 | 499.4585 | 255.6537 | 520.398 | 483.2985 | 460.7903 | 519.5358 | 423.9317
2090.0354 | 504.9382 | 255.7734 | 520.5122 | 483.2722 | 461.1785 | 525.9129 | 425.4913
2091.0354 | 508.1757 | 256.1379 | 521.2556 | 483.3854 | 462.9147 | 532.2573 | 428.1647
2092.0354 | 510.2888 | 256.3069 | 521.1404 | 483.8321 | 463.6307 | 531.8993 | 427.9133
2093.0354 | 512.7059 | 256.3133 | 521.5815 | 483.4571 | 464.5875 | 534.1522 | 428.5784
2094.0354 | 514.5029 | 256.4229 | 521.4282 | 483.9598 | 465.5109 | 534.4957 | 429.3433
2095.0354 | 515.1866 | 256.6654 | 521.7008 | 484.1777 | 468.7001 | 536.9435 | 428.9151
2096.0354 | 517.0177 | 256.8388 | 522.5593 | 483.6632 | 468.2906 | 552.8695 | 427.7715
2097.0354 | 524.1644 | 256.9393 | 523.2103 | 483.5332 | 469.2235 | 564.7416 | 427.9764
2098.0354 | 528.6653 | 257.1272 | 524.7779 | 483.8561 | 469.4726 | 566.4947 | 431.9749
2099.0354 | 531.038 | 257.5182 | 525.6873 | 483.7218 | 469.9137 | 561.5097 | 433.895
2100.0354 | 532.5537 | 257.6059 | 525.6341 | 483.7416 | 469.1797 | 556.0243 | 435.3924
2101.0354 | 534.2992 | 257.8258 | 526.1025 | 483.9586 | 468.8085 | 552.7873 | 437.1792
2102.0354 | 536.203 | 257.959 | 526.1439 | 484.5854 | 469.356 | 546.4471 | 437.5154
2103.0354 | 535.3784 | 258.0693 | 526.3699 | 484.3461 | 468.7911 | 543.1158 | 437.9394
2104.0354 | 534.7741 | 258.1153 | 526.3251 | 484.4948 | 468.2789 | 538.7295 | 438.1764
2105.0354 | 534.0478 | 258.1875 | 525.7235 | 484.086 | 469.2433 | 536.0068 | 437.5247
2106.0354 | 533.1448 | 258.3824 | 526.0545 | 483.6915 | 468.4652 | 530.3762 | 435.8403
2107.0354 | 531.7458 | 258.459 | 526.3009 | 484.05 | 470.8763 | 530.9893 | 436.7469
2108.0354 | 530.476 | 258.5948 | 526.1599 | 483.983 | 471.5688 | 530.2406 | 437.905
2109.0354 | 530.3358 | 258.4705 | 526.3153 | 484.235 | 471.1441 | 528.9058 | 437.7488
2110.0354 | 528.5913 | 258.6553 | 526.8859 | 484.0768 | 470.8373 | 531.022 | 438.1068
2111.0354 | 527.8328 | 259.0433 | 526.8541 | 484.0651 | 471.1555 | 526.7578 | 437.9285
2112.0354 | 526.3489 | 259.1599 | 526.0327 | 483.7577 | 470.5519 | 524.5142 | 437.7362
2113.0354 | 523.1687 | 259.3367 | 526.0855 | 483.7239 | 469.5792 | 525.0354 | 436.7221
2114.0354 | 522.5726 | 259.3555 | 526.7537 | 484.0811 | 469.6186 | 523.1705 | 436.7847
2115.0354 | 521.0348 | 259.4509 | 527.6317 | 484.2045 | 469.8561 | 518.098 | 435.3383
2116.0354 | 523.1297 | 259.6199 | 528.1813 | 483.7952 | 468.9592 | 514.87 | 434.9969
2117.0354 | 525.5232 | 259.8153 | 528.4837 | 483.6998 | 467.4084 | 512.0063 | 435.0774
2118.0354 | 533.222 | 260.2877 | 529.0098 | 484.073 | 467.7556 | 516.0948 | 438.0371
2119.0354 | 533.7119 | 260.1581 | 528.7942 | 484.0084 | 467.6807 | 514.396 | 439.4631
2120.0354 | 532.884 | 260.3583 | 528.6571 | 483.5504 | 467.8845 | 512.3163 | 440.2325
2121.0354 | 531.778 | 260.2488 | 528.6567 | 483.67 | 468.6898 | 513.3097 | 440.5633
2122.0354 | 531.7107 | 260.2717 | 528.4281 | 483.6672 | 469.4775 | 515.5826 | 441.0569
2123.0354 | 532.4752 | 260.3448 | 529.2853 | 483.2989 | 470.105 | 518.5913 | 440.8098
2124.0354 | 533.268 | 260.2497 | 528.7702 | 483.7692 | 469.9627 | 521.3983 | 441.3047
2125.0354 | 534.9096 | 260.5335 | 528.6631 | 483.3068 | 469.6661 | 519.5555 | 439.6883
2126.0354 | 533.8278 | 260.6472 | 528.7947 | 483.2824 | 470.4516 | 519.7413 | 439.8166
2127.0354 | 533.3018 | 260.7568 | 528.284 | 482.6859 | 469.214 | 517.0259 | 438.784
2128.0354 | 534.8954 | 260.7601 | 528.2027 | 483.0466 | 469.2569 | 520.7761 | 438.0544
2129.0354 | 538.7098 | 260.8333 | 527.9919 | 482.8822 | 472.0048 | 527.9508 | 438.9106
2130.0354 | 544.6008 | 260.9835 | 528.2238 | 482.8767 | 472.5593 | 530.3065 | 439.0197
2131.0354 | 549.6532 | 261.1214 | 528.6108 | 482.8506 | 473.4548 | 534.2038 | 439.5032
2132.0354 | 556.2825 | 261.4133 | 528.6965 | 483.1545 | 474.7317 | 536.2131 | 441.3992
2133.0354 | 560.9888 | 261.5038 | 528.4793 | 483.4132 | 475.102 | 535.934 | 444.3196
2134.0354 | 565.4343 | 261.5929 | 528.6425 | 483.1661 | 476.0781 | 536.0226 | 445.0286
2135.0354 | 567.7319 | 261.6891 | 528.2584 | 482.9013 | 476.6232 | 537.5483 | 446.5709
2136.0354 | 571.6383 | 261.7244 | 528.1018 | 482.8601 | 476.7833 | 537.5182 | 446.8728
2137.0354 | 575.042 | 261.9069 | 528.6469 | 482.8657 | 476.8695 | 539.347 | 447.6559
2138.0354 | 577.6367 | 262.011 | 528.5176 | 482.7401 | 477.2142 | 541.8212 | 449.4304
2139.0354 | 582.3138 | 262.1894 | 528.4071 | 483.3965 | 479.351 | 542.9718 | 449.8915
2140.0354 | 583.9481 | 262.2787 | 528.2984 | 482.6169 | 481.5173 | 543.0181 | 450.2323
2141.0354 | 583.9949 | 262.325 | 528.195 | 482.8038 | 483.5598 | 544.5761 | 450.8308
2142.0354 | 583.7658 | 262.489 | 528.3264 | 482.5385 | 485.1563 | 549.003 | 452.8151
2143.0354 | 582.893 | 262.6414 | 528.1377 | 482.146 | 486.361 | 547.6497 | 453.539
2144.0354 | 582.7206 | 262.716 | 527.5854 | 482.6643 | 487.183 | 549.9243 | 452.2914
2145.0354 | 583.6854 | 262.8476 | 527.7392 | 482.3105 | 488.9156 | 549.399 | 453.5358
2146.0354 | 584.3039 | 262.972 | 527.7734 | 482.4272 | 489.0153 | 550.875 | 452.8741
2147.0354 | 585.4714 | 263.1388 | 528.0388 | 482.4955 | 490.4334 | 550.988 | 454.0291
2148.0354 | 585.6788 | 263.2084 | 528.0813 | 482.7049 | 491.7969 | 548.5257 | 453.0601
2149.0354 | 587.5035 | 263.3031 | 527.2374 | 482.1355 | 493.8254 | 547.1705 | 452.4811
2150.0354 | 591.5095 | 263.4062 | 527.0454 | 482.0086 | 497.4519 | 545.7178 | 451.4561
2151.0354 | 595.2886 | 263.571 | 527.6788 | 482.1739 | 498.9101 | 546.079 | 450.4122
2152.0354 | 593.8622 | 263.6922 | 527.9771 | 482.6073 | 499.7211 | 542.3657 | 450.8763
2153.0354 | 591.782 | 263.7714 | 527.6468 | 482.9902 | 500.0202 | 539.2136 | 450.5466
2154.0354 | 590.3999 | 263.8407 | 527.4543 | 483.1866 | 498.9834 | 540.2526 | 449.1372
2155.0354 | 588.1605 | 264.0244 | 528.0861 | 483.0614 | 499.2852 | 538.9259 | 447.26
2156.0354 | 584.4057 | 264.1883 | 527.4082 | 483.2379 | 500.0156 | 536.0534 | 448.5485
2157.0354 | 583.551 | 264.2881 | 527.824 | 484.0234 | 498.9499 | 536.6286 | 447.7981
2158.0354 | 583.2679 | 264.4689 | 527.4521 | 483.2886 | 499.7725 | 540.577 | 448.2159
2159.0354 | 583.7266 | 264.692 | 527.7114 | 483.8088 | 502.6943 | 568.5244 | 449.3886
2160.0354 | 584.658 | 265.0126 | 528.8252 | 483.8451 | 503.1425 | 575.7268 | 449.9371
2161.0354 | 586.7661 | 265.05 | 528.9414 | 483.3659 | 503.7145 | 585.8448 | 450.3178
2162.0354 | 586.7156 | 265.1813 | 528.1446 | 483.3984 | 503.5197 | 581.2748 | 449.9452
2163.0354 | 586.2131 | 265.6383 | 528.465 | 483.6752 | 503.332 | 575.7026 | 450.4532
2164.0354 | 586.3737 | 265.8085 | 530.0861 | 483.6906 | 502.7525 | 571.5696 | 452.1398
2165.0354 | 583.9519 | 265.6564 | 528.8438 | 483.5733 | 501.519 | 564.6969 | 453.0538
2166.0354 | 580.4595 | 265.6337 | 528.7301 | 483.7441 | 500.5303 | 559.323 | 453.0368
2167.0354 | 578.2328 | 265.9008 | 529.0625 | 483.8817 | 499.5328 | 553.5615 | 452.9587
2168.0354 | 574.5219 | 266.0646 | 529.1917 | 483.4907 | 497.9332 | 548.8926 | 451.894
2169.0354 | 571.2933 | 266.0745 | 529.616 | 483.6053 | 496.8449 | 543.73 | 452.365
2170.0354 | 569.1256 | 266.1438 | 529.5004 | 484.0783 | 495.4484 | 538.8896 | 452.2858
2171.0354 | 567.6187 | 266.2477 | 529.327 | 483.7857 | 494.245 | 532.9359 | 452.1344
2172.0354 | 564.4483 | 266.5235 | 530.6101 | 483.4451 | 493.0404 | 528.1997 | 451.2655
2173.0354 | 562.149 | 266.545 | 531.6664 | 483.6308 | 492.0137 | 525.5372 | 449.9979
2174.0354 | 564.2399 | 266.6693 | 531.9359 | 483.7885 | 491.7539 | 523.29 | 450.1894
2175.0354 | 564.7743 | 266.7842 | 532.6161 | 483.869 | 491.4764 | 523.2267 | 450.6238
2176.0354 | 564.148 | 266.9397 | 531.9212 | 483.803 | 491.2367 | 522.2189 | 451.5299
2177.0354 | 564.8445 | 267.2182 | 530.8601 | 483.4578 | 491.155 | 521.6066 | 450.0151
2178.0354 | 568.7317 | 267.2918 | 531.2583 | 483.3652 | 491.3842 | 528.0165 | 451.7269
2179.0354 | 570.7464 | 267.5087 | 531.2784 | 483.3831 | 492.5504 | 528.7161 | 454.5725
2180.0354 | 572.9893 | 267.5228 | 530.8237 | 483.8193 | 492.4085 | 525.8526 | 454.911
2181.0354 | 577.4531 | 267.5213 | 532.0996 | 483.4603 | 493.4002 | 527.3125 | 455.0128
2182.0354 | 576.8945 | 267.5642 | 531.3293 | 483.9436 | 493.3851 | 525.5525 | 453.5954
2183.0354 | 576.4068 | 267.7263 | 532.1806 | 483.9792 | 492.9857 | 522.4954 | 453.0315
2184.0354 | 576.1555 | 267.791 | 531.5139 | 483.7884 | 492.7031 | 520.3116 | 452.0473
2185.0354 | 575.1983 | 267.9186 | 531.4817 | 484.065 | 492.1191 | 518.7279 | 452.05
2186.0354 | 574.4679 | 268.3102 | 533.862 | 484.0443 | 492.0561 | 520.3757 | 452.507
2187.0354 | 573.0222 | 268.5748 | 534.0456 | 484.091 | 491.845 | 519.818 | 453.755
2188.0354 | 571.5027 | 268.4458 | 532.7701 | 483.6037 | 490.6065 | 517.5083 | 451.3575
2189.0354 | 570.5434 | 268.4955 | 532.4213 | 483.9051 | 490.5921 | 518.3992 | 450.0808
2190.0354 | 571.4848 | 268.6156 | 531.8493 | 485.3893 | 490.433 | 521.2637 | 450.7144
2191.0354 | 578.0239 | 268.701 | 531.9313 | 485.1952 | 491.6433 | 522.9525 | 451.2843
2192.0354 | 581.5877 | 268.8762 | 532.2041 | 484.4155 | 491.9936 | 524.0346 | 453.0062
2193.0354 | 584.5464 | 269.0114 | 532.1746 | 484.0524 | 491.986 | 525.9569 | 455.1751
2194.0354 | 585.6009 | 269.1705 | 531.7455 | 484.4365 | 491.5282 | 526.6058 | 455.7006
2195.0354 | 585.3618 | 269.3501 | 532.579 | 483.9711 | 491.3998 | 528.6375 | 457.4961
2196.0354 | 585.8707 | 269.3597 | 531.8226 | 483.9378 | 490.9145 | 525.136 | 457.5903
2197.0354 | 590.1367 | 269.4823 | 531.537 | 483.7331 | 492.2363 | 530.902 | 458.1657
2198.0354 | 592.3868 | 269.6581 | 531.8703 | 483.9102 | 493.3074 | 533.227 | 458.9592
2199.0354 | 596.1312 | 269.7349 | 532.0076 | 483.8429 | 494.307 | 535.0619 | 459.114
2200.0354 | 599.4017 | 269.9691 | 532.1365 | 483.6228 | 495.8106 | 538.0034 | 460.957
2201.0354 | 599.0544 | 270.06 | 531.9879 | 483.6026 | 496.0001 | 541.414 | 462.5678
2202.0354 | 595.596 | 270.0035 | 531.5588 | 483.5799 | 496.0379 | 540.1399 | 462.2336
2203.0354 | 599.6582 | 270.0794 | 531.9985 | 483.8168 | 497.1223 | 541.639 | 461.975
2204.0354 | 600.8374 | 270.3163 | 531.776 | 483.7261 | 498.1562 | 543.9156 | 463.5304
2205.0354 | 605.5407 | 270.4063 | 532.1165 | 483.6151 | 499.5178 | 547.2437 | 464.5941
2206.0354 | 605.6581 | 270.8979 | 532.4478 | 483.529 | 500.322 | 551.6521 | 464.5217
2207.0354 | 604.2796 | 270.9415 | 531.8762 | 483.7193 | 500.6502 | 552.2507 | 465.1832
2208.0354 | 604.8987 | 271.0047 | 531.6953 | 483.6869 | 502.2434 | 553.3547 | 467.3929
2209.0354 | 610.1648 | 271.0326 | 531.3459 | 483.7458 | 504.1373 | 554.8503 | 466.8984
2210.0354 | 613.0192 | 271.1013 | 531.2286 | 483.5549 | 506.2456 | 552.3032 | 466.9246
2211.0354 | 617.4049 | 271.2601 | 530.9954 | 483.3763 | 508.3435 | 552.2617 | 466.4535
2212.0354 | 620.809 | 271.4533 | 530.8294 | 483.0922 | 510.4632 | 553.2436 | 466.8964
2213.0354 | 622.3942 | 271.4903 | 530.7376 | 483.2036 | 512.0801 | 554.3819 | 466.4152
2214.0354 | 626.6107 | 271.6637 | 530.6596 | 483.0708 | 513.984 | 554.2869 | 465.3676
2215.0354 | 631.7534 | 271.888 | 530.4696 | 483.1992 | 516.74 | 555.1401 | 465.7542
2216.0354 | 631.7713 | 272.1173 | 530.5526 | 482.9442 | 517.2572 | 556.1461 | 464.9413
2217.0354 | 629.8576 | 272.1628 | 530.545 | 483.1193 | 518.1129 | 554.0358 | 465.5926
2218.0354 | 630.3101 | 272.3067 | 529.8776 | 483.1802 | 519.861 | 552.9873 | 464.3107
2219.0354 | 631.5241 | 272.4446 | 530.4461 | 483.272 | 522.5018 | 553.1502 | 462.8818
2220.0354 | 629.4238 | 272.4749 | 529.9623 | 483.6621 | 523.7231 | 553.3018 | 463.18
2221.0354 | 627.4223 | 272.5347 | 529.8462 | 483.0901 | 525.0724 | 554.4583 | 463.5081
2222.0354 | 629.9264 | 272.7716 | 529.6806 | 482.6953 | 526.9306 | 552.4002 | 463.9418
2223.0354 | 631.2819 | 272.9012 | 529.3251 | 483.186 | 528.3123 | 552.5078 | 465.2967
2224.0354 | 634.2311 | 273.03 | 529.464 | 483.0714 | 529.3209 | 550.5115 | 465.0357
2225.0354 | 639.4639 | 273.0657 | 529.5671 | 483.3831 | 531.7331 | 550.1663 | 465.4916
2226.0354 | 638.1881 | 273.3238 | 529.632 | 483.0214 | 533.5064 | 551.1257 | 466.0464
2227.0354 | 634.662 | 273.3202 | 529.6157 | 483.088 | 533.5034 | 550.5334 | 467.0825
2228.0354 | 631.2999 | 273.4158 | 529.6132 | 483.1068 | 534.921 | 553.4107 | 468.8257
2229.0354 | 626.7446 | 273.7888 | 529.4597 | 482.7798 | 536.0284 | 554.0045 | 468.8339
2230.0354 | 623.1904 | 273.8908 | 528.9521 | 483.049 | 536.852 | 549.4769 | 466.9115
2231.0354 | 625.188 | 273.9371 | 528.6991 | 482.8588 | 538.7685 | 550.4786 | 465.1989
2232.0354 | 625.2476 | 274.0053 | 528.5209 | 482.7416 | 542.5571 | 554.1802 | 467.4782
2233.0354 | 624.1019 | 274.522 | 528.6494 | 482.7645 | 544.4488 | 555.455 | 467.8509
2234.0354 | 625.8761 | 274.5688 | 528.9102 | 482.7826 | 547.143 | 556.0507 | 469.3749
2235.0354 | 621.0525 | 274.5962 | 528.7419 | 482.2848 | 547.7237 | 553.3005 | 470.4601
2236.0354 | 616.8638 | 274.6784 | 530.4658 | 482.4857 | 547.2487 | 553.3979 | 469.5321
2237.0354 | 612.7246 | 274.832 | 529.1012 | 482.5779 | 548.4969 | 552.2652 | 470.6107
2238.0354 | 609.1119 | 275.1509 | 528.8308 | 482.6137 | 549.5433 | 563.433 | 474.018
2239.0354 | 606.0094 | 275.3161 | 528.7494 | 482.6127 | 551.6028 | 565.6665 | 477.3585
2240.0354 | 602.3055 | 275.3941 | 528.363 | 482.3625 | 551.9345 | 563.0124 | 476.9336
2241.0354 | 599.8725 | 275.5113 | 528.4202 | 483.8704 | 552.9308 | 557.6601 | 475.7135
2242.0354 | 599.5654 | 275.6009 | 528.9504 | 483.5765 | 556.4845 | 554.3332 | 477.3777
2243.0354 | 597.8043 | 275.6251 | 529.4259 | 482.9647 | 558.1661 | 554.27 | 478.3328
2244.0354 | 595.1017 | 275.9691 | 529.9749 | 482.5847 | 558.1517 | 550.5795 | 481.6538
2245.0354 | 591.6509 | 276.3164 | 528.7231 | 482.2728 | 558.548 | 549.2898 | 488.3192
2246.0354 | 591.2204 | 276.3941 | 528.6424 | 482.6005 | 558.9872 | 555.3234 | 497.6632
2247.0354 | 589.2658 | 276.421 | 528.7448 | 483.4642 | 561.1384 | 554.3756 | 504.5947
2248.0354 | 587.0107 | 276.4559 | 528.4218 | 483.8873 | 564.4587 | 548.7757 | 506.824
2249.0354 | 586.9886 | 276.5311 | 528.1734 | 483.4443 | 565.3954 | 551.5312 | 507.538
2250.0354 | 589.8832 | 276.7296 | 528.4212 | 483.0318 | 567.8147 | 549.8517 | 506.7364
2251.0354 | 593.6411 | 276.9766 | 528.2294 | 483.1439 | 568.3608 | 551.2969 | 503.233
2252.0354 | 594.5787 | 277.1157 | 528.9236 | 483.6962 | 567.8852 | 552.0469 | 500.474
2253.0354 | 597.7028 | 277.3566 | 529.8351 | 483.744 | 568.5405 | 553.2801 | 498.424
2254.0354 | 598.6341 | 277.5551 | 530.2159 | 483.5228 | 568.8453 | 558.4205 | 496.723
2255.0354 | 602.3415 | 277.9826 | 530.6825 | 483.0966 | 569.027 | 558.6056 | 494.3517
2256.0354 | 606.5821 | 278.1605 | 531.6133 | 483.3026 | 568.3193 | 560.2077 | 496.8113
2257.0354 | 608.9403 | 278.4028 | 533.6982 | 483.3203 | 565.771 | 560.0042 | 496.0771
2258.0354 | 609.8056 | 278.6553 | 533.9759 | 483.5397 | 563.7194 | 560.6362 | 496.3546
2259.0354 | 609.481 | 278.9272 | 533.5315 | 483.5052 | 563.25 | 559.7801 | 496.0465
2260.0354 | 608.0129 | 279.0839 | 532.8937 | 483.2748 | 561.8209 | 556.4052 | 495.9532
2261.0354 | 604.9993 | 278.9435 | 531.8104 | 483.1096 | 562.0186 | 552.7365 | 494.1691
2262.0354 | 603.6296 | 278.9295 | 531.5167 | 483.0343 | 562.0898 | 550.93 | 491.6621
2263.0354 | 602.625 | 278.866 | 531.7989 | 483.7669 | 562.3925 | 551.7693 | 491.3348
2264.0354 | 602.0797 | 278.9754 | 531.3156 | 483.7156 | 561.8942 | 549.5848 | 489.138
2265.0354 | 608.6503 | 279.22 | 531.8207 | 483.3514 | 564.7733 | 545.7203 | 488.9913
2266.0354 | 610.3167 | 279.2137 | 532.181 | 483.6528 | 566.2358 | 543.3092 | 488.4803
2267.0354 | 610.8504 | 279.4217 | 532.0435 | 483.5394 | 565.9984 | 546.0409 | 489.2765
2268.0354 | 608.3463 | 279.5992 | 532.0626 | 483.0067 | 564.2906 | 549.3974 | 491.2246
2269.0354 | 605.1538 | 279.6171 | 531.562 | 483.3636 | 562.6775 | 548.9502 | 490.3362
2270.0354 | 602.5303 | 279.708 | 531.6953 | 483.1081 | 562.0482 | 549.6981 | 489.7334
2271.0354 | 607.6157 | 279.8656 | 531.8055 | 483.1311 | 562.4691 | 555.0948 | 489.7997
2272.0354 | 608.6743 | 280.168 | 532.8182 | 483.5381 | 562.5893 | 555.3252 | 491.2155
2273.0354 | 607.1529 | 280.51 | 534.0777 | 483.1994 | 561.8934 | 554.9048 | 489.8863
2274.0354 | 609.8296 | 280.6357 | 535.0011 | 483.2188 | 561.6785 | 555.2589 | 491.1331
2275.0354 | 614.6053 | 280.8621 | 533.9335 | 483.6615 | 561.864 | 554.2257 | 492.8515
2276.0354 | 615.7712 | 280.7666 | 532.7432 | 483.3625 | 561.2253 | 553.2006 | 492.6797
2277.0354 | 618.0489 | 280.8843 | 533.013 | 483.2871 | 559.8771 | 556.3231 | 491.4763
2278.0354 | 621.9516 | 280.9426 | 532.7562 | 483.5564 | 560.6552 | 567.5007 | 494.3699
2279.0354 | 624.3524 | 281.0975 | 532.4949 | 483.9658 | 561.9907 | 571.7945 | 498.3479
2280.0354 | 627.318 | 281.3441 | 533.2461 | 483.6001 | 562.3155 | 571.2767 | 499.6957
2281.0354 | 630.7986 | 281.3958 | 533.2052 | 483.1484 | 562.0501 | 570.0977 | 503.6913
2282.0354 | 631.2228 | 281.6407 | 533.6459 | 483.194 | 562.633 | 572.0501 | 508.5619
2283.0354 | 632.1759 | 281.8888 | 534.0322 | 483.2128 | 560.8248 | 575.8719 | 508.4135
2284.0354 | 629.7609 | 281.9487 | 533.2676 | 483.2287 | 557.4011 | 576.7898 | 508.1723
2285.0354 | 628.3138 | 282.067 | 533.2981 | 483.301 | 558.7799 | 576.84 | 507.5944
2286.0354 | 626.1914 | 282.2461 | 532.8854 | 483.9608 | 558.6783 | 571.8358 | 505.1598
2287.0354 | 627.7511 | 282.2422 | 533.0455 | 483.6406 | 558.1006 | 570.3109 | 502.6159
2288.0354 | 631.5361 | 282.4055 | 532.891 | 484.3989 | 556.8671 | 571.0838 | 502.2496
2289.0354 | 633.3874 | 283.4097 | 532.8278 | 484.7375 | 556.7641 | 567.1931 | 499.7509
2290.0354 | 636.7596 | 286.0966 | 533.8094 | 484.9787 | 557.9339 | 567.2179 | 499.3724
2291.0354 | 635.9779 | 283.0002 | 533.1585 | 484.4156 | 555.4918 | 563.94 | 498.9843
2292.0354 | 635.1936 | 283.157 | 535.2044 | 483.9059 | 554.7496 | 566.9772 | 499.3442
2293.0354 | 636.8226 | 283.4413 | 535.1606 | 484.2123 | 552.1823 | 572.0471 | 499.2623
2294.0354 | 634.9591 | 283.5343 | 534.2597 | 484.7015 | 550.1056 | 566.9414 | 500.2989
2295.0354 | 636.4192 | 283.5914 | 534.1237 | 484.3254 | 548.5908 | 567.6488 | 499.2015
2296.0354 | 637.7457 | 283.75 | 534.141 | 484.5743 | 548.2829 | 569.2567 | 499.6284
2297.0354 | 639.9413 | 284.215 | 534.1704 | 485.2074 | 548.9433 | 571.9037 | 501.6113
2298.0354 | 641.5965 | 284.1705 | 533.8705 | 485.3384 | 549.8215 | 571.876 | 503.206
2299.0354 | 642.5868 | 284.2612 | 533.6664 | 484.5835 | 549.6493 | 575.4839 | 505.1023
2300.0354 | 641.6631 | 284.6507 | 534.5078 | 484.4526 | 548.197 | 574.6284 | 505.7567
2301.0354 | 644.4008 | 285.0618 | 537.3425 | 484.678 | 546.1476 | 576.816 | 508.0183
2302.0354 | 644.8113 | 285.1407 | 536.1535 | 485.0686 | 546.0117 | 578.5367 | 508.9807
2303.0354 | 641.9697 | 285.2593 | 536.8132 | 484.9437 | 546.5329 | 575.5036 | 508.8128
2304.0354 | 640.1592 | 285.3581 | 536.8189 | 484.8567 | 548.9142 | 572.0465 | 507.9503
2305.0354 | 637.7638 | 285.8674 | 536.3299 | 484.9935 | 550.9256 | 569.9112 | 508.3161
2306.0354 | 634.7094 | 286.2662 | 536.433 | 484.6559 | 550.6112 | 568.7057 | 506.8976
2307.0354 | 631.7226 | 285.9479 | 535.7746 | 484.4858 | 549.3269 | 565.1914 | 506.3401
2308.0354 | 631.9775 | 285.9413 | 536.676 | 484.5238 | 549.4093 | 565.5013 | 503.2581
2309.0354 | 632.6828 | 286.0996 | 536.0071 | 485.2199 | 550.4976 | 567.4599 | 505.1272
2310.0354 | 634.8584 | 286.2382 | 535.6117 | 484.6416 | 551.3564 | 568.1541 | 508.32
2311.0354 | 634.6859 | 286.9973 | 535.8171 | 485.3434 | 552.3477 | 566.7578 | 507.7149
2312.0354 | 635.6488 | 286.4673 | 536.9453 | 484.8109 | 553.2535 | 567.171 | 510.0675
2313.0354 | 632.7831 | 286.5515 | 536.6574 | 485.0605 | 552.987 | 563.7331 | 509.4487
2314.0354 | 630.2735 | 287.2982 | 537.7446 | 484.9153 | 551.7335 | 559.2228 | 508.4835
2315.0354 | 631.5178 | 287.2596 | 537.1382 | 484.6922 | 551.3528 | 562.499 | 509.4145
2316.0354 | 639.0289 | 287.5626 | 537.5085 | 484.6054 | 551.0019 | 563.7924 | 511.1966
2317.0354 | 642.0227 | 287.5053 | 536.9256 | 484.5286 | 550.8216 | 566.4584 | 513.0812
2318.0354 | 642.1309 | 287.5652 | 537.082 | 485.0874 | 550.8891 | 566.6223 | 510.0545
2319.0354 | 642.03 | 287.8755 | 537.1832 | 484.7001 | 552.115 | 567.0647 | 513.6878
2320.0354 | 643.8267 | 288.0338 | 537.0559 | 484.2969 | 553.2227 | 568.5165 | 514.3361
2321.0354 | 644.0701 | 288.4158 | 537.0505 | 484.3689 | 551.6331 | 567.2212 | 513.1911
2322.0354 | 642.8162 | 288.6278 | 536.9548 | 484.3855 | 551.7727 | 566.0833 | 512.9184
2323.0354 | 644.6899 | 288.6952 | 537.1854 | 484.2697 | 550.1929 | 571.6697 | 515.3602
2324.0354 | 646.5714 | 288.7166 | 537.1496 | 484.2501 | 548.9652 | 576.2248 | 515.2746
2325.0354 | 648.641 | 288.6526 | 536.4934 | 484.3934 | 546.487 | 576.2433 | 516.8624
2326.0354 | 651.882 | 288.7462 | 536.3962 | 483.9725 | 545.8264 | 573.6565 | 515.1222
2327.0354 | 652.2933 | 288.9071 | 537.0921 | 484.0609 | 546.6717 | 574.6158 | 514.5068
2328.0354 | 650.0404 | 289.015 | 536.8195 | 484.0672 | 547.4509 | 571.9753 | 514.0071
2329.0354 | 647.4918 | 289.0935 | 536.7815 | 484.066 | 549.5612 | 576.5764 | 514.5677
2330.0354 | 644.4818 | 289.8118 | 537.4857 | 484.3722 | 550.4434 | 573.274 | 514.2645
2331.0354 | 642.1798 | 289.7086 | 536.8236 | 484.0881 | 553.3016 | 570.8176 | 514.57
2332.0354 | 643.4781 | 289.6862 | 536.3547 | 484.3636 | 554.4391 | 575.3933 | 511.4046
2333.0354 | 647.614 | 289.7838 | 536.7935 | 484.2853 | 554.463 | 577.0388 | 516.6638
2334.0354 | 648.8851 | 289.843 | 536.3322 | 484.002 | 555.5094 | 574.5621 | 515.2137
2335.0354 | 651.5259 | 290.0214 | 536.4544 | 484.5193 | 553.8921 | 567.1431 | 512.8545
2336.0354 | 655.507 | 290.2233 | 536.7966 | 484.6548 | 553.2133 | 570.7556 | 512.937
2337.0354 | 655.8532 | 290.5375 | 537.1318 | 486.4438 | 554.8219 | 568.5899 | 512.325
2338.0354 | 652.995 | 290.8012 | 537.4146 | 484.8563 | 557.0255 | 566.6972 | 508.558
2339.0354 | 651.7211 | 291.1098 | 538.3246 | 484.6866 | 556.402 | 565.6318 | 509.4973
2340.0354 | 648.563 | 291.0921 | 536.9514 | 484.3469 | 557.6654 | 567.5324 | 510.5705
2341.0354 | 649.7226 | 291.2007 | 536.6586 | 484.6017 | 561.0185 | 573.0231 | 511.6113
2342.0354 | 651.5415 | 291.4262 | 536.6641 | 484.3837 | 561.4969 | 571.8957 | 512.6184
2343.0354 | 652.0708 | 291.4375 | 536.6889 | 484.5242 | 560.4311 | 570.6262 | 514.7435
2344.0354 | 649.6916 | 291.6031 | 536.6332 | 485.0102 | 561.301 | 570.379 | 515.1475
2345.0354 | 648.2999 | 292.6908 | 536.7964 | 484.8422 | 562.319 | 568.2479 | 514.4849
2346.0354 | 647.4524 | 293.9609 | 537.1503 | 484.9703 | 562.6561 | 565.6676 | 512.7249
2347.0354 | 646.1725 | 296.2907 | 538.0414 | 485.2634 | 564.6542 | 564.8582 | 510.3228
2348.0354 | 647.5224 | 297.6139 | 537.8819 | 485.4339 | 565.6756 | 564.6572 | 509.8261
2349.0354 | 645.392 | 292.3003 | 535.9271 | 484.6092 | 563.5962 | 563.8481 | 514.2822
2350.0354 | 648.1084 | 293.0928 | 536.2531 | 485.1476 | 564.0674 | 562.7919 | 512.8718
2351.0354 | 649.4306 | 292.5616 | 535.8524 | 484.9081 | 564.917 | 563.1435 | 513.0286
2352.0354 | 650.3782 | 292.8391 | 537.6707 | 484.8142 | 564.5702 | 564.5373 | 513.7958
2353.0354 | 648.9691 | 293.0006 | 537.4498 | 484.5622 | 565.6475 | 566.8488 | 515.0284
2354.0354 | 649.0365 | 293.0176 | 537.2658 | 484.5881 | 564.9508 | 565.9369 | 517.9033
2355.0354 | 647.5071 | 293.1696 | 536.9244 | 484.6721 | 565.1989 | 565.7373 | 518.7822
2356.0354 | 645.1492 | 293.179 | 536.7686 | 484.756 | 566.8194 | 561.664 | 516.7091
2357.0354 | 648.0406 | 293.3137 | 537.4322 | 484.5053 | 568.6051 | 561.5385 | 517.8544
2358.0354 | 650.1862 | 293.5038 | 536.5181 | 484.7222 | 568.9543 | 560.142 | 518.241
2359.0354 | 653.6761 | 293.7291 | 536.4815 | 484.2906 | 567.9649 | 562.1555 | 518.8115
2360.0354 | 655.2441 | 293.9247 | 536.535 | 484.532 | 567.7584 | 564.832 | 519.0143
2361.0354 | 657.6379 | 293.975 | 536.4649 | 484.1802 | 565.7886 | 566.9277 | 518.7118
2362.0354 | 659.0324 | 294.0906 | 536.1851 | 484.5052 | 563.6089 | 567.895 | 519.6952
2363.0354 | 662.9127 | 294.346 | 535.7059 | 484.3117 | 562.0349 | 569.1911 | 516.625
2364.0354 | 663.3421 | 294.4937 | 535.8845 | 484.2074 | 560.56 | 569.0076 | 517.8072
2365.0354 | 658.5105 | 294.7123 | 536.9919 | 484.4279 | 558.8425 | 566.6727 | 516.18
2366.0354 | 653.1527 | 294.9548 | 538.5065 | 484.4404 | 559.3357 | 562.4952 | 514.1894
2367.0354 | 651.7935 | 295.0803 | 538.0274 | 484.1235 | 559.224 | 559.3947 | 512.1281
2368.0354 | 647.4538 | 295.3679 | 537.3699 | 484.0839 | 559.9001 | 559.4154 | 511.4929
2369.0354 | 643.4585 | 295.3036 | 536.6305 | 484.5495 | 560.0638 | 557.5402 | 509.0645
2370.0354 | 648.6372 | 295.27 | 536.5296 | 484.9912 | 562.0242 | 561.0516 | 512.3573
2371.0354 | 650.9918 | 295.4866 | 536.5143 | 484.2436 | 562.3978 | 560.2714 | 512.0088
2372.0354 | 653.1388 | 295.7627 | 536.4075 | 483.8196 | 560.6034 | 566.2851 | 513.8509
2373.0354 | 655.882 | 295.7386 | 536.5271 | 483.7764 | 560.6086 | 568.2704 | 513.7272
2374.0354 | 655.7026 | 295.82 | 536.9763 | 484.0815 | 557.336 | 569.448 | 511.9976
2375.0354 | 653.2815 | 295.9573 | 536.7505 | 484.4358 | 557.9844 | 567.7071 | 512.1782
2376.0823 | 651.7308 | 296.0405 | 537.3405 | 484.1478 | 557.8259 | 563.9486 | 509.4733
2377.0354 | 649.9451 | 296.1698 | 537.1286 | 484.0105 | 557.6752 | 562.3711 | 508.5685
2378.0354 | 651.899 | 296.4205 | 537.1054 | 483.8714 | 558.8416 | 564.5439 | 508.9654
2379.0354 | 651.4013 | 296.5213 | 537.3747 | 484.7199 | 559.524 | 563.7794 | 508.3496
2380.0354 | 649.6073 | 296.639 | 536.3506 | 484.4564 | 559.0506 | 561.4889 | 505.498
2381.0354 | 653.3344 | 296.7623 | 538.2395 | 484.7059 | 560.3449 | 560.3218 | 503.669
2382.0354 | 654.3856 | 297.0738 | 538.1957 | 484.5448 | 560.5502 | 558.3336 | 507.8299
2383.0354 | 658.5625 | 297.294 | 537.4618 | 484.5859 | 562.4449 | 556.2209 | 507.4648
2384.0354 | 661.8545 | 297.4691 | 538.1481 | 484.2257 | 563.99 | 558.2462 | 508.5068
2385.0354 | 660.662 | 297.8332 | 537.8605 | 484.5679 | 564.0767 | 558.7743 | 508.8082
2386.0354 | 658.1823 | 297.9536 | 537.753 | 484.814 | 563.8717 | 556.7865 | 509.8349
2387.0354 | 655.0807 | 297.962 | 537.3349 | 485.2088 | 562.0342 | 557.5323 | 509.3136
2388.0354 | 653.1371 | 298.3829 | 538.4382 | 484.643 | 560.8468 | 557.4105 | 512.402
2389.0354 | 653.5756 | 298.5991 | 537.7959 | 484.3196 | 560.0119 | 557.4472 | 513.4866
2390.0354 | 653.4239 | 298.591 | 537.4885 | 483.9172 | 557.9224 | 561.4382 | 516.8688
2391.0354 | 655.7806 | 298.6564 | 537.8537 | 484.1771 | 556.2429 | 562.8643 | 516.8774
2392.0354 | 656.7811 | 298.8717 | 537.8095 | 484.25 | 554.7586 | 564.1788 | 516.2826
2393.0354 | 653.5018 | 298.7776 | 537.7364 | 484.3521 | 553.8713 | 561.8637 | 514.8168
2394.0354 | 655.5973 | 298.8931 | 537.7727 | 484.0577 | 553.7013 | 562.9072 | 514.6967
2395.0354 | 655.8984 | 299.1389 | 538.2413 | 483.7628 | 553.9955 | 566.9623 | 516.8648
2396.0354 | 652.2895 | 299.4328 | 538.2195 | 484.445 | 554.5047 | 566.4086 | 516.6317
2397.0354 | 653.365 | 299.3268 | 539.1429 | 484.4237 | 555.0391 | 567.8667 | 515.8192
2398.0354 | 652.7761 | 299.5006 | 538.8448 | 484.4856 | 553.9817 | 566.0119 | 516.8676
2399.0354 | 649.8669 | 299.5629 | 537.7542 | 484.8865 | 555.2637 | 565.3212 | 516.7977
2400.0354 | 651.0568 | 299.6369 | 537.826 | 484.5512 | 557.5198 | 566.5278 | 515.8596
2401.0354 | 650.913 | 299.7349 | 538.0562 | 483.7893 | 558.7661 | 564.2326 | 516.8814
2402.0354 | 652.6827 | 300.0579 | 538.0836 | 484.5145 | 558.1507 | 564.6 | 518.9287
2403.0354 | 656.3029 | 300.2215 | 538.0472 | 483.9861 | 557.1247 | 564.6283 | 519.0801
2404.0354 | 657.7215 | 300.3698 | 537.9574 | 483.9932 | 556.2253 | 567.4104 | 520.3595
2405.0354 | 658.1234 | 300.422 | 538.8021 | 483.6537 | 556.3454 | 569.2526 | 519.0055
2406.0354 | 661.085 | 300.5202 | 537.8467 | 484.1317 | 555.6709 | 573.81 | 519.1572
2407.0354 | 664.966 | 300.9123 | 538.2829 | 483.7669 | 554.4182 | 577.016 | 520.8631
2408.0354 | 663.0046 | 301.2051 | 538.7352 | 483.6696 | 554.6435 | 578.14 | 522.4067
2409.0354 | 662.6503 | 301.1321 | 538.102 | 483.8373 | 552.5192 | 576.5855 | 519.698
2410.0354 | 663.0671 | 301.3475 | 538.23 | 483.9524 | 552.6546 | 573.6416 | 520.8843
2411.0354 | 665.4346 | 301.1661 | 538.0686 | 483.9919 | 553.6986 | 571.8173 | 519.5149
2412.0354 | 666.0301 | 301.3309 | 539.6291 | 484.0101 | 554.3492 | 570.8768 | 521.701
2413.0354 | 662.3983 | 301.4253 | 540.3186 | 484.6578 | 554.3516 | 568.8093 | 520.1941
2414.0354 | 658.233 | 301.6682 | 540.8118 | 483.9122 | 553.5724 | 566.2897 | 520.2596
2415.0354 | 656.0349 | 301.7585 | 540.2274 | 483.8276 | 553.4641 | 563.7597 | 518.272
2416.0354 | 654.6812 | 301.8891 | 540.3009 | 483.6053 | 552.7365 | 564.9373 | 519.5112
2417.0354 | 656.2116 | 302.2511 | 542.393 | 483.9915 | 551.9628 | 562.7057 | 519.457
2418.0354 | 656.6222 | 302.24 | 542.2981 | 483.8107 | 551.4411 | 558.4335 | 517.6785
2419.0354 | 658.3288 | 302.3374 | 541.8908 | 483.7137 | 549.8099 | 557.7246 | 521.1895
2420.0354 | 659.16 | 302.6329 | 541.6305 | 483.8759 | 549.0297 | 558.227 | 522.5391
2421.0354 | 660.2248 | 302.8042 | 542.3271 | 484.0708 | 549.8983 | 558.2853 | 523.2487
2422.0354 | 659.9475 | 303.0416 | 542.9189 | 483.8352 | 550.2143 | 559.3041 | 521.1203
2423.0354 | 659.1328 | 303.4546 | 543.7315 | 484.0069 | 549.5141 | 557.1819 | 520.0609
2424.0354 | 659.1145 | 303.6029 | 543.7456 | 483.5259 | 549.5532 | 557.9353 | 520.0855
2425.0354 | 659.5382 | 303.6711 | 544.2624 | 483.5816 | 547.8531 | 558.0442 | 522.9966
2426.0354 | 659.6273 | 303.9443 | 543.798 | 483.4991 | 547.1691 | 557.8583 | 523.9291
2427.0354 | 658.8128 | 304.5486 | 545.9698 | 483.5275 | 548.0913 | 557.0286 | 522.7184
2428.0354 | 658.2423 | 304.8502 | 547.8998 | 483.7598 | 548.5512 | 560.2306 | 524.3772
2429.0354 | 657.3069 | 304.6719 | 546.7284 | 483.4886 | 547.4075 | 561.6851 | 524.7361
2430.0354 | 657.2951 | 304.7117 | 547.8897 | 483.6361 | 548.0112 | 559.6795 | 524.6949
2431.0354 | 656.6432 | 305.204 | 547.8796 | 483.6338 | 549.5679 | 559.0899 | 525.0493
2432.0354 | 655.3989 | 305.7554 | 547.4702 | 483.7304 | 551.5728 | 559.0653 | 524.9056
2433.0354 | 651.0955 | 305.718 | 547.5819 | 483.2681 | 551.5422 | 558.6168 | 525.2494
2434.0354 | 647.1943 | 305.5979 | 547.634 | 483.7705 | 550.6699 | 557.1933 | 524.8758
2435.0354 | 644.4029 | 305.5364 | 547.6488 | 483.4501 | 550.0911 | 555.5226 | 523.5742
2436.0354 | 642.7206 | 305.795 | 549.1468 | 483.219 | 549.6843 | 555.5347 | 522.7487
2437.0354 | 642.1813 | 306.4331 | 549.8193 | 483.165 | 548.3912 | 556.6001 | 525.033
2438.0354 | 644.9962 | 306.9704 | 550.3768 | 483.4749 | 546.8084 | 557.216 | 526.2327
2439.0354 | 649.1354 | 306.6032 | 551.1681 | 483.0525 | 546.5266 | 554.8503 | 526.6113
2440.0354 | 648.0426 | 306.8708 | 550.9837 | 483.6863 | 545.2684 | 551.1089 | 523.7991
2441.0354 | 646.928 | 307.1409 | 551.7337 | 483.0915 | 544.7447 | 550.0195 | 522.6333
2442.0354 | 646.0899 | 307.4805 | 552.2466 | 483.5192 | 544.6065 | 548.177 | 521.4263
2443.0354 | 647.2699 | 307.9934 | 550.8872 | 483.1078 | 544.2191 | 548.8265 | 521.4189
2444.0354 | 646.5117 | 308.1695 | 550.5502 | 483.3885 | 544.9676 | 549.6581 | 522.8397
2445.0354 | 646.8552 | 308.0401 | 551.2401 | 483.2285 | 544.012 | 549.4323 | 520.3416
2446.0354 | 646.788 | 308.3742 | 552.5051 | 482.8572 | 543.8078 | 550.3389 | 521.6027
2447.0354 | 651.5158 | 309.5113 | 553.2433 | 482.7147 | 542.8549 | 548.6861 | 521.9427
2448.0354 | 652.8347 | 309.0278 | 552.8404 | 482.7183 | 541.4533 | 550.3826 | 523.2406
2449.0354 | 651.2516 | 308.5957 | 552.9222 | 482.5281 | 540.4004 | 550.3823 | 525.9095
2450.0354 | 653.1713 | 308.7176 | 552.1883 | 482.2866 | 540.0587 | 553.1422 | 527.3013
2451.0354 | 655.9453 | 308.9727 | 552.6592 | 482.2624 | 540.307 | 556.3299 | 528.5938
2452.0354 | 656.7341 | 309.2508 | 553.3648 | 482.2278 | 539.3625 | 558.9282 | 528.6435
2453.0354 | 657.2989 | 309.2329 | 552.6962 | 482.1287 | 539.3579 | 562.8616 | 529.4861
2454.0354 | 658.9882 | 309.0711 | 552.4916 | 482.0595 | 539.59 | 566.81 | 531.147
2455.0354 | 660.4132 | 309.1595 | 552.7071 | 481.9118 | 540.7289 | 569.7475 | 532.0993
2456.0354 | 662.6282 | 309.4199 | 552.9767 | 482.6238 | 540.6701 | 573.6161 | 530.9047
2457.0354 | 663.1236 | 309.5806 | 552.7576 | 482.3101 | 541.0235 | 571.346 | 530.7213
2458.0354 | 661.6997 | 309.7711 | 553.3756 | 482.0616 | 541.3527 | 570.9969 | 531.7417
2459.0354 | 660.7831 | 309.8611 | 553.0891 | 481.7544 | 542.1191 | 571.8599 | 532.7226
2460.0354 | 661.6421 | 310.0218 | 553.1202 | 481.5808 | 542.2099 | 574.4389 | 531.652
2461.0354 | 663.4967 | 310.2241 | 552.892 | 481.6592 | 542.9293 | 578.9087 | 533.3097
2462.0354 | 664.2014 | 310.3267 | 552.5473 | 481.8532 | 543.2105 | 574.9733 | 533.4872
2463.0354 | 662.6599 | 310.3768 | 552.8047 | 482.1572 | 543.3258 | 571.0625 | 532.4691
2464.0354 | 662.6756 | 310.7522 | 553.1956 | 481.9209 | 543.9701 | 566.8297 | 531.092
2465.0354 | 662.8182 | 310.5278 | 553.0993 | 481.4007 | 545.2832 | 570.6538 | 532.1452
2466.0354 | 664.5151 | 310.6773 | 552.7326 | 481.3822 | 545.7515 | 572.1591 | 533.9321
2467.0354 | 667.2822 | 310.7914 | 552.7553 | 481.5389 | 546.0373 | 573.7208 | 533.1767
2468.0354 | 667.5637 | 310.8639 | 552.6636 | 482.175 | 547.7193 | 572.6227 | 531.1929
2469.0354 | 666.5975 | 311.0471 | 552.614 | 481.7187 | 550.4488 | 570.922 | 530.0737
2470.0354 | 665.9795 | 311.3182 | 553.0046 | 481.6034 | 551.1923 | 569.1303 | 530.2799
2471.0354 | 664.7805 | 311.4796 | 553.3082 | 481.5724 | 551.5157 | 569.3208 | 532.2683
2472.0354 | 664.4811 | 311.7529 | 553.291 | 481.6088 | 551.8182 | 567.4011 | 533.6551
2473.0354 | 662.8814 | 311.9377 | 552.9766 | 481.6807 | 553.2488 | 567.028 | 532.8712
2474.0354 | 661.0789 | 312.031 | 553.8563 | 481.5864 | 554.7506 | 569.0764 | 534.308
2475.0354 | 654.9185 | 312.2088 | 554.2014 | 481.3446 | 555.1536 | 568.5574 | 533.9941
2476.0354 | 653.8719 | 312.2787 | 553.9183 | 481.3478 | 554.1223 | 568.4383 | 533.1925
2477.0354 | 656.3745 | 312.313 | 553.3943 | 481.2626 | 556.1795 | 572.9562 | 535.6979
2478.0354 | 656.7669 | 312.5182 | 553.7511 | 481.22 | 557.9892 | 571.3826 | 536.3509
2479.0354 | 657.3811 | 312.7213 | 555.1712 | 481.2483 | 559.242 | 571.7467 | 536.9838
2480.0354 | 655.6776 | 313.0358 | 555.1089 | 481.1952 | 562.0464 | 569.1859 | 536.3331
2481.0354 | 653.9831 | 313.028 | 555.159 | 480.9849 | 563.7696 | 567.5548 | 535.6354
2482.0354 | 655.5945 | 312.9897 | 554.7919 | 481.2892 | 568.3695 | 565.5001 | 535.5096
2483.0354 | 656.452 | 313.3987 | 555.6375 | 481.4048 | 568.6433 | 565.9664 | 536.991
2484.0354 | 654.7111 | 313.5079 | 556.8042 | 481.2756 | 568.4158 | 565.6034 | 539.2317
2485.0354 | 655.3642 | 313.8049 | 556.075 | 481.7967 | 567.0857 | 563.2699 | 539.1987
2486.0354 | 656.4176 | 313.965 | 556.3331 | 481.4949 | 568.31 | 565.0424 | 540.0865
2487.0354 | 657.0157 | 314.2589 | 556.8872 | 481.3179 | 570.2162 | 565.7889 | 540.8499
2488.0354 | 661.0095 | 314.4958 | 558.0708 | 481.414 | 574.7328 | 568.536 | 543.3031
2489.0354 | 662.609 | 314.6588 | 557.913 | 481.4319 | 576.4526 | 569.4815 | 543.2213
2490.0354 | 661.7161 | 314.5534 | 559.096 | 481.4229 | 580.7932 | 567.3843 | 546.1863
2491.0354 | 661.1571 | 315.5141 | 559.7338 | 481.2438 | 584.6964 | 569.6609 | 551.8695
2492.0354 | 661.046 | 315.5552 | 559.9087 | 481.5638 | 587.3578 | 568.6674 | 553.0251
2493.0354 | 659.3129 | 315.3835 | 559.8723 | 481.7937 | 591.8977 | 568.3972 | 554.4608
2494.0354 | 656.3971 | 315.2926 | 558.3927 | 481.2364 | 596.0211 | 566.4991 | 553.8951
2495.0354 | 660.4949 | 315.3081 | 558.6993 | 481.4709 | 596.2454 | 568.9437 | 553.1791
2496.0354 | 659.0358 | 315.3498 | 559.3091 | 481.2257 | 595.2571 | 572.8455 | 553.8466
2497.0354 | 655.1131 | 315.8423 | 559.1511 | 481.2151 | 596.4068 | 571.8369 | 552.5123
2498.0354 | 657.1308 | 316.2431 | 559.1455 | 481.2423 | 597.1976 | 574.3032 | 550.45
2499.0354 | 656.4816 | 316.4873 | 559.8788 | 481.8424 | 597.8641 | 571.9818 | 551.0607
2500.0354 | 654.9871 | 316.4978 | 560.3732 | 481.389 | 597.1979 | 569.2178 | 548.3118
2501.0354 | 654.6651 | 317.4315 | 560.6811 | 481.185 | 597.3683 | 567.1096 | 548.0342
2502.0354 | 657.1319 | 317.4279 | 560.9737 | 481.5161 | 596.4982 | 569.6121 | 548.9193
2503.0354 | 658.8692 | 317.5581 | 561.7747 | 481.402 | 596.7981 | 570.8074 | 549.5178
2504.0354 | 660.613 | 317.8331 | 562.5971 | 481.3473 | 597.967 | 572.0383 | 549.1992
2505.0354 | 662.4993 | 317.7973 | 563.1629 | 481.4696 | 597.6599 | 575.8304 | 546.7397
2506.0354 | 662.6506 | 318.0638 | 562.9683 | 481.3471 | 598.3927 | 579.7763 | 549.7023
2507.0354 | 663.4708 | 318.0224 | 564.2948 | 481.2631 | 600.6132 | 582.1181 | 548.2645
2508.0354 | 659.7572 | 318.1136 | 564.8089 | 481.3342 | 597.706 | 579.7368 | 547.3704
2509.0354 | 660.3851 | 318.2071 | 564.7253 | 481.8413 | 598.2794 | 577.4402 | 546.9803
2510.0354 | 659.9048 | 318.3389 | 564.1654 | 481.7221 | 600.1198 | 574.8322 | 548.4044
2511.0354 | 660.0848 | 318.5219 | 564.3884 | 481.3348 | 600.7829 | 578.2226 | 550.2055
2512.0354 | 657.2319 | 318.6931 | 564.5809 | 481.4008 | 599.7488 | 577.6609 | 549.8722
2513.0354 | 657.0916 | 319.173 | 565.9504 | 481.5582 | 601.0112 | 577.1214 | 549.34
2514.0354 | 654.8714 | 319.1804 | 566.5911 | 481.4047 | 599.5441 | 574.5449 | 548.8611
2515.0354 | 652.0513 | 319.2103 | 566.3719 | 481.7494 | 599.8277 | 572.331 | 547.484
2516.0354 | 653.9556 | 319.4438 | 566.2889 | 481.4027 | 598.7273 | 570.4479 | 546.3955
2517.0354 | 654.4065 | 319.6527 | 566.8278 | 481.6931 | 597.3176 | 570.2248 | 545.8911
2518.0354 | 652.987 | 320.0266 | 566.9507 | 481.9086 | 595.6262 | 567.5394 | 543.4202
2519.0354 | 652.9085 | 320.1119 | 566.6989 | 482.2348 | 593.404 | 566.7648 | 552.62
2520.0354 | 650.4259 | 320.1094 | 566.6658 | 481.9154 | 592.6366 | 566.2625 | 551.5191
2521.0354 | 646.6876 | 320.1581 | 566.4624 | 481.9645 | 592.8201 | 568.166 | 550.9338
2522.0354 | 646.878 | 320.2499 | 566.1586 | 483.0002 | 593.5824 | 567.5417 | 550.1755
2523.0354 | 644.8243 | 320.1703 | 566.2347 | 482.7116 | 592.446 | 565.7929 | 548.1477
2524.0354 | 643.095 | 320.5267 | 567.716 | 482.9926 | 593.1312 | 562.8072 | 547.4591
2525.0354 | 643.7598 | 320.5254 | 568.4428 | 483.1459 | 590.4859 | 562.8894 | 548.4408
2526.0354 | 642.5967 | 320.7457 | 567.9888 | 483.2016 | 587.7271 | 560.4148 | 549.1709
2527.0354 | 642.4979 | 320.8449 | 567.9048 | 483.2314 | 585.1234 | 558.4074 | 551.6525
2528.0354 | 641.7119 | 320.8693 | 567.9128 | 482.6645 | 583.1939 | 557.7663 | 552.0419
2529.0354 | 640.4407 | 321.532 | 569.4777 | 482.541 | 581.266 | 560.0373 | 551.9382
2530.0354 | 640.5413 | 321.6726 | 569.1547 | 482.5739 | 581.5141 | 562.8881 | 551.8826
2531.0354 | 641.0945 | 321.4288 | 569.1579 | 482.7184 | 580.383 | 562.9307 | 549.1792
2532.0354 | 644.5118 | 321.4234 | 568.3036 | 482.7441 | 580.1355 | 564.3036 | 549.0909
2533.0354 | 646.8595 | 321.4282 | 568.7979 | 482.7601 | 577.1809 | 565.6254 | 549.5274
2534.0354 | 647.9297 | 321.8323 | 569.5068 | 482.6426 | 574.8934 | 566.9475 | 550.06
2535.0354 | 647.3068 | 321.9873 | 570.008 | 483.2425 | 573.0648 | 567.4411 | 549.8861
2536.0354 | 648.0175 | 322.8525 | 571.2821 | 483.4933 | 572.7069 | 564.8648 | 549.3441
2537.0354 | 647.2675 | 322.9566 | 572.1288 | 483.0635 | 573.4754 | 562.6083 | 547.2401
2538.0354 | 650.1289 | 322.824 | 571.6479 | 483.0699 | 572.5182 | 566.1993 | 546.8889
2539.0354 | 649.1294 | 322.916 | 571.4056 | 483.067 | 571.6679 | 565.9954 | 546.1356
2540.0354 | 646.422 | 323.0574 | 570.9118 | 482.7568 | 571.6692 | 564.0375 | 544.064
2541.0354 | 646.2377 | 322.9227 | 570.7794 | 483.0444 | 570.4398 | 565.7868 | 542.9076
2542.0354 | 648.1204 | 323.2369 | 570.8247 | 483.0337 | 568.7802 | 565.3821 | 543.5628
2543.0354 | 649.3919 | 323.31 | 573.0567 | 484.0407 | 569.6071 | 565.0576 | 543.4789
2544.0354 | 648.3904 | 323.3675 | 572.4043 | 483.7398 | 569.0176 | 560.5036 | 541.9306
2545.0354 | 647.2221 | 324.0274 | 571.2353 | 484.2756 | 572.0217 | 559.8032 | 541.7569
2546.0354 | 644.0535 | 323.954 | 572.5902 | 483.4462 | 572.6825 | 560.114 | 542.197
2547.0354 | 637.9657 | 323.8703 | 572.4002 | 483.1645 | 571.2377 | 561.3268 | 539.8382
2548.0354 | 638.1238 | 324.0904 | 572.3914 | 483.2075 | 577.5519 | 558.8599 | 539.2548
2549.0354 | 641.4122 | 323.9548 | 572.0872 | 483.069 | 576.4753 | 563.1402 | 541.4666
2550.0354 | 642.863 | 324.2029 | 572.7611 | 483.24 | 571.7748 | 563.2758 | 541.0055
2551.0354 | 643.6903 | 324.4059 | 572.624 | 483.2471 | 569.0694 | 560.8189 | 538.8241
2552.0354 | 645.3171 | 324.391 | 571.6463 | 483.2216 | 566.4256 | 561.5386 | 536.6968
2553.0354 | 648.7191 | 324.5574 | 571.1488 | 483.1327 | 567.3562 | 561.5948 | 536.7881
2554.0354 | 649.8613 | 324.5297 | 571.3106 | 483.3184 | 567.2842 | 560.2993 | 536.1174
2555.0354 | 652.4271 | 324.5279 | 571.7321 | 483.1794 | 568.5102 | 558.6186 | 534.1505
2556.0354 | 651.5305 | 324.7621 | 571.9921 | 483.1486 | 568.6618 | 561.7132 | 534.7746
2557.0354 | 652.094 | 325.1915 | 571.9557 | 483.1146 | 568.8897 | 565.4418 | 538.0899
2558.0354 | 651.2222 | 325.4023 | 572.0207 | 483.1047 | 565.8273 | 573.1131 | 540.8255
2559.0354 | 652.1535 | 325.7098 | 572.5125 | 483.2883 | 562.3473 | 573.9468 | 540.9952
2560.0354 | 655.5849 | 325.6978 | 572.1876 | 483.0516 | 563.2753 | 573.1135 | 545.399
2561.0354 | 657.0605 | 325.7507 | 572.1111 | 483.4583 | 562.5335 | 571.993 | 544.0693
2562.0354 | 658.4568 | 325.7531 | 572.9195 | 483.6999 | 561.4203 | 568.1294 | 543.774
2563.0354 | 657.948 | 325.7805 | 574.0964 | 483.4981 | 560.7079 | 568.2575 | 541.7266
2564.0354 | 656.9666 | 326.2935 | 575.5268 | 483.1924 | 559.6236 | 567.2946 | 542.1604
2565.0354 | 662.1625 | 326.5218 | 576.4164 | 483.2555 | 559.3832 | 568.6658 | 543.7103
2566.0354 | 664.318 | 326.8839 | 576.1883 | 483.4554 | 559.0958 | 569.2891 | 545.4482
2567.0354 | 666.5024 | 326.8461 | 576.8247 | 483.4526 | 558.5588 | 568.8235 | 547.3491
2568.0354 | 665.3682 | 326.7877 | 576.472 | 483.4112 | 558.1702 | 566.1347 | 548.0083
2569.0354 | 661.3675 | 326.8498 | 575.9388 | 483.204 | 556.3685 | 563.0288 | 545.2745
2570.0354 | 658.8199 | 327.0285 | 575.7164 | 483.0218 | 555.8814 | 561.4065 | 543.0661
2571.0354 | 657.8644 | 327.1643 | 576.6521 | 483.3145 | 553.522 | 561.8724 | 543.4262
2572.0354 | 656.8596 | 327.0496 | 577.2399 | 483.1594 | 552.0588 | 561.4314 | 543.6823
2573.0354 | 655.6128 | 327.0567 | 576.5563 | 482.9186 | 551.0027 | 562.0197 | 546.1953
2574.0354 | 655.1956 | 327.1494 | 576.0159 | 483.025 | 549.6081 | 561.2328 | 546.6714
2575.0354 | 651.2998 | 327.304 | 577.4866 | 482.983 | 550.4072 | 560.3097 | 546.3554
2576.0354 | 647.8359 | 327.7579 | 579.0449 | 483.2006 | 549.3542 | 559.6214 | 547.0948
2577.0354 | 647.2519 | 328.4646 | 579.7311 | 483.2116 | 551.9384 | 559.8896 | 546.3769
2578.0354 | 649.7576 | 328.2024 | 578.6883 | 482.7836 | 554.2432 | 559.4209 | 547.1293
2579.0354 | 652.6642 | 328.515 | 577.8841 | 482.8677 | 555.6981 | 559.3682 | 545.5609
2580.0354 | 653.3853 | 328.4694 | 577.2985 | 483.2857 | 560.5063 | 560.6799 | 544.2944
2581.0354 | 655.4756 | 328.3251 | 576.9889 | 483.294 | 562.0552 | 560.4113 | 543.7829
2582.0354 | 653.7169 | 328.539 | 577.289 | 483.3307 | 563.0761 | 559.2751 | 542.3099
2583.0354 | 654.8775 | 328.6749 | 577.0112 | 483.2672 | 564.3123 | 556.9955 | 541.0427
2584.0354 | 656.9031 | 328.7773 | 577.0241 | 484.1926 | 564.4617 | 556.0106 | 539.5346
2585.0354 | 654.4295 | 328.992 | 577.3265 | 483.4105 | 563.2723 | 553.9477 | 538.1788
2586.0354 | 651.5039 | 329.0798 | 577.7909 | 483.5033 | 560.9953 | 551.4814 | 537.0999
2587.0354 | 646.629 | 329.2448 | 577.5954 | 483.1129 | 558.1007 | 552.0633 | 537.4719
2588.0354 | 643.7574 | 329.748 | 577.5187 | 483.1104 | 556.0631 | 551.853 | 537.6054
2589.0354 | 644.1429 | 329.7439 | 577.636 | 482.8567 | 554.444 | 553.0033 | 537.7495
2590.0354 | 642.6773 | 329.7124 | 577.4344 | 483.3795 | 552.2533 | 553.2096 | 537.1073
2591.0354 | 646.6901 | 329.9443 | 577.0763 | 483.3279 | 550.8568 | 555.3067 | 537.8595
2592.0354 | 648.2371 | 329.8912 | 576.9002 | 483.0819 | 548.1951 | 555.105 | 537.9429
2593.0354 | 646.836 | 329.9147 | 576.4714 | 483.2933 | 546.6343 | 555.0262 | 536.6351
2594.0354 | 645.3561 | 329.9893 | 576.2376 | 482.9263 | 545.5378 | 554.7269 | 535.8721
2595.0354 | 644.5973 | 330.5023 | 576.1621 | 483.0362 | 545.1166 | 556.1011 | 535.4975
2596.0354 | 643.9758 | 330.4716 | 575.8852 | 483.0248 | 544.2787 | 554.4823 | 533.2116
2597.0354 | 646.2577 | 330.5123 | 575.6832 | 483.3061 | 544.6179 | 554.1375 | 531.552
2598.0354 | 645.5838 | 330.6544 | 576.3517 | 483.7174 | 544.7386 | 552.8505 | 530.6608
2599.0354 | 646.8936 | 331.0644 | 576.698 | 483.3762 | 544.4889 | 551.7752 | 530.4064
2600.0354 | 644.399 | 331.2105 | 577.2762 | 483.4999 | 544.2467 | 554.7895 | 530.9079
2601.0354 | 643.2036 | 331.2627 | 577.5472 | 483.2978 | 543.0709 | 552.9826 | 532.2844
2602.0354 | 642.3157 | 331.4099 | 577.8769 | 483.4198 | 542.7924 | 552.6699 | 533.5361
2603.0354 | 639.6104 | 331.3899 | 578.1031 | 483.5086 | 542.4943 | 551.9028 | 533.19
2604.0354 | 634.8539 | 331.6762 | 576.5972 | 483.0429 | 541.7014 | 553.555 | 531.8534
2605.0354 | 638.0834 | 331.7898 | 576.5381 | 483.0342 | 541.9948 | 557.044 | 534.6965
2606.0354 | 638.0214 | 331.7233 | 576.7668 | 482.9668 | 541.3337 | 559.723 | 533.9088
2607.0354 | 636.2223 | 332.109 | 576.4485 | 482.9027 | 540.1633 | 560.7365 | 532.9903
2608.0354 | 634.8605 | 332.1731 | 576.4249 | 482.9844 | 539.4514 | 559.5003 | 534.2834
2609.0354 | 637.7809 | 332.2331 | 576.2901 | 483.0613 | 539.033 | 559.8263 | 534.681
2610.0354 | 638.5876 | 332.1166 | 576.6199 | 483.1739 | 540.2031 | 560.1572 | 534.5361
2611.0354 | 641.9616 | 332.1747 | 577.7376 | 483.0048 | 540.7012 | 559.9396 | 534.675
2612.0354 | 643.7714 | 332.6899 | 578.4836 | 483.1393 | 540.0307 | 561.6804 | 535.3038
2613.0354 | 645.6166 | 333.0425 | 579.6446 | 483.6178 | 539.3996 | 561.7316 | 537.1001
2614.0354 | 646.503 | 333.1933 | 580.1488 | 483.199 | 539.5535 | 560.9021 | 537.2156
2615.0354 | 647.2721 | 333.2718 | 581.0493 | 483.4418 | 539.0613 | 559.3123 | 536.8036
2616.0354 | 645.8422 | 333.3464 | 581.4816 | 483.3098 | 538.3928 | 558.2392 | 537.0401
2617.0354 | 647.331 | 333.4375 | 581.56 | 483.1909 | 537.9465 | 560.4848 | 542.7912
2618.0354 | 650.2682 | 333.6174 | 579.5681 | 482.8139 | 537.6565 | 560.6578 | 543.0443
2619.0354 | 651.8487 | 333.6669 | 578.6068 | 483.4718 | 538.9429 | 563.0774 | 545.3516
2620.0354 | 652.8644 | 334.4524 | 578.57 | 484.2646 | 539.3153 | 560.3569 | 544.5494
2621.0354 | 648.1571 | 334.1921 | 578.5255 | 483.5844 | 539.6998 | 557.0327 | 541.6085
2622.0354 | 647.5294 | 334.4275 | 578.9301 | 483.0436 | 540.2903 | 561.2132 | 542.8256
2623.0354 | 645.9476 | 335.4612 | 580.096 | 483.0062 | 539.8405 | 563.9418 | 544.5362
2624.0354 | 648.0029 | 335.5616 | 580.8008 | 483.2688 | 539.6727 | 565.2967 | 547.9247
2625.0354 | 649.474 | 335.2962 | 579.9177 | 483.01 | 539.44 | 564.4844 | 550.1214
2626.0354 | 651.2913 | 335.3497 | 579.877 | 483.0455 | 539.0248 | 565.6813 | 550.89
2627.0354 | 653.6031 | 335.1327 | 580.7415 | 482.9158 | 539.966 | 565.8819 | 550.0788
2628.0354 | 656.4541 | 335.6081 | 581.3594 | 483.4863 | 540.5087 | 566.2647 | 552.3054
2629.0354 | 659.0138 | 335.9773 | 581.8231 | 483.2478 | 540.7339 | 564.8902 | 551.4756
2630.0354 | 659.4775 | 336.3345 | 581.5176 | 483.0678 | 539.337 | 564.9443 | 553.1134
2631.0354 | 659.9528 | 336.2599 | 582.2133 | 483.0103 | 540.713 | 563.3331 | 550.4599
2632.0354 | 657.5528 | 336.272 | 582.2407 | 482.8517 | 540.7395 | 562.9159 | 549.9093
2633.0354 | 654.5681 | 336.6943 | 582.5193 | 483.0215 | 540.5335 | 559.0153 | 548.2008
2634.0354 | 655.178 | 336.8429 | 583.1722 | 483.0302 | 539.606 | 560.6252 | 546.8555
2635.0354 | 654.6345 | 336.4719 | 581.8904 | 482.8823 | 538.4633 | 558.6831 | 545.0434
2636.0354 | 655.5325 | 336.6253 | 581.3206 | 483.0137 | 537.8017 | 559.3529 | 543.5791
2637.0354 | 657.8896 | 336.7873 | 581.0491 | 483.2163 | 537.0537 | 558.2084 | 542.4697
2638.0354 | 658.1281 | 336.7161 | 581.8881 | 482.889 | 536.4026 | 556.1965 | 540.8155
2639.0354 | 656.1515 | 337.0188 | 581.8344 | 482.7407 | 536.851 | 554.5074 | 538.2917
2640.0354 | 657.3172 | 337.0608 | 581.75 | 482.3875 | 537.4571 | 556.1004 | 536.9682
2641.0354 | 656.9173 | 337.093 | 581.4327 | 482.6999 | 536.7248 | 558.2129 | 536.6859
2642.0354 | 656.858 | 337.1273 | 581.328 | 483.1507 | 537.9619 | 557.0915 | 535.4313
2643.0354 | 657.9645 | 337.4693 | 581.3157 | 483.2081 | 538.1104 | 555.4681 | 533.703
2644.0354 | 659.4798 | 337.8068 | 582.0506 | 482.979 | 537.7129 | 553.2643 | 533.079
2645.0354 | 656.5896 | 338.2026 | 581.7174 | 482.3891 | 537.706 | 551.5602 | 531.4688
2646.0354 | 650.9229 | 339.1303 | 581.9843 | 482.5141 | 536.0915 | 553.833 | 530.3798
2647.0354 | 652.1107 | 338.6145 | 581.8769 | 482.3625 | 534.0303 | 554.9051 | 531.8899
2648.0354 | 650.0683 | 338.6089 | 581.976 | 482.4402 | 532.6269 | 556.7593 | 533.4353
2649.0354 | 647.9172 | 338.5149 | 582.3915 | 483.0078 | 532.7009 | 556.5965 | 532.9878
2650.0354 | 646.171 | 338.8654 | 581.6836 | 484.1976 | 533.815 | 557.7184 | 533.6502
2651.0354 | 644.4276 | 338.9546 | 581.2692 | 483.8424 | 533.497 | 555.3856 | 533.5012
2652.0354 | 642.7767 | 339.2775 | 580.9036 | 483.1198 | 534.0746 | 554.7832 | 532.1803
2653.0354 | 643.7144 | 339.3377 | 580.6361 | 482.8454 | 535.7543 | 556.1102 | 534.012
2654.0354 | 643.0006 | 339.445 | 580.5319 | 482.7541 | 538.0924 | 557.5479 | 533.8946
2655.0354 | 641.6999 | 339.9959 | 580.6973 | 482.8171 | 540.003 | 559.8342 | 535.2052
2656.0354 | 639.7136 | 340.1691 | 581.6488 | 483.4545 | 539.0279 | 560.8431 | 534.7394
2657.0354 | 638.1479 | 340.4958 | 581.3272 | 482.9947 | 538.5116 | 558.7039 | 534.2433
2658.0354 | 639.6328 | 340.3055 | 581.8762 | 483.2109 | 539.7046 | 559.4401 | 535.4008
2659.0354 | 641.1831 | 340.3951 | 581.3651 | 484.4538 | 540.5995 | 559.3725 | 536.534
2660.0354 | 641.2839 | 340.691 | 580.8956 | 484.3713 | 540.3497 | 556.0932 | 535.8772
2661.0354 | 643.2026 | 340.6965 | 580.4474 | 483.4458 | 541.7725 | 555.8153 | 535.2511
2662.0354 | 644.2034 | 340.8649 | 580.9997 | 483.6904 | 543.3029 | 555.9831 | 536.1028
2663.0354 | 644.4309 | 341.3921 | 582.3235 | 483.7808 | 543.081 | 554.0171 | 535.6098
2664.0354 | 644.8395 | 341.5259 | 582.2819 | 483.7661 | 542.6798 | 551.4275 | 535.0759
2665.0354 | 644.5325 | 342.1729 | 583.222 | 483.8712 | 542.1059 | 549.7752 | 535.4497
2666.0354 | 642.5359 | 342.3365 | 583.7452 | 484.0624 | 542.4465 | 550.3063 | 535.2912
2667.0354 | 642.2892 | 341.9608 | 584.3563 | 483.7707 | 541.1606 | 548.2996 | 533.7211
2668.0354 | 642.9103 | 342.172 | 583.9594 | 484.1037 | 541.7906 | 550.5209 | 536.8217
2669.0354 | 645.1291 | 342.8481 | 584.9906 | 484.0346 | 540.5411 | 551.7973 | 539.6802
2670.0354 | 644.7093 | 345.2455 | 586.0316 | 484.0971 | 539.6744 | 550.1027 | 540.2296
2671.0354 | 643.0959 | 344.1474 | 584.1235 | 484.4882 | 539.225 | 550.3021 | 539.1124
2672.0354 | 645.215 | 343.8748 | 583.6421 | 484.4275 | 540.5604 | 551.9058 | 540.3371
2673.0354 | 645.1182 | 344.0169 | 583.5899 | 484.342 | 540.6905 | 551.3787 | 539.2232
2674.0354 | 646.3281 | 344.5353 | 584.2001 | 484.1965 | 541.4874 | 553.7501 | 539.2838
2675.0354 | 646.2991 | 345.2799 | 584.209 | 484.2943 | 541.0568 | 553.5606 | 539.2527
2676.0354 | 646.5402 | 345.102 | 583.6987 | 484.3857 | 540.1169 | 553.1725 | 537.7845
2677.0354 | 650.9262 | 345.3732 | 583.8153 | 484.5326 | 540.7979 | 552.4513 | 537.7681
2678.0354 | 651.1137 | 344.885 | 584.2362 | 484.1035 | 541.3281 | 553.314 | 536.717
2679.0354 | 651.1936 | 346.154 | 585.522 | 484.3184 | 541.8665 | 552.8259 | 536.046
2680.0354 | 651.7946 | 346.5004 | 585.5661 | 484.1654 | 540.8164 | 553.3648 | 538.3445
2681.0354 | 653.6252 | 346.4865 | 584.7524 | 484.5601 | 541.5815 | 554.767 | 538.9963
2682.0354 | 652.2303 | 347.2851 | 585.4416 | 484.8849 | 541.0673 | 552.9696 | 538.9442
2683.0354 | 650.4843 | 347.6844 | 585.0568 | 484.6692 | 540.369 | 551.6433 | 537.4355
2684.0354 | 649.2079 | 347.6665 | 583.9572 | 484.6167 | 540.1857 | 550.1523 | 537.1455
2685.0354 | 651.3009 | 348.136 | 583.9027 | 484.512 | 541.0345 | 550.6508 | 536.163
2686.0354 | 651.7913 | 348.0273 | 584.4448 | 484.8633 | 541.5809 | 549.7691 | 535.0724
2687.0354 | 651.5467 | 347.3742 | 583.6937 | 485.1311 | 541.6335 | 550.9715 | 536.2287
2688.0354 | 652.8768 | 348.0325 | 583.7579 | 484.9017 | 542.5035 | 551.3322 | 534.827
2689.0354 | 654.5552 | 348.643 | 583.7961 | 485.3744 | 543.526 | 552.5879 | 534.9098
2690.0354 | 654.0805 | 348.8702 | 583.4519 | 485.4128 | 544.4806 | 551.8442 | 534.4812
2691.0354 | 653.4663 | 348.6561 | 583.6245 | 484.9805 | 544.8999 | 550.6814 | 534.8358
2692.0354 | 649.7579 | 349.0116 | 583.8136 | 484.8285 | 545.8413 | 550.2514 | 533.5426
2693.0354 | 646.2644 | 350.2914 | 584.1479 | 485.3212 | 545.8469 | 551.5307 | 533.3769
2694.0354 | 646.9369 | 350.7661 | 583.9169 | 485.1252 | 545.453 | 552.1182 | 534.4521
2695.0354 | 651.2495 | 351.409 | 584.5755 | 485.1321 | 546.5794 | 552.9639 | 534.9384
2696.0354 | 652.4799 | 352.0643 | 584.1076 | 485.6506 | 546.5935 | 555.0277 | 533.534
2697.0354 | 650.6591 | 352.4057 | 584.0097 | 486.6239 | 545.2585 | 552.7647 | 531.8074
2698.0354 | 650.1418 | 353.31 | 585.3576 | 486.0676 | 549.8499 | 551.7183 | 531.7556
2699.0354 | 645.6741 | 352.1982 | 585.5306 | 485.4847 | 551.4268 | 549.6405 | 531.6986
2700.0354 | 647.5947 | 352.1887 | 584.7017 | 485.9355 | 552.831 | 549.2193 | 531.9538
2701.0354 | 649.0448 | 352.9199 | 584.8782 | 485.5476 | 552.8701 | 553.7955 | 534.6597
2702.0354 | 652.702 | 354.5653 | 584.0833 | 485.7976 | 559.8344 | 555.2043 | 534.9505
2703.0354 | 653.7637 | 354.7047 | 584.3904 | 485.9492 | 559.0208 | 553.0006 | 535.151
2704.0354 | 654.0026 | 357.2882 | 584.9219 | 486.7863 | 557.8783 | 553.3865 | 535.5838
2705.0354 | 651.6978 | 358.9697 | 584.1563 | 487.3269 | 561.1741 | 551.8899 | 534.8179
2706.0354 | 649.5182 | 357.9527 | 584.8347 | 486.2254 | 562.2138 | 548.8522 | 531.8566
2707.0354 | 650.5617 | 357.0432 | 585.6958 | 486.189 | 562.039 | 548.5153 | 530.6749
2708.0354 | 651.5207 | 357.7679 | 584.3972 | 486.131 | 567.8769 | 551.6819 | 530.9895
2709.0354 | 653.2292 | 357.7346 | 584.5804 | 486.4039 | 571.9681 | 554.7066 | 531.9168
2710.0354 | 652.1131 | 357.9652 | 584.5442 | 487.9644 | 571.2376 | 555.0882 | 533.0222
2711.0354 | 647.9767 | 358.3843 | 584.9398 | 488.0536 | 577.1145 | 552.649 | 532.4919
2712.0354 | 648.3416 | 358.1839 | 584.2728 | 486.7546 | 575.1362 | 554.0793 | 531.2919
2713.0354 | 650.6897 | 359.3886 | 584.9695 | 487.4341 | 575.8263 | 557.6916 | 534.3694
2714.0354 | 652.8235 | 359.5325 | 584.3773 | 487.3031 | 574.9802 | 562.6711 | 536.9701
2715.0354 | 655.518 | 358.8399 | 584.3068 | 487.9105 | 573.8984 | 563.346 | 537.9015
2716.0354 | 656.5331 | 360.7312 | 584.8681 | 487.4999 | 571.7402 | 562.5306 | 536.4445
2717.0354 | 652.8703 | 360.4133 | 585.2782 | 487.7621 | 569.1439 | 560.2916 | 535.2673
2718.0354 | 650.8219 | 359.3947 | 584.5784 | 488.8538 | 566.6528 | 557.671 | 533.1892
2719.0354 | 649.9733 | 359.1582 | 585.2782 | 488.8925 | 565.2754 | 556.5823 | 534.2999
2720.0354 | 649.1347 | 358.9026 | 586.1955 | 488.8157 | 566.1047 | 556.6573 | 536.3723
2721.0354 | 653.5576 | 359.503 | 587.3346 | 488.6147 | 569.8402 | 559.3301 | 540.1826
2722.0354 | 654.4105 | 359.8186 | 586.5393 | 488.9891 | 573.7379 | 560.2362 | 541.9058
2723.0354 | 657.9572 | 359.9438 | 587.1993 | 488.8775 | 581.5989 | 558.0044 | 542.3013
2724.0354 | 660.3237 | 360.4647 | 586.9935 | 489.3944 | 583.0156 | 557.8932 | 543.6369
2725.0354 | 662.3145 | 360.8266 | 585.9576 | 489.1304 | 584.6945 | 560.1762 | 546.9603
2726.0354 | 663.5656 | 362.6055 | 585.5141 | 488.5881 | 591.4879 | 564.8952 | 549.2677
2727.0354 | 667.0522 | 364.552 | 585.1079 | 488.9014 | 593.5919 | 570.6807 | 550.3814
2728.0354 | 669.9466 | 365.1931 | 585.659 | 489.4967 | 593.6295 | 568.2647 | 547.7802
2729.0354 | 671.3681 | 364.2592 | 585.7213 | 489.5878 | 591.925 | 568.5571 | 546.2949
2730.0354 | 670.4388 | 363.7836 | 587.5351 | 489.668 | 588.0179 | 567.1957 | 546.4313
2731.0354 | 668.9116 | 363.4919 | 586.7926 | 489.4593 | 585.9784 | 566.4006 | 546.051
2732.0354 | 670.0941 | 363.9779 | 585.6956 | 489.5996 | 590.5782 | 570.0615 | 547.1149
2733.0354 | 672.4487 | 365.5655 | 585.163 | 489.3087 | 591.6105 | 571.903 | 547.6011
2734.0354 | 673.4601 | 365.7644 | 585.1628 | 489.6224 | 592.4743 | 570.3928 | 546.4544
2735.0354 | 672.9885 | 365.258 | 585.6524 | 490.0792 | 591.6706 | 567.6387 | 544.3154
2736.0354 | 669.1611 | 365.7728 | 586.1421 | 489.9849 | 589.7267 | 564.9115 | 542.5681
2737.0354 | 668.0317 | 367.5317 | 585.6058 | 490.2753 | 586.5375 | 564.2606 | 540.4752
2738.0354 | 669.7633 | 366.8287 | 584.7986 | 489.9221 | 585.7897 | 567.5269 | 541.1218
2739.0354 | 670.0454 | 366.657 | 584.5818 | 489.6927 | 587.7738 | 565.781 | 540.4452
2740.0354 | 673.6422 | 366.5433 | 584.4407 | 489.7008 | 587.9669 | 565.4535 | 539.9422
2741.0354 | 677.6443 | 367.3287 | 585.6876 | 490.4305 | 585.9434 | 566.2491 | 539.806
2742.0354 | 679.5986 | 367.8891 | 584.8325 | 491.0644 | 583.3467 | 566.5719 | 538.9087
2743.0354 | 683.8807 | 368.1095 | 584.5167 | 490.2603 | 583.6378 | 566.6553 | 537.8993
2744.0354 | 683.8186 | 369.6664 | 585.5856 | 490.2221 | 581.3527 | 566.104 | 539.5849
2745.0354 | 683.0171 | 371.0249 | 585.5664 | 490.5625 | 577.9447 | 568.6859 | 540.615
2746.0354 | 680.9445 | 370.5391 | 584.7652 | 490.3466 | 574.7429 | 569.319 | 542.0471
2747.0354 | 681.7018 | 371.8634 | 584.0341 | 490.3805 | 573.7006 | 570.447 | 542.4156
2748.0354 | 682.6891 | 371.5888 | 583.83 | 490.6075 | 576.3565 | 571.5572 | 539.9131
2749.0354 | 684.4158 | 372.1014 | 583.5678 | 490.3105 | 577.5866 | 569.7166 | 537.9824
2750.0354 | 683.5369 | 370.7448 | 583.9343 | 490.9206 | 576.311 | 567.9255 | 540.1175
2751.0354 | 683.217 | 371.4321 | 583.5318 | 491.053 | 576.1016 | 568.583 | 540.8482
2752.0354 | 681.8222 | 372.3405 | 583.2095 | 490.7176 | 577.4346 | 570.4982 | 541.3624
2753.0354 | 681.7705 | 372.5009 | 583.147 | 490.7494 | 578.8219 | 571.3114 | 539.8156
2754.0354 | 682.1442 | 372.4484 | 583.416 | 491.3007 | 579.6343 | 569.4055 | 539.8561
2755.0354 | 681.0706 | 372.2509 | 582.9356 | 491.369 | 578.186 | 569.094 | 539.4459
2756.0354 | 679.9018 | 372.636 | 582.5509 | 492.1839 | 576.6723 | 567.207 | 538.2656
2757.0354 | 676.1642 | 372.303 | 583.1228 | 491.8793 | 576.7078 | 565.3167 | 536.8904
2758.0354 | 673.9994 | 373.4241 | 582.5154 | 491.6199 | 575.3175 | 565.4222 | 536.6202
2759.0354 | 673.6471 | 374.6034 | 582.6188 | 492.1048 | 578.0862 | 567.9608 | 537.1816
2760.0354 | 671.7414 | 373.8673 | 581.96 | 492.185 | 578.4255 | 567.7891 | 537.5213
2761.0354 | 671.6801 | 373.6033 | 581.8358 | 492.8147 | 577.7082 | 566.4238 | 536.8368
2762.0354 | 671.3941 | 374.3066 | 581.6281 | 493.2935 | 577.8311 | 565.1584 | 534.782
2763.0354 | 673.2249 | 373.8792 | 581.2499 | 492.6481 | 580.2329 | 568.352 | 536.2537
2764.0354 | 675.9006 | 375.1668 | 581.0788 | 492.8269 | 581.6287 | 568.2651 | 536.5643
2765.0354 | 677.0654 | 375.4705 | 580.8074 | 493.5077 | 582.1568 | 567.4151 | 535.9556
2766.0354 | 678.5907 | 375.7017 | 580.492 | 493.3397 | 581.7897 | 564.867 | 534.6077
2767.0354 | 679.4154 | 375.7358 | 580.4934 | 493.8537 | 581.2055 | 564.868 | 533.4183
2768.0354 | 680.7161 | 375.8111 | 580.1961 | 493.7962 | 584.7423 | 564.9376 | 535.3573
2769.0354 | 681.3573 | 376.5514 | 579.8945 | 493.9074 | 586.9287 | 567.0836 | 536.6722
2770.0354 | 683.7647 | 377.8764 | 579.6789 | 493.7132 | 588.6532 | 567.8876 | 536.6859
2771.0354 | 684.6797 | 377.2931 | 579.3257 | 493.8409 | 590.2848 | 568.2617 | 536.8032
2772.0354 | 685.4523 | 377.9928 | 579.0741 | 493.8923 | 592.0957 | 569.3378 | 536.6344
2773.0354 | 684.5551 | 378.6237 | 579.1894 | 494.6994 | 592.0669 | 567.7032 | 536.2986
2774.0354 | 684.2632 | 377.8566 | 578.8482 | 494.1743 | 589.4303 | 568.3014 | 534.7377
2775.0354 | 682.9094 | 379.1863 | 579.9613 | 494.7682 | 588.7817 | 568.6963 | 535.248
2776.0354 | 679.0852 | 378.686 | 578.864 | 495.2033 | 587.7153 | 567.9772 | 535.2311
2777.0354 | 682.0165 | 378.63 | 578.464 | 495.6343 | 587.9774 | 567.7715 | 533.8286
2778.0354 | 685.4396 | 379.1651 | 578.1612 | 495.2397 | 587.5027 | 565.7777 | 533.9927
2779.0354 | 681.6429 | 380.0836 | 578.3456 | 496.2514 | 587.5342 | 563.9763 | 533.7396
2780.0354 | 680.7098 | 381.423 | 578.4779 | 496.0446 | 585.9665 | 561.8287 | 531.4307
2781.0354 | 681.4204 | 379.9319 | 578.4095 | 495.7726 | 584.0954 | 561.2384 | 530.9056
2782.0354 | 684.5355 | 379.7469 | 577.8537 | 496.8116 | 582.6875 | 562.5483 | 530.9163
2783.0354 | 687.2469 | 379.6952 | 577.358 | 496.8666 | 583.5002 | 562.1485 | 531.5721
2784.0354 | 688.7055 | 380.0349 | 577.5062 | 496.5844 | 584.0111 | 562.2422 | 532.3624
2785.0354 | 687.8869 | 381.1045 | 578.2037 | 497.274 | 584.1144 | 561.1146 | 532.3239
2786.0354 | 683.8839 | 380.7489 | 577.4729 | 498.4418 | 581.9922 | 559.793 | 531.5256
2787.0354 | 680.4578 | 380.3833 | 577.1412 | 498.0888 | 581.1337 | 558.3639 | 530.3117
2788.0354 | 687.2569 | 382.007 | 576.6009 | 497.6719 | 580.2585 | 557.716 | 528.2178
2789.0354 | 687.7337 | 381.505 | 576.2632 | 498.0485 | 582.1887 | 558.3377 | 528.0388
2790.0354 | 690.5419 | 381.3595 | 576.1006 | 498.7639 | 583.1456 | 557.8667 | 528.1397
2791.0354 | 688.4007 | 382.5754 | 575.6578 | 498.8039 | 582.1501 | 556.5325 | 528.2809
2792.0354 | 688.0984 | 381.8453 | 575.6626 | 499.3752 | 581.5643 | 555.6536 | 527.6938
2793.0354 | 689.0872 | 381.578 | 575.4382 | 500.7483 | 582.2146 | 554.1419 | 526.4947
2794.0354 | 689.0565 | 383.2665 | 576.276 | 500.8998 | 581.2109 | 553.3856 | 526.3642
2795.0354 | 685.5856 | 385.5498 | 575.8933 | 500.4935 | 579.5527 | 553.6164 | 527.5504
2796.0354 | 682.3972 | 385.6694 | 575.2557 | 501.2893 | 578.6672 | 554.8468 | 528.6338
2797.0354 | 680.7934 | 385.0876 | 575.3759 | 502.0343 | 578.4166 | 554.4475 | 529.744
2798.0354 | 678.0251 | 385.1791 | 576.5029 | 501.3726 | 579.137 | 554.0254 | 529.5895
2799.0354 | 673.873 | 386.6048 | 576.7783 | 501.0913 | 576.9401 | 552.5456 | 528.5743
2800.0354 | 672.722 | 386.2312 | 576.8627 | 501.8941 | 576.4618 | 554.3388 | 528.9173
2801.0354 | 671.045 | 387.4751 | 576.1068 | 503.2786 | 577.2494 | 555.8997 | 530.2984
2802.0354 | 667.4674 | 386.946 | 577.3402 | 504.2512 | 576.8564 | 556.2536 | 530.4763
2803.0354 | 663.1662 | 389.5452 | 576.6716 | 503.2406 | 581.1368 | 555.1947 | 528.5403
2804.0354 | 664.0068 | 388.6544 | 575.6556 | 503.2391 | 581.4071 | 560.1359 | 531.3956
2805.0354 | 661.6375 | 388.0919 | 575.9736 | 504.872 | 582.1373 | 561.0449 | 532.4693
2806.0354 | 660.8393 | 387.6 | 575.8496 | 505.657 | 583.602 | 561.4697 | 533.4501
2807.0354 | 661.7 | 389.3721 | 575.6984 | 505.9718 | 583.5801 | 560.9049 | 533.636
2808.0354 | 661.5222 | 389.8704 | 575.2222 | 505.55 | 584.0249 | 560.6877 | 533.2028
2809.0354 | 664.1534 | 388.8923 | 574.824 | 505.6569 | 583.3264 | 562.2986 | 534.8152
2810.0354 | 661.6445 | 390.1975 | 575.0946 | 505.8211 | 582.8456 | 562.9132 | 536.3512
2811.0354 | 662.2451 | 390.2009 | 576.1009 | 506.3867 | 581.3481 | 561.9365 | 536.5293
2812.0354 | 661.54 | 389.9201 | 575.9299 | 506.1172 | 581.3443 | 563.0732 | 536.335
2813.0354 | 658.5629 | 391.0372 | 576.4796 | 506.941 | 580.3886 | 562.7641 | 536.1374
2814.0354 | 657.9283 | 390.4424 | 575.7307 | 507.8598 | 578.5946 | 562.7754 | 535.8088
2815.0354 | 660.7957 | 389.5549 | 575.9985 | 507.7838 | 578.8348 | 563.7542 | 534.7543
2816.0354 | 661.2334 | 389.2416 | 575.6566 | 507.9143 | 579.2318 | 567.0025 | 537.2125
2817.0354 | 660.0415 | 389.3667 | 578.0841 | 509.5287 | 579.5271 | 569.3591 | 539.4197
2818.0354 | 659.3189 | 389.9213 | 578.1895 | 508.726 | 588.0551 | 567.2058 | 539.4337
2819.0354 | 656.8059 | 390.6109 | 578.5851 | 508.62 | 587.95 | 566.7967 | 538.987
2820.0354 | 655.9759 | 390.6334 | 577.9527 | 508.6264 | 585.6922 | 567.7722 | 538.96
2821.0354 | 654.9877 | 392.8718 | 578.7598 | 509.2436 | 583.7814 | 566.7257 | 538.5332
2822.0354 | 654.2598 | 392.4442 | 577.2695 | 509.2566 | 582.0147 | 564.4934 | 536.8606
2823.0354 | 653.7081 | 391.7193 | 577.596 | 509.5662 | 583.464 | 565.2593 | 537.1801
2824.0354 | 651.4188 | 392.1607 | 577.3794 | 509.894 | 584.1483 | 568.3335 | 537.7327
2825.0354 | 654.8689 | 393.1006 | 577.2133 | 509.9553 | 583.7113 | 570.8059 | 539.2132
2826.0354 | 657.0847 | 394.7545 | 578.0361 | 509.8856 | 583.1633 | 571.6901 | 540.5865
2827.0354 | 656.438 | 394.6105 | 577.2744 | 510.3493 | 581.4117 | 572.9107 | 541.3395
2828.0354 | 660.1746 | 394.8926 | 579.4987 | 510.9516 | 581.6941 | 574.522 | 541.7802
2829.0354 | 659.5158 | 395.0168 | 578.6405 | 511.489 | 580.9742 | 572.8264 | 541.1405
2830.0354 | 660.0609 | 396.5708 | 578.2335 | 511.5641 | 579.4401 | 569.671 | 539.0196
2831.0354 | 659.9503 | 397.884 | 577.5209 | 512.7247 | 578.5722 | 567.5669 | 537.3905
2832.0354 | 661.9586 | 397.4955 | 577.3267 | 512.3254 | 578.9855 | 565.6208 | 536.7658
2833.0354 | 666.2018 | 398.5207 | 577.4485 | 513.1298 | 578.9663 | 563.6726 | 535.1689
2834.0354 | 668.9924 | 398.286 | 577.6366 | 512.7554 | 581.3197 | 564.8891 | 535.0498
2835.0354 | 668.6412 | 398.4581 | 577.454 | 512.9481 | 583.041 | 567.7573 | 535.8158
2836.0354 | 672.1269 | 397.9133 | 577.8736 | 513.0257 | 583.0549 | 567.9342 | 536.2872
2837.0354 | 675.4975 | 399.5134 | 577.0258 | 513.3717 | 583.8878 | 568.7236 | 536.2896
2838.0354 | 677.8162 | 399.7756 | 576.8178 | 513.0958 | 583.7124 | 571.4739 | 538.0032
2839.0354 | 675.7242 | 399.0798 | 577.2347 | 514.1257 | 584.8587 | 570.0721 | 537.2418
2840.0354 | 673.6961 | 399.3223 | 577.124 | 514.4599 | 583.8055 | 569.2232 | 536.7706
2841.0354 | 675.7886 | 401.566 | 576.7425 | 514.3314 | 583.7952 | 567.5685 | 535.4713
2842.0354 | 678.9757 | 400.4029 | 576.0468 | 514.0787 | 585.6055 | 570.1757 | 537.1859
2843.0354 | 680.8314 | 400.8629 | 576.5301 | 514.3662 | 585.5792 | 568.8766 | 537.0708
2844.0354 | 680.0597 | 401.5755 | 576.9323 | 514.5053 | 585.4671 | 567.5602 | 536.9621
2845.0354 | 680.8566 | 400.8473 | 576.1733 | 514.7605 | 584.9251 | 568.0328 | 537.235
2846.0354 | 682.1221 | 402.091 | 576.1776 | 515.7301 | 586.1807 | 566.5455 | 536.0537
2847.0354 | 680.6821 | 402.4816 | 576.3687 | 515.6231 | 585.4589 | 567.9036 | 536.3181
2848.0354 | 679.5124 | 402.0525 | 576.5177 | 515.9394 | 587.526 | 568.2161 | 536.8567
2849.0354 | 677.5195 | 400.7287 | 577.291 | 516.75 | 588.7853 | 566.6321 | 535.9451
2850.0354 | 676.2122 | 400.4203 | 576.9341 | 517.3134 | 589.7184 | 565.8443 | 535.7226
2851.0354 | 673.8159 | 400.2873 | 576.5182 | 516.7551 | 589.2946 | 566.9851 | 535.9925
2852.0354 | 672.9303 | 400.0753 | 576.7035 | 517.1336 | 589.4157 | 567.8541 | 537.5037
2853.0354 | 671.5301 | 400.9876 | 577.4811 | 517.2158 | 588.3197 | 568.3824 | 538.2015
2854.0354 | 668.7964 | 400.6299 | 577.6867 | 517.8802 | 587.5684 | 568.8273 | 538.9667
2855.0354 | 667.7086 | 400.5192 | 578.1176 | 518.9935 | 586.9986 | 569.7265 | 539.2575
2856.0354 | 665.7765 | 400.5355 | 577.4874 | 518.6807 | 586.5953 | 569.4427 | 539.179
2857.0354 | 666.5085 | 400.3287 | 576.5843 | 518.809 | 587.8276 | 570.972 | 539.9697
2858.0354 | 667.9972 | 400.1413 | 576.7239 | 518.5485 | 589.3736 | 572.0451 | 540.6214
2859.0354 | 670.1628 | 400.0909 | 576.473 | 519.0081 | 589.4074 | 572.5963 | 540.4272
2860.0354 | 671.7017 | 400.7134 | 576.2181 | 519.283 | 590.7742 | 571.6424 | 540.048
2861.0354 | 678.459 | 401.2919 | 575.9237 | 519.8759 | 592.7308 | 569.4374 | 538.886
2862.0354 | 685.1301 | 402.9426 | 575.5067 | 519.7013 | 593.5914 | 567.6357 | 537.3916
2863.0354 | 687.7165 | 403.1275 | 576.863 | 520.4087 | 594.107 | 567.1336 | 536.8351
2864.0354 | 687.054 | 402.5434 | 577.6049 | 521.6673 | 593.3546 | 566.4763 | 536.3439
2865.0354 | 685.3083 | 402.9502 | 576.8853 | 522.1821 | 595.981 | 565.7333 | 535.9175
2866.0354 | 683.1133 | 402.8293 | 576.2448 | 521.2825 | 596.4852 | 566.4495 | 536.7488
2867.0354 | 680.0514 | 402.7281 | 576.2459 | 522.0581 | 595.4668 | 567.4096 | 537.129
2868.0354 | 679.7893 | 403.4682 | 576.5544 | 523.0499 | 595.0182 | 567.1353 | 536.5094
2869.0354 | 677.7428 | 404.0942 | 575.8475 | 523.1854 | 594.2056 | 565.4824 | 535.0419
2870.0354 | 676.5315 | 404.1368 | 575.8856 | 523.106 | 593.6037 | 564.3705 | 534.56
2871.0354 | 673.1427 | 404.4893 | 576.0946 | 523.255 | 593.4532 | 564.213 | 534.3739
2872.0354 | 670.5189 | 403.6402 | 576.5874 | 523.6985 | 592.4094 | 564.3758 | 534.6752
2873.0354 | 670.0285 | 403.1938 | 576.5936 | 523.7361 | 594.0141 | 566.0265 | 535.3276
2874.0354 | 667.0866 | 403.7724 | 576.1753 | 523.6762 | 594.4003 | 568.1125 | 537.056
2875.0354 | 670.1706 | 403.8129 | 576.087 | 523.9616 | 597.2944 | 570.4569 | 539.4844
2876.0354 | 669.6139 | 404.9119 | 577.281 | 524.9447 | 597.3928 | 572.4361 | 541.265
2877.0354 | 669.2609 | 409.2918 | 577.1153 | 524.8782 | 597.0537 | 573.4444 | 541.6234
2878.0354 | 666.2885 | 406.6606 | 577.1434 | 526.0252 | 596.2466 | 573.8149 | 542.9643
2879.0354 | 664.881 | 405.3652 | 576.2649 | 526.092 | 595.7485 | 573.1983 | 542.8002
2880.0354 | 665.6684 | 405.3778 | 575.9298 | 525.4764 | 593.9593 | 575.1809 | 543.0216
2881.0354 | 663.1517 | 406.2761 | 576.8515 | 525.8382 | 596.2822 | 574.5431 | 543.0357
2882.0354 | 664.1267 | 407.3899 | 577.1061 | 526.3034 | 597.9261 | 575.529 | 542.4205
2883.0354 | 665.5937 | 409.3201 | 576.7429 | 526.6598 | 599.2341 | 575.8229 | 543.7117
2884.0354 | 664.8675 | 408.2464 | 576.8185 | 527.9912 | 598.5736 | 575.8871 | 544.8187
2885.0354 | 666.7203 | 408.0182 | 576.0142 | 527.7289 | 601.0445 | 577.8111 | 545.4664
2886.0354 | 668.1116 | 409.1051 | 576.2528 | 527.2723 | 601.2096 | 575.4737 | 543.9554
2887.0354 | 668.9638 | 409.4873 | 576.6457 | 527.8341 | 602.1543 | 573.0665 | 542.8354
2888.0354 | 670.4969 | 410.2816 | 576.5465 | 528.1704 | 601.4603 | 571.8871 | 541.1899
2889.0354 | 676.8561 | 410.1234 | 577.0577 | 528.2296 | 601.3548 | 570.8132 | 540.932
2890.0354 | 676.5157 | 410.305 | 577.7065 | 529.2009 | 600.8856 | 572.5142 | 542.4578
2891.0354 | 673.8379 | 409.4069 | 577.8887 | 528.8809 | 601.9838 | 573.9697 | 543.5761
2892.0354 | 673.013 | 408.6433 | 577.6412 | 529.4133 | 600.0932 | 573.8711 | 542.6081
2893.0354 | 671.8153 | 408.3852 | 577.3196 | 530.4073 | 600.2124 | 574.943 | 542.4463
2894.0354 | 671.149 | 408.3116 | 576.821 | 530.0414 | 598.2502 | 573.3601 | 541.5889
2895.0354 | 670.3726 | 409.3652 | 578.3985 | 530.0819 | 597.5287 | 571.7792 | 539.8031
2896.0354 | 665.4301 | 409.6528 | 578.3719 | 530.5123 | 597.1813 | 570.9674 | 539.7245
2897.0354 | 670.0923 | 410.2307 | 579.7094 | 531.1724 | 597.0423 | 571.7757 | 540.6059
2898.0354 | 670.0114 | 410.3455 | 579.3623 | 531.825 | 598.6884 | 570.7043 | 541.7855
2899.0354 | 667.4775 | 412.3701 | 578.2656 | 531.817 | 600.4969 | 570.1936 | 541.92
2900.0354 | 665.8302 | 413.5641 | 578.0248 | 530.9484 | 599.4506 | 570.8594 | 542.3417
2901.0354 | 668.3736 | 411.8587 | 578.4547 | 531.7928 | 600.2294 | 572.1824 | 542.0848
2902.0354 | 667.7486 | 411.2936 | 580.1654 | 532.5442 | 602.0643 | 573.4191 | 542.9217
2903.0354 | 661.7338 | 410.5989 | 579.7381 | 532.438 | 601.6438 | 573.1434 | 542.6842
2904.0354 | 663.9065 | 410.4245 | 579.4186 | 532.682 | 601.1025 | 573.6911 | 543.327
2905.0354 | 664.8531 | 411.0815 | 579.7334 | 532.8987 | 602.0759 | 574.6219 | 542.4815
2906.0354 | 667.7245 | 410.1884 | 578.8141 | 533.1314 | 602.4241 | 575.5072 | 543.3232
2907.0354 | 667.0412 | 410.403 | 578.6349 | 533.264 | 602.6557 | 575.4856 | 542.3357
2908.0354 | 675.6382 | 412.5085 | 578.4836 | 533.2206 | 603.2239 | 573.6981 | 541.1865
2909.0354 | 675.93 | 412.3413 | 579.8095 | 533.2874 | 603.2599 | 573.6745 | 540.3692
2910.0354 | 674.4691 | 413.4051 | 579.7757 | 533.4679 | 602.593 | 573.9672 | 540.5872
2911.0354 | 673.1238 | 412.949 | 580.2237 | 533.6288 | 601.627 | 574.0867 | 540.3563
2912.0354 | 671.8396 | 412.734 | 579.4744 | 533.6842 | 602.0724 | 574.5855 | 540.2626
2913.0354 | 675.5809 | 412.5999 | 578.5436 | 533.6798 | 602.2435 | 576.3993 | 540.3358
2914.0354 | 679.6325 | 413.4581 | 578.5222 | 533.5832 | 602.4742 | 574.7617 | 540.1344
2915.0354 | 678.9946 | 413.9953 | 579.199 | 533.6479 | 602.4453 | 574.3589 | 539.9641
2916.0354 | 679.6521 | 416.6216 | 579.3007 | 533.9498 | 601.304 | 574.7661 | 539.4365
2917.0354 | 686.9938 | 414.2851 | 578.2475 | 534.0374 | 600.2416 | 574.246 | 537.8042
2918.0354 | 689.8281 | 415.0082 | 578.3414 | 534.2175 | 600.5358 | 573.072 | 537.1153
2919.0354 | 689.7261 | 414.0895 | 578.2729 | 534.265 | 600.1699 | 574.0407 | 537.8455
2920.0354 | 689.6945 | 414.0462 | 577.8377 | 534.0572 | 599.2833 | 575.8956 | 539.3624
2921.0354 | 687.8949 | 415.0795 | 578.0211 | 535.3788 | 598.5185 | 575.6876 | 539.245
2922.0354 | 684.7615 | 415.0499 | 578.4947 | 535.882 | 599.3979 | 576.526 | 540.1747
2923.0354 | 686.3756 | 414.5445 | 578.2222 | 535.9394 | 599.3061 | 576.7895 | 540.1929
2924.0354 | 686.5609 | 414.4295 | 578.4136 | 536.4545 | 600.8101 | 576.1727 | 540.7776
2925.0354 | 685.5027 | 414.4323 | 578.117 | 536.5515 | 602.5522 | 576.7416 | 542.75
2926.0354 | 686.3844 | 414.2403 | 577.8549 | 536.7351 | 603.9081 | 576.1838 | 543.2271
2927.0354 | 686.3536 | 414.2864 | 577.8291 | 537.0638 | 605.2905 | 577.0614 | 544.7855
2928.0354 | 684.6158 | 414.286 | 578.0773 | 536.2579 | 605.3506 | 577.0405 | 544.866
2929.0354 | 683.1146 | 414.5477 | 580.067 | 536.7984 | 604.6944 | 576.8035 | 545.4539
2930.0354 | 679.3131 | 414.8051 | 579.1885 | 537.3466 | 603.0146 | 576.5916 | 545.3966
2931.0354 | 680.3896 | 416.2753 | 578.4648 | 537.3655 | 603.7014 | 576.9648 | 544.5545
2932.0354 | 679.5496 | 417.2872 | 578.1583 | 537.2325 | 604.9168 | 576.2495 | 543.1508
2933.0354 | 681.5935 | 416.4749 | 577.9902 | 537.2751 | 604.2594 | 575.7069 | 542.2787
2934.0354 | 685.6857 | 415.6328 | 579.941 | 537.5528 | 603.0786 | 574.7166 | 542.3097
2935.0354 | 684.4264 | 415.4616 | 580.865 | 538.3382 | 601.1165 | 575.2604 | 543.3838
2936.0354 | 680.224 | 415.4432 | 579.9287 | 538.1323 | 600.2681 | 575.0652 | 542.8359
2937.0354 | 677.7796 | 415.9332 | 578.8745 | 537.869 | 601.0991 | 579.1136 | 545.1719
2938.0354 | 677.1827 | 416.1814 | 578.869 | 538.7843 | 600.5476 | 579.1712 | 545.007
2939.0354 | 677.0105 | 416.4386 | 578.5961 | 538.9596 | 600.5851 | 576.9305 | 543.9593
2940.0354 | 676.3647 | 417.6248 | 579.0483 | 539.2318 | 599.4727 | 575.2387 | 543.0894
2941.0354 | 673.2264 | 418.1348 | 580.3879 | 538.8114 | 597.9345 | 574.7105 | 542.4347
2942.0354 | 662.8663 | 417.902 | 579.601 | 539.1122 | 599.5116 | 576.2618 | 542.4644
2943.0354 | 661.8367 | 420.4404 | 578.7522 | 538.6678 | 599.1862 | 578.382 | 544.2621
2944.0354 | 662.6609 | 418.8843 | 578.8142 | 538.6752 | 598.2818 | 578.1274 | 544.1194
2945.0354 | 666.2442 | 418.3583 | 578.2274 | 538.9043 | 598.8342 | 581.1735 | 544.8726
2946.0354 | 671.8419 | 418.7747 | 578.3206 | 539.0181 | 599.5481 | 582.3892 | 544.8738
2947.0354 | 684.3703 | 418.6124 | 578.3812 | 539.3151 | 599.4189 | 581.1005 | 543.7834
2948.0354 | 685.8967 | 418.11 | 577.9846 | 539.364 | 601.1036 | 581.2593 | 542.8414
2949.0354 | 687.6546 | 418.1769 | 577.8179 | 539.2904 | 602.6421 | 581.5779 | 542.5161
2950.0354 | 691.7084 | 420.8052 | 577.8728 | 539.147 | 601.7248 | 581.7001 | 542.1215
2951.0354 | 691.7676 | 421.3457 | 577.8172 | 539.4179 | 601.7651 | 582.6314 | 542.346
2952.0354 | 690.659 | 421.789 | 577.3106 | 540.2311 | 600.3499 | 582.4527 | 541.7106
2953.0354 | 692.5642 | 420.0761 | 576.9485 | 539.8073 | 600.3831 | 581.1494 | 541.6787
2954.0354 | 693.4522 | 420.2965 | 576.9996 | 540.0524 | 601.7897 | 578.1437 | 539.068
2955.0354 | 692.7032 | 420.7022 | 578.1956 | 541.1245 | 602.2694 | 576.3932 | 538.7654
2956.0354 | 689.2774 | 420.9854 | 577.3875 | 541.709 | 600.5632 | 574.4382 | 537.4141
2957.0354 | 691.6194 | 422.1137 | 576.9706 | 541.2039 | 601.1946 | 574.7594 | 538.1506
2958.0354 | 691.7144 | 423.2291 | 577.0856 | 540.6289 | 602.0189 | 575.3665 | 538.4453
2959.0354 | 690.77 | 422.3221 | 577.4952 | 541.238 | 602.4146 | 577.6481 | 539.9353
2960.0354 | 689.1604 | 421.1117 | 577.0084 | 541.4015 | 601.1321 | 578.4477 | 540.0148
2961.0354 | 688.9785 | 422.1776 | 577.8989 | 540.8807 | 600.8202 | 580.7459 | 542.8643
2962.0354 | 684.7778 | 422.1939 | 577.2957 | 540.9757 | 598.8251 | 579.9508 | 543.7002
2963.0354 | 680.3418 | 422.4959 | 576.6428 | 541.1772 | 598.3575 | 579.846 | 543.6743
2964.0354 | 681.9014 | 422.233 | 576.1905 | 541.7706 | 600.5142 | 582.0257 | 543.87
2965.0354 | 682.9194 | 422.2295 | 576.0762 | 541.9348 | 601.6437 | 579.824 | 544.6471
2966.0354 | 685.1466 | 423.1486 | 576.4606 | 542.8364 | 600.9353 | 577.8453 | 545.2585
2967.0354 | 684.1437 | 424.7392 | 577.0684 | 543.5065 | 603.5599 | 576.5882 | 547.9855
2968.0354 | 682.0848 | 423.9091 | 577.1334 | 543.8573 | 605.8713 | 574.9615 | 547.4404
2969.0354 | 680.0866 | 423.4423 | 576.6786 | 543.489 | 607.614 | 574.1673 | 546.0831
2970.0354 | 677.7422 | 423.8279 | 576.975 | 543.9033 | 608.1575 | 575.0042 | 546.4028
2971.0354 | 670.9314 | 424.5414 | 576.8028 | 544.8553 | 607.3518 | 576.2726 | 546.0193
2972.0354 | 657.8918 | 424.4988 | 576.7088 | 544.6624 | 605.3801 | 575.8647 | 545.6566
2973.0354 | 654.1647 | 424.4953 | 577.4456 | 544.6251 | 604.0919 | 574.4036 | 544.7294
2974.0354 | 653.156 | 425.355 | 576.9093 | 544.293 | 603.708 | 574.9944 | 544.2674
2975.0354 | 651.452 | 427.2604 | 577.8314 | 544.4135 | 603.3183 | 575.277 | 545.3248
2976.0354 | 648.3486 | 427.2804 | 576.8732 | 544.6726 | 601.6398 | 575.2743 | 545.0462
2977.0354 | 650.9371 | 426.7728 | 577.2556 | 545.0474 | 601.1819 | 575.99 | 544.0718
2978.0354 | 652.3311 | 428.5531 | 578.6606 | 546.1882 | 601.7156 | 575.4125 | 544.925
2979.0354 | 658.3044 | 427.8736 | 577.5553 | 546.099 | 600.5669 | 573.5536 | 543.9494
2980.0354 | 664.9024 | 428.539 | 576.3923 | 545.6145 | 601.776 | 572.9201 | 542.5087
2981.0354 | 654.2427 | 427.5696 | 577.1514 | 545.2624 | 602.514 | 572.2447 | 541.6616
2982.0354 | 657.2034 | 428.4105 | 577.083 | 545.3575 | 601.9488 | 574.1621 | 541.5948
2983.0354 | 658.6592 | 428.3629 | 576.9454 | 545.8779 | 602.1821 | 575.9584 | 541.2597
2984.0354 | 660.0658 | 428.49 | 577.5701 | 546.1394 | 603.4866 | 576.1024 | 541.1949
2985.0354 | 659.1641 | 428.681 | 578.9679 | 545.9756 | 603.3761 | 576.1025 | 541.6834
2986.0354 | 658.5026 | 428.7255 | 578.3298 | 545.9399 | 602.9517 | 577.2847 | 542.5655
2987.0354 | 657.5647 | 430.3385 | 577.3175 | 546.3241 | 603.0974 | 578.6949 | 542.7339
2988.0354 | 658.3547 | 430.6211 | 577.5506 | 546.194 | 603.7948 | 580.5905 | 543.5534
2989.0354 | 657.5524 | 430.3836 | 577.864 | 546.2752 | 603.0238 | 585.418 | 546.1839
2990.0354 | 657.6578 | 429.8742 | 578.1364 | 546.0966 | 602.6824 | 585.0077 | 545.1119
2991.0354 | 672.8202 | 428.6849 | 578.1341 | 547.4525 | 600.6464 | 583.8762 | 545.4743
2992.0354 | 674.5532 | 428.6739 | 578.1923 | 546.843 | 601.21 | 584.3773 | 544.6446
2993.0354 | 671.5027 | 433.3442 | 573.9825 | 546.8272 | 606.648 | 586.1133 | 542.1793
2994.0354 | 679.6986 | 428.3089 | 576.9943 | 546.4533 | 603.3337 | 587.5258 | 545.8572
2995.0354 | 682.8587 | 430.1578 | 577.442 | 546.7371 | 603.1854 | 590.4843 | 547.9946
2996.0354 | 675.13 | 430.2655 | 577.4445 | 547.0896 | 602.0409 | 590.0481 | 548.9922
2997.0354 | 660.7644 | 429.878 | 577.8973 | 547.1198 | 602.5497 | 590.966 | 549.926
2998.0354 | 659.1674 | 430.42 | 578.0464 | 548.4059 | 602.5225 | 588.7133 | 549.4296
2999.0354 | 656.562 | 430.5012 | 579.467 | 548.8724 | 601.4606 | 586.6182 | 548.5627
3000.0354 | 656.2683 | 430.6941 | 578.3623 | 549.0919 | 600.3398 | 584.6367 | 548.0177
3001.0354 | 654.6103 | 430.2508 | 577.5771 | 548.6941 | 600.2776 | 583.8116 | 546.5909
3002.0354 | 670.2857 | 430.1135 | 577.5871 | 548.7092 | 600.4039 | 582.269 | 546.0554
3003.0354 | 654.7575 | 429.9988 | 577.9534 | 549.2009 | 601.0633 | 581.7058 | 546.0226
3004.0354 | 653.9395 | 431.5535 | 577.9301 | 548.6003 | 602.6754 | 581.7025 | 545.7958
3005.0354 | 653.7406 | 431.17 | 578.2018 | 548.9779 | 604.7894 | 583.9409 | 547.4384
3006.0354 | 651.9116 | 430.977 | 578.5803 | 549.0934 | 604.2778 | 584.4726 | 548.1114
3007.0354 | 650.4201 | 432.6698 | 578.2515 | 548.9142 | 603.6667 | 585.3636 | 548.1093
3008.0354 | 652.1198 | 431.7021 | 577.3959 | 549.1315 | 601.5512 | 584.1749 | 548.0992
3009.0354 | 656.153 | 433.3205 | 577.4242 | 548.7722 | 601.2943 | 583.0019 | 545.9564
3010.0354 | 665.5231 | 432.8366 | 577.4998 | 550.4682 | 601.6151 | 580.9816 | 544.9515
3011.0354 | 659.3627 | 433.0335 | 577.3545 | 552.9523 | 601.8555 | 579.9659 | 544.5976
3012.0354 | 656.5986 | 432.4216 | 577.1116 | 552.3637 | 603.2377 | 576.8887 | 543.4675
3013.0354 | 657.4708 | 434.4645 | 577.0219 | 550.6383 | 604.6087 | 575.0851 | 541.9302
3014.0354 | 660.2484 | 434.6885 | 577.4868 | 550.9216 | 605.1488 | 575.9224 | 541.7883
3015.0354 | 676.4668 | 433.0596 | 577.5964 | 551.3273 | 605.4735 | 578.3507 | 542.7004
3016.0354 | 665.4928 | 434.0311 | 578.672 | 551.3202 | 606.3269 | 580.1783 | 543.6915
3017.0354 | 666.9275 | 435.0044 | 578.5717 | 551.7101 | 604.8182 | 580.2866 | 544.0184
3018.0354 | 677.4658 | 435.8683 | 578.0798 | 552.1875 | 604.1814 | 582.1063 | 544.9032
3019.0354 | 660.8065 | 435.9972 | 579.0877 | 551.9108 | 603.76 | 583.2041 | 546.7459
3020.0354 | 657.9955 | 438.4486 | 578.1559 | 552.4155 | 604.0927 | 583.8258 | 546.2614
3021.0354 | 655.1197 | 439.0326 | 579.5122 | 552.3809 | 603.2296 | 582.3367 | 546.383
3022.0354 | 671.5044 | 439.3038 | 579.6597 | 552.209 | 602.0398 | 580.4168 | 545.8484
3023.0354 | 647.7754 | 438.867 | 580.6661 | 552.4729 | 601.1619 | 580.301 | 546.1001
3024.0354 | 660.6313 | 437.1788 | 578.8645 | 553.1532 | 601.4411 | 580.1573 | 545.5265
3025.0354 | 643.8619 | 435.9632 | 578.4409 | 553.0102 | 603.8528 | 582.0114 | 545.4769
3026.0354 | 645.2337 | 435.7689 | 578.1079 | 552.8246 | 603.5569 | 581.5469 | 544.6594
3027.0354 | 645.403 | 436.8465 | 578.4815 | 553.2874 | 603.8155 | 579.1158 | 544.1936
3028.0354 | 646.5495 | 438.6836 | 578.9184 | 554.2032 | 605.1478 | 578.6334 | 543.5012
3029.0354 | 645.402 | 439.7415 | 578.8419 | 554.2384 | 604.2337 | 577.0106 | 543.662
3030.0354 | 644.2747 | 440.2145 | 579.1954 | 553.4977 | 603.5486 | 576.7018 | 543.2078
3031.0354 | 643.3927 | 439.4815 | 579.1481 | 554.3782 | 604.3365 | 578.6446 | 545.1973
3032.0354 | 645.4571 | 440.4441 | 579.0661 | 555.1115 | 604.271 | 578.0411 | 545.4067
3033.0354 | 645.0496 | 440.8159 | 578.974 | 554.5047 | 602.8222 | 576.4919 | 544.799
3034.0354 | 657.4703 | 442.1097 | 579.1622 | 554.8547 | 601.3935 | 576.3563 | 545.1795
3035.0354 | 644.6594 | 442.7934 | 580.1821 | 554.8561 | 601.2434 | 575.1514 | 544.6388
3036.0354 | 643.4462 | 443.8836 | 578.89 | 554.4418 | 600.3217 | 575.4118 | 544.7301
3037.0354 | 647.0187 | 445.2574 | 579.8659 | 555.3486 | 600.243 | 576.3907 | 545.0196
3038.0354 | 646.2186 | 445.2967 | 579.602 | 555.406 | 600.78 | 577.5531 | 545.7492
3039.0354 | 671.6821 | 443.7642 | 579.4129 | 555.3015 | 601.3453 | 579.4068 | 545.8813
3040.0354 | 672.487 | 445.4455 | 579.2941 | 555.3322 | 601.3061 | 579.9005 | 546.397
3041.0354 | 643.1134 | 446.1405 | 578.9568 | 555.6197 | 600.8495 | 579.7725 | 546.239
3042.0354 | 641.783 | 443.1643 | 579.4779 | 555.6178 | 600.9326 | 580.4025 | 546.0012
3043.0354 | 640.7766 | 442.6796 | 579.3832 | 555.6115 | 600.9168 | 579.7721 | 545.079
3044.0354 | 639.6918 | 447.4985 | 580.4485 | 556.0654 | 600.3355 | 578.8686 | 544.0394
3045.0354 | 637.9093 | 445.3974 | 579.4583 | 555.6222 | 600.283 | 578.6974 | 543.8189
3046.0354 | 640.4806 | 446.5125 | 579.4083 | 556.2011 | 600.0618 | 577.1215 | 543.2451
3047.0354 | 639.4791 | 445.8287 | 579.3147 | 557.0631 | 599.1404 | 575.1319 | 542.8621
3048.0354 | 651.2911 | 447.1514 | 579.3036 | 557.4524 | 599.0912 | 574.7734 | 542.1414
3049.0354 | 650.3963 | 446.7518 | 579.1331 | 557.6453 | 597.6289 | 572.4185 | 541.3991
3050.0354 | 649.3012 | 445.9576 | 579.6159 | 557.7041 | 596.769 | 571.6824 | 541.1697
3051.0354 | 648.3721 | 447.4379 | 579.0897 | 557.1482 | 595.7874 | 571.1361 | 541.022
3052.0354 | 647.4003 | 447.6662 | 579.8137 | 557.3708 | 595.0153 | 572.044 | 540.9948
3053.0354 | 645.4697 | 448.2431 | 579.3355 | 557.3536 | 595.6323 | 573.1658 | 540.9168
3054.0354 | 644.7744 | 447.841 | 578.5483 | 558.662 | 596.2153 | 572.5559 | 540.7301
3055.0354 | 644.2082 | 448.5912 | 578.7441 | 558.322 | 597.4952 | 572.2122 | 540.5806
3056.0354 | 642.5701 | 450.2529 | 579.0248 | 557.9587 | 596.665 | 573.4556 | 541.1947
3057.0354 | 644.1786 | 450.6558 | 578.5503 | 557.8497 | 597.691 | 574.2558 | 542.3134
3058.0354 | 644.3718 | 451.2883 | 579.0246 | 557.7929 | 599.5009 | 575.5609 | 542.8652
3059.0354 | 642.2144 | 451.5838 | 581.4558 | 558.1655 | 599.6285 | 576.7197 | 544.0982
3060.0354 | 640.5232 | 449.5574 | 580.0433 | 558.4089 | 598.531 | 577.844 | 544.9872
3061.0354 | 641.7408 | 449.5606 | 579.6525 | 558.2505 | 597.4292 | 583.1418 | 548.6105
3062.0354 | 642.1361 | 452.3174 | 581.1091 | 558.5318 | 596.7608 | 581.4383 | 547.9816
3063.0354 | 637.9084 | 451.3782 | 581.6462 | 558.5747 | 594.5979 | 579.1955 | 547.305
3064.0354 | 635.0626 | 452.6554 | 580.4425 | 558.9063 | 592.9333 | 577.4243 | 545.9975
3065.0354 | 634.9385 | 451.3792 | 579.9785 | 558.8021 | 592.5803 | 576.9966 | 546.5654
3066.0354 | 647.676 | 451.7066 | 582.6766 | 558.9962 | 592.3362 | 576.8079 | 547.4736
3067.0354 | 667.093 | 452.7488 | 582.6248 | 559.5577 | 593.0727 | 576.6985 | 547.8525
3068.0354 | 665.9403 | 452.3831 | 582.8988 | 559.3459 | 592.7682 | 576.2675 | 547.6744
3069.0354 | 664.5505 | 454.8981 | 583.0603 | 559.4198 | 592.9069 | 574.3679 | 546.6092
3070.0354 | 663.5493 | 453.7842 | 584.4311 | 559.9374 | 592.7676 | 573.9798 | 545.745
3071.0354 | 663.5711 | 454.616 | 583.1999 | 559.5919 | 592.2068 | 572.5155 | 545.177
3072.0354 | 665.961 | 453.7763 | 581.867 | 558.9019 | 593.5168 | 576.4353 | 546.4862
3073.0354 | 658.2925 | 455.6008 | 581.9562 | 560.0577 | 593.9117 | 578.9743 | 548.3562
3074.0354 | 665.1856 | 456.7643 | 583.3925 | 559.6482 | 594.3222 | 578.5514 | 548.173
3075.0354 | 663.0743 | 455.7249 | 583.6458 | 559.4953 | 592.4405 | 576.8316 | 547.3346
3076.0354 | 665.0637 | 455.5297 | 583.3578 | 559.329 | 592.3104 | 576.4312 | 546.3798
3077.0354 | 664.1911 | 456.9426 | 585.9026 | 559.5623 | 592.3982 | 576.9747 | 546.5089
3078.0354 | 665.9827 | 456.4852 | 586.2566 | 560.2814 | 592.1729 | 577.696 | 547.7332
3079.0354 | 667.8883 | 457.1874 | 588.2455 | 559.987 | 591.7373 | 579.5222 | 549.4589
3080.0354 | 666.7174 | 455.7815 | 588.3105 | 559.7421 | 590.7961 | 578.204 | 549.4559
3081.0354 | 665.1549 | 454.7685 | 588.667 | 560.1952 | 589.4959 | 578.1712 | 550.2744
3082.0354 | 664.8954 | 455.8628 | 587.1144 | 560.5327 | 588.6714 | 575.7688 | 549.4581
3083.0354 | 666.8724 | 458.4047 | 586.7862 | 560.0181 | 587.2861 | 575.0568 | 548.8309
3084.0354 | 667.3709 | 457.8823 | 588.651 | 560.6713 | 586.2216 | 574.1128 | 548.6261
3085.0354 | 664.682 | 456.2897 | 588.7639 | 560.5108 | 586.6592 | 573.1587 | 548.2234
3086.0354 | 663.1958 | 458.0376 | 589.0068 | 560.6034 | 585.866 | 572.0458 | 547.4135
3087.0354 | 662.604 | 460.2766 | 587.445 | 560.4165 | 586.9614 | 572.3711 | 547.7797
3088.0354 | 665.2005 | 460.9583 | 586.823 | 560.2419 | 589.0766 | 574.4399 | 548.3367
3089.0354 | 667.9599 | 461.5373 | 587.0144 | 560.065 | 591.7921 | 575.8334 | 548.2232
3090.0354 | 669.0016 | 460.8001 | 586.8857 | 560.0459 | 592.512 | 574.9348 | 547.2295
3091.0354 | 672.0469 | 461.2949 | 586.9384 | 560.101 | 593.1108 | 573.873 | 545.9213
3092.0354 | 677.9516 | 459.8722 | 586.591 | 559.9739 | 594.3264 | 574.6774 | 545.4454
3093.0354 | 678.9701 | 461.835 | 586.9326 | 559.8869 | 594.1072 | 574.2698 | 546.0322
3094.0354 | 677.2579 | 461.209 | 587.397 | 559.8535 | 592.2989 | 572.1191 | 545.4571
3095.0354 | 677.1115 | 460.4519 | 587.2635 | 560.3786 | 591.8291 | 573.6315 | 545.154
3096.0354 | 680.8895 | 460.061 | 586.8323 | 560.1991 | 594.2412 | 577.294 | 545.9765
3097.0354 | 684.5279 | 460.1883 | 586.596 | 559.8786 | 595.5884 | 578.7475 | 547.8532
3098.0354 | 685.6551 | 460.8308 | 586.7965 | 560.371 | 595.1824 | 579.2379 | 549.864
3099.0354 | 684.4413 | 462.6836 | 587.2923 | 560.148 | 594.0975 | 579.2138 | 550.678
3100.0354 | 685.6685 | 463.9187 | 586.8583 | 561.2794 | 594.163 | 578.3182 | 549.8667
3101.0354 | 683.2743 | 464.3444 | 587.0006 | 560.6855 | 593.4851 | 577.4215 | 550.2006
3102.0354 | 684.1014 | 462.6381 | 587.3323 | 560.6881 | 593.3569 | 577.7343 | 549.2403
3103.0354 | 684.539 | 463.1739 | 586.5007 | 560.4119 | 594.6896 | 577.4254 | 549.3431
3104.0354 | 683.5939 | 464.5276 | 586.4687 | 560.4669 | 594.2499 | 575.7693 | 547.8348
3105.0354 | 687.1671 | 465.2536 | 586.6361 | 560.5473 | 593.6098 | 573.82 | 546.1522
3106.0354 | 687.715 | 465.3656 | 587.4703 | 560.756 | 592.4993 | 573.1295 | 545.6404
3107.0354 | 688.7528 | 463.6432 | 586.7957 | 561.2702 | 591.017 | 572.3349 | 545.5494
3108.0354 | 691.8426 | 462.8653 | 586.4426 | 562.0496 | 592.1961 | 571.3039 | 545.2228
3109.0354 | 693.2264 | 462.5102 | 586.7069 | 562.2127 | 592.6184 | 570.8599 | 544.2183
3110.0354 | 697.0897 | 464.824 | 587.1753 | 562.395 | 592.0008 | 570.6229 | 544.1033
3111.0354 | 694.8193 | 465.3236 | 586.5465 | 562.3331 | 592.3114 | 569.8219 | 544.6395
3112.0354 | 694.1529 | 465.7354 | 586.513 | 562.2276 | 592.8038 | 570.0374 | 544.4591
3113.0354 | 695.9729 | 465.7526 | 586.2337 | 561.5727 | 593.3997 | 571.1813 | 545.0233
3114.0354 | 698.2536 | 465.9123 | 586.2367 | 561.9528 | 593.9083 | 570.4022 | 544.3238
3115.0354 | 698.1703 | 466.2742 | 585.7003 | 561.4678 | 597.0185 | 573.1504 | 544.5948
3116.0354 | 700.4345 | 466.2921 | 585.9166 | 561.8523 | 598.2492 | 573.9186 | 545.0784
3117.0354 | 699.1236 | 466.3254 | 585.9915 | 562.2401 | 598.0915 | 573.5907 | 544.9546
3118.0354 | 697.289 | 466.2582 | 586.7463 | 562.6156 | 597.1956 | 573.1545 | 544.9362
3119.0354 | 694.3192 | 467.5933 | 585.9482 | 562.2586 | 595.8327 | 573.1233 | 545.1917
3120.0354 | 689.0005 | 468.2277 | 586.7373 | 562.7351 | 595.1224 | 573.0257 | 545.5085
3121.0354 | 684.9257 | 466.6599 | 587.9938 | 562.5218 | 594.4835 | 572.6874 | 545.9453
3122.0354 | 682.2873 | 466.2776 | 588.8277 | 562.3582 | 593.1812 | 572.5958 | 546.3737
3123.0354 | 678.3936 | 466.2993 | 588.5765 | 562.2619 | 591.1498 | 572.7854 | 547.4484
3124.0354 | 675.839 | 468.5841 | 588.5678 | 562.1887 | 588.6166 | 572.6352 | 549.0172
3125.0354 | 673.3412 | 468.8362 | 588.9458 | 562.0551 | 586.4393 | 573.0336 | 549.7425
3126.0354 | 670.194 | 470.114 | 589.277 | 562.2171 | 585.1964 | 572.1405 | 548.9587
3127.0354 | 667.4698 | 468.6601 | 588.7917 | 561.8647 | 583.7991 | 571.2934 | 548.7338
3128.0354 | 667.3989 | 469.009 | 588.1606 | 561.9101 | 582.5307 | 571.6283 | 548.1364
3129.0354 | 666.1365 | 471.327 | 587.6171 | 561.6869 | 584.0652 | 574.1209 | 548.6646
3130.0354 | 666.8338 | 472.4681 | 588.7904 | 562.9344 | 583.9669 | 573.2229 | 548.5687
3131.0354 | 666.1995 | 471.3673 | 590.4429 | 562.0541 | 583.7383 | 573.3742 | 548.8996
3132.0354 | 667.3531 | 472.5395 | 588.6401 | 561.9682 | 582.9018 | 572.5437 | 548.903
3133.0354 | 658.2822 | 473.023 | 588.0454 | 562.8532 | 583.2057 | 573.5788 | 549.1868
3134.0354 | 671.5779 | 473.5778 | 588.3759 | 562.283 | 584.3255 | 574.2143 | 549.4716
3135.0354 | 670.9921 | 473.0027 | 589.2431 | 562.2349 | 583.7236 | 573.7356 | 549.2966
3136.0354 | 670.6283 | 472.1186 | 589.9448 | 562.0709 | 583.074 | 573.1364 | 549.6301
3137.0354 | 668.9219 | 474.9669 | 589.8135 | 562.6185 | 582.8406 | 573.2427 | 549.9233
3138.0354 | 670.1548 | 472.5199 | 590.5582 | 563.1761 | 582.5568 | 575.8527 | 550.3316
3139.0354 | 667.4742 | 472.2055 | 590.3205 | 562.8475 | 582.9251 | 577.032 | 552.1767
3140.0354 | 668.9762 | 473.7752 | 591.17 | 563.436 | 582.6493 | 576.4626 | 551.5544
3141.0354 | 666.3835 | 473.3668 | 591.4571 | 563.1317 | 582.3727 | 575.7537 | 551.0124
3142.0354 | 666.969 | 475.4516 | 591.4996 | 563.7668 | 582.6328 | 576.5065 | 551.4105
3143.0354 | 667.5539 | 475.5735 | 592.7249 | 563.4734 | 583.4084 | 577.059 | 552.9744
3144.0354 | 663.3982 | 474.1446 | 593.4092 | 562.716 | 583.5652 | 576.6397 | 553.3698
3145.0354 | 665.2442 | 475.3328 | 595.5143 | 562.6172 | 583.2177 | 575.9797 | 553.0297
3146.0354 | 663.4125 | 474.4555 | 595.3529 | 562.3555 | 582.2092 | 575.3469 | 553.5544
3147.0354 | 665.0591 | 474.6325 | 594.4062 | 562.398 | 581.7051 | 574.6275 | 553.614
3148.0354 | 663.6912 | 476.4456 | 593.5719 | 562.2569 | 579.8653 | 573.741 | 553.7698
3149.0354 | 665.2576 | 477.6646 | 592.4342 | 562.6121 | 580.1653 | 575.4571 | 554.1376
3150.0354 | 670.67 | 477.007 | 593.7037 | 563.4092 | 581.1816 | 573.7558 | 553.2455
3151.0354 | 671.1209 | 476.312 | 593.3679 | 563.2158 | 580.6063 | 572.1946 | 551.6341
3152.0354 | 667.2958 | 476.5646 | 594.0078 | 563.4294 | 578.8882 | 570.3363 | 551.7518
3153.0354 | 665.1631 | 476.9572 | 593.8598 | 563.0529 | 577.9912 | 569.3643 | 551.3902
3154.0354 | 666.513 | 478.1393 | 593.2215 | 562.6446 | 576.7398 | 568.8621 | 551.6418
3155.0354 | 665.5204 | 477.9285 | 593.2555 | 562.3659 | 577.9345 | 574.3055 | 553.7548
3156.0354 | 669.5284 | 476.0806 | 594.2031 | 562.5852 | 579.2335 | 576.1165 | 554.3718
3157.0354 | 668.168 | 475.581 | 593.9062 | 563.5951 | 579.9552 | 575.8531 | 554.2581
3158.0354 | 669.7597 | 475.4717 | 595.1969 | 563.445 | 580.6552 | 574.3957 | 553.5572
3159.0354 | 670.7011 | 476.6166 | 596.5508 | 563.5212 | 580.3165 | 573.8982 | 553.4621
3160.0354 | 671.0388 | 476.3298 | 595.5251 | 562.7504 | 580.1985 | 573.8126 | 553.0794
3161.0354 | 671.2279 | 476.5792 | 595.5814 | 563.0808 | 580.4003 | 574.3551 | 553.8302
3162.0354 | 673.3652 | 476.1493 | 595.3172 | 562.8306 | 580.2354 | 574.2362 | 553.627
3163.0354 | 672.4309 | 477.2723 | 595.2569 | 562.9796 | 579.2647 | 574.0283 | 552.9723
3164.0354 | 669.8301 | 478.4199 | 595.9509 | 563.7517 | 579.2095 | 573.0152 | 552.4137
3165.0354 | 670.731 | 480.0016 | 595.82 | 564.0135 | 579.539 | 573.4245 | 551.924
3166.0354 | 672.4739 | 479.94 | 595.1602 | 564.265 | 579.7176 | 572.7936 | 551.5351
3167.0354 | 677.7625 | 479.0065 | 594.8403 | 563.4678 | 579.9979 | 573.0839 | 551.3859
3168.0354 | 682.0059 | 479.5226 | 595.3582 | 563.5665 | 580.397 | 573.1007 | 551.2051
3169.0354 | 684.2804 | 478.5089 | 595.9863 | 562.9951 | 581.6584 | 573.3031 | 551.4183
3170.0354 | 686.4223 | 477.5482 | 595.6802 | 562.9126 | 582.2964 | 575.3492 | 552.6737
3171.0354 | 685.6327 | 477.5151 | 595.5218 | 563.137 | 583.2312 | 578.3896 | 554.4878
3172.0354 | 687.5566 | 477.5851 | 595.4458 | 562.9657 | 584.4647 | 580.7318 | 554.9835
3173.0354 | 687.7328 | 480.6487 | 596.4977 | 563.0242 | 585.2078 | 581.3066 | 555.5504
3174.0354 | 685.1859 | 481.3526 | 596.4543 | 562.6423 | 584.5466 | 581.0922 | 555.6618
3175.0354 | 683.4898 | 480.0537 | 596.4004 | 562.6342 | 583.9288 | 580.8509 | 555.2783
3176.0354 | 686.0897 | 482.304 | 596.5038 | 562.4724 | 583.7121 | 581.6191 | 557.538
3177.0354 | 686.4573 | 480.5483 | 597.206 | 562.7049 | 582.3471 | 582.6159 | 558.957
3178.0354 | 686.6062 | 481.3069 | 597.461 | 562.609 | 581.6472 | 580.8851 | 559.4422
3179.0354 | 703.3777 | 481.5426 | 596.7046 | 562.7712 | 580.7528 | 580.7497 | 560.6095
3180.0354 | 702.9231 | 482.4591 | 596.3272 | 562.3149 | 580.6761 | 580.9731 | 559.5981
3181.0354 | 705.9576 | 481.9947 | 597.2652 | 562.3835 | 579.5207 | 580.0185 | 558.7272
3182.0354 | 712.6225 | 483.1025 | 598.6423 | 562.8829 | 579.1007 | 579.3206 | 558.9466
3183.0354 | 722.5439 | 483.377 | 598.9773 | 563.336 | 579.8452 | 579.5317 | 558.6103
3184.0354 | 723.1735 | 482.9928 | 600.8502 | 562.737 | 578.3257 | 577.654 | 557.2033
3185.0354 | 764.7296 | 484.0705 | 600.4956 | 563.1622 | 577.3785 | 576.0975 | 557.7156
3186.0354 | 765.3588 | 483.9429 | 599.6774 | 562.8706 | 577.7731 | 574.7007 | 557.554
3187.0354 | 744.668 | 483.313 | 599.3434 | 563.8906 | 576.8327 | 573.4614 | 556.4586
3188.0354 | 768.6468 | 484.6205 | 598.4063 | 563.6993 | 576.8477 | 573.0904 | 556.2635
3189.0354 | 793.0955 | 484.5335 | 597.9805 | 564.27 | 578.2258 | 572.824 | 555.5084
3190.0354 | 819.3097 | 484.1635 | 598.0455 | 564.4283 | 579.3127 | 570.3854 | 553.2294
3191.0354 | 843.2397 | 484.8776 | 598.6674 | 564.1006 | 578.053 | 567.6039 | 550.8971
3192.0354 | 840.3063 | 485.334 | 598.9024 | 563.6153 | 577.3029 | 566.2083 | 549.3601
3193.0354 | 870.5042 | 485.2868 | 599.052 | 564.2345 | 577.4252 | 566.499 | 549.3566
3194.0354 | 871.7845 | 485.821 | 599.2083 | 564.1821 | 577.8236 | 566.0405 | 548.8172
3195.0354 | 872.302 | 486.5884 | 599.3865 | 563.7469 | 576.4209 | 566.6789 | 548.7979
3196.0354 | 877.6379 | 486.1332 | 599.4243 | 563.417 | 576.0776 | 570.037 | 550.1002
3197.0354 | 878.4096 | 486.0275 | 599.0456 | 563.3953 | 576.4797 | 574.0022 | 552.5808
3198.0354 | 880.1524 | 485.7648 | 600.3486 | 563.5481 | 576.6041 | 575.2949 | 553.566
3199.0354 | 882.2694 | 486.8638 | 599.9535 | 563.8763 | 576.6042 | 575.0466 | 553.5775
3200.0354 | 882.3124 | 489.3066 | 598.6073 | 563.2229 | 577.168 | 576.5143 | 556.6436
3201.0354 | 886.2271 | 488.7945 | 599.7637 | 563.096 | 577.4174 | 575.008 | 558.0199
3202.0354 | 884.8664 | 488.5658 | 599.7457 | 562.9464 | 576.8153 | 574.3997 | 558.8393
3203.0354 | 885.2072 | 488.9685 | 600.0434 | 562.9172 | 576.6867 | 575.926 | 559.8028
3204.0354 | 883.7535 | 490.6424 | 599.8197 | 563.3646 | 576.1129 | 576.2035 | 560.4204
3205.0354 | 883.6441 | 489.9983 | 599.8882 | 563.363 | 575.719 | 575.2335 | 558.7434
3206.0354 | 883.8952 | 489.0276 | 600.4321 | 563.4173 | 575.9474 | 574.348 | 558.0166
3207.0354 | 881.6382 | 490.5672 | 600.0249 | 563.3558 | 575.8935 | 575.8124 | 557.8986
3208.0354 | 881.019 | 491.0388 | 600.2654 | 563.1363 | 576.5842 | 577.7302 | 559.1833
3209.0354 | 886.1072 | 491.9027 | 599.3707 | 562.7768 | 579.3984 | 583.1777 | 561.8936
3210.0354 | 888.319 | 491.6384 | 599.5346 | 563.0804 | 579.5779 | 583.0773 | 561.454
3211.0354 | 889.5116 | 491.8369 | 599.0472 | 562.8906 | 580.1116 | 584.8442 | 561.674
3212.0354 | 888.4966 | 490.9221 | 599.0778 | 562.373 | 579.6176 | 585.4636 | 564.1223
3213.0354 | 892.392 | 491.1382 | 599.5023 | 562.4731 | 578.5833 | 584.8462 | 563.2238
3214.0354 | 894.919 | 490.3315 | 599.2249 | 562.8972 | 577.3304 | 584.8784 | 563.3388
3215.0354 | 896.0728 | 491.2756 | 601.1317 | 563.06 | 578.711 | 584.7783 | 561.7012
3216.0354 | 892.9514 | 491.213 | 601.1167 | 563.1778 | 577.9382 | 583.1964 | 561.3037
3217.0354 | 891.4895 | 491.1763 | 602.5795 | 563.0214 | 577.556 | 581.8357 | 560.8333
3218.0354 | 888.3369 | 491.2147 | 601.8642 | 563.9164 | 578.0445 | 581.1647 | 559.9405
3219.0354 | 889.8868 | 493.3339 | 602.3344 | 563.3037 | 578.3618 | 581.2949 | 560.1856
3220.0354 | 888.0852 | 493.3973 | 601.6783 | 564.2596 | 578.7308 | 582.1538 | 560.9794
3221.0354 | 887.8817 | 493.1731 | 600.8692 | 563.3723 | 578.4394 | 581.0023 | 559.9542
3222.0354 | 886.968 | 494.7377 | 600.8785 | 563.2355 | 577.4891 | 580.1062 | 559.6404
3223.0354 | 892.039 | 495.8209 | 601.5285 | 563.7768 | 576.9297 | 578.8029 | 558.1308
3224.0354 | 890.8239 | 494.184 | 602.5559 | 564.3068 | 576.9928 | 576.6175 | 557.776
3225.0354 | 890.8167 | 494.3696 | 603.9196 | 563.2682 | 576.6584 | 576.2499 | 557.1343
3226.0354 | 889.4171 | 495.277 | 603.9405 | 564.4342 | 577.1343 | 577.7214 | 558.0476
3227.0354 | 559.2128 | 495.4388 | 603.2223 | 564.3225 | 577.2176 | 577.448 | 558.8725
3228.0354 | 562.6858 | 495.6068 | 602.8945 | 563.9845 | 576.1139 | 576.6524 | 558.0556
3229.0354 | 560.3757 | 495.5327 | 603.6514 | 563.5832 | 576.1513 | 577.1229 | 558.2037
3230.0354 | 552.0379 | 496.5625 | 605.2606 | 563.7812 | 575.944 | 577.5811 | 558.9686
3231.0354 | 551.1532 | 495.5549 | 605.5815 | 564.5588 | 574.8517 | 576.4828 | 559.7358
3232.0354 | 542.7096 | 496.165 | 604.4822 | 565.7751 | 574.4332 | 576 | 559.2389
3233.0354 | 541.3645 | 496.2244 | 604.0058 | 564.9322 | 573.9014 | 575.1204 | 558.2179
3234.0354 | 536.6949 | 497.0822 | 604.383 | 564.4229 | 573.8701 | 573.5765 | 556.8606
3235.0354 | 532.9501 | 498.7425 | 605.0217 | 564.2835 | 573.9937 | 572.811 | 555.6543
3236.0354 | 534.6493 | 498.1431 | 605.3246 | 564.6776 | 574.4959 | 573.8527 | 555.3738
3237.0354 | 536.3117 | 498.6932 | 607.9934 | 564.0633 | 574.9822 | 575.1269 | 556.4021
3238.0354 | 537.9383 | 499.0034 | 607.9178 | 564.2239 | 575.9294 | 575.2378 | 557.7217
3239.0354 | 538.7154 | 499.9936 | 608.3813 | 564.9623 | 574.8821 | 575.7691 | 558.7337
3240.0354 | 537.1603 | 501.0077 | 608.0397 | 564.4266 | 575.0611 | 575.7291 | 560.5369
3241.0354 | 535.6802 | 500.6482 | 609.8276 | 564.1512 | 575.2908 | 575.7716 | 562.5073
3242.0354 | 608.1106 | 500.6021 | 609.0402 | 564.3913 | 574.6005 | 576.5352 | 564.8803
3243.0354 | 561.5501 | 500.0837 | 609.882 | 564.4452 | 573.5917 | 574.8175 | 566.1718
3244.0354 | 560.4109 | 501.2733 | 610.3322 | 564.4849 | 574.2656 | 574.9508 | 566.1353
3245.0354 | 570.2427 | 501.7692 | 610.9953 | 565.2778 | 574.822 | 574.3422 | 565.3873
3246.0354 | 625.3694 | 500.7114 | 609.72 | 564.6478 | 574.3329 | 574.2225 | 563.934
3247.0354 | 770.3582 | 501.7167 | 610.4689 | 564.9526 | 574.2357 | 575.102 | 563.1609
3248.0354 | 839.6466 | 500.9226 | 610.4487 | 565.0128 | 574.1012 | 573.7576 | 561.3282
3249.0354 | 848.1396 | 501.4037 | 609.7797 | 564.4034 | 573.6907 | 572.4278 | 558.8274
3250.0354 | 846.5696 | 500.9427 | 609.4763 | 564.6078 | 575.118 | 572.4449 | 563.3457
3251.0354 | 851.7338 | 502.4506 | 610.9044 | 566.4789 | 575.7409 | 573.4114 | 564.6637
3252.0354 | 853.5143 | 502.6175 | 611.4802 | 566.0249 | 576.6001 | 574.9005 | 564.6202
3253.0354 | 855.9861 | 502.5259 | 612.7567 | 566.2622 | 576.4863 | 575.4294 | 565.4326
3254.0354 | 854.8754 | 502.3812 | 612.2055 | 565.3883 | 575.6464 | 573.5345 | 564.7063
3255.0354 | 853.1881 | 502.3501 | 612.2851 | 564.7485 | 574.8185 | 573.3582 | 563.8958
3256.0354 | 854.4506 | 503.1437 | 612.3718 | 565.1101 | 573.7769 | 573.4961 | 563.6638
3257.0354 | 855.2178 | 502.6316 | 611.7578 | 565.2403 | 573.7505 | 575.1658 | 563.547
3258.0354 | 853.3098 | 501.894 | 611.9426 | 566.762 | 573.6429 | 574.3389 | 563.3085
3259.0354 | 853.2522 | 501.9967 | 612.9596 | 565.6208 | 573.773 | 573.8157 | 562.0233
3260.0354 | 852.858 | 501.7748 | 612.5751 | 565.0311 | 573.2885 | 573.2546 | 561.2895
3261.0354 | 853.102 | 501.9571 | 612.0132 | 566.2152 | 573.3379 | 573.5892 | 560.6429
3262.0354 | 852.5226 | 501.7361 | 612.6332 | 566.3765 | 573.325 | 573.3219 | 559.6507
3263.0354 | 853.9296 | 501.7562 | 613.6738 | 565.8822 | 573.2001 | 573.5892 | 559.3397
3264.0354 | 851.8967 | 503.8094 | 612.7622 | 565.7727 | 572.5803 | 572.8868 | 558.6298
3265.0354 | 853.6724 | 505.6223 | 612.5708 | 565.5665 | 571.9078 | 573.6714 | 559.1132
3266.0354 | 853.2933 | 505.2871 | 612.73 | 567.01 | 572.1973 | 572.9594 | 558.6169
3267.0354 | 857.0511 | 505.6712 | 612.8243 | 568.3847 | 572.7869 | 571.3137 | 557.2383
3268.0354 | 858.0353 | 504.836 | 613.3044 | 566.9373 | 573.217 | 569.3464 | 555.7727
3269.0354 | 854.0655 | 505.5737 | 612.7357 | 566.4398 | 572.0092 | 568.365 | 554.0978
3270.0354 | 854.7686 | 506.5155 | 612.7043 | 565.8529 | 571.5497 | 569.9235 | 554.7706
3271.0354 | 855.6767 | 507.4713 | 612.271 | 566.3697 | 571.3821 | 571.9408 | 555.5453
3272.0354 | 856.2518 | 508.2295 | 612.7163 | 566.5414 | 571.8622 | 573.1608 | 555.7777
3273.0354 | 865.508 | 506.847 | 612.4645 | 567.4097 | 572.063 | 572.3595 | 555.054
3274.0354 | 856.0997 | 507.4102 | 612.335 | 568.1301 | 571.7914 | 570.2323 | 553.8946
3275.0354 | 861.586 | 508.277 | 613.8699 | 567.7878 | 571.4284 | 568.0087 | 552.8039
3276.0354 | 876.8898 | 508.2619 | 613.9028 | 567.8256 | 571.242 | 567.669 | 553.2264
3277.0354 | 878.6495 | 508.0932 | 614.1148 | 567.5856 | 571.7199 | 568.8349 | 553.8121
3278.0354 | 759.1303 | 507.705 | 615.0396 | 567.5937 | 571.2961 | 567.4407 | 553.1329
3279.0354 | 876.7145 | 508.5322 | 615.1425 | 568.1711 | 571.142 | 568.593 | 553.9288
3280.0354 | 881.6396 | 507.8365 | 614.9488 | 568.1722 | 570.3059 | 567.188 | 554.7436
3281.0354 | 812.078 | 509.0474 | 614.3958 | 568.4567 | 570.1353 | 566.6972 | 554.3784
3282.0354 | 886.2386 | 509.1101 | 614.8722 | 567.7491 | 569.6738 | 566.2366 | 553.665
3283.0354 | 887.766 | 508.4611 | 615.4763 | 567.7632 | 569.191 | 566.5768 | 554.4471
3284.0354 | 887.4797 | 508.5616 | 616.4131 | 568.0343 | 568.9622 | 567.049 | 556.3882
3285.0354 | 892.6258 | 509.1626 | 614.8751 | 568.1255 | 568.3537 | 567.6051 | 557.2073
3286.0354 | 890.1848 | 511.0446 | 614.0871 | 567.6713 | 569.4392 | 569.5974 | 556.822
3287.0354 | 894.4307 | 509.8111 | 614.4414 | 567.2725 | 570.7408 | 572.1647 | 558.664
3288.0354 | 898.3502 | 509.0612 | 614.0738 | 567.237 | 572.2657 | 574.0522 | 559.7226
3289.0354 | 896.4228 | 508.768 | 615.0439 | 568.081 | 572.2796 | 573.5194 | 560.609
3290.0354 | 899.4336 | 510.9548 | 614.9033 | 567.6141 | 572.5318 | 573.8484 | 560.5421
3291.0354 | 899.0242 | 510.7135 | 616.2364 | 567.871 | 572.6118 | 573.8727 | 560.4794
3292.0354 | 897.1344 | 509.5641 | 614.9373 | 567.9479 | 572.46 | 573.0665 | 559.7517
3293.0354 | 893.4621 | 510.0092 | 614.5602 | 569.5142 | 572.44 | 571.8678 | 558.273
3294.0354 | 896.9836 | 510.3792 | 614.8508 | 569.1637 | 572.5108 | 569.5378 | 556.2973
3295.0354 | 898.3528 | 511.7826 | 614.4617 | 568.6193 | 572.8028 | 566.9769 | 553.9516
3296.0354 | 903.3835 | 511.1583 | 614.9749 | 568.2432 | 571.8389 | 565.6945 | 553.2071
3297.0354 | 906.8745 | 511.9684 | 614.3404 | 568.0921 | 571.9718 | 565.9349 | 553.2621
3298.0354 | 906.4032 | 512.7358 | 613.9985 | 568.2581 | 571.5098 | 565.9431 | 552.883
3299.0354 | 910.7228 | 512.6493 | 613.9521 | 569.3743 | 571.737 | 566.3386 | 552.3392
3300.0354 | 910.9254 | 513.5333 | 614.1582 | 568.8408 | 573.4461 | 566.655 | 551.5159
3301.0354 | 911.5467 | 514.5812 | 615.0441 | 569.5435 | 573.3236 | 566.3014 | 551.3382
3302.0354 | 914.9889 | 512.8162 | 615.2929 | 570.0886 | 573.4335 | 565.2656 | 551.0796
3303.0354 | 917.3604 | 513.3734 | 616.5605 | 569.5763 | 573.0049 | 564.8933 | 551.4415
3304.0354 | 918.769 | 514.0708 | 615.5845 | 569.4289 | 572.4062 | 563.9967 | 551.6121
3305.0354 | 914.5368 | 513.6209 | 615.3205 | 568.7957 | 571.8382 | 563.2803 | 550.5878
3306.0354 | 913.8394 | 513.2537 | 615.2677 | 569.2493 | 570.9537 | 563.4417 | 550.2724
3307.0354 | 916.7056 | 512.8991 | 614.7462 | 569.9313 | 571.0087 | 564.091 | 551.6242
3308.0354 | 930.7648 | 513.7503 | 613.8445 | 569.1952 | 571.2279 | 565.1934 | 551.6269
3309.0354 | 934.5951 | 515.3348 | 613.6888 | 568.896 | 571.1918 | 564.5802 | 551.2196
3310.0354 | 937.0141 | 515.426 | 613.6237 | 568.5898 | 571.8118 | 563.5292 | 549.7829
3311.0354 | 938.2795 | 514.8707 | 614.0469 | 568.4986 | 571.4795 | 562.9839 | 548.9861
3312.0354 | 940.5429 | 515.4938 | 614.1867 | 569.5086 | 570.4249 | 563.1309 | 549.0986
3313.0354 | 939.6745 | 514.3614 | 613.363 | 569.2737 | 569.8623 | 561.4505 | 548.2025
3314.0354 | 941.0445 | 514.6998 | 612.9427 | 568.6261 | 569.3732 | 561.9903 | 547.6665
3315.0354 | 942.3837 | 515.5376 | 612.8997 | 568.3141 | 568.9154 | 563.5793 | 551.0819
3316.0198 | 948.5048 | 514.6826 | 612.7411 | 568.3732 | 569.1921 | 566.9262 | 555.0712
3317.0354 | 948.4478 | 515.0517 | 612.4505 | 568.4326 | 568.6919 | 567.6893 | 557.0321
3318.0354 | 946.0841 | 514.6267 | 612.3241 | 568.2245 | 568.0295 | 568.1055 | 556.2983
3319.0354 | 947.7935 | 515.6915 | 612.2479 | 568.5828 | 567.5395 | 567.3011 | 555.0176
3320.0354 | 948.1856 | 516.6011 | 612.3655 | 568.8052 | 567.4177 | 565.9668 | 554.1298
3321.0354 | 945.8409 | 515.5711 | 612.6282 | 568.867 | 566.8429 | 565.1877 | 552.7257
3322.0354 | 944.2688 | 515.5534 | 611.8392 | 569.7192 | 566.5297 | 564.0448 | 551.0904
3323.0354 | 944.3011 | 516.0786 | 611.5332 | 569.4436 | 566.7145 | 562.9856 | 552.9792
3324.0354 | 942.1525 | 516.2107 | 610.9551 | 569.4516 | 567.1187 | 561.8714 | 551.7804
3325.0354 | 946.6596 | 517.0998 | 611.064 | 569.838 | 567.0071 | 560.1945 | 550.629
3326.0354 | 819.367 | 517.0892 | 611.1613 | 569.6617 | 566.8698 | 559.7871 | 549.5801
3327.0354 | 949.3192 | 517.8191 | 611.0356 | 569.2949 | 567.4296 | 559.9686 | 549.37
3328.0354 | 831.0538 | 518.2523 | 610.829 | 569.5804 | 567.0968 | 561.187 | 551.4615
3329.0354 | 959.5353 | 518.0472 | 610.7577 | 569.3344 | 567.1976 | 561.7626 | 551.3645
3330.0354 | 963.63 | 518.1687 | 610.4408 | 569.3137 | 567.7713 | 561.1984 | 550.7538
3331.0354 | 963.0529 | 518.7862 | 610.1219 | 569.4913 | 567.7783 | 560.5744 | 549.8415
3332.0354 | 958.9388 | 519.394 | 610.0386 | 569.8216 | 567.4509 | 560.0335 | 549.2318
3333.0354 | 962.5994 | 519.5219 | 609.4132 | 569.1112 | 568.1352 | 560.6199 | 548.6223
3334.0354 | 960.8288 | 519.5712 | 608.9585 | 568.6371 | 567.6269 | 560.0364 | 548.9158
3335.0354 | 964.304 | 519.3028 | 610.2529 | 568.3983 | 566.8195 | 558.7675 | 548.2612
3336.0354 | 967.1099 | 518.0147 | 610.5844 | 568.758 | 566.4831 | 560.1067 | 549.8179
3337.0354 | 969.5486 | 517.8447 | 609.7369 | 568.6139 | 566.3119 | 562.0265 | 553.6867
3338.0354 | 971.3703 | 519.8814 | 609.0106 | 568.4177 | 567.7638 | 563.8002 | 554.914
3339.0354 | 967.8349 | 518.6004 | 609.0233 | 568.2039 | 567.8805 | 563.6844 | 554.5376
3340.0354 | 966.4045 | 519.17 | 610.0641 | 568.1239 | 567.1448 | 562.9301 | 554.0758
3341.0354 | 970.3983 | 520.3541 | 609.2282 | 568.0178 | 566.9538 | 564.3377 | 555.3309
3342.0354 | 968.865 | 519.5223 | 609.8093 | 568.242 | 566.047 | 563.8559 | 555.8248
3343.0354 | 976.332 | 518.6884 | 610.4843 | 568.0721 | 565.5095 | 565.2599 | 558.1607
3344.0354 | 978.3716 | 518.7222 | 610.1506 | 568.7126 | 565.1871 | 566.0803 | 559.295
3345.0354 | 980.4104 | 518.7821 | 609.4941 | 568.787 | 565.4613 | 566.125 | 558.2067
3346.0354 | 980.1873 | 518.8042 | 609.2591 | 568.4875 | 565.6243 | 565.8156 | 557.6073
3347.0354 | 982.5833 | 521.5445 | 608.669 | 568.0444 | 565.8439 | 566.278 | 557.2434
3348.0354 | 986.8834 | 521.4167 | 608.9561 | 567.83 | 565.7603 | 566.2367 | 559.5112
3349.0354 | 990.622 | 521.5738 | 611.0594 | 567.9839 | 566.3969 | 566.8824 | 558.9308
3350.0354 | 989.3078 | 520.9546 | 610.387 | 568.5521 | 567.7266 | 569.4116 | 561.2707
3351.0354 | 991.772 | 520.4037 | 612.1706 | 568.7438 | 566.4253 | 567.7525 | 563.5485
3352.0354 | 993.0948 | 522.0802 | 611.9439 | 568.2404 | 565.8202 | 566.4174 | 563.7385
3353.0354 | 995.5019 | 525.3287 | 613.1501 | 568.5103 | 566.1519 | 565.919 | 564.3486
3354.0354 | 998.7569 | 521.8605 | 612.8748 | 569.1052 | 564.839 | 565.4842 | 565.0142
3355.0354 | 1005.944 | 522.9824 | 613.5847 | 568.6449 | 564.5933 | 565.1213 | 563.8508
3356.0354 | 1007.9049 | 522.55 | 613.5851 | 568.4642 | 563.9124 | 564.6353 | 561.9762
3357.0354 | 1016.7805 | 525.4235 | 615.154 | 569.9904 | 564.9162 | 565.3835 | 560.0106
3358.0354 | 867.9686 | 521.4791 | 612.4525 | 569.2138 | 563.4915 | 565.112 | 561.3369
3359.0354 | 1020.7073 | 521.7008 | 612.6643 | 569.2697 | 564.1345 | 565.5274 | 560.2407
3360.0354 | 1022.4007 | 521.017 | 611.7912 | 568.2075 | 564.2484 | 565.0096 | 558.9807
3361.0354 | 920.5918 | 521.2906 | 613.288 | 568.4149 | 564.5389 | 564.964 | 558.1827
3362.0354 | 1024.9726 | 521.2505 | 613.065 | 568.6965 | 564.7988 | 566.0312 | 557.6149
3363.0354 | 1027.5259 | 521.3358 | 613.2711 | 569.3609 | 564.5892 | 566.0727 | 557.2748
3364.0354 | 1029.5495 | 521.6496 | 613.8522 | 569.2105 | 564.512 | 565.7659 | 557.5873
3365.0354 | 1032.1822 | 522.0116 | 614.8474 | 568.9556 | 563.4612 | 564.1675 | 556.8754
3366.0354 | 1032.3162 | 523.1172 | 613.7454 | 568.7163 | 562.5555 | 562.9746 | 556.6415
3367.0354 | 1031.1175 | 524.2428 | 613.3344 | 567.9947 | 561.9505 | 563.5858 | 556.8137
3368.0354 | 1030.915 | 523.5491 | 612.4538 | 567.979 | 562.144 | 565.1811 | 557.0139
3369.0354 | 1029.4949 | 523.8888 | 612.0616 | 568.5297 | 562.2084 | 564.3947 | 555.9174
3370.0354 | 1030.0929 | 523.0766 | 612.0668 | 568.551 | 561.5282 | 563.2324 | 554.3617
3371.0354 | 1032.1133 | 522.3368 | 611.8527 | 568.0402 | 561.2082 | 562.3783 | 553.4045
3372.0354 | 902.6847 | 523.5659 | 611.3829 | 567.6986 | 562.0451 | 562.7336 | 553.0017
3373.0354 | 867.0205 | 523.1244 | 610.8443 | 567.1691 | 563.3894 | 565.4058 | 554.4867
3374.0354 | 1029.5088 | 524.8683 | 610.5679 | 567.2754 | 564.6271 | 565.2253 | 553.6054
3375.0354 | 1036.1878 | 524.2081 | 610.1809 | 567.2225 | 565.8863 | 565.4791 | 555.4099
3376.0354 | 1036.6467 | 523.2691 | 610.4654 | 567.0921 | 565.2227 | 563.5235 | 555.7977
3377.0354 | 1033.9987 | 523.166 | 610.8898 | 567.2514 | 563.9645 | 562.545 | 554.6967
3378.0354 | 1033.8431 | 524.5421 | 610.099 | 568.0458 | 563.0464 | 561.9082 | 554.1783
3379.0354 | 1033.6863 | 524.5155 | 610.9107 | 567.6219 | 562.2211 | 560.8585 | 553.132
3380.0354 | 972.7456 | 523.5614 | 610.7306 | 567.3558 | 561.2595 | 559.8357 | 551.3139
3381.0354 | 1035.879 | 523.4585 | 610.5601 | 567.9445 | 561.3637 | 559.5553 | 553.2774
3382.0354 | 1031.965 | 523.4546 | 609.804 | 567.3303 | 561.5386 | 559.2414 | 552.3587
3383.0354 | 1033.2035 | 525.6246 | 609.126 | 567.0548 | 561.562 | 557.7734 | 550.9572
3384.0354 | 1033.9015 | 525.3554 | 608.8277 | 567.2424 | 561.9946 | 556.7286 | 551.7052
3385.0354 | 1033.5137 | 524.7754 | 608.853 | 566.8736 | 561.2136 | 554.8926 | 552.6694
3386.0354 | 1036.0814 | 524.4927 | 610.265 | 566.7281 | 559.4414 | 552.9893 | 552.2562
3387.0354 | 1030.2808 | 523.7161 | 609.6085 | 567.1617 | 557.9323 | 552.8669 | 551.1157
3388.0354 | 1029.8687 | 523.6898 | 609.4773 | 566.681 | 557.4434 | 553.467 | 551.0634
3389.0354 | 1022.6822 | 524.5418 | 609.1097 | 566.645 | 557.3916 | 554.8628 | 551.9734
3390.0354 | 1020.242 | 525.4206 | 609.3127 | 567.3174 | 557.4731 | 555.6975 | 551.7223
3391.0354 | 1022.8664 | 524.8858 | 608.7614 | 567.8627 | 557.5746 | 555.8111 | 550.9232
3392.0354 | 1020.3093 | 525.6888 | 607.9764 | 566.6749 | 557.7744 | 556.308 | 549.9593
3393.0354 | 1010.2714 | 525.0521 | 609.2286 | 567.4403 | 557.8894 | 556.4511 | 549.7752
3394.0354 | 1017.4759 | 524.9346 | 608.574 | 566.8167 | 557.2236 | 556.3223 | 549.7257
3395.0354 | 1016.2849 | 524.6636 | 611.3222 | 566.7301 | 556.9295 | 556.2101 | 549.0612
3396.0354 | 1025.4538 | 524.9593 | 610.1088 | 566.8152 | 556.7014 | 555.7151 | 549.1579
3397.0354 | 1028.3373 | 524.8068 | 609.8208 | 566.3807 | 556.4473 | 556.3704 | 548.7973
3398.0354 | 1032.7684 | 524.8056 | 609.7576 | 566.5422 | 557.0742 | 557.613 | 549.9422
3399.0354 | 1034.9257 | 524.3813 | 609.7253 | 567.2874 | 558.2377 | 558.329 | 549.4666
3400.0354 | 1038.6092 | 524.9263 | 610.6845 | 567.5046 | 559.2098 | 559.2948 | 552.968
3401.0354 | 1040.8556 | 526.0383 | 609.4736 | 567.3867 | 560.1691 | 560.0778 | 558.1766
3402.0354 | 1036.6693 | 525.3961 | 609.9035 | 567.9503 | 560.2079 | 558.7066 | 556.7417
3403.0354 | 1037.6199 | 524.9212 | 609.0341 | 569.1938 | 560.428 | 558.0224 | 555.8093
3404.0354 | 1038.3436 | 525.4543 | 609.676 | 569.1998 | 559.4798 | 556.754 | 554.6978
3405.0354 | 1038.223 | 526.652 | 608.8636 | 567.5609 | 557.5697 | 554.648 | 552.8739
3406.0354 | 1039.6518 | 527.0951 | 609.7156 | 567.8055 | 556.7406 | 554.2183 | 551.2352
3407.0354 | 1043.7232 | 526.2407 | 609.3384 | 568.1231 | 557.3673 | 555.5513 | 551.3452
3408.0354 | 1055.4734 | 525.7047 | 608.9527 | 568.2241 | 557.8896 | 554.8514 | 551.0208
3409.0354 | 1056.8245 | 525.9401 | 609.3106 | 569.0091 | 557.9881 | 554.2227 | 549.8214
3410.0354 | 1062.1922 | 526.8098 | 609.1703 | 568.7157 | 557.4663 | 553.0318 | 549.0957
3411.0354 | 1055.2024 | 525.9735 | 608.9955 | 567.9378 | 556.8378 | 552.2964 | 548.7872
3412.0354 | 1059.5416 | 525.5494 | 611.0646 | 567.7315 | 556.0341 | 552.7441 | 548.7906
3413.0354 | 1061.7327 | 525.7103 | 609.2671 | 568.33 | 555.7531 | 553.8094 | 549.5065
3414.0354 | 1065.7097 | 525.4065 | 609.2597 | 567.9497 | 555.9602 | 554.1187 | 550.0719
3415.0354 | 1065.8245 | 525.0981 | 610.3574 | 568.7223 | 556.2442 | 554.7838 | 550.3554
3416.0354 | 986.5072 | 525.1624 | 612.0429 | 569.0918 | 556.1534 | 555.0943 | 550.0758
3417.0354 | 1005.1189 | 525.2608 | 611.896 | 568.7854 | 557.7861 | 557.226 | 551.94
3418.0354 | 651.561 | 525.7541 | 611.6233 | 568.8023 | 557.8492 | 558.1697 | 554.7981
3419.0354 | 644.4473 | 527.226 | 610.7005 | 569.0553 | 556.1457 | 556.3468 | 553.9143
3420.0354 | 644.6189 | 526.7467 | 611.4045 | 568.5781 | 556.1575 | 555.7282 | 552.863
3421.0354 | 642.8469 | 526.66 | 611.6705 | 568.7426 | 555.4712 | 556.2671 | 552.5996
3422.0354 | 643.145 | 526.3404 | 611.2126 | 568.4315 | 556.1488 | 557.1624 | 552.3391
3423.0354 | 643.3116 | 526.7672 | 610.8193 | 568.2578 | 556.7214 | 560.4047 | 554.2116
3424.0354 | 644.0502 | 526.9211 | 611.342 | 568.3515 | 557.6961 | 561.0033 | 553.7842
3425.0354 | 644.7642 | 526.2339 | 610.3621 | 568.1132 | 558.9323 | 562.18 | 554.1043
3426.0354 | 644.1693 | 526.8557 | 609.6168 | 567.6661 | 559.9946 | 563.8629 | 553.6308
3427.0354 | 646.4383 | 527.5235 | 610.3864 | 567.9761 | 559.4479 | 563.4559 | 553.7804
3428.0354 | 643.5346 | 526.5344 | 609.669 | 567.6197 | 559.519 | 564.5362 | 553.9764
3429.0354 | 628.3253 | 527.1493 | 609.9026 | 567.6619 | 559.9468 | 563.6606 | 553.7284
3430.0354 | 605.1332 | 527.008 | 609.6395 | 567.2464 | 559.4701 | 562.5799 | 552.4787
3431.0354 | 636.8467 | 526.8742 | 609.1086 | 567.3284 | 558.9481 | 561.4899 | 551.2903
3432.0354 | 636.1612 | 526.9761 | 608.6295 | 567.2557 | 558.0108 | 560.7544 | 550.247
3433.0354 | 625.6448 | 527.1222 | 608.4135 | 566.7292 | 557.83 | 559.6601 | 549.3146
3434.0354 | 638.6032 | 527.8496 | 608.175 | 566.7231 | 557.6085 | 558.8042 | 548.3656
3435.0354 | 638.6342 | 528.342 | 608.1955 | 567.0323 | 558.1217 | 558.5263 | 548.0104
3436.0354 | 639.2276 | 529.3523 | 607.6534 | 566.8173 | 558.7414 | 558.0962 | 546.8821
3437.0354 | 638.602 | 528.8188 | 608.0974 | 566.7441 | 558.1184 | 557.0328 | 546.2307
3438.0354 | 638.1995 | 528.2869 | 608.6984 | 566.7056 | 557.4836 | 555.9488 | 545.3861
3439.0354 | 638.8614 | 527.3791 | 608.2228 | 566.6829 | 556.6958 | 554.4443 | 543.9515
3440.0354 | 639.3335 | 527.2453 | 608.7606 | 566.3864 | 556.4762 | 554.6648 | 543.522
3441.0354 | 637.7676 | 526.9787 | 609.9715 | 566.4868 | 556.1446 | 555.0038 | 543.9351
3442.0354 | 636.3293 | 527.1282 | 610.784 | 566.4958 | 556.0765 | 555.0811 | 544.1583
3443.0354 | 635.7373 | 527.3982 | 611.1481 | 566.2868 | 556.0208 | 555.813 | 545.6298
3444.0354 | 635.8551 | 527.2854 | 611.611 | 566.0766 | 555.4342 | 556.0417 | 547.0666
3445.0354 | 635.4847 | 527.4517 | 611.4889 | 566.1171 | 554.6153 | 555.4204 | 548.1852
3446.0354 | 635.5332 | 527.542 | 610.1269 | 566.0881 | 554.4975 | 556.2491 | 549.0263
3447.0354 | 636.2822 | 527.6661 | 610.6778 | 566.006 | 554.1418 | 557.4226 | 549.8219
3448.0354 | 638.3168 | 527.3073 | 610.8246 | 566.0732 | 555.2275 | 558.0509 | 550.0848
3449.0354 | 638.3413 | 527.3419 | 611.9063 | 565.8025 | 555.8776 | 558.2699 | 550.6078
3450.0354 | 638.4347 | 527.2467 | 611.4393 | 566.5653 | 556.3642 | 557.9975 | 551.5173
3451.0354 | 641.5016 | 527.6358 | 612.3239 | 566.7941 | 556.5844 | 558.5712 | 552.6622
3452.0354 | 640.7517 | 528.2445 | 612.6135 | 566.153 | 556.6852 | 558.8136 | 553.943
3453.0354 | 640.7284 | 528.5377 | 612.2156 | 566.3638 | 556.7447 | 558.6441 | 554.2805
3454.0354 | 640.9346 | 528.3589 | 611.0084 | 566.0042 | 556.3075 | 557.7943 | 553.4145
3455.0354 | 641.3251 | 527.829 | 611.1012 | 566.8527 | 556.2738 | 557.5527 | 552.812
3456.0354 | 641.6964 | 527.6771 | 612.1682 | 566.3467 | 556.187 | 557.6673 | 552.7728
3457.0354 | 640.1497 | 527.8633 | 612.6091 | 566.1882 | 555.3545 | 556.1014 | 554.0229
3458.0354 | 637.2366 | 527.8983 | 613.9444 | 565.752 | 554.4598 | 554.7563 | 554.693
3459.0354 | 635.7722 | 528.7456 | 614.8016 | 565.7187 | 553.446 | 554.3685 | 553.9782
3460.0354 | 638.316 | 529.1972 | 614.9632 | 565.6966 | 552.6867 | 554.2967 | 554.0416
3461.0354 | 637.6806 | 529.2592 | 615.5035 | 565.494 | 553.1839 | 555.6237 | 554.9282
3462.0354 | 635.8795 | 529.0862 | 615.9768 | 565.1263 | 552.6984 | 556.6564 | 554.9656
3463.0354 | 636.0908 | 528.5787 | 614.3209 | 564.9883 | 552.4767 | 556.5861 | 554.981
3464.0354 | 638.2091 | 528.9988 | 616.0422 | 564.9455 | 552.4068 | 558.0253 | 555.9518
3465.0354 | 640.2343 | 529.4881 | 617.6515 | 565.2013 | 552.8389 | 560.247 | 558.6368
3466.0354 | 640.3669 | 529.1282 | 618.7072 | 564.7193 | 553.5066 | 561.7143 | 561.6364
3467.0354 | 641.2724 | 528.8487 | 619.1194 | 564.821 | 552.7078 | 562.4335 | 562.3425
3468.0354 | 643.5571 | 528.7302 | 618.3211 | 564.5835 | 552.177 | 562.5763 | 564.0266
3469.0354 | 639.9275 | 528.5987 | 619.3199 | 564.5411 | 551.7799 | 561.8803 | 563.1001
3470.0354 | 638.9571 | 529.2337 | 618.296 | 564.9569 | 551.736 | 562.3959 | 565.4972
3471.0354 | 636.6575 | 528.942 | 618.5644 | 564.8771 | 550.3664 | 560.7904 | 565.5676
3472.0354 | 636.739 | 528.9946 | 619.9554 | 564.3954 | 550.194 | 559.6793 | 563.2629
3473.0354 | 636.7965 | 529.0014 | 619.9154 | 564.345 | 551.4708 | 559.1919 | 562.0749
3474.0354 | 637.7774 | 528.5805 | 620.0806 | 564.7347 | 551.971 | 559.235 | 560.0551
3475.0354 | 638.9789 | 528.6553 | 619.7582 | 565.3114 | 552.9746 | 560.2453 | 559.2689
3476.0354 | 638.5715 | 528.5235 | 620.8196 | 564.7297 | 553.4336 | 560.4733 | 558.6837
3477.0354 | 638.6547 | 528.3657 | 622.33 | 564.4715 | 553.433 | 559.4719 | 558.3327
3478.0354 | 635.6082 | 528.499 | 621.9056 | 564.1875 | 552.8928 | 558.9564 | 557.4207
3479.0354 | 635.8629 | 528.716 | 620.979 | 564.4732 | 552.7689 | 558.4121 | 557.0112
3480.0354 | 635.3707 | 529.0464 | 620.2477 | 564.9797 | 553.4593 | 557.5468 | 555.5894
3481.0354 | 635.2596 | 529.021 | 621.8956 | 564.6428 | 553.8082 | 556.5404 | 554.0517
3482.0354 | 636.1096 | 528.9479 | 622.5826 | 564.0201 | 554.2005 | 557.5608 | 554.2374
3483.0354 | 637.3396 | 528.9413 | 621.3398 | 564.504 | 555.1338 | 558.2694 | 554.1803
3484.0354 | 638.0689 | 528.7866 | 620.9633 | 564.5774 | 556.164 | 559.4037 | 553.8469
3485.0354 | 638.224 | 528.6784 | 620.341 | 563.9372 | 556.2125 | 558.3197 | 552.2963
3486.0354 | 603.4234 | 528.7512 | 620.4911 | 564.0591 | 555.3864 | 556.8928 | 551.7962
3487.0354 | 612.471 | 528.2233 | 620.6333 | 564.315 | 554.8499 | 556.8076 | 550.9884
3488.0354 | 595.8876 | 528.2053 | 620.1972 | 564.1926 | 554.669 | 555.9415 | 550.1092
3489.0354 | 605.5926 | 528.509 | 620.2678 | 563.6223 | 554.7236 | 556.2353 | 549.2743
3490.0354 | 651.7989 | 529.6325 | 619.5075 | 563.1782 | 554.526 | 557.4669 | 555.0932
3491.0354 | 603.0145 | 529.5737 | 619.8905 | 563.0863 | 553.5362 | 558.4695 | 555.4423
3492.0354 | 623.0523 | 529.779 | 620.0092 | 563.1371 | 552.9209 | 558.594 | 554.132
3493.0354 | 634.1326 | 528.4077 | 619.5461 | 563.0953 | 551.8603 | 557.9433 | 556.543
3494.0354 | 633.4611 | 528.8277 | 619.2461 | 562.9187 | 551.4521 | 557.8594 | 555.0168
3495.0354 | 633.8973 | 528.1151 | 618.9414 | 563.1152 | 551.8144 | 557.2817 | 554.4866
3496.0354 | 632.2659 | 527.7027 | 621.3964 | 562.9446 | 551.7952 | 556.3188 | 552.8449
3497.0354 | 630.8115 | 528.3085 | 621.2845 | 562.7405 | 552.4096 | 555.5541 | 551.5623
3498.0354 | 629.3316 | 528.6524 | 619.6978 | 563.2402 | 552.6454 | 555.5774 | 550.225
3499.0354 | 628.7878 | 528.1457 | 620.4251 | 563.6405 | 552.8571 | 554.4348 | 550.3591
3500.0354 | 625.9642 | 527.8551 | 619.7913 | 564.1173 | 552.872 | 554.0135 | 549.6966
3501.0354 | 624.6084 | 528.9167 | 619.417 | 563.6532 | 553.0186 | 553.3294 | 548.4613
3502.0354 | 623.3098 | 528.5226 | 621.1106 | 562.9975 | 552.8351 | 552.3597 | 547.2191
3503.0354 | 623.9981 | 529.4683 | 620.0196 | 563.1763 | 552.6286 | 551.7896 | 546.4881
3504.0354 | 623.541 | 528.4078 | 620.6561 | 563.8152 | 553.4834 | 551.7989 | 546.4023
3505.0354 | 622.2027 | 527.9955 | 620.6501 | 564.3715 | 553.1707 | 551.3552 | 548.094
3506.0354 | 620.7425 | 528.2348 | 619.4386 | 563.9898 | 553.0836 | 550.649 | 548.2939
3507.0354 | 615.0083 | 529.4664 | 619.9842 | 564.1955 | 553.0186 | 549.4798 | 548.5007
3508.0354 | 615.7429 | 529.1822 | 620.3483 | 563.8795 | 551.6659 | 547.7856 | 548.1327
3509.0354 | 613.9934 | 529.3271 | 619.3335 | 563.7798 | 550.7474 | 545.626 | 546.6839
3510.0354 | 613.4871 | 528.7072 | 620.1189 | 563.3827 | 549.7921 | 544.8466 | 545.1755
3511.0354 | 613.0674 | 528.554 | 621.5549 | 563.1266 | 549.5543 | 545.2642 | 544.6756
3512.0354 | 611.7818 | 529.6961 | 619.9261 | 564.6416 | 549.9747 | 545.1216 | 544.1412
3513.0354 | 611.4649 | 528.8824 | 620.779 | 564.0033 | 551.1266 | 545.9138 | 543.2515
3514.0354 | 612.783 | 528.202 | 620.4285 | 564.2119 | 551.693 | 546.1782 | 543.2735
3515.0354 | 612.9552 | 528.1281 | 619.3654 | 563.6522 | 551.4121 | 545.0788 | 542.373
3516.0354 | 612.8281 | 528.1156 | 620.2063 | 564.1708 | 551.6601 | 544.3341 | 543.3426
3517.0354 | 612.5973 | 528.5111 | 619.9806 | 564.6533 | 551.7337 | 544.454 | 542.854
3518.0354 | 612.8154 | 528.4936 | 620.4039 | 563.6525 | 552.9204 | 545.3909 | 542.8763
3519.0354 | 612.9542 | 529.0461 | 620.6208 | 563.5735 | 552.8245 | 546.8209 | 543.5343
3520.0354 | 612.8688 | 528.8651 | 619.1181 | 564.2957 | 553.0773 | 548.3165 | 543.9394
3521.0354 | 612.5285 | 528.5947 | 619.2334 | 564.5435 | 553.8477 | 548.6237 | 543.6432
3522.0354 | 612.0135 | 528.4047 | 620.7154 | 563.9508 | 553.8371 | 548.3609 | 543.3497
3523.0354 | 612.1517 | 528.9031 | 619.1448 | 563.9861 | 554.1996 | 548.8047 | 542.8822
3524.0354 | 611.8052 | 528.3886 | 618.7162 | 564.0659 | 554.2018 | 548.2833 | 541.9531
3525.0354 | 611.9207 | 528.1319 | 618.9291 | 563.6547 | 553.9787 | 548.3179 | 541.4368
3526.0354 | 612.4475 | 527.884 | 620.0159 | 564.7151 | 554.0421 | 548.4203 | 541.2843
3527.0354 | 612.0455 | 527.7816 | 619.9108 | 564.6558 | 553.8642 | 548.6017 | 542.0114
3528.0354 | 611.0096 | 527.6122 | 618.3383 | 564.3877 | 553.5828 | 548.0738 | 541.3062
3529.0354 | 609.8572 | 527.4711 | 618.0623 | 564.5012 | 554.2638 | 547.4347 | 541.6802
3530.0354 | 608.909 | 527.6059 | 618.2987 | 564.4799 | 554.154 | 545.9296 | 541.6939
3531.0354 | 608.3579 | 529.0126 | 618.9383 | 565.3114 | 553.3766 | 544.9199 | 541.5314
3532.0354 | 608.5112 | 528.0523 | 618.2302 | 564.5088 | 553.2473 | 543.7712 | 541.4039
3533.0354 | 607.9963 | 527.5979 | 617.9216 | 564.2864 | 552.7822 | 544.0106 | 542.27
3534.0354 | 608.2198 | 527.1661 | 617.1747 | 563.7981 | 552.432 | 544.7786 | 543.0144
3535.0354 | 607.4408 | 527.5293 | 616.8336 | 563.688 | 552.6736 | 545.7384 | 542.1267
3536.0354 | 606.1059 | 527.1685 | 618.0671 | 563.9565 | 552.2266 | 545.0791 | 540.2922
3537.0354 | 605.2641 | 527.1453 | 618.0327 | 563.5748 | 551.5112 | 544.4266 | 539.1296
3538.0354 | 605.2664 | 527.0601 | 618.1707 | 563.5664 | 551.1604 | 544.5319 | 538.7523
3539.0354 | 604.97 | 526.8576 | 618.5253 | 563.4711 | 550.5143 | 544.8332 | 539.1898
3540.0354 | 604.3631 | 526.8907 | 616.7564 | 563.4533 | 550.1602 | 544.9811 | 538.889
3541.0354 | 602.8285 | 526.9397 | 615.9881 | 562.9414 | 549.5855 | 544.1424 | 538.0299
3542.0354 | 602.419 | 527.2973 | 615.935 | 562.8408 | 549.1152 | 543.962 | 538.2455
3543.0354 | 601.1623 | 527.1564 | 615.6308 | 562.7494 | 548.4008 | 543.8525 | 538.2723
3544.0354 | 600.7644 | 526.9419 | 615.1235 | 562.5211 | 547.2053 | 543.857 | 538.315
3545.0354 | 601.1055 | 526.843 | 614.7476 | 562.1116 | 546.6538 | 544.5784 | 538.8449
3546.0354 | 601.8343 | 527.4854 | 614.6538 | 562.0578 | 545.6301 | 546.4902 | 540.1581
3547.0354 | 582.3961 | 526.8937 | 614.7391 | 562.3932 | 544.853 | 545.8482 | 541.2014
3548.0354 | 581.5128 | 526.7401 | 616.1969 | 562.4064 | 544.3562 | 544.8222 | 540.955
3549.0354 | 581.7734 | 526.3328 | 616.2342 | 562.2159 | 543.723 | 544.8198 | 540.8864
3550.0354 | 580.7805 | 525.8943 | 615.0877 | 562.1692 | 543.2095 | 544.6126 | 539.9142
3551.0354 | 581.2133 | 525.7877 | 614.1745 | 561.7587 | 543.9921 | 544.79 | 539.613
3552.0354 | 582.9913 | 526.1765 | 613.572 | 561.4807 | 544.9454 | 545.585 | 539.1153
3553.0354 | 582.1601 | 525.8945 | 613.0285 | 561.5177 | 544.9635 | 545.3711 | 538.6412
3554.0354 | 580.8687 | 525.5508 | 613.8399 | 561.8769 | 543.9605 | 543.3387 | 537.0888
3555.0354 | 580.5351 | 525.3204 | 613.1443 | 561.8328 | 543.4166 | 542.3219 | 536.4226
3556.0354 | 579.6238 | 525.4069 | 612.8792 | 562.9313 | 543.1457 | 541.1951 | 534.8881
3557.0354 | 579.8465 | 525.3081 | 612.7278 | 562.543 | 543.351 | 540.0235 | 533.4913
3558.0354 | 578.6645 | 524.97 | 612.1852 | 562.7102 | 543.6973 | 538.5827 | 531.8952
3559.0354 | 595.1117 | 525.5646 | 612.6056 | 562.815 | 544.1495 | 537.1038 | 530.1485
3560.0354 | 598.8699 | 525.1161 | 612.5775 | 561.7156 | 543.673 | 536.3323 | 528.9443
3561.0354 | 598.8787 | 524.9715 | 611.7187 | 561.3525 | 544.9043 | 537.527 | 534.754
3562.0354 | 599.4548 | 524.6926 | 611.9603 | 562.1999 | 545.1967 | 537.3578 | 534.6827
3563.0354 | 599.8011 | 524.2754 | 611.7679 | 562.3505 | 545.4543 | 537.6056 | 533.6509
3564.0354 | 596.2213 | 524.0938 | 612.9481 | 561.9244 | 546.328 | 537.557 | 532.6589
3565.0354 | 589.6059 | 523.9746 | 612.5077 | 562.0993 | 546.3561 | 538.0161 | 532.2613
3566.0354 | 600.7868 | 523.9003 | 611.8194 | 561.5134 | 547.604 | 539.173 | 532.3496
3567.0354 | 600.9103 | 523.7294 | 610.848 | 561.4283 | 548.255 | 538.5571 | 531.9043
3568.0354 | 601.3587 | 523.49 | 611.2489 | 561.1389 | 548.1199 | 537.6446 | 531.2874
3569.0354 | 601.5308 | 523.3432 | 612.6565 | 561.5649 | 547.447 | 537.5324 | 531.2036
3570.0354 | 602.5879 | 523.2179 | 611.8816 | 562.08 | 546.996 | 537.8889 | 531.1511
3571.0354 | 601.3775 | 522.984 | 611.0338 | 562.8698 | 547.8557 | 538.1724 | 530.9565
3572.0354 | 600.5403 | 522.9701 | 611.9777 | 561.7686 | 547.5946 | 537.5082 | 529.7971
3573.0354 | 602.0123 | 523.3734 | 611.496 | 561.7023 | 547.1184 | 537.8577 | 529.1278
3574.0354 | 602.2411 | 523.3372 | 611.0657 | 561.4477 | 547.8025 | 539.9759 | 529.7704
3575.0354 | 603.0104 | 522.6264 | 610.9232 | 561.4508 | 548.4941 | 540.4903 | 529.1389
3576.0354 | 604.8192 | 522.4671 | 613.416 | 561.4317 | 550.657 | 543.7022 | 530.7147
3577.0354 | 603.985 | 522.4545 | 613.3522 | 561.5729 | 550.2143 | 544.8753 | 532.6024
3578.0354 | 604.3332 | 522.3415 | 612.4046 | 561.7802 | 550.1102 | 546.3893 | 533.898
3579.0354 | 604.4872 | 522.0606 | 611.3412 | 561.6315 | 549.1537 | 545.2981 | 533.3901
3580.0354 | 606.1391 | 521.8676 | 613.6532 | 561.0938 | 549.0015 | 545.7147 | 533.1634
3581.0354 | 607.0911 | 521.7373 | 612.6469 | 562.1458 | 549.2536 | 546.11 | 533.7271
3582.0354 | 607.4277 | 521.6057 | 611.7249 | 563.3108 | 549.708 | 544.9402 | 534.3422
3583.0354 | 607.7695 | 521.5381 | 611.5689 | 563.0038 | 550.9216 | 544.6866 | 533.9163
3584.0354 | 606.8496 | 521.5664 | 611.5198 | 563.3507 | 551.615 | 543.4393 | 533.105
3585.0354 | 606.8596 | 521.8265 | 611.7545 | 563.0977 | 551.4174 | 542.4843 | 531.9813
3586.0354 | 606.4925 | 521.315 | 612.8728 | 562.5127 | 551.5943 | 542.2325 | 531.9572
3587.0354 | 605.614 | 521.1748 | 614.2241 | 562.0814 | 550.6344 | 541.2485 | 531.3521
3588.0354 | 605.3949 | 521.0004 | 613.0977 | 562.3765 | 549.3097 | 540.4387 | 530.0324
3589.0354 | 605.3621 | 521.2918 | 611.6729 | 563.338 | 549.0947 | 540.4136 | 529.3819
3590.0354 | 603.9034 | 520.9373 | 612.8237 | 563.1086 | 549.4918 | 540.6122 | 528.8442
3591.0354 | 604.6947 | 520.5053 | 612.8102 | 563.0105 | 549.2683 | 540.4854 | 528.1378
3592.0354 | 606.8504 | 520.773 | 611.6652 | 562.4816 | 549.3738 | 541.0562 | 527.3461
3593.0354 | 607.477 | 520.6076 | 613.3189 | 562.3105 | 549.342 | 542.3945 | 527.863
3594.0354 | 608.4242 | 520.5519 | 611.7298 | 563.1066 | 549.0644 | 542.8955 | 528.5302
3595.0354 | 610.5666 | 520.3669 | 612.1606 | 563.7752 | 549.3557 | 543.1554 | 528.5741
3596.0354 | 610.0962 | 519.9989 | 611.8859 | 563.9884 | 549.1269 | 541.9915 | 527.7218
3597.0354 | 608.6629 | 519.633 | 611.5648 | 563.7734 | 548.7186 | 540.7468 | 526.8179
3598.0354 | 609.1429 | 519.5196 | 612.337 | 563.4295 | 549.2643 | 541.0422 | 526.9304
3599.0354 | 610.5978 | 519.4601 | 614.0285 | 564.3954 | 549.5507 | 541.8526 | 527.409
3600.0354 | 610.4035 | 519.5319 | 613.1805 | 563.8235 | 548.8163 | 541.1664 | 526.6501
3601.0354 | 610.8835 | 519.0739 | 614.5631 | 563.6104 | 547.8729 | 541.5163 | 526.7581
3602.0354 | 611.853 | 519.161 | 615.072 | 562.8613 | 547.5446 | 543.4002 | 528.4296
3603.0354 | 611.1565 | 519.2849 | 614.1286 | 562.7114 | 545.9742 | 542.5658 | 527.8626
3604.0354 | 607.6368 | 518.9565 | 613.2178 | 562.5757 | 545.7548 | 542.6215 | 527.2487
3605.0354 | 608.9983 | 518.7807 | 611.7415 | 563.8648 | 545.5166 | 542.0505 | 526.7143
3606.0354 | 609.9097 | 518.8443 | 611.6432 | 564.295 | 546.4531 | 541.5176 | 526.2022
3607.0354 | 608.8304 | 518.7189 | 611.8113 | 564.2773 | 547.2563 | 541.2503 | 525.856
3608.0354 | 610.3273 | 518.1639 | 613.4644 | 563.5435 | 547.2907 | 541.5164 | 525.8885
3609.0354 | 600.347 | 518.4804 | 613.0523 | 564.7122 | 547.9694 | 542.7776 | 526.4324
3610.0354 | 600.8233 | 518.1728 | 612.1847 | 565.8211 | 547.5977 | 542.3198 | 526.0791
3611.0354 | 602.6398 | 518.4784 | 610.6793 | 564.5737 | 547.5604 | 542.0867 | 524.9511
3612.0354 | 601.1774 | 518.7631 | 610.2225 | 564.8619 | 548.6563 | 542.4407 | 524.6991
3613.0354 | 597.9727 | 517.8185 | 610.1724 | 565.4466 | 548.4751 | 540.4375 | 523.6741
3614.0354 | 602.3432 | 518.3147 | 611.2687 | 564.7524 | 548.1995 | 539.9184 | 523.2811
3615.0354 | 602.6559 | 518.1186 | 611.8085 | 564.6594 | 547.9699 | 539.905 | 523.3951
3616.0354 | 603.7725 | 517.6834 | 611.5354 | 564.8601 | 548.1523 | 541.2198 | 523.866
3617.0354 | 603.2795 | 517.6843 | 611.6442 | 564.7688 | 547.7936 | 540.9617 | 524.1811
3618.0354 | 602.9863 | 517.1837 | 612.8927 | 565.3925 | 547.7347 | 541.158 | 524.1252
3619.0354 | 602.694 | 517.3167 | 612.4498 | 565.176 | 547.2785 | 541.1565 | 524.5305
3620.0354 | 607.5381 | 517.3364 | 613.4344 | 565.1491 | 547.5923 | 542.241 | 524.6664
3621.0354 | 604.1229 | 517.4215 | 614.015 | 565.2737 | 547.4346 | 542.5703 | 524.682
3622.0354 | 603.8218 | 517.4476 | 611.8889 | 566.0179 | 547.137 | 542.2194 | 524.4941
3623.0354 | 604.5866 | 517.2226 | 613.7117 | 565.2753 | 546.9425 | 542.0555 | 524.1997
3624.0354 | 604.7712 | 516.8549 | 612.1088 | 566.1429 | 546.7705 | 541.3806 | 523.3539
3625.0354 | 604.1114 | 517.0834 | 611.2049 | 567.7673 | 546.9208 | 541.0116 | 522.5444
3626.0354 | 603.1861 | 516.9159 | 611.0456 | 568.1361 | 547.3474 | 540.6775 | 521.8137
3627.0354 | 602.7857 | 516.8717 | 611.4815 | 566.6757 | 547.8059 | 539.7577 | 521.2461
3628.0354 | 603.7 | 516.4371 | 612.1457 | 566.0313 | 547.7973 | 539.9055 | 521.5125
3629.0354 | 602.101 | 516.0131 | 614.2108 | 566.8095 | 546.8893 | 539.4465 | 521.5794
3630.0354 | 601.9065 | 515.6489 | 614.1378 | 566.7761 | 545.7539 | 539.6717 | 521.7829
3631.0354 | 602.6395 | 515.8379 | 616.0819 | 566.3193 | 545.3891 | 541.4688 | 523.168
3632.0354 | 604.0911 | 515.8184 | 614.7532 | 566.5768 | 545.4896 | 542.9208 | 524.7826
3633.0354 | 603.9786 | 515.3795 | 613.5539 | 566.8707 | 546.5192 | 543.5015 | 526.0725
3634.0354 | 604.3992 | 515.1902 | 613.7541 | 567.1407 | 547.1241 | 542.8818 | 525.7131
3635.0354 | 607.1507 | 514.9756 | 613.1189 | 567.3707 | 547.2877 | 542.5582 | 525.4054
3636.0354 | 607.4489 | 514.8387 | 614.0032 | 567.3334 | 547.0683 | 542.0743 | 524.9949
3637.0354 | 607.3441 | 514.7332 | 613.7145 | 568.009 | 547.1142 | 540.5695 | 524.4302
3638.0354 | 608.9961 | 514.4426 | 614.3587 | 567.1866 | 547.3844 | 540.7629 | 523.8258
3639.0354 | 607.0594 | 514.3709 | 612.8716 | 567.361 | 547.9854 | 542.3663 | 524.1076
3640.0354 | 610.3259 | 514.2079 | 612.9064 | 567.8386 | 548.1641 | 542.9775 | 523.4138
3641.0354 | 613.1901 | 514.1976 | 613.6667 | 568.1633 | 548.9 | 542.861 | 523.3459
3642.0354 | 613.2025 | 513.8391 | 612.7064 | 570.0144 | 550.5572 | 542.2671 | 523.0255
3643.0354 | 608.9121 | 513.7703 | 612.7989 | 569.8279 | 550.8151 | 540.7375 | 521.2882
3644.0354 | 612.2754 | 513.6458 | 613.7263 | 570.2628 | 550.5958 | 540.5723 | 520.987
3645.0354 | 612.7585 | 513.3943 | 613.6376 | 570.7673 | 550.5114 | 540.6677 | 520.9017
3646.0354 | 613.24 | 513.1443 | 613.5897 | 570.8407 | 551.3319 | 540.3168 | 520.8272
3647.0354 | 614.8283 | 512.9788 | 614.8676 | 569.5854 | 551.5141 | 540.2088 | 520.7686
3648.0354 | 614.831 | 512.9108 | 613.4452 | 568.6511 | 551.1271 | 540.8485 | 520.7903
3649.0354 | 611.5515 | 513.2218 | 615.3188 | 569.1046 | 550.4135 | 541.0767 | 520.9936
3650.0354 | 612.5336 | 512.7434 | 612.9641 | 569.8941 | 549.8575 | 541.8953 | 521.534
3651.0354 | 575.5338 | 513.4585 | 613.163 | 570.1845 | 550.1308 | 541.4069 | 520.8471
3652.0354 | 607.8748 | 512.3322 | 612.6035 | 570.1314 | 550.2856 | 541.8906 | 520.5992
3653.0354 | 611.8799 | 512.0811 | 613.5488 | 569.9156 | 551.4421 | 542.8394 | 520.6325
3654.0354 | 611.7968 | 512.0046 | 612.8732 | 569.4459 | 552.2782 | 543.8077 | 521.5338
3655.0354 | 610.9511 | 511.655 | 611.9147 | 569.1514 | 552.9492 | 544.5648 | 521.4358
3656.0354 | 613.7912 | 511.5317 | 611.937 | 570.5727 | 552.6686 | 544.6306 | 520.9802
3657.0354 | 612.8331 | 511.3599 | 611.9946 | 570.5397 | 552.8183 | 543.4558 | 520.5585
3658.0354 | 613.9178 | 511.0862 | 611.6807 | 570.1766 | 552.4329 | 542.5267 | 519.766
3659.0354 | 615.6075 | 510.8865 | 610.945 | 570.058 | 553.2615 | 542.1606 | 518.8651
3660.0354 | 616.5247 | 510.9188 | 610.8783 | 570.0115 | 554.2626 | 542.6495 | 518.4865
3661.0354 | 618.019 | 510.7225 | 610.5554 | 570.7015 | 554.8013 | 542.5884 | 517.5939
3662.0354 | 616.5549 | 510.2477 | 610.1751 | 571.4424 | 555.6347 | 541.4547 | 517.1013
3663.0354 | 618.0573 | 509.9166 | 609.9891 | 571.1511 | 556.295 | 540.5395 | 515.9693
3664.0354 | 608.9892 | 509.9928 | 610.7781 | 571.3623 | 556.0382 | 539.6078 | 515.1262
3665.0354 | 571.6504 | 509.7439 | 610.5705 | 570.4552 | 556.0644 | 540.501 | 515.8824
3666.0354 | 566.4075 | 509.7895 | 610.9043 | 571.4429 | 555.7276 | 541.0772 | 515.9595
3667.0354 | 565.8878 | 509.5072 | 610.0253 | 571.5526 | 555.7307 | 541.8627 | 516.6882
3668.0354 | 566.8372 | 509.5369 | 609.2213 | 571.0777 | 555.7638 | 542.8354 | 516.2745
3669.0354 | 565.4206 | 509.5903 | 609.2776 | 571.4541 | 555.1599 | 542.2358 | 515.7481
3670.0354 | 564.7972 | 509.4537 | 609.5482 | 573.0302 | 554.9091 | 541.9622 | 515.6049
3671.0354 | 564.9315 | 509.9114 | 610.0787 | 574.6739 | 554.8267 | 540.1903 | 514.516
3672.0354 | 563.7899 | 509.2496 | 609.3044 | 574.8656 | 554.5377 | 538.9108 | 514.1834
3673.0354 | 560.3998 | 509.0144 | 609.0448 | 573.669 | 553.8409 | 537.713 | 514.0885
3674.0354 | 561.18 | 509.3301 | 609.3099 | 573.9367 | 553.3958 | 535.995 | 513.1175
3675.0354 | 611.0738 | 508.475 | 610.3889 | 573.0296 | 552.4719 | 535.3989 | 512.5926
3676.0354 | 654.2854 | 508.0662 | 610.7411 | 574.0871 | 551.7151 | 534.76 | 512.3988
3677.0354 | 652.391 | 507.9393 | 609.2259 | 574.6305 | 550.4588 | 533.4493 | 512.0432
3678.0354 | 657.0322 | 507.885 | 610.628 | 573.4283 | 550.5533 | 535.158 | 512.6007
3679.0354 | 658.9868 | 507.6948 | 609.5878 | 573.4644 | 550.6099 | 535.5919 | 513.6331
3680.0354 | 649.7254 | 507.5115 | 610.9047 | 573.3114 | 550.3627 | 536.5167 | 514.3315
3681.0354 | 652.911 | 507.3748 | 609.9123 | 573.13 | 550.3589 | 537.9738 | 515.0381
3682.0354 | 644.1422 | 507.1036 | 608.9285 | 573.768 | 551.1214 | 539.5324 | 515.436
3683.0354 | 645.8869 | 506.7918 | 608.3207 | 575.2541 | 552.0007 | 538.8573 | 514.6958
3684.0354 | 642.6323 | 506.6693 | 608.5361 | 575.1775 | 552.4972 | 538.4104 | 514.1991
3685.0354 | 640.4061 | 506.2741 | 608.6376 | 576.1415 | 553.0624 | 537.624 | 514.1357
3686.0354 | 639.8446 | 506.2499 | 609.354 | 575.347 | 552.4104 | 537.3784 | 512.9522
3687.0354 | 644.9055 | 506.0513 | 608.543 | 574.4932 | 552.1536 | 538.5243 | 514.0663
3688.0354 | 643.8619 | 505.9337 | 608.7447 | 575.8747 | 551.4367 | 538.4797 | 513.6525
3689.0354 | 644.5063 | 505.7445 | 610.9858 | 576.8688 | 551.3482 | 538.0048 | 513.7611
3690.0354 | 645.9332 | 505.6174 | 610.87 | 576.8738 | 551.4659 | 538.6632 | 513.9683
3691.0354 | 646.7978 | 505.5744 | 611.3086 | 575.924 | 551.0916 | 538.4252 | 513.9765
3692.0354 | 648.7027 | 505.386 | 610.6666 | 576.5784 | 550.8977 | 539.0448 | 514.0987
3693.0354 | 651.4346 | 505.4677 | 611.0118 | 576.3591 | 551.2328 | 539.9248 | 514.4241
3694.0354 | 651.1177 | 505.2286 | 609.5525 | 578.1846 | 553.5852 | 541.1467 | 515.2046
3695.0354 | 649.4851 | 505.4898 | 610.1222 | 578.6012 | 555.861 | 540.9338 | 515.2006
3696.0354 | 651.1388 | 505.463 | 611.9251 | 577.6254 | 556.2913 | 541.0251 | 514.9522
3697.0354 | 649.1019 | 505.2618 | 611.102 | 578.19 | 555.5872 | 540.9593 | 514.3982
3698.0354 | 650.8354 | 505.2128 | 611.2136 | 576.8955 | 554.1281 | 540.1569 | 513.7486
3699.0354 | 657.5056 | 504.9557 | 611.0955 | 576.5597 | 552.8409 | 540.8381 | 515.2992
3700.0354 | 653.9205 | 504.6669 | 609.7085 | 577.0141 | 552.6817 | 542.5146 | 515.6123
3701.0354 | 657.1879 | 504.2663 | 609.4662 | 576.4978 | 552.4903 | 544.3405 | 515.7596
3702.0354 | 659.3043 | 504.3855 | 610.0298 | 576.6953 | 552.8486 | 545.606 | 516.4063
3703.0354 | 659.3835 | 504.0502 | 609.6354 | 577.0905 | 553.2381 | 545.7434 | 516.8934
3704.0354 | 660.4198 | 503.9992 | 609.0639 | 576.4316 | 553.1066 | 545.9089 | 517.3419
3705.0354 | 678.4109 | 503.8007 | 609.2747 | 576.2528 | 553.2999 | 546.2982 | 517.454
3706.0354 | 689.1907 | 503.5789 | 610.1807 | 577.0653 | 553.6042 | 546.4687 | 517.6708
3707.0354 | 668.1109 | 503.5034 | 609.7414 | 578.0624 | 554.1906 | 545.9997 | 517.6447
3708.0354 | 663.5747 | 503.3385 | 609.7589 | 578.3873 | 554.6225 | 545.7386 | 517.5141
3709.0354 | 672.8641 | 503.1457 | 609.7155 | 578.4617 | 555.6003 | 545.3495 | 517.0231
3710.0354 | 659.5463 | 502.9051 | 609.7887 | 577.8797 | 555.2704 | 544.205 | 516.7901
3711.0354 | 660.7023 | 502.8316 | 610.6146 | 577.6924 | 554.5997 | 544.2249 | 517.4279
3712.0354 | 662.2376 | 502.5627 | 612.0993 | 578.2927 | 554.8669 | 544.362 | 518.9607
3713.0354 | 660.9819 | 502.4923 | 612.3985 | 578.4037 | 553.9301 | 544.2871 | 518.9676
3714.0354 | 662.2372 | 502.6301 | 611.3574 | 579.0459 | 554.0383 | 544.9165 | 519.1299
3715.0354 | 658.2219 | 502.4736 | 611.2518 | 578.3695 | 553.9645 | 544.024 | 518.5004
3716.0354 | 660.3714 | 502.3063 | 610.7439 | 579.0139 | 553.5116 | 543.3591 | 518.1684
3717.0354 | 662.6658 | 502.2354 | 610.8007 | 578.061 | 553.1256 | 542.3911 | 517.5165
3718.0354 | 662.1787 | 501.8931 | 610.9588 | 577.8776 | 553.0522 | 542.4432 | 517.1869
3719.0354 | 662.276 | 501.7188 | 610.5835 | 578.0029 | 553.3341 | 542.8177 | 517.7054
3720.0354 | 662.1698 | 501.9013 | 610.0707 | 580.1906 | 553.7211 | 543.6057 | 517.5827
3721.0354 | 663.4554 | 501.8673 | 610.6395 | 579.1891 | 553.7963 | 543.1344 | 516.9975
3722.0354 | 666.6125 | 502.1249 | 610.2306 | 579.2117 | 554.0424 | 542.9208 | 517.1203
3723.0354 | 670.1979 | 501.5504 | 610.2986 | 578.5765 | 553.738 | 542.4514 | 516.5563
3724.0354 | 668.2382 | 501.336 | 609.7522 | 579.8533 | 553.3414 | 541.9135 | 515.9439
3725.0354 | 669.7434 | 501.4938 | 610.978 | 579.4936 | 553.7111 | 542.1524 | 515.875
3726.0354 | 651.949 | 501.0021 | 609.8623 | 579.4745 | 555.0168 | 543.6343 | 516.8435
3727.0354 | 704.379 | 500.6194 | 609.2727 | 579.6869 | 555.7502 | 542.8798 | 516.83
3728.0354 | 706.5612 | 500.7471 | 610.1323 | 580.0393 | 555.1451 | 541.9488 | 516.1663
3729.0354 | 708.5182 | 500.7956 | 609.762 | 580.8063 | 554.8712 | 543.169 | 516.8423
3730.0354 | 711.8753 | 500.4613 | 610.2169 | 580.8192 | 554.887 | 542.9285 | 516.9711
3731.0354 | 706.9545 | 500.2176 | 610.8437 | 580.527 | 555.1686 | 542.1444 | 517.0229
3732.0354 | 689.2571 | 499.9599 | 609.6352 | 579.7576 | 556.3838 | 542.8227 | 517.1981
3733.0354 | 690.8223 | 499.8301 | 608.6026 | 581.2171 | 557.3917 | 543.2645 | 517.1578
3734.0354 | 688.8847 | 499.6652 | 608.9472 | 581.0189 | 557.5211 | 543.5852 | 517.0687
3735.0354 | 673.1066 | 499.7849 | 609.3673 | 580.4462 | 557.8711 | 542.8557 | 516.7896
3736.0354 | 671.8827 | 499.7575 | 609.2603 | 580.9527 | 557.747 | 541.9812 | 516.5765
3737.0354 | 671.3512 | 500.0854 | 608.6513 | 580.4885 | 556.7965 | 541.2335 | 516.0675
3738.0354 | 670.9785 | 499.5577 | 608.3517 | 579.9637 | 556.2651 | 541.8835 | 516.1421
3739.0354 | 666.6667 | 499.3331 | 607.8629 | 579.9809 | 556.8613 | 543.5962 | 515.6726
3740.0354 | 666.5716 | 499.0716 | 607.768 | 579.7276 | 558.051 | 544.3093 | 515.8819
3741.0354 | 666.9224 | 499.1363 | 608.0478 | 580.096 | 558.7632 | 545.0943 | 515.3591
3742.0354 | 670.4463 | 498.777 | 607.1062 | 579.5297 | 558.9439 | 545.0273 | 515.4397
3743.0354 | 668.9664 | 498.4816 | 607.2038 | 579.9468 | 558.1664 | 544.1636 | 514.5513
3744.0354 | 670.6198 | 498.5038 | 607.1017 | 579.6776 | 557.3031 | 542.7944 | 513.6705
3745.0354 | 671.1778 | 498.7479 | 606.625 | 579.7955 | 557.0909 | 542.4008 | 513.4875
3746.0354 | 673.1828 | 498.2354 | 606.2599 | 579.5189 | 557.78 | 542.2094 | 512.6529
3747.0354 | 678.6191 | 497.9352 | 605.7169 | 579.3036 | 559.3081 | 543.872 | 512.4111
3748.0354 | 679.0235 | 498.1883 | 605.2674 | 579.0163 | 560.2959 | 543.0651 | 511.4306
3749.0354 | 682.6918 | 498.1564 | 604.87 | 578.9398 | 560.4924 | 541.686 | 510.226
3750.0354 | 685.2406 | 498.6831 | 604.8583 | 579.0616 | 559.2216 | 540.1284 | 509.3875
3751.0354 | 687.0547 | 498.3815 | 605.4082 | 579.1535 | 558.6144 | 540.4734 | 509.1582
3752.0354 | 690.33 | 497.8021 | 605.0737 | 579.2809 | 558.6419 | 541.4883 | 510.3562
3753.0354 | 695.857 | 497.4706 | 605.3416 | 578.7003 | 557.8589 | 541.1128 | 510.446
3754.0354 | 691.1809 | 497.3921 | 604.7289 | 578.7444 | 557.0866 | 540.5874 | 510.3287
3755.0354 | 702.3369 | 497.1581 | 605.0074 | 578.4336 | 555.998 | 540.5879 | 510.7387
3756.0354 | 704.2674 | 497.3193 | 603.7952 | 578.9879 | 555.3664 | 540.4301 | 511.2434
3757.0354 | 701.779 | 497.2481 | 604.0824 | 579.0192 | 554.8452 | 539.8051 | 510.8332
3758.0354 | 695.7056 | 497.0915 | 603.8838 | 578.6762 | 554.9542 | 539.5788 | 510.5688
3759.0354 | 693.1323 | 496.841 | 604.1173 | 578.4119 | 554.6308 | 539.2141 | 510.5286
3760.0354 | 696.4967 | 496.7774 | 603.521 | 578.3236 | 553.9562 | 540.0287 | 511.4318
3761.0354 | 700.2194 | 496.5917 | 602.5868 | 578.0306 | 553.5992 | 542.5679 | 512.9484
3762.0354 | 703.2926 | 496.2351 | 602.8312 | 577.8425 | 553.2274 | 543.9937 | 513.8427
3763.0354 | 697.751 | 496.1986 | 602.3505 | 577.6375 | 553.2356 | 544.3612 | 514.1734
3764.0354 | 696.4741 | 496.4686 | 601.8071 | 577.6897 | 554.0775 | 544.0991 | 513.904
3765.0354 | 701.0055 | 496.8692 | 602.0371 | 578.1532 | 554.7256 | 543.7884 | 513.7345
3766.0354 | 699.1551 | 496.5973 | 601.6721 | 577.5433 | 554.4723 | 543.4659 | 513.2561
3767.0354 | 700.4467 | 497.4393 | 600.8967 | 577.5717 | 554.8622 | 544.5233 | 513.0674
3768.0354 | 705.0932 | 497.0179 | 601.0278 | 577.6001 | 555.1647 | 545.1723 | 512.8745
3769.0354 | 700.6597 | 496.7663 | 600.6268 | 577.7575 | 554.3425 | 543.0296 | 511.4947
3770.0354 | 708.7904 | 495.9695 | 600.1407 | 577.874 | 554.5894 | 542.2605 | 510.7282
3771.0354 | 708.027 | 496.3439 | 599.7241 | 577.0289 | 554.9393 | 541.8521 | 510.122
3772.0354 | 711.4887 | 496.2488 | 599.797 | 576.8995 | 554.8539 | 541.0313 | 509.3495
3773.0354 | 718.2538 | 495.5636 | 600.5012 | 576.8035 | 553.8039 | 540.7321 | 509.4292
3774.0354 | 713.6761 | 495.3755 | 599.8252 | 576.888 | 552.984 | 541.908 | 510.3762
3775.0354 | 711.0113 | 495.2101 | 599.0955 | 576.8655 | 552.865 | 542.177 | 510.6696
3776.0354 | 717.838 | 494.9595 | 598.88 | 577.0813 | 553.1992 | 540.8416 | 509.4982
3777.0354 | 715.1718 | 495.0346 | 598.4009 | 577.6366 | 554.3351 | 539.5992 | 508.7762
3778.0354 | 715.1101 | 494.9428 | 598.1785 | 576.5925 | 554.4719 | 539.0715 | 507.7911
3779.0354 | 715.1443 | 494.7263 | 598.1825 | 577.0694 | 554.3247 | 537.6334 | 507.3701
3780.0354 | 715.0018 | 494.6217 | 598.7214 | 576.7536 | 553.8201 | 536.88 | 507.0585
3781.0354 | 711.6555 | 494.3242 | 597.9022 | 576.2551 | 553.4152 | 537.0705 | 507.6551
3782.0354 | 711.0623 | 494.4309 | 597.3412 | 575.7449 | 553.1608 | 538.7386 | 508.9253
3783.0354 | 713.3983 | 494.4034 | 597.0344 | 576.2403 | 552.867 | 540.6356 | 509.6533
3784.0354 | 709.1787 | 494.2982 | 596.633 | 575.9252 | 552.6509 | 541.0463 | 509.1435
3785.0354 | 712.5382 | 494.7896 | 596.1173 | 575.436 | 553.1549 | 540.7711 | 508.6951
3786.0354 | 714.5291 | 495.3191 | 595.9268 | 575.4779 | 553.3175 | 540.0398 | 508.3147
3787.0354 | 704.8623 | 494.4455 | 595.476 | 575.2062 | 553.3145 | 539.1754 | 507.4765
3788.0354 | 708.9248 | 493.9025 | 595.8475 | 575.0939 | 552.9762 | 538.5915 | 506.7604
3789.0354 | 713.886 | 493.9826 | 595.0688 | 574.6665 | 552.7787 | 539.1775 | 507.6996
3790.0354 | 713.8967 | 494.189 | 594.6293 | 574.7403 | 552.3381 | 538.951 | 507.3335
3791.0354 | 713.3816 | 493.9085 | 594.4733 | 574.5191 | 552.3179 | 538.1489 | 506.7337
3792.0354 | 717.5099 | 493.4875 | 595.7024 | 574.6619 | 551.6597 | 537.9841 | 506.3386
3793.0354 | 707.2952 | 493.2692 | 593.9901 | 574.5534 | 551.8445 | 538.2066 | 506.7748
3794.0354 | 718.2741 | 493.2563 | 593.5581 | 574.0403 | 552.8642 | 539.1957 | 506.2802
3795.0354 | 724.6554 | 493.4789 | 593.0212 | 574.1874 | 553.911 | 538.0901 | 505.4424
3796.0354 | 724.1562 | 493.1097 | 592.9822 | 573.6518 | 553.898 | 537.0113 | 504.5135
3797.0354 | 729.7716 | 492.6861 | 592.6281 | 573.6103 | 554.915 | 537.0887 | 503.9195
3798.0354 | 726.0854 | 492.683 | 592.4926 | 573.5674 | 555.4246 | 536.4037 | 503.6113
3799.0354 | 727.4068 | 492.4926 | 592.3892 | 573.6099 | 555.3252 | 535.8448 | 503.3897
3800.0354 | 728.7223 | 492.1965 | 592.1345 | 573.6744 | 556.1573 | 534.9887 | 502.6707
3801.0354 | 722.8009 | 491.9811 | 591.4622 | 574.1987 | 555.891 | 533.7165 | 502.1057
3802.0354 | 725.4542 | 492.2147 | 591.9234 | 574.6661 | 555.5391 | 532.612 | 501.6499
3803.0354 | 731.4743 | 492.0283 | 592.3922 | 573.9818 | 554.9305 | 533.0955 | 501.9794
3804.0354 | 729.8527 | 491.7421 | 591.9544 | 574.0198 | 555.1144 | 534.1804 | 502.311
3805.0354 | 726.5262 | 491.6951 | 591.7432 | 573.3433 | 555.8269 | 535.4455 | 502.7555
3806.0354 | 785.2077 | 491.8194 | 591.3921 | 573.5333 | 556.6555 | 536.5661 | 503.0782
3807.0354 | 798.7493 | 491.4442 | 591.0536 | 574.3331 | 556.8627 | 537.125 | 503.1556
3808.0354 | 806.3222 | 491.3778 | 590.421 | 573.9813 | 557.499 | 537.2116 | 503.5326
3809.0354 | 823.5898 | 490.9691 | 589.6629 | 573.5635 | 558.7377 | 536.8845 | 503.0679
3810.0354 | 816.0198 | 490.8383 | 589.4135 | 572.8598 | 558.4534 | 536.2048 | 502.5782
3811.0354 | 790.0549 | 490.8211 | 589.8807 | 573.5235 | 557.3517 | 535.1974 | 501.9835
3812.0354 | 777.4527 | 490.7281 | 590.2163 | 573.8842 | 556.803 | 534.9957 | 501.9929
3813.0354 | 789.845 | 490.4838 | 589.3427 | 574.1632 | 556.6913 | 535.6398 | 501.8115
3814.0354 | 791.471 | 490.5046 | 588.9922 | 573.3334 | 556.9139 | 535.2272 | 501.5296
3815.0354 | 796.1349 | 490.4726 | 588.8667 | 573.2539 | 556.7247 | 535.0973 | 501.3038
3816.0354 | 787.8596 | 490.45 | 588.4835 | 574.0144 | 557.1571 | 535.2745 | 501.514
3817.0354 | 783.0761 | 490.2859 | 587.9122 | 573.912 | 558.0081 | 535.5474 | 501.9633
3818.0354 | 780.9996 | 490.0805 | 587.5279 | 573.0511 | 558.8494 | 536.5822 | 501.9103
3819.0354 | 792.6328 | 489.8535 | 587.3654 | 572.5882 | 559.0265 | 537.7435 | 502.641
3820.0354 | 791.7286 | 489.9489 | 588.1081 | 573.3977 | 559.3679 | 537.755 | 502.9311
3821.0354 | 793.1028 | 489.7752 | 587.6022 | 572.8798 | 558.9547 | 538.7745 | 503.2957
3822.0354 | 794.3742 | 489.614 | 587.5686 | 573.7158 | 558.9623 | 540.109 | 504.4239
3823.0354 | 800.3152 | 489.9558 | 587.2223 | 573.3925 | 560.3974 | 540.5854 | 504.9586
3824.0354 | 849.4761 | 489.862 | 586.2452 | 573.5583 | 561.5724 | 540.4327 | 505.1519
3825.0354 | 856.9363 | 489.9922 | 586.9605 | 574.0601 | 561.0806 | 539.0389 | 504.6857
3826.0354 | 854.2734 | 489.2863 | 586.8213 | 574.2481 | 560.2762 | 538.4568 | 504.7917
3827.0354 | 852.5529 | 489.285 | 586.0182 | 575.915 | 560.4129 | 538.7573 | 505.5956
3828.0354 | 856.9459 | 489.5449 | 585.6533 | 576.6158 | 561.3593 | 538.4037 | 505.8221
3829.0354 | 839.9362 | 489.8589 | 585.1571 | 575.9587 | 561.21 | 536.4875 | 504.3763
3830.0354 | 835.4853 | 490.1986 | 585.1254 | 574.7194 | 560.9249 | 535.8288 | 503.8657
3831.0354 | 833.4376 | 489.2698 | 586.0138 | 575.0946 | 559.8229 | 536.2975 | 503.5728
3832.0354 | 829.959 | 488.9758 | 585.5333 | 574.5795 | 559.337 | 537.6093 | 504.8119
3833.0354 | 845.5681 | 488.7244 | 585.1175 | 576.1307 | 558.7274 | 537.5532 | 504.7703
3834.0354 | 844.258 | 488.8615 | 584.776 | 576.1016 | 558.54 | 537.0001 | 504.7816
3835.0354 | 852.1342 | 488.8265 | 585.8425 | 575.2359 | 558.1984 | 536.4316 | 504.881
3836.0354 | 856.6957 | 488.7225 | 585.3796 | 574.3904 | 557.5125 | 537.5405 | 506.0833
3837.0354 | 853.914 | 488.4818 | 584.6623 | 574.4112 | 557.5511 | 538.492 | 507.8579
3838.0354 | 854.348 | 488.0645 | 584.3783 | 574.3921 | 557.3709 | 538.6879 | 509.9129
3839.0354 | 852.7555 | 488.0702 | 583.8046 | 573.891 | 556.9617 | 539.4154 | 513.1175
3840.0354 | 857.4992 | 488.0394 | 584.0719 | 573.7394 | 556.7295 | 540.9228 | 515.9237
3841.0354 | 853.375 | 487.7431 | 583.2843 | 574.767 | 556.0733 | 540.434 | 518.3811
3842.0354 | 861.5533 | 487.6347 | 582.8354 | 574.8057 | 556.5141 | 540.404 | 520.7307
3843.0354 | 876.1994 | 487.5807 | 582.5446 | 575.2437 | 557.4652 | 539.7315 | 522.1439
3844.0354 | 880.9615 | 487.451 | 582.8936 | 576.0069 | 557.2369 | 538.2321 | 524.7378
3845.0354 | 881.4985 | 487.6838 | 582.973 | 576.2087 | 556.4431 | 537.1888 | 526.6876
3846.0354 | 878.1354 | 487.674 | 584.0792 | 576.867 | 557.8233 | 537.8353 | 529.4902
3847.0354 | 881.0969 | 487.3886 | 583.5785 | 576.8399 | 559.6479 | 537.9564 | 532.0656
3848.0354 | 881.9264 | 487.3455 | 582.6888 | 576.9234 | 560.9707 | 538.1677 | 535.2285
3849.0354 | 881.08 | 487.4463 | 583.852 | 576.2114 | 561.8187 | 538.196 | 537.3006
3850.0354 | 878.5374 | 487.1401 | 584.6411 | 575.6322 | 561.9994 | 539.2232 | 541.8946
3851.0354 | 886.8264 | 486.7871 | 583.7144 | 575.7034 | 562.6738 | 540.1634 | 547.7231
3852.0354 | 887.6769 | 486.7119 | 583.6789 | 576.1111 | 562.8884 | 541.791 | 553.5122
3853.0354 | 890.3343 | 486.5522 | 582.9553 | 577.3386 | 562.5951 | 542.195 | 560.4891
3854.0354 | 890.9982 | 486.391 | 584.0646 | 577.9201 | 562.6503 | 542.3435 | 566.646
3855.0354 | 889.6259 | 486.2393 | 584.7717 | 576.8791 | 562.6551 | 540.9008 | 572.5764
3856.0354 | 890.8053 | 486.0431 | 584.4811 | 577.7662 | 562.0538 | 540.281 | 579.8924
3857.0354 | 895.5412 | 486.0659 | 583.5628 | 577.831 | 560.9107 | 539.8155 | 585.2619
3858.0354 | 895.0848 | 486.104 | 584.1733 | 578.274 | 560.6738 | 540.1923 | 593.5266
3859.0354 | 892.8526 | 485.8367 | 583.7296 | 579.1448 | 560.5962 | 539.9612 | 600.9217
3860.0354 | 903.0961 | 485.8695 | 583.7916 | 578.1142 | 560.5673 | 540.4261 | 607.4614
3861.0354 | 897.2493 | 485.6007 | 583.0826 | 578.5038 | 559.7545 | 539.6304 | 612.0852
3862.0354 | 905.6166 | 485.4238 | 584.5737 | 578.3421 | 559.6273 | 539.7012 | 618.3417
3863.0354 | 904.3451 | 485.3914 | 585.3976 | 578.964 | 560.2153 | 540.2524 | 624.3541
3864.0354 | 897.2711 | 485.2164 | 584.1206 | 579.643 | 561.0647 | 541.0871 | 629.6275
3865.0354 | 894.8773 | 485.1432 | 583.4272 | 580.1046 | 560.482 | 539.9898 | 633.1278
3866.0354 | 891.6847 | 484.9979 | 583.3643 | 578.4123 | 559.6913 | 539.6784 | 636.299
3867.0354 | 893.5955 | 484.8867 | 584.7331 | 579.2625 | 559.8439 | 540.9598 | 636.5085
3868.0354 | 908.8496 | 484.9577 | 585.3996 | 580.523 | 560.0264 | 543.1858 | 639.789
3869.0354 | 902.9439 | 484.7941 | 586.0069 | 580.6566 | 560.3658 | 543.5485 | 645.0839
3870.0354 | 899.3636 | 484.6044 | 586.7839 | 579.922 | 561.4635 | 543.9933 | 649.3449
3871.0354 | 897.5888 | 484.6735 | 586.9712 | 579.8625 | 561.2949 | 543.4291 | 652.3008
3872.0354 | 895.7956 | 484.512 | 587.7619 | 579.3124 | 560.4617 | 543.3436 | 654.9162
3873.0354 | 901.3951 | 484.4382 | 586.7098 | 579.5057 | 560.829 | 544.4347 | 655.0811
3874.0354 | 899.7564 | 484.0486 | 585.9696 | 581.2902 | 561.1422 | 544.5628 | 651.2302
3875.0354 | 898.5584 | 483.8248 | 585.8033 | 581.9719 | 560.545 | 543.9577 | 650.7104
3876.0354 | 910.9767 | 483.8051 | 585.6065 | 582.325 | 560.85 | 543.8501 | 648.2439
3877.0354 | 908.0016 | 483.8571 | 585.5877 | 582.9715 | 561.4461 | 543.8322 | 642.4883
3878.0354 | 903.1849 | 483.8965 | 586.3974 | 583.451 | 561.2455 | 542.9459 | 635.4993
3879.0354 | 920.5745 | 483.5852 | 587.2505 | 582.165 | 560.5327 | 542.1006 | 626.3547
3880.0354 | 913.2502 | 483.6043 | 586.1982 | 582.9428 | 559.2166 | 541.1206 | 621.4967
3881.0354 | 904.7422 | 483.4823 | 586.5918 | 583.3136 | 559.121 | 541.5921 | 608.2421
3882.0354 | 905.4121 | 483.292 | 587.289 | 582.8429 | 558.9274 | 543.0767 | 598.0197
3883.0354 | 906.3649 | 483.2745 | 586.4852 | 583.0647 | 559.3954 | 545.1749 | 587.3699
3884.0354 | 912.1774 | 483.0069 | 585.8818 | 582.7498 | 559.9403 | 545.4798 | 582.3598
3885.0354 | 920.2805 | 482.8167 | 585.8747 | 583.371 | 560.658 | 545.4432 | 578.5064
3886.0354 | 916.8093 | 482.776 | 586.4196 | 583.6499 | 561.0017 | 545.314 | 576.675
3887.0354 | 919.5075 | 482.6629 | 587.0661 | 584.9664 | 561.7377 | 545.3866 | 576.4365
3888.0354 | 914.3902 | 482.5302 | 587.6382 | 584.6832 | 562.8964 | 545.761 | 577.1734
3889.0354 | 910.6541 | 482.3775 | 589.6968 | 583.9469 | 562.7399 | 546.3959 | 577.2472
3890.0354 | 910.984 | 482.4827 | 590.1389 | 583.4642 | 561.4279 | 546.3969 | 578.0737
3891.0354 | 905.7002 | 482.9076 | 591.1725 | 583.2822 | 560.0838 | 546.3081 | 577.3504
3892.0354 | 894.1367 | 482.6395 | 589.856 | 583.4795 | 558.8784 | 546.3533 | 577.868
3893.0354 | 879.4524 | 482.7568 | 591.643 | 583.3071 | 558.4153 | 546.4438 | 578.8872
3894.0354 | 891.9508 | 482.5089 | 589.9711 | 583.7108 | 558.1237 | 547.6473 | 581.7136
3895.0354 | 898.0327 | 482.4679 | 590.0729 | 585.0072 | 558.7268 | 548.1568 | 581.6936
3896.0354 | 893.6781 | 482.3186 | 590.3033 | 584.6383 | 559.0148 | 547.6556 | 582.1642
3897.0354 | 899.349 | 482.1124 | 590.4223 | 585.0069 | 559.835 | 547.0965 | 581.8056
3898.0354 | 918.8055 | 482.0385 | 590.174 | 584.0152 | 560.3301 | 547.4834 | 583.4099
3899.0354 | 923.372 | 481.8827 | 589.6797 | 583.9997 | 562.0137 | 551.7378 | 585.1583
3900.0354 | 926.429 | 481.7114 | 588.896 | 583.3515 | 562.9599 | 555.3925 | 586.6809
3901.0354 | 925.8865 | 481.3803 | 589.5076 | 584.3431 | 563.3071 | 554.1032 | 587.4625
3902.0354 | 929.5046 | 481.4181 | 589.1663 | 585.0322 | 562.725 | 552.624 | 588.7728
3903.0354 | 919.5812 | 481.3187 | 588.7777 | 584.4262 | 562.2215 | 551.2274 | 587.831
3904.0354 | 920.9473 | 481.0478 | 588.4068 | 583.5752 | 561.485 | 551.2114 | 588.3029
3905.0354 | 929.9275 | 480.9816 | 588.6454 | 584.3107 | 560.8264 | 550.4632 | 585.7297
3906.0354 | 928.0674 | 480.9903 | 589.5204 | 585.8012 | 560.6455 | 550.0194 | 587.1695
3907.0354 | 925.3114 | 480.925 | 588.4173 | 586.8723 | 560.9927 | 548.3522 | 587.6778
3908.0354 | 924.7175 | 480.7642 | 589.2597 | 586.9456 | 561.1063 | 546.8457 | 588.2261
3909.0354 | 922.8346 | 480.8155 | 589.8983 | 586.283 | 560.807 | 545.7096 | 589.2147
3910.0354 | 927.0085 | 480.6558 | 589.893 | 586.9122 | 560.7347 | 545.3152 | 591.471
3911.0354 | 932.1896 | 480.4676 | 588.8617 | 586.505 | 559.7438 | 543.8636 | 591.3589
3912.0354 | 930.2365 | 480.4585 | 588.9025 | 586.8534 | 559.6765 | 542.4596 | 591.4665
3913.0354 | 933.5202 | 480.2993 | 588.7413 | 586.3982 | 560.1638 | 541.8289 | 592.4526
3914.0354 | 925.6122 | 480.2873 | 589.1261 | 586.8577 | 559.207 | 541.2339 | 594.7773
3915.0354 | 923.4005 | 480.3734 | 589.6673 | 586.5612 | 559.0014 | 541.1109 | 595.5902
3916.0354 | 925.6281 | 480.1191 | 591.6674 | 586.2267 | 559.6176 | 542.1493 | 595.4909
3917.051 | 928.5328 | 480.0929 | 591.1553 | 586.3829 | 559.6541 | 543.1206 | 595.8991
3918.0354 | 925.097 | 480.2017 | 590.3995 | 587.2016 | 559.5704 | 542.9842 | 595.4259
3919.0354 | 928.8317 | 479.7683 | 590.0683 | 586.4265 | 559.4042 | 542.4478 | 597.0481
3920.0354 | 931.1949 | 479.6192 | 589.7482 | 587.4461 | 559.0262 | 542.4414 | 597.2583
3921.0354 | 930.6075 | 479.5121 | 591.1207 | 587.5516 | 559.6514 | 542.1336 | 598.3994
3922.0354 | 931.2308 | 479.413 | 590.6512 | 587.2039 | 559.5942 | 541.4045 | 598.6448
3923.0354 | 935.1547 | 479.283 | 589.6055 | 586.7029 | 560.4954 | 542.8294 | 598.9905
3924.0354 | 932.6013 | 479.3637 | 589.2707 | 586.7368 | 561.4947 | 544.5592 | 599.8073
3925.0354 | 935.6026 | 479.3868 | 590.2152 | 587.634 | 561.7903 | 544.5003 | 600.1631
3926.0354 | 931.1031 | 479.0704 | 589.8375 | 588.7805 | 561.8819 | 544.2036 | 601.2284
3927.0354 | 934.418 | 479.2738 | 589.7861 | 588.206 | 563.5246 | 543.5167 | 600.5458
3928.0354 | 938.556 | 479.2409 | 589.1709 | 587.9199 | 563.7214 | 543.9597 | 602.0761
3929.0354 | 932.0858 | 479.5098 | 588.9529 | 589.5952 | 563.5263 | 543.3428 | 602.7762
3930.0354 | 935.7688 | 478.9777 | 589.4699 | 591.2631 | 563.4652 | 541.9097 | 604.335
3931.0354 | 935.8437 | 478.6867 | 588.4793 | 590.3014 | 562.9087 | 540.297 | 604.8968
3932.0354 | 930.5391 | 478.6115 | 588.1563 | 590.4384 | 562.5369 | 539.4233 | 604.9873
3933.0354 | 933.9195 | 478.4281 | 589.3191 | 590.2828 | 562.6429 | 539.6261 | 605.7101
3934.0354 | 931.8433 | 478.5584 | 588.3613 | 591.1285 | 563.0436 | 540.3875 | 606.3503
3935.0354 | 938.3787 | 478.1875 | 588.4165 | 592.7439 | 563.4395 | 540.3298 | 606.2248
3936.0354 | 935.5701 | 478.1741 | 588.8395 | 593.0179 | 563.6386 | 539.385 | 607.3259
3937.0354 | 927.4563 | 478.1293 | 590.7083 | 592.0866 | 563.6508 | 538.9817 | 608.0204
3938.0354 | 925.1196 | 478.064 | 589.5603 | 594.1908 | 562.6305 | 538.5524 | 607.942
3939.0198 | 925.3919 | 477.9887 | 589.5725 | 594.0288 | 563.2538 | 538.1276 | 608.0856
3940.0354 | 914.5639 | 478.3844 | 589.4185 | 593.2787 | 562.6446 | 536.8935 | 608.1171
3941.0354 | 854.5525 | 478.1457 | 588.7397 | 593.5314 | 561.6241 | 536.3929 | 610.2505
3942.0354 | 881.8457 | 478.6025 | 589.2957 | 593.556 | 561.2733 | 536.7101 | 611.5181
3943.0354 | 592.2778 | 478.2529 | 590.2596 | 592.8436 | 560.7243 | 536.4807 | 610.299
3944.0354 | 428.6879 | 477.749 | 589.8811 | 592.4078 | 559.3837 | 536.743 | 611.5927
3945.0354 | 468.9173 | 477.7103 | 589.1589 | 592.3381 | 558.747 | 540.3343 | 611.6278
3946.0354 | 705.8976 | 478.8784 | 588.907 | 592.1379 | 560.7506 | 543.1924 | 607.2625
3947.0354 | 417.3308 | 477.5346 | 587.787 | 591.9499 | 560.3932 | 543.2937 | 610.1138
3948.0354 | 417.0034 | 477.7756 | 587.918 | 592.6492 | 560.9537 | 542.8412 | 609.7905
3949.0354 | 417.1624 | 477.2661 | 587.2355 | 592.4159 | 562.5555 | 542.7401 | 609.4574
3950.0354 | 415.7347 | 477.6412 | 587.2037 | 593.3624 | 562.795 | 541.4396 | 609.7547
3951.0354 | 413.9259 | 477.3201 | 587.2043 | 593.4685 | 562.2103 | 539.7783 | 607.536
3952.0354 | 412.7522 | 477.3207 | 586.8014 | 595.6838 | 561.5286 | 538.0941 | 606.4127
3953.0354 | 409.3918 | 477.1641 | 587.5689 | 595.0888 | 561.5132 | 536.1875 | 605.3935
3954.0354 | 410.8938 | 477.1913 | 588.1673 | 594.1781 | 560.8219 | 535.9149 | 603.7054
3955.0354 | 412.2412 | 477.0103 | 587.8153 | 593.7597 | 560.3217 | 536.5918 | 601.8866
3956.0354 | 410.4051 | 476.8776 | 589.7129 | 595.7744 | 560.5992 | 540.3004 | 597.0014
3957.0354 | 409.3988 | 476.6696 | 590.4779 | 596.1653 | 562.2635 | 542.153 | 599.7248
3958.0354 | 410.9456 | 476.7438 | 589.0011 | 595.4542 | 562.3457 | 541.3507 | 602.2885
3959.0354 | 412.2395 | 476.6154 | 590.7381 | 594.7775 | 561.3798 | 540.9088 | 603.3653
3960.0354 | 410.9456 | 476.5438 | 588.9955 | 595.2647 | 561.2599 | 539.8296 | 602.7528
3961.0354 | 411.8736 | 476.3069 | 589.3029 | 595.6625 | 561.46 | 539.549 | 601.1364
3962.0354 | 411.6573 | 476.2702 | 589.6569 | 596.1316 | 562.7302 | 539.9062 | 599.9955
3963.0354 | 409.7483 | 476.1565 | 588.6568 | 595.6387 | 562.0965 | 539.6358 | 597.5648
3964.0354 | 407.3002 | 476.0095 | 588.2743 | 596.8782 | 562.0982 | 540.35 | 593.4678
3965.0354 | 415.9944 | 475.9712 | 587.7692 | 595.0236 | 563.89 | 544.8482 | 591.9959
3966.0354 | 415.4109 | 475.8223 | 587.2651 | 594.9625 | 564.5801 | 544.9263 | 589.409
3967.0354 | 408.019 | 476.1199 | 586.8858 | 595.2849 | 564.9037 | 543.2849 | 586.2758
3968.0354 | 408.3008 | 476.016 | 586.6993 | 595.2105 | 565.478 | 541.9768 | 582.8778
3969.0354 | 405.9256 | 475.8425 | 586.4648 | 595.6276 | 565.1277 | 540.2741 | 581.5909
3970.0354 | 405.362 | 475.5276 | 586.5235 | 596.5518 | 565.0057 | 539.4465 | 580.0351
3971.0354 | 405.0036 | 475.4711 | 587.4795 | 597.0161 | 565.0402 | 539.3446 | 579.3215
3972.0354 | 400.3845 | 475.3462 | 588.2126 | 597.3389 | 564.5225 | 539.5436 | 577.4679
3973.0354 | 398.5674 | 475.3176 | 588.7918 | 597.5207 | 563.9725 | 540.2121 | 577.1071
3974.0354 | 400.0227 | 475.3131 | 587.7597 | 599.1139 | 563.8893 | 539.5007 | 575.3668
3975.0354 | 401.302 | 475.2481 | 586.8932 | 599.1854 | 563.527 | 538.4809 | 575.5917
3976.0354 | 383.6923 | 475.2885 | 586.6208 | 597.906 | 562.6665 | 537.086 | 574.0756
3977.0354 | 384.5092 | 475.1163 | 586.0929 | 598.1819 | 562.0072 | 537.3504 | 573.4349
3978.0354 | 386.9961 | 474.9442 | 585.4331 | 598.0575 | 562.2706 | 537.4353 | 573.2879
3979.0354 | 382.6967 | 474.9847 | 585.2921 | 598.0163 | 562.769 | 536.5971 | 570.9932
3980.0354 | 379.859 | 474.7842 | 585.1639 | 598.5114 | 562.4347 | 535.4768 | 568.1566
3981.0354 | 388.8716 | 474.7593 | 584.8291 | 598.188 | 562.667 | 536.3811 | 564.2834
3982.0354 | 387.7933 | 474.7318 | 584.8043 | 597.6822 | 563.278 | 536.1394 | 562.5611
3983.0354 | 389.4182 | 474.5181 | 584.4095 | 598.878 | 563.4583 | 536.9979 | 562.4376
3984.0354 | 384.8835 | 474.5424 | 584.2006 | 598.3738 | 564.1502 | 537.1247 | 562.4884
3985.0354 | 391.0828 | 474.4438 | 584.8128 | 600.399 | 564.5398 | 536.3968 | 563.1618
3986.0354 | 385.63 | 474.3905 | 585.5881 | 601.305 | 564.8328 | 536.2751 | 563.2975
3987.0354 | 358.5803 | 474.0846 | 585.9134 | 601.0428 | 566.5284 | 536.8674 | 562.734
3988.0354 | 347.2055 | 474.0093 | 585.311 | 601.1719 | 565.9459 | 535.2295 | 563.2717
3989.0354 | 391.8436 | 474.0382 | 585.1853 | 601.6093 | 565.0539 | 534.8509 | 563.5039
3990.0354 | 391.3699 | 474.1538 | 584.9033 | 601.8438 | 564.6899 | 535.7234 | 564.5627
3991.0354 | 389.964 | 474.0366 | 584.1911 | 601.6071 | 563.8202 | 535.1744 | 564.0846
3992.0354 | 383.8182 | 473.9191 | 584.0526 | 600.568 | 563.8444 | 535.4042 | 563.1234
3993.0354 | 377.7934 | 473.9056 | 583.9394 | 600.4791 | 563.3182 | 535.3455 | 562.3778
3994.0354 | 384.3348 | 473.5464 | 584.749 | 601.4765 | 563.5166 | 536.7653 | 562.596
3995.0354 | 378.9182 | 473.29 | 585.864 | 602.4003 | 565.6773 | 538.0919 | 563.1767
3996.0354 | 387.4618 | 473.2527 | 585.8703 | 601.8574 | 566.6925 | 538.4333 | 562.5858
3997.0354 | 400.4869 | 473.2644 | 584.1964 | 602.6745 | 566.6988 | 540.2391 | 563.9077
3998.0354 | 395.2405 | 473.3699 | 585.5598 | 602.0615 | 566.0036 | 539.7898 | 563.5259
3999.0354 | 396.8775 | 473.1624 | 585.3116 | 601.4518 | 565.1331 | 539.7892 | 563.9492
4000.0354 | 396.1765 | 473.0715 | 584.6207 | 600.9814 | 564.8533 | 540.145 | 563.9716
4001.0354 | 393.6606 | 473.1021 | 586.5749 | 601.6534 | 564.6896 | 541.7026 | 563.4629
4002.0198 | 393.4993 | 473.0058 | 585.3217 | 601.9749 | 564.524 | 542.6809 | 564.9488
4003.0354 | 398.0026 | 472.7454 | 584.2017 | 602.356 | 565.3861 | 542.9273 | 564.5798
4004.0354 | 394.4967 | 472.7503 | 584.668 | 602.3551 | 565.8774 | 540.6791 | 564.6986
4005.0354 | 384.8389 | 472.6836 | 585.3815 | 602.7675 | 565.9736 | 539.7895 | 565.5847
4006.0354 | 392.4127 | 472.4564 | 584.2318 | 602.8289 | 566.4607 | 540.0869 | 566.1677
4007.0354 | 320.6344 | 472.3594 | 584.7496 | 603.5572 | 566.0274 | 539.7397 | 567.0496
4008.0354 | 323.918 | 472.2884 | 585.5381 | 602.632 | 566.196 | 539.8562 | 567.2399
4009.0354 | 397.1131 | 472.1888 | 585.0049 | 602.8832 | 565.7008 | 539.8467 | 569.3655
4010.0354 | 363.2371 | 472.2439 | 585.0691 | 602.5476 | 565.2611 | 540.4953 | 570.7798
4011.0354 | 506.1494 | 472.2418 | 584.8775 | 601.9473 | 564.8637 | 540.3714 | 570.3967
4012.0354 | 414.5511 | 471.9204 | 583.6545 | 602.7746 | 564.3183 | 540.694 | 571.1559
4013.0354 | 317.3925 | 471.8978 | 583.0424 | 605.0672 | 564.7916 | 540.5119 | 571.968
4014.0354 | 288.3612 | 471.8659 | 583.8295 | 604.1039 | 565.9217 | 540.5248 | 571.7755
4015.0354 | 306.9897 | 471.8663 | 584.551 | 603.2234 | 565.498 | 539.4987 | 569.5475
4016.0354 | 399.7024 | 471.7735 | 585.2409 | 602.3379 | 564.3925 | 540.3832 | 568.6153
4017.0354 | 398.6085 | 471.7203 | 585.2954 | 602.9946 | 562.8645 | 540.3393 | 567.4076
4018.0354 | 391.6704 | 471.6904 | 586.328 | 604.9268 | 562.7894 | 541.3564 | 567.6232
4019.0354 | 398.1605 | 471.4208 | 585.0263 | 604.6789 | 562.4561 | 540.6961 | 567.8166
4020.0354 | 392.3684 | 471.2578 | 584.6335 | 604.9091 | 562.3038 | 540.6515 | 566.6699
4021.0354 | 398.2934 | 471.4579 | 583.9896 | 603.9965 | 562.3582 | 541.3199 | 564.9315
4022.0354 | 404.1603 | 471.2175 | 583.5418 | 604.7281 | 562.6304 | 540.5728 | 565.1862
4023.0354 | 406.9414 | 471.1339 | 582.9805 | 604.7241 | 563.734 | 539.5177 | 564.3441
4024.0354 | 392.7121 | 471.3377 | 583.0792 | 603.6945 | 564.3615 | 539.2394 | 564.9826
4025.0354 | 388.3393 | 471.2791 | 582.6508 | 603.2047 | 565.4558 | 541.8779 | 564.2917
4026.0354 | 397.9735 | 471.1695 | 582.1783 | 603.167 | 566.8135 | 542.7624 | 563.7007
4027.0354 | 386.1899 | 471.0398 | 581.8205 | 603.5274 | 567.635 | 541.7917 | 562.9646
4028.0354 | 402.6085 | 470.9993 | 581.5849 | 603.3004 | 568.1611 | 541.0093 | 562.432
4029.0354 | 390.7423 | 470.8941 | 581.6705 | 603.5825 | 569.0725 | 540.3626 | 561.73
4030.0354 | 385.2684 | 470.7958 | 581.3608 | 603.9256 | 569.8267 | 539.7907 | 561.8109
4031.0354 | 386.6274 | 470.6269 | 583.0609 | 604.4621 | 570.0744 | 539.006 | 561.7464
4032.0354 | 385.2654 | 470.4705 | 581.916 | 603.2387 | 569.7293 | 539.124 | 561.0576
4033.0354 | 386.8716 | 470.3247 | 581.8458 | 603.1834 | 569.8486 | 539.8751 | 560.0918
4034.0354 | 389.9418 | 470.2536 | 581.0761 | 602.7152 | 572.3106 | 540.703 | 560.6709
4035.0354 | 390.9275 | 470.1626 | 580.7005 | 602.7498 | 574.0846 | 544.0125 | 560.49
4036.0354 | 384.3439 | 470.5703 | 580.4398 | 604.1618 | 573.9158 | 542.3203 | 557.7944
4037.0354 | 593.137 | 470.21 | 580.1975 | 604.296 | 573.0108 | 539.9748 | 557.5639
4038.0354 | 895.2747 | 470.0016 | 580.259 | 603.5455 | 572.4915 | 538.9358 | 556.638
4039.0354 | 879.4367 | 469.8787 | 580.2828 | 602.9328 | 571.1264 | 538.1304 | 556.5439
4040.0354 | 937.4302 | 469.9967 | 579.3968 | 602.8206 | 572.2548 | 538.8026 | 555.9083
4041.0354 | 432.9703 | 469.9212 | 579.0925 | 602.8571 | 573.1897 | 537.7036 | 555.7559
4042.0354 | 429.6651 | 469.6507 | 578.8305 | 602.6277 | 572.766 | 536.0107 | 555.6885
4043.0354 | 385.6002 | 469.6864 | 578.6505 | 602.9934 | 573.739 | 535.1836 | 555.814
4044.0354 | 406.2428 | 469.5275 | 578.297 | 603.7992 | 574.2369 | 533.6029 | 555.4829
4045.0354 | 385.6196 | 469.3981 | 578.0549 | 603.2556 | 573.657 | 532.6847 | 554.9125
4046.0354 | 382.7717 | 469.476 | 577.8873 | 602.6654 | 573.0788 | 531.8223 | 555.1875
4047.0354 | 381.304 | 469.3953 | 577.5702 | 602.4483 | 571.8954 | 531.39 | 556.5877
4048.0354 | 799.4675 | 469.2045 | 577.0702 | 602.4644 | 573.4042 | 530.502 | 556.1845
4049.0354 | 791.379 | 469.0366 | 577.0443 | 602.1332 | 575.2245 | 530.4935 | 555.6091
4050.0354 | 554.1376 | 469.049 | 576.5169 | 601.4642 | 578.5698 | 530.5975 | 556.0995
4051.0354 | 519.6926 | 468.9801 | 576.5839 | 601.5511 | 577.801 | 529.2037 | 553.8221
4052.0354 | 473.831 | 469.2817 | 576.1053 | 601.8259 | 576.6893 | 528.7228 | 552.9998
4053.0354 | 469.8983 | 469.0081 | 576.035 | 601.5551 | 577.6076 | 529.1647 | 553.3687
4054.0354 | 440.8901 | 468.8342 | 575.8094 | 601.4809 | 579.0446 | 529.4019 | 554.6532
4055.0354 | 415.6805 | 468.8129 | 575.261 | 601.0318 | 579.1046 | 529.7228 | 554.7677
4056.0354 | 411.8642 | 469.1295 | 575.1767 | 601.4455 | 577.7277 | 528.9263 | 554.8441
4057.0354 | 421.2964 | 468.8681 | 575.1099 | 600.7486 | 577.0094 | 528.9233 | 555.9839
4058.0354 | 437.8289 | 468.5729 | 576.2033 | 600.5592 | 575.5998 | 528.9069 | 556.7921
4059.0354 | 439.5087 | 468.6023 | 575.2077 | 600.1021 | 574.8745 | 530.1169 | 556.8224
4060.0354 | 435.5307 | 468.4009 | 574.986 | 600.9168 | 574.1498 | 531.2226 | 558.762
4061.0354 | 443.2035 | 468.4587 | 574.173 | 600.1834 | 576.8067 | 532.3404 | 550.2697
4062.0354 | 414.841 | 468.1854 | 573.7648 | 599.9522 | 575.5411 | 531.8539 | 558.9177
4063.0354 | 442.9753 | 468.0076 | 574.0293 | 599.9201 | 575.1369 | 531.1039 | 559.1025
4064.0354 | 435.8976 | 467.8958 | 574.077 | 599.9791 | 574.8509 | 531.2381 | 560.1319
4065.0354 | 434.8019 | 467.8271 | 573.8369 | 600.2516 | 575.5366 | 531.0336 | 559.9477
4066.0354 | 580.2767 | 467.8444 | 573.1195 | 599.8521 | 575.0693 | 530.1329 | 560.3726
4067.0354 | 580.034 | 468.2439 | 572.9279 | 599.7747 | 574.3424 | 528.2149 | 560.0099
4068.0354 | 634.1066 | 467.9189 | 572.9152 | 599.5208 | 573.1906 | 527.2868 | 559.198
4069.0354 | 416.0043 | 467.598 | 572.935 | 599.8589 | 572.6667 | 528.3353 | 559.5505
4070.0354 | 409.9102 | 467.484 | 572.8942 | 599.1149 | 572.9565 | 529.185 | 559.8024
4071.0354 | 409.8722 | 467.3593 | 572.2979 | 599.2108 | 572.8006 | 528.7583 | 559.5725
4072.0354 | 640.5696 | 467.4806 | 572.2812 | 602.0619 | 572.2274 | 528.0685 | 558.6584
4073.0354 | 760.558 | 467.2944 | 571.8899 | 600.7446 | 571.3862 | 528.1052 | 559.6034
4074.0354 | 436.6448 | 467.1797 | 572.8368 | 600.1208 | 571.1369 | 528.1927 | 558.9529
4075.0354 | 395.6816 | 467.14 | 571.99 | 601.1723 | 570.5611 | 528.7534 | 559.3504
4076.0354 | 395.6456 | 467.0493 | 571.76 | 601.403 | 569.962 | 528.5974 | 559.4637
4077.0354 | 376.9576 | 467.0753 | 572.3012 | 602.0388 | 569.4235 | 528.5889 | 559.2382
4078.0354 | 359.9567 | 466.9097 | 574.3212 | 601.3993 | 569.8386 | 528.4078 | 559.177
4079.0354 | 351.5408 | 466.7647 | 574.6084 | 600.8164 | 570.0305 | 528.9598 | 558.7313
4080.0354 | 357.2682 | 466.7899 | 576.0201 | 600.2595 | 570.8555 | 530.9821 | 559.3448
4081.0354 | 351.1699 | 466.6395 | 573.4105 | 600.4447 | 569.6068 | 532.8805 | 560.0674
4082.0354 | 348.3298 | 466.4739 | 572.4611 | 600.8701 | 569.1359 | 532.325 | 560.0939
4083.0354 | 341.2687 | 466.5307 | 573.1881 | 600.898 | 568.1645 | 531.6544 | 560.1514
4084.0354 | 404.0546 | 466.5821 | 572.4274 | 599.5209 | 567.9544 | 533.6369 | 561.1124
4085.0354 | 401.8891 | 466.5145 | 574.6252 | 599.5634 | 565.844 | 535.4128 | 562.1504
4086.0354 | 398.3049 | 466.3267 | 573.9392 | 600.1025 | 566.7779 | 537.7642 | 562.9213
4087.0354 | 398.7207 | 466.2128 | 574.1567 | 600.161 | 566.1335 | 538.6529 | 563.3175
4088.0354 | 419.3743 | 466.1151 | 572.9781 | 600.9766 | 566.4451 | 539.4449 | 563.8149
4089.0354 | 401.8203 | 465.9314 | 572.5153 | 600.0081 | 566.0481 | 537.978 | 562.7056
4090.0354 | 380.869 | 465.8015 | 572.2556 | 600.7197 | 566.0225 | 537.1474 | 562.7849
4091.0354 | 376.9596 | 465.8547 | 572.4044 | 601.9024 | 565.6744 | 536.0367 | 561.8686
4092.0354 | 370.4737 | 465.8694 | 572.9005 | 600.5563 | 564.4211 | 535.6183 | 561.5334
4093.0354 | 370.7874 | 465.7627 | 574.0729 | 600.0721 | 564.0192 | 537.0267 | 562.2032
4094.0354 | 370.512 | 465.5194 | 573.0318 | 600.0587 | 563.486 | 537.8224 | 562.548
4095.0354 | 367.1444 | 465.2955 | 572.7598 | 599.6084 | 563.0407 | 539.3483 | 562.4647
4096.0354 | 373.4573 | 465.2466 | 572.7784 | 599.6154 | 562.8996 | 538.589 | 562.5487
4097.0354 | 375.0018 | 465.1925 | 572.1073 | 599.4105 | 562.5633 | 538.1985 | 561.3999
4098.0354 | 365.9518 | 465.291 | 572.759 | 598.6414 | 561.8833 | 538.7812 | 561.4412
4099.0354 | 359.4609 | 465.2853 | 572.6796 | 598.4344 | 561.5014 | 539.6581 | 561.8252
4100.0354 | 370.8694 | 465.1389 | 572.9913 | 598.8405 | 560.1848 | 540.1802 | 562.4319
4101.0354 | 357.0156 | 465.1255 | 572.0258 | 599.3566 | 561.059 | 540.2403 | 561.2065
4102.0354 | 345.1645 | 464.9076 | 571.2947 | 598.7356 | 561.992 | 539.3245 | 559.5972
4103.0354 | 341.8525 | 464.8238 | 571.0223 | 599.5101 | 562.3709 | 536.9748 | 558.004
4104.0354 | 329.017 | 464.8697 | 571.2185 | 599.7726 | 561.9149 | 535.1483 | 556.8105
4105.0354 | 326.5933 | 464.7849 | 572.1638 | 599.9142 | 561.9532 | 533.4424 | 555.1266
4106.0354 | 802.1781 | 464.7216 | 571.4588 | 599.3982 | 562.135 | 533.0716 | 554.1943
4107.0354 | 392.3949 | 464.7251 | 572.1845 | 599.2631 | 561.6862 | 532.9468 | 554.2841
4108.0354 | 343.8611 | 464.5306 | 571.171 | 598.6051 | 562.0865 | 532.2595 | 555.7494
4109.0354 | 343.7506 | 464.5205 | 571.1081 | 598.0103 | 563.4042 | 532.1213 | 555.8261
4110.0354 | 782.3965 | 464.4265 | 570.875 | 598.797 | 563.6775 | 531.7329 | 554.3016
4111.0354 | 647.4296 | 464.5773 | 570.2474 | 598.6056 | 565.8236 | 532.6836 | 552.5341
4112.0354 | 355.9589 | 464.2257 | 569.9448 | 598.6351 | 566.0653 | 531.9851 | 552.6745
4113.0354 | 351.3561 | 464.2302 | 569.6687 | 597.8253 | 567.7345 | 533.1242 | 551.2519
4114.0354 | 348.1222 | 464.042 | 569.3824 | 597.6112 | 567.7619 | 532.7839 | 550.0732
4115.0354 | 342.8672 | 463.9538 | 569.3157 | 597.2028 | 567.2572 | 531.9707 | 548.8376
4116.0354 | 343.5023 | 463.797 | 569.3623 | 597.2644 | 566.7535 | 530.8783 | 547.8916
4117.0354 | 336.9567 | 463.7514 | 569.0806 | 596.9159 | 566.9115 | 531.2973 | 547.4082
4118.0354 | 337.3894 | 463.4645 | 569.2215 | 596.8564 | 566.4141 | 531.3908 | 547.0349
4119.0354 | 377.7577 | 463.4287 | 568.6972 | 596.7142 | 566.2377 | 531.3327 | 546.6695
4120.0354 | 333.265 | 463.5143 | 568.2152 | 596.7833 | 566.0507 | 530.6782 | 546.6953
4121.0354 | 326.7739 | 463.5348 | 568.6906 | 597.2197 | 565.9656 | 529.7404 | 546.4322
4122.0354 | 321.7839 | 463.3853 | 568.3466 | 596.3107 | 566.7213 | 529.6994 | 545.8492
4123.0354 | 320.4141 | 463.2275 | 567.6648 | 596.0662 | 567.9985 | 529.4661 | 545.5548
4124.0354 | 317.5301 | 463.1205 | 567.7036 | 596.1676 | 568.7006 | 529.1745 | 544.6158
4125.0354 | 311.5269 | 463.0983 | 567.2838 | 595.8925 | 568.7727 | 528.9963 | 543.5518
4126.0354 | 307.6699 | 463.0926 | 567.6001 | 596.6891 | 568.4824 | 527.6101 | 541.8912
4127.0354 | 307.3678 | 462.8895 | 567.7148 | 598.5589 | 568.4865 | 526.7799 | 540.4392
4128.0354 | 828.8204 | 462.7665 | 568.0457 | 597.7618 | 568.7225 | 527.443 | 538.9073
4129.0354 | 973.2111 | 462.7802 | 567.8828 | 597.9825 | 568.7736 | 528.5226 | 538.7639
4130.0354 | 996.2922 | 462.8313 | 569.3614 | 598.3435 | 569.0496 | 529.5612 | 538.7868
4131.0354 | 987.7174 | 462.7142 | 568.421 | 598.0213 | 568.8693 | 529.476 | 538.5287
4132.0354 | 987.647 | 462.6498 | 568.0889 | 598.245 | 568.2868 | 529.0886 | 537.327
4133.0354 | 991.8182 | 462.6707 | 568.4094 | 597.525 | 568.3755 | 530.0963 | 537.3353
4134.0354 | 997.1707 | 462.5431 | 570.4083 | 596.8455 | 567.317 | 530.3876 | 538.2912
4135.0354 | 1003.945 | 462.2733 | 569.2981 | 596.9324 | 566.2957 | 530.7891 | 539.1692
4136.0354 | 1004.6833 | 462.0471 | 568.6174 | 596.9554 | 566.2522 | 531.0635 | 539.9071
4137.0354 | 1003.9486 | 461.9735 | 568.389 | 596.7747 | 565.5079 | 530.8237 | 540.5564
4138.0354 | 1008.8063 | 462.0898 | 568.0977 | 596.8256 | 565.8458 | 531.0091 | 540.9404
4139.0354 | 1016.764 | 461.9262 | 567.4523 | 596.6689 | 565.8295 | 532.1639 | 540.4773
4140.0354 | 1034.3161 | 461.9568 | 567.1976 | 597.015 | 566.6338 | 533.0489 | 539.5262
4141.0354 | 1049.8034 | 461.7373 | 566.7169 | 596.5878 | 567.7969 | 532.9379 | 539.4481
4142.0354 | 1051.9732 | 461.7147 | 566.6322 | 597.6139 | 567.7617 | 531.4086 | 538.7366
4143.0354 | 1050.9324 | 461.7229 | 566.6422 | 597.4166 | 567.6247 | 530.3657 | 538.415
4144.0354 | 1056.363 | 461.7087 | 567.5471 | 596.5851 | 567.387 | 529.7919 | 538.9815
4145.0354 | 1047.4159 | 461.6469 | 567.4279 | 596.6668 | 567.246 | 530.7603 | 539.5198
4146.0354 | 1051.9236 | 461.4921 | 567.0987 | 597.1905 | 567.8602 | 531.5858 | 539.6474
4147.0354 | 1056.3181 | 461.2036 | 566.255 | 596.8841 | 567.3267 | 531.4955 | 538.9758
4148.0354 | 1053.1869 | 461.24 | 566.2837 | 597.1488 | 566.8255 | 530.6529 | 537.9483
4149.0354 | 1070.0202 | 461.2316 | 566.4666 | 596.3759 | 567.0605 | 530.4109 | 537.1014
4150.0354 | 1063.3701 | 461.046 | 565.9883 | 597.3981 | 566.8379 | 530.1749 | 536.1218
4151.0354 | 1079.7391 | 460.9979 | 566.1406 | 598.414 | 566.6645 | 529.0578 | 535.2796
4152.0354 | 1074.5228 | 461.0462 | 565.5573 | 598.721 | 566.9054 | 529.5008 | 534.208
4153.0354 | 1081.6607 | 460.9479 | 566.6546 | 598.5333 | 566.9133 | 529.8979 | 534.091
4154.0354 | 1041.1594 | 460.8706 | 567.3578 | 597.6584 | 567.5117 | 530.8796 | 533.9882
4155.0354 | 1061.4511 | 460.6616 | 566.6993 | 598.7529 | 567.3781 | 532.583 | 534.111
4156.0354 | 1024.1726 | 460.6683 | 566.4233 | 599.5693 | 568.0736 | 533.2844 | 534.1005
4157.0354 | 1037.167 | 460.5465 | 566.2849 | 599.6981 | 567.5439 | 532.7041 | 533.5204
4158.0354 | 960.2392 | 460.5353 | 565.9079 | 599.1855 | 567.5191 | 531.5093 | 532.6193
4159.0354 | 1034.0883 | 460.5334 | 566.2206 | 597.9799 | 566.4778 | 531.5231 | 532.6785
4160.0354 | 1045.6423 | 460.4241 | 565.8638 | 598.3942 | 565.6967 | 534.0457 | 533.6444
4161.0354 | 1026.7576 | 460.2839 | 565.3449 | 598.8758 | 565.8888 | 533.3525 | 532.8975
4162.0354 | 1070.9881 | 460.1515 | 566.1711 | 597.9126 | 566.2335 | 533.2499 | 532.401
4163.0354 | 1114.6505 | 460.0549 | 565.7917 | 597.9252 | 566.0933 | 532.9405 | 531.4435
4164.0354 | 863.9458 | 460.0456 | 565.3126 | 598.0232 | 565.6679 | 532.2143 | 531.0011
4165.0354 | 1025.4001 | 460.061 | 565.3897 | 598.6017 | 565.7121 | 533.293 | 530.7649
4166.0354 | 970.8456 | 459.7932 | 565.8275 | 598.7064 | 566.4864 | 533.9756 | 530.6771
4167.0354 | 1077.5397 | 459.6826 | 565.7014 | 599.5853 | 567.4422 | 534.5274 | 530.8227
4168.0354 | 1057.3812 | 459.7572 | 565.1231 | 599.7105 | 567.5874 | 533.4035 | 530.2794
4169.0354 | 1112.1945 | 459.6816 | 564.6841 | 598.6828 | 567.4535 | 532.5778 | 529.6287
4170.0354 | 1129.1033 | 459.6521 | 564.3966 | 599.6574 | 568.1132 | 531.9841 | 528.7324
4171.0354 | 970.5966 | 459.6603 | 564.0747 | 599.7526 | 568.177 | 530.8903 | 528.096
4172.0354 | 961.6668 | 459.5856 | 564.1768 | 600.6239 | 568.5319 | 530.7014 | 528.8422
4173.0354 | 985.326 | 459.5459 | 563.9978 | 600.2638 | 568.9801 | 530.5975 | 528.6351
4174.0354 | 1140.751 | 459.4815 | 563.3716 | 598.6381 | 569.3824 | 532.8271 | 529.2788
4175.0354 | 1153.6491 | 459.5655 | 562.9564 | 597.8523 | 571.2016 | 536.3519 | 529.936
4176.0354 | 1156.2429 | 459.3611 | 563.2017 | 597.8832 | 570.3744 | 535.9442 | 529.131
4177.0354 | 1163.6412 | 459.281 | 562.8111 | 598.0191 | 570.1402 | 537.9494 | 528.6094
4178.0354 | 998.1982 | 459.1688 | 562.5176 | 597.4745 | 570.5151 | 537.4853 | 528.6105
4179.0354 | 1069.7593 | 458.9296 | 562.1834 | 597.0948 | 571.3883 | 537.6473 | 527.9012
4180.0354 | 1075.9236 | 458.9628 | 561.9713 | 596.7862 | 570.7683 | 536.2472 | 526.5753
4181.0354 | 1070.2478 | 458.8303 | 563.1074 | 596.9355 | 569.7191 | 535.0825 | 525.618
4182.0354 | 1091.7067 | 458.8053 | 564.0955 | 597.1488 | 568.3943 | 534.1962 | 525.5941
4183.0354 | 1067.0178 | 458.7491 | 562.3574 | 598.3685 | 568.0387 | 533.4986 | 525.9127
4184.0354 | 1068.3341 | 458.561 | 561.7771 | 597.3497 | 568.1065 | 532.8579 | 525.0448
4185.0354 | 1087.1508 | 458.4718 | 561.6781 | 597.5622 | 567.2001 | 530.9029 | 523.5638
4186.0354 | 1091.3253 | 458.517 | 561.2945 | 598.1557 | 566.6476 | 530.0498 | 523.4412
4187.0354 | 1104.1955 | 458.3367 | 561.2171 | 597.4643 | 565.8561 | 528.197 | 522.3543
4188.0354 | 1110.0934 | 458.3469 | 561.2161 | 596.7389 | 565.47 | 527.5742 | 522.4149
4189.0354 | 1078.9032 | 458.3682 | 561.5254 | 596.8239 | 564.488 | 526.8117 | 521.8941
4190.0354 | 1079.7857 | 458.3348 | 560.6541 | 596.1658 | 563.9321 | 527.1083 | 522.175
4191.0354 | 1087.3409 | 458.1796 | 560.8575 | 596.3656 | 563.296 | 528.4017 | 521.862
4192.0354 | 1070.3055 | 458.1617 | 560.9887 | 596.0168 | 563.6603 | 528.8826 | 521.0018
4193.0354 | 1087.9854 | 457.9612 | 561.1513 | 595.9275 | 563.9244 | 528.5607 | 521.0644
4194.0354 | 1083.595 | 457.9463 | 560.468 | 595.8485 | 563.8773 | 528.9178 | 521.3
4195.0354 | 1095.404 | 457.9457 | 560.8043 | 595.9616 | 564.8312 | 529.6339 | 521.1793
4196.0354 | 1083.7862 | 457.9258 | 561.3471 | 596.4177 | 564.7166 | 529.1587 | 521.2804
4197.0354 | 1059.2628 | 457.8468 | 560.4825 | 596.7938 | 565.6517 | 529.5979 | 521.9969
4198.0354 | 1110.0444 | 457.6372 | 559.9223 | 596.3678 | 566.5396 | 529.559 | 522.1148
4199.0354 | 1086.4775 | 457.7333 | 559.9974 | 595.5591 | 567.4458 | 528.9663 | 522.0712
4200.0354 | 1120.0821 | 457.6146 | 560.8343 | 595.4871 | 566.4364 | 528.6729 | 520.9807
4201.0354 | 1107.8425 | 457.5869 | 560.6496 | 596.0998 | 566.4141 | 529.1906 | 521.624
4202.0354 | 1105.7634 | 457.5274 | 559.607 | 596.2433 | 566.8993 | 529.7775 | 521.0981
4203.0354 | 1124.2329 | 457.4975 | 559.2059 | 595.1043 | 567.6099 | 531.2755 | 520.3742
4204.0354 | 1106.9846 | 457.2914 | 558.8772 | 594.5791 | 568.1895 | 532.3722 | 520.6462
4205.0354 | 1088.9638 | 457.337 | 558.8634 | 594.5618 | 568.2833 | 532.8485 | 520.2317
4206.0354 | 1127.4425 | 457.2975 | 559.442 | 594.5359 | 568.0182 | 532.7757 | 519.7985
4207.0354 | 1152.4517 | 457.15 | 558.6837 | 594.2621 | 568.3797 | 533.7591 | 521.1917
4208.0354 | 1148.371 | 457.0653 | 558.7627 | 594.2648 | 568.5105 | 534.0289 | 522.6858
4209.0354 | 1151.4529 | 456.9519 | 558.2109 | 593.5414 | 568.8432 | 535.4613 | 522.8412
4210.0354 | 1157.9112 | 456.9056 | 557.778 | 593.4349 | 568.8728 | 536.2045 | 522.8409
4211.0354 | 1152.0659 | 456.8424 | 557.496 | 593.4289 | 568.883 | 535.3753 | 522.4784
4212.0354 | 1150.3933 | 456.7065 | 557.2299 | 592.991 | 567.7071 | 534.162 | 520.7761
4213.0354 | 1156.0636 | 456.6606 | 557.0125 | 592.6483 | 566.1997 | 531.9595 | 518.8747
4214.0354 | 1180.4374 | 456.5935 | 556.9083 | 593.0696 | 564.5881 | 530.222 | 518.1538
4215.0354 | 1182.4907 | 456.5286 | 557.3832 | 592.8723 | 564.2467 | 529.5172 | 517.6499
4216.0667 | 1193.4324 | 456.4266 | 556.9574 | 592.2788 | 564.6999 | 530.8657 | 518.5001
4217.0354 | 1188.422 | 456.2983 | 556.5788 | 591.9167 | 565.4096 | 534.0326 | 519.416
4218.0354 | 1190.0602 | 456.1853 | 556.2018 | 591.6266 | 566.4095 | 535.937 | 519.5419
4219.0354 | 1186.065 | 456.1682 | 556.0426 | 591.4577 | 567.4065 | 535.1157 | 519.3133
4220.0354 | 1196.2149 | 456.0609 | 556.9312 | 591.6523 | 566.1432 | 533.2222 | 518.7209
4221.0354 | 1205.7253 | 455.8574 | 556.0533 | 591.0748 | 565.4984 | 532.7627 | 518.786
4222.0354 | 1207.6753 | 455.8644 | 555.4958 | 590.6489 | 564.8695 | 533.4785 | 518.9121
4223.0354 | 1211.1624 | 455.924 | 555.3673 | 590.6096 | 564.41 | 533.6018 | 518.9351
4224.0354 | 1248.3052 | 455.8375 | 555.0196 | 590.3878 | 565.5135 | 534.1118 | 519.0509
4225.0354 | 1225.3716 | 455.9446 | 555.1131 | 590.0048 | 566.692 | 534.2824 | 518.3932
4226.0354 | 1218.4017 | 456.0155 | 554.4862 | 589.7203 | 567.1626 | 534.5393 | 518.9729
4227.0354 | 1246.6061 | 455.807 | 554.455 | 589.6512 | 566.7518 | 533.2377 | 518.1777
4228.0354 | 1248.8666 | 455.7196 | 554.0912 | 589.4664 | 566.5879 | 533.7524 | 518.3801
4229.0354 | 1246.1465 | 455.5636 | 553.7274 | 588.9646 | 567.3612 | 535.1022 | 518.5259
4230.0354 | 1247.1699 | 455.4958 | 553.9885 | 589.0917 | 566.8131 | 534.0884 | 518.4748
4231.0354 | 1249.1683 | 455.3339 | 553.4012 | 589.2451 | 566.1614 | 532.5597 | 517.608
4232.0354 | 1249.1697 | 455.3173 | 553.1315 | 588.6628 | 566.6015 | 531.9319 | 517.3318
4233.0354 | 1249.1707 | 455.2257 | 553.1726 | 588.6586 | 566.3983 | 531.1663 | 517.7939
4234.0354 | 1249.1717 | 455.2016 | 552.7962 | 589.0738 | 566.7038 | 530.9792 | 517.3845
4235.0354 | 1249.1721 | 455.1604 | 552.5963 | 589.8108 | 567.0749 | 530.0237 | 516.9976
4236.0354 | 1249.1723 | 455.1067 | 552.3146 | 589.2604 | 566.869 | 528.7335 | 517.2658
4237.0354 | 1249.1736 | 455.0092 | 552.2041 | 589.1108 | 566.7188 | 529.2454 | 516.5427
4238.0354 | 1249.1736 | 455.018 | 551.943 | 588.3451 | 566.6493 | 529.6909 | 516.4293
4239.0354 | 874.6343 | 455.0685 | 552.0338 | 588.5515 | 565.7918 | 529.0072 | 520.0935
4240.0354 | 871.4536 | 455.1013 | 555.1487 | 588.0018 | 565.3108 | 529.0455 | 521.7249
4241.0354 | 675.5169 | 454.892 | 553.377 | 587.6912 | 564.025 | 529.1574 | 525.0138
4242.0354 | 686.615 | 454.7239 | 553.3421 | 587.7483 | 562.9642 | 529.2201 | 524.9264
4243.0354 | 1061.4112 | 454.3507 | 552.8776 | 587.3695 | 562.9869 | 530.3102 | 523.0518
4244.0354 | 1045.7785 | 454.446 | 552.1654 | 587.4331 | 564.6778 | 530.7804 | 524.0899
4245.0354 | 1055.951 | 454.4108 | 552.1991 | 588.2298 | 564.866 | 529.6921 | 524.5197
4246.0354 | 1054.5921 | 454.3867 | 553.3094 | 587.3979 | 564.6294 | 529.1178 | 525.1361
4247.0354 | 1035.8889 | 454.2877 | 553.2177 | 586.7857 | 563.7302 | 529.3937 | 525.5382
4248.0354 | 1112.8283 | 454.0976 | 552.4904 | 586.9416 | 562.2506 | 528.869 | 525.0516
4249.0354 | 1037.1207 | 454.0571 | 551.7953 | 586.9286 | 561.1595 | 528.5771 | 525.7168
4250.0354 | 1000.8806 | 454.0683 | 553.0964 | 586.9792 | 560.1632 | 527.5592 | 524.999
4251.0354 | 916.0085 | 454.1304 | 553.911 | 586.4621 | 559.3475 | 526.8387 | 526.9334
4252.0354 | 1158.2505 | 453.9027 | 552.2983 | 586.0859 | 558.5787 | 526.1562 | 525.109
4253.0354 | 416.7923 | 453.7623 | 552.5075 | 586.6946 | 557.2243 | 525.3342 | 532.9505
4254.0354 | 494.9661 | 453.7138 | 552.4478 | 587.4202 | 556.4996 | 525.1577 | 531.6579
4255.0354 | 300.3608 | 453.692 | 552.4476 | 587.6891 | 556.2299 | 525.4538 | 535.8128
4256.0354 | 285.8381 | 453.6918 | 552.3834 | 587.5398 | 555.6896 | 524.7537 | 537.4956
4257.0354 | 298.1264 | 453.6564 | 552.3596 | 587.0579 | 555.3686 | 524.4617 | 538.483
4258.0354 | 279.7954 | 453.6095 | 553.3235 | 587.6235 | 555.9298 | 524.1676 | 538.7833
4259.0354 | 305.5011 | 453.4778 | 553.8399 | 587.6964 | 557.1911 | 525.4902 | 539.5005
4260.0354 | 932.7932 | 453.6185 | 553.6336 | 587.1924 | 557.3015 | 526.1346 | 532.4606
4261.0354 | 1249.1919 | 453.4599 | 553.9961 | 586.7952 | 556.5533 | 526.1366 | 528.6023
4262.0354 | 1233.4261 | 453.5035 | 554.1554 | 587.1444 | 556.6701 | 527.6409 | 530.4443
4263.0354 | 1249.1935 | 453.5006 | 554.4492 | 587.1076 | 556.2295 | 528.8432 | 530.5889
4264.0354 | 1249.1943 | 453.2844 | 554.5442 | 587.318 | 556.0975 | 529.915 | 531.7076
4265.0354 | 1249.1948 | 453.1719 | 553.8272 | 586.2973 | 556.0607 | 530.224 | 532.0368
4266.0354 | 1249.1951 | 453.1674 | 553.7646 | 585.9532 | 555.7996 | 531.1619 | 532.6414
4267.0354 | 1249.1963 | 452.9404 | 553.475 | 585.4714 | 554.9582 | 532.1034 | 533.7857
4268.0354 | 1249.1972 | 452.7918 | 553.0377 | 585.1611 | 555.1771 | 533.3366 | 533.7856
4269.0354 | 1249.1979 | 452.7749 | 552.6063 | 585.0907 | 555.14 | 533.752 | 532.8799
4270.0354 | 1249.1988 | 452.6695 | 552.5706 | 584.7272 | 554.5803 | 532.0936 | 532.0442
4271.0354 | 1249.2002 | 452.6645 | 552.232 | 584.4868 | 553.5065 | 531.0221 | 532.232
4272.0354 | 1249.2 | 452.642 | 552.152 | 584.2543 | 552.958 | 529.7433 | 532.0927
4273.0354 | 1249.2013 | 452.612 | 551.8233 | 584.2738 | 554.2422 | 528.9363 | 532.6274
4274.0354 | 1249.2012 | 452.5323 | 551.8973 | 585.0876 | 553.0609 | 527.1431 | 533.9193
4275.0354 | 1249.2026 | 452.4712 | 552.4143 | 585.1414 | 551.9675 | 526.4723 | 534.8233
4276.0354 | 1249.2029 | 452.3519 | 551.7741 | 584.3762 | 552.0519 | 526.3129 | 534.6227
4277.0354 | 1249.205 | 452.2163 | 551.8222 | 583.9628 | 551.8282 | 525.8813 | 533.176
4278.0354 | 1249.2053 | 452.0841 | 551.5397 | 583.6954 | 551.8837 | 526.2861 | 533.8602
4279.0354 | 1249.206 | 452.0844 | 551.3271 | 584.9783 | 551.5595 | 525.4359 | 533.912
4280.0354 | 1249.2063 | 451.9691 | 551.1081 | 583.5607 | 551.7904 | 525.5215 | 532.7898
4281.0354 | 1249.2066 | 452.0126 | 550.7741 | 583.2923 | 552.1612 | 525.7285 | 532.996
4282.0354 | 1249.2073 | 451.9236 | 550.7687 | 583.2837 | 551.7425 | 526.5411 | 534.5205
4283.0354 | 1249.2077 | 451.6233 | 550.4627 | 582.9868 | 551.7533 | 526.3996 | 534.8915
4284.0354 | 1249.2093 | 451.7051 | 550.6229 | 582.6109 | 551.1326 | 526.5777 | 534.7887
4285.0354 | 1249.2104 | 451.5796 | 550.6297 | 582.4825 | 551.1521 | 527.8627 | 535.026
4286.0354 | 1249.2103 | 451.6327 | 549.9388 | 582.019 | 551.8203 | 528.6913 | 533.6779
4287.0354 | 1249.2118 | 451.4894 | 549.7271 | 581.8601 | 551.8844 | 528.5671 | 533.0205
4288.0354 | 1249.2107 | 451.3551 | 549.8214 | 582.1983 | 551.4243 | 527.7929 | 533.2033
4289.0354 | 1249.2133 | 451.2259 | 549.631 | 581.8674 | 551.3956 | 527.7253 | 534.2715
4290.0354 | 1249.2131 | 451.2431 | 549.2883 | 581.7982 | 552.1474 | 526.8337 | 534.7964
4291.0354 | 1249.2148 | 451.1475 | 549.0696 | 581.6496 | 552.0326 | 526.6094 | 536.199
4292.0354 | 1249.2138 | 451.0843 | 548.8332 | 581.9527 | 551.4039 | 525.6926 | 538.3234
4293.0354 | 1249.2156 | 451.1159 | 548.939 | 581.5246 | 551.3063 | 525.7356 | 539.3804
4294.0354 | 1249.2169 | 451.0011 | 548.7132 | 581.1534 | 552.0177 | 526.0767 | 540.5931
4295.0354 | 1249.2175 | 450.9931 | 548.9867 | 582.2215 | 551.8443 | 525.2509 | 539.6837
4296.0354 | 1249.2175 | 450.8599 | 548.865 | 581.2827 | 551.7347 | 525.6059 | 540.2262
4297.0354 | 1249.2193 | 450.7286 | 548.4077 | 581.3344 | 551.1829 | 525.5837 | 540.5196
4298.0354 | 1249.2179 | 450.6196 | 548.5087 | 581.8117 | 551.1497 | 526.4196 | 539.7074
4299.0354 | 1249.2209 | 450.4189 | 548.0479 | 581.5953 | 551.7764 | 526.9614 | 538.7804
4300.0354 | 1249.2216 | 450.4153 | 548.8593 | 580.941 | 552.2696 | 526.8562 | 538.8939
4301.0354 | 1249.2211 | 450.3538 | 548.9277 | 580.8416 | 552.0088 | 526.9753 | 538.8165
4302.0354 | 1249.2226 | 450.2598 | 548.3026 | 581.9747 | 551.9056 | 527.7506 | 537.9944
4303.0354 | 1249.222 | 450.2347 | 547.9019 | 581.7925 | 552.9822 | 527.8169 | 537.5404
4304.0354 | 1249.2242 | 450.1958 | 547.5301 | 581.3376 | 553.2657 | 527.3065 | 536.0623
4305.0354 | 1249.225 | 450.2062 | 547.793 | 581.0307 | 553.5256 | 528.3027 | 535.3882
4306.0354 | 1249.2261 | 450.0277 | 547.302 | 581.0214 | 553.8392 | 529.0018 | 535.346
4307.0354 | 1249.2268 | 449.8487 | 547.8513 | 580.3509 | 553.37 | 528.3459 | 533.8784
4308.0354 | 1249.2272 | 449.8372 | 547.5698 | 580.0527 | 552.6549 | 528.62 | 532.3517
4309.0354 | 1249.2277 | 449.8241 | 547.1295 | 579.7228 | 552.4881 | 530.5166 | 532.3067
4310.0354 | 1249.228 | 449.8079 | 547.4429 | 579.645 | 551.8296 | 531.4754 | 530.9117
4311.0354 | 1249.2299 | 449.8239 | 546.8672 | 579.4928 | 551.1142 | 531.1719 | 529.4417
4312.0354 | 1249.2293 | 449.7549 | 546.8147 | 579.4887 | 550.0993 | 530.2642 | 526.6555
4313.0354 | 1249.2311 | 449.6217 | 546.7457 | 579.2599 | 549.3781 | 530.1514 | 524.7423
4314.0354 | 1249.2311 | 449.4654 | 546.2605 | 578.7314 | 549.3889 | 530.7272 | 521.9413
4315.0354 | 584.3947 | 449.4424 | 545.9737 | 578.7547 | 549.7698 | 532.144 | 522.9425
4316.0354 | 1249.2322 | 449.4284 | 545.8053 | 578.7621 | 550.2654 | 531.8735 | 518.2809
4317.0354 | 1249.2342 | 449.2684 | 545.8112 | 578.757 | 550.1526 | 530.0819 | 515.4335
4318.0354 | 1249.2342 | 449.2608 | 545.8716 | 577.9506 | 549.2177 | 528.9078 | 513.281
4319.0354 | 1249.2343 | 449.07 | 545.5383 | 577.8602 | 548.2754 | 529.3183 | 512.6046
4320.0354 | 1249.2353 | 449.1061 | 546.0542 | 578.0194 | 547.2796 | 528.7275 | 511.5016
4321.0354 | 1249.2361 | 449.1102 | 546.0536 | 578.0656 | 547.2622 | 529.291 | 510.0678
4322.0354 | 1249.237 | 449.0337 | 545.7048 | 578.903 | 548.144 | 530.1992 | 508.9211
4323.0354 | 1249.2381 | 449.0116 | 545.1315 | 579.6983 | 550.0535 | 530.4189 | 508.0212
4324.0354 | 1249.2377 | 448.98 | 545.0363 | 579.4333 | 550.5293 | 529.0016 | 507.2477
4325.0354 | 1249.2385 | 448.8596 | 546.058 | 578.8726 | 550.2879 | 527.604 | 506.5084
4326.0354 | 1249.2392 | 448.7978 | 546.6027 | 578.3221 | 549.8278 | 528.2844 | 507.2598
4327.0354 | 1249.2397 | 448.736 | 545.9377 | 578.7424 | 549.3377 | 528.3354 | 508.2983
4328.0354 | 1249.2407 | 448.6333 | 545.3343 | 578.9601 | 548.776 | 528.9157 | 507.9583
4329.0354 | 1249.2412 | 448.6445 | 545.4415 | 579.933 | 548.9914 | 528.6026 | 507.6216
4330.0354 | 1249.2418 | 448.5736 | 544.7619 | 579.6454 | 549.3017 | 529.0196 | 508.229
4331.0354 | 1249.2426 | 448.5409 | 544.5789 | 579.0221 | 550.0118 | 528.27 | 507.8828
4332.0354 | 1249.2436 | 448.4838 | 544.4099 | 578.5697 | 549.9131 | 527.1949 | 505.3307
4333.0354 | 1249.2443 | 448.4518 | 544.8682 | 578.2161 | 550.096 | 526.8059 | 504.9386
4334.0354 | 1030.4482 | 448.5675 | 545.0907 | 578.7354 | 549.6259 | 527.3882 | 505.1141
4335.0354 | 1249.2444 | 448.2421 | 544.5331 | 578.0906 | 550.7111 | 529.5017 | 504.9192
4336.0354 | 1249.2454 | 448.1657 | 544.3192 | 578.1672 | 551.0231 | 529.9305 | 505.9063
4337.0354 | 1249.2472 | 447.9991 | 544.1767 | 579.2699 | 551.5109 | 529.7184 | 504.0923
4338.0354 | 1249.2484 | 448.1009 | 544.6978 | 579.0373 | 552.288 | 528.9598 | 502.8994
4339.0354 | 1249.248 | 447.9874 | 544.2297 | 579.1436 | 552.6015 | 528.9003 | 504.3568
4340.0354 | 1249.2487 | 447.9395 | 544.8113 | 579.704 | 552.9981 | 529.4267 | 505.7542
4341.0354 | 1249.249 | 447.9634 | 544.9681 | 579.7527 | 553.4721 | 529.9271 | 507.3176
4342.0354 | 1249.2496 | 447.817 | 544.2782 | 581.9312 | 554.2722 | 530.9532 | 508.1082
4343.0354 | 1249.2511 | 447.8077 | 544.779 | 580.4555 | 555.0688 | 531.4827 | 508.2893
4344.0354 | 1249.2508 | 447.7365 | 545.4421 | 580.3482 | 555.0129 | 530.3939 | 507.3585
4345.0354 | 1249.2529 | 447.6307 | 545.39 | 580.4306 | 554.4564 | 529.1781 | 506.4568
4346.0354 | 1249.2532 | 447.5771 | 544.6983 | 580.7771 | 554.4678 | 530.0063 | 506.8025
4347.0354 | 1249.2537 | 447.5224 | 543.968 | 580.1712 | 554.5702 | 529.6674 | 506.7827
4348.0354 | 1249.2533 | 447.5069 | 543.7977 | 580.5604 | 555.0635 | 529.612 | 506.6727
4349.0354 | 1249.2562 | 447.393 | 543.9459 | 580.0029 | 555.2932 | 529.6597 | 506.0053
4350.0354 | 1249.2564 | 447.3527 | 543.7497 | 581.6381 | 555.0719 | 529.1181 | 505.8601
4351.0354 | 1249.2576 | 447.3217 | 543.8798 | 580.8928 | 555.3895 | 529.4013 | 505.613
4352.0354 | 1249.2578 | 447.223 | 543.4904 | 580.4226 | 555.269 | 530.6874 | 504.9567
4353.0354 | 1249.2578 | 447.217 | 543.2305 | 579.8184 | 555.3682 | 531.9206 | 504.6422
4354.0354 | 1249.258 | 447.1843 | 542.7962 | 579.784 | 555.6405 | 532.2669 | 504.2255
4355.0354 | 1249.2589 | 447.1316 | 542.9517 | 580.2392 | 555.4182 | 531.9871 | 503.4973
4356.0354 | 1249.2603 | 447.1064 | 543.3973 | 579.7002 | 554.6762 | 531.3669 | 502.7003
4357.0354 | 1249.2602 | 446.9236 | 543.8327 | 580.014 | 553.821 | 531.4301 | 502.7116
4358.0354 | 1249.2618 | 446.8343 | 543.0502 | 580.209 | 553.7848 | 531.6516 | 502.41
4359.0354 | 1249.2618 | 446.7824 | 543.2267 | 580.2907 | 553.9886 | 530.2693 | 501.2029
4360.0354 | 1249.2617 | 446.6885 | 542.9894 | 580.1531 | 553.6199 | 529.3179 | 500.2034
4361.0354 | 1249.2633 | 446.7347 | 543.6877 | 581.0414 | 552.7554 | 528.1147 | 499.4427
4362.0354 | 1249.2636 | 446.7388 | 544.3566 | 581.9291 | 552.9963 | 528.454 | 500.2453
4363.0354 | 1249.2643 | 446.7585 | 544.4966 | 582.731 | 554.33 | 529.604 | 501.8122
4364.0354 | 1249.2654 | 446.5888 | 544.3011 | 581.8216 | 554.3571 | 528.7143 | 501.9543
4365.0354 | 1249.2661 | 446.365 | 543.2298 | 581.6727 | 554.996 | 529.5871 | 501.3964
4366.0354 | 1249.2662 | 446.4342 | 542.6854 | 581.0989 | 554.8296 | 528.3214 | 500.5738
4367.0354 | 1249.2662 | 446.4114 | 542.5333 | 581.768 | 554.4014 | 527.2797 | 500.0679
4368.0354 | 1249.2673 | 446.3625 | 542.0823 | 580.9483 | 554.1033 | 527.5353 | 499.8692
4369.0354 | 1249.2684 | 446.3245 | 542.6218 | 580.5352 | 553.8896 | 528.8229 | 500.3138
4370.0354 | 1249.2699 | 446.2835 | 542.8111 | 580.4742 | 553.5163 | 529.6318 | 500.7374
4371.0354 | 1249.2692 | 446.2324 | 542.3431 | 580.3977 | 554.4635 | 530.524 | 501.7566
4372.0354 | 1249.2708 | 445.9692 | 542.3427 | 580.5198 | 554.0268 | 530.3884 | 501.9651
4373.0354 | 1249.2713 | 445.9638 | 541.9538 | 580.229 | 553.9952 | 530.4134 | 501.5855
4374.0354 | 1249.2712 | 445.9837 | 542.1828 | 580.8736 | 553.6885 | 529.1415 | 499.8132
4375.0354 | 1249.2729 | 445.9447 | 541.4828 | 579.9862 | 554.0449 | 528.4225 | 498.7162
4376.0354 | 1249.2733 | 445.8074 | 541.6836 | 579.5592 | 554.4473 | 529.0188 | 498.1253
4377.0354 | 1249.2738 | 445.6444 | 541.9727 | 579.7991 | 553.8826 | 528.262 | 497.4674
4378.0354 | 1249.2741 | 445.4979 | 541.4856 | 579.7467 | 553.8918 | 528.4082 | 497.3372
4379.0354 | 1249.2749 | 445.5138 | 541.919 | 579.4192 | 553.9293 | 527.3952 | 496.4052
4380.0354 | 1249.2752 | 445.5505 | 541.5053 | 579.6018 | 553.6099 | 527.7648 | 496.2142