## Test Conditions
DESIREE-FIRE Intermediate Scale Test 2 - Circuit Simulator Data Only
Test Date: | 2009-12-02
DCSim DAQ Start Time | 12:25
DCSim Time for Synchronization | 12:27
Heat Source Synchronization | 0:01 | hours:minutes:seconds
Heat Source DAQ Start Time | 12:26
Fire Time | 13:59
Offset | 1:34 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 5640 | seconds
Heat Source Offset | 1:33 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 5605 | seconds
Heat Source Stop Time | 15:40
Test Duration | 1:41 | hours:minutes:seconds
| 6060 | seconds
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
Intercable Configuration | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 5, 6, and 7 represents the air temperature 3', 5', and 7' down the cable tray located in D Position. These are labeled as "D Position - 3'", "D Position - Middle", "D Position - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds.
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | Int-Cab_VT7-T1 | Int-Cab_VT7-T2 | Int-Cab_VT7-T3 | Int-Cab_VT7-T4 | Int-Cab_VT7-T5 | Int-Cab_VT7-T6 | Int-Cab_VT7-T7 | Int-Cab_VTU-S1+a | Int-Cab_VTU-S1+b | Int-Cab_VTU-S2+a | Int-Cab_VTU-S2+b | Int-Cab_VTU-S1-a | Int-Cab_VTU-S1-b | Int-Cab_VTU-S2-a | Int-Cab_VTU-S2-b | T1-V(Batt -) | T2 -V(Batt -) | T3 - V(Batt -) | T4 - V(Batt -) | T5 - V(Batt -) | T6 - V(Batt -) | T7 - V(Batt -) | {S1+a} - V(Batt - ) | {S1+b} - V(Batt - ) | {S2+a} - V(Batt - ) | {S2+b} - V(Batt - ) | {S1-a} - V(Batt -) | {S1-b} - V(Batt - ) | {S2-a} - V(Batt - ) | {S2-b} - V(Batt - ) | {S1+a} - {S1-a} | {S1+a} - {S2-a} | {S2+a} - {S1-a} | {S2+a} - {S2-a}
-0.85938 | 121.7651 | -61.528 | 60.1135 | 0.14017 | 0.023583 | -0.012 | -0.029595 | 0.031687 | 0.085583 | -0.076452 | 59.9209 | 59.9656 | 59.9117 | 59.8835 | 61.5102 | 61.5433 | 61.294 | 61.4634 | 61.6682 | 61.5516 | 61.516 | 61.4984 | 61.5597 | 61.6136 | 61.4516 | 59.9667 | 60.0113 | 59.9575 | 59.9293 | 61.556 | 61.589 | 61.3398 | 61.5092 | -1.5893 | -1.3731 | -1.5985 | -1.3823
0.875 | 121.7743 | -61.5372 | 60.1089 | 0.14932 | 0.028162 | -0.007421 | -0.034174 | 0.027109 | 0.085583 | -0.076452 | 59.9209 | 59.961 | 59.9163 | 59.8927 | 61.5194 | 61.5524 | 61.2986 | 61.4496 | 61.6865 | 61.5653 | 61.5297 | 61.503 | 61.5643 | 61.6228 | 61.4607 | 59.9667 | 60.0068 | 59.9621 | 59.9385 | 61.5651 | 61.5982 | 61.3444 | 61.4954 | -1.5985 | -1.3777 | -1.6031 | -1.3823
2.5469 | 121.7606 | -61.6058 | 60.0311 | 0.14017 | 0.019004 | -0.012 | -0.025017 | 0.031687 | 0.085583 | -0.076452 | 59.9163 | 59.961 | 59.9072 | 59.8881 | 61.5239 | 61.5616 | 61.2894 | 61.4542 | 61.746 | 61.6248 | 61.5938 | 61.5808 | 61.6375 | 61.6914 | 61.5294 | 59.9621 | 60.0068 | 59.9529 | 59.9339 | 61.5697 | 61.6074 | 61.3352 | 61.5 | -1.6076 | -1.3731 | -1.6168 | -1.3823
4.2812 | 121.8613 | -61.5509 | 60.0174 | 0.14474 | 0.014425 | -0.007421 | -0.034174 | 0.027109 | 0.085583 | -0.076452 | 59.9209 | 59.961 | 59.9072 | 59.8881 | 61.5102 | 61.5478 | 61.2894 | 61.4588 | 61.6956 | 61.5653 | 61.5435 | 61.5167 | 61.578 | 61.6365 | 61.4745 | 59.9667 | 60.0068 | 59.9529 | 59.9339 | 61.556 | 61.5936 | 61.3352 | 61.5046 | -1.5893 | -1.3686 | -1.6031 | -1.3823
6.0156 | 121.8979 | -61.5646 | 59.9945 | 0.14932 | 0.014425 | -0.007421 | -0.038752 | 0.027109 | 0.081005 | -0.08103 | 59.93 | 59.961 | 59.9117 | 59.8927 | 61.5148 | 61.5524 | 61.2894 | 61.4542 | 61.714 | 61.5791 | 61.5572 | 61.5259 | 61.5917 | 61.6456 | 61.4836 | 59.9758 | 60.0068 | 59.9575 | 59.9385 | 61.5606 | 61.5982 | 61.3352 | 61.5 | -1.5847 | -1.3594 | -1.6031 | -1.3777
7.7031 | 121.8338 | -61.5143 | 60.0952 | 0.14017 | 0.014425 | -0.012 | -0.029595 | 0.022531 | 0.081005 | -0.067295 | 59.9163 | 59.961 | 59.9117 | 59.8881 | 61.5148 | 61.557 | 61.2986 | 61.4634 | 61.6544 | 61.5287 | 61.5023 | 61.4847 | 61.5368 | 61.5953 | 61.447 | 59.9621 | 60.0068 | 59.9575 | 59.9339 | 61.5606 | 61.6028 | 61.3444 | 61.5092 | -1.5985 | -1.3823 | -1.6031 | -1.3869
9.4375 | 121.8658 | -61.5601 | 59.9899 | 0.14474 | 0.014425 | -0.016578 | -0.029595 | 0.027109 | 0.081005 | -0.08103 | 59.9209 | 59.961 | 59.9117 | 59.8973 | 61.5148 | 61.5524 | 61.2894 | 61.4542 | 61.7048 | 61.5745 | 61.5435 | 61.5305 | 61.5872 | 61.6411 | 61.479 | 59.9667 | 60.0068 | 59.9575 | 59.943 | 61.5606 | 61.5982 | 61.3352 | 61.5 | -1.5939 | -1.3686 | -1.6031 | -1.3777
11.1094 | 121.9025 | -61.5601 | 59.9716 | 0.14932 | 0.019004 | -0.012 | -0.029595 | 0.031687 | 0.081005 | -0.071874 | 59.9255 | 59.961 | 59.9117 | 59.9018 | 61.5148 | 61.557 | 61.294 | 61.4588 | 61.7094 | 61.5791 | 61.5481 | 61.5305 | 61.5917 | 61.6411 | 61.4882 | 59.9712 | 60.0068 | 59.9575 | 59.9476 | 61.5606 | 61.6028 | 61.3398 | 61.5046 | -1.5893 | -1.3686 | -1.6031 | -1.3823
12.8594 | 121.7743 | -61.5463 | 60.1273 | 0.14474 | 0.019004 | -0.007421 | -0.029595 | 0.027109 | 0.085583 | -0.08103 | 59.9209 | 59.961 | 59.9209 | 59.8927 | 61.5239 | 61.557 | 61.2894 | 61.4588 | 61.6911 | 61.5653 | 61.5389 | 61.5167 | 61.5734 | 61.6319 | 61.4653 | 59.9667 | 60.0068 | 59.9667 | 59.9385 | 61.5697 | 61.6028 | 61.3352 | 61.5046 | -1.6031 | -1.3686 | -1.6031 | -1.3685
14.5312 | 121.8155 | -61.5463 | 60.0632 | 0.14017 | 0.023583 | -0.016578 | -0.025017 | 0.036265 | 0.085583 | -0.071874 | 59.9255 | 59.9564 | 59.9117 | 59.8881 | 61.5102 | 61.557 | 61.294 | 61.4542 | 61.6865 | 61.5699 | 61.5297 | 61.5213 | 61.5826 | 61.6319 | 61.4745 | 59.9712 | 60.0022 | 59.9575 | 59.9339 | 61.556 | 61.6028 | 61.3398 | 61.5 | -1.5847 | -1.3686 | -1.5985 | -1.3823
16.25 | 121.8475 | -61.5601 | 60.0403 | 0.14474 | 0.009846 | -0.016578 | -0.029595 | 0.031687 | 0.076426 | -0.076452 | 59.9255 | 59.961 | 59.9117 | 59.8835 | 61.5194 | 61.557 | 61.2894 | 61.4542 | 61.7048 | 61.5699 | 61.5435 | 61.5305 | 61.5917 | 61.6365 | 61.4836 | 59.9712 | 60.0068 | 59.9575 | 59.9293 | 61.5651 | 61.6028 | 61.3352 | 61.5 | -1.5939 | -1.364 | -1.6076 | -1.3777
18 | 121.9116 | -61.5143 | 60.0403 | 0.14017 | 0.014425 | -0.007421 | -0.029595 | 0.031687 | 0.076426 | -0.08103 | 59.9209 | 59.9656 | 59.9117 | 59.8835 | 61.5148 | 61.5524 | 61.294 | 61.4496 | 61.6544 | 61.5287 | 61.5069 | 61.4847 | 61.546 | 61.5907 | 61.4333 | 59.9667 | 60.0113 | 59.9575 | 59.9293 | 61.5606 | 61.5982 | 61.3398 | 61.4954 | -1.5939 | -1.3731 | -1.6031 | -1.3823
19.75 | 121.8063 | -61.5326 | 60.0815 | 0.14932 | 0.014425 | -0.012 | -0.029595 | 0.031687 | 0.081005 | -0.08103 | 59.9209 | 59.9656 | 59.9026 | 59.8835 | 61.5194 | 61.557 | 61.294 | 61.4542 | 61.6819 | 61.547 | 61.5206 | 61.503 | 61.5643 | 61.6136 | 61.4516 | 59.9667 | 60.0113 | 59.9484 | 59.9293 | 61.5651 | 61.6028 | 61.3398 | 61.5 | -1.5985 | -1.3731 | -1.6168 | -1.3914
21.4219 | 121.9025 | -61.4914 | 60.054 | 0.14474 | 0.014425 | -0.012 | -0.038752 | 0.027109 | 0.076426 | -0.076452 | 59.9209 | 59.9564 | 59.9072 | 59.8835 | 61.5148 | 61.557 | 61.2894 | 61.4634 | 61.6361 | 61.5058 | 61.4794 | 61.4526 | 61.5185 | 61.5678 | 61.4149 | 59.9667 | 60.0022 | 59.9529 | 59.9293 | 61.5606 | 61.6028 | 61.3352 | 61.5092 | -1.5939 | -1.3686 | -1.6076 | -1.3823
23.1562 | 121.7697 | -61.5234 | 60.1135 | 0.14474 | 0.019004 | -0.012 | -0.029595 | 0.031687 | 0.081005 | -0.08103 | 59.9209 | 59.961 | 59.9072 | 59.8927 | 61.5148 | 61.557 | 61.2894 | 61.4588 | 61.6682 | 61.5424 | 61.5114 | 61.4938 | 61.5551 | 61.6044 | 61.4424 | 59.9667 | 60.0068 | 59.9529 | 59.9385 | 61.5606 | 61.6028 | 61.3352 | 61.5046 | -1.5939 | -1.3686 | -1.6076 | -1.3823
24.8906 | 121.8887 | -61.5143 | 60.022 | 0.14017 | 0.014425 | -0.012 | -0.029595 | 0.031687 | 0.076426 | -0.076452 | 59.9163 | 59.961 | 59.9117 | 59.8881 | 61.5148 | 61.5478 | 61.2849 | 61.4542 | 61.6544 | 61.5287 | 61.5023 | 61.4847 | 61.546 | 61.5907 | 61.4378 | 59.9621 | 60.0068 | 59.9575 | 59.9339 | 61.5606 | 61.5936 | 61.3306 | 61.5 | -1.5985 | -1.3686 | -1.6031 | -1.3731
26.5625 | 121.8109 | -61.5189 | 60.0632 | 0.14017 | 0.009846 | -0.012 | -0.029595 | 0.031687 | 0.085583 | -0.08103 | 59.93 | 59.9656 | 59.9072 | 59.8881 | 61.5148 | 61.5524 | 61.2894 | 61.4542 | 61.659 | 61.5287 | 61.5069 | 61.4893 | 61.5505 | 61.6044 | 61.4378 | 59.9758 | 60.0113 | 59.9529 | 59.9339 | 61.5606 | 61.5982 | 61.3352 | 61.5 | -1.5847 | -1.3594 | -1.6076 | -1.3823
28.2969 | 121.7972 | -61.5326 | 60.1044 | 0.14017 | 0.009846 | -0.007421 | -0.029595 | 0.031687 | 0.085583 | -0.071874 | 59.9209 | 59.9564 | 59.9117 | 59.8927 | 61.5239 | 61.5524 | 61.2894 | 61.4542 | 61.6728 | 61.5424 | 61.5252 | 61.503 | 61.5643 | 61.6182 | 61.4607 | 59.9667 | 60.0022 | 59.9575 | 59.9385 | 61.5697 | 61.5982 | 61.3352 | 61.5 | -1.6031 | -1.3686 | -1.6122 | -1.3777
30.0469 | 121.8475 | -61.5326 | 60.0723 | 0.14474 | 0.019004 | -0.012 | -0.025017 | 0.022531 | 0.076426 | -0.067295 | 59.9255 | 59.961 | 59.9163 | 59.8881 | 61.5194 | 61.5524 | 61.2849 | 61.4542 | 61.6773 | 61.5516 | 61.5206 | 61.5076 | 61.5551 | 61.609 | 61.4653 | 59.9712 | 60.0068 | 59.9621 | 59.9339 | 61.5651 | 61.5982 | 61.3306 | 61.5 | -1.5939 | -1.3594 | -1.6031 | -1.3685
31.7344 | 121.7926 | -61.5967 | 60.0357 | 0.14474 | 0.019004 | -0.007421 | -0.034174 | 0.027109 | 0.081005 | -0.076452 | 59.9209 | 59.9656 | 59.9163 | 59.8835 | 61.5148 | 61.5478 | 61.2849 | 61.4634 | 61.7414 | 61.6157 | 61.5893 | 61.5625 | 61.6238 | 61.6777 | 61.5202 | 59.9667 | 60.0113 | 59.9621 | 59.9293 | 61.5606 | 61.5936 | 61.3306 | 61.5092 | -1.5939 | -1.364 | -1.5985 | -1.3685
33.4844 | 121.8018 | -61.5417 | 60.1044 | 0.14017 | 0.014425 | -0.016578 | -0.025017 | 0.017953 | 0.081005 | -0.071874 | 59.9346 | 59.9564 | 59.9072 | 59.8835 | 61.5194 | 61.557 | 61.294 | 61.4542 | 61.6819 | 61.5562 | 61.5252 | 61.5167 | 61.5597 | 61.6228 | 61.4699 | 59.9804 | 60.0022 | 59.9529 | 59.9293 | 61.5651 | 61.6028 | 61.3398 | 61.5 | -1.5847 | -1.3594 | -1.6122 | -1.3869
35.1562 | 121.756 | -61.615 | 60.0449 | 0.14017 | 0.009846 | -0.007421 | -0.025017 | 0.031687 | 0.090161 | -0.08103 | 59.9163 | 59.9656 | 59.9117 | 59.8881 | 61.5148 | 61.557 | 61.2849 | 61.4588 | 61.7552 | 61.6248 | 61.6076 | 61.59 | 61.6467 | 61.7052 | 61.534 | 59.9621 | 60.0113 | 59.9575 | 59.9339 | 61.5606 | 61.6028 | 61.3306 | 61.5046 | -1.5985 | -1.3686 | -1.6031 | -1.3731
36.9062 | 121.8796 | -61.5005 | 60.0952 | 0.14474 | 0.019004 | -0.012 | -0.034174 | 0.031687 | 0.081005 | -0.071874 | 59.9209 | 59.961 | 59.9117 | 59.8835 | 61.5194 | 61.557 | 61.2894 | 61.4634 | 61.6453 | 61.5196 | 61.4885 | 61.4664 | 61.5322 | 61.5816 | 61.4287 | 59.9667 | 60.0068 | 59.9575 | 59.9293 | 61.5651 | 61.6028 | 61.3352 | 61.5092 | -1.5985 | -1.3686 | -1.6076 | -1.3777
38.6406 | 121.8796 | -61.6013 | 60.0082 | 0.14474 | 0.014425 | -0.016578 | -0.029595 | 0.031687 | 0.085583 | -0.076452 | 59.9209 | 59.9656 | 59.9072 | 59.8927 | 61.5194 | 61.557 | 61.2986 | 61.4634 | 61.746 | 61.6157 | 61.5847 | 61.5717 | 61.6329 | 61.6868 | 61.5248 | 59.9667 | 60.0113 | 59.9529 | 59.9385 | 61.5651 | 61.6028 | 61.3444 | 61.5092 | -1.5985 | -1.3777 | -1.6122 | -1.3914
40.3125 | 121.8567 | -61.5646 | 60.0266 | 0.1539 | 0.019004 | -0.007421 | -0.034174 | 0.027109 | 0.081005 | -0.076452 | 59.9209 | 59.9656 | 59.9117 | 59.8927 | 61.5148 | 61.5387 | 61.2894 | 61.4542 | 61.7185 | 61.5836 | 61.5572 | 61.5305 | 61.5917 | 61.6456 | 61.4882 | 59.9667 | 60.0113 | 59.9575 | 59.9385 | 61.5606 | 61.5845 | 61.3352 | 61.5 | -1.5939 | -1.3686 | -1.6031 | -1.3777
42.0469 | 121.8979 | -61.5646 | 59.9579 | 0.14474 | 0.023583 | -0.016578 | -0.038752 | 0.031687 | 0.085583 | -0.076452 | 59.9209 | 59.9656 | 59.9072 | 59.8835 | 61.5148 | 61.5478 | 61.2894 | 61.4496 | 61.7094 | 61.5882 | 61.5481 | 61.5259 | 61.5963 | 61.6502 | 61.4882 | 59.9667 | 60.0113 | 59.9529 | 59.9293 | 61.5606 | 61.5936 | 61.3352 | 61.4954 | -1.5939 | -1.3686 | -1.6076 | -1.3823
43.7969 | 121.8521 | -61.5463 | 60.0357 | 0.14474 | 0.009846 | -0.012 | -0.029595 | 0.027109 | 0.085583 | -0.085608 | 59.9117 | 59.9701 | 59.9072 | 59.8881 | 61.5194 | 61.5524 | 61.2849 | 61.4542 | 61.6911 | 61.5562 | 61.5343 | 61.5167 | 61.5734 | 61.6319 | 61.4607 | 59.9575 | 60.0159 | 59.9529 | 59.9339 | 61.5651 | 61.5982 | 61.3306 | 61.5 | -1.6076 | -1.3731 | -1.6122 | -1.3777
45.4688 | 121.875 | -61.5738 | 59.9716 | 0.14017 | 0.009846 | -0.007421 | -0.034174 | 0.031687 | 0.076426 | -0.076452 | 59.9255 | 59.961 | 59.9117 | 59.8927 | 61.5148 | 61.5478 | 61.294 | 61.4588 | 61.714 | 61.5836 | 61.5664 | 61.5396 | 61.6055 | 61.6502 | 61.4973 | 59.9712 | 60.0068 | 59.9575 | 59.9385 | 61.5606 | 61.5936 | 61.3398 | 61.5046 | -1.5893 | -1.3686 | -1.6031 | -1.3823
47.2031 | 121.7651 | -61.6196 | 60.0494 | 0.14474 | 0.009846 | -0.012 | -0.038752 | 0.031687 | 0.071848 | -0.076452 | 59.9209 | 59.961 | 59.9072 | 59.8835 | 61.5102 | 61.5524 | 61.2849 | 61.4588 | 61.7643 | 61.6294 | 61.6076 | 61.5808 | 61.6513 | 61.6914 | 61.5431 | 59.9667 | 60.0068 | 59.9529 | 59.9293 | 61.556 | 61.5982 | 61.3306 | 61.5046 | -1.5893 | -1.364 | -1.6031 | -1.3777
48.8906 | 121.907 | -61.5051 | 60.054 | 0.14017 | 0.014425 | -0.012 | -0.029595 | 0.027109 | 0.076426 | -0.08103 | 59.9163 | 59.9656 | 59.9072 | 59.8881 | 61.5148 | 61.557 | 61.294 | 61.4588 | 61.6453 | 61.5196 | 61.4931 | 61.4755 | 61.5322 | 61.5816 | 61.4241 | 59.9621 | 60.0113 | 59.9529 | 59.9339 | 61.5606 | 61.6028 | 61.3398 | 61.5046 | -1.5985 | -1.3777 | -1.6076 | -1.3869
50.625 | 121.8704 | -61.5509 | 60.0357 | 0.14474 | 0.009846 | -0.012 | -0.029595 | 0.027109 | 0.081005 | -0.08103 | 59.9209 | 59.961 | 59.9117 | 59.8835 | 61.5148 | 61.5524 | 61.2894 | 61.4496 | 61.6956 | 61.5607 | 61.5389 | 61.5213 | 61.578 | 61.6319 | 61.4699 | 59.9667 | 60.0068 | 59.9575 | 59.9293 | 61.5606 | 61.5982 | 61.3352 | 61.4954 | -1.5939 | -1.3686 | -1.6031 | -1.3777
52.3594 | 121.9116 | -61.5234 | 60.0266 | 0.14932 | 0.019004 | -0.012 | -0.038752 | 0.027109 | 0.081005 | -0.076452 | 59.9255 | 59.961 | 59.9072 | 59.8927 | 61.5194 | 61.5524 | 61.2894 | 61.4542 | 61.6728 | 61.5424 | 61.5114 | 61.4847 | 61.5505 | 61.6044 | 61.447 | 59.9712 | 60.0068 | 59.9529 | 59.9385 | 61.5651 | 61.5982 | 61.3352 | 61.5 | -1.5939 | -1.364 | -1.6122 | -1.3823
54.0469 | 121.907 | -61.4914 | 60.0769 | 0.14474 | 0.005267 | -0.012 | -0.029595 | 0.036265 | 0.085583 | -0.076452 | 59.9209 | 59.961 | 59.9163 | 59.8835 | 61.5194 | 61.557 | 61.2849 | 61.4542 | 61.6361 | 61.4967 | 61.4794 | 61.4618 | 61.5277 | 61.577 | 61.4149 | 59.9667 | 60.0068 | 59.9621 | 59.9293 | 61.5651 | 61.6028 | 61.3306 | 61.5 | -1.5985 | -1.364 | -1.6031 | -1.3685
55.7812 | 121.7743 | -61.6104 | 60.0174 | 0.14932 | 0.009846 | -0.016578 | -0.029595 | 0.031687 | 0.081005 | -0.08103 | 59.9163 | 59.9656 | 59.9117 | 59.8881 | 61.5148 | 61.5524 | 61.2894 | 61.4542 | 61.7597 | 61.6203 | 61.5938 | 61.5808 | 61.6421 | 61.6914 | 61.5294 | 59.9621 | 60.0113 | 59.9575 | 59.9339 | 61.5606 | 61.5982 | 61.3352 | 61.5 | -1.5985 | -1.3731 | -1.6031 | -1.3777
57.4531 | 121.7834 | -61.5921 | 60.0128 | 0.14474 | 0.014425 | -0.016578 | -0.025017 | 0.031687 | 0.085583 | -0.067295 | 59.9209 | 59.961 | 59.9117 | 59.8881 | 61.5148 | 61.5524 | 61.2894 | 61.4634 | 61.7368 | 61.6065 | 61.5755 | 61.5671 | 61.6238 | 61.6777 | 61.5248 | 59.9667 | 60.0068 | 59.9575 | 59.9339 | 61.5606 | 61.5982 | 61.3352 | 61.5092 | -1.5939 | -1.3686 | -1.6031 | -1.3777
59.2031 | 121.8842 | -61.5097 | 60.0311 | 0.14932 | 0.009846 | -0.012 | -0.038752 | 0.031687 | 0.081005 | -0.071874 | 59.9163 | 59.961 | 59.9072 | 59.8835 | 61.5194 | 61.5524 | 61.2894 | 61.4542 | 61.659 | 61.5196 | 61.4977 | 61.471 | 61.5414 | 61.5907 | 61.4378 | 59.9621 | 60.0068 | 59.9529 | 59.9293 | 61.5651 | 61.5982 | 61.3352 | 61.5 | -1.6031 | -1.3731 | -1.6122 | -1.3823
60.9531 | 121.7743 | -61.5189 | 60.0998 | 0.14017 | 0.014425 | -0.012 | -0.029595 | 0.036265 | 0.076426 | -0.071874 | 59.9209 | 59.961 | 59.9072 | 59.8835 | 61.5194 | 61.5524 | 61.294 | 61.4588 | 61.659 | 61.5333 | 61.5069 | 61.4893 | 61.5551 | 61.5953 | 61.447 | 59.9667 | 60.0068 | 59.9529 | 59.9293 | 61.5651 | 61.5982 | 61.3398 | 61.5046 | -1.5985 | -1.3731 | -1.6122 | -1.3869
62.6406 | 121.788 | -61.528 | 60.0952 | 0.14017 | 0.014425 | -0.012 | -0.025017 | 0.031687 | 0.076426 | -0.08103 | 59.9209 | 59.9701 | 59.9072 | 59.8927 | 61.5148 | 61.5524 | 61.2894 | 61.4588 | 61.6682 | 61.5424 | 61.516 | 61.503 | 61.5597 | 61.6044 | 61.447 | 59.9667 | 60.0159 | 59.9529 | 59.9385 | 61.5606 | 61.5982 | 61.3352 | 61.5046 | -1.5939 | -1.3686 | -1.6076 | -1.3823
64.3906 | 121.7606 | -61.5875 | 60.0494 | 0.14932 | 0.005267 | -0.012 | -0.025017 | 0.027109 | 0.085583 | -0.076452 | 59.9163 | 59.961 | 59.9072 | 59.8835 | 61.5148 | 61.557 | 61.2757 | 61.4496 | 61.7368 | 61.5928 | 61.5755 | 61.5625 | 61.6146 | 61.6731 | 61.5111 | 59.9621 | 60.0068 | 59.9529 | 59.9293 | 61.5606 | 61.6028 | 61.3215 | 61.4954 | -1.5985 | -1.3594 | -1.6076 | -1.3685
66.0781 | 121.8018 | -61.5326 | 60.0403 | 0.14017 | 0.009846 | -0.012 | -0.025017 | 0.031687 | 0.081005 | -0.08103 | 59.9209 | 59.9656 | 59.9072 | 59.8881 | 61.5148 | 61.5478 | 61.2849 | 61.4542 | 61.6728 | 61.5424 | 61.5206 | 61.5076 | 61.5643 | 61.6136 | 61.4516 | 59.9667 | 60.0113 | 59.9529 | 59.9339 | 61.5606 | 61.5936 | 61.3306 | 61.5 | -1.5939 | -1.364 | -1.6076 | -1.3777
67.8125 | 121.8109 | -61.5601 | 60.1044 | 0.14932 | 0.014425 | -0.016578 | -0.025017 | 0.027109 | 0.076426 | -0.08103 | 59.9209 | 59.9701 | 59.9117 | 59.8927 | 61.5102 | 61.5524 | 61.2894 | 61.4634 | 61.7094 | 61.5745 | 61.5435 | 61.535 | 61.5872 | 61.6365 | 61.479 | 59.9667 | 60.0159 | 59.9575 | 59.9385 | 61.556 | 61.5982 | 61.3352 | 61.5092 | -1.5893 | -1.3686 | -1.5985 | -1.3777
69.5 | 121.8613 | -61.5601 | 60.0174 | 0.1539 | 0.019004 | -0.012 | -0.029595 | 0.027109 | 0.081005 | -0.076452 | 59.9209 | 59.961 | 59.9026 | 59.8881 | 61.5194 | 61.5524 | 61.294 | 61.4588 | 61.714 | 61.5791 | 61.5481 | 61.5305 | 61.5872 | 61.6411 | 61.4836 | 59.9667 | 60.0068 | 59.9484 | 59.9339 | 61.5651 | 61.5982 | 61.3398 | 61.5046 | -1.5985 | -1.3731 | -1.6168 | -1.3914
71.2344 | 121.8109 | -61.5555 | 60.0906 | 0.14017 | 0.014425 | -0.002842 | -0.034174 | 0.036265 | 0.085583 | -0.076452 | 59.93 | 59.961 | 59.9117 | 59.8881 | 61.5194 | 61.5616 | 61.294 | 61.4542 | 61.6956 | 61.5699 | 61.5526 | 61.5213 | 61.5917 | 61.6411 | 61.479 | 59.9758 | 60.0068 | 59.9575 | 59.9339 | 61.5651 | 61.6074 | 61.3398 | 61.5 | -1.5893 | -1.364 | -1.6076 | -1.3823
72.9062 | 121.8933 | -61.5738 | 59.9991 | 0.14474 | 0.014425 | -0.016578 | -0.029595 | 0.036265 | 0.081005 | -0.08103 | 59.9209 | 59.9656 | 59.9072 | 59.8927 | 61.5239 | 61.5524 | 61.2894 | 61.4496 | 61.7185 | 61.5882 | 61.5572 | 61.5442 | 61.6101 | 61.6548 | 61.4928 | 59.9667 | 60.0113 | 59.9529 | 59.9385 | 61.5697 | 61.5982 | 61.3352 | 61.4954 | -1.6031 | -1.3686 | -1.6168 | -1.3823
74.6562 | 121.788 | -61.5784 | 60.0403 | 0.14474 | 0.014425 | -0.021157 | -0.034174 | 0.036265 | 0.081005 | -0.076452 | 59.9209 | 59.9656 | 59.9117 | 59.879 | 61.5102 | 61.557 | 61.2849 | 61.4588 | 61.7231 | 61.5928 | 61.5572 | 61.5442 | 61.6146 | 61.6594 | 61.5019 | 59.9667 | 60.0113 | 59.9575 | 59.9247 | 61.556 | 61.6028 | 61.3306 | 61.5046 | -1.5893 | -1.364 | -1.5985 | -1.3731
76.3906 | 121.8704 | -61.5189 | 60.0677 | 0.14932 | 0.009846 | -0.012 | -0.034174 | 0.036265 | 0.076426 | -0.076452 | 59.9209 | 59.9656 | 59.9117 | 59.8835 | 61.5148 | 61.5524 | 61.2986 | 61.4542 | 61.6682 | 61.5287 | 61.5069 | 61.4847 | 61.5551 | 61.5953 | 61.4424 | 59.9667 | 60.0113 | 59.9575 | 59.9293 | 61.5606 | 61.5982 | 61.3444 | 61.5 | -1.5939 | -1.3777 | -1.6031 | -1.3869
78.125 | 121.8887 | -61.5097 | 60.0449 | 0.14932 | 0.014425 | -0.012 | -0.034174 | 0.027109 | 0.090161 | -0.08103 | 59.9209 | 59.9564 | 59.9072 | 59.8835 | 61.5148 | 61.5524 | 61.294 | 61.4542 | 61.659 | 61.5241 | 61.4977 | 61.4755 | 61.5368 | 61.5999 | 61.4287 | 59.9667 | 60.0022 | 59.9529 | 59.9293 | 61.5606 | 61.5982 | 61.3398 | 61.5 | -1.5939 | -1.3731 | -1.6076 | -1.3869
79.7969 | 121.7926 | -61.6013 | 60.0311 | 0.14932 | 0.009846 | -0.016578 | -0.034174 | 0.031687 | 0.085583 | -0.076452 | 59.9163 | 59.9656 | 59.9117 | 59.8835 | 61.5148 | 61.557 | 61.2803 | 61.4496 | 61.7506 | 61.6111 | 61.5847 | 61.5671 | 61.6329 | 61.6868 | 61.5248 | 59.9621 | 60.0113 | 59.9575 | 59.9293 | 61.5606 | 61.6028 | 61.3261 | 61.4954 | -1.5985 | -1.364 | -1.6031 | -1.3685
81.5469 | 121.7926 | -61.5692 | 60.054 | 0.13559 | 0.019004 | -0.007421 | -0.034174 | 0.022531 | 0.081005 | -0.071874 | 59.9209 | 59.961 | 59.9072 | 59.8835 | 61.5148 | 61.5524 | 61.294 | 61.4542 | 61.7048 | 61.5882 | 61.5618 | 61.535 | 61.5917 | 61.6502 | 61.4973 | 59.9667 | 60.0068 | 59.9529 | 59.9293 | 61.5606 | 61.5982 | 61.3398 | 61.5 | -1.5939 | -1.3731 | -1.6076 | -1.3869
83.2188 | 121.8475 | -61.5326 | 60.0952 | 0.14932 | 0.005267 | -0.012 | -0.025017 | 0.036265 | 0.085583 | -0.071874 | 59.9163 | 59.961 | 59.9072 | 59.879 | 61.5148 | 61.5524 | 61.2894 | 61.4542 | 61.6819 | 61.5379 | 61.5206 | 61.5076 | 61.5689 | 61.6182 | 61.4607 | 59.9621 | 60.0068 | 59.9529 | 59.9247 | 61.5606 | 61.5982 | 61.3352 | 61.5 | -1.5985 | -1.3731 | -1.6076 | -1.3823
84.9688 | 121.8658 | -61.5463 | 60.022 | 0.14474 | 0.009846 | -0.012 | -0.029595 | 0.027109 | 0.076426 | -0.085608 | 59.9209 | 59.961 | 59.9072 | 59.8835 | 61.5102 | 61.5478 | 61.2849 | 61.4542 | 61.6911 | 61.5562 | 61.5343 | 61.5167 | 61.5734 | 61.6228 | 61.4607 | 59.9667 | 60.0068 | 59.9529 | 59.9293 | 61.556 | 61.5936 | 61.3306 | 61.5 | -1.5893 | -1.364 | -1.6031 | -1.3777
86.7188 | 121.8521 | -61.5143 | 60.0952 | 0.14474 | 0.005267 | -0.016578 | -0.029595 | 0.031687 | 0.081005 | -0.076452 | 59.9117 | 59.9564 | 59.9072 | 59.8881 | 61.5148 | 61.5524 | 61.294 | 61.4542 | 61.659 | 61.5195 | 61.4977 | 61.4847 | 61.546 | 61.5953 | 61.4378 | 59.9575 | 60.0022 | 59.9529 | 59.9339 | 61.5606 | 61.5982 | 61.3398 | 61.5 | -1.6031 | -1.3823 | -1.6076 | -1.3869
88.4688 | 121.7743 | -61.6013 | 60.0266 | 0.14017 | 0.014425 | -0.007421 | -0.029595 | 0.027109 | 0.090161 | -0.085608 | 59.9255 | 59.961 | 59.9072 | 59.8927 | 61.5102 | 61.5478 | 61.2849 | 61.4496 | 61.7414 | 61.6157 | 61.5938 | 61.5717 | 61.6284 | 61.6914 | 61.5156 | 59.9712 | 60.0068 | 59.9529 | 59.9385 | 61.556 | 61.5936 | 61.3306 | 61.4954 | -1.5847 | -1.3594 | -1.6031 | -1.3777
90.2031 | 121.756 | -61.5326 | 60.1181 | 0.14017 | 0.009846 | -0.016578 | -0.034174 | 0.031687 | 0.085583 | -0.071874 | 59.9163 | 59.9518 | 59.9072 | 59.8927 | 61.5148 | 61.5524 | 61.2849 | 61.4588 | 61.6728 | 61.5424 | 61.516 | 61.4984 | 61.5643 | 61.6182 | 61.4607 | 59.9621 | 59.9976 | 59.9529 | 59.9385 | 61.5606 | 61.5982 | 61.3306 | 61.5046 | -1.5985 | -1.3686 | -1.6076 | -1.3777
91.9062 | 121.8567 | -61.5097 | 60.0952 | 0.14474 | 0.009846 | -0.007421 | -0.029595 | 0.031687 | 0.076426 | -0.071874 | 59.9209 | 59.961 | 59.898 | 59.879 | 61.5148 | 61.5524 | 61.2849 | 61.4496 | 61.6544 | 61.5196 | 61.5023 | 61.4801 | 61.5414 | 61.5861 | 61.4378 | 59.9667 | 60.0068 | 59.9438 | 59.9247 | 61.5606 | 61.5982 | 61.3306 | 61.4954 | -1.5939 | -1.364 | -1.6168 | -1.3869
93.6406 | 121.9025 | -61.5051 | 60.0403 | 0.14474 | 0.009846 | -0.007421 | -0.038752 | 0.036265 | 0.085583 | -0.08103 | 59.9209 | 59.961 | 59.9072 | 59.8881 | 61.5148 | 61.557 | 61.2894 | 61.4496 | 61.6499 | 61.515 | 61.4977 | 61.4664 | 61.5414 | 61.5907 | 61.4241 | 59.9667 | 60.0068 | 59.9529 | 59.9339 | 61.5606 | 61.6028 | 61.3352 | 61.4954 | -1.5939 | -1.3686 | -1.6076 | -1.3823
95.3125 | 121.9025 | -61.4822 | 60.054 | 0.14017 | 0.014425 | -0.016578 | -0.038752 | 0.031687 | 0.081005 | -0.076452 | 59.9163 | 59.9564 | 59.9072 | 59.8835 | 61.5194 | 61.5478 | 61.2849 | 61.4496 | 61.6224 | 61.4967 | 61.4657 | 61.4435 | 61.5139 | 61.5632 | 61.4058 | 59.9621 | 60.0022 | 59.9529 | 59.9293 | 61.5651 | 61.5936 | 61.3306 | 61.4954 | -1.6031 | -1.3686 | -1.6122 | -1.3777
97.0469 | 121.8613 | -61.5921 | 59.9854 | 0.14017 | 0.014425 | -0.012 | -0.025017 | 0.031687 | 0.081005 | -0.071874 | 59.9209 | 59.9656 | 59.9072 | 59.8835 | 61.5194 | 61.5478 | 61.2849 | 61.4542 | 61.7323 | 61.6065 | 61.5801 | 61.5671 | 61.6238 | 61.6731 | 61.5202 | 59.9667 | 60.0113 | 59.9529 | 59.9293 | 61.5651 | 61.5936 | 61.3306 | 61.5 | -1.5985 | -1.364 | -1.6122 | -1.3777
98.7969 | 121.8658 | -61.5784 | 59.9899 | 0.14932 | 0.014425 | -0.012 | -0.034174 | 0.036265 | 0.081005 | -0.076452 | 59.9255 | 59.9564 | 59.9072 | 59.8835 | 61.5148 | 61.5478 | 61.2803 | 61.4496 | 61.7277 | 61.5928 | 61.5664 | 61.5442 | 61.6146 | 61.6594 | 61.5019 | 59.9712 | 60.0022 | 59.9529 | 59.9293 | 61.5606 | 61.5936 | 61.3261 | 61.4954 | -1.5893 | -1.3548 | -1.6076 | -1.3731
100.5469 | 121.8979 | -61.5738 | 59.9579 | 0.14474 | 0.005267 | -0.016578 | -0.025017 | 0.031687 | 0.081005 | -0.08103 | 59.9117 | 59.9518 | 59.9117 | 59.8835 | 61.5194 | 61.5524 | 61.2849 | 61.4542 | 61.7185 | 61.5791 | 61.5572 | 61.5488 | 61.6055 | 61.6548 | 61.4928 | 59.9575 | 59.9976 | 59.9575 | 59.9293 | 61.5651 | 61.5982 | 61.3306 | 61.5 | -1.6076 | -1.3731 | -1.6076 | -1.3731
102.2969 | 121.8201 | -61.5417 | 60.0586 | 0.14474 | 0.009846 | -0.012 | -0.029595 | 0.040843 | 0.081005 | -0.076452 | 59.9163 | 59.961 | 59.9209 | 59.879 | 61.5148 | 61.5524 | 61.2849 | 61.4496 | 61.6865 | 61.5516 | 61.5297 | 61.5122 | 61.5826 | 61.6228 | 61.4653 | 59.9621 | 60.0068 | 59.9667 | 59.9247 | 61.5606 | 61.5982 | 61.3306 | 61.4954 | -1.5985 | -1.3686 | -1.5939 | -1.364
103.9688 | 121.843 | -61.5555 | 60.0128 | 0.14017 | 0.000689 | -0.012 | -0.034174 | 0.027109 | 0.085583 | -0.076452 | 59.9255 | 59.961 | 59.9026 | 59.8927 | 61.5194 | 61.5478 | 61.2894 | 61.4496 | 61.6956 | 61.5562 | 61.5435 | 61.5213 | 61.5826 | 61.6411 | 61.479 | 59.9712 | 60.0068 | 59.9484 | 59.9385 | 61.5651 | 61.5936 | 61.3352 | 61.4954 | -1.5939 | -1.364 | -1.6168 | -1.3869
105.7031 | 121.8613 | -61.5463 | 60.0357 | 0.14474 | 0.019004 | -0.016578 | -0.029595 | 0.027109 | 0.081005 | -0.076452 | 59.9163 | 59.9656 | 59.9072 | 59.8927 | 61.5148 | 61.5524 | 61.2894 | 61.4588 | 61.6911 | 61.5653 | 61.5297 | 61.5167 | 61.5734 | 61.6273 | 61.4699 | 59.9621 | 60.0113 | 59.9529 | 59.9385 | 61.5606 | 61.5982 | 61.3352 | 61.5046 | -1.5985 | -1.3731 | -1.6076 | -1.3823
107.375 | 121.8842 | -61.5692 | 59.9808 | 0.14017 | 0.009846 | -0.012 | -0.029595 | 0.036265 | 0.085583 | -0.071874 | 59.9209 | 59.9656 | 59.9026 | 59.8835 | 61.5148 | 61.5524 | 61.2849 | 61.4542 | 61.7094 | 61.5791 | 61.5572 | 61.5396 | 61.6055 | 61.6548 | 61.4973 | 59.9667 | 60.0113 | 59.9484 | 59.9293 | 61.5606 | 61.5982 | 61.3306 | 61.5 | -1.5939 | -1.364 | -1.6122 | -1.3823
109.125 | 121.8842 | -61.5601 | 59.9762 | 0.14932 | 0.009846 | -0.012 | -0.029595 | 0.027109 | 0.081005 | -0.076452 | 59.9209 | 59.961 | 59.9117 | 59.8927 | 61.5194 | 61.557 | 61.2803 | 61.4542 | 61.7094 | 61.5699 | 61.5481 | 61.5305 | 61.5872 | 61.6411 | 61.4836 | 59.9667 | 60.0068 | 59.9575 | 59.9385 | 61.5651 | 61.6028 | 61.3261 | 61.5 | -1.5985 | -1.3594 | -1.6076 | -1.3685
110.875 | 121.7834 | -61.5738 | 60.0311 | 0.14932 | 0.009846 | -0.007421 | -0.029595 | 0.036265 | 0.085583 | -0.071874 | 59.9209 | 59.961 | 59.9117 | 59.8881 | 61.5194 | 61.5524 | 61.2803 | 61.4496 | 61.7231 | 61.5836 | 61.5664 | 61.5442 | 61.6101 | 61.6594 | 61.5019 | 59.9667 | 60.0068 | 59.9575 | 59.9339 | 61.5651 | 61.5982 | 61.3261 | 61.4954 | -1.5985 | -1.3594 | -1.6076 | -1.3685
112.625 | 121.8796 | -61.5097 | 60.0586 | 0.14474 | 0.009846 | -0.016578 | -0.029595 | 0.031687 | 0.081005 | -0.08103 | 59.9163 | 59.961 | 59.9117 | 59.8881 | 61.5148 | 61.5433 | 61.2849 | 61.4496 | 61.6544 | 61.5196 | 61.4931 | 61.4801 | 61.5414 | 61.5907 | 61.4287 | 59.9621 | 60.0068 | 59.9575 | 59.9339 | 61.5606 | 61.589 | 61.3306 | 61.4954 | -1.5985 | -1.3686 | -1.6031 | -1.3731
114.375 | 121.7514 | -61.615 | 60.0357 | 0.14474 | 0.009846 | -0.007421 | -0.029595 | 0.031687 | 0.09474 | -0.08103 | 59.9209 | 59.961 | 59.9117 | 59.8927 | 61.5148 | 61.5524 | 61.2803 | 61.4496 | 61.7597 | 61.6248 | 61.6076 | 61.5854 | 61.6467 | 61.7097 | 61.534 | 59.9667 | 60.0068 | 59.9575 | 59.9385 | 61.5606 | 61.5982 | 61.3261 | 61.4954 | -1.5939 | -1.3594 | -1.6031 | -1.3685
116.0469 | 121.907 | -61.5738 | 59.9625 | 0.14932 | 0.009846 | -0.012 | -0.034174 | 0.027109 | 0.081005 | -0.071874 | 59.9255 | 59.9473 | 59.9163 | 59.8881 | 61.5102 | 61.5524 | 61.2849 | 61.4496 | 61.7231 | 61.5836 | 61.5618 | 61.5396 | 61.6009 | 61.6548 | 61.5019 | 59.9712 | 59.993 | 59.9621 | 59.9339 | 61.556 | 61.5982 | 61.3306 | 61.4954 | -1.5847 | -1.3594 | -1.5939 | -1.3685
117.7812 | 121.8567 | -61.5509 | 60.022 | 0.14017 | 0.005267 | -0.016578 | -0.038752 | 0.031687 | 0.090161 | -0.08103 | 59.9163 | 59.9518 | 59.9026 | 59.8881 | 61.5102 | 61.5478 | 61.2894 | 61.4496 | 61.6911 | 61.5562 | 61.5343 | 61.5122 | 61.5826 | 61.6411 | 61.4699 | 59.9621 | 59.9976 | 59.9484 | 59.9339 | 61.556 | 61.5936 | 61.3352 | 61.4954 | -1.5939 | -1.3731 | -1.6076 | -1.3869
119.5312 | 121.7743 | -61.5921 | 60.0082 | 0.13559 | 0.009846 | -0.012 | -0.029595 | 0.031687 | 0.076426 | -0.076452 | 59.9209 | 59.9656 | 59.9117 | 59.8881 | 61.5102 | 61.5524 | 61.2849 | 61.4496 | 61.7277 | 61.6019 | 61.5801 | 61.5625 | 61.6238 | 61.6685 | 61.5156 | 59.9667 | 60.0113 | 59.9575 | 59.9339 | 61.556 | 61.5982 | 61.3306 | 61.4954 | -1.5893 | -1.364 | -1.5985 | -1.3731
121.2031 | 121.8155 | -61.5509 | 60.0586 | 0.14932 | 0.009846 | -0.002842 | -0.025017 | 0.031687 | 0.081005 | -0.076452 | 59.9209 | 59.9656 | 59.9117 | 59.8881 | 61.5194 | 61.5478 | 61.2803 | 61.4542 | 61.7002 | 61.5607 | 61.5481 | 61.5259 | 61.5826 | 61.6319 | 61.4745 | 59.9667 | 60.0113 | 59.9575 | 59.9339 | 61.5651 | 61.5936 | 61.3261 | 61.5 | -1.5985 | -1.3594 | -1.6076 | -1.3685
122.9531 | 121.8155 | -61.5509 | 60.0586 | 0.14932 | 0.005267 | -0.012 | -0.025017 | 0.031687 | 0.076426 | -0.08103 | 59.9163 | 59.961 | 59.9072 | 59.8835 | 61.5148 | 61.5524 | 61.2757 | 61.4496 | 61.7002 | 61.5562 | 61.5389 | 61.5259 | 61.5826 | 61.6273 | 61.4699 | 59.9621 | 60.0068 | 59.9529 | 59.9293 | 61.5606 | 61.5982 | 61.3215 | 61.4954 | -1.5985 | -1.3594 | -1.6076 | -1.3685
124.7031 | 121.7926 | -61.5234 | 60.0952 | 0.14932 | 0.000689 | -0.012 | -0.025017 | 0.036265 | 0.081005 | -0.08103 | 59.9255 | 59.961 | 59.9117 | 59.8744 | 61.5148 | 61.5478 | 61.2894 | 61.4496 | 61.6728 | 61.5241 | 61.5114 | 61.4984 | 61.5597 | 61.6044 | 61.4424 | 59.9712 | 60.0068 | 59.9575 | 59.9201 | 61.5606 | 61.5936 | 61.3352 | 61.4954 | -1.5893 | -1.364 | -1.6031 | -1.3777
126.375 | 121.8201 | -61.5372 | 60.0403 | 0.14932 | 0.014425 | -0.007421 | -0.029595 | 0.031687 | 0.081005 | -0.076452 | 59.9209 | 59.9518 | 59.9117 | 59.8835 | 61.5102 | 61.5433 | 61.2849 | 61.4588 | 61.6865 | 61.5516 | 61.5297 | 61.5076 | 61.5689 | 61.6182 | 61.4607 | 59.9667 | 59.9976 | 59.9575 | 59.9293 | 61.556 | 61.589 | 61.3306 | 61.5046 | -1.5893 | -1.364 | -1.5985 | -1.3731
128.1094 | 121.788 | -61.5234 | 60.1318 | 0.14017 | 0.005267 | -0.007421 | -0.029595 | 0.036265 | 0.085583 | -0.076452 | 59.9209 | 59.961 | 59.9026 | 59.8835 | 61.5056 | 61.5478 | 61.2849 | 61.4496 | 61.6636 | 61.5287 | 61.516 | 61.4938 | 61.5597 | 61.609 | 61.447 | 59.9667 | 60.0068 | 59.9484 | 59.9293 | 61.5514 | 61.5936 | 61.3306 | 61.4954 | -1.5847 | -1.364 | -1.6031 | -1.3823
129.8438 | 121.7606 | -61.5875 | 60.022 | 0.14932 | 0.009846 | -0.007421 | -0.025017 | 0.036265 | 0.081005 | -0.08103 | 59.9209 | 59.9656 | 59.9163 | 59.8881 | 61.5148 | 61.5478 | 61.2803 | 61.4542 | 61.7368 | 61.5974 | 61.5801 | 61.5625 | 61.6238 | 61.6685 | 61.5065 | 59.9667 | 60.0113 | 59.9621 | 59.9339 | 61.5606 | 61.5936 | 61.3261 | 61.5 | -1.5939 | -1.3594 | -1.5985 | -1.364
131.5781 | 121.8018 | -61.5692 | 60.0677 | 0.1539 | 0.005267 | -0.012 | -0.025017 | 0.036265 | 0.085583 | -0.071874 | 59.9255 | 59.9656 | 59.9072 | 59.8881 | 61.5194 | 61.5478 | 61.2849 | 61.4542 | 61.7231 | 61.5745 | 61.5572 | 61.5442 | 61.6055 | 61.6548 | 61.4973 | 59.9712 | 60.0113 | 59.9529 | 59.9339 | 61.5651 | 61.5936 | 61.3306 | 61.5 | -1.5939 | -1.3594 | -1.6122 | -1.3777
133.3125 | 121.7834 | -61.5417 | 60.0815 | 0.14017 | 0.009846 | -0.016578 | -0.029595 | 0.031687 | 0.081005 | -0.071874 | 59.9117 | 59.9564 | 59.9026 | 59.8835 | 61.5102 | 61.5524 | 61.2849 | 61.4542 | 61.6819 | 61.5516 | 61.5252 | 61.5122 | 61.5734 | 61.6228 | 61.4699 | 59.9575 | 60.0022 | 59.9484 | 59.9293 | 61.556 | 61.5982 | 61.3306 | 61.5 | -1.5985 | -1.3731 | -1.6076 | -1.3823
135 | 121.8979 | -61.5509 | 59.9762 | 0.14932 | 0.009846 | -0.002842 | -0.029595 | 0.031687 | 0.076426 | -0.076452 | 59.9163 | 59.9701 | 59.9117 | 59.8881 | 61.5102 | 61.5433 | 61.2757 | 61.4542 | 61.7002 | 61.5607 | 61.5481 | 61.5213 | 61.5826 | 61.6273 | 61.4745 | 59.9621 | 60.0159 | 59.9575 | 59.9339 | 61.556 | 61.589 | 61.3215 | 61.5 | -1.5939 | -1.3594 | -1.5985 | -1.364
136.7344 | 121.756 | -61.6013 | 60.0357 | 0.14017 | 0.005267 | -0.007421 | -0.029595 | 0.036265 | 0.085583 | -0.071874 | 59.9255 | 59.9518 | 59.9117 | 59.879 | 61.5056 | 61.5524 | 61.2849 | 61.4496 | 61.7414 | 61.6065 | 61.5938 | 61.5717 | 61.6375 | 61.6868 | 61.5294 | 59.9712 | 59.9976 | 59.9575 | 59.9247 | 61.5514 | 61.5982 | 61.3306 | 61.4954 | -1.5802 | -1.3594 | -1.5939 | -1.3731
138.4844 | 121.756 | -61.5189 | 60.141 | 0.14474 | 0.009846 | -0.002842 | -0.029595 | 0.027109 | 0.081005 | -0.071874 | 59.9163 | 59.961 | 59.9072 | 59.8927 | 61.5148 | 61.5478 | 61.2803 | 61.4542 | 61.6636 | 61.5287 | 61.516 | 61.4893 | 61.546 | 61.5999 | 61.447 | 59.9621 | 60.0068 | 59.9529 | 59.9385 | 61.5606 | 61.5936 | 61.3261 | 61.5 | -1.5985 | -1.364 | -1.6076 | -1.3731
140.1719 | 121.9208 | -61.5692 | 59.9762 | 0.14932 | 0.009846 | -0.016578 | -0.029595 | 0.027109 | 0.076426 | -0.08103 | 59.9209 | 59.9656 | 59.9072 | 59.879 | 61.5148 | 61.5524 | 61.2894 | 61.4496 | 61.7185 | 61.5791 | 61.5526 | 61.5396 | 61.5963 | 61.6456 | 61.4882 | 59.9667 | 60.0113 | 59.9529 | 59.9247 | 61.5606 | 61.5982 | 61.3352 | 61.4954 | -1.5939 | -1.3686 | -1.6076 | -1.3823
141.9219 | 121.756 | -61.5829 | 60.0449 | 0.14474 | 0.009846 | -0.012 | -0.029595 | 0.027109 | 0.090161 | -0.071874 | 59.9255 | 59.9564 | 59.9117 | 59.8835 | 61.5194 | 61.5524 | 61.2803 | 61.4496 | 61.7277 | 61.5928 | 61.5709 | 61.5534 | 61.6101 | 61.6731 | 61.5111 | 59.9712 | 60.0022 | 59.9575 | 59.9293 | 61.5651 | 61.5982 | 61.3261 | 61.4954 | -1.5939 | -1.3548 | -1.6076 | -1.3685
143.6562 | 121.9162 | -61.5189 | 60.0403 | 0.14017 | 0.005267 | -0.007421 | -0.025017 | 0.036265 | 0.076426 | -0.090186 | 59.9117 | 59.9564 | 59.9072 | 59.879 | 61.5148 | 61.5478 | 61.2894 | 61.4496 | 61.659 | 61.5241 | 61.5114 | 61.4938 | 61.5551 | 61.5953 | 61.4287 | 59.9575 | 60.0022 | 59.9529 | 59.9247 | 61.5606 | 61.5936 | 61.3352 | 61.4954 | -1.6031 | -1.3777 | -1.6076 | -1.3823
145.3906 | 121.8979 | -61.5692 | 59.9579 | 0.14474 | 0.009846 | -0.002842 | -0.029595 | 0.027109 | 0.081005 | -0.071874 | 59.9163 | 59.961 | 59.9072 | 59.879 | 61.5148 | 61.5478 | 61.2849 | 61.4496 | 61.714 | 61.5791 | 61.5664 | 61.5396 | 61.5963 | 61.6502 | 61.4973 | 59.9621 | 60.0068 | 59.9529 | 59.9247 | 61.5606 | 61.5936 | 61.3306 | 61.4954 | -1.5985 | -1.3686 | -1.6076 | -1.3777
147.125 | 121.7789 | -61.6013 | 60.022 | 0.14474 | 0.005267 | -0.007421 | -0.029595 | 0.027109 | 0.081005 | -0.071874 | 59.9255 | 59.9564 | 59.9072 | 59.8835 | 61.5102 | 61.5478 | 61.2894 | 61.4542 | 61.746 | 61.6065 | 61.5938 | 61.5717 | 61.6284 | 61.6823 | 61.5294 | 59.9712 | 60.0022 | 59.9529 | 59.9293 | 61.556 | 61.5936 | 61.3352 | 61.5 | -1.5847 | -1.364 | -1.6031 | -1.3823
148.7969 | 121.8521 | -61.5555 | 60.0037 | 0.14474 | 0.009846 | -0.016578 | -0.029595 | 0.031687 | 0.076426 | -0.071874 | 59.93 | 59.961 | 59.9163 | 59.8881 | 61.5102 | 61.5524 | 61.2894 | 61.4542 | 61.7002 | 61.5653 | 61.5389 | 61.5259 | 61.5872 | 61.6319 | 61.4836 | 59.9758 | 60.0068 | 59.9621 | 59.9339 | 61.556 | 61.5982 | 61.3352 | 61.5 | -1.5802 | -1.3594 | -1.5939 | -1.3731
150.5469 | 121.7834 | -61.5326 | 60.0952 | 0.14474 | 0.005267 | -0.016578 | -0.029595 | 0.040843 | 0.081005 | -0.08103 | 59.9163 | 59.9564 | 59.9117 | 59.879 | 61.5148 | 61.5433 | 61.2894 | 61.4542 | 61.6773 | 61.5379 | 61.516 | 61.503 | 61.5734 | 61.6136 | 61.4516 | 59.9621 | 60.0022 | 59.9575 | 59.9247 | 61.5606 | 61.589 | 61.3352 | 61.5 | -1.5985 | -1.3731 | -1.6031 | -1.3777
152.2969 | 121.9116 | -61.5051 | 60.0449 | 0.14932 | 0.005267 | -0.012 | -0.029595 | 0.036265 | 0.076426 | -0.076452 | 59.9117 | 59.9701 | 59.9072 | 59.8744 | 61.5239 | 61.5433 | 61.2849 | 61.4634 | 61.6544 | 61.5104 | 61.4931 | 61.4755 | 61.5414 | 61.5816 | 61.4287 | 59.9575 | 60.0159 | 59.9529 | 59.9201 | 61.5697 | 61.589 | 61.3306 | 61.5092 | -1.6122 | -1.3731 | -1.6168 | -1.3777
154.0469 | 121.7651 | -61.5326 | 60.1089 | 0.14017 | -0.00389 | -0.016578 | -0.029595 | 0.031687 | 0.081005 | -0.076452 | 59.9117 | 59.9518 | 59.9072 | 59.8881 | 61.5148 | 61.5478 | 61.2849 | 61.4542 | 61.6728 | 61.5287 | 61.516 | 61.503 | 61.5643 | 61.6136 | 61.4561 | 59.9575 | 59.9976 | 59.9529 | 59.9339 | 61.5606 | 61.5936 | 61.3306 | 61.5 | -1.6031 | -1.3731 | -1.6076 | -1.3777
155.7344 | 121.8338 | -61.6013 | 59.9991 | 0.14932 | 0.009846 | -0.012 | -0.025017 | 0.036265 | 0.081005 | -0.085608 | 59.9163 | 59.961 | 59.9117 | 59.8835 | 61.5148 | 61.5433 | 61.2894 | 61.4451 | 61.7506 | 61.6111 | 61.5893 | 61.5762 | 61.6375 | 61.6823 | 61.5156 | 59.9621 | 60.0068 | 59.9575 | 59.9293 | 61.5606 | 61.589 | 61.3352 | 61.4908 | -1.5985 | -1.3731 | -1.6031 | -1.3777
157.4688 | 121.7651 | -61.5509 | 60.1227 | 0.14474 | 0.009846 | -0.007421 | -0.034174 | 0.031687 | 0.081005 | -0.08103 | 59.9163 | 59.9564 | 59.9117 | 59.8835 | 61.5056 | 61.5433 | 61.294 | 61.4496 | 61.6956 | 61.5607 | 61.5435 | 61.5167 | 61.5826 | 61.6319 | 61.4699 | 59.9621 | 60.0022 | 59.9575 | 59.9293 | 61.5514 | 61.589 | 61.3398 | 61.4954 | -1.5893 | -1.3777 | -1.5939 | -1.3823
159.1562 | 121.8155 | -61.5417 | 60.0769 | 0.14017 | 0.000689 | -0.007421 | -0.029595 | 0.031687 | 0.085583 | -0.067295 | 59.9209 | 59.9564 | 59.9117 | 59.8881 | 61.5148 | 61.557 | 61.2803 | 61.4542 | 61.6819 | 61.5424 | 61.5343 | 61.5122 | 61.5734 | 61.6273 | 61.4745 | 59.9667 | 60.0022 | 59.9575 | 59.9339 | 61.5606 | 61.6028 | 61.3261 | 61.5 | -1.5939 | -1.3594 | -1.6031 | -1.3685
160.9062 | 121.8658 | -61.5875 | 59.9945 | 0.14932 | 0.014425 | -0.002842 | -0.029595 | 0.027109 | 0.076426 | -0.076452 | 59.9255 | 59.9518 | 59.9163 | 59.8927 | 61.5102 | 61.5478 | 61.2803 | 61.4542 | 61.7368 | 61.6019 | 61.5847 | 61.5579 | 61.6146 | 61.6639 | 61.5111 | 59.9712 | 59.9976 | 59.9621 | 59.9385 | 61.556 | 61.5936 | 61.3261 | 61.5 | -1.5847 | -1.3548 | -1.5939 | -1.364
162.6562 | 121.9025 | -61.5692 | 59.967 | 0.14474 | 0.005267 | -0.012 | -0.029595 | 0.022531 | 0.081005 | -0.076452 | 59.9163 | 59.9656 | 59.9072 | 59.8835 | 61.5148 | 61.5478 | 61.2849 | 61.4496 | 61.714 | 61.5745 | 61.5572 | 61.5396 | 61.5917 | 61.6502 | 61.4928 | 59.9621 | 60.0113 | 59.9529 | 59.9293 | 61.5606 | 61.5936 | 61.3306 | 61.4954 | -1.5985 | -1.3686 | -1.6076 | -1.3777
164.3438 | 121.875 | -61.5005 | 60.0494 | 0.13559 | 0.009846 | -0.016578 | -0.038752 | 0.027109 | 0.076426 | -0.08103 | 59.9209 | 59.9656 | 59.9117 | 59.8835 | 61.5148 | 61.5478 | 61.2803 | 61.4542 | 61.6361 | 61.5104 | 61.484 | 61.4618 | 61.5277 | 61.577 | 61.4195 | 59.9667 | 60.0113 | 59.9575 | 59.9293 | 61.5606 | 61.5936 | 61.3261 | 61.5 | -1.5939 | -1.3594 | -1.6031 | -1.3685
166.0781 | 121.7651 | -61.5051 | 60.0906 | 0.14474 | 0.000689 | -0.012 | -0.025017 | 0.031687 | 0.085583 | -0.076452 | 59.9163 | 59.9656 | 59.9163 | 59.8881 | 61.5148 | 61.5478 | 61.2894 | 61.4496 | 61.6499 | 61.5058 | 61.4931 | 61.4801 | 61.5368 | 61.5907 | 61.4287 | 59.9621 | 60.0113 | 59.9621 | 59.9339 | 61.5606 | 61.5936 | 61.3352 | 61.4954 | -1.5985 | -1.3731 | -1.5985 | -1.3731
167.8125 | 121.907 | -61.5097 | 60.0357 | 0.14017 | 0.000689 | -0.021157 | -0.038752 | 0.036265 | 0.081005 | -0.08103 | 59.9209 | 59.961 | 59.9072 | 59.8835 | 61.5148 | 61.557 | 61.2894 | 61.4588 | 61.6499 | 61.5104 | 61.4885 | 61.471 | 61.546 | 61.5907 | 61.4287 | 59.9667 | 60.0068 | 59.9529 | 59.9293 | 61.5606 | 61.6028 | 61.3352 | 61.5046 | -1.5939 | -1.3686 | -1.6076 | -1.3823
169.5781 | 121.843 | -61.5875 | 59.9762 | 0.14017 | 0.000689 | -0.012 | -0.029595 | 0.036265 | 0.081005 | -0.071874 | 59.9255 | 59.9656 | 59.9117 | 59.8881 | 61.5102 | 61.5524 | 61.2803 | 61.4451 | 61.7277 | 61.5882 | 61.5755 | 61.5579 | 61.6238 | 61.6685 | 61.5157 | 59.9712 | 60.0113 | 59.9575 | 59.9339 | 61.556 | 61.5982 | 61.3261 | 61.4908 | -1.5847 | -1.3548 | -1.5985 | -1.3685
171.25 | 121.7377 | -61.5738 | 60.0449 | 0.14017 | 0.005267 | -0.007421 | -0.038752 | 0.031687 | 0.085583 | -0.071874 | 59.9117 | 59.9564 | 59.9117 | 59.8835 | 61.5148 | 61.5524 | 61.2803 | 61.4496 | 61.714 | 61.5791 | 61.5664 | 61.535 | 61.6055 | 61.6594 | 61.5019 | 59.9575 | 60.0022 | 59.9575 | 59.9293 | 61.5606 | 61.5982 | 61.3261 | 61.4954 | -1.6031 | -1.3686 | -1.6031 | -1.3685
172.9844 | 121.8338 | -61.5005 | 60.0952 | 0.14474 | -0.00389 | -0.016578 | -0.038752 | 0.031687 | 0.085583 | -0.076452 | 59.9209 | 59.9518 | 59.9072 | 59.8835 | 61.5194 | 61.5478 | 61.2894 | 61.4588 | 61.6453 | 61.4967 | 61.484 | 61.4618 | 61.5322 | 61.5861 | 61.4241 | 59.9667 | 59.9976 | 59.9529 | 59.9293 | 61.5651 | 61.5936 | 61.3352 | 61.5046 | -1.5985 | -1.3686 | -1.6122 | -1.3823
174.7344 | 121.8018 | -61.5234 | 60.0677 | 0.14474 | 0.009846 | -0.007421 | -0.025017 | 0.036265 | 0.076426 | -0.076452 | 59.9163 | 59.9564 | 59.9072 | 59.8835 | 61.5102 | 61.5433 | 61.2894 | 61.4496 | 61.6682 | 61.5333 | 61.516 | 61.4984 | 61.5597 | 61.5999 | 61.447 | 59.9621 | 60.0022 | 59.9529 | 59.9293 | 61.556 | 61.589 | 61.3352 | 61.4954 | -1.5939 | -1.3731 | -1.6031 | -1.3823
176.4688 | 121.9162 | -61.5005 | 60.054 | 0.14932 | 0.009846 | -0.007421 | -0.029595 | 0.027109 | 0.076426 | -0.067295 | 59.9163 | 59.9656 | 59.9072 | 59.8881 | 61.5148 | 61.5433 | 61.2849 | 61.4451 | 61.6499 | 61.5104 | 61.4931 | 61.471 | 61.5277 | 61.577 | 61.4333 | 59.9621 | 60.0113 | 59.9529 | 59.9339 | 61.5606 | 61.589 | 61.3306 | 61.4908 | -1.5985 | -1.3686 | -1.6076 | -1.3777
178.1406 | 121.9299 | -61.4914 | 60.0494 | 0.14474 | 0.000689 | -0.007421 | -0.025017 | 0.027109 | 0.081005 | -0.08103 | 59.9209 | 59.961 | 59.9026 | 59.8835 | 61.5102 | 61.5478 | 61.2849 | 61.4542 | 61.6361 | 61.4921 | 61.484 | 61.4664 | 61.5185 | 61.5724 | 61.4104 | 59.9667 | 60.0068 | 59.9484 | 59.9293 | 61.556 | 61.5936 | 61.3306 | 61.5 | -1.5893 | -1.364 | -1.6076 | -1.3823
179.875 | 121.7834 | -61.5417 | 60.1089 | 0.14932 | 0.000689 | -0.012 | -0.034174 | 0.027109 | 0.085583 | -0.076452 | 59.9255 | 59.961 | 59.9117 | 59.8881 | 61.5056 | 61.5524 | 61.2849 | 61.4496 | 61.6911 | 61.5424 | 61.5297 | 61.5076 | 61.5689 | 61.6273 | 61.4653 | 59.9712 | 60.0068 | 59.9575 | 59.9339 | 61.5514 | 61.5982 | 61.3306 | 61.4954 | -1.5802 | -1.3594 | -1.5939 | -1.3731
181.6094 | 121.8155 | -61.5738 | 60.0586 | 0.14474 | 0.005267 | -0.007421 | -0.025017 | 0.027109 | 0.085583 | -0.076452 | 59.9209 | 59.961 | 59.9117 | 59.8835 | 61.5194 | 61.557 | 61.2849 | 61.4496 | 61.7185 | 61.5791 | 61.5664 | 61.5488 | 61.6009 | 61.6594 | 61.4973 | 59.9667 | 60.0068 | 59.9575 | 59.9293 | 61.5651 | 61.6028 | 61.3306 | 61.4954 | -1.5985 | -1.364 | -1.6076 | -1.3731
183.3438 | 121.9025 | -61.5738 | 59.967 | 0.14474 | -0.00389 | -0.012 | -0.029595 | 0.031687 | 0.090161 | -0.076452 | 59.9209 | 59.9656 | 59.9117 | 59.8881 | 61.5148 | 61.5478 | 61.2803 | 61.4542 | 61.7185 | 61.5699 | 61.5618 | 61.5442 | 61.6055 | 61.664 | 61.4973 | 59.9667 | 60.0113 | 59.9575 | 59.9339 | 61.5606 | 61.5936 | 61.3261 | 61.5 | -1.5939 | -1.3594 | -1.6031 | -1.3685
185.0312 | 121.8018 | -61.5463 | 60.0632 | 0.14474 | 0.005267 | -0.007421 | -0.034174 | 0.022531 | 0.090161 | -0.076452 | 59.9209 | 59.9518 | 59.9117 | 59.8835 | 61.5102 | 61.5524 | 61.2803 | 61.4405 | 61.6911 | 61.5516 | 61.5389 | 61.5122 | 61.5689 | 61.6365 | 61.4699 | 59.9667 | 59.9976 | 59.9575 | 59.9293 | 61.556 | 61.5982 | 61.3261 | 61.4863 | -1.5893 | -1.3594 | -1.5985 | -1.3685
186.7656 | 121.875 | -61.5646 | 59.9945 | 0.14932 | 0.005267 | -0.012 | -0.025017 | 0.031687 | 0.085583 | -0.085608 | 59.9163 | 59.961 | 59.9026 | 59.8835 | 61.5148 | 61.5524 | 61.2803 | 61.4496 | 61.714 | 61.5699 | 61.5526 | 61.5396 | 61.5963 | 61.6502 | 61.479 | 59.9621 | 60.0068 | 59.9484 | 59.9293 | 61.5606 | 61.5982 | 61.3261 | 61.4954 | -1.5985 | -1.364 | -1.6122 | -1.3777
188.4375 | 121.9025 | -61.4639 | 60.0494 | 0.14474 | -0.00389 | -0.012 | -0.034174 | 0.031687 | 0.081005 | -0.076452 | 59.9163 | 59.961 | 59.9117 | 59.8835 | 61.5148 | 61.5478 | 61.2894 | 61.4496 | 61.6087 | 61.46 | 61.4519 | 61.4298 | 61.4956 | 61.5449 | 61.3875 | 59.9621 | 60.0068 | 59.9575 | 59.9293 | 61.5606 | 61.5936 | 61.3352 | 61.4954 | -1.5985 | -1.3731 | -1.6031 | -1.3777
190.1719 | 121.8155 | -61.5097 | 60.0815 | 0.14932 | 0.000689 | -0.007421 | -0.025017 | 0.027109 | 0.076426 | -0.076452 | 59.9163 | 59.9564 | 59.9026 | 59.879 | 61.5102 | 61.5478 | 61.2894 | 61.4451 | 61.659 | 61.5104 | 61.5023 | 61.4847 | 61.5368 | 61.5861 | 61.4333 | 59.9621 | 60.0022 | 59.9484 | 59.9247 | 61.556 | 61.5936 | 61.3352 | 61.4908 | -1.5939 | -1.3731 | -1.6076 | -1.3869
191.9062 | 121.7743 | -61.5326 | 60.0952 | 0.14017 | -0.00389 | -0.016578 | -0.020438 | 0.027109 | 0.085583 | -0.076452 | 59.9117 | 59.961 | 59.9117 | 59.8927 | 61.5056 | 61.5387 | 61.2849 | 61.4451 | 61.6728 | 61.5287 | 61.516 | 61.5122 | 61.5597 | 61.6182 | 61.4561 | 59.9575 | 60.0068 | 59.9575 | 59.9385 | 61.5514 | 61.5845 | 61.3306 | 61.4908 | -1.5939 | -1.3731 | -1.5939 | -1.3731
193.5781 | 121.7651 | -61.5967 | 60.0449 | 0.14474 | 0.005267 | -0.007421 | -0.034174 | 0.031687 | 0.085583 | -0.076452 | 59.9255 | 59.9564 | 59.9117 | 59.8927 | 61.5102 | 61.5524 | 61.2803 | 61.4496 | 61.7414 | 61.6019 | 61.5893 | 61.5625 | 61.6284 | 61.6823 | 61.5202 | 59.9712 | 60.0022 | 59.9575 | 59.9385 | 61.556 | 61.5982 | 61.3261 | 61.4954 | -1.5847 | -1.3548 | -1.5985 | -1.3685
195.3281 | 121.8796 | -61.5738 | 59.9716 | 0.14474 | 0.000689 | -0.016578 | -0.034174 | 0.031687 | 0.085583 | -0.076452 | 59.9117 | 59.9518 | 59.9117 | 59.879 | 61.5194 | 61.5433 | 61.2803 | 61.4451 | 61.7185 | 61.5745 | 61.5572 | 61.5396 | 61.6055 | 61.6594 | 61.4973 | 59.9575 | 59.9976 | 59.9575 | 59.9247 | 61.5651 | 61.589 | 61.3261 | 61.4908 | -1.6076 | -1.3686 | -1.6076 | -1.3685
197.0156 | 121.7606 | -61.615 | 60.0266 | 0.14474 | -0.00389 | -0.012 | -0.034174 | 0.031687 | 0.085583 | -0.071874 | 59.9163 | 59.9518 | 59.9117 | 59.8835 | 61.5148 | 61.5433 | 61.2849 | 61.4496 | 61.7597 | 61.6111 | 61.603 | 61.5808 | 61.6467 | 61.7006 | 61.5431 | 59.9621 | 59.9976 | 59.9575 | 59.9293 | 61.5606 | 61.589 | 61.3306 | 61.4954 | -1.5985 | -1.3686 | -1.6031 | -1.3731
198.75 | 121.7834 | -61.5417 | 60.1364 | 0.14474 | -0.00389 | -0.007421 | -0.025017 | 0.027109 | 0.085583 | -0.076452 | 59.9209 | 59.961 | 59.9117 | 59.879 | 61.5102 | 61.5524 | 61.2803 | 61.4542 | 61.6865 | 61.5379 | 61.5343 | 61.5167 | 61.5689 | 61.6273 | 61.4653 | 59.9667 | 60.0068 | 59.9575 | 59.9247 | 61.556 | 61.5982 | 61.3261 | 61.5 | -1.5893 | -1.3594 | -1.5985 | -1.3685
200.4375 | 121.8842 | -61.5143 | 60.0449 | 0.14932 | -0.00389 | -0.016578 | -0.034174 | 0.027109 | 0.085583 | -0.08103 | 59.9163 | 59.9564 | 59.9072 | 59.8881 | 61.5102 | 61.5478 | 61.2711 | 61.4451 | 61.6636 | 61.5104 | 61.4977 | 61.4801 | 61.5414 | 61.5999 | 61.4333 | 59.9621 | 60.0022 | 59.9529 | 59.9339 | 61.556 | 61.5936 | 61.3169 | 61.4908 | -1.5939 | -1.3548 | -1.6031 | -1.364
202.1719 | 121.8887 | -61.5189 | 60.0311 | 0.14017 | 0.000689 | -0.016578 | -0.029595 | 0.027109 | 0.085583 | -0.08103 | 59.9117 | 59.9564 | 59.9117 | 59.8835 | 61.5194 | 61.5478 | 61.2849 | 61.4451 | 61.659 | 61.5195 | 61.5023 | 61.4893 | 61.546 | 61.6044 | 61.4378 | 59.9575 | 60.0022 | 59.9575 | 59.9293 | 61.5651 | 61.5936 | 61.3306 | 61.4908 | -1.6076 | -1.3731 | -1.6076 | -1.3731
203.9062 | 121.8933 | -61.5646 | 59.9808 | 0.1539 | -0.00389 | -0.012 | -0.029595 | 0.031687 | 0.085583 | -0.076452 | 59.9209 | 59.9564 | 59.9072 | 59.8835 | 61.5056 | 61.5524 | 61.2803 | 61.4496 | 61.7185 | 61.5607 | 61.5526 | 61.535 | 61.5963 | 61.6502 | 61.4882 | 59.9667 | 60.0022 | 59.9529 | 59.9293 | 61.5514 | 61.5982 | 61.3261 | 61.4954 | -1.5847 | -1.3594 | -1.5985 | -1.3731
205.5938 | 121.8796 | -61.5005 | 60.0906 | 0.14474 | -0.00389 | -0.012 | -0.025017 | 0.036265 | 0.085583 | -0.08103 | 59.9255 | 59.9564 | 59.9072 | 59.8835 | 61.5102 | 61.5433 | 61.2849 | 61.4542 | 61.6453 | 61.4967 | 61.4885 | 61.4755 | 61.5368 | 61.5861 | 61.4195 | 59.9712 | 60.0022 | 59.9529 | 59.9293 | 61.556 | 61.589 | 61.3306 | 61.5 | -1.5847 | -1.3594 | -1.6031 | -1.3777
207.3281 | 121.756 | -61.6013 | 60.0403 | 0.14932 | 0.000689 | -0.007421 | -0.029595 | 0.031687 | 0.085583 | -0.08103 | 59.9117 | 59.961 | 59.9117 | 59.8927 | 61.5102 | 61.5524 | 61.2757 | 61.4405 | 61.7506 | 61.6019 | 61.5938 | 61.5717 | 61.6329 | 61.6868 | 61.5202 | 59.9575 | 60.0068 | 59.9575 | 59.9385 | 61.556 | 61.5982 | 61.3215 | 61.4863 | -1.5985 | -1.364 | -1.5985 | -1.364
209.0625 | 121.9162 | -61.5005 | 60.0357 | 0.14474 | -0.00389 | -0.002842 | -0.034174 | 0.027109 | 0.085583 | -0.076452 | 59.9117 | 59.9518 | 59.9072 | 59.8835 | 61.5148 | 61.5433 | 61.2894 | 61.4496 | 61.6453 | 61.4967 | 61.4977 | 61.4664 | 61.5277 | 61.5861 | 61.4241 | 59.9575 | 59.9976 | 59.9529 | 59.9293 | 61.5606 | 61.589 | 61.3352 | 61.4954 | -1.6031 | -1.3777 | -1.6076 | -1.3823
210.8125 | 121.9116 | -61.496 | 60.0449 | 0.14474 | -0.00389 | -0.012 | -0.029595 | 0.031687 | 0.076426 | -0.08103 | 59.9163 | 59.9564 | 59.9072 | 59.8881 | 61.5148 | 61.5433 | 61.2849 | 61.4542 | 61.6407 | 61.4921 | 61.484 | 61.4664 | 61.5277 | 61.5724 | 61.4149 | 59.9621 | 60.0022 | 59.9529 | 59.9339 | 61.5606 | 61.589 | 61.3306 | 61.5 | -1.5985 | -1.3686 | -1.6076 | -1.3777
212.4844 | 121.7651 | -61.5234 | 60.1044 | 0.14474 | -0.00389 | -0.007421 | -0.029595 | 0.036265 | 0.085583 | -0.076452 | 59.9209 | 59.9564 | 59.9163 | 59.8881 | 61.5102 | 61.5433 | 61.2849 | 61.4496 | 61.6682 | 61.5195 | 61.516 | 61.4938 | 61.5597 | 61.609 | 61.447 | 59.9667 | 60.0022 | 59.9621 | 59.9339 | 61.556 | 61.589 | 61.3306 | 61.4954 | -1.5893 | -1.364 | -1.5939 | -1.3685
214.2188 | 121.8063 | -61.5143 | 60.0403 | 0.14017 | -0.00389 | -0.016578 | -0.025017 | 0.031687 | 0.085583 | -0.08103 | 59.9209 | 59.9564 | 59.9117 | 59.8835 | 61.5056 | 61.5478 | 61.2757 | 61.4542 | 61.6544 | 61.5104 | 61.4977 | 61.4893 | 61.546 | 61.5999 | 61.4333 | 59.9667 | 60.0022 | 59.9575 | 59.9293 | 61.5514 | 61.5936 | 61.3215 | 61.5 | -1.5847 | -1.3548 | -1.5939 | -1.364
215.9062 | 121.8613 | -61.528 | 60.0174 | 0.14474 | -0.008469 | -0.021157 | -0.029595 | 0.031687 | 0.081005 | -0.076452 | 59.9117 | 59.9564 | 59.9072 | 59.879 | 61.5148 | 61.5478 | 61.2803 | 61.4542 | 61.6728 | 61.5195 | 61.5069 | 61.4984 | 61.5597 | 61.609 | 61.4516 | 59.9575 | 60.0022 | 59.9529 | 59.9247 | 61.5606 | 61.5936 | 61.3261 | 61.5 | -1.6031 | -1.3686 | -1.6076 | -1.3731
217.6562 | 121.8475 | -61.5372 | 60.0174 | 0.14932 | -0.00389 | -0.012 | -0.029595 | 0.031687 | 0.081005 | -0.076452 | 59.9255 | 59.961 | 59.9117 | 59.879 | 61.5102 | 61.5478 | 61.2803 | 61.4542 | 61.6865 | 61.5333 | 61.5252 | 61.5076 | 61.5689 | 61.6182 | 61.4607 | 59.9712 | 60.0068 | 59.9575 | 59.9247 | 61.556 | 61.5936 | 61.3261 | 61.5 | -1.5847 | -1.3548 | -1.5985 | -1.3685
219.4062 | 121.8796 | -61.5555 | 59.9854 | 0.14932 | -0.00389 | -0.016578 | -0.034174 | 0.040843 | 0.085583 | -0.076452 | 59.9209 | 59.961 | 59.9026 | 59.8835 | 61.5194 | 61.5524 | 61.2803 | 61.4496 | 61.7048 | 61.5516 | 61.5389 | 61.5213 | 61.5963 | 61.6411 | 61.479 | 59.9667 | 60.0068 | 59.9484 | 59.9293 | 61.5651 | 61.5982 | 61.3261 | 61.4954 | -1.5985 | -1.3594 | -1.6168 | -1.3777
221.1719 | 121.7651 | -61.5921 | 60.0037 | 0.14474 | -0.00389 | -0.021157 | -0.029595 | 0.031687 | 0.085583 | -0.071874 | 59.9163 | 59.961 | 59.9072 | 59.8881 | 61.5148 | 61.5433 | 61.2757 | 61.4542 | 61.7368 | 61.5882 | 61.5709 | 61.5625 | 61.6238 | 61.6777 | 61.5202 | 59.9621 | 60.0068 | 59.9529 | 59.9339 | 61.5606 | 61.589 | 61.3215 | 61.5 | -1.5985 | -1.3594 | -1.6076 | -1.3685
222.8906 | 121.7606 | -61.5097 | 60.1044 | 0.14474 | -0.00389 | -0.021157 | -0.029595 | 0.027109 | 0.085583 | -0.08103 | 59.9163 | 59.961 | 59.9117 | 59.8835 | 61.5148 | 61.5524 | 61.2757 | 61.4496 | 61.6544 | 61.5058 | 61.4885 | 61.4801 | 61.5368 | 61.5953 | 61.4287 | 59.9621 | 60.0068 | 59.9575 | 59.9293 | 61.5606 | 61.5982 | 61.3215 | 61.4954 | -1.5985 | -1.3594 | -1.6031 | -1.364
224.5625 | 121.7468 | -61.528 | 60.1135 | 0.14017 | -0.00389 | -0.012 | -0.038752 | 0.027109 | 0.085583 | -0.076452 | 59.9255 | 59.961 | 59.9117 | 59.8835 | 61.5148 | 61.5478 | 61.2849 | 61.4451 | 61.6682 | 61.5241 | 61.516 | 61.4893 | 61.5551 | 61.6136 | 61.4516 | 59.9712 | 60.0068 | 59.9575 | 59.9293 | 61.5606 | 61.5936 | 61.3306 | 61.4908 | -1.5893 | -1.3594 | -1.6031 | -1.3731
226.2969 | 121.8613 | -61.5601 | 59.9716 | 0.14474 | -0.008469 | -0.012 | -0.034174 | 0.036265 | 0.085583 | -0.071874 | 59.9163 | 59.961 | 59.9117 | 59.8835 | 61.5102 | 61.5478 | 61.2803 | 61.4542 | 61.7048 | 61.5516 | 61.5481 | 61.5259 | 61.5963 | 61.6456 | 61.4882 | 59.9621 | 60.0068 | 59.9575 | 59.9293 | 61.556 | 61.5936 | 61.3261 | 61.5 | -1.5939 | -1.364 | -1.5985 | -1.3685
227.9688 | 121.8658 | -61.4822 | 60.0677 | 0.14474 | 0.005267 | -0.012 | -0.034174 | 0.031687 | 0.085583 | -0.08103 | 59.9209 | 59.9656 | 59.9026 | 59.879 | 61.5148 | 61.5478 | 61.2849 | 61.4496 | 61.627 | 61.4875 | 61.4702 | 61.4481 | 61.5139 | 61.5678 | 61.4012 | 59.9667 | 60.0113 | 59.9484 | 59.9247 | 61.5606 | 61.5936 | 61.3306 | 61.4954 | -1.5939 | -1.364 | -1.6122 | -1.3823
229.6562 | 121.756 | -61.5784 | 60.0494 | 0.14932 | -0.00389 | -0.007421 | -0.029595 | 0.031687 | 0.09474 | -0.08103 | 59.9209 | 59.9564 | 59.898 | 59.8881 | 61.5194 | 61.5433 | 61.2711 | 61.4542 | 61.7277 | 61.5745 | 61.5709 | 61.5488 | 61.6101 | 61.6731 | 61.4973 | 59.9667 | 60.0022 | 59.9438 | 59.9339 | 61.5651 | 61.589 | 61.3169 | 61.5 | -1.5985 | -1.3502 | -1.6214 | -1.3731
231.3281 | 121.788 | -61.528 | 60.1135 | 0.14932 | 0.000689 | -0.012 | -0.025017 | 0.027109 | 0.090161 | -0.085608 | 59.9163 | 59.961 | 59.9117 | 59.879 | 61.5194 | 61.5433 | 61.2849 | 61.4496 | 61.6773 | 61.5287 | 61.516 | 61.503 | 61.5551 | 61.6182 | 61.4424 | 59.9621 | 60.0068 | 59.9575 | 59.9247 | 61.5651 | 61.589 | 61.3306 | 61.4954 | -1.6031 | -1.3686 | -1.6076 | -1.3731
233.0625 | 121.8155 | -61.5372 | 60.0632 | 0.14474 | -0.00389 | -0.012 | -0.029595 | 0.022531 | 0.099318 | -0.071874 | 59.9163 | 59.961 | 59.9117 | 59.8744 | 61.5056 | 61.5524 | 61.2757 | 61.4542 | 61.6819 | 61.5333 | 61.5252 | 61.5076 | 61.5597 | 61.6365 | 61.4653 | 59.9621 | 60.0068 | 59.9575 | 59.9201 | 61.5514 | 61.5982 | 61.3215 | 61.5 | -1.5893 | -1.3594 | -1.5939 | -1.364
234.75 | 121.8063 | -61.5555 | 60.054 | 0.14474 | 0.005267 | -0.012 | -0.020438 | 0.027109 | 0.090161 | -0.076452 | 59.9255 | 59.961 | 59.9026 | 59.8835 | 61.5194 | 61.5524 | 61.2849 | 61.4496 | 61.7002 | 61.5607 | 61.5435 | 61.535 | 61.5826 | 61.6456 | 61.479 | 59.9712 | 60.0068 | 59.9484 | 59.9293 | 61.5651 | 61.5982 | 61.3306 | 61.4954 | -1.5939 | -1.3594 | -1.6168 | -1.3823
236.4219 | 121.7514 | -61.5829 | 60.0449 | 0.14932 | 0.005267 | -0.012 | -0.034174 | 0.027109 | 0.09474 | -0.076452 | 59.9209 | 59.961 | 59.9072 | 59.879 | 61.5102 | 61.5433 | 61.2757 | 61.4451 | 61.7323 | 61.5882 | 61.5709 | 61.5488 | 61.6101 | 61.6777 | 61.5065 | 59.9667 | 60.0068 | 59.9529 | 59.9247 | 61.556 | 61.589 | 61.3215 | 61.4908 | -1.5893 | -1.3548 | -1.6031 | -1.3685
238.0938 | 121.8704 | -61.5555 | 59.9808 | 0.14474 | 0.000689 | -0.016578 | -0.034174 | 0.036265 | 0.090161 | -0.076452 | 59.9163 | 59.9518 | 59.9072 | 59.8881 | 61.5148 | 61.5478 | 61.2803 | 61.4542 | 61.7002 | 61.5562 | 61.5389 | 61.5213 | 61.5917 | 61.6456 | 61.479 | 59.9621 | 59.9976 | 59.9529 | 59.9339 | 61.5606 | 61.5936 | 61.3261 | 61.5 | -1.5985 | -1.364 | -1.6076 | -1.3731
239.7656 | 121.8521 | -61.5738 | 59.9854 | 0.14474 | -0.008469 | -0.012 | -0.029595 | 0.040843 | 0.09474 | -0.071874 | 59.9209 | 59.9564 | 59.9072 | 59.8881 | 61.5056 | 61.5433 | 61.2803 | 61.4542 | 61.7185 | 61.5653 | 61.5618 | 61.5442 | 61.6146 | 61.6685 | 61.5019 | 59.9667 | 60.0022 | 59.9529 | 59.9339 | 61.5514 | 61.589 | 61.3261 | 61.5 | -1.5847 | -1.3594 | -1.5985 | -1.3731
241.4375 | 121.7743 | -61.615 | 60.0357 | 0.14932 | -0.00389 | -0.007421 | -0.025017 | 0.031687 | 0.090161 | -0.076452 | 59.9209 | 59.961 | 59.9117 | 59.8835 | 61.5148 | 61.5387 | 61.2803 | 61.4542 | 61.7643 | 61.6111 | 61.6076 | 61.59 | 61.6467 | 61.7052 | 61.5385 | 59.9667 | 60.0068 | 59.9575 | 59.9293 | 61.5606 | 61.5845 | 61.3261 | 61.5 | -1.5939 | -1.3594 | -1.6031 | -1.3685
243.1406 | 121.7651 | -61.615 | 60.0357 | 0.14474 | -0.00389 | -0.002842 | -0.034174 | 0.036265 | 0.085583 | -0.085608 | 59.9209 | 59.9564 | 59.9117 | 59.879 | 61.5148 | 61.5387 | 61.2803 | 61.4496 | 61.7597 | 61.6111 | 61.6121 | 61.5808 | 61.6513 | 61.7006 | 61.5294 | 59.9667 | 60.0022 | 59.9575 | 59.9247 | 61.5606 | 61.5845 | 61.3261 | 61.4954 | -1.5939 | -1.3594 | -1.6031 | -1.3685
244.8594 | 121.8109 | -61.5509 | 60.0815 | 0.14932 | 0.000689 | -0.012 | -0.038752 | 0.031687 | 0.090161 | -0.071874 | 59.9163 | 59.9564 | 59.9117 | 59.879 | 61.5148 | 61.5433 | 61.2757 | 61.4542 | 61.7002 | 61.5516 | 61.5389 | 61.5122 | 61.5826 | 61.6411 | 61.479 | 59.9621 | 60.0022 | 59.9575 | 59.9247 | 61.5606 | 61.589 | 61.3215 | 61.5 | -1.5985 | -1.3594 | -1.6031 | -1.364
246.5469 | 121.7743 | -61.5784 | 60.0266 | 0.1539 | 0.000689 | -0.012 | -0.029595 | 0.036265 | 0.090161 | -0.076452 | 59.9255 | 59.9656 | 59.9072 | 59.8835 | 61.5102 | 61.5387 | 61.2757 | 61.4496 | 61.7323 | 61.5791 | 61.5664 | 61.5488 | 61.6146 | 61.6685 | 61.5019 | 59.9712 | 60.0113 | 59.9529 | 59.9293 | 61.556 | 61.5845 | 61.3215 | 61.4954 | -1.5847 | -1.3502 | -1.6031 | -1.3685
248.25 | 121.7926 | -61.5509 | 60.0586 | 0.14474 | -0.00389 | -0.021157 | -0.029595 | 0.027109 | 0.090161 | -0.08103 | 59.9072 | 59.961 | 59.9117 | 59.8835 | 61.5102 | 61.5478 | 61.2757 | 61.4542 | 61.6956 | 61.547 | 61.5297 | 61.5213 | 61.578 | 61.6411 | 61.4699 | 59.9529 | 60.0068 | 59.9575 | 59.9293 | 61.556 | 61.5936 | 61.3215 | 61.5 | -1.6031 | -1.3686 | -1.5985 | -1.364
249.9688 | 121.7789 | -61.5875 | 60.0357 | 0.14017 | 0.005267 | -0.007421 | -0.038752 | 0.031687 | 0.090161 | -0.08103 | 59.9209 | 59.9564 | 59.9072 | 59.8835 | 61.5102 | 61.5478 | 61.2757 | 61.4542 | 61.7277 | 61.5928 | 61.5801 | 61.5488 | 61.6192 | 61.6777 | 61.5065 | 59.9667 | 60.0022 | 59.9529 | 59.9293 | 61.556 | 61.5936 | 61.3215 | 61.5 | -1.5893 | -1.3548 | -1.6031 | -1.3685
251.6719 | 121.9025 | -61.5189 | 60.0494 | 0.14474 | 0.000689 | -0.012 | -0.025017 | 0.036265 | 0.090161 | -0.076452 | 59.9117 | 59.9518 | 59.9072 | 59.8881 | 61.5102 | 61.5433 | 61.2757 | 61.4542 | 61.6636 | 61.5195 | 61.5069 | 61.4938 | 61.5551 | 61.609 | 61.4424 | 59.9575 | 59.9976 | 59.9529 | 59.9339 | 61.556 | 61.589 | 61.3215 | 61.5 | -1.5985 | -1.364 | -1.6031 | -1.3685
253.3438 | 121.875 | -61.4685 | 60.0723 | 0.14017 | 0.009846 | -0.012 | -0.034174 | 0.027109 | 0.085583 | -0.076452 | 59.9026 | 59.961 | 59.9026 | 59.8835 | 61.5102 | 61.5433 | 61.2803 | 61.4542 | 61.6087 | 61.4784 | 61.4565 | 61.4343 | 61.4956 | 61.5541 | 61.3921 | 59.9484 | 60.0068 | 59.9484 | 59.9293 | 61.556 | 61.589 | 61.3261 | 61.5 | -1.6076 | -1.3777 | -1.6076 | -1.3777
255.0156 | 121.8063 | -61.5417 | 60.0586 | 0.14017 | 0.005267 | -0.007421 | -0.025017 | 0.031687 | 0.099318 | -0.076452 | 59.9209 | 59.961 | 59.9117 | 59.8881 | 61.5194 | 61.5478 | 61.2803 | 61.4496 | 61.6819 | 61.547 | 61.5343 | 61.5167 | 61.5734 | 61.6411 | 61.4653 | 59.9667 | 60.0068 | 59.9575 | 59.9339 | 61.5651 | 61.5936 | 61.3261 | 61.4954 | -1.5985 | -1.3594 | -1.6076 | -1.3685
256.7344 | 121.8475 | -61.4914 | 60.0723 | 0.14474 | 0.000689 | -0.016578 | -0.034174 | 0.036265 | 0.085583 | -0.071874 | 59.9209 | 59.961 | 59.9072 | 59.8835 | 61.5102 | 61.5387 | 61.2849 | 61.4496 | 61.6361 | 61.4921 | 61.4748 | 61.4572 | 61.5277 | 61.577 | 61.4195 | 59.9667 | 60.0068 | 59.9529 | 59.9293 | 61.556 | 61.5845 | 61.3306 | 61.4954 | -1.5893 | -1.364 | -1.6031 | -1.3777
258.4531 | 121.8109 | -61.5372 | 60.0449 | 0.14932 | 0.000689 | -0.016578 | -0.034174 | 0.027109 | 0.09474 | -0.076452 | 59.9255 | 59.961 | 59.9163 | 59.879 | 61.5102 | 61.5387 | 61.2803 | 61.4496 | 61.6865 | 61.5379 | 61.5206 | 61.503 | 61.5643 | 61.6319 | 61.4607 | 59.9712 | 60.0068 | 59.9621 | 59.9247 | 61.556 | 61.5845 | 61.3261 | 61.4954 | -1.5847 | -1.3548 | -1.5939 | -1.364
260.1406 | 121.8979 | -61.4914 | 60.0494 | 0.14932 | 0.000689 | -0.021157 | -0.038752 | 0.040843 | 0.085583 | -0.090186 | 59.9163 | 59.9564 | 59.9072 | 59.8835 | 61.5148 | 61.5478 | 61.2849 | 61.4451 | 61.6407 | 61.4921 | 61.4702 | 61.4526 | 61.5322 | 61.577 | 61.4012 | 59.9621 | 60.0022 | 59.9529 | 59.9293 | 61.5606 | 61.5936 | 61.3306 | 61.4908 | -1.5985 | -1.3686 | -1.6076 | -1.3777
261.8281 | 121.7743 | -61.5829 | 59.9899 | 0.14932 | 0.000689 | -0.012 | -0.020438 | 0.031687 | 0.085583 | -0.067295 | 59.9163 | 59.961 | 59.9072 | 59.8835 | 61.5102 | 61.5524 | 61.2803 | 61.4496 | 61.7323 | 61.5836 | 61.5709 | 61.5625 | 61.6146 | 61.6685 | 61.5157 | 59.9621 | 60.0068 | 59.9529 | 59.9293 | 61.556 | 61.5982 | 61.3261 | 61.4954 | -1.5939 | -1.364 | -1.6031 | -1.3731
263.5156 | 121.8842 | -61.5738 | 59.9579 | 0.14932 | 0.000689 | -0.012 | -0.034174 | 0.036265 | 0.09474 | -0.076452 | 59.9209 | 59.961 | 59.9117 | 59.8835 | 61.5148 | 61.5387 | 61.2711 | 61.4451 | 61.7231 | 61.5745 | 61.5618 | 61.5396 | 61.6101 | 61.6685 | 61.4973 | 59.9667 | 60.0068 | 59.9575 | 59.9293 | 61.5606 | 61.5845 | 61.3169 | 61.4908 | -1.5939 | -1.3502 | -1.6031 | -1.3594
265.1875 | 121.7834 | -61.5921 | 59.9991 | 0.14474 | 0.005267 | -0.012 | -0.038752 | 0.036265 | 0.09474 | -0.085608 | 59.9209 | 59.961 | 59.9026 | 59.8835 | 61.5056 | 61.5478 | 61.2803 | 61.4496 | 61.7368 | 61.5974 | 61.5801 | 61.5533 | 61.6284 | 61.6868 | 61.5065 | 59.9667 | 60.0068 | 59.9484 | 59.9293 | 61.5514 | 61.5936 | 61.3261 | 61.4954 | -1.5847 | -1.3594 | -1.6031 | -1.3777
266.875 | 121.8521 | -61.5051 | 60.0677 | 0.14017 | 0.000689 | -0.016578 | -0.029595 | 0.031687 | 0.081005 | -0.071874 | 59.9209 | 59.9564 | 59.9117 | 59.879 | 61.5148 | 61.5387 | 61.2849 | 61.4496 | 61.6453 | 61.5058 | 61.4885 | 61.4755 | 61.5368 | 61.5861 | 61.4333 | 59.9667 | 60.0022 | 59.9575 | 59.9247 | 61.5606 | 61.5845 | 61.3306 | 61.4954 | -1.5939 | -1.364 | -1.6031 | -1.3731
268.5781 | 121.8842 | -61.5097 | 60.0632 | 0.13559 | -0.00389 | -0.016578 | -0.025017 | 0.022531 | 0.085583 | -0.08103 | 59.9163 | 59.961 | 59.9117 | 59.8835 | 61.5148 | 61.5433 | 61.2803 | 61.4542 | 61.6453 | 61.5058 | 61.4931 | 61.4847 | 61.5322 | 61.5953 | 61.4287 | 59.9621 | 60.0068 | 59.9575 | 59.9293 | 61.5606 | 61.589 | 61.3261 | 61.5 | -1.5985 | -1.364 | -1.6031 | -1.3685
270.3125 | 121.7743 | -61.5692 | 60.0082 | 0.14017 | 0.005267 | 0.001736 | -0.025017 | 0.027109 | 0.090161 | -0.076452 | 59.9209 | 59.961 | 59.9163 | 59.8881 | 61.5148 | 61.5433 | 61.2757 | 61.4496 | 61.7094 | 61.5745 | 61.571 | 61.5442 | 61.5963 | 61.6594 | 61.4928 | 59.9667 | 60.0068 | 59.9621 | 59.9339 | 61.5606 | 61.589 | 61.3215 | 61.4954 | -1.5939 | -1.3548 | -1.5985 | -1.3594
272 | 121.8933 | -61.5509 | 59.9808 | 0.14932 | 0.000689 | -0.012 | -0.029595 | 0.027109 | 0.081005 | -0.076452 | 59.9163 | 59.9564 | 59.9072 | 59.8835 | 61.5148 | 61.5433 | 61.2757 | 61.4542 | 61.7002 | 61.5516 | 61.5389 | 61.5213 | 61.578 | 61.6319 | 61.4745 | 59.9621 | 60.0022 | 59.9529 | 59.9293 | 61.5606 | 61.589 | 61.3215 | 61.5 | -1.5985 | -1.3594 | -1.6076 | -1.3685
273.6875 | 121.8521 | -61.5372 | 60.022 | 0.14474 | 0.009846 | -0.007421 | -0.025017 | 0.027109 | 0.085583 | -0.08103 | 59.9163 | 59.9564 | 59.9072 | 59.8835 | 61.5148 | 61.5433 | 61.2894 | 61.4496 | 61.6819 | 61.547 | 61.5297 | 61.5122 | 61.5643 | 61.6228 | 61.4561 | 59.9621 | 60.0022 | 59.9529 | 59.9293 | 61.5606 | 61.589 | 61.3352 | 61.4954 | -1.5985 | -1.3731 | -1.6076 | -1.3823
275.4531 | 121.8155 | -61.5005 | 60.0815 | 0.14474 | 0.005267 | -0.016578 | -0.029595 | 0.027109 | 0.090161 | -0.071874 | 59.9117 | 59.9518 | 59.898 | 59.8881 | 61.5056 | 61.5478 | 61.2803 | 61.4496 | 61.6453 | 61.5058 | 61.484 | 61.471 | 61.5277 | 61.5907 | 61.4287 | 59.9575 | 59.9976 | 59.9438 | 59.9339 | 61.5514 | 61.5936 | 61.3261 | 61.4954 | -1.5939 | -1.3686 | -1.6076 | -1.3823
277.1406 | 121.7606 | -61.5875 | 60.0174 | 0.14017 | 0.014425 | -0.007421 | -0.025017 | 0.031687 | 0.09474 | -0.067295 | 59.9163 | 59.9564 | 59.9117 | 59.8744 | 61.5148 | 61.5478 | 61.2803 | 61.4451 | 61.7277 | 61.6019 | 61.5801 | 61.5625 | 61.6192 | 61.6823 | 61.5202 | 59.9621 | 60.0022 | 59.9575 | 59.9201 | 61.5606 | 61.5936 | 61.3261 | 61.4908 | -1.5985 | -1.364 | -1.6031 | -1.3685
278.8594 | 121.8567 | -61.5234 | 60.0174 | 0.14474 | 0.005267 | -0.016578 | -0.029595 | 0.036265 | 0.090161 | -0.08103 | 59.9163 | 59.9518 | 59.9072 | 59.879 | 61.5148 | 61.5478 | 61.2757 | 61.4451 | 61.6682 | 61.5287 | 61.5069 | 61.4938 | 61.5597 | 61.6136 | 61.4424 | 59.9621 | 59.9976 | 59.9529 | 59.9247 | 61.5606 | 61.5936 | 61.3215 | 61.4908 | -1.5985 | -1.3594 | -1.6076 | -1.3685
280.5469 | 121.7697 | -61.5601 | 60.0494 | 0.14017 | 0.009846 | -0.007421 | -0.029595 | 0.031687 | 0.090161 | -0.071874 | 59.9117 | 59.961 | 59.9117 | 59.8744 | 61.5102 | 61.5433 | 61.2803 | 61.4451 | 61.7002 | 61.5699 | 61.5526 | 61.5305 | 61.5917 | 61.6502 | 61.4882 | 59.9575 | 60.0068 | 59.9575 | 59.9201 | 61.556 | 61.589 | 61.3261 | 61.4908 | -1.5985 | -1.3686 | -1.5985 | -1.3685
282.3281 | 121.7468 | -61.5921 | 60.0311 | 0.14932 | 0.009846 | -0.012 | -0.029595 | 0.027109 | 0.090161 | -0.076452 | 59.9163 | 59.9518 | 59.9026 | 59.879 | 61.5102 | 61.5433 | 61.2711 | 61.4496 | 61.7414 | 61.6019 | 61.5801 | 61.5625 | 61.6192 | 61.6823 | 61.5156 | 59.9621 | 59.9976 | 59.9484 | 59.9247 | 61.556 | 61.589 | 61.3169 | 61.4954 | -1.5939 | -1.3548 | -1.6076 | -1.3685
284.0312 | 121.7606 | -61.6013 | 60.0357 | 0.14932 | 0.014425 | -0.012 | -0.029595 | 0.031687 | 0.085583 | -0.08103 | 59.9255 | 59.9656 | 59.9117 | 59.8835 | 61.5102 | 61.5478 | 61.2803 | 61.4451 | 61.7506 | 61.6157 | 61.5893 | 61.5717 | 61.6329 | 61.6868 | 61.5202 | 59.9712 | 60.0113 | 59.9575 | 59.9293 | 61.556 | 61.5936 | 61.3261 | 61.4908 | -1.5847 | -1.3548 | -1.5985 | -1.3685
285.7031 | 121.7422 | -61.5875 | 60.0494 | 0.14932 | 0.009846 | -0.007421 | -0.034174 | 0.031687 | 0.09474 | -0.076452 | 59.9163 | 59.9564 | 59.9117 | 59.879 | 61.5102 | 61.5478 | 61.2757 | 61.4405 | 61.7368 | 61.5974 | 61.5801 | 61.5534 | 61.6192 | 61.6823 | 61.5111 | 59.9621 | 60.0022 | 59.9575 | 59.9247 | 61.556 | 61.5936 | 61.3215 | 61.4863 | -1.5939 | -1.3594 | -1.5985 | -1.364
287.4062 | 121.756 | -61.5189 | 60.1089 | 0.14474 | 0.014425 | -0.012 | -0.025017 | 0.031687 | 0.090161 | -0.071874 | 59.9117 | 59.9564 | 59.9072 | 59.8835 | 61.5148 | 61.5478 | 61.2803 | 61.4542 | 61.6636 | 61.5333 | 61.5069 | 61.4938 | 61.5505 | 61.609 | 61.447 | 59.9575 | 60.0022 | 59.9529 | 59.9293 | 61.5606 | 61.5936 | 61.3261 | 61.5 | -1.6031 | -1.3686 | -1.6076 | -1.3731
289.125 | 121.788 | -61.5509 | 60.0266 | 0.14474 | 0.014425 | -0.007421 | -0.034174 | 0.036265 | 0.09474 | -0.071874 | 59.9209 | 59.9518 | 59.9117 | 59.879 | 61.5102 | 61.5387 | 61.2711 | 61.4496 | 61.6956 | 61.5653 | 61.5435 | 61.5167 | 61.5872 | 61.6456 | 61.479 | 59.9667 | 59.9976 | 59.9575 | 59.9247 | 61.556 | 61.5845 | 61.3169 | 61.4954 | -1.5893 | -1.3502 | -1.5985 | -1.3594
290.8281 | 121.8887 | -61.4685 | 60.0494 | 0.14017 | 0.005267 | -0.021157 | -0.029595 | 0.027109 | 0.085583 | -0.071874 | 59.9209 | 59.961 | 59.9072 | 59.879 | 61.5148 | 61.5478 | 61.2803 | 61.4451 | 61.6087 | 61.4738 | 61.4473 | 61.4389 | 61.4956 | 61.5541 | 61.3966 | 59.9667 | 60.0068 | 59.9529 | 59.9247 | 61.5606 | 61.5936 | 61.3261 | 61.4908 | -1.5939 | -1.3594 | -1.6076 | -1.3731
292.5156 | 121.7331 | -61.6013 | 60.0266 | 0.14474 | 0.014425 | -0.016578 | -0.029595 | 0.036265 | 0.09474 | -0.08103 | 59.9163 | 59.9564 | 59.9117 | 59.8881 | 61.5056 | 61.5433 | 61.2757 | 61.4451 | 61.746 | 61.6157 | 61.5847 | 61.5717 | 61.6375 | 61.696 | 61.5202 | 59.9621 | 60.0022 | 59.9575 | 59.9339 | 61.5514 | 61.589 | 61.3215 | 61.4908 | -1.5893 | -1.3594 | -1.5939 | -1.364
294.2031 | 121.8887 | -61.5784 | 59.967 | 0.14932 | 0.005267 | -0.012 | -0.034174 | 0.040843 | 0.090161 | -0.076452 | 59.9255 | 59.9564 | 59.9072 | 59.879 | 61.5194 | 61.5524 | 61.2757 | 61.4451 | 61.7277 | 61.5836 | 61.5664 | 61.5442 | 61.6192 | 61.6685 | 61.5019 | 59.9712 | 60.0022 | 59.9529 | 59.9247 | 61.5651 | 61.5982 | 61.3215 | 61.4908 | -1.5939 | -1.3502 | -1.6122 | -1.3685
295.9062 | 121.8979 | -61.5005 | 60.0586 | 0.14932 | 0.014425 | -0.012 | -0.029595 | 0.031687 | 0.085583 | -0.08103 | 59.9255 | 59.961 | 59.9117 | 59.879 | 61.5102 | 61.5478 | 61.2803 | 61.4496 | 61.6499 | 61.515 | 61.4885 | 61.471 | 61.5322 | 61.5861 | 61.4195 | 59.9712 | 60.0068 | 59.9575 | 59.9247 | 61.556 | 61.5936 | 61.3261 | 61.4954 | -1.5847 | -1.3548 | -1.5985 | -1.3685
297.6094 | 121.8933 | -61.5005 | 60.054 | 0.14474 | 0.005267 | -0.016578 | -0.025017 | 0.031687 | 0.081005 | -0.08103 | 59.9163 | 59.961 | 59.9117 | 59.8835 | 61.5102 | 61.5433 | 61.2849 | 61.4496 | 61.6453 | 61.5058 | 61.484 | 61.4755 | 61.5322 | 61.5816 | 61.4195 | 59.9621 | 60.0068 | 59.9575 | 59.9293 | 61.556 | 61.589 | 61.3306 | 61.4954 | -1.5939 | -1.3686 | -1.5985 | -1.3731
299.3438 | 121.7697 | -61.5463 | 60.0494 | 0.14932 | 0.014425 | -0.016578 | -0.020438 | 0.031687 | 0.09474 | -0.071874 | 59.9209 | 59.9564 | 59.9026 | 59.879 | 61.5194 | 61.5478 | 61.2849 | 61.4496 | 61.6956 | 61.5608 | 61.5297 | 61.5259 | 61.578 | 61.6411 | 61.4745 | 59.9667 | 60.0022 | 59.9484 | 59.9247 | 61.5651 | 61.5936 | 61.3306 | 61.4954 | -1.5985 | -1.364 | -1.6168 | -1.3823
301.0312 | 121.7972 | -61.5005 | 60.0861 | 0.13559 | 0.014425 | -0.007421 | -0.029595 | 0.031687 | 0.09474 | -0.076452 | 59.9163 | 59.9564 | 59.9117 | 59.879 | 61.5148 | 61.5433 | 61.2849 | 61.4542 | 61.6361 | 61.515 | 61.4931 | 61.471 | 61.5322 | 61.5953 | 61.4241 | 59.9621 | 60.0022 | 59.9575 | 59.9247 | 61.5606 | 61.589 | 61.3306 | 61.5 | -1.5985 | -1.3686 | -1.6031 | -1.3731
302.7344 | 121.7514 | -61.5646 | 60.0174 | 0.14474 | 0.009846 | -0.007421 | -0.025017 | 0.036265 | 0.090161 | -0.076452 | 59.9163 | 59.961 | 59.9072 | 59.8835 | 61.5194 | 61.5433 | 61.2803 | 61.4451 | 61.7094 | 61.5745 | 61.5572 | 61.5396 | 61.6009 | 61.6548 | 61.4882 | 59.9621 | 60.0068 | 59.9529 | 59.9293 | 61.5651 | 61.589 | 61.3261 | 61.4908 | -1.6031 | -1.364 | -1.6122 | -1.3731
304.4219 | 121.8201 | -61.5097 | 60.0815 | 0.14017 | 0.014425 | -0.002842 | -0.025017 | 0.031687 | 0.090161 | -0.076452 | 59.9163 | 59.9564 | 59.9117 | 59.879 | 61.5102 | 61.5387 | 61.2803 | 61.4451 | 61.6499 | 61.5241 | 61.5069 | 61.4847 | 61.5414 | 61.5999 | 61.4333 | 59.9621 | 60.0022 | 59.9575 | 59.9247 | 61.556 | 61.5845 | 61.3261 | 61.4908 | -1.5939 | -1.364 | -1.5985 | -1.3685
306.125 | 121.875 | -61.5509 | 59.9625 | 0.14017 | 0.000689 | -0.007421 | -0.034174 | 0.031687 | 0.090161 | -0.076452 | 59.9163 | 59.9564 | 59.9072 | 59.8927 | 61.5148 | 61.5433 | 61.2803 | 61.4451 | 61.6911 | 61.5516 | 61.5435 | 61.5167 | 61.5826 | 61.6411 | 61.4745 | 59.9621 | 60.0022 | 59.9529 | 59.9385 | 61.5606 | 61.589 | 61.3261 | 61.4908 | -1.5985 | -1.364 | -1.6076 | -1.3731
307.8281 | 121.8109 | -61.5372 | 60.0586 | 0.14932 | 0.014425 | -0.007421 | -0.029595 | 0.040843 | 0.09474 | -0.071874 | 59.9209 | 59.9518 | 59.9117 | 59.8835 | 61.5056 | 61.5341 | 61.2757 | 61.4451 | 61.6865 | 61.5516 | 61.5297 | 61.5076 | 61.578 | 61.6319 | 61.4653 | 59.9667 | 59.9976 | 59.9575 | 59.9293 | 61.5514 | 61.5799 | 61.3215 | 61.4908 | -1.5847 | -1.3548 | -1.5939 | -1.364
309.5312 | 121.8842 | -61.496 | 60.0449 | 0.14017 | 0.000689 | -0.016578 | -0.029595 | 0.040843 | 0.090161 | -0.08103 | 59.9163 | 59.9564 | 59.9072 | 59.8835 | 61.5102 | 61.5433 | 61.2849 | 61.4405 | 61.6361 | 61.4967 | 61.4794 | 61.4664 | 61.5368 | 61.5861 | 61.4149 | 59.9621 | 60.0022 | 59.9529 | 59.9293 | 61.556 | 61.589 | 61.3306 | 61.4863 | -1.5939 | -1.3686 | -1.6031 | -1.3777
311.2031 | 121.7468 | -61.5189 | 60.1135 | 0.14474 | 0.005267 | -0.012 | -0.029595 | 0.031687 | 0.09474 | -0.076452 | 59.9163 | 59.9518 | 59.9209 | 59.8835 | 61.5148 | 61.5433 | 61.2849 | 61.4496 | 61.6636 | 61.5241 | 61.5069 | 61.4893 | 61.5505 | 61.6136 | 61.4424 | 59.9621 | 59.9976 | 59.9667 | 59.9293 | 61.5606 | 61.589 | 61.3306 | 61.4954 | -1.5985 | -1.3686 | -1.5939 | -1.364
312.875 | 121.8796 | -61.5555 | 59.9899 | 0.14474 | 0.019004 | -0.007421 | -0.029595 | 0.031687 | 0.09474 | -0.076452 | 59.9209 | 59.9564 | 59.9117 | 59.8835 | 61.5148 | 61.5478 | 61.2757 | 61.4451 | 61.7002 | 61.5745 | 61.5481 | 61.5259 | 61.5872 | 61.6502 | 61.479 | 59.9667 | 60.0022 | 59.9575 | 59.9293 | 61.5606 | 61.5936 | 61.3215 | 61.4908 | -1.5939 | -1.3548 | -1.6031 | -1.364
314.5625 | 121.8246 | -61.5326 | 60.0082 | 0.14474 | 0.009846 | -0.016578 | -0.025017 | 0.027109 | 0.090161 | -0.08103 | 59.9209 | 59.9564 | 59.9117 | 59.879 | 61.5102 | 61.5387 | 61.2757 | 61.4496 | 61.6773 | 61.5424 | 61.516 | 61.5076 | 61.5597 | 61.6228 | 61.4516 | 59.9667 | 60.0022 | 59.9575 | 59.9247 | 61.556 | 61.5845 | 61.3215 | 61.4954 | -1.5893 | -1.3548 | -1.5985 | -1.364
316.2969 | 121.8246 | -61.5738 | 59.9945 | 0.14474 | 0.014425 | -0.016578 | -0.029595 | 0.036265 | 0.090161 | -0.076452 | 59.9117 | 59.9518 | 59.9117 | 59.8835 | 61.5194 | 61.5387 | 61.2711 | 61.4496 | 61.7185 | 61.5882 | 61.5572 | 61.5442 | 61.6101 | 61.664 | 61.4973 | 59.9575 | 59.9976 | 59.9575 | 59.9293 | 61.5651 | 61.5845 | 61.3169 | 61.4954 | -1.6076 | -1.3594 | -1.6076 | -1.3594
317.9844 | 121.8887 | -61.5509 | 59.9487 | 0.14932 | 0.005267 | -0.012 | -0.029595 | 0.036265 | 0.085583 | -0.08103 | 59.9163 | 59.9564 | 59.9163 | 59.8835 | 61.5102 | 61.5433 | 61.2803 | 61.4496 | 61.7002 | 61.5562 | 61.5389 | 61.5213 | 61.5872 | 61.6365 | 61.4699 | 59.9621 | 60.0022 | 59.9621 | 59.9293 | 61.556 | 61.589 | 61.3261 | 61.4954 | -1.5939 | -1.364 | -1.5939 | -1.364
319.6875 | 121.756 | -61.5189 | 60.1181 | 0.14474 | 0.014425 | -0.012 | -0.025017 | 0.031687 | 0.099318 | -0.076452 | 59.9163 | 59.9656 | 59.9117 | 59.879 | 61.5102 | 61.5433 | 61.2803 | 61.4542 | 61.6636 | 61.5333 | 61.5069 | 61.4938 | 61.5505 | 61.6182 | 61.4424 | 59.9621 | 60.0113 | 59.9575 | 59.9247 | 61.556 | 61.589 | 61.3261 | 61.5 | -1.5939 | -1.364 | -1.5985 | -1.3685
321.3594 | 121.7789 | -61.5326 | 60.0952 | 0.14017 | 0.009846 | -0.007421 | -0.034174 | 0.031687 | 0.090161 | -0.08103 | 59.9163 | 59.961 | 59.9026 | 59.8835 | 61.5148 | 61.5433 | 61.2757 | 61.4496 | 61.6728 | 61.5424 | 61.5252 | 61.4984 | 61.5643 | 61.6228 | 61.4516 | 59.9621 | 60.0068 | 59.9484 | 59.9293 | 61.5606 | 61.589 | 61.3215 | 61.4954 | -1.5985 | -1.3594 | -1.6122 | -1.3731
323.0625 | 121.8292 | -61.5417 | 60.0403 | 0.14474 | 0.009846 | -0.007421 | -0.034174 | 0.031687 | 0.090161 | -0.076452 | 59.9163 | 59.9564 | 59.898 | 59.879 | 61.5148 | 61.5478 | 61.2803 | 61.4542 | 61.6865 | 61.5516 | 61.5343 | 61.5076 | 61.5734 | 61.6319 | 61.4653 | 59.9621 | 60.0022 | 59.9438 | 59.9247 | 61.5606 | 61.5936 | 61.3261 | 61.5 | -1.5985 | -1.364 | -1.6168 | -1.3823
324.75 | 121.8842 | -61.4822 | 60.0769 | 0.14932 | 0.009846 | -0.016578 | -0.029595 | 0.027109 | 0.090161 | -0.071874 | 59.9209 | 59.9564 | 59.9072 | 59.8835 | 61.5102 | 61.5433 | 61.2849 | 61.4496 | 61.6316 | 61.4921 | 61.4657 | 61.4526 | 61.5093 | 61.5724 | 61.4104 | 59.9667 | 60.0022 | 59.9529 | 59.9293 | 61.556 | 61.589 | 61.3306 | 61.4954 | -1.5893 | -1.364 | -1.6031 | -1.3777
326.4219 | 121.8658 | -61.5509 | 59.9854 | 0.14017 | 0.005267 | -0.016578 | -0.038752 | 0.027109 | 0.090161 | -0.071874 | 59.9117 | 59.9564 | 59.9072 | 59.8835 | 61.5102 | 61.5478 | 61.2757 | 61.4451 | 61.6911 | 61.5562 | 61.5343 | 61.5122 | 61.578 | 61.6411 | 61.479 | 59.9575 | 60.0022 | 59.9529 | 59.9293 | 61.556 | 61.5936 | 61.3215 | 61.4908 | -1.5985 | -1.364 | -1.6031 | -1.3685
328.1406 | 121.8292 | -61.5417 | 60.0082 | 0.14932 | 0.000689 | -0.012 | -0.029595 | 0.040843 | 0.099318 | -0.08103 | 59.9209 | 59.9564 | 59.9117 | 59.8835 | 61.5148 | 61.5478 | 61.2849 | 61.4451 | 61.6911 | 61.5424 | 61.5297 | 61.5122 | 61.5826 | 61.6411 | 61.4607 | 59.9667 | 60.0022 | 59.9575 | 59.9293 | 61.5606 | 61.5936 | 61.3306 | 61.4908 | -1.5939 | -1.364 | -1.6031 | -1.3731
329.875 | 121.9116 | -61.496 | 60.0586 | 0.14474 | 0.000689 | -0.007421 | -0.034174 | 0.031687 | 0.090161 | -0.067295 | 59.9209 | 59.9564 | 59.9072 | 59.8835 | 61.5102 | 61.5387 | 61.2849 | 61.4451 | 61.6407 | 61.4967 | 61.4886 | 61.4618 | 61.5277 | 61.5861 | 61.4287 | 59.9667 | 60.0022 | 59.9529 | 59.9293 | 61.556 | 61.5845 | 61.3306 | 61.4908 | -1.5893 | -1.364 | -1.6031 | -1.3777
331.5625 | 121.7377 | -61.6058 | 60.0266 | 0.14474 | 0.009846 | -0.002842 | -0.029595 | 0.031687 | 0.090161 | -0.067295 | 59.9255 | 59.9518 | 59.9117 | 59.8835 | 61.5056 | 61.5387 | 61.2757 | 61.4451 | 61.7506 | 61.6157 | 61.603 | 61.5762 | 61.6375 | 61.696 | 61.5385 | 59.9712 | 59.9976 | 59.9575 | 59.9293 | 61.5514 | 61.5845 | 61.3215 | 61.4908 | -1.5802 | -1.3502 | -1.5939 | -1.364
333.2812 | 121.8796 | -61.4868 | 60.0311 | 0.1539 | 0.009846 | -0.012 | -0.034174 | 0.040843 | 0.090161 | -0.076452 | 59.9209 | 59.9564 | 59.9072 | 59.8744 | 61.5102 | 61.5387 | 61.2803 | 61.4496 | 61.6407 | 61.4967 | 61.4748 | 61.4526 | 61.5277 | 61.577 | 61.4104 | 59.9667 | 60.0022 | 59.9529 | 59.9201 | 61.556 | 61.5845 | 61.3261 | 61.4954 | -1.5893 | -1.3594 | -1.6031 | -1.3731
335.0312 | 121.8933 | -61.5738 | 59.9899 | 0.14932 | 0.009846 | -0.002842 | -0.025017 | 0.027109 | 0.090161 | -0.08103 | 59.9163 | 59.9564 | 59.9072 | 59.879 | 61.5102 | 61.5478 | 61.2849 | 61.4496 | 61.7231 | 61.5836 | 61.5709 | 61.5488 | 61.6009 | 61.664 | 61.4928 | 59.9621 | 60.0022 | 59.9529 | 59.9247 | 61.556 | 61.5936 | 61.3306 | 61.4954 | -1.5939 | -1.3686 | -1.6031 | -1.3777
336.7188 | 121.788 | -61.5875 | 60.0403 | 0.14474 | 0.000689 | -0.016578 | -0.029595 | 0.031687 | 0.090161 | -0.08103 | 59.9255 | 59.9518 | 59.9117 | 59.8744 | 61.5148 | 61.5478 | 61.2757 | 61.4451 | 61.7323 | 61.5882 | 61.5709 | 61.5579 | 61.6192 | 61.6777 | 61.5065 | 59.9712 | 59.9976 | 59.9575 | 59.9201 | 61.5606 | 61.5936 | 61.3215 | 61.4908 | -1.5893 | -1.3502 | -1.6031 | -1.364
338.4062 | 121.843 | -61.5601 | 60.0037 | 0.14017 | 0.000689 | -0.016578 | -0.01586 | 0.031687 | 0.081005 | -0.08103 | 59.9209 | 59.9564 | 59.9117 | 59.8835 | 61.5056 | 61.5387 | 61.2757 | 61.4496 | 61.7002 | 61.5607 | 61.5435 | 61.5442 | 61.5917 | 61.6411 | 61.479 | 59.9667 | 60.0022 | 59.9575 | 59.9293 | 61.5514 | 61.5845 | 61.3215 | 61.4954 | -1.5847 | -1.3548 | -1.5939 | -1.364
340.1094 | 121.8933 | -61.4777 | 60.0403 | 0.14474 | 0.009846 | -0.007421 | -0.029595 | 0.031687 | 0.09474 | -0.076452 | 59.9163 | 59.9518 | 59.9072 | 59.8881 | 61.5056 | 61.5478 | 61.2803 | 61.4496 | 61.6224 | 61.4875 | 61.4702 | 61.4481 | 61.5093 | 61.5724 | 61.4012 | 59.9621 | 59.9976 | 59.9529 | 59.9339 | 61.5514 | 61.5936 | 61.3261 | 61.4954 | -1.5893 | -1.364 | -1.5985 | -1.3731
341.8281 | 121.8338 | -61.528 | 59.9991 | 0.14017 | 0.009846 | -0.012 | -0.029595 | 0.027109 | 0.085583 | -0.071874 | 59.9209 | 59.9564 | 59.9163 | 59.879 | 61.5056 | 61.5433 | 61.2803 | 61.4451 | 61.6682 | 61.5379 | 61.516 | 61.4984 | 61.5551 | 61.6136 | 61.4561 | 59.9667 | 60.0022 | 59.9621 | 59.9247 | 61.5514 | 61.589 | 61.3261 | 61.4908 | -1.5847 | -1.3594 | -1.5893 | -1.364
343.5156 | 121.8292 | -61.5555 | 60.0037 | 0.1539 | 0.005267 | -0.012 | -0.029595 | 0.040843 | 0.090161 | -0.08103 | 59.9163 | 59.9564 | 59.9117 | 59.8927 | 61.5148 | 61.5478 | 61.2757 | 61.4451 | 61.7094 | 61.5607 | 61.5435 | 61.5259 | 61.5963 | 61.6456 | 61.4745 | 59.9621 | 60.0022 | 59.9575 | 59.9385 | 61.5606 | 61.5936 | 61.3215 | 61.4908 | -1.5985 | -1.3594 | -1.6031 | -1.364
345.25 | 121.7789 | -61.5143 | 60.1044 | 0.14474 | 0.014425 | -0.012 | -0.029595 | 0.036265 | 0.090161 | -0.08103 | 59.9163 | 59.9564 | 59.9117 | 59.879 | 61.5011 | 61.5433 | 61.2803 | 61.4542 | 61.659 | 61.5287 | 61.5023 | 61.4847 | 61.5505 | 61.6044 | 61.4333 | 59.9621 | 60.0022 | 59.9575 | 59.9247 | 61.5468 | 61.589 | 61.3261 | 61.5 | -1.5847 | -1.364 | -1.5893 | -1.3685
346.9375 | 121.8887 | -61.4914 | 60.0494 | 0.14474 | 0.009846 | -0.012 | -0.034174 | 0.036265 | 0.09474 | -0.08103 | 59.9209 | 59.9518 | 59.9117 | 59.8698 | 61.5102 | 61.5433 | 61.2849 | 61.4496 | 61.6361 | 61.5012 | 61.4794 | 61.4572 | 61.5277 | 61.5861 | 61.4104 | 59.9667 | 59.9976 | 59.9575 | 59.9156 | 61.556 | 61.589 | 61.3306 | 61.4954 | -1.5893 | -1.364 | -1.5985 | -1.3731
348.625 | 121.8704 | -61.5234 | 60.0311 | 0.14017 | 0.005267 | -0.012 | -0.029595 | 0.027109 | 0.081005 | -0.076452 | 59.9163 | 59.961 | 59.9117 | 59.8835 | 61.5102 | 61.5433 | 61.2803 | 61.4496 | 61.6636 | 61.5287 | 61.5114 | 61.4938 | 61.5505 | 61.6044 | 61.447 | 59.9621 | 60.0068 | 59.9575 | 59.9293 | 61.556 | 61.589 | 61.3261 | 61.4954 | -1.5939 | -1.364 | -1.5985 | -1.3685
350.3438 | 121.756 | -61.5784 | 60.0311 | 0.14932 | 0.005267 | -0.016578 | -0.025017 | 0.036265 | 0.090161 | -0.071874 | 59.9209 | 59.9564 | 59.9117 | 59.8835 | 61.5056 | 61.5478 | 61.2803 | 61.4496 | 61.7277 | 61.5836 | 61.5618 | 61.5534 | 61.6146 | 61.6685 | 61.5065 | 59.9667 | 60.0022 | 59.9575 | 59.9293 | 61.5514 | 61.5936 | 61.3261 | 61.4954 | -1.5847 | -1.3594 | -1.5939 | -1.3685
352.0469 | 121.7789 | -61.528 | 60.0952 | 0.14474 | 0.005267 | -0.012 | -0.038752 | 0.036265 | 0.090161 | -0.076452 | 59.9163 | 59.9564 | 59.9163 | 59.879 | 61.5102 | 61.5478 | 61.2803 | 61.4496 | 61.6728 | 61.5333 | 61.516 | 61.4893 | 61.5643 | 61.6182 | 61.4516 | 59.9621 | 60.0022 | 59.9621 | 59.9247 | 61.556 | 61.5936 | 61.3261 | 61.4954 | -1.5939 | -1.364 | -1.5939 | -1.364
353.7344 | 121.8475 | -61.5509 | 59.9945 | 0.14932 | 0.005267 | -0.016578 | -0.025017 | 0.036265 | 0.09474 | -0.071874 | 59.9163 | 59.9564 | 59.9163 | 59.8835 | 61.5148 | 61.5433 | 61.2757 | 61.4451 | 61.7002 | 61.5562 | 61.5343 | 61.5259 | 61.5872 | 61.6456 | 61.479 | 59.9621 | 60.0022 | 59.9621 | 59.9293 | 61.5606 | 61.589 | 61.3215 | 61.4908 | -1.5985 | -1.3594 | -1.5985 | -1.3594
355.4375 | 121.8933 | -61.4685 | 60.0174 | 0.14474 | 0.005267 | -0.016578 | -0.034174 | 0.031687 | 0.085583 | -0.071874 | 59.9117 | 59.9473 | 59.9072 | 59.8835 | 61.5056 | 61.5478 | 61.2849 | 61.4496 | 61.6132 | 61.4738 | 61.4519 | 61.4343 | 61.5002 | 61.5541 | 61.3966 | 59.9575 | 59.993 | 59.9529 | 59.9293 | 61.5514 | 61.5936 | 61.3306 | 61.4954 | -1.5939 | -1.3731 | -1.5985 | -1.3777
357.1562 | 121.8292 | -61.5463 | 59.9945 | 0.14474 | 0.009846 | -0.012 | -0.029595 | 0.036265 | 0.085583 | -0.08103 | 59.9209 | 59.961 | 59.9117 | 59.8835 | 61.5148 | 61.5433 | 61.2803 | 61.4496 | 61.6911 | 61.5562 | 61.5343 | 61.5167 | 61.5826 | 61.6319 | 61.4653 | 59.9667 | 60.0068 | 59.9575 | 59.9293 | 61.5606 | 61.589 | 61.3261 | 61.4954 | -1.5939 | -1.3594 | -1.6031 | -1.3685
358.9219 | 121.8109 | -61.5417 | 60.0769 | 0.14474 | 0.014425 | -0.007421 | -0.025017 | 0.031687 | 0.090161 | -0.071874 | 59.9163 | 59.961 | 59.9117 | 59.8835 | 61.5102 | 61.5433 | 61.2803 | 61.4496 | 61.6865 | 61.5562 | 61.5343 | 61.5167 | 61.5734 | 61.6319 | 61.4699 | 59.9621 | 60.0068 | 59.9575 | 59.9293 | 61.556 | 61.589 | 61.3261 | 61.4954 | -1.5939 | -1.364 | -1.5985 | -1.3685
360.6406 | 121.7514 | -61.5234 | 60.1135 | 0.14474 | 0.009846 | -0.007421 | -0.029595 | 0.040843 | 0.085583 | -0.076452 | 59.9209 | 59.9564 | 59.9163 | 59.879 | 61.5102 | 61.5433 | 61.2711 | 61.4451 | 61.6682 | 61.5333 | 61.516 | 61.4938 | 61.5643 | 61.609 | 61.447 | 59.9667 | 60.0022 | 59.9621 | 59.9247 | 61.556 | 61.589 | 61.3169 | 61.4908 | -1.5893 | -1.3502 | -1.5939 | -1.3548
362.4219 | 121.7422 | -61.5829 | 60.0128 | 0.14932 | 0.005267 | -0.007421 | -0.025017 | 0.036265 | 0.090161 | -0.071874 | 59.9163 | 59.9564 | 59.9163 | 59.8835 | 61.5194 | 61.5433 | 61.2757 | 61.4451 | 61.7323 | 61.5882 | 61.5755 | 61.5579 | 61.6192 | 61.6731 | 61.5111 | 59.9621 | 60.0022 | 59.9621 | 59.9293 | 61.5651 | 61.589 | 61.3215 | 61.4908 | -1.6031 | -1.3594 | -1.6031 | -1.3594
364.1094 | 121.788 | -61.5326 | 60.0494 | 0.14017 | 0.009846 | -0.021157 | -0.029595 | 0.027109 | 0.090161 | -0.071874 | 59.9255 | 59.961 | 59.9072 | 59.8835 | 61.5056 | 61.5433 | 61.2849 | 61.4451 | 61.6728 | 61.5424 | 61.5114 | 61.503 | 61.5597 | 61.6228 | 61.4607 | 59.9712 | 60.0068 | 59.9529 | 59.9293 | 61.5514 | 61.589 | 61.3306 | 61.4908 | -1.5802 | -1.3594 | -1.5985 | -1.3777
365.8594 | 121.8246 | -61.5372 | 60.0174 | 0.14474 | 0.005267 | -0.016578 | -0.034174 | 0.036265 | 0.090161 | -0.067295 | 59.9163 | 59.9564 | 59.9072 | 59.8835 | 61.5102 | 61.5387 | 61.2757 | 61.4496 | 61.6819 | 61.5424 | 61.5206 | 61.503 | 61.5734 | 61.6273 | 61.4699 | 59.9621 | 60.0022 | 59.9529 | 59.9293 | 61.556 | 61.5845 | 61.3215 | 61.4954 | -1.5939 | -1.3594 | -1.6031 | -1.3685
367.5469 | 121.8246 | -61.5509 | 60.0128 | 0.14932 | 0.009846 | -0.012 | -0.029595 | 0.027109 | 0.090161 | -0.071874 | 59.9163 | 59.9564 | 59.9117 | 59.879 | 61.5102 | 61.5433 | 61.2803 | 61.4496 | 61.7002 | 61.5607 | 61.5389 | 61.5213 | 61.578 | 61.6411 | 61.479 | 59.9621 | 60.0022 | 59.9575 | 59.9247 | 61.556 | 61.589 | 61.3261 | 61.4954 | -1.5939 | -1.364 | -1.5985 | -1.3685
369.3125 | 121.875 | -61.5738 | 59.9808 | 0.14932 | 0.005267 | -0.016578 | -0.025017 | 0.036265 | 0.090161 | -0.076452 | 59.9163 | 59.9564 | 59.9163 | 59.8835 | 61.5102 | 61.5387 | 61.2803 | 61.4451 | 61.7231 | 61.5791 | 61.5572 | 61.5488 | 61.6101 | 61.664 | 61.4973 | 59.9621 | 60.0022 | 59.9621 | 59.9293 | 61.556 | 61.5845 | 61.3261 | 61.4908 | -1.5939 | -1.364 | -1.5939 | -1.364
371.0781 | 121.7743 | -61.5509 | 60.0357 | 0.14474 | 0.009846 | -0.012 | -0.020438 | 0.036265 | 0.09474 | -0.076452 | 59.9209 | 59.9564 | 59.9072 | 59.8698 | 61.5056 | 61.5433 | 61.2711 | 61.4451 | 61.6956 | 61.5607 | 61.5389 | 61.5305 | 61.5872 | 61.6456 | 61.4745 | 59.9667 | 60.0022 | 59.9529 | 59.9156 | 61.5514 | 61.589 | 61.3169 | 61.4908 | -1.5847 | -1.3502 | -1.5985 | -1.364
372.8438 | 121.7697 | -61.5646 | 60.0357 | 0.14932 | 0.014425 | -0.012 | -0.020438 | 0.031687 | 0.090161 | -0.076452 | 59.9163 | 59.961 | 59.9117 | 59.8835 | 61.5011 | 61.5387 | 61.2803 | 61.4405 | 61.714 | 61.5791 | 61.5526 | 61.5442 | 61.5963 | 61.6548 | 61.4882 | 59.9621 | 60.0068 | 59.9575 | 59.9293 | 61.5468 | 61.5845 | 61.3261 | 61.4863 | -1.5847 | -1.364 | -1.5893 | -1.3685
374.5312 | 121.7697 | -61.5097 | 60.1044 | 0.14474 | 0.005267 | -0.012 | -0.029595 | 0.036265 | 0.09474 | -0.08103 | 59.9209 | 59.9564 | 59.9163 | 59.879 | 61.5102 | 61.5478 | 61.2757 | 61.4451 | 61.6544 | 61.515 | 61.4977 | 61.4801 | 61.546 | 61.6044 | 61.4287 | 59.9667 | 60.0022 | 59.9621 | 59.9247 | 61.556 | 61.5936 | 61.3215 | 61.4908 | -1.5893 | -1.3548 | -1.5939 | -1.3594
376.2656 | 121.756 | -61.6196 | 60.0403 | 0.14474 | 0.009846 | -0.002842 | -0.025017 | 0.031687 | 0.09474 | -0.071874 | 59.9209 | 59.961 | 59.9026 | 59.879 | 61.5102 | 61.5387 | 61.2803 | 61.4496 | 61.7643 | 61.6294 | 61.6167 | 61.5946 | 61.6513 | 61.7143 | 61.5477 | 59.9667 | 60.0068 | 59.9484 | 59.9247 | 61.556 | 61.5845 | 61.3261 | 61.4954 | -1.5893 | -1.3594 | -1.6076 | -1.3777
378.0312 | 121.7743 | -61.5921 | 60.022 | 0.14932 | 0.009846 | -0.002842 | -0.034174 | 0.031687 | 0.085583 | -0.076452 | 59.9209 | 59.9518 | 59.9163 | 59.8881 | 61.5011 | 61.5524 | 61.2757 | 61.4451 | 61.7414 | 61.6019 | 61.5893 | 61.5579 | 61.6238 | 61.6777 | 61.5156 | 59.9667 | 59.9976 | 59.9621 | 59.9339 | 61.5468 | 61.5982 | 61.3215 | 61.4908 | -1.5802 | -1.3548 | -1.5847 | -1.3594
379.7812 | 121.8658 | -61.4731 | 60.0586 | 0.14474 | 0.005267 | -0.012 | -0.034174 | 0.036265 | 0.099318 | -0.085608 | 59.9255 | 59.961 | 59.9026 | 59.8835 | 61.5102 | 61.5433 | 61.2757 | 61.4451 | 61.6178 | 61.4784 | 61.4611 | 61.4389 | 61.5093 | 61.5724 | 61.3875 | 59.9712 | 60.0068 | 59.9484 | 59.9293 | 61.556 | 61.589 | 61.3215 | 61.4908 | -1.5847 | -1.3502 | -1.6076 | -1.3731
381.4531 | 121.7651 | -61.5875 | 60.022 | 0.14932 | 0.014425 | -0.007421 | -0.020438 | 0.045421 | 0.09474 | -0.08103 | 59.9209 | 59.9564 | 59.9117 | 59.879 | 61.5148 | 61.5478 | 61.2757 | 61.4496 | 61.7368 | 61.6019 | 61.5801 | 61.5671 | 61.6329 | 61.6823 | 61.5065 | 59.9667 | 60.0022 | 59.9575 | 59.9247 | 61.5606 | 61.5936 | 61.3215 | 61.4954 | -1.5939 | -1.3548 | -1.6031 | -1.364
383.2031 | 121.7468 | -61.5646 | 60.022 | 0.14474 | 0.009846 | -0.002842 | -0.038752 | 0.036265 | 0.085583 | -0.071874 | 59.9209 | 59.9518 | 59.9117 | 59.8927 | 61.5056 | 61.5387 | 61.2757 | 61.4451 | 61.7094 | 61.5745 | 61.5618 | 61.5259 | 61.6009 | 61.6502 | 61.4928 | 59.9667 | 59.9976 | 59.9575 | 59.9385 | 61.5514 | 61.5845 | 61.3215 | 61.4908 | -1.5847 | -1.3548 | -1.5939 | -1.364
384.9531 | 121.7606 | -61.5601 | 60.054 | 0.14017 | 0.005267 | -0.016578 | -0.029595 | 0.031687 | 0.090161 | -0.071874 | 59.9209 | 59.9564 | 59.9072 | 59.879 | 61.5056 | 61.5387 | 61.2803 | 61.4451 | 61.7002 | 61.5653 | 61.5435 | 61.5305 | 61.5917 | 61.6502 | 61.4882 | 59.9667 | 60.0022 | 59.9529 | 59.9247 | 61.5514 | 61.5845 | 61.3261 | 61.4908 | -1.5847 | -1.3594 | -1.5985 | -1.3731
386.6406 | 121.7606 | -61.5097 | 60.1135 | 0.14474 | 0.009846 | -0.002842 | -0.025017 | 0.036265 | 0.085583 | -0.076452 | 59.9163 | 59.961 | 59.9117 | 59.8881 | 61.5056 | 61.5478 | 61.2757 | 61.4451 | 61.6544 | 61.5196 | 61.5069 | 61.4847 | 61.546 | 61.5953 | 61.4333 | 59.9621 | 60.0068 | 59.9575 | 59.9339 | 61.5514 | 61.5936 | 61.3215 | 61.4908 | -1.5893 | -1.3594 | -1.5939 | -1.364
388.3438 | 121.7514 | -61.5921 | 60.0266 | 0.14932 | 0.009846 | -0.007421 | -0.025017 | 0.031687 | 0.09474 | -0.076452 | 59.9209 | 59.9518 | 59.9072 | 59.879 | 61.5056 | 61.5433 | 61.2711 | 61.4451 | 61.7414 | 61.6019 | 61.5847 | 61.5671 | 61.6238 | 61.6868 | 61.5156 | 59.9667 | 59.9976 | 59.9529 | 59.9247 | 61.5514 | 61.589 | 61.3169 | 61.4908 | -1.5847 | -1.3502 | -1.5985 | -1.364
390.0938 | 121.8567 | -61.5417 | 60.0403 | 0.14932 | 0.005267 | -0.012 | -0.025017 | 0.031687 | 0.085583 | -0.071874 | 59.9209 | 59.9564 | 59.9117 | 59.879 | 61.5056 | 61.5433 | 61.2757 | 61.4542 | 61.6911 | 61.547 | 61.5297 | 61.5167 | 61.5734 | 61.6273 | 61.4699 | 59.9667 | 60.0022 | 59.9575 | 59.9247 | 61.5514 | 61.589 | 61.3215 | 61.5 | -1.5847 | -1.3548 | -1.5939 | -1.364
391.8438 | 121.7789 | -61.5417 | 60.022 | 0.14474 | 0.000689 | -0.016578 | -0.038752 | 0.040843 | 0.090161 | -0.076452 | 59.9163 | 59.9564 | 59.9072 | 59.879 | 61.5148 | 61.5433 | 61.2711 | 61.4496 | 61.6865 | 61.5424 | 61.5252 | 61.503 | 61.5826 | 61.6319 | 61.4653 | 59.9621 | 60.0022 | 59.9529 | 59.9247 | 61.5606 | 61.589 | 61.3169 | 61.4954 | -1.5985 | -1.3548 | -1.6076 | -1.364
393.6094 | 121.756 | -61.5372 | 60.1227 | 0.1539 | 0.009846 | -0.012 | -0.038752 | 0.040843 | 0.085583 | -0.08103 | 59.9255 | 59.9564 | 59.9117 | 59.879 | 61.5148 | 61.5524 | 61.2757 | 61.4451 | 61.6911 | 61.547 | 61.5252 | 61.4984 | 61.578 | 61.6228 | 61.4561 | 59.9712 | 60.0022 | 59.9575 | 59.9247 | 61.5606 | 61.5982 | 61.3215 | 61.4908 | -1.5893 | -1.3502 | -1.6031 | -1.364
395.3594 | 121.7606 | -61.5784 | 60.0403 | 0.14017 | 0.005267 | -0.007421 | -0.025017 | 0.036265 | 0.09474 | -0.08103 | 59.9163 | 59.9564 | 59.898 | 59.8835 | 61.5102 | 61.5433 | 61.2803 | 61.4451 | 61.7185 | 61.5836 | 61.5709 | 61.5534 | 61.6146 | 61.6731 | 61.4973 | 59.9621 | 60.0022 | 59.9438 | 59.9293 | 61.556 | 61.589 | 61.3261 | 61.4908 | -1.5939 | -1.364 | -1.6122 | -1.3823
397.0625 | 121.7972 | -61.5692 | 60.0677 | 0.14932 | 0.009846 | -0.007421 | -0.025017 | 0.036265 | 0.085583 | -0.071874 | 59.9163 | 59.9564 | 59.9072 | 59.879 | 61.5102 | 61.5478 | 61.2757 | 61.4451 | 61.7185 | 61.5791 | 61.5618 | 61.5442 | 61.6055 | 61.6548 | 61.4973 | 59.9621 | 60.0022 | 59.9529 | 59.9247 | 61.556 | 61.5936 | 61.3215 | 61.4908 | -1.5939 | -1.3594 | -1.6031 | -1.3685
398.8281 | 121.8658 | -61.5555 | 59.9854 | 0.14017 | 0.009846 | -0.012 | -0.029595 | 0.036265 | 0.090161 | -0.076452 | 59.9117 | 59.9564 | 59.9072 | 59.8835 | 61.5056 | 61.5478 | 61.2849 | 61.4496 | 61.6956 | 61.5653 | 61.5435 | 61.5259 | 61.5917 | 61.6456 | 61.479 | 59.9575 | 60.0022 | 59.9529 | 59.9293 | 61.5514 | 61.5936 | 61.3306 | 61.4954 | -1.5939 | -1.3731 | -1.5985 | -1.3777
400.5156 | 121.788 | -61.5967 | 60.0082 | 0.14932 | 0.005267 | -0.016578 | -0.029595 | 0.031687 | 0.09474 | -0.076452 | 59.9163 | 59.9518 | 59.9072 | 59.8835 | 61.5011 | 61.5341 | 61.2803 | 61.4451 | 61.746 | 61.6019 | 61.5801 | 61.5671 | 61.6284 | 61.6914 | 61.5202 | 59.9621 | 59.9976 | 59.9529 | 59.9293 | 61.5468 | 61.5799 | 61.3261 | 61.4908 | -1.5847 | -1.364 | -1.5939 | -1.3731
402.2969 | 121.8842 | -61.5692 | 59.9762 | 0.14932 | 0.005267 | -0.007421 | -0.029595 | 0.036265 | 0.085583 | -0.067295 | 59.9209 | 59.9518 | 59.9072 | 59.8881 | 61.5056 | 61.5478 | 61.2711 | 61.4451 | 61.7185 | 61.5745 | 61.5618 | 61.5396 | 61.6055 | 61.6548 | 61.5019 | 59.9667 | 59.9976 | 59.9529 | 59.9339 | 61.5514 | 61.5936 | 61.3169 | 61.4908 | -1.5847 | -1.3502 | -1.5985 | -1.364
404.0625 | 121.8338 | -61.5509 | 60.0266 | 0.14932 | 0.009846 | -0.012 | -0.034174 | 0.027109 | 0.090161 | -0.076452 | 59.9163 | 59.9564 | 59.9117 | 59.8881 | 61.5148 | 61.5433 | 61.2849 | 61.4451 | 61.7002 | 61.5607 | 61.5389 | 61.5167 | 61.578 | 61.6411 | 61.4745 | 59.9621 | 60.0022 | 59.9575 | 59.9339 | 61.5606 | 61.589 | 61.3306 | 61.4908 | -1.5985 | -1.3686 | -1.6031 | -1.3731
405.75 | 121.7651 | -61.6104 | 60.0266 | 0.14474 | 0.000689 | -0.012 | -0.029595 | 0.040843 | 0.085583 | -0.071874 | 59.9209 | 59.9518 | 59.9072 | 59.8881 | 61.5102 | 61.5478 | 61.2711 | 61.4496 | 61.7552 | 61.6111 | 61.5984 | 61.5808 | 61.6513 | 61.696 | 61.5385 | 59.9667 | 59.9976 | 59.9529 | 59.9339 | 61.556 | 61.5936 | 61.3169 | 61.4954 | -1.5893 | -1.3502 | -1.6031 | -1.364
407.4375 | 121.8796 | -61.4822 | 60.0677 | 0.14932 | 0.000689 | -0.016578 | -0.029595 | 0.027109 | 0.090161 | -0.076452 | 59.9163 | 59.9564 | 59.9072 | 59.8744 | 61.5102 | 61.5387 | 61.2803 | 61.4451 | 61.6316 | 61.4829 | 61.4657 | 61.4526 | 61.5093 | 61.5724 | 61.4058 | 59.9621 | 60.0022 | 59.9529 | 59.9201 | 61.556 | 61.5845 | 61.3261 | 61.4908 | -1.5939 | -1.364 | -1.6031 | -1.3731
409.2031 | 121.8842 | -61.5601 | 59.9579 | 0.14932 | 0.000689 | -0.007421 | -0.025017 | 0.027109 | 0.085583 | -0.08103 | 59.9255 | 59.9564 | 59.9117 | 59.8835 | 61.5056 | 61.5387 | 61.2711 | 61.4451 | 61.7094 | 61.5607 | 61.5526 | 61.535 | 61.5872 | 61.6456 | 61.479 | 59.9712 | 60.0022 | 59.9575 | 59.9293 | 61.5514 | 61.5845 | 61.3169 | 61.4908 | -1.5802 | -1.3457 | -1.5939 | -1.3594
410.8906 | 121.7972 | -61.5875 | 59.9945 | 0.14932 | 0.009846 | -0.012 | -0.034174 | 0.036265 | 0.090161 | -0.071874 | 59.9209 | 59.961 | 59.9026 | 59.879 | 61.5102 | 61.5478 | 61.2757 | 61.4496 | 61.7368 | 61.5974 | 61.5755 | 61.5534 | 61.6238 | 61.6777 | 61.5157 | 59.9667 | 60.0068 | 59.9484 | 59.9247 | 61.556 | 61.5936 | 61.3215 | 61.4954 | -1.5893 | -1.3548 | -1.6076 | -1.3731
412.6406 | 121.7743 | -61.5967 | 60.0311 | 0.14474 | 0.005267 | -0.007421 | -0.034174 | 0.040843 | 0.09474 | -0.076452 | 59.9209 | 59.9564 | 59.9163 | 59.8881 | 61.5056 | 61.5433 | 61.2711 | 61.4542 | 61.7414 | 61.6019 | 61.5893 | 61.5625 | 61.6375 | 61.6914 | 61.5202 | 59.9667 | 60.0022 | 59.9621 | 59.9339 | 61.5514 | 61.589 | 61.3169 | 61.5 | -1.5847 | -1.3502 | -1.5893 | -1.3548
414.3906 | 121.8796 | -61.5555 | 59.9854 | 0.14932 | 0.014425 | -0.007421 | -0.025017 | 0.036265 | 0.09474 | -0.071874 | 59.9255 | 59.9564 | 59.9117 | 59.8881 | 61.5148 | 61.5433 | 61.2803 | 61.4496 | 61.7048 | 61.5699 | 61.5481 | 61.5305 | 61.5917 | 61.6502 | 61.4836 | 59.9712 | 60.0022 | 59.9575 | 59.9339 | 61.5606 | 61.589 | 61.3261 | 61.4954 | -1.5893 | -1.3548 | -1.6031 | -1.3685
416.1406 | 121.875 | -61.5692 | 59.9899 | 0.14017 | 0.009846 | -0.012 | -0.034174 | 0.027109 | 0.090161 | -0.076452 | 59.9163 | 59.9564 | 59.9117 | 59.8881 | 61.5011 | 61.5433 | 61.2757 | 61.4451 | 61.7094 | 61.5791 | 61.5572 | 61.535 | 61.5963 | 61.6594 | 61.4928 | 59.9621 | 60.0022 | 59.9575 | 59.9339 | 61.5468 | 61.589 | 61.3215 | 61.4908 | -1.5847 | -1.3594 | -1.5893 | -1.364
417.8906 | 121.788 | -61.5967 | 60.0128 | 0.14932 | 0.009846 | -0.007421 | -0.029595 | 0.031687 | 0.099318 | -0.076452 | 59.9209 | 59.961 | 59.9117 | 59.8881 | 61.5056 | 61.5387 | 61.2757 | 61.4496 | 61.746 | 61.6065 | 61.5893 | 61.5671 | 61.6284 | 61.696 | 61.5202 | 59.9667 | 60.0068 | 59.9575 | 59.9339 | 61.5514 | 61.5845 | 61.3215 | 61.4954 | -1.5847 | -1.3548 | -1.5939 | -1.364
419.5781 | 121.875 | -61.5555 | 59.967 | 0.15848 | 0.005267 | -0.012 | -0.034174 | 0.040843 | 0.081005 | -0.076452 | 59.9209 | 59.9564 | 59.9026 | 59.8835 | 61.5056 | 61.5433 | 61.2711 | 61.4359 | 61.714 | 61.5607 | 61.5435 | 61.5213 | 61.5963 | 61.6365 | 61.479 | 59.9667 | 60.0022 | 59.9484 | 59.9293 | 61.5514 | 61.589 | 61.3169 | 61.4817 | -1.5847 | -1.3502 | -1.6031 | -1.3685
421.3125 | 121.8796 | -61.5051 | 60.0403 | 0.14474 | -0.00389 | -0.012 | -0.025017 | 0.036265 | 0.085583 | -0.08103 | 59.9255 | 59.961 | 59.9026 | 59.8835 | 61.5102 | 61.5433 | 61.2803 | 61.4496 | 61.6499 | 61.5012 | 61.4931 | 61.4801 | 61.5414 | 61.5907 | 61.4241 | 59.9712 | 60.0068 | 59.9484 | 59.9293 | 61.556 | 61.589 | 61.3261 | 61.4954 | -1.5847 | -1.3548 | -1.6076 | -1.3777
423.0625 | 121.8063 | -61.528 | 60.0677 | 0.14474 | 0.009846 | -0.007421 | -0.025017 | 0.036265 | 0.090161 | -0.076452 | 59.9209 | 59.9473 | 59.9117 | 59.8835 | 61.5011 | 61.5387 | 61.2757 | 61.4451 | 61.6728 | 61.5379 | 61.5206 | 61.503 | 61.5643 | 61.6182 | 61.4516 | 59.9667 | 59.993 | 59.9575 | 59.9293 | 61.5468 | 61.5845 | 61.3215 | 61.4908 | -1.5802 | -1.3548 | -1.5893 | -1.364
424.75 | 121.7468 | -61.5189 | 60.1227 | 0.14474 | 0.005267 | -0.012 | -0.025017 | 0.031687 | 0.090161 | -0.08103 | 59.9117 | 59.9473 | 59.9117 | 59.8835 | 61.5056 | 61.5524 | 61.2757 | 61.4405 | 61.6636 | 61.5241 | 61.5069 | 61.4938 | 61.5505 | 61.609 | 61.4378 | 59.9575 | 59.993 | 59.9575 | 59.9293 | 61.5514 | 61.5982 | 61.3215 | 61.4863 | -1.5939 | -1.364 | -1.5939 | -1.364
426.5 | 121.8063 | -61.6013 | 59.9899 | 0.14017 | 0.009846 | -0.007421 | -0.034174 | 0.040843 | 0.085583 | -0.071874 | 59.9255 | 59.961 | 59.9163 | 59.8927 | 61.5102 | 61.5433 | 61.2757 | 61.4496 | 61.7414 | 61.6111 | 61.5938 | 61.5671 | 61.6421 | 61.6868 | 61.5294 | 59.9712 | 60.0068 | 59.9621 | 59.9385 | 61.556 | 61.589 | 61.3215 | 61.4954 | -1.5847 | -1.3502 | -1.5939 | -1.3594
428.2656 | 121.8704 | -61.5601 | 59.9762 | 0.14474 | 0.005267 | -0.007421 | -0.029595 | 0.031687 | 0.09474 | -0.067295 | 59.9209 | 59.961 | 59.9026 | 59.8835 | 61.5056 | 61.5387 | 61.2711 | 61.4542 | 61.7048 | 61.5653 | 61.5526 | 61.5305 | 61.5917 | 61.6548 | 61.4928 | 59.9667 | 60.0068 | 59.9484 | 59.9293 | 61.5514 | 61.5845 | 61.3169 | 61.5 | -1.5847 | -1.3502 | -1.6031 | -1.3685
430.0156 | 121.8018 | -61.5372 | 60.0861 | 0.14474 | 0.009846 | -0.007421 | -0.020438 | 0.027109 | 0.090161 | -0.085608 | 59.9117 | 59.9518 | 59.9072 | 59.879 | 61.5148 | 61.5433 | 61.2711 | 61.4496 | 61.6819 | 61.547 | 61.5297 | 61.5167 | 61.5643 | 61.6273 | 61.4516 | 59.9575 | 59.9976 | 59.9529 | 59.9247 | 61.5606 | 61.589 | 61.3169 | 61.4954 | -1.6031 | -1.3594 | -1.6076 | -1.364
431.7031 | 121.8567 | -61.5372 | 60.0311 | 0.14932 | 0.000689 | -0.016578 | -0.025017 | 0.031687 | 0.090161 | -0.076452 | 59.9209 | 59.961 | 59.9026 | 59.8835 | 61.5102 | 61.5478 | 61.2757 | 61.4496 | 61.6865 | 61.5379 | 61.5206 | 61.5122 | 61.5689 | 61.6273 | 61.4607 | 59.9667 | 60.0068 | 59.9484 | 59.9293 | 61.556 | 61.5936 | 61.3215 | 61.4954 | -1.5893 | -1.3548 | -1.6076 | -1.3731
433.4531 | 121.8109 | -61.5326 | 60.0723 | 0.14474 | 0.000689 | -0.016578 | -0.029595 | 0.036265 | 0.090161 | -0.067295 | 59.9163 | 59.961 | 59.9072 | 59.879 | 61.5056 | 61.5387 | 61.2803 | 61.4359 | 61.6773 | 61.5333 | 61.516 | 61.503 | 61.5689 | 61.6228 | 61.4653 | 59.9621 | 60.0068 | 59.9529 | 59.9247 | 61.5514 | 61.5845 | 61.3261 | 61.4817 | -1.5893 | -1.364 | -1.5985 | -1.3731
435.2031 | 121.8613 | -61.5051 | 60.0174 | 0.14474 | 0.009846 | -0.016578 | -0.029595 | 0.031687 | 0.09474 | -0.076452 | 59.9255 | 59.9564 | 59.9072 | 59.879 | 61.5102 | 61.5387 | 61.2757 | 61.4405 | 61.6499 | 61.515 | 61.4885 | 61.4755 | 61.5368 | 61.5999 | 61.4287 | 59.9712 | 60.0022 | 59.9529 | 59.9247 | 61.556 | 61.5845 | 61.3215 | 61.4863 | -1.5847 | -1.3502 | -1.6031 | -1.3685
436.8906 | 121.843 | -61.5372 | 60.0174 | 0.14474 | 0.005267 | -0.012 | -0.025017 | 0.040843 | 0.090161 | -0.08103 | 59.9209 | 59.9518 | 59.9117 | 59.8881 | 61.5102 | 61.5433 | 61.2757 | 61.4451 | 61.6819 | 61.5424 | 61.5252 | 61.5122 | 61.578 | 61.6273 | 61.4561 | 59.9667 | 59.9976 | 59.9575 | 59.9339 | 61.556 | 61.589 | 61.3215 | 61.4908 | -1.5893 | -1.3548 | -1.5985 | -1.364
438.6406 | 121.8246 | -61.5463 | 60.0174 | 0.14474 | 0.014425 | -0.002842 | -0.029595 | 0.031687 | 0.09474 | -0.08103 | 59.9209 | 59.961 | 59.9072 | 59.8835 | 61.5102 | 61.5478 | 61.2803 | 61.4451 | 61.6911 | 61.5608 | 61.5435 | 61.5167 | 61.578 | 61.6411 | 61.4653 | 59.9667 | 60.0068 | 59.9529 | 59.9293 | 61.556 | 61.5936 | 61.3261 | 61.4908 | -1.5893 | -1.3594 | -1.6031 | -1.3731
440.3906 | 121.756 | -61.5921 | 60.0082 | 0.14017 | 0.009846 | -0.007421 | -0.029595 | 0.040843 | 0.090161 | -0.071874 | 59.9163 | 59.9564 | 59.9072 | 59.8881 | 61.4965 | 61.5387 | 61.2711 | 61.4451 | 61.7323 | 61.6019 | 61.5847 | 61.5625 | 61.6329 | 61.6823 | 61.5202 | 59.9621 | 60.0022 | 59.9529 | 59.9339 | 61.5423 | 61.5845 | 61.3169 | 61.4908 | -1.5802 | -1.3548 | -1.5893 | -1.364
442.1406 | 121.875 | -61.5692 | 59.9487 | 0.14932 | 0.009846 | -0.012 | -0.025017 | 0.036265 | 0.085583 | -0.08103 | 59.9163 | 59.9518 | 59.9163 | 59.8835 | 61.5056 | 61.5433 | 61.2711 | 61.4496 | 61.7185 | 61.5791 | 61.5572 | 61.5442 | 61.6055 | 61.6548 | 61.4882 | 59.9621 | 59.9976 | 59.9621 | 59.9293 | 61.5514 | 61.589 | 61.3169 | 61.4954 | -1.5893 | -1.3548 | -1.5893 | -1.3548
443.8281 | 121.8704 | -61.4822 | 60.0449 | 0.14932 | 0.005267 | -0.007421 | -0.025017 | 0.036265 | 0.090161 | -0.076452 | 59.9255 | 59.9564 | 59.9072 | 59.8835 | 61.5148 | 61.5478 | 61.2803 | 61.4451 | 61.6316 | 61.4875 | 61.4748 | 61.4572 | 61.5185 | 61.5724 | 61.4058 | 59.9712 | 60.0022 | 59.9529 | 59.9293 | 61.5606 | 61.5936 | 61.3261 | 61.4908 | -1.5893 | -1.3548 | -1.6076 | -1.3731
445.5156 | 121.8567 | -61.496 | 60.0494 | 0.14474 | 0.005267 | -0.002842 | -0.038752 | 0.031687 | 0.09474 | -0.071874 | 59.9209 | 59.9564 | 59.9072 | 59.879 | 61.5102 | 61.5433 | 61.2803 | 61.4496 | 61.6407 | 61.5012 | 61.4931 | 61.4572 | 61.5277 | 61.5907 | 61.4241 | 59.9667 | 60.0022 | 59.9529 | 59.9247 | 61.556 | 61.589 | 61.3261 | 61.4954 | -1.5893 | -1.3594 | -1.6031 | -1.3731
447.2656 | 121.788 | -61.5784 | 60.0311 | 0.14474 | 0.009846 | -0.007421 | -0.034174 | 0.036265 | 0.085583 | -0.071874 | 59.9255 | 59.961 | 59.9026 | 59.8835 | 61.5056 | 61.5478 | 61.2711 | 61.4405 | 61.7231 | 61.5882 | 61.5709 | 61.5442 | 61.6146 | 61.664 | 61.5065 | 59.9712 | 60.0068 | 59.9484 | 59.9293 | 61.5514 | 61.5936 | 61.3169 | 61.4863 | -1.5802 | -1.3457 | -1.6031 | -1.3685
449.0312 | 121.756 | -61.615 | 60.0082 | 0.14474 | 0.009846 | -0.007421 | -0.025017 | 0.040843 | 0.09474 | -0.076452 | 59.9209 | 59.9564 | 59.9117 | 59.879 | 61.5102 | 61.5387 | 61.2666 | 61.4451 | 61.7597 | 61.6248 | 61.6076 | 61.59 | 61.6558 | 61.7097 | 61.5385 | 59.9667 | 60.0022 | 59.9575 | 59.9247 | 61.556 | 61.5845 | 61.3123 | 61.4908 | -1.5893 | -1.3457 | -1.5985 | -1.3548
450.7969 | 121.7422 | -61.5875 | 60.0357 | 0.1539 | 0.005267 | -0.002842 | -0.029595 | 0.036265 | 0.09474 | -0.076452 | 59.9255 | 59.9518 | 59.9072 | 59.879 | 61.5102 | 61.5387 | 61.2757 | 61.4405 | 61.7414 | 61.5928 | 61.5847 | 61.5579 | 61.6238 | 61.6823 | 61.5111 | 59.9712 | 59.9976 | 59.9529 | 59.9247 | 61.556 | 61.5845 | 61.3215 | 61.4863 | -1.5847 | -1.3502 | -1.6031 | -1.3685
452.4844 | 121.8063 | -61.5189 | 60.0723 | 0.14017 | 0.005267 | -0.007421 | -0.029595 | 0.036265 | 0.090161 | -0.071874 | 59.9255 | 59.9473 | 59.9072 | 59.8835 | 61.5056 | 61.5387 | 61.2757 | 61.4405 | 61.659 | 61.5241 | 61.5114 | 61.4893 | 61.5551 | 61.609 | 61.447 | 59.9712 | 59.993 | 59.9529 | 59.9293 | 61.5514 | 61.5845 | 61.3215 | 61.4863 | -1.5802 | -1.3502 | -1.5985 | -1.3685
454.25 | 121.7514 | -61.5738 | 59.9991 | 0.14474 | 0.009846 | -0.007421 | -0.025017 | 0.031687 | 0.085583 | -0.08103 | 59.9209 | 59.9564 | 59.9072 | 59.8881 | 61.5056 | 61.5387 | 61.2803 | 61.4451 | 61.7185 | 61.5836 | 61.5664 | 61.5488 | 61.6055 | 61.6594 | 61.4928 | 59.9667 | 60.0022 | 59.9529 | 59.9339 | 61.5514 | 61.5845 | 61.3261 | 61.4908 | -1.5847 | -1.3594 | -1.5985 | -1.3731
455.9375 | 121.7239 | -61.5784 | 60.0311 | 0.14474 | 0.009846 | -0.007421 | -0.029595 | 0.036265 | 0.081005 | -0.08103 | 59.9255 | 59.9564 | 59.9163 | 59.879 | 61.5148 | 61.5524 | 61.2711 | 61.4405 | 61.7231 | 61.5882 | 61.5709 | 61.5488 | 61.6146 | 61.6594 | 61.4973 | 59.9712 | 60.0022 | 59.9621 | 59.9247 | 61.5606 | 61.5982 | 61.3169 | 61.4863 | -1.5893 | -1.3457 | -1.5985 | -1.3548
457.6875 | 121.8567 | -61.5417 | 59.9716 | 0.14017 | 0.009846 | -0.012 | -0.025017 | 0.036265 | 0.085583 | -0.071874 | 59.9209 | 59.9564 | 59.9072 | 59.879 | 61.5102 | 61.5433 | 61.2757 | 61.4451 | 61.6819 | 61.5516 | 61.5297 | 61.5167 | 61.578 | 61.6273 | 61.4699 | 59.9667 | 60.0022 | 59.9529 | 59.9247 | 61.556 | 61.589 | 61.3215 | 61.4908 | -1.5893 | -1.3548 | -1.6031 | -1.3685
459.3906 | 121.8475 | -61.5417 | 59.967 | 0.14474 | 0.005267 | -0.002842 | -0.034174 | 0.031687 | 0.090161 | -0.076452 | 59.9163 | 59.9518 | 59.9026 | 59.8927 | 61.5148 | 61.5433 | 61.2803 | 61.4405 | 61.6865 | 61.547 | 61.5389 | 61.5076 | 61.5734 | 61.6319 | 61.4653 | 59.9621 | 59.9976 | 59.9484 | 59.9385 | 61.5606 | 61.589 | 61.3261 | 61.4863 | -1.5985 | -1.364 | -1.6122 | -1.3777
461.1406 | 121.8933 | -61.5143 | 60.0311 | 0.13559 | 0.000689 | -0.016578 | -0.029595 | 0.031687 | 0.09474 | -0.076452 | 59.9117 | 59.9518 | 59.9117 | 59.8835 | 61.5102 | 61.5433 | 61.2757 | 61.4405 | 61.6499 | 61.515 | 61.4977 | 61.4847 | 61.546 | 61.609 | 61.4378 | 59.9575 | 59.9976 | 59.9575 | 59.9293 | 61.556 | 61.589 | 61.3215 | 61.4863 | -1.5985 | -1.364 | -1.5985 | -1.364
462.9062 | 121.8796 | -61.5555 | 59.9762 | 0.14017 | 0.000689 | -0.012 | -0.025017 | 0.036265 | 0.09474 | -0.076452 | 59.9255 | 59.9518 | 59.9072 | 59.8881 | 61.5102 | 61.5387 | 61.2757 | 61.4451 | 61.6956 | 61.5562 | 61.5435 | 61.5305 | 61.5917 | 61.6502 | 61.479 | 59.9712 | 59.9976 | 59.9529 | 59.9339 | 61.556 | 61.5845 | 61.3215 | 61.4908 | -1.5847 | -1.3502 | -1.6031 | -1.3685
464.6719 | 121.756 | -61.5051 | 60.1135 | 0.14474 | 0.009846 | -0.012 | -0.025017 | 0.036265 | 0.09474 | -0.076452 | 59.9163 | 59.9518 | 59.9072 | 59.879 | 61.5148 | 61.5478 | 61.2757 | 61.4496 | 61.6499 | 61.515 | 61.4931 | 61.4801 | 61.5414 | 61.5999 | 61.4287 | 59.9621 | 59.9976 | 59.9529 | 59.9247 | 61.5606 | 61.5936 | 61.3215 | 61.4954 | -1.5985 | -1.3594 | -1.6076 | -1.3685
466.4062 | 121.7926 | -61.5509 | 60.0357 | 0.1539 | 0.005267 | -0.012 | -0.029595 | 0.040843 | 0.09474 | -0.085608 | 59.9209 | 59.9564 | 59.9072 | 59.8698 | 61.5102 | 61.5387 | 61.2757 | 61.4496 | 61.7048 | 61.5562 | 61.5389 | 61.5213 | 61.5917 | 61.6456 | 61.4653 | 59.9667 | 60.0022 | 59.9529 | 59.9156 | 61.556 | 61.5845 | 61.3215 | 61.4954 | -1.5893 | -1.3548 | -1.6031 | -1.3685
468.0938 | 121.788 | -61.5189 | 60.0677 | 0.14017 | 0.005267 | -0.007421 | -0.025017 | 0.036265 | 0.085583 | -0.076452 | 59.9209 | 59.9473 | 59.9117 | 59.8881 | 61.5056 | 61.5478 | 61.2803 | 61.4496 | 61.659 | 61.5241 | 61.5114 | 61.4938 | 61.5551 | 61.6044 | 61.4424 | 59.9667 | 59.993 | 59.9575 | 59.9339 | 61.5514 | 61.5936 | 61.3261 | 61.4954 | -1.5847 | -1.3594 | -1.5939 | -1.3685
469.8594 | 121.7514 | -61.528 | 60.0906 | 0.14017 | 0.000689 | -0.016578 | -0.025017 | 0.036265 | 0.085583 | -0.076452 | 59.9209 | 59.9518 | 59.9072 | 59.8881 | 61.5148 | 61.5387 | 61.2803 | 61.4496 | 61.6682 | 61.5287 | 61.5114 | 61.503 | 61.5643 | 61.6136 | 61.4516 | 59.9667 | 59.9976 | 59.9529 | 59.9339 | 61.5606 | 61.5845 | 61.3261 | 61.4954 | -1.5939 | -1.3594 | -1.6076 | -1.3731
471.5469 | 121.8704 | -61.4639 | 60.0174 | 0.14932 | 0.000689 | -0.007421 | -0.029595 | 0.040843 | 0.090161 | -0.071874 | 59.9255 | 59.9473 | 59.9072 | 59.879 | 61.5056 | 61.5433 | 61.2757 | 61.4496 | 61.6132 | 61.4646 | 61.4565 | 61.4343 | 61.5048 | 61.5541 | 61.3921 | 59.9712 | 59.993 | 59.9529 | 59.9247 | 61.5514 | 61.589 | 61.3215 | 61.4954 | -1.5802 | -1.3502 | -1.5985 | -1.3685
473.3125 | 121.8384 | -61.5784 | 59.967 | 0.14474 | 0.000689 | -0.007421 | -0.029595 | 0.036265 | 0.085583 | -0.067295 | 59.9209 | 59.9564 | 59.9072 | 59.8881 | 61.5148 | 61.5433 | 61.2666 | 61.4451 | 61.7231 | 61.5791 | 61.5709 | 61.5488 | 61.6146 | 61.664 | 61.5111 | 59.9667 | 60.0022 | 59.9529 | 59.9339 | 61.5606 | 61.589 | 61.3123 | 61.4908 | -1.5939 | -1.3457 | -1.6076 | -1.3594
475 | 121.8475 | -61.5372 | 60.0357 | 0.14474 | 0.005267 | -0.012 | -0.029595 | 0.036265 | 0.085583 | -0.062717 | 59.9209 | 59.9564 | 59.9072 | 59.8881 | 61.5102 | 61.5387 | 61.2757 | 61.4405 | 61.6819 | 61.5424 | 61.5252 | 61.5076 | 61.5734 | 61.6228 | 61.4745 | 59.9667 | 60.0022 | 59.9529 | 59.9339 | 61.556 | 61.5845 | 61.3215 | 61.4863 | -1.5893 | -1.3548 | -1.6031 | -1.3685
476.7344 | 121.8155 | -61.5234 | 60.0632 | 0.14474 | 0.005267 | -0.007421 | -0.029595 | 0.036265 | 0.090161 | -0.071874 | 59.9255 | 59.9473 | 59.9163 | 59.8881 | 61.5056 | 61.5433 | 61.2711 | 61.4451 | 61.6682 | 61.5287 | 61.516 | 61.4938 | 61.5597 | 61.6136 | 61.4516 | 59.9712 | 59.993 | 59.9621 | 59.9339 | 61.5514 | 61.589 | 61.3169 | 61.4908 | -1.5802 | -1.3457 | -1.5893 | -1.3548
478.4844 | 121.8521 | -61.5509 | 59.9808 | 0.14932 | 0.000689 | -0.012 | -0.025017 | 0.031687 | 0.085583 | -0.076452 | 59.9255 | 59.9564 | 59.9072 | 59.879 | 61.5102 | 61.5387 | 61.2803 | 61.4451 | 61.7002 | 61.5516 | 61.5389 | 61.5259 | 61.5826 | 61.6365 | 61.4745 | 59.9712 | 60.0022 | 59.9529 | 59.9247 | 61.556 | 61.5845 | 61.3261 | 61.4908 | -1.5847 | -1.3548 | -1.6031 | -1.3731
480.1875 | 121.7514 | -61.5189 | 60.0861 | 0.14474 | 0.000689 | -0.016578 | -0.029595 | 0.036265 | 0.090161 | -0.08103 | 59.9209 | 59.9518 | 59.9026 | 59.8881 | 61.5102 | 61.5387 | 61.2803 | 61.4451 | 61.6636 | 61.5195 | 61.5023 | 61.4893 | 61.5551 | 61.609 | 61.4378 | 59.9667 | 59.9976 | 59.9484 | 59.9339 | 61.556 | 61.5845 | 61.3261 | 61.4908 | -1.5893 | -1.3594 | -1.6076 | -1.3777
481.9375 | 121.8475 | -61.5509 | 59.9808 | 0.14017 | 0.000689 | -0.012 | -0.029595 | 0.040843 | 0.090161 | -0.076452 | 59.9209 | 59.9564 | 59.9072 | 59.8835 | 61.5102 | 61.5387 | 61.262 | 61.4451 | 61.6911 | 61.5516 | 61.5389 | 61.5213 | 61.5917 | 61.6411 | 61.4745 | 59.9667 | 60.0022 | 59.9529 | 59.9293 | 61.556 | 61.5845 | 61.3077 | 61.4908 | -1.5893 | -1.3411 | -1.6031 | -1.3548
483.6875 | 121.7834 | -61.5601 | 60.0357 | 0.14017 | 0.000689 | -0.012 | -0.029595 | 0.036265 | 0.09474 | -0.071874 | 59.9209 | 59.9564 | 59.9117 | 59.8835 | 61.5011 | 61.5433 | 61.2757 | 61.4451 | 61.7002 | 61.5607 | 61.5481 | 61.5305 | 61.5963 | 61.6548 | 61.4882 | 59.9667 | 60.0022 | 59.9575 | 59.9293 | 61.5468 | 61.589 | 61.3215 | 61.4908 | -1.5802 | -1.3548 | -1.5893 | -1.364
485.4375 | 121.7743 | -61.5555 | 60.0403 | 0.14474 | 0.005267 | -0.012 | -0.020438 | 0.036265 | 0.085583 | -0.067295 | 59.9209 | 59.9564 | 59.9026 | 59.8835 | 61.5102 | 61.5433 | 61.2666 | 61.4451 | 61.7002 | 61.5607 | 61.5435 | 61.535 | 61.5917 | 61.6411 | 61.4882 | 59.9667 | 60.0022 | 59.9484 | 59.9293 | 61.556 | 61.589 | 61.3123 | 61.4908 | -1.5893 | -1.3457 | -1.6076 | -1.364
487.125 | 121.8063 | -61.5372 | 60.0403 | 0.14932 | 0.000689 | -0.012 | -0.029595 | 0.031687 | 0.085583 | -0.076452 | 59.9255 | 59.9518 | 59.9117 | 59.879 | 61.5148 | 61.5433 | 61.2666 | 61.4405 | 61.6865 | 61.5379 | 61.5252 | 61.5076 | 61.5689 | 61.6228 | 61.4607 | 59.9712 | 59.9976 | 59.9575 | 59.9247 | 61.5606 | 61.589 | 61.3123 | 61.4863 | -1.5893 | -1.3411 | -1.6031 | -1.3548
488.875 | 121.7697 | -61.6104 | 59.9899 | 0.14474 | 0.005267 | -0.007421 | -0.034174 | 0.036265 | 0.090161 | -0.076452 | 59.9209 | 59.9564 | 59.9117 | 59.8835 | 61.5102 | 61.5341 | 61.2666 | 61.4496 | 61.7552 | 61.6157 | 61.603 | 61.5762 | 61.6467 | 61.7006 | 61.534 | 59.9667 | 60.0022 | 59.9575 | 59.9293 | 61.556 | 61.5799 | 61.3123 | 61.4954 | -1.5893 | -1.3457 | -1.5985 | -1.3548
490.625 | 121.7377 | -61.5921 | 60.022 | 0.14474 | -0.00389 | -0.016578 | -0.025017 | 0.040843 | 0.085583 | -0.071874 | 59.9117 | 59.9518 | 59.9117 | 59.8835 | 61.5056 | 61.5478 | 61.2711 | 61.4451 | 61.7368 | 61.5882 | 61.5755 | 61.5671 | 61.6329 | 61.6777 | 61.5202 | 59.9575 | 59.9976 | 59.9575 | 59.9293 | 61.5514 | 61.5936 | 61.3169 | 61.4908 | -1.5939 | -1.3594 | -1.5939 | -1.3594
492.3906 | 121.8246 | -61.5372 | 60.0082 | 0.14932 | 0.005267 | -0.007421 | -0.029595 | 0.036265 | 0.085583 | -0.076452 | 59.9255 | 59.9518 | 59.9117 | 59.879 | 61.5102 | 61.5433 | 61.2666 | 61.4359 | 61.6865 | 61.5424 | 61.5297 | 61.5076 | 61.5734 | 61.6228 | 61.4607 | 59.9712 | 59.9976 | 59.9575 | 59.9247 | 61.556 | 61.589 | 61.3123 | 61.4817 | -1.5847 | -1.3411 | -1.5985 | -1.3548
494.0781 | 121.8246 | -61.5417 | 60.0403 | 0.14474 | 0.000689 | -0.016578 | -0.029595 | 0.036265 | 0.085583 | -0.076452 | 59.9163 | 59.9518 | 59.9072 | 59.879 | 61.5102 | 61.5433 | 61.2757 | 61.4405 | 61.6865 | 61.5424 | 61.5252 | 61.5122 | 61.578 | 61.6273 | 61.4653 | 59.9621 | 59.9976 | 59.9529 | 59.9247 | 61.556 | 61.589 | 61.3215 | 61.4863 | -1.5939 | -1.3594 | -1.6031 | -1.3685
495.8281 | 121.8384 | -61.5509 | 60.0082 | 0.14017 | 0.005267 | -0.007421 | -0.025017 | 0.031687 | 0.085583 | -0.071874 | 59.9255 | 59.9518 | 59.9117 | 59.8881 | 61.5148 | 61.5295 | 61.2757 | 61.4405 | 61.6911 | 61.5562 | 61.5435 | 61.5259 | 61.5826 | 61.6365 | 61.479 | 59.9712 | 59.9976 | 59.9575 | 59.9339 | 61.5606 | 61.5753 | 61.3215 | 61.4863 | -1.5893 | -1.3502 | -1.6031 | -1.364
497.5156 | 121.7377 | -61.5829 | 60.0357 | 0.14932 | 0.000689 | -0.012 | -0.025017 | 0.036265 | 0.090161 | -0.076452 | 59.9209 | 59.9656 | 59.9117 | 59.8744 | 61.5011 | 61.5478 | 61.2666 | 61.4451 | 61.7323 | 61.5836 | 61.5709 | 61.5579 | 61.6192 | 61.6731 | 61.5065 | 59.9667 | 60.0113 | 59.9575 | 59.9201 | 61.5468 | 61.5936 | 61.3123 | 61.4908 | -1.5802 | -1.3457 | -1.5893 | -1.3548
499.2656 | 121.7651 | -61.5189 | 60.1044 | 0.14474 | 0.000689 | -0.007421 | -0.034174 | 0.040843 | 0.09474 | -0.076452 | 59.9255 | 59.9518 | 59.9163 | 59.879 | 61.5102 | 61.5433 | 61.2757 | 61.4451 | 61.6636 | 61.5195 | 61.5114 | 61.4847 | 61.5597 | 61.6136 | 61.4424 | 59.9712 | 59.9976 | 59.9621 | 59.9247 | 61.556 | 61.589 | 61.3215 | 61.4908 | -1.5847 | -1.3502 | -1.5939 | -1.3594
501.0156 | 121.756 | -61.6104 | 59.9991 | 0.14474 | -0.00389 | -0.016578 | -0.025017 | 0.031687 | 0.090161 | -0.076452 | 59.9209 | 59.9564 | 59.9026 | 59.879 | 61.5102 | 61.5387 | 61.2757 | 61.4405 | 61.7552 | 61.6065 | 61.5938 | 61.5854 | 61.6421 | 61.7006 | 61.534 | 59.9667 | 60.0022 | 59.9484 | 59.9247 | 61.556 | 61.5845 | 61.3215 | 61.4863 | -1.5893 | -1.3548 | -1.6076 | -1.3731
502.7656 | 121.8933 | -61.4914 | 60.0449 | 0.14474 | 0.000689 | -0.012 | -0.029595 | 0.031687 | 0.085583 | -0.071874 | 59.9209 | 59.9518 | 59.9117 | 59.8835 | 61.5056 | 61.5433 | 61.2757 | 61.4405 | 61.6361 | 61.4921 | 61.4794 | 61.4618 | 61.5231 | 61.577 | 61.4195 | 59.9667 | 59.9976 | 59.9575 | 59.9293 | 61.5514 | 61.589 | 61.3215 | 61.4863 | -1.5847 | -1.3548 | -1.5939 | -1.364
504.4531 | 121.7789 | -61.5326 | 60.0861 | 0.14474 | -0.00389 | -0.007421 | -0.029595 | 0.036265 | 0.090161 | -0.08103 | 59.9163 | 59.9518 | 59.9117 | 59.879 | 61.5056 | 61.5387 | 61.2711 | 61.4359 | 61.6773 | 61.5287 | 61.5252 | 61.503 | 61.5689 | 61.6228 | 61.4516 | 59.9621 | 59.9976 | 59.9575 | 59.9247 | 61.5514 | 61.5845 | 61.3169 | 61.4817 | -1.5893 | -1.3548 | -1.5939 | -1.3594
506.1875 | 121.7926 | -61.528 | 60.0494 | 0.14474 | 0.000689 | -0.012 | -0.029595 | 0.031687 | 0.090161 | -0.076452 | 59.9255 | 59.9518 | 59.9117 | 59.8835 | 61.5102 | 61.5433 | 61.2711 | 61.4359 | 61.6728 | 61.5287 | 61.516 | 61.4984 | 61.5597 | 61.6182 | 61.4516 | 59.9712 | 59.9976 | 59.9575 | 59.9293 | 61.556 | 61.589 | 61.3169 | 61.4817 | -1.5847 | -1.3457 | -1.5985 | -1.3594
507.9375 | 121.7926 | -61.5829 | 60.0174 | 0.14474 | -0.00389 | -0.007421 | -0.034174 | 0.036265 | 0.090161 | -0.071874 | 59.9209 | 59.9656 | 59.9209 | 59.8835 | 61.5102 | 61.5387 | 61.2711 | 61.4451 | 61.7277 | 61.5791 | 61.5755 | 61.5488 | 61.6192 | 61.6731 | 61.5111 | 59.9667 | 60.0113 | 59.9667 | 59.9293 | 61.556 | 61.5845 | 61.3169 | 61.4908 | -1.5893 | -1.3502 | -1.5893 | -1.3502
509.6406 | 121.7331 | -61.5921 | 60.0311 | 0.14474 | 0.014425 | -0.012 | -0.020438 | 0.040843 | 0.081005 | -0.076452 | 59.9209 | 59.9564 | 59.9117 | 59.879 | 61.5102 | 61.5387 | 61.2666 | 61.4451 | 61.7368 | 61.6065 | 61.5801 | 61.5717 | 61.6329 | 61.6731 | 61.5156 | 59.9667 | 60.0022 | 59.9575 | 59.9247 | 61.556 | 61.5845 | 61.3123 | 61.4908 | -1.5893 | -1.3457 | -1.5985 | -1.3548
511.3906 | 121.875 | -61.5646 | 59.9579 | 0.14932 | 0.000689 | -0.012 | -0.01586 | 0.031687 | 0.09474 | -0.076452 | 59.9209 | 59.9564 | 59.9026 | 59.8835 | 61.5056 | 61.5478 | 61.2757 | 61.4405 | 61.714 | 61.5653 | 61.5526 | 61.5488 | 61.5963 | 61.6594 | 61.4882 | 59.9667 | 60.0022 | 59.9484 | 59.9293 | 61.5514 | 61.5936 | 61.3215 | 61.4863 | -1.5847 | -1.3548 | -1.6031 | -1.3731
513.1406 | 121.8704 | -61.4914 | 60.0586 | 0.14474 | 0.005267 | -0.007421 | -0.029595 | 0.031687 | 0.085583 | -0.08103 | 59.9209 | 59.9518 | 59.9117 | 59.879 | 61.5148 | 61.5478 | 61.2757 | 61.4496 | 61.6361 | 61.4967 | 61.484 | 61.4618 | 61.5231 | 61.577 | 61.4104 | 59.9667 | 59.9976 | 59.9575 | 59.9247 | 61.5606 | 61.5936 | 61.3215 | 61.4954 | -1.5939 | -1.3548 | -1.6031 | -1.364
514.8281 | 121.7606 | -61.5509 | 60.0403 | 0.14932 | 0.005267 | -0.012 | -0.029595 | 0.036265 | 0.085583 | -0.076452 | 59.9209 | 59.9518 | 59.9117 | 59.8744 | 61.5148 | 61.5387 | 61.2757 | 61.4496 | 61.7002 | 61.5562 | 61.5389 | 61.5213 | 61.5872 | 61.6365 | 61.4745 | 59.9667 | 59.9976 | 59.9575 | 59.9201 | 61.5606 | 61.5845 | 61.3215 | 61.4954 | -1.5939 | -1.3548 | -1.6031 | -1.364
516.5781 | 121.875 | -61.5601 | 59.9533 | 0.14474 | 0.005267 | -0.016578 | -0.025017 | 0.031687 | 0.099318 | -0.076452 | 59.93 | 59.961 | 59.9072 | 59.8835 | 61.5056 | 61.5478 | 61.2666 | 61.4405 | 61.7048 | 61.5653 | 61.5435 | 61.535 | 61.5917 | 61.6594 | 61.4836 | 59.9758 | 60.0068 | 59.9529 | 59.9293 | 61.5514 | 61.5936 | 61.3123 | 61.4863 | -1.5756 | -1.3365 | -1.5985 | -1.3594
518.3281 | 121.7422 | -61.5692 | 60.0082 | 0.14932 | 0.000689 | -0.016578 | -0.029595 | 0.040843 | 0.090161 | -0.076452 | 59.9255 | 59.9564 | 59.9163 | 59.8835 | 61.5102 | 61.5387 | 61.2711 | 61.4496 | 61.7185 | 61.5699 | 61.5526 | 61.5396 | 61.6101 | 61.6594 | 61.4928 | 59.9712 | 60.0022 | 59.9621 | 59.9293 | 61.556 | 61.5845 | 61.3169 | 61.4954 | -1.5847 | -1.3457 | -1.5939 | -1.3548
520.0156 | 121.843 | -61.5189 | 60.0174 | 0.14474 | 0.005267 | -0.007421 | -0.029595 | 0.045421 | 0.085583 | -0.071874 | 59.9209 | 59.9518 | 59.9117 | 59.879 | 61.5102 | 61.5387 | 61.2757 | 61.4496 | 61.6636 | 61.5241 | 61.5114 | 61.4893 | 61.5643 | 61.6044 | 61.447 | 59.9667 | 59.9976 | 59.9575 | 59.9247 | 61.556 | 61.5845 | 61.3215 | 61.4954 | -1.5893 | -1.3548 | -1.5985 | -1.364
521.7656 | 121.8475 | -61.5692 | 60.0037 | 0.14932 | 0.000689 | -0.012 | -0.029595 | 0.036265 | 0.09474 | -0.076452 | 59.9209 | 59.9518 | 59.9072 | 59.879 | 61.5056 | 61.5387 | 61.2803 | 61.4451 | 61.7185 | 61.5699 | 61.5572 | 61.5396 | 61.6055 | 61.664 | 61.4928 | 59.9667 | 59.9976 | 59.9529 | 59.9247 | 61.5514 | 61.5845 | 61.3261 | 61.4908 | -1.5847 | -1.3594 | -1.5985 | -1.3731
523.4531 | 121.7422 | -61.5189 | 60.1044 | 0.14017 | 0.000689 | -0.012 | -0.025017 | 0.031687 | 0.090161 | -0.076452 | 59.9209 | 59.9473 | 59.9117 | 59.879 | 61.5102 | 61.5387 | 61.2803 | 61.4451 | 61.659 | 61.5195 | 61.5069 | 61.4938 | 61.5505 | 61.609 | 61.4424 | 59.9667 | 59.993 | 59.9575 | 59.9247 | 61.556 | 61.5845 | 61.3261 | 61.4908 | -1.5893 | -1.3594 | -1.5985 | -1.3685
525.2031 | 121.8567 | -61.4914 | 60.0311 | 0.14474 | -0.00389 | -0.012 | -0.025017 | 0.031687 | 0.090161 | -0.076452 | 59.9255 | 59.961 | 59.9072 | 59.8881 | 61.5148 | 61.5478 | 61.2757 | 61.4451 | 61.6361 | 61.4875 | 61.4794 | 61.4664 | 61.5231 | 61.5816 | 61.4149 | 59.9712 | 60.0068 | 59.9529 | 59.9339 | 61.5606 | 61.5936 | 61.3215 | 61.4908 | -1.5893 | -1.3502 | -1.6076 | -1.3685
526.9531 | 121.8475 | -61.5463 | 59.9716 | 0.14932 | 0.000689 | -0.012 | -0.020438 | 0.036265 | 0.085583 | -0.076452 | 59.9163 | 59.961 | 59.9072 | 59.879 | 61.5011 | 61.5387 | 61.2757 | 61.4542 | 61.6956 | 61.547 | 61.5343 | 61.5259 | 61.5826 | 61.6319 | 61.4699 | 59.9621 | 60.0068 | 59.9529 | 59.9247 | 61.5468 | 61.5845 | 61.3215 | 61.5 | -1.5847 | -1.3594 | -1.5939 | -1.3685
528.6406 | 121.7606 | -61.5646 | 60.022 | 0.14932 | 0.000689 | -0.007421 | -0.020438 | 0.040843 | 0.090161 | -0.062717 | 59.93 | 59.961 | 59.9117 | 59.879 | 61.5102 | 61.5387 | 61.2757 | 61.4405 | 61.714 | 61.5653 | 61.5572 | 61.5442 | 61.6055 | 61.6548 | 61.5019 | 59.9758 | 60.0068 | 59.9575 | 59.9247 | 61.556 | 61.5845 | 61.3215 | 61.4863 | -1.5802 | -1.3457 | -1.5985 | -1.364
530.4062 | 121.788 | -61.528 | 60.0723 | 0.14932 | 0.000689 | -0.012 | -0.025017 | 0.036265 | 0.090161 | -0.08103 | 59.9163 | 59.9564 | 59.9117 | 59.879 | 61.5011 | 61.5387 | 61.2711 | 61.4451 | 61.6773 | 61.5287 | 61.516 | 61.503 | 61.5643 | 61.6182 | 61.447 | 59.9621 | 60.0022 | 59.9575 | 59.9247 | 61.5468 | 61.5845 | 61.3169 | 61.4908 | -1.5847 | -1.3548 | -1.5893 | -1.3594
532.1562 | 121.7422 | -61.528 | 60.0998 | 0.14932 | 0.005267 | -0.016578 | -0.020438 | 0.040843 | 0.099318 | -0.067295 | 59.9163 | 59.9564 | 59.9209 | 59.8835 | 61.5102 | 61.5433 | 61.2757 | 61.4496 | 61.6773 | 61.5333 | 61.5114 | 61.5076 | 61.5689 | 61.6273 | 61.4607 | 59.9621 | 60.0022 | 59.9667 | 59.9293 | 61.556 | 61.589 | 61.3215 | 61.4954 | -1.5939 | -1.3594 | -1.5893 | -1.3548
533.8438 | 121.8246 | -61.4914 | 60.0586 | 0.14932 | -0.013048 | -0.007421 | -0.029595 | 0.031687 | 0.085583 | -0.076452 | 59.9209 | 59.9564 | 59.9117 | 59.8835 | 61.5056 | 61.5478 | 61.2803 | 61.4405 | 61.6407 | 61.4783 | 61.484 | 61.4618 | 61.5231 | 61.577 | 61.4149 | 59.9667 | 60.0022 | 59.9575 | 59.9293 | 61.5514 | 61.5936 | 61.3261 | 61.4863 | -1.5847 | -1.3594 | -1.5939 | -1.3685
535.5938 | 121.8201 | -61.5417 | 59.9991 | 0.14017 | 0.000689 | -0.007421 | -0.029595 | 0.040843 | 0.090161 | -0.076452 | 59.9255 | 59.961 | 59.9117 | 59.879 | 61.5102 | 61.5387 | 61.2711 | 61.4451 | 61.6819 | 61.5424 | 61.5343 | 61.5122 | 61.5826 | 61.6319 | 61.4653 | 59.9712 | 60.0068 | 59.9575 | 59.9247 | 61.556 | 61.5845 | 61.3169 | 61.4908 | -1.5847 | -1.3457 | -1.5985 | -1.3594
537.3438 | 121.7422 | -61.5051 | 60.1227 | 0.14932 | 0.000689 | -0.016578 | -0.029595 | 0.031687 | 0.081005 | -0.071874 | 59.9209 | 59.9564 | 59.9072 | 59.8835 | 61.5102 | 61.5433 | 61.2757 | 61.4451 | 61.6544 | 61.5058 | 61.4885 | 61.4755 | 61.5368 | 61.5861 | 61.4333 | 59.9667 | 60.0022 | 59.9529 | 59.9293 | 61.556 | 61.589 | 61.3215 | 61.4908 | -1.5893 | -1.3548 | -1.6031 | -1.3685
539.0312 | 121.8979 | -61.4594 | 60.0311 | 0.14932 | -0.008469 | -0.012 | -0.025017 | 0.031687 | 0.090161 | -0.071874 | 59.9255 | 59.9518 | 59.9026 | 59.8835 | 61.5102 | 61.5433 | 61.2757 | 61.4405 | 61.6087 | 61.4509 | 61.4474 | 61.4343 | 61.491 | 61.5495 | 61.3875 | 59.9712 | 59.9976 | 59.9484 | 59.9293 | 61.556 | 61.589 | 61.3215 | 61.4863 | -1.5847 | -1.3502 | -1.6076 | -1.3731
540.7969 | 121.8201 | -61.528 | 60.022 | 0.14474 | -0.00389 | -0.016578 | -0.029595 | 0.036265 | 0.090161 | -0.076452 | 59.93 | 59.9564 | 59.9117 | 59.879 | 61.5102 | 61.5387 | 61.2711 | 61.4496 | 61.6728 | 61.5241 | 61.5114 | 61.4984 | 61.5643 | 61.6182 | 61.4516 | 59.9758 | 60.0022 | 59.9575 | 59.9247 | 61.556 | 61.5845 | 61.3169 | 61.4954 | -1.5802 | -1.3411 | -1.5985 | -1.3594
542.5469 | 121.756 | -61.5601 | 60.022 | 0.14474 | 0.000689 | -0.012 | -0.029595 | 0.031687 | 0.090161 | -0.071874 | 59.9209 | 59.9564 | 59.9117 | 59.8835 | 61.5056 | 61.5387 | 61.2803 | 61.4451 | 61.7048 | 61.5607 | 61.5481 | 61.5305 | 61.5917 | 61.6502 | 61.4882 | 59.9667 | 60.0022 | 59.9575 | 59.9293 | 61.5514 | 61.5845 | 61.3261 | 61.4908 | -1.5847 | -1.3594 | -1.5939 | -1.3685
544.2969 | 121.8018 | -61.5326 | 60.0494 | 0.14017 | -0.00389 | -0.007421 | -0.025017 | 0.036265 | 0.09474 | -0.071874 | 59.9163 | 59.9564 | 59.9117 | 59.879 | 61.5056 | 61.5433 | 61.2711 | 61.4359 | 61.6728 | 61.5287 | 61.5252 | 61.5076 | 61.5689 | 61.6273 | 61.4607 | 59.9621 | 60.0022 | 59.9575 | 59.9247 | 61.5514 | 61.589 | 61.3169 | 61.4817 | -1.5893 | -1.3548 | -1.5939 | -1.3594
546.0469 | 121.7377 | -61.5738 | 60.0403 | 0.14474 | 0.000689 | -0.016578 | -0.025017 | 0.036265 | 0.09474 | -0.076452 | 59.9209 | 59.9564 | 59.9117 | 59.879 | 61.5056 | 61.5387 | 61.2757 | 61.4451 | 61.7185 | 61.5745 | 61.5572 | 61.5488 | 61.6101 | 61.6685 | 61.4973 | 59.9667 | 60.0022 | 59.9575 | 59.9247 | 61.5514 | 61.5845 | 61.3215 | 61.4908 | -1.5847 | -1.3548 | -1.5939 | -1.364
547.7344 | 121.7926 | -61.5601 | 60.0494 | 0.14474 | -0.008469 | -0.007421 | -0.025017 | 0.031687 | 0.09474 | -0.076452 | 59.9255 | 59.9564 | 59.9072 | 59.879 | 61.5056 | 61.5433 | 61.2711 | 61.4496 | 61.7048 | 61.5516 | 61.5526 | 61.535 | 61.5917 | 61.6548 | 61.4836 | 59.9712 | 60.0022 | 59.9529 | 59.9247 | 61.5514 | 61.589 | 61.3169 | 61.4954 | -1.5802 | -1.3457 | -1.5985 | -1.364
549.4844 | 121.7468 | -61.5326 | 60.1044 | 0.14017 | 0.000689 | -0.007421 | -0.025017 | 0.036265 | 0.085583 | -0.076452 | 59.9163 | 59.9564 | 59.9072 | 59.8835 | 61.5056 | 61.5387 | 61.2757 | 61.4496 | 61.6728 | 61.5333 | 61.5252 | 61.5076 | 61.5689 | 61.6182 | 61.4561 | 59.9621 | 60.0022 | 59.9529 | 59.9293 | 61.5514 | 61.5845 | 61.3215 | 61.4954 | -1.5893 | -1.3594 | -1.5985 | -1.3685
551.25 | 121.8796 | -61.4777 | 60.0494 | 0.14932 | -0.00389 | -0.007421 | -0.025017 | 0.040843 | 0.081005 | -0.076452 | 59.9209 | 59.9564 | 59.9072 | 59.8835 | 61.5102 | 61.5433 | 61.2757 | 61.4451 | 61.627 | 61.4738 | 61.4702 | 61.4526 | 61.5185 | 61.5587 | 61.4012 | 59.9667 | 60.0022 | 59.9529 | 59.9293 | 61.556 | 61.589 | 61.3215 | 61.4908 | -1.5893 | -1.3548 | -1.6031 | -1.3685
552.9531 | 121.8292 | -61.5326 | 60.0082 | 0.14474 | -0.008469 | -0.007421 | -0.025017 | 0.036265 | 0.085583 | -0.076452 | 59.9255 | 59.9656 | 59.9117 | 59.879 | 61.5011 | 61.5387 | 61.2711 | 61.4405 | 61.6773 | 61.5241 | 61.5252 | 61.5076 | 61.5689 | 61.6182 | 61.4561 | 59.9712 | 60.0113 | 59.9575 | 59.9247 | 61.5468 | 61.5845 | 61.3169 | 61.4863 | -1.5756 | -1.3457 | -1.5893 | -1.3594
554.7031 | 121.843 | -61.4777 | 60.0952 | 0.14474 | -0.017627 | -0.012 | -0.029595 | 0.036265 | 0.085583 | -0.08103 | 59.9209 | 59.9564 | 59.9163 | 59.8744 | 61.5102 | 61.5433 | 61.2849 | 61.4451 | 61.6224 | 61.46 | 61.4657 | 61.4481 | 61.5139 | 61.5632 | 61.3966 | 59.9667 | 60.0022 | 59.9621 | 59.9201 | 61.556 | 61.589 | 61.3306 | 61.4908 | -1.5893 | -1.364 | -1.5939 | -1.3685
556.4688 | 121.8475 | -61.5326 | 59.9991 | 0.14932 | -0.00389 | -0.012 | -0.029595 | 0.036265 | 0.09474 | -0.08103 | 59.9117 | 59.961 | 59.9117 | 59.8835 | 61.5102 | 61.5433 | 61.2711 | 61.4405 | 61.6819 | 61.5287 | 61.5206 | 61.503 | 61.5689 | 61.6273 | 61.4516 | 59.9575 | 60.0068 | 59.9575 | 59.9293 | 61.556 | 61.589 | 61.3169 | 61.4863 | -1.5985 | -1.3594 | -1.5985 | -1.3594
558.2188 | 121.7834 | -61.5372 | 60.0815 | 0.14932 | -0.00389 | -0.007421 | -0.025017 | 0.031687 | 0.090161 | -0.076452 | 59.9163 | 59.9656 | 59.9117 | 59.879 | 61.5056 | 61.5387 | 61.2803 | 61.4405 | 61.6865 | 61.5333 | 61.5297 | 61.5122 | 61.5689 | 61.6273 | 61.4607 | 59.9621 | 60.0113 | 59.9575 | 59.9247 | 61.5514 | 61.5845 | 61.3261 | 61.4863 | -1.5893 | -1.364 | -1.5939 | -1.3685
559.9062 | 121.756 | -61.5601 | 60.0403 | 0.14474 | -0.00389 | -0.016578 | -0.025017 | 0.031687 | 0.09474 | -0.08103 | 59.9209 | 59.961 | 59.9117 | 59.8744 | 61.5102 | 61.5433 | 61.2711 | 61.4496 | 61.7048 | 61.5562 | 61.5435 | 61.535 | 61.5917 | 61.6548 | 61.479 | 59.9667 | 60.0068 | 59.9575 | 59.9201 | 61.556 | 61.589 | 61.3169 | 61.4954 | -1.5893 | -1.3502 | -1.5985 | -1.3594
561.6562 | 121.8704 | -61.496 | 60.054 | 0.14474 | -0.00389 | -0.002842 | -0.025017 | 0.036265 | 0.076426 | -0.076452 | 59.9255 | 59.9564 | 59.9117 | 59.8835 | 61.5056 | 61.5433 | 61.2711 | 61.4451 | 61.6407 | 61.4921 | 61.4931 | 61.471 | 61.5322 | 61.5724 | 61.4195 | 59.9712 | 60.0022 | 59.9575 | 59.9293 | 61.5514 | 61.589 | 61.3169 | 61.4908 | -1.5802 | -1.3457 | -1.5939 | -1.3594
563.3438 | 121.875 | -61.5601 | 59.9579 | 0.14474 | -0.00389 | -0.016578 | -0.029595 | 0.031687 | 0.081005 | -0.076452 | 59.9255 | 59.961 | 59.9026 | 59.879 | 61.5056 | 61.5433 | 61.2711 | 61.4451 | 61.7048 | 61.5562 | 61.5435 | 61.5305 | 61.5917 | 61.6411 | 61.4836 | 59.9712 | 60.0068 | 59.9484 | 59.9247 | 61.5514 | 61.589 | 61.3169 | 61.4908 | -1.5802 | -1.3457 | -1.6031 | -1.3685
565.0938 | 121.7377 | -61.5097 | 60.0998 | 0.14932 | 0.000689 | -0.012 | -0.025017 | 0.027109 | 0.090161 | -0.085608 | 59.9209 | 59.961 | 59.9117 | 59.8835 | 61.5011 | 61.5478 | 61.2757 | 61.4451 | 61.659 | 61.5104 | 61.4977 | 61.4847 | 61.5368 | 61.5999 | 61.4241 | 59.9667 | 60.0068 | 59.9575 | 59.9293 | 61.5468 | 61.5936 | 61.3215 | 61.4908 | -1.5802 | -1.3548 | -1.5893 | -1.364
566.8594 | 121.7972 | -61.5646 | 60.054 | 0.14474 | -0.00389 | -0.021157 | -0.029595 | 0.036265 | 0.090161 | -0.071874 | 59.9163 | 59.9473 | 59.9163 | 59.879 | 61.5011 | 61.5387 | 61.2757 | 61.4496 | 61.7094 | 61.5607 | 61.5435 | 61.535 | 61.6009 | 61.6548 | 61.4928 | 59.9621 | 59.993 | 59.9621 | 59.9247 | 61.5468 | 61.5845 | 61.3215 | 61.4954 | -1.5847 | -1.3594 | -1.5847 | -1.3594
568.6094 | 121.8658 | -61.528 | 59.9487 | 0.14932 | -0.00389 | -0.007421 | -0.034174 | 0.036265 | 0.090161 | -0.076452 | 59.9255 | 59.9518 | 59.9072 | 59.879 | 61.5148 | 61.5524 | 61.2711 | 61.4451 | 61.6773 | 61.5241 | 61.5206 | 61.4938 | 61.5643 | 61.6182 | 61.4516 | 59.9712 | 59.9976 | 59.9529 | 59.9247 | 61.5606 | 61.5982 | 61.3169 | 61.4908 | -1.5893 | -1.3457 | -1.6076 | -1.364
570.3594 | 121.8613 | -61.5326 | 59.9716 | 0.14474 | 0.000689 | -0.016578 | -0.025017 | 0.036265 | 0.081005 | -0.076452 | 59.9163 | 59.961 | 59.9117 | 59.8881 | 61.5102 | 61.5433 | 61.2666 | 61.4405 | 61.6773 | 61.5333 | 61.516 | 61.5076 | 61.5689 | 61.6136 | 61.4561 | 59.9621 | 60.0068 | 59.9575 | 59.9339 | 61.556 | 61.589 | 61.3123 | 61.4863 | -1.5939 | -1.3502 | -1.5985 | -1.3548
572.0469 | 121.843 | -61.5646 | 59.9945 | 0.14474 | -0.00389 | -0.016578 | -0.01586 | 0.045421 | 0.076426 | -0.076452 | 59.9209 | 59.9564 | 59.9117 | 59.879 | 61.5056 | 61.5478 | 61.2757 | 61.4496 | 61.7094 | 61.5607 | 61.5481 | 61.5488 | 61.6101 | 61.6411 | 61.4882 | 59.9667 | 60.0022 | 59.9575 | 59.9247 | 61.5514 | 61.5936 | 61.3215 | 61.4954 | -1.5847 | -1.3548 | -1.5939 | -1.364
573.7969 | 121.8155 | -61.5921 | 59.9716 | 0.14932 | -0.008469 | -0.016578 | -0.025017 | 0.040843 | 0.081005 | -0.076452 | 59.9209 | 59.9564 | 59.9117 | 59.8881 | 61.5102 | 61.5433 | 61.2711 | 61.4451 | 61.7414 | 61.5836 | 61.5755 | 61.5671 | 61.6329 | 61.6731 | 61.5156 | 59.9667 | 60.0022 | 59.9575 | 59.9339 | 61.556 | 61.589 | 61.3169 | 61.4908 | -1.5893 | -1.3502 | -1.5985 | -1.3594
575.5625 | 121.7743 | -61.5692 | 60.0403 | 0.14474 | 0.000689 | -0.021157 | -0.025017 | 0.036265 | 0.081005 | -0.08103 | 59.9209 | 59.9564 | 59.9163 | 59.8835 | 61.5056 | 61.5433 | 61.2757 | 61.4451 | 61.714 | 61.5699 | 61.5481 | 61.5442 | 61.6055 | 61.6502 | 61.4882 | 59.9667 | 60.0022 | 59.9621 | 59.9293 | 61.5514 | 61.589 | 61.3215 | 61.4908 | -1.5847 | -1.3548 | -1.5893 | -1.3594
577.3125 | 121.8567 | -61.4822 | 60.0311 | 0.14932 | -0.008469 | -0.016578 | -0.025017 | 0.031687 | 0.090161 | -0.076452 | 59.9209 | 59.961 | 59.9117 | 59.879 | 61.5056 | 61.5433 | 61.2711 | 61.4451 | 61.6316 | 61.4738 | 61.4657 | 61.4572 | 61.5139 | 61.5724 | 61.4058 | 59.9667 | 60.0068 | 59.9575 | 59.9247 | 61.5514 | 61.589 | 61.3169 | 61.4908 | -1.5847 | -1.3502 | -1.5939 | -1.3594
579 | 121.8246 | -61.5738 | 59.967 | 0.14932 | -0.00389 | -0.012 | -0.025017 | 0.036265 | 0.085583 | -0.076452 | 59.9255 | 59.9564 | 59.9117 | 59.8835 | 61.5194 | 61.5387 | 61.2711 | 61.4451 | 61.7231 | 61.5699 | 61.5618 | 61.5488 | 61.6101 | 61.6594 | 61.4973 | 59.9712 | 60.0022 | 59.9575 | 59.9293 | 61.5651 | 61.5845 | 61.3169 | 61.4908 | -1.5939 | -1.3457 | -1.6076 | -1.3594
580.7812 | 121.7834 | -61.5372 | 60.0403 | 0.14474 | 0.005267 | -0.012 | -0.025017 | 0.036265 | 0.085583 | -0.071874 | 59.9209 | 59.961 | 59.9117 | 59.8835 | 61.5056 | 61.5433 | 61.2757 | 61.4405 | 61.6819 | 61.5424 | 61.5252 | 61.5122 | 61.5734 | 61.6228 | 61.4653 | 59.9667 | 60.0068 | 59.9575 | 59.9293 | 61.5514 | 61.589 | 61.3215 | 61.4863 | -1.5847 | -1.3548 | -1.5939 | -1.364
582.4844 | 121.8384 | -61.5417 | 59.9899 | 0.14474 | 0.000689 | -0.016578 | -0.025017 | 0.031687 | 0.09474 | -0.076452 | 59.9163 | 59.9564 | 59.9072 | 59.879 | 61.5102 | 61.5478 | 61.2757 | 61.4451 | 61.6865 | 61.5424 | 61.5252 | 61.5167 | 61.5734 | 61.6365 | 61.4653 | 59.9621 | 60.0022 | 59.9529 | 59.9247 | 61.556 | 61.5936 | 61.3215 | 61.4908 | -1.5939 | -1.3594 | -1.6031 | -1.3685
584.25 | 121.8796 | -61.5555 | 59.9625 | 0.14474 | -0.00389 | -0.016578 | -0.029595 | 0.040843 | 0.090161 | -0.076452 | 59.9209 | 59.961 | 59.9163 | 59.8744 | 61.5056 | 61.5433 | 61.2711 | 61.4451 | 61.7002 | 61.5516 | 61.5389 | 61.5259 | 61.5963 | 61.6456 | 61.479 | 59.9667 | 60.0068 | 59.9621 | 59.9201 | 61.5514 | 61.589 | 61.3169 | 61.4908 | -1.5847 | -1.3502 | -1.5893 | -1.3548
586.0156 | 121.8018 | -61.5509 | 60.0769 | 0.1539 | 0.005267 | -0.007421 | -0.025017 | 0.031687 | 0.085583 | -0.076452 | 59.9163 | 59.9564 | 59.9117 | 59.8744 | 61.5011 | 61.5387 | 61.2803 | 61.4451 | 61.7048 | 61.5562 | 61.5435 | 61.5259 | 61.5826 | 61.6365 | 61.4745 | 59.9621 | 60.0022 | 59.9575 | 59.9201 | 61.5468 | 61.5845 | 61.3261 | 61.4908 | -1.5847 | -1.364 | -1.5893 | -1.3685
587.7656 | 121.8796 | -61.5692 | 59.9579 | 0.1539 | -0.00389 | -0.007421 | -0.020438 | 0.036265 | 0.081005 | -0.071874 | 59.9255 | 59.9564 | 59.9117 | 59.8835 | 61.5056 | 61.5387 | 61.2803 | 61.4451 | 61.7231 | 61.5653 | 61.5618 | 61.5488 | 61.6055 | 61.6502 | 61.4973 | 59.9712 | 60.0022 | 59.9575 | 59.9293 | 61.5514 | 61.5845 | 61.3261 | 61.4908 | -1.5802 | -1.3548 | -1.5939 | -1.3685
589.4688 | 121.7926 | -61.5875 | 59.9854 | 0.14932 | 0.000689 | -0.002842 | -0.029595 | 0.036265 | 0.090161 | -0.076452 | 59.93 | 59.9564 | 59.9117 | 59.8927 | 61.5102 | 61.5478 | 61.2666 | 61.4496 | 61.7368 | 61.5882 | 61.5847 | 61.5579 | 61.6238 | 61.6777 | 61.5111 | 59.9758 | 60.0022 | 59.9575 | 59.9385 | 61.556 | 61.5936 | 61.3123 | 61.4954 | -1.5802 | -1.3365 | -1.5985 | -1.3548
591.2188 | 121.7972 | -61.5646 | 60.0494 | 0.14474 | 0.000689 | -0.007421 | -0.034174 | 0.036265 | 0.090161 | -0.071874 | 59.9209 | 59.9564 | 59.9163 | 59.879 | 61.5056 | 61.5387 | 61.2711 | 61.4405 | 61.7094 | 61.5653 | 61.5572 | 61.5305 | 61.6009 | 61.6548 | 61.4928 | 59.9667 | 60.0022 | 59.9621 | 59.9247 | 61.5514 | 61.5845 | 61.3169 | 61.4863 | -1.5847 | -1.3502 | -1.5893 | -1.3548
592.9062 | 121.7972 | -61.528 | 60.0494 | 0.14474 | 0.000689 | -0.012 | -0.029595 | 0.036265 | 0.09474 | -0.08103 | 59.9255 | 59.9518 | 59.9117 | 59.879 | 61.5102 | 61.5433 | 61.2757 | 61.4451 | 61.6728 | 61.5287 | 61.516 | 61.4984 | 61.5643 | 61.6228 | 61.447 | 59.9712 | 59.9976 | 59.9575 | 59.9247 | 61.556 | 61.589 | 61.3215 | 61.4908 | -1.5847 | -1.3502 | -1.5985 | -1.364
594.6719 | 121.8292 | -61.5601 | 59.9899 | 0.14474 | 0.005267 | -0.007421 | -0.034174 | 0.036265 | 0.090161 | -0.076452 | 59.9255 | 59.9518 | 59.9072 | 59.879 | 61.5056 | 61.5433 | 61.2711 | 61.4359 | 61.7048 | 61.5653 | 61.5526 | 61.5259 | 61.5963 | 61.6502 | 61.4836 | 59.9712 | 59.9976 | 59.9529 | 59.9247 | 61.5514 | 61.589 | 61.3169 | 61.4817 | -1.5802 | -1.3457 | -1.5985 | -1.364
596.4375 | 121.788 | -61.5784 | 60.0082 | 0.14474 | 0.005267 | -0.012 | -0.029595 | 0.036265 | 0.085583 | -0.071874 | 59.9255 | 59.9518 | 59.9163 | 59.8835 | 61.5102 | 61.5478 | 61.2757 | 61.4451 | 61.7231 | 61.5836 | 61.5664 | 61.5488 | 61.6146 | 61.664 | 61.5065 | 59.9712 | 59.9976 | 59.9621 | 59.9293 | 61.556 | 61.5936 | 61.3215 | 61.4908 | -1.5847 | -1.3502 | -1.5939 | -1.3594
598.125 | 121.7606 | -61.5234 | 60.1135 | 0.14474 | 0.009846 | -0.007421 | -0.029595 | 0.036265 | 0.090161 | -0.071874 | 59.9209 | 59.9564 | 59.9072 | 59.879 | 61.5056 | 61.5433 | 61.2849 | 61.4405 | 61.6682 | 61.5333 | 61.516 | 61.4938 | 61.5597 | 61.6136 | 61.4516 | 59.9667 | 60.0022 | 59.9529 | 59.9247 | 61.5514 | 61.589 | 61.3306 | 61.4863 | -1.5847 | -1.364 | -1.5985 | -1.3777
599.875 | 121.8475 | -61.5372 | 60.0037 | 0.14474 | 0.005267 | -0.012 | -0.038752 | 0.036265 | 0.090161 | -0.08103 | 59.9255 | 59.9656 | 59.9072 | 59.8835 | 61.4965 | 61.5387 | 61.2711 | 61.4496 | 61.6819 | 61.5424 | 61.5252 | 61.4984 | 61.5734 | 61.6273 | 61.4561 | 59.9712 | 60.0113 | 59.9529 | 59.9293 | 61.5423 | 61.5845 | 61.3169 | 61.4954 | -1.571 | -1.3457 | -1.5893 | -1.364
601.625 | 121.7606 | -61.5097 | 60.1273 | 0.14474 | 0.000689 | -0.012 | -0.029595 | 0.036265 | 0.090161 | -0.076452 | 59.9209 | 59.9656 | 59.9072 | 59.879 | 61.5148 | 61.5433 | 61.2757 | 61.4451 | 61.6544 | 61.5104 | 61.4977 | 61.4801 | 61.546 | 61.5999 | 61.4333 | 59.9667 | 60.0113 | 59.9529 | 59.9247 | 61.5606 | 61.589 | 61.3215 | 61.4908 | -1.5939 | -1.3548 | -1.6076 | -1.3685
603.375 | 121.843 | -61.5692 | 60.0082 | 0.14474 | 0.005267 | -0.007421 | -0.034174 | 0.031687 | 0.09474 | -0.071874 | 59.9255 | 59.961 | 59.9163 | 59.8835 | 61.5011 | 61.5341 | 61.2757 | 61.4451 | 61.714 | 61.5745 | 61.5618 | 61.535 | 61.6009 | 61.664 | 61.4973 | 59.9712 | 60.0068 | 59.9621 | 59.9293 | 61.5468 | 61.5799 | 61.3215 | 61.4908 | -1.5756 | -1.3502 | -1.5847 | -1.3594
605.125 | 121.7468 | -61.5097 | 60.1089 | 0.14932 | 0.000689 | -0.012 | -0.029595 | 0.040843 | 0.085583 | -0.08103 | 59.9209 | 59.961 | 59.9117 | 59.879 | 61.5102 | 61.5478 | 61.2757 | 61.4405 | 61.659 | 61.5104 | 61.4977 | 61.4801 | 61.5505 | 61.5953 | 61.4287 | 59.9667 | 60.0068 | 59.9575 | 59.9247 | 61.556 | 61.5936 | 61.3215 | 61.4863 | -1.5893 | -1.3548 | -1.5985 | -1.364
606.8906 | 121.8979 | -61.5005 | 60.0449 | 0.1539 | 0.009846 | -0.012 | -0.034174 | 0.036265 | 0.081005 | -0.076452 | 59.9163 | 59.961 | 59.9209 | 59.8835 | 61.5102 | 61.5341 | 61.2757 | 61.4451 | 61.6544 | 61.5104 | 61.4885 | 61.4664 | 61.5368 | 61.5816 | 61.4241 | 59.9621 | 60.0068 | 59.9667 | 59.9293 | 61.556 | 61.5799 | 61.3215 | 61.4908 | -1.5939 | -1.3594 | -1.5893 | -1.3548
608.6406 | 121.7422 | -61.5875 | 59.9991 | 0.1539 | 0.014425 | -0.002842 | -0.025017 | 0.036265 | 0.090161 | -0.071874 | 59.9255 | 59.961 | 59.9209 | 59.879 | 61.5056 | 61.5433 | 61.2711 | 61.4451 | 61.7414 | 61.6019 | 61.5847 | 61.5625 | 61.6238 | 61.6777 | 61.5157 | 59.9712 | 60.0068 | 59.9667 | 59.9247 | 61.5514 | 61.589 | 61.3169 | 61.4908 | -1.5802 | -1.3457 | -1.5847 | -1.3502
610.3281 | 121.8475 | -61.5326 | 59.9991 | 0.14932 | 0.005267 | -0.012 | -0.029595 | 0.036265 | 0.085583 | -0.08103 | 59.9255 | 59.961 | 59.9117 | 59.8881 | 61.5148 | 61.5387 | 61.2757 | 61.4451 | 61.6819 | 61.5379 | 61.5206 | 61.503 | 61.5689 | 61.6182 | 61.4516 | 59.9712 | 60.0068 | 59.9575 | 59.9339 | 61.5606 | 61.5845 | 61.3215 | 61.4908 | -1.5893 | -1.3502 | -1.6031 | -1.364
612.0781 | 121.7697 | -61.5829 | 60.0174 | 0.14474 | 0.000689 | -0.007421 | -0.029595 | 0.040843 | 0.081005 | -0.08103 | 59.9209 | 59.9656 | 59.9117 | 59.879 | 61.5056 | 61.5433 | 61.2711 | 61.4451 | 61.7277 | 61.5836 | 61.5755 | 61.5534 | 61.6238 | 61.664 | 61.5019 | 59.9667 | 60.0113 | 59.9575 | 59.9247 | 61.5514 | 61.589 | 61.3169 | 61.4908 | -1.5847 | -1.3502 | -1.5939 | -1.3594
613.8281 | 121.7606 | -61.496 | 60.1181 | 0.14932 | 0.000689 | -0.007421 | -0.029595 | 0.040843 | 0.081005 | -0.076452 | 59.9255 | 59.9564 | 59.9026 | 59.879 | 61.5102 | 61.5433 | 61.2711 | 61.4405 | 61.6453 | 61.4967 | 61.4886 | 61.4664 | 61.5368 | 61.577 | 61.4195 | 59.9712 | 60.0022 | 59.9484 | 59.9247 | 61.556 | 61.589 | 61.3169 | 61.4863 | -1.5847 | -1.3457 | -1.6076 | -1.3685
615.5781 | 121.7743 | -61.5784 | 60.0128 | 0.14932 | 0.000689 | -0.016578 | -0.029595 | 0.036265 | 0.081005 | -0.071874 | 59.93 | 59.9564 | 59.9117 | 59.879 | 61.5011 | 61.5433 | 61.2757 | 61.4405 | 61.7277 | 61.5791 | 61.5618 | 61.5488 | 61.6146 | 61.6594 | 61.5065 | 59.9758 | 60.0022 | 59.9575 | 59.9247 | 61.5468 | 61.589 | 61.3215 | 61.4863 | -1.571 | -1.3457 | -1.5893 | -1.364
617.3281 | 121.7972 | -61.5417 | 60.0403 | 0.1539 | 0.009846 | -0.012 | -0.029595 | 0.040843 | 0.076426 | -0.076452 | 59.9209 | 59.961 | 59.9072 | 59.879 | 61.5102 | 61.5433 | 61.2711 | 61.4405 | 61.6956 | 61.5516 | 61.5297 | 61.5122 | 61.5826 | 61.6182 | 61.4653 | 59.9667 | 60.0068 | 59.9529 | 59.9247 | 61.556 | 61.589 | 61.3169 | 61.4863 | -1.5893 | -1.3502 | -1.6031 | -1.364
619.0156 | 121.7468 | -61.5005 | 60.1044 | 0.14474 | 0.009846 | -0.016578 | -0.034174 | 0.036265 | 0.076426 | -0.08103 | 59.9255 | 59.961 | 59.9117 | 59.8744 | 61.5056 | 61.5478 | 61.2711 | 61.4451 | 61.6453 | 61.5104 | 61.484 | 61.4664 | 61.5368 | 61.577 | 61.4195 | 59.9712 | 60.0068 | 59.9575 | 59.9201 | 61.5514 | 61.5936 | 61.3169 | 61.4908 | -1.5802 | -1.3457 | -1.5939 | -1.3594
620.7656 | 121.7377 | -61.5738 | 60.0311 | 0.1539 | 0.000689 | -0.007421 | -0.025017 | 0.031687 | 0.090161 | -0.071874 | 59.9255 | 59.9564 | 59.9163 | 59.8835 | 61.5011 | 61.5433 | 61.2711 | 61.4451 | 61.7277 | 61.5745 | 61.5664 | 61.5488 | 61.6055 | 61.664 | 61.5019 | 59.9712 | 60.0022 | 59.9621 | 59.9293 | 61.5468 | 61.589 | 61.3169 | 61.4908 | -1.5756 | -1.3457 | -1.5847 | -1.3548
622.4688 | 121.8887 | -61.4914 | 60.054 | 0.14932 | -0.00389 | -0.012 | -0.020438 | 0.036265 | 0.081005 | -0.071874 | 59.9209 | 59.9564 | 59.9117 | 59.8744 | 61.5102 | 61.5341 | 61.2803 | 61.4496 | 61.6407 | 61.4875 | 61.4794 | 61.471 | 61.5277 | 61.5724 | 61.4195 | 59.9667 | 60.0022 | 59.9575 | 59.9201 | 61.556 | 61.5799 | 61.3261 | 61.4954 | -1.5893 | -1.3594 | -1.5985 | -1.3685
624.2031 | 121.7285 | -61.5829 | 60.0357 | 0.14474 | 0.005267 | -0.007421 | -0.029595 | 0.036265 | 0.090161 | -0.076452 | 59.9255 | 59.961 | 59.9117 | 59.879 | 61.5102 | 61.5433 | 61.2711 | 61.4542 | 61.7277 | 61.5882 | 61.5755 | 61.5534 | 61.6192 | 61.6731 | 61.5065 | 59.9712 | 60.0068 | 59.9575 | 59.9247 | 61.556 | 61.589 | 61.3169 | 61.5 | -1.5847 | -1.3457 | -1.5985 | -1.3594
625.9531 | 121.7834 | -61.5234 | 60.0677 | 0.1539 | 0.000689 | -0.016578 | -0.029595 | 0.036265 | 0.076426 | -0.076452 | 59.9255 | 59.9564 | 59.9163 | 59.879 | 61.5056 | 61.5433 | 61.2711 | 61.4405 | 61.6773 | 61.5241 | 61.5069 | 61.4938 | 61.5597 | 61.5999 | 61.447 | 59.9712 | 60.0022 | 59.9621 | 59.9247 | 61.5514 | 61.589 | 61.3169 | 61.4863 | -1.5802 | -1.3457 | -1.5893 | -1.3548
627.7031 | 121.7285 | -61.5875 | 60.0266 | 0.16306 | 0.000689 | -0.016578 | -0.034174 | 0.040843 | 0.085583 | -0.067295 | 59.9209 | 59.961 | 59.9117 | 59.8835 | 61.5056 | 61.5478 | 61.2711 | 61.4405 | 61.7506 | 61.5882 | 61.5709 | 61.5534 | 61.6284 | 61.6731 | 61.5202 | 59.9667 | 60.0068 | 59.9575 | 59.9293 | 61.5514 | 61.5936 | 61.3169 | 61.4863 | -1.5847 | -1.3502 | -1.5939 | -1.3594
629.4531 | 121.8842 | -61.4731 | 60.0449 | 0.14932 | 0.000689 | -0.012 | -0.034174 | 0.036265 | 0.081005 | -0.076452 | 59.93 | 59.9518 | 59.9117 | 59.8835 | 61.5148 | 61.5433 | 61.2803 | 61.4496 | 61.6224 | 61.4738 | 61.4611 | 61.4389 | 61.5093 | 61.5541 | 61.3966 | 59.9758 | 59.9976 | 59.9575 | 59.9293 | 61.5606 | 61.589 | 61.3261 | 61.4954 | -1.5847 | -1.3502 | -1.6031 | -1.3685
631.1406 | 121.7377 | -61.4914 | 60.0952 | 0.14474 | -0.00389 | -0.012 | -0.029595 | 0.036265 | 0.081005 | -0.071874 | 59.9209 | 59.9518 | 59.9117 | 59.879 | 61.5056 | 61.5387 | 61.2711 | 61.4496 | 61.6361 | 61.4875 | 61.4794 | 61.4618 | 61.5277 | 61.5724 | 61.4195 | 59.9667 | 59.9976 | 59.9575 | 59.9247 | 61.5514 | 61.5845 | 61.3169 | 61.4954 | -1.5847 | -1.3502 | -1.5939 | -1.3594
632.8906 | 121.8292 | -61.5601 | 60.0266 | 0.14932 | -0.00389 | -0.016578 | -0.029595 | 0.036265 | 0.081005 | -0.071874 | 59.93 | 59.961 | 59.9117 | 59.8835 | 61.5102 | 61.5478 | 61.2803 | 61.4451 | 61.7094 | 61.5562 | 61.5435 | 61.5305 | 61.5963 | 61.6411 | 61.4882 | 59.9758 | 60.0068 | 59.9575 | 59.9293 | 61.556 | 61.5936 | 61.3261 | 61.4908 | -1.5802 | -1.3502 | -1.5985 | -1.3685
634.6406 | 121.7514 | -61.5005 | 60.1044 | 0.14932 | -0.00389 | -0.012 | -0.025017 | 0.036265 | 0.081005 | -0.076452 | 59.9209 | 59.9518 | 59.9072 | 59.879 | 61.5056 | 61.5478 | 61.2711 | 61.4496 | 61.6499 | 61.4967 | 61.4885 | 61.4755 | 61.5368 | 61.5816 | 61.4241 | 59.9667 | 59.9976 | 59.9529 | 59.9247 | 61.5514 | 61.5936 | 61.3169 | 61.4954 | -1.5847 | -1.3502 | -1.5985 | -1.364
636.3281 | 121.7468 | -61.5509 | 60.0174 | 0.14474 | -0.00389 | -0.016578 | -0.025017 | 0.036265 | 0.081005 | -0.071874 | 59.9255 | 59.961 | 59.9117 | 59.879 | 61.5056 | 61.5433 | 61.2757 | 61.4496 | 61.6956 | 61.547 | 61.5343 | 61.5259 | 61.5872 | 61.6319 | 61.479 | 59.9712 | 60.0068 | 59.9575 | 59.9247 | 61.5514 | 61.589 | 61.3215 | 61.4954 | -1.5802 | -1.3502 | -1.5939 | -1.364
638.0781 | 121.8384 | -61.5326 | 59.967 | 0.14474 | -0.00389 | -0.016578 | -0.029595 | 0.036265 | 0.081005 | -0.076452 | 59.9255 | 59.961 | 59.9072 | 59.8835 | 61.5102 | 61.5478 | 61.2711 | 61.4405 | 61.6773 | 61.5287 | 61.516 | 61.503 | 61.5689 | 61.6136 | 61.4561 | 59.9712 | 60.0068 | 59.9529 | 59.9293 | 61.556 | 61.5936 | 61.3169 | 61.4863 | -1.5847 | -1.3457 | -1.6031 | -1.364
639.8281 | 121.8933 | -61.5051 | 60.0311 | 0.1539 | -0.008469 | -0.012 | -0.029595 | 0.036265 | 0.076426 | -0.071874 | 59.9209 | 59.9564 | 59.9163 | 59.8835 | 61.5056 | 61.5478 | 61.2711 | 61.4405 | 61.659 | 61.4967 | 61.4931 | 61.4755 | 61.5414 | 61.5816 | 61.4333 | 59.9667 | 60.0022 | 59.9621 | 59.9293 | 61.5514 | 61.5936 | 61.3169 | 61.4863 | -1.5847 | -1.3502 | -1.5893 | -1.3548
641.5938 | 121.8658 | -61.4731 | 60.0403 | 0.14474 | -0.00389 | -0.016578 | -0.034174 | 0.031687 | 0.076426 | -0.076452 | 59.9255 | 59.9518 | 59.9163 | 59.879 | 61.5056 | 61.5387 | 61.2757 | 61.4451 | 61.6178 | 61.4692 | 61.4565 | 61.4389 | 61.5048 | 61.5495 | 61.3966 | 59.9712 | 59.9976 | 59.9621 | 59.9247 | 61.5514 | 61.5845 | 61.3215 | 61.4908 | -1.5802 | -1.3502 | -1.5893 | -1.3594
643.3594 | 121.7514 | -61.528 | 60.0769 | 0.14017 | -0.00389 | -0.007421 | -0.034174 | 0.036265 | 0.081005 | -0.076452 | 59.9163 | 59.9564 | 59.9163 | 59.8835 | 61.5011 | 61.5387 | 61.2803 | 61.4405 | 61.6682 | 61.5241 | 61.5206 | 61.4938 | 61.5643 | 61.609 | 61.4516 | 59.9621 | 60.0022 | 59.9621 | 59.9293 | 61.5468 | 61.5845 | 61.3261 | 61.4863 | -1.5847 | -1.364 | -1.5847 | -1.364
645.1094 | 121.8704 | -61.5417 | 59.9487 | 0.14474 | 0.000689 | -0.012 | -0.034174 | 0.036265 | 0.076426 | -0.076452 | 59.9255 | 59.9564 | 59.9117 | 59.8744 | 61.5011 | 61.5387 | 61.2757 | 61.4496 | 61.6865 | 61.5424 | 61.5297 | 61.5076 | 61.578 | 61.6182 | 61.4653 | 59.9712 | 60.0022 | 59.9575 | 59.9201 | 61.5468 | 61.5845 | 61.3215 | 61.4954 | -1.5756 | -1.3502 | -1.5893 | -1.364
646.8125 | 121.7651 | -61.5189 | 60.0952 | 0.14017 | 0.000689 | -0.012 | -0.034174 | 0.036265 | 0.076426 | -0.076452 | 59.9255 | 59.9518 | 59.9072 | 59.879 | 61.5102 | 61.5478 | 61.2757 | 61.4405 | 61.659 | 61.5195 | 61.5069 | 61.4847 | 61.5551 | 61.5953 | 61.4424 | 59.9712 | 59.9976 | 59.9529 | 59.9247 | 61.556 | 61.5936 | 61.3215 | 61.4863 | -1.5847 | -1.3502 | -1.6031 | -1.3685
648.5625 | 121.7377 | -61.5738 | 60.0403 | 0.1539 | 0.000689 | -0.016578 | -0.034174 | 0.031687 | 0.085583 | -0.071874 | 59.9255 | 59.9564 | 59.9072 | 59.879 | 61.5056 | 61.5433 | 61.2757 | 61.4405 | 61.7277 | 61.5745 | 61.5572 | 61.5396 | 61.6055 | 61.6594 | 61.5019 | 59.9712 | 60.0022 | 59.9529 | 59.9247 | 61.5514 | 61.589 | 61.3215 | 61.4863 | -1.5802 | -1.3502 | -1.5985 | -1.3685
650.3125 | 121.8842 | -61.496 | 60.0449 | 0.14474 | -0.008469 | -0.012 | -0.029595 | 0.036265 | 0.081005 | -0.076452 | 59.9163 | 59.961 | 59.9117 | 59.879 | 61.5102 | 61.5433 | 61.2711 | 61.4405 | 61.6407 | 61.4875 | 61.484 | 61.4664 | 61.5322 | 61.577 | 61.4195 | 59.9621 | 60.0068 | 59.9575 | 59.9247 | 61.556 | 61.589 | 61.3169 | 61.4863 | -1.5939 | -1.3548 | -1.5985 | -1.3594
652.0781 | 121.7926 | -61.5189 | 60.0723 | 0.1539 | -0.008469 | -0.021157 | -0.029595 | 0.036265 | 0.081005 | -0.067295 | 59.93 | 59.961 | 59.9163 | 59.8835 | 61.5102 | 61.5433 | 61.2757 | 61.4451 | 61.6728 | 61.5104 | 61.4977 | 61.4893 | 61.5551 | 61.5999 | 61.4516 | 59.9758 | 60.0068 | 59.9621 | 59.9293 | 61.556 | 61.589 | 61.3215 | 61.4908 | -1.5802 | -1.3457 | -1.5939 | -1.3594
653.8281 | 121.8292 | -61.5646 | 60.022 | 0.1539 | 0.000689 | -0.012 | -0.034174 | 0.040843 | 0.071848 | -0.071874 | 59.9255 | 59.9518 | 59.9072 | 59.8835 | 61.5056 | 61.5387 | 61.2711 | 61.4451 | 61.7185 | 61.5653 | 61.5526 | 61.5305 | 61.6055 | 61.6365 | 61.4928 | 59.9712 | 59.9976 | 59.9529 | 59.9293 | 61.5514 | 61.5845 | 61.3169 | 61.4908 | -1.5802 | -1.3457 | -1.5985 | -1.364
655.5156 | 121.8246 | -61.5326 | 60.0266 | 0.14017 | -0.00389 | -0.012 | -0.020438 | 0.036265 | 0.081005 | -0.076452 | 59.9209 | 59.961 | 59.9117 | 59.8835 | 61.5011 | 61.5433 | 61.2711 | 61.4496 | 61.6728 | 61.5287 | 61.5206 | 61.5122 | 61.5689 | 61.6136 | 61.4561 | 59.9667 | 60.0068 | 59.9575 | 59.9293 | 61.5468 | 61.589 | 61.3169 | 61.4954 | -1.5802 | -1.3502 | -1.5893 | -1.3594
657.2656 | 121.8384 | -61.5463 | 59.9808 | 0.14932 | -0.00389 | -0.012 | -0.025017 | 0.031687 | 0.081005 | -0.076452 | 59.9255 | 59.9656 | 59.9072 | 59.8881 | 61.5011 | 61.5341 | 61.2757 | 61.4496 | 61.6956 | 61.5424 | 61.5343 | 61.5213 | 61.578 | 61.6273 | 61.4699 | 59.9712 | 60.0113 | 59.9529 | 59.9339 | 61.5468 | 61.5799 | 61.3215 | 61.4954 | -1.5756 | -1.3502 | -1.5939 | -1.3685
659.0156 | 121.7972 | -61.4868 | 60.0952 | 0.14474 | -0.00389 | -0.007421 | -0.029595 | 0.031687 | 0.071848 | -0.071874 | 59.93 | 59.9564 | 59.9117 | 59.8744 | 61.5011 | 61.5387 | 61.2757 | 61.4451 | 61.6316 | 61.4829 | 61.4794 | 61.4572 | 61.5185 | 61.5587 | 61.4149 | 59.9758 | 60.0022 | 59.9575 | 59.9201 | 61.5468 | 61.5845 | 61.3215 | 61.4908 | -1.571 | -1.3457 | -1.5893 | -1.364
660.7656 | 121.7239 | -61.5829 | 60.0174 | 0.1539 | 0.000689 | -0.007421 | -0.025017 | 0.040843 | 0.085583 | -0.067295 | 59.9255 | 59.9518 | 59.9072 | 59.879 | 61.5102 | 61.5387 | 61.2757 | 61.4405 | 61.7368 | 61.5836 | 61.5755 | 61.5579 | 61.6238 | 61.6685 | 61.5157 | 59.9712 | 59.9976 | 59.9529 | 59.9247 | 61.556 | 61.5845 | 61.3215 | 61.4863 | -1.5847 | -1.3502 | -1.6031 | -1.3685
662.4531 | 121.8704 | -61.5234 | 60.022 | 0.14932 | -0.013048 | -0.012 | -0.034174 | 0.031687 | 0.085583 | -0.071874 | 59.93 | 59.9564 | 59.9072 | 59.8835 | 61.5102 | 61.5478 | 61.2711 | 61.4405 | 61.6728 | 61.5104 | 61.5114 | 61.4893 | 61.5551 | 61.609 | 61.4516 | 59.9758 | 60.0022 | 59.9529 | 59.9293 | 61.556 | 61.5936 | 61.3169 | 61.4863 | -1.5802 | -1.3411 | -1.6031 | -1.364
664.2031 | 121.875 | -61.5692 | 59.967 | 0.14932 | -0.008469 | -0.016578 | -0.034174 | 0.036265 | 0.081005 | -0.076452 | 59.93 | 59.9518 | 59.9163 | 59.879 | 61.5011 | 61.5387 | 61.2711 | 61.4405 | 61.7185 | 61.5607 | 61.5526 | 61.535 | 61.6055 | 61.6502 | 61.4928 | 59.9758 | 59.9976 | 59.9621 | 59.9247 | 61.5468 | 61.5845 | 61.3169 | 61.4863 | -1.571 | -1.3411 | -1.5847 | -1.3548
665.9375 | 121.8979 | -61.496 | 60.0403 | 0.14017 | 0.000689 | -0.012 | -0.025017 | 0.040843 | 0.081005 | -0.08103 | 59.9255 | 59.9564 | 59.9163 | 59.8835 | 61.5102 | 61.5433 | 61.2757 | 61.4496 | 61.6361 | 61.4967 | 61.484 | 61.471 | 61.5368 | 61.577 | 61.4149 | 59.9712 | 60.0022 | 59.9621 | 59.9293 | 61.556 | 61.589 | 61.3215 | 61.4954 | -1.5847 | -1.3502 | -1.5939 | -1.3594
667.6406 | 121.7606 | -61.5875 | 60.0311 | 0.14474 | -0.008469 | -0.007421 | -0.034174 | 0.036265 | 0.081005 | -0.071874 | 59.93 | 59.961 | 59.9163 | 59.879 | 61.5056 | 61.5387 | 61.2666 | 61.4359 | 61.7323 | 61.5791 | 61.5801 | 61.5534 | 61.6238 | 61.6685 | 61.5157 | 59.9758 | 60.0068 | 59.9621 | 59.9247 | 61.5514 | 61.5845 | 61.3123 | 61.4817 | -1.5756 | -1.3365 | -1.5893 | -1.3502
669.3906 | 121.7789 | -61.4914 | 60.0952 | 0.1539 | -0.00389 | -0.012 | -0.025017 | 0.036265 | 0.076426 | -0.071874 | 59.9209 | 59.9518 | 59.9163 | 59.8835 | 61.5102 | 61.5478 | 61.2666 | 61.4405 | 61.6453 | 61.4875 | 61.4794 | 61.4664 | 61.5277 | 61.5678 | 61.4195 | 59.9667 | 59.9976 | 59.9621 | 59.9293 | 61.556 | 61.5936 | 61.3123 | 61.4863 | -1.5893 | -1.3457 | -1.5939 | -1.3502
671.0781 | 121.8201 | -61.5143 | 60.022 | 0.14017 | -0.00389 | -0.021157 | -0.025017 | 0.040843 | 0.085583 | -0.076452 | 59.93 | 59.961 | 59.9117 | 59.879 | 61.5194 | 61.5433 | 61.2711 | 61.4405 | 61.6544 | 61.5104 | 61.4931 | 61.4893 | 61.5551 | 61.5999 | 61.4378 | 59.9758 | 60.0068 | 59.9575 | 59.9247 | 61.5651 | 61.589 | 61.3169 | 61.4863 | -1.5893 | -1.3411 | -1.6076 | -1.3594
672.8438 | 121.756 | -61.5921 | 60.0266 | 0.14932 | -0.00389 | -0.012 | -0.025017 | 0.031687 | 0.081005 | -0.076452 | 59.93 | 59.9564 | 59.9163 | 59.8835 | 61.5148 | 61.5478 | 61.2711 | 61.4496 | 61.7414 | 61.5882 | 61.5801 | 61.5671 | 61.6238 | 61.6731 | 61.5156 | 59.9758 | 60.0022 | 59.9621 | 59.9293 | 61.5606 | 61.5936 | 61.3169 | 61.4954 | -1.5847 | -1.3411 | -1.5985 | -1.3548
674.5469 | 121.8475 | -61.5463 | 59.9808 | 0.1539 | 0.000689 | -0.012 | -0.029595 | 0.040843 | 0.076426 | -0.076452 | 59.9255 | 59.9564 | 59.9163 | 59.8835 | 61.5102 | 61.5433 | 61.2757 | 61.4451 | 61.7002 | 61.547 | 61.5343 | 61.5167 | 61.5872 | 61.6228 | 61.4699 | 59.9712 | 60.0022 | 59.9621 | 59.9293 | 61.556 | 61.589 | 61.3215 | 61.4908 | -1.5847 | -1.3502 | -1.5939 | -1.3594
676.2969 | 121.7834 | -61.5372 | 60.0861 | 0.14474 | 0.000689 | -0.021157 | -0.025017 | 0.036265 | 0.081005 | -0.067295 | 59.9346 | 59.9564 | 59.9209 | 59.879 | 61.5056 | 61.5433 | 61.2666 | 61.4451 | 61.6819 | 61.5379 | 61.516 | 61.5122 | 61.5734 | 61.6182 | 61.4699 | 59.9804 | 60.0022 | 59.9667 | 59.9247 | 61.5514 | 61.589 | 61.3123 | 61.4908 | -1.571 | -1.3319 | -1.5847 | -1.3457
678.0469 | 121.8063 | -61.5326 | 60.054 | 0.1539 | -0.00389 | -0.021157 | -0.025017 | 0.040843 | 0.081005 | -0.071874 | 59.93 | 59.9518 | 59.9163 | 59.8881 | 61.5148 | 61.5387 | 61.2666 | 61.4496 | 61.6865 | 61.5287 | 61.5114 | 61.5076 | 61.5734 | 61.6136 | 61.4607 | 59.9758 | 59.9976 | 59.9621 | 59.9339 | 61.5606 | 61.5845 | 61.3123 | 61.4954 | -1.5847 | -1.3365 | -1.5985 | -1.3502
679.7344 | 121.8658 | -61.5326 | 59.9762 | 0.14932 | -0.00389 | -0.012 | -0.034174 | 0.040843 | 0.081005 | -0.076452 | 59.9255 | 59.9656 | 59.9163 | 59.8835 | 61.5102 | 61.5433 | 61.2803 | 61.4451 | 61.6819 | 61.5287 | 61.5206 | 61.4984 | 61.5734 | 61.6136 | 61.4561 | 59.9712 | 60.0113 | 59.9621 | 59.9293 | 61.556 | 61.589 | 61.3261 | 61.4908 | -1.5847 | -1.3548 | -1.5939 | -1.364
681.4844 | 121.7972 | -61.5051 | 60.0723 | 0.14474 | 0.005267 | -0.021157 | -0.025017 | 0.040843 | 0.081005 | -0.08103 | 59.9255 | 59.961 | 59.9117 | 59.879 | 61.5148 | 61.5433 | 61.2711 | 61.4496 | 61.6499 | 61.5104 | 61.484 | 61.4801 | 61.546 | 61.5861 | 61.4241 | 59.9712 | 60.0068 | 59.9575 | 59.9247 | 61.5606 | 61.589 | 61.3169 | 61.4954 | -1.5893 | -1.3457 | -1.6031 | -1.3594
683.25 | 121.8521 | -61.4731 | 60.1089 | 0.14017 | -0.00389 | -0.012 | -0.029595 | 0.040843 | 0.081005 | -0.076452 | 59.9163 | 59.9564 | 59.9072 | 59.879 | 61.5056 | 61.5387 | 61.2757 | 61.4542 | 61.6132 | 61.4692 | 61.4611 | 61.4435 | 61.5139 | 61.5541 | 61.3966 | 59.9621 | 60.0022 | 59.9529 | 59.9247 | 61.5514 | 61.5845 | 61.3215 | 61.5 | -1.5893 | -1.3594 | -1.5985 | -1.3685
685.0156 | 121.8521 | -61.5372 | 60.0082 | 0.14474 | -0.00389 | -0.016578 | -0.034174 | 0.040843 | 0.076426 | -0.071874 | 59.93 | 59.961 | 59.9072 | 59.879 | 61.5056 | 61.5433 | 61.2757 | 61.4405 | 61.6819 | 61.5333 | 61.5206 | 61.503 | 61.578 | 61.6136 | 61.4653 | 59.9758 | 60.0068 | 59.9529 | 59.9247 | 61.5514 | 61.589 | 61.3215 | 61.4863 | -1.5756 | -1.3457 | -1.5985 | -1.3685
686.7812 | 121.8567 | -61.5555 | 59.9716 | 0.1539 | -0.00389 | -0.012 | -0.029595 | 0.031687 | 0.081005 | -0.076452 | 59.9255 | 59.961 | 59.9163 | 59.8835 | 61.5148 | 61.5387 | 61.2666 | 61.4451 | 61.7094 | 61.5516 | 61.5435 | 61.5259 | 61.5872 | 61.6365 | 61.479 | 59.9712 | 60.0068 | 59.9621 | 59.9293 | 61.5606 | 61.5845 | 61.3123 | 61.4908 | -1.5893 | -1.3411 | -1.5985 | -1.3502
688.4844 | 121.875 | -61.5463 | 59.967 | 0.14474 | 0.000689 | -0.016578 | -0.029595 | 0.040843 | 0.081005 | -0.076452 | 59.9209 | 59.961 | 59.9209 | 59.8744 | 61.5102 | 61.5387 | 61.2711 | 61.4496 | 61.6911 | 61.547 | 61.5297 | 61.5167 | 61.5872 | 61.6273 | 61.4699 | 59.9667 | 60.0068 | 59.9667 | 59.9201 | 61.556 | 61.5845 | 61.3169 | 61.4954 | -1.5893 | -1.3502 | -1.5893 | -1.3502
690.2344 | 121.7377 | -61.5143 | 60.1089 | 0.14932 | 0.000689 | -0.016578 | -0.020438 | 0.031687 | 0.076426 | -0.076452 | 59.9255 | 59.961 | 59.9072 | 59.879 | 61.5102 | 61.5478 | 61.2803 | 61.4451 | 61.6636 | 61.515 | 61.4977 | 61.4938 | 61.546 | 61.5907 | 61.4378 | 59.9712 | 60.0068 | 59.9529 | 59.9247 | 61.556 | 61.5936 | 61.3261 | 61.4908 | -1.5847 | -1.3548 | -1.6031 | -1.3731
691.9844 | 121.7972 | -61.5143 | 60.0677 | 0.1539 | -0.00389 | -0.007421 | -0.029595 | 0.036265 | 0.076426 | -0.071874 | 59.93 | 59.9564 | 59.9072 | 59.8744 | 61.5056 | 61.5341 | 61.2757 | 61.4496 | 61.6682 | 61.5104 | 61.5069 | 61.4847 | 61.5505 | 61.5907 | 61.4424 | 59.9758 | 60.0022 | 59.9529 | 59.9201 | 61.5514 | 61.5799 | 61.3215 | 61.4954 | -1.5756 | -1.3457 | -1.5985 | -1.3685
693.7344 | 121.8658 | -61.5189 | 60.0449 | 0.14932 | 0.000689 | -0.012 | -0.025017 | 0.045421 | 0.081005 | -0.08103 | 59.9209 | 59.9564 | 59.9072 | 59.879 | 61.5056 | 61.5387 | 61.2757 | 61.4405 | 61.6682 | 61.5195 | 61.5069 | 61.4938 | 61.5643 | 61.5999 | 61.4378 | 59.9667 | 60.0022 | 59.9529 | 59.9247 | 61.5514 | 61.5845 | 61.3215 | 61.4863 | -1.5847 | -1.3548 | -1.5985 | -1.3685
695.4219 | 121.8613 | -61.5372 | 59.9808 | 0.14932 | -0.00389 | -0.021157 | -0.034174 | 0.031687 | 0.076426 | -0.071874 | 59.93 | 59.961 | 59.9117 | 59.8927 | 61.5056 | 61.5433 | 61.2711 | 61.4496 | 61.6865 | 61.5333 | 61.516 | 61.503 | 61.5689 | 61.6136 | 61.4653 | 59.9758 | 60.0068 | 59.9575 | 59.9385 | 61.5514 | 61.589 | 61.3169 | 61.4954 | -1.5756 | -1.3411 | -1.5939 | -1.3594
697.1719 | 121.7331 | -61.5738 | 60.0266 | 0.14932 | 0.000689 | -0.002842 | -0.025017 | 0.040843 | 0.081005 | -0.067295 | 59.9255 | 59.9518 | 59.9163 | 59.8835 | 61.5102 | 61.5478 | 61.2666 | 61.4405 | 61.7231 | 61.5745 | 61.5709 | 61.5488 | 61.6146 | 61.6548 | 61.5065 | 59.9712 | 59.9976 | 59.9621 | 59.9293 | 61.556 | 61.5936 | 61.3123 | 61.4863 | -1.5847 | -1.3411 | -1.5939 | -1.3502
698.9062 | 121.8658 | -61.5555 | 59.9533 | 0.14474 | -0.00389 | -0.012 | -0.034174 | 0.031687 | 0.081005 | -0.08103 | 59.9392 | 59.9564 | 59.9117 | 59.8835 | 61.5148 | 61.5433 | 61.2711 | 61.4359 | 61.7002 | 61.5516 | 61.5435 | 61.5213 | 61.5872 | 61.6365 | 61.4745 | 59.985 | 60.0022 | 59.9575 | 59.9293 | 61.5606 | 61.589 | 61.3169 | 61.4817 | -1.5756 | -1.3319 | -1.6031 | -1.3594
700.6562 | 121.756 | -61.5509 | 60.0449 | 0.14017 | 0.000689 | -0.007421 | -0.038752 | 0.031687 | 0.081005 | -0.076452 | 59.9255 | 59.9518 | 59.9117 | 59.879 | 61.5102 | 61.5433 | 61.2711 | 61.4405 | 61.6911 | 61.5516 | 61.5435 | 61.5122 | 61.5826 | 61.6319 | 61.4745 | 59.9712 | 59.9976 | 59.9575 | 59.9247 | 61.556 | 61.589 | 61.3169 | 61.4863 | -1.5847 | -1.3457 | -1.5985 | -1.3594
702.3594 | 121.8704 | -61.4868 | 60.0723 | 0.14932 | 0.000689 | -0.016578 | -0.034174 | 0.040843 | 0.076426 | -0.076452 | 59.9255 | 59.9518 | 59.9072 | 59.879 | 61.5056 | 61.5341 | 61.2803 | 61.4451 | 61.6361 | 61.4875 | 61.4702 | 61.4526 | 61.5277 | 61.5632 | 61.4104 | 59.9712 | 59.9976 | 59.9529 | 59.9247 | 61.5514 | 61.5799 | 61.3261 | 61.4908 | -1.5802 | -1.3548 | -1.5985 | -1.3731
704.1094 | 121.8018 | -61.5509 | 60.0632 | 0.14474 | 0.005267 | -0.012 | -0.029595 | 0.036265 | 0.081005 | -0.071874 | 59.93 | 59.961 | 59.9163 | 59.879 | 61.5056 | 61.5341 | 61.2711 | 61.4496 | 61.6956 | 61.5562 | 61.5389 | 61.5213 | 61.5872 | 61.6319 | 61.479 | 59.9758 | 60.0068 | 59.9621 | 59.9247 | 61.5514 | 61.5799 | 61.3169 | 61.4954 | -1.5756 | -1.3411 | -1.5893 | -1.3548
705.7969 | 121.7468 | -61.5143 | 60.1089 | 0.14932 | 0.005267 | -0.007421 | -0.034174 | 0.036265 | 0.071848 | -0.076452 | 59.9255 | 59.961 | 59.9117 | 59.8881 | 61.5102 | 61.5387 | 61.2711 | 61.4405 | 61.6636 | 61.5195 | 61.5069 | 61.4801 | 61.5505 | 61.5861 | 61.4378 | 59.9712 | 60.0068 | 59.9575 | 59.9339 | 61.556 | 61.5845 | 61.3169 | 61.4863 | -1.5847 | -1.3457 | -1.5985 | -1.3594
707.5625 | 121.8292 | -61.5692 | 60.0082 | 0.14932 | 0.000689 | -0.002842 | -0.029595 | 0.031687 | 0.076426 | -0.067295 | 59.93 | 59.9473 | 59.9209 | 59.8835 | 61.5056 | 61.5341 | 61.2711 | 61.4405 | 61.7185 | 61.5699 | 61.5664 | 61.5396 | 61.6009 | 61.6456 | 61.5019 | 59.9758 | 59.993 | 59.9667 | 59.9293 | 61.5514 | 61.5799 | 61.3169 | 61.4863 | -1.5756 | -1.3411 | -1.5847 | -1.3502
709.3125 | 121.7422 | -61.5829 | 60.0174 | 0.14474 | 0.005267 | -0.007421 | -0.029595 | 0.040843 | 0.081005 | -0.071874 | 59.93 | 59.9564 | 59.9163 | 59.8835 | 61.5102 | 61.5433 | 61.2666 | 61.4405 | 61.7277 | 61.5882 | 61.5755 | 61.5534 | 61.6238 | 61.664 | 61.5111 | 59.9758 | 60.0022 | 59.9621 | 59.9293 | 61.556 | 61.589 | 61.3123 | 61.4863 | -1.5802 | -1.3365 | -1.5939 | -1.3502
711.0781 | 121.7422 | -61.5143 | 60.1089 | 0.1539 | 0.005267 | -0.016578 | -0.029595 | 0.045421 | 0.076426 | -0.08103 | 59.9346 | 59.9564 | 59.9117 | 59.879 | 61.5148 | 61.5387 | 61.2711 | 61.4405 | 61.6682 | 61.5195 | 61.4977 | 61.4847 | 61.5597 | 61.5907 | 61.4333 | 59.9804 | 60.0022 | 59.9575 | 59.9247 | 61.5606 | 61.5845 | 61.3169 | 61.4863 | -1.5802 | -1.3365 | -1.6031 | -1.3594
712.8438 | 121.8201 | -61.5875 | 59.967 | 0.14474 | 0.000689 | -0.016578 | -0.029595 | 0.036265 | 0.076426 | -0.071874 | 59.93 | 59.9656 | 59.9026 | 59.8835 | 61.5056 | 61.5387 | 61.2757 | 61.4313 | 61.7323 | 61.5882 | 61.5709 | 61.5579 | 61.6238 | 61.6639 | 61.5157 | 59.9758 | 60.0113 | 59.9484 | 59.9293 | 61.5514 | 61.5845 | 61.3215 | 61.4771 | -1.5756 | -1.3457 | -1.6031 | -1.3731
714.5312 | 121.8201 | -61.4822 | 60.0861 | 0.14017 | 0.009846 | -0.007421 | -0.025017 | 0.036265 | 0.081005 | -0.071874 | 59.93 | 59.961 | 59.9163 | 59.879 | 61.5011 | 61.5387 | 61.2711 | 61.4451 | 61.6224 | 61.4921 | 61.4748 | 61.4572 | 61.5185 | 61.5632 | 61.4104 | 59.9758 | 60.0068 | 59.9621 | 59.9247 | 61.5468 | 61.5845 | 61.3169 | 61.4908 | -1.571 | -1.3411 | -1.5847 | -1.3548
716.2969 | 121.7514 | -61.6058 | 60.0174 | 0.1539 | 0.005267 | -0.021157 | -0.025017 | 0.036265 | 0.076426 | -0.076452 | 59.9209 | 59.961 | 59.9117 | 59.879 | 61.5056 | 61.5387 | 61.262 | 61.4451 | 61.7597 | 61.6111 | 61.5847 | 61.5808 | 61.6421 | 61.6823 | 61.5294 | 59.9667 | 60.0068 | 59.9575 | 59.9247 | 61.5514 | 61.5845 | 61.3077 | 61.4908 | -1.5847 | -1.3411 | -1.5939 | -1.3502
718 | 121.8567 | -61.5372 | 59.9762 | 0.1539 | 0.000689 | -0.016578 | -0.025017 | 0.036265 | 0.076426 | -0.076452 | 59.93 | 59.9564 | 59.9163 | 59.8835 | 61.5056 | 61.5341 | 61.2757 | 61.4405 | 61.6911 | 61.5379 | 61.5206 | 61.5122 | 61.5734 | 61.6136 | 61.4607 | 59.9758 | 60.0022 | 59.9621 | 59.9293 | 61.5514 | 61.5799 | 61.3215 | 61.4863 | -1.5756 | -1.3457 | -1.5893 | -1.3594
719.75 | 121.7422 | -61.5051 | 60.0861 | 0.14474 | 0.005267 | -0.007421 | -0.029595 | 0.036265 | 0.081005 | -0.076452 | 59.93 | 59.9518 | 59.9117 | 59.8835 | 61.5148 | 61.5387 | 61.2711 | 61.4451 | 61.6499 | 61.5104 | 61.4977 | 61.4755 | 61.5414 | 61.5861 | 61.4287 | 59.9758 | 59.9976 | 59.9575 | 59.9293 | 61.5606 | 61.5845 | 61.3169 | 61.4908 | -1.5847 | -1.3411 | -1.6031 | -1.3594
721.5 | 121.7926 | -61.5463 | 60.022 | 0.14474 | 0.009846 | -0.007421 | -0.025017 | 0.036265 | 0.071848 | -0.071874 | 59.9255 | 59.961 | 59.9072 | 59.879 | 61.5102 | 61.5433 | 61.2711 | 61.4405 | 61.6911 | 61.5562 | 61.5389 | 61.5213 | 61.5826 | 61.6182 | 61.4745 | 59.9712 | 60.0068 | 59.9529 | 59.9247 | 61.556 | 61.589 | 61.3169 | 61.4863 | -1.5847 | -1.3457 | -1.6031 | -1.364
723.2656 | 121.8338 | -61.5189 | 60.0082 | 0.14017 | 0.005267 | -0.012 | -0.029595 | 0.040843 | 0.071848 | -0.071874 | 59.9346 | 59.961 | 59.9117 | 59.8835 | 61.5102 | 61.5341 | 61.2666 | 61.4359 | 61.659 | 61.5241 | 61.5069 | 61.4893 | 61.5597 | 61.5907 | 61.447 | 59.9804 | 60.0068 | 59.9575 | 59.9293 | 61.556 | 61.5799 | 61.3123 | 61.4817 | -1.5756 | -1.3319 | -1.5985 | -1.3548
724.9531 | 121.8796 | -61.5692 | 59.9487 | 0.14932 | 0.000689 | -0.007421 | -0.029595 | 0.040843 | 0.081005 | -0.071874 | 59.9255 | 59.9564 | 59.9163 | 59.8835 | 61.5056 | 61.5387 | 61.2666 | 61.4405 | 61.7185 | 61.5699 | 61.5618 | 61.5396 | 61.6101 | 61.6502 | 61.4973 | 59.9712 | 60.0022 | 59.9621 | 59.9293 | 61.5514 | 61.5845 | 61.3123 | 61.4863 | -1.5802 | -1.3411 | -1.5893 | -1.3502
726.7031 | 121.7972 | -61.5463 | 60.0632 | 0.14474 | 0.009846 | -0.012 | -0.029595 | 0.036265 | 0.081005 | -0.071874 | 59.93 | 59.961 | 59.9209 | 59.879 | 61.5056 | 61.5387 | 61.2711 | 61.4451 | 61.6911 | 61.5562 | 61.5343 | 61.5167 | 61.5826 | 61.6273 | 61.4745 | 59.9758 | 60.0068 | 59.9667 | 59.9247 | 61.5514 | 61.5845 | 61.3169 | 61.4908 | -1.5756 | -1.3411 | -1.5847 | -1.3502
728.4531 | 121.8246 | -61.5326 | 59.9945 | 0.14474 | 0.014425 | -0.016578 | -0.025017 | 0.036265 | 0.076426 | -0.076452 | 59.93 | 59.9656 | 59.9163 | 59.879 | 61.5056 | 61.5433 | 61.2666 | 61.4451 | 61.6773 | 61.547 | 61.516 | 61.5076 | 61.5689 | 61.609 | 61.4561 | 59.9758 | 60.0113 | 59.9621 | 59.9247 | 61.5514 | 61.589 | 61.3123 | 61.4908 | -1.5756 | -1.3365 | -1.5893 | -1.3502
730.1406 | 121.7743 | -61.5646 | 60.022 | 0.14932 | 0.005267 | -0.012 | -0.034174 | 0.045421 | 0.067269 | -0.076452 | 59.9209 | 59.9473 | 59.9163 | 59.8835 | 61.4965 | 61.5387 | 61.2711 | 61.4359 | 61.714 | 61.5699 | 61.5526 | 61.5305 | 61.6101 | 61.6319 | 61.4882 | 59.9667 | 59.993 | 59.9621 | 59.9293 | 61.5423 | 61.5845 | 61.3169 | 61.4817 | -1.5756 | -1.3502 | -1.5802 | -1.3548
731.8906 | 121.8887 | -61.5005 | 60.0586 | 0.14017 | 0.000689 | -0.021157 | -0.029595 | 0.040843 | 0.076426 | -0.076452 | 59.9255 | 59.9564 | 59.9117 | 59.8881 | 61.5102 | 61.5387 | 61.2711 | 61.4405 | 61.6407 | 61.5012 | 61.4794 | 61.471 | 61.5414 | 61.577 | 61.4241 | 59.9712 | 60.0022 | 59.9575 | 59.9339 | 61.556 | 61.5845 | 61.3169 | 61.4863 | -1.5847 | -1.3457 | -1.5985 | -1.3594
733.6562 | 121.7422 | -61.5326 | 60.1089 | 0.1539 | 0.005267 | -0.007421 | -0.025017 | 0.036265 | 0.081005 | -0.062717 | 59.93 | 59.9656 | 59.9163 | 59.879 | 61.5056 | 61.5341 | 61.2711 | 61.4405 | 61.6865 | 61.5379 | 61.5252 | 61.5076 | 61.5689 | 61.6136 | 61.4699 | 59.9758 | 60.0113 | 59.9621 | 59.9247 | 61.5514 | 61.5799 | 61.3169 | 61.4863 | -1.5756 | -1.3411 | -1.5893 | -1.3548
735.3906 | 121.7422 | -61.5005 | 60.0998 | 0.14474 | 0.005267 | -0.016578 | -0.025017 | 0.031687 | 0.076426 | -0.071874 | 59.93 | 59.9564 | 59.9163 | 59.879 | 61.5011 | 61.5341 | 61.2666 | 61.4451 | 61.6453 | 61.5058 | 61.484 | 61.4755 | 61.5322 | 61.577 | 61.4287 | 59.9758 | 60.0022 | 59.9621 | 59.9247 | 61.5468 | 61.5799 | 61.3123 | 61.4908 | -1.571 | -1.3365 | -1.5847 | -1.3502
737.0781 | 121.9025 | -61.4777 | 60.0494 | 0.13101 | 0.005267 | -0.012 | -0.025017 | 0.027109 | 0.076426 | -0.076452 | 59.9255 | 59.961 | 59.9209 | 59.8881 | 61.5102 | 61.5433 | 61.2666 | 61.4405 | 61.6087 | 61.4829 | 61.4657 | 61.4526 | 61.5048 | 61.5541 | 61.4012 | 59.9712 | 60.0068 | 59.9667 | 59.9339 | 61.556 | 61.589 | 61.3123 | 61.4863 | -1.5847 | -1.3411 | -1.5893 | -1.3457
738.8438 | 121.8292 | -61.5601 | 59.9991 | 0.14932 | 0.005267 | -0.016578 | -0.029595 | 0.036265 | 0.076426 | -0.071874 | 59.93 | 59.961 | 59.9117 | 59.8881 | 61.5011 | 61.5387 | 61.262 | 61.4451 | 61.7094 | 61.5653 | 61.5435 | 61.5305 | 61.5963 | 61.6365 | 61.4882 | 59.9758 | 60.0068 | 59.9575 | 59.9339 | 61.5468 | 61.5845 | 61.3077 | 61.4908 | -1.571 | -1.3319 | -1.5893 | -1.3502
740.5938 | 121.7514 | -61.5738 | 60.0357 | 0.14932 | 0.009846 | -0.007421 | -0.029595 | 0.036265 | 0.085583 | -0.071874 | 59.9255 | 59.961 | 59.9163 | 59.8835 | 61.5056 | 61.5387 | 61.2666 | 61.4405 | 61.7231 | 61.5836 | 61.5664 | 61.5442 | 61.6101 | 61.6594 | 61.5019 | 59.9712 | 60.0068 | 59.9621 | 59.9293 | 61.5514 | 61.5845 | 61.3123 | 61.4863 | -1.5802 | -1.3411 | -1.5893 | -1.3502
742.2812 | 121.7972 | -61.5921 | 59.9945 | 0.14474 | 0.014425 | -0.012 | -0.020438 | 0.045421 | 0.071848 | -0.071874 | 59.9209 | 59.9701 | 59.9209 | 59.8835 | 61.5056 | 61.5341 | 61.2666 | 61.4405 | 61.7368 | 61.6065 | 61.5801 | 61.5717 | 61.6375 | 61.6639 | 61.5202 | 59.9667 | 60.0159 | 59.9667 | 59.9293 | 61.5514 | 61.5799 | 61.3123 | 61.4863 | -1.5847 | -1.3457 | -1.5847 | -1.3457
744.0312 | 121.756 | -61.5555 | 60.0449 | 0.14932 | 0.014425 | -0.007421 | -0.034174 | 0.045421 | 0.076426 | -0.076452 | 59.9209 | 59.961 | 59.9163 | 59.8744 | 61.5056 | 61.5387 | 61.262 | 61.4451 | 61.7048 | 61.5699 | 61.5481 | 61.5213 | 61.6009 | 61.6319 | 61.479 | 59.9667 | 60.0068 | 59.9621 | 59.9201 | 61.5514 | 61.5845 | 61.3077 | 61.4908 | -1.5847 | -1.3411 | -1.5893 | -1.3457
745.7812 | 121.8155 | -61.5189 | 60.0082 | 0.14017 | -0.00389 | -0.012 | -0.029595 | 0.031687 | 0.081005 | -0.076452 | 59.93 | 59.9564 | 59.9163 | 59.8835 | 61.5056 | 61.5295 | 61.2666 | 61.4451 | 61.659 | 61.515 | 61.5069 | 61.4893 | 61.5505 | 61.5999 | 61.4424 | 59.9758 | 60.0022 | 59.9621 | 59.9293 | 61.5514 | 61.5753 | 61.3123 | 61.4908 | -1.5756 | -1.3365 | -1.5893 | -1.3502
747.4844 | 121.7422 | -61.5738 | 60.022 | 0.14932 | 0.014425 | -0.007421 | -0.029595 | 0.040843 | 0.081005 | -0.071874 | 59.9346 | 59.961 | 59.9163 | 59.879 | 61.5011 | 61.5387 | 61.262 | 61.4451 | 61.7231 | 61.5882 | 61.5664 | 61.5442 | 61.6146 | 61.6548 | 61.5019 | 59.9804 | 60.0068 | 59.9621 | 59.9247 | 61.5468 | 61.5845 | 61.3077 | 61.4908 | -1.5664 | -1.3273 | -1.5847 | -1.3457
749.2344 | 121.8704 | -61.4822 | 60.0357 | 0.14932 | 0.000689 | -0.016578 | -0.029595 | 0.036265 | 0.071848 | -0.076452 | 59.93 | 59.961 | 59.9209 | 59.8835 | 61.5056 | 61.5433 | 61.2711 | 61.4405 | 61.6316 | 61.4829 | 61.4657 | 61.4526 | 61.5185 | 61.5541 | 61.4058 | 59.9758 | 60.0068 | 59.9667 | 59.9293 | 61.5514 | 61.589 | 61.3169 | 61.4863 | -1.5756 | -1.3411 | -1.5847 | -1.3502
750.9844 | 121.7468 | -61.4914 | 60.1273 | 0.14474 | 0.005267 | -0.021157 | -0.029595 | 0.040843 | 0.081005 | -0.071874 | 59.9346 | 59.9473 | 59.9209 | 59.8881 | 61.5102 | 61.5387 | 61.2711 | 61.4451 | 61.6361 | 61.4967 | 61.4702 | 61.4618 | 61.5322 | 61.5724 | 61.4195 | 59.9804 | 59.993 | 59.9667 | 59.9339 | 61.556 | 61.5845 | 61.3169 | 61.4908 | -1.5756 | -1.3365 | -1.5893 | -1.3502
752.75 | 121.875 | -61.4914 | 60.054 | 0.14474 | 0.000689 | -0.012 | -0.025017 | 0.036265 | 0.076426 | -0.076452 | 59.9255 | 59.9564 | 59.9117 | 59.879 | 61.5102 | 61.5387 | 61.2711 | 61.4405 | 61.6361 | 61.4921 | 61.4794 | 61.4664 | 61.5277 | 61.5678 | 61.4149 | 59.9712 | 60.0022 | 59.9575 | 59.9247 | 61.556 | 61.5845 | 61.3169 | 61.4863 | -1.5847 | -1.3457 | -1.5985 | -1.3594
754.5 | 121.8887 | -61.5692 | 59.9442 | 0.14474 | 0.009846 | -0.016578 | -0.034174 | 0.040843 | 0.076426 | -0.076452 | 59.93 | 59.9656 | 59.9163 | 59.8835 | 61.5011 | 61.5387 | 61.262 | 61.4359 | 61.714 | 61.5791 | 61.5526 | 61.535 | 61.6101 | 61.6456 | 61.4928 | 59.9758 | 60.0113 | 59.9621 | 59.9293 | 61.5468 | 61.5845 | 61.3077 | 61.4817 | -1.571 | -1.3319 | -1.5847 | -1.3457
756.2656 | 121.8704 | -61.5051 | 60.0586 | 0.14474 | 0.000689 | -0.012 | -0.034174 | 0.040843 | 0.076426 | -0.076452 | 59.9346 | 59.9656 | 59.9163 | 59.8881 | 61.5056 | 61.5341 | 61.2711 | 61.4451 | 61.6499 | 61.5058 | 61.4931 | 61.471 | 61.546 | 61.5816 | 61.4287 | 59.9804 | 60.0113 | 59.9621 | 59.9339 | 61.5514 | 61.5799 | 61.3169 | 61.4908 | -1.571 | -1.3365 | -1.5893 | -1.3548
757.9688 | 121.7422 | -61.5921 | 60.0266 | 0.1539 | 0.009846 | -0.012 | -0.025017 | 0.036265 | 0.085583 | -0.071874 | 59.93 | 59.961 | 59.9163 | 59.879 | 61.4965 | 61.5295 | 61.2711 | 61.4405 | 61.746 | 61.6019 | 61.5801 | 61.5671 | 61.6284 | 61.6777 | 61.5202 | 59.9758 | 60.0068 | 59.9621 | 59.9247 | 61.5423 | 61.5753 | 61.3169 | 61.4863 | -1.5664 | -1.3411 | -1.5802 | -1.3548
759.7188 | 121.8521 | -61.5097 | 60.022 | 0.14932 | 0.005267 | -0.016578 | -0.034174 | 0.031687 | 0.076426 | -0.08103 | 59.9346 | 59.9656 | 59.9163 | 59.8881 | 61.4965 | 61.5387 | 61.2711 | 61.4405 | 61.659 | 61.515 | 61.4931 | 61.4755 | 61.5414 | 61.5861 | 61.4287 | 59.9804 | 60.0113 | 59.9621 | 59.9339 | 61.5423 | 61.5845 | 61.3169 | 61.4863 | -1.5619 | -1.3365 | -1.5802 | -1.3548
761.4688 | 121.8842 | -61.5509 | 59.9487 | 0.14474 | 0.005267 | -0.012 | -0.029595 | 0.040843 | 0.081005 | -0.071874 | 59.9255 | 59.9564 | 59.9163 | 59.8927 | 61.5148 | 61.5387 | 61.262 | 61.4405 | 61.6956 | 61.5562 | 61.5389 | 61.5213 | 61.5917 | 61.6319 | 61.479 | 59.9712 | 60.0022 | 59.9621 | 59.9385 | 61.5606 | 61.5845 | 61.3077 | 61.4863 | -1.5893 | -1.3365 | -1.5985 | -1.3457
763.1719 | 121.7514 | -61.5051 | 60.0952 | 0.1539 | 0.014425 | -0.007421 | -0.029595 | 0.040843 | 0.076426 | -0.076452 | 59.9346 | 59.961 | 59.9163 | 59.8927 | 61.5056 | 61.5387 | 61.2757 | 61.4405 | 61.659 | 61.5196 | 61.4977 | 61.4755 | 61.546 | 61.5816 | 61.4287 | 59.9804 | 60.0068 | 59.9621 | 59.9385 | 61.5514 | 61.5845 | 61.3215 | 61.4863 | -1.571 | -1.3411 | -1.5893 | -1.3594
764.9219 | 121.788 | -61.5326 | 60.0494 | 0.1539 | 0.014425 | -0.007421 | -0.029595 | 0.036265 | 0.081005 | -0.071874 | 59.93 | 59.9656 | 59.9209 | 59.8881 | 61.5056 | 61.5387 | 61.262 | 61.4451 | 61.6865 | 61.547 | 61.5252 | 61.503 | 61.5689 | 61.6136 | 61.4607 | 59.9758 | 60.0113 | 59.9667 | 59.9339 | 61.5514 | 61.5845 | 61.3077 | 61.4908 | -1.5756 | -1.3319 | -1.5847 | -1.3411
766.6719 | 121.8246 | -61.5417 | 60.0128 | 0.1539 | 0.009846 | -0.012 | -0.034174 | 0.031687 | 0.071848 | -0.076452 | 59.9346 | 59.9656 | 59.9163 | 59.8927 | 61.5011 | 61.5341 | 61.2528 | 61.4405 | 61.6956 | 61.5516 | 61.5297 | 61.5076 | 61.5734 | 61.6136 | 61.4653 | 59.9804 | 60.0113 | 59.9621 | 59.9385 | 61.5468 | 61.5799 | 61.2986 | 61.4863 | -1.5664 | -1.3182 | -1.5847 | -1.3365
768.4219 | 121.875 | -61.5509 | 59.9716 | 0.14474 | 0.005267 | -0.012 | -0.029595 | 0.040843 | 0.076426 | -0.067295 | 59.93 | 59.9656 | 59.9163 | 59.8881 | 61.5011 | 61.5295 | 61.2666 | 61.4451 | 61.6956 | 61.5562 | 61.5389 | 61.5213 | 61.5917 | 61.6273 | 61.4836 | 59.9758 | 60.0113 | 59.9621 | 59.9339 | 61.5468 | 61.5753 | 61.3123 | 61.4908 | -1.571 | -1.3365 | -1.5847 | -1.3502
770.1094 | 121.8338 | -61.5097 | 60.0174 | 0.14474 | 0.000689 | -0.016578 | -0.020438 | 0.036265 | 0.081005 | -0.071874 | 59.9255 | 59.961 | 59.9209 | 59.8927 | 61.5056 | 61.5341 | 61.2757 | 61.4313 | 61.6544 | 61.5104 | 61.4931 | 61.4893 | 61.546 | 61.5907 | 61.4378 | 59.9712 | 60.0068 | 59.9667 | 59.9385 | 61.5514 | 61.5799 | 61.3215 | 61.4771 | -1.5802 | -1.3502 | -1.5847 | -1.3548
771.8594 | 121.8338 | -61.5372 | 60.0266 | 0.14474 | 0.005267 | -0.012 | -0.034174 | 0.031687 | 0.076426 | -0.08103 | 59.9392 | 59.9564 | 59.9117 | 59.879 | 61.5056 | 61.5341 | 61.2711 | 61.4405 | 61.6819 | 61.5424 | 61.5252 | 61.503 | 61.5689 | 61.6136 | 61.4561 | 59.985 | 60.0022 | 59.9575 | 59.9247 | 61.5514 | 61.5799 | 61.3169 | 61.4863 | -1.5664 | -1.3319 | -1.5939 | -1.3594
773.5469 | 121.756 | -61.5189 | 60.0952 | 0.1539 | 0.005267 | -0.002842 | -0.025017 | 0.036265 | 0.076426 | -0.071874 | 59.9346 | 59.961 | 59.9163 | 59.8881 | 61.5011 | 61.5341 | 61.2711 | 61.4359 | 61.6728 | 61.5241 | 61.516 | 61.4938 | 61.5551 | 61.5953 | 61.447 | 59.9804 | 60.0068 | 59.9621 | 59.9339 | 61.5468 | 61.5799 | 61.3169 | 61.4817 | -1.5664 | -1.3365 | -1.5847 | -1.3548
775.2969 | 121.875 | -61.5509 | 59.9442 | 0.14932 | 0.000689 | -0.012 | -0.029595 | 0.036265 | 0.076426 | -0.076452 | 59.9392 | 59.9656 | 59.9117 | 59.8973 | 61.5011 | 61.5341 | 61.262 | 61.4359 | 61.7002 | 61.5516 | 61.5389 | 61.5213 | 61.5872 | 61.6273 | 61.4745 | 59.985 | 60.0113 | 59.9575 | 59.943 | 61.5468 | 61.5799 | 61.3077 | 61.4817 | -1.5618 | -1.3228 | -1.5893 | -1.3502
776.9844 | 121.7377 | -61.6013 | 60.0494 | 0.14474 | 0.009846 | -0.007421 | -0.029595 | 0.036265 | 0.076426 | -0.08103 | 59.9346 | 59.9656 | 59.9209 | 59.8881 | 61.5011 | 61.5387 | 61.262 | 61.4359 | 61.746 | 61.6111 | 61.5938 | 61.5717 | 61.6375 | 61.6777 | 61.5202 | 59.9804 | 60.0113 | 59.9667 | 59.9339 | 61.5468 | 61.5845 | 61.3077 | 61.4817 | -1.5664 | -1.3273 | -1.5802 | -1.3411
778.7344 | 121.788 | -61.528 | 60.0449 | 0.14474 | 0.005267 | -0.012 | -0.025017 | 0.036265 | 0.076426 | -0.071874 | 59.9346 | 59.961 | 59.9209 | 59.8973 | 61.5056 | 61.5295 | 61.262 | 61.4359 | 61.6728 | 61.5333 | 61.516 | 61.503 | 61.5643 | 61.6044 | 61.4561 | 59.9804 | 60.0068 | 59.9667 | 59.943 | 61.5514 | 61.5753 | 61.3077 | 61.4817 | -1.571 | -1.3273 | -1.5847 | -1.3411
780.4844 | 121.7743 | -61.5234 | 60.0998 | 0.14474 | 0.009846 | -0.012 | -0.025017 | 0.031687 | 0.076426 | -0.076452 | 59.93 | 59.9747 | 59.9209 | 59.8835 | 61.5102 | 61.5341 | 61.2666 | 61.4359 | 61.6682 | 61.5333 | 61.5114 | 61.4984 | 61.5551 | 61.5999 | 61.447 | 59.9758 | 60.0205 | 59.9667 | 59.9293 | 61.556 | 61.5799 | 61.3123 | 61.4817 | -1.5802 | -1.3365 | -1.5893 | -1.3457
782.1719 | 121.8292 | -61.5051 | 60.054 | 0.14474 | 0.005267 | -0.012 | -0.025017 | 0.045421 | 0.071848 | -0.071874 | 59.9438 | 59.9701 | 59.9163 | 59.8881 | 61.5011 | 61.5341 | 61.2666 | 61.4359 | 61.6499 | 61.5104 | 61.4931 | 61.4801 | 61.5505 | 61.577 | 61.4333 | 59.9896 | 60.0159 | 59.9621 | 59.9339 | 61.5468 | 61.5799 | 61.3123 | 61.4817 | -1.5573 | -1.3228 | -1.5847 | -1.3502
783.9375 | 121.8338 | -61.5372 | 59.9991 | 0.14474 | 0.000689 | -0.012 | -0.029595 | 0.040843 | 0.076426 | -0.076452 | 59.9346 | 59.961 | 59.9209 | 59.8927 | 61.5102 | 61.5295 | 61.2574 | 61.4359 | 61.6819 | 61.5379 | 61.5252 | 61.5076 | 61.578 | 61.6136 | 61.4607 | 59.9804 | 60.0068 | 59.9667 | 59.9385 | 61.556 | 61.5753 | 61.3032 | 61.4817 | -1.5756 | -1.3228 | -1.5893 | -1.3365
785.7031 | 121.7606 | -61.5005 | 60.0815 | 0.14474 | 0.009846 | -0.012 | -0.034174 | 0.031687 | 0.081005 | -0.076452 | 59.9346 | 59.9656 | 59.9163 | 59.8835 | 61.5011 | 61.5295 | 61.2711 | 61.4405 | 61.6453 | 61.5104 | 61.4885 | 61.4664 | 61.5322 | 61.5816 | 61.4241 | 59.9804 | 60.0113 | 59.9621 | 59.9293 | 61.5468 | 61.5753 | 61.3169 | 61.4863 | -1.5664 | -1.3365 | -1.5847 | -1.3548
787.4375 | 121.7514 | -61.4914 | 60.0998 | 0.14474 | 0.005267 | -0.012 | -0.025017 | 0.040843 | 0.085583 | -0.076452 | 59.9346 | 59.9701 | 59.9209 | 59.8835 | 61.4965 | 61.5387 | 61.2666 | 61.4359 | 61.6361 | 61.4967 | 61.4794 | 61.4664 | 61.5322 | 61.577 | 61.4149 | 59.9804 | 60.0159 | 59.9667 | 59.9293 | 61.5423 | 61.5845 | 61.3123 | 61.4817 | -1.5619 | -1.3319 | -1.5756 | -1.3457
789.125 | 121.8658 | -61.5646 | 59.9945 | 0.14474 | 0.005267 | -0.016578 | -0.029595 | 0.036265 | 0.076426 | -0.071874 | 59.9392 | 59.9656 | 59.9163 | 59.8881 | 61.5102 | 61.5341 | 61.2666 | 61.4359 | 61.7094 | 61.5699 | 61.5481 | 61.535 | 61.6009 | 61.6411 | 61.4928 | 59.985 | 60.0113 | 59.9621 | 59.9339 | 61.556 | 61.5799 | 61.3123 | 61.4817 | -1.571 | -1.3273 | -1.5939 | -1.3502
790.875 | 121.7697 | -61.528 | 60.0677 | 0.1539 | 0.009846 | -0.002842 | -0.025017 | 0.040843 | 0.076426 | -0.067295 | 59.9346 | 59.9656 | 59.9255 | 59.8881 | 61.5011 | 61.5295 | 61.262 | 61.4313 | 61.6819 | 61.5379 | 61.5252 | 61.503 | 61.5689 | 61.6044 | 61.4607 | 59.9804 | 60.0113 | 59.9712 | 59.9339 | 61.5468 | 61.5753 | 61.3077 | 61.4771 | -1.5664 | -1.3273 | -1.5756 | -1.3365
792.5625 | 121.8018 | -61.5005 | 60.0769 | 0.14474 | 0.005267 | -0.012 | -0.029595 | 0.031687 | 0.071848 | -0.071874 | 59.9392 | 59.961 | 59.9163 | 59.8927 | 61.5056 | 61.5341 | 61.262 | 61.4359 | 61.6453 | 61.5058 | 61.4885 | 61.471 | 61.5322 | 61.5724 | 61.4287 | 59.985 | 60.0068 | 59.9621 | 59.9385 | 61.5514 | 61.5799 | 61.3077 | 61.4817 | -1.5664 | -1.3228 | -1.5893 | -1.3457
794.3281 | 121.8201 | -61.5326 | 60.0403 | 0.14474 | 0.005267 | -0.012 | -0.025017 | 0.036265 | 0.071848 | -0.071874 | 59.9346 | 59.9701 | 59.9117 | 59.8927 | 61.5056 | 61.5341 | 61.2666 | 61.4359 | 61.6773 | 61.5379 | 61.5206 | 61.5076 | 61.5689 | 61.6044 | 61.4607 | 59.9804 | 60.0159 | 59.9575 | 59.9385 | 61.5514 | 61.5799 | 61.3123 | 61.4817 | -1.571 | -1.3319 | -1.5939 | -1.3548
796.0156 | 121.8704 | -61.4868 | 60.0586 | 0.14932 | 0.000689 | -0.012 | -0.025017 | 0.036265 | 0.076426 | -0.076452 | 59.93 | 59.961 | 59.9209 | 59.8881 | 61.4965 | 61.5341 | 61.262 | 61.4359 | 61.6361 | 61.4875 | 61.4748 | 61.4618 | 61.5231 | 61.5632 | 61.4104 | 59.9758 | 60.0068 | 59.9667 | 59.9339 | 61.5423 | 61.5799 | 61.3077 | 61.4817 | -1.5664 | -1.3319 | -1.5756 | -1.3411
797.7656 | 121.7331 | -61.5097 | 60.1089 | 0.14017 | 0.000689 | -0.002842 | -0.034174 | 0.040843 | 0.076426 | -0.071874 | 59.9346 | 59.9656 | 59.9117 | 59.8835 | 61.4965 | 61.5341 | 61.262 | 61.4359 | 61.6499 | 61.5104 | 61.5069 | 61.4755 | 61.5505 | 61.5861 | 61.4378 | 59.9804 | 60.0113 | 59.9575 | 59.9293 | 61.5423 | 61.5799 | 61.3077 | 61.4817 | -1.5619 | -1.3273 | -1.5847 | -1.3502
799.5156 | 121.8109 | -61.5372 | 60.0632 | 0.14474 | 0.005267 | -0.016578 | -0.029595 | 0.040843 | 0.071848 | -0.067295 | 59.9392 | 59.961 | 59.9209 | 59.8881 | 61.4965 | 61.5341 | 61.262 | 61.4268 | 61.6819 | 61.5424 | 61.5206 | 61.5076 | 61.578 | 61.609 | 61.4699 | 59.985 | 60.0068 | 59.9667 | 59.9339 | 61.5423 | 61.5799 | 61.3077 | 61.4725 | -1.5573 | -1.3228 | -1.5756 | -1.3411
801.2656 | 121.8292 | -61.4777 | 60.0769 | 0.1539 | 0.005267 | -0.012 | -0.029595 | 0.040843 | 0.076426 | -0.071874 | 59.93 | 59.9701 | 59.9255 | 59.8835 | 61.5056 | 61.5295 | 61.2666 | 61.4359 | 61.6316 | 61.4829 | 61.4657 | 61.4481 | 61.5185 | 61.5541 | 61.4058 | 59.9758 | 60.0159 | 59.9712 | 59.9293 | 61.5514 | 61.5753 | 61.3123 | 61.4817 | -1.5756 | -1.3365 | -1.5802 | -1.3411
803.0156 | 121.7926 | -61.5189 | 60.0815 | 0.14932 | 0.014425 | -0.002842 | -0.025017 | 0.036265 | 0.081005 | -0.067295 | 59.9392 | 59.9701 | 59.9255 | 59.8881 | 61.4965 | 61.5295 | 61.262 | 61.4405 | 61.6682 | 61.5333 | 61.516 | 61.4938 | 61.5551 | 61.5999 | 61.4516 | 59.985 | 60.0159 | 59.9712 | 59.9339 | 61.5423 | 61.5753 | 61.3077 | 61.4863 | -1.5573 | -1.3228 | -1.571 | -1.3365
804.7188 | 121.7651 | -61.5738 | 60.0586 | 0.14932 | 0.000689 | -0.012 | -0.025017 | 0.036265 | 0.076426 | -0.067295 | 59.9346 | 59.9656 | 59.9255 | 59.8973 | 61.4965 | 61.5295 | 61.2574 | 61.4405 | 61.7231 | 61.5745 | 61.5618 | 61.5488 | 61.6101 | 61.6502 | 61.5065 | 59.9804 | 60.0113 | 59.9712 | 59.943 | 61.5423 | 61.5753 | 61.3032 | 61.4863 | -1.5619 | -1.3228 | -1.571 | -1.3319
806.4844 | 121.7285 | -61.5921 | 60.0403 | 0.14932 | 0.009846 | -0.002842 | -0.029595 | 0.040843 | 0.081005 | -0.067295 | 59.9346 | 59.9656 | 59.9255 | 59.8973 | 61.4965 | 61.5341 | 61.262 | 61.4405 | 61.7414 | 61.6019 | 61.5893 | 61.5625 | 61.6329 | 61.6731 | 61.5248 | 59.9804 | 60.0113 | 59.9712 | 59.943 | 61.5423 | 61.5799 | 61.3077 | 61.4863 | -1.5619 | -1.3273 | -1.571 | -1.3365
808.1719 | 121.788 | -61.5143 | 60.1044 | 0.14474 | 0.005267 | -0.012 | -0.025017 | 0.036265 | 0.076426 | -0.071874 | 59.9438 | 59.9701 | 59.9163 | 59.8881 | 61.4965 | 61.5295 | 61.262 | 61.4405 | 61.659 | 61.5195 | 61.5023 | 61.4893 | 61.5505 | 61.5907 | 61.4424 | 59.9896 | 60.0159 | 59.9621 | 59.9339 | 61.5423 | 61.5753 | 61.3077 | 61.4863 | -1.5527 | -1.3182 | -1.5802 | -1.3457
809.9219 | 121.756 | -61.5601 | 60.0082 | 0.1539 | 0.009846 | -0.012 | -0.029595 | 0.045421 | 0.081005 | -0.071874 | 59.9346 | 59.9747 | 59.9255 | 59.8973 | 61.4965 | 61.525 | 61.2574 | 61.4359 | 61.714 | 61.5699 | 61.5481 | 61.5305 | 61.6055 | 61.6411 | 61.4882 | 59.9804 | 60.0205 | 59.9712 | 59.943 | 61.5423 | 61.5707 | 61.3032 | 61.4817 | -1.5619 | -1.3228 | -1.571 | -1.3319
811.6875 | 121.8704 | -61.4777 | 60.0677 | 0.14474 | -0.008469 | -0.012 | -0.029595 | 0.036265 | 0.067269 | -0.08103 | 59.9392 | 59.9747 | 59.9163 | 59.8927 | 61.5011 | 61.5295 | 61.262 | 61.4405 | 61.6224 | 61.4692 | 61.4657 | 61.4481 | 61.5139 | 61.5449 | 61.3966 | 59.985 | 60.0205 | 59.9621 | 59.9385 | 61.5468 | 61.5753 | 61.3077 | 61.4863 | -1.5618 | -1.3228 | -1.5847 | -1.3457
813.4375 | 121.7743 | -61.5005 | 60.0952 | 0.14474 | 0.000689 | -0.012 | -0.025017 | 0.031687 | 0.076426 | -0.067295 | 59.9392 | 59.9656 | 59.9255 | 59.8973 | 61.4965 | 61.5295 | 61.262 | 61.4313 | 61.6453 | 61.5012 | 61.4885 | 61.4755 | 61.5322 | 61.577 | 61.4333 | 59.985 | 60.0113 | 59.9712 | 59.943 | 61.5423 | 61.5753 | 61.3077 | 61.4771 | -1.5573 | -1.3228 | -1.571 | -1.3365
815.125 | 121.8155 | -61.5234 | 60.0357 | 0.14474 | -0.00389 | -0.021157 | -0.029595 | 0.040843 | 0.081005 | -0.071874 | 59.9438 | 59.9747 | 59.9209 | 59.8927 | 61.5011 | 61.5295 | 61.2574 | 61.4313 | 61.6682 | 61.5195 | 61.5023 | 61.4938 | 61.5643 | 61.6044 | 61.4516 | 59.9896 | 60.0205 | 59.9667 | 59.9385 | 61.5468 | 61.5753 | 61.3032 | 61.4771 | -1.5573 | -1.3136 | -1.5802 | -1.3365
816.875 | 121.7926 | -61.5189 | 60.0449 | 0.14017 | 0.000689 | -0.012 | -0.025017 | 0.040843 | 0.081005 | -0.067295 | 59.9438 | 59.9701 | 59.9209 | 59.8881 | 61.4965 | 61.525 | 61.2666 | 61.4313 | 61.659 | 61.5195 | 61.5069 | 61.4938 | 61.5597 | 61.5999 | 61.4516 | 59.9896 | 60.0159 | 59.9667 | 59.9339 | 61.5423 | 61.5707 | 61.3123 | 61.4771 | -1.5527 | -1.3228 | -1.5756 | -1.3457
818.625 | 121.7468 | -61.5692 | 60.0586 | 0.14474 | 0.000689 | -0.007421 | -0.01586 | 0.036265 | 0.071848 | -0.071874 | 59.9392 | 59.9747 | 59.9301 | 59.8881 | 61.4965 | 61.5341 | 61.262 | 61.4313 | 61.714 | 61.5699 | 61.5618 | 61.5534 | 61.6055 | 61.6411 | 61.4973 | 59.985 | 60.0205 | 59.9758 | 59.9339 | 61.5423 | 61.5799 | 61.3077 | 61.4771 | -1.5573 | -1.3228 | -1.5664 | -1.3319
820.375 | 121.7789 | -61.528 | 60.0632 | 0.14017 | 0.000689 | -0.012 | -0.029595 | 0.049999 | 0.085583 | -0.071874 | 59.93 | 59.9656 | 59.9255 | 59.8927 | 61.4965 | 61.5295 | 61.2666 | 61.4359 | 61.6682 | 61.5287 | 61.516 | 61.4984 | 61.578 | 61.6136 | 61.4561 | 59.9758 | 60.0113 | 59.9712 | 59.9385 | 61.5423 | 61.5753 | 61.3123 | 61.4817 | -1.5664 | -1.3365 | -1.571 | -1.3411
822.0625 | 121.8887 | -61.5051 | 60.0494 | 0.14474 | -0.00389 | -0.007421 | -0.034174 | 0.040843 | 0.081005 | -0.071874 | 59.9438 | 59.9701 | 59.9117 | 59.8881 | 61.5011 | 61.5387 | 61.262 | 61.4359 | 61.6499 | 61.5012 | 61.4977 | 61.471 | 61.546 | 61.5861 | 61.4333 | 59.9896 | 60.0159 | 59.9575 | 59.9339 | 61.5468 | 61.5845 | 61.3077 | 61.4817 | -1.5573 | -1.3182 | -1.5893 | -1.3502
823.8438 | 121.7514 | -61.5189 | 60.1089 | 0.14017 | 0.009846 | -0.016578 | -0.025017 | 0.036265 | 0.076426 | -0.071874 | 59.9438 | 59.9656 | 59.9255 | 59.8881 | 61.5011 | 61.5387 | 61.262 | 61.4451 | 61.659 | 61.5287 | 61.5023 | 61.4938 | 61.5551 | 61.5953 | 61.447 | 59.9896 | 60.0113 | 59.9712 | 59.9339 | 61.5468 | 61.5845 | 61.3077 | 61.4908 | -1.5573 | -1.3182 | -1.5756 | -1.3365
825.5312 | 121.8658 | -61.496 | 60.0677 | 0.14017 | 0.000689 | -0.012 | -0.029595 | 0.036265 | 0.076426 | -0.071874 | 59.9392 | 59.9656 | 59.9209 | 59.8927 | 61.5011 | 61.5341 | 61.262 | 61.4313 | 61.6361 | 61.4967 | 61.484 | 61.4664 | 61.5322 | 61.5724 | 61.4241 | 59.985 | 60.0113 | 59.9667 | 59.9385 | 61.5468 | 61.5799 | 61.3077 | 61.4771 | -1.5618 | -1.3228 | -1.5802 | -1.3411
827.2812 | 121.7422 | -61.5189 | 60.1181 | 0.14017 | 0.000689 | -0.016578 | -0.020438 | 0.045421 | 0.076426 | -0.076452 | 59.9392 | 59.9701 | 59.9163 | 59.8927 | 61.5056 | 61.5295 | 61.2574 | 61.4313 | 61.659 | 61.5195 | 61.5023 | 61.4984 | 61.5643 | 61.5953 | 61.4424 | 59.985 | 60.0159 | 59.9621 | 59.9385 | 61.5514 | 61.5753 | 61.3032 | 61.4771 | -1.5664 | -1.3182 | -1.5893 | -1.3411
829.0469 | 121.7422 | -61.5005 | 60.1089 | 0.14932 | 0.005267 | -0.012 | -0.020438 | 0.040843 | 0.076426 | -0.067295 | 59.9392 | 59.9701 | 59.9209 | 59.8835 | 61.4919 | 61.5341 | 61.262 | 61.4359 | 61.6499 | 61.5058 | 61.4885 | 61.4801 | 61.5414 | 61.577 | 61.4333 | 59.985 | 60.0159 | 59.9667 | 59.9293 | 61.5377 | 61.5799 | 61.3077 | 61.4817 | -1.5527 | -1.3228 | -1.571 | -1.3411
830.8125 | 121.8658 | -61.4868 | 60.0494 | 0.14474 | 0.005267 | -0.012 | -0.025017 | 0.031687 | 0.076426 | -0.076452 | 59.9392 | 59.9747 | 59.9209 | 59.8973 | 61.5011 | 61.5341 | 61.262 | 61.4359 | 61.6316 | 61.4921 | 61.4748 | 61.4618 | 61.5185 | 61.5632 | 61.4104 | 59.985 | 60.0205 | 59.9667 | 59.943 | 61.5468 | 61.5799 | 61.3077 | 61.4817 | -1.5618 | -1.3228 | -1.5802 | -1.3411
832.5 | 121.8979 | -61.4731 | 60.0311 | 0.14932 | 0.005267 | -0.016578 | -0.029595 | 0.045421 | 0.076426 | -0.071874 | 59.9392 | 59.9701 | 59.9255 | 59.8881 | 61.5011 | 61.5295 | 61.2574 | 61.4451 | 61.6224 | 61.4784 | 61.4565 | 61.4435 | 61.5185 | 61.5495 | 61.4012 | 59.985 | 60.0159 | 59.9712 | 59.9339 | 61.5468 | 61.5753 | 61.3032 | 61.4908 | -1.5618 | -1.3182 | -1.5756 | -1.3319
834.25 | 121.8842 | -61.4822 | 60.0906 | 0.14474 | 0.005267 | -0.007421 | -0.025017 | 0.040843 | 0.071848 | -0.076452 | 59.9438 | 59.9793 | 59.9209 | 59.8881 | 61.4965 | 61.5295 | 61.262 | 61.4359 | 61.627 | 61.4875 | 61.4748 | 61.4572 | 61.5231 | 61.5541 | 61.4058 | 59.9896 | 60.0251 | 59.9667 | 59.9339 | 61.5423 | 61.5753 | 61.3077 | 61.4817 | -1.5527 | -1.3182 | -1.5756 | -1.3411
835.9375 | 121.907 | -61.4548 | 60.054 | 0.14474 | 0.005267 | -0.012 | -0.029595 | 0.036265 | 0.071848 | -0.071874 | 59.9392 | 59.9701 | 59.9255 | 59.8927 | 61.5102 | 61.5387 | 61.2574 | 61.4451 | 61.5995 | 61.46 | 61.4428 | 61.4252 | 61.491 | 61.5266 | 61.3829 | 59.985 | 60.0159 | 59.9712 | 59.9385 | 61.556 | 61.5845 | 61.3032 | 61.4908 | -1.571 | -1.3182 | -1.5847 | -1.3319
837.6875 | 121.8613 | -61.4914 | 60.0494 | 0.14474 | 0.005267 | -0.016578 | -0.034174 | 0.036265 | 0.081005 | -0.071874 | 59.9346 | 59.9747 | 59.9209 | 59.8973 | 61.5011 | 61.5341 | 61.2666 | 61.4313 | 61.6361 | 61.4967 | 61.4748 | 61.4572 | 61.5277 | 61.5724 | 61.4195 | 59.9804 | 60.0205 | 59.9667 | 59.943 | 61.5468 | 61.5799 | 61.3123 | 61.4771 | -1.5664 | -1.3319 | -1.5802 | -1.3457
839.4375 | 121.8796 | -61.4777 | 60.0357 | 0.14474 | 0.000689 | -0.012 | -0.029595 | 0.036265 | 0.081005 | -0.071874 | 59.9346 | 59.9656 | 59.9163 | 59.8973 | 61.5056 | 61.5341 | 61.2574 | 61.4268 | 61.6224 | 61.4783 | 61.4657 | 61.4481 | 61.5139 | 61.5587 | 61.4058 | 59.9804 | 60.0113 | 59.9621 | 59.943 | 61.5514 | 61.5799 | 61.3032 | 61.4725 | -1.571 | -1.3228 | -1.5893 | -1.3411
841.1875 | 121.8842 | -61.5372 | 59.9716 | 0.14932 | 0.005267 | -0.007421 | -0.034174 | 0.045421 | 0.076426 | -0.071874 | 59.9346 | 59.9656 | 59.9209 | 59.8927 | 61.5102 | 61.5387 | 61.2574 | 61.4359 | 61.6865 | 61.5424 | 61.5297 | 61.503 | 61.5826 | 61.6136 | 61.4653 | 59.9804 | 60.0113 | 59.9667 | 59.9385 | 61.556 | 61.5845 | 61.3032 | 61.4817 | -1.5756 | -1.3228 | -1.5893 | -1.3365
842.9375 | 121.7285 | -61.5189 | 60.1181 | 0.14932 | 0.005267 | -0.007421 | -0.025017 | 0.040843 | 0.071848 | -0.076452 | 59.9346 | 59.9701 | 59.9209 | 59.8881 | 61.5011 | 61.5295 | 61.2666 | 61.4405 | 61.6682 | 61.5241 | 61.5114 | 61.4938 | 61.5597 | 61.5907 | 61.4424 | 59.9804 | 60.0159 | 59.9667 | 59.9339 | 61.5468 | 61.5753 | 61.3123 | 61.4863 | -1.5664 | -1.3319 | -1.5802 | -1.3457
844.6875 | 121.788 | -61.496 | 60.1089 | 0.14932 | 0.005267 | -0.007421 | -0.034174 | 0.036265 | 0.071848 | -0.067295 | 59.9392 | 59.9701 | 59.9209 | 59.8927 | 61.5011 | 61.5387 | 61.2711 | 61.4359 | 61.6453 | 61.5012 | 61.4886 | 61.4618 | 61.5322 | 61.5678 | 61.4287 | 59.985 | 60.0159 | 59.9667 | 59.9385 | 61.5468 | 61.5845 | 61.3169 | 61.4817 | -1.5618 | -1.3319 | -1.5802 | -1.3502
846.375 | 121.7468 | -61.5692 | 60.0449 | 0.14932 | 0.009846 | -0.012 | -0.029595 | 0.036265 | 0.081005 | -0.071874 | 59.9392 | 59.9701 | 59.9255 | 59.8835 | 61.5056 | 61.5387 | 61.2574 | 61.4405 | 61.7185 | 61.5791 | 61.5572 | 61.5396 | 61.6055 | 61.6502 | 61.4973 | 59.985 | 60.0159 | 59.9712 | 59.9293 | 61.5514 | 61.5845 | 61.3032 | 61.4863 | -1.5664 | -1.3182 | -1.5802 | -1.3319
848.125 | 121.8613 | -61.5372 | 59.9854 | 0.14932 | 0.005267 | -0.007421 | -0.034174 | 0.040843 | 0.076426 | -0.071874 | 59.9438 | 59.9656 | 59.9209 | 59.8927 | 61.5011 | 61.5295 | 61.262 | 61.4313 | 61.6865 | 61.5424 | 61.5297 | 61.503 | 61.578 | 61.6136 | 61.4653 | 59.9896 | 60.0113 | 59.9667 | 59.9385 | 61.5468 | 61.5753 | 61.3077 | 61.4771 | -1.5573 | -1.3182 | -1.5802 | -1.3411
849.8281 | 121.7422 | -61.5005 | 60.1089 | 0.14932 | 0.000689 | -0.007421 | -0.029595 | 0.036265 | 0.076426 | -0.067295 | 59.9346 | 59.9701 | 59.9209 | 59.8881 | 61.5056 | 61.5387 | 61.2574 | 61.4359 | 61.6499 | 61.5012 | 61.4931 | 61.471 | 61.5368 | 61.577 | 61.4333 | 59.9804 | 60.0159 | 59.9667 | 59.9339 | 61.5514 | 61.5845 | 61.3032 | 61.4817 | -1.571 | -1.3228 | -1.5847 | -1.3365
851.5781 | 121.7651 | -61.5051 | 60.0998 | 0.14474 | -0.00389 | -0.002842 | -0.025017 | 0.036265 | 0.081005 | -0.071874 | 59.9392 | 59.9656 | 59.9209 | 59.8973 | 61.5102 | 61.5341 | 61.262 | 61.4405 | 61.6499 | 61.5012 | 61.5023 | 61.4801 | 61.5414 | 61.5861 | 61.4333 | 59.985 | 60.0113 | 59.9667 | 59.943 | 61.556 | 61.5799 | 61.3077 | 61.4863 | -1.571 | -1.3228 | -1.5893 | -1.3411
853.2656 | 121.875 | -61.4594 | 60.0632 | 0.14474 | 0.000689 | -0.002842 | -0.034174 | 0.036265 | 0.081005 | -0.076452 | 59.9438 | 59.9747 | 59.9209 | 59.8835 | 61.5056 | 61.5295 | 61.2666 | 61.4405 | 61.6041 | 61.46 | 61.4565 | 61.4252 | 61.4956 | 61.5404 | 61.3829 | 59.9896 | 60.0205 | 59.9667 | 59.9293 | 61.5514 | 61.5753 | 61.3123 | 61.4863 | -1.5618 | -1.3228 | -1.5847 | -1.3457
855.0312 | 121.8155 | -61.5326 | 60.0082 | 0.14474 | -0.00389 | -0.012 | -0.025017 | 0.031687 | 0.076426 | -0.071874 | 59.9392 | 59.9747 | 59.9163 | 59.8927 | 61.4965 | 61.5341 | 61.262 | 61.4359 | 61.6773 | 61.5287 | 61.5206 | 61.5076 | 61.5643 | 61.609 | 61.4607 | 59.985 | 60.0205 | 59.9621 | 59.9385 | 61.5423 | 61.5799 | 61.3077 | 61.4817 | -1.5573 | -1.3228 | -1.5802 | -1.3457
856.7969 | 121.8384 | -61.5143 | 60.0128 | 0.14474 | 0.000689 | -0.007421 | -0.034174 | 0.036265 | 0.076426 | -0.067295 | 59.9392 | 59.9701 | 59.9163 | 59.8927 | 61.4919 | 61.5341 | 61.2574 | 61.4313 | 61.659 | 61.515 | 61.5069 | 61.4801 | 61.5505 | 61.5907 | 61.447 | 59.985 | 60.0159 | 59.9621 | 59.9385 | 61.5377 | 61.5799 | 61.3032 | 61.4771 | -1.5527 | -1.3182 | -1.5756 | -1.3411
858.5 | 121.7468 | -61.5646 | 60.0266 | 0.14474 | 0.000689 | -0.007421 | -0.034174 | 0.036265 | 0.081005 | -0.076452 | 59.9438 | 59.9701 | 59.9301 | 59.8927 | 61.5011 | 61.5341 | 61.2528 | 61.4359 | 61.7094 | 61.5653 | 61.5572 | 61.5305 | 61.6009 | 61.6456 | 61.4882 | 59.9896 | 60.0159 | 59.9758 | 59.9385 | 61.5468 | 61.5799 | 61.2986 | 61.4817 | -1.5573 | -1.309 | -1.571 | -1.3228
860.25 | 121.7789 | -61.4731 | 60.1044 | 0.14932 | 0.005267 | -0.012 | -0.029595 | 0.040843 | 0.090161 | -0.071874 | 59.9438 | 59.9747 | 59.9255 | 59.9018 | 61.5011 | 61.5341 | 61.2574 | 61.4359 | 61.6224 | 61.4784 | 61.4611 | 61.4435 | 61.5139 | 61.5632 | 61.4012 | 59.9896 | 60.0205 | 59.9712 | 59.9476 | 61.5468 | 61.5799 | 61.3032 | 61.4817 | -1.5573 | -1.3136 | -1.5756 | -1.3319
861.9531 | 121.7606 | -61.496 | 60.0815 | 0.14474 | 0.000689 | -0.007421 | -0.029595 | 0.031687 | 0.076426 | -0.076452 | 59.9438 | 59.9747 | 59.9301 | 59.8927 | 61.4965 | 61.5295 | 61.2574 | 61.4313 | 61.6407 | 61.4967 | 61.4886 | 61.4664 | 61.5277 | 61.5724 | 61.4195 | 59.9896 | 60.0205 | 59.9758 | 59.9385 | 61.5423 | 61.5753 | 61.3032 | 61.4771 | -1.5527 | -1.3136 | -1.5664 | -1.3273
863.7188 | 121.7148 | -61.5509 | 60.0357 | 0.14474 | 0.000689 | -0.012 | -0.029595 | 0.040843 | 0.085583 | -0.067295 | 59.9438 | 59.9793 | 59.9301 | 59.9064 | 61.4965 | 61.525 | 61.2574 | 61.4313 | 61.6956 | 61.5516 | 61.5389 | 61.5213 | 61.5917 | 61.6365 | 61.4836 | 59.9896 | 60.0251 | 59.9758 | 59.9522 | 61.5423 | 61.5707 | 61.3032 | 61.4771 | -1.5527 | -1.3136 | -1.5664 | -1.3273
865.4688 | 121.7422 | -61.496 | 60.1547 | 0.14474 | 0.000689 | -0.012 | -0.029595 | 0.036265 | 0.085583 | -0.067295 | 59.9438 | 59.9701 | 59.9255 | 59.8927 | 61.4965 | 61.5295 | 61.2574 | 61.4359 | 61.6407 | 61.4967 | 61.484 | 61.4664 | 61.5322 | 61.5816 | 61.4287 | 59.9896 | 60.0159 | 59.9712 | 59.9385 | 61.5423 | 61.5753 | 61.3032 | 61.4817 | -1.5527 | -1.3136 | -1.571 | -1.3319
867.1719 | 121.8292 | -61.4594 | 60.0906 | 0.14932 | 0.005267 | -0.021157 | -0.029595 | 0.045421 | 0.071848 | -0.067295 | 59.9484 | 59.9747 | 59.9209 | 59.8973 | 61.4965 | 61.5341 | 61.2574 | 61.4222 | 61.6087 | 61.4646 | 61.4382 | 61.4298 | 61.5048 | 61.5312 | 61.3921 | 59.9941 | 60.0205 | 59.9667 | 59.943 | 61.5423 | 61.5799 | 61.3032 | 61.468 | -1.5481 | -1.309 | -1.5756 | -1.3365
868.9375 | 121.788 | -61.5097 | 60.1181 | 0.14474 | 0.005267 | -0.007421 | -0.029595 | 0.040843 | 0.076426 | -0.071874 | 59.9484 | 59.9701 | 59.9301 | 59.8927 | 61.4919 | 61.5295 | 61.262 | 61.4313 | 61.6544 | 61.515 | 61.5023 | 61.4801 | 61.5505 | 61.5861 | 61.4378 | 59.9941 | 60.0159 | 59.9758 | 59.9385 | 61.5377 | 61.5753 | 61.3077 | 61.4771 | -1.5435 | -1.3136 | -1.5618 | -1.3319
870.6406 | 121.7422 | -61.5875 | 60.0494 | 0.14474 | 0.005267 | -0.012 | -0.029595 | 0.040843 | 0.081005 | -0.067295 | 59.9392 | 59.9701 | 59.9255 | 59.8973 | 61.4965 | 61.5341 | 61.2574 | 61.4268 | 61.7323 | 61.5928 | 61.5755 | 61.5579 | 61.6284 | 61.6685 | 61.5202 | 59.985 | 60.0159 | 59.9712 | 59.943 | 61.5423 | 61.5799 | 61.3032 | 61.4725 | -1.5573 | -1.3182 | -1.571 | -1.3319
872.3906 | 121.8521 | -61.4731 | 60.0815 | 0.14474 | 0.000689 | -0.012 | -0.029595 | 0.040843 | 0.081005 | -0.067295 | 59.9346 | 59.9701 | 59.9209 | 59.8973 | 61.4919 | 61.525 | 61.2528 | 61.4268 | 61.6178 | 61.4738 | 61.4611 | 61.4435 | 61.5139 | 61.5541 | 61.4058 | 59.9804 | 60.0159 | 59.9667 | 59.943 | 61.5377 | 61.5707 | 61.2986 | 61.4725 | -1.5573 | -1.3182 | -1.571 | -1.3319
874.0781 | 121.7422 | -61.5097 | 60.1089 | 0.14474 | 0.005267 | -0.012 | -0.025017 | 0.036265 | 0.081005 | -0.071874 | 59.9438 | 59.9747 | 59.9301 | 59.9018 | 61.4965 | 61.525 | 61.262 | 61.4268 | 61.6544 | 61.515 | 61.4977 | 61.4847 | 61.546 | 61.5907 | 61.4378 | 59.9896 | 60.0205 | 59.9758 | 59.9476 | 61.5423 | 61.5707 | 61.3077 | 61.4725 | -1.5527 | -1.3182 | -1.5664 | -1.3319
875.8281 | 121.8658 | -61.5463 | 59.967 | 0.14932 | 0.005267 | -0.012 | -0.029595 | 0.040843 | 0.081005 | -0.076452 | 59.9529 | 59.9793 | 59.9301 | 59.9018 | 61.4919 | 61.525 | 61.2574 | 61.4313 | 61.6956 | 61.5516 | 61.5343 | 61.5167 | 61.5872 | 61.6273 | 61.4699 | 59.9987 | 60.0251 | 59.9758 | 59.9476 | 61.5377 | 61.5707 | 61.3032 | 61.4771 | -1.539 | -1.3045 | -1.5618 | -1.3273
877.5781 | 121.8796 | -61.4639 | 60.054 | 0.14017 | 0.005267 | -0.016578 | -0.025017 | 0.040843 | 0.081005 | -0.071874 | 59.9484 | 59.9747 | 59.9301 | 59.8927 | 61.5011 | 61.5295 | 61.2528 | 61.4222 | 61.6041 | 61.4692 | 61.4474 | 61.4389 | 61.5048 | 61.5449 | 61.3921 | 59.9941 | 60.0205 | 59.9758 | 59.9385 | 61.5468 | 61.5753 | 61.2986 | 61.468 | -1.5527 | -1.3045 | -1.571 | -1.3228
879.3281 | 121.7422 | -61.5005 | 60.1181 | 0.14474 | 0.000689 | -0.021157 | -0.020438 | 0.036265 | 0.081005 | -0.076452 | 59.9484 | 59.9747 | 59.9346 | 59.9018 | 61.4919 | 61.525 | 61.262 | 61.4313 | 61.6453 | 61.5012 | 61.4794 | 61.4801 | 61.5368 | 61.5816 | 61.4241 | 59.9941 | 60.0205 | 59.9804 | 59.9476 | 61.5377 | 61.5707 | 61.3077 | 61.4771 | -1.5435 | -1.3136 | -1.5573 | -1.3273
881.0781 | 121.875 | -61.4777 | 60.054 | 0.14474 | -0.008469 | -0.021157 | -0.029595 | 0.036265 | 0.076426 | -0.076452 | 59.9484 | 59.9793 | 59.9346 | 59.8927 | 61.4873 | 61.525 | 61.2528 | 61.4313 | 61.6224 | 61.4692 | 61.4565 | 61.4481 | 61.5139 | 61.5541 | 61.4012 | 59.9941 | 60.0251 | 59.9804 | 59.9385 | 61.5331 | 61.5707 | 61.2986 | 61.4771 | -1.539 | -1.3045 | -1.5527 | -1.3182
882.8281 | 121.8338 | -61.4868 | 60.0266 | 0.14017 | -0.008469 | -0.016578 | -0.029595 | 0.036265 | 0.081005 | -0.071874 | 59.9392 | 59.9747 | 59.9255 | 59.8973 | 61.4965 | 61.525 | 61.2528 | 61.4268 | 61.627 | 61.4783 | 61.4702 | 61.4572 | 61.5231 | 61.5678 | 61.4149 | 59.985 | 60.0205 | 59.9712 | 59.943 | 61.5423 | 61.5707 | 61.2986 | 61.4725 | -1.5573 | -1.3136 | -1.571 | -1.3273
884.5156 | 121.756 | -61.5326 | 60.0494 | 0.14474 | 0.000689 | -0.007421 | -0.025017 | 0.040843 | 0.081005 | -0.071874 | 59.9529 | 59.9839 | 59.9346 | 59.9064 | 61.5011 | 61.5204 | 61.2528 | 61.4268 | 61.6773 | 61.5333 | 61.5252 | 61.5076 | 61.5734 | 61.6136 | 61.4607 | 59.9987 | 60.0297 | 59.9804 | 59.9522 | 61.5468 | 61.5662 | 61.2986 | 61.4725 | -1.5481 | -1.2999 | -1.5664 | -1.3182
886.2656 | 121.7926 | -61.5326 | 60.0586 | 0.14932 | 0.000689 | -0.012 | -0.020438 | 0.045421 | 0.085583 | -0.067295 | 59.9529 | 59.9793 | 59.9255 | 59.8973 | 61.4873 | 61.5204 | 61.2482 | 61.4268 | 61.6819 | 61.5333 | 61.5206 | 61.5122 | 61.578 | 61.6182 | 61.4653 | 59.9987 | 60.0251 | 59.9712 | 59.943 | 61.5331 | 61.5662 | 61.294 | 61.4725 | -1.5344 | -1.2953 | -1.5618 | -1.3228
888.0156 | 121.875 | -61.4868 | 60.0769 | 0.14932 | -0.00389 | -0.007421 | -0.029595 | 0.045421 | 0.085583 | -0.076452 | 59.9529 | 59.9793 | 59.9301 | 59.9064 | 61.4873 | 61.525 | 61.2574 | 61.4222 | 61.6361 | 61.4829 | 61.4794 | 61.4572 | 61.5322 | 61.5724 | 61.4104 | 59.9987 | 60.0251 | 59.9758 | 59.9522 | 61.5331 | 61.5707 | 61.3032 | 61.468 | -1.5344 | -1.3045 | -1.5573 | -1.3273
889.7812 | 121.7606 | -61.5189 | 60.0632 | 0.15848 | 0.000689 | -0.007421 | -0.025017 | 0.045421 | 0.081005 | -0.076452 | 59.9529 | 59.9885 | 59.9392 | 59.9018 | 61.4965 | 61.525 | 61.2391 | 61.4313 | 61.6773 | 61.5195 | 61.5114 | 61.4938 | 61.5643 | 61.5999 | 61.4424 | 59.9987 | 60.0342 | 59.985 | 59.9476 | 61.5423 | 61.5707 | 61.2849 | 61.4771 | -1.5435 | -1.2861 | -1.5573 | -1.2999
891.4688 | 121.7377 | -61.5738 | 60.054 | 0.14932 | -0.00389 | -0.007421 | -0.029595 | 0.045421 | 0.081005 | -0.071874 | 59.9575 | 59.9885 | 59.9392 | 59.911 | 61.4873 | 61.5204 | 61.2482 | 61.4176 | 61.7231 | 61.5699 | 61.5664 | 61.5442 | 61.6192 | 61.6548 | 61.5019 | 60.0033 | 60.0342 | 59.985 | 59.9568 | 61.5331 | 61.5662 | 61.294 | 61.4634 | -1.5298 | -1.2907 | -1.5481 | -1.309
893.2188 | 121.7606 | -61.4822 | 60.1181 | 0.13559 | -0.00389 | -0.016578 | -0.025017 | 0.040843 | 0.076426 | -0.071874 | 59.9575 | 59.993 | 59.9346 | 59.9064 | 61.4827 | 61.5204 | 61.2482 | 61.4268 | 61.6178 | 61.4783 | 61.4657 | 61.4572 | 61.5231 | 61.5587 | 61.4104 | 60.0033 | 60.0388 | 59.9804 | 59.9522 | 61.5285 | 61.5662 | 61.294 | 61.4725 | -1.5252 | -1.2907 | -1.5481 | -1.3136
894.9062 | 121.7468 | -61.5372 | 60.0677 | 0.1539 | 0.000689 | 0.001736 | -0.020438 | 0.045421 | 0.090161 | -0.062717 | 59.9529 | 59.9885 | 59.9392 | 59.911 | 61.4873 | 61.5158 | 61.2482 | 61.413 | 61.6911 | 61.5379 | 61.5389 | 61.5167 | 61.5826 | 61.6273 | 61.4745 | 59.9987 | 60.0342 | 59.985 | 59.9568 | 61.5331 | 61.5616 | 61.294 | 61.4588 | -1.5344 | -1.2953 | -1.5481 | -1.309
896.6562 | 121.8796 | -61.5417 | 59.9899 | 0.14932 | -0.00389 | -0.021157 | -0.025017 | 0.045421 | 0.085583 | -0.076452 | 59.9575 | 59.993 | 59.9438 | 59.9156 | 61.4736 | 61.5158 | 61.2437 | 61.4222 | 61.6911 | 61.5379 | 61.5206 | 61.5167 | 61.5872 | 61.6273 | 61.4653 | 60.0033 | 60.0388 | 59.9896 | 59.9614 | 61.5194 | 61.5616 | 61.2894 | 61.468 | -1.5161 | -1.2861 | -1.5298 | -1.2999
898.4062 | 121.7651 | -61.5051 | 60.1181 | 0.14932 | 0.005267 | -0.016578 | -0.025017 | 0.036265 | 0.085583 | -0.067295 | 59.9484 | 59.9839 | 59.9346 | 59.9018 | 61.4919 | 61.5204 | 61.2437 | 61.4222 | 61.6544 | 61.5104 | 61.4885 | 61.4801 | 61.5414 | 61.5907 | 61.4378 | 59.9941 | 60.0297 | 59.9804 | 59.9476 | 61.5377 | 61.5662 | 61.2894 | 61.468 | -1.5435 | -1.2953 | -1.5573 | -1.309
900.1719 | 121.7606 | -61.5509 | 60.0494 | 0.14474 | -0.00389 | -0.016578 | -0.029595 | 0.040843 | 0.081005 | -0.071874 | 59.9529 | 59.9976 | 59.9529 | 59.911 | 61.4827 | 61.5158 | 61.2345 | 61.413 | 61.6956 | 61.547 | 61.5343 | 61.5213 | 61.5917 | 61.6319 | 61.479 | 59.9987 | 60.0434 | 59.9987 | 59.9568 | 61.5285 | 61.5616 | 61.2803 | 61.4588 | -1.5298 | -1.2816 | -1.5298 | -1.2816
901.8594 | 121.7926 | -61.5234 | 60.0677 | 0.14474 | -0.008469 | -0.007421 | -0.034174 | 0.036265 | 0.081005 | -0.071874 | 59.9575 | 59.9839 | 59.9529 | 59.9064 | 61.4873 | 61.5112 | 61.2391 | 61.413 | 61.6682 | 61.515 | 61.516 | 61.4893 | 61.5597 | 61.6044 | 61.4516 | 60.0033 | 60.0297 | 59.9987 | 59.9522 | 61.5331 | 61.557 | 61.2849 | 61.4588 | -1.5298 | -1.2816 | -1.5344 | -1.2861
903.625 | 121.8887 | -61.4502 | 60.0632 | 0.1539 | -0.00389 | -0.016578 | -0.034174 | 0.036265 | 0.085583 | -0.071874 | 59.9621 | 59.993 | 59.9438 | 59.9156 | 61.4827 | 61.5112 | 61.2482 | 61.4222 | 61.6041 | 61.4463 | 61.4336 | 61.416 | 61.4865 | 61.5358 | 61.3783 | 60.0079 | 60.0388 | 59.9896 | 59.9614 | 61.5285 | 61.557 | 61.294 | 61.468 | -1.5206 | -1.2861 | -1.539 | -1.3045
905.3906 | 121.7743 | -61.4594 | 60.1318 | 0.14474 | -0.00389 | -0.012 | -0.029595 | 0.040843 | 0.076426 | -0.071874 | 59.9667 | 59.993 | 59.9484 | 59.9247 | 61.4827 | 61.5112 | 61.2391 | 61.4084 | 61.6041 | 61.4555 | 61.4474 | 61.4298 | 61.5002 | 61.5358 | 61.3875 | 60.0125 | 60.0388 | 59.9941 | 59.9705 | 61.5285 | 61.557 | 61.2849 | 61.4542 | -1.5161 | -1.2724 | -1.5344 | -1.2907
907.0781 | 121.8338 | -61.4502 | 60.1089 | 0.14474 | -0.008469 | -0.021157 | -0.025017 | 0.040843 | 0.085583 | -0.071874 | 59.9621 | 59.9976 | 59.9484 | 59.911 | 61.4782 | 61.5112 | 61.2391 | 61.413 | 61.5949 | 61.4417 | 61.429 | 61.4252 | 61.491 | 61.5358 | 61.3783 | 60.0079 | 60.0434 | 59.9941 | 59.9568 | 61.5239 | 61.557 | 61.2849 | 61.4588 | -1.5161 | -1.277 | -1.5298 | -1.2907
908.8594 | 121.8704 | -61.4319 | 60.0952 | 0.14474 | -0.00389 | -0.012 | -0.034174 | 0.045421 | 0.076426 | -0.076452 | 59.9575 | 59.9976 | 59.9438 | 59.9202 | 61.4782 | 61.5066 | 61.2391 | 61.4084 | 61.5766 | 61.428 | 61.4199 | 61.3977 | 61.4773 | 61.5083 | 61.3554 | 60.0033 | 60.0434 | 59.9896 | 59.9659 | 61.5239 | 61.5524 | 61.2849 | 61.4542 | -1.5206 | -1.2816 | -1.5344 | -1.2953
910.5625 | 121.7468 | -61.5326 | 60.0723 | 0.14932 | 0.000689 | -0.012 | -0.029595 | 0.040843 | 0.076426 | -0.071874 | 59.9713 | 59.993 | 59.9529 | 59.9156 | 61.4782 | 61.5021 | 61.2345 | 61.3993 | 61.6819 | 61.5333 | 61.5206 | 61.503 | 61.5734 | 61.609 | 61.4607 | 60.017 | 60.0388 | 59.9987 | 59.9614 | 61.5239 | 61.5478 | 61.2803 | 61.4451 | -1.5069 | -1.2632 | -1.5252 | -1.2816
912.3281 | 121.7834 | -61.4777 | 60.1044 | 0.14474 | 0.000689 | -0.012 | -0.025017 | 0.040843 | 0.090161 | -0.071874 | 59.9758 | 59.9976 | 59.9529 | 59.9247 | 61.4736 | 61.4975 | 61.2299 | 61.4084 | 61.6224 | 61.4783 | 61.4657 | 61.4526 | 61.5185 | 61.5678 | 61.4058 | 60.0216 | 60.0434 | 59.9987 | 59.9705 | 61.5194 | 61.5433 | 61.2757 | 61.4542 | -1.4978 | -1.2541 | -1.5206 | -1.277
914.0781 | 121.8292 | -61.4822 | 60.0723 | 0.14932 | -0.00389 | -0.012 | -0.038752 | 0.040843 | 0.085583 | -0.071874 | 59.9758 | 60.0114 | 59.9529 | 59.9247 | 61.469 | 61.4975 | 61.2299 | 61.3947 | 61.6316 | 61.4783 | 61.4702 | 61.4435 | 61.5231 | 61.5678 | 61.4104 | 60.0216 | 60.0571 | 59.9987 | 59.9705 | 61.5148 | 61.5433 | 61.2757 | 61.4405 | -1.4932 | -1.2541 | -1.5161 | -1.277
915.7812 | 121.7972 | -61.4777 | 60.0952 | 0.14474 | -0.00389 | -0.012 | -0.034174 | 0.036265 | 0.085583 | -0.071874 | 59.9667 | 60.0068 | 59.9575 | 59.9293 | 61.469 | 61.4975 | 61.2299 | 61.3947 | 61.6224 | 61.4738 | 61.4657 | 61.4435 | 61.5139 | 61.5632 | 61.4058 | 60.0125 | 60.0526 | 60.0033 | 59.9751 | 61.5148 | 61.5433 | 61.2757 | 61.4405 | -1.5023 | -1.2632 | -1.5115 | -1.2724
917.5312 | 121.7514 | -61.4685 | 60.141 | 0.14474 | -0.00389 | -0.012 | -0.025017 | 0.049999 | 0.090161 | -0.071874 | 59.985 | 60.0159 | 59.9713 | 59.9339 | 61.4507 | 61.4746 | 61.2116 | 61.3901 | 61.6132 | 61.4646 | 61.4565 | 61.4435 | 61.5185 | 61.5587 | 61.3966 | 60.0308 | 60.0617 | 60.017 | 59.9797 | 61.4965 | 61.5204 | 61.2574 | 61.4359 | -1.4657 | -1.2266 | -1.4794 | -1.2404
919.2188 | 121.756 | -61.4456 | 60.1547 | 0.14932 | -0.00389 | -0.021157 | -0.034174 | 0.040843 | 0.085583 | -0.076452 | 59.9987 | 60.0297 | 59.9804 | 59.9385 | 61.4461 | 61.4792 | 61.2116 | 61.381 | 61.5949 | 61.4417 | 61.4245 | 61.4114 | 61.4865 | 61.5312 | 61.3692 | 60.0445 | 60.0754 | 60.0262 | 59.9843 | 61.4919 | 61.525 | 61.2574 | 61.4268 | -1.4474 | -1.2129 | -1.4657 | -1.2312
920.9688 | 121.7789 | -61.4868 | 60.0952 | 0.14474 | -0.008469 | -0.002842 | -0.029595 | 0.040843 | 0.09474 | -0.071874 | 60.0033 | 60.0251 | 59.9896 | 59.9568 | 61.4415 | 61.47 | 61.1933 | 61.3764 | 61.6316 | 61.4783 | 61.484 | 61.4572 | 61.5277 | 61.5816 | 61.4149 | 60.0491 | 60.0709 | 60.0353 | 60.0026 | 61.4873 | 61.5158 | 61.2391 | 61.4222 | -1.4382 | -1.19 | -1.452 | -1.2037
922.7188 | 121.8155 | -61.4548 | 60.1273 | 0.14474 | 0.000689 | -0.012 | -0.038752 | 0.040843 | 0.085583 | -0.067295 | 60.017 | 60.0526 | 59.9896 | 59.9522 | 61.4324 | 61.47 | 61.1887 | 61.3672 | 61.5995 | 61.4555 | 61.4428 | 61.416 | 61.4956 | 61.5404 | 61.3875 | 60.0628 | 60.0983 | 60.0353 | 59.998 | 61.4782 | 61.5158 | 61.2345 | 61.413 | -1.4153 | -1.1717 | -1.4428 | -1.1991
924.4062 | 121.875 | -61.4685 | 60.0311 | 0.14017 | 0.005267 | -0.012 | -0.025017 | 0.040843 | 0.085583 | -0.071874 | 60.017 | 60.048 | 59.9941 | 59.9705 | 61.4278 | 61.4563 | 61.1841 | 61.3627 | 61.6087 | 61.4738 | 61.4565 | 61.4435 | 61.5093 | 61.5541 | 61.3966 | 60.0628 | 60.0938 | 60.0399 | 60.0163 | 61.4736 | 61.5021 | 61.2299 | 61.4084 | -1.4108 | -1.1671 | -1.4337 | -1.19
926.1562 | 121.7743 | -61.4639 | 60.141 | 0.14474 | -0.00389 | -0.007421 | -0.029595 | 0.040843 | 0.090161 | -0.071874 | 60.0262 | 60.0526 | 60.0079 | 59.9751 | 61.4186 | 61.4517 | 61.1841 | 61.3489 | 61.6087 | 61.46 | 61.4565 | 61.4343 | 61.5048 | 61.5541 | 61.3921 | 60.072 | 60.0983 | 60.0537 | 60.0209 | 61.4644 | 61.4975 | 61.2299 | 61.3947 | -1.3925 | -1.1579 | -1.4108 | -1.1763
927.9062 | 121.8933 | -61.4227 | 60.1181 | 0.14474 | 0.000689 | -0.007421 | -0.029595 | 0.036265 | 0.081005 | -0.076452 | 60.0216 | 60.0617 | 60.0125 | 59.9797 | 61.4095 | 61.4471 | 61.1841 | 61.3489 | 61.5675 | 61.4234 | 61.4153 | 61.3931 | 61.459 | 61.5037 | 61.3463 | 60.0674 | 60.1075 | 60.0582 | 60.0255 | 61.4553 | 61.4929 | 61.2299 | 61.3947 | -1.3879 | -1.1625 | -1.397 | -1.1717
929.6562 | 121.8338 | -61.4273 | 60.141 | 0.14474 | 0.005267 | -0.012 | -0.034174 | 0.040843 | 0.090161 | -0.071874 | 60.0354 | 60.0663 | 60.0216 | 59.9797 | 61.4049 | 61.4426 | 61.1704 | 61.3443 | 61.572 | 61.4326 | 61.4153 | 61.3931 | 61.4682 | 61.5175 | 61.3554 | 60.0811 | 60.1121 | 60.0674 | 60.0255 | 61.4507 | 61.4883 | 61.2162 | 61.3901 | -1.3696 | -1.1351 | -1.3833 | -1.1488
931.3594 | 121.7422 | -61.3953 | 60.2005 | 0.14017 | -0.00389 | -0.016578 | -0.029595 | 0.036265 | 0.085583 | -0.076452 | 60.0399 | 60.0709 | 60.0262 | 59.9934 | 61.4095 | 61.4334 | 61.1567 | 61.3398 | 61.5354 | 61.3914 | 61.3787 | 61.3657 | 61.4315 | 61.4808 | 61.3188 | 60.0857 | 60.1167 | 60.072 | 60.0392 | 61.4553 | 61.4792 | 61.2024 | 61.3855 | -1.3696 | -1.1167 | -1.3833 | -1.1305
933.1094 | 121.8704 | -61.4548 | 60.0815 | 0.14474 | -0.008469 | -0.012 | -0.029595 | 0.036265 | 0.076426 | -0.071874 | 60.0445 | 60.08 | 60.0308 | 60.0026 | 61.4003 | 61.4334 | 61.1567 | 61.326 | 61.5995 | 61.4463 | 61.4428 | 61.4252 | 61.491 | 61.5312 | 61.3829 | 60.0903 | 60.1258 | 60.0765 | 60.0484 | 61.4461 | 61.4792 | 61.2024 | 61.3718 | -1.3558 | -1.1122 | -1.3696 | -1.1259
934.7969 | 121.8658 | -61.3998 | 60.1318 | 0.14017 | -0.00389 | -0.007421 | -0.025017 | 0.036265 | 0.085583 | -0.076452 | 60.0399 | 60.0892 | 60.0308 | 60.0026 | 61.3912 | 61.4197 | 61.1475 | 61.3306 | 61.54 | 61.396 | 61.3924 | 61.3748 | 61.4361 | 61.4854 | 61.3234 | 60.0857 | 60.135 | 60.0765 | 60.0484 | 61.437 | 61.4654 | 61.1933 | 61.3764 | -1.3512 | -1.1076 | -1.3604 | -1.1167
936.5625 | 121.7651 | -61.409 | 60.2051 | 0.14474 | -0.00389 | -0.012 | -0.029595 | 0.040843 | 0.085583 | -0.067295 | 60.0491 | 60.0846 | 60.0445 | 60.0026 | 61.382 | 61.4197 | 61.1567 | 61.3215 | 61.5537 | 61.4051 | 61.397 | 61.3794 | 61.4498 | 61.4946 | 61.3417 | 60.0949 | 60.1304 | 60.0903 | 60.0484 | 61.4278 | 61.4654 | 61.2024 | 61.3672 | -1.3329 | -1.1076 | -1.3375 | -1.1122
938.3281 | 121.7514 | -61.3953 | 60.2234 | 0.14017 | 0.000689 | -0.007421 | -0.029595 | 0.036265 | 0.085583 | -0.067295 | 60.0537 | 60.0938 | 60.0491 | 60.0026 | 61.382 | 61.4151 | 61.1475 | 61.3169 | 61.5354 | 61.396 | 61.3878 | 61.3657 | 61.4315 | 61.4808 | 61.328 | 60.0994 | 60.1395 | 60.0949 | 60.0484 | 61.4278 | 61.4609 | 61.1933 | 61.3627 | -1.3284 | -1.0938 | -1.3329 | -1.0984
940.0312 | 121.7377 | -61.377 | 60.2051 | 0.13559 | -0.00389 | -0.012 | -0.029595 | 0.036265 | 0.085583 | -0.076452 | 60.0582 | 60.0846 | 60.0445 | 60.0072 | 61.3866 | 61.4151 | 61.1429 | 61.3123 | 61.5125 | 61.3731 | 61.365 | 61.3474 | 61.4132 | 61.4625 | 61.3005 | 60.104 | 60.1304 | 60.0903 | 60.0529 | 61.4324 | 61.4609 | 61.1887 | 61.3581 | -1.3284 | -1.0847 | -1.3421 | -1.0984
941.7812 | 121.8567 | -61.377 | 60.1547 | 0.14017 | -0.008469 | -0.012 | -0.025017 | 0.031687 | 0.081005 | -0.08103 | 60.0582 | 60.0892 | 60.0491 | 60.0209 | 61.382 | 61.4151 | 61.1429 | 61.3123 | 61.5171 | 61.3685 | 61.365 | 61.3519 | 61.4086 | 61.458 | 61.2959 | 60.104 | 60.135 | 60.0949 | 60.0667 | 61.4278 | 61.4609 | 61.1887 | 61.3581 | -1.3238 | -1.0847 | -1.3329 | -1.0938
943.5312 | 121.8109 | -61.4227 | 60.1181 | 0.14474 | -0.008469 | -0.012 | -0.029595 | 0.040843 | 0.085583 | -0.076452 | 60.0674 | 60.0892 | 60.0445 | 60.0117 | 61.3866 | 61.4151 | 61.1384 | 61.3123 | 61.5675 | 61.4143 | 61.4107 | 61.3931 | 61.4636 | 61.5083 | 61.3463 | 60.1132 | 60.135 | 60.0903 | 60.0575 | 61.4324 | 61.4609 | 61.1841 | 61.3581 | -1.3192 | -1.071 | -1.3421 | -1.0938
945.2812 | 121.8338 | -61.3998 | 60.141 | 0.1539 | 0.000689 | -0.012 | -0.029595 | 0.036265 | 0.081005 | -0.08103 | 60.0582 | 60.0892 | 60.0399 | 60.0117 | 61.3729 | 61.4197 | 61.1429 | 61.326 | 61.5537 | 61.4005 | 61.3878 | 61.3702 | 61.4361 | 61.4808 | 61.3188 | 60.104 | 60.135 | 60.0857 | 60.0575 | 61.4186 | 61.4654 | 61.1887 | 61.3718 | -1.3146 | -1.0847 | -1.3329 | -1.103
947.0312 | 121.788 | -61.409 | 60.1959 | 0.14017 | 0.000689 | -0.007421 | -0.025017 | 0.031687 | 0.081005 | -0.076452 | 60.0537 | 60.0846 | 60.0354 | 60.0026 | 61.3912 | 61.4197 | 61.1429 | 61.3215 | 61.5492 | 61.4097 | 61.4016 | 61.384 | 61.4407 | 61.49 | 61.3325 | 60.0994 | 60.1304 | 60.0811 | 60.0484 | 61.437 | 61.4654 | 61.1887 | 61.3672 | -1.3375 | -1.0893 | -1.3558 | -1.1076
948.7344 | 121.7789 | -61.409 | 60.173 | 0.1539 | -0.00389 | -0.012 | -0.025017 | 0.040843 | 0.090161 | -0.071874 | 60.0537 | 60.0846 | 60.0262 | 59.998 | 61.3958 | 61.4242 | 61.1475 | 61.326 | 61.5629 | 61.4051 | 61.397 | 61.384 | 61.4498 | 61.4992 | 61.3371 | 60.0994 | 60.1304 | 60.072 | 60.0438 | 61.4415 | 61.47 | 61.1933 | 61.3718 | -1.3421 | -1.0938 | -1.3696 | -1.1213
950.5 | 121.8292 | -61.377 | 60.1501 | 0.14474 | -0.008469 | -0.012 | -0.029595 | 0.040843 | 0.09474 | -0.076452 | 60.0491 | 60.0755 | 60.0262 | 59.9934 | 61.4003 | 61.438 | 61.1475 | 61.3306 | 61.5217 | 61.3685 | 61.365 | 61.3474 | 61.4178 | 61.4717 | 61.3005 | 60.0949 | 60.1212 | 60.072 | 60.0392 | 61.4461 | 61.4837 | 61.1933 | 61.3764 | -1.3512 | -1.0984 | -1.3741 | -1.1213
952.25 | 121.8521 | -61.4456 | 60.0769 | 0.14474 | -0.00389 | -0.012 | -0.029595 | 0.045421 | 0.081005 | -0.071874 | 60.0537 | 60.08 | 60.0399 | 59.998 | 61.3866 | 61.4242 | 61.1521 | 61.3352 | 61.5904 | 61.4417 | 61.4336 | 61.416 | 61.491 | 61.5266 | 61.3737 | 60.0994 | 60.1258 | 60.0857 | 60.0438 | 61.4324 | 61.47 | 61.1979 | 61.381 | -1.3329 | -1.0984 | -1.3467 | -1.1122
953.9375 | 121.8338 | -61.3953 | 60.1456 | 0.14932 | 0.005267 | -0.016578 | -0.029595 | 0.045421 | 0.081005 | -0.076452 | 60.0491 | 60.0755 | 60.0354 | 59.998 | 61.3912 | 61.4334 | 61.1521 | 61.326 | 61.5446 | 61.4005 | 61.3787 | 61.3657 | 61.4407 | 61.4763 | 61.3188 | 60.0949 | 60.1212 | 60.0811 | 60.0438 | 61.437 | 61.4792 | 61.1979 | 61.3718 | -1.3421 | -1.103 | -1.3558 | -1.1167
955.6875 | 121.7422 | -61.4548 | 60.1181 | 0.14474 | 0.000689 | -0.012 | -0.025017 | 0.036265 | 0.090161 | -0.071874 | 60.0491 | 60.0892 | 60.0354 | 59.998 | 61.4003 | 61.4242 | 61.1521 | 61.326 | 61.5995 | 61.4555 | 61.4428 | 61.4298 | 61.491 | 61.5449 | 61.3829 | 60.0949 | 60.135 | 60.0811 | 60.0438 | 61.4461 | 61.47 | 61.1979 | 61.3718 | -1.3512 | -1.103 | -1.365 | -1.1167
957.4375 | 121.7789 | -61.377 | 60.1822 | 0.14017 | 0.005267 | -0.016578 | -0.029595 | 0.036265 | 0.085583 | -0.08103 | 60.0491 | 60.0709 | 60.0262 | 59.9843 | 61.3958 | 61.4288 | 61.1658 | 61.3352 | 61.5171 | 61.3822 | 61.3604 | 61.3474 | 61.4132 | 61.4625 | 61.2959 | 60.0949 | 60.1167 | 60.072 | 60.03 | 61.4415 | 61.4746 | 61.2116 | 61.381 | -1.3467 | -1.1167 | -1.3696 | -1.1396
959.1875 | 121.8018 | -61.441 | 60.1639 | 0.13559 | -0.00389 | -0.012 | -0.034174 | 0.036265 | 0.085583 | -0.067295 | 60.0354 | 60.0709 | 60.0079 | 59.9705 | 61.4141 | 61.4426 | 61.1796 | 61.3581 | 61.5766 | 61.4372 | 61.429 | 61.4069 | 61.4773 | 61.5266 | 61.3737 | 60.0811 | 60.1167 | 60.0537 | 60.0163 | 61.4598 | 61.4883 | 61.2253 | 61.4039 | -1.3787 | -1.1442 | -1.4062 | -1.1717
960.8906 | 121.7468 | -61.5051 | 60.1273 | 0.14932 | 0.000689 | -0.016578 | -0.029595 | 0.040843 | 0.085583 | -0.076452 | 60.0262 | 60.0617 | 60.0079 | 59.9705 | 61.4186 | 61.4471 | 61.175 | 61.3535 | 61.6544 | 61.5058 | 61.4885 | 61.4755 | 61.546 | 61.5907 | 61.4287 | 60.072 | 60.1075 | 60.0537 | 60.0163 | 61.4644 | 61.4929 | 61.2208 | 61.3993 | -1.3925 | -1.1488 | -1.4108 | -1.1671
962.6562 | 121.8201 | -61.4456 | 60.1089 | 0.14932 | 0.005267 | -0.016578 | -0.029595 | 0.040843 | 0.081005 | -0.071874 | 60.0262 | 60.0571 | 60.0033 | 59.966 | 61.4232 | 61.4517 | 61.1841 | 61.3489 | 61.5949 | 61.4509 | 61.429 | 61.416 | 61.4865 | 61.5266 | 61.3737 | 60.072 | 60.1029 | 60.0491 | 60.0117 | 61.469 | 61.4975 | 61.2299 | 61.3947 | -1.397 | -1.1579 | -1.4199 | -1.1808
964.3438 | 121.8246 | -61.441 | 60.0861 | 0.14932 | 0.000689 | -0.012 | -0.025017 | 0.040843 | 0.081005 | -0.071874 | 60.017 | 60.0434 | 59.9987 | 59.966 | 61.4232 | 61.4563 | 61.1796 | 61.3581 | 61.5904 | 61.4417 | 61.429 | 61.416 | 61.4819 | 61.522 | 61.3692 | 60.0628 | 60.0892 | 60.0445 | 60.0117 | 61.469 | 61.5021 | 61.2253 | 61.4039 | -1.4062 | -1.1625 | -1.4245 | -1.1808
966.0938 | 121.8658 | -61.4639 | 60.054 | 0.14932 | 0.000689 | -0.016578 | -0.029595 | 0.036265 | 0.085583 | -0.062717 | 60.0125 | 60.0526 | 59.9941 | 59.9568 | 61.437 | 61.4609 | 61.1887 | 61.3718 | 61.6132 | 61.4646 | 61.4474 | 61.4343 | 61.5002 | 61.5495 | 61.4012 | 60.0582 | 60.0983 | 60.0399 | 60.0026 | 61.4827 | 61.5066 | 61.2345 | 61.4176 | -1.4245 | -1.1763 | -1.4428 | -1.1946
967.8594 | 121.8292 | -61.409 | 60.1364 | 0.14474 | 0.005267 | -0.012 | -0.020438 | 0.036265 | 0.09474 | -0.067295 | 59.9804 | 60.0251 | 59.9758 | 59.9431 | 61.4553 | 61.4792 | 61.2162 | 61.3856 | 61.5537 | 61.4143 | 61.397 | 61.3886 | 61.4453 | 61.5037 | 61.3417 | 60.0262 | 60.0709 | 60.0216 | 59.9888 | 61.501 | 61.525 | 61.262 | 61.4313 | -1.4749 | -1.2358 | -1.4794 | -1.2404
969.5625 | 121.756 | -61.5051 | 60.1044 | 0.14474 | 0.000689 | -0.007421 | -0.034174 | 0.040843 | 0.085583 | -0.08103 | 59.9529 | 59.9839 | 59.9301 | 59.9064 | 61.4919 | 61.525 | 61.2528 | 61.4268 | 61.6499 | 61.5058 | 61.4977 | 61.471 | 61.546 | 61.5907 | 61.4241 | 59.9987 | 60.0297 | 59.9758 | 59.9522 | 61.5377 | 61.5707 | 61.2986 | 61.4725 | -1.539 | -1.2999 | -1.5618 | -1.3228
971.3281 | 121.7468 | -61.528 | 60.0952 | 0.14474 | 0.000689 | -0.016578 | -0.025017 | 0.040843 | 0.085583 | -0.067295 | 59.9209 | 59.9518 | 59.9072 | 59.8652 | 61.5285 | 61.557 | 61.2803 | 61.4542 | 61.6728 | 61.5287 | 61.5114 | 61.503 | 61.5689 | 61.6136 | 61.4607 | 59.9667 | 59.9976 | 59.9529 | 59.911 | 61.5743 | 61.6028 | 61.3261 | 61.5 | -1.6076 | -1.3594 | -1.6214 | -1.3731
973.0938 | 121.8979 | -61.528 | 60.0128 | 0.14474 | 0.000689 | -0.007421 | -0.029595 | 0.045421 | 0.090161 | -0.076452 | 59.9072 | 59.9381 | 59.8843 | 59.8515 | 61.5377 | 61.5707 | 61.294 | 61.4725 | 61.6728 | 61.5287 | 61.5206 | 61.4984 | 61.5734 | 61.6182 | 61.4516 | 59.9529 | 59.9839 | 59.93 | 59.8973 | 61.5835 | 61.6165 | 61.3398 | 61.5183 | -1.6305 | -1.3869 | -1.6534 | -1.4098
974.8594 | 121.8658 | -61.528 | 60.0082 | 0.14474 | 0.005267 | -0.021157 | -0.025017 | 0.040843 | 0.085583 | -0.076452 | 59.8934 | 59.9244 | 59.8751 | 59.8469 | 61.5606 | 61.5845 | 61.3215 | 61.4863 | 61.6728 | 61.5333 | 61.5069 | 61.503 | 61.5689 | 61.6136 | 61.4516 | 59.9392 | 59.9701 | 59.9209 | 59.8927 | 61.6063 | 61.6302 | 61.3673 | 61.532 | -1.6672 | -1.4281 | -1.6855 | -1.4464
976.5625 | 121.875 | -61.7294 | 59.8206 | 0.14932 | -0.00389 | -0.016578 | -0.034174 | 0.036265 | 0.090161 | -0.067295 | 59.7973 | 59.8328 | 59.7927 | 59.7553 | 61.643 | 61.6715 | 61.3993 | 61.5733 | 61.8788 | 61.7255 | 61.7129 | 61.6953 | 61.7657 | 61.8196 | 61.6621 | 59.843 | 59.8786 | 59.8385 | 59.8011 | 61.6888 | 61.7172 | 61.4451 | 61.619 | -1.8457 | -1.6021 | -1.8503 | -1.6066
978.3125 | 121.7651 | -61.9171 | 59.7107 | 0.14474 | 0.005267 | -0.012 | -0.029595 | 0.040843 | 0.085583 | -0.058139 | 59.6737 | 59.7046 | 59.6599 | 59.6225 | 61.7666 | 61.7905 | 61.5229 | 61.706 | 62.0619 | 61.9224 | 61.9051 | 61.8875 | 61.958 | 62.0027 | 61.859 | 59.7194 | 59.7504 | 59.7057 | 59.6683 | 61.8124 | 61.8363 | 61.5687 | 61.7518 | -2.0929 | -1.8493 | -2.1067 | -1.863
980 | 121.7834 | -61.6974 | 59.8846 | 0.1539 | 0.000689 | -0.007421 | -0.029595 | 0.045421 | 0.085583 | -0.067295 | 59.7149 | 59.7412 | 59.7011 | 59.6592 | 61.7391 | 61.763 | 61.4909 | 61.674 | 61.8513 | 61.6981 | 61.69 | 61.6678 | 61.7428 | 61.783 | 61.6301 | 59.7606 | 59.787 | 59.7469 | 59.7049 | 61.7849 | 61.8088 | 61.5367 | 61.7198 | -2.0243 | -1.776 | -2.038 | -1.7898
981.7656 | 121.875 | -61.7477 | 59.7656 | 0.14932 | 0.000689 | -0.012 | -0.034174 | 0.036265 | 0.085583 | -0.08103 | 59.7103 | 59.7412 | 59.7011 | 59.6592 | 61.7437 | 61.7676 | 61.4909 | 61.6694 | 61.8971 | 61.7484 | 61.7357 | 61.7136 | 61.784 | 61.8333 | 61.6667 | 59.7561 | 59.787 | 59.7469 | 59.7049 | 61.7895 | 61.8134 | 61.5367 | 61.7152 | -2.0334 | -1.7806 | -2.0426 | -1.7898
983.4531 | 121.8521 | -61.7569 | 59.7885 | 0.14474 | 0.000689 | -0.007421 | -0.029595 | 0.040843 | 0.081005 | -0.076452 | 59.7149 | 59.7366 | 59.6874 | 59.6637 | 61.73 | 61.763 | 61.4909 | 61.674 | 61.9016 | 61.7576 | 61.7495 | 61.7273 | 61.7977 | 61.8379 | 61.6804 | 59.7606 | 59.7824 | 59.7332 | 59.7095 | 61.7757 | 61.8088 | 61.5367 | 61.7198 | -2.0151 | -1.776 | -2.0426 | -1.8035
985.2031 | 121.7422 | -61.8301 | 59.7702 | 0.14017 | -0.00389 | -0.007421 | -0.034174 | 0.045421 | 0.081005 | -0.067295 | 59.692 | 59.7183 | 59.6782 | 59.6408 | 61.7574 | 61.7813 | 61.5092 | 61.6923 | 61.9703 | 61.8262 | 61.8227 | 61.796 | 61.8756 | 61.9111 | 61.7628 | 59.7377 | 59.7641 | 59.724 | 59.6866 | 61.8032 | 61.8271 | 61.555 | 61.7381 | -2.0655 | -1.8172 | -2.0792 | -1.831
986.9062 | 121.8155 | -61.8851 | 59.6649 | 0.14017 | -0.00389 | -0.012 | -0.029595 | 0.040843 | 0.081005 | -0.071874 | 59.6233 | 59.6634 | 59.6096 | 59.5813 | 61.8215 | 61.8408 | 61.5733 | 61.7472 | 62.0252 | 61.8812 | 61.8731 | 61.8555 | 61.9259 | 61.9661 | 61.8132 | 59.6691 | 59.7091 | 59.6553 | 59.6271 | 61.8673 | 61.8866 | 61.6191 | 61.793 | -2.1982 | -1.95 | -2.212 | -1.9637
988.6562 | 121.8201 | -61.9171 | 59.6191 | 0.14932 | 0.000689 | -0.012 | -0.034174 | 0.036265 | 0.081005 | -0.071874 | 59.4539 | 59.4802 | 59.4402 | 59.4073 | 61.9863 | 62.0148 | 61.7381 | 61.9304 | 62.0664 | 61.9178 | 61.9051 | 61.8829 | 61.9534 | 61.9981 | 61.8452 | 59.4997 | 59.526 | 59.486 | 59.4531 | 62.0321 | 62.0606 | 61.7839 | 61.9761 | -2.5325 | -2.2842 | -2.5462 | -2.2979
990.3594 | 121.8292 | -61.972 | 59.5642 | 0.14932 | 0.005267 | -0.007421 | -0.025017 | 0.036265 | 0.081005 | -0.071874 | 59.5271 | 59.5535 | 59.5134 | 59.476 | 61.9177 | 61.9507 | 61.6649 | 61.8525 | 62.1214 | 61.9773 | 61.9646 | 61.947 | 62.0083 | 62.0531 | 61.9002 | 59.5729 | 59.5992 | 59.5592 | 59.5218 | 61.9634 | 61.9965 | 61.7106 | 61.8983 | -2.3905 | -2.1377 | -2.4042 | -2.1514
992.125 | 121.843 | -61.8668 | 59.6924 | 0.14932 | -0.00389 | -0.016578 | -0.038752 | 0.040843 | 0.085583 | -0.071874 | 59.5821 | 59.6176 | 59.5638 | 59.5309 | 61.8627 | 61.8912 | 61.6145 | 61.793 | 62.0161 | 61.8629 | 61.8502 | 61.828 | 61.9076 | 61.9523 | 61.7949 | 59.6279 | 59.6634 | 59.6096 | 59.5767 | 61.9085 | 61.937 | 61.6603 | 61.8388 | -2.2806 | -2.0324 | -2.2989 | -2.0507
993.8906 | 121.788 | -61.9675 | 59.6008 | 0.14932 | 0.009846 | -0.007421 | -0.020438 | 0.040843 | 0.085583 | -0.071874 | 59.5638 | 59.5855 | 59.5363 | 59.4943 | 61.8994 | 61.9141 | 61.6374 | 61.8205 | 62.1168 | 61.9773 | 61.96 | 61.947 | 62.0083 | 62.0531 | 61.8956 | 59.6095 | 59.6313 | 59.5821 | 59.5401 | 61.9451 | 61.9599 | 61.6832 | 61.8663 | -2.3356 | -2.0736 | -2.363 | -2.1011
995.5781 | 121.7422 | -61.9675 | 59.6603 | 0.14017 | -0.00389 | -0.016578 | -0.025017 | 0.040843 | 0.081005 | -0.067295 | 59.5409 | 59.5764 | 59.5272 | 59.4897 | 61.9039 | 61.9324 | 61.6557 | 61.8342 | 62.1076 | 61.9636 | 61.9509 | 61.9425 | 62.0083 | 62.0485 | 61.9002 | 59.5867 | 59.6221 | 59.5729 | 59.5355 | 61.9497 | 61.9782 | 61.7015 | 61.88 | -2.3631 | -2.1148 | -2.3768 | -2.1286
997.3281 | 121.756 | -61.9949 | 59.6146 | 0.14474 | 0.000689 | -0.012 | -0.034174 | 0.031687 | 0.081005 | -0.067295 | 59.5042 | 59.5306 | 59.486 | 59.4531 | 61.9451 | 61.969 | 61.6878 | 61.8754 | 62.1397 | 61.9956 | 61.9829 | 61.9608 | 62.0266 | 62.0759 | 61.9276 | 59.55 | 59.5764 | 59.5317 | 59.4989 | 61.9909 | 62.0148 | 61.7335 | 61.9212 | -2.4409 | -2.1835 | -2.4592 | -2.2018
999.0781 | 121.7789 | -61.9812 | 59.61 | 0.14474 | 0.000689 | -0.007421 | -0.029595 | 0.036265 | 0.085583 | -0.085608 | 59.4539 | 59.4894 | 59.4356 | 59.4027 | 61.9955 | 62.0148 | 61.7427 | 61.9258 | 62.1259 | 61.9819 | 61.9738 | 61.9516 | 62.0175 | 62.0668 | 61.8956 | 59.4997 | 59.5351 | 59.4814 | 59.4485 | 62.0413 | 62.0606 | 61.7885 | 61.9716 | -2.5416 | -2.2888 | -2.5599 | -2.3071
1000.8281 | 121.8842 | -62.1002 | 59.4269 | 0.14932 | 0.009846 | -0.007421 | -0.029595 | 0.040843 | 0.081005 | -0.067295 | 59.3852 | 59.4115 | 59.3669 | 59.334 | 62.0642 | 62.0972 | 61.816 | 62.0036 | 62.2495 | 62.1101 | 62.0928 | 62.0706 | 62.1411 | 62.1812 | 62.0329 | 59.431 | 59.4573 | 59.4127 | 59.3798 | 62.1099 | 62.143 | 61.8617 | 62.0494 | -2.679 | -2.4307 | -2.6972 | -2.449
1002.5312 | 121.8658 | -61.7615 | 59.7519 | 0.14932 | 0.000689 | -0.007421 | -0.034174 | 0.036265 | 0.085583 | -0.076452 | 59.6599 | 59.6863 | 59.637 | 59.5493 | 61.7849 | 61.818 | 61.5458 | 61.7198 | 61.9108 | 61.7622 | 61.7541 | 61.7273 | 61.7977 | 61.8471 | 61.685 | 59.7057 | 59.732 | 59.6828 | 59.595 | 61.8307 | 61.8637 | 61.5916 | 61.7655 | -2.125 | -1.8859 | -2.1479 | -1.9088
1004.2969 | 121.756 | -62.4573 | 59.1476 | 0.14474 | 0.005267 | -0.012 | -0.029595 | 0.036265 | 0.081005 | -0.076452 | 59.0739 | 59.1048 | 59.0602 | 58.9723 | 62.3663 | 62.3902 | 62.1227 | 62.2966 | 62.602 | 62.4625 | 62.4453 | 62.4277 | 62.4935 | 62.5383 | 62.3808 | 59.1196 | 59.1505 | 59.106 | 59.0181 | 62.4121 | 62.436 | 62.1685 | 62.3424 | -3.2925 | -3.0488 | -3.3062 | -3.0625
1006.0625 | 121.8521 | -62.8967 | 58.6349 | 0.1539 | 0.005267 | -0.016578 | -0.029595 | 0.040843 | 0.081005 | -0.067295 | 58.4832 | 58.5187 | 58.4742 | 58.3862 | 62.9569 | 62.9945 | 62.7133 | 62.8918 | 63.0506 | 62.902 | 62.8802 | 62.8671 | 62.9376 | 62.9777 | 62.8294 | 58.529 | 58.5644 | 58.5199 | 58.432 | 63.0027 | 63.0403 | 62.7591 | 62.9375 | -4.4737 | -4.2301 | -4.4828 | -4.2392
1007.8281 | 121.8567 | -63.2538 | 58.255 | 0.14932 | 0.005267 | -0.012 | -0.034174 | 0.040843 | 0.076426 | -0.076452 | 58.1582 | 58.2027 | 58.1491 | 58.0611 | 63.282 | 63.3104 | 63.0292 | 63.2077 | 63.4031 | 63.2591 | 63.2418 | 63.2196 | 63.2946 | 63.3302 | 63.1773 | 58.2039 | 58.2485 | 58.1949 | 58.1069 | 63.3277 | 63.3562 | 63.075 | 63.2534 | -5.1238 | -4.8711 | -5.1329 | -4.8801
1009.5156 | 121.8338 | -64.0411 | 57.5134 | 0.14932 | 0.005267 | -0.016578 | -0.034174 | 0.045421 | 0.081005 | -0.076452 | 57.4531 | 57.4793 | 57.444 | 57.3467 | 63.9962 | 64.0246 | 63.7435 | 63.9264 | 64.1905 | 64.0464 | 64.0246 | 64.007 | 64.0866 | 64.1221 | 63.9647 | 57.4989 | 57.525 | 57.4898 | 57.3925 | 64.0419 | 64.0704 | 63.7892 | 63.9722 | -6.5431 | -6.2904 | -6.5521 | -6.2994
1011.2656 | 121.8063 | -64.4623 | 57.0923 | 0.14017 | 0.005267 | -0.016578 | -0.029595 | 0.040843 | 0.081005 | -0.067295 | 57.0044 | 57.0443 | 56.9908 | 56.9026 | 64.4402 | 64.4641 | 64.183 | 64.3659 | 64.6024 | 64.4675 | 64.4457 | 64.4327 | 64.5031 | 64.5433 | 64.395 | 57.0502 | 57.0901 | 57.0366 | 56.9484 | 64.486 | 64.5099 | 64.2288 | 64.4117 | -7.4359 | -7.1786 | -7.4494 | -7.1922
1013.0156 | 121.7926 | -65.1169 | 56.4972 | 0.14474 | 0.009846 | -0.007421 | -0.029595 | 0.036265 | 0.081005 | -0.071874 | 56.368 | 56.4124 | 56.3681 | 56.2753 | 65.0675 | 65.0913 | 64.8102 | 64.9977 | 65.2616 | 65.1267 | 65.1095 | 65.0873 | 65.1531 | 65.1979 | 65.045 | 56.4138 | 56.4582 | 56.4139 | 56.321 | 65.1132 | 65.137 | 64.856 | 65.0435 | -8.6995 | -8.4422 | -8.6993 | -8.4421
1014.7344 | 121.8979 | -71.0449 | 50.4639 | 0.14932 | 0.009846 | -0.007421 | -0.025017 | 0.036265 | 0.081005 | -0.076452 | 50.4342 | 50.4599 | 50.4164 | 50.382 | 71.0008 | 71.029 | 70.7301 | 70.9173 | 71.1942 | 71.0548 | 71.0375 | 71.0199 | 71.0812 | 71.1259 | 70.9685 | 50.48 | 50.5057 | 50.4622 | 50.4278 | 71.0465 | 71.0748 | 70.7759 | 70.9631 | -20.5665 | -20.2958 | -20.5844 | -20.3137
1016.5156 | 121.8979 | -73.2559 | 48.2346 | 0.14017 | -0.008469 | -0.012 | -0.034174 | 0.040843 | 0.085583 | -0.071874 | 48.1084 | 48.1476 | 48.0952 | 48.065 | 73.3265 | 73.3547 | 73.0239 | 73.2568 | 73.3961 | 73.2475 | 73.2439 | 73.2217 | 73.2968 | 73.3415 | 73.184 | 48.1541 | 48.1934 | 48.141 | 48.1108 | 73.3723 | 73.4005 | 73.0696 | 73.3025 | -25.2181 | -24.9155 | -25.2313 | -24.9287
1018.2031 | 121.907 | -74.1486 | 47.3694 | 0.14474 | 0.005267 | -0.016578 | -0.029595 | 0.036265 | 0.076426 | -0.076452 | 47.2614 | 47.3097 | 47.2528 | 47.2271 | 74.1734 | 74.2062 | 73.8525 | 74.0946 | 74.2933 | 74.1538 | 74.132 | 74.119 | 74.1848 | 74.225 | 74.0721 | 47.3071 | 47.3555 | 47.2986 | 47.2729 | 74.2192 | 74.252 | 73.8983 | 74.1403 | -26.9121 | -26.5912 | -26.9206 | -26.5997
1019.9531 | 121.7697 | -76.3733 | 45.2087 | 0.14474 | 0.000689 | -0.007421 | -0.029595 | 0.045421 | 0.085583 | -0.071874 | 45.3338 | 45.3775 | 45.3208 | 45.2993 | 76.1054 | 76.1336 | 75.7846 | 76.0266 | 76.518 | 76.374 | 76.3659 | 76.3437 | 76.4187 | 76.4589 | 76.3014 | 45.3796 | 45.4232 | 45.3665 | 45.3451 | 76.1512 | 76.1793 | 75.8304 | 76.0723 | -30.7716 | -30.4508 | -30.7847 | -30.4639
1021.7344 | 121.8155 | -76.3733 | 45.1996 | 0.14932 | 0.000689 | -0.012 | -0.029595 | 0.036265 | 0.081005 | -0.071874 | 44.8805 | 44.915 | 44.8584 | 44.8323 | 76.5632 | 76.5914 | 76.2516 | 76.4844 | 76.5226 | 76.374 | 76.3613 | 76.3437 | 76.4096 | 76.4543 | 76.3014 | 44.9263 | 44.9608 | 44.9041 | 44.878 | 76.609 | 76.6371 | 76.2974 | 76.5301 | -31.6827 | -31.3711 | -31.7049 | -31.3933
1023.4844 | 121.9208 | -78.2684 | 43.222 | 0.14474 | 0.005267 | -0.016578 | -0.029595 | 0.031687 | 0.081005 | -0.071874 | 43.1361 | 43.1888 | 43.1232 | 43.1014 | 78.2938 | 78.3265 | 77.9822 | 78.2103 | 78.4132 | 78.2737 | 78.2519 | 78.2388 | 78.3001 | 78.3494 | 78.1966 | 43.1819 | 43.2346 | 43.169 | 43.1472 | 78.3396 | 78.3722 | 78.028 | 78.2561 | -35.1577 | -34.8461 | -35.1706 | -34.8591
1025.2344 | 121.8933 | -79.747 | 41.7618 | 0.14017 | 0.005267 | -0.012 | -0.029595 | 0.036265 | 0.081005 | -0.076452 | 41.6069 | 41.6549 | 41.6032 | 41.5674 | 79.8275 | 79.851 | 79.516 | 79.7394 | 79.8872 | 79.7523 | 79.735 | 79.7174 | 79.7833 | 79.828 | 79.6706 | 41.6527 | 41.7007 | 41.649 | 41.6132 | 79.8733 | 79.8967 | 79.5618 | 79.7852 | -38.2206 | -37.9091 | -38.2243 | -37.9128
1026.9375 | 121.8155 | -83.6609 | 37.8891 | 0.14474 | 0.005267 | -0.012 | -0.020438 | 0.045421 | 0.085583 | -0.071874 | 37.88 | 37.9415 | 37.8719 | 37.8492 | 83.5404 | 83.5821 | 83.2245 | 83.4615 | 83.8056 | 83.6662 | 83.6489 | 83.6405 | 83.7063 | 83.7465 | 83.589 | 37.9258 | 37.9872 | 37.9177 | 37.895 | 83.5862 | 83.6279 | 83.2703 | 83.5073 | -45.6604 | -45.3445 | -45.6685 | -45.3526
1028.6875 | 121.8933 | -72.2992 | 49.2599 | 0.14474 | 0.005267 | -0.021157 | -0.029595 | 0.040843 | 0.081005 | -0.071874 | 49.3217 | 49.3061 | 49.3039 | 49.2144 | 71.9256 | 72.1461 | 71.8197 | 71.9428 | 72.4439 | 72.3045 | 72.278 | 72.2696 | 72.34 | 72.3802 | 72.2273 | 49.3675 | 49.3519 | 49.3496 | 49.2602 | 71.9713 | 72.1918 | 71.8655 | 71.9886 | -22.6039 | -22.4981 | -22.6217 | -22.5159
1030.4375 | 121.8475 | -97.5037 | 23.9868 | 0.14932 | 0.009846 | -0.012 | -0.029595 | 0.036265 | 0.085583 | -0.067295 | 25.0373 | 25.0658 | 25.0664 | 25.0096 | 96.3364 | 96.4007 | 96.0302 | 96.1339 | 97.653 | 97.5135 | 97.4917 | 97.4741 | 97.5399 | 97.5892 | 97.4364 | 25.0831 | 25.1116 | 25.1122 | 25.0554 | 96.3822 | 96.4464 | 96.076 | 96.1797 | -71.299 | -70.9929 | -71.2699 | -70.9638
1032.2188 | 119.7647 | -108.1421 | 13.3347 | 0.14017 | 0.000689 | -0.016578 | -0.029595 | 0.036265 | 0.081005 | -0.071874 | 13.5087 | 13.573 | 13.5246 | 13.4934 | 107.91 | 107.9649 | 107.5953 | 107.6938 | 108.2823 | 108.1428 | 108.1255 | 108.1125 | 108.1784 | 108.2231 | 108.0702 | 13.5545 | 13.6188 | 13.5704 | 13.5391 | 107.9558 | 108.0106 | 107.641 | 107.7396 | -94.4013 | -94.0866 | -94.3854 | -94.0707
1033.9844 | 121.9208 | -110.6461 | 10.8307 | 0.14932 | 0.000689 | -0.002842 | -0.034174 | 0.040843 | 0.085583 | -0.067295 | 10.8806 | 10.9585 | 10.8921 | 10.8696 | 110.5516 | 110.5972 | 110.2187 | 110.3262 | 110.7954 | 110.6467 | 110.6432 | 110.6119 | 110.6869 | 110.7316 | 110.5788 | 10.9264 | 11.0043 | 10.9379 | 10.9154 | 110.5974 | 110.643 | 110.2644 | 110.372 | -99.671 | -99.338 | -99.6595 | -99.3266
1035.6875 | 121.8338 | -111.7676 | 9.7961 | 0.14932 | 0.005267 | -0.016578 | -0.025017 | 0.045421 | 0.085583 | -0.067295 | 9.7681 | 9.8504 | 9.7887 | 9.7706 | 111.6504 | 111.696 | 111.3266 | 111.425 | 111.9169 | 111.7728 | 111.751 | 111.7426 | 111.813 | 111.8532 | 111.7003 | 9.8138 | 9.8962 | 9.8345 | 9.8164 | 111.6961 | 111.7418 | 111.3724 | 111.4708 | -101.8823 | -101.5586 | -101.8616 | -101.5379
1037.4375 | 121.8338 | -111.731 | 9.8053 | 0.14474 | 0.000689 | -0.012 | -0.029595 | 0.036265 | 0.085583 | -0.076452 | 9.6856 | 9.7726 | 9.688 | 9.679 | 111.7328 | 111.7875 | 111.4136 | 111.5165 | 111.8757 | 111.7316 | 111.719 | 111.7014 | 111.7672 | 111.8165 | 111.6545 | 9.7314 | 9.8183 | 9.7338 | 9.7248 | 111.7785 | 111.8333 | 111.4594 | 111.5623 | -102.0471 | -101.728 | -102.0448 | -101.7256
1039.125 | 121.843 | -111.3922 | 10.1852 | 0.14932 | 0.000689 | -0.012 | -0.038752 | 0.040843 | 0.085583 | -0.067295 | 10.171 | 10.2442 | 10.1458 | 10.1552 | 111.2521 | 111.2977 | 110.9237 | 111.0313 | 111.5415 | 111.3929 | 111.3802 | 111.3535 | 111.4331 | 111.4778 | 111.3249 | 10.2167 | 10.29 | 10.1916 | 10.201 | 111.2978 | 111.3435 | 110.9695 | 111.077 | -101.0811 | -100.7528 | -101.1062 | -100.7779
1040.875 | 121.7743 | -112.1475 | 9.4482 | 0.14474 | 0.005267 | -0.012 | -0.029595 | 0.036265 | 0.09474 | -0.067295 | 9.3606 | 9.4475 | 9.3355 | 9.3677 | 112.0487 | 112.0897 | 111.725 | 111.8279 | 112.2923 | 112.1528 | 112.1355 | 112.1179 | 112.1838 | 112.2423 | 112.0802 | 9.4063 | 9.4933 | 9.3812 | 9.4134 | 112.0944 | 112.1355 | 111.7707 | 111.8736 | -102.6881 | -102.3644 | -102.7132 | -102.3895
1042.6406 | 121.7651 | -112.6053 | 8.9722 | 0.13559 | 0.005267 | -0.021157 | -0.029595 | 0.036265 | 0.085583 | -0.071874 | 8.9302 | 9.0262 | 8.9051 | 8.9281 | 112.4699 | 112.5155 | 112.1462 | 112.2582 | 112.7409 | 112.6106 | 112.5841 | 112.5757 | 112.6416 | 112.6909 | 112.5334 | 8.976 | 9.072 | 8.9509 | 8.9738 | 112.5156 | 112.5612 | 112.192 | 112.304 | -103.5397 | -103.216 | -103.5647 | -103.2411
1044.3906 | 121.843 | -112.8754 | 8.6609 | 0.14932 | 0.005267 | -0.012 | -0.029595 | 0.031687 | 0.085583 | -0.067295 | 8.6097 | 8.7011 | 8.5846 | 8.603 | 112.7903 | 112.8359 | 112.4621 | 112.6886 | 113.0247 | 112.8806 | 112.8634 | 112.8458 | 112.9071 | 112.9609 | 112.8081 | 8.6555 | 8.7469 | 8.6304 | 8.6487 | 112.8361 | 112.8817 | 112.5079 | 112.7343 | -104.1806 | -103.8524 | -104.2057 | -103.8774
1046.1406 | 121.7285 | -113.1683 | 8.4412 | 0.1539 | 0.000689 | -0.012 | -0.025017 | 0.036265 | 0.081005 | -0.071874 | 8.3533 | 8.4356 | 8.3191 | 8.3465 | 113.0513 | 113.106 | 112.7231 | 112.9541 | 113.3222 | 113.169 | 113.1563 | 113.1433 | 113.2046 | 113.2493 | 113.0965 | 8.3991 | 8.4813 | 8.3649 | 8.3923 | 113.0971 | 113.1518 | 112.7688 | 112.9999 | -104.698 | -104.3698 | -104.7322 | -104.404
1047.8906 | 121.7468 | -113.3743 | 8.2306 | 0.14474 | 0.009846 | -0.016578 | -0.025017 | 0.031687 | 0.085583 | -0.076452 | 8.1427 | 8.2341 | 8.1268 | 8.1405 | 113.2481 | 113.2937 | 112.9291 | 113.1464 | 113.5191 | 113.3842 | 113.3578 | 113.3493 | 113.406 | 113.4599 | 113.2979 | 8.1885 | 8.2799 | 8.1726 | 8.1862 | 113.2939 | 113.3395 | 112.9749 | 113.1922 | -105.1055 | -104.7864 | -105.1213 | -104.8023
1049.6406 | 121.8292 | -113.4476 | 8.0429 | 0.14474 | 0.000689 | -0.012 | -0.029595 | 0.031687 | 0.085583 | -0.076452 | 7.9916 | 8.0876 | 7.9574 | 7.9939 | 113.4084 | 113.4494 | 113.0802 | 113.3066 | 113.5923 | 113.4483 | 113.4356 | 113.418 | 113.4793 | 113.5332 | 113.3711 | 8.0374 | 8.1333 | 8.0032 | 8.0397 | 113.4542 | 113.4952 | 113.1259 | 113.3524 | -105.4168 | -105.0886 | -105.451 | -105.1228
1051.3281 | 121.8201 | -113.6078 | 7.9239 | 0.14474 | 0.000689 | -0.012 | -0.029595 | 0.036265 | 0.081005 | -0.076452 | 7.8542 | 7.941 | 7.8338 | 7.8612 | 113.5366 | 113.573 | 113.2129 | 113.4302 | 113.7525 | 113.6085 | 113.5958 | 113.5782 | 113.6441 | 113.6888 | 113.5313 | 7.9 | 7.9868 | 7.8796 | 7.9069 | 113.5823 | 113.6188 | 113.2587 | 113.476 | -105.6823 | -105.3587 | -105.7028 | -105.3791
1053.0781 | 121.788 | -113.6948 | 7.8827 | 0.14017 | -0.00389 | -0.012 | -0.034174 | 0.036265 | 0.071848 | -0.076452 | 7.7673 | 7.8449 | 7.7468 | 7.7604 | 113.6236 | 113.6737 | 113.2999 | 113.5309 | 113.8349 | 113.6909 | 113.6828 | 113.6606 | 113.731 | 113.7666 | 113.6183 | 7.813 | 7.8907 | 7.7926 | 7.8062 | 113.6693 | 113.7195 | 113.3457 | 113.5767 | -105.8563 | -105.5327 | -105.8767 | -105.5531
1054.7656 | 121.7743 | -113.7543 | 7.8049 | 0.14474 | 0.000689 | -0.012 | -0.034174 | 0.040843 | 0.085583 | -0.076452 | 7.6024 | 7.6984 | 7.5774 | 7.6093 | 113.7746 | 113.8294 | 113.451 | 113.6729 | 113.899 | 113.755 | 113.7423 | 113.7201 | 113.7951 | 113.8399 | 113.6778 | 7.6482 | 7.7441 | 7.6232 | 7.6551 | 113.8204 | 113.8751 | 113.4968 | 113.7186 | -106.1722 | -105.8486 | -106.1972 | -105.8736
1056.5156 | 121.6965 | -113.9786 | 7.5897 | 0.14932 | -0.00389 | -0.021157 | -0.025017 | 0.031687 | 0.085583 | -0.067295 | 7.5337 | 7.6159 | 7.5042 | 7.5269 | 113.8525 | 113.898 | 113.5288 | 113.7507 | 114.1279 | 113.9747 | 113.9574 | 113.9536 | 114.0103 | 114.0642 | 113.9113 | 7.5795 | 7.6617 | 7.5499 | 7.5727 | 113.8982 | 113.9438 | 113.5746 | 113.7965 | -106.3187 | -105.9951 | -106.3483 | -106.0247
1058.2812 | 121.7377 | -113.942 | 7.6035 | 0.14474 | 0.000689 | -0.016578 | -0.034174 | 0.036265 | 0.081005 | -0.067295 | 7.52 | 7.6114 | 7.4996 | 7.5269 | 113.8616 | 113.9072 | 113.5288 | 113.7599 | 114.0867 | 113.9426 | 113.9254 | 113.9078 | 113.9782 | 114.023 | 113.8747 | 7.5658 | 7.6571 | 7.5454 | 7.5727 | 113.9074 | 113.953 | 113.5746 | 113.8056 | -106.3416 | -106.0088 | -106.362 | -106.0293
1060.0469 | 121.7194 | -114.0793 | 7.5073 | 0.14474 | -0.00389 | -0.012 | -0.025017 | 0.040843 | 0.085583 | -0.071874 | 7.3781 | 7.474 | 7.3668 | 7.3849 | 113.9852 | 114.0445 | 113.6754 | 113.888 | 114.224 | 114.0754 | 114.0673 | 114.0543 | 114.1201 | 114.1649 | 114.0074 | 7.4239 | 7.5198 | 7.4126 | 7.4307 | 114.031 | 114.0903 | 113.7211 | 113.9338 | -106.6072 | -106.2973 | -106.6184 | -106.3085
1061.7344 | 121.7148 | -114.1983 | 7.3608 | 0.14474 | -0.00389 | -0.012 | -0.025017 | 0.040843 | 0.081005 | -0.076452 | 7.259 | 7.3504 | 7.2386 | 7.2613 | 114.1134 | 114.1636 | 113.7898 | 114.0117 | 114.343 | 114.1944 | 114.1863 | 114.1733 | 114.2391 | 114.2793 | 114.1219 | 7.3048 | 7.3962 | 7.2844 | 7.3071 | 114.1592 | 114.2093 | 113.8356 | 114.0574 | -106.8544 | -106.5308 | -106.8748 | -106.5512
1063.4844 | 121.7377 | -114.3585 | 7.1548 | 0.14474 | 0.000689 | -0.007421 | -0.025017 | 0.040843 | 0.085583 | -0.067295 | 7.1904 | 7.2771 | 7.1654 | 7.1926 | 114.1867 | 114.2231 | 113.8631 | 114.0895 | 114.5033 | 114.3592 | 114.3511 | 114.3335 | 114.3994 | 114.4441 | 114.2912 | 7.2361 | 7.3229 | 7.2111 | 7.2384 | 114.2324 | 114.2689 | 113.9088 | 114.1353 | -106.9963 | -106.6727 | -107.0213 | -106.6977
1065.1719 | 121.6919 | -114.299 | 7.2968 | 0.14017 | 0.000689 | -0.021157 | -0.025017 | 0.040843 | 0.081005 | -0.071874 | 7.1766 | 7.2725 | 7.1562 | 7.1789 | 114.1867 | 114.246 | 113.8676 | 114.0941 | 114.4392 | 114.2997 | 114.2779 | 114.274 | 114.3399 | 114.38 | 114.2271 | 7.2224 | 7.3183 | 7.202 | 7.2247 | 114.2324 | 114.2917 | 113.9134 | 114.1398 | -107.01 | -106.691 | -107.0305 | -106.7114
1066.9062 | 121.7102 | -114.2899 | 7.2922 | 0.14474 | 0.000689 | -0.016578 | -0.025017 | 0.045421 | 0.085583 | -0.076452 | 7.1904 | 7.2817 | 7.1562 | 7.1972 | 114.1775 | 114.2277 | 113.8539 | 114.0803 | 114.4346 | 114.2905 | 114.2733 | 114.2648 | 114.3353 | 114.3754 | 114.2134 | 7.2361 | 7.3275 | 7.202 | 7.243 | 114.2233 | 114.2734 | 113.8997 | 114.1261 | -106.9872 | -106.6636 | -107.0213 | -106.6977
1068.6719 | 121.7514 | -114.2807 | 7.2098 | 0.14017 | -0.008469 | -0.016578 | -0.029595 | 0.027109 | 0.085583 | -0.08103 | 7.1446 | 7.2451 | 7.1287 | 7.156 | 114.2187 | 114.2643 | 113.8951 | 114.117 | 114.4209 | 114.2722 | 114.2641 | 114.2511 | 114.3078 | 114.3663 | 114.1997 | 7.1904 | 7.2908 | 7.1745 | 7.2018 | 114.2645 | 114.3101 | 113.9409 | 114.1627 | -107.0741 | -106.7505 | -107.09 | -106.7664
1070.4062 | 121.701 | -114.2578 | 7.2784 | 0.1539 | 0.000689 | -0.021157 | -0.029595 | 0.040843 | 0.090161 | -0.071874 | 7.1766 | 7.2634 | 7.1562 | 7.1789 | 114.1867 | 114.2368 | 113.8585 | 114.0849 | 114.4117 | 114.2585 | 114.2367 | 114.2282 | 114.2987 | 114.348 | 114.1859 | 7.2224 | 7.3092 | 7.202 | 7.2247 | 114.2324 | 114.2826 | 113.9043 | 114.1307 | -107.01 | -106.6819 | -107.0305 | -106.7023
1072.1562 | 121.6736 | -114.4455 | 7.1503 | 0.13559 | -0.00389 | -0.012 | -0.025017 | 0.040843 | 0.081005 | -0.076452 | 7.1171 | 7.2176 | 7.1013 | 7.1331 | 114.237 | 114.2826 | 113.9134 | 114.1398 | 114.5811 | 114.4416 | 114.4335 | 114.4205 | 114.4863 | 114.5265 | 114.369 | 7.1629 | 7.2634 | 7.147 | 7.1789 | 114.2828 | 114.3284 | 113.9592 | 114.1856 | -107.1199 | -106.7963 | -107.1358 | -106.8122
1073.9219 | 121.7194 | -114.3906 | 7.1457 | 0.14474 | 0.000689 | -0.012 | -0.025017 | 0.045421 | 0.076426 | -0.071874 | 7.0851 | 7.1718 | 7.0601 | 7.0919 | 114.2828 | 114.3238 | 113.9455 | 114.1719 | 114.5353 | 114.3913 | 114.3786 | 114.3655 | 114.436 | 114.467 | 114.3187 | 7.1308 | 7.2176 | 7.1058 | 7.1376 | 114.3286 | 114.3696 | 113.9913 | 114.2177 | -107.1978 | -106.8604 | -107.2227 | -106.8854
1075.6719 | 121.6873 | -114.4684 | 7.077 | 0.14474 | 0.000689 | -0.016578 | -0.025017 | 0.036265 | 0.085583 | -0.071874 | 7.0072 | 7.1031 | 6.9868 | 7.0186 | 114.3515 | 114.397 | 114.0233 | 114.2451 | 114.6131 | 114.4691 | 114.4518 | 114.4434 | 114.5046 | 114.554 | 114.3965 | 7.053 | 7.1489 | 7.0326 | 7.0644 | 114.3973 | 114.4428 | 114.0691 | 114.2909 | -107.3443 | -107.0161 | -107.3647 | -107.0365
1077.3594 | 121.6644 | -114.3814 | 7.2006 | 0.14474 | 0.000689 | -0.012 | -0.029595 | 0.040843 | 0.085583 | -0.062717 | 7.0667 | 7.1718 | 7.0555 | 7.0827 | 114.2782 | 114.3329 | 113.9546 | 114.1765 | 114.5262 | 114.3821 | 114.3694 | 114.3518 | 114.4223 | 114.467 | 114.3187 | 7.1125 | 7.2176 | 7.1013 | 7.1285 | 114.324 | 114.3787 | 114.0004 | 114.2222 | -107.2115 | -106.8879 | -107.2227 | -106.8991
1079.125 | 121.7972 | -114.3127 | 7.1365 | 0.14017 | -0.008469 | -0.012 | -0.034174 | 0.031687 | 0.081005 | -0.076452 | 7.0759 | 7.1626 | 7.0555 | 7.0827 | 114.2874 | 114.3238 | 113.9638 | 114.181 | 114.4529 | 114.3043 | 114.3007 | 114.2786 | 114.3444 | 114.3937 | 114.2363 | 7.1217 | 7.2084 | 7.1013 | 7.1285 | 114.3332 | 114.3696 | 114.0096 | 114.2268 | -107.2115 | -106.8879 | -107.2319 | -106.9083
1080.8906 | 121.7834 | -114.2441 | 7.2235 | 0.14017 | -0.00389 | -0.021157 | -0.025017 | 0.036265 | 0.081005 | -0.071874 | 7.1629 | 7.2496 | 7.1425 | 7.1651 | 114.1958 | 114.2368 | 113.8676 | 114.0941 | 114.3842 | 114.2402 | 114.2229 | 114.2191 | 114.2803 | 114.3251 | 114.1722 | 7.2087 | 7.2954 | 7.1883 | 7.2109 | 114.2416 | 114.2826 | 113.9134 | 114.1398 | -107.0329 | -106.7048 | -107.0534 | -106.7252
1082.6406 | 121.6507 | -114.386 | 7.1365 | 0.14017 | 0.000689 | -0.007421 | -0.029595 | 0.036265 | 0.090161 | -0.071874 | 7.0255 | 7.1169 | 7.0051 | 7.0323 | 114.3286 | 114.365 | 113.9913 | 114.2177 | 114.5262 | 114.3867 | 114.3786 | 114.3564 | 114.4223 | 114.4761 | 114.3141 | 7.0713 | 7.1626 | 7.0509 | 7.0781 | 114.3744 | 114.4108 | 114.037 | 114.2634 | -107.3031 | -106.9657 | -107.3235 | -106.9861
1084.3281 | 121.7422 | -113.9969 | 7.457 | 0.14474 | -0.00389 | -0.016578 | -0.025017 | 0.031687 | 0.081005 | -0.076452 | 7.3964 | 7.4969 | 7.3805 | 7.4124 | 113.9486 | 113.9987 | 113.6296 | 113.856 | 114.1416 | 113.993 | 113.9803 | 113.9719 | 114.0286 | 114.0779 | 113.9204 | 7.4422 | 7.5427 | 7.4263 | 7.4582 | 113.9944 | 114.0445 | 113.6753 | 113.9018 | -106.5522 | -106.2332 | -106.5681 | -106.249
1086.0781 | 121.6644 | -113.7588 | 7.7957 | 0.14017 | -0.00389 | -0.007421 | -0.034174 | 0.036265 | 0.081005 | -0.076452 | 7.694 | 7.7899 | 7.6781 | 7.7009 | 113.6602 | 113.7012 | 113.3274 | 113.5538 | 113.899 | 113.755 | 113.7514 | 113.7247 | 113.7951 | 113.8399 | 113.6824 | 7.7398 | 7.8357 | 7.7239 | 7.7467 | 113.706 | 113.747 | 113.3732 | 113.5996 | -105.9662 | -105.6334 | -105.982 | -105.6493
1087.7656 | 121.7331 | -113.7222 | 7.7911 | 0.14474 | -0.008469 | -0.016578 | -0.029595 | 0.031687 | 0.076426 | -0.062717 | 7.6803 | 7.7671 | 7.6552 | 7.678 | 113.6693 | 113.7103 | 113.3366 | 113.563 | 113.867 | 113.7138 | 113.7057 | 113.6926 | 113.7539 | 113.7987 | 113.6595 | 7.726 | 7.8128 | 7.701 | 7.7238 | 113.7151 | 113.7561 | 113.3823 | 113.6088 | -105.9891 | -105.6563 | -106.0141 | -105.6813
1089.5156 | 121.7285 | -113.7314 | 7.7728 | 0.14017 | -0.00389 | -0.016578 | -0.034174 | 0.040843 | 0.081005 | -0.067295 | 7.7123 | 7.7991 | 7.6781 | 7.7192 | 113.6419 | 113.692 | 113.3137 | 113.5309 | 113.8715 | 113.7275 | 113.7148 | 113.6972 | 113.7722 | 113.8124 | 113.6641 | 7.7581 | 7.8449 | 7.7239 | 7.765 | 113.6876 | 113.7378 | 113.3594 | 113.5767 | -105.9296 | -105.6014 | -105.9637 | -105.6355
1091.2656 | 121.7743 | -113.7131 | 7.7179 | 0.14474 | 0.000689 | -0.012 | -0.025017 | 0.031687 | 0.081005 | -0.067295 | 7.6391 | 7.7304 | 7.6186 | 7.6368 | 113.706 | 113.7424 | 113.3732 | 113.6042 | 113.8578 | 113.7138 | 113.7011 | 113.6881 | 113.7448 | 113.7941 | 113.6458 | 7.6848 | 7.7762 | 7.6644 | 7.6826 | 113.7517 | 113.7882 | 113.419 | 113.65 | -106.0669 | -105.7341 | -106.0873 | -105.7546
1093.0156 | 121.7468 | -113.4888 | 7.9971 | 0.14017 | -0.008469 | -0.012 | -0.025017 | 0.036265 | 0.071848 | -0.076452 | 7.8726 | 7.9639 | 7.8475 | 7.8749 | 113.4771 | 113.5135 | 113.1397 | 113.3661 | 113.6289 | 113.4803 | 113.4768 | 113.4638 | 113.525 | 113.5606 | 113.4123 | 7.9183 | 8.0097 | 7.8933 | 7.9207 | 113.5228 | 113.5593 | 113.1855 | 113.4119 | -105.6045 | -105.2671 | -105.6295 | -105.2922
1094.7031 | 121.6736 | -81.7062 | 39.6561 | 0.14474 | 0.000689 | -0.012 | -0.020438 | 0.040843 | 0.081005 | -0.067295 | 38.2967 | 38.3398 | 38.3297 | 38.2613 | 82.9864 | 83.0098 | 82.8216 | 82.8938 | 81.851 | 81.7069 | 81.6942 | 81.6858 | 81.7471 | 81.7872 | 81.6389 | 38.3424 | 38.3856 | 38.3755 | 38.3071 | 83.0322 | 83.0556 | 82.8674 | 82.9396 | -44.6898 | -44.5249 | -44.6567 | -44.4919
1096.4531 | 121.4493 | -72.5876 | 48.7656 | 0.15848 | 0.023583 | 0.006315 | 0.002454 | 0.063733 | 0.10848 | -0.048983 | 29.4464 | 29.5485 | 29.4295 | 29.4238 | 91.717 | 91.7631 | 91.5526 | 91.6564 | 72.7461 | 72.6112 | 72.5939 | 72.59 | 72.6513 | 72.6961 | 72.5386 | 29.4922 | 29.5943 | 29.4753 | 29.4696 | 91.7628 | 91.8089 | 91.5984 | 91.7022 | -62.2706 | -62.1062 | -62.2875 | -62.123
1098.2188 | 121.5546 | -77.9251 | 43.1168 | 0.14474 | 0.009846 | 0.006315 | -0.002124 | 0.063733 | 0.1039 | -0.048983 | 31.2732 | 31.4945 | 31.2563 | 31.3012 | 89.872 | 89.8952 | 89.7121 | 89.8526 | 78.0699 | 77.935 | 77.9314 | 77.923 | 77.9888 | 78.029 | 77.8761 | 31.319 | 31.5403 | 31.3021 | 31.347 | 89.9178 | 89.941 | 89.7579 | 89.8984 | -58.5987 | -58.4388 | -58.6157 | -58.4558
1099.9062 | 121.431 | -83.67 | 37.5183 | 0.14017 | -0.00389 | -0.007421 | -0.020438 | 0.045421 | 0.085583 | -0.067295 | 36.3874 | 36.4762 | 36.4252 | 36.3748 | 84.6849 | 84.7083 | 84.5293 | 84.606 | 83.8102 | 83.6662 | 83.6626 | 83.6496 | 83.7155 | 83.7556 | 83.6027 | 36.4332 | 36.522 | 36.4709 | 36.4206 | 84.7307 | 84.7541 | 84.5751 | 84.6518 | -48.2975 | -48.1419 | -48.2598 | -48.1042
1101.6562 | 121.2799 | -52.652 | 68.3899 | 0.14017 | 0.000689 | -0.012 | -0.029595 | 0.036265 | 0.076426 | -0.071874 | 69.2381 | 69.2697 | 69.2652 | 69.179 | 51.7267 | 51.7554 | 51.5741 | 51.6615 | 52.7921 | 52.6527 | 52.64 | 52.6224 | 52.6882 | 52.7284 | 52.5801 | 69.2839 | 69.3155 | 69.3109 | 69.2247 | 51.7724 | 51.8011 | 51.6199 | 51.7073 | 17.5115 | 17.664 | 17.5385 | 17.6911
1103.4062 | 121.1472 | -55.6183 | 65.5746 | 0.14474 | -0.008469 | -0.012 | -0.020438 | 0.040843 | 0.081005 | -0.071874 | 67.4205 | 67.4474 | 67.4201 | 67.3428 | 53.4755 | 53.5133 | 53.323 | 53.4241 | 55.763 | 55.6098 | 55.6063 | 55.5978 | 55.6591 | 55.6993 | 55.5464 | 67.4662 | 67.4931 | 67.4659 | 67.3886 | 53.5213 | 53.5591 | 53.3688 | 53.4699 | 13.9449 | 14.0974 | 13.9446 | 14.0971
1105.1562 | 121.3074 | -55.2612 | 65.799 | 0.14474 | -0.008469 | -0.016578 | -0.025017 | 0.040843 | 0.081005 | -0.076452 | 66.633 | 66.6598 | 66.6555 | 66.5506 | 54.2355 | 54.2596 | 54.0876 | 54.1658 | 55.406 | 55.2528 | 55.2447 | 55.2362 | 55.3021 | 55.3422 | 55.1848 | 66.6787 | 66.7056 | 66.7013 | 66.5964 | 54.2813 | 54.3053 | 54.1334 | 54.2115 | 12.3975 | 12.5453 | 12.4201 | 12.5679
1106.9219 | 120.9366 | -49.0814 | 71.8506 | 0.1539 | 0.005267 | -0.007421 | -0.020438 | 0.045421 | 0.090161 | -0.071874 | 68.7986 | 68.8943 | 68.789 | 68.7394 | 51.8594 | 51.9064 | 51.7298 | 51.8263 | 49.2353 | 49.0867 | 49.074 | 49.061 | 49.1268 | 49.1716 | 49.0095 | 68.8444 | 68.94 | 68.8348 | 68.7852 | 51.9052 | 51.9522 | 51.7755 | 51.8721 | 16.9392 | 17.0688 | 16.9296 | 17.0593
1108.6875 | 120.6024 | -50.3128 | 70.1477 | 0.14474 | -0.00389 | -0.007421 | -0.020438 | 0.045421 | 0.085583 | -0.067295 | 65.5708 | 65.6112 | 65.5476 | 65.4654 | 54.7757 | 54.8227 | 54.6462 | 54.738 | 50.4575 | 50.3089 | 50.3054 | 50.2924 | 50.3582 | 50.3984 | 50.2455 | 65.6165 | 65.657 | 65.5934 | 65.5111 | 54.8215 | 54.8684 | 54.692 | 54.7838 | 10.795 | 10.9246 | 10.7719 | 10.9014
1110.3906 | 121.1792 | -0.19684 | 121.0739 | 0.14474 | 0.000689 | -0.007421 | -0.025017 | 0.045421 | 0.085583 | -0.076452 | 120.7233 | 120.7356 | 120.7571 | 120.6656 | 0.06197 | 0.13767 | 0.062662 | 0.1067 | 0.34158 | 0.19753 | 0.18942 | 0.17182 | 0.24226 | 0.28242 | 0.12039 | 120.7691 | 120.7814 | 120.8029 | 120.7114 | 0.10775 | 0.18345 | 0.10844 | 0.15248 | 120.6613 | 120.6606 | 120.6951 | 120.6944
1112.1406 | 121.344 | -0.2243 | 121.1014 | 0.13559 | -0.013048 | -0.012 | -0.020438 | 0.040843 | 0.085583 | -0.071874 | 120.8652 | 120.8684 | 120.9173 | 120.8121 | 0.048236 | 0.12851 | 0.048926 | 0.09297 | 0.35989 | 0.21126 | 0.2123 | 0.20387 | 0.26515 | 0.30989 | 0.15243 | 120.911 | 120.9142 | 120.9631 | 120.8579 | 0.094012 | 0.17429 | 0.094702 | 0.13875 | 120.817 | 120.8163 | 120.8691 | 120.8684
1113.8594 | 121.4447 | -0.23804 | 121.1151 | 0.14474 | -0.00389 | -0.016578 | -0.029595 | 0.045421 | 0.085583 | -0.071874 | 120.8927 | 120.905 | 120.9402 | 120.8304 | 0.066548 | 0.16056 | 0.10845 | 0.11586 | 0.38278 | 0.23415 | 0.22146 | 0.20844 | 0.28346 | 0.32362 | 0.16616 | 120.9385 | 120.9508 | 120.986 | 120.8762 | 0.11232 | 0.20634 | 0.15422 | 0.16164 | 120.8262 | 120.7843 | 120.8737 | 120.8318
1115.6094 | 121.4493 | -0.35706 | 120.9869 | 0.14932 | -0.013048 | -0.012 | -0.025017 | 0.036265 | 0.076426 | -0.076452 | 120.792 | 120.786 | 120.8258 | 120.7251 | 0.1398 | 0.2567 | 0.20917 | 0.20285 | 0.50638 | 0.34401 | 0.34506 | 0.33204 | 0.39332 | 0.43348 | 0.2806 | 120.8378 | 120.8318 | 120.8715 | 120.7709 | 0.18557 | 0.30248 | 0.25495 | 0.24862 | 120.6522 | 120.5828 | 120.686 | 120.6166
1117.3125 | 121.4081 | -0.38452 | 120.9732 | 0.14474 | -0.00389 | -0.007421 | -0.029595 | 0.036265 | 0.085583 | -0.071874 | 120.7508 | 120.7494 | 120.7846 | 120.6793 | 0.16727 | 0.29333 | 0.25038 | 0.24863 | 0.52926 | 0.38063 | 0.3771 | 0.35493 | 0.42079 | 0.4701 | 0.31265 | 120.7966 | 120.7951 | 120.8303 | 120.7251 | 0.21304 | 0.3391 | 0.29615 | 0.2944 | 120.5835 | 120.5004 | 120.6173 | 120.5342
1119.0781 | 121.4584 | -0.37537 | 120.9457 | 0.14017 | -0.00389 | -0.012 | -0.025017 | 0.040843 | 0.081005 | -0.076452 | 120.7416 | 120.7448 | 120.7846 | 120.6748 | 0.18558 | 0.30248 | 0.25038 | 0.25778 | 0.51553 | 0.37148 | 0.36337 | 0.35035 | 0.41621 | 0.45637 | 0.29891 | 120.7874 | 120.7906 | 120.8303 | 120.7205 | 0.23136 | 0.34826 | 0.29615 | 0.30356 | 120.556 | 120.4912 | 120.599 | 120.5342
1120.7812 | 121.4722 | -0.39825 | 120.9 | 0.14474 | -0.008469 | -0.012 | -0.034174 | 0.040843 | 0.081005 | -0.071874 | 120.7233 | 120.7265 | 120.7662 | 120.661 | 0.19016 | 0.32079 | 0.27327 | 0.26694 | 0.543 | 0.38978 | 0.38625 | 0.36408 | 0.4391 | 0.47926 | 0.32638 | 120.7691 | 120.7722 | 120.812 | 120.7068 | 0.23594 | 0.36657 | 0.31904 | 0.31272 | 120.5331 | 120.45 | 120.5761 | 120.493
1122.5312 | 121.4172 | -0.44861 | 120.8679 | 0.14017 | -0.008469 | -0.012 | -0.029595 | 0.040843 | 0.076426 | -0.076452 | 120.6958 | 120.6853 | 120.7296 | 120.6244 | 0.22221 | 0.362 | 0.30532 | 0.30814 | 0.58877 | 0.44014 | 0.43661 | 0.41901 | 0.48945 | 0.52503 | 0.37216 | 120.7416 | 120.731 | 120.7754 | 120.6702 | 0.26798 | 0.40777 | 0.35109 | 0.35392 | 120.4736 | 120.3905 | 120.5074 | 120.4243
1124.2969 | 121.4218 | -0.47607 | 120.8908 | 0.14932 | 0.000689 | -0.012 | -0.025017 | 0.036265 | 0.081005 | -0.071874 | 120.6684 | 120.6624 | 120.7021 | 120.5969 | 0.24968 | 0.38947 | 0.33737 | 0.33104 | 0.6254 | 0.47676 | 0.46407 | 0.45106 | 0.51234 | 0.55708 | 0.4042 | 120.7141 | 120.7081 | 120.7479 | 120.6427 | 0.29545 | 0.43524 | 0.38314 | 0.37681 | 120.4187 | 120.331 | 120.4525 | 120.3648
1126.0469 | 121.3898 | -0.48523 | 120.8633 | 0.14474 | -0.00389 | -0.007421 | -0.020438 | 0.040843 | 0.081005 | -0.067295 | 120.6592 | 120.6578 | 120.693 | 120.5969 | 0.2451 | 0.38031 | 0.33279 | 0.32646 | 0.62997 | 0.48134 | 0.47781 | 0.46479 | 0.52607 | 0.56623 | 0.41793 | 120.705 | 120.7036 | 120.7388 | 120.6427 | 0.29087 | 0.42608 | 0.37856 | 0.37223 | 120.4141 | 120.3264 | 120.4479 | 120.3602
1127.7344 | 121.4264 | -0.47607 | 120.8542 | 0.14017 | -0.00389 | -0.007421 | -0.029595 | 0.040843 | 0.085583 | -0.071874 | 120.6638 | 120.6532 | 120.7021 | 120.5878 | 0.24052 | 0.38031 | 0.33279 | 0.32188 | 0.61624 | 0.47218 | 0.46865 | 0.44648 | 0.51692 | 0.56166 | 0.4042 | 120.7096 | 120.699 | 120.7479 | 120.6335 | 0.2863 | 0.42608 | 0.37856 | 0.36766 | 120.4233 | 120.331 | 120.4616 | 120.3694
1129.4844 | 121.3303 | -0.54016 | 120.8725 | 0.14017 | -0.00389 | -0.016578 | -0.025017 | 0.045421 | 0.081005 | -0.071874 | 120.6409 | 120.6395 | 120.6884 | 120.5832 | 0.25883 | 0.39404 | 0.34652 | 0.33561 | 0.68033 | 0.53627 | 0.52358 | 0.51514 | 0.58558 | 0.62117 | 0.46829 | 120.6867 | 120.6853 | 120.7342 | 120.629 | 0.30461 | 0.43982 | 0.3923 | 0.38139 | 120.3821 | 120.2944 | 120.4296 | 120.3419
1131.1875 | 121.376 | -0.51727 | 120.8725 | 0.14932 | -0.00389 | -0.007421 | -0.034174 | 0.036265 | 0.085583 | -0.067295 | 120.6501 | 120.6486 | 120.693 | 120.5786 | 0.25425 | 0.39862 | 0.33279 | 0.34019 | 0.66659 | 0.51338 | 0.50985 | 0.4831 | 0.55354 | 0.60286 | 0.44998 | 120.6958 | 120.6944 | 120.7388 | 120.6244 | 0.30003 | 0.4444 | 0.37856 | 0.38597 | 120.3958 | 120.3173 | 120.4387 | 120.3602
1132.9375 | 121.3531 | -0.53558 | 120.845 | 0.14017 | -0.008469 | -0.012 | -0.029595 | 0.045421 | 0.081005 | -0.071874 | 120.6455 | 120.6349 | 120.6838 | 120.5649 | 0.25425 | 0.39862 | 0.34194 | 0.35393 | 0.67575 | 0.52711 | 0.52358 | 0.50599 | 0.581 | 0.61659 | 0.46371 | 120.6912 | 120.6807 | 120.7296 | 120.6106 | 0.30003 | 0.4444 | 0.38772 | 0.3997 | 120.3912 | 120.3035 | 120.4296 | 120.3419
1134.6875 | 121.4493 | -0.55389 | 120.7489 | 0.14474 | 0.000689 | -0.007421 | -0.034174 | 0.040843 | 0.090161 | -0.071874 | 120.6684 | 120.6624 | 120.7021 | 120.5969 | 0.35497 | 0.37115 | 0.32363 | 0.37224 | 0.69864 | 0.55458 | 0.54647 | 0.51972 | 0.59474 | 0.64406 | 0.48202 | 120.7141 | 120.7081 | 120.7479 | 120.6427 | 0.40075 | 0.41693 | 0.36941 | 0.41801 | 120.3134 | 120.3447 | 120.3472 | 120.3785
1136.4375 | 121.4539 | -0.60883 | 120.6894 | 0.14932 | -0.00389 | -0.007421 | -0.020438 | 0.049999 | 0.081005 | -0.062717 | 120.6546 | 120.6395 | 120.6884 | 120.574 | 0.36871 | 0.4032 | 0.34194 | 0.39513 | 0.75815 | 0.60494 | 0.6014 | 0.58839 | 0.65882 | 0.68983 | 0.54611 | 120.7004 | 120.6853 | 120.7342 | 120.6198 | 0.41448 | 0.44897 | 0.38772 | 0.4409 | 120.2859 | 120.3127 | 120.3197 | 120.3465
1138.125 | 121.4172 | -0.64087 | 120.7306 | 0.14474 | 0.000689 | -0.016578 | -0.029595 | 0.036265 | 0.081005 | -0.071874 | 120.6775 | 120.6669 | 120.7159 | 120.6061 | 0.34582 | 0.37573 | 0.31905 | 0.37224 | 0.78561 | 0.64156 | 0.62429 | 0.61127 | 0.67713 | 0.72187 | 0.569 | 120.7233 | 120.7127 | 120.7617 | 120.6518 | 0.39159 | 0.42151 | 0.36483 | 0.41801 | 120.3317 | 120.3585 | 120.3701 | 120.3968
1139.875 | 121.5179 | -0.42114 | 120.9045 | 0.14932 | -0.00389 | -0.012 | -0.025017 | 0.040843 | 0.076426 | -0.067295 | 120.7416 | 120.7952 | 120.78 | 120.6748 | 0.30919 | 0.32995 | 0.29158 | 0.32646 | 0.57046 | 0.41725 | 0.40914 | 0.39613 | 0.46199 | 0.49757 | 0.35385 | 120.7874 | 120.8409 | 120.8258 | 120.7205 | 0.35497 | 0.37573 | 0.33736 | 0.37223 | 120.4324 | 120.45 | 120.4708 | 120.4884
1141.6406 | 121.5179 | -0.49896 | 120.8817 | 0.14932 | -0.008469 | -0.012 | -0.025017 | 0.040843 | 0.081005 | -0.076452 | 120.8652 | 120.8547 | 120.8441 | 120.7434 | 0.24968 | 0.27959 | 0.27327 | 0.27152 | 0.64828 | 0.49049 | 0.48696 | 0.47395 | 0.5398 | 0.57997 | 0.42251 | 120.911 | 120.9005 | 120.8899 | 120.7892 | 0.29545 | 0.32537 | 0.31904 | 0.31729 | 120.6156 | 120.592 | 120.5944 | 120.5708
1143.3438 | 121.4127 | -0.36163 | 121.0281 | 0.14474 | -0.008469 | -0.012 | -0.020438 | 0.045421 | 0.090161 | -0.071874 | 120.6363 | 120.6303 | 120.6197 | 120.5008 | 0.46027 | 0.48561 | 0.41978 | 0.48669 | 0.50638 | 0.35316 | 0.34963 | 0.34119 | 0.40705 | 0.45179 | 0.28976 | 120.6821 | 120.6761 | 120.6655 | 120.5465 | 0.50605 | 0.53138 | 0.46555 | 0.53247 | 120.176 | 120.2165 | 120.1595 | 120.2
1145.0938 | 121.3715 | -4.5868 | 116.803 | 0.14474 | -0.017627 | -0.012 | -0.025017 | 0.040843 | 0.081005 | -0.067295 | 117.4039 | 117.3839 | 117.4104 | 117.2863 | 3.7108 | 3.704 | 3.6109 | 3.7051 | 4.7315 | 4.5692 | 4.5748 | 4.5618 | 4.6276 | 4.6678 | 4.5195 | 117.4497 | 117.4297 | 117.4561 | 117.3321 | 3.7565 | 3.7498 | 3.6567 | 3.7509 | 113.6931 | 113.793 | 113.6996 | 113.7995
1146.8594 | 121.4355 | -5.5984 | 115.7455 | 0.14932 | -0.00389 | -0.007421 | -0.029595 | 0.036265 | 0.076426 | -0.067295 | 116.2181 | 116.2026 | 116.2658 | 116.1507 | 4.8507 | 4.8668 | 4.8288 | 4.8543 | 5.7478 | 5.5946 | 5.591 | 5.5689 | 5.6347 | 5.6749 | 5.5312 | 116.2638 | 116.2484 | 116.3116 | 116.1965 | 4.8965 | 4.9126 | 4.8745 | 4.9 | 111.3673 | 111.3893 | 111.4151 | 111.437
1148.5625 | 121.3028 | -4.9896 | 116.3589 | 0.14017 | -0.013048 | -0.016578 | -0.025017 | 0.045421 | 0.081005 | -0.067295 | 116.2318 | 116.1797 | 116.2246 | 116.114 | 4.7958 | 4.8302 | 4.7601 | 4.8085 | 5.1298 | 4.9766 | 4.973 | 4.9646 | 5.035 | 5.0706 | 4.9223 | 116.2776 | 116.2255 | 116.2704 | 116.1598 | 4.8416 | 4.876 | 4.8059 | 4.8543 | 111.436 | 111.4717 | 111.4288 | 111.4645
1150.3125 | 121.3577 | -5.1132 | 116.0477 | 0.14932 | -0.008469 | -0.007421 | -0.029595 | 0.045421 | 0.081005 | -0.067295 | 116.3234 | 116.3262 | 116.3253 | 116.201 | 4.6447 | 4.6928 | 4.6273 | 4.6345 | 5.2625 | 5.1048 | 5.1058 | 5.0836 | 5.1586 | 5.1942 | 5.0459 | 116.3691 | 116.372 | 116.3711 | 116.2468 | 4.6905 | 4.7386 | 4.6731 | 4.6803 | 111.6787 | 111.6961 | 111.6806 | 111.698
1152.0625 | 121.2341 | -5.2139 | 116.0248 | 0.13559 | -0.008469 | -0.012 | -0.025017 | 0.045421 | 0.081005 | -0.071874 | 116.5752 | 116.4956 | 116.5588 | 116.4392 | 4.4341 | 4.4548 | 4.3892 | 4.4377 | 5.3495 | 5.2055 | 5.2019 | 5.1889 | 5.2593 | 5.2949 | 5.1421 | 116.621 | 116.5414 | 116.6046 | 116.4849 | 4.4799 | 4.5006 | 4.435 | 4.4834 | 112.1411 | 112.186 | 112.1247 | 112.1696
1153.8281 | 121.2708 | -0.10986 | 121.0144 | 0.14474 | 0.000689 | -0.007421 | -0.020438 | 0.040843 | 0.099318 | -0.071874 | 116.9003 | 116.9261 | 116.9022 | 116.8192 | 3.8435 | 3.9741 | 3.9131 | 3.9112 | 0.25461 | 0.11055 | 0.10244 | 0.089425 | 0.15071 | 0.20918 | 0.037989 | 116.946 | 116.9718 | 116.948 | 116.865 | 3.8893 | 4.0199 | 3.9589 | 3.9569 | 113.0567 | 112.9872 | 113.0586 | 112.9891
1155.5156 | 121.106 | -7.8964 | 113.2004 | 0.14474 | 0.000689 | -0.016578 | -0.025017 | 0.045421 | 0.09474 | -0.067295 | 112.3309 | 112.3289 | 112.3376 | 112.2585 | 8.4309 | 8.4698 | 8.3907 | 8.4481 | 8.0412 | 7.8971 | 7.8798 | 7.8714 | 7.9418 | 7.9912 | 7.8291 | 112.3767 | 112.3747 | 112.3834 | 112.3043 | 8.4766 | 8.5155 | 8.4365 | 8.4939 | 103.9001 | 103.9402 | 103.9068 | 103.9469
1157.25 | 121.1929 | -3.0533 | 117.8833 | 0.14017 | -0.00389 | -0.012 | -0.029595 | 0.040843 | 0.085583 | -0.067295 | 118.4066 | 118.3409 | 118.3764 | 118.2708 | 2.2366 | 2.3763 | 2.329 | 2.318 | 3.1934 | 3.0494 | 3.0413 | 3.0237 | 3.0941 | 3.1389 | 2.986 | 118.4524 | 118.3867 | 118.4222 | 118.3165 | 2.2824 | 2.4221 | 2.3747 | 2.3637 | 116.17 | 116.0776 | 116.1398 | 116.0474
1159.0156 | 120.7352 | -13.5727 | 107.0389 | 0.14474 | -0.008469 | -0.016578 | -0.034174 | 0.036265 | 0.081005 | -0.076452 | 110.353 | 110.328 | 110.3827 | 110.2987 | 10.1614 | 10.1499 | 10.0893 | 10.1375 | 13.7174 | 13.5642 | 13.5561 | 13.5385 | 13.609 | 13.6537 | 13.4962 | 110.3988 | 110.3738 | 110.4285 | 110.3444 | 10.2072 | 10.1957 | 10.1351 | 10.1833 | 100.1916 | 100.2637 | 100.2213 | 100.2934
1160.7812 | 120.845 | -9.1736 | 111.3373 | 0.15848 | -0.008469 | -0.016578 | -0.020438 | 0.036265 | 0.081005 | -0.071874 | 112.3355 | 112.306 | 112.3743 | 112.2631 | 8.0967 | 8.0989 | 8.0245 | 8.0727 | 9.3321 | 9.1651 | 9.157 | 9.1531 | 9.2098 | 9.2546 | 9.1017 | 112.3813 | 112.3518 | 112.42 | 112.3089 | 8.1424 | 8.1447 | 8.0703 | 8.1185 | 104.2388 | 104.311 | 104.2776 | 104.3498
1162.4688 | 120.5521 | -13.4949 | 106.8054 | 0.14932 | -0.00389 | -0.012 | -0.029595 | 0.040843 | 0.076426 | -0.08103 | 108.3247 | 108.3179 | 108.3728 | 108.261 | 11.9149 | 11.9262 | 11.8703 | 11.9092 | 13.6442 | 13.491 | 13.4829 | 13.4653 | 13.5357 | 13.5713 | 13.4138 | 108.3705 | 108.3637 | 108.4186 | 108.3068 | 11.9606 | 11.972 | 11.9161 | 11.955 | 96.4099 | 96.4544 | 96.458 | 96.5025
1164.2188 | 121.0648 | -116.3818 | 4.6234 | 0.14932 | -0.008469 | -0.016578 | -0.029595 | 0.036265 | 0.081005 | -0.062717 | 4.5211 | 4.6122 | 4.542 | 4.5185 | 116.224 | 116.2878 | 116.0973 | 116.1268 | 116.5312 | 116.3734 | 116.3653 | 116.3522 | 116.4181 | 116.4628 | 116.3191 | 4.5669 | 4.658 | 4.5878 | 4.5642 | 116.2697 | 116.3336 | 116.1431 | 116.1725 | -111.7029 | -111.5762 | -111.6819 | -111.5553
1165.9688 | 121.2296 | -116.629 | 4.3991 | 0.14017 | -0.008469 | -0.016578 | -0.029595 | 0.045421 | 0.076426 | -0.071874 | 4.3196 | 4.4108 | 4.3406 | 4.317 | 116.5124 | 116.5625 | 116.372 | 116.4106 | 116.7692 | 116.6206 | 116.6125 | 116.5994 | 116.6744 | 116.7055 | 116.5572 | 4.3654 | 4.4566 | 4.3863 | 4.3628 | 116.5582 | 116.6082 | 116.4178 | 116.4564 | -112.1927 | -112.0524 | -112.1718 | -112.0315
1167.6562 | 121.3074 | -116.5558 | 4.4495 | 0.14474 | -0.008469 | -0.016578 | -0.029595 | 0.036265 | 0.076426 | -0.067295 | 4.4478 | 4.539 | 4.4642 | 4.4406 | 116.4254 | 116.4755 | 116.2805 | 116.3191 | 116.7005 | 116.5473 | 116.5392 | 116.5262 | 116.5921 | 116.6322 | 116.4885 | 4.4936 | 4.5848 | 4.51 | 4.4864 | 116.4712 | 116.5213 | 116.3262 | 116.3648 | -111.9776 | -111.8326 | -111.9612 | -111.8163
1169.4062 | 121.3165 | -116.1758 | 4.8386 | 0.14017 | -0.00389 | -0.012 | -0.029595 | 0.031687 | 0.081005 | -0.062717 | 4.7912 | 4.8824 | 4.7663 | 4.7886 | 116.0958 | 116.155 | 115.7723 | 116.0032 | 116.316 | 116.172 | 116.1638 | 116.1462 | 116.2075 | 116.2568 | 116.1131 | 4.837 | 4.9282 | 4.8121 | 4.8344 | 116.1415 | 116.2008 | 115.818 | 116.0489 | -111.3045 | -110.981 | -111.3294 | -111.0059
1171.1562 | 121.3531 | -116.4505 | 4.6097 | 0.14017 | -0.00389 | -0.016578 | -0.029595 | 0.036265 | 0.085583 | -0.062717 | 4.5303 | 4.6122 | 4.5008 | 4.5185 | 116.3934 | 116.4434 | 116.1111 | 116.2916 | 116.5907 | 116.4466 | 116.4339 | 116.4209 | 116.4868 | 116.5361 | 116.3878 | 4.576 | 4.658 | 4.5466 | 4.5642 | 116.4391 | 116.4892 | 116.1568 | 116.3374 | -111.8631 | -111.5808 | -111.8925 | -111.6102
1172.9062 | 121.257 | -116.5375 | 4.5822 | 0.14474 | -0.008469 | -0.012 | -0.020438 | 0.040843 | 0.081005 | -0.071874 | 4.5577 | 4.6489 | 4.5741 | 4.5551 | 116.3659 | 116.4205 | 116.2026 | 116.2687 | 116.6822 | 116.529 | 116.5255 | 116.517 | 116.5783 | 116.6185 | 116.4656 | 4.6035 | 4.6947 | 4.6198 | 4.6009 | 116.4117 | 116.4663 | 116.2484 | 116.3145 | -111.8082 | -111.6449 | -111.7918 | -111.6286
1174.6094 | 121.3165 | -107.0847 | 13.9938 | 0.14474 | -0.008469 | -0.016578 | -0.029595 | 0.040843 | 0.081005 | -0.076452 | 16.0085 | 16.0959 | 16.0335 | 15.9844 | 104.8701 | 104.9159 | 104.7109 | 104.7912 | 107.2294 | 107.0762 | 107.0681 | 107.0551 | 107.1255 | 107.1657 | 107.0082 | 16.0543 | 16.1417 | 16.0793 | 16.0301 | 104.9159 | 104.9616 | 104.7566 | 104.837 | -88.8615 | -88.7023 | -88.8366 | -88.6774
1176.375 | 121.1975 | -1.3733 | 119.9707 | 0.14474 | -0.008469 | -0.012 | -0.029595 | 0.027109 | 0.090161 | -0.067295 | 119.684 | 119.6871 | 119.7224 | 119.6216 | 1.0509 | 1.2547 | 1.1752 | 1.1688 | 1.518 | 1.3648 | 1.3613 | 1.3437 | 1.4004 | 1.4635 | 1.306 | 119.7298 | 119.7329 | 119.7682 | 119.6674 | 1.0966 | 1.3005 | 1.221 | 1.2146 | 118.6331 | 118.5088 | 118.6715 | 118.5472
1178.0625 | 121.2433 | -1.1856 | 120.1263 | 0.14474 | -0.008469 | -0.012 | -0.029595 | 0.040843 | 0.085583 | -0.071874 | 119.8763 | 119.8748 | 119.9055 | 119.7956 | 0.89978 | 1.0945 | 1.0195 | 1.0178 | 1.3304 | 1.1771 | 1.1736 | 1.156 | 1.2265 | 1.2712 | 1.1137 | 119.9221 | 119.9206 | 119.9513 | 119.8414 | 0.94555 | 1.1403 | 1.0653 | 1.0635 | 118.9765 | 118.8567 | 119.0057 | 118.886
1179.8125 | 121.2982 | -0.9201 | 120.4147 | 0.1539 | -0.00389 | -0.012 | -0.025017 | 0.040843 | 0.081005 | -0.067295 | 120.1693 | 120.1724 | 120.2123 | 120.1161 | 0.61593 | 0.81522 | 0.74484 | 0.72934 | 1.074 | 0.91622 | 0.9081 | 0.89509 | 0.96095 | 1.0011 | 0.85281 | 120.2151 | 120.2182 | 120.258 | 120.1619 | 0.6617 | 0.861 | 0.79062 | 0.77511 | 119.5534 | 119.4245 | 119.5963 | 119.4674
1181.5625 | 121.3806 | -1.03 | 120.2591 | 0.13101 | -0.013048 | -0.012 | -0.025017 | 0.040843 | 0.085583 | -0.067295 | 120.0777 | 120.0809 | 120.1207 | 120.0108 | 0.72123 | 0.92968 | 0.85014 | 0.84379 | 1.161 | 1.0169 | 1.018 | 1.005 | 1.0708 | 1.1156 | 0.96267 | 120.1235 | 120.1266 | 120.1665 | 120.0566 | 0.767 | 0.97545 | 0.89592 | 0.88957 | 119.3565 | 119.2276 | 119.3995 | 119.2706
1183.3125 | 121.3303 | -2.2156 | 119.0735 | 0.14474 | -0.008469 | -0.016578 | -0.034174 | 0.040843 | 0.085583 | -0.067295 | 118.8278 | 118.8354 | 118.8022 | 118.7058 | 2.0352 | 2.239 | 2.1458 | 2.1577 | 2.3603 | 2.2071 | 2.199 | 2.1814 | 2.2564 | 2.3012 | 2.1483 | 118.8736 | 118.8812 | 118.8479 | 118.7516 | 2.0809 | 2.2848 | 2.1916 | 2.2035 | 116.7926 | 116.682 | 116.767 | 116.6563
1185.0938 | 121.3394 | -1.2955 | 120.0394 | 0.14474 | -0.008469 | -0.012 | -0.025017 | 0.045421 | 0.081005 | -0.067295 | 119.9083 | 119.9069 | 119.8826 | 119.7773 | 0.98218 | 1.186 | 1.102 | 1.0956 | 1.4402 | 1.287 | 1.2835 | 1.2705 | 1.3409 | 1.3765 | 1.2282 | 119.9541 | 119.9526 | 119.9284 | 119.823 | 1.028 | 1.2318 | 1.1477 | 1.1414 | 118.9262 | 118.8064 | 118.9005 | 118.7807
1186.8438 | 121.3394 | -1.1398 | 120.2454 | 0.14932 | 0.005267 | -0.007421 | -0.029595 | 0.040843 | 0.09474 | -0.076452 | 120.1052 | 120.1083 | 120.0749 | 119.9833 | 0.7899 | 0.99377 | 0.90509 | 0.90789 | 1.2892 | 1.1451 | 1.1324 | 1.1102 | 1.1807 | 1.2346 | 1.0634 | 120.151 | 120.1541 | 120.1207 | 120.0291 | 0.83568 | 1.0395 | 0.95086 | 0.95366 | 119.3153 | 119.2001 | 119.285 | 119.1698
1188.5312 | 121.3028 | -1.0345 | 120.3964 | 0.14474 | 0.005267 | -0.016578 | -0.025017 | 0.045421 | 0.085583 | -0.076452 | 120.2059 | 120.2182 | 120.1894 | 120.0932 | 0.69376 | 0.89763 | 0.81352 | 0.80259 | 1.1793 | 1.0398 | 1.018 | 1.0095 | 1.08 | 1.1201 | 0.95809 | 120.2517 | 120.264 | 120.2352 | 120.139 | 0.73953 | 0.94341 | 0.85929 | 0.84836 | 119.5122 | 119.3924 | 119.4956 | 119.3759
1190.2969 | 121.344 | -0.97961 | 120.4376 | 0.14474 | -0.00389 | -0.007421 | -0.025017 | 0.040843 | 0.081005 | -0.071874 | 120.2655 | 120.2549 | 120.2397 | 120.1344 | 0.65255 | 0.85185 | 0.78147 | 0.76596 | 1.1244 | 0.97572 | 0.97219 | 0.9546 | 1.0205 | 1.0606 | 0.90774 | 120.3112 | 120.3006 | 120.2855 | 120.1802 | 0.69833 | 0.89763 | 0.82725 | 0.81174 | 119.6129 | 119.484 | 119.5872 | 119.4583
1192.0625 | 121.4905 | -0.92926 | 120.4102 | 0.14474 | 0.000689 | -0.012 | -0.029595 | 0.045421 | 0.085583 | -0.076452 | 120.2792 | 120.2777 | 120.2581 | 120.1527 | 0.6434 | 0.85185 | 0.77231 | 0.7568 | 1.074 | 0.92995 | 0.91726 | 0.89966 | 0.97468 | 1.0148 | 0.85281 | 120.325 | 120.3235 | 120.3038 | 120.1985 | 0.68917 | 0.89763 | 0.81809 | 0.80258 | 119.6358 | 119.5069 | 119.6147 | 119.4857
1193.8438 | 121.431 | -0.97046 | 120.4285 | 0.14017 | -0.00389 | -0.012 | -0.034174 | 0.036265 | 0.081005 | -0.071874 | 120.2838 | 120.2777 | 120.2489 | 120.1573 | 0.64798 | 0.86101 | 0.78147 | 0.77512 | 1.1106 | 0.96657 | 0.95846 | 0.93628 | 1.0067 | 1.0515 | 0.89858 | 120.3295 | 120.3235 | 120.2947 | 120.2031 | 0.69375 | 0.90678 | 0.82725 | 0.82089 | 119.6358 | 119.5023 | 119.6009 | 119.4674
1195.5312 | 121.4081 | -1.0117 | 120.4147 | 0.14474 | 0.000689 | -0.012 | -0.020438 | 0.036265 | 0.085583 | -0.076452 | 120.27 | 120.264 | 120.2397 | 120.1436 | 0.67544 | 0.8839 | 0.80436 | 0.79343 | 1.1564 | 1.0123 | 0.99966 | 0.99122 | 1.0479 | 1.0972 | 0.93521 | 120.3158 | 120.3098 | 120.2855 | 120.1894 | 0.72122 | 0.92967 | 0.85014 | 0.83921 | 119.5946 | 119.4657 | 119.5643 | 119.4354
1197.2656 | 121.4081 | -1.0117 | 120.4102 | 0.14932 | -0.00389 | -0.021157 | -0.025017 | 0.040843 | 0.085583 | -0.071874 | 120.2883 | 120.2869 | 120.2672 | 120.1619 | 0.65255 | 0.86558 | 0.77689 | 0.77054 | 1.161 | 1.0078 | 0.9905 | 0.98664 | 1.0525 | 1.0972 | 0.93978 | 120.3341 | 120.3327 | 120.313 | 120.2077 | 0.69833 | 0.91136 | 0.82267 | 0.81632 | 119.6358 | 119.5115 | 119.6147 | 119.4903
1198.9531 | 121.3943 | -1.0391 | 120.3964 | 0.14474 | -0.00389 | -0.007421 | -0.025017 | 0.036265 | 0.085583 | -0.067295 | 120.2517 | 120.2411 | 120.226 | 120.1161 | 0.69834 | 0.90679 | 0.82725 | 0.82548 | 1.1839 | 1.0352 | 1.0317 | 1.0141 | 1.0754 | 1.1247 | 0.97183 | 120.2975 | 120.2869 | 120.2718 | 120.1619 | 0.74411 | 0.95256 | 0.87303 | 0.87125 | 119.5534 | 119.4245 | 119.5277 | 119.3988
1200.7031 | 121.4767 | -1.0483 | 120.3461 | 0.14474 | 0.005267 | -0.016578 | -0.029595 | 0.036265 | 0.081005 | -0.071874 | 120.2243 | 120.2228 | 120.2031 | 120.0886 | 0.73496 | 0.93425 | 0.86388 | 0.84837 | 1.193 | 1.0535 | 1.0317 | 1.0187 | 1.0845 | 1.1293 | 0.9764 | 120.27 | 120.2686 | 120.2489 | 120.1344 | 0.78074 | 0.98003 | 0.90966 | 0.89414 | 119.4893 | 119.3604 | 119.4682 | 119.3392
1202.4688 | 121.5454 | -1.2451 | 120.1263 | 0.14017 | -0.00389 | -0.016578 | -0.034174 | 0.040843 | 0.090161 | -0.08103 | 120.0136 | 120.0076 | 119.9925 | 119.8826 | 0.95471 | 1.1494 | 1.0745 | 1.0681 | 1.3853 | 1.2412 | 1.2285 | 1.2109 | 1.286 | 1.3353 | 1.1641 | 120.0594 | 120.0534 | 120.0383 | 119.9284 | 1.0005 | 1.1952 | 1.1203 | 1.1139 | 119.0589 | 118.9392 | 119.0378 | 118.918
1204.1719 | 121.4493 | -1.6251 | 119.7968 | 0.14017 | 0.000689 | -0.012 | -0.029595 | 0.036265 | 0.085583 | -0.071874 | 119.6931 | 119.6871 | 119.6675 | 119.5621 | 1.2752 | 1.4745 | 1.395 | 1.3886 | 1.7652 | 1.6258 | 1.6131 | 1.5955 | 1.6613 | 1.7106 | 1.5532 | 119.7389 | 119.7329 | 119.7132 | 119.6078 | 1.321 | 1.5202 | 1.4407 | 1.4344 | 118.418 | 118.2982 | 118.3923 | 118.2725
1205.9375 | 121.4905 | -1.7258 | 119.6365 | 0.14017 | -0.008469 | -0.012 | -0.029595 | 0.040843 | 0.081005 | -0.067295 | 119.5787 | 119.5772 | 119.553 | 119.4476 | 1.3942 | 1.5981 | 1.5094 | 1.5122 | 1.8659 | 1.7173 | 1.7138 | 1.6962 | 1.7666 | 1.8068 | 1.6585 | 119.6245 | 119.623 | 119.5988 | 119.4934 | 1.44 | 1.6439 | 1.5552 | 1.558 | 118.1845 | 118.0693 | 118.1588 | 118.0436
1207.6406 | 121.5042 | -2.2385 | 119.1605 | 0.14017 | 0.000689 | -0.016578 | -0.029595 | 0.036265 | 0.076426 | -0.071874 | 119.0522 | 119.0506 | 119.0357 | 118.9256 | 1.9299 | 2.1291 | 2.0359 | 2.0341 | 2.3786 | 2.2392 | 2.2219 | 2.2089 | 2.2747 | 2.3149 | 2.1666 | 119.0979 | 119.0964 | 119.0814 | 118.9713 | 1.9756 | 2.1749 | 2.0817 | 2.0799 | 117.1223 | 117.0162 | 117.1058 | 116.9997
1209.3906 | 121.4813 | -2.4216 | 119.0094 | 0.14474 | 0.005267 | -0.012 | -0.025017 | 0.031687 | 0.085583 | -0.071874 | 118.8919 | 118.8812 | 118.8617 | 118.7561 | 2.0947 | 2.3077 | 2.2053 | 2.1989 | 2.5663 | 2.4268 | 2.4096 | 2.3966 | 2.4533 | 2.5072 | 2.3497 | 118.9377 | 118.927 | 118.9075 | 118.8019 | 2.1405 | 2.3535 | 2.2511 | 2.2447 | 116.7972 | 116.6866 | 116.767 | 116.6563
1211.1562 | 121.5637 | -2.6184 | 118.7851 | 0.14932 | 0.000689 | -0.016578 | -0.025017 | 0.036265 | 0.085583 | -0.071874 | 118.7042 | 118.6981 | 118.6785 | 118.5592 | 2.287 | 2.4908 | 2.4022 | 2.4004 | 2.7677 | 2.6191 | 2.6018 | 2.5934 | 2.6547 | 2.704 | 2.5465 | 118.75 | 118.7438 | 118.7243 | 118.605 | 2.3327 | 2.5366 | 2.448 | 2.4461 | 116.4172 | 116.302 | 116.3916 | 116.2763
1212.9062 | 121.5179 | -2.6276 | 118.7759 | 0.14017 | 0.000689 | -0.012 | -0.025017 | 0.045421 | 0.076426 | -0.062717 | 118.7317 | 118.7347 | 118.706 | 118.605 | 2.2641 | 2.4633 | 2.3702 | 2.3729 | 2.7677 | 2.6283 | 2.6156 | 2.6025 | 2.673 | 2.704 | 2.5648 | 118.7774 | 118.7805 | 118.7518 | 118.6508 | 2.3098 | 2.5091 | 2.4159 | 2.4187 | 116.4676 | 116.3615 | 116.4419 | 116.3358
1214.6562 | 121.5088 | -2.6184 | 118.7851 | 0.14474 | -0.00389 | -0.021157 | -0.020438 | 0.040843 | 0.071848 | -0.071874 | 118.6813 | 118.6706 | 118.6557 | 118.5547 | 2.3099 | 2.5274 | 2.4251 | 2.4278 | 2.7632 | 2.6145 | 2.5973 | 2.598 | 2.6593 | 2.6903 | 2.5465 | 118.7271 | 118.7164 | 118.7014 | 118.6004 | 2.3556 | 2.5732 | 2.4709 | 2.4736 | 116.3714 | 116.2562 | 116.3458 | 116.2305
1216.3438 | 121.5591 | -2.6825 | 118.7302 | 0.14474 | -0.00389 | -0.016578 | -0.029595 | 0.031687 | 0.085583 | -0.076452 | 118.6218 | 118.6294 | 118.6007 | 118.4997 | 2.3648 | 2.5732 | 2.4892 | 2.4828 | 2.8272 | 2.6786 | 2.6659 | 2.6529 | 2.7142 | 2.7681 | 2.606 | 118.6676 | 118.6751 | 118.6465 | 118.5455 | 2.4106 | 2.619 | 2.535 | 2.5286 | 116.257 | 116.1326 | 116.2359 | 116.1115
1218.0938 | 121.4539 | -2.6733 | 118.7897 | 0.15848 | 0.000689 | -0.012 | -0.020438 | 0.049999 | 0.081005 | -0.071874 | 118.6721 | 118.666 | 118.6465 | 118.5455 | 2.3327 | 2.5457 | 2.448 | 2.4462 | 2.8318 | 2.674 | 2.6613 | 2.6529 | 2.7233 | 2.7543 | 2.6015 | 118.7179 | 118.7118 | 118.6923 | 118.5913 | 2.3785 | 2.5915 | 2.4938 | 2.4919 | 116.3394 | 116.2241 | 116.3138 | 116.1985
1219.8594 | 121.4447 | -2.6413 | 118.8309 | 0.14932 | 0.000689 | -0.012 | -0.020438 | 0.036265 | 0.085583 | -0.076452 | 118.7088 | 118.6935 | 118.6785 | 118.573 | 2.3144 | 2.5137 | 2.4251 | 2.4278 | 2.7906 | 2.642 | 2.6293 | 2.6209 | 2.6776 | 2.7269 | 2.5648 | 118.7545 | 118.7393 | 118.7243 | 118.6188 | 2.3602 | 2.5595 | 2.4709 | 2.4736 | 116.3943 | 116.2837 | 116.3641 | 116.2534
1221.5625 | 121.431 | -2.742 | 118.7485 | 0.14932 | 0.005267 | -0.012 | -0.034174 | 0.036265 | 0.081005 | -0.071874 | 118.6309 | 118.6248 | 118.6007 | 118.4951 | 2.3877 | 2.5915 | 2.5029 | 2.5011 | 2.8913 | 2.7473 | 2.73 | 2.7078 | 2.7783 | 2.823 | 2.6701 | 118.6767 | 118.6706 | 118.6465 | 118.5409 | 2.4335 | 2.6373 | 2.5487 | 2.5469 | 116.2433 | 116.128 | 116.213 | 116.0978
1223.3281 | 121.4813 | -2.7969 | 118.7027 | 0.14474 | 0.000689 | -0.016578 | -0.025017 | 0.045421 | 0.076426 | -0.071874 | 118.5577 | 118.5515 | 118.5366 | 118.4265 | 2.4609 | 2.6648 | 2.5716 | 2.5698 | 2.9417 | 2.7976 | 2.7804 | 2.7719 | 2.8424 | 2.8734 | 2.7251 | 118.6035 | 118.5973 | 118.5824 | 118.4722 | 2.5067 | 2.7105 | 2.6174 | 2.6155 | 116.0967 | 115.9861 | 116.0757 | 115.965
1225.0938 | 121.5775 | -3.2455 | 118.1992 | 0.14474 | 0.000689 | -0.012 | -0.025017 | 0.045421 | 0.076426 | -0.071874 | 118.0724 | 118.0616 | 118.0467 | 117.9365 | 2.9462 | 3.1592 | 3.0615 | 3.0596 | 3.3903 | 3.2462 | 3.2335 | 3.2205 | 3.291 | 3.322 | 3.1737 | 118.1181 | 118.1074 | 118.0925 | 117.9823 | 2.992 | 3.205 | 3.1073 | 3.1054 | 115.1261 | 115.0109 | 115.1005 | 114.9852
1226.8438 | 121.4859 | -3.6987 | 117.8192 | 0.14474 | 0.000689 | -0.012 | -0.029595 | 0.040843 | 0.081005 | -0.067295 | 117.7427 | 117.7411 | 117.7217 | 117.6205 | 3.285 | 3.4842 | 3.3912 | 3.3893 | 3.8435 | 3.6994 | 3.6867 | 3.6691 | 3.7396 | 3.7797 | 3.6314 | 117.7885 | 117.7869 | 117.7675 | 117.6663 | 3.3308 | 3.53 | 3.4369 | 3.435 | 114.4577 | 114.3516 | 114.4367 | 114.3305
1228.5469 | 121.4813 | -3.6713 | 117.8284 | 0.14474 | -0.00389 | -0.016578 | -0.029595 | 0.036265 | 0.085583 | -0.076452 | 117.7107 | 117.7045 | 117.6896 | 117.5839 | 3.3171 | 3.5209 | 3.4278 | 3.4259 | 3.816 | 3.6674 | 3.6547 | 3.6417 | 3.7075 | 3.7568 | 3.5948 | 117.7564 | 117.7502 | 117.7354 | 117.6297 | 3.3628 | 3.5666 | 3.4736 | 3.4717 | 114.3936 | 114.2829 | 114.3726 | 114.2619
1230.3125 | 121.5225 | -3.6987 | 117.8192 | 0.14474 | 0.005267 | -0.007421 | -0.025017 | 0.040843 | 0.081005 | -0.071874 | 117.6603 | 117.6587 | 117.6439 | 117.5381 | 3.3674 | 3.5712 | 3.4736 | 3.4762 | 3.8435 | 3.704 | 3.6913 | 3.6737 | 3.7396 | 3.7797 | 3.6269 | 117.7061 | 117.7044 | 117.6896 | 117.5839 | 3.4132 | 3.617 | 3.5193 | 3.522 | 114.2929 | 114.1867 | 114.2764 | 114.1703
1232.0781 | 121.5134 | -3.6804 | 117.8238 | 0.13559 | -0.00389 | -0.012 | -0.025017 | 0.036265 | 0.081005 | -0.067295 | 117.7061 | 117.6999 | 117.6851 | 117.5748 | 3.3308 | 3.5438 | 3.4415 | 3.4442 | 3.816 | 3.6765 | 3.6684 | 3.6554 | 3.7167 | 3.7614 | 3.6131 | 117.7519 | 117.7456 | 117.7308 | 117.6205 | 3.3766 | 3.5895 | 3.4873 | 3.49 | 114.3753 | 114.2646 | 114.3543 | 114.2435
1233.8438 | 121.5546 | -3.0487 | 118.3731 | 0.14474 | 0.005267 | -0.016578 | -0.020438 | 0.040843 | 0.081005 | -0.071874 | 118.2921 | 118.2997 | 118.2665 | 118.1654 | 2.7448 | 2.9532 | 2.8601 | 2.8536 | 3.1934 | 3.054 | 3.0321 | 3.0283 | 3.0895 | 3.1297 | 2.9768 | 118.3379 | 118.3455 | 118.3123 | 118.2112 | 2.7906 | 2.999 | 2.9058 | 2.8994 | 115.5473 | 115.4321 | 115.5217 | 115.4064
1235.5312 | 121.4676 | -2.9572 | 118.5471 | 0.14474 | 0.000689 | -0.012 | -0.025017 | 0.040843 | 0.081005 | -0.062717 | 118.4157 | 118.4096 | 118.3855 | 118.2845 | 2.6303 | 2.8479 | 2.7548 | 2.7437 | 3.1019 | 2.9578 | 2.9452 | 2.9321 | 2.998 | 3.0382 | 2.8944 | 118.4615 | 118.4554 | 118.4313 | 118.3303 | 2.6761 | 2.8937 | 2.8005 | 2.7895 | 115.7854 | 115.661 | 115.7552 | 115.6308
1237.2812 | 121.6049 | -2.9617 | 118.4601 | 0.14474 | -0.008469 | -0.021157 | -0.034174 | 0.040843 | 0.085583 | -0.071874 | 118.4936 | 118.4874 | 118.4679 | 118.3623 | 2.5525 | 2.7609 | 2.6769 | 2.6705 | 3.1065 | 2.9533 | 2.9406 | 2.9276 | 3.0026 | 3.0473 | 2.8899 | 118.5394 | 118.5332 | 118.5137 | 118.4081 | 2.5983 | 2.8067 | 2.7227 | 2.7163 | 115.9411 | 115.8167 | 115.9154 | 115.791
1239.0312 | 121.4859 | -3.2547 | 118.2816 | 0.14017 | 0.000689 | -0.012 | -0.020438 | 0.045421 | 0.081005 | -0.071874 | 118.0953 | 118.0891 | 118.0742 | 117.9731 | 2.9554 | 3.1638 | 3.0661 | 3.0688 | 3.3949 | 3.2554 | 3.2427 | 3.2343 | 3.3001 | 3.3357 | 3.1828 | 118.141 | 118.1348 | 118.12 | 118.0189 | 3.0012 | 3.2095 | 3.1119 | 3.1146 | 115.1399 | 115.0292 | 115.1188 | 115.0081
1240.7344 | 121.5454 | -3.3417 | 118.1717 | 0.14474 | 0.000689 | -0.016578 | -0.025017 | 0.036265 | 0.085583 | -0.067295 | 118.0174 | 118.0204 | 117.9964 | 117.8907 | 3.0424 | 3.2508 | 3.1485 | 3.1558 | 3.4864 | 3.3424 | 3.3251 | 3.3167 | 3.3779 | 3.4273 | 3.2744 | 118.0632 | 118.0662 | 118.0422 | 117.9365 | 3.0881 | 3.2965 | 3.1943 | 3.2015 | 114.9751 | 114.8689 | 114.954 | 114.8479
1242.4844 | 121.637 | -3.0487 | 118.3777 | 0.14474 | -0.00389 | -0.012 | -0.029595 | 0.045421 | 0.090161 | -0.067295 | 118.2509 | 118.2585 | 118.239 | 118.1334 | 2.8043 | 3.0081 | 2.9104 | 2.9131 | 3.1934 | 3.0448 | 3.0367 | 3.0191 | 3.0941 | 3.1389 | 2.9814 | 118.2967 | 118.3043 | 118.2848 | 118.1792 | 2.8501 | 3.0539 | 2.9562 | 2.9589 | 115.4466 | 115.3405 | 115.4347 | 115.3286
1244.25 | 121.6049 | -2.9068 | 118.5562 | 0.14017 | 0.005267 | -0.012 | -0.025017 | 0.036265 | 0.081005 | -0.076452 | 118.4524 | 118.4554 | 118.4359 | 118.3257 | 2.612 | 2.8113 | 2.7227 | 2.7208 | 3.047 | 2.9121 | 2.8948 | 2.8818 | 2.9431 | 2.9878 | 2.8303 | 118.4981 | 118.5012 | 118.4817 | 118.3715 | 2.6578 | 2.857 | 2.7685 | 2.7666 | 115.8404 | 115.7297 | 115.8239 | 115.7132
1246.0156 | 121.6095 | -2.9572 | 118.4875 | 0.1539 | -0.00389 | -0.007421 | -0.020438 | 0.036265 | 0.081005 | -0.071874 | 118.402 | 118.405 | 118.381 | 118.2799 | 2.6624 | 2.8708 | 2.7822 | 2.7804 | 3.1111 | 2.9533 | 2.9497 | 2.9367 | 2.9934 | 3.0382 | 2.8853 | 118.4478 | 118.4508 | 118.4267 | 118.3257 | 2.7081 | 2.9166 | 2.828 | 2.8261 | 115.7396 | 115.6198 | 115.7186 | 115.5987
1247.7031 | 121.5134 | -3.0853 | 118.4372 | 0.14474 | 0.000689 | -0.012 | -0.025017 | 0.045421 | 0.090161 | -0.067295 | 118.3196 | 118.3134 | 118.2986 | 118.1838 | 2.7539 | 2.9623 | 2.8692 | 2.8673 | 3.2301 | 3.086 | 3.0733 | 3.0603 | 3.1307 | 3.1755 | 3.018 | 118.3654 | 118.3592 | 118.3443 | 118.2295 | 2.7997 | 3.0081 | 2.915 | 2.9131 | 115.5657 | 115.4504 | 115.5446 | 115.4293
1249.4531 | 121.4996 | -3.241 | 118.3044 | 0.14474 | 0.000689 | -0.002842 | -0.025017 | 0.040843 | 0.085583 | -0.067295 | 118.1822 | 118.1806 | 118.1612 | 118.051 | 2.8913 | 3.1088 | 3.002 | 3.0047 | 3.3857 | 3.2417 | 3.2381 | 3.2159 | 3.2818 | 3.3266 | 3.1737 | 118.228 | 118.2264 | 118.207 | 118.0968 | 2.9371 | 3.1546 | 3.0478 | 3.0505 | 115.291 | 115.1803 | 115.2699 | 115.1592
1251.2344 | 121.5546 | -3.4058 | 118.1259 | 0.14474 | -0.00389 | -0.012 | -0.029595 | 0.045421 | 0.081005 | -0.071874 | 117.9945 | 117.9838 | 117.9735 | 117.8678 | 3.0836 | 3.2965 | 3.1943 | 3.1924 | 3.5505 | 3.4019 | 3.3938 | 3.3762 | 3.4512 | 3.4868 | 3.3339 | 118.0403 | 118.0295 | 118.0193 | 117.9136 | 3.1293 | 3.3423 | 3.2401 | 3.2382 | 114.911 | 114.8002 | 114.8899 | 114.7792
1252.9844 | 121.637 | -3.3508 | 118.1213 | 0.14932 | -0.00389 | -0.007421 | -0.025017 | 0.040843 | 0.081005 | -0.071874 | 118.0357 | 118.0387 | 118.0193 | 117.9044 | 3.0424 | 3.2553 | 3.1531 | 3.142 | 3.5002 | 3.3469 | 3.3434 | 3.3258 | 3.3917 | 3.4318 | 3.279 | 118.0815 | 118.0845 | 118.0651 | 117.9502 | 3.0881 | 3.3011 | 3.1988 | 3.1878 | 114.9934 | 114.8827 | 114.9769 | 114.8662
1254.6875 | 121.6415 | -3.2135 | 118.277 | 0.14017 | 0.000689 | -0.012 | -0.034174 | 0.040843 | 0.081005 | -0.062717 | 118.1639 | 118.1578 | 118.1383 | 118.0327 | 2.9188 | 3.1271 | 3.034 | 3.0276 | 3.3537 | 3.2142 | 3.2015 | 3.1793 | 3.2543 | 3.2945 | 3.1508 | 118.2097 | 118.2035 | 118.1841 | 118.0784 | 2.9645 | 3.1729 | 3.0798 | 3.0734 | 115.2452 | 115.1299 | 115.2196 | 115.1043
1256.4531 | 121.5408 | -3.0121 | 118.5471 | 0.14932 | 0.005267 | -0.007421 | -0.025017 | 0.045421 | 0.081005 | -0.067295 | 118.4203 | 118.4279 | 118.4039 | 118.2891 | 2.6624 | 2.8662 | 2.7685 | 2.7804 | 3.1614 | 3.0174 | 3.0047 | 2.9871 | 3.0575 | 3.0931 | 2.9448 | 118.4661 | 118.4737 | 118.4496 | 118.3349 | 2.7081 | 2.912 | 2.8143 | 2.8261 | 115.758 | 115.6518 | 115.7415 | 115.6354
1258.2031 | 121.55 | -2.9022 | 118.6752 | 0.14474 | -0.00389 | -0.012 | -0.025017 | 0.040843 | 0.081005 | -0.071874 | 118.5165 | 118.5103 | 118.5 | 118.3944 | 2.5754 | 2.7838 | 2.6907 | 2.6888 | 3.047 | 2.8983 | 2.8902 | 2.8772 | 2.9431 | 2.9832 | 2.8303 | 118.5622 | 118.5561 | 118.5458 | 118.4402 | 2.6212 | 2.8296 | 2.7364 | 2.7346 | 115.9411 | 115.8258 | 115.9246 | 115.8093
1259.9531 | 121.5088 | -2.8519 | 118.7393 | 0.14474 | -0.008469 | -0.007421 | -0.025017 | 0.040843 | 0.085583 | -0.071874 | 118.5714 | 118.5744 | 118.5549 | 118.4402 | 2.5159 | 2.7289 | 2.6357 | 2.6339 | 2.9966 | 2.8434 | 2.8444 | 2.8269 | 2.8927 | 2.9375 | 2.78 | 118.6172 | 118.6202 | 118.6007 | 118.486 | 2.5616 | 2.7746 | 2.6815 | 2.6796 | 116.0555 | 115.9357 | 116.0391 | 115.9192
1261.6562 | 121.5775 | -2.7374 | 118.8126 | 0.14474 | 0.005267 | -0.012 | -0.025017 | 0.049999 | 0.085583 | -0.071874 | 118.6905 | 118.6843 | 118.6694 | 118.5638 | 2.4152 | 2.6144 | 2.5213 | 2.5148 | 2.8822 | 2.7427 | 2.7254 | 2.7124 | 2.7874 | 2.823 | 2.6656 | 118.7362 | 118.7301 | 118.7152 | 118.6096 | 2.4609 | 2.6602 | 2.567 | 2.5606 | 116.2753 | 116.1692 | 116.2542 | 116.1481
1263.3906 | 121.6461 | -2.7008 | 118.8034 | 0.14932 | -0.008469 | -0.007421 | -0.025017 | 0.040843 | 0.076426 | -0.071874 | 118.6996 | 118.7026 | 118.6785 | 118.5684 | 2.4014 | 2.6144 | 2.5121 | 2.5148 | 2.8501 | 2.6923 | 2.6934 | 2.6758 | 2.7416 | 2.7772 | 2.6289 | 118.7454 | 118.7484 | 118.7243 | 118.6142 | 2.4472 | 2.6602 | 2.5579 | 2.5606 | 116.2982 | 116.1875 | 116.2771 | 116.1664
1265.1562 | 121.6003 | -2.6001 | 118.9407 | 0.14932 | 0.000689 | -0.012 | -0.025017 | 0.031687 | 0.081005 | -0.071874 | 118.8232 | 118.8217 | 118.8022 | 118.6875 | 2.2778 | 2.5 | 2.4068 | 2.4049 | 2.7494 | 2.6008 | 2.5881 | 2.5751 | 2.6318 | 2.6811 | 2.5282 | 118.869 | 118.8675 | 118.8479 | 118.7332 | 2.3236 | 2.5457 | 2.4526 | 2.4507 | 116.5454 | 116.4164 | 116.5244 | 116.3954
1266.9219 | 121.6782 | -2.449 | 119.014 | 0.14474 | 0.000689 | -0.016578 | -0.025017 | 0.045421 | 0.081005 | -0.071874 | 118.9743 | 118.9682 | 118.9441 | 118.8386 | 2.1405 | 2.3489 | 2.2557 | 2.2493 | 2.5938 | 2.4497 | 2.4325 | 2.424 | 2.4945 | 2.53 | 2.3772 | 119.0201 | 119.014 | 118.9899 | 118.8843 | 2.1862 | 2.3947 | 2.3015 | 2.2951 | 116.8339 | 116.7186 | 116.8036 | 116.6884
1268.625 | 121.6324 | -2.623 | 118.9041 | 0.14474 | -0.008469 | -0.016578 | -0.029595 | 0.045421 | 0.090161 | -0.071874 | 118.7912 | 118.7805 | 118.7747 | 118.66 | 2.319 | 2.5274 | 2.4297 | 2.437 | 2.7677 | 2.6145 | 2.6064 | 2.5934 | 2.6684 | 2.7131 | 2.5511 | 118.837 | 118.8263 | 118.8205 | 118.7058 | 2.3648 | 2.5732 | 2.4755 | 2.4828 | 116.4722 | 116.3615 | 116.4557 | 116.345
1270.3906 | 121.637 | -2.504 | 119.014 | 0.14932 | 0.005267 | -0.012 | -0.025017 | 0.040843 | 0.081005 | -0.076452 | 118.9194 | 118.9133 | 118.8937 | 118.7928 | 2.2 | 2.4084 | 2.3152 | 2.318 | 2.6533 | 2.5092 | 2.492 | 2.4789 | 2.5448 | 2.585 | 2.4275 | 118.9652 | 118.959 | 118.9395 | 118.8386 | 2.2458 | 2.4542 | 2.361 | 2.3637 | 116.7194 | 116.6042 | 116.6937 | 116.5785
1272.1562 | 121.6415 | -2.179 | 119.3344 | 0.14932 | -0.00389 | -0.016578 | -0.029595 | 0.040843 | 0.081005 | -0.071874 | 119.2261 | 119.2155 | 119.2096 | 119.0996 | 1.8932 | 2.0971 | 2.0085 | 2.0112 | 2.3283 | 2.1751 | 2.1624 | 2.1494 | 2.2198 | 2.26 | 2.1071 | 119.2719 | 119.2612 | 119.2554 | 119.1453 | 1.939 | 2.1429 | 2.0543 | 2.057 | 117.3329 | 117.2177 | 117.3164 | 117.2012
1273.9219 | 121.5729 | -2.2339 | 119.3802 | 0.14932 | 0.000689 | -0.007421 | -0.020438 | 0.045421 | 0.085583 | -0.067295 | 119.2582 | 119.2475 | 119.2371 | 119.1316 | 1.8658 | 2.0696 | 1.9764 | 1.9838 | 2.3832 | 2.2346 | 2.2265 | 2.2134 | 2.2793 | 2.3195 | 2.1666 | 119.304 | 119.2933 | 119.2829 | 119.1774 | 1.9115 | 2.1154 | 2.0222 | 2.0295 | 117.3924 | 117.2818 | 117.3713 | 117.2607
1275.6094 | 121.6461 | -1.8494 | 119.6732 | 0.14474 | -0.00389 | -0.012 | -0.025017 | 0.036265 | 0.081005 | -0.071874 | 119.6199 | 119.6138 | 119.6034 | 119.4888 | 1.5087 | 1.7125 | 1.6239 | 1.6312 | 1.9941 | 1.8455 | 1.8374 | 1.8243 | 1.8856 | 1.9304 | 1.7775 | 119.6657 | 119.6596 | 119.6491 | 119.5346 | 1.5544 | 1.7583 | 1.6697 | 1.677 | 118.1112 | 117.996 | 118.0947 | 117.9795
1277.3594 | 121.6782 | -2.0737 | 119.4168 | 0.14932 | 0.000689 | -0.016578 | -0.025017 | 0.040843 | 0.085583 | -0.067295 | 119.336 | 119.3391 | 119.3195 | 119.2003 | 1.7925 | 1.9918 | 1.9123 | 1.9151 | 2.223 | 2.0744 | 2.0571 | 2.0487 | 2.1145 | 2.1593 | 2.0064 | 119.3818 | 119.3849 | 119.3653 | 119.2461 | 1.8383 | 2.0376 | 1.9581 | 1.9609 | 117.5435 | 117.4237 | 117.527 | 117.4072
1279.125 | 121.6827 | -2.3071 | 119.2062 | 0.14474 | 0.000689 | -0.016578 | -0.029595 | 0.036265 | 0.085583 | -0.076452 | 119.13 | 119.1193 | 119.0997 | 118.9851 | 2.0077 | 2.207 | 2.1184 | 2.1211 | 2.4519 | 2.3078 | 2.2906 | 2.2775 | 2.3434 | 2.3927 | 2.2307 | 119.1758 | 119.1651 | 119.1455 | 119.0309 | 2.0535 | 2.2527 | 2.1641 | 2.1669 | 117.1223 | 117.0116 | 117.0921 | 116.9814
1280.8906 | 121.6049 | -2.1057 | 119.4763 | 0.14474 | 0.000689 | -0.012 | -0.025017 | 0.036265 | 0.09474 | -0.067295 | 119.3452 | 119.3482 | 119.3332 | 119.2232 | 1.7925 | 1.9918 | 1.9032 | 1.9013 | 2.2505 | 2.1064 | 2.0937 | 2.0807 | 2.142 | 2.2005 | 2.0384 | 119.391 | 119.394 | 119.379 | 119.269 | 1.8383 | 2.0376 | 1.9489 | 1.9471 | 117.5527 | 117.442 | 117.5407 | 117.4301
1282.5781 | 121.5408 | -1.9684 | 119.632 | 0.14474 | 0.000689 | -0.016578 | -0.034174 | 0.045421 | 0.090161 | -0.067295 | 119.5008 | 119.4902 | 119.4889 | 119.3606 | 1.6323 | 1.8361 | 1.7475 | 1.7503 | 2.1131 | 1.9691 | 1.9518 | 1.9342 | 2.0138 | 2.0585 | 1.9011 | 119.5466 | 119.536 | 119.5347 | 119.4064 | 1.6781 | 1.8819 | 1.7933 | 1.796 | 117.8686 | 117.7533 | 117.8566 | 117.7414
1284.3281 | 121.6827 | -1.9043 | 119.6182 | 0.14017 | -0.00389 | -0.007421 | -0.025017 | 0.040843 | 0.085583 | -0.071874 | 119.5283 | 119.5222 | 119.5118 | 119.3926 | 1.614 | 1.8224 | 1.7338 | 1.7365 | 2.0445 | 1.9004 | 1.8969 | 1.8793 | 1.9451 | 1.9899 | 1.8324 | 119.5741 | 119.568 | 119.5576 | 119.4384 | 1.6597 | 1.8682 | 1.7795 | 1.7823 | 117.9143 | 117.7945 | 117.8978 | 117.778
1286.0938 | 121.6965 | -1.7899 | 119.7464 | 0.14474 | 0.005267 | -0.007421 | -0.029595 | 0.040843 | 0.081005 | -0.076452 | 119.629 | 119.6184 | 119.5988 | 119.4979 | 1.5178 | 1.7217 | 1.6422 | 1.645 | 1.9346 | 1.7951 | 1.7824 | 1.7603 | 1.8307 | 1.8709 | 1.7134 | 119.6748 | 119.6642 | 119.6446 | 119.5437 | 1.5636 | 1.7675 | 1.688 | 1.6907 | 118.1112 | 117.9868 | 118.081 | 117.9566
1287.8438 | 121.7102 | -1.5793 | 119.9432 | 0.14474 | 0.005267 | -0.007421 | -0.020438 | 0.049999 | 0.081005 | -0.076452 | 119.8397 | 119.8382 | 119.8185 | 119.7086 | 1.3027 | 1.5111 | 1.427 | 1.4206 | 1.724 | 1.5846 | 1.5719 | 1.5588 | 1.6293 | 1.6603 | 1.5028 | 119.8854 | 119.884 | 119.8643 | 119.7544 | 1.3484 | 1.5569 | 1.4728 | 1.4664 | 118.537 | 118.4126 | 118.5159 | 118.3915
1289.5312 | 121.6965 | -1.3779 | 120.1813 | 0.14474 | 0.000689 | -0.007421 | -0.020438 | 0.040843 | 0.090161 | -0.071874 | 120.0777 | 120.0763 | 120.0612 | 119.9421 | 1.0783 | 1.273 | 1.2027 | 1.1917 | 1.5226 | 1.3786 | 1.3704 | 1.3574 | 1.4187 | 1.468 | 1.306 | 120.1235 | 120.1221 | 120.107 | 119.9879 | 1.1241 | 1.3188 | 1.2485 | 1.2375 | 118.9994 | 118.8751 | 118.9829 | 118.8585
1291.2812 | 121.669 | -1.4145 | 120.1721 | 0.14474 | 0.000689 | -0.016578 | -0.029595 | 0.040843 | 0.085583 | -0.067295 | 120.0503 | 120.0534 | 120.0291 | 119.9192 | 1.1058 | 1.3051 | 1.2256 | 1.2146 | 1.5592 | 1.4152 | 1.3979 | 1.3849 | 1.4553 | 1.5001 | 1.3472 | 120.096 | 120.0992 | 120.0749 | 119.965 | 1.1516 | 1.3509 | 1.2713 | 1.2604 | 118.9445 | 118.8247 | 118.9233 | 118.8036
1293.0312 | 121.6415 | -1.3962 | 120.1447 | 0.14474 | 0.000689 | -0.021157 | -0.029595 | 0.045421 | 0.081005 | -0.071874 | 120.0686 | 120.0625 | 120.0475 | 119.933 | 1.0921 | 1.2959 | 1.2164 | 1.2055 | 1.5409 | 1.3969 | 1.375 | 1.3666 | 1.4416 | 1.4772 | 1.3243 | 120.1144 | 120.1083 | 120.0932 | 119.9787 | 1.1378 | 1.3417 | 1.2622 | 1.2512 | 118.9765 | 118.8522 | 118.9554 | 118.831
1294.7188 | 121.701 | -1.4923 | 120.0485 | 0.14474 | 0.000689 | -0.012 | -0.025017 | 0.045421 | 0.090161 | -0.067295 | 119.9495 | 119.9435 | 119.9284 | 119.8185 | 1.2065 | 1.415 | 1.3309 | 1.3337 | 1.6371 | 1.493 | 1.4803 | 1.4673 | 1.5377 | 1.5825 | 1.425 | 119.9953 | 119.9893 | 119.9742 | 119.8643 | 1.2523 | 1.4607 | 1.3767 | 1.3794 | 118.743 | 118.6187 | 118.7219 | 118.5975
1296.4844 | 121.6507 | -1.4557 | 120.1263 | 0.14474 | -0.00389 | -0.012 | -0.025017 | 0.036265 | 0.090161 | -0.071874 | 120.0411 | 120.0305 | 120.0108 | 119.9055 | 1.1287 | 1.3234 | 1.2439 | 1.2467 | 1.6004 | 1.4518 | 1.4437 | 1.4307 | 1.492 | 1.5458 | 1.3838 | 120.0869 | 120.0763 | 120.0566 | 119.9513 | 1.1745 | 1.3692 | 1.2897 | 1.2924 | 118.9124 | 118.7972 | 118.8821 | 118.7669
1298.25 | 121.5866 | -1.4328 | 120.1904 | 0.14932 | 0.000689 | -0.007421 | -0.025017 | 0.040843 | 0.085583 | -0.067295 | 120.0823 | 120.0809 | 120.0703 | 119.9559 | 1.0829 | 1.2822 | 1.2073 | 1.1963 | 1.5821 | 1.4335 | 1.4254 | 1.4078 | 1.4736 | 1.5184 | 1.3655 | 120.1281 | 120.1266 | 120.1161 | 120.0016 | 1.1287 | 1.328 | 1.253 | 1.2421 | 118.9994 | 118.8751 | 118.9874 | 118.8631
1300.0156 | 121.701 | -1.3321 | 120.2042 | 0.14932 | 0.005267 | -0.016578 | -0.025017 | 0.040843 | 0.090161 | -0.071874 | 120.1464 | 120.1404 | 120.1253 | 120.02 | 1.028 | 1.2273 | 1.1477 | 1.1414 | 1.4814 | 1.3374 | 1.3155 | 1.3071 | 1.3729 | 1.4223 | 1.2602 | 120.1922 | 120.1862 | 120.1711 | 120.0657 | 1.0737 | 1.273 | 1.1935 | 1.1871 | 119.1185 | 118.9987 | 119.0973 | 118.9775
1301.7188 | 121.7194 | -1.2955 | 120.282 | 0.14474 | 0.000689 | -0.007421 | -0.029595 | 0.045421 | 0.085583 | -0.067295 | 120.1922 | 120.1816 | 120.1573 | 120.0612 | 0.97303 | 1.1952 | 1.102 | 1.0956 | 1.4402 | 1.2962 | 1.2881 | 1.2659 | 1.3409 | 1.3811 | 1.2282 | 120.238 | 120.2274 | 120.2031 | 120.1069 | 1.0188 | 1.241 | 1.1477 | 1.1414 | 119.2192 | 119.0902 | 119.1843 | 119.0554
1303.4688 | 121.7331 | -1.2405 | 120.3049 | 0.13559 | -0.00389 | -0.021157 | -0.020438 | 0.040843 | 0.081005 | -0.071874 | 120.2334 | 120.2274 | 120.2123 | 120.1024 | 0.94098 | 1.1448 | 1.0608 | 1.059 | 1.3761 | 1.2367 | 1.2194 | 1.2201 | 1.2814 | 1.3215 | 1.1687 | 120.2792 | 120.2732 | 120.258 | 120.1482 | 0.98676 | 1.1906 | 1.1065 | 1.1047 | 119.2924 | 119.1727 | 119.2713 | 119.1515
1305.2344 | 121.6003 | -1.2909 | 120.3461 | 0.13559 | 0.005267 | -0.012 | -0.020438 | 0.040843 | 0.085583 | -0.067295 | 120.2197 | 120.2136 | 120.2031 | 120.0978 | 0.94556 | 1.1586 | 1.0745 | 1.0681 | 1.4265 | 1.2962 | 1.2789 | 1.2705 | 1.3317 | 1.3765 | 1.2236 | 120.2654 | 120.2594 | 120.2489 | 120.1436 | 0.99133 | 1.2044 | 1.1203 | 1.1139 | 119.2741 | 119.1452 | 119.2576 | 119.1286
1307 | 121.6919 | -1.3138 | 120.2866 | 0.13559 | -0.00389 | -0.021157 | -0.029595 | 0.040843 | 0.09474 | -0.071874 | 120.1693 | 120.1724 | 120.1482 | 120.0383 | 1.0051 | 1.2135 | 1.134 | 1.1276 | 1.4494 | 1.3099 | 1.2926 | 1.2842 | 1.3546 | 1.4085 | 1.2419 | 120.2151 | 120.2182 | 120.194 | 120.084 | 1.0509 | 1.2593 | 1.1798 | 1.1734 | 119.1642 | 119.0353 | 119.1431 | 119.0142
1308.6875 | 121.7331 | -1.268 | 120.3094 | 0.14017 | -0.00389 | -0.012 | -0.020438 | 0.036265 | 0.085583 | -0.076452 | 120.2243 | 120.2182 | 120.194 | 120.0886 | 0.96387 | 1.1677 | 1.0836 | 1.0773 | 1.4082 | 1.2641 | 1.256 | 1.2476 | 1.3043 | 1.3536 | 1.1916 | 120.27 | 120.264 | 120.2397 | 120.1344 | 1.0096 | 1.2135 | 1.1294 | 1.1231 | 119.2604 | 119.1406 | 119.2301 | 119.1103
1310.4375 | 121.7102 | -1.2039 | 120.369 | 0.14474 | 0.000689 | -0.016578 | -0.020438 | 0.040843 | 0.085583 | -0.076452 | 120.2792 | 120.2777 | 120.2581 | 120.1436 | 0.8952 | 1.1036 | 1.0241 | 1.0178 | 1.3487 | 1.2046 | 1.1873 | 1.1835 | 1.2448 | 1.2895 | 1.1275 | 120.325 | 120.3235 | 120.3038 | 120.1894 | 0.94097 | 1.1494 | 1.0699 | 1.0635 | 119.384 | 119.2551 | 119.3629 | 119.2339
1312.2031 | 121.6919 | -1.1902 | 120.3873 | 0.13559 | -0.00389 | -0.012 | -0.025017 | 0.040843 | 0.085583 | -0.071874 | 120.325 | 120.3098 | 120.2855 | 120.1848 | 0.87231 | 1.0762 | 1.0012 | 0.98571 | 1.3258 | 1.1863 | 1.1782 | 1.1652 | 1.231 | 1.2758 | 1.1183 | 120.3708 | 120.3556 | 120.3313 | 120.2306 | 0.91808 | 1.122 | 1.047 | 1.0315 | 119.4527 | 119.3237 | 119.4132 | 119.2843
1313.9688 | 121.5958 | -1.2177 | 120.4514 | 0.14474 | 0.005267 | -0.007421 | -0.025017 | 0.045421 | 0.090161 | -0.076452 | 120.3158 | 120.3144 | 120.2947 | 120.1848 | 0.86773 | 1.0853 | 0.99207 | 0.99487 | 1.3624 | 1.2229 | 1.2102 | 1.1926 | 1.2631 | 1.3078 | 1.1412 | 120.3616 | 120.3602 | 120.3405 | 120.2306 | 0.91351 | 1.1311 | 1.0378 | 1.0406 | 119.4481 | 119.3237 | 119.427 | 119.3026
1315.6562 | 121.5912 | -1.1719 | 120.5246 | 0.14932 | -0.00389 | -0.012 | -0.025017 | 0.031687 | 0.090161 | -0.067295 | 120.357 | 120.3556 | 120.345 | 120.2398 | 0.8311 | 1.0258 | 0.95087 | 0.93993 | 1.3212 | 1.168 | 1.1599 | 1.1469 | 1.2036 | 1.262 | 1.1046 | 120.4028 | 120.4014 | 120.3908 | 120.2855 | 0.87688 | 1.0716 | 0.99665 | 0.98571 | 119.5259 | 119.4062 | 119.5139 | 119.3942
1317.4219 | 121.7331 | -1.0712 | 120.52 | 0.14474 | 0.000689 | -0.007421 | -0.034174 | 0.036265 | 0.090161 | -0.08103 | 120.4165 | 120.4197 | 120.4 | 120.2901 | 0.77616 | 0.97546 | 0.90051 | 0.89873 | 1.2159 | 1.0719 | 1.0637 | 1.037 | 1.1074 | 1.1613 | 0.99014 | 120.4623 | 120.4655 | 120.4458 | 120.3359 | 0.82194 | 1.0212 | 0.94628 | 0.9445 | 119.6404 | 119.516 | 119.6238 | 119.4995
1319.1719 | 121.6461 | -1.1032 | 120.575 | 0.14474 | 0.000689 | -0.012 | -0.029595 | 0.040843 | 0.085583 | -0.067295 | 120.4486 | 120.4472 | 120.432 | 120.3222 | 0.7487 | 0.94799 | 0.86846 | 0.87584 | 1.248 | 1.1039 | 1.0912 | 1.0736 | 1.1441 | 1.1888 | 1.0359 | 120.4944 | 120.4929 | 120.4778 | 120.3679 | 0.79447 | 0.99377 | 0.91423 | 0.92161 | 119.6999 | 119.5801 | 119.6833 | 119.5636
1320.9375 | 121.6278 | -1.0483 | 120.5704 | 0.14474 | 0.005267 | -0.012 | -0.025017 | 0.049999 | 0.09474 | -0.067295 | 120.4715 | 120.4655 | 120.4503 | 120.3359 | 0.73496 | 0.93425 | 0.8593 | 0.84379 | 1.193 | 1.0535 | 1.0363 | 1.0233 | 1.0983 | 1.143 | 0.98098 | 120.5173 | 120.5113 | 120.4961 | 120.3817 | 0.78074 | 0.98003 | 0.90508 | 0.88957 | 119.7365 | 119.6122 | 119.7154 | 119.591
1322.6406 | 121.6415 | -1.0941 | 120.5978 | 0.14017 | 0.000689 | -0.012 | -0.025017 | 0.040843 | 0.090161 | -0.08103 | 120.4669 | 120.4655 | 120.4412 | 120.3313 | 0.73954 | 0.94341 | 0.86846 | 0.85752 | 1.2342 | 1.0947 | 1.0821 | 1.069 | 1.1349 | 1.1842 | 1.013 | 120.5127 | 120.5113 | 120.487 | 120.3771 | 0.78532 | 0.98919 | 0.91423 | 0.9033 | 119.7274 | 119.5985 | 119.7016 | 119.5727
1324.4062 | 121.6141 | -1.0895 | 120.6116 | 0.14932 | 0.000689 | -0.012 | -0.025017 | 0.040843 | 0.09474 | -0.076452 | 120.4944 | 120.4884 | 120.4687 | 120.3588 | 0.71207 | 0.92052 | 0.83641 | 0.83006 | 1.2388 | 1.0902 | 1.0775 | 1.0645 | 1.1303 | 1.1842 | 1.013 | 120.5402 | 120.5341 | 120.5144 | 120.4046 | 0.75785 | 0.9663 | 0.88218 | 0.87583 | 119.7823 | 119.658 | 119.7566 | 119.6322
1326.1719 | 121.7743 | -1.0162 | 120.5566 | 0.14474 | -0.008469 | -0.007421 | -0.034174 | 0.040843 | 0.081005 | -0.071874 | 120.499 | 120.4792 | 120.4641 | 120.3542 | 0.71207 | 0.92052 | 0.84099 | 0.83921 | 1.161 | 1.0078 | 1.0088 | 0.98206 | 1.0571 | 1.0972 | 0.94436 | 120.5447 | 120.525 | 120.5099 | 120.4 | 0.75785 | 0.9663 | 0.88676 | 0.88499 | 119.7869 | 119.658 | 119.752 | 119.6231
1327.9219 | 121.6095 | -1.0803 | 120.6162 | 0.14017 | 0.000689 | -0.012 | -0.025017 | 0.045421 | 0.085583 | -0.076452 | 120.499 | 120.493 | 120.4641 | 120.3634 | 0.71665 | 0.92052 | 0.84557 | 0.83006 | 1.2205 | 1.081 | 1.0683 | 1.0553 | 1.1257 | 1.1659 | 1.0039 | 120.5447 | 120.5387 | 120.5099 | 120.4092 | 0.76243 | 0.9663 | 0.89134 | 0.87583 | 119.7823 | 119.6534 | 119.7474 | 119.6185
1329.6094 | 121.6324 | -1.062 | 120.6253 | 0.14017 | 0.000689 | -0.012 | -0.025017 | 0.040843 | 0.090161 | -0.071874 | 120.4944 | 120.493 | 120.4824 | 120.368 | 0.71207 | 0.9251 | 0.84099 | 0.83463 | 1.2022 | 1.0627 | 1.05 | 1.037 | 1.1029 | 1.1522 | 0.99014 | 120.5402 | 120.5387 | 120.5282 | 120.4137 | 0.75785 | 0.97088 | 0.88676 | 0.88041 | 119.7823 | 119.6534 | 119.7703 | 119.6414
1331.375 | 121.7194 | -1.0254 | 120.575 | 0.14017 | 0.005267 | -0.016578 | -0.020438 | 0.040843 | 0.09474 | -0.071874 | 120.5081 | 120.5021 | 120.4778 | 120.3634 | 0.71207 | 0.92052 | 0.83641 | 0.83006 | 1.1656 | 1.0307 | 1.0088 | 1.005 | 1.0662 | 1.1201 | 0.95352 | 120.5539 | 120.5479 | 120.5236 | 120.4092 | 0.75785 | 0.9663 | 0.88218 | 0.87583 | 119.796 | 119.6717 | 119.7657 | 119.6414
1333.1406 | 121.7148 | -1.062 | 120.5338 | 0.14932 | -0.008469 | -0.016578 | -0.025017 | 0.036265 | 0.090161 | -0.067295 | 120.4715 | 120.4609 | 120.4412 | 120.3313 | 0.75785 | 0.96172 | 0.88677 | 0.87584 | 1.2113 | 1.0535 | 1.0454 | 1.037 | 1.0983 | 1.1522 | 0.99472 | 120.5173 | 120.5067 | 120.487 | 120.3771 | 0.80363 | 1.0075 | 0.93255 | 0.92161 | 119.7136 | 119.5847 | 119.6833 | 119.5544
1334.9062 | 121.7468 | -1.1627 | 120.4834 | 0.14474 | -0.00389 | -0.012 | -0.029595 | 0.036265 | 0.090161 | -0.067295 | 120.3845 | 120.3785 | 120.3588 | 120.2443 | 0.84484 | 1.0487 | 0.9646 | 0.96282 | 1.3075 | 1.1588 | 1.1507 | 1.1331 | 1.199 | 1.2529 | 1.0954 | 120.4303 | 120.4243 | 120.4046 | 120.2901 | 0.89061 | 1.0945 | 1.0104 | 1.0086 | 119.5397 | 119.4199 | 119.5139 | 119.3942
1336.6719 | 121.6782 | -1.2726 | 120.4102 | 0.14017 | 0.000689 | -0.012 | -0.01586 | 0.040843 | 0.081005 | -0.062717 | 120.2883 | 120.2915 | 120.2764 | 120.1665 | 0.91809 | 1.1311 | 1.047 | 1.0361 | 1.4127 | 1.2733 | 1.2606 | 1.2567 | 1.3134 | 1.3536 | 1.2099 | 120.3341 | 120.3373 | 120.3221 | 120.2123 | 0.96387 | 1.1769 | 1.0928 | 1.0818 | 119.3703 | 119.2413 | 119.3583 | 119.2294
1338.3594 | 121.6095 | -1.3504 | 120.3415 | 0.14474 | 0.000689 | -0.016578 | -0.025017 | 0.045421 | 0.09474 | -0.071874 | 120.2426 | 120.232 | 120.226 | 120.1207 | 0.96845 | 1.1815 | 1.102 | 1.0956 | 1.4951 | 1.3511 | 1.3338 | 1.3254 | 1.3958 | 1.4451 | 1.2785 | 120.2883 | 120.2777 | 120.2718 | 120.1665 | 1.0142 | 1.2272 | 1.1477 | 1.1414 | 119.2741 | 119.1406 | 119.2576 | 119.124
1340.1094 | 121.6187 | -1.3687 | 120.3415 | 0.14932 | 0.005267 | -0.012 | -0.020438 | 0.036265 | 0.085583 | -0.062717 | 120.2197 | 120.2091 | 120.194 | 120.0841 | 1.0005 | 1.2181 | 1.1294 | 1.1231 | 1.518 | 1.374 | 1.3567 | 1.3483 | 1.405 | 1.4543 | 1.306 | 120.2654 | 120.2548 | 120.2397 | 120.1298 | 1.0463 | 1.2639 | 1.1752 | 1.1688 | 119.2192 | 119.0902 | 119.1935 | 119.0645
1341.875 | 121.7697 | -1.3321 | 120.2866 | 0.14017 | 0.000689 | -0.012 | -0.025017 | 0.040843 | 0.085583 | -0.071874 | 120.2151 | 120.2136 | 120.1985 | 120.0795 | 1.0142 | 1.2135 | 1.1432 | 1.1276 | 1.4723 | 1.3328 | 1.3201 | 1.3071 | 1.3729 | 1.4177 | 1.2602 | 120.2609 | 120.2594 | 120.2443 | 120.1253 | 1.06 | 1.2593 | 1.1889 | 1.1734 | 119.2009 | 119.0719 | 119.1843 | 119.0554
1343.5938 | 121.7194 | -1.442 | 120.2271 | 0.14474 | -0.008469 | -0.012 | -0.025017 | 0.045421 | 0.090161 | -0.067295 | 120.1006 | 120.0992 | 120.0841 | 119.965 | 1.1241 | 1.328 | 1.2485 | 1.2512 | 1.5867 | 1.4335 | 1.43 | 1.4169 | 1.4874 | 1.5321 | 1.3747 | 120.1464 | 120.145 | 120.1299 | 120.0108 | 1.1699 | 1.3737 | 1.2942 | 1.297 | 118.9765 | 118.8522 | 118.96 | 118.8356
1345.3281 | 121.7743 | -1.5106 | 120.1309 | 0.14474 | 0.000689 | -0.012 | -0.029595 | 0.040843 | 0.090161 | -0.076452 | 120.0136 | 120.0122 | 119.9971 | 119.878 | 1.2111 | 1.4195 | 1.3355 | 1.3291 | 1.6554 | 1.5113 | 1.4986 | 1.481 | 1.5515 | 1.6008 | 1.4342 | 120.0594 | 120.058 | 120.0429 | 119.9238 | 1.2569 | 1.4653 | 1.3812 | 1.3749 | 118.8025 | 118.6782 | 118.786 | 118.6616
1347.0938 | 121.7285 | -1.6205 | 120.0027 | 0.1539 | 0.005267 | -0.016578 | -0.020438 | 0.040843 | 0.090161 | -0.076452 | 119.9358 | 119.9298 | 119.9101 | 119.7956 | 1.2981 | 1.5019 | 1.4179 | 1.4115 | 1.7744 | 1.6257 | 1.6039 | 1.6 | 1.6613 | 1.7106 | 1.544 | 119.9816 | 119.9755 | 119.9559 | 119.8414 | 1.3439 | 1.5477 | 1.4636 | 1.4573 | 118.6377 | 118.5179 | 118.612 | 118.4922
1348.8594 | 121.6461 | -1.7166 | 119.9661 | 0.14932 | 0.005267 | -0.012 | -0.025017 | 0.040843 | 0.090161 | -0.071874 | 119.8625 | 119.8473 | 119.8323 | 119.7132 | 1.3713 | 1.566 | 1.4911 | 1.4893 | 1.8659 | 1.7219 | 1.7046 | 1.6916 | 1.7575 | 1.8068 | 1.6447 | 119.9083 | 119.8931 | 119.8781 | 119.7589 | 1.4171 | 1.6118 | 1.5369 | 1.5351 | 118.4912 | 118.3714 | 118.4609 | 118.3412
1350.5469 | 121.7056 | -1.6708 | 119.9661 | 0.14932 | -0.00389 | -0.012 | -0.01586 | 0.040843 | 0.090161 | -0.071874 | 119.8946 | 119.8931 | 119.8826 | 119.7498 | 1.3301 | 1.5431 | 1.4545 | 1.4573 | 1.8202 | 1.6669 | 1.6588 | 1.655 | 1.7117 | 1.761 | 1.599 | 119.9404 | 119.9389 | 119.9284 | 119.7956 | 1.3759 | 1.5889 | 1.5003 | 1.503 | 118.5645 | 118.4401 | 118.5525 | 118.4281
1352.3125 | 121.788 | -1.6205 | 120.0165 | 0.14474 | -0.00389 | -0.012 | -0.025017 | 0.036265 | 0.090161 | -0.067295 | 119.9129 | 119.916 | 119.9009 | 119.7773 | 1.321 | 1.5202 | 1.4453 | 1.4298 | 1.7652 | 1.6166 | 1.6085 | 1.5955 | 1.6567 | 1.7106 | 1.5532 | 119.9587 | 119.9618 | 119.9467 | 119.823 | 1.3667 | 1.566 | 1.4911 | 1.4756 | 118.5919 | 118.4676 | 118.58 | 118.4556
1354.0156 | 121.6919 | -1.6022 | 120.0806 | 0.14017 | 0.000689 | -0.012 | -0.025017 | 0.036265 | 0.099318 | -0.067295 | 119.9587 | 119.9572 | 119.9422 | 119.8231 | 1.2752 | 1.4836 | 1.395 | 1.3932 | 1.7423 | 1.6029 | 1.5902 | 1.5772 | 1.6384 | 1.7015 | 1.5349 | 120.0045 | 120.003 | 119.9879 | 119.8688 | 1.321 | 1.5294 | 1.4407 | 1.4389 | 118.6835 | 118.5637 | 118.667 | 118.5472
1355.7812 | 121.7926 | -1.5472 | 120.0806 | 0.14474 | 0.000689 | -0.012 | -0.029595 | 0.036265 | 0.085583 | -0.076452 | 119.9816 | 119.9755 | 119.9605 | 119.846 | 1.2523 | 1.4607 | 1.3858 | 1.3749 | 1.692 | 1.5479 | 1.5352 | 1.5176 | 1.5835 | 1.6328 | 1.4708 | 120.0274 | 120.0213 | 120.0062 | 119.8917 | 1.2981 | 1.5065 | 1.4316 | 1.4206 | 118.7293 | 118.5958 | 118.7082 | 118.5746
1357.5469 | 121.788 | -1.5289 | 120.1172 | 0.14474 | 0.000689 | -0.007421 | -0.025017 | 0.040843 | 0.090161 | -0.071874 | 120.0182 | 120.0122 | 119.9971 | 119.8734 | 1.2248 | 1.4378 | 1.3446 | 1.3474 | 1.6737 | 1.5296 | 1.5215 | 1.5039 | 1.5698 | 1.6191 | 1.4571 | 120.064 | 120.058 | 120.0429 | 119.9192 | 1.2706 | 1.4836 | 1.3904 | 1.3932 | 118.7934 | 118.6736 | 118.7723 | 118.6525
1359.3281 | 121.7651 | -1.5152 | 120.1172 | 0.14474 | -0.013048 | -0.012 | -0.020438 | 0.036265 | 0.090161 | -0.076452 | 120.0457 | 120.0396 | 120.0246 | 119.9101 | 1.2019 | 1.4104 | 1.3263 | 1.3153 | 1.6599 | 1.5022 | 1.5032 | 1.4948 | 1.5515 | 1.6054 | 1.4387 | 120.0915 | 120.0854 | 120.0703 | 119.9558 | 1.2477 | 1.4562 | 1.3721 | 1.3611 | 118.8438 | 118.7194 | 118.8226 | 118.6983
1361.0938 | 121.7422 | -1.506 | 120.1218 | 0.14474 | -0.008469 | -0.016578 | -0.020438 | 0.036265 | 0.090161 | -0.071874 | 120.0594 | 120.0534 | 120.0337 | 119.9192 | 1.179 | 1.4012 | 1.3171 | 1.3062 | 1.6508 | 1.4976 | 1.4895 | 1.4856 | 1.5423 | 1.5962 | 1.4342 | 120.1052 | 120.0992 | 120.0795 | 119.965 | 1.2248 | 1.447 | 1.3629 | 1.352 | 118.8804 | 118.7423 | 118.8547 | 118.7166
1362.8594 | 121.6187 | -1.4923 | 120.2133 | 0.14474 | -0.00389 | -0.012 | -0.020438 | 0.045421 | 0.085583 | -0.067295 | 120.0915 | 120.0946 | 120.0795 | 119.9604 | 1.1424 | 1.3554 | 1.2622 | 1.2741 | 1.6371 | 1.4884 | 1.4803 | 1.4719 | 1.5377 | 1.5779 | 1.425 | 120.1373 | 120.1404 | 120.1253 | 120.0062 | 1.1882 | 1.4012 | 1.308 | 1.3199 | 118.9491 | 118.8293 | 118.9371 | 118.8173
1364.5469 | 121.7926 | -1.4603 | 120.1721 | 0.14474 | -0.008469 | -0.016578 | -0.01586 | 0.036265 | 0.085583 | -0.071874 | 120.0961 | 120.09 | 120.0795 | 119.9559 | 1.1424 | 1.3554 | 1.2668 | 1.265 | 1.605 | 1.4518 | 1.4437 | 1.4444 | 1.4965 | 1.5458 | 1.3884 | 120.1418 | 120.1358 | 120.1253 | 120.0016 | 1.1882 | 1.4012 | 1.3126 | 1.3108 | 118.9536 | 118.8293 | 118.9371 | 118.8127
1366.2969 | 121.701 | -1.474 | 120.2087 | 0.13559 | -0.00389 | -0.016578 | -0.020438 | 0.045421 | 0.090161 | -0.071874 | 120.1281 | 120.1221 | 120.0978 | 119.9879 | 1.1241 | 1.3371 | 1.2439 | 1.2421 | 1.6096 | 1.4701 | 1.4574 | 1.4536 | 1.5194 | 1.5642 | 1.4021 | 120.1739 | 120.1678 | 120.1436 | 120.0337 | 1.1699 | 1.3829 | 1.2897 | 1.2879 | 119.004 | 118.8842 | 118.9737 | 118.8539
1368.0469 | 121.7377 | -1.4374 | 120.2408 | 0.14017 | -0.00389 | -0.007421 | -0.025017 | 0.036265 | 0.09474 | -0.071874 | 120.1327 | 120.1358 | 120.1161 | 120.0016 | 1.1104 | 1.3188 | 1.2393 | 1.2329 | 1.5775 | 1.4335 | 1.43 | 1.4124 | 1.4736 | 1.5321 | 1.3655 | 120.1785 | 120.1816 | 120.1619 | 120.0474 | 1.1561 | 1.3646 | 1.2851 | 1.2787 | 119.0223 | 118.8934 | 119.0058 | 118.8768
1369.75 | 121.6827 | -1.4603 | 120.2637 | 0.14017 | -0.00389 | -0.016578 | -0.029595 | 0.036265 | 0.081005 | -0.067295 | 120.1327 | 120.1358 | 120.1161 | 119.9971 | 1.1241 | 1.3325 | 1.2485 | 1.2467 | 1.6004 | 1.4564 | 1.4437 | 1.4307 | 1.4965 | 1.5413 | 1.393 | 120.1785 | 120.1816 | 120.1619 | 120.0428 | 1.1699 | 1.3783 | 1.2942 | 1.2924 | 119.0086 | 118.8842 | 118.992 | 118.8677
1371.5 | 121.8155 | -1.4511 | 120.2225 | 0.14474 | -0.00389 | -0.007421 | -0.020438 | 0.040843 | 0.081005 | -0.067295 | 120.1281 | 120.1266 | 120.1024 | 119.9925 | 1.1241 | 1.328 | 1.253 | 1.2467 | 1.5959 | 1.4472 | 1.4437 | 1.4307 | 1.492 | 1.5321 | 1.3838 | 120.1739 | 120.1724 | 120.1482 | 120.0383 | 1.1699 | 1.3737 | 1.2988 | 1.2924 | 119.004 | 118.8751 | 118.9783 | 118.8494
1373.2656 | 121.7102 | -1.474 | 120.2408 | 0.14017 | -0.008469 | -0.012 | -0.020438 | 0.036265 | 0.085583 | -0.067295 | 120.1281 | 120.1266 | 120.1024 | 119.9971 | 1.1287 | 1.3463 | 1.2576 | 1.2604 | 1.6142 | 1.4655 | 1.462 | 1.4536 | 1.5103 | 1.5596 | 1.4067 | 120.1739 | 120.1724 | 120.1482 | 120.0428 | 1.1745 | 1.3921 | 1.3034 | 1.3062 | 118.9994 | 118.8705 | 118.9737 | 118.8448
1375.0312 | 121.6644 | -1.5015 | 120.2362 | 0.14932 | 0.005267 | -0.012 | -0.025017 | 0.036265 | 0.090161 | -0.067295 | 120.1235 | 120.1175 | 120.0978 | 119.9833 | 1.1241 | 1.3417 | 1.2622 | 1.2512 | 1.6508 | 1.5067 | 1.4895 | 1.4764 | 1.5377 | 1.5916 | 1.4342 | 120.1693 | 120.1633 | 120.1436 | 120.0291 | 1.1699 | 1.3875 | 1.308 | 1.297 | 118.9994 | 118.8613 | 118.9737 | 118.8356
1376.7344 | 121.6873 | -1.4603 | 120.2774 | 0.14932 | 0.005267 | -0.012 | -0.01586 | 0.040843 | 0.090161 | -0.071874 | 120.151 | 120.145 | 120.1344 | 120.0062 | 1.1058 | 1.3188 | 1.2347 | 1.2284 | 1.6096 | 1.4655 | 1.4483 | 1.4444 | 1.5011 | 1.5504 | 1.3884 | 120.1968 | 120.1907 | 120.1802 | 120.052 | 1.1516 | 1.3646 | 1.2805 | 1.2741 | 119.0452 | 118.9163 | 119.0286 | 118.8997
1378.4844 | 121.8018 | -1.387 | 120.2545 | 0.14474 | -0.00389 | -0.012 | -0.025017 | 0.040843 | 0.081005 | -0.071874 | 120.1647 | 120.1587 | 120.1436 | 120.0245 | 1.1058 | 1.3142 | 1.221 | 1.2192 | 1.5318 | 1.3831 | 1.375 | 1.362 | 1.4279 | 1.468 | 1.3152 | 120.2105 | 120.2045 | 120.1894 | 120.0703 | 1.1516 | 1.36 | 1.2668 | 1.265 | 119.0589 | 118.9437 | 119.0378 | 118.9226
1380.2344 | 121.8063 | -1.4008 | 120.2454 | 0.1539 | -0.00389 | -0.007421 | -0.01586 | 0.040843 | 0.090161 | -0.062717 | 120.1785 | 120.1816 | 120.1619 | 120.0429 | 1.0829 | 1.2959 | 1.2118 | 1.2055 | 1.5547 | 1.3969 | 1.3933 | 1.3849 | 1.4416 | 1.4909 | 1.338 | 120.2242 | 120.2274 | 120.2077 | 120.0886 | 1.1287 | 1.3417 | 1.2576 | 1.2512 | 119.0956 | 118.9666 | 119.079 | 118.9501
1381.9844 | 121.8338 | -1.3916 | 120.282 | 0.14474 | -0.00389 | -0.012 | -0.020438 | 0.040843 | 0.085583 | -0.076452 | 120.2014 | 120.1907 | 120.1711 | 120.0566 | 1.0737 | 1.2776 | 1.1981 | 1.1917 | 1.5363 | 1.3877 | 1.3796 | 1.3712 | 1.4324 | 1.4772 | 1.3152 | 120.2471 | 120.2365 | 120.2168 | 120.1024 | 1.1195 | 1.3234 | 1.2439 | 1.2375 | 119.1276 | 119.0033 | 119.0973 | 118.973
1383.6719 | 121.6827 | -1.4236 | 120.3323 | 0.14474 | 0.000689 | -0.002842 | -0.020438 | 0.045421 | 0.099318 | -0.071874 | 120.2151 | 120.2136 | 120.194 | 120.0795 | 1.0554 | 1.2593 | 1.1798 | 1.1734 | 1.5684 | 1.4243 | 1.4208 | 1.4032 | 1.4691 | 1.523 | 1.3518 | 120.2609 | 120.2594 | 120.2397 | 120.1253 | 1.1012 | 1.3051 | 1.2256 | 1.2192 | 119.1597 | 119.0353 | 119.1385 | 119.0142
1385.4219 | 121.7697 | -1.355 | 120.3278 | 0.14474 | -0.008469 | -0.012 | -0.029595 | 0.045421 | 0.090161 | -0.071874 | 120.2517 | 120.2457 | 120.2306 | 120.1115 | 1.0234 | 1.2318 | 1.1477 | 1.146 | 1.4997 | 1.3465 | 1.343 | 1.3254 | 1.4004 | 1.4451 | 1.2831 | 120.2975 | 120.2915 | 120.2764 | 120.1573 | 1.0692 | 1.2776 | 1.1935 | 1.1917 | 119.2283 | 119.104 | 119.2072 | 119.0828
1387.1875 | 121.7377 | -1.3275 | 120.3735 | 0.14017 | -0.008469 | -0.002842 | -0.020438 | 0.040843 | 0.085583 | -0.067295 | 120.2883 | 120.2823 | 120.2626 | 120.1482 | 0.99134 | 1.1952 | 1.1157 | 1.1139 | 1.4677 | 1.319 | 1.3247 | 1.3071 | 1.3684 | 1.4131 | 1.2602 | 120.3341 | 120.3281 | 120.3084 | 120.1939 | 1.0371 | 1.241 | 1.1615 | 1.1597 | 119.297 | 119.1727 | 119.2713 | 119.1469
1388.9531 | 121.7834 | -1.2955 | 120.3644 | 0.14017 | -0.008469 | -0.007421 | -0.025017 | 0.040843 | 0.085583 | -0.071874 | 120.2929 | 120.2915 | 120.2672 | 120.1527 | 0.9776 | 1.186 | 1.1111 | 1.1093 | 1.4356 | 1.287 | 1.2881 | 1.2705 | 1.3363 | 1.3811 | 1.2236 | 120.3387 | 120.3373 | 120.313 | 120.1985 | 1.0234 | 1.2318 | 1.1569 | 1.1551 | 119.3153 | 119.1818 | 119.2896 | 119.1561
1390.6406 | 121.8018 | -1.2955 | 120.3964 | 0.14017 | -0.008469 | -0.016578 | -0.020438 | 0.036265 | 0.081005 | -0.071874 | 120.3112 | 120.3052 | 120.2809 | 120.1802 | 0.96387 | 1.1723 | 1.102 | 1.0864 | 1.4356 | 1.287 | 1.2789 | 1.275 | 1.3317 | 1.3765 | 1.2236 | 120.357 | 120.351 | 120.3267 | 120.226 | 1.0096 | 1.2181 | 1.1477 | 1.1322 | 119.3474 | 119.2093 | 119.3171 | 119.179
1392.3906 | 121.7972 | -1.2451 | 120.4239 | 0.14017 | -0.013048 | -0.012 | -0.020438 | 0.040843 | 0.09474 | -0.067295 | 120.3341 | 120.3235 | 120.313 | 120.194 | 0.95014 | 1.1586 | 1.0745 | 1.0727 | 1.3853 | 1.2321 | 1.2331 | 1.2247 | 1.286 | 1.3399 | 1.1778 | 120.3799 | 120.3693 | 120.3588 | 120.2397 | 0.99591 | 1.2044 | 1.1203 | 1.1185 | 119.384 | 119.2597 | 119.3629 | 119.2385
1394.1562 | 121.6782 | -1.2772 | 120.4697 | 0.14474 | -0.00389 | -0.002842 | -0.020438 | 0.040843 | 0.085583 | -0.067295 | 120.3616 | 120.351 | 120.3267 | 120.2169 | 0.9364 | 1.1448 | 1.0562 | 1.059 | 1.4219 | 1.2733 | 1.2743 | 1.2567 | 1.318 | 1.3627 | 1.2099 | 120.4074 | 120.3968 | 120.3725 | 120.2626 | 0.98218 | 1.1906 | 1.1019 | 1.1047 | 119.4252 | 119.3054 | 119.3903 | 119.2706
1395.9219 | 121.7102 | -1.2589 | 120.4834 | 0.14474 | -0.008469 | -0.012 | -0.020438 | 0.040843 | 0.085583 | -0.071874 | 120.3708 | 120.3693 | 120.3496 | 120.226 | 0.91351 | 1.122 | 1.047 | 1.0407 | 1.4036 | 1.2504 | 1.2469 | 1.2384 | 1.2997 | 1.3444 | 1.187 | 120.4165 | 120.4151 | 120.3954 | 120.2718 | 0.95929 | 1.1677 | 1.0928 | 1.0864 | 119.4573 | 119.3237 | 119.4361 | 119.3026
1397.625 | 121.8063 | -1.1856 | 120.4834 | 0.15848 | 0.000689 | -0.016578 | -0.020438 | 0.031687 | 0.085583 | -0.076452 | 120.4165 | 120.4151 | 120.3954 | 120.281 | 0.87689 | 1.0853 | 0.99665 | 0.99945 | 1.3441 | 1.1863 | 1.169 | 1.1652 | 1.2173 | 1.2712 | 1.1092 | 120.4623 | 120.4609 | 120.4412 | 120.3267 | 0.92266 | 1.1311 | 1.0424 | 1.0452 | 119.5397 | 119.4199 | 119.5185 | 119.3987
1399.375 | 121.7194 | -1.2177 | 120.5475 | 0.14017 | -0.008469 | -0.007421 | -0.025017 | 0.040843 | 0.09474 | -0.067295 | 120.4349 | 120.438 | 120.4137 | 120.2947 | 0.84484 | 1.0533 | 0.98292 | 0.96282 | 1.3578 | 1.2092 | 1.2102 | 1.1926 | 1.2585 | 1.3124 | 1.1504 | 120.4806 | 120.4838 | 120.4595 | 120.3405 | 0.89061 | 1.0991 | 1.0287 | 1.0086 | 119.59 | 119.4519 | 119.5689 | 119.4308
1401.1406 | 121.8063 | -1.149 | 120.5292 | 0.14017 | -0.00389 | -0.012 | -0.025017 | 0.040843 | 0.090161 | -0.071874 | 120.4486 | 120.4426 | 120.432 | 120.2993 | 0.84026 | 1.0441 | 0.9646 | 0.96282 | 1.2892 | 1.1451 | 1.137 | 1.124 | 1.1898 | 1.2391 | 1.0771 | 120.4944 | 120.4884 | 120.4778 | 120.3451 | 0.88604 | 1.0899 | 1.0104 | 1.0086 | 119.6083 | 119.484 | 119.5918 | 119.4674
1402.8906 | 121.8109 | -1.1261 | 120.5521 | 0.14474 | -0.008469 | -0.012 | -0.020438 | 0.049999 | 0.090161 | -0.071874 | 120.4806 | 120.4701 | 120.4549 | 120.3313 | 0.81279 | 1.0258 | 0.95087 | 0.94451 | 1.2708 | 1.1176 | 1.1141 | 1.1057 | 1.1761 | 1.2163 | 1.0542 | 120.5264 | 120.5158 | 120.5007 | 120.3771 | 0.85857 | 1.0716 | 0.99665 | 0.99029 | 119.6679 | 119.5298 | 119.6421 | 119.5041
1404.5781 | 121.7148 | -1.1673 | 120.5658 | 0.14932 | 0.000689 | -0.016578 | -0.025017 | 0.045421 | 0.085583 | -0.067295 | 120.4669 | 120.4655 | 120.4503 | 120.3268 | 0.82195 | 1.0258 | 0.95545 | 0.95367 | 1.3166 | 1.168 | 1.1507 | 1.1423 | 1.2127 | 1.2529 | 1.1 | 120.5127 | 120.5113 | 120.4961 | 120.3725 | 0.86772 | 1.0716 | 1.0012 | 0.99944 | 119.645 | 119.5115 | 119.6284 | 119.4949
1406.3438 | 121.7972 | -1.1536 | 120.5612 | 0.14017 | -0.013048 | -0.012 | -0.01586 | 0.036265 | 0.090161 | -0.067295 | 120.4715 | 120.4609 | 120.4458 | 120.3313 | 0.82652 | 1.0304 | 0.95545 | 0.95367 | 1.2937 | 1.1405 | 1.1416 | 1.1377 | 1.1898 | 1.2437 | 1.0863 | 120.5173 | 120.5067 | 120.4915 | 120.3771 | 0.8723 | 1.0762 | 1.0012 | 0.99944 | 119.645 | 119.516 | 119.6192 | 119.4903
1408.0938 | 121.7194 | -1.1673 | 120.6162 | 0.14474 | -0.00389 | -0.012 | -0.020438 | 0.040843 | 0.090161 | -0.067295 | 120.4852 | 120.4792 | 120.4641 | 120.3359 | 0.82195 | 1.0258 | 0.94171 | 0.94451 | 1.312 | 1.1634 | 1.1553 | 1.1469 | 1.2081 | 1.2575 | 1.1 | 120.531 | 120.525 | 120.5099 | 120.3817 | 0.86772 | 1.0716 | 0.98749 | 0.99029 | 119.6633 | 119.5435 | 119.6421 | 119.5224
1409.8438 | 121.7148 | -1.1856 | 120.6024 | 0.14474 | -0.00389 | -0.012 | -0.020438 | 0.040843 | 0.090161 | -0.071874 | 120.4898 | 120.4746 | 120.4549 | 120.3451 | 0.81279 | 1.0258 | 0.94629 | 0.93535 | 1.3304 | 1.1817 | 1.1736 | 1.1652 | 1.2265 | 1.2758 | 1.1137 | 120.5356 | 120.5204 | 120.5007 | 120.3908 | 0.85857 | 1.0716 | 0.99207 | 0.98113 | 119.677 | 119.5435 | 119.6421 | 119.5086
1411.5312 | 121.6873 | -1.1993 | 120.5933 | 0.14932 | 0.000689 | -0.007421 | -0.025017 | 0.036265 | 0.09474 | -0.062717 | 120.4806 | 120.4655 | 120.4503 | 120.3359 | 0.82652 | 1.0396 | 0.95087 | 0.94909 | 1.3487 | 1.2 | 1.1919 | 1.1743 | 1.2356 | 1.2941 | 1.1366 | 120.5264 | 120.5113 | 120.4961 | 120.3817 | 0.8723 | 1.0853 | 0.99665 | 0.99486 | 119.6541 | 119.5298 | 119.6238 | 119.4995
1413.2969 | 121.7514 | -1.1307 | 120.6207 | 0.14474 | 0.000689 | -0.012 | -0.01586 | 0.045421 | 0.090161 | -0.071874 | 120.5264 | 120.5158 | 120.4961 | 120.3771 | 0.78074 | 1.0029 | 0.90966 | 0.90789 | 1.2754 | 1.1314 | 1.1187 | 1.1148 | 1.1761 | 1.2208 | 1.0588 | 120.5722 | 120.5616 | 120.5419 | 120.4229 | 0.82652 | 1.0487 | 0.95544 | 0.95366 | 119.7457 | 119.6168 | 119.7154 | 119.5865
1415.0625 | 121.7331 | -1.0986 | 120.6665 | 0.14932 | -0.00389 | -0.012 | -0.025017 | 0.040843 | 0.090161 | -0.062717 | 120.5447 | 120.5387 | 120.5144 | 120.3954 | 0.75785 | 0.97546 | 0.89593 | 0.89415 | 1.248 | 1.0947 | 1.0866 | 1.0736 | 1.1395 | 1.1888 | 1.0359 | 120.5905 | 120.5845 | 120.5602 | 120.4412 | 0.80363 | 1.0212 | 0.9417 | 0.93993 | 119.7869 | 119.6488 | 119.7566 | 119.6185
1416.8281 | 121.7422 | -1.0941 | 120.6619 | 0.14474 | 0.000689 | -0.016578 | -0.020438 | 0.040843 | 0.085583 | -0.058139 | 120.5539 | 120.5571 | 120.519 | 120.4092 | 0.75327 | 0.96172 | 0.88677 | 0.88499 | 1.2388 | 1.0947 | 1.0775 | 1.0736 | 1.1349 | 1.1796 | 1.0359 | 120.5997 | 120.6028 | 120.5648 | 120.455 | 0.79905 | 1.0075 | 0.93255 | 0.93077 | 119.8006 | 119.6671 | 119.7657 | 119.6322
1418.5312 | 121.8246 | -1.062 | 120.6436 | 0.14474 | -0.008469 | -0.012 | -0.029595 | 0.040843 | 0.090161 | -0.071874 | 120.5676 | 120.5571 | 120.5328 | 120.4183 | 0.7487 | 0.95257 | 0.87762 | 0.87584 | 1.2068 | 1.0535 | 1.05 | 1.0324 | 1.1029 | 1.1522 | 0.99014 | 120.6134 | 120.6028 | 120.5785 | 120.4641 | 0.79447 | 0.99834 | 0.92339 | 0.92161 | 119.8189 | 119.69 | 119.7841 | 119.6551
1420.2812 | 121.8384 | -1.0437 | 120.6528 | 0.14474 | 0.000689 | -0.012 | -0.029595 | 0.045421 | 0.085583 | -0.067295 | 120.5905 | 120.5799 | 120.5511 | 120.4366 | 0.72581 | 0.93425 | 0.86388 | 0.8621 | 1.1884 | 1.0444 | 1.0317 | 1.0141 | 1.0891 | 1.1293 | 0.97641 | 120.6363 | 120.6257 | 120.5968 | 120.4824 | 0.77158 | 0.98003 | 0.90966 | 0.90788 | 119.8647 | 119.7267 | 119.8253 | 119.6872
1422.0469 | 121.7239 | -1.0666 | 120.6894 | 0.14474 | 0.000689 | -0.007421 | -0.025017 | 0.040843 | 0.090161 | -0.062717 | 120.5905 | 120.5845 | 120.5648 | 120.4458 | 0.71665 | 0.92968 | 0.85014 | 0.84837 | 1.2113 | 1.0673 | 1.0592 | 1.0416 | 1.1074 | 1.1567 | 1.0039 | 120.6363 | 120.6303 | 120.6106 | 120.4916 | 0.76243 | 0.97545 | 0.89592 | 0.89414 | 119.8739 | 119.7404 | 119.8481 | 119.7147
1423.8281 | 121.7148 | -1.1124 | 120.7169 | 0.14017 | 0.000689 | -0.007421 | -0.025017 | 0.036265 | 0.090161 | -0.071874 | 120.5905 | 120.5845 | 120.5602 | 120.4458 | 0.73038 | 0.93883 | 0.8593 | 0.85295 | 1.2525 | 1.1131 | 1.1049 | 1.0873 | 1.1486 | 1.2025 | 1.0405 | 120.6363 | 120.6303 | 120.606 | 120.4916 | 0.77616 | 0.98461 | 0.90508 | 0.89872 | 119.8601 | 119.7312 | 119.8298 | 119.7009
1425.5156 | 121.7285 | -1.0574 | 120.7306 | 0.14474 | -0.00389 | -0.007421 | -0.01586 | 0.036265 | 0.09474 | -0.071874 | 120.6134 | 120.6074 | 120.5877 | 120.4687 | 0.70291 | 0.90679 | 0.83183 | 0.82548 | 1.2022 | 1.0535 | 1.05 | 1.0416 | 1.0937 | 1.1522 | 0.98556 | 120.6592 | 120.6532 | 120.6335 | 120.5145 | 0.74869 | 0.95256 | 0.87761 | 0.87125 | 119.9105 | 119.7816 | 119.8848 | 119.7559
1427.2656 | 121.7285 | -1.03 | 120.7489 | 0.14932 | -0.00389 | -0.012 | -0.01586 | 0.040843 | 0.090161 | -0.067295 | 120.6317 | 120.6257 | 120.6014 | 120.487 | 0.6846 | 0.89305 | 0.8181 | 0.80259 | 1.1793 | 1.0261 | 1.018 | 1.0141 | 1.0708 | 1.1201 | 0.96267 | 120.6775 | 120.6715 | 120.6472 | 120.5328 | 0.73038 | 0.93883 | 0.86387 | 0.84836 | 119.9471 | 119.8136 | 119.9168 | 119.7833
1429.0312 | 121.756 | -1.0162 | 120.7306 | 0.13559 | 0.000689 | -0.016578 | -0.020438 | 0.045421 | 0.085583 | -0.062717 | 120.6455 | 120.6441 | 120.6152 | 120.5053 | 0.67544 | 0.8839 | 0.79978 | 0.79801 | 1.1518 | 1.0169 | 0.99966 | 0.9958 | 1.0617 | 1.1018 | 0.95352 | 120.6912 | 120.6898 | 120.6609 | 120.5511 | 0.72122 | 0.92967 | 0.84556 | 0.84379 | 119.97 | 119.8457 | 119.9397 | 119.8154
1430.7188 | 121.7056 | -1.0025 | 120.7535 | 0.14474 | -0.008469 | -0.016578 | -0.025017 | 0.040843 | 0.090161 | -0.067295 | 120.6546 | 120.6532 | 120.6197 | 120.5099 | 0.66629 | 0.8839 | 0.80436 | 0.79343 | 1.1472 | 0.99403 | 0.98592 | 0.97749 | 1.0433 | 1.0927 | 0.93521 | 120.7004 | 120.699 | 120.6655 | 120.5557 | 0.71207 | 0.92967 | 0.85014 | 0.83921 | 119.9883 | 119.8503 | 119.9534 | 119.8154
1432.4688 | 121.7056 | -1.0345 | 120.7352 | 0.14474 | 0.005267 | -0.012 | -0.025017 | 0.040843 | 0.090161 | -0.076452 | 120.6684 | 120.6532 | 120.6381 | 120.5191 | 0.65713 | 0.86558 | 0.78605 | 0.78427 | 1.1793 | 1.0398 | 1.0225 | 1.0095 | 1.0754 | 1.1247 | 0.95809 | 120.7141 | 120.699 | 120.6838 | 120.5648 | 0.70291 | 0.91136 | 0.83182 | 0.83005 | 120.0112 | 119.8823 | 119.9809 | 119.852
1434.2188 | 121.7697 | -1.0208 | 120.7489 | 0.14932 | 0.000689 | -0.016578 | -0.020438 | 0.036265 | 0.090161 | -0.067295 | 120.6729 | 120.6578 | 120.6335 | 120.5145 | 0.66171 | 0.87016 | 0.7952 | 0.78885 | 1.1701 | 1.0215 | 1.0042 | 1.0004 | 1.0571 | 1.111 | 0.95352 | 120.7187 | 120.7036 | 120.6792 | 120.5603 | 0.70749 | 0.91594 | 0.84098 | 0.83463 | 120.0112 | 119.8777 | 119.9718 | 119.8383
1435.9688 | 121.8796 | -0.98877 | 120.7306 | 0.14474 | -0.00389 | -0.012 | -0.029595 | 0.040843 | 0.085583 | -0.067295 | 120.6592 | 120.6578 | 120.6335 | 120.5053 | 0.67087 | 0.87016 | 0.79978 | 0.80259 | 1.1335 | 0.98488 | 0.97677 | 0.95917 | 1.0296 | 1.0744 | 0.92148 | 120.705 | 120.7036 | 120.6792 | 120.5511 | 0.71664 | 0.91594 | 0.84556 | 0.84836 | 119.9883 | 119.8594 | 119.9626 | 119.8337
1437.6719 | 121.7422 | -1.03 | 120.7672 | 0.14932 | -0.00389 | -0.007421 | -0.01586 | 0.045421 | 0.090161 | -0.071874 | 120.6592 | 120.6486 | 120.6289 | 120.5099 | 0.67087 | 0.8839 | 0.80436 | 0.80259 | 1.1793 | 1.0261 | 1.0225 | 1.0141 | 1.0754 | 1.1201 | 0.95809 | 120.705 | 120.6944 | 120.6747 | 120.5557 | 0.71664 | 0.92967 | 0.85014 | 0.84836 | 119.9883 | 119.8548 | 119.958 | 119.8245
1439.4219 | 121.7972 | -0.97046 | 120.7626 | 0.14474 | -0.008469 | -0.002842 | -0.025017 | 0.040843 | 0.085583 | -0.067295 | 120.6729 | 120.6624 | 120.6335 | 120.5191 | 0.66629 | 0.87474 | 0.78605 | 0.78427 | 1.1152 | 0.96199 | 0.96762 | 0.94544 | 1.0113 | 1.056 | 0.90316 | 120.7187 | 120.7081 | 120.6792 | 120.5648 | 0.71207 | 0.92052 | 0.83182 | 0.83005 | 120.0067 | 119.8869 | 119.9672 | 119.8474
1441.125 | 121.8521 | -0.98877 | 120.7489 | 0.14017 | -0.008469 | -0.016578 | -0.029595 | 0.036265 | 0.085583 | -0.067295 | 120.6729 | 120.6624 | 120.6381 | 120.5145 | 0.66171 | 0.87932 | 0.79978 | 0.7797 | 1.1289 | 0.9803 | 0.97219 | 0.95917 | 1.025 | 1.0744 | 0.92148 | 120.7187 | 120.7081 | 120.6838 | 120.5603 | 0.70749 | 0.92509 | 0.84556 | 0.82547 | 120.0112 | 119.8732 | 119.9763 | 119.8383
1442.8906 | 121.7239 | -1.0208 | 120.7443 | 0.14474 | 0.000689 | -0.016578 | -0.020438 | 0.045421 | 0.090161 | -0.076452 | 120.6638 | 120.6486 | 120.6335 | 120.5145 | 0.67087 | 0.8839 | 0.79978 | 0.78885 | 1.1656 | 1.0215 | 1.0042 | 1.0004 | 1.0662 | 1.111 | 0.94436 | 120.7096 | 120.6944 | 120.6792 | 120.5603 | 0.71664 | 0.92967 | 0.84556 | 0.83463 | 119.9929 | 119.864 | 119.9626 | 119.8337
1444.6094 | 121.7422 | -1.0254 | 120.7443 | 0.14932 | -0.008469 | -0.012 | -0.025017 | 0.045421 | 0.090161 | -0.067295 | 120.6546 | 120.6395 | 120.6197 | 120.4962 | 0.69834 | 0.89763 | 0.8181 | 0.80259 | 1.1747 | 1.0169 | 1.0134 | 1.0004 | 1.0708 | 1.1156 | 0.9581 | 120.7004 | 120.6853 | 120.6655 | 120.542 | 0.74411 | 0.94341 | 0.86387 | 0.84836 | 119.9563 | 119.8365 | 119.9214 | 119.8016
1446.3438 | 121.8658 | -0.99792 | 120.7077 | 0.14017 | -0.00389 | -0.012 | -0.020438 | 0.049999 | 0.090161 | -0.071874 | 120.6546 | 120.6441 | 120.6243 | 120.5053 | 0.68002 | 0.88847 | 0.81352 | 0.80717 | 1.1381 | 0.99404 | 0.98592 | 0.97749 | 1.0479 | 1.0881 | 0.92605 | 120.7004 | 120.6898 | 120.6701 | 120.5511 | 0.7258 | 0.93425 | 0.85929 | 0.85294 | 119.9746 | 119.8411 | 119.9443 | 119.8108
1448.0938 | 121.8842 | -1.0437 | 120.6985 | 0.14474 | -0.013048 | -0.012 | -0.025017 | 0.036265 | 0.085583 | -0.067295 | 120.6272 | 120.6212 | 120.5923 | 120.4733 | 0.71207 | 0.9251 | 0.83641 | 0.84379 | 1.1884 | 1.0307 | 1.0317 | 1.0187 | 1.08 | 1.1293 | 0.97641 | 120.6729 | 120.6669 | 120.638 | 120.5191 | 0.75785 | 0.97088 | 0.88218 | 0.88957 | 119.9151 | 119.7908 | 119.8802 | 119.7559
1449.8438 | 121.8521 | -0.99792 | 120.7169 | 0.14474 | -0.008469 | -0.016578 | -0.025017 | 0.031687 | 0.090161 | -0.067295 | 120.6684 | 120.6578 | 120.6243 | 120.5145 | 0.6846 | 0.88847 | 0.80894 | 0.80717 | 1.1427 | 0.98946 | 0.98135 | 0.97291 | 1.0296 | 1.0881 | 0.93063 | 120.7141 | 120.7036 | 120.6701 | 120.5603 | 0.73038 | 0.93425 | 0.85472 | 0.85294 | 119.9838 | 119.8594 | 119.9397 | 119.8154
1451.5312 | 121.7697 | -1.0483 | 120.7581 | 0.14474 | -0.00389 | -0.012 | -0.025017 | 0.036265 | 0.090161 | -0.071874 | 120.6592 | 120.6486 | 120.6289 | 120.5099 | 0.68918 | 0.89763 | 0.8181 | 0.80717 | 1.193 | 1.0444 | 1.0363 | 1.0233 | 1.0845 | 1.1384 | 0.9764 | 120.705 | 120.6944 | 120.6747 | 120.5557 | 0.73496 | 0.94341 | 0.86387 | 0.85294 | 119.97 | 119.8411 | 119.9397 | 119.8108
1453.2812 | 121.7422 | -1.0666 | 120.7626 | 0.14474 | 0.005267 | -0.012 | -0.029595 | 0.040843 | 0.085583 | -0.058139 | 120.6455 | 120.6349 | 120.6152 | 120.5008 | 0.70291 | 0.90679 | 0.82725 | 0.81174 | 1.2113 | 1.0719 | 1.0546 | 1.037 | 1.1074 | 1.1522 | 1.0085 | 120.6912 | 120.6807 | 120.6609 | 120.5465 | 0.74869 | 0.95256 | 0.87303 | 0.85752 | 119.9426 | 119.8182 | 119.9122 | 119.7879
1455.0312 | 121.7789 | -1.03 | 120.7672 | 0.14474 | -0.00389 | -0.012 | -0.025017 | 0.045421 | 0.090161 | -0.071874 | 120.6638 | 120.6532 | 120.6289 | 120.5145 | 0.6846 | 0.89305 | 0.82725 | 0.80717 | 1.1747 | 1.0261 | 1.018 | 1.005 | 1.0754 | 1.1201 | 0.95809 | 120.7096 | 120.699 | 120.6747 | 120.5603 | 0.73038 | 0.93883 | 0.87303 | 0.85294 | 119.9792 | 119.8365 | 119.9443 | 119.8016
1456.7344 | 121.8613 | -1.0025 | 120.726 | 0.14932 | -0.00389 | -0.016578 | -0.020438 | 0.049999 | 0.085583 | -0.076452 | 120.6546 | 120.6486 | 120.6197 | 120.5008 | 0.69376 | 0.90221 | 0.82725 | 0.81632 | 1.1518 | 0.99861 | 0.98592 | 0.98206 | 1.0525 | 1.0881 | 0.92605 | 120.7004 | 120.6944 | 120.6655 | 120.5465 | 0.73953 | 0.94799 | 0.87303 | 0.8621 | 119.9609 | 119.8274 | 119.926 | 119.7925
1458.5 | 121.7194 | -1.0849 | 120.7214 | 0.14932 | 0.000689 | -0.007421 | -0.01586 | 0.036265 | 0.090161 | -0.067295 | 120.6455 | 120.6349 | 120.6106 | 120.5008 | 0.70749 | 0.90679 | 0.83183 | 0.81632 | 1.2342 | 1.0856 | 1.0775 | 1.069 | 1.1212 | 1.1751 | 1.0176 | 120.6912 | 120.6807 | 120.6564 | 120.5465 | 0.75327 | 0.95256 | 0.87761 | 0.8621 | 119.938 | 119.8136 | 119.9031 | 119.7788
1460.2656 | 121.8201 | -1.0254 | 120.7123 | 0.14932 | 0.000689 | -0.016578 | -0.020438 | 0.054577 | 0.090161 | -0.067295 | 120.6592 | 120.6395 | 120.6152 | 120.4916 | 0.69834 | 0.90679 | 0.83183 | 0.8209 | 1.1747 | 1.0261 | 1.0088 | 1.005 | 1.08 | 1.1156 | 0.9581 | 120.705 | 120.6853 | 120.6609 | 120.5374 | 0.74411 | 0.95256 | 0.87761 | 0.86668 | 119.9609 | 119.8274 | 119.9168 | 119.7833
1461.9688 | 121.8521 | -1.03 | 120.6985 | 0.14474 | 0.005267 | -0.016578 | -0.020438 | 0.040843 | 0.081005 | -0.071874 | 120.5768 | 120.5754 | 120.5419 | 120.4183 | 0.78074 | 0.98461 | 0.90966 | 0.90331 | 1.1747 | 1.0352 | 1.0134 | 1.0095 | 1.0708 | 1.111 | 0.95809 | 120.6226 | 120.6211 | 120.5877 | 120.4641 | 0.82652 | 1.0304 | 0.95544 | 0.94908 | 119.7961 | 119.6671 | 119.7612 | 119.6322
1463.7344 | 121.788 | -1.0437 | 120.7443 | 0.14474 | -0.00389 | -0.007421 | -0.01586 | 0.040843 | 0.085583 | -0.062717 | 120.6363 | 120.6257 | 120.606 | 120.487 | 0.71207 | 0.91136 | 0.84557 | 0.83921 | 1.1884 | 1.0398 | 1.0363 | 1.0278 | 1.0845 | 1.1293 | 0.98098 | 120.6821 | 120.6715 | 120.6518 | 120.5328 | 0.75785 | 0.95714 | 0.89134 | 0.88499 | 119.9242 | 119.7907 | 119.8939 | 119.7604
1465.4844 | 121.7697 | -1.0757 | 120.726 | 0.14474 | -0.00389 | -0.012 | -0.020438 | 0.040843 | 0.085583 | -0.071874 | 120.6546 | 120.6532 | 120.6152 | 120.5008 | 0.70291 | 0.90679 | 0.8181 | 0.81632 | 1.2205 | 1.0719 | 1.0637 | 1.0553 | 1.1166 | 1.1613 | 1.0039 | 120.7004 | 120.699 | 120.6609 | 120.5465 | 0.74869 | 0.95256 | 0.86387 | 0.8621 | 119.9517 | 119.8365 | 119.9122 | 119.7971
1467.1875 | 121.8521 | -1.0712 | 120.6528 | 0.14932 | 0.005267 | -0.012 | -0.020438 | 0.040843 | 0.085583 | -0.067295 | 120.5905 | 120.5845 | 120.5602 | 120.4366 | 0.75785 | 0.9663 | 0.89135 | 0.88499 | 1.2205 | 1.0764 | 1.0592 | 1.0507 | 1.112 | 1.1567 | 1.0039 | 120.6363 | 120.6303 | 120.606 | 120.4824 | 0.80363 | 1.0121 | 0.93713 | 0.93077 | 119.8327 | 119.6992 | 119.8024 | 119.6689
1468.9531 | 121.8155 | -1.1078 | 120.6528 | 0.1539 | 0.000689 | -0.012 | -0.020438 | 0.049999 | 0.090161 | -0.071874 | 120.586 | 120.5616 | 120.5465 | 120.4275 | 0.77616 | 0.98919 | 0.91424 | 0.90331 | 1.2617 | 1.1085 | 1.0958 | 1.0874 | 1.1578 | 1.1979 | 1.0359 | 120.6317 | 120.6074 | 120.5923 | 120.4733 | 0.82194 | 1.035 | 0.96002 | 0.94908 | 119.8098 | 119.6717 | 119.7703 | 119.6322
1470.7188 | 121.8338 | -1.0574 | 120.6802 | 0.14932 | -0.00389 | -0.016578 | -0.025017 | 0.045421 | 0.090161 | -0.071874 | 120.618 | 120.612 | 120.5785 | 120.4595 | 0.74412 | 0.95715 | 0.87304 | 0.87126 | 1.2068 | 1.0535 | 1.0409 | 1.0324 | 1.1029 | 1.1476 | 0.98556 | 120.6638 | 120.6578 | 120.6243 | 120.5053 | 0.78989 | 1.0029 | 0.91881 | 0.91704 | 119.8739 | 119.745 | 119.8344 | 119.7055
1472.4219 | 121.8567 | -1.0941 | 120.639 | 0.14017 | 0.005267 | -0.021157 | -0.020438 | 0.040843 | 0.081005 | -0.067295 | 120.5997 | 120.5845 | 120.5602 | 120.4458 | 0.76243 | 0.97088 | 0.89135 | 0.88957 | 1.2342 | 1.0993 | 1.0729 | 1.0736 | 1.1349 | 1.1751 | 1.0268 | 120.6455 | 120.6303 | 120.606 | 120.4916 | 0.80821 | 1.0167 | 0.93713 | 0.93535 | 119.8373 | 119.7083 | 119.7978 | 119.6689
1474.1875 | 121.756 | -1.1765 | 120.6345 | 0.13559 | 0.000689 | -0.012 | -0.020438 | 0.049999 | 0.09474 | -0.076452 | 120.5493 | 120.5387 | 120.5099 | 120.3954 | 0.81279 | 1.0304 | 0.93713 | 0.93078 | 1.312 | 1.1771 | 1.1645 | 1.156 | 1.2265 | 1.2712 | 1.1 | 120.5951 | 120.5845 | 120.5556 | 120.4412 | 0.85857 | 1.0762 | 0.98291 | 0.97655 | 119.7365 | 119.6122 | 119.6971 | 119.5727
1475.9375 | 121.8063 | -1.1536 | 120.6207 | 0.14932 | 0.000689 | -0.016578 | -0.020438 | 0.045421 | 0.09474 | -0.067295 | 120.5447 | 120.5387 | 120.5144 | 120.3909 | 0.81737 | 1.0304 | 0.94629 | 0.94451 | 1.3029 | 1.1543 | 1.137 | 1.1331 | 1.199 | 1.2483 | 1.0863 | 120.5905 | 120.5845 | 120.5602 | 120.4366 | 0.86315 | 1.0762 | 0.99207 | 0.99029 | 119.7274 | 119.5985 | 119.6971 | 119.5681
1477.625 | 121.7651 | -1.1581 | 120.6299 | 0.14932 | 0.005267 | -0.007421 | -0.020438 | 0.049999 | 0.090161 | -0.058139 | 120.5539 | 120.5387 | 120.5099 | 120.3954 | 0.81279 | 1.0258 | 0.94629 | 0.93078 | 1.3075 | 1.1634 | 1.1507 | 1.1377 | 1.2081 | 1.2483 | 1.1 | 120.5997 | 120.5845 | 120.5556 | 120.4412 | 0.85857 | 1.0716 | 0.99207 | 0.97655 | 119.7411 | 119.6076 | 119.6971 | 119.5636
1479.3906 | 121.8338 | -1.1673 | 120.5933 | 0.13559 | 0.000689 | -0.007421 | -0.025017 | 0.049999 | 0.085583 | -0.071874 | 120.531 | 120.5158 | 120.487 | 120.368 | 0.83568 | 1.0441 | 0.97376 | 0.9674 | 1.3029 | 1.168 | 1.1599 | 1.1423 | 1.2173 | 1.2529 | 1.0954 | 120.5768 | 120.5616 | 120.5327 | 120.4137 | 0.88146 | 1.0899 | 1.0195 | 1.0132 | 119.6953 | 119.5572 | 119.6513 | 119.5132
1481.0938 | 121.8063 | -1.1581 | 120.607 | 0.14932 | -0.00389 | -0.021157 | -0.029595 | 0.045421 | 0.090161 | -0.071874 | 120.5127 | 120.5021 | 120.4595 | 120.3588 | 0.86315 | 1.0808 | 0.9875 | 0.98113 | 1.3075 | 1.1543 | 1.137 | 1.1285 | 1.2036 | 1.2483 | 1.0863 | 120.5585 | 120.5479 | 120.5053 | 120.4046 | 0.90893 | 1.1265 | 1.0333 | 1.0269 | 119.6495 | 119.5252 | 119.5963 | 119.472
1482.8594 | 121.8246 | -1.2634 | 120.4971 | 0.14017 | 0.000689 | -0.007421 | -0.020438 | 0.031687 | 0.090161 | -0.067295 | 120.4349 | 120.4243 | 120.4 | 120.2947 | 0.9364 | 1.1357 | 1.0608 | 1.059 | 1.4036 | 1.2641 | 1.256 | 1.243 | 1.2951 | 1.3536 | 1.1961 | 120.4806 | 120.47 | 120.4458 | 120.3405 | 0.98218 | 1.1815 | 1.1065 | 1.1047 | 119.4985 | 119.3741 | 119.4636 | 119.3392
1484.625 | 121.8018 | -1.2817 | 120.5246 | 0.14474 | 0.000689 | -0.007421 | -0.01586 | 0.045421 | 0.085583 | -0.067295 | 120.4394 | 120.4334 | 120.4 | 120.2993 | 0.93182 | 1.1311 | 1.0516 | 1.0544 | 1.4265 | 1.2824 | 1.2743 | 1.2659 | 1.3272 | 1.3673 | 1.2144 | 120.4852 | 120.4792 | 120.4458 | 120.3451 | 0.9776 | 1.1769 | 1.0974 | 1.1002 | 119.5076 | 119.3878 | 119.4682 | 119.3484
1486.3281 | 121.8933 | -1.2634 | 120.4834 | 0.14474 | -0.00389 | -0.007421 | -0.025017 | 0.036265 | 0.090161 | -0.067295 | 120.4578 | 120.4426 | 120.4183 | 120.3084 | 0.91809 | 1.1265 | 1.0516 | 1.0452 | 1.4082 | 1.2595 | 1.256 | 1.2384 | 1.2997 | 1.3536 | 1.1961 | 120.5035 | 120.4884 | 120.4641 | 120.3542 | 0.96387 | 1.1723 | 1.0974 | 1.091 | 119.5397 | 119.4062 | 119.5002 | 119.3667
1488.0781 | 121.875 | -1.2863 | 120.4742 | 0.1539 | 0.005267 | -0.012 | -0.025017 | 0.040843 | 0.090161 | -0.071874 | 120.3982 | 120.3876 | 120.3588 | 120.2398 | 0.96845 | 1.1815 | 1.102 | 1.1002 | 1.4402 | 1.2916 | 1.2743 | 1.2613 | 1.3272 | 1.3765 | 1.2144 | 120.444 | 120.4334 | 120.4046 | 120.2855 | 1.0142 | 1.2272 | 1.1477 | 1.1459 | 119.4298 | 119.2963 | 119.3903 | 119.2568
1489.8438 | 121.9025 | -1.268 | 120.4788 | 0.14017 | 0.000689 | -0.012 | -0.020438 | 0.045421 | 0.090161 | -0.071874 | 120.4028 | 120.3922 | 120.3588 | 120.2535 | 0.98218 | 1.1769 | 1.1065 | 1.1002 | 1.4082 | 1.2687 | 1.256 | 1.2476 | 1.3134 | 1.3582 | 1.1961 | 120.4486 | 120.438 | 120.4046 | 120.2993 | 1.028 | 1.2227 | 1.1523 | 1.1459 | 119.4206 | 119.2963 | 119.3766 | 119.2522
1491.5469 | 121.8155 | -1.3321 | 120.4834 | 0.14932 | 0.000689 | -0.007421 | -0.020438 | 0.045421 | 0.085583 | -0.071874 | 120.3845 | 120.3739 | 120.345 | 120.2398 | 0.98218 | 1.1906 | 1.1111 | 1.1231 | 1.4814 | 1.3328 | 1.3247 | 1.3117 | 1.3775 | 1.4177 | 1.2602 | 120.4303 | 120.4197 | 120.3908 | 120.2855 | 1.028 | 1.2364 | 1.1569 | 1.1688 | 119.4023 | 119.2734 | 119.3629 | 119.2339
1493.3125 | 121.7651 | -1.3824 | 120.4468 | 0.14474 | 0.005267 | -0.007421 | -0.020438 | 0.040843 | 0.09474 | -0.067295 | 120.3799 | 120.3647 | 120.3359 | 120.2214 | 1.0051 | 1.2089 | 1.134 | 1.1231 | 1.5272 | 1.3877 | 1.375 | 1.362 | 1.4233 | 1.4772 | 1.3152 | 120.4257 | 120.4105 | 120.3817 | 120.2672 | 1.0509 | 1.2547 | 1.1798 | 1.1688 | 119.3748 | 119.2459 | 119.3308 | 119.2019
1495.0781 | 121.756 | -1.3687 | 120.4651 | 0.14017 | -0.00389 | -0.012 | -0.025017 | 0.049999 | 0.090161 | -0.062717 | 120.3708 | 120.3602 | 120.3359 | 120.2214 | 1.0188 | 1.2181 | 1.1432 | 1.1322 | 1.5089 | 1.3648 | 1.3567 | 1.3437 | 1.4187 | 1.4589 | 1.306 | 120.4165 | 120.4059 | 120.3817 | 120.2672 | 1.0646 | 1.2639 | 1.1889 | 1.178 | 119.352 | 119.2276 | 119.3171 | 119.1927
1496.7812 | 121.8155 | -1.355 | 120.4605 | 0.14932 | 0.000689 | -0.016578 | -0.01586 | 0.045421 | 0.090161 | -0.067295 | 120.3799 | 120.3693 | 120.3405 | 120.2214 | 1.0051 | 1.2044 | 1.1294 | 1.1276 | 1.5043 | 1.3557 | 1.3384 | 1.3391 | 1.4004 | 1.4451 | 1.2877 | 120.4257 | 120.4151 | 120.3862 | 120.2672 | 1.0509 | 1.2501 | 1.1752 | 1.1734 | 119.3748 | 119.2505 | 119.3354 | 119.211
1498.5469 | 121.8887 | -1.3046 | 120.433 | 0.14474 | -0.00389 | -0.012 | -0.025017 | 0.040843 | 0.090161 | -0.071874 | 120.3799 | 120.3693 | 120.3405 | 120.2306 | 1.0051 | 1.2089 | 1.1294 | 1.1276 | 1.4494 | 1.3007 | 1.2926 | 1.2796 | 1.3455 | 1.3948 | 1.2328 | 120.4257 | 120.4151 | 120.3862 | 120.2764 | 1.0509 | 1.2547 | 1.1752 | 1.1734 | 119.3748 | 119.2505 | 119.3354 | 119.211
1500.2344 | 121.8796 | -1.2451 | 120.52 | 0.14474 | 0.000689 | -0.016578 | -0.020438 | 0.040843 | 0.090161 | -0.071874 | 120.444 | 120.4334 | 120.4 | 120.2901 | 0.93182 | 1.154 | 1.0608 | 1.0498 | 1.3899 | 1.2458 | 1.2285 | 1.2247 | 1.286 | 1.3353 | 1.1732 | 120.4898 | 120.4792 | 120.4458 | 120.3359 | 0.9776 | 1.1998 | 1.1065 | 1.0956 | 119.5122 | 119.3833 | 119.4682 | 119.3392
1502 | 121.7697 | -1.3275 | 120.5109 | 0.14474 | 0.005267 | -0.012 | -0.01586 | 0.045421 | 0.085583 | -0.067295 | 120.4257 | 120.406 | 120.3954 | 120.2672 | 0.95929 | 1.1769 | 1.0836 | 1.091 | 1.4723 | 1.3328 | 1.3155 | 1.3117 | 1.3729 | 1.4131 | 1.2602 | 120.4715 | 120.4517 | 120.4412 | 120.313 | 1.0051 | 1.2227 | 1.1294 | 1.1368 | 119.4664 | 119.3421 | 119.4361 | 119.3118
1503.7812 | 121.756 | -1.3458 | 120.4834 | 0.14932 | 0.000689 | -0.012 | -0.025017 | 0.036265 | 0.090161 | -0.062717 | 120.3982 | 120.3785 | 120.3542 | 120.2352 | 0.99134 | 1.1998 | 1.1157 | 1.1139 | 1.4951 | 1.3465 | 1.3338 | 1.3208 | 1.3821 | 1.436 | 1.2831 | 120.444 | 120.4243 | 120.4 | 120.2809 | 1.0371 | 1.2456 | 1.1615 | 1.1597 | 119.4069 | 119.2825 | 119.3629 | 119.2385
1505.4844 | 121.7834 | -1.3412 | 120.4742 | 0.1539 | 0.009846 | -0.007421 | -0.020438 | 0.045421 | 0.085583 | -0.067295 | 120.3891 | 120.3785 | 120.3542 | 120.2398 | 0.98676 | 1.1998 | 1.1203 | 1.1276 | 1.4951 | 1.3511 | 1.3338 | 1.3208 | 1.3867 | 1.4268 | 1.274 | 120.4349 | 120.4243 | 120.4 | 120.2855 | 1.0325 | 1.2456 | 1.166 | 1.1734 | 119.4023 | 119.2688 | 119.3674 | 119.2339
1507.25 | 121.7789 | -1.3641 | 120.4605 | 0.14474 | 0.005267 | -0.007421 | -0.020438 | 0.036265 | 0.085583 | -0.067295 | 120.3845 | 120.3785 | 120.345 | 120.2306 | 0.99592 | 1.2089 | 1.1294 | 1.1276 | 1.5089 | 1.3694 | 1.3567 | 1.3437 | 1.4004 | 1.4497 | 1.2968 | 120.4303 | 120.4243 | 120.3908 | 120.2764 | 1.0417 | 1.2547 | 1.1752 | 1.1734 | 119.3886 | 119.2551 | 119.3491 | 119.2156
1509.0156 | 121.8658 | -1.3092 | 120.4559 | 0.14474 | 0.000689 | -0.012 | -0.01586 | 0.040843 | 0.085583 | -0.067295 | 120.4074 | 120.3922 | 120.3725 | 120.2535 | 0.98218 | 1.186 | 1.1065 | 1.1002 | 1.4539 | 1.3099 | 1.2972 | 1.2933 | 1.35 | 1.3948 | 1.2419 | 120.4532 | 120.438 | 120.4183 | 120.2993 | 1.028 | 1.2318 | 1.1523 | 1.1459 | 119.4252 | 119.3009 | 119.3903 | 119.266
1510.7031 | 121.8521 | -1.3092 | 120.4788 | 0.14932 | 0.000689 | -0.016578 | -0.025017 | 0.031687 | 0.090161 | -0.071874 | 120.4211 | 120.4014 | 120.3771 | 120.2626 | 0.97303 | 1.186 | 1.102 | 1.0956 | 1.4585 | 1.3099 | 1.2926 | 1.2842 | 1.3409 | 1.3994 | 1.2373 | 120.4669 | 120.4472 | 120.4229 | 120.3084 | 1.0188 | 1.2318 | 1.1477 | 1.1414 | 119.4481 | 119.3192 | 119.4041 | 119.2751
1512.4688 | 121.7606 | -1.3046 | 120.5612 | 0.1539 | 0.000689 | -0.012 | -0.01586 | 0.036265 | 0.085583 | -0.067295 | 120.4349 | 120.4288 | 120.4 | 120.2855 | 0.95014 | 1.1632 | 1.0791 | 1.0727 | 1.4585 | 1.3053 | 1.2926 | 1.2888 | 1.3409 | 1.3902 | 1.2373 | 120.4806 | 120.4746 | 120.4458 | 120.3313 | 0.99591 | 1.2089 | 1.1248 | 1.1185 | 119.4847 | 119.3558 | 119.4498 | 119.3209
1514.2344 | 121.875 | -1.181 | 120.5795 | 0.14017 | 0.000689 | -0.021157 | -0.01586 | 0.040843 | 0.085583 | -0.067295 | 120.4532 | 120.438 | 120.4137 | 120.2993 | 0.94098 | 1.1494 | 1.0699 | 1.0681 | 1.3212 | 1.1817 | 1.1599 | 1.1652 | 1.2219 | 1.2666 | 1.1137 | 120.499 | 120.4838 | 120.4595 | 120.3451 | 0.98676 | 1.1952 | 1.1157 | 1.1139 | 119.5122 | 119.3833 | 119.4727 | 119.3438
1515.9844 | 121.8155 | -1.268 | 120.5429 | 0.14474 | 0.000689 | -0.007421 | -0.020438 | 0.045421 | 0.081005 | -0.062717 | 120.4669 | 120.4472 | 120.4183 | 120.3084 | 0.94556 | 1.1448 | 1.0562 | 1.059 | 1.4127 | 1.2687 | 1.2606 | 1.2476 | 1.3134 | 1.349 | 1.2053 | 120.5127 | 120.4929 | 120.4641 | 120.3542 | 0.99133 | 1.1906 | 1.1019 | 1.1047 | 119.5214 | 119.4107 | 119.4727 | 119.3621
1517.6719 | 121.8246 | -1.2863 | 120.5521 | 0.14474 | 0.000689 | 0.001736 | -0.020438 | 0.040843 | 0.090161 | -0.071874 | 120.4715 | 120.4609 | 120.432 | 120.3268 | 0.92724 | 1.122 | 1.047 | 1.0452 | 1.4311 | 1.287 | 1.2881 | 1.2659 | 1.3272 | 1.3765 | 1.2144 | 120.5173 | 120.5067 | 120.4778 | 120.3725 | 0.97302 | 1.1677 | 1.0928 | 1.091 | 119.5442 | 119.4245 | 119.5048 | 119.385
1519.4375 | 121.8063 | -1.2543 | 120.6116 | 0.14932 | -0.00389 | -0.007421 | -0.020438 | 0.045421 | 0.090161 | -0.067295 | 120.4761 | 120.4609 | 120.4458 | 120.3359 | 0.90435 | 1.1265 | 1.047 | 1.0452 | 1.4036 | 1.2504 | 1.2469 | 1.2338 | 1.2997 | 1.3444 | 1.187 | 120.5218 | 120.5067 | 120.4915 | 120.3817 | 0.95013 | 1.1723 | 1.0928 | 1.091 | 119.5717 | 119.4291 | 119.5414 | 119.3987
1521.2031 | 121.8246 | -1.236 | 120.5795 | 0.14474 | 0.000689 | -0.012 | -0.020438 | 0.045421 | 0.090161 | -0.071874 | 120.5219 | 120.5113 | 120.487 | 120.368 | 0.87231 | 1.0808 | 1.0012 | 0.99945 | 1.3807 | 1.2367 | 1.224 | 1.2155 | 1.2814 | 1.3261 | 1.1641 | 120.5676 | 120.557 | 120.5327 | 120.4137 | 0.91808 | 1.1265 | 1.047 | 1.0452 | 119.6495 | 119.5206 | 119.6147 | 119.4857
1522.8906 | 121.7972 | -1.0895 | 120.7764 | 0.14474 | 0.005267 | -0.012 | -0.01586 | 0.040843 | 0.090161 | -0.067295 | 120.6592 | 120.6441 | 120.6197 | 120.5099 | 0.75327 | 0.95715 | 0.87304 | 0.87126 | 1.2342 | 1.0947 | 1.0775 | 1.0736 | 1.1303 | 1.1796 | 1.0222 | 120.705 | 120.6898 | 120.6655 | 120.5557 | 0.79905 | 1.0029 | 0.91881 | 0.91704 | 119.9059 | 119.7862 | 119.8665 | 119.7467
1524.6562 | 121.8979 | -1.0483 | 120.7123 | 0.14474 | 0.000689 | -0.012 | -0.025017 | 0.040843 | 0.090161 | -0.067295 | 120.6684 | 120.6532 | 120.6243 | 120.5145 | 0.72581 | 0.93883 | 0.85472 | 0.85295 | 1.193 | 1.049 | 1.0363 | 1.0233 | 1.0891 | 1.1384 | 0.98098 | 120.7141 | 120.699 | 120.6701 | 120.5603 | 0.77158 | 0.98461 | 0.9005 | 0.89872 | 119.9426 | 119.8136 | 119.8985 | 119.7696
1526.3594 | 121.8658 | -1.0483 | 120.7535 | 0.14017 | 0.005267 | -0.012 | -0.025017 | 0.040843 | 0.090161 | -0.067295 | 120.6775 | 120.6761 | 120.6426 | 120.5328 | 0.71207 | 0.92052 | 0.83641 | 0.83921 | 1.1884 | 1.0535 | 1.0363 | 1.0233 | 1.0891 | 1.1384 | 0.98098 | 120.7233 | 120.7219 | 120.6884 | 120.5786 | 0.75785 | 0.9663 | 0.88218 | 0.88499 | 119.9655 | 119.8411 | 119.9306 | 119.8062
1528.1094 | 121.7697 | -1.0254 | 120.8221 | 0.14932 | 0.005267 | -0.012 | -0.020438 | 0.036265 | 0.090161 | -0.067295 | 120.7279 | 120.7173 | 120.6884 | 120.5786 | 0.67544 | 0.87474 | 0.80436 | 0.79343 | 1.1747 | 1.0307 | 1.0134 | 1.005 | 1.0617 | 1.1156 | 0.9581 | 120.7737 | 120.7631 | 120.7342 | 120.6244 | 0.72122 | 0.92052 | 0.85014 | 0.83921 | 120.0524 | 119.9235 | 120.013 | 119.8841
1529.8125 | 121.8338 | -1.0391 | 120.7535 | 0.14474 | 0.000689 | -0.016578 | -0.025017 | 0.045421 | 0.09474 | -0.071874 | 120.7004 | 120.6944 | 120.6564 | 120.5465 | 0.70749 | 0.91594 | 0.84099 | 0.82548 | 1.1839 | 1.0398 | 1.0225 | 1.0141 | 1.0845 | 1.1339 | 0.96725 | 120.7462 | 120.7402 | 120.7021 | 120.5923 | 0.75327 | 0.96172 | 0.88676 | 0.87125 | 119.9929 | 119.8594 | 119.9489 | 119.8154
1531.5781 | 121.8842 | -1.0162 | 120.7718 | 0.14474 | 0.000689 | -0.012 | -0.020438 | 0.040843 | 0.085583 | -0.067295 | 120.7142 | 120.6898 | 120.6564 | 120.5465 | 0.69376 | 0.90221 | 0.83183 | 0.82548 | 1.161 | 1.0169 | 1.0042 | 0.9958 | 1.0571 | 1.1018 | 0.94894 | 120.7599 | 120.7356 | 120.7021 | 120.5923 | 0.73953 | 0.94799 | 0.87761 | 0.87125 | 120.0204 | 119.8823 | 119.9626 | 119.8245
1533.2656 | 121.875 | -1.0849 | 120.7077 | 0.14474 | 0.000689 | -0.021157 | -0.020438 | 0.045421 | 0.090161 | -0.062717 | 120.6546 | 120.6441 | 120.6106 | 120.5053 | 0.75327 | 0.96172 | 0.88219 | 0.87584 | 1.2296 | 1.0856 | 1.0637 | 1.0645 | 1.1303 | 1.1751 | 1.0222 | 120.7004 | 120.6898 | 120.6564 | 120.5511 | 0.79905 | 1.0075 | 0.92797 | 0.92161 | 119.9014 | 119.7724 | 119.8573 | 119.7284
1535.0156 | 121.9299 | -1.0757 | 120.7169 | 0.14017 | -0.00389 | -0.012 | -0.029595 | 0.040843 | 0.085583 | -0.076452 | 120.6546 | 120.6486 | 120.6106 | 120.5053 | 0.75327 | 0.95715 | 0.88677 | 0.88042 | 1.2159 | 1.0719 | 1.0637 | 1.0461 | 1.1166 | 1.1613 | 0.99929 | 120.7004 | 120.6944 | 120.6564 | 120.5511 | 0.79905 | 1.0029 | 0.93255 | 0.92619 | 119.9014 | 119.7679 | 119.8573 | 119.7238
1536.7031 | 121.8292 | -1.0895 | 120.7581 | 0.1539 | 0.000689 | -0.012 | -0.020438 | 0.045421 | 0.085583 | -0.062717 | 120.6638 | 120.6578 | 120.6289 | 120.5191 | 0.73954 | 0.95715 | 0.87304 | 0.86668 | 1.2434 | 1.0902 | 1.0775 | 1.069 | 1.1349 | 1.1751 | 1.0268 | 120.7096 | 120.7036 | 120.6747 | 120.5648 | 0.78532 | 1.0029 | 0.91881 | 0.91246 | 119.9242 | 119.7908 | 119.8894 | 119.7559
1538.4688 | 121.7789 | -1.0666 | 120.7718 | 0.13559 | 0.009846 | -0.012 | -0.020438 | 0.045421 | 0.081005 | -0.071874 | 120.6958 | 120.6898 | 120.6518 | 120.5465 | 0.72123 | 0.92052 | 0.84557 | 0.83921 | 1.2022 | 1.0764 | 1.0546 | 1.0462 | 1.112 | 1.1476 | 0.99472 | 120.7416 | 120.7356 | 120.6976 | 120.5923 | 0.767 | 0.9663 | 0.89134 | 0.88499 | 119.9746 | 119.8503 | 119.9306 | 119.8062
1540.2344 | 121.8292 | -1.0208 | 120.813 | 0.14017 | 0.000689 | -0.012 | -0.025017 | 0.049999 | 0.085583 | -0.062717 | 120.7462 | 120.7265 | 120.693 | 120.5786 | 0.68002 | 0.8839 | 0.80894 | 0.80259 | 1.161 | 1.0215 | 1.0088 | 0.9958 | 1.0708 | 1.1064 | 0.9581 | 120.792 | 120.7722 | 120.7388 | 120.6244 | 0.7258 | 0.92967 | 0.85472 | 0.84836 | 120.0662 | 119.9373 | 120.013 | 119.8841
1541.9219 | 121.9116 | -0.97961 | 120.8359 | 0.14474 | 0.005267 | -0.012 | -0.025017 | 0.049999 | 0.090161 | -0.067295 | 120.7599 | 120.7585 | 120.7159 | 120.6061 | 0.65255 | 0.85643 | 0.78605 | 0.77054 | 1.1244 | 0.98488 | 0.96761 | 0.9546 | 1.0296 | 1.0698 | 0.91232 | 120.8057 | 120.8043 | 120.7617 | 120.6518 | 0.69833 | 0.9022 | 0.83182 | 0.81632 | 120.1074 | 119.9739 | 120.0633 | 119.9298
1543.6719 | 121.907 | -0.9201 | 120.8725 | 0.14932 | 0.000689 | -0.007421 | -0.025017 | 0.045421 | 0.085583 | -0.067295 | 120.792 | 120.7814 | 120.7479 | 120.6381 | 0.62966 | 0.83812 | 0.74942 | 0.75223 | 1.0694 | 0.92079 | 0.91268 | 0.89509 | 0.96553 | 1.0057 | 0.85281 | 120.8378 | 120.8272 | 120.7937 | 120.6839 | 0.67544 | 0.88389 | 0.7952 | 0.798 | 120.1623 | 120.0426 | 120.1183 | 119.9985
1545.375 | 121.8018 | -0.98419 | 120.8633 | 0.14474 | 0.000689 | -0.012 | -0.020438 | 0.045421 | 0.081005 | -0.067295 | 120.7874 | 120.7768 | 120.7479 | 120.6381 | 0.62509 | 0.83354 | 0.75858 | 0.74307 | 1.1289 | 0.98488 | 0.97219 | 0.96375 | 1.0296 | 1.0652 | 0.9169 | 120.8332 | 120.8226 | 120.7937 | 120.6839 | 0.67086 | 0.87931 | 0.80435 | 0.78885 | 120.1623 | 120.0288 | 120.1228 | 119.9894
1547.125 | 121.8475 | -0.94299 | 120.8954 | 0.14932 | 0.005267 | -0.016578 | -0.029595 | 0.040843 | 0.085583 | -0.067295 | 120.8011 | 120.7952 | 120.7617 | 120.6473 | 0.62051 | 0.82438 | 0.74484 | 0.74307 | 1.0923 | 0.94826 | 0.92641 | 0.9134 | 0.98384 | 1.0286 | 0.8757 | 120.8469 | 120.8409 | 120.8074 | 120.6931 | 0.66628 | 0.87016 | 0.79062 | 0.78885 | 120.1806 | 120.0563 | 120.1412 | 120.0168
1548.8125 | 121.875 | -0.90179 | 120.8908 | 0.14474 | 0.005267 | -0.012 | -0.025017 | 0.045421 | 0.090161 | -0.067295 | 120.8469 | 120.8318 | 120.7937 | 120.6885 | 0.5793 | 0.78318 | 0.70821 | 0.70187 | 1.0465 | 0.90706 | 0.88979 | 0.87678 | 0.94722 | 0.99196 | 0.8345 | 120.8927 | 120.8776 | 120.8395 | 120.7343 | 0.62508 | 0.82895 | 0.75399 | 0.74764 | 120.2676 | 120.1387 | 120.2144 | 120.0855
1550.5781 | 121.8384 | -0.87891 | 120.9869 | 0.14474 | 0.005267 | -0.012 | -0.025017 | 0.045421 | 0.090161 | -0.067295 | 120.8607 | 120.8455 | 120.8074 | 120.6977 | 0.57015 | 0.76945 | 0.69448 | 0.68813 | 1.0236 | 0.88417 | 0.86691 | 0.85389 | 0.92433 | 0.96907 | 0.81161 | 120.9064 | 120.8913 | 120.8532 | 120.7434 | 0.61592 | 0.81522 | 0.74025 | 0.73391 | 120.2905 | 120.1662 | 120.2373 | 120.113
1552.2656 | 121.7926 | -0.83771 | 121.0281 | 0.14474 | 0.009846 | -0.012 | -0.020438 | 0.049999 | 0.081005 | -0.062717 | 120.911 | 120.905 | 120.8761 | 120.7663 | 0.51063 | 0.71451 | 0.63954 | 0.63319 | 0.98245 | 0.84755 | 0.82571 | 0.81727 | 0.88771 | 0.91871 | 0.77499 | 120.9568 | 120.9508 | 120.9219 | 120.8121 | 0.55641 | 0.76028 | 0.68532 | 0.67897 | 120.4004 | 120.2715 | 120.3655 | 120.2366
1554.0312 | 121.9254 | -0.77362 | 121.0373 | 0.14932 | 0.000689 | -0.021157 | -0.020438 | 0.040843 | 0.090161 | -0.067295 | 120.9797 | 120.9646 | 120.9356 | 120.8259 | 0.44196 | 0.65041 | 0.57086 | 0.57368 | 0.92294 | 0.77431 | 0.75246 | 0.75318 | 0.81446 | 0.86378 | 0.70633 | 121.0255 | 121.0103 | 120.9814 | 120.8716 | 0.48773 | 0.69619 | 0.61664 | 0.61945 | 120.5377 | 120.4088 | 120.4937 | 120.3648
1555.7812 | 121.8842 | -0.76446 | 121.0648 | 0.14017 | -0.008469 | -0.012 | -0.025017 | 0.040843 | 0.085583 | -0.071874 | 120.9705 | 120.96 | 120.9311 | 120.8167 | 0.45111 | 0.65957 | 0.58002 | 0.58283 | 0.90463 | 0.756 | 0.75246 | 0.73945 | 0.80531 | 0.85005 | 0.69259 | 121.0163 | 121.0058 | 120.9768 | 120.8625 | 0.49689 | 0.70535 | 0.62579 | 0.62861 | 120.5194 | 120.3905 | 120.4799 | 120.351
1557.5312 | 121.9254 | -0.70953 | 121.0831 | 0.14474 | 0.005267 | -0.016578 | -0.025017 | 0.040843 | 0.085583 | -0.071874 | 121.0118 | 120.9966 | 120.9677 | 120.8579 | 0.41907 | 0.62295 | 0.54797 | 0.55079 | 0.85428 | 0.7148 | 0.69296 | 0.68452 | 0.75038 | 0.79512 | 0.63766 | 121.0575 | 121.0424 | 121.0135 | 120.9037 | 0.46484 | 0.66872 | 0.59375 | 0.59656 | 120.5927 | 120.4638 | 120.5486 | 120.4197
1559.2969 | 121.9345 | -0.72784 | 121.0648 | 0.14474 | 0.005267 | -0.016578 | -0.025017 | 0.040843 | 0.076426 | -0.071874 | 121.0026 | 120.992 | 120.9585 | 120.8442 | 0.42822 | 0.63668 | 0.55713 | 0.55536 | 0.87259 | 0.73311 | 0.71127 | 0.70283 | 0.76869 | 0.80427 | 0.65597 | 121.0484 | 121.0378 | 121.0043 | 120.89 | 0.474 | 0.68246 | 0.6029 | 0.60114 | 120.5744 | 120.4455 | 120.5303 | 120.4014
1561.0625 | 121.8979 | -0.73242 | 121.0693 | 0.14017 | -0.00389 | -0.016578 | -0.020438 | 0.036265 | 0.081005 | -0.067295 | 121.0072 | 120.9875 | 120.954 | 120.8488 | 0.43738 | 0.64126 | 0.56628 | 0.55079 | 0.87259 | 0.72853 | 0.71584 | 0.71198 | 0.76869 | 0.81343 | 0.66513 | 121.053 | 121.0332 | 120.9997 | 120.8945 | 0.48316 | 0.68704 | 0.61206 | 0.59656 | 120.5698 | 120.4409 | 120.5166 | 120.3877
1562.8438 | 121.9299 | -0.81482 | 120.9778 | 0.14932 | 0.000689 | -0.012 | -0.020438 | 0.040843 | 0.085583 | -0.067295 | 120.9522 | 120.9371 | 120.9036 | 120.7892 | 0.47858 | 0.68704 | 0.61207 | 0.60572 | 0.96414 | 0.81551 | 0.80282 | 0.79438 | 0.85566 | 0.9004 | 0.74752 | 120.998 | 120.9829 | 120.9494 | 120.835 | 0.52436 | 0.73282 | 0.65784 | 0.6515 | 120.4736 | 120.3402 | 120.425 | 120.2915
1564.5469 | 121.7972 | -0.86975 | 120.9869 | 0.14932 | 0.000689 | -0.012 | -0.020438 | 0.045421 | 0.085583 | -0.067295 | 120.9064 | 120.9005 | 120.8532 | 120.7526 | 0.52437 | 0.72824 | 0.6487 | 0.64693 | 1.0191 | 0.87044 | 0.85775 | 0.84931 | 0.91517 | 0.95533 | 0.80246 | 120.9522 | 120.9462 | 120.899 | 120.7984 | 0.57014 | 0.77402 | 0.69447 | 0.69271 | 120.3821 | 120.2578 | 120.3289 | 120.2045
1566.2969 | 121.7926 | -1.1261 | 120.7535 | 0.14932 | 0.014425 | -0.021157 | -0.011281 | 0.036265 | 0.09474 | -0.067295 | 120.7325 | 120.7219 | 120.693 | 120.5832 | 0.69834 | 0.90221 | 0.82725 | 0.8209 | 1.2754 | 1.1405 | 1.1049 | 1.1148 | 1.1624 | 1.2208 | 1.0588 | 120.7782 | 120.7677 | 120.7388 | 120.629 | 0.74411 | 0.94799 | 0.87303 | 0.86668 | 120.0341 | 119.9052 | 119.9947 | 119.8657
1568.0469 | 121.8475 | -0.99335 | 120.8633 | 0.1539 | -0.00389 | -0.007421 | -0.020438 | 0.040843 | 0.090161 | -0.067295 | 120.7737 | 120.7585 | 120.725 | 120.6198 | 0.66629 | 0.87016 | 0.79063 | 0.78885 | 1.1472 | 0.98946 | 0.98593 | 0.97291 | 1.0342 | 1.0835 | 0.92605 | 120.8194 | 120.8043 | 120.7708 | 120.6656 | 0.71207 | 0.91594 | 0.8364 | 0.83463 | 120.1074 | 119.983 | 120.0587 | 119.9344
1569.8125 | 121.8201 | -0.99792 | 120.8725 | 0.14932 | -0.00389 | -0.007421 | -0.020438 | 0.049999 | 0.090161 | -0.067295 | 120.7828 | 120.7677 | 120.7296 | 120.6244 | 0.65713 | 0.86101 | 0.78147 | 0.7797 | 1.1472 | 0.99404 | 0.9905 | 0.97749 | 1.0479 | 1.0881 | 0.93063 | 120.8286 | 120.8135 | 120.7754 | 120.6702 | 0.70291 | 0.90678 | 0.82725 | 0.82547 | 120.1257 | 120.0014 | 120.0725 | 119.9481
1571.5 | 121.9299 | -0.93384 | 120.8588 | 0.14932 | 0.005267 | -0.016578 | -0.020438 | 0.040843 | 0.085583 | -0.071874 | 120.8195 | 120.8043 | 120.7754 | 120.6564 | 0.61593 | 0.82438 | 0.74942 | 0.74307 | 1.0832 | 0.9391 | 0.91726 | 0.9134 | 0.97468 | 1.0194 | 0.86196 | 120.8652 | 120.8501 | 120.8212 | 120.7022 | 0.6617 | 0.87016 | 0.7952 | 0.78885 | 120.2035 | 120.07 | 120.1595 | 120.026
1573.25 | 121.8704 | -0.93384 | 120.9229 | 0.14474 | -0.00389 | -0.021157 | -0.020438 | 0.031687 | 0.085583 | -0.071874 | 120.8378 | 120.8272 | 120.8029 | 120.6931 | 0.59762 | 0.79691 | 0.72195 | 0.72934 | 1.0786 | 0.92995 | 0.91268 | 0.9134 | 0.96552 | 1.0194 | 0.86196 | 120.8835 | 120.873 | 120.8486 | 120.7389 | 0.64339 | 0.84269 | 0.76772 | 0.77511 | 120.2402 | 120.1158 | 120.2053 | 120.0809
1575.0156 | 121.8018 | -0.97504 | 120.9137 | 0.14474 | 0.000689 | -0.021157 | -0.011281 | 0.045421 | 0.085583 | -0.071874 | 120.8469 | 120.8318 | 120.7983 | 120.6931 | 0.59762 | 0.80149 | 0.71737 | 0.7156 | 1.1198 | 0.97573 | 0.95388 | 0.96376 | 1.0205 | 1.0606 | 0.90316 | 120.8927 | 120.8776 | 120.8441 | 120.7389 | 0.64339 | 0.84727 | 0.76315 | 0.76138 | 120.2493 | 120.1296 | 120.2007 | 120.0809
1576.7812 | 121.9299 | -0.93842 | 120.8908 | 0.14474 | 0.000689 | -0.016578 | -0.020438 | 0.036265 | 0.085583 | -0.062717 | 120.8332 | 120.818 | 120.7846 | 120.6793 | 0.6022 | 0.8198 | 0.73569 | 0.73849 | 1.0832 | 0.93911 | 0.92184 | 0.91798 | 0.97468 | 1.024 | 0.8757 | 120.879 | 120.8638 | 120.8303 | 120.7251 | 0.64797 | 0.86558 | 0.78146 | 0.78427 | 120.231 | 120.0975 | 120.1824 | 120.0489
1578.4844 | 121.8155 | -0.85602 | 121.0327 | 0.14932 | 0.009846 | -0.016578 | -0.020438 | 0.040843 | 0.085583 | -0.067295 | 120.9477 | 120.9371 | 120.9036 | 120.7938 | 0.4969 | 0.70077 | 0.62123 | 0.62404 | 1.0053 | 0.86586 | 0.83944 | 0.83558 | 0.89686 | 0.9416 | 0.78872 | 120.9934 | 120.9829 | 120.9494 | 120.8396 | 0.54267 | 0.74655 | 0.667 | 0.66981 | 120.4508 | 120.3264 | 120.4067 | 120.2824
1580.25 | 121.7972 | -0.88806 | 121.0236 | 0.14474 | 0.000689 | -0.012 | -0.011281 | 0.045421 | 0.081005 | -0.067295 | 120.9248 | 120.9096 | 120.8715 | 120.7663 | 0.52437 | 0.73282 | 0.6487 | 0.64693 | 1.0328 | 0.88875 | 0.87606 | 0.87678 | 0.93348 | 0.96907 | 0.82077 | 120.9705 | 120.9554 | 120.9173 | 120.8121 | 0.57014 | 0.7786 | 0.69447 | 0.69271 | 120.4004 | 120.2761 | 120.3472 | 120.2228
1582 | 121.9666 | -0.89722 | 120.9 | 0.14474 | -0.00389 | -0.021157 | -0.025017 | 0.045421 | 0.085583 | -0.067295 | 120.911 | 120.8959 | 120.8624 | 120.748 | 0.5381 | 0.7374 | 0.65785 | 0.66066 | 1.042 | 0.89333 | 0.87606 | 0.8722 | 0.94264 | 0.9828 | 0.82992 | 120.9568 | 120.9417 | 120.9082 | 120.7938 | 0.58388 | 0.78317 | 0.70363 | 0.70644 | 120.3729 | 120.2532 | 120.3243 | 120.2045
1583.7656 | 121.8567 | -0.84686 | 121.0281 | 0.14474 | 0.005267 | -0.016578 | -0.020438 | 0.049999 | 0.090161 | -0.071874 | 120.9293 | 120.9096 | 120.8853 | 120.7801 | 0.51063 | 0.71451 | 0.64412 | 0.63319 | 0.99161 | 0.85213 | 0.83029 | 0.82643 | 0.89686 | 0.93702 | 0.77499 | 120.9751 | 120.9554 | 120.9311 | 120.8259 | 0.55641 | 0.76028 | 0.68989 | 0.67897 | 120.4187 | 120.2852 | 120.3746 | 120.2412
1585.4688 | 121.8979 | -0.86517 | 120.9824 | 0.14017 | 0.005267 | -0.012 | -0.025017 | 0.040843 | 0.085583 | -0.067295 | 120.9385 | 120.9188 | 120.8853 | 120.7755 | 0.51063 | 0.71909 | 0.63954 | 0.63777 | 1.0053 | 0.87044 | 0.85317 | 0.84016 | 0.90602 | 0.95076 | 0.79788 | 120.9843 | 120.9646 | 120.9311 | 120.8213 | 0.55641 | 0.76486 | 0.68532 | 0.68355 | 120.4279 | 120.299 | 120.3746 | 120.2457
1587.2188 | 121.8567 | -0.88806 | 121.0052 | 0.14474 | -0.00389 | -0.012 | -0.01586 | 0.045421 | 0.085583 | -0.067295 | 120.9293 | 120.9142 | 120.8761 | 120.7755 | 0.51063 | 0.72824 | 0.65327 | 0.64693 | 1.0328 | 0.88417 | 0.87606 | 0.8722 | 0.93348 | 0.97364 | 0.82077 | 120.9751 | 120.96 | 120.9219 | 120.8213 | 0.55641 | 0.77402 | 0.69905 | 0.69271 | 120.4187 | 120.2761 | 120.3655 | 120.2228
1588.9688 | 121.9482 | -0.70953 | 121.0648 | 0.14474 | 0.000689 | -0.016578 | -0.029595 | 0.045421 | 0.09474 | -0.062717 | 121.0255 | 121.0104 | 120.9814 | 120.8762 | 0.42822 | 0.62752 | 0.54797 | 0.55079 | 0.85428 | 0.71022 | 0.69296 | 0.67994 | 0.75496 | 0.80427 | 0.64682 | 121.0713 | 121.0561 | 121.0272 | 120.922 | 0.474 | 0.6733 | 0.59375 | 0.59656 | 120.5973 | 120.4775 | 120.5532 | 120.4335
1590.7344 | 121.8246 | -0.85602 | 121.019 | 0.14474 | -0.008469 | -0.012 | -0.01586 | 0.040843 | 0.09474 | -0.067295 | 120.966 | 120.9508 | 120.9219 | 120.8167 | 0.47401 | 0.68246 | 0.59833 | 0.60115 | 1.0008 | 0.84755 | 0.84402 | 0.84016 | 0.89686 | 0.95076 | 0.78872 | 121.0117 | 120.9966 | 120.9677 | 120.8625 | 0.51978 | 0.72824 | 0.64411 | 0.64692 | 120.492 | 120.3676 | 120.4479 | 120.3236
1592.5 | 121.9528 | -0.76446 | 121.0464 | 0.14932 | 0.005267 | -0.016578 | -0.020438 | 0.045421 | 0.085583 | -0.071874 | 120.9797 | 120.9783 | 120.9311 | 120.8304 | 0.46485 | 0.67331 | 0.58918 | 0.59199 | 0.91379 | 0.76973 | 0.74789 | 0.74403 | 0.80989 | 0.85005 | 0.69259 | 121.0255 | 121.0241 | 120.9768 | 120.8762 | 0.51062 | 0.71908 | 0.63495 | 0.63777 | 120.5149 | 120.3905 | 120.4662 | 120.3419
1594.1875 | 121.8201 | -0.78278 | 121.1105 | 0.14474 | 0.005267 | -0.012 | -0.029595 | 0.040843 | 0.085583 | -0.071874 | 121.0163 | 121.0058 | 120.9677 | 120.8625 | 0.44196 | 0.63668 | 0.56171 | 0.56452 | 0.92752 | 0.78804 | 0.77078 | 0.75318 | 0.82362 | 0.86836 | 0.7109 | 121.0621 | 121.0516 | 121.0135 | 120.9083 | 0.48773 | 0.68246 | 0.60748 | 0.6103 | 120.5744 | 120.4546 | 120.5257 | 120.406
1595.9375 | 121.9574 | -0.72784 | 121.0648 | 0.14474 | -0.00389 | -0.012 | -0.020438 | 0.036265 | 0.090161 | -0.071874 | 121.0438 | 121.0287 | 120.9952 | 120.8808 | 0.41907 | 0.61837 | 0.55255 | 0.54163 | 0.87259 | 0.72395 | 0.71584 | 0.70741 | 0.76411 | 0.81801 | 0.65597 | 121.0896 | 121.0744 | 121.0409 | 120.9266 | 0.46484 | 0.66414 | 0.59832 | 0.58741 | 120.6247 | 120.4913 | 120.5761 | 120.4426
1597.6875 | 121.9711 | -0.70953 | 121.106 | 0.14474 | 0.005267 | -0.012 | -0.01586 | 0.040843 | 0.090161 | -0.071874 | 121.0575 | 121.047 | 121.0089 | 120.9037 | 0.40533 | 0.60006 | 0.53424 | 0.53248 | 0.85428 | 0.7148 | 0.69753 | 0.69367 | 0.75038 | 0.7997 | 0.63766 | 121.1033 | 121.0928 | 121.0547 | 120.9495 | 0.45111 | 0.64583 | 0.58001 | 0.57825 | 120.6522 | 120.5233 | 120.6036 | 120.4747
1599.375 | 121.8567 | -0.74158 | 121.1288 | 0.14017 | 0.005267 | -0.016578 | -0.029595 | 0.054577 | 0.085583 | -0.062717 | 121.0621 | 121.0561 | 121.018 | 120.9129 | 0.39618 | 0.60006 | 0.5205 | 0.52332 | 0.88174 | 0.74684 | 0.725 | 0.71198 | 0.79615 | 0.82716 | 0.67886 | 121.1079 | 121.1019 | 121.0638 | 120.9586 | 0.44195 | 0.64583 | 0.56628 | 0.56909 | 120.6659 | 120.5416 | 120.6219 | 120.4975
1601.125 | 121.9345 | -0.71411 | 121.1197 | 0.14932 | 0.005267 | -0.007421 | -0.020438 | 0.040843 | 0.081005 | -0.067295 | 121.0896 | 121.079 | 121.0409 | 120.9266 | 0.38244 | 0.58174 | 0.50219 | 0.50043 | 0.86343 | 0.71938 | 0.70669 | 0.69367 | 0.75495 | 0.79512 | 0.64682 | 121.1354 | 121.1248 | 121.0867 | 120.9724 | 0.42822 | 0.62752 | 0.54796 | 0.5462 | 120.7071 | 120.5874 | 120.6585 | 120.5388
1602.8906 | 121.9528 | -0.74158 | 121.0785 | 0.14474 | 0.005267 | -0.012 | -0.020438 | 0.040843 | 0.090161 | -0.071874 | 121.0484 | 121.0424 | 120.9997 | 120.89 | 0.40991 | 0.61379 | 0.53424 | 0.53705 | 0.88632 | 0.74684 | 0.72958 | 0.72114 | 0.78242 | 0.83174 | 0.6697 | 121.0942 | 121.0882 | 121.0455 | 120.9357 | 0.45569 | 0.65957 | 0.58001 | 0.58283 | 120.6385 | 120.5141 | 120.5898 | 120.4655
1604.5938 | 121.8567 | -0.77362 | 121.1334 | 0.14932 | 0.005267 | -0.012 | -0.020438 | 0.040843 | 0.090161 | -0.071874 | 121.0346 | 121.0195 | 120.9768 | 120.8762 | 0.42822 | 0.6321 | 0.54797 | 0.55536 | 0.92294 | 0.77889 | 0.76162 | 0.75318 | 0.81446 | 0.86378 | 0.70175 | 121.0804 | 121.0653 | 121.0226 | 120.922 | 0.474 | 0.67788 | 0.59375 | 0.60114 | 120.6064 | 120.4867 | 120.5486 | 120.4289
1606.3594 | 121.843 | -0.84228 | 121.051 | 0.1539 | 0.005267 | -0.016578 | -0.01586 | 0.045421 | 0.085583 | -0.067295 | 120.9934 | 120.9829 | 120.9448 | 120.8396 | 0.46485 | 0.66873 | 0.58918 | 0.58741 | 0.99618 | 0.84755 | 0.82571 | 0.82642 | 0.88771 | 0.92787 | 0.77499 | 121.0392 | 121.0287 | 120.9906 | 120.8854 | 0.51062 | 0.7145 | 0.63495 | 0.63319 | 120.5286 | 120.4043 | 120.4799 | 120.3556
1608.0469 | 121.8704 | -0.90179 | 120.9824 | 0.1539 | 0.005267 | -0.012 | -0.020438 | 0.040843 | 0.085583 | -0.062717 | 120.9339 | 120.9096 | 120.8853 | 120.7709 | 0.52894 | 0.7374 | 0.65785 | 0.65609 | 1.0557 | 0.90706 | 0.88979 | 0.88136 | 0.94264 | 0.98738 | 0.83908 | 120.9797 | 120.9554 | 120.9311 | 120.8167 | 0.57472 | 0.78317 | 0.70363 | 0.70186 | 120.405 | 120.2761 | 120.3563 | 120.2274
1609.8125 | 121.9666 | -0.85602 | 120.9961 | 0.14474 | -0.00389 | -0.007421 | -0.01586 | 0.036265 | 0.085583 | -0.067295 | 120.9339 | 120.9279 | 120.8944 | 120.7801 | 0.51979 | 0.72366 | 0.6487 | 0.65151 | 1.0008 | 0.85213 | 0.8486 | 0.84016 | 0.89228 | 0.9416 | 0.78872 | 120.9797 | 120.9737 | 120.9402 | 120.8259 | 0.56556 | 0.76944 | 0.69447 | 0.69728 | 120.4141 | 120.2852 | 120.3746 | 120.2457
1611.5781 | 121.9299 | -1.0254 | 120.8038 | 0.14474 | 0.000689 | -0.012 | -0.020438 | 0.049999 | 0.081005 | -0.067295 | 120.7554 | 120.7448 | 120.7021 | 120.5969 | 0.70749 | 0.91594 | 0.83641 | 0.83006 | 1.1701 | 1.0261 | 1.0134 | 1.005 | 1.0754 | 1.1064 | 0.9581 | 120.8011 | 120.7906 | 120.7479 | 120.6427 | 0.75327 | 0.96172 | 0.88218 | 0.87583 | 120.0479 | 119.9189 | 119.9947 | 119.8657
1613.3281 | 121.8567 | -1.0345 | 120.8771 | 0.14017 | 0.000689 | -0.016578 | -0.01586 | 0.045421 | 0.081005 | -0.067295 | 120.7828 | 120.7723 | 120.7296 | 120.6244 | 0.6846 | 0.88847 | 0.80894 | 0.80717 | 1.1747 | 1.0352 | 1.018 | 1.0187 | 1.08 | 1.1156 | 0.96725 | 120.8286 | 120.818 | 120.7754 | 120.6702 | 0.73038 | 0.93425 | 0.85472 | 0.85294 | 120.0982 | 119.9739 | 120.045 | 119.9207
1615.0156 | 121.9345 | -0.88806 | 120.9549 | 0.14474 | 0.005267 | -0.016578 | -0.025017 | 0.040843 | 0.090161 | -0.071874 | 120.7187 | 120.7082 | 120.6655 | 120.5511 | 0.74412 | 0.95715 | 0.87304 | 0.87126 | 1.0328 | 0.89333 | 0.87148 | 0.86305 | 0.9289 | 0.97822 | 0.81619 | 120.7645 | 120.7539 | 120.7113 | 120.5969 | 0.78989 | 1.0029 | 0.91881 | 0.91704 | 119.9746 | 119.8457 | 119.9214 | 119.7925
1616.7656 | 121.9299 | -1.0254 | 120.8084 | 0.14474 | 0.005267 | -0.016578 | -0.020438 | 0.049999 | 0.085583 | -0.062717 | 120.7645 | 120.7585 | 120.725 | 120.6152 | 0.69376 | 0.90679 | 0.82725 | 0.82548 | 1.1701 | 1.0307 | 1.0088 | 1.005 | 1.0754 | 1.111 | 0.96267 | 120.8103 | 120.8043 | 120.7708 | 120.661 | 0.73953 | 0.95256 | 0.87303 | 0.87125 | 120.0708 | 119.9373 | 120.0313 | 119.8978
1618.4531 | 121.962 | -1.03 | 120.8038 | 0.1539 | 0.005267 | -0.012 | -0.020438 | 0.045421 | 0.085583 | -0.071874 | 120.7554 | 120.7356 | 120.7021 | 120.5923 | 0.71207 | 0.9251 | 0.84557 | 0.83921 | 1.1839 | 1.0352 | 1.018 | 1.0095 | 1.0754 | 1.1156 | 0.95809 | 120.8011 | 120.7814 | 120.7479 | 120.6381 | 0.75785 | 0.97088 | 0.89134 | 0.88499 | 120.0433 | 119.9098 | 119.9901 | 119.8566
1620.2031 | 121.9025 | -0.99335 | 120.8954 | 0.14932 | 0.000689 | -0.012 | -0.025017 | 0.040843 | 0.081005 | -0.062717 | 120.8195 | 120.8089 | 120.78 | 120.6656 | 0.63882 | 0.85185 | 0.76773 | 0.76138 | 1.1427 | 0.99404 | 0.98135 | 0.96833 | 1.0342 | 1.0744 | 0.93063 | 120.8652 | 120.8547 | 120.8258 | 120.7114 | 0.6846 | 0.89763 | 0.81351 | 0.80716 | 120.1806 | 120.0517 | 120.1412 | 120.0122
1621.9531 | 121.9757 | -0.91095 | 120.9091 | 0.15848 | 0.000689 | -0.002842 | -0.025017 | 0.045421 | 0.081005 | -0.067295 | 120.7554 | 120.7448 | 120.6976 | 120.5878 | 0.71665 | 0.9251 | 0.84557 | 0.84379 | 1.0694 | 0.91164 | 0.90811 | 0.88593 | 0.95637 | 0.99196 | 0.84366 | 120.8011 | 120.7906 | 120.7433 | 120.6335 | 0.76243 | 0.97088 | 0.89134 | 0.88957 | 120.0387 | 119.9098 | 119.9809 | 119.852
1623.7031 | 121.9666 | -1.1124 | 120.7352 | 0.14474 | 0.005267 | -0.012 | -0.025017 | 0.036265 | 0.085583 | -0.076452 | 120.7874 | 120.7723 | 120.7296 | 120.6198 | 0.68002 | 0.88847 | 0.81352 | 0.80717 | 1.2571 | 1.1176 | 1.1004 | 1.0873 | 1.1486 | 1.1979 | 1.0359 | 120.8332 | 120.818 | 120.7754 | 120.6656 | 0.7258 | 0.93425 | 0.85929 | 0.85294 | 120.1074 | 119.9739 | 120.0496 | 119.9161
1625.3906 | 121.8109 | -0.65002 | 121.2479 | 0.14932 | 0.000689 | -0.012 | -0.020438 | 0.045421 | 0.090161 | -0.067295 | 121.1674 | 121.1523 | 121.1188 | 121.009 | 0.3275 | 0.5085 | 0.43351 | 0.44549 | 0.79935 | 0.65071 | 0.63802 | 0.62959 | 0.69545 | 0.74019 | 0.58273 | 121.2132 | 121.1981 | 121.1645 | 121.0548 | 0.37328 | 0.55427 | 0.47929 | 0.49127 | 120.8399 | 120.7339 | 120.7913 | 120.6853
1627.1406 | 121.8658 | -0.59967 | 121.3348 | 0.14017 | 0.000689 | -0.012 | -0.020438 | 0.040843 | 0.090161 | -0.062717 | 121.2269 | 121.221 | 121.1829 | 121.0731 | 0.28172 | 0.4444 | 0.37857 | 0.39971 | 0.73984 | 0.60036 | 0.58767 | 0.57923 | 0.64051 | 0.68983 | 0.53695 | 121.2727 | 121.2668 | 121.2286 | 121.1189 | 0.3275 | 0.49018 | 0.42435 | 0.44548 | 120.9452 | 120.8484 | 120.9011 | 120.8043
1628.8281 | 121.9299 | -0.49896 | 121.376 | 0.14474 | 0.000689 | -0.016578 | -0.01586 | 0.045421 | 0.085583 | -0.062717 | 121.2956 | 121.2897 | 121.247 | 121.1418 | 0.23594 | 0.37573 | 0.33279 | 0.32646 | 0.6437 | 0.49965 | 0.48238 | 0.4831 | 0.54438 | 0.58454 | 0.43624 | 121.3414 | 121.3354 | 121.2927 | 121.1876 | 0.28172 | 0.42151 | 0.37856 | 0.37223 | 121.0597 | 120.9628 | 121.011 | 120.9142
1630.6094 | 121.9849 | -0.44403 | 121.3989 | 0.14474 | 0.000689 | -0.012 | -0.025017 | 0.045421 | 0.081005 | -0.062717 | 121.346 | 121.3309 | 121.2927 | 121.183 | 0.19474 | 0.33453 | 0.29616 | 0.29899 | 0.58877 | 0.44472 | 0.43203 | 0.41901 | 0.48945 | 0.52504 | 0.38131 | 121.3918 | 121.3767 | 121.3385 | 121.2288 | 0.24051 | 0.3803 | 0.34193 | 0.34476 | 121.1512 | 121.0498 | 121.098 | 120.9966
1632.375 | 121.9254 | -0.40283 | 121.4539 | 0.14932 | -0.00389 | -0.012 | -0.025017 | 0.045421 | 0.085583 | -0.067295 | 121.4009 | 121.3904 | 121.3385 | 121.2426 | 0.15811 | 0.27959 | 0.24122 | 0.23947 | 0.55215 | 0.39894 | 0.39083 | 0.37782 | 0.44825 | 0.48842 | 0.33554 | 121.4467 | 121.4362 | 121.3843 | 121.2883 | 0.20389 | 0.32537 | 0.287 | 0.28525 | 121.2428 | 121.1597 | 121.1804 | 121.0973
1634.0781 | 121.8292 | -0.41199 | 121.5271 | 0.14474 | 0.000689 | -0.012 | -0.01586 | 0.040843 | 0.085583 | -0.071874 | 121.4376 | 121.4225 | 121.3889 | 121.2655 | 0.13522 | 0.25212 | 0.21833 | 0.21658 | 0.55673 | 0.41268 | 0.39999 | 0.39613 | 0.45283 | 0.49757 | 0.34011 | 121.4833 | 121.4682 | 121.4347 | 121.3112 | 0.181 | 0.2979 | 0.2641 | 0.26236 | 121.3023 | 121.2192 | 121.2537 | 121.1706
1635.8438 | 121.9711 | -0.34332 | 121.4905 | 0.14474 | 0.005267 | -0.016578 | -0.020438 | 0.036265 | 0.085583 | -0.067295 | 121.4421 | 121.4362 | 121.3935 | 121.2792 | 0.12149 | 0.23839 | 0.20459 | 0.19827 | 0.48807 | 0.34859 | 0.32675 | 0.32288 | 0.37959 | 0.42891 | 0.27603 | 121.4879 | 121.482 | 121.4392 | 121.325 | 0.16726 | 0.28417 | 0.25037 | 0.24404 | 121.3206 | 121.2375 | 121.272 | 121.1889
1637.6094 | 121.8796 | -0.37994 | 121.4996 | 0.14474 | 0.000689 | -0.016578 | -0.020438 | 0.045421 | 0.081005 | -0.067295 | 121.4421 | 121.4316 | 121.398 | 121.2883 | 0.12149 | 0.24297 | 0.20459 | 0.20285 | 0.52469 | 0.38063 | 0.36337 | 0.35951 | 0.42536 | 0.46095 | 0.31265 | 121.4879 | 121.4774 | 121.4438 | 121.3341 | 0.16726 | 0.28874 | 0.25037 | 0.24862 | 121.3206 | 121.2375 | 121.2766 | 121.1935
1639.3594 | 121.843 | -0.41657 | 121.5408 | 0.14474 | -0.00389 | -0.012 | -0.01586 | 0.036265 | 0.085583 | -0.08103 | 121.4376 | 121.427 | 121.3935 | 121.2746 | 0.12607 | 0.24754 | 0.20459 | 0.21658 | 0.56131 | 0.41268 | 0.40457 | 0.40071 | 0.45283 | 0.50215 | 0.33554 | 121.4833 | 121.4728 | 121.4392 | 121.3204 | 0.17184 | 0.29332 | 0.25037 | 0.26236 | 121.3115 | 121.233 | 121.2674 | 121.1889
1641.125 | 121.9528 | -0.34332 | 121.4722 | 0.14017 | 0.005267 | -0.012 | -0.01586 | 0.036265 | 0.090161 | -0.062717 | 121.4467 | 121.4362 | 121.398 | 121.2838 | 0.11691 | 0.23839 | 0.20001 | 0.19827 | 0.48349 | 0.34859 | 0.33132 | 0.32746 | 0.37959 | 0.43348 | 0.28061 | 121.4925 | 121.482 | 121.4438 | 121.3295 | 0.16268 | 0.28417 | 0.24579 | 0.24404 | 121.3298 | 121.2467 | 121.2811 | 121.198
1642.8906 | 121.8521 | -0.39368 | 121.5225 | 0.14932 | 0.009846 | -0.012 | -0.01586 | 0.045421 | 0.076426 | -0.062717 | 121.4421 | 121.4316 | 121.3889 | 121.2746 | 0.13522 | 0.24297 | 0.21375 | 0.21658 | 0.543 | 0.40352 | 0.38168 | 0.37782 | 0.4391 | 0.4701 | 0.33096 | 121.4879 | 121.4774 | 121.4347 | 121.3204 | 0.181 | 0.28874 | 0.25952 | 0.26236 | 121.3069 | 121.2284 | 121.2537 | 121.1751
1644.5938 | 121.8292 | -0.41657 | 121.5179 | 0.14474 | 0.000689 | -0.007421 | -0.025017 | 0.040843 | 0.090161 | -0.062717 | 121.4421 | 121.4316 | 121.3935 | 121.2792 | 0.12607 | 0.24297 | 0.20459 | 0.212 | 0.56131 | 0.41725 | 0.40914 | 0.39155 | 0.45741 | 0.50673 | 0.35385 | 121.4879 | 121.4774 | 121.4392 | 121.325 | 0.17184 | 0.28874 | 0.25037 | 0.25778 | 121.3161 | 121.2375 | 121.2674 | 121.1889
1646.3594 | 121.8613 | -0.37079 | 121.5363 | 0.14474 | 0.000689 | -0.012 | -0.01586 | 0.040843 | 0.085583 | -0.076452 | 121.4559 | 121.4453 | 121.4118 | 121.3067 | 0.11691 | 0.22465 | 0.18628 | 0.18453 | 0.51553 | 0.37148 | 0.35879 | 0.35493 | 0.41163 | 0.45637 | 0.29434 | 121.5016 | 121.4911 | 121.4576 | 121.3524 | 0.16268 | 0.27043 | 0.23205 | 0.23031 | 121.339 | 121.2696 | 121.2949 | 121.2255
1648.1094 | 121.8338 | -0.36163 | 121.55 | 0.14932 | 0.000689 | -0.012 | -0.01586 | 0.040843 | 0.09474 | -0.067295 | 121.4788 | 121.4637 | 121.4255 | 121.3204 | 0.098596 | 0.2155 | 0.17712 | 0.1708 | 0.51095 | 0.36232 | 0.34963 | 0.34577 | 0.40248 | 0.45637 | 0.29434 | 121.5245 | 121.5094 | 121.4713 | 121.3662 | 0.14437 | 0.26127 | 0.2229 | 0.21658 | 121.3802 | 121.3016 | 121.3269 | 121.2484
1649.7969 | 121.9711 | -0.29755 | 121.5271 | 0.14474 | 0.005267 | -0.012 | -0.020438 | 0.045421 | 0.081005 | -0.071874 | 121.4879 | 121.4728 | 121.4347 | 121.3204 | 0.098596 | 0.21092 | 0.17254 | 0.16164 | 0.44229 | 0.30281 | 0.28555 | 0.27711 | 0.34297 | 0.37855 | 0.22567 | 121.5337 | 121.5186 | 121.4804 | 121.3662 | 0.14437 | 0.2567 | 0.21832 | 0.20742 | 121.3893 | 121.3154 | 121.3361 | 121.2621
1651.5625 | 121.875 | -0.35248 | 121.5729 | 0.14932 | -0.008469 | -0.012 | -0.01586 | 0.049999 | 0.090161 | -0.062717 | 121.4879 | 121.4728 | 121.4347 | 121.3296 | 0.094017 | 0.20634 | 0.17254 | 0.16622 | 0.5018 | 0.34401 | 0.34048 | 0.33662 | 0.40248 | 0.44264 | 0.28976 | 121.5337 | 121.5186 | 121.4804 | 121.3753 | 0.13979 | 0.25212 | 0.21832 | 0.212 | 121.3939 | 121.3154 | 121.3407 | 121.2621
1653.25 | 121.8475 | -0.35706 | 121.55 | 0.14474 | -0.00389 | -0.012 | -0.020438 | 0.040843 | 0.090161 | -0.067295 | 121.4879 | 121.482 | 121.4393 | 121.3341 | 0.089439 | 0.20176 | 0.17254 | 0.16622 | 0.5018 | 0.35317 | 0.34506 | 0.33662 | 0.3979 | 0.44722 | 0.28976 | 121.5337 | 121.5278 | 121.485 | 121.3799 | 0.13522 | 0.24754 | 0.21832 | 0.212 | 121.3985 | 121.3154 | 121.3498 | 121.2667
1655.0156 | 121.9208 | -0.33417 | 121.5546 | 0.14474 | 0.000689 | -0.012 | -0.01586 | 0.040843 | 0.085583 | -0.067295 | 121.4925 | 121.4866 | 121.453 | 121.3387 | 0.089439 | 0.20176 | 0.16339 | 0.16164 | 0.47891 | 0.33486 | 0.32217 | 0.31831 | 0.37501 | 0.41975 | 0.26687 | 121.5383 | 121.5323 | 121.4988 | 121.3845 | 0.13522 | 0.24754 | 0.20916 | 0.20742 | 121.4031 | 121.3291 | 121.3635 | 121.2896
1656.7812 | 121.9894 | -0.3067 | 121.5225 | 0.1539 | 0.000689 | -0.012 | -0.025017 | 0.036265 | 0.085583 | -0.062717 | 121.4925 | 121.482 | 121.4438 | 121.3296 | 0.094017 | 0.20176 | 0.17712 | 0.16164 | 0.4606 | 0.30739 | 0.2947 | 0.28168 | 0.34297 | 0.39228 | 0.24398 | 121.5383 | 121.5278 | 121.4896 | 121.3753 | 0.13979 | 0.24754 | 0.2229 | 0.20742 | 121.3985 | 121.3154 | 121.3498 | 121.2667
1658.4688 | 121.9482 | -0.30212 | 121.5637 | 0.14474 | -0.00389 | -0.012 | -0.020438 | 0.045421 | 0.090161 | -0.071874 | 121.4971 | 121.4866 | 121.4438 | 121.3341 | 0.089439 | 0.20176 | 0.16339 | 0.16622 | 0.44687 | 0.29823 | 0.29012 | 0.28169 | 0.34754 | 0.39228 | 0.23025 | 121.5428 | 121.5323 | 121.4896 | 121.3799 | 0.13522 | 0.24754 | 0.20916 | 0.212 | 121.4076 | 121.3337 | 121.3544 | 121.2804
1660.2188 | 121.8521 | -0.34332 | 121.5866 | 0.14474 | 0.009846 | -0.016578 | -0.020438 | 0.036265 | 0.090161 | -0.071874 | 121.5062 | 121.4911 | 121.4576 | 121.3433 | 0.089439 | 0.18803 | 0.15881 | 0.15249 | 0.48807 | 0.35317 | 0.32675 | 0.32288 | 0.37959 | 0.43348 | 0.27145 | 121.552 | 121.5369 | 121.5033 | 121.3891 | 0.13522 | 0.23381 | 0.20458 | 0.19826 | 121.4168 | 121.3474 | 121.3681 | 121.2988
1661.9688 | 121.8979 | -0.34332 | 121.582 | 0.14474 | -0.00389 | -0.016578 | -0.020438 | 0.040843 | 0.090161 | -0.071874 | 121.5017 | 121.4957 | 121.4621 | 121.3525 | 0.084861 | 0.19261 | 0.15423 | 0.15706 | 0.48807 | 0.33943 | 0.32675 | 0.32288 | 0.38417 | 0.43348 | 0.27145 | 121.5474 | 121.5415 | 121.5079 | 121.3982 | 0.13064 | 0.23838 | 0.2 | 0.20284 | 121.4168 | 121.3474 | 121.3773 | 121.3079
1663.7344 | 121.843 | -0.3479 | 121.5775 | 0.14474 | 0.000689 | -0.016578 | -0.020438 | 0.049999 | 0.081005 | -0.067295 | 121.5154 | 121.5003 | 121.4576 | 121.3387 | 0.084861 | 0.19261 | 0.15423 | 0.14791 | 0.49264 | 0.34859 | 0.33132 | 0.32746 | 0.3979 | 0.4289 | 0.2806 | 121.5612 | 121.5461 | 121.5033 | 121.3845 | 0.13064 | 0.23838 | 0.2 | 0.19368 | 121.4305 | 121.3612 | 121.3727 | 121.3033
1665.4219 | 121.9666 | -0.31586 | 121.5866 | 0.14932 | 0.000689 | -0.012 | -0.020438 | 0.040843 | 0.081005 | -0.071874 | 121.5062 | 121.5003 | 121.4484 | 121.3387 | 0.084861 | 0.18803 | 0.15881 | 0.15706 | 0.46518 | 0.31655 | 0.30386 | 0.29542 | 0.3567 | 0.39686 | 0.24398 | 121.552 | 121.5461 | 121.4942 | 121.3845 | 0.13064 | 0.23381 | 0.20458 | 0.20284 | 121.4214 | 121.3474 | 121.3635 | 121.2896
1667.1875 | 121.9482 | -0.29297 | 121.5591 | 0.14474 | -0.00389 | -0.016578 | -0.01586 | 0.040843 | 0.085583 | -0.067295 | 121.5062 | 121.5003 | 121.4621 | 121.3479 | 0.084861 | 0.19261 | 0.15423 | 0.15706 | 0.43771 | 0.28908 | 0.27639 | 0.27711 | 0.33381 | 0.37855 | 0.22567 | 121.552 | 121.5461 | 121.5079 | 121.3937 | 0.13064 | 0.23838 | 0.2 | 0.20284 | 121.4214 | 121.352 | 121.3773 | 121.3079
1668.9375 | 121.8704 | -0.33417 | 121.6049 | 0.14474 | 0.005267 | -0.016578 | -0.01586 | 0.040843 | 0.085583 | -0.062717 | 121.52 | 121.4911 | 121.4621 | 121.3479 | 0.080283 | 0.18345 | 0.14965 | 0.15249 | 0.47891 | 0.33943 | 0.31759 | 0.31831 | 0.37501 | 0.41975 | 0.27145 | 121.5657 | 121.5369 | 121.5079 | 121.3937 | 0.12606 | 0.22923 | 0.19543 | 0.19826 | 121.4397 | 121.3703 | 121.3819 | 121.3125
1670.7031 | 121.8842 | -0.32959 | 121.5958 | 0.14474 | 0.005267 | -0.007421 | -0.020438 | 0.049999 | 0.085583 | -0.067295 | 121.5062 | 121.5049 | 121.4621 | 121.3479 | 0.080283 | 0.18803 | 0.15881 | 0.15249 | 0.47433 | 0.33486 | 0.32217 | 0.30915 | 0.37959 | 0.41517 | 0.2623 | 121.552 | 121.5506 | 121.5079 | 121.3937 | 0.12606 | 0.23381 | 0.20458 | 0.19826 | 121.4259 | 121.3474 | 121.3819 | 121.3033
1672.4062 | 121.9482 | -0.31586 | 121.5591 | 0.14474 | -0.00389 | -0.002842 | -0.020438 | 0.040843 | 0.081005 | -0.067295 | 121.5154 | 121.5003 | 121.4621 | 121.357 | 0.080283 | 0.18803 | 0.15423 | 0.15249 | 0.4606 | 0.31197 | 0.31301 | 0.29542 | 0.3567 | 0.39686 | 0.24856 | 121.5612 | 121.5461 | 121.5079 | 121.4028 | 0.12606 | 0.23381 | 0.2 | 0.19826 | 121.4351 | 121.3612 | 121.3819 | 121.3079
1674.1562 | 121.875 | -0.3479 | 121.5637 | 0.14932 | 0.000689 | -0.012 | -0.025017 | 0.045421 | 0.085583 | -0.067295 | 121.5108 | 121.4957 | 121.4576 | 121.357 | 0.075705 | 0.18803 | 0.15881 | 0.14791 | 0.49722 | 0.34859 | 0.3359 | 0.32288 | 0.39332 | 0.43348 | 0.2806 | 121.5566 | 121.5415 | 121.5033 | 121.4028 | 0.12148 | 0.23381 | 0.20458 | 0.19368 | 121.4351 | 121.352 | 121.3819 | 121.2988
1675.9062 | 121.8658 | -0.32959 | 121.5866 | 0.14474 | 0.000689 | -0.016578 | -0.025017 | 0.045421 | 0.081005 | -0.062717 | 121.5245 | 121.5049 | 121.4713 | 121.357 | 0.084861 | 0.18345 | 0.15423 | 0.14791 | 0.47433 | 0.33028 | 0.31301 | 0.30457 | 0.37501 | 0.41059 | 0.26687 | 121.5703 | 121.5506 | 121.5171 | 121.4028 | 0.13064 | 0.22923 | 0.2 | 0.19368 | 121.4397 | 121.3703 | 121.3864 | 121.3171
1677.6719 | 121.843 | -0.31586 | 121.6187 | 0.14932 | 0.005267 | -0.002842 | -0.01586 | 0.040843 | 0.09474 | -0.067295 | 121.5245 | 121.514 | 121.4759 | 121.3616 | 0.071126 | 0.18345 | 0.14507 | 0.13417 | 0.46518 | 0.32112 | 0.31301 | 0.3 | 0.3567 | 0.4106 | 0.24856 | 121.5703 | 121.5598 | 121.5217 | 121.4074 | 0.1169 | 0.22923 | 0.19085 | 0.17995 | 121.4534 | 121.3795 | 121.4047 | 121.3308
1679.4375 | 121.8521 | -0.33875 | 121.6049 | 0.1539 | 0.005267 | -0.012 | -0.01586 | 0.036265 | 0.085583 | -0.062717 | 121.5291 | 121.514 | 121.4759 | 121.3616 | 0.075705 | 0.17887 | 0.14049 | 0.13875 | 0.49264 | 0.34401 | 0.32675 | 0.32289 | 0.37501 | 0.42433 | 0.27603 | 121.5749 | 121.5598 | 121.5217 | 121.4074 | 0.12148 | 0.22465 | 0.18627 | 0.18453 | 121.4534 | 121.3886 | 121.4002 | 121.3354
1681.2188 | 121.8887 | -0.31586 | 121.6141 | 0.14474 | 0.009846 | -0.012 | -0.011281 | 0.049999 | 0.09474 | -0.067295 | 121.5291 | 121.5232 | 121.485 | 121.3708 | 0.066548 | 0.1743 | 0.14507 | 0.13417 | 0.4606 | 0.3257 | 0.30386 | 0.30458 | 0.36586 | 0.4106 | 0.24856 | 121.5749 | 121.569 | 121.5308 | 121.4165 | 0.11232 | 0.22007 | 0.19085 | 0.17995 | 121.4626 | 121.384 | 121.4185 | 121.34
1682.9219 | 121.9025 | -0.33875 | 121.5958 | 0.14474 | 0.000689 | -0.016578 | -0.01586 | 0.054577 | 0.090161 | -0.062717 | 121.5291 | 121.5232 | 121.485 | 121.3754 | 0.075705 | 0.1743 | 0.14049 | 0.13875 | 0.48349 | 0.33943 | 0.32217 | 0.32289 | 0.39332 | 0.42891 | 0.27603 | 121.5749 | 121.569 | 121.5308 | 121.4211 | 0.12148 | 0.22007 | 0.18627 | 0.18453 | 121.4534 | 121.3886 | 121.4093 | 121.3445
1684.6875 | 121.9208 | -0.32959 | 121.5958 | 0.14932 | 0.000689 | -0.012 | -0.01586 | 0.049999 | 0.09474 | -0.067295 | 121.5245 | 121.5232 | 121.485 | 121.3616 | 0.075705 | 0.18345 | 0.13134 | 0.14791 | 0.47891 | 0.33028 | 0.31759 | 0.31373 | 0.37959 | 0.42433 | 0.2623 | 121.5703 | 121.569 | 121.5308 | 121.4074 | 0.12148 | 0.22923 | 0.17711 | 0.19368 | 121.4488 | 121.3932 | 121.4093 | 121.3537
1686.4531 | 121.8521 | -0.38452 | 121.5912 | 0.14932 | 0.009846 | -0.012 | -0.025017 | 0.045421 | 0.090161 | -0.062717 | 121.5017 | 121.4957 | 121.4621 | 121.3387 | 0.094017 | 0.20176 | 0.16797 | 0.15706 | 0.53384 | 0.39437 | 0.37252 | 0.3595 | 0.42994 | 0.47468 | 0.3218 | 121.5474 | 121.5415 | 121.5079 | 121.3845 | 0.13979 | 0.24754 | 0.21374 | 0.20284 | 121.4076 | 121.3337 | 121.3681 | 121.2942
1688.1562 | 121.9025 | -0.41657 | 121.5042 | 0.14932 | 0.005267 | -0.012 | -0.020438 | 0.045421 | 0.085583 | -0.067295 | 121.4467 | 121.4316 | 121.4026 | 121.2883 | 0.14438 | 0.26586 | 0.22748 | 0.22574 | 0.56589 | 0.42183 | 0.40457 | 0.39613 | 0.46199 | 0.50215 | 0.34927 | 121.4925 | 121.4774 | 121.4484 | 121.3341 | 0.19015 | 0.31163 | 0.27326 | 0.27151 | 121.3023 | 121.2192 | 121.2582 | 121.1751
1689.9219 | 121.9666 | -0.40283 | 121.463 | 0.14017 | 0.000689 | -0.016578 | -0.025017 | 0.045421 | 0.090161 | -0.071874 | 121.4192 | 121.4179 | 121.3706 | 121.2563 | 0.16269 | 0.29333 | 0.25495 | 0.24863 | 0.543 | 0.40352 | 0.38625 | 0.37782 | 0.44825 | 0.49299 | 0.33096 | 121.465 | 121.4636 | 121.4164 | 121.3021 | 0.20847 | 0.3391 | 0.30073 | 0.2944 | 121.2565 | 121.1643 | 121.2079 | 121.1156
1691.625 | 121.8704 | -0.4303 | 121.4996 | 0.14474 | 0.000689 | -0.016578 | -0.020438 | 0.045421 | 0.090161 | -0.058139 | 121.4238 | 121.427 | 121.3752 | 121.2655 | 0.15811 | 0.28417 | 0.2458 | 0.23947 | 0.57504 | 0.43099 | 0.41372 | 0.40986 | 0.47572 | 0.52046 | 0.37216 | 121.4696 | 121.4728 | 121.4209 | 121.3112 | 0.20389 | 0.32995 | 0.29157 | 0.28525 | 121.2657 | 121.178 | 121.217 | 121.1294
1693.375 | 121.962 | -0.40283 | 121.4584 | 0.1539 | 0.005267 | -0.012 | -0.01586 | 0.045421 | 0.085583 | -0.067295 | 121.4238 | 121.4041 | 121.3706 | 121.2563 | 0.16269 | 0.30248 | 0.25495 | 0.25778 | 0.55673 | 0.4081 | 0.39083 | 0.38697 | 0.44825 | 0.48842 | 0.33554 | 121.4696 | 121.4499 | 121.4164 | 121.3021 | 0.20847 | 0.34826 | 0.30073 | 0.30356 | 121.2611 | 121.1689 | 121.2079 | 121.1156
1695.0781 | 121.994 | -0.41199 | 121.4493 | 0.14932 | 0.000689 | -0.007421 | -0.025017 | 0.054577 | 0.085583 | -0.071874 | 121.4147 | 121.4087 | 121.3706 | 121.2563 | 0.16269 | 0.29333 | 0.25953 | 0.25778 | 0.56131 | 0.41268 | 0.40457 | 0.38697 | 0.46656 | 0.49757 | 0.34011 | 121.4604 | 121.4545 | 121.4164 | 121.3021 | 0.20847 | 0.3391 | 0.30531 | 0.30356 | 121.252 | 121.1551 | 121.2079 | 121.111
1696.8438 | 121.8842 | -0.44403 | 121.4813 | 0.14474 | 0.000689 | -0.016578 | -0.01586 | 0.045421 | 0.09474 | -0.067295 | 121.4147 | 121.4087 | 121.3614 | 121.2517 | 0.16269 | 0.30248 | 0.25953 | 0.26236 | 0.58877 | 0.44472 | 0.42745 | 0.42817 | 0.48945 | 0.53877 | 0.37674 | 121.4604 | 121.4545 | 121.4072 | 121.2975 | 0.20847 | 0.34826 | 0.30531 | 0.30814 | 121.252 | 121.1551 | 121.1987 | 121.1019
1698.5312 | 121.962 | -0.40741 | 121.4493 | 0.14932 | -0.00389 | -0.021157 | -0.01586 | 0.045421 | 0.090161 | -0.067295 | 121.4192 | 121.4041 | 121.366 | 121.2426 | 0.16727 | 0.2979 | 0.25038 | 0.25778 | 0.55673 | 0.40352 | 0.38625 | 0.39155 | 0.45283 | 0.49757 | 0.34012 | 121.465 | 121.4499 | 121.4118 | 121.2883 | 0.21304 | 0.34368 | 0.29615 | 0.30356 | 121.252 | 121.1689 | 121.1987 | 121.1156
1700.2812 | 121.9666 | -0.40283 | 121.4676 | 0.14474 | -0.00389 | -0.012 | -0.01586 | 0.045421 | 0.090161 | -0.067295 | 121.4147 | 121.3996 | 121.3706 | 121.2517 | 0.17185 | 0.30248 | 0.26411 | 0.26236 | 0.54758 | 0.39894 | 0.39083 | 0.38697 | 0.44825 | 0.49299 | 0.33554 | 121.4604 | 121.4453 | 121.4164 | 121.2975 | 0.21762 | 0.34826 | 0.30989 | 0.30814 | 121.2428 | 121.1505 | 121.1987 | 121.1065
1701.9844 | 121.9116 | -0.44403 | 121.4813 | 0.14932 | 0.000689 | -0.021157 | -0.020438 | 0.045421 | 0.076426 | -0.067295 | 121.4192 | 121.4087 | 121.3797 | 121.2517 | 0.17185 | 0.29333 | 0.25495 | 0.25778 | 0.59335 | 0.44472 | 0.42287 | 0.42359 | 0.48945 | 0.52046 | 0.37674 | 121.465 | 121.4545 | 121.4255 | 121.2975 | 0.21762 | 0.3391 | 0.30073 | 0.30356 | 121.2474 | 121.1643 | 121.2079 | 121.1248
1703.75 | 121.8292 | -0.45319 | 121.4996 | 0.14474 | -0.00389 | -0.012 | -0.025017 | 0.045421 | 0.090161 | -0.062717 | 121.4192 | 121.4041 | 121.3614 | 121.2517 | 0.17185 | 0.30248 | 0.25953 | 0.26236 | 0.59793 | 0.4493 | 0.44119 | 0.42817 | 0.49861 | 0.54335 | 0.39047 | 121.465 | 121.4499 | 121.4072 | 121.2975 | 0.21762 | 0.34826 | 0.30531 | 0.30814 | 121.2474 | 121.1597 | 121.1896 | 121.1019
1705.4375 | 121.843 | -0.44861 | 121.5179 | 0.14474 | 0.000689 | -0.016578 | -0.025017 | 0.045421 | 0.085583 | -0.071874 | 121.4147 | 121.4041 | 121.366 | 121.2471 | 0.17642 | 0.30706 | 0.26869 | 0.27152 | 0.59335 | 0.4493 | 0.43203 | 0.42359 | 0.49403 | 0.53419 | 0.37673 | 121.4604 | 121.4499 | 121.4118 | 121.2929 | 0.2222 | 0.35284 | 0.31446 | 0.31729 | 121.2382 | 121.146 | 121.1896 | 121.0973
1707.2031 | 121.9025 | -0.44403 | 121.4905 | 0.13101 | -0.008469 | -0.012 | -0.020438 | 0.040843 | 0.090161 | -0.062717 | 121.4055 | 121.4087 | 121.366 | 121.2426 | 0.17642 | 0.30706 | 0.26411 | 0.27152 | 0.57504 | 0.43556 | 0.43203 | 0.42359 | 0.48487 | 0.53419 | 0.38131 | 121.4513 | 121.4545 | 121.4118 | 121.2883 | 0.2222 | 0.35284 | 0.30989 | 0.31729 | 121.2291 | 121.1414 | 121.1896 | 121.1019
1708.9531 | 121.8658 | -0.48065 | 121.4722 | 0.14474 | -0.008469 | -0.007421 | -0.025017 | 0.036265 | 0.09474 | -0.062717 | 121.4101 | 121.3996 | 121.3523 | 121.2426 | 0.181 | 0.31622 | 0.27327 | 0.27152 | 0.6254 | 0.47218 | 0.47323 | 0.45564 | 0.51692 | 0.57539 | 0.41794 | 121.4559 | 121.4453 | 121.398 | 121.2883 | 0.22678 | 0.36199 | 0.31904 | 0.31729 | 121.2291 | 121.1368 | 121.1713 | 121.079
1710.7188 | 121.8658 | -0.47607 | 121.4951 | 0.14474 | 0.000689 | -0.012 | -0.025017 | 0.045421 | 0.085583 | -0.071874 | 121.4055 | 121.4041 | 121.366 | 121.2426 | 0.181 | 0.31164 | 0.26411 | 0.27152 | 0.62082 | 0.47676 | 0.46407 | 0.45106 | 0.5215 | 0.56166 | 0.4042 | 121.4513 | 121.4499 | 121.4118 | 121.2883 | 0.22678 | 0.35741 | 0.30989 | 0.31729 | 121.2245 | 121.1414 | 121.185 | 121.1019
1712.4219 | 121.8842 | -0.47607 | 121.4767 | 0.14474 | -0.008469 | -0.012 | -0.025017 | 0.040843 | 0.090161 | -0.067295 | 121.4101 | 121.395 | 121.366 | 121.2471 | 0.181 | 0.31622 | 0.26869 | 0.27152 | 0.62082 | 0.4676 | 0.46407 | 0.45106 | 0.51692 | 0.56624 | 0.40878 | 121.4559 | 121.4408 | 121.4118 | 121.2929 | 0.22678 | 0.36199 | 0.31446 | 0.31729 | 121.2291 | 121.1414 | 121.185 | 121.0973
1714.1719 | 121.8887 | -0.4715 | 121.4676 | 0.14932 | -0.008469 | -0.012 | -0.020438 | 0.045421 | 0.09474 | -0.062717 | 121.4055 | 121.395 | 121.3523 | 121.2426 | 0.17642 | 0.31622 | 0.27327 | 0.2761 | 0.62082 | 0.46303 | 0.4595 | 0.45106 | 0.51692 | 0.56624 | 0.40878 | 121.4513 | 121.4408 | 121.398 | 121.2883 | 0.2222 | 0.36199 | 0.31904 | 0.32187 | 121.2291 | 121.1322 | 121.1758 | 121.079
1715.9219 | 121.907 | -0.50812 | 121.4264 | 0.14017 | 0.000689 | -0.012 | -0.01586 | 0.040843 | 0.090161 | -0.071874 | 121.3551 | 121.3446 | 121.3065 | 121.1922 | 0.21763 | 0.37115 | 0.32363 | 0.32646 | 0.64828 | 0.50881 | 0.49612 | 0.49226 | 0.54896 | 0.59828 | 0.43624 | 121.4009 | 121.3904 | 121.3523 | 121.238 | 0.2634 | 0.41693 | 0.36941 | 0.37223 | 121.1375 | 121.0315 | 121.0889 | 120.9828
1717.625 | 121.8658 | -0.52643 | 121.463 | 0.14932 | 0.000689 | -0.021157 | -0.020438 | 0.045421 | 0.090161 | -0.071874 | 121.3689 | 121.3583 | 121.3111 | 121.2013 | 0.20847 | 0.362 | 0.30989 | 0.31272 | 0.67575 | 0.52712 | 0.50527 | 0.50599 | 0.57185 | 0.61659 | 0.45455 | 121.4147 | 121.4041 | 121.3568 | 121.2471 | 0.25425 | 0.40777 | 0.35567 | 0.3585 | 121.1604 | 121.059 | 121.1026 | 121.0012
1719.375 | 121.9528 | -0.46692 | 121.3943 | 0.14017 | -0.00389 | -0.016578 | -0.01586 | 0.040843 | 0.090161 | -0.067295 | 121.3643 | 121.3629 | 121.3111 | 121.2013 | 0.20847 | 0.35742 | 0.31447 | 0.31272 | 0.60708 | 0.46303 | 0.45034 | 0.45106 | 0.50776 | 0.55708 | 0.39962 | 121.4101 | 121.4087 | 121.3568 | 121.2471 | 0.25425 | 0.40319 | 0.36025 | 0.3585 | 121.1558 | 121.0498 | 121.1026 | 120.9966
1721.125 | 121.8521 | -0.50812 | 121.463 | 0.14932 | 0.000689 | -0.007421 | -0.01586 | 0.045421 | 0.085583 | -0.067295 | 121.3735 | 121.3767 | 121.3248 | 121.2105 | 0.20389 | 0.35284 | 0.30074 | 0.30357 | 0.65744 | 0.50881 | 0.5007 | 0.49226 | 0.55354 | 0.5937 | 0.44082 | 121.4192 | 121.4224 | 121.3706 | 121.2563 | 0.24967 | 0.39862 | 0.34651 | 0.34934 | 121.1696 | 121.0727 | 121.1209 | 121.0241
1722.8281 | 122.0123 | -0.44861 | 121.431 | 0.14932 | -0.00389 | -0.021157 | -0.025017 | 0.049999 | 0.090161 | -0.071874 | 121.3826 | 121.3721 | 121.3248 | 121.2105 | 0.20847 | 0.33911 | 0.29616 | 0.29899 | 0.59793 | 0.44472 | 0.42745 | 0.42359 | 0.49861 | 0.53877 | 0.37673 | 121.4284 | 121.4179 | 121.3706 | 121.2563 | 0.25425 | 0.38488 | 0.34193 | 0.34476 | 121.1741 | 121.0865 | 121.1163 | 121.0286
1724.5938 | 122.0032 | -0.37994 | 121.5225 | 0.14474 | -0.00389 | -0.016578 | -0.020438 | 0.045421 | 0.081005 | -0.071874 | 121.4604 | 121.4499 | 121.4164 | 121.2975 | 0.1398 | 0.26128 | 0.23206 | 0.23031 | 0.52469 | 0.37605 | 0.36337 | 0.35951 | 0.42536 | 0.46095 | 0.30807 | 121.5062 | 121.4957 | 121.4621 | 121.3433 | 0.18557 | 0.30705 | 0.27784 | 0.27609 | 121.3206 | 121.2284 | 121.2766 | 121.1843
1726.3594 | 121.9254 | -0.32959 | 121.6003 | 0.14932 | 0.000689 | -0.016578 | -0.020438 | 0.045421 | 0.090161 | -0.076452 | 121.5245 | 121.514 | 121.4805 | 121.3662 | 0.089439 | 0.20634 | 0.16339 | 0.16164 | 0.47891 | 0.33028 | 0.31301 | 0.30915 | 0.37501 | 0.41975 | 0.25314 | 121.5703 | 121.5598 | 121.5262 | 121.412 | 0.13522 | 0.25212 | 0.20916 | 0.20742 | 121.4351 | 121.3612 | 121.391 | 121.3171
1728.0625 | 121.9894 | -0.29755 | 121.6095 | 0.14932 | -0.008469 | -0.007421 | -0.01586 | 0.036265 | 0.085583 | -0.067295 | 121.5566 | 121.5461 | 121.5079 | 121.3891 | 0.071126 | 0.16972 | 0.13592 | 0.14333 | 0.44687 | 0.28908 | 0.29012 | 0.28169 | 0.33381 | 0.38313 | 0.23025 | 121.6024 | 121.5919 | 121.5537 | 121.4349 | 0.1169 | 0.21549 | 0.18169 | 0.18911 | 121.4855 | 121.4207 | 121.4368 | 121.372
1729.8281 | 121.9254 | -0.32044 | 121.6415 | 0.14474 | -0.00389 | -0.012 | -0.025017 | 0.040843 | 0.090161 | -0.067295 | 121.5612 | 121.5552 | 121.5125 | 121.4028 | 0.057392 | 0.16514 | 0.13134 | 0.13875 | 0.46518 | 0.31655 | 0.30844 | 0.29542 | 0.36128 | 0.4106 | 0.25314 | 121.6069 | 121.601 | 121.5583 | 121.4486 | 0.10317 | 0.21092 | 0.17711 | 0.18453 | 121.5038 | 121.4298 | 121.4551 | 121.3812
1731.5156 | 121.9894 | -0.27924 | 121.6141 | 0.14932 | 0.000689 | -0.012 | -0.020438 | 0.045421 | 0.090161 | -0.067295 | 121.5612 | 121.569 | 121.5217 | 121.4028 | 0.066548 | 0.16056 | 0.12218 | 0.12959 | 0.42856 | 0.27992 | 0.26724 | 0.2588 | 0.32466 | 0.3694 | 0.21194 | 121.6069 | 121.6148 | 121.5674 | 121.4486 | 0.11232 | 0.20634 | 0.16796 | 0.17537 | 121.4946 | 121.439 | 121.4551 | 121.3995
1733.2656 | 121.9528 | -0.27008 | 121.6507 | 0.14474 | 0.000689 | -0.016578 | -0.020438 | 0.045421 | 0.09474 | -0.067295 | 121.5703 | 121.5644 | 121.5262 | 121.4166 | 0.052814 | 0.16514 | 0.10387 | 0.12502 | 0.41482 | 0.27077 | 0.2535 | 0.24964 | 0.3155 | 0.36482 | 0.20279 | 121.6161 | 121.6102 | 121.572 | 121.4623 | 0.09859 | 0.21092 | 0.14964 | 0.17079 | 121.5175 | 121.4665 | 121.4734 | 121.4224
1734.9531 | 121.9666 | -0.27466 | 121.6232 | 0.14474 | 0.000689 | -0.016578 | -0.029595 | 0.045421 | 0.090161 | -0.062717 | 121.5703 | 121.5644 | 121.5171 | 121.412 | 0.052814 | 0.15598 | 0.12676 | 0.11586 | 0.4194 | 0.27535 | 0.25808 | 0.24506 | 0.32008 | 0.36482 | 0.21194 | 121.6161 | 121.6102 | 121.5629 | 121.4578 | 0.09859 | 0.20176 | 0.17253 | 0.16164 | 121.5175 | 121.4436 | 121.4643 | 121.3903
1736.7188 | 121.9116 | -0.3067 | 121.6461 | 0.14932 | 0.000689 | -0.016578 | -0.020438 | 0.040843 | 0.09474 | -0.071874 | 121.5703 | 121.5644 | 121.5171 | 121.4166 | 0.052814 | 0.16056 | 0.12218 | 0.12502 | 0.45602 | 0.30739 | 0.29012 | 0.28626 | 0.34754 | 0.40144 | 0.23483 | 121.6161 | 121.6102 | 121.5629 | 121.4623 | 0.09859 | 0.20634 | 0.16796 | 0.17079 | 121.5175 | 121.4481 | 121.4643 | 121.3949
1738.4844 | 122.0123 | -0.27924 | 121.6049 | 0.14932 | 0.000689 | -0.016578 | -0.020438 | 0.045421 | 0.081005 | -0.071874 | 121.5612 | 121.5507 | 121.5079 | 121.4028 | 0.071126 | 0.18345 | 0.13592 | 0.13875 | 0.42856 | 0.27992 | 0.26266 | 0.2588 | 0.32466 | 0.36024 | 0.20736 | 121.6069 | 121.5964 | 121.5537 | 121.4486 | 0.1169 | 0.22923 | 0.18169 | 0.18453 | 121.49 | 121.4253 | 121.4368 | 121.372
1740.2344 | 122.0123 | -0.29755 | 121.5866 | 0.14017 | 0.000689 | -0.012 | -0.020438 | 0.049999 | 0.090161 | -0.067295 | 121.5474 | 121.5323 | 121.4896 | 121.3799 | 0.094017 | 0.18803 | 0.15881 | 0.15249 | 0.43771 | 0.29823 | 0.28555 | 0.27711 | 0.34754 | 0.38771 | 0.23025 | 121.5932 | 121.5781 | 121.5354 | 121.4257 | 0.13979 | 0.23381 | 0.20458 | 0.19826 | 121.4534 | 121.3886 | 121.3956 | 121.3308
1741.9844 | 121.9528 | -0.3067 | 121.6095 | 0.14474 | -0.00389 | -0.012 | -0.020438 | 0.040843 | 0.090161 | -0.067295 | 121.552 | 121.5507 | 121.5079 | 121.3937 | 0.071126 | 0.17887 | 0.14507 | 0.13875 | 0.45144 | 0.30281 | 0.2947 | 0.28626 | 0.34754 | 0.39686 | 0.23941 | 121.5978 | 121.5964 | 121.5537 | 121.4394 | 0.1169 | 0.22465 | 0.19085 | 0.18453 | 121.4809 | 121.4069 | 121.4368 | 121.3629
1743.6875 | 121.9666 | -0.28381 | 121.6003 | 0.15848 | 0.005267 | -0.021157 | -0.020438 | 0.040843 | 0.085583 | -0.067295 | 121.5749 | 121.5781 | 121.5217 | 121.4166 | 0.057392 | 0.15141 | 0.10387 | 0.12959 | 0.44229 | 0.28908 | 0.26266 | 0.26337 | 0.32466 | 0.3694 | 0.21652 | 121.6207 | 121.6239 | 121.5674 | 121.4623 | 0.10317 | 0.19718 | 0.14964 | 0.17537 | 121.5175 | 121.471 | 121.4643 | 121.4178
1745.4531 | 121.8796 | -0.32501 | 121.637 | 0.14932 | -0.008469 | -0.012 | -0.020438 | 0.049999 | 0.085583 | -0.067295 | 121.5657 | 121.5598 | 121.5171 | 121.4028 | 0.066548 | 0.16514 | 0.13134 | 0.12959 | 0.47433 | 0.31654 | 0.31301 | 0.30457 | 0.37501 | 0.4106 | 0.25772 | 121.6115 | 121.6056 | 121.5629 | 121.4486 | 0.11232 | 0.21092 | 0.17711 | 0.17537 | 121.4992 | 121.4344 | 121.4505 | 121.3857
1747.2344 | 122.0123 | -0.25635 | 121.6232 | 0.14474 | -0.00389 | -0.016578 | -0.025017 | 0.040843 | 0.085583 | -0.062717 | 121.5749 | 121.5781 | 121.5262 | 121.4074 | 0.06197 | 0.15598 | 0.1176 | 0.12502 | 0.40109 | 0.25246 | 0.23977 | 0.23133 | 0.29719 | 0.34193 | 0.19363 | 121.6207 | 121.6239 | 121.572 | 121.4532 | 0.10775 | 0.20176 | 0.16338 | 0.17079 | 121.5129 | 121.4573 | 121.4643 | 121.4086
1748.9844 | 121.9528 | -0.31586 | 121.5912 | 0.14932 | -0.00389 | -0.012 | -0.020438 | 0.040843 | 0.085583 | -0.071874 | 121.5474 | 121.5415 | 121.4988 | 121.3708 | 0.075705 | 0.17887 | 0.15881 | 0.15249 | 0.46518 | 0.31197 | 0.30386 | 0.29542 | 0.3567 | 0.40144 | 0.24398 | 121.5932 | 121.5873 | 121.5445 | 121.4165 | 0.12148 | 0.22465 | 0.20458 | 0.19826 | 121.4717 | 121.3886 | 121.4231 | 121.34
1750.7031 | 121.9986 | -0.32501 | 121.5775 | 0.14474 | -0.00389 | -0.016578 | -0.020438 | 0.045421 | 0.085583 | -0.062717 | 121.5474 | 121.5415 | 121.5079 | 121.3799 | 0.089439 | 0.19261 | 0.15423 | 0.15706 | 0.46976 | 0.32112 | 0.30843 | 0.30457 | 0.37043 | 0.4106 | 0.2623 | 121.5932 | 121.5873 | 121.5537 | 121.4257 | 0.13522 | 0.23838 | 0.2 | 0.20284 | 121.458 | 121.3932 | 121.4185 | 121.3537
1752.4688 | 121.907 | -0.35706 | 121.5775 | 0.14932 | 0.000689 | -0.016578 | -0.01586 | 0.045421 | 0.090161 | -0.062717 | 121.5337 | 121.5232 | 121.4896 | 121.3754 | 0.094017 | 0.20176 | 0.16339 | 0.16164 | 0.50638 | 0.35774 | 0.34048 | 0.3412 | 0.40248 | 0.44722 | 0.29434 | 121.5795 | 121.569 | 121.5354 | 121.4211 | 0.13979 | 0.24754 | 0.20916 | 0.20742 | 121.4397 | 121.3703 | 121.3956 | 121.3262
1754.2188 | 121.907 | -0.35706 | 121.5912 | 0.14474 | -0.013048 | -0.016578 | -0.025017 | 0.036265 | 0.090161 | -0.071874 | 121.5291 | 121.5186 | 121.485 | 121.3616 | 0.10317 | 0.2155 | 0.17712 | 0.17996 | 0.5018 | 0.34401 | 0.34048 | 0.33204 | 0.39332 | 0.44722 | 0.28518 | 121.5749 | 121.5644 | 121.5308 | 121.4074 | 0.14895 | 0.26127 | 0.2229 | 0.22573 | 121.4259 | 121.352 | 121.3819 | 121.3079
1755.9844 | 121.8842 | -0.46234 | 121.5271 | 0.14932 | -0.00389 | -0.012 | -0.020438 | 0.036265 | 0.090161 | -0.062717 | 121.4376 | 121.4225 | 121.3843 | 121.27 | 0.17642 | 0.30706 | 0.26869 | 0.26236 | 0.61166 | 0.45845 | 0.45034 | 0.4419 | 0.49861 | 0.5525 | 0.39962 | 121.4833 | 121.4682 | 121.4301 | 121.3158 | 0.2222 | 0.35284 | 0.31446 | 0.30814 | 121.2611 | 121.1689 | 121.2079 | 121.1156
1757.6875 | 122.0352 | -0.39368 | 121.4722 | 0.14932 | -0.008469 | -0.016578 | -0.029595 | 0.040843 | 0.090161 | -0.062717 | 121.4467 | 121.4408 | 121.398 | 121.2838 | 0.16727 | 0.30248 | 0.25038 | 0.26236 | 0.543 | 0.38521 | 0.3771 | 0.36408 | 0.43452 | 0.48384 | 0.33096 | 121.4925 | 121.4865 | 121.4438 | 121.3295 | 0.21304 | 0.34826 | 0.29615 | 0.30814 | 121.2794 | 121.1963 | 121.2308 | 121.1477
1759.4531 | 122.0306 | -0.43488 | 121.431 | 0.14474 | -0.013048 | -0.016578 | -0.020438 | 0.045421 | 0.090161 | -0.071874 | 121.4284 | 121.4179 | 121.3797 | 121.2655 | 0.17642 | 0.31164 | 0.26411 | 0.27152 | 0.57962 | 0.42183 | 0.4183 | 0.41444 | 0.4803 | 0.52504 | 0.363 | 121.4742 | 121.4636 | 121.4255 | 121.3112 | 0.2222 | 0.35741 | 0.30989 | 0.31729 | 121.252 | 121.1643 | 121.2033 | 121.1156
1761.2188 | 122.0123 | -0.42572 | 121.4447 | 0.14932 | -0.008469 | -0.012 | -0.020438 | 0.045421 | 0.090161 | -0.071874 | 121.4376 | 121.427 | 121.3843 | 121.2655 | 0.181 | 0.30706 | 0.26869 | 0.26694 | 0.57504 | 0.41725 | 0.41372 | 0.40528 | 0.47114 | 0.51588 | 0.35385 | 121.4833 | 121.4728 | 121.4301 | 121.3112 | 0.22678 | 0.35284 | 0.31446 | 0.31272 | 121.2565 | 121.1689 | 121.2033 | 121.1156
1762.9844 | 122.0032 | -0.42114 | 121.4905 | 0.14932 | -0.00389 | -0.016578 | -0.029595 | 0.040843 | 0.085583 | -0.071874 | 121.4376 | 121.4316 | 121.3797 | 121.27 | 0.17185 | 0.31164 | 0.26869 | 0.26694 | 0.57046 | 0.41725 | 0.40457 | 0.39155 | 0.46199 | 0.50673 | 0.34927 | 121.4833 | 121.4774 | 121.4255 | 121.3158 | 0.21762 | 0.35741 | 0.31446 | 0.31272 | 121.2657 | 121.1689 | 121.2079 | 121.111
1764.6875 | 121.9757 | -0.41657 | 121.4996 | 0.14474 | -0.00389 | -0.025735 | -0.020438 | 0.045421 | 0.085583 | -0.076452 | 121.4376 | 121.4316 | 121.3843 | 121.2746 | 0.16727 | 0.30706 | 0.26869 | 0.27152 | 0.56131 | 0.41268 | 0.39083 | 0.39613 | 0.46199 | 0.50215 | 0.34011 | 121.4833 | 121.4774 | 121.4301 | 121.3204 | 0.21304 | 0.35284 | 0.31446 | 0.31729 | 121.2703 | 121.1689 | 121.217 | 121.1156
1766.4531 | 121.9025 | -0.46234 | 121.4996 | 0.14474 | 0.000689 | -0.012 | -0.020438 | 0.040843 | 0.085583 | -0.071874 | 121.4467 | 121.427 | 121.3935 | 121.27 | 0.17185 | 0.30248 | 0.25495 | 0.26694 | 0.60708 | 0.46303 | 0.45034 | 0.4419 | 0.50318 | 0.54792 | 0.39047 | 121.4925 | 121.4728 | 121.4392 | 121.3158 | 0.21762 | 0.34826 | 0.30073 | 0.31272 | 121.2749 | 121.1918 | 121.2216 | 121.1385
1768.2188 | 121.994 | -0.40283 | 121.4813 | 0.14474 | -0.008469 | -0.016578 | -0.020438 | 0.040843 | 0.085583 | -0.071874 | 121.4559 | 121.4408 | 121.3935 | 121.2838 | 0.15811 | 0.2979 | 0.25495 | 0.24863 | 0.54758 | 0.39436 | 0.38625 | 0.38239 | 0.44368 | 0.48842 | 0.33096 | 121.5016 | 121.4865 | 121.4392 | 121.3295 | 0.20389 | 0.34368 | 0.30073 | 0.2944 | 121.2978 | 121.2009 | 121.2354 | 121.1385
1769.9688 | 121.8933 | -0.44861 | 121.5363 | 0.14474 | -0.008469 | -0.012 | -0.01586 | 0.045421 | 0.081005 | -0.067295 | 121.4513 | 121.4453 | 121.4026 | 121.2883 | 0.17185 | 0.2979 | 0.25495 | 0.26236 | 0.59335 | 0.44014 | 0.43661 | 0.43275 | 0.49403 | 0.52961 | 0.38131 | 121.4971 | 121.4911 | 121.4484 | 121.3341 | 0.21762 | 0.34368 | 0.30073 | 0.30814 | 121.2794 | 121.1963 | 121.2308 | 121.1477
1771.6562 | 121.9116 | -0.36621 | 121.5729 | 0.14932 | -0.00389 | -0.016578 | -0.020438 | 0.045421 | 0.09474 | -0.067295 | 121.5245 | 121.514 | 121.4759 | 121.357 | 0.11691 | 0.22465 | 0.18628 | 0.17996 | 0.51553 | 0.36232 | 0.34963 | 0.34577 | 0.41163 | 0.46095 | 0.29892 | 121.5703 | 121.5598 | 121.5217 | 121.4028 | 0.16268 | 0.27043 | 0.23205 | 0.22573 | 121.4076 | 121.3383 | 121.359 | 121.2896
1773.4219 | 122.0306 | -0.28839 | 121.5775 | 0.14932 | -0.00389 | -0.012 | -0.020438 | 0.049999 | 0.090161 | -0.067295 | 121.5612 | 121.5552 | 121.5079 | 121.3845 | 0.080283 | 0.19261 | 0.16339 | 0.15706 | 0.43771 | 0.2845 | 0.27639 | 0.26795 | 0.33839 | 0.37855 | 0.2211 | 121.6069 | 121.601 | 121.5537 | 121.4303 | 0.12606 | 0.23838 | 0.20916 | 0.20284 | 121.4809 | 121.3978 | 121.4276 | 121.3445
1775.1875 | 122.0078 | -0.36621 | 121.5225 | 0.14932 | 0.000689 | -0.016578 | -0.025017 | 0.049999 | 0.085583 | -0.071874 | 121.4833 | 121.4728 | 121.4255 | 121.3112 | 0.14438 | 0.27501 | 0.22748 | 0.22574 | 0.51553 | 0.3669 | 0.34963 | 0.34119 | 0.41621 | 0.45179 | 0.29434 | 121.5291 | 121.5186 | 121.4713 | 121.357 | 0.19015 | 0.32079 | 0.27326 | 0.27151 | 121.339 | 121.2559 | 121.2811 | 121.198
1776.9375 | 121.9025 | -0.45319 | 121.5271 | 0.14932 | 0.000689 | -0.007421 | -0.01586 | 0.040843 | 0.081005 | -0.076452 | 121.4604 | 121.4453 | 121.4026 | 121.2975 | 0.15811 | 0.29333 | 0.25495 | 0.25321 | 0.60251 | 0.45387 | 0.44576 | 0.43733 | 0.49403 | 0.53419 | 0.37673 | 121.5062 | 121.4911 | 121.4484 | 121.3433 | 0.20389 | 0.3391 | 0.30073 | 0.29898 | 121.3023 | 121.2055 | 121.2445 | 121.1477
1778.6562 | 122.0352 | -0.3891 | 121.4951 | 0.14474 | -0.008469 | -0.012 | -0.01586 | 0.045421 | 0.085583 | -0.067295 | 121.4742 | 121.4545 | 121.4164 | 121.3112 | 0.15353 | 0.28875 | 0.2458 | 0.24863 | 0.53384 | 0.38063 | 0.3771 | 0.37324 | 0.43452 | 0.47468 | 0.3218 | 121.52 | 121.5003 | 121.4621 | 121.357 | 0.19931 | 0.33452 | 0.29157 | 0.2944 | 121.3206 | 121.2284 | 121.2628 | 121.1706
1780.4062 | 121.9254 | -0.4303 | 121.5179 | 0.14932 | -0.013048 | -0.016578 | -0.01586 | 0.045421 | 0.09474 | -0.062717 | 121.4742 | 121.4545 | 121.4209 | 121.3112 | 0.15353 | 0.28875 | 0.2458 | 0.23489 | 0.57962 | 0.41725 | 0.41372 | 0.41444 | 0.47572 | 0.52504 | 0.36758 | 121.52 | 121.5003 | 121.4667 | 121.357 | 0.19931 | 0.33452 | 0.29157 | 0.28067 | 121.3206 | 121.2284 | 121.2674 | 121.1751
1782.1562 | 121.8704 | -0.4303 | 121.582 | 0.14017 | 0.005267 | -0.007421 | -0.020438 | 0.040843 | 0.090161 | -0.067295 | 121.4788 | 121.4682 | 121.4301 | 121.3158 | 0.15353 | 0.27959 | 0.23664 | 0.23031 | 0.57046 | 0.43557 | 0.42288 | 0.40986 | 0.47114 | 0.52046 | 0.363 | 121.5245 | 121.514 | 121.4759 | 121.3616 | 0.19931 | 0.32537 | 0.28242 | 0.27609 | 121.3252 | 121.2421 | 121.2766 | 121.1935
1783.9219 | 121.9757 | -0.40283 | 121.5408 | 0.14932 | -0.008469 | -0.012 | -0.025017 | 0.045421 | 0.090161 | -0.067295 | 121.4925 | 121.4728 | 121.4255 | 121.3204 | 0.14896 | 0.27044 | 0.23206 | 0.23031 | 0.55215 | 0.39436 | 0.39083 | 0.37782 | 0.44825 | 0.49299 | 0.33554 | 121.5383 | 121.5186 | 121.4713 | 121.3662 | 0.19473 | 0.31621 | 0.27784 | 0.27609 | 121.3435 | 121.2604 | 121.2766 | 121.1935
1785.625 | 122.0123 | -0.36621 | 121.5363 | 0.14932 | -0.00389 | -0.012 | -0.025017 | 0.049999 | 0.081005 | -0.067295 | 121.4879 | 121.4774 | 121.4301 | 121.3204 | 0.1398 | 0.26586 | 0.23206 | 0.22574 | 0.51553 | 0.36232 | 0.35421 | 0.34119 | 0.41621 | 0.44722 | 0.29892 | 121.5337 | 121.5232 | 121.4759 | 121.3662 | 0.18557 | 0.31163 | 0.27784 | 0.27151 | 121.3481 | 121.2559 | 121.2903 | 121.198
1787.375 | 121.9254 | -0.39368 | 121.5591 | 0.1539 | -0.008469 | -0.021157 | -0.01586 | 0.045421 | 0.085583 | -0.062717 | 121.4925 | 121.482 | 121.4393 | 121.3296 | 0.14438 | 0.26586 | 0.22748 | 0.22574 | 0.54758 | 0.38521 | 0.37252 | 0.37782 | 0.4391 | 0.47926 | 0.33096 | 121.5383 | 121.5278 | 121.485 | 121.3753 | 0.19015 | 0.31163 | 0.27326 | 0.27151 | 121.3481 | 121.265 | 121.2949 | 121.2118
1789.125 | 121.9528 | -0.38452 | 121.5317 | 0.14932 | -0.00389 | -0.012 | -0.020438 | 0.036265 | 0.09474 | -0.071874 | 121.4971 | 121.482 | 121.453 | 121.325 | 0.13064 | 0.2567 | 0.21833 | 0.21658 | 0.53384 | 0.38063 | 0.37252 | 0.36408 | 0.42079 | 0.47926 | 0.31265 | 121.5428 | 121.5278 | 121.4988 | 121.3708 | 0.17642 | 0.30248 | 0.2641 | 0.26236 | 121.3664 | 121.2787 | 121.3223 | 121.2347
1790.8125 | 122.0306 | -0.37079 | 121.5637 | 0.14474 | -0.008469 | -0.021157 | -0.025017 | 0.040843 | 0.09474 | -0.071874 | 121.5017 | 121.4866 | 121.4484 | 121.3387 | 0.13064 | 0.25212 | 0.21833 | 0.21658 | 0.51553 | 0.36232 | 0.34963 | 0.34577 | 0.41163 | 0.46553 | 0.29891 | 121.5474 | 121.5323 | 121.4942 | 121.3845 | 0.17642 | 0.2979 | 0.2641 | 0.26236 | 121.371 | 121.2833 | 121.3178 | 121.2301
1792.5 | 122.0123 | -0.36621 | 121.5591 | 0.14474 | -0.008469 | -0.012 | -0.01586 | 0.040843 | 0.085583 | -0.071874 | 121.5062 | 121.4957 | 121.4484 | 121.3387 | 0.13064 | 0.25212 | 0.20917 | 0.21658 | 0.51095 | 0.35774 | 0.35421 | 0.35035 | 0.40705 | 0.45179 | 0.29434 | 121.552 | 121.5415 | 121.4942 | 121.3845 | 0.17642 | 0.2979 | 0.25495 | 0.26236 | 121.3756 | 121.2971 | 121.3178 | 121.2392
1794.2656 | 121.8887 | -0.42114 | 121.5683 | 0.14932 | -0.00389 | -0.007421 | -0.01586 | 0.036265 | 0.081005 | -0.062717 | 121.5062 | 121.5003 | 121.4621 | 121.3387 | 0.13064 | 0.24297 | 0.21375 | 0.20742 | 0.57046 | 0.41725 | 0.41372 | 0.40528 | 0.45741 | 0.50215 | 0.35843 | 121.552 | 121.5461 | 121.5079 | 121.3845 | 0.17642 | 0.28874 | 0.25952 | 0.2532 | 121.3756 | 121.2925 | 121.3315 | 121.2484
1796.0156 | 121.8933 | -0.40741 | 121.5958 | 0.14932 | -0.00389 | -0.016578 | -0.020438 | 0.040843 | 0.085583 | -0.071874 | 121.52 | 121.5003 | 121.4576 | 121.3433 | 0.12149 | 0.24297 | 0.20917 | 0.20285 | 0.55673 | 0.40352 | 0.39083 | 0.38697 | 0.44825 | 0.49299 | 0.33554 | 121.5657 | 121.5461 | 121.5033 | 121.3891 | 0.16726 | 0.28874 | 0.25495 | 0.24862 | 121.3985 | 121.3108 | 121.3361 | 121.2484
1797.7188 | 122.0169 | -0.36621 | 121.5637 | 0.14932 | -0.00389 | -0.012 | -0.011281 | 0.031687 | 0.085583 | -0.067295 | 121.52 | 121.5049 | 121.4621 | 121.3479 | 0.12149 | 0.23839 | 0.20001 | 0.20742 | 0.51553 | 0.36232 | 0.35421 | 0.35493 | 0.3979 | 0.45179 | 0.29892 | 121.5657 | 121.5506 | 121.5079 | 121.3937 | 0.16726 | 0.28417 | 0.24579 | 0.2532 | 121.3985 | 121.32 | 121.3407 | 121.2621
1799.4844 | 121.9208 | -0.36621 | 121.5958 | 0.14932 | -0.00389 | -0.016578 | -0.011281 | 0.045421 | 0.085583 | -0.067295 | 121.5337 | 121.5232 | 121.4805 | 121.3662 | 0.11691 | 0.23381 | 0.19086 | 0.17996 | 0.51553 | 0.36232 | 0.34963 | 0.35493 | 0.41163 | 0.45179 | 0.29892 | 121.5795 | 121.569 | 121.5262 | 121.412 | 0.16268 | 0.27959 | 0.23663 | 0.22573 | 121.4168 | 121.3428 | 121.3635 | 121.2896
1801.25 | 121.9345 | -0.37994 | 121.6049 | 0.14932 | -0.00389 | -0.012 | -0.01586 | 0.040843 | 0.090161 | -0.071874 | 121.5245 | 121.5094 | 121.4759 | 121.357 | 0.11691 | 0.23381 | 0.20001 | 0.19369 | 0.52926 | 0.37605 | 0.36794 | 0.36408 | 0.42079 | 0.4701 | 0.30807 | 121.5703 | 121.5552 | 121.5217 | 121.4028 | 0.16268 | 0.27959 | 0.24579 | 0.23947 | 121.4076 | 121.3245 | 121.359 | 121.2759
1802.9688 | 121.907 | -0.3891 | 121.6003 | 0.14932 | 0.000689 | -0.012 | -0.020438 | 0.045421 | 0.09474 | -0.067295 | 121.5337 | 121.5186 | 121.4713 | 121.3616 | 0.11691 | 0.22923 | 0.20001 | 0.20285 | 0.53842 | 0.38979 | 0.3771 | 0.36866 | 0.43452 | 0.48384 | 0.3218 | 121.5795 | 121.5644 | 121.5171 | 121.4074 | 0.16268 | 0.27501 | 0.24579 | 0.24862 | 121.4168 | 121.3337 | 121.3544 | 121.2713
1804.7188 | 121.907 | -0.40283 | 121.6095 | 0.14932 | -0.00389 | -0.012 | -0.020438 | 0.049999 | 0.090161 | -0.062717 | 121.5291 | 121.5232 | 121.485 | 121.3708 | 0.11233 | 0.22923 | 0.19543 | 0.19369 | 0.55215 | 0.39894 | 0.39083 | 0.38239 | 0.45283 | 0.49299 | 0.34012 | 121.5749 | 121.569 | 121.5308 | 121.4165 | 0.15811 | 0.27501 | 0.24121 | 0.23947 | 121.4168 | 121.3337 | 121.3727 | 121.2896
1806.4062 | 121.9025 | -0.37079 | 121.6003 | 0.14017 | -0.008469 | -0.007421 | -0.025017 | 0.040843 | 0.090161 | -0.071874 | 121.5337 | 121.5278 | 121.485 | 121.3708 | 0.11233 | 0.22008 | 0.1817 | 0.17996 | 0.51095 | 0.36232 | 0.36337 | 0.34577 | 0.41163 | 0.46095 | 0.29891 | 121.5795 | 121.5735 | 121.5308 | 121.4165 | 0.15811 | 0.26585 | 0.22748 | 0.22573 | 121.4214 | 121.352 | 121.3727 | 121.3033
1808.1562 | 121.8979 | -0.37079 | 121.5912 | 0.14474 | -0.00389 | -0.021157 | -0.020438 | 0.036265 | 0.090161 | -0.058139 | 121.5337 | 121.5323 | 121.4942 | 121.3708 | 0.11233 | 0.22465 | 0.1817 | 0.18453 | 0.51553 | 0.3669 | 0.34963 | 0.35035 | 0.40705 | 0.46095 | 0.31265 | 121.5795 | 121.5781 | 121.54 | 121.4165 | 0.15811 | 0.27043 | 0.22748 | 0.23031 | 121.4214 | 121.352 | 121.3819 | 121.3125
1809.9062 | 121.9025 | -0.37994 | 121.6278 | 0.14932 | -0.008469 | -0.016578 | -0.01586 | 0.036265 | 0.090161 | -0.067295 | 121.5566 | 121.5415 | 121.4988 | 121.3845 | 0.10317 | 0.22008 | 0.18628 | 0.17996 | 0.52926 | 0.37147 | 0.36337 | 0.36408 | 0.41621 | 0.4701 | 0.31265 | 121.6024 | 121.5873 | 121.5445 | 121.4303 | 0.14895 | 0.26585 | 0.23205 | 0.22573 | 121.4534 | 121.3703 | 121.3956 | 121.3125
1811.6719 | 121.9711 | -0.35706 | 121.6095 | 0.14474 | -0.008469 | -0.012 | -0.01586 | 0.049999 | 0.081005 | -0.062717 | 121.5566 | 121.5415 | 121.5125 | 121.3845 | 0.10317 | 0.21092 | 0.17254 | 0.1708 | 0.5018 | 0.34859 | 0.34506 | 0.3412 | 0.40706 | 0.43806 | 0.29434 | 121.6024 | 121.5873 | 121.5583 | 121.4303 | 0.14895 | 0.2567 | 0.21832 | 0.21658 | 121.4534 | 121.3841 | 121.4093 | 121.34
1813.4219 | 122.0352 | -0.3067 | 121.6095 | 0.14474 | -0.008469 | -0.021157 | -0.025017 | 0.040843 | 0.090161 | -0.058139 | 121.5612 | 121.5507 | 121.5125 | 121.3937 | 0.094017 | 0.20634 | 0.16797 | 0.16622 | 0.45144 | 0.29823 | 0.28554 | 0.28168 | 0.34754 | 0.39686 | 0.24856 | 121.6069 | 121.5964 | 121.5583 | 121.4394 | 0.13979 | 0.25212 | 0.21374 | 0.212 | 121.4672 | 121.3932 | 121.4185 | 121.3445
1815.1875 | 121.9849 | -0.32044 | 121.6095 | 0.14474 | -0.008469 | -0.012 | -0.025017 | 0.040843 | 0.085583 | -0.067295 | 121.5612 | 121.5552 | 121.5125 | 121.3982 | 0.084861 | 0.20176 | 0.16339 | 0.15249 | 0.46518 | 0.31197 | 0.30844 | 0.29542 | 0.36128 | 0.40602 | 0.25314 | 121.6069 | 121.601 | 121.5583 | 121.444 | 0.13064 | 0.24754 | 0.20916 | 0.19826 | 121.4763 | 121.3978 | 121.4276 | 121.3491
1816.8906 | 121.9894 | -0.29297 | 121.6141 | 0.14932 | -0.013048 | -0.012 | -0.01586 | 0.049999 | 0.090161 | -0.071874 | 121.5841 | 121.5736 | 121.5308 | 121.412 | 0.075705 | 0.17887 | 0.14965 | 0.13875 | 0.44229 | 0.27992 | 0.28097 | 0.27711 | 0.34297 | 0.38313 | 0.22109 | 121.6298 | 121.6193 | 121.5766 | 121.4578 | 0.12148 | 0.22465 | 0.19543 | 0.18453 | 121.5084 | 121.4344 | 121.4551 | 121.3812
1818.6719 | 121.962 | -0.31128 | 121.6461 | 0.1539 | -0.008469 | -0.007421 | -0.01586 | 0.045421 | 0.085583 | -0.067295 | 121.5886 | 121.5827 | 121.5491 | 121.4303 | 0.075705 | 0.1743 | 0.12676 | 0.14333 | 0.46518 | 0.30281 | 0.30386 | 0.29542 | 0.3567 | 0.39686 | 0.24398 | 121.6344 | 121.6285 | 121.5949 | 121.4761 | 0.12148 | 0.22007 | 0.17253 | 0.18911 | 121.5129 | 121.4619 | 121.4734 | 121.4224
1820.4219 | 121.9254 | -0.32501 | 121.6553 | 0.1539 | -0.013048 | -0.007421 | -0.020438 | 0.045421 | 0.09474 | -0.062717 | 121.5932 | 121.5873 | 121.54 | 121.4257 | 0.066548 | 0.16972 | 0.14049 | 0.13417 | 0.47891 | 0.31196 | 0.31759 | 0.30457 | 0.37043 | 0.41975 | 0.2623 | 121.639 | 121.6331 | 121.5857 | 121.4715 | 0.11232 | 0.21549 | 0.18627 | 0.17995 | 121.5267 | 121.4527 | 121.4734 | 121.3995
1822.125 | 121.9894 | -0.27924 | 121.669 | 0.14932 | -0.008469 | -0.012 | -0.01586 | 0.049999 | 0.085583 | -0.067295 | 121.6024 | 121.5873 | 121.5537 | 121.4303 | 0.057392 | 0.16514 | 0.10387 | 0.13417 | 0.42856 | 0.27077 | 0.26724 | 0.26338 | 0.32923 | 0.36482 | 0.21194 | 121.6482 | 121.6331 | 121.5995 | 121.4761 | 0.10317 | 0.21092 | 0.14964 | 0.17995 | 121.545 | 121.4985 | 121.4963 | 121.4498
1823.8906 | 121.8933 | -0.29297 | 121.6919 | 0.14932 | -0.013048 | -0.012 | -0.01586 | 0.045421 | 0.09474 | -0.067295 | 121.6161 | 121.6056 | 121.5629 | 121.4532 | 0.048236 | 0.15141 | 0.080975 | 0.11586 | 0.44229 | 0.27992 | 0.28097 | 0.27711 | 0.33839 | 0.38771 | 0.22567 | 121.6619 | 121.6514 | 121.6086 | 121.499 | 0.094012 | 0.19718 | 0.12675 | 0.16164 | 121.5679 | 121.5351 | 121.5146 | 121.4819
1825.6406 | 121.9299 | -0.3067 | 121.6919 | 0.14932 | -0.008469 | -0.012 | -0.020438 | 0.049999 | 0.090161 | -0.067295 | 121.6161 | 121.6102 | 121.5629 | 121.4532 | 0.052814 | 0.15141 | 0.071818 | 0.12502 | 0.45602 | 0.29823 | 0.2947 | 0.28626 | 0.3567 | 0.39686 | 0.23941 | 121.6619 | 121.656 | 121.6086 | 121.499 | 0.09859 | 0.19718 | 0.11759 | 0.17079 | 121.5633 | 121.5443 | 121.5101 | 121.491
1827.3281 | 122.0444 | -0.27008 | 121.6553 | 0.14932 | -0.013048 | -0.012 | -0.01586 | 0.054577 | 0.085583 | -0.071874 | 121.6207 | 121.6102 | 121.5674 | 121.4486 | 0.052814 | 0.14683 | 0.085554 | 0.11586 | 0.4194 | 0.25703 | 0.25808 | 0.25422 | 0.32466 | 0.35566 | 0.19821 | 121.6665 | 121.656 | 121.6132 | 121.4944 | 0.09859 | 0.1926 | 0.13133 | 0.16164 | 121.5679 | 121.5351 | 121.5146 | 121.4819
1829.0938 | 121.9391 | -0.29297 | 121.6965 | 0.14474 | -0.013048 | -0.012 | -0.020438 | 0.040843 | 0.085583 | -0.067295 | 121.639 | 121.6148 | 121.5766 | 121.4532 | 0.048236 | 0.14225 | 0.053505 | 0.11128 | 0.43771 | 0.27992 | 0.28097 | 0.27253 | 0.33381 | 0.37855 | 0.22567 | 121.6848 | 121.6605 | 121.6224 | 121.499 | 0.094012 | 0.18803 | 0.099281 | 0.15706 | 121.5908 | 121.5855 | 121.5284 | 121.5231
1830.8438 | 122.0581 | -0.23346 | 121.669 | 0.14474 | -0.00389 | -0.016578 | -0.029595 | 0.040843 | 0.090161 | -0.067295 | 121.6436 | 121.6285 | 121.5858 | 121.4624 | 0.029923 | 0.12851 | 0.048926 | 0.10213 | 0.3782 | 0.22957 | 0.21688 | 0.20386 | 0.2743 | 0.32362 | 0.16616 | 121.6894 | 121.6743 | 121.6315 | 121.5081 | 0.075699 | 0.17429 | 0.094702 | 0.1479 | 121.6137 | 121.5947 | 121.5558 | 121.5368
1832.5938 | 121.994 | -0.24719 | 121.6965 | 0.14932 | -0.00389 | -0.012 | -0.020438 | 0.045421 | 0.081005 | -0.062717 | 121.6482 | 121.6422 | 121.5995 | 121.4807 | 0.029923 | 0.11478 | 0.03977 | 0.088392 | 0.39651 | 0.2433 | 0.23519 | 0.22675 | 0.29261 | 0.3282 | 0.18448 | 121.6939 | 121.688 | 121.6453 | 121.5264 | 0.075699 | 0.16056 | 0.085546 | 0.13417 | 121.6182 | 121.6084 | 121.5696 | 121.5597
1834.3594 | 121.9208 | -0.28839 | 121.7468 | 0.1539 | -0.017627 | -0.021157 | -0.01586 | 0.040843 | 0.085583 | -0.076452 | 121.6665 | 121.6514 | 121.6086 | 121.499 | 0.016188 | 0.10562 | 0.03977 | 0.079235 | 0.44229 | 0.27076 | 0.26723 | 0.27253 | 0.32923 | 0.37397 | 0.21194 | 121.7123 | 121.6972 | 121.6544 | 121.5448 | 0.061964 | 0.1514 | 0.085546 | 0.12501 | 121.6503 | 121.6267 | 121.5925 | 121.5689
1836.125 | 121.9391 | -0.23346 | 121.7285 | 0.1539 | -0.00389 | -0.012 | -0.020438 | 0.040843 | 0.085583 | -0.067295 | 121.6756 | 121.6697 | 121.6315 | 121.5127 | 0.007032 | 0.10562 | 0.026035 | 0.079235 | 0.38736 | 0.22957 | 0.22146 | 0.21302 | 0.2743 | 0.31904 | 0.16616 | 121.7214 | 121.7155 | 121.6773 | 121.5585 | 0.052808 | 0.1514 | 0.071811 | 0.12501 | 121.6686 | 121.6496 | 121.6245 | 121.6055
1837.8906 | 122.0398 | -0.2243 | 121.6873 | 0.14932 | -0.00389 | -0.012 | -0.025017 | 0.045421 | 0.085583 | -0.067295 | 121.6802 | 121.6743 | 121.6315 | 121.5036 | 0.007032 | 0.096469 | 0.026035 | 0.065501 | 0.37362 | 0.22041 | 0.2123 | 0.19929 | 0.26972 | 0.30989 | 0.15701 | 121.726 | 121.7201 | 121.6773 | 121.5493 | 0.052808 | 0.14225 | 0.071811 | 0.11128 | 121.6732 | 121.6542 | 121.6245 | 121.6055
1839.5938 | 122.0032 | -0.18768 | 121.7468 | 0.14474 | -0.022205 | -0.016578 | -0.01586 | 0.049999 | 0.090161 | -0.071874 | 121.7123 | 121.7018 | 121.659 | 121.5402 | -0.011281 | 0.064423 | 0.012299 | 0.047188 | 0.33243 | 0.16548 | 0.1711 | 0.17182 | 0.23768 | 0.27784 | 0.11581 | 121.758 | 121.7475 | 121.7048 | 121.586 | 0.034495 | 0.1102 | 0.058075 | 0.092964 | 121.7235 | 121.7 | 121.6703 | 121.6467
1841.3438 | 122.0444 | -0.15106 | 121.7468 | 0.14932 | -0.00389 | -0.007421 | -0.020438 | 0.045421 | 0.090161 | -0.058139 | 121.7352 | 121.7201 | 121.6865 | 121.5631 | -0.025015 | 0.04611 | 0.003143 | 0.033454 | 0.30038 | 0.14717 | 0.14364 | 0.13062 | 0.19648 | 0.24122 | 0.092923 | 121.7809 | 121.7659 | 121.7323 | 121.6089 | 0.020761 | 0.091886 | 0.048919 | 0.07923 | 121.7602 | 121.732 | 121.7115 | 121.6833
1843.0312 | 122.0032 | -0.16022 | 121.8018 | 0.14474 | -0.008469 | -0.021157 | -0.020438 | 0.045421 | 0.085583 | -0.067295 | 121.7397 | 121.7292 | 121.6865 | 121.5722 | -0.034171 | 0.032376 | -0.006014 | 0.019719 | 0.30496 | 0.15175 | 0.13906 | 0.13978 | 0.20564 | 0.2458 | 0.092922 | 121.7855 | 121.775 | 121.7323 | 121.618 | 0.011605 | 0.078152 | 0.039762 | 0.065495 | 121.7739 | 121.7457 | 121.7206 | 121.6925
1844.7812 | 121.9254 | -0.19684 | 121.8109 | 0.14474 | -0.00389 | -0.002842 | -0.020438 | 0.045421 | 0.085583 | -0.067295 | 121.7397 | 121.7292 | 121.6956 | 121.5768 | -0.034171 | 0.027798 | -0.001436 | 0.024297 | 0.34158 | 0.19295 | 0.194 | 0.1764 | 0.24226 | 0.28242 | 0.12954 | 121.7855 | 121.775 | 121.7414 | 121.6226 | 0.011605 | 0.073574 | 0.04434 | 0.070073 | 121.7739 | 121.7412 | 121.7298 | 121.6971
1846.5469 | 121.9391 | -0.16937 | 121.7834 | 0.14932 | -0.008469 | -0.012 | -0.011281 | 0.040843 | 0.085583 | -0.062717 | 121.7489 | 121.7384 | 121.7048 | 121.5768 | -0.025015 | 0.027798 | -0.010593 | 0.019719 | 0.31869 | 0.1609 | 0.15737 | 0.15809 | 0.21022 | 0.25496 | 0.10666 | 121.7947 | 121.7842 | 121.7506 | 121.6226 | 0.020761 | 0.073574 | 0.035183 | 0.065495 | 121.7739 | 121.7595 | 121.7298 | 121.7154
1848.2656 | 121.9162 | -0.1831 | 121.8018 | 0.14474 | -0.00389 | -0.012 | -0.01586 | 0.045421 | 0.085583 | -0.071874 | 121.7535 | 121.7338 | 121.7094 | 121.586 | -0.034171 | 0.027798 | -0.010593 | 0.024297 | 0.32785 | 0.17921 | 0.1711 | 0.16724 | 0.22853 | 0.26869 | 0.11123 | 121.7992 | 121.7796 | 121.7551 | 121.6318 | 0.011605 | 0.073574 | 0.035183 | 0.070073 | 121.7876 | 121.7641 | 121.7435 | 121.72
1850.0312 | 122.0398 | -0.12817 | 121.7789 | 0.14474 | -0.008469 | -0.016578 | -0.01586 | 0.040843 | 0.085583 | -0.071874 | 121.7535 | 121.7384 | 121.7048 | 121.5814 | -0.043328 | 0.02322 | -0.015171 | 0.019719 | 0.27292 | 0.11971 | 0.1116 | 0.11231 | 0.16902 | 0.21376 | 0.0563 | 121.7992 | 121.7842 | 121.7506 | 121.6272 | 0.002448 | 0.068996 | 0.030605 | 0.065495 | 121.7968 | 121.7686 | 121.7481 | 121.72
1851.7969 | 121.9894 | -0.15564 | 121.8063 | 0.14474 | -0.008469 | -0.016578 | -0.020438 | 0.036265 | 0.085583 | -0.067295 | 121.758 | 121.7384 | 121.7048 | 121.5951 | -0.043328 | 0.018642 | -0.010593 | 0.015141 | 0.30038 | 0.14717 | 0.13906 | 0.1352 | 0.1919 | 0.24122 | 0.088345 | 121.8038 | 121.7842 | 121.7506 | 121.6409 | 0.002448 | 0.064418 | 0.035183 | 0.060917 | 121.8014 | 121.7686 | 121.7481 | 121.7154
1853.4844 | 121.9528 | -0.16937 | 121.8292 | 0.1539 | -0.013048 | -0.012 | -0.025017 | 0.040843 | 0.090161 | -0.062717 | 121.758 | 121.7521 | 121.7185 | 121.586 | -0.043328 | 0.014064 | -0.010593 | 0.010563 | 0.32327 | 0.15632 | 0.15737 | 0.14436 | 0.21022 | 0.25953 | 0.10666 | 121.8038 | 121.7979 | 121.7643 | 121.6318 | 0.002448 | 0.05984 | 0.035183 | 0.056339 | 121.8014 | 121.7686 | 121.7619 | 121.7291
1855.25 | 122.0398 | -0.13275 | 121.8018 | 0.14474 | -0.008469 | -0.007421 | -0.025017 | 0.045421 | 0.090161 | -0.067295 | 121.7626 | 121.7475 | 121.7185 | 121.586 | -0.043328 | 0.014064 | -0.019749 | 0.015141 | 0.27749 | 0.12428 | 0.12533 | 0.10773 | 0.17817 | 0.22291 | 0.065456 | 121.8084 | 121.7933 | 121.7643 | 121.6318 | 0.002448 | 0.05984 | 0.026027 | 0.060917 | 121.806 | 121.7824 | 121.7619 | 121.7383
1857.0156 | 121.9437 | -0.17853 | 121.8292 | 0.14932 | -0.017627 | -0.012 | -0.029595 | 0.045421 | 0.09474 | -0.071874 | 121.7718 | 121.7521 | 121.7139 | 121.5951 | -0.043328 | 0.014064 | -0.015171 | 0.005985 | 0.32785 | 0.1609 | 0.16653 | 0.14893 | 0.22395 | 0.27327 | 0.10665 | 121.8176 | 121.7979 | 121.7597 | 121.6409 | 0.002448 | 0.05984 | 0.030605 | 0.051761 | 121.8151 | 121.787 | 121.7573 | 121.7291
1858.7812 | 121.9803 | -0.14648 | 121.8063 | 0.14474 | -0.008469 | -0.016578 | -0.020438 | 0.040843 | 0.081005 | -0.067295 | 121.7718 | 121.7567 | 121.7139 | 121.5951 | -0.03875 | 0.014064 | -0.010593 | 0.005985 | 0.29123 | 0.13801 | 0.12991 | 0.12605 | 0.18733 | 0.22749 | 0.079189 | 121.8176 | 121.8025 | 121.7597 | 121.6409 | 0.007026 | 0.05984 | 0.035183 | 0.051761 | 121.8105 | 121.7824 | 121.7527 | 121.7245
1860.4844 | 122.0032 | -0.15106 | 121.8201 | 0.14474 | -0.00389 | -0.016578 | -0.025017 | 0.031687 | 0.085583 | -0.067295 | 121.7672 | 121.7521 | 121.7094 | 121.5906 | -0.047906 | 0.018642 | -0.019749 | 0.005985 | 0.2958 | 0.14717 | 0.13448 | 0.12604 | 0.18275 | 0.23664 | 0.083767 | 121.813 | 121.7979 | 121.7551 | 121.6363 | -0.00213 | 0.064418 | 0.026027 | 0.051761 | 121.8151 | 121.787 | 121.7573 | 121.7291
1862.25 | 121.8979 | -0.17853 | 121.8384 | 0.14932 | -0.008469 | -0.012 | -0.01586 | 0.045421 | 0.090161 | -0.062717 | 121.7626 | 121.7567 | 121.7185 | 121.5951 | -0.03875 | 0.02322 | -0.001436 | 0.015141 | 0.32785 | 0.17006 | 0.16653 | 0.16267 | 0.22395 | 0.26869 | 0.11581 | 121.8084 | 121.8025 | 121.7643 | 121.6409 | 0.007026 | 0.068996 | 0.04434 | 0.060917 | 121.8014 | 121.7641 | 121.7573 | 121.72
1863.9531 | 121.9254 | -0.1831 | 121.8475 | 0.14932 | -0.008469 | -0.016578 | -0.020438 | 0.045421 | 0.085583 | -0.062717 | 121.7718 | 121.7475 | 121.7185 | 121.5951 | -0.047906 | 0.014064 | -0.015171 | 0.010563 | 0.33243 | 0.17464 | 0.16653 | 0.16267 | 0.22853 | 0.26869 | 0.12039 | 121.8176 | 121.7933 | 121.7643 | 121.6409 | -0.00213 | 0.05984 | 0.030605 | 0.056339 | 121.8197 | 121.787 | 121.7664 | 121.7337
1865.7188 | 122.0123 | -0.11902 | 121.8063 | 0.14474 | -0.008469 | -0.012 | -0.025017 | 0.040843 | 0.085583 | -0.062717 | 121.7718 | 121.7613 | 121.7139 | 121.5997 | -0.047906 | 0.014064 | -0.019749 | 0.015141 | 0.26376 | 0.11055 | 0.10702 | 0.094002 | 0.15986 | 0.2046 | 0.056302 | 121.8176 | 121.8071 | 121.7597 | 121.6455 | -0.00213 | 0.05984 | 0.026027 | 0.060917 | 121.8197 | 121.7915 | 121.7619 | 121.7337
1867.4844 | 121.907 | -0.15564 | 121.8521 | 0.14932 | -0.008469 | -0.012 | -0.020438 | 0.045421 | 0.090161 | -0.067295 | 121.7718 | 121.7567 | 121.7185 | 121.6089 | -0.043328 | 0.009486 | -0.015171 | 0.010563 | 0.30496 | 0.14717 | 0.14364 | 0.1352 | 0.20106 | 0.2458 | 0.088345 | 121.8176 | 121.8025 | 121.7643 | 121.6547 | 0.002448 | 0.055262 | 0.030605 | 0.056339 | 121.8151 | 121.787 | 121.7619 | 121.7337
1869.25 | 121.9299 | -0.18768 | 121.875 | 0.14932 | -0.013048 | -0.016578 | -0.020438 | 0.045421 | 0.085583 | -0.067295 | 121.7764 | 121.7567 | 121.7323 | 121.6089 | -0.052484 | 0.009486 | -0.015171 | 0.015141 | 0.337 | 0.17463 | 0.1711 | 0.16724 | 0.2331 | 0.27327 | 0.12039 | 121.8221 | 121.8025 | 121.778 | 121.6547 | -0.006708 | 0.055262 | 0.030605 | 0.060917 | 121.8288 | 121.7915 | 121.7847 | 121.7474
1871 | 122.0535 | -0.12817 | 121.8109 | 0.14474 | -0.013048 | -0.012 | -0.020438 | 0.045421 | 0.085583 | -0.062717 | 121.7855 | 121.775 | 121.7277 | 121.6043 | -0.047906 | 0.018642 | -0.015171 | 0.010563 | 0.27292 | 0.11513 | 0.11617 | 0.10774 | 0.17359 | 0.21376 | 0.065457 | 121.8313 | 121.8208 | 121.7735 | 121.6501 | -0.00213 | 0.064418 | 0.030605 | 0.056339 | 121.8334 | 121.8007 | 121.7756 | 121.7429
1872.6875 | 121.9528 | -0.14648 | 121.8704 | 0.14932 | -0.008469 | -0.012 | -0.020438 | 0.045421 | 0.085583 | -0.067295 | 121.7855 | 121.7704 | 121.7368 | 121.6089 | -0.052484 | 0.00033 | -0.019749 | 0.001406 | 0.2958 | 0.13801 | 0.13448 | 0.12605 | 0.1919 | 0.23207 | 0.079189 | 121.8313 | 121.8162 | 121.7826 | 121.6547 | -0.006708 | 0.046106 | 0.026027 | 0.047182 | 121.838 | 121.8053 | 121.7893 | 121.7566
1874.4531 | 121.9299 | -0.16022 | 121.8063 | 0.14474 | -0.013048 | -0.012 | -0.025017 | 0.040843 | 0.09474 | -0.071874 | 121.7764 | 121.775 | 121.7323 | 121.6089 | -0.052484 | 0.00033 | -0.015171 | 0.005985 | 0.30496 | 0.14717 | 0.14822 | 0.1352 | 0.20106 | 0.25496 | 0.088343 | 121.8221 | 121.8208 | 121.778 | 121.6547 | -0.006708 | 0.046106 | 0.030605 | 0.051761 | 121.8288 | 121.7915 | 121.7847 | 121.7474
1876.2031 | 121.9574 | -0.15564 | 121.8658 | 0.1539 | -0.00389 | -0.016578 | -0.020438 | 0.045421 | 0.085583 | -0.058139 | 121.7855 | 121.7659 | 121.7414 | 121.6135 | -0.052484 | 0.004908 | -0.019749 | 0.005985 | 0.30954 | 0.15175 | 0.13906 | 0.1352 | 0.20106 | 0.24122 | 0.097501 | 121.8313 | 121.8116 | 121.7872 | 121.6592 | -0.006708 | 0.050684 | 0.026027 | 0.051761 | 121.838 | 121.8053 | 121.7939 | 121.7612
1877.9688 | 121.9666 | -0.16022 | 121.8475 | 0.14474 | -0.008469 | -0.012 | -0.01586 | 0.036265 | 0.090161 | -0.067295 | 121.7855 | 121.7704 | 121.7414 | 121.6226 | -0.047906 | -0.004248 | -0.024328 | -0.003172 | 0.30496 | 0.15175 | 0.14822 | 0.14436 | 0.19648 | 0.25038 | 0.092922 | 121.8313 | 121.8162 | 121.7872 | 121.6684 | -0.00213 | 0.041528 | 0.021448 | 0.042604 | 121.8334 | 121.8098 | 121.7893 | 121.7657
1879.6719 | 121.9986 | -0.14648 | 121.8292 | 0.14474 | -0.00389 | -0.021157 | -0.020438 | 0.036265 | 0.085583 | -0.067295 | 121.7855 | 121.7842 | 121.7414 | 121.6135 | -0.047906 | 0.00033 | -0.028906 | 0.001406 | 0.29123 | 0.14259 | 0.12533 | 0.12605 | 0.18275 | 0.23207 | 0.079189 | 121.8313 | 121.83 | 121.7872 | 121.6592 | -0.00213 | 0.046106 | 0.01687 | 0.047182 | 121.8334 | 121.8144 | 121.7893 | 121.7703
1881.4375 | 122.0535 | -0.11902 | 121.8201 | 0.14474 | -0.008469 | -0.012 | -0.025017 | 0.040843 | 0.085583 | -0.067295 | 121.7809 | 121.7796 | 121.7506 | 121.6272 | -0.052484 | -0.004248 | -0.024328 | -0.00775 | 0.26376 | 0.11055 | 0.10702 | 0.094002 | 0.15986 | 0.2046 | 0.051724 | 121.8267 | 121.8254 | 121.7963 | 121.673 | -0.006708 | 0.041528 | 0.021448 | 0.038026 | 121.8334 | 121.8053 | 121.8031 | 121.7749
1883.2031 | 122.0215 | -0.11444 | 121.8338 | 0.14932 | -0.00389 | -0.016578 | -0.025017 | 0.036265 | 0.090161 | -0.067295 | 121.7855 | 121.775 | 121.7368 | 121.618 | -0.043328 | -0.004248 | -0.024328 | -0.003172 | 0.26376 | 0.11055 | 0.097863 | 0.089424 | 0.15071 | 0.2046 | 0.047146 | 121.8313 | 121.8208 | 121.7826 | 121.6638 | 0.002448 | 0.041528 | 0.021448 | 0.042604 | 121.8288 | 121.8098 | 121.7802 | 121.7612
1884.9844 | 121.9528 | -0.15106 | 121.8658 | 0.14932 | -0.008469 | -0.016578 | -0.025017 | 0.040843 | 0.085583 | -0.062717 | 121.7901 | 121.7796 | 121.746 | 121.618 | -0.052484 | -0.008827 | -0.024328 | 0.001406 | 0.30038 | 0.14259 | 0.13448 | 0.12604 | 0.1919 | 0.23664 | 0.088345 | 121.8359 | 121.8254 | 121.7918 | 121.6638 | -0.006708 | 0.036949 | 0.021448 | 0.047182 | 121.8426 | 121.8144 | 121.7985 | 121.7703
1886.6875 | 121.9299 | -0.15564 | 121.8842 | 0.14017 | -0.013048 | -0.012 | -0.020438 | 0.045421 | 0.090161 | -0.058139 | 121.7947 | 121.7796 | 121.7368 | 121.6272 | -0.043328 | -0.013405 | -0.033484 | 0.005985 | 0.2958 | 0.14259 | 0.14364 | 0.1352 | 0.20106 | 0.2458 | 0.097501 | 121.8405 | 121.8254 | 121.7826 | 121.673 | 0.002448 | 0.032371 | 0.012292 | 0.051761 | 121.838 | 121.8282 | 121.7802 | 121.7703
1888.4375 | 121.9711 | -0.15564 | 121.8475 | 0.14932 | -0.008469 | -0.016578 | -0.020438 | 0.049999 | 0.090161 | -0.058139 | 121.7993 | 121.7933 | 121.746 | 121.6272 | -0.061641 | -0.008827 | -0.024328 | -0.003172 | 0.30496 | 0.14717 | 0.13906 | 0.1352 | 0.20564 | 0.2458 | 0.097501 | 121.845 | 121.8391 | 121.7918 | 121.673 | -0.015865 | 0.036949 | 0.021448 | 0.042604 | 121.8609 | 121.8236 | 121.8076 | 121.7703
1890.1406 | 122.0123 | -0.11444 | 121.843 | 0.14474 | -0.013048 | -0.012 | -0.025017 | 0.040843 | 0.090161 | -0.071874 | 121.7993 | 121.7842 | 121.746 | 121.6272 | -0.061641 | -0.004248 | -0.028906 | -0.00775 | 0.25918 | 0.10139 | 0.10244 | 0.089424 | 0.15528 | 0.2046 | 0.042567 | 121.845 | 121.83 | 121.7918 | 121.673 | -0.015865 | 0.041528 | 0.01687 | 0.038026 | 121.8609 | 121.8282 | 121.8076 | 121.7749
1891.9062 | 121.9208 | -0.17853 | 121.8704 | 0.14474 | -0.008469 | -0.007421 | -0.020438 | 0.040843 | 0.090161 | -0.058139 | 121.7809 | 121.7659 | 121.7368 | 121.6135 | -0.052484 | 0.004908 | -0.019749 | 0.001406 | 0.32327 | 0.17006 | 0.17111 | 0.15809 | 0.21937 | 0.26869 | 0.12039 | 121.8267 | 121.8116 | 121.7826 | 121.6592 | -0.006708 | 0.050684 | 0.026027 | 0.047182 | 121.8334 | 121.8007 | 121.7893 | 121.7566
1893.6094 | 122.0306 | -0.14191 | 121.7972 | 0.14932 | -0.008469 | -0.012 | -0.01586 | 0.040843 | 0.085583 | -0.067295 | 121.7626 | 121.7521 | 121.7139 | 121.5951 | -0.020437 | 0.027798 | -0.001436 | 0.028875 | 0.29123 | 0.13344 | 0.12991 | 0.12605 | 0.18275 | 0.22749 | 0.074612 | 121.8084 | 121.7979 | 121.7597 | 121.6409 | 0.025339 | 0.073574 | 0.04434 | 0.074651 | 121.7831 | 121.7641 | 121.7344 | 121.7154
1895.3906 | 122.0169 | -0.17853 | 121.788 | 0.15848 | -0.013048 | -0.012 | -0.01586 | 0.040843 | 0.085583 | -0.071874 | 121.7443 | 121.7292 | 121.6956 | 121.5722 | -0.025015 | 0.050688 | 0.003143 | 0.04261 | 0.33701 | 0.16548 | 0.16653 | 0.16267 | 0.21937 | 0.26411 | 0.10665 | 121.7901 | 121.775 | 121.7414 | 121.618 | 0.020761 | 0.096464 | 0.048919 | 0.088386 | 121.7693 | 121.7412 | 121.7206 | 121.6925
1897.1406 | 121.9711 | -0.19226 | 121.7834 | 0.14474 | -0.008469 | -0.012 | -0.020438 | 0.045421 | 0.09474 | -0.067295 | 121.7306 | 121.7247 | 121.6865 | 121.5631 | -0.025015 | 0.050688 | 0.003143 | 0.04261 | 0.337 | 0.18379 | 0.18026 | 0.17182 | 0.23768 | 0.287 | 0.12497 | 121.7764 | 121.7704 | 121.7323 | 121.6089 | 0.020761 | 0.096464 | 0.048919 | 0.088386 | 121.7556 | 121.7274 | 121.7115 | 121.6833
1898.9062 | 122.0581 | -0.16022 | 121.7743 | 0.14932 | -0.017627 | -0.016578 | -0.020438 | 0.036265 | 0.090161 | -0.067295 | 121.7352 | 121.7201 | 121.6911 | 121.5722 | -0.025015 | 0.050688 | 0.007721 | 0.04261 | 0.30954 | 0.14259 | 0.14364 | 0.13978 | 0.19648 | 0.25038 | 0.092922 | 121.7809 | 121.7659 | 121.7368 | 121.618 | 0.020761 | 0.096464 | 0.053497 | 0.088386 | 121.7602 | 121.7274 | 121.7161 | 121.6833
1900.6094 | 121.9803 | -0.20142 | 121.7926 | 0.14932 | -0.013048 | -0.002842 | -0.01586 | 0.049999 | 0.085583 | -0.071874 | 121.7352 | 121.7247 | 121.6911 | 121.5631 | -0.020437 | 0.055266 | 0.007721 | 0.038032 | 0.35074 | 0.18837 | 0.19857 | 0.18556 | 0.25141 | 0.287 | 0.12954 | 121.7809 | 121.7704 | 121.7368 | 121.6089 | 0.025339 | 0.10104 | 0.053497 | 0.083808 | 121.7556 | 121.7274 | 121.7115 | 121.6833
1902.3594 | 122.0398 | -0.19226 | 121.7789 | 0.14932 | -0.008469 | -0.012 | -0.011281 | 0.045421 | 0.085583 | -0.067295 | 121.7397 | 121.7201 | 121.6911 | 121.5677 | -0.020437 | 0.055266 | 0.016878 | 0.047188 | 0.34158 | 0.18379 | 0.18026 | 0.18098 | 0.23768 | 0.27784 | 0.12497 | 121.7855 | 121.7659 | 121.7368 | 121.6134 | 0.025339 | 0.10104 | 0.062654 | 0.092964 | 121.7602 | 121.7229 | 121.7115 | 121.6742
1904.0469 | 122.081 | -0.16937 | 121.7834 | 0.14932 | -0.013048 | -0.012 | -0.020438 | 0.045421 | 0.085583 | -0.062717 | 121.7306 | 121.7201 | 121.6911 | 121.5631 | -0.015859 | 0.055266 | 0.012299 | 0.04261 | 0.31869 | 0.15632 | 0.15737 | 0.14893 | 0.21479 | 0.25496 | 0.10666 | 121.7764 | 121.7659 | 121.7368 | 121.6089 | 0.029917 | 0.10104 | 0.058075 | 0.088386 | 121.7464 | 121.7183 | 121.7069 | 121.6788
1905.8125 | 122.0215 | -0.16022 | 121.7834 | 0.13559 | -0.013048 | -0.021157 | -0.025017 | 0.036265 | 0.090161 | -0.067295 | 121.7352 | 121.7292 | 121.6911 | 121.5722 | -0.011281 | 0.055266 | 0.012299 | 0.033454 | 0.2958 | 0.14717 | 0.13906 | 0.1352 | 0.19648 | 0.25038 | 0.092922 | 121.7809 | 121.775 | 121.7368 | 121.618 | 0.034495 | 0.10104 | 0.058075 | 0.07923 | 121.7464 | 121.7229 | 121.7023 | 121.6788
1907.5625 | 122.049 | -0.16937 | 121.7834 | 0.14017 | -0.013048 | -0.021157 | -0.020438 | 0.040843 | 0.090161 | -0.071874 | 121.7352 | 121.7338 | 121.6911 | 121.5722 | -0.020437 | 0.055266 | 0.007721 | 0.04261 | 0.30954 | 0.15632 | 0.14822 | 0.14893 | 0.21022 | 0.25953 | 0.097499 | 121.7809 | 121.7796 | 121.7368 | 121.618 | 0.025339 | 0.10104 | 0.053497 | 0.088386 | 121.7556 | 121.7274 | 121.7115 | 121.6833
1909.25 | 122.0718 | -0.16937 | 121.7789 | 0.14932 | -0.013048 | -0.016578 | -0.020438 | 0.040843 | 0.090161 | -0.067295 | 121.7443 | 121.7338 | 121.7002 | 121.5631 | -0.025015 | 0.04611 | 0.012299 | 0.04261 | 0.31869 | 0.15632 | 0.15279 | 0.14893 | 0.21022 | 0.25953 | 0.10208 | 121.7901 | 121.7796 | 121.746 | 121.6089 | 0.020761 | 0.091886 | 0.058075 | 0.088386 | 121.7693 | 121.732 | 121.7252 | 121.6879
1911.0156 | 121.994 | -0.18768 | 121.8018 | 0.14017 | -0.008469 | -0.012 | -0.020438 | 0.045421 | 0.085583 | -0.062717 | 121.7489 | 121.7338 | 121.6956 | 121.5768 | -0.025015 | 0.04611 | 0.003143 | 0.033454 | 0.32785 | 0.17921 | 0.17568 | 0.16724 | 0.2331 | 0.27327 | 0.12497 | 121.7947 | 121.7796 | 121.7414 | 121.6226 | 0.020761 | 0.091886 | 0.048919 | 0.07923 | 121.7739 | 121.7457 | 121.7206 | 121.6925
1912.7188 | 121.9574 | -0.19684 | 121.7972 | 0.15848 | -0.017627 | -0.007421 | -0.01586 | 0.049999 | 0.085583 | -0.062717 | 121.7489 | 121.7384 | 121.7002 | 121.5722 | -0.025015 | 0.04611 | 0.007721 | 0.033454 | 0.35532 | 0.17921 | 0.18942 | 0.18098 | 0.24684 | 0.28242 | 0.13412 | 121.7947 | 121.7842 | 121.746 | 121.618 | 0.020761 | 0.091886 | 0.053497 | 0.07923 | 121.7739 | 121.7412 | 121.7252 | 121.6925
1914.4844 | 122.0078 | -0.16937 | 121.8018 | 0.14474 | -0.017627 | -0.016578 | -0.020438 | 0.040843 | 0.085583 | -0.062717 | 121.7443 | 121.7384 | 121.7002 | 121.5814 | -0.020437 | 0.050688 | 0.003143 | 0.033454 | 0.31412 | 0.15175 | 0.15279 | 0.14893 | 0.21022 | 0.25496 | 0.10666 | 121.7901 | 121.7842 | 121.746 | 121.6272 | 0.025339 | 0.096464 | 0.048919 | 0.07923 | 121.7647 | 121.7412 | 121.7206 | 121.6971
1916.2656 | 121.9757 | -0.20599 | 121.7926 | 0.14932 | -0.00389 | -0.012 | -0.025017 | 0.040843 | 0.085583 | -0.062717 | 121.7489 | 121.7338 | 121.7048 | 121.5768 | -0.025015 | 0.050688 | 0.003143 | 0.04261 | 0.35532 | 0.2021 | 0.19399 | 0.18098 | 0.24684 | 0.29158 | 0.14328 | 121.7947 | 121.7796 | 121.7506 | 121.6226 | 0.020761 | 0.096464 | 0.048919 | 0.088386 | 121.7739 | 121.7457 | 121.7298 | 121.7016
1918.0312 | 121.9345 | -0.21973 | 121.8246 | 0.14932 | -0.00389 | -0.016578 | -0.020438 | 0.040843 | 0.085583 | -0.067295 | 121.7397 | 121.7338 | 121.7048 | 121.5722 | -0.020437 | 0.055266 | 0.007721 | 0.038032 | 0.36905 | 0.21584 | 0.20315 | 0.19929 | 0.26057 | 0.30531 | 0.15243 | 121.7855 | 121.7796 | 121.7506 | 121.618 | 0.025339 | 0.10104 | 0.053497 | 0.083808 | 121.7602 | 121.732 | 121.7252 | 121.6971
1919.7344 | 121.9757 | -0.20142 | 121.788 | 0.14932 | -0.008469 | -0.012 | -0.01586 | 0.045421 | 0.085583 | -0.071874 | 121.7443 | 121.7384 | 121.7002 | 121.5722 | -0.020437 | 0.04611 | 0.003143 | 0.033454 | 0.35074 | 0.19295 | 0.18942 | 0.18556 | 0.24684 | 0.287 | 0.12954 | 121.7901 | 121.7842 | 121.746 | 121.618 | 0.025339 | 0.091886 | 0.048919 | 0.07923 | 121.7647 | 121.7412 | 121.7206 | 121.6971
1921.5 | 121.9437 | -0.21057 | 121.7972 | 0.14932 | -0.013048 | -0.012 | -0.01586 | 0.045421 | 0.09474 | -0.062717 | 121.7535 | 121.7338 | 121.7094 | 121.5814 | -0.025015 | 0.050688 | 0.007721 | 0.038032 | 0.35989 | 0.19752 | 0.19857 | 0.19471 | 0.25599 | 0.30531 | 0.14785 | 121.7992 | 121.7796 | 121.7551 | 121.6272 | 0.020761 | 0.096464 | 0.053497 | 0.083808 | 121.7785 | 121.7457 | 121.7344 | 121.7016
1923.2656 | 122.0535 | -0.15564 | 121.756 | 0.14932 | -0.00389 | -0.016578 | -0.01586 | 0.045421 | 0.085583 | -0.071874 | 121.7535 | 121.743 | 121.7094 | 121.5814 | -0.034171 | 0.041532 | -0.001436 | 0.033454 | 0.30496 | 0.15175 | 0.13906 | 0.13978 | 0.20106 | 0.24122 | 0.083766 | 121.7992 | 121.7887 | 121.7551 | 121.6272 | 0.011605 | 0.087308 | 0.04434 | 0.07923 | 121.7876 | 121.7549 | 121.7435 | 121.7108
1924.9688 | 121.9711 | -0.20142 | 121.8201 | 0.14932 | -0.00389 | -0.007421 | -0.01586 | 0.045421 | 0.085583 | -0.067295 | 121.7626 | 121.7567 | 121.7185 | 121.5906 | -0.034171 | 0.027798 | -0.001436 | 0.024297 | 0.35074 | 0.19753 | 0.194 | 0.18556 | 0.24684 | 0.287 | 0.13412 | 121.8084 | 121.8025 | 121.7643 | 121.6363 | 0.011605 | 0.073574 | 0.04434 | 0.070073 | 121.7968 | 121.7641 | 121.7527 | 121.72
1926.7344 | 121.9757 | -0.17395 | 121.8292 | 0.1539 | -0.008469 | -0.007421 | -0.025017 | 0.040843 | 0.090161 | -0.058139 | 121.7672 | 121.7521 | 121.7185 | 121.5906 | -0.034171 | 0.036954 | -0.006014 | 0.024297 | 0.32785 | 0.16548 | 0.16653 | 0.14893 | 0.21479 | 0.26411 | 0.11581 | 121.813 | 121.7979 | 121.7643 | 121.6363 | 0.011605 | 0.08273 | 0.039762 | 0.070073 | 121.8014 | 121.7732 | 121.7527 | 121.7245
1928.4844 | 121.9391 | -0.20142 | 121.8384 | 0.14474 | -0.008469 | -0.012 | -0.020438 | 0.040843 | 0.085583 | -0.062717 | 121.7626 | 121.7475 | 121.7231 | 121.5951 | -0.034171 | 0.04611 | -0.010593 | 0.019719 | 0.34616 | 0.19295 | 0.18942 | 0.18098 | 0.24226 | 0.287 | 0.1387 | 121.8084 | 121.7933 | 121.7689 | 121.6409 | 0.011605 | 0.091886 | 0.035183 | 0.065495 | 121.7968 | 121.7732 | 121.7573 | 121.7337
1930.1875 | 121.9116 | -0.1831 | 121.8475 | 0.14474 | -0.00389 | -0.007421 | -0.011281 | 0.045421 | 0.090161 | -0.067295 | 121.7764 | 121.7613 | 121.7277 | 121.6089 | -0.034171 | 0.027798 | -0.006014 | 0.028875 | 0.32785 | 0.17921 | 0.17568 | 0.17182 | 0.22853 | 0.27327 | 0.11581 | 121.8221 | 121.8071 | 121.7735 | 121.6547 | 0.011605 | 0.073574 | 0.039762 | 0.074651 | 121.8105 | 121.7824 | 121.7619 | 121.7337
1931.9531 | 121.9711 | -0.1831 | 121.8338 | 0.14932 | -0.008469 | -0.007421 | -0.020438 | 0.045421 | 0.085583 | -0.062717 | 121.7764 | 121.7613 | 121.7277 | 121.6043 | -0.034171 | 0.02322 | -0.001436 | 0.019719 | 0.33243 | 0.17464 | 0.17568 | 0.16267 | 0.22853 | 0.26869 | 0.12039 | 121.8221 | 121.8071 | 121.7735 | 121.6501 | 0.011605 | 0.068996 | 0.04434 | 0.065495 | 121.8105 | 121.7778 | 121.7619 | 121.7291
1933.6719 | 121.9391 | -0.19226 | 121.8384 | 0.14474 | -0.00389 | -0.012 | -0.011281 | 0.045421 | 0.085583 | -0.067295 | 121.7718 | 121.7613 | 121.7368 | 121.6043 | -0.03875 | 0.027798 | -0.001436 | 0.019719 | 0.337 | 0.18837 | 0.18026 | 0.18098 | 0.23768 | 0.27784 | 0.12497 | 121.8176 | 121.8071 | 121.7826 | 121.6501 | 0.007026 | 0.073574 | 0.04434 | 0.065495 | 121.8105 | 121.7732 | 121.7756 | 121.7383
1935.4375 | 121.9391 | -0.17395 | 121.8292 | 0.14474 | -0.013048 | -0.021157 | -0.020438 | 0.045421 | 0.085583 | -0.058139 | 121.7809 | 121.7659 | 121.7323 | 121.6043 | -0.029593 | 0.02322 | -0.010593 | 0.019719 | 0.31869 | 0.1609 | 0.15279 | 0.15351 | 0.21937 | 0.25953 | 0.11581 | 121.8267 | 121.8116 | 121.778 | 121.6501 | 0.016183 | 0.068996 | 0.035183 | 0.065495 | 121.8105 | 121.7915 | 121.7619 | 121.7429
1937.2031 | 121.9894 | -0.16479 | 121.8292 | 0.14932 | 0.000689 | -0.016578 | -0.01586 | 0.045421 | 0.085583 | -0.062717 | 121.7809 | 121.7704 | 121.7323 | 121.6089 | -0.03875 | 0.02322 | -0.015171 | 0.019719 | 0.31412 | 0.16548 | 0.14822 | 0.14893 | 0.21022 | 0.25038 | 0.10208 | 121.8267 | 121.8162 | 121.778 | 121.6547 | 0.007026 | 0.068996 | 0.030605 | 0.065495 | 121.8197 | 121.7961 | 121.771 | 121.7474
1938.9062 | 122.049 | -0.13733 | 121.8201 | 0.14474 | -0.00389 | -0.021157 | -0.020438 | 0.040843 | 0.085583 | -0.071874 | 121.7809 | 121.7704 | 121.7368 | 121.6089 | -0.03875 | 0.014064 | -0.001436 | 0.010563 | 0.28207 | 0.13344 | 0.11617 | 0.11689 | 0.17817 | 0.22291 | 0.065455 | 121.8267 | 121.8162 | 121.7826 | 121.6547 | 0.007026 | 0.05984 | 0.04434 | 0.056339 | 121.8197 | 121.7824 | 121.7756 | 121.7383
1940.6719 | 121.9528 | -0.16937 | 121.8704 | 0.14474 | -0.013048 | -0.012 | -0.020438 | 0.045421 | 0.085583 | -0.062717 | 121.7809 | 121.7704 | 121.7323 | 121.6089 | -0.034171 | 0.014064 | -0.006014 | 0.015141 | 0.31412 | 0.15632 | 0.15737 | 0.14893 | 0.21479 | 0.25496 | 0.10666 | 121.8267 | 121.8162 | 121.778 | 121.6547 | 0.011605 | 0.05984 | 0.039762 | 0.060917 | 121.8151 | 121.787 | 121.7664 | 121.7383
1942.375 | 121.994 | -0.16022 | 121.8384 | 0.14017 | -0.013048 | -0.016578 | -0.01586 | 0.049999 | 0.090161 | -0.071874 | 121.7855 | 121.7704 | 121.7368 | 121.6089 | -0.034171 | 0.02322 | -0.015171 | 0.015141 | 0.30038 | 0.14717 | 0.14364 | 0.14436 | 0.21022 | 0.25038 | 0.088343 | 121.8313 | 121.8162 | 121.7826 | 121.6547 | 0.011605 | 0.068996 | 0.030605 | 0.060917 | 121.8197 | 121.8007 | 121.771 | 121.752
1944.125 | 121.9437 | -0.18768 | 121.8658 | 0.14932 | -0.017627 | -0.016578 | -0.020438 | 0.045421 | 0.090161 | -0.062717 | 121.7901 | 121.775 | 121.7323 | 121.6135 | -0.034171 | 0.018642 | -0.010593 | 0.019719 | 0.337 | 0.17006 | 0.1711 | 0.16724 | 0.2331 | 0.27784 | 0.12497 | 121.8359 | 121.8208 | 121.778 | 121.6592 | 0.011605 | 0.064418 | 0.035183 | 0.065495 | 121.8243 | 121.8007 | 121.7664 | 121.7429
1945.9062 | 122.0078 | -0.16479 | 121.8475 | 0.14017 | -0.017627 | -0.016578 | -0.025017 | 0.045421 | 0.081005 | -0.071874 | 121.7947 | 121.7704 | 121.7414 | 121.6135 | -0.03875 | 0.018642 | -0.006014 | 0.010563 | 0.30496 | 0.14717 | 0.14822 | 0.13978 | 0.21022 | 0.2458 | 0.092921 | 121.8405 | 121.8162 | 121.7872 | 121.6592 | 0.007026 | 0.064418 | 0.039762 | 0.056339 | 121.8334 | 121.8007 | 121.7802 | 121.7474
1947.5938 | 121.9528 | -0.16937 | 121.8704 | 0.14474 | -0.008469 | -0.012 | -0.020438 | 0.040843 | 0.090161 | -0.058139 | 121.7901 | 121.775 | 121.746 | 121.6135 | -0.043328 | 0.018642 | -0.006014 | 0.010563 | 0.31412 | 0.1609 | 0.15737 | 0.14893 | 0.21022 | 0.25953 | 0.11123 | 121.8359 | 121.8208 | 121.7918 | 121.6592 | 0.002448 | 0.064418 | 0.039762 | 0.056339 | 121.8334 | 121.7961 | 121.7893 | 121.752
1949.3438 | 122.0352 | -0.14648 | 121.7972 | 0.14932 | -0.013048 | -0.016578 | -0.020438 | 0.040843 | 0.081005 | -0.067295 | 121.7901 | 121.7842 | 121.746 | 121.618 | -0.034171 | 0.018642 | -0.015171 | 0.015141 | 0.2958 | 0.13344 | 0.12991 | 0.12605 | 0.18733 | 0.22749 | 0.079189 | 121.8359 | 121.83 | 121.7918 | 121.6638 | 0.011605 | 0.064418 | 0.030605 | 0.060917 | 121.8243 | 121.8053 | 121.7802 | 121.7612
1951.1094 | 122.0352 | -0.13733 | 121.8384 | 0.14474 | -0.013048 | -0.012 | -0.020438 | 0.040843 | 0.085583 | -0.062717 | 121.7947 | 121.7796 | 121.7506 | 121.618 | -0.043328 | 0.018642 | -0.015171 | 0.010563 | 0.28207 | 0.12428 | 0.12533 | 0.11689 | 0.17817 | 0.22291 | 0.074612 | 121.8405 | 121.8254 | 121.7963 | 121.6638 | 0.002448 | 0.064418 | 0.030605 | 0.056339 | 121.838 | 121.8098 | 121.7939 | 121.7657
1952.7969 | 121.962 | -0.14648 | 121.843 | 0.1539 | -0.013048 | -0.007421 | -0.025017 | 0.045421 | 0.090161 | -0.062717 | 121.7993 | 121.7842 | 121.7506 | 121.6226 | -0.047906 | 0.009486 | -0.015171 | 0.010563 | 0.30038 | 0.13344 | 0.13906 | 0.12147 | 0.1919 | 0.23664 | 0.083767 | 121.845 | 121.83 | 121.7963 | 121.6684 | -0.00213 | 0.055262 | 0.030605 | 0.056339 | 121.8472 | 121.8144 | 121.7985 | 121.7657
1954.5469 | 122.0032 | -0.11902 | 121.843 | 0.14474 | -0.013048 | -0.007421 | -0.025017 | 0.045421 | 0.090161 | -0.067295 | 121.8176 | 121.8071 | 121.7735 | 121.6455 | -0.057062 | -0.013405 | -0.024328 | -0.012328 | 0.26376 | 0.10597 | 0.1116 | 0.094002 | 0.16444 | 0.20918 | 0.051724 | 121.8633 | 121.8528 | 121.8192 | 121.6913 | -0.011286 | 0.032371 | 0.021448 | 0.033448 | 121.8746 | 121.8419 | 121.8305 | 121.7978
1956.3281 | 121.9391 | -0.15564 | 121.8567 | 0.14932 | -0.017627 | -0.016578 | -0.025017 | 0.036265 | 0.09474 | -0.067295 | 121.8221 | 121.8254 | 121.7872 | 121.6593 | -0.066219 | -0.022561 | -0.033484 | -0.012328 | 0.30496 | 0.13801 | 0.13906 | 0.13062 | 0.1919 | 0.25038 | 0.088345 | 121.8679 | 121.8712 | 121.833 | 121.705 | -0.020443 | 0.023215 | 0.012292 | 0.033448 | 121.8884 | 121.8556 | 121.8534 | 121.8207
1958.0781 | 121.9711 | -0.14191 | 121.8842 | 0.14932 | -0.008469 | -0.012 | -0.020438 | 0.049999 | 0.085583 | -0.062717 | 121.8267 | 121.8117 | 121.7872 | 121.6547 | -0.066219 | -0.022561 | -0.033484 | -0.016906 | 0.29123 | 0.13344 | 0.12991 | 0.12147 | 0.19191 | 0.22749 | 0.07919 | 121.8725 | 121.8574 | 121.833 | 121.7004 | -0.020443 | 0.023215 | 0.012292 | 0.02887 | 121.8929 | 121.8602 | 121.8534 | 121.8207
1959.7656 | 122.0673 | -0.07782 | 121.8475 | 0.14474 | -0.017627 | -0.016578 | -0.020438 | 0.045421 | 0.099318 | -0.071874 | 121.8359 | 121.8162 | 121.7872 | 121.6547 | -0.057062 | -0.022561 | -0.028906 | -0.012328 | 0.22256 | 0.060193 | 0.061242 | 0.057382 | 0.12324 | 0.17714 | 0.005946 | 121.8817 | 121.862 | 121.833 | 121.7004 | -0.011286 | 0.023215 | 0.01687 | 0.033448 | 121.8929 | 121.8648 | 121.8443 | 121.8161
1961.5156 | 122.0215 | -0.11902 | 121.8521 | 0.14932 | -0.008469 | -0.007421 | -0.020438 | 0.045421 | 0.081005 | -0.062717 | 121.8313 | 121.8208 | 121.7872 | 121.6593 | -0.066219 | -0.022561 | -0.033484 | -0.012328 | 0.26834 | 0.11055 | 0.1116 | 0.098581 | 0.16444 | 0.20002 | 0.056302 | 121.8771 | 121.8666 | 121.833 | 121.705 | -0.020443 | 0.023215 | 0.012292 | 0.033448 | 121.8975 | 121.8648 | 121.8534 | 121.8207
1963.2656 | 122.0764 | -0.07782 | 121.875 | 0.1539 | -0.017627 | -0.012 | -0.025017 | 0.045421 | 0.090161 | -0.062717 | 121.8359 | 121.8208 | 121.7826 | 121.6547 | -0.061641 | -0.017983 | -0.033484 | -0.016906 | 0.23172 | 0.060193 | 0.06582 | 0.052803 | 0.12324 | 0.16798 | 0.015103 | 121.8817 | 121.8666 | 121.8284 | 121.7004 | -0.015865 | 0.027793 | 0.012292 | 0.02887 | 121.8975 | 121.8694 | 121.8443 | 121.8161
1964.9688 | 121.962 | -0.14648 | 121.9162 | 0.14474 | -0.013048 | -0.012 | -0.01586 | 0.040843 | 0.081005 | -0.067295 | 121.8267 | 121.8208 | 121.7872 | 121.6547 | -0.066219 | -0.022561 | -0.033484 | -0.016906 | 0.29123 | 0.13344 | 0.13448 | 0.13062 | 0.18733 | 0.22749 | 0.079189 | 121.8725 | 121.8666 | 121.833 | 121.7004 | -0.020443 | 0.023215 | 0.012292 | 0.02887 | 121.8929 | 121.8602 | 121.8534 | 121.8207
1966.7344 | 122.0169 | -0.10986 | 121.8475 | 0.14932 | -0.013048 | -0.016578 | -0.020438 | 0.036265 | 0.090161 | -0.062717 | 121.8313 | 121.8162 | 121.778 | 121.6547 | -0.061641 | -0.022561 | -0.033484 | -0.012328 | 0.25918 | 0.096815 | 0.093285 | 0.089425 | 0.14613 | 0.20002 | 0.047146 | 121.8771 | 121.862 | 121.8238 | 121.7004 | -0.015865 | 0.023215 | 0.012292 | 0.033448 | 121.8929 | 121.8648 | 121.8397 | 121.8115
1968.4375 | 122.0673 | -0.082397 | 121.843 | 0.14932 | -0.013048 | -0.007421 | -0.01586 | 0.049999 | 0.090161 | -0.062717 | 121.8313 | 121.8254 | 121.7872 | 121.6593 | -0.066219 | -0.022561 | -0.024328 | -0.016906 | 0.23172 | 0.069349 | 0.074976 | 0.066537 | 0.1324 | 0.17256 | 0.01968 | 121.8771 | 121.8712 | 121.833 | 121.705 | -0.020443 | 0.023215 | 0.021448 | 0.02887 | 121.8975 | 121.8556 | 121.8534 | 121.8115
1970.1875 | 122.0581 | -0.10986 | 121.8613 | 0.14932 | -0.013048 | -0.012 | -0.01586 | 0.045421 | 0.090161 | -0.062717 | 121.8313 | 121.8208 | 121.7918 | 121.6593 | -0.066219 | -0.017983 | -0.038063 | -0.012328 | 0.25918 | 0.096815 | 0.097863 | 0.094003 | 0.15528 | 0.20002 | 0.047146 | 121.8771 | 121.8666 | 121.8376 | 121.705 | -0.020443 | 0.027793 | 0.007713 | 0.033448 | 121.8975 | 121.8694 | 121.858 | 121.8298
1971.9531 | 121.9482 | -0.13733 | 121.907 | 0.14932 | -0.008469 | -0.007421 | -0.025017 | 0.040843 | 0.09474 | -0.062717 | 121.8313 | 121.8254 | 121.7872 | 121.6638 | -0.066219 | -0.027139 | -0.033484 | -0.012328 | 0.28665 | 0.12886 | 0.12991 | 0.11231 | 0.17817 | 0.23207 | 0.074612 | 121.8771 | 121.8712 | 121.833 | 121.7096 | -0.020443 | 0.018637 | 0.012292 | 0.033448 | 121.8975 | 121.8648 | 121.8534 | 121.8207
1973.6562 | 122.0673 | -0.10529 | 121.875 | 0.14474 | -0.017627 | -0.012 | -0.01586 | 0.040843 | 0.085583 | -0.067295 | 121.8405 | 121.8254 | 121.7872 | 121.6593 | -0.075375 | -0.017983 | -0.038063 | -0.016906 | 0.25003 | 0.087659 | 0.093286 | 0.089426 | 0.14613 | 0.19087 | 0.037991 | 121.8862 | 121.8712 | 121.833 | 121.705 | -0.029599 | 0.027793 | 0.007713 | 0.02887 | 121.9158 | 121.8785 | 121.8626 | 121.8253
1975.4062 | 122.0673 | -0.086975 | 121.8521 | 0.14932 | -0.008469 | -0.012 | -0.020438 | 0.040843 | 0.090161 | -0.067295 | 121.8405 | 121.8254 | 121.7872 | 121.6593 | -0.070797 | -0.013405 | -0.033484 | -0.016906 | 0.2363 | 0.078506 | 0.074975 | 0.066537 | 0.12782 | 0.17714 | 0.01968 | 121.8862 | 121.8712 | 121.833 | 121.705 | -0.025021 | 0.032371 | 0.012292 | 0.02887 | 121.9113 | 121.8739 | 121.858 | 121.8207
1977.0938 | 121.9345 | -0.13733 | 121.8887 | 0.14474 | -0.00389 | -0.016578 | -0.020438 | 0.036265 | 0.085583 | -0.067295 | 121.8359 | 121.8254 | 121.7918 | 121.6638 | -0.066219 | -0.027139 | -0.038063 | -0.016906 | 0.28207 | 0.13344 | 0.12075 | 0.11689 | 0.17359 | 0.22291 | 0.070034 | 121.8817 | 121.8712 | 121.8376 | 121.7096 | -0.020443 | 0.018637 | 0.007713 | 0.02887 | 121.9021 | 121.8739 | 121.858 | 121.8298
1978.8438 | 122.0535 | -0.086975 | 121.8704 | 0.14932 | -0.017627 | -0.012 | -0.01586 | 0.040843 | 0.090161 | -0.067295 | 121.8359 | 121.8254 | 121.7826 | 121.673 | -0.070797 | -0.022561 | -0.038063 | -0.012328 | 0.2363 | 0.069348 | 0.074975 | 0.071115 | 0.12782 | 0.17714 | 0.01968 | 121.8817 | 121.8712 | 121.8284 | 121.7188 | -0.025021 | 0.023215 | 0.007713 | 0.033448 | 121.9067 | 121.8739 | 121.8534 | 121.8207
1980.5938 | 121.9528 | -0.13733 | 121.9208 | 0.14017 | -0.017627 | -0.016578 | -0.025017 | 0.036265 | 0.085583 | -0.067295 | 121.8405 | 121.8208 | 121.7918 | 121.6684 | -0.066219 | -0.013405 | -0.033484 | -0.016906 | 0.27749 | 0.1197 | 0.12075 | 0.11231 | 0.17359 | 0.22291 | 0.070034 | 121.8862 | 121.8666 | 121.8376 | 121.7142 | -0.020443 | 0.032371 | 0.012292 | 0.02887 | 121.9067 | 121.8739 | 121.858 | 121.8253
1982.3594 | 121.962 | -0.1236 | 121.907 | 0.14474 | -0.013048 | -0.012 | -0.020438 | 0.040843 | 0.085583 | -0.067295 | 121.8313 | 121.8254 | 121.7918 | 121.6684 | -0.066219 | -0.022561 | -0.038063 | -0.016906 | 0.26834 | 0.11055 | 0.1116 | 0.10316 | 0.16444 | 0.20918 | 0.056301 | 121.8771 | 121.8712 | 121.8376 | 121.7142 | -0.020443 | 0.023215 | 0.007713 | 0.02887 | 121.8975 | 121.8694 | 121.858 | 121.8298
1984.125 | 121.9574 | -0.11902 | 121.9116 | 0.14017 | -0.013048 | -0.012 | -0.01586 | 0.040843 | 0.076426 | -0.067295 | 121.8313 | 121.8345 | 121.7964 | 121.6638 | -0.061641 | -0.027139 | -0.028906 | -0.021484 | 0.25918 | 0.10597 | 0.10702 | 0.10316 | 0.15986 | 0.19544 | 0.051724 | 121.8771 | 121.8803 | 121.8421 | 121.7096 | -0.015865 | 0.018637 | 0.01687 | 0.024292 | 121.8929 | 121.8602 | 121.858 | 121.8253
1985.9062 | 121.962 | -0.1236 | 121.9437 | 0.14932 | -0.008469 | -0.012 | -0.020438 | 0.045421 | 0.090161 | -0.062717 | 121.8405 | 121.8254 | 121.7918 | 121.6638 | -0.066219 | -0.022561 | -0.028906 | -0.016906 | 0.27292 | 0.11513 | 0.1116 | 0.10316 | 0.16902 | 0.21376 | 0.060879 | 121.8862 | 121.8712 | 121.8376 | 121.7096 | -0.020443 | 0.023215 | 0.01687 | 0.02887 | 121.9067 | 121.8694 | 121.858 | 121.8207
1987.6094 | 121.9391 | -0.11902 | 121.8887 | 0.14474 | -0.013048 | -0.007421 | -0.020438 | 0.045421 | 0.090161 | -0.062717 | 121.845 | 121.83 | 121.7964 | 121.673 | -0.075375 | -0.027139 | -0.033484 | -0.012328 | 0.26376 | 0.10597 | 0.1116 | 0.098581 | 0.16444 | 0.20918 | 0.056302 | 121.8908 | 121.8757 | 121.8421 | 121.7188 | -0.029599 | 0.018637 | 0.012292 | 0.033448 | 121.9204 | 121.8785 | 121.8717 | 121.8298
1989.3594 | 122.0901 | -0.09613 | 121.8704 | 0.14932 | -0.00389 | -0.016578 | -0.034174 | 0.040843 | 0.085583 | -0.067295 | 121.8359 | 121.8254 | 121.7964 | 121.6638 | -0.070797 | -0.017983 | -0.033484 | -0.021484 | 0.24545 | 0.09224 | 0.079552 | 0.061956 | 0.13697 | 0.18171 | 0.028835 | 121.8817 | 121.8712 | 121.8421 | 121.7096 | -0.025021 | 0.027793 | 0.012292 | 0.024292 | 121.9067 | 121.8694 | 121.8672 | 121.8298
1991.0625 | 122.0673 | -0.07782 | 121.8475 | 0.1539 | -0.013048 | -0.016578 | -0.020438 | 0.040843 | 0.090161 | -0.071874 | 121.8359 | 121.8254 | 121.7918 | 121.6684 | -0.066219 | -0.031717 | -0.028906 | -0.016906 | 0.23172 | 0.064772 | 0.061242 | 0.057382 | 0.11866 | 0.16798 | 0.005946 | 121.8817 | 121.8712 | 121.8376 | 121.7142 | -0.020443 | 0.014059 | 0.01687 | 0.02887 | 121.9021 | 121.8648 | 121.858 | 121.8207
1992.8281 | 121.9757 | -0.13275 | 121.8933 | 0.14932 | -0.013048 | -0.007421 | -0.020438 | 0.045421 | 0.090161 | -0.067295 | 121.8405 | 121.8254 | 121.7964 | 121.673 | -0.066219 | -0.031717 | -0.033484 | -0.016906 | 0.28207 | 0.1197 | 0.12533 | 0.11231 | 0.17817 | 0.22291 | 0.065456 | 121.8862 | 121.8712 | 121.8421 | 121.7188 | -0.020443 | 0.014059 | 0.012292 | 0.02887 | 121.9067 | 121.8739 | 121.8626 | 121.8298
1994.5938 | 121.9574 | -0.13275 | 121.9254 | 0.14932 | -0.013048 | -0.021157 | -0.01586 | 0.040843 | 0.090161 | -0.067295 | 121.8405 | 121.8254 | 121.7872 | 121.673 | -0.066219 | -0.022561 | -0.038063 | -0.016906 | 0.28207 | 0.1197 | 0.11159 | 0.11689 | 0.17359 | 0.22291 | 0.065456 | 121.8862 | 121.8712 | 121.833 | 121.7188 | -0.020443 | 0.023215 | 0.007713 | 0.02887 | 121.9067 | 121.8785 | 121.8534 | 121.8253
1996.3125 | 122.0032 | -0.11902 | 121.8933 | 0.14474 | -0.008469 | -0.012 | -0.029595 | 0.045421 | 0.090161 | -0.067295 | 121.8405 | 121.83 | 121.7964 | 121.6776 | -0.070797 | -0.027139 | -0.038063 | -0.021484 | 0.26376 | 0.11055 | 0.10702 | 0.089424 | 0.16444 | 0.20918 | 0.051724 | 121.8862 | 121.8757 | 121.8421 | 121.7233 | -0.025021 | 0.018637 | 0.007713 | 0.024292 | 121.9113 | 121.8785 | 121.8672 | 121.8344
1998.0625 | 122.0581 | -0.091553 | 121.9025 | 0.14932 | -0.013048 | -0.021157 | -0.020438 | 0.036265 | 0.085583 | -0.067295 | 121.845 | 121.8254 | 121.7964 | 121.673 | -0.061641 | -0.027139 | -0.038063 | -0.021484 | 0.24087 | 0.078505 | 0.070396 | 0.071115 | 0.12782 | 0.17714 | 0.024258 | 121.8908 | 121.8712 | 121.8421 | 121.7188 | -0.015865 | 0.018637 | 0.007713 | 0.024292 | 121.9067 | 121.8831 | 121.858 | 121.8344
1999.8125 | 122.0535 | -0.10071 | 121.8796 | 0.14932 | -0.013048 | -0.016578 | -0.025017 | 0.040843 | 0.085583 | -0.067295 | 121.845 | 121.8254 | 121.7918 | 121.673 | -0.057062 | -0.022561 | -0.033484 | -0.021484 | 0.25003 | 0.08766 | 0.08413 | 0.075691 | 0.14155 | 0.18629 | 0.033413 | 121.8908 | 121.8712 | 121.8376 | 121.7188 | -0.011286 | 0.023215 | 0.012292 | 0.024292 | 121.9021 | 121.8785 | 121.8488 | 121.8253
2001.5625 | 122.0215 | -0.1236 | 121.8887 | 0.14474 | -0.013048 | -0.021157 | -0.020438 | 0.045421 | 0.076426 | -0.067295 | 121.8496 | 121.8254 | 121.7964 | 121.6638 | -0.066219 | -0.031717 | -0.038063 | -0.016906 | 0.26834 | 0.11055 | 0.10244 | 0.10316 | 0.16902 | 0.20002 | 0.056301 | 121.8954 | 121.8712 | 121.8421 | 121.7096 | -0.020443 | 0.014059 | 0.007713 | 0.02887 | 121.9158 | 121.8877 | 121.8626 | 121.8344
2003.3281 | 121.9482 | -0.13275 | 121.9025 | 0.14932 | -0.013048 | -0.016578 | -0.01586 | 0.045421 | 0.081005 | -0.071874 | 121.8542 | 121.83 | 121.7964 | 121.673 | -0.066219 | -0.022561 | -0.033484 | -0.016906 | 0.28207 | 0.1197 | 0.11617 | 0.11689 | 0.17817 | 0.21376 | 0.060877 | 121.9 | 121.8757 | 121.8421 | 121.7188 | -0.020443 | 0.023215 | 0.012292 | 0.02887 | 121.9204 | 121.8877 | 121.8626 | 121.8298
2005.0938 | 121.9803 | -0.13275 | 121.8887 | 0.14932 | -0.017627 | -0.012 | -0.020438 | 0.040843 | 0.090161 | -0.062717 | 121.8496 | 121.8254 | 121.8009 | 121.6776 | -0.070797 | -0.027139 | -0.038063 | -0.016906 | 0.28207 | 0.11512 | 0.12075 | 0.11231 | 0.17359 | 0.22291 | 0.070034 | 121.8954 | 121.8712 | 121.8467 | 121.7233 | -0.025021 | 0.018637 | 0.007713 | 0.02887 | 121.9204 | 121.8877 | 121.8717 | 121.839
2006.7969 | 121.9803 | -0.11444 | 121.9162 | 0.14932 | -0.013048 | -0.016578 | -0.020438 | 0.045421 | 0.085583 | -0.062717 | 121.845 | 121.83 | 121.7964 | 121.6776 | -0.070797 | -0.022561 | -0.033484 | -0.026063 | 0.26376 | 0.10139 | 0.097863 | 0.094003 | 0.15986 | 0.20002 | 0.051724 | 121.8908 | 121.8757 | 121.8421 | 121.7233 | -0.025021 | 0.023215 | 0.012292 | 0.019713 | 121.9158 | 121.8785 | 121.8672 | 121.8298
2008.5469 | 122.0535 | -0.09613 | 121.8704 | 0.14474 | -0.008469 | -0.012 | -0.025017 | 0.040843 | 0.090161 | -0.067295 | 121.8496 | 121.83 | 121.8009 | 121.673 | -0.066219 | -0.031717 | -0.042641 | -0.021484 | 0.24087 | 0.087661 | 0.08413 | 0.071113 | 0.13697 | 0.18629 | 0.028835 | 121.8954 | 121.8757 | 121.8467 | 121.7188 | -0.020443 | 0.014059 | 0.003135 | 0.024292 | 121.9158 | 121.8923 | 121.8672 | 121.8436
2010.3125 | 121.9803 | -0.1236 | 121.9025 | 0.14474 | -0.008469 | -0.007421 | -0.025017 | 0.045421 | 0.085583 | -0.062717 | 121.845 | 121.8345 | 121.8009 | 121.6821 | -0.066219 | -0.022561 | -0.038063 | -0.021484 | 0.26834 | 0.11513 | 0.11618 | 0.098579 | 0.16902 | 0.20918 | 0.060879 | 121.8908 | 121.8803 | 121.8467 | 121.7279 | -0.020443 | 0.023215 | 0.007713 | 0.024292 | 121.9113 | 121.8831 | 121.8672 | 121.839
2012.0156 | 122.0306 | -0.10529 | 121.8658 | 0.14932 | -0.022205 | -0.007421 | -0.020438 | 0.040843 | 0.090161 | -0.058139 | 121.845 | 121.8345 | 121.7964 | 121.673 | -0.066219 | -0.022561 | -0.038063 | -0.016906 | 0.25461 | 0.083081 | 0.097865 | 0.084848 | 0.14613 | 0.19545 | 0.047147 | 121.8908 | 121.8803 | 121.8421 | 121.7188 | -0.020443 | 0.023215 | 0.007713 | 0.02887 | 121.9113 | 121.8831 | 121.8626 | 121.8344
2013.7656 | 121.9574 | -0.13733 | 121.907 | 0.14932 | -0.008469 | -0.021157 | -0.025017 | 0.040843 | 0.085583 | -0.062717 | 121.845 | 121.8345 | 121.7918 | 121.673 | -0.066219 | -0.031717 | -0.033484 | -0.016906 | 0.28665 | 0.12886 | 0.11617 | 0.11231 | 0.17817 | 0.22291 | 0.074612 | 121.8908 | 121.8803 | 121.8376 | 121.7188 | -0.020443 | 0.014059 | 0.012292 | 0.02887 | 121.9113 | 121.8785 | 121.858 | 121.8253
2015.4688 | 121.9437 | -0.15106 | 121.8842 | 0.14474 | -0.008469 | -0.016578 | -0.011281 | 0.040843 | 0.085583 | -0.067295 | 121.845 | 121.8345 | 121.7964 | 121.6776 | -0.070797 | -0.027139 | -0.033484 | -0.021484 | 0.2958 | 0.14259 | 0.13448 | 0.13978 | 0.1919 | 0.23664 | 0.083767 | 121.8908 | 121.8803 | 121.8421 | 121.7233 | -0.025021 | 0.018637 | 0.012292 | 0.024292 | 121.9158 | 121.8785 | 121.8672 | 121.8298
2017.2344 | 121.962 | -0.14648 | 121.8933 | 0.14474 | -0.013048 | -0.007421 | -0.011281 | 0.045421 | 0.090161 | -0.067295 | 121.8496 | 121.8391 | 121.8009 | 121.673 | -0.070797 | -0.027139 | -0.042641 | -0.021484 | 0.29123 | 0.13344 | 0.13906 | 0.1352 | 0.1919 | 0.23664 | 0.079189 | 121.8954 | 121.8849 | 121.8467 | 121.7188 | -0.025021 | 0.018637 | 0.003135 | 0.024292 | 121.9204 | 121.8923 | 121.8717 | 121.8436
2019 | 121.994 | -0.12817 | 121.9116 | 0.14932 | -0.008469 | -0.021157 | -0.020438 | 0.045421 | 0.085583 | -0.062717 | 121.8496 | 121.8345 | 121.8009 | 121.673 | -0.066219 | -0.027139 | -0.033484 | -0.016906 | 0.2775 | 0.11971 | 0.10702 | 0.10774 | 0.17359 | 0.21376 | 0.065457 | 121.8954 | 121.8803 | 121.8467 | 121.7188 | -0.020443 | 0.018637 | 0.012292 | 0.02887 | 121.9158 | 121.8831 | 121.8672 | 121.8344
2020.7031 | 121.9711 | -0.14191 | 121.9345 | 0.14932 | -0.008469 | -0.016578 | -0.025017 | 0.040843 | 0.085583 | -0.062717 | 121.845 | 121.8391 | 121.7964 | 121.6776 | -0.066219 | -0.027139 | -0.033484 | -0.021484 | 0.29123 | 0.13344 | 0.12533 | 0.11689 | 0.18275 | 0.22749 | 0.07919 | 121.8908 | 121.8849 | 121.8421 | 121.7233 | -0.020443 | 0.018637 | 0.012292 | 0.024292 | 121.9113 | 121.8785 | 121.8626 | 121.8298
2022.4531 | 121.9757 | -0.13275 | 121.8979 | 0.14932 | -0.013048 | -0.016578 | -0.029595 | 0.040843 | 0.090161 | -0.067295 | 121.8542 | 121.8345 | 121.8009 | 121.6776 | -0.070797 | -0.022561 | -0.033484 | -0.021484 | 0.28207 | 0.1197 | 0.11617 | 0.10316 | 0.17359 | 0.22291 | 0.065456 | 121.9 | 121.8803 | 121.8467 | 121.7233 | -0.025021 | 0.023215 | 0.012292 | 0.024292 | 121.925 | 121.8877 | 121.8717 | 121.8344
2024.2031 | 121.962 | -0.12817 | 121.8933 | 0.14474 | -0.017627 | -0.012 | -0.020438 | 0.045421 | 0.081005 | -0.067295 | 121.8542 | 121.8345 | 121.7964 | 121.673 | -0.070797 | -0.027139 | -0.038063 | -0.021484 | 0.27292 | 0.11055 | 0.11617 | 0.10774 | 0.17359 | 0.20918 | 0.060879 | 121.9 | 121.8803 | 121.8421 | 121.7188 | -0.025021 | 0.018637 | 0.007713 | 0.024292 | 121.925 | 121.8923 | 121.8672 | 121.8344
2025.9219 | 121.9391 | -0.13733 | 121.9345 | 0.14932 | 0.000689 | -0.016578 | -0.020438 | 0.049999 | 0.090161 | -0.062717 | 121.8542 | 121.83 | 121.7918 | 121.673 | -0.061641 | -0.027139 | -0.028906 | -0.012328 | 0.28665 | 0.13802 | 0.12075 | 0.11689 | 0.18733 | 0.22749 | 0.074612 | 121.9 | 121.8757 | 121.8376 | 121.7188 | -0.015865 | 0.018637 | 0.01687 | 0.033448 | 121.9158 | 121.8831 | 121.8534 | 121.8207
2027.6875 | 122.0856 | -0.086975 | 121.8567 | 0.1539 | -0.013048 | -0.012 | -0.020438 | 0.031687 | 0.090161 | -0.062717 | 121.8542 | 121.83 | 121.7918 | 121.6776 | -0.057062 | -0.017983 | -0.038063 | -0.016906 | 0.24088 | 0.073927 | 0.074975 | 0.066537 | 0.11866 | 0.17714 | 0.024258 | 121.9 | 121.8757 | 121.8376 | 121.7233 | -0.011286 | 0.027793 | 0.007713 | 0.02887 | 121.9113 | 121.8923 | 121.8488 | 121.8298
2029.4375 | 122.0673 | -0.11444 | 121.8658 | 0.14474 | -0.013048 | -0.012 | -0.020438 | 0.049999 | 0.081005 | -0.067295 | 121.8405 | 121.8254 | 121.7872 | 121.6638 | -0.066219 | -0.013405 | -0.028906 | -0.00775 | 0.25918 | 0.10139 | 0.10244 | 0.094003 | 0.16444 | 0.19545 | 0.047146 | 121.8862 | 121.8712 | 121.833 | 121.7096 | -0.020443 | 0.032371 | 0.01687 | 0.038026 | 121.9067 | 121.8694 | 121.8534 | 121.8161
2031.125 | 121.9757 | -0.14191 | 121.8704 | 0.14932 | -0.017627 | -0.007421 | -0.025017 | 0.054577 | 0.090161 | -0.062717 | 121.8405 | 121.8254 | 121.778 | 121.6638 | -0.061641 | -0.013405 | -0.028906 | -0.00775 | 0.29123 | 0.12428 | 0.13449 | 0.11689 | 0.19648 | 0.23207 | 0.07919 | 121.8862 | 121.8712 | 121.8238 | 121.7096 | -0.015865 | 0.032371 | 0.01687 | 0.038026 | 121.9021 | 121.8694 | 121.8397 | 121.8069
2032.8906 | 122.0581 | -0.10986 | 121.8979 | 0.14932 | -0.017627 | -0.016578 | -0.025017 | 0.036265 | 0.090161 | -0.062717 | 121.8313 | 121.8162 | 121.7872 | 121.6593 | -0.052484 | -0.008827 | -0.019749 | -0.00775 | 0.25918 | 0.092236 | 0.093285 | 0.084846 | 0.14613 | 0.20002 | 0.047146 | 121.8771 | 121.862 | 121.833 | 121.705 | -0.006708 | 0.036949 | 0.026027 | 0.038026 | 121.8838 | 121.8511 | 121.8397 | 121.8069
2034.6406 | 122.1085 | -0.086975 | 121.8613 | 0.1539 | -0.013048 | -0.016578 | -0.025017 | 0.040843 | 0.081005 | -0.062717 | 121.8313 | 121.83 | 121.7872 | 121.6638 | -0.057062 | -0.004248 | -0.033484 | -0.00775 | 0.24088 | 0.073927 | 0.070397 | 0.061958 | 0.12782 | 0.16798 | 0.024258 | 121.8771 | 121.8757 | 121.833 | 121.7096 | -0.011286 | 0.041528 | 0.012292 | 0.038026 | 121.8884 | 121.8648 | 121.8443 | 121.8207
2036.4062 | 121.9666 | -0.14648 | 121.9025 | 0.14932 | -0.017627 | -0.012 | -0.01586 | 0.045421 | 0.090161 | -0.067295 | 121.8405 | 121.8208 | 121.7872 | 121.6684 | -0.052484 | -0.013405 | -0.038063 | -0.003172 | 0.2958 | 0.12886 | 0.13448 | 0.13062 | 0.1919 | 0.23664 | 0.079189 | 121.8862 | 121.8666 | 121.833 | 121.7142 | -0.006708 | 0.032371 | 0.007713 | 0.042604 | 121.8929 | 121.8785 | 121.8397 | 121.8253
2038.1094 | 121.9574 | -0.15564 | 121.9116 | 0.14474 | -0.017627 | -0.002842 | -0.020438 | 0.045421 | 0.090161 | -0.058139 | 121.8542 | 121.8254 | 121.7964 | 121.6684 | -0.052484 | -0.017983 | -0.033484 | -0.00775 | 0.30038 | 0.13801 | 0.1528 | 0.1352 | 0.20106 | 0.2458 | 0.097501 | 121.9 | 121.8712 | 121.8421 | 121.7142 | -0.006708 | 0.027793 | 0.012292 | 0.038026 | 121.9067 | 121.8877 | 121.8488 | 121.8298
2039.8594 | 121.9986 | -0.13275 | 121.8933 | 0.14474 | -0.013048 | -0.016578 | -0.020438 | 0.045421 | 0.090161 | -0.067295 | 121.8359 | 121.83 | 121.7872 | 121.6638 | -0.052484 | -0.013405 | -0.028906 | -0.003172 | 0.27749 | 0.1197 | 0.11617 | 0.11231 | 0.17817 | 0.22291 | 0.065456 | 121.8817 | 121.8757 | 121.833 | 121.7096 | -0.006708 | 0.032371 | 0.01687 | 0.042604 | 121.8884 | 121.8648 | 121.8397 | 121.8161
2041.5625 | 122.0947 | -0.10529 | 121.8796 | 0.1539 | -0.008469 | -0.012 | -0.020438 | 0.045421 | 0.081005 | -0.067295 | 121.8405 | 121.83 | 121.7872 | 121.6638 | -0.052484 | -0.013405 | -0.028906 | -0.003172 | 0.25919 | 0.096817 | 0.093286 | 0.084848 | 0.15071 | 0.18629 | 0.037991 | 121.8862 | 121.8757 | 121.833 | 121.7096 | -0.006708 | 0.032371 | 0.01687 | 0.042604 | 121.8929 | 121.8694 | 121.8397 | 121.8161
2043.3281 | 122.1085 | -0.091553 | 121.8292 | 0.14474 | -0.008469 | -0.012 | -0.025017 | 0.040843 | 0.085583 | -0.067295 | 121.845 | 121.8208 | 121.7826 | 121.6638 | -0.057062 | -0.013405 | -0.028906 | -0.00775 | 0.2363 | 0.083084 | 0.079553 | 0.066536 | 0.1324 | 0.17714 | 0.024258 | 121.8908 | 121.8666 | 121.8284 | 121.7096 | -0.011286 | 0.032371 | 0.01687 | 0.038026 | 121.9021 | 121.8739 | 121.8397 | 121.8115
2045.0938 | 122.0764 | -0.10071 | 121.8796 | 0.14474 | -0.017627 | -0.012 | -0.01586 | 0.040843 | 0.085583 | -0.076452 | 121.8313 | 121.8254 | 121.778 | 121.6638 | -0.052484 | -0.004248 | -0.028906 | 0.001406 | 0.24545 | 0.083081 | 0.088708 | 0.084848 | 0.14155 | 0.18629 | 0.024256 | 121.8771 | 121.8712 | 121.8238 | 121.7096 | -0.006708 | 0.041528 | 0.01687 | 0.047182 | 121.8838 | 121.8602 | 121.8305 | 121.8069
2046.7969 | 121.9437 | -0.1236 | 121.8979 | 0.1539 | -0.013048 | -0.012 | -0.01586 | 0.049999 | 0.090161 | -0.062717 | 121.845 | 121.8254 | 121.778 | 121.673 | -0.070797 | -0.013405 | -0.033484 | -0.012328 | 0.2775 | 0.11055 | 0.1116 | 0.10774 | 0.17359 | 0.21376 | 0.060879 | 121.8908 | 121.8712 | 121.8238 | 121.7188 | -0.025021 | 0.032371 | 0.012292 | 0.033448 | 121.9158 | 121.8785 | 121.8488 | 121.8115
2048.5469 | 121.9391 | -0.16022 | 121.8796 | 0.14474 | -0.013048 | -0.012 | -0.01586 | 0.036265 | 0.085583 | -0.058139 | 121.8405 | 121.83 | 121.7826 | 121.6638 | -0.057062 | -0.008827 | -0.028906 | -0.00775 | 0.30496 | 0.14717 | 0.14822 | 0.14436 | 0.19648 | 0.2458 | 0.10208 | 121.8862 | 121.8757 | 121.8284 | 121.7096 | -0.011286 | 0.036949 | 0.01687 | 0.038026 | 121.8975 | 121.8694 | 121.8397 | 121.8115
2050.2969 | 121.9666 | -0.13275 | 121.875 | 0.14474 | -0.008469 | -0.007421 | -0.01586 | 0.045421 | 0.090161 | -0.058139 | 121.8405 | 121.8345 | 121.7872 | 121.673 | -0.066219 | -0.017983 | -0.028906 | -0.00775 | 0.27749 | 0.12428 | 0.12533 | 0.11689 | 0.17817 | 0.22291 | 0.074612 | 121.8862 | 121.8803 | 121.833 | 121.7188 | -0.020443 | 0.027793 | 0.01687 | 0.038026 | 121.9067 | 121.8694 | 121.8534 | 121.8161
2052 | 122.0856 | -0.10529 | 121.8521 | 0.14932 | -0.008469 | -0.016578 | -0.020438 | 0.049999 | 0.081005 | -0.067295 | 121.8496 | 121.8391 | 121.7872 | 121.673 | -0.061641 | -0.017983 | -0.033484 | -0.00775 | 0.25461 | 0.096817 | 0.088708 | 0.084848 | 0.15529 | 0.18629 | 0.037991 | 121.8954 | 121.8849 | 121.833 | 121.7188 | -0.015865 | 0.027793 | 0.012292 | 0.038026 | 121.9113 | 121.8831 | 121.8488 | 121.8207
2053.75 | 122.0764 | -0.13733 | 121.8796 | 0.14932 | -0.022205 | -0.016578 | -0.025017 | 0.040843 | 0.081005 | -0.062717 | 121.8405 | 121.8391 | 121.7964 | 121.6684 | -0.057062 | -0.017983 | -0.033484 | -0.012328 | 0.28665 | 0.11512 | 0.12075 | 0.11231 | 0.17817 | 0.21833 | 0.074612 | 121.8862 | 121.8849 | 121.8421 | 121.7142 | -0.011286 | 0.027793 | 0.012292 | 0.033448 | 121.8975 | 121.8739 | 121.8534 | 121.8298
2055.5 | 122.0856 | -0.10529 | 121.8842 | 0.14932 | -0.008469 | -0.012 | -0.020438 | 0.036265 | 0.090161 | -0.062717 | 121.8405 | 121.8345 | 121.7918 | 121.6776 | -0.052484 | -0.022561 | -0.033484 | -0.00775 | 0.25461 | 0.096817 | 0.093286 | 0.084848 | 0.14155 | 0.19545 | 0.042569 | 121.8862 | 121.8803 | 121.8376 | 121.7233 | -0.006708 | 0.023215 | 0.012292 | 0.038026 | 121.8929 | 121.8739 | 121.8443 | 121.8253
2057.2812 | 122.0627 | -0.11444 | 121.8704 | 0.14474 | -0.008469 | -0.012 | -0.025017 | 0.040843 | 0.085583 | -0.076452 | 121.845 | 121.8345 | 121.7872 | 121.673 | -0.061641 | -0.022561 | -0.038063 | -0.00775 | 0.25918 | 0.10597 | 0.10244 | 0.089424 | 0.15528 | 0.20002 | 0.037989 | 121.8908 | 121.8803 | 121.833 | 121.7188 | -0.015865 | 0.023215 | 0.007713 | 0.038026 | 121.9067 | 121.8831 | 121.8488 | 121.8253
2059.0469 | 122.0352 | -0.11444 | 121.8613 | 0.14932 | -0.008469 | -0.016578 | -0.01586 | 0.036265 | 0.085583 | -0.058139 | 121.8496 | 121.8391 | 121.7918 | 121.673 | -0.066219 | -0.013405 | -0.028906 | -0.00775 | 0.26376 | 0.10597 | 0.097863 | 0.098581 | 0.15071 | 0.20002 | 0.056302 | 121.8954 | 121.8849 | 121.8376 | 121.7188 | -0.020443 | 0.032371 | 0.01687 | 0.038026 | 121.9158 | 121.8785 | 121.858 | 121.8207
2060.8125 | 122.0535 | -0.09613 | 121.8796 | 0.14932 | -0.017627 | -0.012 | -0.020438 | 0.040843 | 0.081005 | -0.071874 | 121.8496 | 121.8345 | 121.7872 | 121.673 | -0.057062 | -0.017983 | -0.038063 | -0.016906 | 0.24545 | 0.078503 | 0.08413 | 0.075692 | 0.13697 | 0.17713 | 0.024256 | 121.8954 | 121.8803 | 121.833 | 121.7188 | -0.011286 | 0.027793 | 0.007713 | 0.02887 | 121.9067 | 121.8877 | 121.8443 | 121.8253
2062.5156 | 122.0352 | -0.1236 | 121.8658 | 0.14932 | -0.008469 | -0.016578 | -0.020438 | 0.049999 | 0.090161 | -0.062717 | 121.8496 | 121.8345 | 121.7872 | 121.6684 | -0.061641 | -0.017983 | -0.033484 | -0.00775 | 0.27292 | 0.11513 | 0.10702 | 0.10316 | 0.17359 | 0.21376 | 0.060879 | 121.8954 | 121.8803 | 121.833 | 121.7142 | -0.015865 | 0.027793 | 0.012292 | 0.038026 | 121.9113 | 121.8831 | 121.8488 | 121.8207
2064.2812 | 122.0901 | -0.10986 | 121.8567 | 0.14474 | -0.017627 | -0.012 | -0.025017 | 0.040843 | 0.090161 | -0.067295 | 121.8496 | 121.8391 | 121.7872 | 121.673 | -0.061641 | -0.008827 | -0.033484 | -0.00775 | 0.25461 | 0.092236 | 0.097863 | 0.084846 | 0.15071 | 0.20002 | 0.042568 | 121.8954 | 121.8849 | 121.833 | 121.7188 | -0.015865 | 0.036949 | 0.012292 | 0.038026 | 121.9113 | 121.8831 | 121.8488 | 121.8207
2066.0469 | 122.0078 | -0.1236 | 121.8796 | 0.14017 | -0.008469 | -0.012 | -0.01586 | 0.045421 | 0.090161 | -0.062717 | 121.8588 | 121.8437 | 121.7918 | 121.6776 | -0.057062 | -0.013405 | -0.028906 | -0.012328 | 0.26376 | 0.11513 | 0.1116 | 0.10774 | 0.16902 | 0.21376 | 0.060879 | 121.9046 | 121.8895 | 121.8376 | 121.7233 | -0.011286 | 0.032371 | 0.01687 | 0.033448 | 121.9158 | 121.8877 | 121.8488 | 121.8207
2067.75 | 121.962 | -0.15106 | 121.907 | 0.14932 | -0.008469 | -0.012 | -0.020438 | 0.040843 | 0.085583 | -0.071874 | 121.8542 | 121.8345 | 121.8009 | 121.6776 | -0.061641 | -0.013405 | -0.038063 | -0.00775 | 0.30038 | 0.14259 | 0.13906 | 0.13062 | 0.1919 | 0.23664 | 0.079188 | 121.9 | 121.8803 | 121.8467 | 121.7233 | -0.015865 | 0.032371 | 0.007713 | 0.038026 | 121.9158 | 121.8923 | 121.8626 | 121.839
2069.5156 | 121.994 | -0.1236 | 121.907 | 0.14932 | -0.013048 | -0.016578 | -0.020438 | 0.049999 | 0.090161 | -0.062717 | 121.8588 | 121.8391 | 121.7918 | 121.6776 | -0.057062 | -0.017983 | -0.033484 | -0.012328 | 0.27292 | 0.11055 | 0.10702 | 0.10316 | 0.17359 | 0.21376 | 0.060879 | 121.9046 | 121.8849 | 121.8376 | 121.7233 | -0.011286 | 0.027793 | 0.012292 | 0.033448 | 121.9158 | 121.8923 | 121.8488 | 121.8253
2071.2188 | 122.0627 | -0.10529 | 121.8887 | 0.14474 | -0.013048 | -0.016578 | -0.020438 | 0.036265 | 0.081005 | -0.062717 | 121.8496 | 121.8345 | 121.7964 | 121.6821 | -0.066219 | -0.022561 | -0.028906 | -0.016906 | 0.25003 | 0.092238 | 0.088708 | 0.084848 | 0.14155 | 0.18629 | 0.042569 | 121.8954 | 121.8803 | 121.8421 | 121.7279 | -0.020443 | 0.023215 | 0.01687 | 0.02887 | 121.9158 | 121.8785 | 121.8626 | 121.8253
2072.9844 | 122.0352 | -0.10071 | 121.8933 | 0.14932 | -0.013048 | -0.016578 | -0.01586 | 0.040843 | 0.085583 | -0.067295 | 121.8542 | 121.8391 | 121.7918 | 121.6821 | -0.066219 | -0.022561 | -0.033484 | -0.016906 | 0.25003 | 0.08766 | 0.08413 | 0.084848 | 0.14155 | 0.18629 | 0.033413 | 121.9 | 121.8849 | 121.8376 | 121.7279 | -0.020443 | 0.023215 | 0.012292 | 0.02887 | 121.9204 | 121.8877 | 121.858 | 121.8253
2074.7344 | 122.0581 | -0.10986 | 121.8796 | 0.14474 | -0.022205 | -0.021157 | -0.025017 | 0.036265 | 0.085583 | -0.071874 | 121.8542 | 121.8437 | 121.7964 | 121.6776 | -0.057062 | -0.027139 | -0.038063 | -0.016906 | 0.25461 | 0.087658 | 0.088706 | 0.084846 | 0.14613 | 0.19545 | 0.037989 | 121.9 | 121.8895 | 121.8421 | 121.7233 | -0.011286 | 0.018637 | 0.007713 | 0.02887 | 121.9113 | 121.8923 | 121.8534 | 121.8344
2076.4375 | 122.0032 | -0.13275 | 121.907 | 0.14932 | -0.017627 | -0.012 | -0.01586 | 0.040843 | 0.085583 | -0.076452 | 121.8542 | 121.8437 | 121.8009 | 121.6821 | -0.070797 | -0.022561 | -0.033484 | -0.00775 | 0.28207 | 0.11512 | 0.12075 | 0.11689 | 0.17359 | 0.21833 | 0.056299 | 121.9 | 121.8895 | 121.8467 | 121.7279 | -0.025021 | 0.023215 | 0.012292 | 0.038026 | 121.925 | 121.8877 | 121.8717 | 121.8344
2078.2031 | 122.0856 | -0.068665 | 121.843 | 0.1539 | -0.008469 | -0.021157 | -0.025017 | 0.049999 | 0.09474 | -0.067295 | 121.8588 | 121.8574 | 121.7918 | 121.6821 | -0.066219 | -0.022561 | -0.033484 | -0.016906 | 0.22257 | 0.060196 | 0.047508 | 0.043648 | 0.11866 | 0.16341 | 0.00137 | 121.9046 | 121.9032 | 121.8376 | 121.7279 | -0.020443 | 0.023215 | 0.012292 | 0.02887 | 121.925 | 121.8923 | 121.858 | 121.8253
2079.9531 | 122.0352 | -0.09613 | 121.8842 | 0.14474 | -0.017627 | -0.012 | -0.025017 | 0.045421 | 0.085583 | -0.076452 | 121.8634 | 121.8483 | 121.7918 | 121.6867 | -0.066219 | -0.017983 | -0.033484 | -0.012328 | 0.24087 | 0.078503 | 0.08413 | 0.071113 | 0.14155 | 0.18171 | 0.019678 | 121.9091 | 121.8941 | 121.8376 | 121.7325 | -0.020443 | 0.027793 | 0.012292 | 0.033448 | 121.9296 | 121.8968 | 121.858 | 121.8253
2081.7031 | 122.0398 | -0.10529 | 121.8933 | 0.14474 | -0.008469 | -0.016578 | -0.020438 | 0.040843 | 0.085583 | -0.067295 | 121.8634 | 121.8483 | 121.7918 | 121.6776 | -0.070797 | -0.027139 | -0.028906 | -0.016906 | 0.25003 | 0.096817 | 0.088708 | 0.084848 | 0.14613 | 0.19087 | 0.037991 | 121.9091 | 121.8941 | 121.8376 | 121.7233 | -0.025021 | 0.018637 | 0.01687 | 0.02887 | 121.9341 | 121.8923 | 121.8626 | 121.8207
2083.4062 | 121.9482 | -0.12817 | 121.9208 | 0.1539 | -0.013048 | -0.016578 | -0.01586 | 0.040843 | 0.081005 | -0.058139 | 121.8588 | 121.8483 | 121.8055 | 121.6913 | -0.070797 | -0.022561 | -0.038063 | -0.016906 | 0.28207 | 0.11513 | 0.1116 | 0.11231 | 0.16902 | 0.20918 | 0.070035 | 121.9046 | 121.8941 | 121.8513 | 121.7371 | -0.025021 | 0.023215 | 0.007713 | 0.02887 | 121.9296 | 121.8968 | 121.8763 | 121.8436
2085.1719 | 121.9574 | -0.1236 | 121.9254 | 0.14932 | -0.017627 | -0.016578 | -0.025017 | 0.045421 | 0.090161 | -0.067295 | 121.8634 | 121.8529 | 121.8009 | 121.6867 | -0.070797 | -0.027139 | -0.042641 | -0.012328 | 0.27292 | 0.10597 | 0.10702 | 0.098579 | 0.16902 | 0.21376 | 0.056301 | 121.9091 | 121.8986 | 121.8467 | 121.7325 | -0.025021 | 0.018637 | 0.003135 | 0.033448 | 121.9341 | 121.906 | 121.8717 | 121.8436
2086.9375 | 122.0352 | -0.10986 | 121.9208 | 0.14932 | -0.013048 | -0.016578 | -0.025017 | 0.036265 | 0.085583 | -0.067295 | 121.8588 | 121.8529 | 121.8009 | 121.6821 | -0.070797 | -0.027139 | -0.038063 | -0.021484 | 0.25918 | 0.096815 | 0.093285 | 0.084846 | 0.14613 | 0.19545 | 0.042568 | 121.9046 | 121.8986 | 121.8467 | 121.7279 | -0.025021 | 0.018637 | 0.007713 | 0.024292 | 121.9296 | 121.8968 | 121.8717 | 121.839
2088.7031 | 122.049 | -0.082397 | 121.907 | 0.14932 | -0.013048 | -0.012 | -0.025017 | 0.040843 | 0.085583 | -0.067295 | 121.8634 | 121.8574 | 121.8055 | 121.6821 | -0.066219 | -0.017983 | -0.042641 | -0.026063 | 0.23172 | 0.069349 | 0.070397 | 0.05738 | 0.12324 | 0.16798 | 0.015102 | 121.9091 | 121.9032 | 121.8513 | 121.7279 | -0.020443 | 0.027793 | 0.003135 | 0.019713 | 121.9296 | 121.906 | 121.8717 | 121.8482
2090.3906 | 122.0078 | -0.12817 | 121.9025 | 0.1539 | -0.017627 | -0.021157 | -0.020438 | 0.040843 | 0.081005 | -0.062717 | 121.8634 | 121.8529 | 121.8055 | 121.6959 | -0.075375 | -0.027139 | -0.038063 | -0.016906 | 0.28207 | 0.11055 | 0.10702 | 0.10774 | 0.16902 | 0.20918 | 0.065457 | 121.9091 | 121.8986 | 121.8513 | 121.7417 | -0.029599 | 0.018637 | 0.007713 | 0.02887 | 121.9387 | 121.9014 | 121.8809 | 121.8436
2092.1406 | 122.1039 | -0.086975 | 121.8979 | 0.14474 | -0.013048 | -0.007421 | -0.020438 | 0.040843 | 0.099318 | -0.062717 | 121.8634 | 121.8483 | 121.7872 | 121.6913 | -0.066219 | -0.027139 | -0.033484 | -0.012328 | 0.23172 | 0.073927 | 0.079554 | 0.066537 | 0.12782 | 0.18629 | 0.024258 | 121.9091 | 121.8941 | 121.833 | 121.7371 | -0.020443 | 0.018637 | 0.012292 | 0.033448 | 121.9296 | 121.8968 | 121.8534 | 121.8207
2093.9062 | 121.9849 | -0.1236 | 121.907 | 0.14932 | -0.00389 | -0.016578 | -0.029595 | 0.049999 | 0.090161 | -0.058139 | 121.8634 | 121.8574 | 121.8055 | 121.6959 | -0.070797 | -0.022561 | -0.033484 | -0.016906 | 0.27292 | 0.11971 | 0.10702 | 0.094001 | 0.17359 | 0.21376 | 0.065457 | 121.9091 | 121.9032 | 121.8513 | 121.7417 | -0.025021 | 0.023215 | 0.012292 | 0.02887 | 121.9341 | 121.8968 | 121.8763 | 121.839
2095.6719 | 122.0764 | -0.09613 | 121.8979 | 0.1539 | -0.008469 | -0.012 | -0.01586 | 0.040843 | 0.090161 | -0.062717 | 121.8634 | 121.8483 | 121.8009 | 121.6913 | -0.075375 | -0.022561 | -0.042641 | -0.021484 | 0.25003 | 0.087661 | 0.08413 | 0.08027 | 0.13697 | 0.18629 | 0.033413 | 121.9091 | 121.8941 | 121.8467 | 121.7371 | -0.029599 | 0.023215 | 0.003135 | 0.024292 | 121.9387 | 121.906 | 121.8763 | 121.8436
2097.3594 | 121.994 | -0.11902 | 121.9025 | 0.1539 | -0.017627 | -0.007421 | -0.025017 | 0.036265 | 0.085583 | -0.062717 | 121.8679 | 121.8483 | 121.8009 | 121.6913 | -0.066219 | -0.031717 | -0.033484 | -0.016906 | 0.27292 | 0.10139 | 0.1116 | 0.094002 | 0.15528 | 0.2046 | 0.056302 | 121.9137 | 121.8941 | 121.8467 | 121.7371 | -0.020443 | 0.014059 | 0.012292 | 0.02887 | 121.9342 | 121.9014 | 121.8672 | 121.8344
2099.125 | 122.0535 | -0.10529 | 121.9025 | 0.14474 | -0.026784 | -0.012 | -0.020438 | 0.040843 | 0.085583 | -0.062717 | 121.8771 | 121.8483 | 121.8055 | 121.6867 | -0.066219 | -0.022561 | -0.038063 | -0.016906 | 0.25003 | 0.078502 | 0.093286 | 0.084848 | 0.14613 | 0.19087 | 0.042569 | 121.9229 | 121.8941 | 121.8513 | 121.7325 | -0.020443 | 0.023215 | 0.007713 | 0.02887 | 121.9433 | 121.9152 | 121.8717 | 121.8436
2100.875 | 122.0901 | -0.07782 | 121.9025 | 0.14017 | -0.017627 | -0.016578 | -0.029595 | 0.036265 | 0.085583 | -0.071874 | 121.8634 | 121.8483 | 121.8055 | 121.7005 | -0.066219 | -0.036295 | -0.033484 | -0.021484 | 0.21799 | 0.060193 | 0.061242 | 0.048225 | 0.11408 | 0.1634 | 0.005946 | 121.9091 | 121.8941 | 121.8513 | 121.7462 | -0.020443 | 0.009481 | 0.012292 | 0.024292 | 121.9296 | 121.8968 | 121.8717 | 121.839
2102.5781 | 122.0398 | -0.11444 | 121.8979 | 0.14932 | -0.017627 | -0.012 | -0.020438 | 0.040843 | 0.085583 | -0.062717 | 121.8725 | 121.8574 | 121.8147 | 121.6913 | -0.066219 | -0.027139 | -0.038063 | -0.021484 | 0.26376 | 0.096814 | 0.10244 | 0.094003 | 0.15528 | 0.20002 | 0.051724 | 121.9183 | 121.9032 | 121.8604 | 121.7371 | -0.020443 | 0.018637 | 0.007713 | 0.024292 | 121.9387 | 121.9106 | 121.8809 | 121.8527
2104.3594 | 122.0901 | -0.082397 | 121.8933 | 0.14474 | -0.013048 | -0.021157 | -0.025017 | 0.040843 | 0.085583 | -0.067295 | 121.8634 | 121.8574 | 121.8055 | 121.6913 | -0.061641 | -0.022561 | -0.038063 | -0.016906 | 0.22714 | 0.069349 | 0.06124 | 0.05738 | 0.12324 | 0.16798 | 0.015102 | 121.9091 | 121.9032 | 121.8513 | 121.7371 | -0.015865 | 0.023215 | 0.007713 | 0.02887 | 121.925 | 121.9014 | 121.8672 | 121.8436
2106.0625 | 122.081 | -0.10071 | 121.907 | 0.14474 | -0.013048 | -0.021157 | -0.025017 | 0.040843 | 0.085583 | -0.071874 | 121.8679 | 121.8574 | 121.8101 | 121.6913 | -0.070797 | -0.022561 | -0.038063 | -0.016906 | 0.24545 | 0.08766 | 0.079551 | 0.075691 | 0.14155 | 0.18629 | 0.028834 | 121.9137 | 121.9032 | 121.8559 | 121.7371 | -0.025021 | 0.023215 | 0.007713 | 0.02887 | 121.9387 | 121.906 | 121.8809 | 121.8482
2107.8125 | 122.0169 | -0.1236 | 121.9345 | 0.14017 | -0.017627 | -0.012 | -0.01586 | 0.045421 | 0.090161 | -0.067295 | 121.8725 | 121.8574 | 121.8055 | 121.7005 | -0.066219 | -0.031717 | -0.038063 | -0.016906 | 0.26376 | 0.10597 | 0.1116 | 0.10774 | 0.16902 | 0.21376 | 0.056301 | 121.9183 | 121.9032 | 121.8513 | 121.7462 | -0.020443 | 0.014059 | 0.007713 | 0.02887 | 121.9387 | 121.9106 | 121.8717 | 121.8436
2109.5 | 121.9894 | -0.12817 | 121.9437 | 0.14474 | -0.017627 | -0.016578 | -0.020438 | 0.036265 | 0.090161 | -0.067295 | 121.8771 | 121.8666 | 121.8147 | 121.6959 | -0.070797 | -0.022561 | -0.038063 | -0.021484 | 0.27292 | 0.11055 | 0.1116 | 0.10774 | 0.16444 | 0.21834 | 0.060879 | 121.9229 | 121.9124 | 121.8604 | 121.7417 | -0.025021 | 0.023215 | 0.007713 | 0.024292 | 121.9479 | 121.9152 | 121.8855 | 121.8527
2111.25 | 122.0901 | -0.082397 | 121.8933 | 0.14474 | -0.008469 | -0.012 | -0.025017 | 0.036265 | 0.09474 | -0.076452 | 121.8725 | 121.862 | 121.8147 | 121.7005 | -0.070797 | -0.027139 | -0.038063 | -0.021484 | 0.22714 | 0.073928 | 0.070397 | 0.05738 | 0.11866 | 0.17714 | 0.005945 | 121.9183 | 121.9078 | 121.8604 | 121.7462 | -0.025021 | 0.018637 | 0.007713 | 0.024292 | 121.9433 | 121.9106 | 121.8855 | 121.8527
2113 | 121.9986 | -0.1236 | 121.9116 | 0.1539 | -0.013048 | -0.016578 | -0.029595 | 0.040843 | 0.090161 | -0.071874 | 121.8771 | 121.8666 | 121.8101 | 121.6959 | -0.070797 | -0.036295 | -0.033484 | -0.021484 | 0.2775 | 0.11055 | 0.10702 | 0.094001 | 0.16444 | 0.21376 | 0.051722 | 121.9229 | 121.9124 | 121.8559 | 121.7417 | -0.025021 | 0.009481 | 0.012292 | 0.024292 | 121.9479 | 121.9106 | 121.8809 | 121.8436
2114.6875 | 122.0444 | -0.091553 | 121.8842 | 0.1539 | -0.017627 | -0.021157 | -0.020438 | 0.045421 | 0.085583 | -0.062717 | 121.8725 | 121.8666 | 121.8101 | 121.705 | -0.075375 | -0.031717 | -0.033484 | -0.016906 | 0.24545 | 0.073926 | 0.070396 | 0.071115 | 0.13697 | 0.17714 | 0.028836 | 121.9183 | 121.9124 | 121.8559 | 121.7508 | -0.029599 | 0.014059 | 0.012292 | 0.02887 | 121.9479 | 121.906 | 121.8855 | 121.8436
2116.4375 | 122.0078 | -0.11444 | 121.9162 | 0.14932 | -0.013048 | -0.007421 | -0.025017 | 0.036265 | 0.081005 | -0.058139 | 121.8771 | 121.8666 | 121.8055 | 121.705 | -0.070797 | -0.031717 | -0.042641 | -0.026063 | 0.26376 | 0.10139 | 0.10702 | 0.089424 | 0.15071 | 0.19545 | 0.056302 | 121.9229 | 121.9124 | 121.8513 | 121.7508 | -0.025021 | 0.014059 | 0.003135 | 0.019713 | 121.9479 | 121.9197 | 121.8763 | 121.8482
2118.2031 | 122.0261 | -0.09613 | 121.9254 | 0.14474 | -0.017627 | -0.016578 | -0.01586 | 0.049999 | 0.085583 | -0.062717 | 121.8679 | 121.8666 | 121.8192 | 121.7005 | -0.079953 | -0.027139 | -0.042641 | -0.030641 | 0.24087 | 0.078503 | 0.079552 | 0.08027 | 0.14613 | 0.18171 | 0.033413 | 121.9137 | 121.9124 | 121.865 | 121.7462 | -0.034177 | 0.018637 | 0.003135 | 0.015135 | 121.9479 | 121.9106 | 121.8992 | 121.8619
2119.9531 | 122.0123 | -0.1236 | 121.9437 | 0.14932 | -0.013048 | -0.016578 | -0.01586 | 0.040843 | 0.085583 | -0.067295 | 121.8725 | 121.862 | 121.8192 | 121.705 | -0.075375 | -0.031717 | -0.038063 | -0.026063 | 0.27292 | 0.11055 | 0.10702 | 0.10774 | 0.16444 | 0.20918 | 0.056301 | 121.9183 | 121.9078 | 121.865 | 121.7508 | -0.029599 | 0.014059 | 0.007713 | 0.019713 | 121.9479 | 121.9106 | 121.8946 | 121.8573
2121.7031 | 121.9894 | -0.13275 | 121.9162 | 0.14474 | -0.008469 | -0.016578 | -0.025017 | 0.045421 | 0.090161 | -0.062717 | 121.8725 | 121.8712 | 121.8147 | 121.705 | -0.070797 | -0.031717 | -0.038063 | -0.026063 | 0.27749 | 0.12428 | 0.11617 | 0.10773 | 0.17817 | 0.22291 | 0.070034 | 121.9183 | 121.917 | 121.8604 | 121.7508 | -0.025021 | 0.014059 | 0.007713 | 0.019713 | 121.9433 | 121.9106 | 121.8855 | 121.8527
2123.4062 | 122.0535 | -0.086975 | 121.9116 | 0.14932 | -0.013048 | -0.012 | -0.020438 | 0.045421 | 0.085583 | -0.067295 | 121.8771 | 121.8712 | 121.8147 | 121.705 | -0.075375 | -0.036295 | -0.038063 | -0.021484 | 0.2363 | 0.073927 | 0.074975 | 0.066537 | 0.1324 | 0.17256 | 0.01968 | 121.9229 | 121.917 | 121.8604 | 121.7508 | -0.029599 | 0.009481 | 0.007713 | 0.024292 | 121.9525 | 121.9152 | 121.89 | 121.8527
2125.1562 | 122.0901 | -0.082397 | 121.9025 | 0.14932 | -0.017627 | -0.016578 | -0.029595 | 0.045421 | 0.085583 | -0.067295 | 121.8725 | 121.8712 | 121.8192 | 121.7005 | -0.070797 | -0.031717 | -0.033484 | -0.030641 | 0.23172 | 0.06477 | 0.065819 | 0.052802 | 0.12782 | 0.16798 | 0.015102 | 121.9183 | 121.917 | 121.865 | 121.7462 | -0.025021 | 0.014059 | 0.012292 | 0.015135 | 121.9433 | 121.906 | 121.89 | 121.8527
2126.9062 | 121.9803 | -0.13733 | 121.9391 | 0.14932 | -0.013048 | -0.012 | -0.025017 | 0.045421 | 0.085583 | -0.062717 | 121.8817 | 121.8712 | 121.8192 | 121.705 | -0.075375 | -0.036295 | -0.04722 | -0.021484 | 0.28665 | 0.12428 | 0.12533 | 0.11231 | 0.18275 | 0.22291 | 0.074612 | 121.9274 | 121.917 | 121.865 | 121.7508 | -0.029599 | 0.009481 | -0.001444 | 0.024292 | 121.957 | 121.9289 | 121.8946 | 121.8665
2128.6719 | 122.0078 | -0.12817 | 121.9391 | 0.14932 | -0.022205 | -0.012 | -0.020438 | 0.045421 | 0.085583 | -0.062717 | 121.8817 | 121.8712 | 121.8192 | 121.7096 | -0.070797 | -0.036295 | -0.04722 | -0.021484 | 0.2775 | 0.10597 | 0.11617 | 0.10774 | 0.17359 | 0.21376 | 0.065457 | 121.9274 | 121.917 | 121.865 | 121.7554 | -0.025021 | 0.009481 | -0.001444 | 0.024292 | 121.9525 | 121.9289 | 121.89 | 121.8665
2130.4375 | 121.9666 | -0.1236 | 121.9666 | 0.14474 | -0.017627 | -0.016578 | -0.020438 | 0.036265 | 0.081005 | -0.067295 | 121.8725 | 121.8712 | 121.8284 | 121.7096 | -0.075375 | -0.031717 | -0.04722 | -0.030641 | 0.26834 | 0.10597 | 0.10702 | 0.10316 | 0.15986 | 0.2046 | 0.056301 | 121.9183 | 121.917 | 121.8742 | 121.7554 | -0.029599 | 0.014059 | -0.001444 | 0.015135 | 121.9479 | 121.9197 | 121.9038 | 121.8756
2132.1875 | 122.0627 | -0.086975 | 121.9254 | 0.14932 | -0.013048 | -0.021157 | -0.01586 | 0.040843 | 0.085583 | -0.067295 | 121.8862 | 121.8803 | 121.8192 | 121.7096 | -0.075375 | -0.036295 | -0.042641 | -0.026063 | 0.2363 | 0.073927 | 0.065818 | 0.071115 | 0.12782 | 0.17256 | 0.01968 | 121.932 | 121.9261 | 121.865 | 121.7554 | -0.029599 | 0.009481 | 0.003135 | 0.019713 | 121.9616 | 121.9289 | 121.8946 | 121.8619
2133.9062 | 122.0627 | -0.091553 | 121.9208 | 0.14474 | -0.017627 | -0.016578 | -0.020438 | 0.040843 | 0.076426 | -0.062717 | 121.8862 | 121.8803 | 121.8192 | 121.7096 | -0.066219 | -0.036295 | -0.038063 | -0.021484 | 0.2363 | 0.073926 | 0.074975 | 0.071115 | 0.1324 | 0.16798 | 0.028836 | 121.932 | 121.9261 | 121.865 | 121.7554 | -0.020443 | 0.009481 | 0.007713 | 0.024292 | 121.9525 | 121.9243 | 121.8855 | 121.8573
2135.6719 | 122.0947 | -0.073242 | 121.8933 | 0.14017 | -0.013048 | -0.016578 | -0.020438 | 0.040843 | 0.085583 | -0.062717 | 121.8771 | 121.8712 | 121.8238 | 121.705 | -0.075375 | -0.031717 | -0.033484 | -0.026063 | 0.21341 | 0.060194 | 0.056664 | 0.052804 | 0.11408 | 0.15882 | 0.010525 | 121.9229 | 121.917 | 121.8696 | 121.7508 | -0.029599 | 0.014059 | 0.012292 | 0.019713 | 121.9525 | 121.9106 | 121.8992 | 121.8573
2137.4219 | 121.9803 | -0.11444 | 121.9528 | 0.14932 | -0.013048 | -0.016578 | -0.025017 | 0.040843 | 0.090161 | -0.062717 | 121.8817 | 121.8712 | 121.8192 | 121.7142 | -0.070797 | -0.036295 | -0.038063 | -0.030641 | 0.26376 | 0.10139 | 0.097863 | 0.089424 | 0.15528 | 0.2046 | 0.051724 | 121.9274 | 121.917 | 121.865 | 121.76 | -0.025021 | 0.009481 | 0.007713 | 0.015135 | 121.9525 | 121.9197 | 121.89 | 121.8573
2139.125 | 121.9757 | -0.11444 | 121.9299 | 0.1539 | -0.013048 | -0.012 | -0.025017 | 0.036265 | 0.076426 | -0.058139 | 121.8862 | 121.8666 | 121.8284 | 121.7188 | -0.070797 | -0.040873 | -0.042641 | -0.030641 | 0.26834 | 0.10139 | 0.10244 | 0.089424 | 0.15071 | 0.19087 | 0.056302 | 121.932 | 121.9124 | 121.8742 | 121.7646 | -0.025021 | 0.004903 | 0.003135 | 0.015135 | 121.957 | 121.9289 | 121.8992 | 121.871
2140.8906 | 122.1039 | -0.073242 | 121.9025 | 0.14474 | -0.022205 | -0.016578 | -0.020438 | 0.045421 | 0.081005 | -0.062717 | 121.8771 | 121.8712 | 121.8192 | 121.7096 | -0.075375 | -0.040873 | -0.033484 | -0.026063 | 0.21799 | 0.051037 | 0.056664 | 0.052804 | 0.11866 | 0.15425 | 0.010525 | 121.9229 | 121.917 | 121.865 | 121.7554 | -0.029599 | 0.004903 | 0.012292 | 0.019713 | 121.9525 | 121.9106 | 121.8946 | 121.8527
2142.5781 | 122.0627 | -0.082397 | 121.9299 | 0.14932 | -0.008469 | -0.012 | -0.025017 | 0.036265 | 0.081005 | -0.071874 | 121.8862 | 121.8712 | 121.8192 | 121.705 | -0.075375 | -0.031717 | -0.042641 | -0.026063 | 0.23172 | 0.073928 | 0.070397 | 0.05738 | 0.11866 | 0.1634 | 0.010523 | 121.932 | 121.917 | 121.865 | 121.7508 | -0.029599 | 0.014059 | 0.003135 | 0.019713 | 121.9616 | 121.9289 | 121.8946 | 121.8619
2144.3281 | 121.9757 | -0.13733 | 121.9528 | 0.1539 | -0.017627 | -0.016578 | -0.020438 | 0.040843 | 0.085583 | -0.062717 | 121.8817 | 121.8758 | 121.8192 | 121.7096 | -0.075375 | -0.036295 | -0.042641 | -0.026063 | 0.29123 | 0.1197 | 0.12075 | 0.11689 | 0.17817 | 0.22291 | 0.074612 | 121.9274 | 121.9215 | 121.865 | 121.7554 | -0.029599 | 0.009481 | 0.003135 | 0.019713 | 121.957 | 121.9243 | 121.8946 | 121.8619
2146.1094 | 121.9986 | -0.10529 | 121.9528 | 0.14932 | -0.008469 | -0.016578 | -0.029595 | 0.045421 | 0.090161 | -0.067295 | 121.8817 | 121.8758 | 121.8192 | 121.7096 | -0.079953 | -0.036295 | -0.04722 | -0.021484 | 0.25461 | 0.096817 | 0.088708 | 0.075691 | 0.15071 | 0.19545 | 0.037991 | 121.9274 | 121.9215 | 121.865 | 121.7554 | -0.034177 | 0.009481 | -0.001444 | 0.024292 | 121.9616 | 121.9289 | 121.8992 | 121.8665
2147.8125 | 121.9849 | -0.10529 | 121.9299 | 0.14932 | -0.008469 | -0.016578 | -0.01586 | 0.040843 | 0.085583 | -0.067295 | 121.8862 | 121.8758 | 121.8147 | 121.7142 | -0.075375 | -0.040873 | -0.04722 | -0.026063 | 0.25461 | 0.096817 | 0.088708 | 0.089426 | 0.14613 | 0.19087 | 0.037991 | 121.932 | 121.9215 | 121.8604 | 121.76 | -0.029599 | 0.004903 | -0.001444 | 0.019713 | 121.9616 | 121.9335 | 121.89 | 121.8619
2149.5781 | 122.1405 | -0.073242 | 121.8887 | 0.14932 | -0.022205 | -0.016578 | -0.020438 | 0.040843 | 0.081005 | -0.071874 | 121.8908 | 121.8803 | 121.8192 | 121.7142 | -0.066219 | -0.036295 | -0.038063 | -0.026063 | 0.22256 | 0.051037 | 0.056664 | 0.052804 | 0.11408 | 0.15425 | 0.001368 | 121.9366 | 121.9261 | 121.865 | 121.76 | -0.020443 | 0.009481 | 0.007713 | 0.019713 | 121.957 | 121.9289 | 121.8855 | 121.8573
2151.3281 | 122.1268 | -0.068665 | 121.9162 | 0.14474 | -0.017627 | -0.021157 | -0.020438 | 0.045421 | 0.081005 | -0.062717 | 121.8817 | 121.8712 | 121.8238 | 121.7142 | -0.070797 | -0.031717 | -0.042641 | -0.030641 | 0.21341 | 0.051038 | 0.047508 | 0.048227 | 0.11409 | 0.14967 | 0.005948 | 121.9274 | 121.917 | 121.8696 | 121.76 | -0.025021 | 0.014059 | 0.003135 | 0.015135 | 121.9525 | 121.9243 | 121.8946 | 121.8665
2153.0781 | 122.0673 | -0.07782 | 121.9025 | 0.1539 | -0.013048 | -0.016578 | -0.020438 | 0.045421 | 0.090161 | -0.067295 | 121.8954 | 121.8758 | 121.8192 | 121.7096 | -0.075375 | -0.040873 | -0.042641 | -0.021484 | 0.23172 | 0.064772 | 0.061242 | 0.057382 | 0.12324 | 0.16798 | 0.010525 | 121.9412 | 121.9215 | 121.865 | 121.7554 | -0.029599 | 0.004903 | 0.003135 | 0.024292 | 121.9708 | 121.938 | 121.8946 | 121.8619
2154.8438 | 122.0627 | -0.082397 | 121.9116 | 0.14932 | -0.013048 | -0.012 | -0.020438 | 0.036265 | 0.076426 | -0.067295 | 121.8817 | 121.8803 | 121.8192 | 121.7096 | -0.079953 | -0.036295 | -0.042641 | -0.026063 | 0.23172 | 0.069349 | 0.070397 | 0.061959 | 0.11866 | 0.15882 | 0.015102 | 121.9274 | 121.9261 | 121.865 | 121.7554 | -0.034177 | 0.009481 | 0.003135 | 0.019713 | 121.9616 | 121.9243 | 121.8992 | 121.8619
2156.5312 | 122.0169 | -0.1236 | 121.9391 | 0.1539 | -0.008469 | -0.016578 | -0.020438 | 0.040843 | 0.09474 | -0.062717 | 121.8862 | 121.8758 | 121.833 | 121.7142 | -0.075375 | -0.036295 | -0.042641 | -0.030641 | 0.2775 | 0.11513 | 0.10702 | 0.10316 | 0.16444 | 0.21834 | 0.060879 | 121.932 | 121.9215 | 121.8788 | 121.76 | -0.029599 | 0.009481 | 0.003135 | 0.015135 | 121.9616 | 121.9289 | 121.9084 | 121.8756
2158.2812 | 122.0947 | -0.073242 | 121.9208 | 0.14017 | -0.017627 | -0.021157 | -0.01586 | 0.045421 | 0.076426 | -0.067295 | 121.8862 | 121.8803 | 121.8284 | 121.7142 | -0.070797 | -0.036295 | -0.04722 | -0.026063 | 0.21341 | 0.055615 | 0.052085 | 0.057382 | 0.11866 | 0.14967 | 0.005947 | 121.932 | 121.9261 | 121.8742 | 121.76 | -0.025021 | 0.009481 | -0.001444 | 0.019713 | 121.957 | 121.9335 | 121.8992 | 121.8756
2160.0312 | 121.994 | -0.1236 | 121.9482 | 0.1539 | -0.008469 | -0.012 | -0.025017 | 0.040843 | 0.081005 | -0.067295 | 121.8862 | 121.8849 | 121.8238 | 121.7142 | -0.066219 | -0.036295 | -0.042641 | -0.026063 | 0.2775 | 0.11513 | 0.1116 | 0.098579 | 0.16444 | 0.2046 | 0.056301 | 121.932 | 121.9307 | 121.8696 | 121.76 | -0.020443 | 0.009481 | 0.003135 | 0.019713 | 121.9525 | 121.9289 | 121.89 | 121.8665
2161.7969 | 122.0261 | -0.11444 | 121.907 | 0.14932 | -0.022205 | -0.016578 | -0.025017 | 0.040843 | 0.081005 | -0.067295 | 121.8908 | 121.8803 | 121.8238 | 121.7096 | -0.070797 | -0.040873 | -0.042641 | -0.026063 | 0.26376 | 0.092236 | 0.097863 | 0.089424 | 0.15528 | 0.19545 | 0.047146 | 121.9366 | 121.9261 | 121.8696 | 121.7554 | -0.025021 | 0.004903 | 0.003135 | 0.019713 | 121.9616 | 121.9335 | 121.8946 | 121.8665
2163.5 | 122.1039 | -0.054932 | 121.8933 | 0.14932 | -0.013048 | -0.016578 | -0.020438 | 0.040843 | 0.081005 | -0.067295 | 121.8954 | 121.8803 | 121.8192 | 121.7188 | -0.066219 | -0.040873 | -0.042641 | -0.021484 | 0.20425 | 0.041884 | 0.038354 | 0.034494 | 0.095775 | 0.13594 | -0.012363 | 121.9412 | 121.9261 | 121.865 | 121.7646 | -0.020443 | 0.004903 | 0.003135 | 0.024292 | 121.9616 | 121.938 | 121.8855 | 121.8619
2165.25 | 121.9757 | -0.12817 | 121.9482 | 0.1539 | -0.008469 | -0.012 | -0.01586 | 0.045421 | 0.090161 | -0.062717 | 121.8954 | 121.8803 | 121.8284 | 121.7142 | -0.075375 | -0.036295 | -0.042641 | -0.030641 | 0.28207 | 0.11971 | 0.11617 | 0.11231 | 0.17359 | 0.21834 | 0.065457 | 121.9412 | 121.9261 | 121.8742 | 121.76 | -0.029599 | 0.009481 | 0.003135 | 0.015135 | 121.9708 | 121.938 | 121.9038 | 121.871
2166.9531 | 122.049 | -0.082397 | 121.9254 | 0.14932 | -0.013048 | -0.012 | -0.020438 | 0.045421 | 0.090161 | -0.062717 | 121.8908 | 121.8895 | 121.8192 | 121.7142 | -0.066219 | -0.040873 | -0.04722 | -0.026063 | 0.23172 | 0.069349 | 0.070397 | 0.061959 | 0.12782 | 0.17256 | 0.01968 | 121.9366 | 121.9353 | 121.865 | 121.76 | -0.020443 | 0.004903 | -0.001444 | 0.019713 | 121.957 | 121.938 | 121.8855 | 121.8665
2168.7188 | 121.994 | -0.1236 | 121.9254 | 0.14932 | -0.013048 | -0.021157 | -0.020438 | 0.040843 | 0.085583 | -0.067295 | 121.8908 | 121.8849 | 121.8238 | 121.7188 | -0.075375 | -0.040873 | -0.038063 | -0.021484 | 0.27292 | 0.11055 | 0.10244 | 0.10316 | 0.16444 | 0.20918 | 0.056301 | 121.9366 | 121.9307 | 121.8696 | 121.7646 | -0.029599 | 0.004903 | 0.007713 | 0.024292 | 121.9662 | 121.9289 | 121.8992 | 121.8619
2170.4688 | 121.9849 | -0.10986 | 121.9391 | 0.14932 | -0.008469 | -0.021157 | -0.025017 | 0.040843 | 0.081005 | -0.062717 | 121.8862 | 121.8803 | 121.8284 | 121.7188 | -0.075375 | -0.027139 | -0.04722 | -0.030641 | 0.25918 | 0.10139 | 0.088706 | 0.084846 | 0.15071 | 0.19087 | 0.047146 | 121.932 | 121.9261 | 121.8742 | 121.7646 | -0.029599 | 0.018637 | -0.001444 | 0.015135 | 121.9616 | 121.9335 | 121.9038 | 121.8756
2172.1562 | 122.1039 | -0.064087 | 121.9208 | 0.1539 | -0.013048 | -0.012 | -0.025017 | 0.040843 | 0.085583 | -0.062717 | 121.8862 | 121.8849 | 121.8238 | 121.7188 | -0.070797 | -0.045451 | -0.042641 | -0.030641 | 0.21799 | 0.051039 | 0.052087 | 0.03907 | 0.10493 | 0.14967 | 0.00137 | 121.932 | 121.9307 | 121.8696 | 121.7646 | -0.025021 | 0.000325 | 0.003135 | 0.015135 | 121.957 | 121.9289 | 121.8946 | 121.8665
2173.9219 | 122.0535 | -0.09613 | 121.9254 | 0.1539 | -0.013048 | -0.016578 | -0.025017 | 0.040843 | 0.085583 | -0.067295 | 121.8908 | 121.8849 | 121.8284 | 121.7096 | -0.070797 | -0.031717 | -0.042641 | -0.021484 | 0.25003 | 0.083082 | 0.079552 | 0.071113 | 0.13697 | 0.18171 | 0.028835 | 121.9366 | 121.9307 | 121.8742 | 121.7554 | -0.025021 | 0.014059 | 0.003135 | 0.024292 | 121.9616 | 121.9335 | 121.8992 | 121.871
2175.6875 | 121.9803 | -0.12817 | 121.9711 | 0.14017 | -0.017627 | -0.012 | -0.025017 | 0.045421 | 0.085583 | -0.062717 | 121.8954 | 121.8803 | 121.8238 | 121.7188 | -0.075375 | -0.031717 | -0.051798 | -0.026063 | 0.26834 | 0.11055 | 0.11617 | 0.10316 | 0.17359 | 0.21376 | 0.065457 | 121.9412 | 121.9261 | 121.8696 | 121.7646 | -0.029599 | 0.014059 | -0.006022 | 0.019713 | 121.9708 | 121.9472 | 121.8992 | 121.8756
2177.3906 | 122.0215 | -0.11902 | 121.9437 | 0.15848 | -0.017627 | -0.016578 | -0.025017 | 0.040843 | 0.085583 | -0.062717 | 121.8908 | 121.8849 | 121.8284 | 121.7188 | -0.079953 | -0.036295 | -0.042641 | -0.021484 | 0.2775 | 0.10139 | 0.10244 | 0.094002 | 0.15986 | 0.2046 | 0.056302 | 121.9366 | 121.9307 | 121.8742 | 121.7646 | -0.034177 | 0.009481 | 0.003135 | 0.024292 | 121.9708 | 121.9335 | 121.9084 | 121.871
2179.1719 | 121.9711 | -0.11444 | 121.9757 | 0.14474 | -0.017627 | -0.025735 | -0.020438 | 0.040843 | 0.085583 | -0.071874 | 121.8862 | 121.8849 | 121.8238 | 121.7234 | -0.075375 | -0.040873 | -0.042641 | -0.035219 | 0.25918 | 0.096814 | 0.088706 | 0.094003 | 0.15528 | 0.20002 | 0.042567 | 121.932 | 121.9307 | 121.8696 | 121.7691 | -0.029599 | 0.004903 | 0.003135 | 0.010557 | 121.9616 | 121.9289 | 121.8992 | 121.8665
2180.9375 | 122.0032 | -0.10071 | 121.9711 | 0.14474 | -0.017627 | -0.007421 | -0.020438 | 0.040843 | 0.085583 | -0.062717 | 121.8817 | 121.8849 | 121.833 | 121.7188 | -0.075375 | -0.045451 | -0.042641 | -0.021484 | 0.24545 | 0.083081 | 0.093287 | 0.08027 | 0.14155 | 0.18629 | 0.037991 | 121.9274 | 121.9307 | 121.8788 | 121.7646 | -0.029599 | 0.000325 | 0.003135 | 0.024292 | 121.957 | 121.9243 | 121.9084 | 121.8756
2182.625 | 122.0627 | -0.073242 | 121.9162 | 0.14932 | -0.017627 | -0.016578 | -0.025017 | 0.045421 | 0.085583 | -0.067295 | 121.8954 | 121.8895 | 121.8284 | 121.7142 | -0.075375 | -0.040873 | -0.04722 | -0.021484 | 0.22256 | 0.055615 | 0.056664 | 0.048225 | 0.11866 | 0.15882 | 0.005947 | 121.9412 | 121.9353 | 121.8742 | 121.76 | -0.029599 | 0.004903 | -0.001444 | 0.024292 | 121.9708 | 121.9426 | 121.9038 | 121.8756
2184.375 | 121.9803 | -0.11444 | 121.9666 | 0.14474 | -0.008469 | -0.012 | -0.025017 | 0.045421 | 0.085583 | -0.071874 | 121.8954 | 121.8803 | 121.833 | 121.7188 | -0.079953 | -0.040873 | -0.042641 | -0.035219 | 0.25918 | 0.10597 | 0.10244 | 0.089424 | 0.15986 | 0.20002 | 0.042567 | 121.9412 | 121.9261 | 121.8788 | 121.7646 | -0.034177 | 0.004903 | 0.003135 | 0.010557 | 121.9754 | 121.938 | 121.9129 | 121.8756
2186.0781 | 122.0993 | -0.091553 | 121.9116 | 0.14932 | -0.013048 | -0.016578 | -0.020438 | 0.045421 | 0.090161 | -0.067295 | 121.8908 | 121.8849 | 121.8284 | 121.7188 | -0.079953 | -0.045451 | -0.042641 | -0.030641 | 0.24087 | 0.078505 | 0.074975 | 0.071115 | 0.13697 | 0.18171 | 0.024258 | 121.9366 | 121.9307 | 121.8742 | 121.7646 | -0.034177 | 0.000325 | 0.003135 | 0.015135 | 121.9708 | 121.9335 | 121.9084 | 121.871
2187.8281 | 121.994 | -0.10529 | 121.9574 | 0.14932 | -0.013048 | -0.021157 | -0.020438 | 0.040843 | 0.085583 | -0.062717 | 121.8954 | 121.8758 | 121.8238 | 121.7234 | -0.070797 | -0.045451 | -0.042641 | -0.030641 | 0.25461 | 0.092238 | 0.084129 | 0.084848 | 0.14613 | 0.19087 | 0.042569 | 121.9412 | 121.9215 | 121.8696 | 121.7691 | -0.025021 | 0.000325 | 0.003135 | 0.015135 | 121.9662 | 121.938 | 121.8946 | 121.8665
2189.6094 | 122.0032 | -0.11902 | 121.9528 | 0.14474 | -0.013048 | -0.012 | -0.01586 | 0.040843 | 0.081005 | -0.062717 | 121.8954 | 121.8803 | 121.8284 | 121.7234 | -0.070797 | -0.031717 | -0.042641 | -0.026063 | 0.26376 | 0.10597 | 0.10702 | 0.10316 | 0.15986 | 0.20002 | 0.056302 | 121.9412 | 121.9261 | 121.8742 | 121.7691 | -0.025021 | 0.014059 | 0.003135 | 0.019713 | 121.9662 | 121.938 | 121.8992 | 121.871
2191.2969 | 122.049 | -0.10529 | 121.9162 | 0.14932 | -0.017627 | -0.021157 | -0.025017 | 0.045421 | 0.081005 | -0.067295 | 121.8908 | 121.8849 | 121.833 | 121.7234 | -0.075375 | -0.040873 | -0.042641 | -0.026063 | 0.25461 | 0.087659 | 0.084129 | 0.080269 | 0.15071 | 0.18629 | 0.037991 | 121.9366 | 121.9307 | 121.8788 | 121.7691 | -0.029599 | 0.004903 | 0.003135 | 0.019713 | 121.9662 | 121.9335 | 121.9084 | 121.8756
2193.0469 | 122.0673 | -0.086975 | 121.9391 | 0.14932 | -0.026784 | -0.016578 | -0.020438 | 0.040843 | 0.081005 | -0.067295 | 121.8862 | 121.8941 | 121.8238 | 121.7142 | -0.079953 | -0.036295 | -0.038063 | -0.030641 | 0.2363 | 0.060191 | 0.070397 | 0.066537 | 0.12782 | 0.16798 | 0.01968 | 121.932 | 121.9398 | 121.8696 | 121.76 | -0.034177 | 0.009481 | 0.007713 | 0.015135 | 121.9662 | 121.9243 | 121.9038 | 121.8619
2194.8281 | 121.9894 | -0.13275 | 121.962 | 0.14932 | -0.008469 | -0.021157 | -0.011281 | 0.040843 | 0.090161 | -0.058139 | 121.8908 | 121.8849 | 121.833 | 121.7234 | -0.079953 | -0.040873 | -0.04722 | -0.026063 | 0.28207 | 0.12428 | 0.11159 | 0.12147 | 0.17359 | 0.22291 | 0.074612 | 121.9366 | 121.9307 | 121.8788 | 121.7691 | -0.034177 | 0.004903 | -0.001444 | 0.019713 | 121.9708 | 121.938 | 121.9129 | 121.8802
2196.5312 | 122.113 | -0.07782 | 121.907 | 0.1539 | -0.013048 | -0.016578 | -0.029595 | 0.045421 | 0.090161 | -0.071874 | 121.8908 | 121.8895 | 121.8376 | 121.7234 | -0.079953 | -0.036295 | -0.042641 | -0.030641 | 0.23172 | 0.064772 | 0.061242 | 0.048225 | 0.12324 | 0.16798 | 0.005946 | 121.9366 | 121.9353 | 121.8833 | 121.7691 | -0.034177 | 0.009481 | 0.003135 | 0.015135 | 121.9708 | 121.9335 | 121.9175 | 121.8802
2198.2812 | 122.0352 | -0.12817 | 121.9482 | 0.14932 | -0.017627 | -0.012 | -0.025017 | 0.045421 | 0.081005 | -0.062717 | 121.8954 | 121.8895 | 121.8376 | 121.7142 | -0.075375 | -0.040873 | -0.042641 | -0.021484 | 0.2775 | 0.11055 | 0.11617 | 0.10316 | 0.17359 | 0.20918 | 0.065457 | 121.9412 | 121.9353 | 121.8833 | 121.76 | -0.029599 | 0.004903 | 0.003135 | 0.024292 | 121.9708 | 121.938 | 121.9129 | 121.8802
2200.0469 | 122.0764 | -0.10071 | 121.9299 | 0.14932 | -0.017627 | -0.007421 | -0.034174 | 0.040843 | 0.090161 | -0.067295 | 121.8954 | 121.8895 | 121.833 | 121.7188 | -0.066219 | -0.036295 | -0.038063 | -0.026063 | 0.25003 | 0.083081 | 0.093287 | 0.066534 | 0.14155 | 0.19087 | 0.033413 | 121.9412 | 121.9353 | 121.8788 | 121.7646 | -0.020443 | 0.009481 | 0.007713 | 0.019713 | 121.9616 | 121.9335 | 121.8992 | 121.871
2201.8125 | 122.0398 | -0.10986 | 121.9391 | 0.15848 | -0.00389 | -0.021157 | -0.025017 | 0.040843 | 0.085583 | -0.067295 | 121.8954 | 121.8895 | 121.8376 | 121.7234 | -0.084531 | -0.031717 | -0.038063 | -0.035219 | 0.26834 | 0.10597 | 0.088706 | 0.084846 | 0.15071 | 0.19545 | 0.042568 | 121.9412 | 121.9353 | 121.8833 | 121.7691 | -0.038755 | 0.014059 | 0.007713 | 0.010557 | 121.9799 | 121.9335 | 121.9221 | 121.8756
2203.5156 | 121.9894 | -0.1236 | 121.9666 | 0.14932 | -0.013048 | -0.021157 | -0.025017 | 0.045421 | 0.085583 | -0.058139 | 121.8954 | 121.8895 | 121.833 | 121.7234 | -0.075375 | -0.036295 | -0.04722 | -0.026063 | 0.27292 | 0.11055 | 0.10244 | 0.098579 | 0.16902 | 0.20918 | 0.065457 | 121.9412 | 121.9353 | 121.8788 | 121.7691 | -0.029599 | 0.009481 | -0.001444 | 0.019713 | 121.9708 | 121.9426 | 121.9084 | 121.8802
2205.2656 | 122.0306 | -0.1236 | 121.9391 | 0.14474 | -0.013048 | -0.016578 | -0.029595 | 0.040843 | 0.090161 | -0.071874 | 121.8908 | 121.8895 | 121.8238 | 121.7279 | -0.075375 | -0.040873 | -0.033484 | -0.016906 | 0.26834 | 0.11055 | 0.10702 | 0.094001 | 0.16444 | 0.21376 | 0.051722 | 121.9366 | 121.9353 | 121.8696 | 121.7737 | -0.029599 | 0.004903 | 0.012292 | 0.02887 | 121.9662 | 121.9243 | 121.8992 | 121.8573
2207.0312 | 122.0535 | -0.09613 | 121.9116 | 0.15848 | -0.013048 | -0.016578 | -0.029595 | 0.036265 | 0.076426 | -0.062717 | 121.8908 | 121.8803 | 121.8376 | 121.7142 | -0.070797 | -0.031717 | -0.042641 | -0.026063 | 0.25461 | 0.083082 | 0.079552 | 0.066535 | 0.13239 | 0.17256 | 0.033413 | 121.9366 | 121.9261 | 121.8833 | 121.76 | -0.025021 | 0.014059 | 0.003135 | 0.019713 | 121.9616 | 121.9335 | 121.9084 | 121.8802
2208.7969 | 122.0764 | -0.068665 | 121.9528 | 0.14017 | -0.013048 | -0.016578 | -0.020438 | 0.040843 | 0.081005 | -0.067295 | 121.8954 | 121.8895 | 121.8376 | 121.7279 | -0.075375 | -0.036295 | -0.04722 | -0.026063 | 0.20883 | 0.055617 | 0.052087 | 0.048227 | 0.10951 | 0.14967 | 0.00137 | 121.9412 | 121.9353 | 121.8833 | 121.7737 | -0.029599 | 0.009481 | -0.001444 | 0.019713 | 121.9708 | 121.9426 | 121.9129 | 121.8848
2210.5 | 122.0901 | -0.086975 | 121.9299 | 0.14474 | -0.026784 | -0.021157 | -0.029595 | 0.045421 | 0.081005 | -0.067295 | 121.9 | 121.8895 | 121.833 | 121.7234 | -0.075375 | -0.040873 | -0.038063 | -0.026063 | 0.23172 | 0.060191 | 0.065818 | 0.05738 | 0.1324 | 0.16798 | 0.01968 | 121.9458 | 121.9353 | 121.8788 | 121.7691 | -0.029599 | 0.004903 | 0.007713 | 0.019713 | 121.9754 | 121.938 | 121.9084 | 121.871
2212.2656 | 122.0627 | -0.10071 | 121.9528 | 0.14932 | -0.008469 | -0.016578 | -0.029595 | 0.040843 | 0.085583 | -0.062717 | 121.9 | 121.8895 | 121.8284 | 121.7188 | -0.079953 | -0.040873 | -0.042641 | -0.026063 | 0.25003 | 0.092239 | 0.08413 | 0.071113 | 0.14155 | 0.18629 | 0.037991 | 121.9458 | 121.9353 | 121.8742 | 121.7646 | -0.034177 | 0.004903 | 0.003135 | 0.019713 | 121.9799 | 121.9426 | 121.9084 | 121.871
2214.0312 | 122.1085 | -0.059509 | 121.9299 | 0.14932 | -0.017627 | -0.021157 | -0.029595 | 0.040843 | 0.081005 | -0.067295 | 121.9 | 121.8849 | 121.8284 | 121.7188 | -0.070797 | -0.045451 | -0.038063 | -0.030641 | 0.20883 | 0.041882 | 0.038352 | 0.029914 | 0.10035 | 0.14051 | -0.007786 | 121.9458 | 121.9307 | 121.8742 | 121.7646 | -0.025021 | 0.000325 | 0.007713 | 0.015135 | 121.9708 | 121.938 | 121.8992 | 121.8665
2215.75 | 122.0673 | -0.064087 | 121.9025 | 0.14932 | -0.013048 | -0.012 | -0.025017 | 0.045421 | 0.076426 | -0.062717 | 121.9046 | 121.8895 | 121.833 | 121.7188 | -0.070797 | -0.036295 | -0.038063 | -0.035219 | 0.21341 | 0.051039 | 0.052087 | 0.03907 | 0.10951 | 0.14051 | 0.00137 | 121.9503 | 121.9353 | 121.8788 | 121.7646 | -0.025021 | 0.009481 | 0.007713 | 0.010557 | 121.9754 | 121.9426 | 121.9038 | 121.871
2217.5 | 122.1085 | -0.064087 | 121.9208 | 0.1539 | -0.017627 | -0.016578 | -0.020438 | 0.040843 | 0.081005 | -0.062717 | 121.9 | 121.8941 | 121.8284 | 121.7279 | -0.075375 | -0.040873 | -0.04722 | -0.026063 | 0.21799 | 0.04646 | 0.047509 | 0.043649 | 0.10493 | 0.14509 | 0.00137 | 121.9458 | 121.9398 | 121.8742 | 121.7737 | -0.029599 | 0.004903 | -0.001444 | 0.019713 | 121.9754 | 121.9472 | 121.9038 | 121.8756
2219.2656 | 122.0947 | -0.10071 | 121.9299 | 0.14932 | -0.017627 | -0.021157 | -0.029595 | 0.036265 | 0.081005 | -0.067295 | 121.8908 | 121.8941 | 121.8376 | 121.7234 | -0.070797 | -0.036295 | -0.04722 | -0.026063 | 0.25003 | 0.083081 | 0.079551 | 0.071113 | 0.13697 | 0.18171 | 0.033413 | 121.9366 | 121.9398 | 121.8833 | 121.7691 | -0.025021 | 0.009481 | -0.001444 | 0.019713 | 121.9616 | 121.938 | 121.9084 | 121.8848
2220.9844 | 122.0993 | -0.073242 | 121.8933 | 0.14932 | -0.008469 | -0.016578 | -0.020438 | 0.045421 | 0.085583 | -0.071874 | 121.9 | 121.8941 | 121.8376 | 121.7188 | -0.066219 | -0.045451 | -0.04722 | -0.026063 | 0.22256 | 0.064773 | 0.056664 | 0.052804 | 0.11866 | 0.15882 | 0.001368 | 121.9458 | 121.9398 | 121.8833 | 121.7646 | -0.020443 | 0.000325 | -0.001444 | 0.019713 | 121.9662 | 121.9472 | 121.9038 | 121.8848
2222.75 | 122.0856 | -0.086975 | 121.9437 | 0.14474 | -0.013048 | -0.021157 | -0.029595 | 0.045421 | 0.081005 | -0.076452 | 121.8954 | 121.8895 | 121.8284 | 121.7279 | -0.079953 | -0.040873 | -0.042641 | -0.026063 | 0.23172 | 0.073927 | 0.065818 | 0.05738 | 0.1324 | 0.16798 | 0.010523 | 121.9412 | 121.9353 | 121.8742 | 121.7737 | -0.034177 | 0.004903 | 0.003135 | 0.019713 | 121.9754 | 121.938 | 121.9084 | 121.871
2224.5156 | 121.994 | -0.14191 | 121.9482 | 0.1539 | -0.013048 | -0.021157 | -0.029595 | 0.045421 | 0.090161 | -0.062717 | 121.9046 | 121.8895 | 121.833 | 121.7279 | -0.075375 | -0.040873 | -0.04722 | -0.026063 | 0.29581 | 0.12886 | 0.12075 | 0.11231 | 0.18733 | 0.23207 | 0.07919 | 121.9503 | 121.9353 | 121.8788 | 121.7737 | -0.029599 | 0.004903 | -0.001444 | 0.019713 | 121.9799 | 121.9518 | 121.9084 | 121.8802
2226.2188 | 122.0901 | -0.082397 | 121.9025 | 0.13101 | -0.013048 | -0.012 | -0.029595 | 0.040843 | 0.081005 | -0.071874 | 121.9 | 121.8986 | 121.8284 | 121.7234 | -0.070797 | -0.036295 | -0.04722 | -0.026063 | 0.21341 | 0.069349 | 0.070397 | 0.052802 | 0.12324 | 0.1634 | 0.010523 | 121.9458 | 121.9444 | 121.8742 | 121.7691 | -0.025021 | 0.009481 | -0.001444 | 0.019713 | 121.9708 | 121.9472 | 121.8992 | 121.8756
2227.9844 | 122.0718 | -0.09613 | 121.9482 | 0.1539 | -0.026784 | -0.021157 | -0.029595 | 0.040843 | 0.081005 | -0.062717 | 121.9046 | 121.8895 | 121.8284 | 121.7234 | -0.075375 | -0.040873 | -0.04722 | -0.026063 | 0.25003 | 0.069346 | 0.074973 | 0.066535 | 0.13697 | 0.17713 | 0.033413 | 121.9503 | 121.9353 | 121.8742 | 121.7691 | -0.029599 | 0.004903 | -0.001444 | 0.019713 | 121.9799 | 121.9518 | 121.9038 | 121.8756
2229.7031 | 122.0764 | -0.091553 | 121.9345 | 0.14932 | -0.017627 | -0.012 | -0.020438 | 0.040843 | 0.085583 | -0.071874 | 121.8954 | 121.8895 | 121.8284 | 121.7279 | -0.070797 | -0.040873 | -0.042641 | -0.026063 | 0.24087 | 0.073926 | 0.079553 | 0.071115 | 0.1324 | 0.17714 | 0.019679 | 121.9412 | 121.9353 | 121.8742 | 121.7737 | -0.025021 | 0.004903 | 0.003135 | 0.019713 | 121.9662 | 121.938 | 121.8992 | 121.871
2231.4688 | 122.0856 | -0.07782 | 121.9254 | 0.14932 | -0.013048 | -0.016578 | -0.029595 | 0.036265 | 0.076426 | -0.071874 | 121.9046 | 121.8895 | 121.833 | 121.7279 | -0.070797 | -0.040873 | -0.051798 | -0.035219 | 0.22714 | 0.064772 | 0.061242 | 0.048225 | 0.11408 | 0.15425 | 0.005946 | 121.9503 | 121.9353 | 121.8788 | 121.7737 | -0.025021 | 0.004903 | -0.006022 | 0.010557 | 121.9754 | 121.9564 | 121.9038 | 121.8848
2233.1719 | 121.9803 | -0.11902 | 121.9666 | 0.14017 | -0.008469 | -0.016578 | -0.029595 | 0.040843 | 0.085583 | -0.067295 | 121.8954 | 121.8941 | 121.8284 | 121.7234 | -0.08911 | -0.040873 | -0.04722 | -0.030641 | 0.25918 | 0.11055 | 0.10244 | 0.089424 | 0.15986 | 0.2046 | 0.051724 | 121.9412 | 121.9398 | 121.8742 | 121.7691 | -0.043334 | 0.004903 | -0.001444 | 0.015135 | 121.9845 | 121.9426 | 121.9175 | 121.8756
2234.9375 | 122.0947 | -0.082397 | 121.9025 | 0.14017 | -0.017627 | -0.021157 | -0.025017 | 0.031687 | 0.081005 | -0.062717 | 121.9046 | 121.8941 | 121.833 | 121.7279 | -0.079953 | -0.036295 | -0.042641 | -0.026063 | 0.22256 | 0.06477 | 0.06124 | 0.05738 | 0.11408 | 0.1634 | 0.01968 | 121.9503 | 121.9398 | 121.8788 | 121.7737 | -0.034177 | 0.009481 | 0.003135 | 0.019713 | 121.9845 | 121.9472 | 121.9129 | 121.8756
2236.6406 | 122.0947 | -0.07782 | 121.9528 | 0.1539 | -0.008469 | -0.016578 | -0.01586 | 0.031687 | 0.081005 | -0.076452 | 121.9046 | 121.8895 | 121.833 | 121.7188 | -0.070797 | -0.040873 | -0.042641 | -0.021484 | 0.23172 | 0.069351 | 0.061242 | 0.06196 | 0.10951 | 0.15882 | 0.001368 | 121.9503 | 121.9353 | 121.8788 | 121.7646 | -0.025021 | 0.004903 | 0.003135 | 0.024292 | 121.9754 | 121.9472 | 121.9038 | 121.8756
2238.3906 | 122.1313 | -0.086975 | 121.8979 | 0.14932 | -0.013048 | -0.021157 | -0.025017 | 0.040843 | 0.081005 | -0.071874 | 121.8954 | 121.8941 | 121.8376 | 121.7234 | -0.079953 | -0.040873 | -0.042641 | -0.030641 | 0.2363 | 0.073927 | 0.065818 | 0.061958 | 0.12782 | 0.16798 | 0.015101 | 121.9412 | 121.9398 | 121.8833 | 121.7691 | -0.034177 | 0.004903 | 0.003135 | 0.015135 | 121.9754 | 121.938 | 121.9175 | 121.8802
2240.1562 | 122.1268 | -0.068665 | 121.9299 | 0.14474 | -0.013048 | -0.016578 | -0.034174 | 0.031687 | 0.081005 | -0.067295 | 121.9 | 121.8895 | 121.833 | 121.7325 | -0.070797 | -0.036295 | -0.042641 | -0.026063 | 0.21341 | 0.055617 | 0.052087 | 0.034491 | 0.10035 | 0.14967 | 0.00137 | 121.9458 | 121.9353 | 121.8788 | 121.7783 | -0.025021 | 0.009481 | 0.003135 | 0.019713 | 121.9708 | 121.9426 | 121.9038 | 121.8756
2241.8594 | 121.9711 | -0.13275 | 121.9391 | 0.14474 | -0.008469 | -0.021157 | -0.020438 | 0.040843 | 0.085583 | -0.067295 | 121.9046 | 121.9032 | 121.833 | 121.7279 | -0.079953 | -0.040873 | -0.038063 | -0.026063 | 0.27749 | 0.12428 | 0.11159 | 0.11231 | 0.17359 | 0.21833 | 0.065456 | 121.9503 | 121.949 | 121.8788 | 121.7737 | -0.034177 | 0.004903 | 0.007713 | 0.019713 | 121.9845 | 121.9426 | 121.9129 | 121.871
2243.625 | 122.0123 | -0.12817 | 121.9803 | 0.14932 | -0.013048 | -0.016578 | -0.020438 | 0.040843 | 0.085583 | -0.071874 | 121.8954 | 121.8986 | 121.8284 | 121.7279 | -0.079953 | -0.040873 | -0.038063 | -0.030641 | 0.2775 | 0.11513 | 0.1116 | 0.10774 | 0.16902 | 0.21376 | 0.0563 | 121.9412 | 121.9444 | 121.8742 | 121.7737 | -0.034177 | 0.004903 | 0.007713 | 0.015135 | 121.9754 | 121.9335 | 121.9084 | 121.8665
2245.3281 | 122.0993 | -0.068665 | 121.9254 | 0.14932 | -0.013048 | -0.016578 | -0.029595 | 0.036265 | 0.085583 | -0.076452 | 121.9091 | 121.8941 | 121.833 | 121.7325 | -0.075375 | -0.040873 | -0.042641 | -0.026063 | 0.21799 | 0.055617 | 0.052087 | 0.03907 | 0.10493 | 0.15425 | -0.007787 | 121.9549 | 121.9398 | 121.8788 | 121.7783 | -0.029599 | 0.004903 | 0.003135 | 0.019713 | 121.9845 | 121.9518 | 121.9084 | 121.8756
2247.0781 | 122.049 | -0.09613 | 121.9254 | 0.14932 | -0.013048 | -0.016578 | -0.029595 | 0.031687 | 0.085583 | -0.067295 | 121.9091 | 121.8941 | 121.8421 | 121.7325 | -0.070797 | -0.031717 | -0.038063 | -0.030641 | 0.24545 | 0.083082 | 0.079552 | 0.066535 | 0.12782 | 0.18171 | 0.028835 | 121.9549 | 121.9398 | 121.8879 | 121.7783 | -0.025021 | 0.014059 | 0.007713 | 0.015135 | 121.9799 | 121.9472 | 121.9129 | 121.8802
2248.8281 | 122.113 | -0.091553 | 121.907 | 0.14474 | -0.013048 | -0.021157 | -0.025017 | 0.036265 | 0.085583 | -0.067295 | 121.8954 | 121.8941 | 121.8376 | 121.7188 | -0.070797 | -0.036295 | -0.042641 | -0.021484 | 0.2363 | 0.078505 | 0.070396 | 0.066536 | 0.12782 | 0.17714 | 0.024258 | 121.9412 | 121.9398 | 121.8833 | 121.7646 | -0.025021 | 0.009481 | 0.003135 | 0.024292 | 121.9662 | 121.938 | 121.9084 | 121.8802
2250.5312 | 122.081 | -0.09613 | 121.9162 | 0.14932 | -0.022205 | -0.016578 | -0.029595 | 0.040843 | 0.085583 | -0.062717 | 121.9 | 121.8941 | 121.833 | 121.7234 | -0.075375 | -0.036295 | -0.038063 | -0.026063 | 0.24545 | 0.073925 | 0.079552 | 0.066535 | 0.13697 | 0.18171 | 0.033413 | 121.9458 | 121.9398 | 121.8788 | 121.7691 | -0.029599 | 0.009481 | 0.007713 | 0.019713 | 121.9754 | 121.938 | 121.9084 | 121.871
2252.3125 | 121.994 | -0.10986 | 121.9482 | 0.14474 | -0.013048 | -0.021157 | -0.025017 | 0.040843 | 0.081005 | -0.076452 | 121.9091 | 121.8986 | 121.8421 | 121.7325 | -0.070797 | -0.036295 | -0.042641 | -0.030641 | 0.25461 | 0.096815 | 0.088706 | 0.084846 | 0.15071 | 0.19087 | 0.033411 | 121.9549 | 121.9444 | 121.8879 | 121.7783 | -0.025021 | 0.009481 | 0.003135 | 0.015135 | 121.9799 | 121.9518 | 121.9129 | 121.8848
2254.0156 | 122.1085 | -0.091553 | 121.9254 | 0.14017 | -0.017627 | -0.021157 | -0.025017 | 0.040843 | 0.076426 | -0.062717 | 121.9046 | 121.9032 | 121.8376 | 121.7279 | -0.070797 | -0.040873 | -0.042641 | -0.030641 | 0.23172 | 0.073926 | 0.070396 | 0.066536 | 0.1324 | 0.16798 | 0.028836 | 121.9503 | 121.949 | 121.8833 | 121.7737 | -0.025021 | 0.004903 | 0.003135 | 0.015135 | 121.9754 | 121.9472 | 121.9084 | 121.8802
2255.7812 | 121.9894 | -0.11444 | 121.9528 | 0.14932 | -0.008469 | -0.016578 | -0.020438 | 0.036265 | 0.081005 | -0.067295 | 121.9 | 121.9032 | 121.833 | 121.7279 | -0.079953 | -0.036295 | -0.042641 | -0.026063 | 0.26376 | 0.10597 | 0.097863 | 0.094003 | 0.15071 | 0.19545 | 0.047146 | 121.9458 | 121.949 | 121.8788 | 121.7737 | -0.034177 | 0.009481 | 0.003135 | 0.019713 | 121.9799 | 121.9426 | 121.9129 | 121.8756
2257.5312 | 121.9803 | -0.09613 | 121.9482 | 0.14932 | -0.013048 | -0.021157 | -0.025017 | 0.045421 | 0.085583 | -0.067295 | 121.9091 | 121.9032 | 121.833 | 121.7417 | -0.075375 | -0.031717 | -0.051798 | -0.030641 | 0.24545 | 0.083082 | 0.074973 | 0.071113 | 0.14155 | 0.18171 | 0.028835 | 121.9549 | 121.949 | 121.8788 | 121.7874 | -0.029599 | 0.014059 | -0.006022 | 0.015135 | 121.9845 | 121.9609 | 121.9084 | 121.8848
2259.2969 | 121.9986 | -0.1236 | 121.9574 | 0.1539 | -0.017627 | -0.007421 | -0.025017 | 0.040843 | 0.081005 | -0.062717 | 121.9 | 121.9032 | 121.8421 | 121.7279 | -0.079953 | -0.036295 | -0.042641 | -0.030641 | 0.2775 | 0.10597 | 0.11618 | 0.098579 | 0.16444 | 0.2046 | 0.060879 | 121.9458 | 121.949 | 121.8879 | 121.7737 | -0.034177 | 0.009481 | 0.003135 | 0.015135 | 121.9799 | 121.9426 | 121.9221 | 121.8848
2261 | 122.1176 | -0.064087 | 121.9254 | 0.14932 | -0.008469 | -0.012 | -0.025017 | 0.045421 | 0.090161 | -0.067295 | 121.9046 | 121.8986 | 121.8376 | 121.7279 | -0.079953 | -0.036295 | -0.038063 | -0.016906 | 0.21341 | 0.055618 | 0.052087 | 0.03907 | 0.10951 | 0.15425 | -0.003208 | 121.9503 | 121.9444 | 121.8833 | 121.7737 | -0.034177 | 0.009481 | 0.007713 | 0.02887 | 121.9845 | 121.9426 | 121.9175 | 121.8756
2262.7656 | 122.1085 | -0.07782 | 121.9025 | 0.14017 | -0.008469 | -0.021157 | -0.025017 | 0.040843 | 0.090161 | -0.067295 | 121.9046 | 121.8941 | 121.8376 | 121.7325 | -0.070797 | -0.040873 | -0.042641 | -0.035219 | 0.21799 | 0.069351 | 0.056663 | 0.052803 | 0.11866 | 0.16798 | 0.010525 | 121.9503 | 121.9398 | 121.8833 | 121.7783 | -0.025021 | 0.004903 | 0.003135 | 0.010557 | 121.9754 | 121.9472 | 121.9084 | 121.8802
2264.5312 | 122.0398 | -0.10529 | 121.9528 | 0.14932 | -0.008469 | -0.021157 | -0.020438 | 0.040843 | 0.076426 | -0.071874 | 121.9091 | 121.8986 | 121.8376 | 121.7325 | -0.070797 | -0.031717 | -0.038063 | -0.026063 | 0.25461 | 0.096817 | 0.084129 | 0.084848 | 0.14613 | 0.18171 | 0.033412 | 121.9549 | 121.9444 | 121.8833 | 121.7783 | -0.025021 | 0.014059 | 0.007713 | 0.019713 | 121.9799 | 121.9472 | 121.9084 | 121.8756
2266.25 | 122.113 | -0.086975 | 121.9482 | 0.14017 | -0.013048 | -0.012 | -0.025017 | 0.031687 | 0.085583 | -0.067295 | 121.9091 | 121.9032 | 121.8421 | 121.7279 | -0.079953 | -0.045451 | -0.04722 | -0.021484 | 0.22714 | 0.073927 | 0.074975 | 0.061958 | 0.11866 | 0.17256 | 0.01968 | 121.9549 | 121.949 | 121.8879 | 121.7737 | -0.034177 | 0.000325 | -0.001444 | 0.024292 | 121.9891 | 121.9564 | 121.9221 | 121.8894
2268 | 122.1222 | -0.07782 | 121.9254 | 0.14474 | -0.008469 | -0.021157 | -0.025017 | 0.040843 | 0.085583 | -0.062717 | 121.9046 | 121.8986 | 121.8376 | 121.7234 | -0.075375 | -0.036295 | -0.042641 | -0.026063 | 0.22256 | 0.069351 | 0.056663 | 0.052803 | 0.11866 | 0.1634 | 0.015103 | 121.9503 | 121.9444 | 121.8833 | 121.7691 | -0.029599 | 0.009481 | 0.003135 | 0.019713 | 121.9799 | 121.9472 | 121.9129 | 121.8802
2269.7656 | 122.0718 | -0.07782 | 121.9299 | 0.14932 | -0.013048 | -0.021157 | -0.025017 | 0.040843 | 0.081005 | -0.062717 | 121.9046 | 121.9078 | 121.8421 | 121.7279 | -0.070797 | -0.036295 | -0.04722 | -0.021484 | 0.22714 | 0.064772 | 0.056663 | 0.052803 | 0.11866 | 0.15882 | 0.015103 | 121.9503 | 121.9536 | 121.8879 | 121.7737 | -0.025021 | 0.009481 | -0.001444 | 0.024292 | 121.9754 | 121.9518 | 121.9129 | 121.8894
2271.4688 | 122.0306 | -0.10986 | 121.9757 | 0.14932 | -0.013048 | -0.012 | -0.025017 | 0.040843 | 0.090161 | -0.071874 | 121.9091 | 121.8986 | 121.833 | 121.7325 | -0.070797 | -0.040873 | -0.042641 | -0.016906 | 0.25918 | 0.096815 | 0.097863 | 0.084846 | 0.15071 | 0.20002 | 0.037989 | 121.9549 | 121.9444 | 121.8788 | 121.7783 | -0.025021 | 0.004903 | 0.003135 | 0.02887 | 121.9799 | 121.9518 | 121.9038 | 121.8756
2273.2344 | 121.9986 | -0.10986 | 121.9437 | 0.1539 | -0.008469 | -0.021157 | -0.025017 | 0.036265 | 0.090161 | -0.071874 | 121.9091 | 121.9032 | 121.8421 | 121.7279 | -0.079953 | -0.031717 | -0.038063 | -0.026063 | 0.26376 | 0.10139 | 0.088706 | 0.084846 | 0.14613 | 0.20002 | 0.037989 | 121.9549 | 121.949 | 121.8879 | 121.7737 | -0.034177 | 0.014059 | 0.007713 | 0.019713 | 121.9891 | 121.9472 | 121.9221 | 121.8802
2274.9844 | 122.0123 | -0.1236 | 121.9437 | 0.1539 | -0.013048 | -0.016578 | -0.020438 | 0.036265 | 0.085583 | -0.058139 | 121.9046 | 121.8986 | 121.8376 | 121.7371 | -0.075375 | -0.040873 | -0.042641 | -0.026063 | 0.2775 | 0.11055 | 0.10702 | 0.10316 | 0.15986 | 0.20918 | 0.065457 | 121.9503 | 121.9444 | 121.8833 | 121.7829 | -0.029599 | 0.004903 | 0.003135 | 0.019713 | 121.9799 | 121.9472 | 121.9129 | 121.8802
2276.75 | 122.1313 | -0.082397 | 121.9299 | 0.1539 | -0.00389 | -0.016578 | -0.025017 | 0.040843 | 0.085583 | -0.071874 | 121.9091 | 121.9078 | 121.8467 | 121.7325 | -0.070797 | -0.036295 | -0.042641 | -0.030641 | 0.2363 | 0.078507 | 0.065819 | 0.05738 | 0.12324 | 0.16798 | 0.010523 | 121.9549 | 121.9536 | 121.8925 | 121.7783 | -0.025021 | 0.009481 | 0.003135 | 0.015135 | 121.9799 | 121.9518 | 121.9175 | 121.8894
2278.4531 | 122.1313 | -0.068665 | 121.9116 | 0.14474 | -0.017627 | -0.021157 | -0.020438 | 0.045421 | 0.085583 | -0.067295 | 121.9091 | 121.9032 | 121.8376 | 121.7371 | -0.075375 | -0.040873 | -0.04722 | -0.026063 | 0.21341 | 0.051038 | 0.047508 | 0.048227 | 0.11409 | 0.15425 | 0.00137 | 121.9549 | 121.949 | 121.8833 | 121.7829 | -0.029599 | 0.004903 | -0.001444 | 0.019713 | 121.9845 | 121.9564 | 121.9129 | 121.8848
2280.2031 | 122.1085 | -0.068665 | 121.9162 | 0.14932 | -0.013048 | -0.016578 | -0.025017 | 0.031687 | 0.085583 | -0.067295 | 121.9091 | 121.9078 | 121.8421 | 121.7325 | -0.070797 | -0.040873 | -0.042641 | -0.026063 | 0.21799 | 0.055617 | 0.052087 | 0.043648 | 0.10035 | 0.15425 | 0.00137 | 121.9549 | 121.9536 | 121.8879 | 121.7783 | -0.025021 | 0.004903 | 0.003135 | 0.019713 | 121.9799 | 121.9518 | 121.9129 | 121.8848
2281.9531 | 122.0718 | -0.073242 | 121.9116 | 0.14932 | -0.013048 | -0.016578 | -0.025017 | 0.031687 | 0.081005 | -0.071874 | 121.9091 | 121.8986 | 121.8376 | 121.7371 | -0.075375 | -0.036295 | -0.038063 | -0.021484 | 0.22256 | 0.060194 | 0.056664 | 0.048225 | 0.10493 | 0.15425 | 0.001368 | 121.9549 | 121.9444 | 121.8833 | 121.7829 | -0.029599 | 0.009481 | 0.007713 | 0.024292 | 121.9845 | 121.9472 | 121.9129 | 121.8756
2283.7188 | 122.0947 | -0.091553 | 121.9391 | 0.14932 | -0.008469 | -0.021157 | -0.025017 | 0.036265 | 0.081005 | -0.062717 | 121.9137 | 121.8986 | 121.8467 | 121.7325 | -0.070797 | -0.036295 | -0.042641 | -0.035219 | 0.24087 | 0.083084 | 0.070396 | 0.066536 | 0.12782 | 0.17256 | 0.028836 | 121.9595 | 121.9444 | 121.8925 | 121.7783 | -0.025021 | 0.009481 | 0.003135 | 0.010557 | 121.9845 | 121.9564 | 121.9175 | 121.8894
2285.4219 | 122.0673 | -0.086975 | 121.9208 | 0.14932 | -0.013048 | -0.016578 | -0.029595 | 0.040843 | 0.085583 | -0.067295 | 121.9183 | 121.9032 | 121.8421 | 121.7417 | -0.075375 | -0.040873 | -0.042641 | -0.030641 | 0.2363 | 0.073927 | 0.070397 | 0.05738 | 0.12782 | 0.17256 | 0.01968 | 121.9641 | 121.949 | 121.8879 | 121.7874 | -0.029599 | 0.004903 | 0.003135 | 0.015135 | 121.9937 | 121.9609 | 121.9175 | 121.8848
2287.1719 | 122.0993 | -0.086975 | 121.9254 | 0.14474 | -0.008469 | -0.025735 | -0.029595 | 0.031687 | 0.090161 | -0.067295 | 121.9137 | 121.9078 | 121.8467 | 121.7371 | -0.075375 | -0.036295 | -0.04722 | -0.026063 | 0.23172 | 0.078506 | 0.06124 | 0.05738 | 0.11866 | 0.17714 | 0.01968 | 121.9595 | 121.9536 | 121.8925 | 121.7829 | -0.029599 | 0.009481 | -0.001444 | 0.019713 | 121.9891 | 121.9609 | 121.9221 | 121.8939
2288.9219 | 122.1405 | -0.068665 | 121.907 | 0.14474 | -0.017627 | -0.025735 | -0.01586 | 0.036265 | 0.081005 | -0.071874 | 121.9091 | 121.9078 | 121.8376 | 121.7371 | -0.070797 | -0.036295 | -0.04722 | -0.026063 | 0.21341 | 0.051038 | 0.04293 | 0.052805 | 0.10493 | 0.14967 | -0.003209 | 121.9549 | 121.9536 | 121.8833 | 121.7829 | -0.025021 | 0.009481 | -0.001444 | 0.019713 | 121.9799 | 121.9564 | 121.9084 | 121.8848
2290.625 | 122.1176 | -0.091553 | 121.9391 | 0.14932 | -0.008469 | -0.016578 | -0.029595 | 0.036265 | 0.085583 | -0.076452 | 121.9091 | 121.9032 | 121.8376 | 121.7325 | -0.084531 | -0.040873 | -0.042641 | -0.021484 | 0.24087 | 0.083084 | 0.074975 | 0.061958 | 0.12782 | 0.17714 | 0.015101 | 121.9549 | 121.949 | 121.8833 | 121.7783 | -0.038755 | 0.004903 | 0.003135 | 0.024292 | 121.9937 | 121.9518 | 121.9221 | 121.8802
2292.375 | 122.0901 | -0.091553 | 121.9528 | 0.1539 | -0.008469 | -0.012 | -0.020438 | 0.049999 | 0.081005 | -0.076452 | 121.9091 | 121.9078 | 121.8467 | 121.7417 | -0.079953 | -0.036295 | -0.056376 | -0.030641 | 0.24545 | 0.083084 | 0.079553 | 0.071115 | 0.14155 | 0.17256 | 0.015101 | 121.9549 | 121.9536 | 121.8925 | 121.7874 | -0.034177 | 0.009481 | -0.0106 | 0.015135 | 121.9891 | 121.9655 | 121.9267 | 121.9031
2294.1406 | 122.0352 | -0.10071 | 121.9391 | 0.1539 | -0.013048 | -0.021157 | -0.025017 | 0.040843 | 0.090161 | -0.067295 | 121.9137 | 121.9032 | 121.8467 | 121.7325 | -0.075375 | -0.040873 | -0.038063 | -0.026063 | 0.25461 | 0.08766 | 0.079551 | 0.075691 | 0.14155 | 0.19087 | 0.033413 | 121.9595 | 121.949 | 121.8925 | 121.7783 | -0.029599 | 0.004903 | 0.007713 | 0.019713 | 121.9891 | 121.9518 | 121.9221 | 121.8848
2295.9219 | 121.9803 | -0.10986 | 121.9757 | 0.15848 | -0.013048 | -0.012 | -0.029595 | 0.031687 | 0.085583 | -0.062717 | 121.9091 | 121.9078 | 121.8421 | 121.7325 | -0.079953 | -0.036295 | -0.051798 | -0.030641 | 0.26834 | 0.096815 | 0.097863 | 0.080268 | 0.14155 | 0.19545 | 0.047146 | 121.9549 | 121.9536 | 121.8879 | 121.7783 | -0.034177 | 0.009481 | -0.006022 | 0.015135 | 121.9891 | 121.9609 | 121.9221 | 121.8939
2297.6875 | 122.1222 | -0.068665 | 121.907 | 0.14474 | -0.008469 | -0.016578 | -0.029595 | 0.040843 | 0.081005 | -0.071874 | 121.9183 | 121.9032 | 121.8513 | 121.7371 | -0.070797 | -0.040873 | -0.04722 | -0.030641 | 0.21341 | 0.060196 | 0.052087 | 0.03907 | 0.10951 | 0.14967 | -0.003209 | 121.9641 | 121.949 | 121.8971 | 121.7829 | -0.025021 | 0.004903 | -0.001444 | 0.015135 | 121.9891 | 121.9655 | 121.9221 | 121.8985
2299.3906 | 122.0764 | -0.10071 | 121.9574 | 0.14017 | -0.008469 | -0.021157 | -0.029595 | 0.031687 | 0.090161 | -0.076452 | 121.9091 | 121.9078 | 121.8467 | 121.7325 | -0.075375 | -0.040873 | -0.04722 | -0.021484 | 0.24087 | 0.092239 | 0.079551 | 0.071113 | 0.1324 | 0.19087 | 0.024256 | 121.9549 | 121.9536 | 121.8925 | 121.7783 | -0.029599 | 0.004903 | -0.001444 | 0.024292 | 121.9845 | 121.9564 | 121.9221 | 121.8939
2301.1719 | 122.0627 | -0.073242 | 121.9299 | 0.14932 | -0.00389 | -0.016578 | -0.029595 | 0.040843 | 0.076426 | -0.062717 | 121.9091 | 121.9032 | 121.8513 | 121.7417 | -0.070797 | -0.040873 | -0.04722 | -0.021484 | 0.22256 | 0.069352 | 0.056664 | 0.043647 | 0.11408 | 0.14967 | 0.010525 | 121.9549 | 121.949 | 121.8971 | 121.7874 | -0.025021 | 0.004903 | -0.001444 | 0.024292 | 121.9799 | 121.9564 | 121.9221 | 121.8985
2302.9375 | 122.0627 | -0.082397 | 121.9528 | 0.14932 | -0.013048 | -0.021157 | -0.025017 | 0.040843 | 0.081005 | -0.067295 | 121.9137 | 121.9078 | 121.8421 | 121.7417 | -0.070797 | -0.040873 | -0.042641 | -0.030641 | 0.23172 | 0.069349 | 0.06124 | 0.05738 | 0.12324 | 0.1634 | 0.015102 | 121.9595 | 121.9536 | 121.8879 | 121.7874 | -0.025021 | 0.004903 | 0.003135 | 0.015135 | 121.9845 | 121.9564 | 121.9129 | 121.8848
2304.7031 | 122.0123 | -0.09613 | 121.9574 | 0.1539 | -0.008469 | -0.016578 | -0.025017 | 0.036265 | 0.085583 | -0.067295 | 121.9046 | 121.9032 | 121.8513 | 121.7417 | -0.070797 | -0.040873 | -0.042641 | -0.021484 | 0.25003 | 0.087661 | 0.079552 | 0.071113 | 0.13239 | 0.18171 | 0.028835 | 121.9503 | 121.949 | 121.8971 | 121.7874 | -0.025021 | 0.004903 | 0.003135 | 0.024292 | 121.9754 | 121.9472 | 121.9221 | 121.8939
2306.4844 | 122.0032 | -0.11444 | 121.9574 | 0.15848 | -0.008469 | -0.021157 | -0.025017 | 0.040843 | 0.081005 | -0.062717 | 121.9137 | 121.9078 | 121.8467 | 121.7325 | -0.084531 | -0.036295 | -0.042641 | -0.030641 | 0.27292 | 0.10597 | 0.093284 | 0.089424 | 0.15528 | 0.19545 | 0.051724 | 121.9595 | 121.9536 | 121.8925 | 121.7783 | -0.038755 | 0.009481 | 0.003135 | 0.015135 | 121.9982 | 121.9564 | 121.9312 | 121.8894
2308.25 | 122.081 | -0.086975 | 121.9254 | 0.1539 | -0.008469 | -0.021157 | -0.029595 | 0.036265 | 0.081005 | -0.076452 | 121.9137 | 121.9124 | 121.8421 | 121.7371 | -0.075375 | -0.040873 | -0.042641 | -0.026063 | 0.24088 | 0.078506 | 0.065818 | 0.05738 | 0.12324 | 0.16798 | 0.010523 | 121.9595 | 121.9582 | 121.8879 | 121.7829 | -0.029599 | 0.004903 | 0.003135 | 0.019713 | 121.9891 | 121.9564 | 121.9175 | 121.8848
2310 | 122.0306 | -0.10071 | 121.9757 | 0.1539 | -0.017627 | -0.021157 | -0.029595 | 0.031687 | 0.085583 | -0.071874 | 121.9137 | 121.9032 | 121.8467 | 121.7417 | -0.079953 | -0.040873 | -0.042641 | -0.026063 | 0.25461 | 0.083081 | 0.079551 | 0.071113 | 0.1324 | 0.18629 | 0.028834 | 121.9595 | 121.949 | 121.8925 | 121.7874 | -0.034177 | 0.004903 | 0.003135 | 0.019713 | 121.9937 | 121.9564 | 121.9267 | 121.8894
2311.7031 | 122.1497 | -0.064087 | 121.9391 | 0.14474 | -0.008469 | -0.016578 | -0.025017 | 0.040843 | 0.085583 | -0.062717 | 121.9091 | 121.9078 | 121.8467 | 121.7417 | -0.079953 | -0.036295 | -0.04722 | -0.026063 | 0.20883 | 0.055618 | 0.047509 | 0.03907 | 0.10493 | 0.14967 | 0.00137 | 121.9549 | 121.9536 | 121.8925 | 121.7874 | -0.034177 | 0.009481 | -0.001444 | 0.019713 | 121.9891 | 121.9564 | 121.9267 | 121.8939
2313.4531 | 122.1313 | -0.064087 | 121.9666 | 0.14932 | -0.013048 | -0.012 | -0.020438 | 0.045421 | 0.085583 | -0.067295 | 121.9137 | 121.9078 | 121.8559 | 121.7371 | -0.075375 | -0.040873 | -0.033484 | -0.026063 | 0.21341 | 0.051039 | 0.052087 | 0.043649 | 0.10951 | 0.14967 | -0.003208 | 121.9595 | 121.9536 | 121.9017 | 121.7829 | -0.029599 | 0.004903 | 0.012292 | 0.019713 | 121.9891 | 121.9472 | 121.9312 | 121.8894
2315.1406 | 121.9849 | -0.10529 | 121.9711 | 0.14474 | -0.013048 | -0.021157 | -0.020438 | 0.036265 | 0.085583 | -0.067295 | 121.9046 | 121.9124 | 121.8467 | 121.7417 | -0.070797 | -0.040873 | -0.04722 | -0.030641 | 0.25003 | 0.092238 | 0.084129 | 0.084848 | 0.14155 | 0.19087 | 0.037991 | 121.9503 | 121.9582 | 121.8925 | 121.7874 | -0.025021 | 0.004903 | -0.001444 | 0.015135 | 121.9754 | 121.9518 | 121.9175 | 121.8939
2316.9062 | 122.0078 | -0.11444 | 121.9666 | 0.1539 | -0.013048 | -0.021157 | -0.025017 | 0.036265 | 0.085583 | -0.071874 | 121.9137 | 121.9032 | 121.8467 | 121.7371 | -0.070797 | -0.040873 | -0.04722 | -0.026063 | 0.26834 | 0.10139 | 0.093284 | 0.089424 | 0.15071 | 0.20002 | 0.042567 | 121.9595 | 121.949 | 121.8925 | 121.7829 | -0.025021 | 0.004903 | -0.001444 | 0.019713 | 121.9845 | 121.9609 | 121.9175 | 121.8939
2318.6719 | 122.0398 | -0.09613 | 121.9528 | 0.14932 | -0.013048 | -0.021157 | -0.025017 | 0.040843 | 0.081005 | -0.071874 | 121.9137 | 121.9078 | 121.8467 | 121.7463 | -0.075375 | -0.040873 | -0.042641 | -0.026063 | 0.24545 | 0.083082 | 0.074973 | 0.071113 | 0.13697 | 0.17713 | 0.024256 | 121.9595 | 121.9536 | 121.8925 | 121.792 | -0.029599 | 0.004903 | 0.003135 | 0.019713 | 121.9891 | 121.9564 | 121.9221 | 121.8894
2320.3594 | 121.9849 | -0.11444 | 121.9803 | 0.14474 | -0.013048 | -0.021157 | -0.011281 | 0.045421 | 0.076426 | -0.071874 | 121.9091 | 121.9078 | 121.8559 | 121.7371 | -0.075375 | -0.040873 | -0.042641 | -0.030641 | 0.25918 | 0.10139 | 0.093284 | 0.10316 | 0.15986 | 0.19087 | 0.042567 | 121.9549 | 121.9536 | 121.9017 | 121.7829 | -0.029599 | 0.004903 | 0.003135 | 0.015135 | 121.9845 | 121.9518 | 121.9312 | 121.8985
2322.1094 | 122.0856 | -0.091553 | 121.9116 | 0.14474 | -0.008469 | -0.025735 | -0.029595 | 0.040843 | 0.085583 | -0.067295 | 121.9137 | 121.9032 | 121.8421 | 121.7371 | -0.070797 | -0.031717 | -0.051798 | -0.026063 | 0.2363 | 0.083084 | 0.065818 | 0.061958 | 0.1324 | 0.17714 | 0.024258 | 121.9595 | 121.949 | 121.8879 | 121.7829 | -0.025021 | 0.014059 | -0.006022 | 0.019713 | 121.9845 | 121.9655 | 121.9129 | 121.8939
2323.7969 | 122.0947 | -0.054932 | 121.9116 | 0.1539 | -0.017627 | -0.016578 | -0.025017 | 0.045421 | 0.081005 | -0.071874 | 121.9137 | 121.9124 | 121.8421 | 121.7417 | -0.079953 | -0.036295 | -0.042641 | -0.030641 | 0.20883 | 0.037305 | 0.038354 | 0.029915 | 0.10035 | 0.13594 | -0.016942 | 121.9595 | 121.9582 | 121.8879 | 121.7874 | -0.034177 | 0.009481 | 0.003135 | 0.015135 | 121.9937 | 121.9564 | 121.9221 | 121.8848
2325.5625 | 122.1222 | -0.07782 | 121.9208 | 0.14932 | -0.008469 | -0.016578 | -0.034174 | 0.036265 | 0.081005 | -0.071874 | 121.9091 | 121.9124 | 121.8513 | 121.7325 | -0.075375 | -0.036295 | -0.04722 | -0.030641 | 0.22714 | 0.069351 | 0.061242 | 0.043646 | 0.11408 | 0.15882 | 0.005946 | 121.9549 | 121.9582 | 121.8971 | 121.7783 | -0.029599 | 0.009481 | -0.001444 | 0.015135 | 121.9845 | 121.9564 | 121.9267 | 121.8985
2327.3281 | 122.0169 | -0.12817 | 121.9482 | 0.14474 | -0.013048 | -0.016578 | -0.025017 | 0.040843 | 0.081005 | -0.067295 | 121.9137 | 121.9078 | 121.8467 | 121.7417 | -0.079953 | -0.045451 | -0.038063 | -0.030641 | 0.27292 | 0.11513 | 0.1116 | 0.10316 | 0.16902 | 0.20918 | 0.060879 | 121.9595 | 121.9536 | 121.8925 | 121.7874 | -0.034177 | 0.000325 | 0.007713 | 0.015135 | 121.9937 | 121.9518 | 121.9267 | 121.8848
2329.0938 | 122.0901 | -0.086975 | 121.9345 | 0.14932 | -0.00389 | -0.016578 | -0.034174 | 0.031687 | 0.085583 | -0.076452 | 121.9183 | 121.9124 | 121.8467 | 121.7371 | -0.079953 | -0.040873 | -0.04722 | -0.030641 | 0.2363 | 0.083085 | 0.070397 | 0.052801 | 0.11866 | 0.17256 | 0.010523 | 121.9641 | 121.9582 | 121.8925 | 121.7829 | -0.034177 | 0.004903 | -0.001444 | 0.015135 | 121.9982 | 121.9655 | 121.9267 | 121.8939
2330.7969 | 122.0306 | -0.13275 | 121.9437 | 0.14932 | -0.008469 | -0.021157 | -0.025017 | 0.040843 | 0.085583 | -0.067295 | 121.9137 | 121.9032 | 121.8559 | 121.7371 | -0.066219 | -0.045451 | -0.042641 | -0.030641 | 0.28207 | 0.12428 | 0.11159 | 0.10773 | 0.17359 | 0.21833 | 0.065456 | 121.9595 | 121.949 | 121.9017 | 121.7829 | -0.020443 | 0.000325 | 0.003135 | 0.015135 | 121.9799 | 121.9564 | 121.9221 | 121.8985
2332.5625 | 122.1497 | -0.073242 | 121.9299 | 0.14932 | -0.008469 | -0.016578 | -0.025017 | 0.036265 | 0.085583 | -0.062717 | 121.9091 | 121.9124 | 121.8513 | 121.7463 | -0.075375 | -0.036295 | -0.04722 | -0.026063 | 0.22256 | 0.064773 | 0.056664 | 0.048225 | 0.10951 | 0.15882 | 0.010525 | 121.9549 | 121.9582 | 121.8971 | 121.792 | -0.029599 | 0.009481 | -0.001444 | 0.019713 | 121.9845 | 121.9564 | 121.9267 | 121.8985
2334.2656 | 122.0398 | -0.10071 | 121.9299 | 0.1539 | 0.000689 | -0.012 | -0.025017 | 0.045421 | 0.085583 | -0.062717 | 121.9137 | 121.9124 | 121.8559 | 121.7463 | -0.075375 | -0.031717 | -0.042641 | -0.026063 | 0.25461 | 0.1014 | 0.088708 | 0.075691 | 0.14613 | 0.18629 | 0.037991 | 121.9595 | 121.9582 | 121.9017 | 121.792 | -0.029599 | 0.014059 | 0.003135 | 0.019713 | 121.9891 | 121.9564 | 121.9312 | 121.8985
2336.0469 | 121.994 | -0.12817 | 121.9803 | 0.14017 | -0.017627 | -0.016578 | -0.025017 | 0.045421 | 0.085583 | -0.067295 | 121.9183 | 121.9078 | 121.8559 | 121.7417 | -0.070797 | -0.040873 | -0.04722 | -0.026063 | 0.26834 | 0.11055 | 0.1116 | 0.10316 | 0.17359 | 0.21376 | 0.060879 | 121.9641 | 121.9536 | 121.9017 | 121.7874 | -0.025021 | 0.004903 | -0.001444 | 0.019713 | 121.9891 | 121.9655 | 121.9267 | 121.9031
2337.8125 | 122.0032 | -0.1236 | 121.9528 | 0.14932 | -0.00389 | -0.016578 | -0.025017 | 0.040843 | 0.076426 | -0.071874 | 121.9183 | 121.9078 | 121.8513 | 121.7371 | -0.075375 | -0.036295 | -0.04722 | -0.026063 | 0.27292 | 0.11971 | 0.10702 | 0.098579 | 0.16444 | 0.20002 | 0.051722 | 121.9641 | 121.9536 | 121.8971 | 121.7829 | -0.029599 | 0.009481 | -0.001444 | 0.019713 | 121.9937 | 121.9655 | 121.9267 | 121.8985
2339.5 | 122.1222 | -0.068665 | 121.9574 | 0.14474 | -0.008469 | -0.016578 | -0.020438 | 0.040843 | 0.081005 | -0.071874 | 121.9183 | 121.9032 | 121.8467 | 121.7463 | -0.070797 | -0.036295 | -0.042641 | -0.026063 | 0.21341 | 0.060196 | 0.052087 | 0.048227 | 0.10951 | 0.14967 | -0.003209 | 121.9641 | 121.949 | 121.8925 | 121.792 | -0.025021 | 0.009481 | 0.003135 | 0.019713 | 121.9891 | 121.9609 | 121.9175 | 121.8894
2341.2812 | 122.0169 | -0.1236 | 121.9711 | 0.14932 | -0.008469 | -0.012 | -0.025017 | 0.045421 | 0.076426 | -0.067295 | 121.9137 | 121.9078 | 121.8467 | 121.7417 | -0.075375 | -0.031717 | -0.04722 | -0.021484 | 0.27292 | 0.11513 | 0.1116 | 0.098579 | 0.16902 | 0.20002 | 0.056301 | 121.9595 | 121.9536 | 121.8925 | 121.7874 | -0.029599 | 0.014059 | -0.001444 | 0.024292 | 121.9891 | 121.9609 | 121.9221 | 121.8939
2342.9844 | 122.1176 | -0.073242 | 121.9437 | 0.14474 | -0.00389 | -0.012 | -0.025017 | 0.031687 | 0.081005 | -0.071874 | 121.9229 | 121.9124 | 121.8559 | 121.7371 | -0.079953 | -0.036295 | -0.042641 | -0.021484 | 0.21799 | 0.069352 | 0.061242 | 0.048225 | 0.10493 | 0.15425 | 0.001368 | 121.9686 | 121.9582 | 121.9017 | 121.7829 | -0.034177 | 0.009481 | 0.003135 | 0.024292 | 122.0028 | 121.9655 | 121.9358 | 121.8985
2344.7344 | 122.1176 | -0.07782 | 121.9345 | 0.14017 | -0.008469 | -0.025735 | -0.034174 | 0.040843 | 0.085583 | -0.067295 | 121.9091 | 121.9124 | 121.8421 | 121.7508 | -0.070797 | -0.036295 | -0.04722 | -0.021484 | 0.21799 | 0.069351 | 0.052085 | 0.043646 | 0.11866 | 0.1634 | 0.010525 | 121.9549 | 121.9582 | 121.8879 | 121.7966 | -0.025021 | 0.009481 | -0.001444 | 0.024292 | 121.9799 | 121.9564 | 121.9129 | 121.8894
2346.5 | 122.1176 | -0.073242 | 121.9299 | 0.14017 | -0.008469 | -0.025735 | -0.020438 | 0.027109 | 0.081005 | -0.071874 | 121.9229 | 121.9078 | 121.8513 | 121.7417 | -0.075375 | -0.036295 | -0.04722 | -0.030641 | 0.21341 | 0.064773 | 0.047507 | 0.052804 | 0.10035 | 0.15425 | 0.001368 | 121.9686 | 121.9536 | 121.8971 | 121.7874 | -0.029599 | 0.009481 | -0.001444 | 0.015135 | 121.9982 | 121.9701 | 121.9267 | 121.8985
2348.1875 | 122.0032 | -0.10986 | 121.994 | 0.14932 | -0.008469 | -0.016578 | -0.029595 | 0.036265 | 0.081005 | -0.067295 | 121.9183 | 121.9032 | 121.8559 | 121.7508 | -0.079953 | -0.036295 | -0.038063 | -0.030641 | 0.25918 | 0.10139 | 0.093285 | 0.080268 | 0.14613 | 0.19087 | 0.042568 | 121.9641 | 121.949 | 121.9017 | 121.7966 | -0.034177 | 0.009481 | 0.007713 | 0.015135 | 121.9982 | 121.9564 | 121.9358 | 121.8939
2349.9375 | 122.1222 | -0.068665 | 121.962 | 0.14932 | -0.008469 | -0.025735 | -0.029595 | 0.040843 | 0.081005 | -0.062717 | 121.9137 | 121.9078 | 121.8513 | 121.7508 | -0.070797 | -0.040873 | -0.033484 | -0.021484 | 0.21799 | 0.060196 | 0.04293 | 0.03907 | 0.10951 | 0.14967 | 0.005948 | 121.9595 | 121.9536 | 121.8971 | 121.7966 | -0.025021 | 0.004903 | 0.012292 | 0.024292 | 121.9845 | 121.9472 | 121.9221 | 121.8848
2351.7031 | 121.9986 | -0.10986 | 121.9849 | 0.14932 | -0.013048 | -0.016578 | -0.020438 | 0.040843 | 0.081005 | -0.062717 | 121.9183 | 121.9124 | 121.8559 | 121.7463 | -0.075375 | -0.036295 | -0.038063 | -0.026063 | 0.25918 | 0.096815 | 0.093285 | 0.089425 | 0.15071 | 0.19087 | 0.047146 | 121.9641 | 121.9582 | 121.9017 | 121.792 | -0.029599 | 0.009481 | 0.007713 | 0.019713 | 121.9937 | 121.9564 | 121.9312 | 121.8939
2353.4062 | 122.1313 | -0.054932 | 121.9299 | 0.14474 | -0.017627 | -0.012 | -0.029595 | 0.040843 | 0.081005 | -0.071874 | 121.9183 | 121.9032 | 121.8559 | 121.7371 | -0.075375 | -0.040873 | -0.04722 | -0.016906 | 0.19968 | 0.037305 | 0.042932 | 0.025337 | 0.095775 | 0.13594 | -0.016942 | 121.9641 | 121.949 | 121.9017 | 121.7829 | -0.029599 | 0.004903 | -0.001444 | 0.02887 | 121.9937 | 121.9655 | 121.9312 | 121.9031
2355.1719 | 122.081 | -0.09613 | 121.9482 | 0.1539 | -0.008469 | -0.021157 | -0.029595 | 0.036265 | 0.081005 | -0.067295 | 121.9137 | 121.9124 | 121.8421 | 121.7463 | -0.075375 | -0.031717 | -0.051798 | -0.026063 | 0.25003 | 0.087661 | 0.074973 | 0.066535 | 0.13239 | 0.17713 | 0.028835 | 121.9595 | 121.9582 | 121.8879 | 121.792 | -0.029599 | 0.014059 | -0.006022 | 0.019713 | 121.9891 | 121.9655 | 121.9175 | 121.8939
2356.9375 | 121.9986 | -0.1236 | 121.9666 | 0.1539 | -0.017627 | -0.012 | -0.034174 | 0.036265 | 0.076426 | -0.071874 | 121.9137 | 121.917 | 121.8559 | 121.7463 | -0.070797 | -0.040873 | -0.051798 | -0.030641 | 0.2775 | 0.10597 | 0.1116 | 0.089422 | 0.15986 | 0.20002 | 0.051722 | 121.9595 | 121.9627 | 121.9017 | 121.792 | -0.025021 | 0.004903 | -0.006022 | 0.015135 | 121.9845 | 121.9655 | 121.9267 | 121.9077
2358.6406 | 122.0078 | -0.1236 | 121.9711 | 0.14932 | -0.008469 | -0.021157 | -0.029595 | 0.036265 | 0.081005 | -0.067295 | 121.9229 | 121.9078 | 121.8513 | 121.7371 | -0.070797 | -0.036295 | -0.04722 | -0.016906 | 0.27292 | 0.11513 | 0.10244 | 0.094001 | 0.15986 | 0.2046 | 0.056301 | 121.9686 | 121.9536 | 121.8971 | 121.7829 | -0.025021 | 0.009481 | -0.001444 | 0.02887 | 121.9937 | 121.9701 | 121.9221 | 121.8985
2360.4062 | 122.0215 | -0.11902 | 121.9757 | 0.14474 | -0.00389 | -0.012 | -0.020438 | 0.036265 | 0.085583 | -0.071874 | 121.9183 | 121.9032 | 121.8605 | 121.7463 | -0.084531 | -0.040873 | -0.04722 | -0.026063 | 0.26376 | 0.11513 | 0.10702 | 0.098581 | 0.15528 | 0.2046 | 0.047145 | 121.9641 | 121.949 | 121.9062 | 121.792 | -0.038755 | 0.004903 | -0.001444 | 0.019713 | 122.0028 | 121.9655 | 121.945 | 121.9077
2362.1719 | 122.0444 | -0.12817 | 121.9574 | 0.14932 | 0.000689 | -0.021157 | -0.029595 | 0.040843 | 0.076426 | -0.071874 | 121.9137 | 121.9124 | 121.8513 | 121.7508 | -0.079953 | -0.045451 | -0.042641 | -0.026063 | 0.2775 | 0.12886 | 0.10702 | 0.098579 | 0.16902 | 0.2046 | 0.0563 | 121.9595 | 121.9582 | 121.8971 | 121.7966 | -0.034177 | 0.000325 | 0.003135 | 0.019713 | 121.9937 | 121.9564 | 121.9312 | 121.8939
2363.9375 | 121.9894 | -0.10986 | 121.9711 | 0.14017 | -0.008469 | -0.021157 | -0.029595 | 0.036265 | 0.090161 | -0.062717 | 121.9183 | 121.9124 | 121.8513 | 121.7325 | -0.079953 | -0.045451 | -0.04722 | -0.030641 | 0.25003 | 0.10139 | 0.088706 | 0.080268 | 0.14613 | 0.20002 | 0.047146 | 121.9641 | 121.9582 | 121.8971 | 121.7783 | -0.034177 | 0.000325 | -0.001444 | 0.015135 | 121.9982 | 121.9655 | 121.9312 | 121.8985
2365.6406 | 122.1542 | -0.068665 | 121.9574 | 0.14474 | -0.017627 | -0.021157 | -0.034174 | 0.031687 | 0.081005 | -0.071874 | 121.9183 | 121.9124 | 121.8559 | 121.7463 | -0.084531 | -0.040873 | -0.042641 | -0.026063 | 0.21341 | 0.051038 | 0.047508 | 0.034491 | 0.10035 | 0.14967 | -0.003209 | 121.9641 | 121.9582 | 121.9017 | 121.792 | -0.038755 | 0.004903 | 0.003135 | 0.019713 | 122.0028 | 121.9609 | 121.9404 | 121.8985
2367.3906 | 122.1268 | -0.086975 | 121.9299 | 0.14474 | -0.013048 | -0.016578 | -0.034174 | 0.036265 | 0.090161 | -0.076452 | 121.9183 | 121.917 | 121.8559 | 121.7463 | -0.070797 | -0.036295 | -0.042641 | -0.021484 | 0.23172 | 0.073927 | 0.070397 | 0.052801 | 0.12324 | 0.17714 | 0.010523 | 121.9641 | 121.9627 | 121.9017 | 121.792 | -0.025021 | 0.009481 | 0.003135 | 0.024292 | 121.9891 | 121.9609 | 121.9267 | 121.8985
2369.1406 | 122.0078 | -0.1236 | 121.9803 | 0.14932 | -0.013048 | -0.016578 | -0.025017 | 0.036265 | 0.081005 | -0.076452 | 121.9183 | 121.917 | 121.8467 | 121.7417 | -0.070797 | -0.036295 | -0.042641 | -0.026063 | 0.27292 | 0.11055 | 0.10702 | 0.098579 | 0.15986 | 0.2046 | 0.047144 | 121.9641 | 121.9627 | 121.8925 | 121.7874 | -0.025021 | 0.009481 | 0.003135 | 0.019713 | 121.9891 | 121.9609 | 121.9175 | 121.8894
2370.8438 | 122.1451 | -0.064087 | 121.9254 | 0.14932 | -0.013048 | -0.016578 | -0.029595 | 0.040843 | 0.085583 | -0.076452 | 121.9229 | 121.9124 | 121.8559 | 121.7417 | -0.075375 | -0.040873 | -0.04722 | -0.021484 | 0.21341 | 0.051039 | 0.047509 | 0.034492 | 0.10493 | 0.14967 | -0.012365 | 121.9686 | 121.9582 | 121.9017 | 121.7874 | -0.029599 | 0.004903 | -0.001444 | 0.024292 | 121.9982 | 121.9701 | 121.9312 | 121.9031
2372.6094 | 122.1085 | -0.07782 | 121.9116 | 0.14474 | -0.013048 | -0.021157 | -0.020438 | 0.040843 | 0.076426 | -0.076452 | 121.9137 | 121.9078 | 121.8559 | 121.7371 | -0.075375 | -0.031717 | -0.042641 | -0.030641 | 0.22256 | 0.064772 | 0.056663 | 0.057382 | 0.11866 | 0.15425 | 0.001368 | 121.9595 | 121.9536 | 121.9017 | 121.7829 | -0.029599 | 0.014059 | 0.003135 | 0.015135 | 121.9891 | 121.9564 | 121.9312 | 121.8985
2374.3125 | 121.9803 | -0.1236 | 121.9757 | 0.14932 | -0.008469 | -0.025735 | -0.025017 | 0.036265 | 0.085583 | -0.067295 | 121.9183 | 121.917 | 121.8559 | 121.7463 | -0.070797 | -0.031717 | -0.04722 | -0.026063 | 0.27292 | 0.11513 | 0.097861 | 0.098579 | 0.15986 | 0.20918 | 0.056301 | 121.9641 | 121.9627 | 121.9017 | 121.792 | -0.025021 | 0.014059 | -0.001444 | 0.019713 | 121.9891 | 121.9655 | 121.9267 | 121.9031
2376.0781 | 121.9986 | -0.11902 | 121.9574 | 0.14474 | -0.013048 | -0.012 | -0.020438 | 0.040843 | 0.076426 | -0.062717 | 121.9183 | 121.917 | 121.8559 | 121.7417 | -0.075375 | -0.045451 | -0.04722 | -0.021484 | 0.26376 | 0.10597 | 0.10702 | 0.098581 | 0.15986 | 0.19544 | 0.056302 | 121.9641 | 121.9627 | 121.9017 | 121.7874 | -0.029599 | 0.000325 | -0.001444 | 0.024292 | 121.9937 | 121.9655 | 121.9312 | 121.9031
2377.8438 | 122.0901 | -0.064087 | 121.9574 | 0.13559 | -0.00389 | -0.025735 | -0.025017 | 0.036265 | 0.081005 | -0.067295 | 121.9275 | 121.917 | 121.8605 | 121.7463 | -0.070797 | -0.040873 | -0.051798 | -0.026063 | 0.19967 | 0.060197 | 0.038352 | 0.03907 | 0.10035 | 0.14509 | -0.003208 | 121.9732 | 121.9627 | 121.9062 | 121.792 | -0.025021 | 0.004903 | -0.006022 | 0.019713 | 121.9982 | 121.9792 | 121.9312 | 121.9123
2379.5312 | 122.0352 | -0.10986 | 121.9437 | 0.1539 | -0.008469 | -0.021157 | -0.025017 | 0.036265 | 0.085583 | -0.067295 | 121.9229 | 121.917 | 121.8559 | 121.7417 | -0.075375 | -0.040873 | -0.04722 | -0.030641 | 0.26376 | 0.10139 | 0.088706 | 0.084846 | 0.14613 | 0.19545 | 0.042568 | 121.9686 | 121.9627 | 121.9017 | 121.7874 | -0.029599 | 0.004903 | -0.001444 | 0.015135 | 121.9982 | 121.9701 | 121.9312 | 121.9031
2381.2969 | 122.1359 | -0.059509 | 121.9391 | 0.14932 | -0.008469 | -0.025735 | -0.029595 | 0.045421 | 0.085583 | -0.067295 | 121.9137 | 121.9124 | 121.8559 | 121.7463 | -0.075375 | -0.045451 | -0.033484 | -0.026063 | 0.20883 | 0.05104 | 0.033774 | 0.029914 | 0.10493 | 0.14509 | -0.007786 | 121.9595 | 121.9582 | 121.9017 | 121.792 | -0.029599 | 0.000325 | 0.012292 | 0.019713 | 121.9891 | 121.9472 | 121.9312 | 121.8894
2383 | 122.0352 | -0.10529 | 121.9482 | 0.14474 | -0.008469 | -0.021157 | -0.025017 | 0.045421 | 0.090161 | -0.067295 | 121.9229 | 121.917 | 121.8559 | 121.7508 | -0.075375 | -0.036295 | -0.042641 | -0.030641 | 0.25003 | 0.096817 | 0.084129 | 0.080269 | 0.15071 | 0.19545 | 0.037991 | 121.9686 | 121.9627 | 121.9017 | 121.7966 | -0.029599 | 0.009481 | 0.003135 | 0.015135 | 121.9982 | 121.9655 | 121.9312 | 121.8985
2384.75 | 122.0947 | -0.073242 | 121.9437 | 0.1539 | -0.00389 | -0.016578 | -0.020438 | 0.036265 | 0.081005 | -0.067295 | 121.9229 | 121.917 | 121.8559 | 121.7508 | -0.075375 | -0.036295 | -0.04722 | -0.021484 | 0.22714 | 0.069352 | 0.056664 | 0.052804 | 0.10951 | 0.15425 | 0.005947 | 121.9686 | 121.9627 | 121.9017 | 121.7966 | -0.029599 | 0.009481 | -0.001444 | 0.024292 | 121.9982 | 121.9701 | 121.9312 | 121.9031
2386.5 | 122.0078 | -0.11902 | 121.9574 | 0.1539 | -0.013048 | -0.021157 | -0.020438 | 0.040843 | 0.081005 | -0.058139 | 121.9183 | 121.917 | 121.8559 | 121.7417 | -0.075375 | -0.040873 | -0.04722 | -0.026063 | 0.27292 | 0.10597 | 0.097862 | 0.098581 | 0.15986 | 0.20002 | 0.06088 | 121.9641 | 121.9627 | 121.9017 | 121.7874 | -0.029599 | 0.004903 | -0.001444 | 0.019713 | 121.9937 | 121.9655 | 121.9312 | 121.9031
2388.2656 | 122.0078 | -0.11444 | 121.994 | 0.14932 | -0.013048 | -0.016578 | -0.020438 | 0.040843 | 0.090161 | -0.071874 | 121.9275 | 121.917 | 121.8513 | 121.7463 | -0.070797 | -0.036295 | -0.042641 | -0.030641 | 0.26376 | 0.10139 | 0.097863 | 0.094003 | 0.15528 | 0.2046 | 0.042567 | 121.9732 | 121.9627 | 121.8971 | 121.792 | -0.025021 | 0.009481 | 0.003135 | 0.015135 | 121.9982 | 121.9701 | 121.9221 | 121.8939
2389.9531 | 122.113 | -0.073242 | 121.9711 | 0.14474 | -0.022205 | -0.016578 | -0.029595 | 0.040843 | 0.085583 | -0.071874 | 121.932 | 121.9124 | 121.8605 | 121.7371 | -0.075375 | -0.036295 | -0.042641 | -0.030641 | 0.21799 | 0.051037 | 0.056664 | 0.043647 | 0.11408 | 0.15882 | 0.001368 | 121.9778 | 121.9582 | 121.9062 | 121.7829 | -0.029599 | 0.009481 | 0.003135 | 0.015135 | 122.0074 | 121.9747 | 121.9358 | 121.9031
2391.7188 | 122.1451 | -0.09613 | 121.9482 | 0.14932 | -0.008469 | -0.021157 | -0.025017 | 0.036265 | 0.076426 | -0.071874 | 121.9183 | 121.9215 | 121.8605 | 121.7508 | -0.075375 | -0.031717 | -0.04722 | -0.021484 | 0.24545 | 0.087661 | 0.074973 | 0.071113 | 0.13239 | 0.17256 | 0.024256 | 121.9641 | 121.9673 | 121.9062 | 121.7966 | -0.029599 | 0.014059 | -0.001444 | 0.024292 | 121.9937 | 121.9655 | 121.9358 | 121.9077
2393.4844 | 122.0032 | -0.11444 | 121.9803 | 0.14932 | -0.00389 | -0.025735 | -0.020438 | 0.036265 | 0.076426 | -0.067295 | 121.9229 | 121.9124 | 121.8605 | 121.7417 | -0.070797 | -0.040873 | -0.042641 | -0.026063 | 0.26376 | 0.11055 | 0.088706 | 0.094003 | 0.15071 | 0.19087 | 0.047146 | 121.9686 | 121.9582 | 121.9062 | 121.7874 | -0.025021 | 0.004903 | 0.003135 | 0.019713 | 121.9937 | 121.9655 | 121.9312 | 121.9031
2395.25 | 122.1039 | -0.07782 | 121.9528 | 0.14932 | -0.008469 | -0.016578 | -0.029595 | 0.040843 | 0.081005 | -0.071874 | 121.9183 | 121.9215 | 121.8559 | 121.7463 | -0.075375 | -0.031717 | -0.038063 | -0.026063 | 0.22714 | 0.069351 | 0.061242 | 0.048225 | 0.11866 | 0.15882 | 0.005946 | 121.9641 | 121.9673 | 121.9017 | 121.792 | -0.029599 | 0.014059 | 0.007713 | 0.019713 | 121.9937 | 121.9564 | 121.9312 | 121.8939
2397.0156 | 122.0032 | -0.10986 | 121.9757 | 0.14474 | -0.008469 | -0.021157 | -0.025017 | 0.036265 | 0.085583 | -0.062717 | 121.9137 | 121.917 | 121.8605 | 121.7508 | -0.075375 | -0.036295 | -0.042641 | -0.030641 | 0.25461 | 0.10139 | 0.088706 | 0.084846 | 0.14613 | 0.19545 | 0.047146 | 121.9595 | 121.9627 | 121.9062 | 121.7966 | -0.029599 | 0.009481 | 0.003135 | 0.015135 | 121.9891 | 121.9564 | 121.9358 | 121.9031
2398.7031 | 122.1039 | -0.086975 | 121.9391 | 0.14932 | -0.00389 | -0.016578 | -0.020438 | 0.031687 | 0.076426 | -0.067295 | 121.9183 | 121.9215 | 121.8559 | 121.7554 | -0.079953 | -0.036295 | -0.04722 | -0.030641 | 0.2363 | 0.083085 | 0.070397 | 0.066537 | 0.11866 | 0.1634 | 0.01968 | 121.9641 | 121.9673 | 121.9017 | 121.8012 | -0.034177 | 0.009481 | -0.001444 | 0.015135 | 121.9982 | 121.9655 | 121.9358 | 121.9031
2400.4688 | 122.0947 | -0.082397 | 121.9803 | 0.14474 | 0.000689 | -0.016578 | -0.029595 | 0.031687 | 0.076426 | -0.067295 | 121.9183 | 121.9215 | 121.8605 | 121.7508 | -0.075375 | -0.031717 | -0.038063 | -0.026063 | 0.22714 | 0.083086 | 0.065819 | 0.052802 | 0.11408 | 0.15882 | 0.015102 | 121.9641 | 121.9673 | 121.9062 | 121.7966 | -0.029599 | 0.014059 | 0.007713 | 0.019713 | 121.9937 | 121.9564 | 121.9358 | 121.8985
2402.2344 | 122.1359 | -0.07782 | 121.9299 | 0.14474 | -0.00389 | -0.021157 | -0.025017 | 0.036265 | 0.085583 | -0.067295 | 121.9229 | 121.917 | 121.8559 | 121.7463 | -0.075375 | -0.040873 | -0.038063 | -0.030641 | 0.22256 | 0.07393 | 0.056663 | 0.052803 | 0.11408 | 0.1634 | 0.010525 | 121.9686 | 121.9627 | 121.9017 | 121.792 | -0.029599 | 0.004903 | 0.007713 | 0.015135 | 121.9982 | 121.9609 | 121.9312 | 121.8939
2403.9375 | 121.9986 | -0.13733 | 121.994 | 0.14474 | -0.008469 | -0.012 | -0.025017 | 0.027109 | 0.085583 | -0.076452 | 121.9275 | 121.9124 | 121.8559 | 121.7554 | -0.075375 | -0.036295 | -0.042641 | -0.035219 | 0.28207 | 0.12886 | 0.12533 | 0.11231 | 0.16444 | 0.22291 | 0.060877 | 121.9732 | 121.9582 | 121.9017 | 121.8012 | -0.029599 | 0.009481 | 0.003135 | 0.010557 | 122.0028 | 121.9701 | 121.9312 | 121.8985
2405.6875 | 122.1451 | -0.07782 | 121.9345 | 0.1539 | -0.008469 | -0.021157 | -0.025017 | 0.036265 | 0.085583 | -0.076452 | 121.9229 | 121.917 | 121.8513 | 121.7508 | -0.079953 | -0.040873 | -0.038063 | -0.026063 | 0.23172 | 0.069351 | 0.056663 | 0.052803 | 0.11408 | 0.1634 | 0.001368 | 121.9686 | 121.9627 | 121.8971 | 121.7966 | -0.034177 | 0.004903 | 0.007713 | 0.019713 | 122.0028 | 121.9609 | 121.9312 | 121.8894
2407.4531 | 122.0032 | -0.10986 | 122.0078 | 0.14474 | -0.008469 | -0.021157 | -0.029595 | 0.040843 | 0.081005 | -0.071874 | 121.9183 | 121.9215 | 121.865 | 121.7463 | -0.079953 | -0.045451 | -0.042641 | -0.026063 | 0.25461 | 0.10139 | 0.088706 | 0.080268 | 0.15071 | 0.19087 | 0.037989 | 121.9641 | 121.9673 | 121.9108 | 121.792 | -0.034177 | 0.000325 | 0.003135 | 0.019713 | 121.9982 | 121.9609 | 121.945 | 121.9077
2409.1562 | 122.1222 | -0.073242 | 121.9528 | 0.1539 | -0.008469 | -0.021157 | -0.029595 | 0.040843 | 0.081005 | -0.067295 | 121.9229 | 121.917 | 121.8559 | 121.7554 | -0.075375 | -0.040873 | -0.042641 | -0.026063 | 0.22714 | 0.064773 | 0.052085 | 0.043647 | 0.11408 | 0.15425 | 0.005947 | 121.9686 | 121.9627 | 121.9017 | 121.8012 | -0.029599 | 0.004903 | 0.003135 | 0.019713 | 121.9982 | 121.9655 | 121.9312 | 121.8985
2410.9219 | 122.1497 | -0.086975 | 121.9528 | 0.14932 | -0.013048 | -0.021157 | -0.025017 | 0.040843 | 0.085583 | -0.076452 | 121.9229 | 121.9078 | 121.8605 | 121.7508 | -0.079953 | -0.036295 | -0.042641 | -0.030641 | 0.2363 | 0.073927 | 0.065818 | 0.061958 | 0.12782 | 0.17256 | 0.010523 | 121.9686 | 121.9536 | 121.9062 | 121.7966 | -0.034177 | 0.009481 | 0.003135 | 0.015135 | 122.0028 | 121.9655 | 121.9404 | 121.9031
2412.6875 | 122.0627 | -0.086975 | 121.9528 | 0.14474 | -0.013048 | -0.016578 | -0.025017 | 0.036265 | 0.081005 | -0.062717 | 121.9229 | 121.9261 | 121.865 | 121.7508 | -0.070797 | -0.045451 | -0.04722 | -0.030641 | 0.23172 | 0.073927 | 0.070397 | 0.061958 | 0.12324 | 0.16798 | 0.024258 | 121.9686 | 121.9719 | 121.9108 | 121.7966 | -0.025021 | 0.000325 | -0.001444 | 0.015135 | 121.9937 | 121.9701 | 121.9358 | 121.9123
2414.3906 | 122.1268 | -0.07782 | 121.9482 | 0.14474 | -0.013048 | -0.021157 | -0.025017 | 0.036265 | 0.085583 | -0.071874 | 121.9229 | 121.917 | 121.8605 | 121.7463 | -0.075375 | -0.040873 | -0.042641 | -0.026063 | 0.22256 | 0.064772 | 0.056663 | 0.052803 | 0.11408 | 0.1634 | 0.005946 | 121.9686 | 121.9627 | 121.9062 | 121.792 | -0.029599 | 0.004903 | 0.003135 | 0.019713 | 121.9982 | 121.9655 | 121.9358 | 121.9031
2416.1406 | 122.1359 | -0.082397 | 121.8979 | 0.14932 | -0.008469 | -0.012 | -0.025017 | 0.036265 | 0.076426 | -0.062717 | 121.9275 | 121.917 | 121.8559 | 121.7463 | -0.075375 | -0.036295 | -0.042641 | -0.021484 | 0.23172 | 0.073928 | 0.070397 | 0.05738 | 0.11866 | 0.15882 | 0.01968 | 121.9732 | 121.9627 | 121.9017 | 121.792 | -0.029599 | 0.009481 | 0.003135 | 0.024292 | 122.0028 | 121.9701 | 121.9312 | 121.8985
2417.9062 | 122.0947 | -0.09613 | 121.9391 | 0.14932 | -0.00389 | -0.016578 | -0.020438 | 0.036265 | 0.081005 | -0.062717 | 121.9229 | 121.9215 | 121.8605 | 121.7554 | -0.075375 | -0.031717 | -0.04722 | -0.021484 | 0.24545 | 0.09224 | 0.079552 | 0.075692 | 0.13239 | 0.17713 | 0.033413 | 121.9686 | 121.9673 | 121.9062 | 121.8012 | -0.029599 | 0.014059 | -0.001444 | 0.024292 | 121.9982 | 121.9701 | 121.9358 | 121.9077
2419.6562 | 122.1405 | -0.07782 | 121.9437 | 0.14932 | -0.013048 | -0.021157 | -0.020438 | 0.031687 | 0.081005 | -0.071874 | 121.9183 | 121.9215 | 121.865 | 121.7508 | -0.070797 | -0.031717 | -0.042641 | -0.035219 | 0.22714 | 0.064772 | 0.056663 | 0.057382 | 0.10951 | 0.15882 | 0.005946 | 121.9641 | 121.9673 | 121.9108 | 121.7966 | -0.025021 | 0.014059 | 0.003135 | 0.010557 | 121.9891 | 121.9609 | 121.9358 | 121.9077
2421.4219 | 122.0306 | -0.11444 | 121.962 | 0.14932 | -0.017627 | -0.016578 | -0.025017 | 0.040843 | 0.081005 | -0.067295 | 121.9183 | 121.9215 | 121.865 | 121.7508 | -0.079953 | -0.040873 | -0.04722 | -0.021484 | 0.26376 | 0.096814 | 0.097863 | 0.089424 | 0.15528 | 0.19545 | 0.047146 | 121.9641 | 121.9673 | 121.9108 | 121.7966 | -0.034177 | 0.004903 | -0.001444 | 0.024292 | 121.9982 | 121.9655 | 121.945 | 121.9123
2423.1406 | 122.0261 | -0.1236 | 121.9757 | 0.14932 | -0.013048 | -0.016578 | -0.01586 | 0.036265 | 0.081005 | -0.062717 | 121.932 | 121.917 | 121.8513 | 121.7508 | -0.079953 | -0.040873 | -0.038063 | -0.021484 | 0.27292 | 0.11055 | 0.10702 | 0.10774 | 0.15986 | 0.2046 | 0.060879 | 121.9778 | 121.9627 | 121.8971 | 121.7966 | -0.034177 | 0.004903 | 0.007713 | 0.024292 | 122.012 | 121.9701 | 121.9312 | 121.8894
2424.9062 | 122.0947 | -0.10071 | 121.962 | 0.1539 | -0.008469 | -0.016578 | -0.029595 | 0.036265 | 0.081005 | -0.067295 | 121.9366 | 121.917 | 121.8559 | 121.7463 | -0.075375 | -0.040873 | -0.038063 | -0.030641 | 0.25461 | 0.092239 | 0.08413 | 0.071113 | 0.13697 | 0.18171 | 0.033413 | 121.9824 | 121.9627 | 121.9017 | 121.792 | -0.029599 | 0.004903 | 0.007713 | 0.015135 | 122.012 | 121.9747 | 121.9312 | 121.8939
2426.5938 | 122.0078 | -0.11902 | 121.9666 | 0.15848 | -0.008469 | -0.012 | -0.01586 | 0.045421 | 0.085583 | -0.071874 | 121.932 | 121.9124 | 121.8559 | 121.7554 | -0.075375 | -0.036295 | -0.038063 | -0.021484 | 0.2775 | 0.11055 | 0.10702 | 0.10316 | 0.16444 | 0.2046 | 0.047145 | 121.9778 | 121.9582 | 121.9017 | 121.8012 | -0.029599 | 0.009481 | 0.007713 | 0.024292 | 122.0074 | 121.9701 | 121.9312 | 121.8939
2428.375 | 122.0627 | -0.09613 | 121.9803 | 0.14932 | -0.00389 | -0.016578 | -0.020438 | 0.040843 | 0.081005 | -0.062717 | 121.9183 | 121.9215 | 121.8605 | 121.7508 | -0.075375 | -0.040873 | -0.04722 | -0.026063 | 0.24545 | 0.09224 | 0.079552 | 0.075692 | 0.13697 | 0.17713 | 0.033413 | 121.9641 | 121.9673 | 121.9062 | 121.7966 | -0.029599 | 0.004903 | -0.001444 | 0.019713 | 121.9937 | 121.9655 | 121.9358 | 121.9077
2430.0781 | 122.0032 | -0.1236 | 121.9849 | 0.14474 | -0.013048 | -0.012 | -0.025017 | 0.045421 | 0.085583 | -0.062717 | 121.9275 | 121.9124 | 121.865 | 121.7417 | -0.079953 | -0.036295 | -0.042641 | -0.026063 | 0.26834 | 0.11055 | 0.1116 | 0.098579 | 0.16902 | 0.20918 | 0.060879 | 121.9732 | 121.9582 | 121.9108 | 121.7874 | -0.034177 | 0.009481 | 0.003135 | 0.019713 | 122.0074 | 121.9701 | 121.945 | 121.9077
2431.8281 | 122.0947 | -0.082397 | 121.9757 | 0.14474 | -0.013048 | -0.012 | -0.025017 | 0.040843 | 0.085583 | -0.071874 | 121.9275 | 121.917 | 121.8605 | 121.7463 | -0.079953 | -0.040873 | -0.038063 | -0.026063 | 0.22714 | 0.069349 | 0.070397 | 0.05738 | 0.12324 | 0.16798 | 0.010523 | 121.9732 | 121.9627 | 121.9062 | 121.792 | -0.034177 | 0.004903 | 0.007713 | 0.019713 | 122.0074 | 121.9655 | 121.9404 | 121.8985
2433.5938 | 122.0444 | -0.10529 | 121.9666 | 0.14474 | -0.013048 | -0.007421 | -0.025017 | 0.036265 | 0.09474 | -0.062717 | 121.9229 | 121.917 | 121.8605 | 121.7463 | -0.075375 | -0.040873 | -0.04722 | -0.026063 | 0.25003 | 0.092238 | 0.097865 | 0.080269 | 0.14155 | 0.20003 | 0.042569 | 121.9686 | 121.9627 | 121.9062 | 121.792 | -0.029599 | 0.004903 | -0.001444 | 0.019713 | 121.9982 | 121.9701 | 121.9358 | 121.9077
2435.2969 | 122.1085 | -0.07782 | 121.9208 | 0.14474 | -0.008469 | -0.016578 | -0.025017 | 0.036265 | 0.081005 | -0.067295 | 121.9229 | 121.9124 | 121.8605 | 121.7463 | -0.084531 | -0.045451 | -0.042641 | -0.030641 | 0.22256 | 0.069351 | 0.061242 | 0.052803 | 0.11408 | 0.15882 | 0.010525 | 121.9686 | 121.9582 | 121.9062 | 121.792 | -0.038755 | 0.000325 | 0.003135 | 0.015135 | 122.0074 | 121.9655 | 121.945 | 121.9031
2437.0625 | 122.0261 | -0.11444 | 121.9894 | 0.14474 | -0.008469 | -0.021157 | -0.020438 | 0.036265 | 0.09474 | -0.062717 | 121.9229 | 121.917 | 121.865 | 121.76 | -0.075375 | -0.040873 | -0.042641 | -0.021484 | 0.25918 | 0.10597 | 0.093284 | 0.094003 | 0.15071 | 0.20918 | 0.051724 | 121.9686 | 121.9627 | 121.9108 | 121.8058 | -0.029599 | 0.004903 | 0.003135 | 0.024292 | 121.9982 | 121.9655 | 121.9404 | 121.9077
2438.8125 | 122.1176 | -0.059509 | 121.9254 | 0.14474 | -0.00389 | -0.025735 | -0.020438 | 0.045421 | 0.081005 | -0.067295 | 121.9275 | 121.917 | 121.865 | 121.7463 | -0.075375 | -0.036295 | -0.042641 | -0.016906 | 0.20425 | 0.055619 | 0.033774 | 0.039071 | 0.10493 | 0.14051 | -0.007786 | 121.9732 | 121.9627 | 121.9108 | 121.792 | -0.029599 | 0.009481 | 0.003135 | 0.02887 | 122.0028 | 121.9701 | 121.9404 | 121.9077
2440.5156 | 122.1039 | -0.068665 | 121.9391 | 0.14017 | -0.008469 | -0.016578 | -0.025017 | 0.036265 | 0.081005 | -0.067295 | 121.9275 | 121.9215 | 121.8696 | 121.7508 | -0.075375 | -0.045451 | -0.038063 | -0.030641 | 0.20883 | 0.060196 | 0.052087 | 0.043648 | 0.10493 | 0.14967 | 0.00137 | 121.9732 | 121.9673 | 121.9154 | 121.7966 | -0.029599 | 0.000325 | 0.007713 | 0.015135 | 122.0028 | 121.9655 | 121.945 | 121.9077
2442.2812 | 122.0535 | -0.11444 | 121.9711 | 0.14932 | -0.008469 | -0.007421 | -0.025017 | 0.045421 | 0.090161 | -0.067295 | 121.9275 | 121.917 | 121.865 | 121.76 | -0.079953 | -0.040873 | -0.04722 | -0.026063 | 0.26376 | 0.10597 | 0.10702 | 0.089424 | 0.15986 | 0.2046 | 0.047146 | 121.9732 | 121.9627 | 121.9108 | 121.8058 | -0.034177 | 0.004903 | -0.001444 | 0.019713 | 122.0074 | 121.9747 | 121.945 | 121.9123
2444.0312 | 122.0947 | -0.059509 | 121.9345 | 0.14932 | -0.008469 | -0.016578 | -0.025017 | 0.045421 | 0.090161 | -0.067295 | 121.9275 | 121.9261 | 121.865 | 121.7508 | -0.079953 | -0.040873 | -0.04722 | -0.026063 | 0.20883 | 0.05104 | 0.042931 | 0.034492 | 0.10493 | 0.14967 | -0.007786 | 121.9732 | 121.9719 | 121.9108 | 121.7966 | -0.034177 | 0.004903 | -0.001444 | 0.019713 | 122.0074 | 121.9747 | 121.945 | 121.9123
2445.9062 | 121.9711 | -0.11444 | 121.9711 | 0.14932 | 0.000689 | -0.016578 | -0.01586 | 0.045421 | 0.090161 | -0.067295 | 121.932 | 121.9215 | 121.8696 | 121.7508 | -0.079953 | -0.045451 | -0.042641 | -0.021484 | 0.26376 | 0.11513 | 0.097863 | 0.098581 | 0.15986 | 0.2046 | 0.047146 | 121.9778 | 121.9673 | 121.9154 | 121.7966 | -0.034177 | 0.000325 | 0.003135 | 0.024292 | 122.012 | 121.9747 | 121.9496 | 121.9123
2449.4844 | 122.0856 | -0.082397 | 121.9528 | 0.1539 | -0.00389 | -0.012 | -0.025017 | 0.045421 | 0.085583 | -0.058139 | 121.9275 | 121.917 | 121.865 | 121.7554 | -0.079953 | -0.031717 | -0.042641 | -0.026063 | 0.2363 | 0.078507 | 0.070397 | 0.05738 | 0.12782 | 0.16798 | 0.024258 | 121.9732 | 121.9627 | 121.9108 | 121.8012 | -0.034177 | 0.014059 | 0.003135 | 0.019713 | 122.0074 | 121.9701 | 121.945 | 121.9077
2453.375 | 122.1039 | -0.07782 | 121.9345 | 0.1539 | 0.000689 | -0.016578 | -0.020438 | 0.049999 | 0.09474 | -0.067295 | 121.9275 | 121.9261 | 121.8696 | 121.7463 | -0.070797 | -0.045451 | -0.042641 | -0.026063 | 0.23172 | 0.078509 | 0.061242 | 0.057382 | 0.12782 | 0.17256 | 0.010525 | 121.9732 | 121.9719 | 121.9154 | 121.792 | -0.025021 | 0.000325 | 0.003135 | 0.019713 | 121.9982 | 121.9701 | 121.9404 | 121.9123
2459.2188 | 122.0764 | -0.09613 | 121.9345 | 0.14932 | 0.009846 | -0.012 | -0.01586 | 0.049999 | 0.090161 | -0.062717 | 121.9275 | 121.9215 | 121.865 | 121.7463 | -0.070797 | -0.036295 | -0.042641 | -0.030641 | 0.24545 | 0.10598 | 0.08413 | 0.08027 | 0.14613 | 0.18629 | 0.033413 | 121.9732 | 121.9673 | 121.9108 | 121.792 | -0.025021 | 0.009481 | 0.003135 | 0.015135 | 121.9982 | 121.9701 | 121.9358 | 121.9077
2460.9375 | 122.0856 | -0.10071 | 121.9757 | 0.14474 | 0.000689 | -0.012 | -0.020438 | 0.049999 | 0.09474 | -0.062717 | 121.9275 | 121.9261 | 121.8605 | 121.76 | -0.075375 | -0.045451 | -0.04722 | -0.021484 | 0.24545 | 0.1014 | 0.088708 | 0.08027 | 0.15071 | 0.19545 | 0.037991 | 121.9732 | 121.9719 | 121.9062 | 121.8058 | -0.029599 | 0.000325 | -0.001444 | 0.024292 | 122.0028 | 121.9747 | 121.9358 | 121.9077
2462.6406 | 121.9803 | -0.11444 | 121.9757 | 0.15848 | 0.000689 | -0.007421 | -0.006703 | 0.059155 | 0.09474 | -0.058139 | 121.932 | 121.9215 | 121.8696 | 121.7554 | -0.075375 | -0.040873 | -0.04722 | -0.021484 | 0.27292 | 0.11513 | 0.10702 | 0.10774 | 0.1736 | 0.20918 | 0.056302 | 121.9778 | 121.9673 | 121.9154 | 121.8012 | -0.029599 | 0.004903 | -0.001444 | 0.024292 | 122.0074 | 121.9792 | 121.945 | 121.9168
2464.4062 | 122.1268 | -0.09613 | 121.9437 | 0.14474 | 0.005267 | 0.001736 | -0.01586 | 0.045421 | 0.090161 | -0.058139 | 121.9275 | 121.917 | 121.8742 | 121.76 | -0.070797 | -0.031717 | -0.042641 | -0.026063 | 0.24087 | 0.1014 | 0.097866 | 0.08027 | 0.14155 | 0.18629 | 0.037991 | 121.9732 | 121.9627 | 121.92 | 121.8058 | -0.025021 | 0.014059 | 0.003135 | 0.019713 | 121.9982 | 121.9701 | 121.945 | 121.9168
2466.1719 | 122.0535 | -0.10071 | 121.9528 | 0.14932 | 0.005267 | -0.002842 | -0.011281 | 0.059155 | 0.1039 | -0.058139 | 121.9275 | 121.9261 | 121.8696 | 121.7554 | -0.075375 | -0.040873 | -0.038063 | -0.030641 | 0.25003 | 0.10597 | 0.097866 | 0.089427 | 0.15986 | 0.2046 | 0.042569 | 121.9732 | 121.9719 | 121.9154 | 121.8012 | -0.029599 | 0.004903 | 0.007713 | 0.015135 | 122.0028 | 121.9655 | 121.945 | 121.9077
2467.9375 | 122.1405 | -0.082397 | 121.9528 | 0.1539 | 0.009846 | -0.007421 | -0.011281 | 0.049999 | 0.099318 | -0.058139 | 121.9275 | 121.9261 | 121.8696 | 121.7463 | -0.070797 | -0.031717 | -0.04722 | -0.026063 | 0.2363 | 0.092243 | 0.074976 | 0.071116 | 0.1324 | 0.18172 | 0.024258 | 121.9732 | 121.9719 | 121.9154 | 121.792 | -0.025021 | 0.014059 | -0.001444 | 0.019713 | 121.9982 | 121.9747 | 121.9404 | 121.9168
2469.7031 | 122.049 | -0.1236 | 121.9528 | 0.14932 | 0.014425 | 0.006315 | -0.011281 | 0.059155 | 0.099318 | -0.048983 | 121.932 | 121.9215 | 121.865 | 121.7554 | -0.075375 | -0.040873 | -0.042641 | -0.026063 | 0.27292 | 0.13802 | 0.12991 | 0.11231 | 0.18275 | 0.22291 | 0.074613 | 121.9778 | 121.9673 | 121.9108 | 121.8012 | -0.029599 | 0.004903 | 0.003135 | 0.019713 | 122.0074 | 121.9747 | 121.9404 | 121.9077
2471.4062 | 122.0398 | -0.11902 | 121.9574 | 0.14932 | 0.014425 | 0.006315 | -0.011281 | 0.059155 | 0.1039 | -0.048983 | 121.9275 | 121.9215 | 121.865 | 121.7508 | -0.075375 | -0.040873 | -0.04722 | -0.030641 | 0.26834 | 0.13344 | 0.12533 | 0.10774 | 0.17817 | 0.22292 | 0.070036 | 121.9732 | 121.9673 | 121.9108 | 121.7966 | -0.029599 | 0.004903 | -0.001444 | 0.015135 | 122.0028 | 121.9747 | 121.9404 | 121.9123
2473.1094 | 122.1313 | -0.082397 | 121.9482 | 0.14474 | 0.009846 | 0.006315 | -0.002124 | 0.059155 | 0.099318 | -0.053561 | 121.932 | 121.9307 | 121.865 | 121.76 | -0.079953 | -0.036295 | -0.04722 | -0.030641 | 0.22714 | 0.092243 | 0.088712 | 0.080273 | 0.14155 | 0.18172 | 0.028836 | 121.9778 | 121.9765 | 121.9108 | 121.8058 | -0.034177 | 0.009481 | -0.001444 | 0.015135 | 122.012 | 121.9792 | 121.945 | 121.9123
2474.875 | 122.0901 | -0.068665 | 121.9437 | 0.14932 | 0.019004 | 0.010893 | -0.002124 | 0.06831 | 0.1039 | -0.048983 | 121.932 | 121.9307 | 121.8696 | 121.7554 | -0.079953 | -0.040873 | -0.042641 | -0.026063 | 0.21799 | 0.087669 | 0.079558 | 0.066541 | 0.13698 | 0.17256 | 0.019682 | 121.9778 | 121.9765 | 121.9154 | 121.8012 | -0.034177 | 0.004903 | 0.003135 | 0.019713 | 122.012 | 121.9747 | 121.9496 | 121.9123
2476.5625 | 122.1313 | -0.068665 | 121.9345 | 0.1539 | 0.019004 | 0.010893 | 0.002454 | 0.072888 | 0.11305 | -0.039826 | 121.9366 | 121.9261 | 121.8696 | 121.76 | -0.075375 | -0.036295 | -0.042641 | -0.021484 | 0.22257 | 0.087669 | 0.079558 | 0.071119 | 0.14155 | 0.18172 | 0.028839 | 121.9824 | 121.9719 | 121.9154 | 121.8058 | -0.029599 | 0.009481 | 0.003135 | 0.024292 | 122.012 | 121.9792 | 121.945 | 121.9123
2478.3125 | 122.0444 | -0.10529 | 121.994 | 0.14932 | 0.03274 | 0.010893 | 0.002454 | 0.072888 | 0.11763 | -0.039826 | 121.9366 | 121.9215 | 121.8696 | 121.7508 | -0.079953 | -0.040873 | -0.038063 | -0.030641 | 0.25461 | 0.13803 | 0.11618 | 0.10774 | 0.17817 | 0.22292 | 0.06546 | 121.9824 | 121.9673 | 121.9154 | 121.7966 | -0.034177 | 0.004903 | 0.007713 | 0.015135 | 122.0166 | 121.9747 | 121.9496 | 121.9077
2480.0781 | 122.1313 | -0.064087 | 121.9391 | 0.14932 | 0.03274 | 0.020051 | 0.007033 | 0.06831 | 0.11763 | -0.039826 | 121.932 | 121.9261 | 121.8605 | 121.7554 | -0.079953 | -0.040873 | -0.042641 | -0.026063 | 0.21341 | 0.096827 | 0.084138 | 0.07112 | 0.1324 | 0.18172 | 0.024261 | 121.9778 | 121.9719 | 121.9062 | 121.8012 | -0.034177 | 0.004903 | 0.003135 | 0.019713 | 122.012 | 121.9747 | 121.9404 | 121.9031
2481.8281 | 122.0581 | -0.13275 | 121.962 | 0.1539 | 0.028162 | 0.024629 | 0.01619 | 0.082044 | 0.13137 | -0.03067 | 121.932 | 121.9215 | 121.8742 | 121.7508 | -0.075375 | -0.040873 | -0.042641 | -0.030641 | 0.28665 | 0.16091 | 0.15738 | 0.14894 | 0.2148 | 0.26412 | 0.10208 | 121.9778 | 121.9673 | 121.92 | 121.7966 | -0.029599 | 0.004903 | 0.003135 | 0.015135 | 122.0074 | 121.9747 | 121.9496 | 121.9168
2483.5312 | 122.0261 | -0.10986 | 121.9849 | 0.14932 | 0.037319 | 0.024629 | 0.01619 | 0.086622 | 0.13137 | -0.026092 | 121.9366 | 121.9307 | 121.865 | 121.7508 | -0.079953 | -0.040873 | -0.042641 | -0.030641 | 0.25918 | 0.14718 | 0.13449 | 0.12605 | 0.19649 | 0.24123 | 0.083771 | 121.9824 | 121.9765 | 121.9108 | 121.7966 | -0.034177 | 0.004903 | 0.003135 | 0.015135 | 122.0166 | 121.9792 | 121.945 | 121.9077
2485.2969 | 122.1085 | -0.073242 | 121.962 | 0.14474 | 0.03274 | 0.038365 | 0.020768 | 0.082044 | 0.13137 | -0.021514 | 121.932 | 121.9261 | 121.8696 | 121.7554 | -0.075375 | -0.036295 | -0.038063 | -0.030641 | 0.21799 | 0.10598 | 0.11161 | 0.09401 | 0.15529 | 0.20461 | 0.051728 | 121.9778 | 121.9719 | 121.9154 | 121.8012 | -0.029599 | 0.009481 | 0.007713 | 0.015135 | 122.0074 | 121.9701 | 121.945 | 121.9077
2487.0469 | 122.0581 | -0.09613 | 121.9574 | 0.15848 | 0.046477 | 0.029208 | 0.025347 | 0.0912 | 0.13137 | -0.007779 | 121.9366 | 121.9307 | 121.8696 | 121.7508 | -0.079953 | -0.045451 | -0.042641 | -0.030641 | 0.25461 | 0.14261 | 0.12534 | 0.12148 | 0.18733 | 0.2275 | 0.088351 | 121.9824 | 121.9765 | 121.9154 | 121.7966 | -0.034177 | 0.000325 | 0.003135 | 0.015135 | 122.0166 | 121.9792 | 121.9496 | 121.9123
2488.75 | 122.0947 | -0.09613 | 121.9574 | 0.14932 | 0.051056 | 0.042944 | 0.039082 | 0.10493 | 0.13595 | -0.026092 | 121.932 | 121.9261 | 121.8696 | 121.7508 | -0.084531 | -0.036295 | -0.042641 | -0.035219 | 0.24545 | 0.14719 | 0.13907 | 0.13521 | 0.20106 | 0.23208 | 0.070038 | 121.9778 | 121.9719 | 121.9154 | 121.7966 | -0.038755 | 0.009481 | 0.003135 | 0.010557 | 122.0166 | 121.9747 | 121.9541 | 121.9123
2490.5312 | 122.1313 | -0.054932 | 121.9391 | 0.14474 | 0.060213 | 0.047522 | 0.034504 | 0.10951 | 0.1451 | -0.003201 | 121.9275 | 121.9307 | 121.8696 | 121.7463 | -0.075375 | -0.045451 | -0.04722 | -0.021484 | 0.19968 | 0.11514 | 0.10245 | 0.089436 | 0.16444 | 0.20003 | 0.051731 | 121.9732 | 121.9765 | 121.9154 | 121.792 | -0.029599 | 0.000325 | -0.001444 | 0.024292 | 122.0028 | 121.9747 | 121.945 | 121.9168
2492.2969 | 122.0947 | -0.082397 | 121.9574 | 0.14932 | 0.055634 | 0.052101 | 0.043661 | 0.11867 | 0.15426 | -0.007779 | 121.932 | 121.9215 | 121.8696 | 121.76 | -0.075375 | -0.040873 | -0.042641 | -0.026063 | 0.23172 | 0.13803 | 0.1345 | 0.12606 | 0.20106 | 0.23666 | 0.074618 | 121.9778 | 121.9673 | 121.9154 | 121.8058 | -0.029599 | 0.004903 | 0.003135 | 0.019713 | 122.0074 | 121.9747 | 121.945 | 121.9123
2494.0625 | 122.1497 | -0.07782 | 121.9666 | 0.14932 | 0.069371 | 0.065837 | 0.043661 | 0.12325 | 0.15884 | 0.010533 | 121.9275 | 121.9215 | 121.865 | 121.7554 | -0.075375 | -0.054607 | -0.04722 | -0.026063 | 0.22714 | 0.14719 | 0.14366 | 0.12148 | 0.20107 | 0.23666 | 0.088353 | 121.9732 | 121.9673 | 121.9108 | 121.8012 | -0.029599 | -0.008831 | -0.001444 | 0.019713 | 122.0028 | 121.9747 | 121.9404 | 121.9123
2495.8281 | 122.0993 | -0.07782 | 121.9574 | 0.1539 | 0.078529 | 0.074994 | 0.057396 | 0.12782 | 0.16799 | 0.010533 | 121.932 | 121.9307 | 121.8696 | 121.7508 | -0.075375 | -0.040873 | -0.042641 | -0.021484 | 0.23172 | 0.15635 | 0.15281 | 0.13522 | 0.20564 | 0.24581 | 0.088353 | 121.9778 | 121.9765 | 121.9154 | 121.7966 | -0.029599 | 0.004903 | 0.003135 | 0.024292 | 122.0074 | 121.9747 | 121.945 | 121.9123
2497.5312 | 122.1313 | -0.091553 | 121.9574 | 0.14474 | 0.087686 | 0.079572 | 0.061975 | 0.13698 | 0.17715 | 0.028846 | 121.9412 | 121.9353 | 121.8742 | 121.76 | -0.075375 | -0.036295 | -0.04722 | -0.035219 | 0.2363 | 0.17924 | 0.17112 | 0.15353 | 0.22853 | 0.2687 | 0.1204 | 121.987 | 121.9811 | 121.92 | 121.8058 | -0.029599 | 0.009481 | -0.001444 | 0.010557 | 122.0166 | 121.9884 | 121.9496 | 121.9214
2499.2969 | 122.1222 | -0.073242 | 121.9482 | 0.1539 | 0.10142 | 0.079572 | 0.07571 | 0.14614 | 0.18173 | 0.033424 | 121.932 | 121.9307 | 121.8742 | 121.7508 | -0.070797 | -0.036295 | -0.04722 | -0.030641 | 0.22714 | 0.17467 | 0.15281 | 0.14895 | 0.21938 | 0.25497 | 0.10667 | 121.9778 | 121.9765 | 121.92 | 121.7966 | -0.025021 | 0.009481 | -0.001444 | 0.015135 | 122.0028 | 121.9792 | 121.945 | 121.9214
2501.0625 | 122.0627 | -0.10071 | 121.9711 | 0.15848 | 0.106 | 0.097887 | 0.084867 | 0.15529 | 0.19546 | 0.038003 | 121.932 | 121.9307 | 121.8696 | 121.76 | -0.079953 | -0.040873 | -0.042641 | -0.021484 | 0.25919 | 0.20671 | 0.1986 | 0.18557 | 0.256 | 0.29617 | 0.13871 | 121.9778 | 121.9765 | 121.9154 | 121.8058 | -0.034177 | 0.004903 | 0.003135 | 0.024292 | 122.012 | 121.9747 | 121.9496 | 121.9123
2502.8281 | 122.1039 | -0.073242 | 121.9894 | 0.14474 | 0.11974 | 0.10247 | 0.094024 | 0.15987 | 0.2092 | 0.042581 | 121.9366 | 121.9307 | 121.8696 | 121.76 | -0.075375 | -0.036295 | -0.042641 | -0.030641 | 0.21799 | 0.19298 | 0.17571 | 0.16727 | 0.23311 | 0.28244 | 0.11582 | 121.9824 | 121.9765 | 121.9154 | 121.8058 | -0.029599 | 0.009481 | 0.003135 | 0.015135 | 122.012 | 121.9792 | 121.945 | 121.9123
2504.5312 | 122.0032 | -0.11902 | 121.9849 | 0.1539 | 0.1289 | 0.1162 | 0.098602 | 0.16903 | 0.21836 | 0.056315 | 121.9412 | 121.9353 | 121.865 | 121.76 | -0.075375 | -0.045451 | -0.04722 | -0.026063 | 0.27292 | 0.24791 | 0.23522 | 0.21762 | 0.28804 | 0.33737 | 0.17533 | 121.987 | 121.9811 | 121.9108 | 121.8058 | -0.029599 | 0.000325 | -0.001444 | 0.019713 | 122.0166 | 121.9884 | 121.9404 | 121.9123
2506.3125 | 122.1268 | -0.086975 | 121.9299 | 0.1539 | 0.14263 | 0.12994 | 0.10776 | 0.18276 | 0.22751 | 0.065472 | 121.9366 | 121.9353 | 121.8742 | 121.7554 | -0.079953 | -0.040873 | -0.04722 | -0.030641 | 0.24088 | 0.22961 | 0.21691 | 0.19473 | 0.26973 | 0.31449 | 0.15245 | 121.9824 | 121.9811 | 121.92 | 121.8012 | -0.034177 | 0.004903 | -0.001444 | 0.015135 | 122.0166 | 121.9838 | 121.9541 | 121.9214
2508.0781 | 122.0261 | -0.12817 | 122.0032 | 0.1539 | 0.15179 | 0.14825 | 0.12607 | 0.19649 | 0.24583 | 0.079206 | 121.9366 | 121.9261 | 121.8742 | 121.7508 | -0.075375 | -0.040873 | -0.042641 | -0.030641 | 0.28207 | 0.27996 | 0.27643 | 0.25425 | 0.32467 | 0.374 | 0.20738 | 121.9824 | 121.9719 | 121.92 | 121.7966 | -0.029599 | 0.004903 | 0.003135 | 0.015135 | 122.012 | 121.9792 | 121.9496 | 121.9168
2509.7812 | 122.1268 | -0.054932 | 121.9391 | 0.1539 | 0.16095 | 0.15741 | 0.13523 | 0.2148 | 0.25498 | 0.088362 | 121.932 | 121.9307 | 121.8742 | 121.7691 | -0.075375 | -0.036295 | -0.042641 | -0.021484 | 0.20883 | 0.21588 | 0.21234 | 0.19016 | 0.26974 | 0.30991 | 0.14329 | 121.9778 | 121.9765 | 121.92 | 121.8149 | -0.029599 | 0.009481 | 0.003135 | 0.024292 | 122.0074 | 121.9747 | 121.9496 | 121.9168
2511.5469 | 122.0947 | -0.091553 | 121.962 | 0.15848 | 0.17926 | 0.17114 | 0.15354 | 0.22396 | 0.26872 | 0.11125 | 121.9412 | 121.9307 | 121.8696 | 121.76 | -0.075375 | -0.036295 | -0.04722 | -0.030641 | 0.25003 | 0.27082 | 0.2627 | 0.2451 | 0.31551 | 0.36027 | 0.20281 | 121.987 | 121.9765 | 121.9154 | 121.8058 | -0.029599 | 0.009481 | -0.001444 | 0.015135 | 122.0166 | 121.9884 | 121.945 | 121.9168
2513.2969 | 122.0215 | -0.1236 | 121.9803 | 0.15848 | 0.18842 | 0.1803 | 0.1627 | 0.24227 | 0.28245 | 0.11583 | 121.932 | 121.9261 | 121.8788 | 121.76 | -0.079953 | -0.045451 | -0.042641 | -0.030641 | 0.28207 | 0.31202 | 0.3039 | 0.2863 | 0.36587 | 0.40605 | 0.23943 | 121.9778 | 121.9719 | 121.9245 | 121.8058 | -0.034177 | 0.000325 | 0.003135 | 0.015135 | 122.012 | 121.9747 | 121.9587 | 121.9214
2515.0625 | 122.049 | -0.10986 | 121.994 | 0.1539 | 0.20674 | 0.19862 | 0.18559 | 0.25143 | 0.29619 | 0.13414 | 121.9229 | 121.9307 | 121.8742 | 121.76 | -0.079953 | -0.040873 | -0.051798 | -0.026063 | 0.26376 | 0.3166 | 0.30848 | 0.29546 | 0.36129 | 0.40605 | 0.24401 | 121.9686 | 121.9765 | 121.92 | 121.8058 | -0.034177 | 0.004903 | -0.006022 | 0.019713 | 122.0028 | 121.9747 | 121.9541 | 121.926
2516.8281 | 122.1451 | -0.064087 | 121.9528 | 0.14932 | 0.22047 | 0.21693 | 0.19933 | 0.26516 | 0.3145 | 0.14788 | 121.9366 | 121.9307 | 121.8742 | 121.7508 | -0.075375 | -0.036295 | -0.04722 | -0.035219 | 0.21341 | 0.28456 | 0.28102 | 0.26342 | 0.32925 | 0.37859 | 0.21197 | 121.9824 | 121.9765 | 121.92 | 121.7966 | -0.029599 | 0.009481 | -0.001444 | 0.010557 | 122.012 | 121.9838 | 121.9496 | 121.9214
2518.5469 | 122.1222 | -0.086975 | 121.9757 | 0.15848 | 0.24337 | 0.23067 | 0.20849 | 0.29263 | 0.32824 | 0.16619 | 121.9412 | 121.9307 | 121.8788 | 121.7554 | -0.075375 | -0.040873 | -0.04722 | -0.030641 | 0.24545 | 0.33034 | 0.31764 | 0.29546 | 0.3796 | 0.41521 | 0.25317 | 121.987 | 121.9765 | 121.9245 | 121.8012 | -0.029599 | 0.004903 | -0.001444 | 0.015135 | 122.0166 | 121.9884 | 121.9541 | 121.926
2520.3281 | 122.0078 | -0.13275 | 122.0032 | 0.15848 | 0.25252 | 0.23982 | 0.23138 | 0.30636 | 0.35113 | 0.17993 | 121.9366 | 121.9307 | 121.8742 | 121.76 | -0.079953 | -0.036295 | -0.04722 | -0.030641 | 0.29123 | 0.38528 | 0.37257 | 0.36413 | 0.43912 | 0.48388 | 0.31268 | 121.9824 | 121.9765 | 121.92 | 121.8058 | -0.034177 | 0.009481 | -0.001444 | 0.015135 | 122.0166 | 121.9838 | 121.9541 | 121.9214
2522.0312 | 122.0398 | -0.10529 | 121.9803 | 0.16306 | 0.26626 | 0.26272 | 0.24511 | 0.31552 | 0.37402 | 0.19824 | 121.932 | 121.9261 | 121.8696 | 121.7554 | -0.079953 | -0.036295 | -0.042641 | -0.030641 | 0.26834 | 0.37155 | 0.368 | 0.3504 | 0.42081 | 0.47931 | 0.30352 | 121.9778 | 121.9719 | 121.9154 | 121.8012 | -0.034177 | 0.009481 | 0.003135 | 0.015135 | 122.012 | 121.9747 | 121.9496 | 121.9123
2523.7812 | 122.0856 | -0.10071 | 121.9437 | 0.16764 | 0.28458 | 0.27645 | 0.25427 | 0.33841 | 0.36944 | 0.21655 | 121.9458 | 121.9307 | 121.8742 | 121.7508 | -0.079953 | -0.031717 | -0.04722 | -0.026063 | 0.26834 | 0.38528 | 0.37716 | 0.35498 | 0.43912 | 0.47015 | 0.31726 | 121.9915 | 121.9765 | 121.92 | 121.7966 | -0.034177 | 0.014059 | -0.001444 | 0.019713 | 122.0257 | 121.993 | 121.9541 | 121.9214
2525.5625 | 122.1039 | -0.07782 | 121.9437 | 0.16764 | 0.31205 | 0.29935 | 0.27716 | 0.35672 | 0.3786 | 0.23029 | 121.9366 | 121.9307 | 121.8788 | 121.76 | -0.070797 | -0.040873 | -0.04722 | -0.021484 | 0.24546 | 0.38987 | 0.37717 | 0.35498 | 0.43454 | 0.45642 | 0.30811 | 121.9824 | 121.9765 | 121.9245 | 121.8058 | -0.025021 | 0.004903 | -0.001444 | 0.024292 | 122.0074 | 121.9838 | 121.9496 | 121.926
2527.2656 | 122.0993 | -0.064087 | 121.962 | 0.16306 | 0.33036 | 0.33597 | 0.30463 | 0.38877 | 0.41065 | 0.25318 | 121.9412 | 121.9353 | 121.8696 | 121.7508 | -0.075375 | -0.036295 | -0.04722 | -0.030641 | 0.22714 | 0.39445 | 0.40006 | 0.36872 | 0.45286 | 0.47474 | 0.31726 | 121.987 | 121.9811 | 121.9154 | 121.7966 | -0.029599 | 0.009481 | -0.001444 | 0.015135 | 122.0166 | 121.9884 | 121.945 | 121.9168
2529.0312 | 122.0306 | -0.10529 | 121.9711 | 0.16306 | 0.34868 | 0.35429 | 0.33211 | 0.40708 | 0.42896 | 0.27607 | 121.932 | 121.9307 | 121.8696 | 121.76 | -0.075375 | -0.045451 | -0.04722 | -0.030641 | 0.26834 | 0.45397 | 0.45958 | 0.43739 | 0.51237 | 0.53425 | 0.38135 | 121.9778 | 121.9765 | 121.9154 | 121.8058 | -0.029599 | 0.000325 | -0.001444 | 0.015135 | 122.0074 | 121.9792 | 121.945 | 121.9168
2530.7969 | 122.1222 | -0.086975 | 121.9894 | 0.16764 | 0.37615 | 0.3726 | 0.355 | 0.42997 | 0.45185 | 0.30812 | 121.9275 | 121.9307 | 121.8696 | 121.7508 | -0.079953 | -0.036295 | -0.042641 | -0.030641 | 0.25461 | 0.46313 | 0.45958 | 0.44197 | 0.51694 | 0.53883 | 0.39509 | 121.9732 | 121.9765 | 121.9154 | 121.7966 | -0.034177 | 0.009481 | 0.003135 | 0.015135 | 122.0074 | 121.9701 | 121.9496 | 121.9123
2532.5469 | 122.0444 | -0.10071 | 121.994 | 0.16306 | 0.4082 | 0.40923 | 0.36873 | 0.45744 | 0.47932 | 0.32185 | 121.9412 | 121.9261 | 121.8742 | 121.7554 | -0.070797 | -0.040873 | -0.04722 | -0.026063 | 0.26377 | 0.50891 | 0.50994 | 0.46944 | 0.55815 | 0.58003 | 0.42256 | 121.987 | 121.9719 | 121.92 | 121.8012 | -0.025021 | 0.004903 | -0.001444 | 0.019713 | 122.012 | 121.9884 | 121.945 | 121.9214
2534.2969 | 122.0352 | -0.10986 | 121.9757 | 0.16764 | 0.4311 | 0.41839 | 0.40078 | 0.47117 | 0.4839 | 0.34474 | 121.932 | 121.9307 | 121.865 | 121.76 | -0.075375 | -0.045451 | -0.04722 | -0.035219 | 0.2775 | 0.54096 | 0.52825 | 0.51065 | 0.58103 | 0.59377 | 0.4546 | 121.9778 | 121.9765 | 121.9108 | 121.8058 | -0.029599 | 0.000325 | -0.001444 | 0.010557 | 122.0074 | 121.9792 | 121.9404 | 121.9123
2536 | 122.1222 | -0.073242 | 121.9528 | 0.17679 | 0.44941 | 0.44586 | 0.40994 | 0.50322 | 0.51137 | 0.36305 | 121.932 | 121.9215 | 121.8742 | 121.76 | -0.079953 | -0.045451 | -0.04722 | -0.026063 | 0.25003 | 0.52265 | 0.5191 | 0.48318 | 0.57646 | 0.58461 | 0.43629 | 121.9778 | 121.9673 | 121.92 | 121.8058 | -0.034177 | 0.000325 | -0.001444 | 0.019713 | 122.012 | 121.9792 | 121.9541 | 121.9214
2537.7656 | 121.994 | -0.11444 | 121.9849 | 0.18137 | 0.47231 | 0.47333 | 0.44199 | 0.52153 | 0.548 | 0.3951 | 121.9366 | 121.9307 | 121.8788 | 121.7554 | -0.075375 | -0.036295 | -0.038063 | -0.026063 | 0.29581 | 0.58675 | 0.58777 | 0.55643 | 0.63597 | 0.66244 | 0.50954 | 121.9824 | 121.9765 | 121.9245 | 121.8012 | -0.029599 | 0.009481 | 0.007713 | 0.019713 | 122.012 | 121.9747 | 121.9541 | 121.9168
2539.4531 | 122.1451 | -0.050354 | 121.9391 | 0.18595 | 0.47689 | 0.5008 | 0.47404 | 0.56273 | 0.57547 | 0.41799 | 121.9366 | 121.9261 | 121.8696 | 121.7646 | -0.075375 | -0.040873 | -0.038063 | -0.030641 | 0.2363 | 0.52724 | 0.55116 | 0.52439 | 0.61308 | 0.62582 | 0.46835 | 121.9824 | 121.9719 | 121.9154 | 121.8103 | -0.029599 | 0.004903 | 0.007713 | 0.015135 | 122.012 | 121.9747 | 121.945 | 121.9077
2541.2188 | 122.1359 | -0.064087 | 121.9345 | 0.18137 | 0.4952 | 0.52828 | 0.50151 | 0.57646 | 0.59836 | 0.45004 | 121.9366 | 121.9307 | 121.865 | 121.7646 | -0.070797 | -0.040873 | -0.04722 | -0.030641 | 0.24546 | 0.55929 | 0.59236 | 0.5656 | 0.64055 | 0.66245 | 0.51412 | 121.9824 | 121.9765 | 121.9108 | 121.8103 | -0.025021 | 0.004903 | -0.001444 | 0.015135 | 122.0074 | 121.9838 | 121.9358 | 121.9123
2542.9844 | 122.081 | -0.10071 | 121.9757 | 0.19053 | 0.54557 | 0.56948 | 0.54272 | 0.62682 | 0.63499 | 0.49124 | 121.9366 | 121.9261 | 121.8833 | 121.76 | -0.079953 | -0.036295 | -0.04722 | -0.030641 | 0.29124 | 0.64628 | 0.67019 | 0.64343 | 0.72753 | 0.7357 | 0.59195 | 121.9824 | 121.9719 | 121.9291 | 121.8058 | -0.034177 | 0.009481 | -0.001444 | 0.015135 | 122.0166 | 121.9838 | 121.9633 | 121.9306
2544.6875 | 122.049 | -0.10986 | 121.9849 | 0.19968 | 0.57304 | 0.60611 | 0.57019 | 0.65429 | 0.66704 | 0.51871 | 121.9366 | 121.9353 | 121.8742 | 121.76 | -0.079953 | -0.045451 | -0.04722 | -0.021484 | 0.30955 | 0.6829 | 0.71598 | 0.68005 | 0.76415 | 0.7769 | 0.62857 | 121.9824 | 121.9811 | 121.92 | 121.8058 | -0.034177 | 0.000325 | -0.001444 | 0.024292 | 122.0166 | 121.9838 | 121.9541 | 121.9214
2546.4531 | 122.1176 | -0.07782 | 121.9437 | 0.20426 | 0.60509 | 0.63358 | 0.60224 | 0.69091 | 0.70366 | 0.54618 | 121.9412 | 121.9353 | 121.8696 | 121.7554 | -0.079953 | -0.040873 | -0.042641 | -0.039797 | 0.28208 | 0.68291 | 0.7114 | 0.68006 | 0.76873 | 0.78148 | 0.624 | 121.987 | 121.9811 | 121.9154 | 121.8012 | -0.034177 | 0.004903 | 0.003135 | 0.005979 | 122.0211 | 121.9838 | 121.9496 | 121.9123
2548.2188 | 122.0901 | -0.082397 | 121.9528 | 0.218 | 0.63257 | 0.67021 | 0.62971 | 0.72296 | 0.73114 | 0.58281 | 121.932 | 121.9353 | 121.8833 | 121.7554 | -0.079953 | -0.040873 | -0.038063 | -0.030641 | 0.30039 | 0.71496 | 0.75261 | 0.7121 | 0.80536 | 0.81353 | 0.6652 | 121.9778 | 121.9811 | 121.9291 | 121.8012 | -0.034177 | 0.004903 | 0.007713 | 0.015135 | 122.012 | 121.9701 | 121.9633 | 121.9214
2549.9844 | 122.1497 | -0.059509 | 121.9666 | 0.21342 | 0.65546 | 0.68395 | 0.66176 | 0.73669 | 0.75861 | 0.60112 | 121.9366 | 121.9261 | 121.8742 | 121.76 | -0.075375 | -0.040873 | -0.042641 | -0.026063 | 0.27293 | 0.71497 | 0.74346 | 0.72127 | 0.7962 | 0.81812 | 0.66063 | 121.9824 | 121.9719 | 121.92 | 121.8058 | -0.029599 | 0.004903 | 0.003135 | 0.019713 | 122.012 | 121.9792 | 121.9496 | 121.9168
2551.6875 | 122.1451 | -0.07782 | 121.9391 | 0.22715 | 0.69209 | 0.73889 | 0.69839 | 0.78705 | 0.80439 | 0.6469 | 121.9412 | 121.9399 | 121.8742 | 121.7554 | -0.075375 | -0.045451 | -0.038063 | -0.035219 | 0.30497 | 0.76991 | 0.81671 | 0.77621 | 0.86487 | 0.88221 | 0.72472 | 121.987 | 121.9856 | 121.92 | 121.8012 | -0.029599 | 0.000325 | 0.007713 | 0.010557 | 122.0166 | 121.9792 | 121.9496 | 121.9123
2553.4531 | 122.0993 | -0.091553 | 121.9528 | 0.23173 | 0.72872 | 0.75721 | 0.73043 | 0.81452 | 0.8227 | 0.66979 | 121.9412 | 121.9399 | 121.8696 | 121.76 | -0.075375 | -0.040873 | -0.038063 | -0.030641 | 0.32328 | 0.82027 | 0.84876 | 0.82199 | 0.90607 | 0.91426 | 0.76134 | 121.987 | 121.9856 | 121.9154 | 121.8058 | -0.029599 | 0.004903 | 0.007713 | 0.015135 | 122.0166 | 121.9792 | 121.945 | 121.9077
2555.1562 | 122.0123 | -0.11444 | 121.9528 | 0.24547 | 0.76535 | 0.80299 | 0.76248 | 0.84656 | 0.86391 | 0.71557 | 121.9412 | 121.9261 | 121.8742 | 121.7554 | -0.075375 | -0.040873 | -0.038063 | -0.035219 | 0.35991 | 0.87979 | 0.91743 | 0.87693 | 0.961 | 0.97835 | 0.83001 | 121.987 | 121.9719 | 121.92 | 121.8012 | -0.029599 | 0.004903 | 0.007713 | 0.010557 | 122.0166 | 121.9792 | 121.9496 | 121.9123
2556.9219 | 122.0856 | -0.073242 | 121.962 | 0.26378 | 0.80198 | 0.83504 | 0.80369 | 0.89234 | 0.90054 | 0.7522 | 121.9366 | 121.9353 | 121.8788 | 121.7646 | -0.079953 | -0.045451 | -0.04722 | -0.021484 | 0.33702 | 0.87522 | 0.90828 | 0.87693 | 0.96559 | 0.97378 | 0.82544 | 121.9824 | 121.9811 | 121.9245 | 121.8103 | -0.034177 | 0.000325 | -0.001444 | 0.024292 | 122.0166 | 121.9838 | 121.9587 | 121.926
2558.625 | 122.1268 | -0.064087 | 121.9528 | 0.26378 | 0.82946 | 0.85336 | 0.82658 | 0.91523 | 0.92801 | 0.77509 | 121.9366 | 121.9307 | 121.865 | 121.76 | -0.075375 | -0.036295 | -0.04722 | -0.035219 | 0.32787 | 0.89354 | 0.91744 | 0.89067 | 0.97932 | 0.99209 | 0.83918 | 121.9824 | 121.9765 | 121.9108 | 121.8058 | -0.029599 | 0.009481 | -0.001444 | 0.010557 | 122.012 | 121.9838 | 121.9404 | 121.9123
2560.3906 | 122.0352 | -0.086975 | 121.9894 | 0.26836 | 0.85693 | 0.89456 | 0.85863 | 0.95186 | 0.96005 | 0.80714 | 121.9366 | 121.9307 | 121.8742 | 121.7554 | -0.079953 | -0.036295 | -0.042641 | -0.021484 | 0.35533 | 0.9439 | 0.98154 | 0.94561 | 1.0388 | 1.047 | 0.89411 | 121.9824 | 121.9765 | 121.92 | 121.8012 | -0.034177 | 0.009481 | 0.003135 | 0.024292 | 122.0166 | 121.9792 | 121.9541 | 121.9168
2562.0938 | 122.1039 | -0.07782 | 121.9299 | 0.28209 | 0.90272 | 0.93577 | 0.89984 | 0.97475 | 1.0013 | 0.83918 | 121.9412 | 121.9353 | 121.8833 | 121.7646 | -0.084531 | -0.036295 | -0.042641 | -0.035219 | 0.35991 | 0.98054 | 1.0136 | 0.97766 | 1.0526 | 1.0791 | 0.917 | 121.987 | 121.9811 | 121.9291 | 121.8103 | -0.038755 | 0.009481 | 0.003135 | 0.010557 | 122.0257 | 121.9838 | 121.9679 | 121.926
2563.8438 | 122.1542 | -0.050354 | 121.9666 | 0.30499 | 0.95766 | 0.98614 | 0.95936 | 1.0434 | 1.0608 | 0.90328 | 121.932 | 121.9307 | 121.8742 | 121.7646 | -0.075375 | -0.036295 | -0.042641 | -0.035219 | 0.35534 | 1.008 | 1.0365 | 1.0097 | 1.0938 | 1.1111 | 0.95363 | 121.9778 | 121.9765 | 121.92 | 121.8103 | -0.029599 | 0.009481 | 0.003135 | 0.010557 | 122.0074 | 121.9747 | 121.9496 | 121.9168
2565.625 | 122.0032 | -0.1236 | 121.9894 | 0.31872 | 1.008 | 1.0365 | 1.0097 | 1.0846 | 1.1066 | 0.95364 | 121.932 | 121.9399 | 121.8879 | 121.7691 | -0.075375 | -0.040873 | -0.042641 | -0.030641 | 0.44232 | 1.1316 | 1.1601 | 1.1333 | 1.2082 | 1.2302 | 1.0772 | 121.9778 | 121.9856 | 121.9337 | 121.8149 | -0.029599 | 0.004903 | 0.003135 | 0.015135 | 122.0074 | 121.9747 | 121.9633 | 121.9306
2567.3125 | 122.0352 | -0.11902 | 121.994 | 0.33703 | 1.0401 | 1.0686 | 1.0326 | 1.1212 | 1.1386 | 0.99026 | 121.9412 | 121.9353 | 121.8742 | 121.7646 | -0.075375 | -0.040873 | -0.042641 | -0.021484 | 0.45605 | 1.1591 | 1.1876 | 1.1516 | 1.2403 | 1.2576 | 1.1093 | 121.987 | 121.9811 | 121.92 | 121.8103 | -0.029599 | 0.004903 | 0.003135 | 0.024292 | 122.0166 | 121.9838 | 121.9496 | 121.9168
2569.0781 | 122.0856 | -0.09613 | 121.9391 | 0.35535 | 1.095 | 1.1189 | 1.0921 | 1.1762 | 1.189 | 1.0406 | 121.9412 | 121.9353 | 121.8833 | 121.7554 | -0.079953 | -0.045451 | -0.04722 | -0.030641 | 0.45148 | 1.1912 | 1.215 | 1.1883 | 1.2723 | 1.2851 | 1.1368 | 121.987 | 121.9811 | 121.9291 | 121.8012 | -0.034177 | 0.000325 | -0.001444 | 0.015135 | 122.0211 | 121.9884 | 121.9633 | 121.9306
2570.7812 | 122.0215 | -0.11902 | 121.9757 | 0.37366 | 1.1271 | 1.1601 | 1.1288 | 1.2082 | 1.2164 | 1.0635 | 121.9275 | 121.9353 | 121.8788 | 121.7646 | -0.075375 | -0.045451 | -0.04722 | -0.021484 | 0.49268 | 1.2461 | 1.2791 | 1.2478 | 1.3272 | 1.3355 | 1.1825 | 121.9732 | 121.9811 | 121.9245 | 121.8103 | -0.029599 | 0.000325 | -0.001444 | 0.024292 | 122.0028 | 121.9747 | 121.9541 | 121.926
2572.5469 | 122.1039 | -0.07782 | 121.9528 | 0.39198 | 1.1454 | 1.183 | 1.1471 | 1.2357 | 1.2531 | 1.0956 | 121.9412 | 121.9261 | 121.8788 | 121.7646 | -0.079953 | -0.040873 | -0.042641 | -0.026063 | 0.4698 | 1.2232 | 1.2608 | 1.2249 | 1.3135 | 1.3309 | 1.1734 | 121.987 | 121.9719 | 121.9245 | 121.8103 | -0.034177 | 0.004903 | 0.003135 | 0.019713 | 122.0211 | 121.9838 | 121.9587 | 121.9214
2574.2969 | 122.0215 | -0.11444 | 121.9803 | 0.40571 | 1.1729 | 1.2013 | 1.17 | 1.2494 | 1.2714 | 1.1185 | 121.9366 | 121.9353 | 121.8742 | 121.76 | -0.075375 | -0.045451 | -0.042641 | -0.026063 | 0.52015 | 1.2873 | 1.3158 | 1.2844 | 1.3639 | 1.3858 | 1.2329 | 121.9824 | 121.9811 | 121.92 | 121.8058 | -0.029599 | 0.000325 | 0.003135 | 0.019713 | 122.012 | 121.9792 | 121.9496 | 121.9168
2576 | 122.1268 | -0.064087 | 121.9345 | 0.4286 | 1.2278 | 1.2654 | 1.2295 | 1.3089 | 1.3217 | 1.178 | 121.9366 | 121.9307 | 121.8742 | 121.7508 | -0.075375 | -0.040873 | -0.042641 | -0.035219 | 0.49269 | 1.2919 | 1.3295 | 1.2936 | 1.373 | 1.3858 | 1.2421 | 121.9824 | 121.9765 | 121.92 | 121.7966 | -0.029599 | 0.004903 | 0.003135 | 0.010557 | 122.012 | 121.9792 | 121.9496 | 121.9168
2577.7656 | 122.1085 | -0.073242 | 121.9437 | 0.45149 | 1.2965 | 1.325 | 1.2982 | 1.3776 | 1.3858 | 1.2421 | 121.9412 | 121.9307 | 121.8833 | 121.76 | -0.075375 | -0.040873 | -0.042641 | -0.030641 | 0.52474 | 1.3697 | 1.3982 | 1.3714 | 1.4508 | 1.4591 | 1.3153 | 121.987 | 121.9765 | 121.9291 | 121.8058 | -0.029599 | 0.004903 | 0.003135 | 0.015135 | 122.0166 | 121.9838 | 121.9587 | 121.926
2579.5156 | 122.0215 | -0.10986 | 122.0078 | 0.45607 | 1.2828 | 1.3112 | 1.2799 | 1.373 | 1.3858 | 1.2237 | 121.9412 | 121.9307 | 121.8788 | 121.76 | -0.079953 | -0.040873 | -0.042641 | -0.030641 | 0.56594 | 1.3926 | 1.4211 | 1.3897 | 1.4829 | 1.4957 | 1.3336 | 121.987 | 121.9765 | 121.9245 | 121.8058 | -0.034177 | 0.004903 | 0.003135 | 0.015135 | 122.0211 | 121.9838 | 121.9587 | 121.9214
2581.2812 | 122.1588 | -0.07782 | 121.9528 | 0.47896 | 1.3469 | 1.3753 | 1.3348 | 1.428 | 1.4316 | 1.2833 | 121.9366 | 121.9353 | 121.8788 | 121.7646 | -0.079953 | -0.040873 | -0.04722 | -0.030641 | 0.55678 | 1.4247 | 1.4531 | 1.4126 | 1.5058 | 1.5094 | 1.3611 | 121.9824 | 121.9811 | 121.9245 | 121.8103 | -0.034177 | 0.004903 | -0.001444 | 0.015135 | 122.0166 | 121.9838 | 121.9587 | 121.926
2582.9844 | 122.0169 | -0.1236 | 121.9711 | 0.50644 | 1.3926 | 1.4348 | 1.4081 | 1.4829 | 1.5003 | 1.3428 | 121.9412 | 121.9353 | 121.8742 | 121.7691 | -0.079953 | -0.045451 | -0.042641 | -0.030641 | 0.63003 | 1.5162 | 1.5584 | 1.5316 | 1.6065 | 1.6239 | 1.4664 | 121.987 | 121.9811 | 121.92 | 121.8149 | -0.034177 | 0.000325 | 0.003135 | 0.015135 | 122.0211 | 121.9838 | 121.9541 | 121.9168
2584.75 | 122.168 | -0.068665 | 121.9391 | 0.52475 | 1.4339 | 1.4669 | 1.4218 | 1.5241 | 1.5278 | 1.384 | 121.9366 | 121.9353 | 121.8742 | 121.76 | -0.075375 | -0.045451 | -0.051798 | -0.030641 | 0.59341 | 1.5025 | 1.5356 | 1.4905 | 1.5928 | 1.5964 | 1.4526 | 121.9824 | 121.9811 | 121.92 | 121.8058 | -0.029599 | 0.000325 | -0.006022 | 0.015135 | 122.012 | 121.9884 | 121.9496 | 121.926
2586.5 | 122.049 | -0.12817 | 121.9894 | 0.52933 | 1.4201 | 1.4486 | 1.4126 | 1.5012 | 1.5095 | 1.3657 | 121.9366 | 121.9353 | 121.8788 | 121.7646 | -0.066219 | -0.040873 | -0.04722 | -0.030641 | 0.6575 | 1.5483 | 1.5767 | 1.5408 | 1.6294 | 1.6376 | 1.4938 | 121.9824 | 121.9811 | 121.9245 | 121.8103 | -0.020443 | 0.004903 | -0.001444 | 0.015135 | 122.0028 | 121.9838 | 121.945 | 121.926
2588.2656 | 122.1359 | -0.073242 | 121.9299 | 0.56595 | 1.5117 | 1.5493 | 1.5088 | 1.5928 | 1.6056 | 1.4618 | 121.9412 | 121.9353 | 121.8742 | 121.7508 | -0.070797 | -0.040873 | -0.042641 | -0.030641 | 0.6392 | 1.5849 | 1.6225 | 1.582 | 1.666 | 1.6788 | 1.5351 | 121.987 | 121.9811 | 121.92 | 121.7966 | -0.025021 | 0.004903 | 0.003135 | 0.015135 | 122.012 | 121.9838 | 121.945 | 121.9168
2589.9688 | 122.0123 | -0.10986 | 121.9849 | 0.58885 | 1.5254 | 1.5493 | 1.5225 | 1.6065 | 1.6148 | 1.4664 | 121.9412 | 121.9307 | 121.8833 | 121.7691 | -0.075375 | -0.040873 | -0.038063 | -0.026063 | 0.69871 | 1.6353 | 1.6592 | 1.6324 | 1.7164 | 1.7246 | 1.5763 | 121.987 | 121.9765 | 121.9291 | 121.8149 | -0.029599 | 0.004903 | 0.007713 | 0.019713 | 122.0166 | 121.9792 | 121.9587 | 121.9214
2591.7344 | 122.0169 | -0.11902 | 121.9757 | 0.62547 | 1.5941 | 1.6226 | 1.6003 | 1.6798 | 1.6972 | 1.5442 | 121.9458 | 121.9307 | 121.8788 | 121.7554 | -0.079953 | -0.036295 | -0.04722 | -0.030641 | 0.74449 | 1.7131 | 1.7416 | 1.7194 | 1.7988 | 1.8162 | 1.6632 | 121.9915 | 121.9765 | 121.9245 | 121.8012 | -0.034177 | 0.009481 | -0.001444 | 0.015135 | 122.0257 | 121.993 | 121.9587 | 121.926
2593.4844 | 122.0261 | -0.12817 | 122.0078 | 0.64379 | 1.6262 | 1.6592 | 1.6324 | 1.7164 | 1.7246 | 1.5717 | 121.9366 | 121.9399 | 121.8879 | 121.76 | -0.075375 | -0.040873 | -0.042641 | -0.030641 | 0.77196 | 1.7543 | 1.7874 | 1.7606 | 1.8445 | 1.8528 | 1.6999 | 121.9824 | 121.9856 | 121.9337 | 121.8058 | -0.029599 | 0.004903 | 0.003135 | 0.015135 | 122.012 | 121.9792 | 121.9633 | 121.9306
2595.1875 | 122.1313 | -0.07782 | 121.9391 | 0.66668 | 1.6674 | 1.6958 | 1.6644 | 1.7484 | 1.7567 | 1.6129 | 121.9366 | 121.9307 | 121.8742 | 121.7554 | -0.075375 | -0.040873 | -0.042641 | -0.030641 | 0.7445 | 1.7452 | 1.7736 | 1.7423 | 1.8262 | 1.8345 | 1.6907 | 121.9824 | 121.9765 | 121.92 | 121.8012 | -0.029599 | 0.004903 | 0.003135 | 0.015135 | 122.012 | 121.9792 | 121.9496 | 121.9168
2596.9688 | 122.0535 | -0.10529 | 121.9757 | 0.68957 | 1.6903 | 1.7279 | 1.6965 | 1.7805 | 1.7933 | 1.6449 | 121.9366 | 121.9307 | 121.8833 | 121.76 | -0.079953 | -0.045451 | -0.042641 | -0.035219 | 0.79486 | 1.7956 | 1.8332 | 1.8018 | 1.8858 | 1.8986 | 1.7502 | 121.9824 | 121.9765 | 121.9291 | 121.8058 | -0.034177 | 0.000325 | 0.003135 | 0.010557 | 122.0166 | 121.9792 | 121.9633 | 121.926
2598.6719 | 122.1359 | -0.073242 | 121.9574 | 0.71704 | 1.7452 | 1.7737 | 1.7469 | 1.8308 | 1.8437 | 1.6953 | 121.9412 | 121.9307 | 121.8788 | 121.76 | -0.075375 | -0.045451 | -0.042641 | -0.030641 | 0.79028 | 1.8185 | 1.8469 | 1.8201 | 1.9041 | 1.9169 | 1.7685 | 121.987 | 121.9765 | 121.9245 | 121.8058 | -0.029599 | 0.000325 | 0.003135 | 0.015135 | 122.0166 | 121.9838 | 121.9541 | 121.9214
2600.4219 | 122.0261 | -0.14648 | 122.0078 | 0.76282 | 1.8322 | 1.8606 | 1.8384 | 1.9132 | 1.9261 | 1.7777 | 121.9366 | 121.9353 | 121.8879 | 121.7646 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.90931 | 1.9787 | 2.0071 | 1.9849 | 2.0597 | 2.0726 | 1.9242 | 121.9824 | 121.9811 | 121.9337 | 121.8103 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 122.0211 | 121.9884 | 121.9725 | 121.9397
2602.1875 | 122.0169 | -0.10986 | 122.0032 | 0.79945 | 1.878 | 1.911 | 1.8751 | 1.959 | 1.9719 | 1.8235 | 121.9458 | 121.9307 | 121.8788 | 121.7646 | -0.075375 | -0.040873 | -0.04722 | -0.030641 | 0.90932 | 1.9879 | 2.0209 | 1.9849 | 2.0689 | 2.0817 | 1.9334 | 121.9915 | 121.9765 | 121.9245 | 121.8103 | -0.029599 | 0.004903 | -0.001444 | 0.015135 | 122.0211 | 121.993 | 121.9541 | 121.926
2603.9531 | 122.0993 | -0.07782 | 121.9574 | 0.81319 | 1.9009 | 1.9431 | 1.9071 | 1.9865 | 2.0085 | 1.8555 | 121.9412 | 121.9353 | 121.8788 | 121.7646 | -0.079953 | -0.045451 | -0.04722 | -0.030641 | 0.89101 | 1.9787 | 2.0209 | 1.9849 | 2.0643 | 2.0863 | 1.9334 | 121.987 | 121.9811 | 121.9245 | 121.8103 | -0.034177 | 0.000325 | -0.001444 | 0.015135 | 122.0211 | 121.9884 | 121.9587 | 121.926
2605.6562 | 122.1542 | -0.059509 | 121.9574 | 0.83608 | 1.9284 | 1.9568 | 1.9392 | 2.0185 | 2.0268 | 1.883 | 121.9412 | 121.9353 | 121.8788 | 121.7554 | -0.070797 | -0.040873 | -0.042641 | -0.026063 | 0.89559 | 1.9879 | 2.0163 | 1.9987 | 2.078 | 2.0863 | 1.9425 | 121.987 | 121.9811 | 121.9245 | 121.8012 | -0.025021 | 0.004903 | 0.003135 | 0.019713 | 122.012 | 121.9838 | 121.9496 | 121.9214
2607.3594 | 122.0718 | -0.09613 | 121.994 | 0.87271 | 1.9787 | 2.0117 | 1.9758 | 2.0643 | 2.0772 | 1.9196 | 121.932 | 121.9307 | 121.8879 | 121.76 | -0.075375 | -0.050029 | -0.042641 | -0.026063 | 0.96884 | 2.0749 | 2.1079 | 2.0719 | 2.1604 | 2.1733 | 2.0158 | 121.9778 | 121.9765 | 121.9337 | 121.8058 | -0.029599 | -0.004253 | 0.003135 | 0.019713 | 122.0074 | 121.9747 | 121.9633 | 121.9306
2609.0469 | 122.1085 | -0.07782 | 121.9528 | 0.89102 | 2.0199 | 2.053 | 2.0261 | 2.1009 | 2.1092 | 1.9608 | 121.9412 | 121.9353 | 121.8742 | 121.7554 | -0.070797 | -0.031717 | -0.042641 | -0.026063 | 0.96884 | 2.0978 | 2.1308 | 2.104 | 2.1787 | 2.1871 | 2.0387 | 121.987 | 121.9811 | 121.92 | 121.8012 | -0.025021 | 0.014059 | 0.003135 | 0.019713 | 122.012 | 121.9838 | 121.945 | 121.9168
2610.8125 | 122.1451 | -0.068665 | 121.9574 | 0.94596 | 2.0886 | 2.1308 | 2.0994 | 2.1833 | 2.1916 | 2.0432 | 121.9458 | 121.9307 | 121.8742 | 121.7554 | -0.079953 | -0.040873 | -0.04722 | -0.035219 | 1.0146 | 2.1573 | 2.1995 | 2.1681 | 2.252 | 2.2603 | 2.1119 | 121.9915 | 121.9765 | 121.92 | 121.8012 | -0.034177 | 0.004903 | -0.001444 | 0.010557 | 122.0257 | 121.993 | 121.9541 | 121.9214
2612.5312 | 122.1222 | -0.068665 | 121.9757 | 0.9597 | 2.0978 | 2.1262 | 2.0994 | 2.1833 | 2.1916 | 2.0478 | 121.9412 | 121.9261 | 121.8742 | 121.7646 | -0.079953 | -0.040873 | -0.04722 | -0.021484 | 1.0284 | 2.1665 | 2.1949 | 2.1681 | 2.252 | 2.2603 | 2.1165 | 121.987 | 121.9719 | 121.92 | 121.8103 | -0.034177 | 0.004903 | -0.001444 | 0.024292 | 122.0211 | 121.9884 | 121.9541 | 121.9214
2614.2969 | 122.1085 | -0.082397 | 121.9849 | 1.0101 | 2.1619 | 2.1949 | 2.1727 | 2.2474 | 2.2603 | 2.1119 | 121.9458 | 121.9261 | 121.8788 | 121.7646 | -0.079953 | -0.036295 | -0.04722 | -0.035219 | 1.0925 | 2.2443 | 2.2773 | 2.2551 | 2.3298 | 2.3427 | 2.1943 | 121.9915 | 121.9719 | 121.9245 | 121.8103 | -0.034177 | 0.009481 | -0.001444 | 0.010557 | 122.0257 | 121.993 | 121.9587 | 121.926
2616 | 122.0352 | -0.1236 | 121.9894 | 1.0513 | 2.2306 | 2.2727 | 2.2459 | 2.3207 | 2.3336 | 2.1897 | 121.9458 | 121.9307 | 121.8788 | 121.76 | -0.075375 | -0.040873 | -0.056376 | -0.026063 | 1.1749 | 2.3542 | 2.3963 | 2.3695 | 2.4443 | 2.4572 | 2.3133 | 121.9915 | 121.9765 | 121.9245 | 121.8058 | -0.029599 | 0.004903 | -0.0106 | 0.019713 | 122.0211 | 122.0021 | 121.9541 | 121.9351
2617.7812 | 122.0078 | -0.10529 | 121.994 | 1.1062 | 2.3313 | 2.3597 | 2.3375 | 2.4168 | 2.4206 | 2.2859 | 121.9412 | 121.9399 | 121.8833 | 121.7691 | -0.079953 | -0.040873 | -0.038063 | -0.021484 | 1.2115 | 2.4366 | 2.465 | 2.4428 | 2.5221 | 2.5258 | 2.3912 | 121.987 | 121.9856 | 121.9291 | 121.8149 | -0.034177 | 0.004903 | 0.007713 | 0.024292 | 122.0211 | 121.9792 | 121.9633 | 121.9214
2619.4688 | 122.1542 | -0.068665 | 121.962 | 1.1474 | 2.4 | 2.4421 | 2.397 | 2.4855 | 2.4984 | 2.3454 | 121.932 | 121.9353 | 121.8788 | 121.7646 | -0.070797 | -0.040873 | -0.04722 | -0.030641 | 1.2161 | 2.4687 | 2.5108 | 2.4657 | 2.5541 | 2.5671 | 2.4141 | 121.9778 | 121.9811 | 121.9245 | 121.8103 | -0.025021 | 0.004903 | -0.001444 | 0.015135 | 122.0028 | 121.9792 | 121.9496 | 121.926
2621.1562 | 122.1313 | -0.082397 | 121.9803 | 1.184 | 2.4366 | 2.4742 | 2.4474 | 2.5221 | 2.535 | 2.4003 | 121.9412 | 121.9307 | 121.8879 | 121.7554 | -0.079953 | -0.045451 | -0.042641 | -0.026063 | 1.2664 | 2.519 | 2.5566 | 2.5298 | 2.6045 | 2.6174 | 2.4827 | 121.987 | 121.9765 | 121.9337 | 121.8012 | -0.034177 | 0.000325 | 0.003135 | 0.019713 | 122.0211 | 121.9838 | 121.9679 | 121.9306
2622.9219 | 122.0581 | -0.09613 | 121.9574 | 1.2161 | 2.4824 | 2.5154 | 2.484 | 2.5679 | 2.5762 | 2.4324 | 121.9412 | 121.9353 | 121.8788 | 121.76 | -0.070797 | -0.040873 | -0.04722 | -0.030641 | 1.3122 | 2.5785 | 2.6115 | 2.5801 | 2.664 | 2.6724 | 2.5285 | 121.987 | 121.9811 | 121.9245 | 121.8058 | -0.025021 | 0.004903 | -0.001444 | 0.015135 | 122.012 | 121.9884 | 121.9496 | 121.926
2624.6875 | 122.1405 | -0.064087 | 121.9299 | 1.2252 | 2.4641 | 2.5017 | 2.4748 | 2.5496 | 2.5625 | 2.4232 | 121.9503 | 121.9399 | 121.8788 | 121.7646 | -0.075375 | -0.045451 | -0.04722 | -0.030641 | 1.2893 | 2.5282 | 2.5657 | 2.5389 | 2.6137 | 2.6266 | 2.4873 | 121.9961 | 121.9856 | 121.9245 | 121.8103 | -0.029599 | 0.000325 | -0.001444 | 0.015135 | 122.0257 | 121.9976 | 121.9541 | 121.926
2626.3906 | 122.1634 | -0.082397 | 121.9711 | 1.2619 | 2.4916 | 2.5291 | 2.4932 | 2.5633 | 2.5854 | 2.437 | 121.9458 | 121.9444 | 121.8788 | 121.76 | -0.079953 | -0.045451 | -0.04722 | -0.021484 | 1.3443 | 2.574 | 2.6115 | 2.5756 | 2.6457 | 2.6678 | 2.5194 | 121.9915 | 121.9902 | 121.9245 | 121.8058 | -0.034177 | 0.000325 | -0.001444 | 0.024292 | 122.0257 | 121.993 | 121.9587 | 121.926
2628.1562 | 122.0535 | -0.086975 | 121.9574 | 1.2893 | 2.5282 | 2.5612 | 2.5298 | 2.6091 | 2.622 | 2.4782 | 121.9458 | 121.9444 | 121.8879 | 121.7646 | -0.079953 | -0.040873 | -0.042641 | -0.035219 | 1.3763 | 2.6152 | 2.6481 | 2.6168 | 2.6961 | 2.709 | 2.5651 | 121.9915 | 121.9902 | 121.9337 | 121.8103 | -0.034177 | 0.004903 | 0.003135 | 0.010557 | 122.0257 | 121.9884 | 121.9679 | 121.9306
2629.9219 | 121.9757 | -0.10529 | 121.9849 | 1.3305 | 2.606 | 2.6344 | 2.6168 | 2.6823 | 2.6953 | 2.556 | 121.9458 | 121.9444 | 121.8879 | 121.7554 | -0.084531 | -0.040873 | -0.042641 | -0.030641 | 1.4358 | 2.7113 | 2.7397 | 2.7221 | 2.7876 | 2.8005 | 2.6613 | 121.9915 | 121.9902 | 121.9337 | 121.8012 | -0.038755 | 0.004903 | 0.003135 | 0.015135 | 122.0303 | 121.9884 | 121.9725 | 121.9306
2631.6406 | 122.0535 | -0.10529 | 121.9528 | 1.3672 | 2.6335 | 2.6665 | 2.6305 | 2.7098 | 2.7182 | 2.5835 | 121.9458 | 121.9307 | 121.8879 | 121.76 | -0.070797 | -0.036295 | -0.038063 | -0.026063 | 1.4725 | 2.7388 | 2.7718 | 2.7358 | 2.8151 | 2.8234 | 2.6888 | 121.9915 | 121.9765 | 121.9337 | 121.8058 | -0.025021 | 0.009481 | 0.007713 | 0.019713 | 122.0166 | 121.9838 | 121.9587 | 121.926
2633.4062 | 122.0444 | -0.11444 | 121.9986 | 1.4221 | 2.7159 | 2.7489 | 2.7221 | 2.7556 | 2.8051 | 2.6705 | 121.9412 | 121.9399 | 121.8788 | 121.7691 | -0.075375 | -0.045451 | -0.04722 | -0.030641 | 1.5366 | 2.8304 | 2.8633 | 2.8365 | 2.87 | 2.9196 | 2.7849 | 121.987 | 121.9856 | 121.9245 | 121.8149 | -0.029599 | 0.000325 | -0.001444 | 0.015135 | 122.0166 | 121.9884 | 121.9541 | 121.926
2635.1719 | 122.0398 | -0.11444 | 122.0078 | 1.4587 | 2.7388 | 2.7718 | 2.745 | 2.7922 | 2.828 | 2.6933 | 121.9503 | 121.9307 | 121.8833 | 121.7646 | -0.075375 | -0.040873 | -0.04722 | -0.030641 | 1.5732 | 2.8533 | 2.8862 | 2.8594 | 2.9066 | 2.9425 | 2.8078 | 121.9961 | 121.9765 | 121.9291 | 121.8103 | -0.029599 | 0.004903 | -0.001444 | 0.015135 | 122.0257 | 121.9976 | 121.9587 | 121.9306
2636.9375 | 122.1359 | -0.059509 | 121.9345 | 1.4999 | 2.7892 | 2.8222 | 2.7953 | 2.838 | 2.883 | 2.7483 | 121.9503 | 121.9353 | 121.8833 | 121.76 | -0.079953 | -0.040873 | -0.042641 | -0.030641 | 1.5595 | 2.8487 | 2.8817 | 2.8548 | 2.8975 | 2.9425 | 2.8078 | 121.9961 | 121.9811 | 121.9291 | 121.8058 | -0.034177 | 0.004903 | 0.003135 | 0.015135 | 122.0303 | 121.993 | 121.9633 | 121.926
2638.6406 | 121.994 | -0.11444 | 121.994 | 1.532 | 2.8396 | 2.8725 | 2.8503 | 2.8883 | 2.9379 | 2.7986 | 121.9412 | 121.9261 | 121.8788 | 121.7646 | -0.075375 | -0.040873 | -0.04722 | -0.026063 | 1.6464 | 2.954 | 2.987 | 2.9647 | 3.0028 | 3.0524 | 2.9131 | 121.987 | 121.9719 | 121.9245 | 121.8103 | -0.029599 | 0.004903 | -0.001444 | 0.019713 | 122.0166 | 121.9884 | 121.9541 | 121.926
2640.4062 | 122.0032 | -0.11902 | 121.9894 | 1.5686 | 2.8716 | 2.9046 | 2.8823 | 2.9158 | 2.9608 | 2.8261 | 121.9412 | 121.9353 | 121.8788 | 121.76 | -0.079953 | -0.036295 | -0.051798 | -0.030641 | 1.6876 | 2.9906 | 3.0236 | 3.0013 | 3.0348 | 3.0798 | 2.9451 | 121.987 | 121.9811 | 121.9245 | 121.8058 | -0.034177 | 0.009481 | -0.006022 | 0.015135 | 122.0211 | 121.993 | 121.9587 | 121.9306
2642.1719 | 122.113 | -0.050354 | 121.9666 | 1.5961 | 2.8991 | 2.932 | 2.9144 | 2.9524 | 2.9929 | 2.8582 | 121.9412 | 121.9307 | 121.8879 | 121.76 | -0.079953 | -0.040873 | -0.042641 | -0.030641 | 1.6464 | 2.9494 | 2.9824 | 2.9647 | 3.0028 | 3.0432 | 2.9085 | 121.987 | 121.9765 | 121.9337 | 121.8058 | -0.034177 | 0.004903 | 0.003135 | 0.015135 | 122.0211 | 121.9838 | 121.9679 | 121.9306
2643.9375 | 122.1268 | -0.10071 | 121.9437 | 1.6236 | 2.9128 | 2.9504 | 2.9098 | 2.957 | 3.0066 | 2.8582 | 121.9458 | 121.9353 | 121.8788 | 121.76 | -0.070797 | -0.036295 | -0.04722 | -0.035219 | 1.7243 | 3.0135 | 3.0511 | 3.0105 | 3.0577 | 3.1073 | 2.9589 | 121.9915 | 121.9811 | 121.9245 | 121.8058 | -0.025021 | 0.009481 | -0.001444 | 0.010557 | 122.0166 | 121.993 | 121.9496 | 121.926
2645.6406 | 122.1359 | -0.068665 | 121.9528 | 1.6419 | 2.922 | 2.9458 | 2.9235 | 2.9662 | 3.0066 | 2.8765 | 121.9412 | 121.9307 | 121.8742 | 121.7646 | -0.075375 | -0.040873 | -0.04722 | -0.026063 | 1.7105 | 2.9906 | 3.0144 | 2.9922 | 3.0348 | 3.0753 | 2.9451 | 121.987 | 121.9765 | 121.92 | 121.8103 | -0.029599 | 0.004903 | -0.001444 | 0.019713 | 122.0166 | 121.9884 | 121.9496 | 121.9214
2647.4062 | 122.168 | -0.059509 | 121.9574 | 1.6648 | 2.9311 | 2.9595 | 2.9281 | 2.9753 | 3.0203 | 2.8765 | 121.9412 | 121.9353 | 121.8788 | 121.76 | -0.084531 | -0.036295 | -0.042641 | -0.026063 | 1.7243 | 2.9906 | 3.019 | 2.9876 | 3.0348 | 3.0798 | 2.936 | 121.987 | 121.9811 | 121.9245 | 121.8058 | -0.038755 | 0.009481 | 0.003135 | 0.019713 | 122.0257 | 121.9838 | 121.9633 | 121.9214
2649.1719 | 122.0856 | -0.10529 | 121.9666 | 1.7197 | 3.0135 | 3.0465 | 3.0197 | 3.0577 | 3.0982 | 2.9635 | 121.9412 | 121.9399 | 121.8833 | 121.7646 | -0.070797 | -0.040873 | -0.04722 | -0.026063 | 1.825 | 3.1188 | 3.1518 | 3.125 | 3.163 | 3.2034 | 3.0687 | 121.987 | 121.9856 | 121.9291 | 121.8103 | -0.025021 | 0.004903 | -0.001444 | 0.019713 | 122.012 | 121.9884 | 121.9541 | 121.9306
2650.9375 | 122.1085 | -0.09613 | 121.9574 | 1.7701 | 3.0456 | 3.0877 | 3.0563 | 3.0989 | 3.1485 | 3.0092 | 121.9412 | 121.9399 | 121.8833 | 121.7646 | -0.075375 | -0.040873 | -0.038063 | -0.026063 | 1.8662 | 3.1417 | 3.1838 | 3.1524 | 3.195 | 3.2447 | 3.1054 | 121.987 | 121.9856 | 121.9291 | 121.8103 | -0.029599 | 0.004903 | 0.007713 | 0.019713 | 122.0166 | 121.9792 | 121.9587 | 121.9214
2652.6562 | 122.0352 | -0.11902 | 121.9803 | 1.8113 | 3.0914 | 3.1335 | 3.1113 | 3.1539 | 3.1943 | 3.055 | 121.9412 | 121.9307 | 121.8788 | 121.7691 | -0.070797 | -0.036295 | -0.04722 | -0.026063 | 1.9303 | 3.2104 | 3.2525 | 3.2303 | 3.2729 | 3.3133 | 3.174 | 121.987 | 121.9765 | 121.9245 | 121.8149 | -0.025021 | 0.009481 | -0.001444 | 0.019713 | 122.012 | 121.9884 | 121.9496 | 121.926
2654.4219 | 122.1588 | -0.082397 | 121.962 | 1.8571 | 3.1555 | 3.1884 | 3.157 | 3.1996 | 3.2447 | 3.1054 | 121.9366 | 121.9307 | 121.8742 | 121.7646 | -0.075375 | -0.040873 | -0.051798 | -0.021484 | 1.9395 | 3.2379 | 3.2708 | 3.2394 | 3.282 | 3.3271 | 3.1878 | 121.9824 | 121.9765 | 121.92 | 121.8103 | -0.029599 | 0.004903 | -0.006022 | 0.024292 | 122.012 | 121.9884 | 121.9496 | 121.926
2656.1875 | 122.0306 | -0.11444 | 122.0032 | 1.8845 | 3.1784 | 3.2113 | 3.1799 | 3.2271 | 3.2721 | 3.1283 | 121.9366 | 121.9399 | 121.8833 | 121.76 | -0.075375 | -0.040873 | -0.04722 | -0.026063 | 1.999 | 3.2928 | 3.3258 | 3.2944 | 3.3415 | 3.3866 | 3.2427 | 121.9824 | 121.9856 | 121.9291 | 121.8058 | -0.029599 | 0.004903 | -0.001444 | 0.019713 | 122.012 | 121.9838 | 121.9587 | 121.9306
2657.8906 | 122.0215 | -0.11902 | 122.0078 | 1.9212 | 3.2196 | 3.2571 | 3.2303 | 3.2775 | 3.3133 | 3.1832 | 121.9458 | 121.9399 | 121.8833 | 121.7691 | -0.075375 | -0.036295 | -0.038063 | -0.026063 | 2.0402 | 3.3386 | 3.3761 | 3.3493 | 3.3965 | 3.4324 | 3.3022 | 121.9915 | 121.9856 | 121.9291 | 121.8149 | -0.029599 | 0.009481 | 0.007713 | 0.019713 | 122.0211 | 121.9838 | 121.9587 | 121.9214
2659.6562 | 122.0352 | -0.11444 | 122.0032 | 1.9761 | 3.2791 | 3.3166 | 3.2807 | 3.3324 | 3.3729 | 3.2427 | 121.9412 | 121.9399 | 121.8833 | 121.7646 | -0.070797 | -0.045451 | -0.042641 | -0.030641 | 2.0905 | 3.3936 | 3.4311 | 3.3951 | 3.4468 | 3.4873 | 3.3572 | 121.987 | 121.9856 | 121.9291 | 121.8103 | -0.025021 | 0.000325 | 0.003135 | 0.015135 | 122.012 | 121.9838 | 121.9541 | 121.926
2661.4062 | 122.0901 | -0.09613 | 121.9666 | 2.0265 | 3.3524 | 3.3853 | 3.3539 | 3.3965 | 3.437 | 3.3022 | 121.9412 | 121.9353 | 121.8788 | 121.76 | -0.079953 | -0.040873 | -0.04722 | -0.021484 | 2.1226 | 3.4485 | 3.4815 | 3.45 | 3.4926 | 3.5331 | 3.3984 | 121.987 | 121.9811 | 121.9245 | 121.8058 | -0.034177 | 0.004903 | -0.001444 | 0.024292 | 122.0211 | 121.9884 | 121.9587 | 121.926
2663.1094 | 122.0078 | -0.11902 | 122.0032 | 2.0814 | 3.4073 | 3.4357 | 3.4134 | 3.456 | 3.5011 | 3.3663 | 121.9458 | 121.9307 | 121.8788 | 121.76 | -0.075375 | -0.036295 | -0.04722 | -0.030641 | 2.2004 | 3.5263 | 3.5547 | 3.5325 | 3.575 | 3.6201 | 3.4854 | 121.9915 | 121.9765 | 121.9245 | 121.8058 | -0.029599 | 0.009481 | -0.001444 | 0.015135 | 122.0211 | 121.993 | 121.9541 | 121.926
2664.8594 | 122.0718 | -0.10529 | 121.9803 | 2.1226 | 3.4623 | 3.4952 | 3.4638 | 3.5018 | 3.5514 | 3.4167 | 121.9458 | 121.9307 | 121.8833 | 121.7737 | -0.075375 | -0.036295 | -0.042641 | -0.030641 | 2.2279 | 3.5676 | 3.6005 | 3.5691 | 3.6071 | 3.6567 | 3.522 | 121.9915 | 121.9765 | 121.9291 | 121.8195 | -0.029599 | 0.009481 | 0.003135 | 0.015135 | 122.0211 | 121.9884 | 121.9587 | 121.926
2666.5625 | 122.1497 | -0.07782 | 121.9803 | 2.1592 | 3.4852 | 3.5273 | 3.4958 | 3.543 | 3.5835 | 3.4533 | 121.9412 | 121.9353 | 121.8788 | 121.76 | -0.075375 | -0.040873 | -0.042641 | -0.035219 | 2.2371 | 3.563 | 3.6051 | 3.5737 | 3.6208 | 3.6613 | 3.5311 | 121.987 | 121.9811 | 121.9245 | 121.8058 | -0.029599 | 0.004903 | 0.003135 | 0.010557 | 122.0166 | 121.9838 | 121.9541 | 121.9214
2668.3281 | 122.1542 | -0.068665 | 121.9574 | 2.2371 | 3.5996 | 3.6371 | 3.6149 | 3.6483 | 3.6934 | 3.5678 | 121.9412 | 121.9353 | 121.8833 | 121.76 | -0.070797 | -0.040873 | -0.04722 | -0.030641 | 2.3057 | 3.6683 | 3.7058 | 3.6836 | 3.7169 | 3.762 | 3.6364 | 121.987 | 121.9811 | 121.9291 | 121.8058 | -0.025021 | 0.004903 | -0.001444 | 0.015135 | 122.012 | 121.9884 | 121.9541 | 121.9306
2670.0156 | 122.1268 | -0.059509 | 121.9711 | 2.292 | 3.6775 | 3.7104 | 3.6836 | 3.7169 | 3.7666 | 3.6227 | 121.9412 | 121.9353 | 121.8788 | 121.7646 | -0.079953 | -0.045451 | -0.038063 | -0.030641 | 2.3515 | 3.737 | 3.7699 | 3.7431 | 3.7765 | 3.8261 | 3.6822 | 121.987 | 121.9811 | 121.9245 | 121.8103 | -0.034177 | 0.000325 | 0.007713 | 0.015135 | 122.0211 | 121.9792 | 121.9587 | 121.9168
2671.7656 | 121.994 | -0.11444 | 121.9803 | 2.3882 | 3.7828 | 3.8203 | 3.7934 | 3.8405 | 3.8719 | 3.7463 | 121.9412 | 121.949 | 121.8879 | 121.7691 | -0.070797 | -0.040873 | -0.038063 | -0.021484 | 2.5026 | 3.8972 | 3.9347 | 3.9079 | 3.955 | 3.9864 | 3.8608 | 121.987 | 121.9948 | 121.9337 | 121.8149 | -0.025021 | 0.004903 | 0.007713 | 0.024292 | 122.012 | 121.9792 | 121.9587 | 121.926
2673.5312 | 122.0215 | -0.10986 | 121.9803 | 2.4156 | 3.8194 | 3.8569 | 3.8255 | 3.8726 | 3.9131 | 3.7738 | 121.9503 | 121.9307 | 121.8788 | 121.76 | -0.075375 | -0.045451 | -0.042641 | -0.030641 | 2.5255 | 3.9293 | 3.9668 | 3.9354 | 3.9825 | 4.023 | 3.8837 | 121.9961 | 121.9765 | 121.9245 | 121.8058 | -0.029599 | 0.000325 | 0.003135 | 0.015135 | 122.0257 | 121.993 | 121.9541 | 121.9214
2675.2969 | 122.0581 | -0.10986 | 121.962 | 2.5072 | 3.9476 | 3.976 | 3.9629 | 3.9916 | 4.0322 | 3.9066 | 121.9412 | 121.9353 | 121.8788 | 121.7646 | -0.075375 | -0.045451 | -0.042641 | -0.035219 | 2.6171 | 4.0575 | 4.0858 | 4.0727 | 4.1015 | 4.142 | 4.0164 | 121.987 | 121.9811 | 121.9245 | 121.8103 | -0.029599 | 0.000325 | 0.003135 | 0.010557 | 122.0166 | 121.9838 | 121.9541 | 121.9214
2677.0625 | 122.1451 | -0.064087 | 121.962 | 2.553 | 3.998 | 4.0355 | 3.9995 | 4.0557 | 4.0871 | 3.9523 | 121.9366 | 121.9353 | 121.8833 | 121.76 | -0.075375 | -0.045451 | -0.04722 | -0.026063 | 2.6171 | 4.0621 | 4.0996 | 4.0636 | 4.1198 | 4.1512 | 4.0164 | 121.9824 | 121.9811 | 121.9291 | 121.8058 | -0.029599 | 0.000325 | -0.001444 | 0.019713 | 122.012 | 121.9838 | 121.9587 | 121.9306
2678.7812 | 122.0581 | -0.091553 | 121.9666 | 2.6033 | 4.0392 | 4.0767 | 4.0498 | 4.0923 | 4.1283 | 3.9981 | 121.9412 | 121.9353 | 121.8833 | 121.7508 | -0.079953 | -0.050029 | -0.042641 | -0.030641 | 2.6949 | 4.1308 | 4.1682 | 4.1414 | 4.1839 | 4.2199 | 4.0897 | 121.987 | 121.9811 | 121.9291 | 121.7966 | -0.034177 | -0.004253 | 0.003135 | 0.015135 | 122.0211 | 121.9838 | 121.9633 | 121.926
2680.5469 | 122.1268 | -0.073242 | 121.9666 | 2.6857 | 4.1628 | 4.1957 | 4.1735 | 4.2114 | 4.2473 | 4.1172 | 121.9412 | 121.9353 | 121.8788 | 121.7646 | -0.075375 | -0.040873 | -0.04722 | -0.021484 | 2.759 | 4.2361 | 4.269 | 4.2467 | 4.2846 | 4.3206 | 4.1904 | 121.987 | 121.9811 | 121.9245 | 121.8103 | -0.029599 | 0.004903 | -0.001444 | 0.024292 | 122.0166 | 121.9884 | 121.9541 | 121.926
2682.25 | 122.0673 | -0.11444 | 121.994 | 2.7224 | 4.1903 | 4.2278 | 4.1964 | 4.2388 | 4.2794 | 4.14 | 121.9503 | 121.9399 | 121.8833 | 121.7646 | -0.079953 | -0.036295 | -0.04722 | -0.026063 | 2.8368 | 4.3047 | 4.3422 | 4.3108 | 4.3533 | 4.3938 | 4.2545 | 121.9961 | 121.9856 | 121.9291 | 121.8103 | -0.034177 | 0.009481 | -0.001444 | 0.019713 | 122.0303 | 121.9976 | 121.9633 | 121.9306
2684.0156 | 122.0169 | -0.11444 | 121.994 | 2.7636 | 4.2407 | 4.2736 | 4.2421 | 4.2846 | 4.3206 | 4.1858 | 121.9412 | 121.9399 | 121.8788 | 121.76 | -0.075375 | -0.040873 | -0.042641 | -0.026063 | 2.878 | 4.3551 | 4.388 | 4.3566 | 4.3991 | 4.435 | 4.3003 | 121.987 | 121.9856 | 121.9245 | 121.8058 | -0.029599 | 0.004903 | 0.003135 | 0.019713 | 122.0166 | 121.9838 | 121.9541 | 121.9214
2685.7812 | 122.049 | -0.086975 | 121.9849 | 2.8506 | 4.3368 | 4.3743 | 4.3429 | 4.3945 | 4.4259 | 4.2865 | 121.9412 | 121.9399 | 121.8833 | 121.7646 | -0.079953 | -0.036295 | -0.051798 | -0.035219 | 2.9375 | 4.4238 | 4.4613 | 4.4298 | 4.4815 | 4.5129 | 4.3735 | 121.987 | 121.9856 | 121.9291 | 121.8103 | -0.034177 | 0.009481 | -0.006022 | 0.010557 | 122.0211 | 121.993 | 121.9633 | 121.9351
2687.5469 | 121.9986 | -0.10529 | 121.994 | 2.9147 | 4.4147 | 4.4476 | 4.4161 | 4.4632 | 4.4991 | 4.369 | 121.9503 | 121.9399 | 121.8833 | 121.7554 | -0.079953 | -0.045451 | -0.04722 | -0.026063 | 3.02 | 4.52 | 4.5528 | 4.5214 | 4.5684 | 4.6044 | 4.4742 | 121.9961 | 121.9856 | 121.9291 | 121.8012 | -0.034177 | 0.000325 | -0.001444 | 0.019713 | 122.0303 | 121.9976 | 121.9633 | 121.9306
2689.3125 | 122.1313 | -0.059509 | 121.9574 | 2.9376 | 4.433 | 4.475 | 4.4482 | 4.486 | 4.5175 | 4.3964 | 121.9458 | 121.9215 | 121.8742 | 121.76 | -0.075375 | -0.040873 | -0.042641 | -0.030641 | 2.9971 | 4.4925 | 4.5345 | 4.5077 | 4.5456 | 4.577 | 4.4559 | 121.9915 | 121.9673 | 121.92 | 121.8058 | -0.029599 | 0.004903 | 0.003135 | 0.015135 | 122.0211 | 121.9884 | 121.9496 | 121.9168
2691.0625 | 122.1222 | -0.07782 | 121.9666 | 2.9879 | 4.4971 | 4.5391 | 4.5031 | 4.5501 | 4.5907 | 4.4468 | 121.9412 | 121.9353 | 121.8788 | 121.76 | -0.075375 | -0.040873 | -0.042641 | -0.030641 | 3.0657 | 4.5749 | 4.617 | 4.5809 | 4.628 | 4.6685 | 4.5246 | 121.987 | 121.9811 | 121.9245 | 121.8058 | -0.029599 | 0.004903 | 0.003135 | 0.015135 | 122.0166 | 121.9838 | 121.9541 | 121.9214
2692.7656 | 122.1222 | -0.07782 | 121.9345 | 3.0474 | 4.5475 | 4.5849 | 4.5581 | 4.5959 | 4.6365 | 4.5063 | 121.9458 | 121.9399 | 121.8879 | 121.76 | -0.075375 | -0.040873 | -0.042641 | -0.026063 | 3.1253 | 4.6253 | 4.6627 | 4.6359 | 4.6737 | 4.7143 | 4.5841 | 121.9915 | 121.9856 | 121.9337 | 121.8058 | -0.029599 | 0.004903 | 0.003135 | 0.019713 | 122.0211 | 121.9884 | 121.9633 | 121.9306
2694.5312 | 122.0581 | -0.10986 | 122.0078 | 3.0978 | 4.607 | 4.6444 | 4.6176 | 4.6508 | 4.6823 | 4.5612 | 121.9412 | 121.9353 | 121.8833 | 121.7646 | -0.079953 | -0.036295 | -0.04722 | -0.026063 | 3.2077 | 4.7168 | 4.7543 | 4.7274 | 4.7607 | 4.7921 | 4.6711 | 121.987 | 121.9811 | 121.9291 | 121.8103 | -0.034177 | 0.009481 | -0.001444 | 0.019713 | 122.0211 | 121.9884 | 121.9633 | 121.9306
2696.2969 | 122.1451 | -0.07782 | 121.9391 | 3.1482 | 4.639 | 4.6765 | 4.6496 | 4.6875 | 4.7143 | 4.6024 | 121.9458 | 121.9399 | 121.8788 | 121.76 | -0.075375 | -0.040873 | -0.038063 | -0.026063 | 3.226 | 4.7168 | 4.7543 | 4.7274 | 4.7653 | 4.7922 | 4.6803 | 121.9915 | 121.9856 | 121.9245 | 121.8058 | -0.029599 | 0.004903 | 0.007713 | 0.019713 | 122.0211 | 121.9838 | 121.9541 | 121.9168
2698 | 122.0169 | -0.09613 | 122.0169 | 3.1527 | 4.639 | 4.6719 | 4.645 | 4.6829 | 4.7235 | 4.5933 | 121.9366 | 121.9353 | 121.8833 | 121.76 | -0.070797 | -0.045451 | -0.04722 | -0.021484 | 3.2489 | 4.7352 | 4.768 | 4.7412 | 4.779 | 4.8196 | 4.6894 | 121.9824 | 121.9811 | 121.9291 | 121.8058 | -0.025021 | 0.000325 | -0.001444 | 0.024292 | 122.0074 | 121.9838 | 121.9541 | 121.9306
2699.7656 | 122.1313 | -0.064087 | 121.9437 | 3.2352 | 4.7306 | 4.7589 | 4.732 | 4.779 | 4.8105 | 4.6848 | 121.9412 | 121.9353 | 121.8788 | 121.7646 | -0.075375 | -0.040873 | -0.042641 | -0.035219 | 3.2992 | 4.7947 | 4.823 | 4.7961 | 4.8431 | 4.8746 | 4.7489 | 121.987 | 121.9811 | 121.9245 | 121.8103 | -0.029599 | 0.004903 | 0.003135 | 0.010557 | 122.0166 | 121.9838 | 121.9541 | 121.9214
2701.5156 | 122.0352 | -0.10986 | 121.9849 | 3.2855 | 4.7856 | 4.8276 | 4.8007 | 4.834 | 4.8746 | 4.7489 | 121.9412 | 121.9307 | 121.8879 | 121.7691 | -0.079953 | -0.040873 | -0.038063 | -0.026063 | 3.3954 | 4.8954 | 4.9374 | 4.9106 | 4.9438 | 4.9844 | 4.8588 | 121.987 | 121.9765 | 121.9337 | 121.8149 | -0.034177 | 0.004903 | 0.007713 | 0.019713 | 122.0211 | 121.9792 | 121.9679 | 121.926
2703.2969 | 122.1039 | -0.07782 | 121.9711 | 3.313 | 4.7993 | 4.8276 | 4.8099 | 4.8431 | 4.8837 | 4.7489 | 121.9458 | 121.9399 | 121.8788 | 121.7646 | -0.075375 | -0.040873 | -0.038063 | -0.026063 | 3.3908 | 4.8771 | 4.9054 | 4.8877 | 4.9209 | 4.9616 | 4.8268 | 121.9915 | 121.9856 | 121.9245 | 121.8103 | -0.029599 | 0.004903 | 0.007713 | 0.019713 | 122.0211 | 121.9838 | 121.9541 | 121.9168
2705.0625 | 122.1313 | -0.086975 | 121.9391 | 3.3725 | 4.8542 | 4.9008 | 4.8694 | 4.9072 | 4.9524 | 4.8176 | 121.9412 | 121.9444 | 121.8742 | 121.7646 | -0.075375 | -0.045451 | -0.042641 | -0.030641 | 3.4595 | 4.9412 | 4.9878 | 4.9564 | 4.9942 | 5.0394 | 4.9046 | 121.987 | 121.9902 | 121.92 | 121.8103 | -0.029599 | 0.000325 | 0.003135 | 0.015135 | 122.0166 | 121.9838 | 121.9496 | 121.9168
2706.8281 | 122.0123 | -0.11902 | 121.9803 | 3.4366 | 4.9367 | 4.9741 | 4.9472 | 4.985 | 5.0302 | 4.8954 | 121.9412 | 121.9307 | 121.8788 | 121.7646 | -0.079953 | -0.040873 | -0.042641 | -0.030641 | 3.5556 | 5.0557 | 5.0931 | 5.0662 | 5.1041 | 5.1493 | 5.0145 | 121.987 | 121.9765 | 121.9245 | 121.8103 | -0.034177 | 0.004903 | 0.003135 | 0.015135 | 122.0211 | 121.9838 | 121.9587 | 121.9214
2708.5469 | 122.1451 | -0.073242 | 121.9528 | 3.4687 | 4.9641 | 5.0061 | 4.9839 | 5.0217 | 5.0531 | 4.9321 | 121.9458 | 121.9353 | 121.8742 | 121.7646 | -0.070797 | -0.040873 | -0.04722 | -0.021484 | 3.5419 | 5.0374 | 5.0794 | 5.0571 | 5.0949 | 5.1264 | 5.0053 | 121.9915 | 121.9811 | 121.92 | 121.8103 | -0.025021 | 0.004903 | -0.001444 | 0.024292 | 122.0166 | 121.993 | 121.945 | 121.9214
2710.3125 | 122.1085 | -0.068665 | 121.9711 | 3.5236 | 5.0191 | 5.0565 | 5.0296 | 5.072 | 5.0989 | 4.9779 | 121.9458 | 121.9399 | 121.8833 | 121.76 | -0.075375 | -0.036295 | -0.051798 | -0.030641 | 3.5923 | 5.0877 | 5.1252 | 5.0983 | 5.1407 | 5.1676 | 5.0465 | 121.9915 | 121.9856 | 121.9291 | 121.8058 | -0.029599 | 0.009481 | -0.006022 | 0.015135 | 122.0211 | 121.9976 | 121.9587 | 121.9351
2712.0781 | 122.0215 | -0.13275 | 121.9849 | 3.6014 | 5.1152 | 5.1618 | 5.1304 | 5.1682 | 5.2088 | 5.074 | 121.9412 | 121.9353 | 121.8788 | 121.76 | -0.079953 | -0.045451 | -0.042641 | -0.026063 | 3.7342 | 5.248 | 5.2946 | 5.2631 | 5.3009 | 5.3415 | 5.2067 | 121.987 | 121.9811 | 121.9245 | 121.8058 | -0.034177 | 0.000325 | 0.003135 | 0.019713 | 122.0211 | 121.9838 | 121.9587 | 121.9214
2713.8438 | 121.994 | -0.11902 | 122.0169 | 3.6243 | 5.129 | 5.171 | 5.1441 | 5.1773 | 5.2134 | 5.0877 | 121.9549 | 121.9353 | 121.8833 | 121.7646 | -0.084531 | -0.045451 | -0.042641 | -0.030641 | 3.7433 | 5.248 | 5.29 | 5.2631 | 5.2963 | 5.3324 | 5.2067 | 122.0007 | 121.9811 | 121.9291 | 121.8103 | -0.038755 | 0.000325 | 0.003135 | 0.015135 | 122.0395 | 121.9976 | 121.9679 | 121.926
2715.5469 | 122.1359 | -0.068665 | 121.9345 | 3.693 | 5.1976 | 5.2305 | 5.2082 | 5.246 | 5.2821 | 5.1518 | 121.9458 | 121.9353 | 121.8742 | 121.7554 | -0.075375 | -0.045451 | -0.042641 | -0.039797 | 3.7617 | 5.2663 | 5.2992 | 5.2769 | 5.3146 | 5.3507 | 5.2205 | 121.9915 | 121.9811 | 121.92 | 121.8012 | -0.029599 | 0.000325 | 0.003135 | 0.005979 | 122.0211 | 121.9884 | 121.9496 | 121.9168
2717.25 | 122.1176 | -0.068665 | 121.9574 | 3.7159 | 5.2068 | 5.2534 | 5.2265 | 5.2734 | 5.3049 | 5.1656 | 121.9458 | 121.9444 | 121.8788 | 121.7646 | -0.079953 | -0.036295 | -0.042641 | -0.026063 | 3.7846 | 5.2755 | 5.3221 | 5.2952 | 5.3421 | 5.3736 | 5.2342 | 121.9915 | 121.9902 | 121.9245 | 121.8103 | -0.034177 | 0.009481 | 0.003135 | 0.019713 | 122.0257 | 121.9884 | 121.9587 | 121.9214
2718.9688 | 122.0398 | -0.11444 | 121.9666 | 3.7754 | 5.2663 | 5.3083 | 5.2815 | 5.3238 | 5.3553 | 5.2297 | 121.9412 | 121.9399 | 121.8788 | 121.7737 | -0.084531 | -0.036295 | -0.042641 | -0.026063 | 3.8898 | 5.3808 | 5.4228 | 5.3959 | 5.4382 | 5.4697 | 5.3441 | 121.987 | 121.9856 | 121.9245 | 121.8195 | -0.038755 | 0.009481 | 0.003135 | 0.019713 | 122.0257 | 121.9838 | 121.9633 | 121.9214
2720.6719 | 122.0444 | -0.10529 | 121.9574 | 3.8303 | 5.3213 | 5.3633 | 5.3227 | 5.3696 | 5.4102 | 5.2846 | 121.9412 | 121.9353 | 121.8833 | 121.7737 | -0.079953 | -0.036295 | -0.038063 | -0.026063 | 3.9356 | 5.4266 | 5.4686 | 5.428 | 5.4749 | 5.5155 | 5.3899 | 121.987 | 121.9811 | 121.9291 | 121.8195 | -0.034177 | 0.009481 | 0.007713 | 0.019713 | 122.0211 | 121.9792 | 121.9633 | 121.9214
2722.375 | 122.1451 | -0.068665 | 121.9528 | 3.9173 | 5.4174 | 5.4594 | 5.4325 | 5.4749 | 5.5064 | 5.3853 | 121.9458 | 121.9307 | 121.8788 | 121.76 | -0.070797 | -0.036295 | -0.042641 | -0.035219 | 3.986 | 5.4861 | 5.5281 | 5.5012 | 5.5435 | 5.5751 | 5.454 | 121.9915 | 121.9765 | 121.9245 | 121.8058 | -0.025021 | 0.009481 | 0.003135 | 0.010557 | 122.0166 | 121.9884 | 121.9496 | 121.9214
2724.0938 | 122.0169 | -0.12817 | 121.9894 | 3.954 | 5.4632 | 5.5052 | 5.4783 | 5.5207 | 5.5613 | 5.4265 | 121.9412 | 121.9399 | 121.8788 | 121.76 | -0.079953 | -0.031717 | -0.038063 | -0.026063 | 4.0821 | 5.5914 | 5.6334 | 5.6065 | 5.6488 | 5.6895 | 5.5547 | 121.987 | 121.9856 | 121.9245 | 121.8058 | -0.034177 | 0.014059 | 0.007713 | 0.019713 | 122.0211 | 121.9792 | 121.9587 | 121.9168
2725.8594 | 122.0215 | -0.10529 | 121.994 | 3.9997 | 5.4998 | 5.5373 | 5.5241 | 5.5527 | 5.5888 | 5.4586 | 121.9412 | 121.9399 | 121.8788 | 121.7737 | -0.075375 | -0.036295 | -0.04722 | -0.030641 | 4.105 | 5.6051 | 5.6426 | 5.6294 | 5.658 | 5.6941 | 5.5638 | 121.987 | 121.9856 | 121.9245 | 121.8195 | -0.029599 | 0.009481 | -0.001444 | 0.015135 | 122.0166 | 121.9884 | 121.9541 | 121.926
2727.5469 | 122.1588 | -0.068665 | 121.9391 | 4.0455 | 5.5365 | 5.5831 | 5.5424 | 5.5848 | 5.63 | 5.4998 | 121.9458 | 121.9353 | 121.8788 | 121.7691 | -0.070797 | -0.036295 | -0.038063 | -0.026063 | 4.1142 | 5.6051 | 5.6517 | 5.6111 | 5.6534 | 5.6987 | 5.5684 | 121.9915 | 121.9811 | 121.9245 | 121.8149 | -0.025021 | 0.009481 | 0.007713 | 0.019713 | 122.0166 | 121.9838 | 121.9496 | 121.9168
2729.3125 | 122.168 | -0.068665 | 121.9116 | 4.0867 | 5.5731 | 5.6151 | 5.5836 | 5.6168 | 5.6666 | 5.5318 | 121.9503 | 121.9399 | 121.8788 | 121.7691 | -0.075375 | -0.040873 | -0.042641 | -0.030641 | 4.1554 | 5.6418 | 5.6838 | 5.6523 | 5.6855 | 5.7353 | 5.6005 | 121.9961 | 121.9856 | 121.9245 | 121.8149 | -0.029599 | 0.004903 | 0.003135 | 0.015135 | 122.0257 | 121.993 | 121.9541 | 121.9214
2731.0781 | 122.0306 | -0.11444 | 121.9803 | 4.1463 | 5.6235 | 5.6655 | 5.6432 | 5.6809 | 5.7124 | 5.5822 | 121.9458 | 121.9353 | 121.8879 | 121.76 | -0.079953 | -0.036295 | -0.042641 | -0.026063 | 4.2607 | 5.7379 | 5.7799 | 5.7576 | 5.7953 | 5.8269 | 5.6966 | 121.9915 | 121.9811 | 121.9337 | 121.8058 | -0.034177 | 0.009481 | 0.003135 | 0.019713 | 122.0257 | 121.9884 | 121.9679 | 121.9306
2732.8438 | 122.081 | -0.09613 | 121.9849 | 4.1691 | 5.6372 | 5.67 | 5.6477 | 5.69 | 5.7124 | 5.5959 | 121.9458 | 121.9399 | 121.8879 | 121.7646 | -0.070797 | -0.045451 | -0.038063 | -0.030641 | 4.2653 | 5.7333 | 5.7662 | 5.7439 | 5.7862 | 5.8086 | 5.692 | 121.9915 | 121.9856 | 121.9337 | 121.8103 | -0.025021 | 0.000325 | 0.007713 | 0.015135 | 122.0166 | 121.9838 | 121.9587 | 121.926
2734.5625 | 122.0718 | -0.091553 | 121.9482 | 4.2058 | 5.6601 | 5.7021 | 5.6752 | 5.7221 | 5.7536 | 5.628 | 121.9503 | 121.9353 | 121.8788 | 121.7691 | -0.079953 | -0.045451 | -0.038063 | -0.026063 | 4.2973 | 5.7517 | 5.7936 | 5.7668 | 5.8136 | 5.8452 | 5.7195 | 121.9961 | 121.9811 | 121.9245 | 121.8149 | -0.034177 | 0.000325 | 0.007713 | 0.019713 | 122.0303 | 121.9884 | 121.9587 | 121.9168
2736.3281 | 122.1085 | -0.07782 | 121.962 | 4.2195 | 5.6509 | 5.6975 | 5.6661 | 5.7038 | 5.7445 | 5.6051 | 121.9458 | 121.9353 | 121.8833 | 121.76 | -0.079953 | -0.036295 | -0.04722 | -0.026063 | 4.2973 | 5.7288 | 5.7753 | 5.7439 | 5.7816 | 5.8223 | 5.6829 | 121.9915 | 121.9811 | 121.9291 | 121.8058 | -0.034177 | 0.009481 | -0.001444 | 0.019713 | 122.0257 | 121.993 | 121.9633 | 121.9306
2738.0938 | 122.1497 | -0.07782 | 121.9391 | 4.2424 | 5.6738 | 5.7113 | 5.6889 | 5.7221 | 5.7628 | 5.6325 | 121.9366 | 121.9399 | 121.8742 | 121.7646 | -0.079953 | -0.040873 | -0.04722 | -0.026063 | 4.3202 | 5.7517 | 5.7891 | 5.7668 | 5.7999 | 5.8406 | 5.7104 | 121.9824 | 121.9856 | 121.92 | 121.8103 | -0.034177 | 0.004903 | -0.001444 | 0.019713 | 122.0166 | 121.9838 | 121.9541 | 121.9214
2739.8594 | 122.0215 | -0.11902 | 121.994 | 4.3111 | 5.7425 | 5.7845 | 5.7485 | 5.7953 | 5.8223 | 5.6966 | 121.9458 | 121.9399 | 121.8833 | 121.7646 | -0.079953 | -0.036295 | -0.042641 | -0.026063 | 4.4301 | 5.8615 | 5.9035 | 5.8675 | 5.9144 | 5.9413 | 5.8156 | 121.9915 | 121.9856 | 121.9291 | 121.8103 | -0.034177 | 0.009481 | 0.003135 | 0.019713 | 122.0257 | 121.9884 | 121.9633 | 121.926
2741.5625 | 122.081 | -0.10071 | 121.9711 | 4.3477 | 5.77 | 5.8074 | 5.7805 | 5.8182 | 5.8589 | 5.7287 | 121.9549 | 121.9353 | 121.8788 | 121.76 | -0.075375 | -0.036295 | -0.042641 | -0.030641 | 4.4484 | 5.8707 | 5.9081 | 5.8812 | 5.9189 | 5.9596 | 5.8294 | 122.0007 | 121.9811 | 121.9245 | 121.8058 | -0.029599 | 0.009481 | 0.003135 | 0.015135 | 122.0303 | 121.9976 | 121.9541 | 121.9214
2743.3125 | 122.1085 | -0.086975 | 122.0032 | 4.3889 | 5.7929 | 5.8349 | 5.808 | 5.8503 | 5.8864 | 5.7607 | 121.9503 | 121.9353 | 121.8833 | 121.76 | -0.070797 | -0.036295 | -0.056376 | -0.030641 | 4.4759 | 5.8799 | 5.9219 | 5.895 | 5.9372 | 5.9734 | 5.8477 | 121.9961 | 121.9811 | 121.9291 | 121.8058 | -0.025021 | 0.009481 | -0.0106 | 0.015135 | 122.0211 | 122.0067 | 121.9541 | 121.9397
2745.0938 | 122.0673 | -0.11444 | 121.9757 | 4.4072 | 5.7929 | 5.8349 | 5.8126 | 5.8503 | 5.8818 | 5.747 | 121.9412 | 121.9399 | 121.8833 | 121.7646 | -0.075375 | -0.040873 | -0.042641 | -0.026063 | 4.5217 | 5.9073 | 5.9493 | 5.927 | 5.9647 | 5.9963 | 5.8614 | 121.987 | 121.9856 | 121.9291 | 121.8103 | -0.029599 | 0.004903 | 0.003135 | 0.019713 | 122.0166 | 121.9838 | 121.9587 | 121.926
2746.8594 | 122.0306 | -0.1236 | 121.9711 | 4.3843 | 5.7425 | 5.7754 | 5.7576 | 5.7908 | 5.8315 | 5.6966 | 121.9458 | 121.9353 | 121.8788 | 121.7646 | -0.070797 | -0.036295 | -0.038063 | -0.030641 | 4.5079 | 5.8661 | 5.899 | 5.8812 | 5.9144 | 5.9551 | 5.8202 | 121.9915 | 121.9811 | 121.9245 | 121.8103 | -0.025021 | 0.009481 | 0.007713 | 0.015135 | 122.0166 | 121.9838 | 121.9496 | 121.9168
2748.5781 | 122.1451 | -0.086975 | 121.9757 | 4.3981 | 5.7563 | 5.7982 | 5.7668 | 5.8091 | 5.8452 | 5.7104 | 121.9412 | 121.9353 | 121.8788 | 121.7691 | -0.075375 | -0.031717 | -0.051798 | -0.021484 | 4.485 | 5.8432 | 5.8852 | 5.8538 | 5.896 | 5.9322 | 5.7973 | 121.987 | 121.9811 | 121.9245 | 121.8149 | -0.029599 | 0.014059 | -0.006022 | 0.024292 | 122.0166 | 121.993 | 121.9541 | 121.9306
2750.3438 | 122.1497 | -0.073242 | 121.9391 | 4.4118 | 5.7517 | 5.7891 | 5.7714 | 5.7999 | 5.8452 | 5.7012 | 121.9412 | 121.9399 | 121.8788 | 121.7554 | -0.070797 | -0.040873 | -0.042641 | -0.030641 | 4.485 | 5.8249 | 5.8623 | 5.8446 | 5.8732 | 5.9184 | 5.7744 | 121.987 | 121.9856 | 121.9245 | 121.8012 | -0.025021 | 0.004903 | 0.003135 | 0.015135 | 122.012 | 121.9838 | 121.9496 | 121.9214
2752.0938 | 122.049 | -0.11444 | 121.9574 | 4.4622 | 5.7883 | 5.8349 | 5.8034 | 5.8411 | 5.8864 | 5.7424 | 121.9458 | 121.9399 | 121.8833 | 121.76 | -0.079953 | -0.031717 | -0.051798 | -0.026063 | 4.5766 | 5.9028 | 5.9493 | 5.9178 | 5.9556 | 6.0008 | 5.8568 | 121.9915 | 121.9856 | 121.9291 | 121.8058 | -0.034177 | 0.014059 | -0.006022 | 0.019713 | 122.0257 | 121.9976 | 121.9633 | 121.9351
2753.8594 | 122.0215 | -0.13733 | 121.9894 | 4.5079 | 5.8295 | 5.8715 | 5.8492 | 5.8869 | 5.9276 | 5.7928 | 121.9412 | 121.9353 | 121.8788 | 121.7646 | -0.084531 | -0.036295 | -0.038063 | -0.026063 | 4.6453 | 5.9669 | 6.0088 | 5.9865 | 6.0242 | 6.0649 | 5.9301 | 121.987 | 121.9811 | 121.9245 | 121.8103 | -0.038755 | 0.009481 | 0.007713 | 0.019713 | 122.0257 | 121.9792 | 121.9633 | 121.9168
2755.5625 | 122.1313 | -0.064087 | 121.9666 | 4.5537 | 5.8616 | 5.899 | 5.8721 | 5.9189 | 5.9597 | 5.8248 | 121.9412 | 121.9353 | 121.8742 | 121.76 | -0.079953 | -0.040873 | -0.042641 | -0.026063 | 4.6178 | 5.9257 | 5.9631 | 5.9362 | 5.983 | 6.0237 | 5.8889 | 121.987 | 121.9811 | 121.92 | 121.8058 | -0.034177 | 0.004903 | 0.003135 | 0.019713 | 122.0211 | 121.9838 | 121.9541 | 121.9168
2757.3281 | 122.0261 | -0.11444 | 121.9711 | 4.6041 | 5.9119 | 5.9493 | 5.927 | 5.9601 | 6.0054 | 5.866 | 121.9412 | 121.9399 | 121.8742 | 121.76 | -0.070797 | -0.040873 | -0.042641 | -0.026063 | 4.7185 | 6.0264 | 6.0638 | 6.0415 | 6.0746 | 6.1199 | 5.9805 | 121.987 | 121.9856 | 121.92 | 121.8058 | -0.025021 | 0.004903 | 0.003135 | 0.019713 | 122.012 | 121.9838 | 121.945 | 121.9168
2759.0312 | 122.0215 | -0.10529 | 121.994 | 4.6407 | 5.9348 | 5.986 | 5.9637 | 5.9968 | 6.0375 | 5.9072 | 121.9412 | 121.9307 | 121.8788 | 121.76 | -0.075375 | -0.040873 | -0.051798 | -0.021484 | 4.746 | 6.0401 | 6.0913 | 6.0689 | 6.1021 | 6.1428 | 6.0125 | 121.987 | 121.9765 | 121.9245 | 121.8058 | -0.029599 | 0.004903 | -0.006022 | 0.024292 | 122.0166 | 121.993 | 121.9541 | 121.9306
2760.7969 | 122.0352 | -0.11902 | 121.9711 | 4.6682 | 5.9577 | 6.0043 | 5.9911 | 6.0197 | 6.0512 | 5.921 | 121.9412 | 121.9353 | 121.8788 | 121.76 | -0.084531 | -0.040873 | -0.038063 | -0.030641 | 4.7872 | 6.0767 | 6.1233 | 6.1101 | 6.1387 | 6.1702 | 6.04 | 121.987 | 121.9811 | 121.9245 | 121.8058 | -0.038755 | 0.004903 | 0.007713 | 0.015135 | 122.0257 | 121.9792 | 121.9633 | 121.9168
2762.5625 | 122.0627 | -0.10071 | 121.9986 | 4.714 | 6.0035 | 6.0363 | 6.0186 | 6.0563 | 6.0878 | 5.9622 | 121.9503 | 121.9399 | 121.8833 | 121.76 | -0.075375 | -0.031717 | -0.042641 | -0.026063 | 4.8147 | 6.1042 | 6.137 | 6.1193 | 6.157 | 6.1886 | 6.0629 | 121.9961 | 121.9856 | 121.9291 | 121.8058 | -0.029599 | 0.014059 | 0.003135 | 0.019713 | 122.0257 | 121.993 | 121.9587 | 121.926
2764.2656 | 122.0352 | -0.1236 | 122.0123 | 4.7643 | 6.0447 | 6.0867 | 6.069 | 6.1066 | 6.1382 | 6.0079 | 121.9458 | 121.9399 | 121.8788 | 121.76 | -0.084531 | -0.031717 | -0.042641 | -0.030641 | 4.8879 | 6.1683 | 6.2103 | 6.1926 | 6.2302 | 6.2618 | 6.1315 | 121.9915 | 121.9856 | 121.9245 | 121.8058 | -0.038755 | 0.014059 | 0.003135 | 0.015135 | 122.0303 | 121.9884 | 121.9633 | 121.9214
2765.9531 | 122.1085 | -0.086975 | 121.9574 | 4.7872 | 6.0493 | 6.0959 | 6.069 | 6.1112 | 6.1428 | 6.0079 | 121.9412 | 121.9353 | 121.8788 | 121.76 | -0.075375 | -0.040873 | -0.042641 | -0.030641 | 4.8742 | 6.1363 | 6.1828 | 6.1559 | 6.1982 | 6.2298 | 6.0949 | 121.987 | 121.9811 | 121.9245 | 121.8058 | -0.029599 | 0.004903 | 0.003135 | 0.015135 | 122.0166 | 121.9838 | 121.9541 | 121.9214
2767.6562 | 122.1085 | -0.059509 | 121.9894 | 4.8559 | 6.1271 | 6.1691 | 6.1468 | 6.1936 | 6.2252 | 6.0903 | 121.9503 | 121.9307 | 121.8788 | 121.76 | -0.070797 | -0.036295 | -0.038063 | -0.021484 | 4.9154 | 6.1867 | 6.2286 | 6.2063 | 6.2531 | 6.2847 | 6.1499 | 121.9961 | 121.9765 | 121.9245 | 121.8058 | -0.025021 | 0.009481 | 0.007713 | 0.024292 | 122.0211 | 121.9884 | 121.9496 | 121.9168
2769.3594 | 122.1542 | -0.068665 | 121.9482 | 4.8559 | 6.0951 | 6.1416 | 6.1285 | 6.157 | 6.2023 | 6.0583 | 121.9458 | 121.9399 | 121.8833 | 121.7646 | -0.075375 | -0.040873 | -0.04722 | -0.035219 | 4.9246 | 6.1638 | 6.2103 | 6.1971 | 6.2257 | 6.271 | 6.127 | 121.9915 | 121.9856 | 121.9291 | 121.8103 | -0.029599 | 0.004903 | -0.001444 | 0.010557 | 122.0211 | 121.993 | 121.9587 | 121.9306
2771.1094 | 122.1497 | -0.10071 | 121.9574 | 4.9108 | 6.15 | 6.1966 | 6.1743 | 6.2165 | 6.2435 | 6.1132 | 121.9412 | 121.9307 | 121.8788 | 121.7646 | -0.075375 | -0.040873 | -0.038063 | -0.026063 | 5.0116 | 6.2507 | 6.2973 | 6.275 | 6.3172 | 6.3442 | 6.2139 | 121.987 | 121.9765 | 121.9245 | 121.8103 | -0.029599 | 0.004903 | 0.007713 | 0.019713 | 122.0166 | 121.9792 | 121.9541 | 121.9168
2772.875 | 122.0261 | -0.11902 | 121.9849 | 4.9612 | 6.205 | 6.247 | 6.2292 | 6.2623 | 6.2985 | 6.1682 | 121.9412 | 121.9307 | 121.8833 | 121.76 | -0.079953 | -0.036295 | -0.042641 | -0.030641 | 5.0802 | 6.324 | 6.366 | 6.3482 | 6.3813 | 6.4175 | 6.2872 | 121.987 | 121.9765 | 121.9291 | 121.8058 | -0.034177 | 0.009481 | 0.003135 | 0.015135 | 122.0211 | 121.9838 | 121.9633 | 121.926
2774.6406 | 122.1268 | -0.059509 | 121.9345 | 4.9795 | 6.205 | 6.247 | 6.2292 | 6.2577 | 6.2985 | 6.1682 | 121.9458 | 121.9444 | 121.8788 | 121.76 | -0.075375 | -0.036295 | -0.042641 | -0.026063 | 5.039 | 6.2645 | 6.3065 | 6.2887 | 6.3172 | 6.358 | 6.2277 | 121.9915 | 121.9902 | 121.9245 | 121.8058 | -0.029599 | 0.009481 | 0.003135 | 0.019713 | 122.0211 | 121.9884 | 121.9541 | 121.9214
2776.4062 | 122.1451 | -0.073242 | 121.9528 | 5.0207 | 6.2279 | 6.2744 | 6.2567 | 6.2852 | 6.3259 | 6.1911 | 121.9458 | 121.9444 | 121.8788 | 121.76 | -0.075375 | -0.036295 | -0.042641 | -0.026063 | 5.094 | 6.3011 | 6.3477 | 6.3299 | 6.3584 | 6.3992 | 6.2643 | 121.9915 | 121.9902 | 121.9245 | 121.8058 | -0.029599 | 0.009481 | 0.003135 | 0.019713 | 122.0211 | 121.9884 | 121.9541 | 121.9214
2778.1719 | 122.0398 | -0.10986 | 122.0123 | 4.9933 | 6.1684 | 6.2149 | 6.1926 | 6.2348 | 6.2664 | 6.127 | 121.9412 | 121.9307 | 121.8833 | 121.7554 | -0.079953 | -0.040873 | -0.028906 | -0.026063 | 5.1031 | 6.2782 | 6.3248 | 6.3024 | 6.3447 | 6.3763 | 6.2368 | 121.987 | 121.9765 | 121.9291 | 121.8012 | -0.034177 | 0.004903 | 0.01687 | 0.019713 | 122.0211 | 121.9701 | 121.9633 | 121.9122
2779.8906 | 122.1451 | -0.07782 | 121.9849 | 5.0299 | 6.2096 | 6.2561 | 6.2384 | 6.2714 | 6.303 | 6.1773 | 121.9412 | 121.9399 | 121.8833 | 121.7554 | -0.075375 | -0.040873 | -0.042641 | -0.021484 | 5.1077 | 6.2874 | 6.3339 | 6.3162 | 6.3493 | 6.3809 | 6.2552 | 121.987 | 121.9856 | 121.9291 | 121.8012 | -0.029599 | 0.004903 | 0.003135 | 0.024292 | 122.0166 | 121.9838 | 121.9587 | 121.926
2781.6719 | 122.0123 | -0.12817 | 122.0032 | 5.0848 | 6.2599 | 6.3065 | 6.2841 | 6.3172 | 6.358 | 6.2231 | 121.9503 | 121.9353 | 121.8788 | 121.7646 | -0.079953 | -0.036295 | -0.042641 | -0.021484 | 5.213 | 6.3881 | 6.4346 | 6.4123 | 6.4454 | 6.4861 | 6.3513 | 121.9961 | 121.9811 | 121.9245 | 121.8103 | -0.034177 | 0.009481 | 0.003135 | 0.024292 | 122.0303 | 121.993 | 121.9587 | 121.9214
2783.375 | 122.1039 | -0.09613 | 121.9345 | 5.0848 | 6.237 | 6.2836 | 6.2704 | 6.2898 | 6.3259 | 6.2002 | 121.9412 | 121.9353 | 121.8833 | 121.7554 | -0.075375 | -0.036295 | -0.042641 | -0.030641 | 5.181 | 6.3332 | 6.3797 | 6.3665 | 6.3859 | 6.4221 | 6.2964 | 121.987 | 121.9811 | 121.9291 | 121.8012 | -0.029599 | 0.009481 | 0.003135 | 0.015135 | 122.0166 | 121.9838 | 121.9587 | 121.926
2785.1406 | 122.0215 | -0.1236 | 121.9894 | 5.1855 | 6.3423 | 6.3843 | 6.362 | 6.4134 | 6.4404 | 6.3055 | 121.9412 | 121.9399 | 121.8879 | 121.7691 | -0.075375 | -0.036295 | -0.042641 | -0.026063 | 5.3091 | 6.4659 | 6.5079 | 6.4856 | 6.537 | 6.564 | 6.4291 | 121.987 | 121.9856 | 121.9337 | 121.8149 | -0.029599 | 0.009481 | 0.003135 | 0.019713 | 122.0166 | 121.9838 | 121.9633 | 121.9306
2786.9062 | 122.0169 | -0.1236 | 121.9757 | 5.2039 | 6.3469 | 6.3889 | 6.3711 | 6.4134 | 6.4404 | 6.3147 | 121.9412 | 121.9353 | 121.8833 | 121.76 | -0.070797 | -0.036295 | -0.04722 | -0.030641 | 5.3275 | 6.4705 | 6.5125 | 6.4947 | 6.537 | 6.564 | 6.4383 | 121.987 | 121.9811 | 121.9291 | 121.8058 | -0.025021 | 0.009481 | -0.001444 | 0.015135 | 122.012 | 121.9884 | 121.9541 | 121.9306
2788.6094 | 122.0306 | -0.11444 | 121.9711 | 5.1581 | 6.2645 | 6.311 | 6.2933 | 6.331 | 6.3534 | 6.2368 | 121.9412 | 121.9353 | 121.8696 | 121.7691 | -0.075375 | -0.036295 | -0.04722 | -0.030641 | 5.2725 | 6.379 | 6.4255 | 6.4077 | 6.4454 | 6.4678 | 6.3513 | 121.987 | 121.9811 | 121.9154 | 121.8149 | -0.029599 | 0.009481 | -0.001444 | 0.015135 | 122.0166 | 121.9884 | 121.945 | 121.9168
2790.3906 | 122.0352 | -0.11444 | 122.0123 | 5.1627 | 6.2554 | 6.2973 | 6.2796 | 6.3126 | 6.3442 | 6.2048 | 121.9458 | 121.9399 | 121.8742 | 121.76 | -0.070797 | -0.036295 | -0.042641 | -0.026063 | 5.2771 | 6.3698 | 6.4118 | 6.394 | 6.4271 | 6.4587 | 6.3192 | 121.9915 | 121.9856 | 121.92 | 121.8058 | -0.025021 | 0.009481 | 0.003135 | 0.019713 | 122.0166 | 121.9884 | 121.945 | 121.9168
2792.0938 | 122.0947 | -0.07782 | 121.9482 | 5.2039 | 6.292 | 6.3431 | 6.3208 | 6.363 | 6.3854 | 6.2597 | 121.9412 | 121.9307 | 121.8788 | 121.76 | -0.079953 | -0.031717 | -0.042641 | -0.030641 | 5.2817 | 6.3698 | 6.4209 | 6.3986 | 6.4408 | 6.4633 | 6.3376 | 121.987 | 121.9765 | 121.9245 | 121.8058 | -0.034177 | 0.014059 | 0.003135 | 0.015135 | 122.0211 | 121.9838 | 121.9587 | 121.9214
2793.8594 | 122.1268 | -0.07782 | 121.9391 | 5.2313 | 6.3149 | 6.3431 | 6.3345 | 6.3722 | 6.4038 | 6.2689 | 121.9412 | 121.9353 | 121.8788 | 121.7646 | -0.084531 | -0.040873 | -0.042641 | -0.026063 | 5.3092 | 6.3927 | 6.4209 | 6.4123 | 6.45 | 6.4816 | 6.3467 | 121.987 | 121.9811 | 121.9245 | 121.8103 | -0.038755 | 0.004903 | 0.003135 | 0.019713 | 122.0257 | 121.9838 | 121.9633 | 121.9214
2795.625 | 122.1497 | -0.064087 | 121.9391 | 5.2222 | 6.2737 | 6.3156 | 6.2979 | 6.331 | 6.3671 | 6.2323 | 121.9366 | 121.9399 | 121.8742 | 121.76 | -0.075375 | -0.031717 | -0.042641 | -0.021484 | 5.2863 | 6.3378 | 6.3797 | 6.362 | 6.395 | 6.4312 | 6.2964 | 121.9824 | 121.9856 | 121.92 | 121.8058 | -0.029599 | 0.014059 | 0.003135 | 0.024292 | 122.012 | 121.9792 | 121.9496 | 121.9168
2797.375 | 122.1085 | -0.10071 | 121.9711 | 5.2588 | 6.3057 | 6.3568 | 6.3437 | 6.3676 | 6.3992 | 6.2643 | 121.9366 | 121.9353 | 121.8742 | 121.7646 | -0.079953 | -0.031717 | -0.042641 | -0.026063 | 5.3595 | 6.4064 | 6.4575 | 6.4444 | 6.4683 | 6.4999 | 6.365 | 121.9824 | 121.9811 | 121.92 | 121.8103 | -0.034177 | 0.014059 | 0.003135 | 0.019713 | 122.0166 | 121.9792 | 121.9541 | 121.9168
2799.0781 | 122.0627 | -0.10529 | 121.9666 | 5.2909 | 6.3332 | 6.3752 | 6.3482 | 6.3996 | 6.4312 | 6.2964 | 121.9458 | 121.9353 | 121.8788 | 121.7646 | -0.075375 | -0.036295 | -0.042641 | -0.026063 | 5.3961 | 6.4385 | 6.4804 | 6.4535 | 6.5049 | 6.5365 | 6.4017 | 121.9915 | 121.9811 | 121.9245 | 121.8103 | -0.029599 | 0.009481 | 0.003135 | 0.019713 | 122.0211 | 121.9884 | 121.9541 | 121.9214
2800.8438 | 122.1542 | -0.064087 | 121.9391 | 5.3229 | 6.3423 | 6.398 | 6.3711 | 6.4179 | 6.4495 | 6.3193 | 121.9366 | 121.9399 | 121.8788 | 121.7646 | -0.070797 | -0.040873 | -0.042641 | -0.026063 | 5.387 | 6.4064 | 6.4621 | 6.4352 | 6.482 | 6.5136 | 6.3833 | 121.9824 | 121.9856 | 121.9245 | 121.8103 | -0.025021 | 0.004903 | 0.003135 | 0.019713 | 122.0074 | 121.9792 | 121.9496 | 121.9214
2802.6094 | 122.0535 | -0.10986 | 121.9666 | 5.3458 | 6.3607 | 6.4026 | 6.3849 | 6.4225 | 6.4679 | 6.3238 | 121.9458 | 121.9353 | 121.8788 | 121.76 | -0.079953 | -0.040873 | -0.042641 | -0.026063 | 5.4557 | 6.4705 | 6.5125 | 6.4947 | 6.5324 | 6.5777 | 6.4337 | 121.9915 | 121.9811 | 121.9245 | 121.8058 | -0.034177 | 0.004903 | 0.003135 | 0.019713 | 122.0257 | 121.9884 | 121.9587 | 121.9214
2804.3125 | 122.0261 | -0.13275 | 121.9894 | 5.3183 | 6.3011 | 6.3431 | 6.3299 | 6.3676 | 6.3992 | 6.2597 | 121.9412 | 121.9399 | 121.8788 | 121.7646 | -0.075375 | -0.031717 | -0.042641 | -0.021484 | 5.4511 | 6.4339 | 6.4759 | 6.4627 | 6.5003 | 6.5319 | 6.3925 | 121.987 | 121.9856 | 121.9245 | 121.8103 | -0.029599 | 0.014059 | 0.003135 | 0.024292 | 122.0166 | 121.9838 | 121.9541 | 121.9214
2806.0781 | 122.0078 | -0.12817 | 121.9894 | 5.3275 | 6.3103 | 6.3568 | 6.3345 | 6.3722 | 6.4083 | 6.2689 | 121.9458 | 121.9307 | 121.8788 | 121.7646 | -0.079953 | -0.040873 | -0.042641 | -0.026063 | 5.4557 | 6.4385 | 6.485 | 6.4627 | 6.5003 | 6.5365 | 6.3971 | 121.9915 | 121.9765 | 121.9245 | 121.8103 | -0.034177 | 0.004903 | 0.003135 | 0.019713 | 122.0257 | 121.9884 | 121.9587 | 121.9214
2807.8281 | 122.0352 | -0.10071 | 121.9849 | 5.3229 | 6.2874 | 6.3248 | 6.3162 | 6.3447 | 6.3763 | 6.2552 | 121.9458 | 121.9353 | 121.8788 | 121.76 | -0.079953 | -0.027139 | -0.04722 | -0.026063 | 5.4236 | 6.3881 | 6.4255 | 6.4169 | 6.4454 | 6.477 | 6.3559 | 121.9915 | 121.9811 | 121.9245 | 121.8058 | -0.034177 | 0.018637 | -0.001444 | 0.019713 | 122.0257 | 121.993 | 121.9587 | 121.926
2809.5938 | 122.1497 | -0.064087 | 121.9574 | 5.3366 | 6.2691 | 6.3065 | 6.2933 | 6.331 | 6.3671 | 6.2277 | 121.9458 | 121.9399 | 121.8742 | 121.7554 | -0.079953 | -0.031717 | -0.042641 | -0.026063 | 5.4007 | 6.3332 | 6.3706 | 6.3574 | 6.395 | 6.4312 | 6.2918 | 121.9915 | 121.9856 | 121.92 | 121.8012 | -0.034177 | 0.014059 | 0.003135 | 0.019713 | 122.0257 | 121.9884 | 121.9541 | 121.9168
2811.3438 | 122.1268 | -0.073242 | 121.9574 | 5.3458 | 6.2737 | 6.3156 | 6.3025 | 6.331 | 6.3671 | 6.2323 | 121.9412 | 121.9353 | 121.8833 | 121.76 | -0.075375 | -0.040873 | -0.042641 | -0.026063 | 5.419 | 6.3469 | 6.3889 | 6.3757 | 6.4042 | 6.4404 | 6.3055 | 121.987 | 121.9811 | 121.9291 | 121.8058 | -0.029599 | 0.004903 | 0.003135 | 0.019713 | 122.0166 | 121.9838 | 121.9587 | 121.926
2813.0469 | 122.0032 | -0.11902 | 121.994 | 5.3183 | 6.2279 | 6.2653 | 6.2521 | 6.2898 | 6.3213 | 6.2002 | 121.9458 | 121.9261 | 121.8788 | 121.76 | -0.079953 | -0.040873 | -0.042641 | -0.026063 | 5.4373 | 6.3469 | 6.3843 | 6.3711 | 6.4088 | 6.4404 | 6.3192 | 121.9915 | 121.9719 | 121.9245 | 121.8058 | -0.034177 | 0.004903 | 0.003135 | 0.019713 | 122.0257 | 121.9884 | 121.9587 | 121.9214
2814.8281 | 122.1451 | -0.082397 | 121.9437 | 5.3229 | 6.205 | 6.247 | 6.2292 | 6.2714 | 6.303 | 6.1636 | 121.9458 | 121.9399 | 121.8788 | 121.7646 | -0.075375 | -0.031717 | -0.038063 | -0.026063 | 5.4053 | 6.2874 | 6.3293 | 6.3116 | 6.3538 | 6.3854 | 6.246 | 121.9915 | 121.9856 | 121.9245 | 121.8103 | -0.029599 | 0.014059 | 0.007713 | 0.019713 | 122.0211 | 121.9838 | 121.9541 | 121.9168
2816.5938 | 122.0673 | -0.11444 | 121.9711 | 5.2542 | 6.0997 | 6.1462 | 6.1285 | 6.1662 | 6.2023 | 6.0629 | 121.9366 | 121.9261 | 121.8788 | 121.7508 | -0.075375 | -0.031717 | -0.042641 | -0.030641 | 5.3687 | 6.2141 | 6.2607 | 6.2429 | 6.2806 | 6.3167 | 6.1773 | 121.9824 | 121.9719 | 121.9245 | 121.7966 | -0.029599 | 0.014059 | 0.003135 | 0.015135 | 122.012 | 121.9792 | 121.9541 | 121.9214
2818.3594 | 122.0535 | -0.11444 | 121.9986 | 5.2954 | 6.1409 | 6.1829 | 6.156 | 6.2028 | 6.2389 | 6.0949 | 121.9458 | 121.9399 | 121.8788 | 121.76 | -0.070797 | -0.036295 | -0.04722 | -0.021484 | 5.4099 | 6.2553 | 6.2973 | 6.2704 | 6.3172 | 6.3534 | 6.2094 | 121.9915 | 121.9856 | 121.9245 | 121.8058 | -0.025021 | 0.009481 | -0.001444 | 0.024292 | 122.0166 | 121.993 | 121.9496 | 121.926
2820.0625 | 122.1405 | -0.068665 | 121.962 | 5.2405 | 6.0722 | 6.1096 | 6.0919 | 6.1295 | 6.1657 | 6.0263 | 121.9412 | 121.9353 | 121.8788 | 121.7646 | -0.075375 | -0.036295 | -0.038063 | -0.021484 | 5.3092 | 6.1409 | 6.1783 | 6.1605 | 6.1982 | 6.2343 | 6.0949 | 121.987 | 121.9811 | 121.9245 | 121.8103 | -0.029599 | 0.009481 | 0.007713 | 0.024292 | 122.0166 | 121.9792 | 121.9541 | 121.9168
2821.8281 | 122.1588 | -0.064087 | 121.9345 | 5.213 | 6.0173 | 6.0546 | 6.0369 | 6.0792 | 6.1153 | 5.9805 | 121.9412 | 121.9307 | 121.8788 | 121.76 | -0.079953 | -0.036295 | -0.04722 | -0.026063 | 5.2771 | 6.0813 | 6.1187 | 6.101 | 6.1433 | 6.1794 | 6.0446 | 121.987 | 121.9765 | 121.9245 | 121.8058 | -0.034177 | 0.009481 | -0.001444 | 0.019713 | 122.0211 | 121.9884 | 121.9587 | 121.926
2823.5156 | 122.0215 | -0.1236 | 121.9711 | 5.181 | 5.9669 | 5.9951 | 5.982 | 6.0151 | 6.0558 | 5.921 | 121.9458 | 121.9307 | 121.8742 | 121.76 | -0.066219 | -0.040873 | -0.04722 | -0.035219 | 5.3046 | 6.0905 | 6.1187 | 6.1056 | 6.1387 | 6.1794 | 6.0446 | 121.9915 | 121.9765 | 121.92 | 121.8058 | -0.020443 | 0.004903 | -0.001444 | 0.010557 | 122.012 | 121.993 | 121.9404 | 121.9214
2825.2812 | 122.0993 | -0.07782 | 121.9391 | 5.1627 | 5.9211 | 5.9631 | 5.9408 | 5.9785 | 6.0192 | 5.8843 | 121.9366 | 121.9307 | 121.8788 | 121.7554 | -0.075375 | -0.045451 | -0.042641 | -0.026063 | 5.2405 | 5.9989 | 6.0409 | 6.0186 | 6.0563 | 6.097 | 5.9622 | 121.9824 | 121.9765 | 121.9245 | 121.8012 | -0.029599 | 0.000325 | 0.003135 | 0.019713 | 122.012 | 121.9792 | 121.9541 | 121.9214
2826.9844 | 122.0627 | -0.10986 | 121.9528 | 5.1718 | 5.9211 | 5.9631 | 5.9362 | 5.9785 | 6.01 | 5.8798 | 121.9412 | 121.9353 | 121.8742 | 121.7691 | -0.070797 | -0.031717 | -0.038063 | -0.021484 | 5.2817 | 6.031 | 6.0729 | 6.046 | 6.0883 | 6.1199 | 5.9896 | 121.987 | 121.9811 | 121.92 | 121.8149 | -0.025021 | 0.014059 | 0.007713 | 0.024292 | 122.012 | 121.9792 | 121.945 | 121.9123
2828.75 | 122.0581 | -0.091553 | 121.9574 | 5.1352 | 5.8616 | 5.8944 | 5.8812 | 5.9189 | 5.9551 | 5.8157 | 121.9458 | 121.9399 | 121.8788 | 121.7646 | -0.079953 | -0.027139 | -0.042641 | -0.021484 | 5.2267 | 5.9531 | 5.986 | 5.9728 | 6.0105 | 6.0466 | 5.9072 | 121.9915 | 121.9856 | 121.9245 | 121.8103 | -0.034177 | 0.018637 | 0.003135 | 0.024292 | 122.0257 | 121.9884 | 121.9587 | 121.9214
2830.4531 | 122.0261 | -0.11444 | 121.9803 | 5.1077 | 5.8112 | 5.8532 | 5.8309 | 5.8732 | 5.9047 | 5.7653 | 121.9412 | 121.9353 | 121.8742 | 121.76 | -0.079953 | -0.040873 | -0.038063 | -0.016906 | 5.2222 | 5.9256 | 5.9676 | 5.9453 | 5.9876 | 6.0192 | 5.8797 | 121.987 | 121.9811 | 121.92 | 121.8058 | -0.034177 | 0.004903 | 0.007713 | 0.02887 | 122.0211 | 121.9792 | 121.9541 | 121.9123
2832.2188 | 122.0718 | -0.091553 | 121.9803 | 5.1215 | 5.8204 | 5.8578 | 5.8492 | 5.8823 | 5.9093 | 5.7745 | 121.9412 | 121.9399 | 121.8742 | 121.7646 | -0.075375 | -0.040873 | -0.04722 | -0.021484 | 5.213 | 5.9119 | 5.9493 | 5.9407 | 5.9739 | 6.0008 | 5.866 | 121.987 | 121.9856 | 121.92 | 121.8103 | -0.029599 | 0.004903 | -0.001444 | 0.024292 | 122.0166 | 121.9884 | 121.9496 | 121.9214
2833.9844 | 122.1497 | -0.068665 | 121.9299 | 5.1901 | 5.8799 | 5.931 | 5.9133 | 5.9464 | 5.978 | 5.8523 | 121.9458 | 121.9307 | 121.8742 | 121.76 | -0.075375 | -0.040873 | -0.042641 | -0.021484 | 5.2588 | 5.9486 | 5.9997 | 5.982 | 6.0151 | 6.0466 | 5.9209 | 121.9915 | 121.9765 | 121.92 | 121.8058 | -0.029599 | 0.004903 | 0.003135 | 0.024292 | 122.0211 | 121.9884 | 121.9496 | 121.9168
2835.7031 | 121.9894 | -0.10986 | 121.9849 | 5.1855 | 5.8616 | 5.9036 | 5.8721 | 5.9189 | 5.9551 | 5.8202 | 121.9412 | 121.9261 | 121.8742 | 121.7554 | -0.070797 | -0.031717 | -0.04722 | -0.030641 | 5.2954 | 5.9714 | 6.0134 | 5.9819 | 6.0288 | 6.0649 | 5.9301 | 121.987 | 121.9719 | 121.92 | 121.8012 | -0.025021 | 0.014059 | -0.001444 | 0.015135 | 122.012 | 121.9884 | 121.945 | 121.9214
2837.4531 | 122.0627 | -0.09613 | 121.9803 | 5.1993 | 5.8616 | 5.9036 | 5.8858 | 5.9281 | 5.9642 | 5.8248 | 121.9366 | 121.9353 | 121.8788 | 121.76 | -0.079953 | -0.031717 | -0.042641 | -0.026063 | 5.2954 | 5.9577 | 5.9997 | 5.9819 | 6.0242 | 6.0604 | 5.9209 | 121.9824 | 121.9811 | 121.9245 | 121.8058 | -0.034177 | 0.014059 | 0.003135 | 0.019713 | 122.0166 | 121.9792 | 121.9587 | 121.9214
2839.1562 | 122.1313 | -0.091553 | 121.9666 | 5.181 | 5.8295 | 5.8761 | 5.8629 | 5.8961 | 5.9276 | 5.7973 | 121.9412 | 121.9261 | 121.8696 | 121.7554 | -0.070797 | -0.031717 | -0.042641 | -0.026063 | 5.2725 | 5.9211 | 5.9676 | 5.9545 | 5.9876 | 6.0192 | 5.8889 | 121.987 | 121.9719 | 121.9154 | 121.8012 | -0.025021 | 0.014059 | 0.003135 | 0.019713 | 122.012 | 121.9838 | 121.9404 | 121.9123
2840.9219 | 122.0078 | -0.11444 | 121.994 | 5.213 | 5.8524 | 5.8852 | 5.8767 | 5.9144 | 5.9413 | 5.8111 | 121.9412 | 121.9307 | 121.8696 | 121.76 | -0.075375 | -0.031717 | -0.038063 | -0.026063 | 5.3275 | 5.9669 | 5.9997 | 5.9911 | 6.0288 | 6.0558 | 5.9255 | 121.987 | 121.9765 | 121.9154 | 121.8058 | -0.029599 | 0.014059 | 0.007713 | 0.019713 | 122.0166 | 121.9792 | 121.945 | 121.9077
2842.6875 | 122.0261 | -0.1236 | 121.9849 | 5.1901 | 5.8204 | 5.8623 | 5.8492 | 5.8823 | 5.9139 | 5.7745 | 121.9366 | 121.9353 | 121.8742 | 121.76 | -0.070797 | -0.036295 | -0.038063 | -0.021484 | 5.3137 | 5.944 | 5.9859 | 5.9728 | 6.0059 | 6.0375 | 5.8981 | 121.9824 | 121.9811 | 121.92 | 121.8058 | -0.025021 | 0.009481 | 0.007713 | 0.024292 | 122.0074 | 121.9747 | 121.945 | 121.9123
2844.3906 | 122.0215 | -0.12817 | 121.9757 | 5.1993 | 5.8204 | 5.8669 | 5.8492 | 5.8869 | 5.923 | 5.7836 | 121.9412 | 121.9307 | 121.8742 | 121.7646 | -0.075375 | -0.036295 | -0.033484 | -0.021484 | 5.3275 | 5.9485 | 5.9951 | 5.9774 | 6.0151 | 6.0512 | 5.9118 | 121.987 | 121.9765 | 121.92 | 121.8103 | -0.029599 | 0.009481 | 0.012292 | 0.024292 | 122.0166 | 121.9747 | 121.9496 | 121.9077
2846.1562 | 122.1588 | -0.091553 | 121.9299 | 5.1306 | 5.7242 | 5.7616 | 5.7439 | 5.7816 | 5.8086 | 5.6737 | 121.9366 | 121.9307 | 121.8742 | 121.76 | -0.070797 | -0.036295 | -0.038063 | -0.030641 | 5.2222 | 5.8158 | 5.8532 | 5.8354 | 5.8732 | 5.9001 | 5.7653 | 121.9824 | 121.9765 | 121.92 | 121.8058 | -0.025021 | 0.009481 | 0.007713 | 0.015135 | 122.0074 | 121.9747 | 121.945 | 121.9123
2847.9219 | 122.1222 | -0.09613 | 121.9711 | 5.2405 | 5.8295 | 5.8761 | 5.8492 | 5.8915 | 5.9322 | 5.7882 | 121.9412 | 121.9261 | 121.8788 | 121.76 | -0.075375 | -0.040873 | -0.033484 | -0.021484 | 5.3366 | 5.9257 | 5.9722 | 5.9453 | 5.9876 | 6.0283 | 5.8843 | 121.987 | 121.9719 | 121.9245 | 121.8058 | -0.029599 | 0.004903 | 0.012292 | 0.024292 | 122.0166 | 121.9747 | 121.9541 | 121.9122
2849.6719 | 121.9986 | -0.14191 | 121.994 | 5.1901 | 5.77 | 5.812 | 5.7897 | 5.8274 | 5.8589 | 5.7287 | 121.9412 | 121.9353 | 121.8742 | 121.7646 | -0.070797 | -0.036295 | -0.038063 | -0.021484 | 5.332 | 5.9119 | 5.9539 | 5.9316 | 5.9693 | 6.0008 | 5.8706 | 121.987 | 121.9811 | 121.92 | 121.8103 | -0.025021 | 0.009481 | 0.007713 | 0.024292 | 122.012 | 121.9792 | 121.945 | 121.9123
2851.4375 | 122.0444 | -0.11902 | 121.9757 | 5.1169 | 5.6693 | 5.7158 | 5.7027 | 5.7358 | 5.7674 | 5.628 | 121.9412 | 121.9399 | 121.8833 | 121.7508 | -0.070797 | -0.036295 | -0.033484 | -0.026063 | 5.2359 | 5.7883 | 5.8349 | 5.8217 | 5.8548 | 5.8864 | 5.747 | 121.987 | 121.9856 | 121.9291 | 121.7966 | -0.025021 | 0.009481 | 0.012292 | 0.019713 | 122.012 | 121.9747 | 121.9541 | 121.9168
2853.2031 | 121.994 | -0.10986 | 122.0078 | 5.1489 | 5.6922 | 5.7387 | 5.721 | 5.7587 | 5.7994 | 5.6554 | 121.9412 | 121.9307 | 121.8742 | 121.7508 | -0.075375 | -0.036295 | -0.04722 | -0.021484 | 5.2588 | 5.802 | 5.8486 | 5.8309 | 5.8686 | 5.9093 | 5.7653 | 121.987 | 121.9765 | 121.92 | 121.7966 | -0.029599 | 0.009481 | -0.001444 | 0.024292 | 122.0166 | 121.9884 | 121.9496 | 121.9214
2854.9688 | 122.0261 | -0.10071 | 121.9849 | 5.1627 | 5.6922 | 5.7479 | 5.7256 | 5.7633 | 5.7903 | 5.6646 | 121.932 | 121.9353 | 121.8742 | 121.7508 | -0.066219 | -0.036295 | -0.04722 | -0.026063 | 5.2634 | 5.7929 | 5.8486 | 5.8263 | 5.864 | 5.891 | 5.7653 | 121.9778 | 121.9811 | 121.92 | 121.7966 | -0.020443 | 0.009481 | -0.001444 | 0.019713 | 121.9982 | 121.9792 | 121.9404 | 121.9214
2856.6875 | 122.0444 | -0.11902 | 121.962 | 5.1352 | 5.6555 | 5.7067 | 5.6752 | 5.7175 | 5.7628 | 5.6188 | 121.9366 | 121.9307 | 121.8742 | 121.7508 | -0.070797 | -0.031717 | -0.04722 | -0.026063 | 5.2542 | 5.7745 | 5.8257 | 5.7942 | 5.8365 | 5.8818 | 5.7378 | 121.9824 | 121.9765 | 121.92 | 121.7966 | -0.025021 | 0.014059 | -0.001444 | 0.019713 | 122.0074 | 121.9838 | 121.945 | 121.9214
2858.4531 | 122.1542 | -0.068665 | 121.9391 | 5.1398 | 5.6326 | 5.6838 | 5.6706 | 5.7084 | 5.7399 | 5.6005 | 121.9458 | 121.9307 | 121.8742 | 121.7646 | -0.075375 | -0.036295 | -0.042641 | -0.026063 | 5.2084 | 5.7013 | 5.7524 | 5.7393 | 5.777 | 5.8086 | 5.6691 | 121.9915 | 121.9765 | 121.92 | 121.8103 | -0.029599 | 0.009481 | 0.003135 | 0.019713 | 122.0211 | 121.9884 | 121.9496 | 121.9168
2860.1562 | 122.1085 | -0.091553 | 121.9574 | 5.1215 | 5.6189 | 5.6655 | 5.6523 | 5.6855 | 5.717 | 5.5867 | 121.9412 | 121.9261 | 121.8742 | 121.76 | -0.066219 | -0.036295 | -0.033484 | -0.026063 | 5.213 | 5.7104 | 5.757 | 5.7439 | 5.777 | 5.8086 | 5.6783 | 121.987 | 121.9719 | 121.92 | 121.8058 | -0.020443 | 0.009481 | 0.012292 | 0.019713 | 122.0074 | 121.9747 | 121.9404 | 121.9077
2861.9219 | 122.0078 | -0.13733 | 121.9894 | 5.126 | 5.5914 | 5.6426 | 5.634 | 5.6672 | 5.7033 | 5.5593 | 121.9412 | 121.9261 | 121.8696 | 121.7554 | -0.075375 | -0.040873 | -0.038063 | -0.026063 | 5.2634 | 5.7288 | 5.7799 | 5.7713 | 5.8045 | 5.8406 | 5.6966 | 121.987 | 121.9719 | 121.9154 | 121.8012 | -0.029599 | 0.004903 | 0.007713 | 0.019713 | 122.0166 | 121.9792 | 121.945 | 121.9077
2863.625 | 122.1222 | -0.086975 | 121.9482 | 5.1031 | 5.564 | 5.6197 | 5.602 | 5.6397 | 5.6758 | 5.541 | 121.9412 | 121.9307 | 121.8742 | 121.76 | -0.075375 | -0.036295 | -0.038063 | -0.026063 | 5.1901 | 5.6509 | 5.7067 | 5.6889 | 5.7267 | 5.7628 | 5.6279 | 121.987 | 121.9765 | 121.92 | 121.8058 | -0.029599 | 0.009481 | 0.007713 | 0.019713 | 122.0166 | 121.9792 | 121.9496 | 121.9123
2865.3906 | 122.0169 | -0.13733 | 121.994 | 5.094 | 5.5411 | 5.5922 | 5.5791 | 5.6168 | 5.6483 | 5.5181 | 121.9366 | 121.9307 | 121.8788 | 121.7554 | -0.070797 | -0.040873 | -0.042641 | -0.026063 | 5.2313 | 5.6784 | 5.7295 | 5.7164 | 5.7541 | 5.7857 | 5.6554 | 121.9824 | 121.9765 | 121.9245 | 121.8012 | -0.025021 | 0.004903 | 0.003135 | 0.019713 | 122.0074 | 121.9792 | 121.9496 | 121.9214
2867.0938 | 122.1359 | -0.073242 | 121.9345 | 5.0574 | 5.4998 | 5.5464 | 5.5379 | 5.5756 | 5.598 | 5.4677 | 121.9412 | 121.9307 | 121.8696 | 121.7508 | -0.079953 | -0.036295 | -0.042641 | -0.026063 | 5.1306 | 5.5731 | 5.6197 | 5.6111 | 5.6488 | 5.6712 | 5.541 | 121.987 | 121.9765 | 121.9154 | 121.7966 | -0.034177 | 0.009481 | 0.003135 | 0.019713 | 122.0211 | 121.9838 | 121.9496 | 121.9123
2868.875 | 122.1176 | -0.10071 | 121.962 | 5.0299 | 5.4632 | 5.5052 | 5.4966 | 5.5344 | 5.5613 | 5.4357 | 121.9366 | 121.9353 | 121.8742 | 121.7508 | -0.070797 | -0.036295 | -0.042641 | -0.021484 | 5.1306 | 5.5639 | 5.6059 | 5.5974 | 5.6351 | 5.662 | 5.5364 | 121.9824 | 121.9811 | 121.92 | 121.7966 | -0.025021 | 0.009481 | 0.003135 | 0.024292 | 122.0074 | 121.9792 | 121.945 | 121.9168
2870.6406 | 122.0581 | -0.12817 | 122.0032 | 5.039 | 5.4586 | 5.5144 | 5.4921 | 5.5298 | 5.5613 | 5.4219 | 121.9412 | 121.9215 | 121.8696 | 121.76 | -0.075375 | -0.036295 | -0.04722 | -0.016906 | 5.1672 | 5.5868 | 5.6425 | 5.6202 | 5.658 | 5.6895 | 5.5501 | 121.987 | 121.9673 | 121.9154 | 121.8058 | -0.029599 | 0.009481 | -0.001444 | 0.02887 | 122.0166 | 121.9884 | 121.945 | 121.9168
2872.3281 | 122.0901 | -0.086975 | 121.9482 | 5.0161 | 5.4174 | 5.4686 | 5.4509 | 5.4795 | 5.5247 | 5.3853 | 121.9458 | 121.9261 | 121.8742 | 121.7508 | -0.079953 | -0.036295 | -0.051798 | -0.026063 | 5.1031 | 5.5044 | 5.5556 | 5.5378 | 5.5664 | 5.6117 | 5.4723 | 121.9915 | 121.9719 | 121.92 | 121.7966 | -0.034177 | 0.009481 | -0.006022 | 0.019713 | 122.0257 | 121.9976 | 121.9541 | 121.926
2874.0938 | 122.0169 | -0.11902 | 121.9894 | 4.9383 | 5.3213 | 5.3724 | 5.3501 | 5.3879 | 5.424 | 5.2892 | 121.932 | 121.9261 | 121.8742 | 121.76 | -0.070797 | -0.031717 | -0.042641 | -0.021484 | 5.0573 | 5.4403 | 5.4915 | 5.4692 | 5.5069 | 5.543 | 5.4082 | 121.9778 | 121.9719 | 121.92 | 121.8058 | -0.025021 | 0.014059 | 0.003135 | 0.024292 | 122.0028 | 121.9747 | 121.945 | 121.9168
2875.8438 | 122.0947 | -0.086975 | 121.9757 | 4.9429 | 5.3167 | 5.3587 | 5.341 | 5.3833 | 5.4102 | 5.2846 | 121.932 | 121.9307 | 121.8696 | 121.76 | -0.075375 | -0.036295 | -0.042641 | -0.016906 | 5.0299 | 5.4037 | 5.4457 | 5.428 | 5.4703 | 5.4972 | 5.3716 | 121.9778 | 121.9765 | 121.9154 | 121.8058 | -0.029599 | 0.009481 | 0.003135 | 0.02887 | 122.0074 | 121.9747 | 121.945 | 121.9123
2877.6094 | 122.0215 | -0.11444 | 121.9711 | 4.9292 | 5.2846 | 5.3358 | 5.3135 | 5.3559 | 5.3919 | 5.2571 | 121.9366 | 121.9353 | 121.8742 | 121.7508 | -0.070797 | -0.036295 | -0.042641 | -0.021484 | 5.0436 | 5.3991 | 5.4502 | 5.4279 | 5.4703 | 5.5064 | 5.3716 | 121.9824 | 121.9811 | 121.92 | 121.7966 | -0.025021 | 0.009481 | 0.003135 | 0.024292 | 122.0074 | 121.9792 | 121.945 | 121.9168
2879.2969 | 122.1176 | -0.09613 | 121.9574 | 4.9795 | 5.335 | 5.3999 | 5.3685 | 5.4154 | 5.4377 | 5.3029 | 121.9412 | 121.9353 | 121.8696 | 121.7554 | -0.079953 | -0.036295 | -0.042641 | -0.030641 | 5.0757 | 5.4311 | 5.496 | 5.4646 | 5.5115 | 5.5338 | 5.399 | 121.987 | 121.9811 | 121.9154 | 121.8012 | -0.034177 | 0.009481 | 0.003135 | 0.015135 | 122.0211 | 121.9838 | 121.9496 | 121.9123
2881.0625 | 122.0123 | -0.13275 | 121.9849 | 5.0207 | 5.3808 | 5.4274 | 5.4142 | 5.4474 | 5.4789 | 5.3533 | 121.9412 | 121.9307 | 121.8742 | 121.7691 | -0.066219 | -0.036295 | -0.038063 | -0.026063 | 5.1535 | 5.5135 | 5.5601 | 5.547 | 5.5802 | 5.6117 | 5.486 | 121.987 | 121.9765 | 121.92 | 121.8149 | -0.020443 | 0.009481 | 0.007713 | 0.019713 | 122.0074 | 121.9792 | 121.9404 | 121.9123
2882.8281 | 122.0306 | -0.13275 | 121.9528 | 5.0345 | 5.3762 | 5.4228 | 5.4005 | 5.4383 | 5.4743 | 5.3441 | 121.932 | 121.9353 | 121.8696 | 121.7508 | -0.075375 | -0.027139 | -0.038063 | -0.021484 | 5.1672 | 5.509 | 5.5556 | 5.5333 | 5.571 | 5.6071 | 5.4769 | 121.9778 | 121.9811 | 121.9154 | 121.7966 | -0.029599 | 0.018637 | 0.007713 | 0.024292 | 122.0074 | 121.9701 | 121.945 | 121.9077
2884.5312 | 121.9986 | -0.11902 | 121.9849 | 4.9978 | 5.3304 | 5.3816 | 5.3639 | 5.4016 | 5.4377 | 5.3029 | 121.9366 | 121.9261 | 121.8696 | 121.7646 | -0.070797 | -0.031717 | -0.042641 | -0.026063 | 5.1169 | 5.4495 | 5.5006 | 5.4829 | 5.5207 | 5.5567 | 5.4219 | 121.9824 | 121.9719 | 121.9154 | 121.8103 | -0.025021 | 0.014059 | 0.003135 | 0.019713 | 122.0074 | 121.9792 | 121.9404 | 121.9123
2886.2969 | 122.1176 | -0.082397 | 121.9437 | 5.0253 | 5.3487 | 5.3999 | 5.3822 | 5.4291 | 5.4606 | 5.3166 | 121.9366 | 121.9307 | 121.8742 | 121.76 | -0.070797 | -0.031717 | -0.038063 | -0.021484 | 5.1077 | 5.4311 | 5.4823 | 5.4646 | 5.5115 | 5.543 | 5.399 | 121.9824 | 121.9765 | 121.92 | 121.8058 | -0.025021 | 0.014059 | 0.007713 | 0.024292 | 122.0074 | 121.9747 | 121.945 | 121.9123
2888.0625 | 122.049 | -0.11444 | 121.9482 | 5.0665 | 5.3808 | 5.4411 | 5.4142 | 5.4474 | 5.4835 | 5.3441 | 121.9366 | 121.9307 | 121.865 | 121.76 | -0.070797 | -0.036295 | -0.042641 | -0.021484 | 5.181 | 5.4952 | 5.5556 | 5.5287 | 5.5619 | 5.5979 | 5.4585 | 121.9824 | 121.9765 | 121.9108 | 121.8058 | -0.025021 | 0.009481 | 0.003135 | 0.024292 | 122.0074 | 121.9792 | 121.9358 | 121.9077
2889.8281 | 122.0901 | -0.11444 | 121.9391 | 5.0299 | 5.3487 | 5.3908 | 5.373 | 5.4154 | 5.4469 | 5.3166 | 121.9366 | 121.9307 | 121.8696 | 121.7554 | -0.070797 | -0.036295 | -0.038063 | -0.030641 | 5.1443 | 5.4632 | 5.5052 | 5.4875 | 5.5298 | 5.5613 | 5.4311 | 121.9824 | 121.9765 | 121.9154 | 121.8012 | -0.025021 | 0.009481 | 0.007713 | 0.015135 | 122.0074 | 121.9747 | 121.9404 | 121.9077
2891.5469 | 122.1497 | -0.082397 | 121.9482 | 4.9841 | 5.2892 | 5.3267 | 5.3135 | 5.3513 | 5.3828 | 5.2434 | 121.932 | 121.9353 | 121.8696 | 121.7508 | -0.070797 | -0.031717 | -0.033484 | -0.021484 | 5.0665 | 5.3716 | 5.409 | 5.3959 | 5.4337 | 5.4652 | 5.3258 | 121.9778 | 121.9811 | 121.9154 | 121.7966 | -0.025021 | 0.014059 | 0.012292 | 0.024292 | 122.0028 | 121.9655 | 121.9404 | 121.9031
2893.3125 | 121.994 | -0.10529 | 121.9711 | 4.9566 | 5.248 | 5.2992 | 5.2769 | 5.3101 | 5.3416 | 5.2113 | 121.932 | 121.9353 | 121.8605 | 121.7554 | -0.079953 | -0.031717 | -0.038063 | -0.021484 | 5.0619 | 5.3533 | 5.4045 | 5.3822 | 5.4154 | 5.4469 | 5.3166 | 121.9778 | 121.9811 | 121.9062 | 121.8012 | -0.034177 | 0.014059 | 0.007713 | 0.024292 | 122.012 | 121.9701 | 121.9404 | 121.8985
2895.0625 | 122.1085 | -0.082397 | 121.9528 | 4.9429 | 5.2205 | 5.2671 | 5.254 | 5.2872 | 5.3233 | 5.1793 | 121.9275 | 121.9307 | 121.8742 | 121.7554 | -0.070797 | -0.040873 | -0.033484 | -0.026063 | 5.0253 | 5.3029 | 5.3495 | 5.3364 | 5.3696 | 5.4057 | 5.2617 | 121.9732 | 121.9765 | 121.92 | 121.8012 | -0.025021 | 0.004903 | 0.012292 | 0.019713 | 121.9982 | 121.9609 | 121.945 | 121.9077
2896.7656 | 122.1222 | -0.082397 | 121.9528 | 4.9154 | 5.1885 | 5.2305 | 5.2082 | 5.2551 | 5.2821 | 5.1518 | 121.932 | 121.9261 | 121.8742 | 121.7554 | -0.070797 | -0.040873 | -0.042641 | -0.021484 | 4.9978 | 5.2709 | 5.3129 | 5.2906 | 5.3375 | 5.3645 | 5.2342 | 121.9778 | 121.9719 | 121.92 | 121.8012 | -0.025021 | 0.004903 | 0.003135 | 0.024292 | 122.0028 | 121.9747 | 121.945 | 121.9168
2898.5312 | 122.1176 | -0.09613 | 121.9482 | 4.9017 | 5.1519 | 5.203 | 5.1899 | 5.2185 | 5.2592 | 5.1106 | 121.9366 | 121.9215 | 121.865 | 121.7554 | -0.075375 | -0.036295 | -0.033484 | -0.012328 | 4.9978 | 5.248 | 5.2992 | 5.286 | 5.3146 | 5.3553 | 5.2067 | 121.9824 | 121.9673 | 121.9108 | 121.8012 | -0.029599 | 0.009481 | 0.012292 | 0.033448 | 122.012 | 121.9701 | 121.9404 | 121.8985
2900.2969 | 122.1222 | -0.07782 | 121.9345 | 4.8513 | 5.1061 | 5.1527 | 5.1349 | 5.1727 | 5.2042 | 5.0648 | 121.9366 | 121.9261 | 121.8696 | 121.7554 | -0.070797 | -0.031717 | -0.033484 | -0.021484 | 4.9291 | 5.1839 | 5.2305 | 5.2128 | 5.2506 | 5.282 | 5.1427 | 121.9824 | 121.9719 | 121.9154 | 121.8012 | -0.025021 | 0.014059 | 0.012292 | 0.024292 | 122.0074 | 121.9701 | 121.9404 | 121.9031
2902.0625 | 122.1313 | -0.07782 | 121.9162 | 4.8147 | 5.0511 | 5.1069 | 5.0846 | 5.1178 | 5.1539 | 5.0145 | 121.9275 | 121.9307 | 121.8742 | 121.76 | -0.066219 | -0.036295 | -0.038063 | -0.021484 | 4.8925 | 5.1289 | 5.1847 | 5.1624 | 5.1956 | 5.2317 | 5.0923 | 121.9732 | 121.9765 | 121.92 | 121.8058 | -0.020443 | 0.009481 | 0.007713 | 0.024292 | 121.9937 | 121.9655 | 121.9404 | 121.9123
2903.8281 | 121.9986 | -0.11902 | 122.0169 | 4.8239 | 5.0557 | 5.1069 | 5.0846 | 5.1224 | 5.1539 | 5.0099 | 121.932 | 121.9307 | 121.8696 | 121.7463 | -0.066219 | -0.036295 | -0.038063 | -0.021484 | 4.9429 | 5.1747 | 5.2259 | 5.2036 | 5.2414 | 5.2729 | 5.1289 | 121.9778 | 121.9765 | 121.9154 | 121.792 | -0.020443 | 0.009481 | 0.007713 | 0.024292 | 121.9982 | 121.9701 | 121.9358 | 121.9077
2905.5156 | 122.1313 | -0.10529 | 121.9437 | 4.7964 | 5.0145 | 5.0794 | 5.048 | 5.0858 | 5.1172 | 4.9824 | 121.9366 | 121.9307 | 121.8696 | 121.7554 | -0.075375 | -0.031717 | -0.038063 | -0.021484 | 4.9017 | 5.1198 | 5.1847 | 5.1532 | 5.191 | 5.2225 | 5.0877 | 121.9824 | 121.9765 | 121.9154 | 121.8012 | -0.029599 | 0.014059 | 0.007713 | 0.024292 | 122.012 | 121.9747 | 121.945 | 121.9077
2907.2812 | 122.0306 | -0.1236 | 121.9711 | 4.8193 | 5.0328 | 5.0748 | 5.0571 | 5.0949 | 5.1218 | 4.9824 | 121.932 | 121.9261 | 121.8742 | 121.7508 | -0.075375 | -0.031717 | -0.04722 | -0.016906 | 4.9429 | 5.1564 | 5.1984 | 5.1807 | 5.2185 | 5.2454 | 5.106 | 121.9778 | 121.9719 | 121.92 | 121.7966 | -0.029599 | 0.014059 | -0.001444 | 0.02887 | 122.0074 | 121.9792 | 121.9496 | 121.9214
2909.0469 | 122.1405 | -0.068665 | 121.9391 | 4.8422 | 5.0557 | 5.0977 | 5.0892 | 5.1178 | 5.1584 | 5.0145 | 121.932 | 121.9307 | 121.8696 | 121.7417 | -0.070797 | -0.036295 | -0.042641 | -0.021484 | 4.9108 | 5.1244 | 5.1664 | 5.1578 | 5.1865 | 5.2271 | 5.0831 | 121.9778 | 121.9765 | 121.9154 | 121.7874 | -0.025021 | 0.009481 | 0.003135 | 0.024292 | 122.0028 | 121.9747 | 121.9404 | 121.9123
2910.75 | 122.0123 | -0.1236 | 121.9528 | 4.833 | 5.0328 | 5.0931 | 5.0663 | 5.1086 | 5.1401 | 5.0007 | 121.9366 | 121.9261 | 121.8696 | 121.76 | -0.070797 | -0.036295 | -0.042641 | -0.021484 | 4.9566 | 5.1564 | 5.2167 | 5.1899 | 5.2322 | 5.2637 | 5.1243 | 121.9824 | 121.9719 | 121.9154 | 121.8058 | -0.025021 | 0.009481 | 0.003135 | 0.024292 | 122.0074 | 121.9792 | 121.9404 | 121.9123
2912.5312 | 122.0444 | -0.13733 | 121.9757 | 4.7094 | 4.9046 | 4.9512 | 4.9381 | 4.9713 | 4.9982 | 4.868 | 121.9366 | 121.9261 | 121.8605 | 121.7554 | -0.075375 | -0.031717 | -0.042641 | -0.026063 | 4.8467 | 5.0419 | 5.0885 | 5.0754 | 5.1086 | 5.1355 | 5.0053 | 121.9824 | 121.9719 | 121.9062 | 121.8012 | -0.029599 | 0.014059 | 0.003135 | 0.019713 | 122.012 | 121.9792 | 121.9358 | 121.9031
2914.2969 | 122.0398 | -0.10529 | 121.9437 | 4.8055 | 4.9779 | 5.0336 | 5.0251 | 5.0583 | 5.0852 | 4.9504 | 121.9275 | 121.9261 | 121.8696 | 121.7508 | -0.075375 | -0.031717 | -0.042641 | -0.026063 | 4.9108 | 5.0831 | 5.1389 | 5.1303 | 5.1636 | 5.1905 | 5.0557 | 121.9732 | 121.9719 | 121.9154 | 121.7966 | -0.029599 | 0.014059 | 0.003135 | 0.019713 | 122.0028 | 121.9701 | 121.945 | 121.9123
2916.0156 | 121.994 | -0.11444 | 121.9849 | 4.8101 | 4.9916 | 5.0382 | 5.0251 | 5.0629 | 5.0943 | 4.9504 | 121.9366 | 121.9307 | 121.8605 | 121.7554 | -0.061641 | -0.036295 | -0.042641 | -0.026063 | 4.9246 | 5.106 | 5.1526 | 5.1395 | 5.1773 | 5.2088 | 5.0648 | 121.9824 | 121.9765 | 121.9062 | 121.8012 | -0.015865 | 0.009481 | 0.003135 | 0.019713 | 121.9982 | 121.9792 | 121.9221 | 121.9031
2917.7188 | 122.0123 | -0.11902 | 121.9894 | 4.8147 | 4.9824 | 5.0428 | 5.0251 | 5.0583 | 5.0898 | 4.9595 | 121.9366 | 121.9215 | 121.8696 | 121.7508 | -0.075375 | -0.036295 | -0.042641 | -0.026063 | 4.9337 | 5.1015 | 5.1618 | 5.1441 | 5.1773 | 5.2088 | 5.0786 | 121.9824 | 121.9673 | 121.9154 | 121.7966 | -0.029599 | 0.009481 | 0.003135 | 0.019713 | 122.012 | 121.9792 | 121.945 | 121.9123
2919.4219 | 122.1222 | -0.07782 | 121.9391 | 4.8055 | 4.9687 | 5.0199 | 4.9976 | 5.0446 | 5.0669 | 4.9366 | 121.9366 | 121.9215 | 121.865 | 121.7463 | -0.079953 | -0.027139 | -0.038063 | -0.026063 | 4.8834 | 5.0465 | 5.0977 | 5.0754 | 5.1224 | 5.1447 | 5.0145 | 121.9824 | 121.9673 | 121.9108 | 121.792 | -0.034177 | 0.018637 | 0.007713 | 0.019713 | 122.0166 | 121.9747 | 121.945 | 121.9031
2921.1875 | 122.0078 | -0.13733 | 121.9894 | 4.7781 | 4.9367 | 4.9787 | 4.9655 | 4.9988 | 5.0394 | 4.8954 | 121.932 | 121.9215 | 121.8696 | 121.7508 | -0.075375 | -0.031717 | -0.042641 | -0.026063 | 4.9154 | 5.074 | 5.116 | 5.1029 | 5.1361 | 5.1767 | 5.0328 | 121.9778 | 121.9673 | 121.9154 | 121.7966 | -0.029599 | 0.014059 | 0.003135 | 0.019713 | 122.0074 | 121.9747 | 121.945 | 121.9123
2922.9531 | 122.1085 | -0.07782 | 121.9299 | 4.7872 | 4.9229 | 4.9787 | 4.961 | 5.0034 | 5.0257 | 4.8909 | 121.9366 | 121.9307 | 121.865 | 121.7463 | -0.079953 | -0.027139 | -0.038063 | -0.026063 | 4.865 | 5.0007 | 5.0565 | 5.0388 | 5.0812 | 5.1035 | 4.9687 | 121.9824 | 121.9765 | 121.9108 | 121.792 | -0.034177 | 0.018637 | 0.007713 | 0.019713 | 122.0166 | 121.9747 | 121.945 | 121.9031
2924.7188 | 122.0856 | -0.09613 | 121.9666 | 4.746 | 4.8954 | 4.9466 | 4.9243 | 4.9621 | 4.9936 | 4.8497 | 121.932 | 121.9261 | 121.865 | 121.7463 | -0.070797 | -0.027139 | -0.038063 | -0.035219 | 4.8422 | 4.9916 | 5.0428 | 5.0205 | 5.0583 | 5.0897 | 4.9458 | 121.9778 | 121.9719 | 121.9108 | 121.792 | -0.025021 | 0.018637 | 0.007713 | 0.010557 | 122.0028 | 121.9701 | 121.9358 | 121.9031
2926.5 | 122.1542 | -0.064087 | 121.9299 | 4.7414 | 4.8771 | 4.9283 | 4.9106 | 4.9484 | 4.9707 | 4.8359 | 121.9366 | 121.9215 | 121.865 | 121.7463 | -0.070797 | -0.031717 | -0.038063 | -0.016906 | 4.8055 | 4.9412 | 4.9924 | 4.9747 | 5.0125 | 5.0348 | 4.9 | 121.9824 | 121.9673 | 121.9108 | 121.792 | -0.025021 | 0.014059 | 0.007713 | 0.02887 | 122.0074 | 121.9747 | 121.9358 | 121.9031
2928.2656 | 122.0123 | -0.11902 | 121.9803 | 4.7414 | 4.8542 | 4.9192 | 4.9014 | 4.9347 | 4.9753 | 4.8313 | 121.932 | 121.917 | 121.865 | 121.76 | -0.075375 | -0.027139 | -0.033484 | -0.021484 | 4.8605 | 4.9733 | 5.0382 | 5.0205 | 5.0537 | 5.0943 | 4.9504 | 121.9778 | 121.9627 | 121.9108 | 121.8058 | -0.029599 | 0.018637 | 0.012292 | 0.024292 | 122.0074 | 121.9655 | 121.9404 | 121.8985
2930.0312 | 122.0444 | -0.10529 | 121.9757 | 4.7186 | 4.8451 | 4.8917 | 4.8786 | 4.9118 | 4.9478 | 4.8039 | 121.9366 | 121.9215 | 121.8696 | 121.7554 | -0.070797 | -0.036295 | -0.042641 | -0.021484 | 4.8238 | 4.9504 | 4.997 | 4.9838 | 5.0171 | 5.0531 | 4.9092 | 121.9824 | 121.9673 | 121.9154 | 121.8012 | -0.025021 | 0.009481 | 0.003135 | 0.024292 | 122.0074 | 121.9792 | 121.9404 | 121.9123
2931.75 | 122.0032 | -0.1236 | 121.9711 | 4.7094 | 4.8313 | 4.8779 | 4.8602 | 4.9026 | 4.9295 | 4.7901 | 121.9275 | 121.9215 | 121.8696 | 121.7508 | -0.075375 | -0.031717 | -0.038063 | -0.021484 | 4.833 | 4.9549 | 5.0015 | 4.9838 | 5.0262 | 5.0531 | 4.9137 | 121.9732 | 121.9673 | 121.9154 | 121.7966 | -0.029599 | 0.014059 | 0.007713 | 0.024292 | 122.0028 | 121.9655 | 121.945 | 121.9077
2933.5156 | 122.1451 | -0.068665 | 121.9208 | 4.6636 | 4.7672 | 4.8093 | 4.7961 | 4.834 | 4.8608 | 4.7352 | 121.932 | 121.9215 | 121.8605 | 121.7508 | -0.075375 | -0.036295 | -0.038063 | -0.016906 | 4.7323 | 4.8359 | 4.8779 | 4.8648 | 4.9026 | 4.9295 | 4.8039 | 121.9778 | 121.9673 | 121.9062 | 121.7966 | -0.029599 | 0.009481 | 0.007713 | 0.02887 | 122.0074 | 121.9701 | 121.9358 | 121.8985
2935.2188 | 122.1451 | -0.073242 | 121.9391 | 4.6545 | 4.7489 | 4.7955 | 4.787 | 4.8248 | 4.8517 | 4.7123 | 121.9275 | 121.9261 | 121.8605 | 121.7463 | -0.075375 | -0.036295 | -0.038063 | -0.026063 | 4.7277 | 4.8222 | 4.8688 | 4.8602 | 4.8981 | 4.9249 | 4.7856 | 121.9732 | 121.9719 | 121.9062 | 121.792 | -0.029599 | 0.009481 | 0.007713 | 0.019713 | 122.0028 | 121.9655 | 121.9358 | 121.8985
2936.9844 | 122.0032 | -0.13275 | 121.994 | 4.6087 | 4.6986 | 4.7406 | 4.7275 | 4.7699 | 4.7922 | 4.6574 | 121.9275 | 121.917 | 121.8605 | 121.7463 | -0.070797 | -0.036295 | -0.042641 | -0.021484 | 4.7414 | 4.8313 | 4.8733 | 4.8602 | 4.9026 | 4.9249 | 4.7901 | 121.9732 | 121.9627 | 121.9062 | 121.792 | -0.025021 | 0.009481 | 0.003135 | 0.024292 | 121.9982 | 121.9701 | 121.9312 | 121.9031
2938.75 | 122.0718 | -0.091553 | 121.9803 | 4.6361 | 4.7169 | 4.7635 | 4.7504 | 4.7882 | 4.8196 | 4.6848 | 121.9275 | 121.917 | 121.865 | 121.7554 | -0.070797 | -0.031717 | -0.038063 | -0.021484 | 4.7277 | 4.8084 | 4.855 | 4.8419 | 4.8797 | 4.9112 | 4.7764 | 121.9732 | 121.9627 | 121.9108 | 121.8012 | -0.025021 | 0.014059 | 0.007713 | 0.024292 | 121.9982 | 121.9655 | 121.9358 | 121.9031
2940.5156 | 122.0215 | -0.11902 | 121.9757 | 4.6361 | 4.7031 | 4.7589 | 4.7366 | 4.7699 | 4.8013 | 4.6711 | 121.932 | 121.9215 | 121.8605 | 121.7508 | -0.070797 | -0.036295 | -0.038063 | -0.026063 | 4.7552 | 4.8222 | 4.8779 | 4.8556 | 4.8889 | 4.9203 | 4.7901 | 121.9778 | 121.9673 | 121.9062 | 121.7966 | -0.025021 | 0.009481 | 0.007713 | 0.019713 | 122.0028 | 121.9701 | 121.9312 | 121.8985
2942.2188 | 122.1039 | -0.09613 | 121.9528 | 4.6361 | 4.7031 | 4.7452 | 4.7366 | 4.779 | 4.8151 | 4.6665 | 121.932 | 121.9124 | 121.8605 | 121.7463 | -0.070797 | -0.036295 | -0.038063 | -0.026063 | 4.7323 | 4.7993 | 4.8413 | 4.8327 | 4.8752 | 4.9112 | 4.7627 | 121.9778 | 121.9582 | 121.9062 | 121.792 | -0.025021 | 0.009481 | 0.007713 | 0.019713 | 122.0028 | 121.9701 | 121.9312 | 121.8985
2943.9844 | 122.0581 | -0.11902 | 121.9391 | 4.6132 | 4.6802 | 4.7314 | 4.7091 | 4.7561 | 4.783 | 4.6436 | 121.932 | 121.9215 | 121.865 | 121.7417 | -0.079953 | -0.027139 | -0.042641 | -0.016906 | 4.7323 | 4.7993 | 4.8505 | 4.8282 | 4.8752 | 4.902 | 4.7627 | 121.9778 | 121.9673 | 121.9108 | 121.7874 | -0.034177 | 0.018637 | 0.003135 | 0.02887 | 122.012 | 121.9747 | 121.945 | 121.9077
2945.75 | 122.0261 | -0.12817 | 121.962 | 4.6132 | 4.6757 | 4.7085 | 4.7046 | 4.7424 | 4.7693 | 4.6253 | 121.9366 | 121.917 | 121.865 | 121.7371 | -0.070797 | -0.036295 | -0.038063 | -0.026063 | 4.7414 | 4.8038 | 4.8367 | 4.8327 | 4.8706 | 4.8974 | 4.7535 | 121.9824 | 121.9627 | 121.9108 | 121.7829 | -0.025021 | 0.009481 | 0.007713 | 0.019713 | 122.0074 | 121.9747 | 121.9358 | 121.9031
2947.5156 | 122.049 | -0.11902 | 121.962 | 4.6087 | 4.6619 | 4.7177 | 4.6908 | 4.7287 | 4.7647 | 4.6299 | 121.932 | 121.9215 | 121.8559 | 121.7508 | -0.075375 | -0.036295 | -0.042641 | -0.021484 | 4.7277 | 4.7809 | 4.8367 | 4.8099 | 4.8477 | 4.8837 | 4.7489 | 121.9778 | 121.9673 | 121.9017 | 121.7966 | -0.029599 | 0.009481 | 0.003135 | 0.024292 | 122.0074 | 121.9747 | 121.9312 | 121.8985
2949.2656 | 121.9894 | -0.13733 | 121.9711 | 4.5858 | 4.6207 | 4.6765 | 4.6588 | 4.6966 | 4.7235 | 4.5887 | 121.932 | 121.9261 | 121.8605 | 121.7417 | -0.070797 | -0.031717 | -0.04722 | -0.021484 | 4.7231 | 4.758 | 4.8138 | 4.7961 | 4.834 | 4.8608 | 4.726 | 121.9778 | 121.9719 | 121.9062 | 121.7874 | -0.025021 | 0.014059 | -0.001444 | 0.024292 | 122.0028 | 121.9792 | 121.9312 | 121.9077
2950.9688 | 122.0581 | -0.10529 | 121.9482 | 4.5537 | 4.5978 | 4.6399 | 4.6222 | 4.6692 | 4.696 | 4.5567 | 121.9275 | 121.917 | 121.865 | 121.76 | -0.075375 | -0.031717 | -0.042641 | -0.021484 | 4.659 | 4.7031 | 4.7451 | 4.7274 | 4.7744 | 4.8013 | 4.6619 | 121.9732 | 121.9627 | 121.9108 | 121.8058 | -0.029599 | 0.014059 | 0.003135 | 0.024292 | 122.0028 | 121.9701 | 121.9404 | 121.9077
2952.7344 | 122.0352 | -0.10529 | 121.9528 | 4.5125 | 4.552 | 4.5987 | 4.5809 | 4.6142 | 4.6502 | 4.5155 | 121.9275 | 121.9215 | 121.8513 | 121.7508 | -0.070797 | -0.036295 | -0.042641 | -0.026063 | 4.6178 | 4.6573 | 4.7039 | 4.6862 | 4.7195 | 4.7555 | 4.6207 | 121.9732 | 121.9673 | 121.8971 | 121.7966 | -0.025021 | 0.009481 | 0.003135 | 0.019713 | 121.9982 | 121.9701 | 121.9221 | 121.8939
2954.4219 | 122.1451 | -0.082397 | 121.9528 | 4.5034 | 4.5154 | 4.5712 | 4.5581 | 4.5913 | 4.6319 | 4.4834 | 121.9229 | 121.9261 | 121.8605 | 121.7463 | -0.070797 | -0.031717 | -0.042641 | -0.030641 | 4.5858 | 4.5978 | 4.6536 | 4.6405 | 4.6737 | 4.7143 | 4.5658 | 121.9686 | 121.9719 | 121.9062 | 121.792 | -0.025021 | 0.014059 | 0.003135 | 0.015135 | 121.9937 | 121.9655 | 121.9312 | 121.9031
2956.1875 | 122.1313 | -0.068665 | 121.9528 | 4.453 | 4.4605 | 4.5117 | 4.494 | 4.5364 | 4.5587 | 4.4285 | 121.9229 | 121.917 | 121.8559 | 121.7417 | -0.075375 | -0.036295 | -0.038063 | -0.016906 | 4.5217 | 4.5291 | 4.5803 | 4.5626 | 4.6051 | 4.6273 | 4.4971 | 121.9686 | 121.9627 | 121.9017 | 121.7874 | -0.029599 | 0.009481 | 0.007713 | 0.02887 | 121.9982 | 121.9609 | 121.9312 | 121.8939
2957.9531 | 122.0169 | -0.13275 | 121.9711 | 4.4347 | 4.4513 | 4.4979 | 4.4894 | 4.5135 | 4.5495 | 4.4102 | 121.9275 | 121.9215 | 121.865 | 121.7417 | -0.070797 | -0.036295 | -0.038063 | -0.016906 | 4.5674 | 4.584 | 4.6307 | 4.6221 | 4.6463 | 4.6823 | 4.5429 | 121.9732 | 121.9673 | 121.9108 | 121.7874 | -0.025021 | 0.009481 | 0.007713 | 0.02887 | 121.9982 | 121.9655 | 121.9358 | 121.9031
2959.7031 | 122.0901 | -0.11444 | 121.9437 | 4.4164 | 4.4147 | 4.475 | 4.4436 | 4.4769 | 4.522 | 4.3781 | 121.932 | 121.9215 | 121.865 | 121.7371 | -0.070797 | -0.036295 | -0.038063 | -0.021484 | 4.5308 | 4.5291 | 4.5895 | 4.558 | 4.5913 | 4.6365 | 4.4926 | 121.9778 | 121.9673 | 121.9108 | 121.7829 | -0.025021 | 0.009481 | 0.007713 | 0.024292 | 122.0028 | 121.9701 | 121.9358 | 121.9031
2961.4062 | 122.0627 | -0.10529 | 121.9711 | 4.3843 | 4.378 | 4.4292 | 4.4115 | 4.4494 | 4.4808 | 4.3369 | 121.9275 | 121.9215 | 121.865 | 121.7463 | -0.070797 | -0.031717 | -0.033484 | -0.021484 | 4.4896 | 4.4833 | 4.5345 | 4.5168 | 4.5547 | 4.5861 | 4.4422 | 121.9732 | 121.9673 | 121.9108 | 121.792 | -0.025021 | 0.014059 | 0.012292 | 0.024292 | 121.9982 | 121.9609 | 121.9358 | 121.8985
2963.1719 | 122.0535 | -0.10529 | 121.9162 | 4.334 | 4.3139 | 4.3651 | 4.3474 | 4.3899 | 4.4213 | 4.2774 | 121.9229 | 121.9215 | 121.8559 | 121.7417 | -0.061641 | -0.036295 | -0.038063 | -0.016906 | 4.4393 | 4.4192 | 4.4704 | 4.4527 | 4.4952 | 4.5266 | 4.3827 | 121.9686 | 121.9673 | 121.9017 | 121.7874 | -0.015865 | 0.009481 | 0.007713 | 0.02887 | 121.9845 | 121.9609 | 121.9175 | 121.8939
2964.875 | 122.0306 | -0.12817 | 121.9666 | 4.2973 | 4.2773 | 4.3239 | 4.3062 | 4.3441 | 4.3801 | 4.2362 | 121.9275 | 121.9215 | 121.865 | 121.7371 | -0.070797 | -0.022561 | -0.038063 | -0.021484 | 4.4255 | 4.4055 | 4.4521 | 4.4344 | 4.4723 | 4.5083 | 4.3644 | 121.9732 | 121.9673 | 121.9108 | 121.7829 | -0.025021 | 0.023215 | 0.007713 | 0.024292 | 121.9982 | 121.9655 | 121.9358 | 121.9031
2966.6406 | 122.0856 | -0.10071 | 121.9574 | 4.2653 | 4.2269 | 4.2782 | 4.265 | 4.2983 | 4.3343 | 4.1904 | 121.9229 | 121.9215 | 121.8605 | 121.7417 | -0.070797 | -0.031717 | -0.042641 | -0.026063 | 4.366 | 4.3276 | 4.3789 | 4.3657 | 4.3991 | 4.435 | 4.2911 | 121.9686 | 121.9673 | 121.9062 | 121.7874 | -0.025021 | 0.014059 | 0.003135 | 0.019713 | 121.9937 | 121.9655 | 121.9312 | 121.9031
2968.3438 | 122.0169 | -0.13275 | 121.9849 | 4.2195 | 4.1857 | 4.2369 | 4.2101 | 4.2617 | 4.2931 | 4.1492 | 121.9229 | 121.9215 | 121.8513 | 121.7417 | -0.066219 | -0.031717 | -0.033484 | -0.026063 | 4.3523 | 4.3185 | 4.3697 | 4.3428 | 4.3945 | 4.4259 | 4.282 | 121.9686 | 121.9673 | 121.8971 | 121.7874 | -0.020443 | 0.014059 | 0.012292 | 0.019713 | 121.9891 | 121.9564 | 121.9175 | 121.8848
2970.0938 | 122.0261 | -0.13733 | 121.9666 | 4.2332 | 4.1857 | 4.2324 | 4.2192 | 4.2526 | 4.2931 | 4.1446 | 121.9229 | 121.917 | 121.8605 | 121.7417 | -0.070797 | -0.027139 | -0.038063 | -0.021484 | 4.3706 | 4.3231 | 4.3697 | 4.3566 | 4.3899 | 4.4305 | 4.282 | 121.9686 | 121.9627 | 121.9062 | 121.7874 | -0.025021 | 0.018637 | 0.007713 | 0.024292 | 121.9937 | 121.9609 | 121.9312 | 121.8985
2971.8594 | 122.0901 | -0.07782 | 121.9482 | 4.192 | 4.1491 | 4.2003 | 4.1872 | 4.2251 | 4.2473 | 4.1126 | 121.9275 | 121.9261 | 121.8513 | 121.7325 | -0.075375 | -0.031717 | -0.038063 | -0.021484 | 4.2699 | 4.2269 | 4.2781 | 4.265 | 4.3029 | 4.3252 | 4.1904 | 121.9732 | 121.9719 | 121.8971 | 121.7783 | -0.029599 | 0.014059 | 0.007713 | 0.024292 | 122.0028 | 121.9655 | 121.9267 | 121.8894
2973.5938 | 122.1222 | -0.082397 | 121.9299 | 4.1875 | 4.1308 | 4.1774 | 4.1643 | 4.2068 | 4.229 | 4.0943 | 121.9275 | 121.917 | 121.8559 | 121.7325 | -0.075375 | -0.036295 | -0.042641 | -0.021484 | 4.2699 | 4.2132 | 4.2598 | 4.2467 | 4.2892 | 4.3114 | 4.1767 | 121.9732 | 121.9627 | 121.9017 | 121.7783 | -0.029599 | 0.009481 | 0.003135 | 0.024292 | 122.0028 | 121.9701 | 121.9312 | 121.8985
2975.3281 | 122.0261 | -0.13275 | 121.9574 | 4.1691 | 4.117 | 4.1591 | 4.1414 | 4.1839 | 4.2199 | 4.076 | 121.9275 | 121.9215 | 121.8513 | 121.7371 | -0.066219 | -0.031717 | -0.033484 | -0.021484 | 4.3019 | 4.2498 | 4.2919 | 4.2742 | 4.3166 | 4.3526 | 4.2087 | 121.9732 | 121.9673 | 121.8971 | 121.7829 | -0.020443 | 0.014059 | 0.012292 | 0.024292 | 121.9937 | 121.9609 | 121.9175 | 121.8848
2977.0938 | 122.0901 | -0.10071 | 121.9025 | 4.1554 | 4.0942 | 4.1271 | 4.1094 | 4.1473 | 4.1787 | 4.0439 | 121.932 | 121.917 | 121.8513 | 121.7325 | -0.066219 | -0.036295 | -0.033484 | -0.016906 | 4.2561 | 4.1949 | 4.2278 | 4.2101 | 4.248 | 4.2794 | 4.1446 | 121.9778 | 121.9627 | 121.8971 | 121.7783 | -0.020443 | 0.009481 | 0.012292 | 0.02887 | 121.9982 | 121.9655 | 121.9175 | 121.8848
2978.8594 | 122.0398 | -0.10986 | 121.9666 | 4.1417 | 4.0713 | 4.1179 | 4.0911 | 4.1335 | 4.1695 | 4.0302 | 121.9229 | 121.9032 | 121.8467 | 121.7417 | -0.070797 | -0.036295 | -0.038063 | -0.016906 | 4.2515 | 4.1811 | 4.2278 | 4.2009 | 4.2434 | 4.2794 | 4.14 | 121.9686 | 121.949 | 121.8925 | 121.7874 | -0.025021 | 0.009481 | 0.007713 | 0.02887 | 121.9937 | 121.9609 | 121.9175 | 121.8848
2980.6094 | 122.0215 | -0.12817 | 121.9666 | 4.1234 | 4.0438 | 4.0858 | 4.0682 | 4.1106 | 4.1466 | 4.0027 | 121.9275 | 121.9124 | 121.865 | 121.7417 | -0.070797 | -0.027139 | -0.033484 | -0.016906 | 4.2515 | 4.172 | 4.214 | 4.1963 | 4.2388 | 4.2748 | 4.1309 | 121.9732 | 121.9582 | 121.9108 | 121.7874 | -0.025021 | 0.018637 | 0.012292 | 0.02887 | 121.9982 | 121.9609 | 121.9358 | 121.8985
2982.375 | 122.0032 | -0.1236 | 121.9894 | 4.105 | 4.03 | 4.0675 | 4.0544 | 4.0969 | 4.1283 | 3.9798 | 121.9229 | 121.9124 | 121.8605 | 121.7371 | -0.070797 | -0.031717 | -0.033484 | -0.021484 | 4.2286 | 4.1536 | 4.1911 | 4.178 | 4.2205 | 4.2519 | 4.1034 | 121.9686 | 121.9582 | 121.9062 | 121.7829 | -0.025021 | 0.014059 | 0.012292 | 0.024292 | 121.9937 | 121.9564 | 121.9312 | 121.8939
2984.0781 | 122.1497 | -0.07782 | 121.9116 | 4.0501 | 3.9614 | 4.0034 | 3.9812 | 4.0237 | 4.055 | 3.9111 | 121.9137 | 121.9078 | 121.8559 | 121.7463 | -0.061641 | -0.031717 | -0.038063 | -0.016906 | 4.1279 | 4.0392 | 4.0813 | 4.059 | 4.1015 | 4.1329 | 3.989 | 121.9595 | 121.9536 | 121.9017 | 121.792 | -0.015865 | 0.014059 | 0.007713 | 0.02887 | 121.9754 | 121.9518 | 121.9175 | 121.8939
2985.8438 | 122.1176 | -0.086975 | 121.9254 | 4.0135 | 3.911 | 3.9622 | 3.94 | 3.987 | 4.023 | 3.8699 | 121.9229 | 121.9124 | 121.8421 | 121.7371 | -0.066219 | -0.027139 | -0.04722 | -0.021484 | 4.1005 | 3.998 | 4.0492 | 4.0269 | 4.074 | 4.11 | 3.9569 | 121.9686 | 121.9582 | 121.8879 | 121.7829 | -0.020443 | 0.018637 | -0.001444 | 0.024292 | 121.9891 | 121.9701 | 121.9084 | 121.8894
2987.6094 | 122.0581 | -0.13275 | 121.9482 | 3.9723 | 3.8744 | 3.9073 | 3.8988 | 3.9458 | 3.9635 | 3.8379 | 121.9183 | 121.9078 | 121.8513 | 121.7417 | -0.075375 | -0.027139 | -0.033484 | -0.021484 | 4.105 | 4.0071 | 4.04 | 4.0315 | 4.0786 | 4.0962 | 3.9706 | 121.9641 | 121.9536 | 121.8971 | 121.7874 | -0.029599 | 0.018637 | 0.012292 | 0.024292 | 121.9937 | 121.9518 | 121.9267 | 121.8848
2989.3594 | 121.9986 | -0.13733 | 121.9757 | 3.9585 | 3.8515 | 3.889 | 3.8759 | 3.9184 | 3.9497 | 3.8104 | 121.9137 | 121.9078 | 121.8559 | 121.7417 | -0.075375 | -0.027139 | -0.033484 | -0.012328 | 4.0959 | 3.9888 | 4.0263 | 4.0132 | 4.0557 | 4.0871 | 3.9477 | 121.9595 | 121.9536 | 121.9017 | 121.7874 | -0.029599 | 0.018637 | 0.012292 | 0.033448 | 121.9891 | 121.9472 | 121.9312 | 121.8894
2991.0625 | 122.0673 | -0.10071 | 121.9345 | 3.9311 | 3.8148 | 3.8707 | 3.8484 | 3.8909 | 3.9131 | 3.7784 | 121.9137 | 121.9032 | 121.8467 | 121.7417 | -0.075375 | -0.031717 | -0.042641 | -0.016906 | 4.0318 | 3.9156 | 3.9714 | 3.9491 | 3.9916 | 4.0138 | 3.8791 | 121.9595 | 121.949 | 121.8925 | 121.7874 | -0.029599 | 0.014059 | 0.003135 | 0.02887 | 121.9891 | 121.9564 | 121.9221 | 121.8894
2992.8438 | 122.113 | -0.10986 | 121.9208 | 3.9173 | 3.7919 | 3.8432 | 3.8118 | 3.8634 | 3.8811 | 3.7601 | 121.9229 | 121.9124 | 121.8513 | 121.7279 | -0.066219 | -0.022561 | -0.033484 | -0.021484 | 4.0272 | 3.9018 | 3.953 | 3.9216 | 3.9733 | 3.9909 | 3.8699 | 121.9686 | 121.9582 | 121.8971 | 121.7737 | -0.020443 | 0.023215 | 0.012292 | 0.024292 | 121.9891 | 121.9564 | 121.9175 | 121.8848
2994.5469 | 122.0856 | -0.10071 | 121.9391 | 3.8944 | 3.7691 | 3.8157 | 3.8026 | 3.8451 | 3.8719 | 3.7326 | 121.9183 | 121.9124 | 121.8467 | 121.7371 | -0.066219 | -0.027139 | -0.042641 | -0.021484 | 3.9952 | 3.8698 | 3.9164 | 3.9033 | 3.9458 | 3.9726 | 3.8333 | 121.9641 | 121.9582 | 121.8925 | 121.7829 | -0.020443 | 0.018637 | 0.003135 | 0.024292 | 121.9845 | 121.9609 | 121.9129 | 121.8894
2996.3125 | 122.0123 | -0.13733 | 121.9666 | 3.8212 | 3.6866 | 3.7287 | 3.711 | 3.7536 | 3.7849 | 3.6456 | 121.9183 | 121.9124 | 121.8421 | 121.7325 | -0.070797 | -0.031717 | -0.033484 | -0.012328 | 3.9585 | 3.824 | 3.866 | 3.8484 | 3.8909 | 3.9222 | 3.7829 | 121.9641 | 121.9582 | 121.8879 | 121.7783 | -0.025021 | 0.014059 | 0.012292 | 0.033448 | 121.9891 | 121.9518 | 121.9129 | 121.8756
2998.0781 | 122.0169 | -0.13733 | 121.9666 | 3.7937 | 3.65 | 3.6967 | 3.6744 | 3.7261 | 3.7574 | 3.6044 | 121.9137 | 121.9078 | 121.8421 | 121.7325 | -0.066219 | -0.031717 | -0.038063 | -0.030641 | 3.931 | 3.7873 | 3.834 | 3.8117 | 3.8634 | 3.8948 | 3.7417 | 121.9595 | 121.9536 | 121.8879 | 121.7783 | -0.020443 | 0.014059 | 0.007713 | 0.015135 | 121.9799 | 121.9518 | 121.9084 | 121.8802
2999.8594 | 122.0856 | -0.10529 | 121.9208 | 3.7708 | 3.6225 | 3.6646 | 3.6515 | 3.6849 | 3.7208 | 3.5769 | 121.9091 | 121.8941 | 121.8421 | 121.7325 | -0.066219 | -0.022561 | -0.038063 | -0.016906 | 3.8761 | 3.7278 | 3.7699 | 3.7568 | 3.7902 | 3.8261 | 3.6822 | 121.9549 | 121.9398 | 121.8879 | 121.7783 | -0.020443 | 0.023215 | 0.007713 | 0.02887 | 121.9754 | 121.9472 | 121.9084 | 121.8802
3001.5625 | 122.1039 | -0.09613 | 121.9299 | 3.7479 | 3.5996 | 3.6509 | 3.624 | 3.662 | 3.7025 | 3.5632 | 121.9183 | 121.8986 | 121.8421 | 121.7325 | -0.061641 | -0.027139 | -0.033484 | -0.012328 | 3.8441 | 3.6958 | 3.747 | 3.7202 | 3.7581 | 3.7986 | 3.6593 | 121.9641 | 121.9444 | 121.8879 | 121.7783 | -0.015865 | 0.018637 | 0.012292 | 0.033448 | 121.9799 | 121.9518 | 121.9038 | 121.8756
3003.3281 | 122.1085 | -0.09613 | 121.9254 | 3.7159 | 3.5539 | 3.6005 | 3.5874 | 3.6254 | 3.6567 | 3.522 | 121.9091 | 121.8986 | 121.8421 | 121.7279 | -0.061641 | -0.022561 | -0.033484 | -0.016906 | 3.812 | 3.65 | 3.6966 | 3.6835 | 3.7215 | 3.7529 | 3.6181 | 121.9549 | 121.9444 | 121.8879 | 121.7737 | -0.015865 | 0.023215 | 0.012292 | 0.02887 | 121.9708 | 121.9426 | 121.9038 | 121.8756
3005.0312 | 122.1497 | -0.091553 | 121.9208 | 3.6884 | 3.5355 | 3.5868 | 3.5554 | 3.5979 | 3.6384 | 3.4945 | 121.9137 | 121.8986 | 121.8376 | 121.7188 | -0.066219 | -0.027139 | -0.028906 | -0.016906 | 3.78 | 3.6271 | 3.6783 | 3.6469 | 3.6895 | 3.73 | 3.5861 | 121.9595 | 121.9444 | 121.8833 | 121.7646 | -0.020443 | 0.018637 | 0.01687 | 0.02887 | 121.9799 | 121.9426 | 121.9038 | 121.8665
3006.7969 | 122.0764 | -0.091553 | 121.9254 | 3.6426 | 3.4852 | 3.5364 | 3.5096 | 3.5521 | 3.5835 | 3.4442 | 121.9091 | 121.8941 | 121.8376 | 121.7188 | -0.070797 | -0.017983 | -0.033484 | -0.016906 | 3.7342 | 3.5767 | 3.628 | 3.6011 | 3.6437 | 3.675 | 3.5357 | 121.9549 | 121.9398 | 121.8833 | 121.7646 | -0.025021 | 0.027793 | 0.012292 | 0.02887 | 121.9799 | 121.9426 | 121.9084 | 121.871
3008.5625 | 122.0947 | -0.10071 | 121.8842 | 3.6106 | 3.4394 | 3.4815 | 3.4546 | 3.5018 | 3.5331 | 3.3984 | 121.9091 | 121.8941 | 121.8238 | 121.7142 | -0.061641 | -0.013405 | -0.028906 | -0.012328 | 3.7113 | 3.5401 | 3.5822 | 3.5553 | 3.6025 | 3.6338 | 3.4991 | 121.9549 | 121.9398 | 121.8696 | 121.76 | -0.015865 | 0.032371 | 0.01687 | 0.033448 | 121.9708 | 121.938 | 121.8855 | 121.8527
3010.3125 | 122.0444 | -0.11444 | 121.9345 | 3.5556 | 3.389 | 3.4265 | 3.4043 | 3.4468 | 3.4873 | 3.3434 | 121.9046 | 121.9032 | 121.8376 | 121.7234 | -0.070797 | -0.017983 | -0.028906 | -0.012328 | 3.6701 | 3.5035 | 3.541 | 3.5187 | 3.5613 | 3.6018 | 3.4579 | 121.9503 | 121.949 | 121.8833 | 121.7691 | -0.025021 | 0.027793 | 0.01687 | 0.033448 | 121.9754 | 121.9335 | 121.9084 | 121.8665
3012.0156 | 122.0901 | -0.10529 | 121.8979 | 3.5236 | 3.3524 | 3.3945 | 3.3768 | 3.4194 | 3.4507 | 3.3114 | 121.9 | 121.8849 | 121.833 | 121.7142 | -0.066219 | -0.017983 | -0.028906 | -0.00775 | 3.6289 | 3.4577 | 3.4998 | 3.4821 | 3.5247 | 3.556 | 3.4167 | 121.9458 | 121.9307 | 121.8788 | 121.76 | -0.020443 | 0.027793 | 0.01687 | 0.038026 | 121.9662 | 121.9289 | 121.8992 | 121.8619
3013.7812 | 122.1268 | -0.10986 | 121.907 | 3.4687 | 3.2837 | 3.3258 | 3.3035 | 3.3461 | 3.382 | 3.2336 | 121.8908 | 121.8941 | 121.8192 | 121.705 | -0.057062 | -0.008827 | -0.028906 | -0.00775 | 3.5785 | 3.3936 | 3.4357 | 3.4134 | 3.456 | 3.4919 | 3.3434 | 121.9366 | 121.9398 | 121.865 | 121.7508 | -0.011286 | 0.036949 | 0.01687 | 0.038026 | 121.9479 | 121.9197 | 121.8763 | 121.8482
3015.4688 | 122.0261 | -0.15106 | 121.8933 | 3.4732 | 3.2929 | 3.335 | 3.3127 | 3.3553 | 3.4003 | 3.2565 | 121.8908 | 121.8758 | 121.8147 | 121.705 | -0.057062 | -0.004248 | -0.024328 | -0.003172 | 3.6243 | 3.4439 | 3.486 | 3.4638 | 3.5063 | 3.5514 | 3.4075 | 121.9366 | 121.9215 | 121.8604 | 121.7508 | -0.011286 | 0.041528 | 0.021448 | 0.042604 | 121.9479 | 121.9152 | 121.8717 | 121.839
3017.2188 | 121.9986 | -0.091553 | 121.9528 | 2.498 | 2.2993 | 2.3414 | 2.3238 | 2.3985 | 2.4022 | 2.263 | 121.9137 | 121.9078 | 3.3105 | 3.2501 | -0.084531 | -0.054607 | -0.042641 | -0.039797 | 2.5896 | 2.3908 | 2.433 | 2.4153 | 2.49 | 2.4938 | 2.3545 | 121.9595 | 121.9536 | 3.3562 | 3.2958 | -0.038755 | -0.008831 | 0.003135 | 0.005979 | 121.9982 | 121.9564 | 3.395 | 3.3531
3018.9844 | 121.994 | -0.11444 | 121.9437 | 2.3973 | 2.2031 | 2.2407 | 2.2047 | 2.2932 | 2.3061 | 2.1577 | 121.9183 | 121.9078 | 2.4589 | 2.4075 | -0.079953 | -0.040873 | -0.042641 | -0.039797 | 2.5118 | 2.3175 | 2.3551 | 2.3192 | 2.4076 | 2.4205 | 2.2721 | 121.9641 | 121.9536 | 2.5047 | 2.4533 | -0.034177 | 0.004903 | 0.003135 | 0.005979 | 121.9982 | 121.9609 | 2.5388 | 2.5015
3020.6875 | 122.0535 | -0.09613 | 121.9528 | 2.3698 | 2.1573 | 2.204 | 2.1727 | 2.2474 | 2.2695 | 2.1165 | 121.9275 | 121.9215 | 1.7584 | 1.7115 | -0.075375 | -0.040873 | -0.04722 | -0.030641 | 2.466 | 2.2534 | 2.3002 | 2.2688 | 2.3435 | 2.3656 | 2.2126 | 121.9732 | 121.9673 | 1.8042 | 1.7573 | -0.029599 | 0.004903 | -0.001444 | 0.015135 | 122.0028 | 121.9747 | 1.8338 | 1.8056
3022.4531 | 122.0306 | -0.09613 | 121.9482 | 2.3653 | 2.1619 | 2.1995 | 2.1727 | 2.252 | 2.2649 | 2.1211 | 121.9229 | 121.9124 | 1.763 | 1.7207 | -0.079953 | -0.045451 | -0.04722 | -0.035219 | 2.4614 | 2.258 | 2.2956 | 2.2688 | 2.3481 | 2.361 | 2.2172 | 121.9686 | 121.9582 | 1.8088 | 1.7664 | -0.034177 | 0.000325 | -0.001444 | 0.010557 | 122.0028 | 121.9701 | 1.8429 | 1.8102
3024.1562 | 121.9849 | -0.11902 | 121.9391 | 2.3424 | 2.139 | 2.1812 | 2.1589 | 2.1971 | 2.242 | 2.0982 | 121.9275 | 121.9215 | 1.3281 | 1.2811 | -0.079953 | -0.040873 | -0.051798 | -0.035219 | 2.4614 | 2.258 | 2.3002 | 2.2779 | 2.3161 | 2.361 | 2.2172 | 121.9732 | 121.9673 | 1.3738 | 1.3269 | -0.034177 | 0.004903 | -0.006022 | 0.010557 | 122.0074 | 121.9792 | 1.408 | 1.3799
3025.9062 | 122.0764 | -0.068665 | 121.9299 | 2.3469 | 2.1482 | 2.1812 | 2.1543 | 2.2108 | 2.2328 | 2.0936 | 121.9275 | 121.9215 | 1.1312 | 1.0933 | -0.079953 | -0.050029 | -0.051798 | -0.030641 | 2.4156 | 2.2168 | 2.2498 | 2.223 | 2.2795 | 2.3015 | 2.1623 | 121.9732 | 121.9673 | 1.177 | 1.1391 | -0.034177 | -0.004253 | -0.006022 | 0.015135 | 122.0074 | 121.9792 | 1.2111 | 1.183
3027.6719 | 121.994 | -0.11444 | 121.9803 | 2.3195 | 2.1115 | 2.1491 | 2.1223 | 2.165 | 2.2145 | 2.0753 | 121.9275 | 121.9215 | 1.0808 | 1.043 | -0.075375 | -0.040873 | -0.051798 | -0.039797 | 2.4339 | 2.226 | 2.2635 | 2.2367 | 2.2795 | 2.329 | 2.1897 | 121.9732 | 121.9673 | 1.1266 | 1.0887 | -0.029599 | 0.004903 | -0.006022 | 0.005979 | 122.0028 | 121.9792 | 1.1562 | 1.1326
3029.375 | 122.113 | -0.064087 | 121.9299 | 2.3103 | 2.0932 | 2.1399 | 2.1086 | 2.1559 | 2.2054 | 2.057 | 121.932 | 121.9215 | 1.0671 | 1.0247 | -0.075375 | -0.036295 | -0.04722 | -0.030641 | 2.3744 | 2.1573 | 2.204 | 2.1726 | 2.2199 | 2.2695 | 2.1211 | 121.9778 | 121.9673 | 1.1129 | 1.0704 | -0.029599 | 0.009481 | -0.001444 | 0.015135 | 122.0074 | 121.9792 | 1.1425 | 1.1143
3031.1406 | 122.1405 | -0.082397 | 121.9437 | 2.2874 | 2.0886 | 2.1216 | 2.104 | 2.1467 | 2.1916 | 2.0432 | 121.9229 | 121.9215 | 1.0625 | 1.0247 | -0.075375 | -0.050029 | -0.042641 | -0.030641 | 2.3698 | 2.171 | 2.204 | 2.1864 | 2.2291 | 2.274 | 2.1256 | 121.9686 | 121.9673 | 1.1083 | 1.0704 | -0.029599 | -0.004253 | 0.003135 | 0.015135 | 121.9982 | 121.9655 | 1.1379 | 1.1052
3032.9062 | 122.0993 | -0.073242 | 121.8979 | 2.2737 | 2.0703 | 2.1033 | 2.0811 | 2.1238 | 2.1687 | 2.0204 | 121.9366 | 121.9261 | 1.0534 | 1.0063 | -0.075375 | -0.036295 | -0.042641 | -0.030641 | 2.3469 | 2.1436 | 2.1766 | 2.1543 | 2.1971 | 2.242 | 2.0936 | 121.9824 | 121.9719 | 1.0991 | 1.0521 | -0.029599 | 0.009481 | 0.003135 | 0.015135 | 122.012 | 121.9792 | 1.1287 | 1.096
3034.6719 | 121.9849 | -0.1236 | 121.962 | 2.2645 | 2.0703 | 2.0987 | 2.0628 | 2.1192 | 2.1642 | 2.0158 | 121.932 | 121.9215 | 1.0167 | 0.96971 | -0.079953 | -0.040873 | -0.042641 | -0.035219 | 2.3881 | 2.1939 | 2.2223 | 2.1864 | 2.2428 | 2.2878 | 2.1394 | 121.9778 | 121.9673 | 1.0625 | 1.0155 | -0.034177 | 0.004903 | 0.003135 | 0.010557 | 122.012 | 121.9747 | 1.0967 | 1.0594
3036.375 | 121.9986 | -0.12817 | 121.9849 | 2.2371 | 2.0291 | 2.0713 | 2.0307 | 2.0872 | 2.123 | 1.9791 | 121.932 | 121.9215 | 1.0122 | 0.96513 | -0.075375 | -0.045451 | -0.042641 | -0.021484 | 2.3652 | 2.1573 | 2.1994 | 2.1589 | 2.2154 | 2.2511 | 2.1073 | 121.9778 | 121.9673 | 1.0579 | 1.0109 | -0.029599 | 0.000325 | 0.003135 | 0.024292 | 122.0074 | 121.9747 | 1.0875 | 1.0548
3038.1406 | 122.1039 | -0.068665 | 121.9574 | 2.205 | 2.0016 | 2.0484 | 2.0124 | 2.0643 | 2.1092 | 1.9563 | 121.9366 | 121.9215 | 1.0076 | 0.96971 | -0.075375 | -0.050029 | -0.042641 | -0.030641 | 2.2737 | 2.0703 | 2.117 | 2.0811 | 2.133 | 2.1779 | 2.0249 | 121.9824 | 121.9673 | 1.0534 | 1.0155 | -0.029599 | -0.004253 | 0.003135 | 0.015135 | 122.012 | 121.9792 | 1.083 | 1.0502
3039.8438 | 122.0444 | -0.086975 | 121.994 | 2.205 | 1.9925 | 2.0392 | 2.0124 | 2.0689 | 2.1001 | 1.9608 | 121.932 | 121.9261 | 0.97095 | 0.9285 | -0.079953 | -0.050029 | -0.04722 | -0.035219 | 2.292 | 2.0794 | 2.1262 | 2.0994 | 2.1559 | 2.187 | 2.0478 | 121.9778 | 121.9719 | 1.0167 | 0.97427 | -0.034177 | -0.004253 | -0.001444 | 0.010557 | 122.012 | 121.9792 | 1.0509 | 1.0182
3041.625 | 122.0261 | -0.10071 | 122.0078 | 2.2279 | 2.0199 | 2.0667 | 2.0353 | 2.0872 | 2.1184 | 1.9791 | 121.9366 | 121.9307 | 0.92975 | 0.89186 | -0.08911 | -0.036295 | -0.04722 | -0.026063 | 2.3286 | 2.1207 | 2.1674 | 2.136 | 2.1879 | 2.2191 | 2.0799 | 121.9824 | 121.9765 | 0.97553 | 0.93764 | -0.043334 | 0.009481 | -0.001444 | 0.019713 | 122.0257 | 121.9838 | 1.0189 | 0.97697
3043.3906 | 122.1497 | -0.068665 | 121.9299 | 2.2004 | 1.9971 | 2.0438 | 2.0124 | 2.0597 | 2.1001 | 1.9517 | 121.9366 | 121.9261 | 0.92517 | 0.87355 | -0.075375 | -0.036295 | -0.04722 | -0.035219 | 2.2691 | 2.0657 | 2.1125 | 2.0811 | 2.1284 | 2.1687 | 2.0203 | 121.9824 | 121.9719 | 0.97095 | 0.91932 | -0.029599 | 0.009481 | -0.001444 | 0.010557 | 122.012 | 121.9838 | 1.0005 | 0.97239
3045.0938 | 122.113 | -0.054932 | 121.907 | 2.2096 | 2.0016 | 2.0438 | 2.0124 | 2.0643 | 2.1092 | 1.9654 | 121.9366 | 121.9261 | 0.8977 | 0.85981 | -0.075375 | -0.045451 | -0.04722 | -0.030641 | 2.2645 | 2.0566 | 2.0987 | 2.0673 | 2.1192 | 2.1642 | 2.0203 | 121.9824 | 121.9719 | 0.94348 | 0.90559 | -0.029599 | 0.000325 | -0.001444 | 0.015135 | 122.012 | 121.9838 | 0.97308 | 0.94492
3046.8594 | 121.9803 | -0.10529 | 121.9757 | 2.2142 | 2.0154 | 2.0575 | 2.0261 | 2.0735 | 2.1092 | 1.97 | 121.9458 | 121.9261 | 0.94349 | 0.90102 | -0.075375 | -0.050029 | -0.051798 | -0.026063 | 2.3195 | 2.1207 | 2.1628 | 2.1314 | 2.1787 | 2.2145 | 2.0753 | 121.9915 | 121.9719 | 0.98926 | 0.9468 | -0.029599 | -0.004253 | -0.006022 | 0.019713 | 122.0211 | 121.9976 | 1.0189 | 0.99528
3048.5781 | 122.0581 | -0.086975 | 121.9757 | 2.1959 | 2.0016 | 2.0484 | 2.017 | 2.0506 | 2.1047 | 1.9563 | 121.932 | 121.9261 | 1.3647 | 1.3269 | -0.079953 | -0.040873 | -0.042641 | -0.030641 | 2.2828 | 2.0886 | 2.1353 | 2.104 | 2.1375 | 2.1916 | 2.0432 | 121.9778 | 121.9719 | 1.4105 | 1.3726 | -0.034177 | 0.004903 | 0.003135 | 0.015135 | 122.012 | 121.9747 | 1.4446 | 1.4073
3050.3438 | 122.0901 | -0.068665 | 121.9528 | 2.1913 | 1.9879 | 2.0346 | 1.9987 | 2.0414 | 2.0863 | 1.9471 | 121.9412 | 121.9261 | 1.7996 | 1.8214 | -0.079953 | -0.050029 | -0.042641 | -0.030641 | 2.2599 | 2.0566 | 2.1033 | 2.0673 | 2.1101 | 2.155 | 2.0158 | 121.987 | 121.9719 | 1.8454 | 1.8672 | -0.034177 | -0.004253 | 0.003135 | 0.015135 | 122.0211 | 121.9838 | 1.8796 | 1.8423
3052.0938 | 122.1176 | -0.07782 | 121.9711 | 2.2004 | 1.9971 | 2.0438 | 2.0078 | 2.0506 | 2.0909 | 1.9563 | 121.9366 | 121.9261 | 2.4085 | 2.4167 | -0.075375 | -0.045451 | -0.042641 | -0.035219 | 2.2783 | 2.0749 | 2.1216 | 2.0857 | 2.1284 | 2.1687 | 2.0341 | 121.9824 | 121.9719 | 2.4543 | 2.4625 | -0.029599 | 0.000325 | 0.003135 | 0.010557 | 122.012 | 121.9792 | 2.4839 | 2.4512
3053.8125 | 121.9986 | -0.10529 | 121.9666 | 2.1684 | 1.965 | 2.0026 | 1.9758 | 2.0185 | 2.068 | 1.9242 | 121.932 | 121.9261 | 2.4131 | 2.4213 | -0.079953 | -0.036295 | -0.04722 | -0.035219 | 2.2737 | 2.0703 | 2.1079 | 2.0811 | 2.1238 | 2.1733 | 2.0295 | 121.9778 | 121.9719 | 2.4589 | 2.467 | -0.034177 | 0.009481 | -0.001444 | 0.010557 | 122.012 | 121.9792 | 2.4931 | 2.4603
3055.5781 | 122.081 | -0.07782 | 121.9482 | 2.1501 | 1.9467 | 1.9934 | 1.9621 | 2.0139 | 2.0497 | 1.8922 | 121.9366 | 121.9307 | 2.4223 | 2.4304 | -0.075375 | -0.036295 | -0.042641 | -0.035219 | 2.2279 | 2.0245 | 2.0712 | 2.0399 | 2.0918 | 2.1275 | 1.97 | 121.9824 | 121.9765 | 2.468 | 2.4762 | -0.029599 | 0.009481 | 0.003135 | 0.010557 | 122.012 | 121.9792 | 2.4976 | 2.4649
3057.3438 | 122.0306 | -0.11444 | 121.9528 | 2.1318 | 1.9284 | 1.9705 | 1.9392 | 1.9865 | 2.0314 | 1.8784 | 121.9458 | 121.9307 | 2.436 | 2.4487 | -0.075375 | -0.045451 | -0.042641 | -0.035219 | 2.2462 | 2.0428 | 2.085 | 2.0536 | 2.1009 | 2.1458 | 1.9929 | 121.9915 | 121.9765 | 2.4818 | 2.4945 | -0.029599 | 0.000325 | 0.003135 | 0.010557 | 122.0211 | 121.9884 | 2.5114 | 2.4786
3059.1406 | 122.1542 | -0.068665 | 121.9345 | 2.1089 | 1.9146 | 1.9568 | 1.9254 | 1.9727 | 2.0131 | 1.8693 | 121.9366 | 121.9261 | 2.4268 | 2.4396 | -0.075375 | -0.045451 | -0.04722 | -0.030641 | 2.1775 | 1.9833 | 2.0255 | 1.9941 | 2.0414 | 2.0817 | 1.9379 | 121.9824 | 121.9719 | 2.4726 | 2.4854 | -0.029599 | 0.000325 | -0.001444 | 0.015135 | 122.012 | 121.9838 | 2.5022 | 2.4741
3060.8438 | 122.0901 | -0.073242 | 121.9391 | 2.0906 | 1.8917 | 1.9339 | 1.9025 | 1.9499 | 1.9856 | 1.8464 | 121.9366 | 121.9261 | 2.2987 | 2.3068 | -0.075375 | -0.040873 | -0.042641 | -0.035219 | 2.1638 | 1.965 | 2.0071 | 1.9758 | 2.0231 | 2.0589 | 1.9196 | 121.9824 | 121.9719 | 2.3444 | 2.3526 | -0.029599 | 0.004903 | 0.003135 | 0.010557 | 122.012 | 121.9792 | 2.374 | 2.3413
3062.5938 | 122.0901 | -0.09613 | 121.9391 | 2.0814 | 1.8917 | 1.9247 | 1.9025 | 1.9453 | 1.9902 | 1.8326 | 121.9412 | 121.9261 | 2.2575 | 2.2656 | -0.079953 | -0.040873 | -0.04722 | -0.030641 | 2.1775 | 1.9879 | 2.0209 | 1.9987 | 2.0414 | 2.0863 | 1.9288 | 121.987 | 121.9719 | 2.3032 | 2.3113 | -0.034177 | 0.004903 | -0.001444 | 0.015135 | 122.0211 | 121.9884 | 2.3374 | 2.3047
3064.2969 | 122.1405 | -0.068665 | 121.9482 | 2.0219 | 1.8231 | 1.8698 | 1.8339 | 1.8858 | 1.9261 | 1.7731 | 121.9366 | 121.9353 | 2.2483 | 2.2427 | -0.075375 | -0.040873 | -0.04722 | -0.030641 | 2.0905 | 1.8917 | 1.9385 | 1.9025 | 1.9544 | 1.9948 | 1.8418 | 121.9824 | 121.9811 | 2.2941 | 2.2885 | -0.029599 | 0.004903 | -0.001444 | 0.015135 | 122.012 | 121.9838 | 2.3237 | 2.2955
3066.0469 | 122.081 | -0.10071 | 121.9849 | 2.0173 | 1.8139 | 1.8561 | 1.8293 | 1.8674 | 1.9124 | 1.7686 | 121.9549 | 121.9307 | 2.3078 | 2.3068 | -0.084531 | -0.054607 | -0.051798 | -0.039797 | 2.118 | 1.9146 | 1.9568 | 1.93 | 1.9682 | 2.0131 | 1.8693 | 122.0007 | 121.9765 | 2.3536 | 2.3526 | -0.038755 | -0.008831 | -0.006022 | 0.005979 | 122.0395 | 122.0067 | 2.3923 | 2.3596
3067.8125 | 122.1085 | -0.073242 | 121.9162 | 1.9898 | 1.7864 | 1.8332 | 1.8018 | 1.8491 | 1.8895 | 1.7365 | 121.9366 | 121.9261 | 2.2712 | 2.2747 | -0.079953 | -0.031717 | -0.038063 | -0.035219 | 2.0631 | 1.8597 | 1.9064 | 1.875 | 1.9224 | 1.9627 | 1.8097 | 121.9824 | 121.9719 | 2.317 | 2.3205 | -0.034177 | 0.014059 | 0.007713 | 0.010557 | 122.0166 | 121.9747 | 2.3511 | 2.3092
3069.5156 | 121.9986 | -0.1236 | 121.9849 | 1.9578 | 1.759 | 1.792 | 1.7743 | 1.8125 | 1.8528 | 1.7045 | 121.9275 | 121.9353 | 2.1384 | 2.1465 | -0.079953 | -0.040873 | -0.042641 | -0.039797 | 2.0814 | 1.8825 | 1.9156 | 1.8979 | 1.9361 | 1.9764 | 1.8281 | 121.9732 | 121.9811 | 2.1842 | 2.1923 | -0.034177 | 0.004903 | 0.003135 | 0.005979 | 122.0074 | 121.9701 | 2.2184 | 2.1811
3071.2656 | 122.0261 | -0.10071 | 121.9482 | 1.9212 | 1.7223 | 1.7737 | 1.7469 | 1.7942 | 1.8208 | 1.677 | 121.9458 | 121.9353 | 2.4406 | 2.4396 | -0.079953 | -0.040873 | -0.04722 | -0.035219 | 2.0219 | 1.823 | 1.8744 | 1.8476 | 1.8949 | 1.9215 | 1.7777 | 121.9915 | 121.9811 | 2.4864 | 2.4854 | -0.034177 | 0.004903 | -0.001444 | 0.010557 | 122.0257 | 121.993 | 2.5205 | 2.4878
3072.9688 | 122.1588 | -0.068665 | 121.9757 | 1.8845 | 1.6949 | 1.7416 | 1.7102 | 1.7484 | 1.7933 | 1.6495 | 121.9458 | 121.9307 | 2.0789 | 2.0916 | -0.075375 | -0.045451 | -0.042641 | -0.039797 | 1.9532 | 1.7635 | 1.8103 | 1.7789 | 1.8171 | 1.862 | 1.7182 | 121.9915 | 121.9765 | 2.1247 | 2.1373 | -0.029599 | 0.000325 | 0.003135 | 0.005979 | 122.0211 | 121.9884 | 2.1543 | 2.1215
3074.75 | 122.0261 | -0.10986 | 121.9803 | 1.8616 | 1.6674 | 1.7096 | 1.6782 | 1.7255 | 1.7704 | 1.6083 | 121.9412 | 121.9353 | 2.0789 | 2.0961 | -0.079953 | -0.045451 | -0.042641 | -0.030641 | 1.9715 | 1.7772 | 1.8194 | 1.788 | 1.8354 | 1.8803 | 1.7182 | 121.987 | 121.9811 | 2.1247 | 2.1419 | -0.034177 | 0.000325 | 0.003135 | 0.015135 | 122.0211 | 121.9838 | 2.1589 | 2.1215
3076.5156 | 122.1451 | -0.054932 | 121.9437 | 1.8021 | 1.6079 | 1.65 | 1.6278 | 1.6706 | 1.7109 | 1.5534 | 121.9366 | 121.9307 | 2.024 | 2.0366 | -0.079953 | -0.045451 | -0.04722 | -0.039797 | 1.8571 | 1.6628 | 1.705 | 1.6828 | 1.7255 | 1.7658 | 1.6083 | 121.9824 | 121.9765 | 2.0697 | 2.0824 | -0.034177 | 0.000325 | -0.001444 | 0.005979 | 122.0166 | 121.9838 | 2.1039 | 2.0712
3078.2656 | 122.0673 | -0.10071 | 121.9666 | 1.8021 | 1.5941 | 1.6455 | 1.6232 | 1.6569 | 1.7018 | 1.5442 | 121.9412 | 121.9353 | 1.9278 | 1.9313 | -0.075375 | -0.045451 | -0.051798 | -0.035219 | 1.9028 | 1.6948 | 1.7462 | 1.7239 | 1.7576 | 1.8025 | 1.6449 | 121.987 | 121.9811 | 1.9736 | 1.9771 | -0.029599 | 0.000325 | -0.006022 | 0.010557 | 122.0166 | 121.993 | 2.0032 | 1.9796
3079.9688 | 122.049 | -0.10986 | 121.9757 | 1.7289 | 1.53 | 1.5676 | 1.55 | 1.5928 | 1.6377 | 1.4801 | 121.9503 | 121.9353 | 1.9049 | 1.9176 | -0.079953 | -0.050029 | -0.04722 | -0.035219 | 1.8387 | 1.6399 | 1.6775 | 1.6598 | 1.7026 | 1.7475 | 1.59 | 121.9961 | 121.9811 | 1.9507 | 1.9633 | -0.034177 | -0.004253 | -0.001444 | 0.010557 | 122.0303 | 121.9976 | 1.9849 | 1.9521
3081.6719 | 122.0444 | -0.10529 | 121.9803 | 1.564 | 1.356 | 1.3982 | 1.3806 | 1.4371 | 1.4683 | 1.3107 | 121.9458 | 121.9399 | 2.3994 | 2.4121 | -0.075375 | -0.045451 | -0.04722 | -0.030641 | 1.6693 | 1.4613 | 1.5035 | 1.4859 | 1.5424 | 1.5735 | 1.416 | 121.9915 | 121.9856 | 2.4452 | 2.4579 | -0.029599 | 0.000325 | -0.001444 | 0.015135 | 122.0211 | 121.993 | 2.4748 | 2.4466
3083.4219 | 122.0032 | -0.11444 | 121.9757 | 1.3718 | 1.15 | 1.1922 | 1.1929 | 1.2403 | 1.276 | 1.1093 | 121.9366 | 121.9307 | 2.3994 | 2.4167 | -0.075375 | -0.054607 | -0.042641 | -0.035219 | 1.4862 | 1.2644 | 1.3066 | 1.3073 | 1.3547 | 1.3904 | 1.2237 | 121.9824 | 121.9765 | 2.4452 | 2.4625 | -0.029599 | -0.008831 | 0.003135 | 0.010557 | 122.012 | 121.9792 | 2.4748 | 2.442
3085.1875 | 122.0032 | -0.10529 | 121.9757 | 1.2481 | 1.0263 | 1.0548 | 1.0692 | 1.1167 | 1.1615 | 0.99026 | 121.9412 | 121.9399 | 2.056 | 2.0641 | -0.084531 | -0.045451 | -0.042641 | -0.030641 | 1.3534 | 1.1316 | 1.1601 | 1.1745 | 1.2219 | 1.2668 | 1.0955 | 121.987 | 121.9856 | 2.1018 | 2.1099 | -0.038755 | 0.000325 | 0.003135 | 0.015135 | 122.0257 | 121.9838 | 2.1405 | 2.0986
3086.9531 | 122.1313 | -0.068665 | 121.9574 | 1.2848 | 1.0584 | 1.1143 | 1.1013 | 1.1579 | 1.1936 | 1.0177 | 121.9458 | 121.9444 | 1.7859 | 1.7894 | -0.084531 | -0.050029 | -0.056376 | -0.044375 | 1.3534 | 1.1271 | 1.183 | 1.17 | 1.2265 | 1.2622 | 1.0864 | 121.9915 | 121.9902 | 1.8317 | 1.8351 | -0.038755 | -0.004253 | -0.0106 | 0.001401 | 122.0303 | 122.0021 | 1.8704 | 1.8423
3088.6562 | 122.0169 | -0.10529 | 121.9711 | 1.3397 | 1.1088 | 1.1693 | 1.1654 | 1.2128 | 1.2531 | 1.0772 | 121.9503 | 121.9353 | 1.763 | 1.771 | -0.084531 | -0.054607 | -0.051798 | -0.039797 | 1.445 | 1.214 | 1.2746 | 1.2707 | 1.3181 | 1.3584 | 1.1825 | 121.9961 | 121.9811 | 1.8088 | 1.8168 | -0.038755 | -0.008831 | -0.006022 | 0.005979 | 122.0349 | 122.0021 | 1.8475 | 1.8148
3090.4219 | 122.0901 | -0.082397 | 121.9666 | 1.2893 | 1.0538 | 1.1327 | 1.1196 | 1.1624 | 1.189 | 1.0177 | 121.9503 | 121.9399 | 1.7767 | 1.7939 | -0.084531 | -0.045451 | -0.051798 | -0.044375 | 1.3717 | 1.1362 | 1.215 | 1.202 | 1.2448 | 1.2714 | 1.1001 | 121.9961 | 121.9856 | 1.8225 | 1.8397 | -0.038755 | 0.000325 | -0.006022 | 0.001401 | 122.0349 | 122.0021 | 1.8613 | 1.8285
3092.125 | 122.0215 | -0.10986 | 121.994 | 1.4816 | 1.2644 | 1.3478 | 1.3211 | 1.3685 | 1.3767 | 1.21 | 121.9412 | 121.9307 | 1.7905 | 1.8077 | -0.084531 | -0.040873 | -0.04722 | -0.039797 | 1.5915 | 1.3743 | 1.4577 | 1.4309 | 1.4783 | 1.4866 | 1.3199 | 121.987 | 121.9765 | 1.8362 | 1.8534 | -0.038755 | 0.004903 | -0.001444 | 0.005979 | 122.0257 | 121.9884 | 1.875 | 1.8377
3093.9062 | 122.0993 | -0.07782 | 121.962 | 1.4358 | 1.2049 | 1.2929 | 1.2753 | 1.3044 | 1.3172 | 1.1322 | 121.9412 | 121.9307 | 1.7126 | 1.7252 | -0.079953 | -0.054607 | -0.051798 | -0.030641 | 1.5137 | 1.2827 | 1.3707 | 1.3531 | 1.3822 | 1.395 | 1.21 | 121.987 | 121.9765 | 1.7584 | 1.771 | -0.034177 | -0.008831 | -0.006022 | 0.015135 | 122.0211 | 121.993 | 1.7926 | 1.7644
3095.6719 | 121.994 | -0.11444 | 121.9894 | 1.2802 | 1.0492 | 1.1555 | 1.1196 | 1.1533 | 1.1707 | 0.96737 | 121.9412 | 121.9307 | 1.8591 | 1.8764 | -0.079953 | -0.045451 | -0.051798 | -0.030641 | 1.3946 | 1.1637 | 1.27 | 1.234 | 1.2677 | 1.2851 | 1.0818 | 121.987 | 121.9765 | 1.9049 | 1.9221 | -0.034177 | 0.000325 | -0.006022 | 0.015135 | 122.0211 | 121.993 | 1.9391 | 1.9109
3097.4219 | 122.0627 | -0.10529 | 121.994 | 0.7674 | 0.52267 | 0.59238 | 0.59308 | 0.64513 | 0.67162 | 0.48208 | 121.9458 | 121.9353 | 1.9324 | 1.9542 | -0.079953 | -0.045451 | -0.04722 | -0.039797 | 0.87269 | 0.62796 | 0.69766 | 0.69837 | 0.75042 | 0.7769 | 0.58737 | 121.9915 | 121.9811 | 1.9782 | 2 | -0.034177 | 0.000325 | -0.001444 | 0.005979 | 122.0257 | 121.993 | 2.0123 | 1.9796
3099.2031 | 122.0993 | -0.07782 | 121.9711 | 0.7674 | 0.53183 | 0.59238 | 0.60224 | 0.65887 | 0.68077 | 0.48666 | 121.9458 | 121.9353 | 1.9599 | 1.9679 | -0.084531 | -0.040873 | -0.056376 | -0.039797 | 0.84522 | 0.60965 | 0.6702 | 0.68006 | 0.73669 | 0.75859 | 0.56448 | 121.9915 | 121.9811 | 2.0056 | 2.0137 | -0.038755 | 0.004903 | -0.0106 | 0.005979 | 122.0303 | 122.0021 | 2.0444 | 2.0162
3100.9688 | 122.0123 | -0.11444 | 121.9666 | 1.0604 | 0.84319 | 0.91288 | 0.89526 | 0.93812 | 0.9509 | 0.78424 | 121.9366 | 121.9261 | 1.937 | 1.9588 | -0.084531 | -0.045451 | -0.04722 | -0.035219 | 1.1749 | 0.95763 | 1.0273 | 1.0097 | 1.0526 | 1.0653 | 0.89869 | 121.9824 | 121.9719 | 1.9827 | 2.0046 | -0.038755 | 0.000325 | -0.001444 | 0.010557 | 122.0211 | 121.9838 | 2.0215 | 1.9842
3102.6719 | 122.1451 | -0.073242 | 121.9345 | 0.90018 | 0.6692 | 0.73431 | 0.72128 | 0.77789 | 0.80439 | 0.62401 | 121.9412 | 121.9307 | 1.9461 | 1.9634 | -0.079953 | -0.050029 | -0.038063 | -0.026063 | 0.97342 | 0.74244 | 0.80756 | 0.79452 | 0.85114 | 0.87763 | 0.69725 | 121.987 | 121.9765 | 1.9919 | 2.0091 | -0.034177 | -0.004253 | 0.007713 | 0.019713 | 122.0211 | 121.9792 | 2.0261 | 1.9842
3104.4375 | 122.0306 | -0.10529 | 122.0169 | 0.74909 | 0.52267 | 0.56948 | 0.57019 | 0.6314 | 0.66246 | 0.48208 | 121.9412 | 121.9307 | 2.0056 | 2.0137 | -0.084531 | -0.045451 | -0.056376 | -0.044375 | 0.85438 | 0.62796 | 0.67477 | 0.67547 | 0.73669 | 0.76775 | 0.58737 | 121.987 | 121.9765 | 2.0514 | 2.0595 | -0.038755 | 0.000325 | -0.0106 | 0.001401 | 122.0257 | 121.9976 | 2.0902 | 2.062
3106.1562 | 122.0032 | -0.10986 | 121.9803 | 0.94596 | 0.73788 | 0.78926 | 0.77622 | 0.8191 | 0.84559 | 0.66521 | 121.9366 | 121.9353 | 2.0194 | 2.0229 | -0.084531 | -0.040873 | -0.04722 | -0.035219 | 1.0558 | 0.84774 | 0.89912 | 0.88608 | 0.92896 | 0.95546 | 0.77508 | 121.9824 | 121.9811 | 2.0652 | 2.0687 | -0.038755 | 0.004903 | -0.001444 | 0.010557 | 122.0211 | 121.9838 | 2.1039 | 2.0666
3107.9219 | 122.0261 | -0.10071 | 121.9437 | 0.94138 | 0.72872 | 0.77094 | 0.77164 | 0.81452 | 0.83186 | 0.65606 | 121.9458 | 121.9307 | 2.0423 | 2.0504 | -0.079953 | -0.045451 | -0.042641 | -0.035219 | 1.0421 | 0.82943 | 0.87165 | 0.87235 | 0.91523 | 0.93257 | 0.75676 | 121.9915 | 121.9765 | 2.088 | 2.0961 | -0.034177 | 0.000325 | 0.003135 | 0.010557 | 122.0257 | 121.9884 | 2.1222 | 2.0849
3109.7031 | 122.1405 | -0.073242 | 121.9482 | 0.97343 | 0.76077 | 0.79841 | 0.79911 | 0.83283 | 0.85933 | 0.68353 | 121.9458 | 121.9261 | 2.0697 | 2.087 | -0.084531 | -0.045451 | -0.042641 | -0.035219 | 1.0467 | 0.83401 | 0.87166 | 0.87235 | 0.90607 | 0.93257 | 0.75677 | 121.9915 | 121.9719 | 2.1155 | 2.1328 | -0.038755 | 0.000325 | 0.003135 | 0.010557 | 122.0303 | 121.9884 | 2.1543 | 2.1124
3111.4062 | 122.1542 | -0.032043 | 121.9482 | 1.0284 | 0.82946 | 0.85794 | 0.85863 | 0.88777 | 0.90969 | 0.74304 | 121.9458 | 121.9353 | 2.1522 | 2.1557 | -0.079953 | -0.045451 | -0.04722 | -0.039797 | 1.0604 | 0.8615 | 0.88998 | 0.89068 | 0.91981 | 0.94174 | 0.77508 | 121.9915 | 121.9811 | 2.1979 | 2.2015 | -0.034177 | 0.000325 | -0.001444 | 0.005979 | 122.0257 | 121.993 | 2.2321 | 2.1994
3113.1562 | 122.081 | -0.07782 | 121.962 | 1.0009 | 0.79282 | 0.83962 | 0.83116 | 0.87403 | 0.8868 | 0.70642 | 121.9458 | 121.9307 | 2.0972 | 2.119 | -0.079953 | -0.040873 | -0.051798 | -0.044375 | 1.0787 | 0.87064 | 0.91744 | 0.90898 | 0.95185 | 0.96462 | 0.78424 | 121.9915 | 121.9765 | 2.143 | 2.1648 | -0.034177 | 0.004903 | -0.006022 | 0.001401 | 122.0257 | 121.9976 | 2.1772 | 2.149
3114.9219 | 122.0444 | -0.11444 | 121.9666 | 0.94596 | 0.7333 | 0.77094 | 0.77622 | 0.8191 | 0.83644 | 0.65148 | 121.9458 | 121.9353 | 2.0743 | 2.087 | -0.075375 | -0.040873 | -0.04722 | -0.035219 | 1.0604 | 0.84774 | 0.88538 | 0.89066 | 0.93354 | 0.95088 | 0.76592 | 121.9915 | 121.9811 | 2.1201 | 2.1328 | -0.029599 | 0.004903 | -0.001444 | 0.010557 | 122.0211 | 121.993 | 2.1497 | 2.1215
3116.6875 | 122.0535 | -0.10529 | 121.9757 | 0.52933 | 0.33952 | 0.3726 | 0.38705 | 0.41624 | 0.42438 | 0.17993 | 121.9458 | 121.9353 | 2.0789 | 2.087 | -0.075375 | -0.040873 | -0.042641 | -0.035219 | 0.63461 | 0.44481 | 0.47789 | 0.49233 | 0.52152 | 0.52967 | 0.28521 | 121.9915 | 121.9811 | 2.1247 | 2.1328 | -0.029599 | 0.004903 | 0.003135 | 0.010557 | 122.0211 | 121.9884 | 2.1543 | 2.1215
3118.3906 | 122.0947 | -0.064087 | 121.9437 | 0.52017 | 0.32121 | 0.3726 | 0.37331 | 0.41166 | 0.41065 | 0.17077 | 121.9503 | 121.9307 | 2.1705 | 2.1786 | -0.079953 | -0.045451 | -0.04722 | -0.030641 | 0.58426 | 0.38529 | 0.43669 | 0.4374 | 0.47574 | 0.47474 | 0.23486 | 121.9961 | 121.9765 | 2.2162 | 2.2243 | -0.034177 | 0.000325 | -0.001444 | 0.015135 | 122.0303 | 121.9976 | 2.2504 | 2.2177
3120.1562 | 122.1313 | -0.059509 | 121.962 | 0.51559 | 0.32121 | 0.35429 | 0.36873 | 0.40708 | 0.40149 | 0.17077 | 121.9366 | 121.9399 | 2.1796 | 2.2015 | -0.079953 | -0.045451 | -0.056376 | -0.039797 | 0.5751 | 0.38071 | 0.4138 | 0.42824 | 0.46659 | 0.461 | 0.23028 | 121.9824 | 121.9856 | 2.2254 | 2.2472 | -0.034177 | 0.000325 | -0.0106 | 0.005979 | 122.0166 | 121.993 | 2.2596 | 2.236
3121.9062 | 122.1497 | -0.082397 | 121.9437 | 0.33703 | 0.17926 | 0.20777 | 0.20391 | 0.22854 | 0.15884 | 0.033424 | 121.9366 | 121.9353 | 1.5203 | 1.51 | -0.075375 | -0.045451 | -0.04722 | -0.030641 | 0.41943 | 0.26166 | 0.29017 | 0.28631 | 0.31094 | 0.24123 | 0.11582 | 121.9824 | 121.9811 | 1.5661 | 1.5558 | -0.029599 | 0.000325 | -0.001444 | 0.015135 | 122.012 | 121.9838 | 1.5957 | 1.5676
3123.6562 | 122.0261 | -0.086975 | 121.9803 | 0.30956 | 0.14721 | 0.17572 | 0.17644 | 0.20565 | 0.13595 | -0.012357 | 121.9458 | 121.9261 | 1.8179 | 1.8306 | -0.079953 | -0.040873 | -0.042641 | -0.030641 | 0.39654 | 0.23419 | 0.2627 | 0.26341 | 0.29262 | 0.22292 | 0.074618 | 121.9915 | 121.9719 | 1.8637 | 1.8763 | -0.034177 | 0.004903 | 0.003135 | 0.015135 | 122.0257 | 121.9884 | 1.8979 | 1.8606
3125.3594 | 122.1313 | -0.082397 | 121.9482 | 0.29583 | 0.13347 | 0.16199 | 0.1627 | 0.20107 | 0.12221 | -0.007779 | 121.9366 | 121.9307 | 1.5295 | 1.5421 | -0.070797 | -0.040873 | -0.04722 | -0.030641 | 0.37823 | 0.21587 | 0.24438 | 0.2451 | 0.28347 | 0.20461 | 0.074618 | 121.9824 | 121.9765 | 1.5753 | 1.5879 | -0.025021 | 0.004903 | -0.001444 | 0.015135 | 122.0074 | 121.9838 | 1.6003 | 1.5767
3127.125 | 122.0581 | -0.10071 | 121.9711 | 0.28667 | 0.13347 | 0.16199 | 0.1627 | 0.20107 | 0.12679 | -0.012357 | 121.9412 | 121.9261 | 1.0625 | 1.0796 | -0.075375 | -0.040873 | -0.042641 | -0.035219 | 0.38738 | 0.23418 | 0.2627 | 0.26341 | 0.30178 | 0.2275 | 0.088351 | 121.987 | 121.9719 | 1.1083 | 1.1254 | -0.029599 | 0.004903 | 0.003135 | 0.010557 | 122.0166 | 121.9838 | 1.1379 | 1.1052
3128.9062 | 121.994 | -0.12817 | 121.994 | 0.28209 | 0.1289 | 0.15283 | 0.15354 | 0.19192 | 0.11763 | -0.012357 | 121.9366 | 121.9307 | 0.71915 | 0.73618 | -0.084531 | -0.040873 | -0.04722 | -0.035219 | 0.41027 | 0.25707 | 0.281 | 0.28172 | 0.32009 | 0.24581 | 0.11582 | 121.9824 | 121.9765 | 0.76493 | 0.78195 | -0.038755 | 0.004903 | -0.001444 | 0.010557 | 122.0211 | 121.9838 | 0.80368 | 0.76637
3130.6719 | 122.1085 | -0.064087 | 121.9528 | 0.27752 | 0.12432 | 0.14367 | 0.13981 | 0.18734 | 0.11763 | -0.026092 | 121.9366 | 121.9353 | 0.1606 | 0.15464 | -0.070797 | -0.036295 | -0.051798 | -0.030641 | 0.3416 | 0.1884 | 0.20776 | 0.2039 | 0.25142 | 0.18172 | 0.037995 | 121.9824 | 121.9811 | 0.20637 | 0.20042 | -0.025021 | 0.009481 | -0.006022 | 0.015135 | 122.0074 | 121.9884 | 0.2314 | 0.2124
3132.3594 | 122.049 | -0.10529 | 121.994 | 0.26836 | 0.11516 | 0.13909 | 0.13065 | 0.17818 | 0.11305 | -0.021514 | 121.9412 | 121.9261 | 0.069033 | 0.063059 | -0.075375 | -0.045451 | -0.04722 | -0.030641 | 0.37365 | 0.22045 | 0.24438 | 0.23594 | 0.28347 | 0.21834 | 0.083772 | 121.987 | 121.9719 | 0.11481 | 0.10884 | -0.029599 | 0.000325 | -0.001444 | 0.015135 | 122.0166 | 121.9884 | 0.14441 | 0.11625
3134.125 | 122.0947 | -0.091553 | 121.9528 | 0.28209 | 0.13805 | 0.15741 | 0.15354 | 0.19649 | 0.12221 | -0.016936 | 121.9458 | 121.9307 | 0.055298 | 0.040164 | -0.075375 | -0.040873 | -0.042641 | -0.030641 | 0.37365 | 0.22961 | 0.24896 | 0.2451 | 0.28805 | 0.21376 | 0.074617 | 121.9915 | 121.9765 | 0.10107 | 0.08594 | -0.029599 | 0.004903 | 0.003135 | 0.015135 | 122.0211 | 121.9884 | 0.13067 | 0.097939
3135.8906 | 122.081 | -0.09613 | 121.9711 | 0.29583 | 0.14263 | 0.16657 | 0.1627 | 0.19649 | 0.13137 | -0.012357 | 121.9366 | 121.9307 | 0.046142 | 0.026427 | -0.079953 | -0.036295 | -0.04722 | -0.026063 | 0.39196 | 0.23876 | 0.2627 | 0.25883 | 0.29262 | 0.2275 | 0.083773 | 121.9824 | 121.9765 | 0.091918 | 0.072203 | -0.034177 | 0.009481 | -0.001444 | 0.019713 | 122.0166 | 121.9838 | 0.1261 | 0.093362
3137.5938 | 122.0993 | -0.086975 | 121.9528 | 0.27294 | 0.11516 | 0.12994 | 0.11692 | 0.1736 | 0.12221 | -0.012357 | 121.9412 | 121.9307 | 0.041563 | 0.031006 | -0.084531 | -0.040873 | -0.04722 | -0.030641 | 0.35991 | 0.20213 | 0.21691 | 0.20389 | 0.26058 | 0.20919 | 0.074618 | 121.987 | 121.9765 | 0.087339 | 0.076782 | -0.038755 | 0.004903 | -0.001444 | 0.015135 | 122.0257 | 121.9884 | 0.12609 | 0.088783
3139.3594 | 122.0993 | -0.068665 | 121.962 | 0.218 | 0.051056 | 0.061258 | 0.052818 | 0.11409 | 0.1039 | -0.039826 | 121.9503 | 121.9353 | 0.041563 | 0.021847 | -0.08911 | -0.045451 | -0.042641 | -0.030641 | 0.28666 | 0.11972 | 0.12992 | 0.12148 | 0.18276 | 0.17256 | 0.028839 | 121.9961 | 121.9811 | 0.087339 | 0.067623 | -0.043334 | 0.000325 | 0.003135 | 0.015135 | 122.0395 | 121.993 | 0.13067 | 0.084204
3141.125 | 122.1313 | -0.054932 | 121.9437 | 0.22258 | 0.051056 | 0.061258 | 0.048239 | 0.10493 | 0.10848 | -0.035248 | 121.9412 | 121.9215 | 0.036985 | 0.026427 | -0.075375 | -0.040873 | -0.04722 | -0.035219 | 0.27751 | 0.10599 | 0.11619 | 0.10317 | 0.15987 | 0.16341 | 0.019684 | 121.987 | 121.9673 | 0.082761 | 0.072203 | -0.029599 | 0.004903 | -0.001444 | 0.010557 | 122.0166 | 121.9884 | 0.11236 | 0.084205
3142.8125 | 122.0032 | -0.10986 | 121.9894 | 0.21342 | 0.055634 | 0.061258 | 0.057396 | 0.10951 | 0.1039 | -0.035248 | 121.9366 | 121.9307 | 0.032407 | 0.026427 | -0.075375 | -0.040873 | -0.042641 | -0.035219 | 0.32328 | 0.1655 | 0.17112 | 0.16726 | 0.21937 | 0.21376 | 0.074615 | 121.9824 | 121.9765 | 0.078183 | 0.072203 | -0.029599 | 0.004903 | 0.003135 | 0.010557 | 122.012 | 121.9792 | 0.10778 | 0.075048
3144.5781 | 122.081 | -0.082397 | 121.9528 | 0.20884 | 0.037319 | 0.052101 | 0.048239 | 0.10036 | 0.09474 | -0.044405 | 121.932 | 121.9307 | 0.036985 | 0.021847 | -0.075375 | -0.036295 | -0.042641 | -0.030641 | 0.29124 | 0.11972 | 0.1345 | 0.13064 | 0.18275 | 0.17714 | 0.037992 | 121.9778 | 121.9765 | 0.082761 | 0.067623 | -0.029599 | 0.009481 | 0.003135 | 0.015135 | 122.0074 | 121.9747 | 0.11236 | 0.079626
3146.3438 | 122.0261 | -0.11444 | 121.9666 | 0.20426 | 0.037319 | 0.042944 | 0.048239 | 0.095778 | 0.1039 | -0.044405 | 121.9458 | 121.9307 | 0.041563 | 0.017268 | -0.075375 | -0.045451 | -0.051798 | -0.035219 | 0.3187 | 0.15176 | 0.15738 | 0.16268 | 0.21022 | 0.21834 | 0.070036 | 121.9915 | 121.9765 | 0.087339 | 0.063044 | -0.029599 | 0.000325 | -0.006022 | 0.010557 | 122.0211 | 121.9976 | 0.11694 | 0.093361
3148.1094 | 122.1176 | -0.068665 | 121.9299 | 0.19968 | 0.028162 | 0.042944 | 0.034504 | 0.086622 | 0.099318 | -0.039826 | 121.9412 | 121.9353 | 0.036985 | 0.031006 | -0.084531 | -0.045451 | -0.051798 | -0.044375 | 0.26835 | 0.096827 | 0.11161 | 0.10317 | 0.15529 | 0.16798 | 0.028839 | 121.987 | 121.9811 | 0.082761 | 0.076782 | -0.038755 | 0.000325 | -0.006022 | 0.001401 | 122.0257 | 121.993 | 0.12152 | 0.088783
3149.8281 | 122.1451 | -0.064087 | 121.9391 | 0.19968 | 0.037319 | 0.047522 | 0.034504 | 0.0912 | 0.099318 | -0.035248 | 121.9412 | 121.9307 | 0.046142 | 0.035585 | -0.08911 | -0.050029 | -0.04722 | -0.035219 | 0.26377 | 0.10141 | 0.11161 | 0.098591 | 0.15529 | 0.16341 | 0.028839 | 121.987 | 121.9765 | 0.091918 | 0.081361 | -0.043334 | -0.004253 | -0.001444 | 0.010557 | 122.0303 | 121.9884 | 0.13525 | 0.093362
3151.5938 | 122.0581 | -0.10529 | 122.0123 | 0.20426 | 0.046477 | 0.056679 | 0.048239 | 0.086622 | 0.1039 | -0.039826 | 121.9458 | 121.9353 | 0.046142 | 0.035585 | -0.084531 | -0.045451 | -0.04722 | -0.035219 | 0.30955 | 0.15176 | 0.16196 | 0.15352 | 0.19191 | 0.20918 | 0.06546 | 121.9915 | 121.9811 | 0.091918 | 0.081361 | -0.038755 | 0.000325 | -0.001444 | 0.010557 | 122.0303 | 121.993 | 0.13067 | 0.093362
3153.3594 | 122.1313 | -0.064087 | 121.9391 | 0.21342 | 0.055634 | 0.065837 | 0.052818 | 0.095778 | 0.099318 | -0.039826 | 121.9412 | 121.9353 | 0.05072 | 0.040164 | -0.084531 | -0.054607 | -0.04722 | -0.035219 | 0.27751 | 0.11972 | 0.12992 | 0.11691 | 0.15987 | 0.16341 | 0.024261 | 121.987 | 121.9811 | 0.096496 | 0.08594 | -0.038755 | -0.008831 | -0.001444 | 0.010557 | 122.0257 | 121.9884 | 0.13525 | 0.09794
3155.1406 | 122.0444 | -0.091553 | 121.9849 | 0.20426 | 0.051056 | 0.052101 | 0.048239 | 0.0912 | 0.1039 | -0.035248 | 121.9412 | 121.9353 | 0.059877 | 0.044743 | -0.08911 | -0.050029 | -0.051798 | -0.030641 | 0.29581 | 0.14261 | 0.14365 | 0.13979 | 0.18275 | 0.19545 | 0.056305 | 121.987 | 121.9811 | 0.10565 | 0.090519 | -0.043334 | -0.004253 | -0.006022 | 0.015135 | 122.0303 | 121.993 | 0.14899 | 0.11167
3156.9062 | 122.1039 | -0.07782 | 121.9528 | 0.19511 | 0.046477 | 0.047522 | 0.034504 | 0.086622 | 0.099318 | -0.03067 | 121.9503 | 121.9307 | 0.069033 | 0.063059 | -0.093688 | -0.040873 | -0.051798 | -0.044375 | 0.27292 | 0.1243 | 0.12534 | 0.11232 | 0.16444 | 0.17714 | 0.04715 | 121.9961 | 121.9765 | 0.11481 | 0.10884 | -0.047912 | 0.004903 | -0.006022 | 0.001401 | 122.044 | 122.0021 | 0.16272 | 0.12083
3158.6562 | 122.0261 | -0.12817 | 121.9803 | 0.20426 | 0.046477 | 0.061258 | 0.052818 | 0.086622 | 0.099318 | -0.03067 | 121.9366 | 121.9399 | 0.091925 | 0.076796 | -0.08911 | -0.045451 | -0.056376 | -0.035219 | 0.33244 | 0.17465 | 0.18943 | 0.18099 | 0.2148 | 0.22749 | 0.097504 | 121.9824 | 121.9856 | 0.1377 | 0.12257 | -0.043334 | 0.000325 | -0.0106 | 0.010557 | 122.0257 | 121.993 | 0.18104 | 0.1483
3160.3594 | 122.0581 | -0.086975 | 121.9666 | 0.21342 | 0.060213 | 0.065837 | 0.057396 | 0.095778 | 0.10848 | -0.026092 | 121.9458 | 121.9307 | 0.11482 | 0.10427 | -0.084531 | -0.054607 | -0.042641 | -0.035219 | 0.30039 | 0.14719 | 0.15281 | 0.14437 | 0.18275 | 0.19545 | 0.060883 | 121.9915 | 121.9765 | 0.16059 | 0.15005 | -0.038755 | -0.008831 | 0.003135 | 0.010557 | 122.0303 | 121.9884 | 0.19935 | 0.15746
3162.125 | 122.0398 | -0.09613 | 121.9986 | 0.22715 | 0.07395 | 0.08873 | 0.089445 | 0.11409 | 0.11763 | -0.021514 | 121.9366 | 121.9353 | 0.12397 | 0.10885 | -0.084531 | -0.050029 | -0.04722 | -0.035219 | 0.32328 | 0.17008 | 0.18486 | 0.18557 | 0.21022 | 0.21376 | 0.074616 | 121.9824 | 121.9811 | 0.16975 | 0.15463 | -0.038755 | -0.004253 | -0.001444 | 0.010557 | 122.0211 | 121.9838 | 0.2085 | 0.17119
3163.9062 | 121.9986 | -0.11444 | 121.9894 | 0.26378 | 0.11974 | 0.14825 | 0.15354 | 0.15071 | 0.12221 | -0.003201 | 121.9366 | 121.9215 | 0.13771 | 0.1409 | -0.075375 | -0.045451 | -0.042641 | -0.035219 | 0.37822 | 0.23418 | 0.26269 | 0.26799 | 0.26515 | 0.23665 | 0.11124 | 121.9824 | 121.9673 | 0.18348 | 0.18668 | -0.029599 | 0.000325 | 0.003135 | 0.010557 | 122.012 | 121.9792 | 0.21308 | 0.18035
3165.625 | 122.1313 | -0.064087 | 121.9482 | 0.27294 | 0.12432 | 0.14825 | 0.16728 | 0.16445 | 0.13137 | 0.005955 | 121.9229 | 121.9215 | 0.14686 | 0.14548 | -0.070797 | -0.036295 | -0.042641 | -0.030641 | 0.33703 | 0.1884 | 0.21234 | 0.23137 | 0.22854 | 0.19545 | 0.070042 | 121.9686 | 121.9673 | 0.19264 | 0.19126 | -0.025021 | 0.009481 | 0.003135 | 0.015135 | 121.9937 | 121.9655 | 0.21766 | 0.1895
3167.3906 | 122.0352 | -0.1236 | 121.9803 | 0.23173 | 0.17011 | 0.19862 | 0.20391 | 0.18734 | 0.13595 | 0.015112 | 121.932 | 121.9261 | 0.14686 | 0.14548 | -0.070797 | -0.045451 | -0.038063 | -0.026063 | 0.35533 | 0.2937 | 0.32221 | 0.3275 | 0.31093 | 0.25954 | 0.13871 | 121.9778 | 121.9719 | 0.19264 | 0.19126 | -0.025021 | 0.000325 | 0.007713 | 0.019713 | 122.0028 | 121.9701 | 0.21766 | 0.18493
3169.0938 | 122.0535 | -0.11902 | 121.9711 | 0.25462 | 0.193 | 0.23982 | 0.24511 | 0.2148 | 0.1451 | 0.038003 | 121.9229 | 121.917 | 0.14686 | 0.1409 | -0.079953 | -0.036295 | -0.038063 | -0.026063 | 0.37364 | 0.31202 | 0.35884 | 0.36413 | 0.33382 | 0.26412 | 0.15702 | 121.9686 | 121.9627 | 0.19264 | 0.18668 | -0.034177 | 0.009481 | 0.007713 | 0.019713 | 122.0028 | 121.9609 | 0.22682 | 0.18493
3170.8594 | 122.0673 | -0.10529 | 121.9574 | 0.20426 | 0.087686 | 0.10247 | 0.094024 | 0.11867 | 0.12679 | -0.012357 | 121.9275 | 121.9215 | 0.12855 | 0.12259 | -0.079953 | -0.045451 | -0.042641 | -0.035219 | 0.30955 | 0.19297 | 0.20775 | 0.19931 | 0.22395 | 0.23207 | 0.092929 | 121.9732 | 121.9673 | 0.17433 | 0.16836 | -0.034177 | 0.000325 | 0.003135 | 0.010557 | 122.0074 | 121.9701 | 0.2085 | 0.17119
3172.5625 | 122.1313 | -0.073242 | 121.9345 | 0.20426 | 0.11058 | 0.12078 | 0.10318 | 0.12325 | 0.11763 | -0.012357 | 121.9229 | 121.9215 | 0.14229 | 0.13632 | -0.070797 | -0.036295 | -0.04722 | -0.026063 | 0.2775 | 0.18382 | 0.19402 | 0.17642 | 0.19649 | 0.19087 | 0.060885 | 121.9686 | 121.9673 | 0.18806 | 0.1821 | -0.025021 | 0.009481 | -0.001444 | 0.019713 | 121.9937 | 121.9701 | 0.21308 | 0.18951
3174.3281 | 122.0444 | -0.11444 | 121.9757 | 0.218 | 0.13347 | 0.14825 | 0.1215 | 0.14614 | 0.13137 | 0.001377 | 121.9183 | 121.917 | 0.1606 | 0.1638 | -0.075375 | -0.045451 | -0.042641 | -0.035219 | 0.33244 | 0.24791 | 0.26269 | 0.23594 | 0.26058 | 0.24581 | 0.11582 | 121.9641 | 121.9627 | 0.20637 | 0.20957 | -0.029599 | 0.000325 | 0.003135 | 0.010557 | 121.9937 | 121.9609 | 0.23597 | 0.20324
3176.0938 | 122.1268 | -0.091553 | 121.907 | 0.23173 | 0.069371 | 0.084151 | 0.084867 | 0.11867 | 0.13595 | 0.015112 | 121.9183 | 121.9124 | 0.11482 | 0.10885 | -0.075375 | -0.036295 | -0.042641 | -0.021484 | 0.32328 | 0.16092 | 0.1757 | 0.17642 | 0.21022 | 0.2275 | 0.10666 | 121.9641 | 121.9582 | 0.16059 | 0.15463 | -0.029599 | 0.009481 | 0.003135 | 0.024292 | 121.9937 | 121.9609 | 0.19019 | 0.15746
3177.8594 | 122.0947 | -0.10529 | 121.9482 | 0.22715 | 0.064792 | 0.074994 | 0.07571 | 0.11409 | 0.14052 | 0.015112 | 121.9229 | 121.9124 | 0.10108 | 0.095112 | -0.070797 | -0.040873 | -0.042641 | -0.026063 | 0.33244 | 0.17008 | 0.18028 | 0.181 | 0.21938 | 0.24581 | 0.1204 | 121.9686 | 121.9582 | 0.14686 | 0.14089 | -0.025021 | 0.004903 | 0.003135 | 0.019713 | 121.9937 | 121.9655 | 0.17188 | 0.14372
3179.6406 | 122.0123 | -0.10529 | 121.9666 | 0.19968 | 0.037319 | 0.029208 | 0.043661 | 0.0912 | 0.12221 | -0.026092 | 121.9183 | 121.9078 | 0.055298 | 0.049322 | -0.066219 | -0.045451 | -0.051798 | -0.026063 | 0.30497 | 0.14261 | 0.13449 | 0.14895 | 0.19649 | 0.2275 | 0.079194 | 121.9641 | 121.9536 | 0.10107 | 0.095098 | -0.020443 | 0.000325 | -0.006022 | 0.019713 | 121.9845 | 121.9701 | 0.12152 | 0.1071
3181.4062 | 122.0123 | -0.10986 | 121.962 | 0.18137 | 0.023583 | 0.020051 | 0.034504 | 0.086622 | 0.10848 | -0.03067 | 121.9229 | 121.9078 | 0.041563 | 0.035585 | -0.079953 | -0.040873 | -0.04722 | -0.030641 | 0.29123 | 0.13345 | 0.12991 | 0.14437 | 0.19649 | 0.21834 | 0.079193 | 121.9686 | 121.9536 | 0.087339 | 0.081361 | -0.034177 | 0.004903 | -0.001444 | 0.015135 | 122.0028 | 121.9701 | 0.12152 | 0.088783
3183.1094 | 122.0901 | -0.10071 | 121.9666 | 0.18137 | 0.019004 | 0.020051 | 0.029925 | 0.082044 | 0.1039 | -0.035248 | 121.9137 | 121.9032 | 0.032407 | 0.031006 | -0.070797 | -0.036295 | -0.042641 | -0.016906 | 0.28208 | 0.11971 | 0.12076 | 0.13063 | 0.18275 | 0.2046 | 0.06546 | 121.9595 | 121.949 | 0.078183 | 0.076782 | -0.025021 | 0.009481 | 0.003135 | 0.02887 | 121.9845 | 121.9564 | 0.1032 | 0.075048
3184.875 | 122.0169 | -0.13733 | 121.9437 | 0.18137 | 0.014425 | 0.015472 | 0.01619 | 0.072888 | 0.10848 | -0.035248 | 121.9091 | 121.9032 | 0.036985 | 0.021847 | -0.070797 | -0.036295 | -0.042641 | -0.021484 | 0.3187 | 0.15175 | 0.1528 | 0.15352 | 0.21022 | 0.2458 | 0.10208 | 121.9549 | 121.949 | 0.082761 | 0.067623 | -0.025021 | 0.009481 | 0.003135 | 0.024292 | 121.9799 | 121.9518 | 0.10778 | 0.079626
3186.5781 | 121.9849 | -0.1236 | 121.9666 | 0.18137 | 0.009846 | 0.006315 | 0.020768 | 0.072888 | 0.1039 | -0.03067 | 121.9183 | 121.9124 | 0.027829 | 0.017268 | -0.075375 | -0.045451 | -0.042641 | -0.026063 | 0.30497 | 0.13344 | 0.12991 | 0.14436 | 0.19648 | 0.22749 | 0.092926 | 121.9641 | 121.9582 | 0.073605 | 0.063044 | -0.029599 | 0.000325 | 0.003135 | 0.019713 | 121.9937 | 121.9609 | 0.1032 | 0.07047
3188.3438 | 122.0901 | -0.086975 | 121.9254 | 0.18137 | 0.019004 | 0.010893 | 0.011611 | 0.063733 | 0.1039 | -0.039826 | 121.9091 | 121.9124 | 0.032407 | 0.017268 | -0.070797 | -0.036295 | -0.051798 | -0.021484 | 0.26835 | 0.10598 | 0.097868 | 0.098586 | 0.15071 | 0.19087 | 0.047149 | 121.9549 | 121.9582 | 0.078183 | 0.063044 | -0.025021 | 0.009481 | -0.006022 | 0.024292 | 121.9799 | 121.9609 | 0.1032 | 0.084205
3190.0469 | 122.0261 | -0.11444 | 121.9345 | 0.18595 | 0.019004 | 0.006315 | 0.011611 | 0.072888 | 0.10848 | -0.039826 | 121.9091 | 121.9078 | 0.032407 | 0.026427 | -0.079953 | -0.031717 | -0.038063 | -0.030641 | 0.30039 | 0.13345 | 0.12076 | 0.12605 | 0.18733 | 0.22292 | 0.074615 | 121.9549 | 121.9536 | 0.078183 | 0.072203 | -0.034177 | 0.014059 | 0.007713 | 0.015135 | 121.9891 | 121.9472 | 0.11236 | 0.07047
3191.8125 | 121.994 | -0.11902 | 121.9528 | 0.17679 | 0.014425 | 0.010893 | 0.011611 | 0.059155 | 0.1039 | -0.039826 | 121.9137 | 121.8986 | 0.027829 | 0.017268 | -0.079953 | -0.036295 | -0.04722 | -0.021484 | 0.29581 | 0.13344 | 0.12991 | 0.13063 | 0.17817 | 0.22292 | 0.079193 | 121.9595 | 121.9444 | 0.073605 | 0.063044 | -0.034177 | 0.009481 | -0.001444 | 0.024292 | 121.9937 | 121.9609 | 0.10778 | 0.075049
3193.5781 | 122.1176 | -0.064087 | 121.9254 | 0.18137 | 0.019004 | -0.002842 | 0.011611 | 0.059155 | 0.1039 | -0.03067 | 121.9046 | 121.9032 | 0.036985 | 0.031006 | -0.079953 | -0.045451 | -0.04722 | -0.021484 | 0.24546 | 0.083091 | 0.061245 | 0.075698 | 0.12324 | 0.16798 | 0.033417 | 121.9503 | 121.949 | 0.082761 | 0.076782 | -0.034177 | 0.000325 | -0.001444 | 0.024292 | 121.9845 | 121.9518 | 0.11694 | 0.084205
3195.2812 | 121.994 | -0.12817 | 121.9666 | 0.18137 | 0.014425 | 0.010893 | 0.01619 | 0.063733 | 0.11305 | -0.035248 | 121.9046 | 121.8986 | 0.032407 | 0.026427 | -0.070797 | -0.040873 | -0.038063 | -0.026063 | 0.30954 | 0.1426 | 0.13907 | 0.14436 | 0.19191 | 0.24123 | 0.092926 | 121.9503 | 121.9444 | 0.078183 | 0.072203 | -0.025021 | 0.004903 | 0.007713 | 0.019713 | 121.9754 | 121.9426 | 0.1032 | 0.07047
3197.0469 | 122.1176 | -0.073242 | 121.9116 | 0.18137 | 0.019004 | 0.010893 | 0.01619 | 0.06831 | 0.1039 | -0.039826 | 121.9046 | 121.8941 | 0.036985 | 0.026427 | -0.070797 | -0.036295 | -0.042641 | -0.021484 | 0.25461 | 0.092246 | 0.084135 | 0.089432 | 0.14155 | 0.17714 | 0.033416 | 121.9503 | 121.9398 | 0.082761 | 0.072203 | -0.025021 | 0.009481 | 0.003135 | 0.024292 | 121.9754 | 121.9472 | 0.10778 | 0.079626
3198.8125 | 122.0673 | -0.091553 | 121.9299 | 0.18595 | 0.023583 | 0.010893 | 0.020768 | 0.063733 | 0.12221 | -0.026092 | 121.9 | 121.8849 | 0.036985 | 0.031006 | -0.061641 | -0.036295 | -0.042641 | -0.021484 | 0.2775 | 0.11514 | 0.10245 | 0.11232 | 0.15529 | 0.21376 | 0.065461 | 121.9458 | 121.9307 | 0.082761 | 0.076782 | -0.015865 | 0.009481 | 0.003135 | 0.024292 | 121.9616 | 121.9426 | 0.098626 | 0.079626
3200.5156 | 121.843 | -1.6983 | 119.9615 | 0.18137 | 0.014425 | 0.020051 | 0.011611 | 0.063733 | 0.11305 | -0.03067 | 119.9907 | 119.9252 | 0.041563 | 0.040164 | 1.1607 | 1.1998 | 1.1844 | 1.1963 | 1.8797 | 1.7127 | 1.7184 | 1.7099 | 1.762 | 1.8114 | 1.6676 | 120.0365 | 119.971 | 0.087339 | 0.08594 | 1.2065 | 1.2456 | 1.2301 | 1.2421 | 118.83 | 118.8064 | -1.1192 | -1.1428
3202.2812 | 122.0352 | -0.041199 | 121.8246 | 0.14474 | -0.013048 | -0.016578 | -0.025017 | 0.031687 | 0.076426 | -0.058139 | 0.12574 | 0.20284 | 0.009515 | -0.001048 | -0.084531 | -0.059185 | -0.051798 | -0.039797 | 0.18594 | 0.028151 | 0.024621 | 0.016182 | 0.072886 | 0.11762 | -0.01694 | 0.17152 | 0.24862 | 0.055291 | 0.044728 | -0.038755 | -0.013409 | -0.006022 | 0.005979 | 0.21027 | 0.17754 | 0.094046 | 0.061313
3203.9844 | 122.0581 | -0.050354 | 121.8475 | 0.14932 | -0.017627 | -0.016578 | -0.020438 | 0.022531 | 0.067269 | -0.067295 | 0.10285 | 0.17537 | 0.009515 | -0.005627 | -0.084531 | -0.059185 | -0.042641 | -0.039797 | 0.19968 | 0.032727 | 0.033776 | 0.029916 | 0.072885 | 0.11762 | -0.016941 | 0.14863 | 0.22115 | 0.055291 | 0.040149 | -0.038755 | -0.013409 | 0.003135 | 0.005979 | 0.18738 | 0.14549 | 0.094046 | 0.052156
3205.75 | 121.9208 | -0.10986 | 121.9162 | 0.1539 | -0.013048 | -0.016578 | -0.025017 | 0.027109 | 0.076426 | -0.053561 | 0.093694 | 0.17537 | 0.004937 | 0.00811 | -0.08911 | -0.054607 | -0.051798 | -0.044375 | 0.26376 | 0.096815 | 0.093285 | 0.084846 | 0.13697 | 0.18629 | 0.056302 | 0.13947 | 0.22115 | 0.050713 | 0.053886 | -0.043334 | -0.008831 | -0.006022 | 0.001401 | 0.1828 | 0.14549 | 0.094047 | 0.056735
3207.5156 | 122.0444 | -0.059509 | 121.8704 | 0.14017 | -0.017627 | -0.021157 | -0.025017 | 0.027109 | 0.076426 | -0.062717 | 0.084537 | 0.17079 | 0.009515 | -0.001048 | -0.084531 | -0.063763 | -0.051798 | -0.039797 | 0.19967 | 0.041882 | 0.038352 | 0.034492 | 0.086618 | 0.13594 | -0.003208 | 0.13031 | 0.21657 | 0.055291 | 0.044728 | -0.038755 | -0.017987 | -0.006022 | 0.005979 | 0.16907 | 0.13633 | 0.094046 | 0.061313
3209.2969 | 122.0673 | -0.054932 | 121.8842 | 0.14932 | -0.017627 | -0.021157 | -0.01586 | 0.027109 | 0.076426 | -0.062717 | 0.098273 | 0.17537 | 0.004937 | -0.001048 | -0.084531 | -0.054607 | -0.04722 | -0.035219 | 0.20425 | 0.037305 | 0.033775 | 0.039072 | 0.082041 | 0.13136 | -0.007785 | 0.14405 | 0.22115 | 0.050713 | 0.044728 | -0.038755 | -0.008831 | -0.001444 | 0.010557 | 0.1828 | 0.14549 | 0.089468 | 0.052157
3211 | 122.0581 | -0.064087 | 121.8842 | 0.14932 | -0.008469 | -0.012 | -0.020438 | 0.027109 | 0.067269 | -0.062717 | 0.10743 | 0.17995 | 0.004937 | 0.003531 | -0.079953 | -0.059185 | -0.056376 | -0.035219 | 0.21341 | 0.055618 | 0.052087 | 0.043649 | 0.091196 | 0.13136 | 0.00137 | 0.15321 | 0.22573 | 0.050713 | 0.049307 | -0.034177 | -0.013409 | -0.0106 | 0.010557 | 0.18738 | 0.16381 | 0.08489 | 0.061313
3212.7656 | 121.9711 | -0.09613 | 121.8979 | 0.14932 | -0.013048 | -0.016578 | -0.025017 | 0.031687 | 0.081005 | -0.062717 | 0.079959 | 0.16164 | 0.009515 | 0.003531 | -0.084531 | -0.050029 | -0.04722 | -0.030641 | 0.24545 | 0.083082 | 0.079552 | 0.071113 | 0.12782 | 0.17713 | 0.033413 | 0.12573 | 0.20741 | 0.055291 | 0.049307 | -0.038755 | -0.004253 | -0.001444 | 0.015135 | 0.16449 | 0.12718 | 0.094046 | 0.056735
3214.5312 | 121.9803 | -0.10529 | 121.9254 | 0.14017 | -0.00389 | -0.012 | -0.029595 | 0.027109 | 0.081005 | -0.058139 | 0.07538 | 0.16164 | 0.004937 | 0.00811 | -0.079953 | -0.050029 | -0.051798 | -0.035219 | 0.24545 | 0.1014 | 0.093286 | 0.075691 | 0.1324 | 0.18629 | 0.047147 | 0.12116 | 0.20741 | 0.050713 | 0.053886 | -0.034177 | -0.004253 | -0.006022 | 0.010557 | 0.15533 | 0.12718 | 0.08489 | 0.056735
3216.25 | 122.0718 | -0.054932 | 121.9025 | 0.1539 | -0.013048 | -0.012 | -0.020438 | 0.027109 | 0.076426 | -0.062717 | 0.070802 | 0.16164 | 0.014094 | 0.003531 | -0.08911 | -0.054607 | -0.051798 | -0.030641 | 0.20883 | 0.041884 | 0.042932 | 0.034494 | 0.082041 | 0.13136 | -0.007785 | 0.11658 | 0.20741 | 0.05987 | 0.049307 | -0.043334 | -0.008831 | -0.006022 | 0.015135 | 0.15991 | 0.1226 | 0.1032 | 0.065892
3218.0156 | 122.081 | -0.054932 | 121.8842 | 0.1539 | -0.017627 | -0.016578 | -0.020438 | 0.027109 | 0.076426 | -0.062717 | 0.070802 | 0.15248 | 0.009515 | 0.003531 | -0.08911 | -0.050029 | -0.04722 | -0.039797 | 0.20883 | 0.037305 | 0.038354 | 0.034494 | 0.082041 | 0.13136 | -0.007785 | 0.11658 | 0.19825 | 0.055291 | 0.049307 | -0.043334 | -0.004253 | -0.001444 | 0.005979 | 0.15991 | 0.11802 | 0.098625 | 0.056735
3219.7812 | 122.0627 | -0.07782 | 121.9025 | 0.1539 | -0.013048 | -0.021157 | -0.020438 | 0.027109 | 0.071848 | -0.058139 | 0.070802 | 0.15248 | 0.009515 | 0.003531 | -0.08911 | -0.050029 | -0.051798 | -0.035219 | 0.23172 | 0.064772 | 0.056663 | 0.057382 | 0.10493 | 0.14967 | 0.019681 | 0.11658 | 0.19825 | 0.055291 | 0.049307 | -0.043334 | -0.004253 | -0.006022 | 0.010557 | 0.15991 | 0.1226 | 0.098625 | 0.061313
3221.4844 | 122.0261 | -0.068665 | 121.8796 | 0.1539 | -0.013048 | -0.012 | -0.020438 | 0.031687 | 0.076426 | -0.058139 | 0.066223 | 0.15248 | 0.000359 | 0.003531 | -0.08911 | -0.050029 | -0.051798 | -0.035219 | 0.22257 | 0.055617 | 0.056665 | 0.048227 | 0.10035 | 0.14509 | 0.010526 | 0.112 | 0.19825 | 0.046135 | 0.049307 | -0.043334 | -0.004253 | -0.006022 | 0.010557 | 0.15533 | 0.11802 | 0.089469 | 0.052157
3223.25 | 122.0169 | -0.11444 | 121.9528 | 0.14932 | -0.013048 | -0.016578 | -0.01586 | 0.031687 | 0.076426 | -0.058139 | 0.061645 | 0.15248 | 0.009515 | -0.010206 | -0.084531 | -0.050029 | -0.056376 | -0.035219 | 0.26376 | 0.10139 | 0.097863 | 0.098581 | 0.14613 | 0.19087 | 0.056302 | 0.10742 | 0.19825 | 0.055291 | 0.03557 | -0.038755 | -0.004253 | -0.0106 | 0.010557 | 0.14618 | 0.11802 | 0.094046 | 0.065891
3225.0156 | 121.9574 | -0.11444 | 121.9574 | 0.14474 | -0.013048 | -0.012 | -0.020438 | 0.031687 | 0.071848 | -0.058139 | 0.061645 | 0.1479 | 0.004937 | 0.003531 | -0.084531 | -0.054607 | -0.051798 | -0.035219 | 0.25918 | 0.10139 | 0.10244 | 0.094003 | 0.14613 | 0.18629 | 0.056302 | 0.10742 | 0.19367 | 0.050713 | 0.049307 | -0.038755 | -0.008831 | -0.006022 | 0.010557 | 0.14618 | 0.11344 | 0.089468 | 0.056735
3226.7344 | 122.1268 | -0.050354 | 121.9116 | 0.14017 | -0.017627 | -0.012 | -0.025017 | 0.031687 | 0.071848 | -0.067295 | 0.066223 | 0.1479 | 0.009515 | 0.00811 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.19052 | 0.032727 | 0.038354 | 0.025337 | 0.082041 | 0.1222 | -0.016941 | 0.112 | 0.19367 | 0.055291 | 0.053886 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.15075 | 0.11802 | 0.094046 | 0.061313
3228.4844 | 122.0078 | -0.10071 | 121.9574 | 0.14474 | -0.008469 | -0.007421 | -0.01586 | 0.031687 | 0.081005 | -0.058139 | 0.057066 | 0.1479 | 0.004937 | -0.005627 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.24545 | 0.092239 | 0.093287 | 0.084848 | 0.1324 | 0.18171 | 0.042569 | 0.10284 | 0.19367 | 0.050713 | 0.040149 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.1416 | 0.10886 | 0.089468 | 0.056735
3230.25 | 121.9574 | -0.086975 | 121.9437 | 0.14932 | -0.013048 | -0.012 | -0.020438 | 0.022531 | 0.081005 | -0.058139 | 0.066223 | 0.1479 | 0.009515 | 0.003531 | -0.075375 | -0.054607 | -0.04722 | -0.035219 | 0.2363 | 0.073927 | 0.074975 | 0.066537 | 0.10951 | 0.16798 | 0.028836 | 0.112 | 0.19367 | 0.055291 | 0.049307 | -0.029599 | -0.008831 | -0.001444 | 0.010557 | 0.1416 | 0.11344 | 0.08489 | 0.056735
3231.9531 | 121.9757 | -0.10986 | 121.9757 | 0.15848 | -0.008469 | -0.016578 | -0.020438 | 0.027109 | 0.081005 | -0.053561 | 0.061645 | 0.1479 | 0.009515 | -0.001048 | -0.079953 | -0.050029 | -0.04722 | -0.035219 | 0.26834 | 0.10139 | 0.093285 | 0.089425 | 0.13697 | 0.19087 | 0.056302 | 0.10742 | 0.19367 | 0.055291 | 0.044728 | -0.034177 | -0.004253 | -0.001444 | 0.010557 | 0.1416 | 0.10886 | 0.089468 | 0.056735
3233.7188 | 122.0718 | -0.064087 | 121.9162 | 0.1539 | -0.013048 | -0.016578 | -0.020438 | 0.031687 | 0.076426 | -0.062717 | 0.057066 | 0.13874 | 0.009515 | -0.005627 | -0.075375 | -0.045451 | -0.051798 | -0.044375 | 0.21799 | 0.051039 | 0.047509 | 0.043649 | 0.095774 | 0.14051 | 0.00137 | 0.10284 | 0.18452 | 0.055291 | 0.040149 | -0.029599 | 0.000325 | -0.006022 | 0.001401 | 0.13244 | 0.10886 | 0.08489 | 0.061313
3235.4219 | 122.113 | -0.064087 | 121.9528 | 0.14932 | -0.013048 | -0.012 | -0.01586 | 0.031687 | 0.076426 | -0.067295 | 0.052488 | 0.13874 | 0.004937 | -0.001048 | -0.079953 | -0.050029 | -0.051798 | -0.035219 | 0.21341 | 0.051039 | 0.052087 | 0.048227 | 0.095774 | 0.14051 | -0.003208 | 0.098264 | 0.18452 | 0.050713 | 0.044728 | -0.034177 | -0.004253 | -0.006022 | 0.010557 | 0.13244 | 0.10429 | 0.08489 | 0.056735
3237.2031 | 122.0673 | -0.082397 | 121.9437 | 0.14932 | -0.008469 | -0.012 | -0.025017 | 0.027109 | 0.081005 | -0.062717 | 0.052488 | 0.14332 | 0.004937 | 0.003531 | -0.079953 | -0.054607 | -0.04722 | -0.026063 | 0.23172 | 0.073928 | 0.070397 | 0.05738 | 0.10951 | 0.1634 | 0.01968 | 0.098264 | 0.1891 | 0.050713 | 0.049307 | -0.034177 | -0.008831 | -0.001444 | 0.019713 | 0.13244 | 0.099708 | 0.08489 | 0.052157
3238.9531 | 122.0215 | -0.091553 | 121.9482 | 0.14932 | -0.013048 | -0.012 | -0.020438 | 0.027109 | 0.085583 | -0.053561 | 0.052488 | 0.13874 | 0.000359 | -0.005627 | -0.079953 | -0.050029 | -0.042641 | -0.035219 | 0.24087 | 0.078505 | 0.079553 | 0.071115 | 0.11866 | 0.17714 | 0.037992 | 0.098264 | 0.18452 | 0.046135 | 0.040149 | -0.034177 | -0.004253 | 0.003135 | 0.010557 | 0.13244 | 0.095129 | 0.080312 | 0.043
3240.7188 | 122.1176 | -0.045776 | 121.9162 | 0.14474 | -0.013048 | -0.012 | -0.020438 | 0.027109 | 0.076426 | -0.058139 | 0.057066 | 0.14332 | 0.004937 | 0.003531 | -0.075375 | -0.045451 | -0.04722 | -0.026063 | 0.19052 | 0.032728 | 0.033776 | 0.025338 | 0.072885 | 0.1222 | -0.012363 | 0.10284 | 0.1891 | 0.050713 | 0.049307 | -0.029599 | 0.000325 | -0.001444 | 0.019713 | 0.13244 | 0.10429 | 0.080312 | 0.052157
3242.4375 | 122.1085 | -0.059509 | 121.9437 | 0.14932 | -0.008469 | -0.016578 | -0.025017 | 0.027109 | 0.071848 | -0.067295 | 0.047909 | 0.14332 | 0.004937 | -0.001048 | -0.079953 | -0.050029 | -0.051798 | -0.039797 | 0.20883 | 0.05104 | 0.042931 | 0.034492 | 0.086618 | 0.13136 | -0.007786 | 0.093685 | 0.1891 | 0.050713 | 0.044728 | -0.034177 | -0.004253 | -0.006022 | 0.005979 | 0.12786 | 0.099707 | 0.08489 | 0.056735
3244.2031 | 121.9894 | -0.10529 | 121.9482 | 0.14932 | -0.017627 | -0.021157 | -0.025017 | 0.031687 | 0.081005 | -0.067295 | 0.052488 | 0.14332 | 0.009515 | 0.003531 | -0.084531 | -0.059185 | -0.04722 | -0.026063 | 0.25461 | 0.087659 | 0.084129 | 0.080269 | 0.13697 | 0.18629 | 0.037991 | 0.098264 | 0.1891 | 0.055291 | 0.049307 | -0.038755 | -0.013409 | -0.001444 | 0.019713 | 0.13702 | 0.099708 | 0.094046 | 0.056735
3245.9688 | 122.0535 | -0.091553 | 121.9208 | 0.14474 | -0.017627 | -0.016578 | -0.020438 | 0.031687 | 0.071848 | -0.062717 | 0.047909 | 0.13874 | 0.000359 | 0.003531 | -0.075375 | -0.045451 | -0.042641 | -0.035219 | 0.2363 | 0.073926 | 0.074975 | 0.071115 | 0.12324 | 0.1634 | 0.028836 | 0.093685 | 0.18452 | 0.046135 | 0.049307 | -0.029599 | 0.000325 | 0.003135 | 0.010557 | 0.12328 | 0.09055 | 0.075734 | 0.043
3247.75 | 122.0078 | -0.10071 | 121.9437 | 0.1539 | -0.008469 | -0.012 | -0.020438 | 0.022531 | 0.076426 | -0.062717 | 0.052488 | 0.13874 | 0.009515 | -0.010206 | -0.079953 | -0.054607 | -0.04722 | -0.044375 | 0.25461 | 0.092239 | 0.088708 | 0.08027 | 0.12324 | 0.17713 | 0.037991 | 0.098264 | 0.18452 | 0.055291 | 0.03557 | -0.034177 | -0.008831 | -0.001444 | 0.001401 | 0.13244 | 0.099708 | 0.089468 | 0.056735
3249.4531 | 122.0947 | -0.07782 | 121.962 | 0.14017 | -0.008469 | -0.012 | -0.025017 | 0.022531 | 0.081005 | -0.062717 | 0.043331 | 0.13416 | 0.014094 | -0.010206 | -0.079953 | -0.045451 | -0.04722 | -0.044375 | 0.21799 | 0.069351 | 0.06582 | 0.052803 | 0.10035 | 0.15882 | 0.015103 | 0.089107 | 0.17994 | 0.05987 | 0.03557 | -0.034177 | 0.000325 | -0.001444 | 0.001401 | 0.12328 | 0.090551 | 0.094047 | 0.061314
3251.2188 | 122.0215 | -0.10529 | 121.9208 | 0.14474 | -0.008469 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.071874 | 0.043331 | 0.13874 | 0.000359 | -0.010206 | -0.084531 | -0.050029 | -0.04722 | -0.035219 | 0.25003 | 0.096817 | 0.079551 | 0.080269 | 0.12782 | 0.17713 | 0.033412 | 0.089107 | 0.18452 | 0.046135 | 0.03557 | -0.038755 | -0.004253 | -0.001444 | 0.010557 | 0.12786 | 0.090551 | 0.08489 | 0.047579
3253 | 122.0032 | -0.12817 | 121.9574 | 0.14474 | -0.017627 | -0.021157 | -0.020438 | 0.027109 | 0.076426 | -0.067295 | 0.047909 | 0.13874 | 0.000359 | -0.001048 | -0.084531 | -0.050029 | -0.04722 | -0.030641 | 0.27292 | 0.11055 | 0.10702 | 0.10774 | 0.15528 | 0.2046 | 0.060879 | 0.093685 | 0.18452 | 0.046135 | 0.044728 | -0.038755 | -0.004253 | -0.001444 | 0.015135 | 0.13244 | 0.095129 | 0.08489 | 0.047579
3254.7031 | 121.9757 | -0.11902 | 121.9711 | 0.14932 | -0.013048 | -0.016578 | -0.025017 | 0.031687 | 0.081005 | -0.062717 | 0.038752 | 0.13416 | 0.004937 | -0.005627 | -0.08911 | -0.054607 | -0.04722 | -0.030641 | 0.26834 | 0.10597 | 0.10244 | 0.094002 | 0.15071 | 0.20002 | 0.056302 | 0.084528 | 0.17994 | 0.050713 | 0.040149 | -0.043334 | -0.008831 | -0.001444 | 0.015135 | 0.12786 | 0.085972 | 0.094047 | 0.052157
3256.4219 | 122.049 | -0.086975 | 121.9711 | 0.14474 | -0.017627 | -0.016578 | -0.020438 | 0.022531 | 0.076426 | -0.058139 | 0.043331 | 0.13416 | 0.000359 | -0.005627 | -0.084531 | -0.045451 | -0.04722 | -0.039797 | 0.23172 | 0.069348 | 0.070397 | 0.066537 | 0.10951 | 0.1634 | 0.028836 | 0.089107 | 0.17994 | 0.046135 | 0.040149 | -0.038755 | 0.000325 | -0.001444 | 0.005979 | 0.12786 | 0.090551 | 0.08489 | 0.047579
3258.1875 | 122.0718 | -0.073242 | 121.9528 | 0.14017 | -0.022205 | -0.016578 | -0.025017 | 0.017953 | 0.067269 | -0.071874 | 0.043331 | 0.13874 | 0.000359 | -0.005627 | -0.08911 | -0.050029 | -0.051798 | -0.030641 | 0.21341 | 0.051037 | 0.056664 | 0.048225 | 0.091195 | 0.14051 | 0.001368 | 0.089107 | 0.18452 | 0.046135 | 0.040149 | -0.043334 | -0.004253 | -0.006022 | 0.015135 | 0.13244 | 0.095129 | 0.089469 | 0.052157
3259.9531 | 121.9757 | -0.11444 | 121.9849 | 0.14932 | -0.013048 | -0.012 | -0.025017 | 0.031687 | 0.071848 | -0.062717 | 0.043331 | 0.13874 | 0.000359 | -0.005627 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.26376 | 0.10139 | 0.10244 | 0.089424 | 0.14613 | 0.18629 | 0.051724 | 0.089107 | 0.18452 | 0.046135 | 0.040149 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.12786 | 0.095129 | 0.08489 | 0.052157
3261.6562 | 122.1085 | -0.068665 | 121.9208 | 0.14932 | -0.022205 | -0.016578 | -0.034174 | 0.022531 | 0.076426 | -0.062717 | 0.034174 | 0.12958 | 0.000359 | -0.005627 | -0.084531 | -0.050029 | -0.04722 | -0.039797 | 0.21799 | 0.04646 | 0.052087 | 0.034491 | 0.091196 | 0.14509 | 0.005948 | 0.07995 | 0.17536 | 0.046135 | 0.040149 | -0.038755 | -0.004253 | -0.001444 | 0.005979 | 0.11871 | 0.081394 | 0.08489 | 0.047579
3263.4219 | 122.081 | -0.073242 | 121.9299 | 0.14474 | -0.017627 | -0.021157 | -0.025017 | 0.022531 | 0.067269 | -0.067295 | 0.034174 | 0.12958 | 0.000359 | -0.005627 | -0.084531 | -0.054607 | -0.04722 | -0.035219 | 0.21799 | 0.055615 | 0.052085 | 0.048225 | 0.095773 | 0.14051 | 0.005947 | 0.07995 | 0.17536 | 0.046135 | 0.040149 | -0.038755 | -0.008831 | -0.001444 | 0.010557 | 0.11871 | 0.081394 | 0.08489 | 0.047579
3265.125 | 122.0718 | -0.068665 | 121.9254 | 0.14932 | -0.013048 | -0.016578 | -0.020438 | 0.022531 | 0.076426 | -0.062717 | 0.038752 | 0.13416 | 0.000359 | -0.005627 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.21799 | 0.055617 | 0.052087 | 0.048227 | 0.091196 | 0.14509 | 0.005948 | 0.084528 | 0.17994 | 0.046135 | 0.040149 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.12328 | 0.09055 | 0.08489 | 0.052157
3266.8906 | 121.9986 | -0.11902 | 121.994 | 0.14017 | -0.013048 | -0.016578 | -0.025017 | 0.022531 | 0.085583 | -0.062717 | 0.034174 | 0.12958 | 0.004937 | -0.005627 | -0.079953 | -0.054607 | -0.042641 | -0.039797 | 0.25918 | 0.10597 | 0.10244 | 0.094002 | 0.14155 | 0.2046 | 0.056302 | 0.07995 | 0.17536 | 0.050713 | 0.040149 | -0.034177 | -0.008831 | 0.003135 | 0.005979 | 0.11413 | 0.076815 | 0.08489 | 0.047578
3268.5938 | 122.081 | -0.07782 | 121.9345 | 0.14474 | -0.022205 | -0.021157 | -0.020438 | 0.017953 | 0.071848 | -0.067295 | 0.038752 | 0.13416 | -0.008798 | -0.001048 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.22256 | 0.055615 | 0.056663 | 0.057382 | 0.095773 | 0.14967 | 0.010525 | 0.084528 | 0.17994 | 0.036978 | 0.044728 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.12328 | 0.09055 | 0.075733 | 0.043
3270.3594 | 122.0581 | -0.073242 | 121.9803 | 0.14474 | -0.017627 | -0.007421 | -0.01586 | 0.036265 | 0.076426 | -0.058139 | 0.034174 | 0.12958 | 0.000359 | -0.005627 | -0.079953 | -0.040873 | -0.04722 | -0.030641 | 0.21799 | 0.055615 | 0.065821 | 0.057382 | 0.10951 | 0.14967 | 0.015103 | 0.07995 | 0.17536 | 0.046135 | 0.040149 | -0.034177 | 0.004903 | -0.001444 | 0.015135 | 0.11413 | 0.081394 | 0.080312 | 0.047579
3272.1406 | 121.9711 | -0.10529 | 121.9666 | 0.14932 | -0.008469 | -0.021157 | -0.020438 | 0.022531 | 0.076426 | -0.053561 | 0.034174 | 0.12501 | 0.004937 | -0.005627 | -0.084531 | -0.045451 | -0.04722 | -0.035219 | 0.25461 | 0.096817 | 0.084129 | 0.084848 | 0.12782 | 0.18171 | 0.051725 | 0.07995 | 0.17078 | 0.050713 | 0.040149 | -0.038755 | 0.000325 | -0.001444 | 0.010557 | 0.11871 | 0.081394 | 0.089468 | 0.052157
3273.8594 | 121.994 | -0.11444 | 121.9849 | 0.14932 | -0.008469 | -0.021157 | -0.025017 | 0.027109 | 0.076426 | -0.067295 | 0.043331 | 0.13416 | 0.004937 | -0.005627 | -0.075375 | -0.054607 | -0.051798 | -0.035219 | 0.26376 | 0.10597 | 0.093284 | 0.089424 | 0.14155 | 0.19087 | 0.047146 | 0.089107 | 0.17994 | 0.050713 | 0.040149 | -0.029599 | -0.008831 | -0.006022 | 0.010557 | 0.11871 | 0.095129 | 0.080312 | 0.056735
3275.625 | 122.0993 | -0.059509 | 121.9482 | 0.14017 | -0.013048 | -0.021157 | -0.025017 | 0.031687 | 0.071848 | -0.058139 | 0.034174 | 0.12958 | -0.004219 | -0.005627 | -0.075375 | -0.040873 | -0.060955 | -0.030641 | 0.19967 | 0.046461 | 0.038352 | 0.034492 | 0.091196 | 0.13136 | 0.00137 | 0.07995 | 0.17536 | 0.041557 | 0.040149 | -0.029599 | 0.004903 | -0.015179 | 0.015135 | 0.10955 | 0.095129 | 0.071156 | 0.056736
3277.3906 | 121.9803 | -0.11444 | 121.9894 | 0.14932 | -0.008469 | -0.021157 | -0.025017 | 0.027109 | 0.071848 | -0.058139 | 0.034174 | 0.13416 | 0.004937 | -0.005627 | -0.079953 | -0.050029 | -0.04722 | -0.035219 | 0.26376 | 0.10597 | 0.093284 | 0.089424 | 0.14155 | 0.18629 | 0.056302 | 0.07995 | 0.17994 | 0.050713 | 0.040149 | -0.034177 | -0.004253 | -0.001444 | 0.010557 | 0.11413 | 0.081394 | 0.08489 | 0.052157
3279.1562 | 121.9894 | -0.10071 | 121.9849 | 0.14474 | -0.013048 | -0.016578 | -0.029595 | 0.027109 | 0.076426 | -0.062717 | 0.038752 | 0.12958 | 0.009515 | -0.014785 | -0.084531 | -0.050029 | -0.04722 | -0.035219 | 0.24545 | 0.08766 | 0.08413 | 0.071113 | 0.12782 | 0.17713 | 0.037991 | 0.084528 | 0.17536 | 0.055291 | 0.030991 | -0.038755 | -0.004253 | -0.001444 | 0.010557 | 0.12328 | 0.085972 | 0.094046 | 0.056735
3280.8594 | 121.994 | -0.11444 | 121.994 | 0.14474 | -0.022205 | -0.016578 | -0.020438 | 0.027109 | 0.076426 | -0.062717 | 0.034174 | 0.13416 | 0.000359 | -0.001048 | -0.079953 | -0.050029 | -0.051798 | -0.026063 | 0.25918 | 0.092236 | 0.097863 | 0.094003 | 0.14155 | 0.19087 | 0.051724 | 0.07995 | 0.17994 | 0.046135 | 0.044728 | -0.034177 | -0.004253 | -0.006022 | 0.019713 | 0.11413 | 0.085972 | 0.080312 | 0.052157
3282.625 | 122.1176 | -0.082397 | 121.9574 | 0.14017 | -0.013048 | -0.016578 | -0.025017 | 0.027109 | 0.076426 | -0.062717 | 0.034174 | 0.12501 | 0.000359 | -0.014785 | -0.084531 | -0.054607 | -0.051798 | -0.030641 | 0.22256 | 0.069349 | 0.065819 | 0.05738 | 0.10951 | 0.15882 | 0.01968 | 0.07995 | 0.17078 | 0.046135 | 0.030991 | -0.038755 | -0.008831 | -0.006022 | 0.015135 | 0.11871 | 0.085972 | 0.08489 | 0.052157
3284.4062 | 122.1176 | -0.054932 | 121.9482 | 0.14932 | -0.008469 | -0.016578 | -0.025017 | 0.027109 | 0.067269 | -0.062717 | 0.043331 | 0.12501 | -0.008798 | -0.005627 | -0.08911 | -0.050029 | -0.04722 | -0.030641 | 0.20425 | 0.046463 | 0.038354 | 0.029915 | 0.082041 | 0.1222 | -0.007785 | 0.089107 | 0.17078 | 0.036978 | 0.040149 | -0.043334 | -0.004253 | -0.001444 | 0.015135 | 0.13244 | 0.090551 | 0.080312 | 0.038422
3286.125 | 122.0581 | -0.09613 | 121.9482 | 0.14932 | -0.013048 | -0.012 | -0.020438 | 0.022531 | 0.081005 | -0.067295 | 0.029595 | 0.12958 | 0.000359 | -0.010206 | -0.084531 | -0.045451 | -0.04722 | -0.035219 | 0.24545 | 0.083082 | 0.08413 | 0.075692 | 0.11866 | 0.17713 | 0.028835 | 0.075371 | 0.17536 | 0.046135 | 0.03557 | -0.038755 | 0.000325 | -0.001444 | 0.010557 | 0.11413 | 0.076815 | 0.08489 | 0.047579
3287.8906 | 122.081 | -0.068665 | 121.9391 | 0.14474 | -0.017627 | -0.016578 | -0.020438 | 0.013375 | 0.067269 | -0.071874 | 0.029595 | 0.12958 | 0.000359 | -0.005627 | -0.084531 | -0.045451 | -0.04722 | -0.035219 | 0.21341 | 0.051038 | 0.052087 | 0.048227 | 0.08204 | 0.13593 | -0.003209 | 0.075371 | 0.17536 | 0.046135 | 0.040149 | -0.038755 | 0.000325 | -0.001444 | 0.010557 | 0.11413 | 0.076815 | 0.08489 | 0.047579
3289.5938 | 122.0718 | -0.064087 | 121.9254 | 0.14474 | -0.017627 | -0.021157 | -0.029595 | 0.027109 | 0.076426 | -0.067295 | 0.029595 | 0.12501 | -0.004219 | -0.010206 | -0.079953 | -0.045451 | -0.042641 | -0.035219 | 0.20883 | 0.04646 | 0.04293 | 0.034492 | 0.091196 | 0.14051 | -0.003208 | 0.075371 | 0.17078 | 0.041557 | 0.03557 | -0.034177 | 0.000325 | 0.003135 | 0.010557 | 0.10955 | 0.072236 | 0.075734 | 0.038422
3291.3594 | 122.0215 | -0.10529 | 121.9849 | 0.14932 | -0.008469 | -0.012 | -0.029595 | 0.027109 | 0.076426 | -0.062717 | 0.034174 | 0.12501 | 0.000359 | -0.014785 | -0.079953 | -0.045451 | -0.051798 | -0.035219 | 0.25461 | 0.096817 | 0.093286 | 0.075691 | 0.1324 | 0.18171 | 0.042569 | 0.07995 | 0.17078 | 0.046135 | 0.030991 | -0.034177 | 0.000325 | -0.006022 | 0.010557 | 0.11413 | 0.085972 | 0.080312 | 0.052157
3293.1406 | 122.0032 | -0.1236 | 121.994 | 0.13559 | -0.008469 | -0.012 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | 0.034174 | 0.12958 | 0.000359 | -0.014785 | -0.084531 | -0.054607 | -0.051798 | -0.048953 | 0.25918 | 0.11513 | 0.1116 | 0.098579 | 0.14613 | 0.19544 | 0.060879 | 0.07995 | 0.17536 | 0.046135 | 0.030991 | -0.038755 | -0.008831 | -0.006022 | -0.003177 | 0.11871 | 0.085972 | 0.08489 | 0.052157
3294.9062 | 122.1313 | -0.054932 | 121.9437 | 0.14932 | -0.022205 | -0.016578 | -0.025017 | 0.027109 | 0.076426 | -0.062717 | 0.029595 | 0.12501 | -0.008798 | -0.005627 | -0.08911 | -0.050029 | -0.04722 | -0.030641 | 0.20425 | 0.032727 | 0.038354 | 0.029915 | 0.082041 | 0.13136 | -0.007785 | 0.075371 | 0.17078 | 0.036978 | 0.040149 | -0.043334 | -0.004253 | -0.001444 | 0.015135 | 0.1187 | 0.076815 | 0.080312 | 0.038422
3296.6094 | 122.113 | -0.082397 | 121.9345 | 0.14932 | -0.017627 | -0.012 | -0.025017 | 0.027109 | 0.071848 | -0.058139 | 0.034174 | 0.12958 | 0.000359 | -0.005627 | -0.079953 | -0.050029 | -0.051798 | -0.035219 | 0.23172 | 0.06477 | 0.070397 | 0.05738 | 0.10951 | 0.15424 | 0.024258 | 0.07995 | 0.17536 | 0.046135 | 0.040149 | -0.034177 | -0.004253 | -0.006022 | 0.010557 | 0.11413 | 0.085972 | 0.080312 | 0.052157
3298.375 | 122.0947 | -0.082397 | 121.9528 | 0.13559 | -0.013048 | -0.021157 | -0.020438 | 0.022531 | 0.085583 | -0.067295 | 0.029595 | 0.12501 | 0.000359 | -0.010206 | -0.084531 | -0.050029 | -0.042641 | -0.035219 | 0.21798 | 0.069349 | 0.06124 | 0.061959 | 0.10493 | 0.16798 | 0.015102 | 0.075371 | 0.17078 | 0.046135 | 0.03557 | -0.038755 | -0.004253 | 0.003135 | 0.010557 | 0.11413 | 0.072236 | 0.08489 | 0.043
3300.0781 | 122.1039 | -0.059509 | 121.9391 | 0.14932 | -0.013048 | -0.016578 | -0.029595 | 0.027109 | 0.071848 | -0.071874 | 0.034174 | 0.12501 | 0.000359 | -0.005627 | -0.079953 | -0.050029 | -0.051798 | -0.030641 | 0.20883 | 0.046461 | 0.042931 | 0.029914 | 0.086618 | 0.13136 | -0.012365 | 0.07995 | 0.17078 | 0.046135 | 0.040149 | -0.034177 | -0.004253 | -0.006022 | 0.015135 | 0.11413 | 0.085972 | 0.080312 | 0.052157
3301.8438 | 122.0261 | -0.10529 | 121.9528 | 0.14474 | -0.013048 | -0.016578 | -0.01586 | 0.027109 | 0.071848 | -0.067295 | 0.025017 | 0.12043 | -0.004219 | -0.010206 | -0.08911 | -0.045451 | -0.04722 | -0.035219 | 0.25003 | 0.092238 | 0.088708 | 0.089426 | 0.1324 | 0.17713 | 0.037991 | 0.070793 | 0.1662 | 0.041557 | 0.03557 | -0.043334 | 0.000325 | -0.001444 | 0.010557 | 0.11413 | 0.072237 | 0.084891 | 0.043001
3303.6094 | 122.1405 | -0.050354 | 121.9437 | 0.14932 | -0.013048 | -0.007421 | -0.029595 | 0.027109 | 0.071848 | -0.067295 | 0.025017 | 0.12501 | -0.004219 | -0.010206 | -0.084531 | -0.050029 | -0.056376 | -0.035219 | 0.19968 | 0.037306 | 0.042933 | 0.020759 | 0.077463 | 0.1222 | -0.016941 | 0.070793 | 0.17078 | 0.041557 | 0.03557 | -0.038755 | -0.004253 | -0.0106 | 0.010557 | 0.10955 | 0.081393 | 0.080312 | 0.052157
3305.3594 | 121.9986 | -0.13275 | 122.0032 | 0.14474 | -0.022205 | -0.016578 | -0.020438 | 0.022531 | 0.076426 | -0.062717 | 0.029595 | 0.12043 | -0.004219 | -0.014785 | -0.084531 | -0.050029 | -0.051798 | -0.044375 | 0.27749 | 0.11055 | 0.11617 | 0.11231 | 0.15528 | 0.20918 | 0.070034 | 0.075371 | 0.1662 | 0.041557 | 0.030991 | -0.038755 | -0.004253 | -0.006022 | 0.001401 | 0.11413 | 0.081393 | 0.080312 | 0.047579
3307.0625 | 122.0856 | -0.073242 | 121.962 | 0.14017 | -0.013048 | -0.016578 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | 0.029595 | 0.12501 | 0.000359 | -0.010206 | -0.093688 | -0.050029 | -0.051798 | -0.030641 | 0.21341 | 0.060194 | 0.056664 | 0.048225 | 0.095773 | 0.14051 | 0.010525 | 0.075371 | 0.17078 | 0.046135 | 0.03557 | -0.047912 | -0.004253 | -0.006022 | 0.015135 | 0.12328 | 0.081393 | 0.094047 | 0.052157
3308.8438 | 122.1176 | -0.064087 | 121.9437 | 0.14017 | -0.013048 | -0.012 | -0.025017 | 0.022531 | 0.067269 | -0.058139 | 0.034174 | 0.11585 | 0.000359 | -0.014785 | -0.079953 | -0.045451 | -0.04722 | -0.039797 | 0.20425 | 0.051039 | 0.052087 | 0.03907 | 0.086618 | 0.13136 | 0.005948 | 0.07995 | 0.16162 | 0.046135 | 0.030991 | -0.034177 | 0.000325 | -0.001444 | 0.005979 | 0.11413 | 0.081394 | 0.080312 | 0.047579
3310.5312 | 122.1359 | -0.045776 | 121.9345 | 0.14017 | -0.008469 | -0.012 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | 0.034174 | 0.12043 | -0.004219 | -0.010206 | -0.093688 | -0.050029 | -0.04722 | -0.039797 | 0.18594 | 0.037307 | 0.033776 | 0.020759 | 0.068307 | 0.11762 | -0.016941 | 0.07995 | 0.1662 | 0.041557 | 0.03557 | -0.047912 | -0.004253 | -0.001444 | 0.005979 | 0.12786 | 0.081394 | 0.089469 | 0.043001
3312.2969 | 122.0306 | -0.086975 | 121.9391 | 0.14932 | -0.013048 | -0.016578 | -0.029595 | 0.022531 | 0.081005 | -0.071874 | 0.025017 | 0.12501 | -0.004219 | -0.001048 | -0.084531 | -0.054607 | -0.051798 | -0.035219 | 0.2363 | 0.073927 | 0.070397 | 0.05738 | 0.10951 | 0.16798 | 0.015101 | 0.070793 | 0.17078 | 0.041557 | 0.044728 | -0.038755 | -0.008831 | -0.006022 | 0.010557 | 0.10955 | 0.076815 | 0.080312 | 0.047579
3314 | 122.0627 | -0.073242 | 121.9666 | 0.14474 | -0.008469 | -0.021157 | -0.029595 | 0.027109 | 0.085583 | -0.067295 | 0.025017 | 0.12043 | -0.004219 | -0.014785 | -0.079953 | -0.050029 | -0.04722 | -0.039797 | 0.21799 | 0.064773 | 0.052085 | 0.043647 | 0.10035 | 0.15882 | 0.005947 | 0.070793 | 0.1662 | 0.041557 | 0.030991 | -0.034177 | -0.004253 | -0.001444 | 0.005979 | 0.10497 | 0.072237 | 0.075734 | 0.043001
3315.7656 | 122.1313 | -0.041199 | 121.9345 | 0.14932 | -0.013048 | -0.021157 | -0.025017 | 0.027109 | 0.071848 | -0.071874 | 0.025017 | 0.11585 | 0.000359 | -0.014785 | -0.08911 | -0.050029 | -0.051798 | -0.035219 | 0.19052 | 0.028151 | 0.020042 | 0.016182 | 0.068308 | 0.11305 | -0.030675 | 0.070793 | 0.16162 | 0.046135 | 0.030991 | -0.043334 | -0.004253 | -0.006022 | 0.010557 | 0.11413 | 0.076815 | 0.089469 | 0.052157
3317.4844 | 121.9894 | -0.091553 | 121.9757 | 0.14474 | -0.00389 | -0.012 | -0.020438 | 0.031687 | 0.071848 | -0.067295 | 0.020438 | 0.11585 | 0.000359 | -0.019364 | -0.093688 | -0.045451 | -0.04722 | -0.035219 | 0.2363 | 0.087663 | 0.079553 | 0.071115 | 0.12324 | 0.1634 | 0.024258 | 0.066214 | 0.16162 | 0.046135 | 0.026412 | -0.047912 | 0.000325 | -0.001444 | 0.010557 | 0.11413 | 0.067658 | 0.094047 | 0.047579
3319.25 | 122.1085 | -0.082397 | 121.9437 | 0.13559 | -0.013048 | -0.021157 | -0.025017 | 0.027109 | 0.076426 | -0.067295 | 0.029595 | 0.12501 | -0.008798 | -0.010206 | -0.084531 | -0.045451 | -0.051798 | -0.035219 | 0.21798 | 0.069349 | 0.06124 | 0.05738 | 0.10951 | 0.15882 | 0.015102 | 0.075371 | 0.17078 | 0.036978 | 0.03557 | -0.038755 | 0.000325 | -0.006022 | 0.010557 | 0.11413 | 0.081393 | 0.075733 | 0.043
3320.9531 | 122.0718 | -0.10071 | 121.9482 | 0.14017 | -0.017627 | -0.016578 | -0.025017 | 0.031687 | 0.076426 | -0.062717 | 0.020438 | 0.12501 | -0.013376 | -0.010206 | -0.084531 | -0.050029 | -0.056376 | -0.039797 | 0.24087 | 0.083081 | 0.08413 | 0.075691 | 0.1324 | 0.17713 | 0.037991 | 0.066214 | 0.17078 | 0.0324 | 0.03557 | -0.038755 | -0.004253 | -0.0106 | 0.005979 | 0.10497 | 0.076814 | 0.071155 | 0.043
3322.7188 | 122.081 | -0.073242 | 121.9437 | 0.14474 | -0.013048 | -0.016578 | -0.025017 | 0.031687 | 0.081005 | -0.071874 | 0.025017 | 0.12043 | 0.000359 | -0.014785 | -0.084531 | -0.059185 | -0.051798 | -0.039797 | 0.21799 | 0.060194 | 0.056664 | 0.048225 | 0.10493 | 0.15425 | 0.001368 | 0.070793 | 0.1662 | 0.046135 | 0.030991 | -0.038755 | -0.013409 | -0.006022 | 0.005979 | 0.10955 | 0.076815 | 0.08489 | 0.052157
3324.4844 | 122.0947 | -0.07782 | 121.9391 | 0.13559 | -0.017627 | -0.016578 | -0.025017 | 0.027109 | 0.076426 | -0.067295 | 0.029595 | 0.11585 | 0.000359 | -0.001048 | -0.084531 | -0.050029 | -0.04722 | -0.039797 | 0.21341 | 0.060193 | 0.061242 | 0.052803 | 0.10493 | 0.15425 | 0.010525 | 0.075371 | 0.16162 | 0.046135 | 0.044728 | -0.038755 | -0.004253 | -0.001444 | 0.005979 | 0.11413 | 0.076815 | 0.08489 | 0.047579
3326.1875 | 122.0123 | -0.086975 | 121.9757 | 0.1539 | -0.013048 | -0.016578 | -0.020438 | 0.013375 | 0.081005 | -0.067295 | 0.01586 | 0.12501 | -0.008798 | -0.014785 | -0.084531 | -0.050029 | -0.04722 | -0.044375 | 0.24088 | 0.073927 | 0.070397 | 0.066537 | 0.10035 | 0.16798 | 0.01968 | 0.061636 | 0.17078 | 0.036978 | 0.030991 | -0.038755 | -0.004253 | -0.001444 | 0.001401 | 0.10039 | 0.06308 | 0.075733 | 0.038422
3327.9688 | 121.9986 | -0.11902 | 121.9894 | 0.14017 | -0.013048 | -0.021157 | -0.020438 | 0.022531 | 0.076426 | -0.067295 | 0.020438 | 0.12043 | 0.000359 | -0.014785 | -0.093688 | -0.050029 | -0.051798 | -0.035219 | 0.25918 | 0.10597 | 0.097862 | 0.098581 | 0.14155 | 0.19544 | 0.051724 | 0.066214 | 0.1662 | 0.046135 | 0.030991 | -0.047912 | -0.004253 | -0.006022 | 0.010557 | 0.11413 | 0.072236 | 0.094047 | 0.052157
3329.7344 | 122.0123 | -0.10529 | 121.9757 | 0.14932 | -0.008469 | -0.021157 | -0.025017 | 0.027109 | 0.081005 | -0.067295 | 0.025017 | 0.12501 | -0.004219 | -0.010206 | -0.079953 | -0.054607 | -0.04722 | -0.035219 | 0.25461 | 0.096817 | 0.084129 | 0.080269 | 0.1324 | 0.18629 | 0.037991 | 0.070793 | 0.17078 | 0.041557 | 0.03557 | -0.034177 | -0.008831 | -0.001444 | 0.010557 | 0.10497 | 0.072237 | 0.075734 | 0.043001
3331.4375 | 121.9986 | -0.10071 | 121.9803 | 0.14474 | -0.017627 | -0.016578 | -0.029595 | 0.022531 | 0.076426 | -0.067295 | 0.020438 | 0.12501 | 0.000359 | -0.014785 | -0.08911 | -0.054607 | -0.056376 | -0.035219 | 0.24545 | 0.083081 | 0.08413 | 0.071113 | 0.12324 | 0.17713 | 0.033413 | 0.066214 | 0.17078 | 0.046135 | 0.030991 | -0.043334 | -0.008831 | -0.0106 | 0.010557 | 0.10955 | 0.076814 | 0.089469 | 0.056735
3333.2031 | 122.0718 | -0.082397 | 121.9574 | 0.14932 | -0.013048 | -0.007421 | -0.020438 | 0.027109 | 0.076426 | -0.067295 | 0.01586 | 0.12501 | 0.004937 | -0.005627 | -0.084531 | -0.054607 | -0.042641 | -0.035219 | 0.23172 | 0.069349 | 0.074976 | 0.061959 | 0.10951 | 0.15882 | 0.015102 | 0.061636 | 0.17078 | 0.050713 | 0.040149 | -0.038755 | -0.008831 | 0.003135 | 0.010557 | 0.10039 | 0.058501 | 0.089468 | 0.047578
3334.9688 | 121.9986 | -0.1236 | 121.9986 | 0.14017 | -0.022205 | -0.016578 | -0.025017 | 0.027109 | 0.076426 | -0.062717 | 0.025017 | 0.11585 | 0.004937 | -0.005627 | -0.079953 | -0.050029 | -0.056376 | -0.035219 | 0.26376 | 0.10139 | 0.10702 | 0.098579 | 0.15071 | 0.20002 | 0.060879 | 0.070793 | 0.16162 | 0.050713 | 0.040149 | -0.034177 | -0.004253 | -0.0106 | 0.010557 | 0.10497 | 0.081393 | 0.08489 | 0.061313
3336.75 | 122.113 | -0.082397 | 121.9528 | 0.14017 | -0.017627 | -0.021157 | -0.025017 | 0.022531 | 0.076426 | -0.071874 | 0.011281 | 0.12043 | -0.013376 | -0.010206 | -0.08911 | -0.054607 | -0.042641 | -0.035219 | 0.22256 | 0.06477 | 0.06124 | 0.05738 | 0.10493 | 0.15882 | 0.010523 | 0.057057 | 0.1662 | 0.0324 | 0.03557 | -0.043334 | -0.008831 | 0.003135 | 0.010557 | 0.10039 | 0.053922 | 0.075734 | 0.029265
3338.4688 | 122.049 | -0.09613 | 121.9528 | 0.14474 | -0.017627 | -0.021157 | -0.025017 | 0.027109 | 0.081005 | -0.062717 | 0.01586 | 0.12043 | -0.013376 | -0.014785 | -0.084531 | -0.054607 | -0.056376 | -0.039797 | 0.24087 | 0.078503 | 0.074973 | 0.071113 | 0.12324 | 0.17713 | 0.033413 | 0.061636 | 0.1662 | 0.0324 | 0.030991 | -0.038755 | -0.008831 | -0.0106 | 0.005979 | 0.10039 | 0.072236 | 0.071155 | 0.043
3340.2344 | 122.1222 | -0.045776 | 121.9254 | 0.14017 | -0.013048 | -0.016578 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | 0.01586 | 0.11585 | -0.004219 | -0.010206 | -0.084531 | -0.045451 | -0.051798 | -0.035219 | 0.18594 | 0.032728 | 0.029198 | 0.020759 | 0.068307 | 0.11762 | -0.016941 | 0.061636 | 0.16162 | 0.041557 | 0.03557 | -0.038755 | 0.000325 | -0.006022 | 0.010557 | 0.10039 | 0.067658 | 0.080312 | 0.047579
3341.9844 | 122.0993 | -0.064087 | 121.9574 | 0.14017 | -0.017627 | -0.012 | -0.029595 | 0.022531 | 0.076426 | -0.071874 | 0.020438 | 0.12043 | -0.004219 | -0.014785 | -0.084531 | -0.054607 | -0.042641 | -0.035219 | 0.20425 | 0.04646 | 0.052087 | 0.034492 | 0.086618 | 0.14051 | -0.007787 | 0.066214 | 0.1662 | 0.041557 | 0.030991 | -0.038755 | -0.008831 | 0.003135 | 0.010557 | 0.10497 | 0.063079 | 0.080312 | 0.038422
3343.75 | 121.962 | -0.11902 | 121.9986 | 0.14474 | -0.017627 | -0.021157 | -0.01586 | 0.022531 | 0.081005 | -0.067295 | 0.020438 | 0.11585 | -0.004219 | -0.019364 | -0.079953 | -0.050029 | -0.04722 | -0.035219 | 0.26376 | 0.10139 | 0.097862 | 0.10316 | 0.14155 | 0.20002 | 0.051724 | 0.066214 | 0.16162 | 0.041557 | 0.026412 | -0.034177 | -0.004253 | -0.001444 | 0.010557 | 0.10039 | 0.067658 | 0.075734 | 0.043001
3345.5 | 122.0673 | -0.068665 | 121.9666 | 0.14474 | -0.013048 | -0.016578 | -0.025017 | 0.031687 | 0.081005 | -0.067295 | 0.01586 | 0.12043 | -0.013376 | -0.010206 | -0.084531 | -0.045451 | -0.04722 | -0.039797 | 0.21341 | 0.055617 | 0.052087 | 0.043648 | 0.10035 | 0.14967 | 0.00137 | 0.061636 | 0.1662 | 0.0324 | 0.03557 | -0.038755 | 0.000325 | -0.001444 | 0.005979 | 0.10039 | 0.06308 | 0.071155 | 0.033844
3347.2656 | 121.9894 | -0.10986 | 121.9757 | 0.14474 | -0.008469 | -0.016578 | -0.020438 | 0.031687 | 0.081005 | -0.062717 | 0.01586 | 0.11127 | -0.004219 | -0.019364 | -0.079953 | -0.054607 | -0.056376 | -0.035219 | 0.25461 | 0.10139 | 0.093285 | 0.089425 | 0.14155 | 0.19087 | 0.047146 | 0.061636 | 0.15704 | 0.041557 | 0.026412 | -0.034177 | -0.008831 | -0.0106 | 0.010557 | 0.095813 | 0.072236 | 0.075734 | 0.052157
3349.0312 | 121.994 | -0.10986 | 121.9803 | 0.14474 | -0.017627 | -0.025735 | -0.020438 | 0.022531 | 0.071848 | -0.062717 | 0.01586 | 0.11127 | -0.004219 | -0.019364 | -0.084531 | -0.054607 | -0.056376 | -0.039797 | 0.25461 | 0.092236 | 0.084128 | 0.089425 | 0.13239 | 0.18171 | 0.047146 | 0.061636 | 0.15704 | 0.041557 | 0.026412 | -0.038755 | -0.008831 | -0.0106 | 0.005979 | 0.10039 | 0.072236 | 0.080312 | 0.052157
3350.7344 | 122.0078 | -0.09613 | 121.994 | 0.14932 | -0.017627 | -0.016578 | -0.025017 | 0.022531 | 0.076426 | -0.062717 | 0.01586 | 0.12043 | 0.000359 | -0.014785 | -0.075375 | -0.045451 | -0.051798 | -0.035219 | 0.24545 | 0.078503 | 0.079552 | 0.071113 | 0.11866 | 0.17256 | 0.033413 | 0.061636 | 0.1662 | 0.046135 | 0.030991 | -0.029599 | 0.000325 | -0.006022 | 0.010557 | 0.091235 | 0.067658 | 0.075734 | 0.052157
3352.5 | 122.0398 | -0.10071 | 121.9666 | 0.14474 | -0.008469 | -0.016578 | -0.029595 | 0.031687 | 0.076426 | -0.071874 | 0.01586 | 0.10211 | -0.008798 | -0.014785 | -0.08911 | -0.054607 | -0.051798 | -0.030641 | 0.24545 | 0.092239 | 0.08413 | 0.071113 | 0.1324 | 0.17713 | 0.028834 | 0.061636 | 0.14789 | 0.036978 | 0.030991 | -0.043334 | -0.008831 | -0.006022 | 0.015135 | 0.10497 | 0.067658 | 0.080312 | 0.043
3354.2812 | 122.0123 | -0.1236 | 122.0261 | 0.14017 | -0.013048 | -0.016578 | -0.025017 | 0.022531 | 0.076426 | -0.067295 | 0.006703 | 0.11127 | -0.008798 | -0.014785 | -0.08911 | -0.054607 | -0.04722 | -0.039797 | 0.26376 | 0.11055 | 0.10702 | 0.098579 | 0.14613 | 0.20002 | 0.056301 | 0.052479 | 0.15704 | 0.036978 | 0.030991 | -0.043334 | -0.008831 | -0.001444 | 0.005979 | 0.095813 | 0.053923 | 0.080312 | 0.038422
3356.0469 | 121.994 | -0.10986 | 121.9849 | 0.13559 | -0.008469 | -0.012 | -0.020438 | 0.027109 | 0.071848 | -0.062717 | 0.006703 | 0.11127 | -0.004219 | -0.019364 | -0.079953 | -0.050029 | -0.051798 | -0.035219 | 0.24545 | 0.10139 | 0.097863 | 0.089425 | 0.13697 | 0.18171 | 0.047146 | 0.052479 | 0.15704 | 0.041557 | 0.026412 | -0.034177 | -0.004253 | -0.006022 | 0.010557 | 0.086656 | 0.058501 | 0.075734 | 0.047579
3357.75 | 122.0261 | -0.086975 | 122.0032 | 0.14474 | -0.022205 | -0.025735 | -0.025017 | 0.017953 | 0.081005 | -0.062717 | 0.011281 | 0.10669 | -0.008798 | -0.010206 | -0.08911 | -0.045451 | -0.04722 | -0.039797 | 0.23172 | 0.06477 | 0.06124 | 0.061958 | 0.10493 | 0.16798 | 0.024258 | 0.057057 | 0.15247 | 0.036978 | 0.03557 | -0.043334 | 0.000325 | -0.001444 | 0.005979 | 0.10039 | 0.058501 | 0.080312 | 0.038422
3359.5156 | 122.0856 | -0.068665 | 121.9757 | 0.14474 | -0.017627 | -0.016578 | -0.01586 | 0.022531 | 0.076426 | -0.067295 | 0.011281 | 0.10669 | 0.000359 | -0.019364 | -0.08911 | -0.054607 | -0.051798 | -0.030641 | 0.21341 | 0.051038 | 0.052087 | 0.052805 | 0.091196 | 0.14509 | 0.00137 | 0.057057 | 0.15247 | 0.046135 | 0.026412 | -0.043334 | -0.008831 | -0.006022 | 0.015135 | 0.10039 | 0.063079 | 0.089469 | 0.052157
3361.2188 | 122.113 | -0.054932 | 121.9482 | 0.14932 | -0.017627 | -0.021157 | -0.025017 | 0.027109 | 0.071848 | -0.062717 | 0.002124 | 0.11127 | -0.004219 | -0.019364 | -0.08911 | -0.050029 | -0.04722 | -0.035219 | 0.20425 | 0.037305 | 0.033775 | 0.029915 | 0.082041 | 0.12678 | -0.007785 | 0.0479 | 0.15704 | 0.041557 | 0.026412 | -0.043334 | -0.004253 | -0.001444 | 0.010557 | 0.091234 | 0.049344 | 0.084891 | 0.043001
3362.9844 | 122.0215 | -0.07782 | 121.9437 | 0.14474 | -0.017627 | -0.025735 | -0.020438 | 0.027109 | 0.081005 | -0.062717 | 0.011281 | 0.10211 | -0.013376 | -0.023943 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.22256 | 0.060193 | 0.052085 | 0.057382 | 0.10493 | 0.15882 | 0.015103 | 0.057057 | 0.14789 | 0.0324 | 0.021833 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.095812 | 0.063079 | 0.071155 | 0.038422
3364.6875 | 122.0352 | -0.10986 | 121.994 | 0.14017 | -0.017627 | -0.021157 | -0.025017 | 0.022531 | 0.081005 | -0.062717 | 0.002124 | 0.10669 | -0.004219 | -0.014785 | -0.084531 | -0.050029 | -0.042641 | -0.035219 | 0.25003 | 0.092236 | 0.088706 | 0.084846 | 0.13239 | 0.19087 | 0.047146 | 0.0479 | 0.15247 | 0.041557 | 0.030991 | -0.038755 | -0.004253 | 0.003135 | 0.010557 | 0.086655 | 0.044765 | 0.080312 | 0.038422
3366.4531 | 122.1222 | -0.059509 | 121.9391 | 0.14017 | -0.017627 | -0.021157 | -0.029595 | 0.022531 | 0.067269 | -0.053561 | -0.002454 | 0.10211 | -0.008798 | -0.014785 | -0.08911 | -0.050029 | -0.051798 | -0.039797 | 0.19967 | 0.041882 | 0.038352 | 0.029914 | 0.08204 | 0.12678 | 0.005948 | 0.043322 | 0.14789 | 0.036978 | 0.030991 | -0.043334 | -0.004253 | -0.006022 | 0.005979 | 0.086656 | 0.049344 | 0.080312 | 0.043
3368.2344 | 122.049 | -0.091553 | 121.9849 | 0.14932 | -0.017627 | -0.012 | -0.020438 | 0.027109 | 0.081005 | -0.062717 | 0.011281 | 0.10669 | -0.008798 | -0.014785 | -0.093688 | -0.050029 | -0.056376 | -0.035219 | 0.24087 | 0.073926 | 0.079553 | 0.071115 | 0.11866 | 0.17256 | 0.028836 | 0.057057 | 0.15247 | 0.036978 | 0.030991 | -0.047912 | -0.004253 | -0.0106 | 0.010557 | 0.10497 | 0.067657 | 0.08489 | 0.047578
3369.9375 | 121.994 | -0.11444 | 121.9986 | 0.14474 | -0.017627 | -0.021157 | -0.025017 | 0.022531 | 0.076426 | -0.067295 | 0.002124 | 0.10211 | -0.008798 | -0.019364 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.25918 | 0.096814 | 0.093284 | 0.089424 | 0.13697 | 0.19087 | 0.047146 | 0.0479 | 0.14789 | 0.036978 | 0.026412 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.086655 | 0.053922 | 0.075733 | 0.043
3371.7031 | 122.0444 | -0.09613 | 121.9986 | 0.15848 | -0.013048 | -0.021157 | -0.020438 | 0.031687 | 0.076426 | -0.067295 | 0.002124 | 0.097532 | -0.008798 | -0.019364 | -0.084531 | -0.050029 | -0.04722 | -0.030641 | 0.25461 | 0.083082 | 0.074973 | 0.075692 | 0.12782 | 0.17256 | 0.028835 | 0.0479 | 0.14331 | 0.036978 | 0.026412 | -0.038755 | -0.004253 | -0.001444 | 0.015135 | 0.086655 | 0.049344 | 0.075733 | 0.038422
3373.4531 | 122.0581 | -0.09613 | 121.994 | 0.14474 | -0.017627 | -0.012 | -0.029595 | 0.022531 | 0.076426 | -0.058139 | 0.011281 | 0.097532 | -0.013376 | -0.019364 | -0.084531 | -0.050029 | -0.056376 | -0.039797 | 0.24087 | 0.078503 | 0.08413 | 0.066535 | 0.11866 | 0.17256 | 0.037991 | 0.057057 | 0.14331 | 0.0324 | 0.026412 | -0.038755 | -0.004253 | -0.0106 | 0.005979 | 0.095812 | 0.067657 | 0.071155 | 0.043
3375.1562 | 122.1222 | -0.064087 | 121.9482 | 0.13559 | -0.013048 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.071874 | 0.006703 | 0.10669 | -0.013376 | -0.023943 | -0.079953 | -0.059185 | -0.051798 | -0.035219 | 0.19967 | 0.051039 | 0.04293 | 0.03907 | 0.086618 | 0.13594 | -0.007787 | 0.052479 | 0.15247 | 0.0324 | 0.021833 | -0.034177 | -0.013409 | -0.006022 | 0.010557 | 0.086656 | 0.058501 | 0.066577 | 0.038422
3376.9219 | 122.0856 | -0.073242 | 121.962 | 0.14017 | -0.013048 | -0.021157 | -0.025017 | 0.017953 | 0.071848 | -0.071874 | 0.011281 | 0.097532 | -0.004219 | -0.019364 | -0.08911 | -0.050029 | -0.051798 | -0.039797 | 0.21341 | 0.060194 | 0.052085 | 0.048225 | 0.091195 | 0.14509 | 0.001368 | 0.057057 | 0.14331 | 0.041557 | 0.026412 | -0.043334 | -0.004253 | -0.006022 | 0.005979 | 0.10039 | 0.063079 | 0.084891 | 0.047579
3378.6875 | 121.9849 | -0.10529 | 121.9803 | 0.14932 | -0.008469 | -0.012 | -0.029595 | 0.027109 | 0.076426 | -0.067295 | 0.006703 | 0.10211 | -0.013376 | -0.019364 | -0.084531 | -0.054607 | -0.051798 | -0.030641 | 0.25461 | 0.096817 | 0.093286 | 0.075691 | 0.1324 | 0.18171 | 0.037991 | 0.052479 | 0.14789 | 0.0324 | 0.026412 | -0.038755 | -0.008831 | -0.006022 | 0.015135 | 0.091234 | 0.058501 | 0.071155 | 0.038422
3380.3906 | 122.1359 | -0.073242 | 121.9299 | 0.14474 | -0.013048 | -0.012 | -0.025017 | 0.022531 | 0.076426 | -0.067295 | -0.002454 | 0.10211 | -0.008798 | -0.014785 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.21799 | 0.060194 | 0.061242 | 0.048225 | 0.095773 | 0.14967 | 0.005947 | 0.043322 | 0.14789 | 0.036978 | 0.030991 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.082077 | 0.049344 | 0.075733 | 0.043
3382.1562 | 122.0764 | -0.073242 | 121.9574 | 0.14017 | -0.017627 | -0.021157 | -0.025017 | 0.027109 | 0.071848 | -0.071874 | 0.006703 | 0.097532 | -0.004219 | -0.014785 | -0.075375 | -0.054607 | -0.04722 | -0.035219 | 0.21341 | 0.055615 | 0.052085 | 0.048225 | 0.10035 | 0.14509 | 0.001368 | 0.052479 | 0.14331 | 0.041557 | 0.030991 | -0.029599 | -0.008831 | -0.001444 | 0.010557 | 0.082078 | 0.053923 | 0.071156 | 0.043001
3383.9219 | 122.1313 | -0.041199 | 121.9482 | 0.14474 | -0.013048 | -0.016578 | -0.020438 | 0.027109 | 0.067269 | -0.067295 | -0.002454 | 0.10211 | -0.013376 | -0.014785 | -0.084531 | -0.054607 | -0.051798 | -0.030641 | 0.18594 | 0.028151 | 0.024621 | 0.020761 | 0.068308 | 0.10847 | -0.026096 | 0.043322 | 0.14789 | 0.0324 | 0.030991 | -0.038755 | -0.008831 | -0.006022 | 0.015135 | 0.082077 | 0.049344 | 0.071155 | 0.038422
3385.6406 | 122.0764 | -0.068665 | 121.9482 | 0.14474 | -0.017627 | -0.016578 | -0.020438 | 0.022531 | 0.081005 | -0.058139 | 0.002124 | 0.10211 | -0.013376 | -0.028522 | -0.084531 | -0.054607 | -0.042641 | -0.044375 | 0.21341 | 0.051038 | 0.052087 | 0.048227 | 0.091196 | 0.14967 | 0.010526 | 0.0479 | 0.14789 | 0.0324 | 0.017254 | -0.038755 | -0.008831 | 0.003135 | 0.001401 | 0.086655 | 0.044765 | 0.071155 | 0.029265
3387.4062 | 122.0306 | -0.13275 | 121.994 | 0.14474 | -0.022205 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | 0.002124 | 0.10211 | -0.008798 | -0.019364 | -0.084531 | -0.045451 | -0.04722 | -0.035219 | 0.27749 | 0.11055 | 0.10702 | 0.10773 | 0.15528 | 0.2046 | 0.065456 | 0.0479 | 0.14789 | 0.036978 | 0.026412 | -0.038755 | 0.000325 | -0.001444 | 0.010557 | 0.086655 | 0.049344 | 0.075733 | 0.038422
3389.125 | 122.0261 | -0.091553 | 121.9894 | 0.14017 | -0.022205 | -0.016578 | -0.025017 | 0.022531 | 0.076426 | -0.071874 | -0.002454 | 0.10211 | -0.013376 | -0.023943 | -0.093688 | -0.050029 | -0.051798 | -0.035219 | 0.23172 | 0.069348 | 0.074975 | 0.066536 | 0.11408 | 0.16798 | 0.019679 | 0.043322 | 0.14789 | 0.0324 | 0.021833 | -0.047912 | -0.004253 | -0.006022 | 0.010557 | 0.091234 | 0.049344 | 0.080312 | 0.038422
3390.8906 | 122.0947 | -0.064087 | 121.9391 | 0.14017 | -0.017627 | -0.016578 | -0.029595 | 0.027109 | 0.071848 | -0.062717 | 0.002124 | 0.10211 | -0.013376 | -0.014785 | -0.08911 | -0.050029 | -0.04722 | -0.044375 | 0.20425 | 0.04646 | 0.047509 | 0.034492 | 0.091196 | 0.13594 | 0.00137 | 0.0479 | 0.14789 | 0.0324 | 0.030991 | -0.043334 | -0.004253 | -0.001444 | 0.001401 | 0.091234 | 0.049344 | 0.075734 | 0.033844
3392.5938 | 121.994 | -0.10986 | 121.9894 | 0.14932 | -0.013048 | -0.016578 | -0.01586 | 0.031687 | 0.076426 | -0.058139 | -0.002454 | 0.10211 | -0.013376 | -0.014785 | -0.084531 | -0.050029 | -0.051798 | -0.044375 | 0.25918 | 0.096815 | 0.093285 | 0.094003 | 0.14155 | 0.18629 | 0.051724 | 0.043322 | 0.14789 | 0.0324 | 0.030991 | -0.038755 | -0.004253 | -0.006022 | 0.001401 | 0.082077 | 0.049344 | 0.071155 | 0.038422
3394.375 | 122.1405 | -0.068665 | 121.9803 | 0.14474 | -0.013048 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | 0.002124 | 0.097532 | -0.017954 | -0.014785 | -0.079953 | -0.050029 | -0.051798 | -0.035219 | 0.21341 | 0.055617 | 0.04293 | 0.03907 | 0.091196 | 0.14051 | 0.00137 | 0.0479 | 0.14331 | 0.027822 | 0.030991 | -0.034177 | -0.004253 | -0.006022 | 0.010557 | 0.082077 | 0.053922 | 0.061999 | 0.033844
3396.1406 | 122.0901 | -0.082397 | 121.9482 | 0.14474 | -0.017627 | -0.021157 | -0.025017 | 0.013375 | 0.067269 | -0.058139 | 0.002124 | 0.10211 | -0.008798 | -0.014785 | -0.075375 | -0.054607 | -0.051798 | -0.035219 | 0.22714 | 0.06477 | 0.06124 | 0.05738 | 0.095772 | 0.14967 | 0.024258 | 0.0479 | 0.14789 | 0.036978 | 0.030991 | -0.029599 | -0.008831 | -0.006022 | 0.010557 | 0.077499 | 0.053922 | 0.066577 | 0.043
3397.9062 | 121.9849 | -0.10071 | 121.9894 | 0.14932 | -0.022205 | -0.012 | -0.025017 | 0.031687 | 0.071848 | -0.058139 | 0.002124 | 0.097532 | -0.013376 | -0.023943 | -0.084531 | -0.054607 | -0.04722 | -0.026063 | 0.25003 | 0.078503 | 0.088708 | 0.075691 | 0.1324 | 0.17256 | 0.042569 | 0.0479 | 0.14331 | 0.0324 | 0.021833 | -0.038755 | -0.008831 | -0.001444 | 0.019713 | 0.086655 | 0.049344 | 0.071155 | 0.033844
3399.625 | 122.1359 | -0.036621 | 121.9391 | 0.14017 | -0.017627 | -0.025735 | -0.025017 | 0.013375 | 0.067269 | -0.067295 | 0.006703 | 0.11127 | -0.017954 | -0.019364 | -0.079953 | -0.050029 | -0.051798 | -0.035219 | 0.17679 | 0.018994 | 0.010886 | 0.011604 | 0.049996 | 0.10389 | -0.030674 | 0.052479 | 0.15704 | 0.027822 | 0.026412 | -0.034177 | -0.004253 | -0.006022 | 0.010557 | 0.086656 | 0.058501 | 0.061999 | 0.033844
3401.3906 | 122.0032 | -0.10529 | 121.9849 | 0.14017 | -0.008469 | -0.016578 | -0.020438 | 0.022531 | 0.076426 | -0.058139 | 0.006703 | 0.097532 | -0.013376 | -0.019364 | -0.084531 | -0.054607 | -0.04722 | -0.044375 | 0.24545 | 0.096817 | 0.088708 | 0.084848 | 0.12782 | 0.18171 | 0.047147 | 0.052479 | 0.14331 | 0.0324 | 0.026412 | -0.038755 | -0.008831 | -0.001444 | 0.001401 | 0.091234 | 0.053923 | 0.071155 | 0.033844
3403.1875 | 122.1451 | -0.07782 | 121.9391 | 0.14474 | -0.022205 | -0.016578 | -0.020438 | 0.017953 | 0.071848 | -0.067295 | 0.002124 | 0.10211 | -0.013376 | -0.014785 | -0.084531 | -0.054607 | -0.04722 | -0.039797 | 0.22256 | 0.055615 | 0.061242 | 0.057382 | 0.095773 | 0.14967 | 0.010525 | 0.0479 | 0.14789 | 0.0324 | 0.030991 | -0.038755 | -0.008831 | -0.001444 | 0.005979 | 0.086655 | 0.049344 | 0.071155 | 0.033844
3404.9688 | 122.1405 | -0.07782 | 121.9482 | 0.14017 | -0.013048 | -0.021157 | -0.025017 | 0.027109 | 0.081005 | -0.067295 | 0.002124 | 0.10669 | -0.008798 | -0.019364 | -0.08911 | -0.045451 | -0.056376 | -0.035219 | 0.21799 | 0.064772 | 0.056663 | 0.052803 | 0.10493 | 0.15882 | 0.010525 | 0.0479 | 0.15247 | 0.036978 | 0.026412 | -0.043334 | 0.000325 | -0.0106 | 0.010557 | 0.091234 | 0.0585 | 0.080312 | 0.047578
3406.75 | 122.0169 | -0.10529 | 121.9757 | 0.14932 | -0.017627 | -0.016578 | -0.025017 | 0.027109 | 0.081005 | -0.071874 | 0.002124 | 0.097532 | -0.013376 | -0.019364 | -0.079953 | -0.050029 | -0.051798 | -0.039797 | 0.25461 | 0.087659 | 0.088708 | 0.080269 | 0.1324 | 0.18629 | 0.033412 | 0.0479 | 0.14331 | 0.0324 | 0.026412 | -0.034177 | -0.004253 | -0.006022 | 0.005979 | 0.082077 | 0.053922 | 0.066577 | 0.038422
3408.4688 | 122.1542 | -0.050354 | 121.9437 | 0.14017 | -0.013048 | -0.016578 | -0.029595 | 0.027109 | 0.076426 | -0.071874 | -0.002454 | 0.10211 | -0.017954 | -0.019364 | -0.079953 | -0.050029 | -0.051798 | -0.039797 | 0.19052 | 0.037306 | 0.033776 | 0.020759 | 0.077463 | 0.12678 | -0.02152 | 0.043322 | 0.14789 | 0.027822 | 0.026412 | -0.034177 | -0.004253 | -0.006022 | 0.005979 | 0.077499 | 0.049344 | 0.061999 | 0.033844
3410.2344 | 122.049 | -0.09613 | 121.9986 | 0.14017 | -0.013048 | -0.016578 | -0.01586 | 0.022531 | 0.076426 | -0.062717 | 0.002124 | 0.097532 | -0.013376 | -0.023943 | -0.084531 | -0.054607 | -0.056376 | -0.030641 | 0.2363 | 0.083082 | 0.079552 | 0.08027 | 0.11866 | 0.17256 | 0.033413 | 0.0479 | 0.14331 | 0.0324 | 0.021833 | -0.038755 | -0.008831 | -0.0106 | 0.015135 | 0.086655 | 0.0585 | 0.071155 | 0.043
3411.9375 | 122.0764 | -0.07782 | 121.9711 | 0.14017 | -0.017627 | -0.025735 | -0.025017 | 0.017953 | 0.076426 | -0.062717 | 0.006703 | 0.097532 | -0.008798 | -0.014785 | -0.084531 | -0.050029 | -0.04722 | -0.039797 | 0.21799 | 0.060193 | 0.052085 | 0.052803 | 0.095773 | 0.15425 | 0.015103 | 0.052479 | 0.14331 | 0.036978 | 0.030991 | -0.038755 | -0.004253 | -0.001444 | 0.005979 | 0.091234 | 0.053923 | 0.075733 | 0.038422
3413.7031 | 122.0444 | -0.082397 | 122.0078 | 0.14017 | -0.017627 | -0.016578 | -0.025017 | 0.027109 | 0.076426 | -0.071874 | -0.002454 | 0.10211 | -0.013376 | -0.014785 | -0.079953 | -0.045451 | -0.04722 | -0.039797 | 0.22256 | 0.06477 | 0.065819 | 0.05738 | 0.10951 | 0.15882 | 0.010523 | 0.043322 | 0.14789 | 0.0324 | 0.030991 | -0.034177 | 0.000325 | -0.001444 | 0.005979 | 0.077499 | 0.044766 | 0.066577 | 0.033844
3415.4688 | 122.1497 | -0.059509 | 121.9666 | 0.14017 | -0.017627 | -0.016578 | -0.025017 | 0.022531 | 0.076426 | -0.071874 | -0.002454 | 0.10211 | -0.008798 | -0.019364 | -0.084531 | -0.054607 | -0.04722 | -0.035219 | 0.19967 | 0.041882 | 0.042931 | 0.034492 | 0.08204 | 0.13594 | -0.012365 | 0.043322 | 0.14789 | 0.036978 | 0.026412 | -0.038755 | -0.008831 | -0.001444 | 0.010557 | 0.082077 | 0.044766 | 0.075733 | 0.038422
3417.2344 | 122.0078 | -0.11444 | 121.9803 | 0.14474 | -0.013048 | -0.016578 | -0.020438 | 0.027109 | 0.076426 | -0.071874 | -0.002454 | 0.10211 | -0.013376 | -0.014785 | -0.084531 | -0.045451 | -0.04722 | -0.039797 | 0.25918 | 0.10139 | 0.097863 | 0.094003 | 0.14155 | 0.19087 | 0.042567 | 0.043322 | 0.14789 | 0.0324 | 0.030991 | -0.038755 | 0.000325 | -0.001444 | 0.005979 | 0.082077 | 0.044766 | 0.071155 | 0.033844
3419 | 122.049 | -0.086975 | 121.994 | 0.14474 | -0.017627 | -0.021157 | -0.025017 | 0.027109 | 0.081005 | -0.071874 | -0.007033 | 0.092954 | -0.013376 | -0.019364 | -0.08911 | -0.054607 | -0.051798 | -0.030641 | 0.23172 | 0.069348 | 0.065818 | 0.061958 | 0.11408 | 0.16798 | 0.015101 | 0.038743 | 0.13873 | 0.0324 | 0.026412 | -0.043334 | -0.008831 | -0.006022 | 0.015135 | 0.082077 | 0.044765 | 0.075734 | 0.038422
3420.7656 | 122.0306 | -0.091553 | 121.9574 | 0.14017 | -0.017627 | -0.021157 | -0.020438 | 0.031687 | 0.081005 | -0.058139 | -0.007033 | 0.10211 | -0.013376 | -0.019364 | -0.08911 | -0.054607 | -0.051798 | -0.039797 | 0.23172 | 0.073926 | 0.070396 | 0.071115 | 0.12324 | 0.17256 | 0.033414 | 0.038743 | 0.14789 | 0.0324 | 0.026412 | -0.043334 | -0.008831 | -0.006022 | 0.005979 | 0.082077 | 0.044765 | 0.075734 | 0.038422
3422.4688 | 122.0581 | -0.091553 | 121.9894 | 0.14017 | -0.013048 | -0.012 | -0.029595 | 0.017953 | 0.076426 | -0.067295 | -0.002454 | 0.10211 | -0.013376 | -0.019364 | -0.075375 | -0.059185 | -0.04722 | -0.035219 | 0.23172 | 0.078505 | 0.079553 | 0.061958 | 0.10951 | 0.16798 | 0.024258 | 0.043322 | 0.14789 | 0.0324 | 0.026412 | -0.029599 | -0.013409 | -0.001444 | 0.010557 | 0.072921 | 0.044766 | 0.061999 | 0.033844
3424.2344 | 122.1039 | -0.064087 | 121.9345 | 0.14474 | -0.013048 | -0.016578 | -0.025017 | 0.027109 | 0.076426 | -0.062717 | 0.002124 | 0.092954 | -0.017954 | -0.019364 | -0.093688 | -0.054607 | -0.051798 | -0.039797 | 0.20883 | 0.051039 | 0.047509 | 0.03907 | 0.091196 | 0.14051 | 0.00137 | 0.0479 | 0.13873 | 0.027822 | 0.026412 | -0.047912 | -0.008831 | -0.006022 | 0.005979 | 0.095812 | 0.053922 | 0.075734 | 0.033844
3426.0156 | 122.0993 | -0.068665 | 121.9437 | 0.14017 | -0.013048 | -0.021157 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | 0.006703 | 0.097532 | -0.008798 | -0.023943 | -0.08911 | -0.050029 | -0.051798 | -0.039797 | 0.20883 | 0.055617 | 0.047508 | 0.043648 | 0.091196 | 0.13593 | 0.005948 | 0.052479 | 0.14331 | 0.036978 | 0.021833 | -0.043334 | -0.004253 | -0.006022 | 0.005979 | 0.095813 | 0.058501 | 0.080312 | 0.043
3427.7812 | 122.0215 | -0.091553 | 121.9849 | 0.14017 | -0.017627 | -0.016578 | -0.029595 | 0.027109 | 0.071848 | -0.071874 | -0.002454 | 0.10211 | -0.017954 | -0.023943 | -0.08911 | -0.059185 | -0.04722 | -0.048953 | 0.23172 | 0.073926 | 0.074975 | 0.061958 | 0.11866 | 0.1634 | 0.019679 | 0.043322 | 0.14789 | 0.027822 | 0.021833 | -0.043334 | -0.013409 | -0.001444 | -0.003177 | 0.086656 | 0.044766 | 0.071156 | 0.029266
3429.5 | 122.0764 | -0.068665 | 121.962 | 0.14932 | -0.017627 | -0.021157 | -0.029595 | 0.027109 | 0.076426 | -0.067295 | 0.002124 | 0.092954 | -0.013376 | -0.023943 | -0.084531 | -0.054607 | -0.051798 | -0.039797 | 0.21799 | 0.051038 | 0.047508 | 0.03907 | 0.095774 | 0.14509 | 0.00137 | 0.0479 | 0.13873 | 0.0324 | 0.021833 | -0.038755 | -0.008831 | -0.006022 | 0.005979 | 0.086655 | 0.053922 | 0.071155 | 0.038422
3431.2656 | 122.0398 | -0.082397 | 121.962 | 0.1539 | -0.017627 | -0.016578 | -0.020438 | 0.031687 | 0.081005 | -0.071874 | 0.002124 | 0.10211 | -0.017954 | -0.019364 | -0.084531 | -0.054607 | -0.051798 | -0.035219 | 0.2363 | 0.06477 | 0.065819 | 0.061959 | 0.11408 | 0.1634 | 0.010523 | 0.0479 | 0.14789 | 0.027822 | 0.026412 | -0.038755 | -0.008831 | -0.006022 | 0.010557 | 0.086655 | 0.053922 | 0.066577 | 0.033844
3432.9688 | 122.1176 | -0.064087 | 121.9574 | 0.14017 | -0.022205 | -0.021157 | -0.029595 | 0.022531 | 0.067269 | -0.071874 | -0.007033 | 0.10211 | -0.017954 | -0.023943 | -0.093688 | -0.050029 | -0.056376 | -0.039797 | 0.20425 | 0.041882 | 0.04293 | 0.034492 | 0.086618 | 0.13136 | -0.007787 | 0.038743 | 0.14789 | 0.027822 | 0.021833 | -0.047912 | -0.004253 | -0.0106 | 0.005979 | 0.086655 | 0.049343 | 0.075734 | 0.038422
3434.7344 | 122.049 | -0.10071 | 121.9803 | 0.14932 | -0.008469 | -0.012 | -0.01586 | 0.022531 | 0.076426 | -0.062717 | 0.002124 | 0.10669 | -0.013376 | -0.014785 | -0.093688 | -0.059185 | -0.051798 | -0.044375 | 0.25003 | 0.092239 | 0.088708 | 0.084848 | 0.12324 | 0.17713 | 0.037991 | 0.0479 | 0.15247 | 0.0324 | 0.030991 | -0.047912 | -0.013409 | -0.006022 | 0.001401 | 0.095812 | 0.053922 | 0.080312 | 0.038422
3436.5 | 122.0306 | -0.10071 | 122.0078 | 0.14017 | -0.022205 | -0.016578 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.002454 | 0.10669 | -0.013376 | -0.019364 | -0.079953 | -0.054607 | -0.056376 | -0.039797 | 0.24087 | 0.078503 | 0.08413 | 0.075691 | 0.12324 | 0.17256 | 0.037991 | 0.043322 | 0.15247 | 0.0324 | 0.026412 | -0.034177 | -0.008831 | -0.0106 | 0.005979 | 0.077499 | 0.053922 | 0.066577 | 0.043
3438.2812 | 121.9849 | -0.11444 | 121.9849 | 0.14017 | -0.008469 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.071874 | 0.002124 | 0.10211 | -0.013376 | -0.023943 | -0.079953 | -0.050029 | -0.056376 | -0.044375 | 0.25461 | 0.10597 | 0.088706 | 0.089424 | 0.13697 | 0.18629 | 0.042567 | 0.0479 | 0.14789 | 0.0324 | 0.021833 | -0.034177 | -0.004253 | -0.0106 | 0.001401 | 0.082077 | 0.0585 | 0.066577 | 0.043
3439.9844 | 122.0444 | -0.086975 | 121.9711 | 0.14474 | -0.026784 | -0.025735 | -0.020438 | 0.022531 | 0.071848 | -0.067295 | 0.002124 | 0.097532 | -0.013376 | -0.023943 | -0.093688 | -0.045451 | -0.051798 | -0.044375 | 0.23172 | 0.060191 | 0.06124 | 0.066537 | 0.10951 | 0.15882 | 0.01968 | 0.0479 | 0.14331 | 0.0324 | 0.021833 | -0.047912 | 0.000325 | -0.006022 | 0.001401 | 0.095812 | 0.053922 | 0.080312 | 0.038422
3441.75 | 122.1313 | -0.068665 | 121.9574 | 0.14017 | -0.017627 | -0.025735 | -0.025017 | 0.017953 | 0.081005 | -0.071874 | 0.002124 | 0.10669 | -0.013376 | -0.019364 | -0.08911 | -0.054607 | -0.051798 | -0.030641 | 0.20883 | 0.051038 | 0.04293 | 0.043648 | 0.086618 | 0.14967 | -0.003209 | 0.0479 | 0.15247 | 0.0324 | 0.026412 | -0.043334 | -0.008831 | -0.006022 | 0.015135 | 0.091234 | 0.053922 | 0.075734 | 0.038422
3443.5156 | 122.049 | -0.09613 | 121.9757 | 0.14017 | -0.013048 | -0.016578 | -0.025017 | 0.022531 | 0.076426 | -0.062717 | -0.002454 | 0.10211 | -0.013376 | -0.019364 | -0.084531 | -0.054607 | -0.042641 | -0.044375 | 0.2363 | 0.083082 | 0.079552 | 0.071113 | 0.11866 | 0.17256 | 0.033413 | 0.043322 | 0.14789 | 0.0324 | 0.026412 | -0.038755 | -0.008831 | 0.003135 | 0.001401 | 0.082077 | 0.040187 | 0.071155 | 0.029265
3445.2188 | 122.1497 | -0.064087 | 121.9482 | 0.14932 | -0.017627 | -0.021157 | -0.029595 | 0.022531 | 0.067269 | -0.067295 | -0.002454 | 0.10211 | -0.017954 | -0.019364 | -0.084531 | -0.054607 | -0.051798 | -0.039797 | 0.21341 | 0.04646 | 0.04293 | 0.034492 | 0.086618 | 0.13136 | -0.003208 | 0.043322 | 0.14789 | 0.027822 | 0.026412 | -0.038755 | -0.008831 | -0.006022 | 0.005979 | 0.082077 | 0.049344 | 0.066577 | 0.033844
3446.9844 | 122.0352 | -0.09613 | 121.994 | 0.14017 | -0.017627 | -0.021157 | -0.020438 | 0.022531 | 0.076426 | -0.067295 | -0.007033 | 0.097532 | -0.017954 | -0.023943 | -0.08911 | -0.054607 | -0.051798 | -0.039797 | 0.2363 | 0.078503 | 0.074973 | 0.075692 | 0.11866 | 0.17256 | 0.028835 | 0.038743 | 0.14331 | 0.027822 | 0.021833 | -0.043334 | -0.008831 | -0.006022 | 0.005979 | 0.082077 | 0.044765 | 0.071156 | 0.033844
3448.7656 | 122.081 | -0.091553 | 121.9803 | 0.13559 | -0.022205 | -0.030314 | -0.029595 | 0.022531 | 0.076426 | -0.067295 | -0.002454 | 0.10211 | -0.013376 | -0.019364 | -0.084531 | -0.050029 | -0.051798 | -0.044375 | 0.22714 | 0.069348 | 0.061239 | 0.061958 | 0.11408 | 0.16798 | 0.024258 | 0.043322 | 0.14789 | 0.0324 | 0.026412 | -0.038755 | -0.004253 | -0.006022 | 0.001401 | 0.082077 | 0.049344 | 0.071155 | 0.038422
3450.4844 | 122.1313 | -0.086975 | 121.9391 | 0.14474 | -0.013048 | -0.025735 | -0.034174 | 0.027109 | 0.071848 | -0.067295 | 0.002124 | 0.10669 | -0.017954 | -0.023943 | -0.084531 | -0.050029 | -0.042641 | -0.039797 | 0.23172 | 0.073927 | 0.06124 | 0.052801 | 0.11408 | 0.15882 | 0.01968 | 0.0479 | 0.15247 | 0.027822 | 0.021833 | -0.038755 | -0.004253 | 0.003135 | 0.005979 | 0.086655 | 0.044765 | 0.066577 | 0.024687
3452.25 | 122.0581 | -0.091553 | 121.994 | 0.14932 | -0.017627 | -0.016578 | -0.025017 | 0.017953 | 0.071848 | -0.067295 | 0.002124 | 0.092954 | -0.017954 | -0.023943 | -0.08911 | -0.054607 | -0.051798 | -0.035219 | 0.24087 | 0.073926 | 0.074975 | 0.066536 | 0.10951 | 0.1634 | 0.024258 | 0.0479 | 0.13873 | 0.027822 | 0.021833 | -0.043334 | -0.008831 | -0.006022 | 0.010557 | 0.091234 | 0.053922 | 0.071156 | 0.033844
3453.9531 | 122.1313 | -0.054932 | 121.9391 | 0.14017 | -0.017627 | -0.016578 | -0.025017 | 0.027109 | 0.076426 | -0.071874 | 0.002124 | 0.10211 | -0.013376 | -0.023943 | -0.08911 | -0.059185 | -0.04722 | -0.044375 | 0.1951 | 0.037305 | 0.038354 | 0.029915 | 0.082041 | 0.13136 | -0.016942 | 0.0479 | 0.14789 | 0.0324 | 0.021833 | -0.043334 | -0.013409 | -0.001444 | 0.001401 | 0.091234 | 0.049344 | 0.075734 | 0.033844
3455.7188 | 122.1085 | -0.041199 | 121.9482 | 0.14017 | -0.017627 | -0.016578 | -0.01586 | 0.022531 | 0.071848 | -0.067295 | -0.011611 | 0.097532 | -0.017954 | -0.023943 | -0.093688 | -0.054607 | -0.056376 | -0.030641 | 0.18136 | 0.023572 | 0.024621 | 0.025339 | 0.06373 | 0.11305 | -0.026096 | 0.034165 | 0.14331 | 0.027822 | 0.021833 | -0.047912 | -0.008831 | -0.0106 | 0.015135 | 0.082077 | 0.044765 | 0.075734 | 0.038422
3457.4688 | 122.0764 | -0.068665 | 121.9208 | 0.14474 | -0.017627 | -0.025735 | -0.025017 | 0.017953 | 0.071848 | -0.062717 | -0.011611 | 0.10211 | -0.022532 | -0.019364 | -0.084531 | -0.050029 | -0.04722 | -0.039797 | 0.21341 | 0.051038 | 0.04293 | 0.043648 | 0.086618 | 0.14051 | 0.005948 | 0.034165 | 0.14789 | 0.023244 | 0.026412 | -0.038755 | -0.004253 | -0.001444 | 0.005979 | 0.07292 | 0.035609 | 0.061999 | 0.024688
3459.1719 | 122.0993 | -0.054932 | 121.9345 | 0.14017 | -0.022205 | -0.016578 | -0.029595 | 0.017953 | 0.067269 | -0.067295 | -0.002454 | 0.092954 | -0.022532 | -0.023943 | -0.084531 | -0.054607 | -0.042641 | -0.044375 | 0.1951 | 0.032727 | 0.038354 | 0.025337 | 0.072885 | 0.1222 | -0.012363 | 0.043322 | 0.13873 | 0.023244 | 0.021833 | -0.038755 | -0.008831 | 0.003135 | 0.001401 | 0.082077 | 0.040187 | 0.061999 | 0.020109
3460.9375 | 121.9986 | -0.091553 | 121.9711 | 0.14932 | -0.013048 | -0.021157 | -0.020438 | 0.022531 | 0.071848 | -0.062717 | -0.011611 | 0.092954 | -0.017954 | -0.023943 | -0.08911 | -0.050029 | -0.056376 | -0.044375 | 0.24087 | 0.078505 | 0.070396 | 0.071115 | 0.11408 | 0.1634 | 0.028836 | 0.034165 | 0.13873 | 0.027822 | 0.021833 | -0.043334 | -0.004253 | -0.0106 | 0.001401 | 0.077499 | 0.044765 | 0.071156 | 0.038422
3462.6562 | 122.0032 | -0.10986 | 122.0169 | 0.14474 | -0.017627 | -0.016578 | -0.020438 | 0.022531 | 0.067269 | -0.058139 | -0.002454 | 0.10211 | -0.013376 | -0.023943 | -0.084531 | -0.054607 | -0.04722 | -0.039797 | 0.25461 | 0.092236 | 0.093285 | 0.089425 | 0.13239 | 0.17713 | 0.051724 | 0.043322 | 0.14789 | 0.0324 | 0.021833 | -0.038755 | -0.008831 | -0.001444 | 0.005979 | 0.082077 | 0.044766 | 0.071155 | 0.033844
3464.4219 | 122.1222 | -0.050354 | 121.9254 | 0.14474 | -0.013048 | -0.016578 | -0.025017 | 0.031687 | 0.071848 | -0.067295 | -0.002454 | 0.092954 | -0.013376 | -0.03768 | -0.08911 | -0.059185 | -0.056376 | -0.035219 | 0.1951 | 0.037306 | 0.033776 | 0.025337 | 0.082041 | 0.1222 | -0.016941 | 0.043322 | 0.13873 | 0.0324 | 0.008096 | -0.043334 | -0.013409 | -0.0106 | 0.010557 | 0.086656 | 0.053922 | 0.075734 | 0.043
3466.1406 | 122.049 | -0.10071 | 121.9666 | 0.14932 | -0.017627 | -0.021157 | -0.025017 | 0.022531 | 0.076426 | -0.062717 | -0.007033 | 0.10211 | -0.017954 | -0.023943 | -0.08911 | -0.054607 | -0.051798 | -0.039797 | 0.25003 | 0.083081 | 0.079551 | 0.075691 | 0.12324 | 0.17713 | 0.037991 | 0.038743 | 0.14789 | 0.027822 | 0.021833 | -0.043334 | -0.008831 | -0.006022 | 0.005979 | 0.082077 | 0.044765 | 0.071156 | 0.033844
3467.9062 | 122.1268 | -0.064087 | 121.9391 | 0.14474 | -0.017627 | -0.021157 | -0.020438 | 0.022531 | 0.081005 | -0.062717 | 0.002124 | 0.092954 | -0.022532 | -0.023943 | -0.084531 | -0.054607 | -0.060955 | -0.039797 | 0.20883 | 0.04646 | 0.04293 | 0.043649 | 0.086618 | 0.14509 | 0.00137 | 0.0479 | 0.13873 | 0.023244 | 0.021833 | -0.038755 | -0.008831 | -0.015179 | 0.005979 | 0.086655 | 0.063079 | 0.061999 | 0.038423
3469.6562 | 121.9986 | -0.10071 | 121.9711 | 0.14474 | -0.022205 | -0.025735 | -0.025017 | 0.017953 | 0.071848 | -0.062717 | -0.007033 | 0.092954 | -0.013376 | -0.019364 | -0.084531 | -0.054607 | -0.056376 | -0.039797 | 0.24545 | 0.078503 | 0.074973 | 0.075691 | 0.11866 | 0.17256 | 0.037991 | 0.038743 | 0.13873 | 0.0324 | 0.026412 | -0.038755 | -0.008831 | -0.0106 | 0.005979 | 0.077498 | 0.049343 | 0.071155 | 0.043
3471.375 | 122.1176 | -0.050354 | 121.9299 | 0.14474 | -0.022205 | -0.025735 | -0.029595 | 0.027109 | 0.071848 | -0.071874 | -0.011611 | 0.097532 | -0.013376 | -0.019364 | -0.093688 | -0.054607 | -0.060955 | -0.035219 | 0.1951 | 0.028149 | 0.024619 | 0.020759 | 0.077463 | 0.1222 | -0.02152 | 0.034165 | 0.14331 | 0.0324 | 0.026412 | -0.047912 | -0.008831 | -0.015179 | 0.010557 | 0.082077 | 0.049344 | 0.080312 | 0.047579
3473.1406 | 122.0032 | -0.10071 | 121.994 | 0.14932 | -0.008469 | -0.025735 | -0.020438 | 0.022531 | 0.071848 | -0.071874 | -0.011611 | 0.097532 | -0.022532 | -0.028522 | -0.08911 | -0.054607 | -0.060955 | -0.039797 | 0.25003 | 0.092239 | 0.074973 | 0.08027 | 0.12324 | 0.17256 | 0.028834 | 0.034165 | 0.14331 | 0.023244 | 0.017254 | -0.043334 | -0.008831 | -0.015179 | 0.005979 | 0.077499 | 0.049344 | 0.066578 | 0.038423
3474.8438 | 122.113 | -0.036621 | 121.9208 | 0.14017 | -0.022205 | -0.021157 | -0.025017 | 0.022531 | 0.076426 | -0.067295 | -0.011611 | 0.097532 | -0.013376 | -0.023943 | -0.084531 | -0.059185 | -0.051798 | -0.039797 | 0.17679 | 0.014416 | 0.015464 | 0.011604 | 0.059152 | 0.11305 | -0.030674 | 0.034165 | 0.14331 | 0.0324 | 0.021833 | -0.038755 | -0.013409 | -0.006022 | 0.005979 | 0.07292 | 0.040187 | 0.071155 | 0.038422
3476.6094 | 122.0444 | -0.082397 | 121.9803 | 0.14017 | -0.017627 | -0.016578 | -0.025017 | 0.027109 | 0.081005 | -0.062717 | -0.007033 | 0.097532 | -0.022532 | -0.023943 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.22256 | 0.06477 | 0.065819 | 0.05738 | 0.10951 | 0.1634 | 0.01968 | 0.038743 | 0.14331 | 0.023244 | 0.021833 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.077498 | 0.044765 | 0.061999 | 0.029266
3478.375 | 122.081 | -0.073242 | 121.962 | 0.14017 | -0.022205 | -0.025735 | -0.029595 | 0.017953 | 0.076426 | -0.067295 | -0.007033 | 0.097532 | -0.013376 | -0.019364 | -0.08911 | -0.054607 | -0.04722 | -0.039797 | 0.21341 | 0.051037 | 0.047507 | 0.043647 | 0.091195 | 0.14967 | 0.005947 | 0.038743 | 0.14331 | 0.0324 | 0.026412 | -0.043334 | -0.008831 | -0.001444 | 0.005979 | 0.082077 | 0.040187 | 0.075734 | 0.033844
3480.0781 | 122.0535 | -0.073242 | 121.9574 | 0.14017 | -0.017627 | -0.021157 | -0.01586 | 0.022531 | 0.071848 | -0.067295 | -0.007033 | 0.10211 | -0.022532 | -0.023943 | -0.084531 | -0.054607 | -0.04722 | -0.030641 | 0.21341 | 0.055615 | 0.052085 | 0.057382 | 0.095773 | 0.14509 | 0.005947 | 0.038743 | 0.14789 | 0.023244 | 0.021833 | -0.038755 | -0.008831 | -0.001444 | 0.015135 | 0.077498 | 0.040187 | 0.061999 | 0.024688
3481.8438 | 122.049 | -0.086975 | 121.9849 | 0.14932 | -0.017627 | -0.016578 | -0.025017 | 0.017953 | 0.076426 | -0.067295 | -0.007033 | 0.092954 | -0.022532 | -0.023943 | -0.093688 | -0.059185 | -0.060955 | -0.039797 | 0.2363 | 0.069348 | 0.070397 | 0.061958 | 0.10493 | 0.1634 | 0.01968 | 0.038743 | 0.13873 | 0.023244 | 0.021833 | -0.047912 | -0.013409 | -0.015179 | 0.005979 | 0.086655 | 0.053922 | 0.071156 | 0.038423
3483.6094 | 122.0215 | -0.10071 | 121.9849 | 0.13559 | -0.017627 | -0.025735 | -0.029595 | 0.027109 | 0.076426 | -0.062717 | -0.011611 | 0.088375 | -0.017954 | -0.023943 | -0.084531 | -0.050029 | -0.056376 | -0.044375 | 0.23629 | 0.083081 | 0.074973 | 0.071113 | 0.12782 | 0.17713 | 0.037991 | 0.034165 | 0.13415 | 0.027822 | 0.021833 | -0.038755 | -0.004253 | -0.0106 | 0.001401 | 0.07292 | 0.044765 | 0.066577 | 0.038422
3485.3125 | 122.113 | -0.059509 | 121.9528 | 0.14017 | -0.008469 | -0.025735 | -0.025017 | 0.027109 | 0.076426 | -0.071874 | -0.007033 | 0.097532 | -0.017954 | -0.028522 | -0.079953 | -0.054607 | -0.04722 | -0.044375 | 0.19967 | 0.05104 | 0.033774 | 0.034492 | 0.086618 | 0.13594 | -0.012365 | 0.038743 | 0.14331 | 0.027822 | 0.017254 | -0.034177 | -0.008831 | -0.001444 | 0.001401 | 0.07292 | 0.040187 | 0.061999 | 0.029266
3487.0938 | 122.113 | -0.064087 | 121.9437 | 0.14474 | -0.022205 | -0.025735 | -0.029595 | 0.027109 | 0.062691 | -0.067295 | -0.011611 | 0.092954 | -0.017954 | -0.023943 | -0.084531 | -0.054607 | -0.056376 | -0.035219 | 0.20883 | 0.041882 | 0.038352 | 0.034492 | 0.091196 | 0.12678 | -0.003208 | 0.034165 | 0.13873 | 0.027822 | 0.021833 | -0.038755 | -0.008831 | -0.0106 | 0.010557 | 0.07292 | 0.044765 | 0.066577 | 0.038422
3488.8594 | 122.0032 | -0.12817 | 121.994 | 0.14017 | -0.017627 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.071874 | -0.01619 | 0.092954 | -0.017954 | -0.023943 | -0.093688 | -0.050029 | -0.065533 | -0.039797 | 0.26834 | 0.11055 | 0.10244 | 0.098579 | 0.15071 | 0.20002 | 0.0563 | 0.029586 | 0.13873 | 0.027822 | 0.021833 | -0.047912 | -0.004253 | -0.019757 | 0.005979 | 0.077498 | 0.049343 | 0.075734 | 0.047579
3490.5625 | 122.0352 | -0.10529 | 121.9757 | 0.13559 | -0.022205 | -0.025735 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | -0.007033 | 0.097532 | -0.017954 | -0.019364 | -0.08911 | -0.059185 | -0.056376 | -0.044375 | 0.24087 | 0.083081 | 0.079551 | 0.080269 | 0.12782 | 0.17256 | 0.042569 | 0.038743 | 0.14331 | 0.027822 | 0.026412 | -0.043334 | -0.013409 | -0.0106 | 0.001401 | 0.082077 | 0.049343 | 0.071156 | 0.038422
3492.3281 | 122.1359 | -0.064087 | 121.9482 | 0.14017 | -0.022205 | -0.025735 | -0.020438 | 0.027109 | 0.071848 | -0.067295 | -0.007033 | 0.097532 | -0.013376 | -0.028522 | -0.084531 | -0.063763 | -0.056376 | -0.035219 | 0.20425 | 0.041882 | 0.038352 | 0.043649 | 0.091196 | 0.13594 | -0.003208 | 0.038743 | 0.14331 | 0.0324 | 0.017254 | -0.038755 | -0.017987 | -0.0106 | 0.010557 | 0.077498 | 0.049343 | 0.071155 | 0.043
3494.0312 | 122.1039 | -0.050354 | 121.9345 | 0.14474 | -0.022205 | -0.016578 | -0.029595 | 0.017953 | 0.071848 | -0.071874 | -0.011611 | 0.092954 | -0.017954 | -0.023943 | -0.084531 | -0.054607 | -0.056376 | -0.035219 | 0.1951 | 0.028149 | 0.033776 | 0.020759 | 0.068307 | 0.1222 | -0.02152 | 0.034165 | 0.13873 | 0.027822 | 0.021833 | -0.038755 | -0.008831 | -0.0106 | 0.010557 | 0.07292 | 0.044765 | 0.066577 | 0.038422
3495.7969 | 122.0901 | -0.07782 | 121.9437 | 0.14932 | -0.022205 | -0.016578 | -0.025017 | 0.022531 | 0.081005 | -0.067295 | -0.002454 | 0.092954 | -0.017954 | -0.014785 | -0.08911 | -0.050029 | -0.051798 | -0.039797 | 0.22714 | 0.055615 | 0.061242 | 0.052803 | 0.10035 | 0.15882 | 0.010525 | 0.043322 | 0.13873 | 0.027822 | 0.030991 | -0.043334 | -0.004253 | -0.006022 | 0.005979 | 0.086656 | 0.049344 | 0.071156 | 0.033844
3497.5781 | 121.9894 | -0.11902 | 121.9849 | 0.14474 | -0.022205 | -0.021157 | -0.020438 | 0.027109 | 0.071848 | -0.067295 | -0.002454 | 0.092954 | -0.013376 | -0.019364 | -0.08911 | -0.045451 | -0.051798 | -0.044375 | 0.26376 | 0.096814 | 0.097862 | 0.098581 | 0.14613 | 0.19087 | 0.051724 | 0.043322 | 0.13873 | 0.0324 | 0.026412 | -0.043334 | 0.000325 | -0.006022 | 0.001401 | 0.086656 | 0.049344 | 0.075734 | 0.038422
3499.3438 | 122.081 | -0.059509 | 121.9437 | 0.14017 | -0.022205 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.011611 | 0.10211 | -0.013376 | -0.023943 | -0.084531 | -0.054607 | -0.051798 | -0.039797 | 0.19967 | 0.037304 | 0.038352 | 0.034492 | 0.08204 | 0.13136 | -0.007786 | 0.034165 | 0.14789 | 0.0324 | 0.021833 | -0.038755 | -0.008831 | -0.006022 | 0.005979 | 0.07292 | 0.040187 | 0.071155 | 0.038422
3501.0625 | 121.9986 | -0.10529 | 121.9803 | 0.14017 | -0.013048 | -0.021157 | -0.025017 | 0.022531 | 0.081005 | -0.062717 | -0.011611 | 0.088375 | -0.017954 | -0.023943 | -0.08911 | -0.054607 | -0.051798 | -0.039797 | 0.24545 | 0.092238 | 0.084129 | 0.080269 | 0.12782 | 0.18629 | 0.042569 | 0.034165 | 0.13415 | 0.027822 | 0.021833 | -0.043334 | -0.008831 | -0.006022 | 0.005979 | 0.077499 | 0.040187 | 0.071156 | 0.033844
3502.8281 | 122.0673 | -0.09613 | 121.9574 | 0.14474 | -0.017627 | -0.025735 | -0.025017 | 0.027109 | 0.076426 | -0.071874 | -0.011611 | 0.097532 | -0.017954 | -0.023943 | -0.08911 | -0.054607 | -0.056376 | -0.039797 | 0.24087 | 0.078503 | 0.070395 | 0.071113 | 0.12324 | 0.17256 | 0.024256 | 0.034165 | 0.14331 | 0.027822 | 0.021833 | -0.043334 | -0.008831 | -0.0106 | 0.005979 | 0.077499 | 0.044765 | 0.071156 | 0.038422
3504.5938 | 122.1268 | -0.07782 | 121.9299 | 0.14932 | -0.022205 | -0.021157 | -0.020438 | 0.022531 | 0.076426 | -0.067295 | -0.007033 | 0.092954 | -0.022532 | -0.023943 | -0.084531 | -0.045451 | -0.051798 | -0.044375 | 0.22714 | 0.055615 | 0.056663 | 0.057382 | 0.10035 | 0.15425 | 0.010525 | 0.038743 | 0.13873 | 0.023244 | 0.021833 | -0.038755 | 0.000325 | -0.006022 | 0.001401 | 0.077498 | 0.044765 | 0.061999 | 0.029266
3506.3594 | 122.1359 | -0.073242 | 121.9254 | 0.14932 | -0.026784 | -0.025735 | -0.029595 | 0.017953 | 0.071848 | -0.067295 | -0.011611 | 0.092954 | -0.017954 | -0.028522 | -0.08911 | -0.045451 | -0.056376 | -0.035219 | 0.22256 | 0.046458 | 0.047507 | 0.043647 | 0.091195 | 0.14509 | 0.005947 | 0.034165 | 0.13873 | 0.027822 | 0.017254 | -0.043334 | 0.000325 | -0.0106 | 0.010557 | 0.077499 | 0.044765 | 0.071156 | 0.038422
3508.0625 | 122.1222 | -0.050354 | 121.9345 | 0.14474 | -0.013048 | -0.025735 | -0.025017 | 0.027109 | 0.071848 | -0.067295 | -0.01619 | 0.097532 | -0.017954 | -0.023943 | -0.084531 | -0.045451 | -0.051798 | -0.035219 | 0.1951 | 0.037306 | 0.024619 | 0.025337 | 0.077463 | 0.1222 | -0.016941 | 0.029586 | 0.14331 | 0.027822 | 0.021833 | -0.038755 | 0.000325 | -0.006022 | 0.010557 | 0.068341 | 0.035608 | 0.066577 | 0.033844
3509.8281 | 122.0764 | -0.086975 | 121.9345 | 0.14017 | -0.022205 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.007033 | 0.092954 | -0.022532 | -0.019364 | -0.08911 | -0.054607 | -0.051798 | -0.039797 | 0.22714 | 0.06477 | 0.06124 | 0.05738 | 0.10951 | 0.15882 | 0.01968 | 0.038743 | 0.13873 | 0.023244 | 0.026412 | -0.043334 | -0.008831 | -0.006022 | 0.005979 | 0.082077 | 0.044765 | 0.066578 | 0.029266
3511.5469 | 122.0581 | -0.091553 | 121.962 | 0.14474 | -0.022205 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.01619 | 0.092954 | -0.022532 | -0.028522 | -0.08911 | -0.054607 | -0.051798 | -0.039797 | 0.2363 | 0.069348 | 0.070396 | 0.066536 | 0.11408 | 0.1634 | 0.024258 | 0.029586 | 0.13873 | 0.023244 | 0.017254 | -0.043334 | -0.008831 | -0.006022 | 0.005979 | 0.07292 | 0.035608 | 0.066578 | 0.029266
3513.3125 | 121.9986 | -0.10986 | 121.9849 | 0.14017 | -0.017627 | -0.021157 | -0.020438 | 0.017953 | 0.076426 | -0.062717 | -0.01619 | 0.088375 | -0.022532 | -0.028522 | -0.084531 | -0.054607 | -0.051798 | -0.035219 | 0.25003 | 0.092236 | 0.088706 | 0.089425 | 0.12782 | 0.18629 | 0.047146 | 0.029586 | 0.13415 | 0.023244 | 0.017254 | -0.038755 | -0.008831 | -0.006022 | 0.010557 | 0.068341 | 0.035608 | 0.061999 | 0.029266
3515.0781 | 122.0123 | -0.11444 | 121.9849 | 0.14017 | -0.022205 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.011611 | 0.092954 | -0.022532 | -0.019364 | -0.08911 | -0.050029 | -0.056376 | -0.039797 | 0.25461 | 0.092236 | 0.088706 | 0.084846 | 0.13697 | 0.18629 | 0.047146 | 0.034165 | 0.13873 | 0.023244 | 0.026412 | -0.043334 | -0.004253 | -0.0106 | 0.005979 | 0.077499 | 0.044765 | 0.066578 | 0.033844
3516.8594 | 122.0215 | -0.09613 | 122.0032 | 0.14474 | -0.026784 | -0.021157 | -0.025017 | 0.022531 | 0.076426 | -0.062717 | -0.020768 | 0.092954 | -0.017954 | -0.023943 | -0.084531 | -0.059185 | -0.051798 | -0.044375 | 0.24087 | 0.069346 | 0.074973 | 0.071113 | 0.11866 | 0.17256 | 0.033413 | 0.025008 | 0.13873 | 0.027822 | 0.021833 | -0.038755 | -0.013409 | -0.006022 | 0.001401 | 0.063763 | 0.03103 | 0.066577 | 0.033844
3518.5625 | 122.0306 | -0.091553 | 121.9849 | 0.14017 | -0.022205 | -0.021157 | -0.025017 | 0.027109 | 0.071848 | -0.062717 | -0.020768 | 0.088375 | -0.017954 | -0.028522 | -0.084531 | -0.054607 | -0.051798 | -0.039797 | 0.23172 | 0.069348 | 0.070396 | 0.066536 | 0.11866 | 0.1634 | 0.028836 | 0.025008 | 0.13415 | 0.027822 | 0.017254 | -0.038755 | -0.008831 | -0.006022 | 0.005979 | 0.063763 | 0.03103 | 0.066577 | 0.033844
3520.3281 | 122.1176 | -0.068665 | 121.9345 | 0.13559 | -0.022205 | -0.021157 | -0.029595 | 0.027109 | 0.071848 | -0.067295 | -0.01619 | 0.088375 | -0.017954 | -0.019364 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.20425 | 0.04646 | 0.047508 | 0.03907 | 0.095774 | 0.14051 | 0.00137 | 0.029586 | 0.13415 | 0.027822 | 0.026412 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.068341 | 0.035608 | 0.066577 | 0.033844
3522.0469 | 122.1039 | -0.054932 | 121.9711 | 0.14017 | -0.026784 | -0.021157 | -0.025017 | 0.027109 | 0.071848 | -0.071874 | -0.011611 | 0.088375 | -0.022532 | -0.023943 | -0.08911 | -0.054607 | -0.051798 | -0.039797 | 0.1951 | 0.028148 | 0.033775 | 0.029915 | 0.082041 | 0.12678 | -0.016942 | 0.034165 | 0.13415 | 0.023244 | 0.021833 | -0.043334 | -0.008831 | -0.006022 | 0.005979 | 0.077499 | 0.040187 | 0.066578 | 0.029266
3523.8125 | 121.9711 | -0.11444 | 121.994 | 0.14932 | -0.017627 | -0.021157 | -0.020438 | 0.022531 | 0.081005 | -0.067295 | -0.01619 | 0.088375 | -0.013376 | -0.019364 | -0.084531 | -0.050029 | -0.056376 | -0.035219 | 0.26376 | 0.096814 | 0.093284 | 0.094003 | 0.13697 | 0.19545 | 0.047146 | 0.029586 | 0.13415 | 0.0324 | 0.026412 | -0.038755 | -0.004253 | -0.0106 | 0.010557 | 0.068341 | 0.040186 | 0.071155 | 0.043
3525.5781 | 122.0581 | -0.07782 | 121.9437 | 0.14474 | -0.017627 | -0.021157 | -0.029595 | 0.027109 | 0.071848 | -0.071874 | -0.011611 | 0.088375 | -0.022532 | -0.023943 | -0.08911 | -0.054607 | -0.060955 | -0.035219 | 0.22256 | 0.060193 | 0.056663 | 0.048225 | 0.10493 | 0.14967 | 0.005946 | 0.034165 | 0.13415 | 0.023244 | 0.021833 | -0.043334 | -0.008831 | -0.015179 | 0.010557 | 0.077499 | 0.049344 | 0.066578 | 0.038423
3527.3594 | 122.1176 | -0.064087 | 121.9208 | 0.14017 | -0.017627 | -0.016578 | -0.025017 | 0.022531 | 0.071848 | -0.071874 | -0.007033 | 0.088375 | -0.022532 | -0.028522 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.20425 | 0.04646 | 0.047509 | 0.03907 | 0.086618 | 0.13594 | -0.007787 | 0.038743 | 0.13415 | 0.023244 | 0.017254 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.077498 | 0.044765 | 0.061999 | 0.029266
3529.0625 | 121.9849 | -0.12817 | 121.994 | 0.14474 | -0.022205 | -0.016578 | -0.029595 | 0.022531 | 0.076426 | -0.067295 | -0.011611 | 0.097532 | -0.013376 | -0.033101 | -0.084531 | -0.054607 | -0.051798 | -0.035219 | 0.27292 | 0.10597 | 0.1116 | 0.098579 | 0.15071 | 0.2046 | 0.060879 | 0.034165 | 0.14331 | 0.0324 | 0.012675 | -0.038755 | -0.008831 | -0.006022 | 0.010557 | 0.07292 | 0.040187 | 0.071155 | 0.038422
3530.8438 | 122.0352 | -0.09613 | 121.9849 | 0.13559 | -0.026784 | -0.016578 | -0.020438 | 0.022531 | 0.076426 | -0.062717 | -0.01619 | 0.083796 | -0.027111 | -0.023943 | -0.08911 | -0.054607 | -0.056376 | -0.039797 | 0.23172 | 0.069346 | 0.079552 | 0.075692 | 0.11866 | 0.17256 | 0.033413 | 0.029586 | 0.12957 | 0.018665 | 0.021833 | -0.043334 | -0.008831 | -0.0106 | 0.005979 | 0.07292 | 0.040186 | 0.061999 | 0.029265
3532.625 | 122.1222 | -0.059509 | 121.9437 | 0.14474 | -0.026784 | -0.021157 | -0.025017 | 0.013375 | 0.071848 | -0.067295 | -0.020768 | 0.083796 | -0.022532 | -0.019364 | -0.08911 | -0.050029 | -0.051798 | -0.035219 | 0.20425 | 0.032725 | 0.038352 | 0.034492 | 0.072884 | 0.13136 | -0.007786 | 0.025008 | 0.12957 | 0.023244 | 0.026412 | -0.043334 | -0.004253 | -0.006022 | 0.010557 | 0.068342 | 0.03103 | 0.066578 | 0.029266
3534.3281 | 122.0718 | -0.073242 | 121.9482 | 0.14474 | -0.017627 | -0.025735 | -0.025017 | 0.017953 | 0.071848 | -0.067295 | -0.020768 | 0.088375 | -0.022532 | -0.023943 | -0.084531 | -0.054607 | -0.056376 | -0.035219 | 0.21799 | 0.055615 | 0.047507 | 0.048225 | 0.091195 | 0.14509 | 0.005947 | 0.025008 | 0.13415 | 0.023244 | 0.021833 | -0.038755 | -0.008831 | -0.0106 | 0.010557 | 0.063763 | 0.035608 | 0.061999 | 0.033844
3536.0781 | 121.9894 | -0.10986 | 121.9894 | 0.14017 | -0.017627 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.058139 | -0.011611 | 0.088375 | -0.017954 | -0.033101 | -0.084531 | -0.050029 | -0.051798 | -0.044375 | 0.25003 | 0.092236 | 0.088706 | 0.084846 | 0.13239 | 0.18171 | 0.051724 | 0.034165 | 0.13415 | 0.027822 | 0.012675 | -0.038755 | -0.004253 | -0.006022 | 0.001401 | 0.07292 | 0.040187 | 0.066577 | 0.033844
3537.7812 | 122.0306 | -0.091553 | 121.962 | 0.14017 | -0.022205 | -0.025735 | -0.01586 | 0.027109 | 0.076426 | -0.067295 | -0.01619 | 0.092954 | -0.017954 | -0.023943 | -0.079953 | -0.050029 | -0.051798 | -0.035219 | 0.23172 | 0.069348 | 0.065818 | 0.075693 | 0.11866 | 0.16798 | 0.024258 | 0.029586 | 0.13873 | 0.027822 | 0.021833 | -0.034177 | -0.004253 | -0.006022 | 0.010557 | 0.063763 | 0.035608 | 0.061999 | 0.033844
3539.5469 | 122.1176 | -0.059509 | 121.9528 | 0.14017 | -0.022205 | -0.025735 | -0.020438 | 0.022531 | 0.067269 | -0.067295 | -0.01619 | 0.092954 | -0.022532 | -0.028522 | -0.08911 | -0.054607 | -0.04722 | -0.039797 | 0.19967 | 0.037304 | 0.033774 | 0.039071 | 0.08204 | 0.12678 | -0.007786 | 0.029586 | 0.13873 | 0.023244 | 0.017254 | -0.043334 | -0.008831 | -0.001444 | 0.005979 | 0.07292 | 0.03103 | 0.066578 | 0.024688
3541.3125 | 122.1039 | -0.059509 | 121.9482 | 0.14017 | -0.026784 | -0.021157 | -0.034174 | 0.013375 | 0.076426 | -0.067295 | -0.020768 | 0.092954 | -0.017954 | -0.023943 | -0.08911 | -0.054607 | -0.056376 | -0.044375 | 0.19967 | 0.032725 | 0.038352 | 0.025335 | 0.072884 | 0.13594 | -0.007786 | 0.025008 | 0.13873 | 0.027822 | 0.021833 | -0.043334 | -0.008831 | -0.0106 | 0.001401 | 0.068342 | 0.035608 | 0.071156 | 0.038422
3543.0156 | 122.0306 | -0.082397 | 121.994 | 0.13559 | -0.022205 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.071874 | -0.01619 | 0.083796 | -0.022532 | -0.028522 | -0.084531 | -0.050029 | -0.04722 | -0.039797 | 0.21798 | 0.060192 | 0.052083 | 0.052802 | 0.10493 | 0.15424 | 0.010523 | 0.029586 | 0.12957 | 0.023244 | 0.017254 | -0.038755 | -0.004253 | -0.001444 | 0.005979 | 0.068341 | 0.03103 | 0.061999 | 0.024688
3544.7812 | 122.0078 | -0.10529 | 121.9528 | 0.14932 | -0.026784 | -0.016578 | -0.029595 | 0.017953 | 0.071848 | -0.062717 | -0.01619 | 0.092954 | -0.031689 | -0.023943 | -0.075375 | -0.054607 | -0.060955 | -0.044375 | 0.25461 | 0.078502 | 0.088708 | 0.075691 | 0.12324 | 0.17713 | 0.042569 | 0.029586 | 0.13873 | 0.014087 | 0.021833 | -0.029599 | -0.008831 | -0.015179 | 0.001401 | 0.059185 | 0.044765 | 0.043686 | 0.029266
3546.5469 | 122.0947 | -0.059509 | 121.9849 | 0.14017 | -0.017627 | -0.016578 | -0.029595 | 0.031687 | 0.071848 | -0.067295 | -0.01619 | 0.083796 | -0.017954 | -0.028522 | -0.098266 | -0.045451 | -0.051798 | -0.044375 | 0.19967 | 0.041882 | 0.042931 | 0.029914 | 0.091196 | 0.13136 | -0.007786 | 0.029586 | 0.12957 | 0.027822 | 0.017254 | -0.05249 | 0.000325 | -0.006022 | 0.001401 | 0.082076 | 0.035608 | 0.080312 | 0.033844
3548.25 | 122.0352 | -0.10071 | 121.9986 | 0.14474 | -0.022205 | -0.021157 | -0.025017 | 0.013375 | 0.076426 | -0.058139 | -0.020768 | 0.088375 | -0.022532 | -0.019364 | -0.079953 | -0.050029 | -0.056376 | -0.044375 | 0.24545 | 0.078503 | 0.079551 | 0.075691 | 0.11408 | 0.17713 | 0.042569 | 0.025008 | 0.13415 | 0.023244 | 0.026412 | -0.034177 | -0.004253 | -0.0106 | 0.001401 | 0.059185 | 0.035608 | 0.057421 | 0.033844
3550.0156 | 122.1268 | -0.059509 | 121.9162 | 0.14474 | -0.026784 | -0.021157 | -0.034174 | 0.022531 | 0.067269 | -0.062717 | -0.011611 | 0.083796 | -0.027111 | -0.023943 | -0.08911 | -0.050029 | -0.060955 | -0.039797 | 0.20425 | 0.032725 | 0.038352 | 0.025335 | 0.08204 | 0.12678 | -0.003208 | 0.034165 | 0.12957 | 0.018665 | 0.021833 | -0.043334 | -0.004253 | -0.015179 | 0.005979 | 0.077499 | 0.049344 | 0.061999 | 0.033844
3551.7812 | 122.0535 | -0.09613 | 121.9574 | 0.14932 | -0.017627 | -0.016578 | -0.029595 | 0.022531 | 0.071848 | -0.071874 | -0.01619 | 0.083796 | -0.022532 | -0.028522 | -0.093688 | -0.054607 | -0.04722 | -0.044375 | 0.24545 | 0.078503 | 0.079552 | 0.066535 | 0.11866 | 0.16798 | 0.024256 | 0.029586 | 0.12957 | 0.023244 | 0.017254 | -0.047912 | -0.008831 | -0.001444 | 0.001401 | 0.077498 | 0.03103 | 0.071156 | 0.024688
3553.5469 | 122.0261 | -0.10071 | 121.9849 | 0.14017 | -0.017627 | -0.016578 | -0.020438 | 0.017953 | 0.076426 | -0.067295 | -0.01619 | 0.088375 | -0.027111 | -0.019364 | -0.084531 | -0.050029 | -0.04722 | -0.035219 | 0.24087 | 0.083081 | 0.08413 | 0.08027 | 0.11866 | 0.17713 | 0.033413 | 0.029586 | 0.13415 | 0.018665 | 0.026412 | -0.038755 | -0.004253 | -0.001444 | 0.010557 | 0.068341 | 0.03103 | 0.05742 | 0.020109
3555.3125 | 122.081 | -0.068665 | 121.962 | 0.13559 | -0.017627 | -0.030314 | -0.029595 | 0.022531 | 0.067269 | -0.076452 | -0.01619 | 0.083796 | -0.027111 | -0.023943 | -0.084531 | -0.050029 | -0.04722 | -0.035219 | 0.20425 | 0.051038 | 0.038351 | 0.03907 | 0.091196 | 0.13593 | -0.007787 | 0.029586 | 0.12957 | 0.018665 | 0.021833 | -0.038755 | -0.004253 | -0.001444 | 0.010557 | 0.068341 | 0.03103 | 0.05742 | 0.020109
3557.0781 | 122.1268 | -0.059509 | 121.9299 | 0.14017 | -0.013048 | -0.016578 | -0.025017 | 0.027109 | 0.076426 | -0.067295 | -0.020768 | 0.088375 | -0.017954 | -0.023943 | -0.084531 | -0.054607 | -0.056376 | -0.035219 | 0.19967 | 0.046461 | 0.042931 | 0.034492 | 0.086618 | 0.13594 | -0.007786 | 0.025008 | 0.13415 | 0.027822 | 0.021833 | -0.038755 | -0.008831 | -0.0106 | 0.010557 | 0.063763 | 0.035608 | 0.066577 | 0.038422
3558.7812 | 122.113 | -0.068665 | 121.9208 | 0.14017 | -0.022205 | -0.021157 | -0.029595 | 0.022531 | 0.081005 | -0.067295 | -0.01619 | 0.088375 | -0.027111 | -0.028522 | -0.08911 | -0.050029 | -0.04722 | -0.039797 | 0.20883 | 0.04646 | 0.047508 | 0.03907 | 0.091196 | 0.14967 | 0.00137 | 0.029586 | 0.13415 | 0.018665 | 0.017254 | -0.043334 | -0.004253 | -0.001444 | 0.005979 | 0.07292 | 0.03103 | 0.061999 | 0.020109
3560.5469 | 122.0306 | -0.073242 | 121.9849 | 0.13559 | -0.017627 | -0.025735 | -0.025017 | 0.027109 | 0.076426 | -0.067295 | -0.020768 | 0.088375 | -0.022532 | -0.023943 | -0.08911 | -0.050029 | -0.051798 | -0.035219 | 0.20883 | 0.055615 | 0.047507 | 0.048225 | 0.10035 | 0.14967 | 0.005947 | 0.025008 | 0.13415 | 0.023244 | 0.021833 | -0.043334 | -0.004253 | -0.006022 | 0.010557 | 0.068342 | 0.03103 | 0.066578 | 0.029266
3562.3281 | 122.0398 | -0.09613 | 121.9711 | 0.14017 | -0.013048 | -0.030314 | -0.020438 | 0.022531 | 0.071848 | -0.067295 | -0.020768 | 0.092954 | -0.017954 | -0.028522 | -0.093688 | -0.045451 | -0.060955 | -0.039797 | 0.2363 | 0.083082 | 0.065816 | 0.075692 | 0.11866 | 0.16798 | 0.028835 | 0.025008 | 0.13873 | 0.027822 | 0.017254 | -0.047912 | 0.000325 | -0.015179 | 0.005979 | 0.07292 | 0.040187 | 0.075734 | 0.043001
3564.0938 | 122.0032 | -0.10986 | 121.9711 | 0.13559 | -0.017627 | -0.025735 | -0.025017 | 0.027109 | 0.067269 | -0.067295 | -0.01619 | 0.083796 | -0.022532 | -0.023943 | -0.084531 | -0.054607 | -0.056376 | -0.035219 | 0.24545 | 0.092236 | 0.084128 | 0.084846 | 0.13697 | 0.17713 | 0.042568 | 0.029586 | 0.12957 | 0.023244 | 0.021833 | -0.038755 | -0.008831 | -0.0106 | 0.010557 | 0.068341 | 0.040186 | 0.061999 | 0.033844
3565.7969 | 122.0627 | -0.068665 | 121.9162 | 0.14017 | -0.017627 | -0.030314 | -0.029595 | 0.027109 | 0.067269 | -0.071874 | -0.01619 | 0.088375 | -0.027111 | -0.028522 | -0.084531 | -0.054607 | -0.056376 | -0.039797 | 0.20883 | 0.051038 | 0.038351 | 0.03907 | 0.095774 | 0.13593 | -0.003209 | 0.029586 | 0.13415 | 0.018665 | 0.017254 | -0.038755 | -0.008831 | -0.0106 | 0.005979 | 0.068341 | 0.040186 | 0.05742 | 0.029265
3567.5781 | 122.113 | -0.041199 | 121.9437 | 0.14474 | -0.013048 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.01619 | 0.088375 | -0.017954 | -0.019364 | -0.084531 | -0.054607 | -0.051798 | -0.035219 | 0.18594 | 0.028151 | 0.015464 | 0.016182 | 0.06373 | 0.11305 | -0.026096 | 0.029586 | 0.13415 | 0.027822 | 0.026412 | -0.038755 | -0.008831 | -0.006022 | 0.010557 | 0.068341 | 0.035608 | 0.066577 | 0.033844
3569.2656 | 121.9849 | -0.10529 | 121.9711 | 0.14017 | -0.017627 | -0.016578 | -0.025017 | 0.022531 | 0.071848 | -0.071874 | -0.011611 | 0.088375 | -0.022532 | -0.028522 | -0.084531 | -0.054607 | -0.051798 | -0.039797 | 0.24545 | 0.087659 | 0.088708 | 0.080269 | 0.12782 | 0.17713 | 0.033412 | 0.034165 | 0.13415 | 0.023244 | 0.017254 | -0.038755 | -0.008831 | -0.006022 | 0.005979 | 0.07292 | 0.040187 | 0.061999 | 0.029266
3571.0312 | 122.0993 | -0.059509 | 121.9254 | 0.14017 | -0.013048 | -0.021157 | -0.034174 | 0.013375 | 0.067269 | -0.062717 | -0.01619 | 0.083796 | -0.022532 | -0.023943 | -0.079953 | -0.050029 | -0.051798 | -0.039797 | 0.19967 | 0.046461 | 0.038352 | 0.025335 | 0.072884 | 0.12678 | -0.003208 | 0.029586 | 0.12957 | 0.023244 | 0.021833 | -0.034177 | -0.004253 | -0.006022 | 0.005979 | 0.063763 | 0.035608 | 0.057421 | 0.029266
3572.7969 | 122.0261 | -0.091553 | 121.9574 | 0.14017 | -0.008469 | -0.021157 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.025347 | 0.079217 | -0.017954 | -0.019364 | -0.093688 | -0.045451 | -0.056376 | -0.039797 | 0.23172 | 0.083084 | 0.070396 | 0.061958 | 0.11408 | 0.1634 | 0.028836 | 0.020429 | 0.12499 | 0.027822 | 0.026412 | -0.047912 | 0.000325 | -0.0106 | 0.005979 | 0.068341 | 0.031029 | 0.075734 | 0.038422
3574.5 | 121.9803 | -0.09613 | 121.9757 | 0.14017 | -0.013048 | -0.021157 | -0.025017 | 0.027109 | 0.067269 | -0.071874 | -0.020768 | 0.092954 | -0.022532 | -0.028522 | -0.08911 | -0.050029 | -0.051798 | -0.039797 | 0.2363 | 0.083082 | 0.074973 | 0.071113 | 0.12324 | 0.1634 | 0.024256 | 0.025008 | 0.13873 | 0.023244 | 0.017254 | -0.043334 | -0.004253 | -0.006022 | 0.005979 | 0.068342 | 0.03103 | 0.066578 | 0.029266
3576.2656 | 122.1176 | -0.032043 | 121.907 | 0.13559 | -0.022205 | -0.021157 | -0.034174 | 0.017953 | 0.076426 | -0.067295 | -0.020768 | 0.088375 | -0.027111 | -0.023943 | -0.08911 | -0.050029 | -0.04722 | -0.035219 | 0.16763 | 0.009838 | 0.010886 | -0.002131 | 0.049996 | 0.10847 | -0.035252 | 0.025008 | 0.13415 | 0.018665 | 0.021833 | -0.043334 | -0.004253 | -0.001444 | 0.010557 | 0.068342 | 0.026452 | 0.061999 | 0.020109
3578.0469 | 121.9849 | -0.1236 | 121.9528 | 0.14017 | -0.017627 | -0.021157 | -0.020438 | 0.027109 | 0.067269 | -0.067295 | -0.020768 | 0.083796 | -0.031689 | -0.023943 | -0.084531 | -0.054607 | -0.056376 | -0.039797 | 0.26376 | 0.10597 | 0.10244 | 0.10316 | 0.15071 | 0.19087 | 0.056301 | 0.025008 | 0.12957 | 0.014087 | 0.021833 | -0.038755 | -0.008831 | -0.0106 | 0.005979 | 0.063763 | 0.035608 | 0.052842 | 0.024687
3579.75 | 122.1039 | -0.054932 | 121.8979 | 0.14474 | -0.017627 | -0.016578 | -0.025017 | 0.022531 | 0.067269 | -0.071874 | -0.020768 | 0.088375 | -0.027111 | -0.028522 | -0.084531 | -0.050029 | -0.051798 | -0.044375 | 0.19968 | 0.037305 | 0.038354 | 0.029915 | 0.077463 | 0.1222 | -0.016942 | 0.025008 | 0.13415 | 0.018665 | 0.017254 | -0.038755 | -0.004253 | -0.006022 | 0.001401 | 0.063763 | 0.03103 | 0.05742 | 0.024687
3581.5156 | 121.9894 | -0.11444 | 121.9574 | 0.14017 | -0.017627 | -0.021157 | -0.034174 | 0.022531 | 0.076426 | -0.067295 | -0.020768 | 0.088375 | -0.022532 | -0.033101 | -0.084531 | -0.054607 | -0.04722 | -0.044375 | 0.25461 | 0.096814 | 0.093284 | 0.080267 | 0.13697 | 0.19087 | 0.047146 | 0.025008 | 0.13415 | 0.023244 | 0.012675 | -0.038755 | -0.008831 | -0.001444 | 0.001401 | 0.063763 | 0.026452 | 0.061999 | 0.024688
3583.2812 | 122.0764 | -0.07782 | 121.9574 | 0.13101 | -0.013048 | -0.016578 | -0.029595 | 0.027109 | 0.067269 | -0.067295 | -0.020768 | 0.088375 | -0.022532 | -0.023943 | -0.084531 | -0.045451 | -0.051798 | -0.035219 | 0.20883 | 0.064772 | 0.061242 | 0.048225 | 0.10493 | 0.14509 | 0.010525 | 0.025008 | 0.13415 | 0.023244 | 0.021833 | -0.038755 | 0.000325 | -0.006022 | 0.010557 | 0.063763 | 0.03103 | 0.061999 | 0.029266
3584.9844 | 122.0169 | -0.082397 | 121.9437 | 0.13559 | -0.013048 | -0.021157 | -0.029595 | 0.022531 | 0.067269 | -0.067295 | -0.01619 | 0.083796 | -0.022532 | -0.028522 | -0.079953 | -0.054607 | -0.04722 | -0.039797 | 0.21798 | 0.069349 | 0.06124 | 0.052802 | 0.10493 | 0.14967 | 0.015102 | 0.029586 | 0.12957 | 0.023244 | 0.017254 | -0.034177 | -0.008831 | -0.001444 | 0.005979 | 0.063763 | 0.03103 | 0.057421 | 0.024688
3586.75 | 121.994 | -0.09613 | 121.9666 | 0.13559 | -0.013048 | -0.021157 | -0.025017 | 0.022531 | 0.081005 | -0.058139 | -0.025347 | 0.083796 | -0.027111 | -0.028522 | -0.084531 | -0.054607 | -0.056376 | -0.035219 | 0.23172 | 0.083082 | 0.074973 | 0.071113 | 0.11866 | 0.17713 | 0.037991 | 0.020429 | 0.12957 | 0.018665 | 0.017254 | -0.038755 | -0.008831 | -0.0106 | 0.010557 | 0.059184 | 0.031029 | 0.05742 | 0.029265
3588.5156 | 122.0718 | -0.073242 | 121.9162 | 0.14017 | -0.017627 | -0.025735 | -0.029595 | 0.017953 | 0.071848 | -0.067295 | -0.020768 | 0.079217 | -0.013376 | -0.028522 | -0.08911 | -0.045451 | -0.051798 | -0.039797 | 0.21341 | 0.055615 | 0.047507 | 0.043647 | 0.091195 | 0.14509 | 0.005947 | 0.025008 | 0.12499 | 0.0324 | 0.017254 | -0.043334 | 0.000325 | -0.006022 | 0.005979 | 0.068342 | 0.03103 | 0.075734 | 0.038422
3590.2188 | 122.0901 | -0.050354 | 121.9345 | 0.14474 | -0.022205 | -0.016578 | -0.020438 | 0.022531 | 0.071848 | -0.067295 | -0.01619 | 0.092954 | -0.022532 | -0.023943 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.1951 | 0.028149 | 0.033776 | 0.029916 | 0.072885 | 0.1222 | -0.016941 | 0.029586 | 0.13873 | 0.023244 | 0.021833 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.068341 | 0.035608 | 0.061999 | 0.029266
3591.9844 | 122.0535 | -0.073242 | 121.907 | 0.14474 | -0.013048 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.011611 | 0.079217 | -0.027111 | -0.028522 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.21799 | 0.060194 | 0.047507 | 0.048225 | 0.095773 | 0.14509 | 0.005947 | 0.034165 | 0.12499 | 0.018665 | 0.017254 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.07292 | 0.040187 | 0.05742 | 0.024687
3593.7656 | 122.0306 | -0.09613 | 121.9345 | 0.14017 | -0.013048 | -0.021157 | -0.029595 | 0.017953 | 0.076426 | -0.071874 | -0.025347 | 0.088375 | -0.027111 | -0.028522 | -0.093688 | -0.059185 | -0.056376 | -0.039797 | 0.2363 | 0.083082 | 0.074973 | 0.066535 | 0.11408 | 0.17256 | 0.024256 | 0.020429 | 0.13415 | 0.018665 | 0.017254 | -0.047912 | -0.013409 | -0.0106 | 0.005979 | 0.068341 | 0.031029 | 0.066577 | 0.029265
3595.5312 | 122.0032 | -0.12817 | 121.9574 | 0.14017 | -0.017627 | -0.021157 | -0.029595 | 0.027109 | 0.085583 | -0.067295 | -0.011611 | 0.083796 | -0.027111 | -0.033101 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.26834 | 0.11055 | 0.10702 | 0.098579 | 0.15528 | 0.21376 | 0.060879 | 0.034165 | 0.12957 | 0.018665 | 0.012675 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.07292 | 0.040187 | 0.05742 | 0.024687
3597.2969 | 122.1176 | -0.059509 | 121.9208 | 0.14017 | -0.017627 | -0.021157 | -0.025017 | 0.027109 | 0.076426 | -0.067295 | -0.020768 | 0.088375 | -0.027111 | -0.03768 | -0.084531 | -0.054607 | -0.056376 | -0.035219 | 0.19967 | 0.041882 | 0.038352 | 0.034492 | 0.086618 | 0.13594 | -0.007786 | 0.025008 | 0.13415 | 0.018665 | 0.008096 | -0.038755 | -0.008831 | -0.0106 | 0.010557 | 0.063763 | 0.035608 | 0.05742 | 0.029265
3599 | 122.0627 | -0.09613 | 121.9208 | 0.14017 | -0.013048 | -0.030314 | -0.025017 | 0.017953 | 0.062691 | -0.067295 | -0.020768 | 0.088375 | -0.017954 | -0.033101 | -0.08911 | -0.050029 | -0.056376 | -0.035219 | 0.2363 | 0.083082 | 0.065816 | 0.071113 | 0.11408 | 0.15882 | 0.028835 | 0.025008 | 0.13415 | 0.027822 | 0.012675 | -0.043334 | -0.004253 | -0.0106 | 0.010557 | 0.068342 | 0.035608 | 0.071156 | 0.038422
3600.7812 | 122.1268 | -0.045776 | 121.9299 | 0.13559 | -0.013048 | -0.021157 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.020768 | 0.088375 | -0.017954 | -0.028522 | -0.08911 | -0.059185 | -0.04722 | -0.035219 | 0.18136 | 0.032728 | 0.024619 | 0.016181 | 0.068307 | 0.11762 | -0.021519 | 0.025008 | 0.13415 | 0.027822 | 0.017254 | -0.043334 | -0.013409 | -0.001444 | 0.010557 | 0.068342 | 0.026452 | 0.071156 | 0.029266
3602.5 | 122.0169 | -0.091553 | 121.9757 | 0.14017 | -0.013048 | -0.021157 | -0.025017 | 0.022531 | 0.062691 | -0.067295 | -0.01619 | 0.088375 | -0.022532 | -0.028522 | -0.084531 | -0.050029 | -0.04722 | -0.048953 | 0.23172 | 0.078505 | 0.070396 | 0.066536 | 0.11408 | 0.15424 | 0.024258 | 0.029586 | 0.13415 | 0.023244 | 0.017254 | -0.038755 | -0.004253 | -0.001444 | -0.003177 | 0.068341 | 0.03103 | 0.061999 | 0.024688
3604.2812 | 122.0215 | -0.082397 | 121.9299 | 0.13559 | -0.013048 | -0.021157 | -0.025017 | 0.017953 | 0.076426 | -0.071874 | -0.020768 | 0.083796 | -0.031689 | -0.033101 | -0.084531 | -0.050029 | -0.04722 | -0.035219 | 0.21798 | 0.069349 | 0.06124 | 0.05738 | 0.10035 | 0.15882 | 0.010523 | 0.025008 | 0.12957 | 0.014087 | 0.012675 | -0.038755 | -0.004253 | -0.001444 | 0.010557 | 0.063763 | 0.026452 | 0.052842 | 0.015531
3605.9844 | 122.0215 | -0.086975 | 121.9666 | 0.14932 | -0.013048 | -0.025735 | -0.025017 | 0.022531 | 0.081005 | -0.062717 | -0.025347 | 0.079217 | -0.027111 | -0.028522 | -0.08911 | -0.045451 | -0.051798 | -0.035219 | 0.2363 | 0.073927 | 0.06124 | 0.061958 | 0.10951 | 0.16798 | 0.024258 | 0.020429 | 0.12499 | 0.018665 | 0.017254 | -0.043334 | 0.000325 | -0.006022 | 0.010557 | 0.063763 | 0.026451 | 0.061999 | 0.024687
3607.7656 | 122.0856 | -0.059509 | 121.9254 | 0.14474 | -0.013048 | -0.025735 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | -0.020768 | 0.083796 | -0.027111 | -0.028522 | -0.084531 | -0.045451 | -0.04722 | -0.039797 | 0.20425 | 0.046461 | 0.033774 | 0.034492 | 0.08204 | 0.12678 | -0.003208 | 0.025008 | 0.12957 | 0.018665 | 0.017254 | -0.038755 | 0.000325 | -0.001444 | 0.005979 | 0.063763 | 0.026452 | 0.05742 | 0.020109
3609.5312 | 122.0947 | -0.059509 | 121.9345 | 0.13559 | -0.013048 | -0.021157 | -0.025017 | 0.013375 | 0.076426 | -0.067295 | -0.025347 | 0.083796 | -0.031689 | -0.028522 | -0.084531 | -0.054607 | -0.04722 | -0.035219 | 0.1951 | 0.046461 | 0.038352 | 0.034492 | 0.072884 | 0.13594 | -0.007786 | 0.020429 | 0.12957 | 0.014087 | 0.017254 | -0.038755 | -0.008831 | -0.001444 | 0.010557 | 0.059184 | 0.021873 | 0.052842 | 0.015531
3611.2969 | 122.0306 | -0.10529 | 121.9666 | 0.14017 | -0.013048 | -0.012 | -0.029595 | 0.017953 | 0.081005 | -0.062717 | -0.01619 | 0.074638 | -0.027111 | -0.028522 | -0.08911 | -0.050029 | -0.051798 | -0.039797 | 0.24545 | 0.092238 | 0.093286 | 0.075691 | 0.12324 | 0.18629 | 0.042569 | 0.029586 | 0.12041 | 0.018665 | 0.017254 | -0.043334 | -0.004253 | -0.006022 | 0.005979 | 0.07292 | 0.035608 | 0.061999 | 0.024687
3613.0156 | 122.0078 | -0.09613 | 121.9574 | 0.14017 | -0.00389 | -0.012 | -0.025017 | 0.027109 | 0.067269 | -0.067295 | -0.020768 | 0.088375 | -0.022532 | -0.023943 | -0.079953 | -0.059185 | -0.056376 | -0.039797 | 0.2363 | 0.09224 | 0.08413 | 0.071113 | 0.12324 | 0.1634 | 0.028835 | 0.025008 | 0.13415 | 0.023244 | 0.021833 | -0.034177 | -0.013409 | -0.0106 | 0.005979 | 0.059185 | 0.035608 | 0.057421 | 0.033844
3614.7812 | 122.0673 | -0.059509 | 121.9437 | 0.14017 | -0.017627 | -0.025735 | -0.020438 | 0.027109 | 0.067269 | -0.067295 | -0.025347 | 0.083796 | -0.017954 | -0.028522 | -0.084531 | -0.050029 | -0.051798 | -0.044375 | 0.19967 | 0.041882 | 0.033774 | 0.039071 | 0.086618 | 0.12678 | -0.007786 | 0.020429 | 0.12957 | 0.027822 | 0.017254 | -0.038755 | -0.004253 | -0.006022 | 0.001401 | 0.059184 | 0.026451 | 0.066577 | 0.033844
3616.5625 | 122.0535 | -0.09613 | 121.9528 | 0.14474 | -0.008469 | -0.021157 | -0.025017 | 0.022531 | 0.067269 | -0.067295 | -0.025347 | 0.083796 | -0.031689 | -0.028522 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.24087 | 0.087661 | 0.074973 | 0.071113 | 0.11866 | 0.1634 | 0.028835 | 0.020429 | 0.12957 | 0.014087 | 0.017254 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.059184 | 0.026451 | 0.052842 | 0.020109
3618.2812 | 121.9437 | -0.091553 | 121.9803 | 0.14474 | -0.013048 | -0.016578 | -0.020438 | 0.027109 | 0.076426 | -0.062717 | -0.025347 | 0.079217 | -0.022532 | -0.023943 | -0.084531 | -0.059185 | -0.056376 | -0.035219 | 0.2363 | 0.078505 | 0.074975 | 0.071115 | 0.11866 | 0.16798 | 0.028836 | 0.020429 | 0.12499 | 0.023244 | 0.021833 | -0.038755 | -0.013409 | -0.0106 | 0.010557 | 0.059184 | 0.031029 | 0.061999 | 0.033844
3620.0469 | 122.0947 | -0.07782 | 121.9254 | 0.14474 | -0.013048 | -0.016578 | -0.029595 | 0.027109 | 0.076426 | -0.067295 | -0.020768 | 0.079217 | -0.027111 | -0.023943 | -0.08911 | -0.050029 | -0.056376 | -0.039797 | 0.22256 | 0.064772 | 0.061242 | 0.048225 | 0.10493 | 0.15425 | 0.010525 | 0.025008 | 0.12499 | 0.018665 | 0.021833 | -0.043334 | -0.004253 | -0.0106 | 0.005979 | 0.068342 | 0.035608 | 0.061999 | 0.029265
3621.7969 | 121.9803 | -0.11902 | 121.9666 | 0.14017 | -0.008469 | -0.021157 | -0.029595 | 0.013375 | 0.067269 | -0.067295 | -0.029925 | 0.083796 | -0.027111 | -0.023943 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.25918 | 0.11055 | 0.097862 | 0.089424 | 0.13239 | 0.18629 | 0.051724 | 0.015851 | 0.12957 | 0.018665 | 0.021833 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.054606 | 0.021873 | 0.05742 | 0.024687
3623.5625 | 122.1359 | -0.064087 | 121.9345 | 0.14017 | -0.013048 | -0.021157 | -0.029595 | 0.017953 | 0.076426 | -0.067295 | -0.020768 | 0.079217 | -0.027111 | -0.028522 | -0.098266 | -0.054607 | -0.056376 | -0.030641 | 0.20425 | 0.051039 | 0.04293 | 0.034492 | 0.08204 | 0.14051 | -0.003208 | 0.025008 | 0.12499 | 0.018665 | 0.017254 | -0.05249 | -0.008831 | -0.0106 | 0.015135 | 0.077498 | 0.035608 | 0.071155 | 0.029265
3625.3281 | 122.0169 | -0.09613 | 121.9528 | 0.14017 | -0.017627 | -0.030314 | -0.025017 | 0.022531 | 0.081005 | -0.062717 | -0.020768 | 0.088375 | -0.022532 | -0.033101 | -0.084531 | -0.054607 | -0.056376 | -0.039797 | 0.2363 | 0.078503 | 0.065816 | 0.071113 | 0.11866 | 0.17713 | 0.033413 | 0.025008 | 0.13415 | 0.023244 | 0.012675 | -0.038755 | -0.008831 | -0.0106 | 0.005979 | 0.063763 | 0.035608 | 0.061999 | 0.033844
3627.0312 | 121.994 | -0.10529 | 121.9574 | 0.14017 | -0.017627 | -0.021157 | -0.020438 | 0.017953 | 0.071848 | -0.067295 | -0.025347 | 0.079217 | -0.027111 | -0.028522 | -0.084531 | -0.050029 | -0.04722 | -0.039797 | 0.24545 | 0.087659 | 0.084129 | 0.084848 | 0.12324 | 0.17713 | 0.037991 | 0.020429 | 0.12499 | 0.018665 | 0.017254 | -0.038755 | -0.004253 | -0.001444 | 0.005979 | 0.059184 | 0.021873 | 0.05742 | 0.020109
3628.7969 | 122.0718 | -0.068665 | 121.9437 | 0.13559 | -0.017627 | -0.025735 | -0.020438 | 0.022531 | 0.071848 | -0.067295 | -0.025347 | 0.083796 | -0.022532 | -0.028522 | -0.084531 | -0.045451 | -0.051798 | -0.044375 | 0.20425 | 0.051038 | 0.04293 | 0.048227 | 0.091196 | 0.14051 | 0.00137 | 0.020429 | 0.12957 | 0.023244 | 0.017254 | -0.038755 | 0.000325 | -0.006022 | 0.001401 | 0.059184 | 0.026451 | 0.061999 | 0.029266
3630.5625 | 122.0993 | -0.059509 | 121.9391 | 0.14017 | -0.013048 | -0.025735 | -0.020438 | 0.022531 | 0.071848 | -0.067295 | -0.025347 | 0.074638 | -0.031689 | -0.023943 | -0.08911 | -0.059185 | -0.051798 | -0.039797 | 0.19967 | 0.046461 | 0.033774 | 0.039071 | 0.08204 | 0.13136 | -0.007786 | 0.020429 | 0.12041 | 0.014087 | 0.021833 | -0.043334 | -0.013409 | -0.006022 | 0.005979 | 0.063763 | 0.026451 | 0.057421 | 0.020109
3632.3438 | 122.0352 | -0.10071 | 121.962 | 0.14932 | -0.013048 | -0.016578 | -0.020438 | 0.017953 | 0.071848 | -0.067295 | -0.025347 | 0.083796 | -0.027111 | -0.028522 | -0.08911 | -0.054607 | -0.056376 | -0.035219 | 0.25003 | 0.08766 | 0.08413 | 0.08027 | 0.11866 | 0.17256 | 0.033413 | 0.020429 | 0.12957 | 0.018665 | 0.017254 | -0.043334 | -0.008831 | -0.0106 | 0.010557 | 0.063763 | 0.031029 | 0.061999 | 0.029265
3634.1094 | 121.994 | -0.09613 | 121.9666 | 0.14017 | -0.022205 | -0.030314 | -0.025017 | 0.017953 | 0.076426 | -0.062717 | -0.020768 | 0.083796 | -0.017954 | -0.033101 | -0.084531 | -0.050029 | -0.04722 | -0.039797 | 0.2363 | 0.073925 | 0.065816 | 0.071113 | 0.11408 | 0.17256 | 0.033413 | 0.025008 | 0.12957 | 0.027822 | 0.012675 | -0.038755 | -0.004253 | -0.001444 | 0.005979 | 0.063763 | 0.026452 | 0.066577 | 0.029266
3635.8125 | 122.0993 | -0.068665 | 121.9345 | 0.14474 | -0.013048 | -0.025735 | -0.025017 | 0.017953 | 0.071848 | -0.058139 | -0.020768 | 0.083796 | -0.031689 | -0.028522 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.21341 | 0.055617 | 0.04293 | 0.043648 | 0.086618 | 0.14051 | 0.010526 | 0.025008 | 0.12957 | 0.014087 | 0.017254 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.063763 | 0.03103 | 0.052842 | 0.020109
3637.5781 | 122.0901 | -0.073242 | 121.9345 | 0.14017 | -0.017627 | -0.025735 | -0.025017 | 0.027109 | 0.071848 | -0.067295 | -0.020768 | 0.088375 | -0.031689 | -0.028522 | -0.08911 | -0.045451 | -0.04722 | -0.039797 | 0.21341 | 0.055615 | 0.047507 | 0.048225 | 0.10035 | 0.14509 | 0.005947 | 0.025008 | 0.13415 | 0.014087 | 0.017254 | -0.043334 | 0.000325 | -0.001444 | 0.005979 | 0.068342 | 0.026452 | 0.057421 | 0.015531
3639.2812 | 122.0673 | -0.059509 | 121.9482 | 0.14474 | -0.026784 | -0.016578 | -0.025017 | 0.027109 | 0.071848 | -0.071874 | -0.020768 | 0.083796 | -0.027111 | -0.033101 | -0.08911 | -0.050029 | -0.051798 | -0.035219 | 0.20425 | 0.032725 | 0.042931 | 0.034492 | 0.086618 | 0.13136 | -0.012365 | 0.025008 | 0.12957 | 0.018665 | 0.012675 | -0.043334 | -0.004253 | -0.006022 | 0.010557 | 0.068342 | 0.03103 | 0.061999 | 0.024687
3641.0312 | 122.0352 | -0.07782 | 121.9757 | 0.14017 | -0.022205 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.058139 | -0.029925 | 0.079217 | -0.017954 | -0.028522 | -0.08911 | -0.050029 | -0.051798 | -0.039797 | 0.21799 | 0.055615 | 0.056663 | 0.052803 | 0.10035 | 0.14967 | 0.019681 | 0.015851 | 0.12499 | 0.027822 | 0.017254 | -0.043334 | -0.004253 | -0.006022 | 0.005979 | 0.059185 | 0.021873 | 0.071156 | 0.033844
3642.7969 | 121.9803 | -0.10071 | 121.9574 | 0.14017 | -0.013048 | -0.021157 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.025347 | 0.079217 | -0.022532 | -0.028522 | -0.08911 | -0.045451 | -0.051798 | -0.030641 | 0.24087 | 0.08766 | 0.079551 | 0.071113 | 0.12324 | 0.17256 | 0.033413 | 0.020429 | 0.12499 | 0.023244 | 0.017254 | -0.043334 | 0.000325 | -0.006022 | 0.015135 | 0.063763 | 0.026451 | 0.066578 | 0.029266
3644.5781 | 121.9894 | -0.11902 | 121.9711 | 0.14017 | -0.013048 | -0.021157 | -0.01586 | 0.027109 | 0.071848 | -0.058139 | -0.029925 | 0.079217 | -0.017954 | -0.023943 | -0.084531 | -0.045451 | -0.060955 | -0.035219 | 0.25918 | 0.10597 | 0.097862 | 0.10316 | 0.14613 | 0.19087 | 0.06088 | 0.015851 | 0.12499 | 0.027822 | 0.021833 | -0.038755 | 0.000325 | -0.015179 | 0.010557 | 0.054606 | 0.03103 | 0.066577 | 0.043001
3646.3594 | 121.9894 | -0.091553 | 121.9528 | 0.14474 | -0.022205 | -0.016578 | -0.025017 | 0.027109 | 0.067269 | -0.067295 | -0.025347 | 0.083796 | -0.027111 | -0.023943 | -0.08911 | -0.059185 | -0.051798 | -0.039797 | 0.2363 | 0.069348 | 0.074975 | 0.066536 | 0.11866 | 0.15882 | 0.024258 | 0.020429 | 0.12957 | 0.018665 | 0.021833 | -0.043334 | -0.013409 | -0.006022 | 0.005979 | 0.063763 | 0.026451 | 0.061999 | 0.024687
3648.125 | 122.081 | -0.091553 | 121.9162 | 0.14017 | -0.022205 | -0.021157 | -0.020438 | 0.027109 | 0.071848 | -0.062717 | -0.025347 | 0.074638 | -0.027111 | -0.028522 | -0.084531 | -0.045451 | -0.04722 | -0.035219 | 0.23172 | 0.069348 | 0.070396 | 0.071115 | 0.11866 | 0.1634 | 0.028836 | 0.020429 | 0.12041 | 0.018665 | 0.017254 | -0.038755 | 0.000325 | -0.001444 | 0.010557 | 0.059184 | 0.021873 | 0.05742 | 0.020109
3649.8906 | 122.0901 | -0.036621 | 121.9162 | 0.14474 | -0.013048 | -0.021157 | -0.020438 | 0.022531 | 0.067269 | -0.067295 | -0.025347 | 0.079217 | -0.022532 | -0.028522 | -0.084531 | -0.054607 | -0.04722 | -0.030641 | 0.18136 | 0.023573 | 0.015464 | 0.016183 | 0.059152 | 0.10389 | -0.030674 | 0.020429 | 0.12499 | 0.023244 | 0.017254 | -0.038755 | -0.008831 | -0.001444 | 0.015135 | 0.059184 | 0.021873 | 0.061999 | 0.024688
3651.6406 | 122.0535 | -0.073242 | 121.9345 | 0.14017 | -0.022205 | -0.025735 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | -0.025347 | 0.088375 | -0.040846 | -0.03768 | -0.08911 | -0.050029 | -0.04722 | -0.044375 | 0.21341 | 0.051037 | 0.047507 | 0.048225 | 0.095773 | 0.14051 | 0.010525 | 0.020429 | 0.13415 | 0.00493 | 0.008096 | -0.043334 | -0.004253 | -0.001444 | 0.001401 | 0.063763 | 0.021873 | 0.048264 | 0.006374
3653.3594 | 122.0306 | -0.082397 | 121.9757 | 0.14474 | -0.008469 | -0.021157 | -0.020438 | 0.022531 | 0.067269 | -0.067295 | -0.020768 | 0.074638 | -0.022532 | -0.028522 | -0.08911 | -0.045451 | -0.051798 | -0.044375 | 0.22714 | 0.073928 | 0.06124 | 0.061959 | 0.10493 | 0.14967 | 0.015102 | 0.025008 | 0.12041 | 0.023244 | 0.017254 | -0.043334 | 0.000325 | -0.006022 | 0.001401 | 0.068342 | 0.03103 | 0.066578 | 0.029266
3655.1406 | 121.9757 | -0.10529 | 121.962 | 0.14474 | -0.013048 | -0.016578 | -0.034174 | 0.022531 | 0.071848 | -0.062717 | -0.025347 | 0.083796 | -0.027111 | -0.028522 | -0.08911 | -0.045451 | -0.051798 | -0.035219 | 0.25003 | 0.092238 | 0.088708 | 0.071112 | 0.12782 | 0.17713 | 0.042569 | 0.020429 | 0.12957 | 0.018665 | 0.017254 | -0.043334 | 0.000325 | -0.006022 | 0.010557 | 0.063763 | 0.026451 | 0.061999 | 0.024687
3656.9062 | 122.0581 | -0.082397 | 121.9254 | 0.14017 | -0.017627 | -0.021157 | -0.025017 | 0.022531 | 0.076426 | -0.071874 | -0.025347 | 0.079217 | -0.027111 | -0.028522 | -0.084531 | -0.054607 | -0.051798 | -0.035219 | 0.22256 | 0.06477 | 0.06124 | 0.05738 | 0.10493 | 0.15882 | 0.010523 | 0.020429 | 0.12499 | 0.018665 | 0.017254 | -0.038755 | -0.008831 | -0.006022 | 0.010557 | 0.059184 | 0.026451 | 0.05742 | 0.024687
3658.625 | 121.9986 | -0.10529 | 121.9482 | 0.14474 | -0.013048 | -0.021157 | -0.020438 | 0.022531 | 0.071848 | -0.062717 | -0.01619 | 0.083796 | -0.031689 | -0.023943 | -0.084531 | -0.050029 | -0.051798 | -0.044375 | 0.25003 | 0.092238 | 0.084129 | 0.084848 | 0.12782 | 0.17713 | 0.042569 | 0.029586 | 0.12957 | 0.014087 | 0.021833 | -0.038755 | -0.004253 | -0.006022 | 0.001401 | 0.068341 | 0.035608 | 0.052842 | 0.020109
3660.3906 | 122.1085 | -0.064087 | 121.8979 | 0.14017 | -0.017627 | -0.025735 | -0.020438 | 0.017953 | 0.076426 | -0.071874 | -0.020768 | 0.079217 | -0.027111 | -0.028522 | -0.084531 | -0.050029 | -0.051798 | -0.048953 | 0.20425 | 0.04646 | 0.038352 | 0.043649 | 0.08204 | 0.14051 | -0.007787 | 0.025008 | 0.12499 | 0.018665 | 0.017254 | -0.038755 | -0.004253 | -0.006022 | -0.003177 | 0.063763 | 0.03103 | 0.05742 | 0.024687
3662.1562 | 122.0947 | -0.064087 | 121.9025 | 0.14474 | -0.013048 | -0.021157 | -0.025017 | 0.022531 | 0.076426 | -0.067295 | -0.025347 | 0.079217 | -0.027111 | -0.033101 | -0.08911 | -0.050029 | -0.051798 | -0.039797 | 0.20883 | 0.051039 | 0.04293 | 0.03907 | 0.086618 | 0.14051 | -0.003208 | 0.020429 | 0.12499 | 0.018665 | 0.012675 | -0.043334 | -0.004253 | -0.006022 | 0.005979 | 0.063763 | 0.026451 | 0.061999 | 0.024687
3663.8594 | 122.081 | -0.064087 | 121.9208 | 0.14017 | -0.017627 | -0.021157 | -0.020438 | 0.022531 | 0.081005 | -0.062717 | -0.01619 | 0.088375 | -0.027111 | -0.03768 | -0.08911 | -0.054607 | -0.051798 | -0.035219 | 0.20425 | 0.04646 | 0.04293 | 0.043649 | 0.086618 | 0.14509 | 0.00137 | 0.029586 | 0.13415 | 0.018665 | 0.008096 | -0.043334 | -0.008831 | -0.006022 | 0.010557 | 0.07292 | 0.035608 | 0.061999 | 0.024687
3665.6406 | 121.9757 | -0.13275 | 121.962 | 0.14017 | -0.013048 | -0.021157 | -0.025017 | 0.017953 | 0.071848 | -0.071874 | -0.025347 | 0.079217 | -0.027111 | -0.023943 | -0.079953 | -0.050029 | -0.042641 | -0.035219 | 0.27292 | 0.1197 | 0.11159 | 0.10773 | 0.1507 | 0.2046 | 0.060877 | 0.020429 | 0.12499 | 0.018665 | 0.021833 | -0.034177 | -0.004253 | 0.003135 | 0.010557 | 0.054606 | 0.017294 | 0.052842 | 0.01553
3667.4062 | 122.0856 | -0.068665 | 121.8887 | 0.14474 | -0.008469 | -0.025735 | -0.029595 | 0.027109 | 0.067269 | -0.067295 | -0.025347 | 0.083796 | -0.027111 | -0.033101 | -0.084531 | -0.050029 | -0.056376 | -0.035219 | 0.21341 | 0.060196 | 0.04293 | 0.03907 | 0.095774 | 0.13593 | 0.00137 | 0.020429 | 0.12957 | 0.018665 | 0.012675 | -0.038755 | -0.004253 | -0.0106 | 0.010557 | 0.059184 | 0.031029 | 0.05742 | 0.029265
3669.1719 | 121.9666 | -0.11444 | 121.9711 | 0.14932 | -0.017627 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.025347 | 0.083796 | -0.027111 | -0.028522 | -0.084531 | -0.054607 | -0.060955 | -0.035219 | 0.26376 | 0.096814 | 0.088706 | 0.089424 | 0.13697 | 0.18629 | 0.051724 | 0.020429 | 0.12957 | 0.018665 | 0.017254 | -0.038755 | -0.008831 | -0.015179 | 0.010557 | 0.059184 | 0.035608 | 0.05742 | 0.033844
3670.875 | 122.0169 | -0.091553 | 121.9345 | 0.14474 | -0.013048 | -0.025735 | -0.025017 | 0.022531 | 0.076426 | -0.062717 | -0.020768 | 0.083796 | -0.022532 | -0.028522 | -0.08911 | -0.054607 | -0.056376 | -0.039797 | 0.2363 | 0.078505 | 0.065818 | 0.066536 | 0.11408 | 0.16798 | 0.028836 | 0.025008 | 0.12957 | 0.023244 | 0.017254 | -0.043334 | -0.008831 | -0.0106 | 0.005979 | 0.068342 | 0.035608 | 0.066578 | 0.033844
3672.6562 | 122.0215 | -0.10071 | 121.9528 | 0.14474 | -0.013048 | -0.021157 | -0.038752 | 0.013375 | 0.076426 | -0.062717 | -0.029925 | 0.083796 | -0.031689 | -0.028522 | -0.08911 | -0.054607 | -0.056376 | -0.039797 | 0.24545 | 0.08766 | 0.079551 | 0.061956 | 0.11408 | 0.17713 | 0.037991 | 0.015851 | 0.12957 | 0.014087 | 0.017254 | -0.043334 | -0.008831 | -0.0106 | 0.005979 | 0.059185 | 0.026451 | 0.057421 | 0.024687
3674.4375 | 122.0123 | -0.10071 | 121.9528 | 0.14017 | -0.013048 | -0.016578 | -0.020438 | 0.027109 | 0.071848 | -0.067295 | -0.034504 | 0.079217 | -0.022532 | -0.03768 | -0.084531 | -0.054607 | -0.04722 | -0.044375 | 0.24087 | 0.08766 | 0.08413 | 0.08027 | 0.12782 | 0.17256 | 0.033413 | 0.011272 | 0.12499 | 0.023244 | 0.008096 | -0.038755 | -0.008831 | -0.001444 | 0.001401 | 0.050027 | 0.012716 | 0.061999 | 0.024688
3676.2031 | 122.0627 | -0.059509 | 121.9025 | 0.14474 | -0.022205 | -0.021157 | -0.034174 | 0.017953 | 0.071848 | -0.071874 | -0.011611 | 0.079217 | -0.027111 | -0.028522 | -0.08911 | -0.050029 | -0.051798 | -0.039797 | 0.20425 | 0.037304 | 0.038352 | 0.025335 | 0.077462 | 0.13136 | -0.012365 | 0.034165 | 0.12499 | 0.018665 | 0.017254 | -0.043334 | -0.004253 | -0.006022 | 0.005979 | 0.077499 | 0.040187 | 0.061999 | 0.024687
3677.9688 | 121.9711 | -0.091553 | 121.9528 | 0.13559 | -0.013048 | -0.025735 | -0.029595 | 0.027109 | 0.071848 | -0.071874 | -0.025347 | 0.079217 | -0.031689 | -0.03768 | -0.079953 | -0.045451 | -0.056376 | -0.035219 | 0.22714 | 0.078505 | 0.065818 | 0.061958 | 0.11866 | 0.1634 | 0.019679 | 0.020429 | 0.12499 | 0.014087 | 0.008096 | -0.034177 | 0.000325 | -0.0106 | 0.010557 | 0.054606 | 0.031029 | 0.048264 | 0.024687
3679.6719 | 122.0535 | -0.064087 | 121.9208 | 0.14474 | -0.013048 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.071874 | -0.025347 | 0.083796 | -0.027111 | -0.028522 | -0.084531 | -0.050029 | -0.04722 | -0.030641 | 0.20883 | 0.051039 | 0.038352 | 0.034492 | 0.086618 | 0.13594 | -0.007787 | 0.020429 | 0.12957 | 0.018665 | 0.017254 | -0.038755 | -0.004253 | -0.001444 | 0.015135 | 0.059184 | 0.021873 | 0.05742 | 0.020109
3681.4219 | 122.1085 | -0.073242 | 121.907 | 0.13559 | -0.013048 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.071874 | -0.029925 | 0.083796 | -0.027111 | -0.028522 | -0.079953 | -0.050029 | -0.051798 | -0.039797 | 0.20883 | 0.060194 | 0.047507 | 0.048225 | 0.095773 | 0.14509 | 0.001368 | 0.015851 | 0.12957 | 0.018665 | 0.017254 | -0.034177 | -0.004253 | -0.006022 | 0.005979 | 0.050028 | 0.021873 | 0.052842 | 0.024687
3683.1875 | 122.0352 | -0.086975 | 121.9208 | 0.14017 | -0.017627 | -0.016578 | -0.020438 | 0.017953 | 0.071848 | -0.071874 | -0.025347 | 0.079217 | -0.027111 | -0.028522 | -0.084531 | -0.054607 | -0.04722 | -0.039797 | 0.22714 | 0.069348 | 0.070397 | 0.066537 | 0.10493 | 0.15882 | 0.015101 | 0.020429 | 0.12499 | 0.018665 | 0.017254 | -0.038755 | -0.008831 | -0.001444 | 0.005979 | 0.059184 | 0.021873 | 0.05742 | 0.020109
3684.9531 | 121.9803 | -0.10529 | 121.9574 | 0.13559 | -0.013048 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.025347 | 0.079217 | -0.031689 | -0.028522 | -0.079953 | -0.054607 | -0.056376 | -0.039797 | 0.24087 | 0.092238 | 0.079551 | 0.080269 | 0.12782 | 0.17713 | 0.037991 | 0.020429 | 0.12499 | 0.014087 | 0.017254 | -0.034177 | -0.008831 | -0.0106 | 0.005979 | 0.054606 | 0.031029 | 0.048264 | 0.024687
3686.6719 | 122.113 | -0.064087 | 121.907 | 0.14017 | -0.017627 | -0.016578 | -0.020438 | 0.017953 | 0.067269 | -0.062717 | -0.029925 | 0.079217 | -0.027111 | -0.028522 | -0.084531 | -0.059185 | -0.04722 | -0.039797 | 0.20425 | 0.04646 | 0.047509 | 0.043649 | 0.08204 | 0.13136 | 0.00137 | 0.015851 | 0.12499 | 0.018665 | 0.017254 | -0.038755 | -0.013409 | -0.001444 | 0.005979 | 0.054606 | 0.017295 | 0.05742 | 0.020109
3688.4375 | 122.0398 | -0.086975 | 121.9162 | 0.14474 | -0.026784 | -0.021157 | -0.029595 | 0.027109 | 0.067269 | -0.067295 | -0.029925 | 0.074638 | -0.031689 | -0.023943 | -0.079953 | -0.050029 | -0.060955 | -0.044375 | 0.23172 | 0.060191 | 0.065818 | 0.05738 | 0.11408 | 0.15424 | 0.01968 | 0.015851 | 0.12041 | 0.014087 | 0.021833 | -0.034177 | -0.004253 | -0.015179 | 0.001401 | 0.050028 | 0.03103 | 0.048264 | 0.029266
3690.2188 | 122.0535 | -0.086975 | 121.9254 | 0.14474 | -0.013048 | -0.016578 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.029925 | 0.07006 | -0.027111 | -0.033101 | -0.079953 | -0.059185 | -0.051798 | -0.044375 | 0.23172 | 0.073927 | 0.070397 | 0.061958 | 0.10951 | 0.15882 | 0.01968 | 0.015851 | 0.11584 | 0.018665 | 0.012675 | -0.034177 | -0.013409 | -0.006022 | 0.001401 | 0.050028 | 0.021873 | 0.052842 | 0.024687
3691.9375 | 121.9711 | -0.091553 | 121.9437 | 0.13559 | -0.017627 | -0.016578 | -0.025017 | 0.022531 | 0.081005 | -0.062717 | -0.025347 | 0.083796 | -0.031689 | -0.028522 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.22714 | 0.073926 | 0.074975 | 0.066536 | 0.11408 | 0.17256 | 0.028836 | 0.020429 | 0.12957 | 0.014087 | 0.017254 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.059184 | 0.026451 | 0.052842 | 0.020109
3693.6875 | 122.0764 | -0.073242 | 121.9025 | 0.14474 | -0.017627 | -0.025735 | -0.025017 | 0.022531 | 0.076426 | -0.067295 | -0.029925 | 0.074638 | -0.027111 | -0.03768 | -0.075375 | -0.054607 | -0.051798 | -0.035219 | 0.21799 | 0.055615 | 0.047507 | 0.048225 | 0.095773 | 0.14967 | 0.005947 | 0.015851 | 0.12041 | 0.018665 | 0.008096 | -0.029599 | -0.008831 | -0.006022 | 0.010557 | 0.04545 | 0.021873 | 0.048264 | 0.024687
3695.4688 | 121.994 | -0.091553 | 121.9482 | 0.14017 | -0.017627 | -0.025735 | -0.020438 | 0.027109 | 0.076426 | -0.062717 | -0.034504 | 0.083796 | -0.027111 | -0.028522 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.23172 | 0.073926 | 0.065818 | 0.071115 | 0.11866 | 0.16798 | 0.028836 | 0.011272 | 0.12957 | 0.018665 | 0.017254 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.050027 | 0.017294 | 0.05742 | 0.024687
3697.1719 | 122.0901 | -0.059509 | 121.8979 | 0.14017 | -0.008469 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.025347 | 0.079217 | -0.027111 | -0.033101 | -0.08911 | -0.059185 | -0.056376 | -0.044375 | 0.19967 | 0.05104 | 0.033774 | 0.029914 | 0.08204 | 0.13136 | -0.007786 | 0.020429 | 0.12499 | 0.018665 | 0.012675 | -0.043334 | -0.013409 | -0.0106 | 0.001401 | 0.063763 | 0.031029 | 0.061999 | 0.029265
3698.9375 | 122.049 | -0.07782 | 121.9254 | 0.14474 | -0.022205 | -0.025735 | -0.029595 | 0.027109 | 0.081005 | -0.071874 | -0.029925 | 0.083796 | -0.031689 | -0.03768 | -0.084531 | -0.045451 | -0.04722 | -0.039797 | 0.22256 | 0.055615 | 0.052085 | 0.048225 | 0.10493 | 0.15882 | 0.005946 | 0.015851 | 0.12957 | 0.014087 | 0.008096 | -0.038755 | 0.000325 | -0.001444 | 0.005979 | 0.054606 | 0.017295 | 0.052842 | 0.015531
3700.7188 | 122.0901 | -0.054932 | 121.8796 | 0.14474 | -0.017627 | -0.016578 | -0.020438 | 0.027109 | 0.071848 | -0.067295 | -0.029925 | 0.074638 | -0.027111 | -0.023943 | -0.084531 | -0.054607 | -0.051798 | -0.044375 | 0.19968 | 0.037305 | 0.038354 | 0.034494 | 0.082041 | 0.12678 | -0.012363 | 0.015851 | 0.12041 | 0.018665 | 0.021833 | -0.038755 | -0.008831 | -0.006022 | 0.001401 | 0.054606 | 0.021873 | 0.05742 | 0.024687
3702.4688 | 121.9986 | -0.082397 | 121.9757 | 0.14017 | -0.017627 | -0.016578 | -0.029595 | 0.031687 | 0.076426 | -0.071874 | -0.01619 | 0.079217 | -0.027111 | -0.033101 | -0.084531 | -0.050029 | -0.056376 | -0.035219 | 0.22256 | 0.06477 | 0.065819 | 0.052802 | 0.11408 | 0.15882 | 0.010523 | 0.029586 | 0.12499 | 0.018665 | 0.012675 | -0.038755 | -0.004253 | -0.0106 | 0.010557 | 0.068341 | 0.040186 | 0.05742 | 0.029265
3704.25 | 121.9528 | -0.09613 | 121.9391 | 0.14474 | -0.022205 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.029925 | 0.074638 | -0.031689 | -0.033101 | -0.08911 | -0.050029 | -0.051798 | -0.035219 | 0.24087 | 0.073925 | 0.074973 | 0.071113 | 0.11866 | 0.16798 | 0.033413 | 0.015851 | 0.12041 | 0.014087 | 0.012675 | -0.043334 | -0.004253 | -0.006022 | 0.010557 | 0.059185 | 0.021873 | 0.057421 | 0.020109
3705.9844 | 122.049 | -0.073242 | 121.9345 | 0.14017 | -0.022205 | -0.021157 | -0.034174 | 0.022531 | 0.071848 | -0.071874 | -0.025347 | 0.079217 | -0.027111 | -0.028522 | -0.084531 | -0.050029 | -0.056376 | -0.035219 | 0.21341 | 0.051037 | 0.052085 | 0.039068 | 0.095773 | 0.14509 | 0.001368 | 0.020429 | 0.12499 | 0.018665 | 0.017254 | -0.038755 | -0.004253 | -0.0106 | 0.010557 | 0.059184 | 0.031029 | 0.05742 | 0.029265
3707.7344 | 122.0993 | -0.050354 | 121.9162 | 0.14017 | -0.013048 | -0.025735 | -0.038752 | 0.022531 | 0.071848 | -0.071874 | -0.025347 | 0.079217 | -0.031689 | -0.033101 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.19052 | 0.037306 | 0.024619 | 0.011602 | 0.072885 | 0.1222 | -0.02152 | 0.020429 | 0.12499 | 0.014087 | 0.012675 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.059184 | 0.026451 | 0.052842 | 0.020109
3709.4531 | 121.9574 | -0.11444 | 121.9528 | 0.13559 | -0.013048 | -0.021157 | -0.020438 | 0.027109 | 0.071848 | -0.062717 | -0.025347 | 0.083796 | -0.027111 | -0.023943 | -0.079953 | -0.045451 | -0.04722 | -0.030641 | 0.25003 | 0.10139 | 0.093284 | 0.094003 | 0.14155 | 0.18629 | 0.051724 | 0.020429 | 0.12957 | 0.018665 | 0.021833 | -0.034177 | 0.000325 | -0.001444 | 0.015135 | 0.054606 | 0.021873 | 0.052842 | 0.020109
3711.1875 | 122.0398 | -0.09613 | 121.9254 | 0.13559 | -0.017627 | -0.025735 | -0.029595 | 0.022531 | 0.081005 | -0.067295 | -0.029925 | 0.074638 | -0.027111 | -0.023943 | -0.08911 | -0.050029 | -0.051798 | -0.035219 | 0.23172 | 0.078503 | 0.070395 | 0.066535 | 0.11866 | 0.17713 | 0.028835 | 0.015851 | 0.12041 | 0.018665 | 0.021833 | -0.043334 | -0.004253 | -0.006022 | 0.010557 | 0.059185 | 0.021873 | 0.061999 | 0.024687
3713 | 121.9803 | -0.10529 | 121.9391 | 0.14017 | -0.017627 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.034504 | 0.074638 | -0.027111 | -0.033101 | -0.08911 | -0.059185 | -0.051798 | -0.030641 | 0.24545 | 0.087659 | 0.074972 | 0.075691 | 0.12782 | 0.17713 | 0.037991 | 0.011272 | 0.12041 | 0.018665 | 0.012675 | -0.043334 | -0.013409 | -0.006022 | 0.015135 | 0.054606 | 0.017294 | 0.061999 | 0.024687
3714.7031 | 122.0215 | -0.073242 | 121.9299 | 0.14474 | -0.017627 | -0.021157 | -0.020438 | 0.022531 | 0.071848 | -0.067295 | -0.025347 | 0.074638 | -0.036267 | -0.033101 | -0.070797 | -0.050029 | -0.051798 | -0.030641 | 0.21799 | 0.055615 | 0.052085 | 0.052804 | 0.095773 | 0.14509 | 0.005947 | 0.020429 | 0.12041 | 0.009509 | 0.012675 | -0.025021 | -0.004253 | -0.006022 | 0.015135 | 0.04545 | 0.026451 | 0.03453 | 0.015531
3716.4844 | 121.9711 | -0.10071 | 121.994 | 0.14017 | -0.013048 | -0.021157 | -0.029595 | 0.022531 | 0.076426 | -0.067295 | -0.034504 | 0.079217 | -0.031689 | -0.033101 | -0.084531 | -0.054607 | -0.056376 | -0.039797 | 0.24087 | 0.08766 | 0.079551 | 0.071113 | 0.12324 | 0.17713 | 0.033413 | 0.011272 | 0.12499 | 0.014087 | 0.012675 | -0.038755 | -0.008831 | -0.0106 | 0.005979 | 0.050027 | 0.021872 | 0.052842 | 0.024687
3718.2344 | 121.994 | -0.09613 | 121.9482 | 0.14017 | -0.017627 | -0.021157 | -0.029595 | 0.027109 | 0.067269 | -0.071874 | -0.025347 | 0.079217 | -0.027111 | -0.03768 | -0.093688 | -0.054607 | -0.051798 | -0.039797 | 0.2363 | 0.078503 | 0.074973 | 0.066535 | 0.12324 | 0.1634 | 0.024256 | 0.020429 | 0.12499 | 0.018665 | 0.008096 | -0.047912 | -0.008831 | -0.006022 | 0.005979 | 0.068341 | 0.026451 | 0.066577 | 0.024687
3720 | 122.0032 | -0.10986 | 121.9574 | 0.14017 | -0.008469 | -0.021157 | -0.029595 | 0.022531 | 0.081005 | -0.067295 | -0.034504 | 0.079217 | -0.027111 | -0.033101 | -0.079953 | -0.050029 | -0.04722 | -0.035219 | 0.25003 | 0.10139 | 0.088706 | 0.080268 | 0.13239 | 0.19087 | 0.042568 | 0.011272 | 0.12499 | 0.018665 | 0.012675 | -0.034177 | -0.004253 | -0.001444 | 0.010557 | 0.045449 | 0.012716 | 0.052842 | 0.020109
3721.7656 | 121.9482 | -0.10529 | 121.9391 | 0.14017 | -0.008469 | -0.021157 | -0.029595 | 0.022531 | 0.076426 | -0.071874 | -0.034504 | 0.074638 | -0.022532 | -0.033101 | -0.084531 | -0.054607 | -0.051798 | -0.039797 | 0.24545 | 0.096817 | 0.084129 | 0.075691 | 0.12782 | 0.18171 | 0.033412 | 0.011272 | 0.12041 | 0.023244 | 0.012675 | -0.038755 | -0.008831 | -0.006022 | 0.005979 | 0.050027 | 0.017294 | 0.061999 | 0.029266
3723.4688 | 122.1085 | -0.064087 | 121.8979 | 0.14017 | -0.017627 | -0.016578 | -0.029595 | 0.017953 | 0.067269 | -0.067295 | -0.025347 | 0.079217 | -0.031689 | -0.033101 | -0.079953 | -0.045451 | -0.04722 | -0.035219 | 0.20425 | 0.04646 | 0.047509 | 0.034492 | 0.08204 | 0.13136 | -0.003208 | 0.020429 | 0.12499 | 0.014087 | 0.012675 | -0.034177 | 0.000325 | -0.001444 | 0.010557 | 0.054606 | 0.021873 | 0.048264 | 0.015531
3725.25 | 121.9666 | -0.10071 | 121.9254 | 0.13559 | -0.008469 | -0.016578 | -0.025017 | 0.017953 | 0.067269 | -0.067295 | -0.029925 | 0.074638 | -0.031689 | -0.033101 | -0.084531 | -0.050029 | -0.056376 | -0.039797 | 0.23629 | 0.092239 | 0.08413 | 0.075691 | 0.11866 | 0.16798 | 0.033413 | 0.015851 | 0.12041 | 0.014087 | 0.012675 | -0.038755 | -0.004253 | -0.0106 | 0.005979 | 0.054606 | 0.026451 | 0.052842 | 0.024687
3727 | 121.9437 | -0.10986 | 121.9345 | 0.14017 | -0.013048 | -0.021157 | -0.029595 | 0.027109 | 0.071848 | -0.062717 | -0.025347 | 0.074638 | -0.027111 | -0.03768 | -0.079953 | -0.045451 | -0.04722 | -0.035219 | 0.25003 | 0.096815 | 0.088706 | 0.080268 | 0.13697 | 0.18171 | 0.047146 | 0.020429 | 0.12041 | 0.018665 | 0.008096 | -0.034177 | 0.000325 | -0.001444 | 0.010557 | 0.054606 | 0.021873 | 0.052842 | 0.020109
3728.7031 | 121.9574 | -0.10529 | 121.9299 | 0.13559 | -0.013048 | -0.025735 | -0.025017 | 0.017953 | 0.076426 | -0.071874 | -0.034504 | 0.065481 | -0.027111 | -0.028522 | -0.084531 | -0.054607 | -0.051798 | -0.039797 | 0.24087 | 0.092238 | 0.079551 | 0.080269 | 0.12324 | 0.18171 | 0.033412 | 0.011272 | 0.11126 | 0.018665 | 0.017254 | -0.038755 | -0.008831 | -0.006022 | 0.005979 | 0.050027 | 0.017294 | 0.05742 | 0.024687
3730.4688 | 121.9803 | -0.11902 | 121.9528 | 0.14017 | -0.017627 | -0.021157 | -0.029595 | 0.027109 | 0.076426 | -0.062717 | -0.034504 | 0.079217 | -0.031689 | -0.033101 | -0.084531 | -0.045451 | -0.04722 | -0.035219 | 0.25918 | 0.10139 | 0.097862 | 0.089424 | 0.14613 | 0.19544 | 0.056302 | 0.011272 | 0.12499 | 0.014087 | 0.012675 | -0.038755 | 0.000325 | -0.001444 | 0.010557 | 0.050027 | 0.012716 | 0.052842 | 0.015531
3732.2188 | 122.0673 | -0.073242 | 121.8933 | 0.14017 | -0.013048 | -0.016578 | -0.025017 | 0.022531 | 0.076426 | -0.076452 | -0.029925 | 0.083796 | -0.027111 | -0.028522 | -0.08911 | -0.054607 | -0.051798 | -0.035219 | 0.21341 | 0.060194 | 0.056664 | 0.048225 | 0.095773 | 0.14967 | -0.00321 | 0.015851 | 0.12957 | 0.018665 | 0.017254 | -0.043334 | -0.008831 | -0.006022 | 0.010557 | 0.059185 | 0.021873 | 0.061999 | 0.024687
3733.9844 | 121.994 | -0.09613 | 121.9391 | 0.14474 | -0.013048 | -0.025735 | -0.029595 | 0.027109 | 0.071848 | -0.067295 | -0.034504 | 0.083796 | -0.027111 | -0.042259 | -0.084531 | -0.045451 | -0.04722 | -0.035219 | 0.24087 | 0.083082 | 0.070395 | 0.066535 | 0.12324 | 0.16798 | 0.028835 | 0.011272 | 0.12957 | 0.018665 | 0.003517 | -0.038755 | 0.000325 | -0.001444 | 0.010557 | 0.050027 | 0.012716 | 0.05742 | 0.020109
3735.7031 | 122.0764 | -0.059509 | 121.9025 | 0.13559 | -0.013048 | -0.030314 | -0.020438 | 0.022531 | 0.071848 | -0.067295 | -0.029925 | 0.079217 | -0.031689 | -0.028522 | -0.08911 | -0.050029 | -0.051798 | -0.035219 | 0.1951 | 0.046461 | 0.029195 | 0.039071 | 0.08204 | 0.13136 | -0.007786 | 0.015851 | 0.12499 | 0.014087 | 0.017254 | -0.043334 | -0.004253 | -0.006022 | 0.010557 | 0.059185 | 0.021873 | 0.057421 | 0.020109
3737.4688 | 121.9666 | -0.11902 | 121.9482 | 0.14474 | -0.017627 | -0.021157 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.029925 | 0.07006 | -0.022532 | -0.03768 | -0.08911 | -0.040873 | -0.042641 | -0.039797 | 0.26376 | 0.10139 | 0.097862 | 0.089424 | 0.14155 | 0.19087 | 0.056302 | 0.015851 | 0.11584 | 0.023244 | 0.008096 | -0.043334 | 0.004903 | 0.003135 | 0.005979 | 0.059185 | 0.012716 | 0.066578 | 0.020109
3739.2344 | 122.0901 | -0.064087 | 121.9162 | 0.14474 | -0.017627 | -0.021157 | -0.029595 | 0.027109 | 0.071848 | -0.067295 | -0.025347 | 0.083796 | -0.027111 | -0.033101 | -0.075375 | -0.045451 | -0.04722 | -0.035219 | 0.20883 | 0.04646 | 0.04293 | 0.034492 | 0.091196 | 0.13594 | -0.003208 | 0.020429 | 0.12957 | 0.018665 | 0.012675 | -0.029599 | 0.000325 | -0.001444 | 0.010557 | 0.050028 | 0.021873 | 0.048264 | 0.020109
3741 | 122.081 | -0.073242 | 121.9025 | 0.14017 | -0.017627 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.025347 | 0.074638 | -0.031689 | -0.033101 | -0.079953 | -0.054607 | -0.051798 | -0.035219 | 0.21341 | 0.055615 | 0.052085 | 0.048225 | 0.095773 | 0.14509 | 0.005947 | 0.020429 | 0.12041 | 0.014087 | 0.012675 | -0.034177 | -0.008831 | -0.006022 | 0.010557 | 0.054606 | 0.026451 | 0.048264 | 0.020109
3742.7031 | 122.081 | -0.045776 | 121.9162 | 0.13559 | -0.017627 | -0.025735 | -0.029595 | 0.027109 | 0.067269 | -0.071874 | -0.029925 | 0.074638 | -0.031689 | -0.033101 | -0.084531 | -0.045451 | -0.051798 | -0.039797 | 0.18136 | 0.028149 | 0.020041 | 0.016181 | 0.072885 | 0.11304 | -0.026098 | 0.015851 | 0.12041 | 0.014087 | 0.012675 | -0.038755 | 0.000325 | -0.006022 | 0.005979 | 0.054606 | 0.021873 | 0.052842 | 0.020109
3744.4688 | 122.0856 | -0.036621 | 121.9025 | 0.13559 | -0.022205 | -0.021157 | -0.020438 | 0.022531 | 0.076426 | -0.071874 | -0.025347 | 0.074638 | -0.027111 | -0.033101 | -0.084531 | -0.054607 | -0.051798 | -0.035219 | 0.17221 | 0.014416 | 0.015464 | 0.016183 | 0.059152 | 0.11305 | -0.035253 | 0.020429 | 0.12041 | 0.018665 | 0.012675 | -0.038755 | -0.008831 | -0.006022 | 0.010557 | 0.059184 | 0.026451 | 0.05742 | 0.024687
3746.25 | 122.049 | -0.054932 | 121.9025 | 0.13559 | -0.022205 | -0.025735 | -0.020438 | 0.022531 | 0.071848 | -0.067295 | -0.029925 | 0.07006 | -0.031689 | -0.03768 | -0.084531 | -0.054607 | -0.04722 | -0.039797 | 0.19052 | 0.032727 | 0.029197 | 0.034494 | 0.077463 | 0.12678 | -0.012363 | 0.015851 | 0.11584 | 0.014087 | 0.008096 | -0.038755 | -0.008831 | -0.001444 | 0.005979 | 0.054606 | 0.017295 | 0.052842 | 0.015531
3747.9531 | 122.0764 | -0.073242 | 121.907 | 0.13559 | -0.017627 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.076452 | -0.034504 | 0.079217 | -0.031689 | -0.028522 | -0.093688 | -0.045451 | -0.056376 | -0.039797 | 0.20883 | 0.055615 | 0.047507 | 0.043647 | 0.095773 | 0.14509 | -0.00321 | 0.011272 | 0.12499 | 0.014087 | 0.017254 | -0.047912 | 0.000325 | -0.0106 | 0.005979 | 0.059184 | 0.021872 | 0.061999 | 0.024687
3749.7188 | 121.9711 | -0.09613 | 121.9299 | 0.14932 | -0.013048 | -0.025735 | -0.029595 | 0.027109 | 0.071848 | -0.062717 | -0.034504 | 0.074638 | -0.031689 | -0.042259 | -0.079953 | -0.050029 | -0.056376 | -0.035219 | 0.24545 | 0.083082 | 0.070395 | 0.066535 | 0.12324 | 0.16798 | 0.033413 | 0.011272 | 0.12041 | 0.014087 | 0.003517 | -0.034177 | -0.004253 | -0.0106 | 0.010557 | 0.045449 | 0.021872 | 0.048264 | 0.024687
3751.4844 | 122.0306 | -0.07782 | 121.9025 | 0.14017 | -0.008469 | -0.025735 | -0.025017 | 0.031687 | 0.071848 | -0.071874 | -0.034504 | 0.074638 | -0.031689 | -0.033101 | -0.084531 | -0.045451 | -0.051798 | -0.035219 | 0.21799 | 0.069351 | 0.052085 | 0.052803 | 0.10951 | 0.14967 | 0.005946 | 0.011272 | 0.12041 | 0.014087 | 0.012675 | -0.038755 | 0.000325 | -0.006022 | 0.010557 | 0.050027 | 0.017294 | 0.052842 | 0.020109
3753.1875 | 122.0398 | -0.045776 | 121.8796 | 0.14017 | -0.017627 | -0.025735 | -0.029595 | 0.017953 | 0.067269 | -0.071874 | -0.029925 | 0.07006 | -0.027111 | -0.023943 | -0.070797 | -0.054607 | -0.042641 | -0.035219 | 0.18594 | 0.028149 | 0.020041 | 0.016181 | 0.063729 | 0.11304 | -0.026098 | 0.015851 | 0.11584 | 0.018665 | 0.021833 | -0.025021 | -0.008831 | 0.003135 | 0.010557 | 0.040872 | 0.012716 | 0.043686 | 0.01553
3754.8906 | 121.9803 | -0.09613 | 121.9299 | 0.14017 | -0.013048 | -0.030314 | -0.025017 | 0.027109 | 0.076426 | -0.071874 | -0.029925 | 0.083796 | -0.027111 | -0.03768 | -0.08911 | -0.050029 | -0.051798 | -0.044375 | 0.2363 | 0.083082 | 0.065816 | 0.071113 | 0.12324 | 0.17256 | 0.024256 | 0.015851 | 0.12957 | 0.018665 | 0.008096 | -0.043334 | -0.004253 | -0.006022 | 0.001401 | 0.059185 | 0.021873 | 0.061999 | 0.024687
3756.6562 | 121.9299 | -0.11444 | 121.9345 | 0.14017 | -0.017627 | -0.021157 | -0.029595 | 0.017953 | 0.071848 | -0.071874 | -0.029925 | 0.079217 | -0.022532 | -0.028522 | -0.084531 | -0.054607 | -0.04722 | -0.044375 | 0.25461 | 0.096814 | 0.093284 | 0.084846 | 0.13239 | 0.18629 | 0.042567 | 0.015851 | 0.12499 | 0.023244 | 0.017254 | -0.038755 | -0.008831 | -0.001444 | 0.001401 | 0.054606 | 0.017295 | 0.061999 | 0.024688
3758.375 | 121.9574 | -0.10071 | 121.9299 | 0.13559 | -0.013048 | -0.030314 | -0.025017 | 0.031687 | 0.076426 | -0.058139 | -0.039082 | 0.074638 | -0.031689 | -0.028522 | -0.084531 | -0.054607 | -0.056376 | -0.030641 | 0.23629 | 0.08766 | 0.070394 | 0.075691 | 0.1324 | 0.17713 | 0.042569 | 0.006694 | 0.12041 | 0.014087 | 0.017254 | -0.038755 | -0.008831 | -0.0106 | 0.015135 | 0.045449 | 0.017294 | 0.052842 | 0.024687
3760.1406 | 122.0856 | -0.054932 | 121.8842 | 0.13559 | -0.017627 | -0.025735 | -0.029595 | 0.017953 | 0.076426 | -0.067295 | -0.039082 | 0.083796 | -0.027111 | -0.033101 | -0.08911 | -0.054607 | -0.056376 | -0.039797 | 0.19052 | 0.037305 | 0.029197 | 0.025337 | 0.072885 | 0.13136 | -0.012363 | 0.006694 | 0.12957 | 0.018665 | 0.012675 | -0.043334 | -0.008831 | -0.0106 | 0.005979 | 0.050028 | 0.017294 | 0.061999 | 0.029265
3761.9062 | 122.081 | -0.073242 | 121.8979 | 0.14017 | -0.013048 | -0.016578 | -0.020438 | 0.022531 | 0.071848 | -0.067295 | -0.029925 | 0.074638 | -0.031689 | -0.033101 | -0.079953 | -0.050029 | -0.051798 | -0.039797 | 0.21341 | 0.060194 | 0.056664 | 0.052804 | 0.095773 | 0.14509 | 0.005947 | 0.015851 | 0.12041 | 0.014087 | 0.012675 | -0.034177 | -0.004253 | -0.006022 | 0.005979 | 0.050028 | 0.021873 | 0.048264 | 0.020109
3763.6094 | 121.9574 | -0.10071 | 121.9299 | 0.14017 | -0.008469 | -0.021157 | -0.029595 | 0.027109 | 0.071848 | -0.067295 | -0.034504 | 0.074638 | -0.031689 | -0.03768 | -0.084531 | -0.054607 | -0.04722 | -0.039797 | 0.24087 | 0.092239 | 0.079551 | 0.071113 | 0.12782 | 0.17256 | 0.033413 | 0.011272 | 0.12041 | 0.014087 | 0.008096 | -0.038755 | -0.008831 | -0.001444 | 0.005979 | 0.050027 | 0.012716 | 0.052842 | 0.015531
3765.375 | 122.113 | -0.050354 | 121.8887 | 0.14017 | -0.013048 | -0.021157 | -0.034174 | 0.017953 | 0.076426 | -0.067295 | -0.025347 | 0.074638 | -0.031689 | -0.033101 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.19052 | 0.037306 | 0.029197 | 0.01618 | 0.068307 | 0.12678 | -0.016941 | 0.020429 | 0.12041 | 0.014087 | 0.012675 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.059184 | 0.026451 | 0.052842 | 0.020109
3767.1562 | 122.0764 | -0.054932 | 121.9482 | 0.13559 | -0.013048 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.034504 | 0.065481 | -0.040846 | -0.033101 | -0.093688 | -0.050029 | -0.04722 | -0.039797 | 0.19052 | 0.041884 | 0.029197 | 0.025337 | 0.077463 | 0.12678 | -0.012363 | 0.011272 | 0.11126 | 0.00493 | 0.012675 | -0.047912 | -0.004253 | -0.001444 | 0.005979 | 0.059184 | 0.012716 | 0.052842 | 0.006374
3768.9219 | 122.081 | -0.041199 | 121.875 | 0.14017 | -0.008469 | -0.016578 | -0.029595 | 0.017953 | 0.071848 | -0.062717 | -0.025347 | 0.07006 | -0.031689 | -0.023943 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.18136 | 0.03273 | 0.024621 | 0.011604 | 0.059152 | 0.11305 | -0.021518 | 0.020429 | 0.11584 | 0.014087 | 0.021833 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.059184 | 0.026451 | 0.052842 | 0.020109
3770.6406 | 121.9757 | -0.086975 | 121.9208 | 0.14017 | -0.017627 | -0.012 | -0.020438 | 0.027109 | 0.071848 | -0.062717 | -0.029925 | 0.079217 | -0.031689 | -0.033101 | -0.084531 | -0.050029 | -0.042641 | -0.044375 | 0.22714 | 0.069348 | 0.074975 | 0.066537 | 0.11408 | 0.15882 | 0.024258 | 0.015851 | 0.12499 | 0.014087 | 0.012675 | -0.038755 | -0.004253 | 0.003135 | 0.001401 | 0.054606 | 0.012716 | 0.052842 | 0.010952
3772.4062 | 122.0032 | -0.10071 | 121.9162 | 0.13559 | -0.022205 | -0.025735 | -0.025017 | 0.027109 | 0.062691 | -0.062717 | -0.034504 | 0.074638 | -0.031689 | -0.033101 | -0.079953 | -0.059185 | -0.056376 | -0.044375 | 0.23629 | 0.078503 | 0.074973 | 0.075691 | 0.12782 | 0.1634 | 0.037991 | 0.011272 | 0.12041 | 0.014087 | 0.012675 | -0.034177 | -0.013409 | -0.0106 | 0.001401 | 0.045449 | 0.021872 | 0.048264 | 0.024687
3774.1094 | 121.9803 | -0.10529 | 121.9574 | 0.14474 | -0.013048 | -0.021157 | -0.025017 | 0.022531 | 0.076426 | -0.071874 | -0.039082 | 0.074638 | -0.031689 | -0.023943 | -0.079953 | -0.050029 | -0.042641 | -0.035219 | 0.25003 | 0.092238 | 0.084129 | 0.080269 | 0.12782 | 0.18171 | 0.033412 | 0.006694 | 0.12041 | 0.014087 | 0.021833 | -0.034177 | -0.004253 | 0.003135 | 0.010557 | 0.040871 | 0.003559 | 0.048264 | 0.010952
3775.9062 | 122.0947 | -0.059509 | 121.8842 | 0.14017 | -0.013048 | -0.021157 | -0.020438 | 0.022531 | 0.071848 | -0.067295 | -0.039082 | 0.074638 | -0.027111 | -0.033101 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.19967 | 0.046461 | 0.038352 | 0.039071 | 0.08204 | 0.13136 | -0.007786 | 0.006694 | 0.12041 | 0.018665 | 0.012675 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.045449 | 0.012716 | 0.05742 | 0.024687
3777.6875 | 121.994 | -0.10529 | 121.9162 | 0.14017 | -0.008469 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.071874 | -0.039082 | 0.079217 | -0.036267 | -0.028522 | -0.084531 | -0.040873 | -0.04722 | -0.039797 | 0.24545 | 0.096817 | 0.079551 | 0.080269 | 0.12782 | 0.17713 | 0.033412 | 0.006694 | 0.12499 | 0.009509 | 0.017254 | -0.038755 | 0.004903 | -0.001444 | 0.005979 | 0.045449 | 0.008138 | 0.048264 | 0.010953
3779.4375 | 121.9666 | -0.09613 | 121.9254 | 0.14474 | -0.013048 | -0.016578 | -0.025017 | 0.017953 | 0.067269 | -0.067295 | -0.039082 | 0.074638 | -0.036267 | -0.03768 | -0.084531 | -0.045451 | -0.051798 | -0.039797 | 0.24087 | 0.083082 | 0.079552 | 0.071113 | 0.11408 | 0.1634 | 0.028835 | 0.006694 | 0.12041 | 0.009509 | 0.008096 | -0.038755 | 0.000325 | -0.006022 | 0.005979 | 0.045449 | 0.012716 | 0.048264 | 0.015531
3781.1562 | 121.994 | -0.082397 | 121.907 | 0.14017 | -0.013048 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.039082 | 0.07006 | -0.040846 | -0.033101 | -0.084531 | -0.045451 | -0.051798 | -0.039797 | 0.22256 | 0.069349 | 0.06124 | 0.05738 | 0.10493 | 0.15424 | 0.015102 | 0.006694 | 0.11584 | 0.00493 | 0.012675 | -0.038755 | 0.000325 | -0.006022 | 0.005979 | 0.045449 | 0.012716 | 0.043685 | 0.010952
3782.9219 | 121.9528 | -0.091553 | 121.9208 | 0.13559 | -0.026784 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.039082 | 0.065481 | -0.031689 | -0.03768 | -0.084531 | -0.054607 | -0.04722 | -0.035219 | 0.22714 | 0.064769 | 0.061239 | 0.061958 | 0.11408 | 0.1634 | 0.028836 | 0.006694 | 0.11126 | 0.014087 | 0.008096 | -0.038755 | -0.008831 | -0.001444 | 0.010557 | 0.045449 | 0.008138 | 0.052842 | 0.015531
3784.6719 | 121.9666 | -0.1236 | 121.9437 | 0.14474 | -0.00389 | -0.025735 | -0.025017 | 0.022531 | 0.076426 | -0.067295 | -0.034504 | 0.074638 | -0.036267 | -0.028522 | -0.084531 | -0.054607 | -0.051798 | -0.039797 | 0.26834 | 0.11971 | 0.097861 | 0.098579 | 0.14613 | 0.20002 | 0.056301 | 0.011272 | 0.12041 | 0.009509 | 0.017254 | -0.038755 | -0.008831 | -0.006022 | 0.005979 | 0.050027 | 0.017294 | 0.048264 | 0.015531
3786.4375 | 122.0673 | -0.054932 | 121.9162 | 0.14017 | -0.031363 | -0.030314 | -0.025017 | 0.027109 | 0.071848 | -0.076452 | -0.043661 | 0.07006 | -0.031689 | -0.023943 | -0.084531 | -0.054607 | -0.051798 | -0.039797 | 0.1951 | 0.023569 | 0.024618 | 0.029915 | 0.082041 | 0.12678 | -0.02152 | 0.002115 | 0.11584 | 0.014087 | 0.021833 | -0.038755 | -0.008831 | -0.006022 | 0.005979 | 0.04087 | 0.008137 | 0.052842 | 0.020109
3788.1406 | 122.0718 | -0.041199 | 121.8842 | 0.14474 | -0.022205 | -0.030314 | -0.029595 | 0.017953 | 0.076426 | -0.067295 | -0.034504 | 0.07006 | -0.031689 | -0.03768 | -0.08911 | -0.045451 | -0.051798 | -0.035219 | 0.18594 | 0.018994 | 0.010885 | 0.011604 | 0.059152 | 0.11762 | -0.026096 | 0.011272 | 0.11584 | 0.014087 | 0.008096 | -0.043334 | 0.000325 | -0.006022 | 0.010557 | 0.054606 | 0.017294 | 0.057421 | 0.020109
3789.9219 | 121.9254 | -0.09613 | 121.9208 | 0.14017 | -0.017627 | -0.025735 | -0.029595 | 0.017953 | 0.067269 | -0.062717 | -0.034504 | 0.07006 | -0.027111 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.044375 | 0.2363 | 0.078503 | 0.070395 | 0.066535 | 0.11408 | 0.1634 | 0.033413 | 0.011272 | 0.11584 | 0.018665 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.001401 | 0.050027 | 0.017294 | 0.05742 | 0.024687
3791.7031 | 121.9345 | -0.091553 | 121.9116 | 0.14017 | -0.017627 | -0.021157 | -0.034174 | 0.027109 | 0.081005 | -0.062717 | -0.034504 | 0.074638 | -0.036267 | -0.033101 | -0.084531 | -0.050029 | -0.051798 | -0.030641 | 0.23172 | 0.073926 | 0.070396 | 0.057379 | 0.11866 | 0.17256 | 0.028836 | 0.011272 | 0.12041 | 0.009509 | 0.012675 | -0.038755 | -0.004253 | -0.006022 | 0.015135 | 0.050027 | 0.017294 | 0.048264 | 0.015531
3793.4062 | 122.0993 | -0.045776 | 121.875 | 0.14017 | -0.022205 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.029925 | 0.07006 | -0.031689 | -0.033101 | -0.084531 | -0.059185 | -0.04722 | -0.044375 | 0.18594 | 0.023571 | 0.024619 | 0.020759 | 0.068307 | 0.11762 | -0.021519 | 0.015851 | 0.11584 | 0.014087 | 0.012675 | -0.038755 | -0.013409 | -0.001444 | 0.001401 | 0.054606 | 0.017295 | 0.052842 | 0.015531
3795.1562 | 121.9391 | -0.1236 | 121.9162 | 0.14017 | -0.026784 | -0.021157 | -0.029595 | 0.022531 | 0.071848 | -0.071874 | -0.039082 | 0.07006 | -0.027111 | -0.028522 | -0.079953 | -0.050029 | -0.056376 | -0.035219 | 0.26376 | 0.096812 | 0.10244 | 0.094001 | 0.14613 | 0.19544 | 0.051722 | 0.006694 | 0.11584 | 0.018665 | 0.017254 | -0.034177 | -0.004253 | -0.0106 | 0.010557 | 0.040871 | 0.017294 | 0.052842 | 0.029265
3796.8594 | 121.962 | -0.10071 | 121.9254 | 0.14474 | -0.017627 | -0.025735 | -0.020438 | 0.027109 | 0.081005 | -0.071874 | -0.039082 | 0.07006 | -0.031689 | -0.03768 | -0.079953 | -0.054607 | -0.04722 | -0.035219 | 0.24545 | 0.083081 | 0.074973 | 0.08027 | 0.12782 | 0.18171 | 0.028834 | 0.006694 | 0.11584 | 0.014087 | 0.008096 | -0.034177 | -0.008831 | -0.001444 | 0.010557 | 0.040871 | 0.008138 | 0.048264 | 0.015531
3798.625 | 122.0444 | -0.045776 | 121.8842 | 0.14017 | -0.022205 | -0.021157 | -0.029595 | 0.031687 | 0.067269 | -0.067295 | -0.043661 | 0.074638 | -0.040846 | -0.03768 | -0.084531 | -0.054607 | -0.051798 | -0.039797 | 0.18594 | 0.023571 | 0.024619 | 0.016181 | 0.077463 | 0.11304 | -0.021519 | 0.002115 | 0.12041 | 0.00493 | 0.008096 | -0.038755 | -0.008831 | -0.006022 | 0.005979 | 0.04087 | 0.008137 | 0.043685 | 0.010952
3800.3906 | 121.9757 | -0.1236 | 121.9208 | 0.14017 | -0.022205 | -0.016578 | -0.025017 | 0.017953 | 0.076426 | -0.067295 | -0.039082 | 0.079217 | -0.040846 | -0.033101 | -0.08911 | -0.054607 | -0.051798 | -0.039797 | 0.26376 | 0.10139 | 0.10702 | 0.098579 | 0.14155 | 0.20002 | 0.056301 | 0.006694 | 0.12499 | 0.00493 | 0.012675 | -0.043334 | -0.008831 | -0.006022 | 0.005979 | 0.050028 | 0.012716 | 0.048264 | 0.010952
3802.0938 | 121.9391 | -0.09613 | 121.9391 | 0.14017 | -0.013048 | -0.025735 | -0.020438 | 0.027109 | 0.071848 | -0.062717 | -0.034504 | 0.074638 | -0.031689 | -0.033101 | -0.084531 | -0.045451 | -0.056376 | -0.039797 | 0.2363 | 0.083082 | 0.070395 | 0.075692 | 0.12324 | 0.16798 | 0.033413 | 0.011272 | 0.12041 | 0.014087 | 0.012675 | -0.038755 | 0.000325 | -0.0106 | 0.005979 | 0.050027 | 0.021872 | 0.052842 | 0.024687
3803.8594 | 122.0718 | -0.041199 | 121.8796 | 0.13559 | -0.013048 | -0.021157 | -0.034174 | 0.022531 | 0.071848 | -0.071874 | -0.034504 | 0.074638 | -0.036267 | -0.033101 | -0.084531 | -0.045451 | -0.051798 | -0.030641 | 0.17679 | 0.028151 | 0.020042 | 0.007025 | 0.06373 | 0.11305 | -0.030675 | 0.011272 | 0.12041 | 0.009509 | 0.012675 | -0.038755 | 0.000325 | -0.006022 | 0.015135 | 0.050027 | 0.017294 | 0.048264 | 0.015531
3805.625 | 121.9894 | -0.10529 | 121.8979 | 0.14017 | -0.013048 | -0.025735 | -0.025017 | 0.013375 | 0.067269 | -0.067295 | -0.034504 | 0.07006 | -0.040846 | -0.042259 | -0.079953 | -0.054607 | -0.04722 | -0.030641 | 0.24545 | 0.092238 | 0.079551 | 0.080269 | 0.11866 | 0.17256 | 0.037991 | 0.011272 | 0.11584 | 0.00493 | 0.003517 | -0.034177 | -0.008831 | -0.001444 | 0.015135 | 0.045449 | 0.012716 | 0.039107 | 0.006374
3807.3906 | 121.9986 | -0.10071 | 121.907 | 0.14017 | -0.017627 | -0.016578 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.029925 | 0.07006 | -0.036267 | -0.03768 | -0.079953 | -0.045451 | -0.051798 | -0.030641 | 0.24087 | 0.083081 | 0.08413 | 0.071113 | 0.12324 | 0.17256 | 0.037991 | 0.015851 | 0.11584 | 0.009509 | 0.008096 | -0.034177 | 0.000325 | -0.006022 | 0.015135 | 0.050028 | 0.021873 | 0.043686 | 0.015531
3809.0938 | 121.9345 | -0.1236 | 121.9299 | 0.14017 | -0.022205 | -0.025735 | -0.038752 | 0.027109 | 0.076426 | -0.062717 | -0.029925 | 0.07006 | -0.027111 | -0.03768 | -0.079953 | -0.050029 | -0.060955 | -0.039797 | 0.26376 | 0.10139 | 0.097861 | 0.084844 | 0.15071 | 0.20002 | 0.060879 | 0.015851 | 0.11584 | 0.018665 | 0.008096 | -0.034177 | -0.004253 | -0.015179 | 0.005979 | 0.050028 | 0.03103 | 0.052842 | 0.033844
3810.8594 | 121.9894 | -0.10529 | 121.9208 | 0.13559 | -0.022205 | -0.025735 | -0.025017 | 0.022531 | 0.067269 | -0.067295 | -0.034504 | 0.07006 | -0.036267 | -0.028522 | -0.084531 | -0.045451 | -0.04722 | -0.035219 | 0.24087 | 0.083081 | 0.079551 | 0.080269 | 0.12782 | 0.17256 | 0.037991 | 0.011272 | 0.11584 | 0.009509 | 0.017254 | -0.038755 | 0.000325 | -0.001444 | 0.010557 | 0.050027 | 0.012716 | 0.048264 | 0.010953
3812.5625 | 122.0627 | -0.050354 | 121.8796 | 0.14017 | -0.022205 | -0.030314 | -0.020438 | 0.027109 | 0.067269 | -0.067295 | -0.043661 | 0.065481 | -0.031689 | -0.033101 | -0.079953 | -0.050029 | -0.051798 | -0.035219 | 0.19052 | 0.028149 | 0.02004 | 0.029916 | 0.077463 | 0.11762 | -0.016941 | 0.002115 | 0.11126 | 0.014087 | 0.012675 | -0.034177 | -0.004253 | -0.006022 | 0.010557 | 0.036292 | 0.008137 | 0.048264 | 0.020109
3814.3281 | 121.9894 | -0.07782 | 121.9025 | 0.14474 | -0.013048 | -0.021157 | -0.029595 | 0.017953 | 0.071848 | -0.067295 | -0.034504 | 0.065481 | -0.031689 | -0.042259 | -0.084531 | -0.045451 | -0.04722 | -0.039797 | 0.22256 | 0.064772 | 0.056663 | 0.048225 | 0.095773 | 0.14967 | 0.010525 | 0.011272 | 0.11126 | 0.014087 | 0.003517 | -0.038755 | 0.000325 | -0.001444 | 0.005979 | 0.050027 | 0.012716 | 0.052842 | 0.015531
3816.0312 | 122.0947 | -0.064087 | 121.8613 | 0.13559 | -0.022205 | -0.016578 | -0.029595 | 0.022531 | 0.067269 | -0.062717 | -0.043661 | 0.07006 | -0.036267 | -0.033101 | -0.079953 | -0.050029 | -0.04722 | -0.039797 | 0.19967 | 0.041882 | 0.047509 | 0.034492 | 0.086618 | 0.13136 | 0.00137 | 0.002115 | 0.11584 | 0.009509 | 0.012675 | -0.034177 | -0.004253 | -0.001444 | 0.005979 | 0.036292 | 0.003559 | 0.043686 | 0.010953
3817.7969 | 122.0673 | -0.068665 | 121.8842 | 0.14474 | -0.022205 | -0.021157 | -0.034174 | 0.017953 | 0.062691 | -0.062717 | -0.029925 | 0.07006 | -0.036267 | -0.033101 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.21341 | 0.04646 | 0.047508 | 0.034491 | 0.086618 | 0.13136 | 0.005948 | 0.015851 | 0.11584 | 0.009509 | 0.012675 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.054606 | 0.021873 | 0.048264 | 0.015531
3819.5625 | 121.9849 | -0.091553 | 121.8979 | 0.13559 | -0.022205 | -0.025735 | -0.025017 | 0.017953 | 0.067269 | -0.062717 | -0.034504 | 0.07006 | -0.031689 | -0.03768 | -0.079953 | -0.054607 | -0.051798 | -0.035219 | 0.22714 | 0.069348 | 0.065818 | 0.066536 | 0.10951 | 0.15882 | 0.028836 | 0.011272 | 0.11584 | 0.014087 | 0.008096 | -0.034177 | -0.008831 | -0.006022 | 0.010557 | 0.045449 | 0.017294 | 0.048264 | 0.020109
3821.2656 | 121.9528 | -0.10986 | 121.9299 | 0.14017 | -0.022205 | -0.030314 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | -0.034504 | 0.079217 | -0.031689 | -0.03768 | -0.084531 | -0.050029 | -0.042641 | -0.030641 | 0.25003 | 0.087658 | 0.079549 | 0.084846 | 0.13239 | 0.17713 | 0.047146 | 0.011272 | 0.12499 | 0.014087 | 0.008096 | -0.038755 | -0.004253 | 0.003135 | 0.015135 | 0.050027 | 0.008137 | 0.052842 | 0.010952
3823.0312 | 122.0215 | -0.054932 | 121.8796 | 0.13559 | -0.022205 | -0.025735 | -0.029595 | 0.022531 | 0.062691 | -0.071874 | -0.039082 | 0.07006 | -0.027111 | -0.03768 | -0.084531 | -0.054607 | -0.051798 | -0.035219 | 0.19052 | 0.032727 | 0.029197 | 0.025337 | 0.077463 | 0.11762 | -0.016942 | 0.006694 | 0.11584 | 0.018665 | 0.008096 | -0.038755 | -0.008831 | -0.006022 | 0.010557 | 0.045449 | 0.012716 | 0.05742 | 0.024687
3824.7969 | 122.0444 | -0.059509 | 121.8796 | 0.14017 | -0.026784 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.039082 | 0.07006 | -0.031689 | -0.03768 | -0.079953 | -0.050029 | -0.051798 | -0.039797 | 0.19967 | 0.032725 | 0.033774 | 0.029914 | 0.08204 | 0.13136 | -0.003208 | 0.006694 | 0.11584 | 0.014087 | 0.008096 | -0.034177 | -0.004253 | -0.006022 | 0.005979 | 0.040871 | 0.012716 | 0.048264 | 0.020109
3826.5 | 122.0306 | -0.068665 | 121.843 | 0.13101 | -0.017627 | -0.030314 | -0.025017 | 0.017953 | 0.067269 | -0.067295 | -0.039082 | 0.074638 | -0.036267 | -0.028522 | -0.079953 | -0.054607 | -0.04722 | -0.039797 | 0.19967 | 0.051038 | 0.038351 | 0.043648 | 0.086618 | 0.13593 | 0.00137 | 0.006694 | 0.12041 | 0.009509 | 0.017254 | -0.034177 | -0.008831 | -0.001444 | 0.005979 | 0.040871 | 0.008138 | 0.043686 | 0.010953
3828.2656 | 121.9711 | -0.091553 | 121.8979 | 0.14017 | -0.017627 | -0.021157 | -0.025017 | 0.027109 | 0.076426 | -0.062717 | -0.052818 | 0.07006 | -0.036267 | -0.03768 | -0.079953 | -0.054607 | -0.04722 | -0.039797 | 0.23172 | 0.073926 | 0.070396 | 0.066536 | 0.11866 | 0.16798 | 0.028836 | -0.007042 | 0.11584 | 0.009509 | 0.008096 | -0.034177 | -0.008831 | -0.001444 | 0.005979 | 0.027135 | -0.005598 | 0.043686 | 0.010953
3830.0469 | 121.9574 | -0.091553 | 121.9025 | 0.14474 | -0.022205 | -0.025735 | -0.029595 | 0.022531 | 0.062691 | -0.062717 | -0.039082 | 0.07006 | -0.036267 | -0.033101 | -0.079953 | -0.045451 | -0.04722 | -0.035219 | 0.2363 | 0.069348 | 0.065818 | 0.061958 | 0.11408 | 0.15424 | 0.028836 | 0.006694 | 0.11584 | 0.009509 | 0.012675 | -0.034177 | 0.000325 | -0.001444 | 0.010557 | 0.040871 | 0.008138 | 0.043686 | 0.010953
3831.75 | 121.9162 | -0.11902 | 121.8979 | 0.14017 | -0.022205 | -0.025735 | -0.020438 | 0.022531 | 0.071848 | -0.071874 | -0.039082 | 0.07006 | -0.031689 | -0.03768 | -0.079953 | -0.054607 | -0.056376 | -0.039797 | 0.25918 | 0.096814 | 0.093284 | 0.098581 | 0.14155 | 0.19087 | 0.047145 | 0.006694 | 0.11584 | 0.014087 | 0.008096 | -0.034177 | -0.008831 | -0.0106 | 0.005979 | 0.040871 | 0.017294 | 0.048264 | 0.024687
3833.5156 | 122.0444 | -0.059509 | 121.8521 | 0.14017 | -0.017627 | -0.025735 | -0.034174 | 0.022531 | 0.067269 | -0.071874 | -0.039082 | 0.065481 | -0.027111 | -0.03768 | -0.084531 | -0.045451 | -0.051798 | -0.044375 | 0.19967 | 0.041882 | 0.033774 | 0.025335 | 0.08204 | 0.12678 | -0.012365 | 0.006694 | 0.11126 | 0.018665 | 0.008096 | -0.038755 | 0.000325 | -0.006022 | 0.001401 | 0.045449 | 0.012716 | 0.05742 | 0.024687
3835.2188 | 121.9345 | -0.10071 | 121.8979 | 0.14017 | -0.022205 | -0.016578 | -0.025017 | 0.027109 | 0.071848 | -0.076452 | -0.039082 | 0.07006 | -0.031689 | -0.03768 | -0.079953 | -0.054607 | -0.056376 | -0.039797 | 0.24087 | 0.078503 | 0.08413 | 0.075691 | 0.12782 | 0.17256 | 0.024256 | 0.006694 | 0.11584 | 0.014087 | 0.008096 | -0.034177 | -0.008831 | -0.0106 | 0.005979 | 0.040871 | 0.017294 | 0.048264 | 0.024687
3837 | 121.9711 | -0.086975 | 121.907 | 0.14017 | -0.013048 | -0.025735 | -0.029595 | 0.031687 | 0.071848 | -0.067295 | -0.034504 | 0.074638 | -0.036267 | -0.03768 | -0.08911 | -0.045451 | -0.051798 | -0.035219 | 0.22714 | 0.073927 | 0.06124 | 0.05738 | 0.11866 | 0.15882 | 0.01968 | 0.011272 | 0.12041 | 0.009509 | 0.008096 | -0.043334 | 0.000325 | -0.006022 | 0.010557 | 0.054606 | 0.017294 | 0.052843 | 0.015531
3838.7656 | 122.0535 | -0.059509 | 121.8475 | 0.14932 | -0.026784 | -0.021157 | -0.025017 | 0.022531 | 0.076426 | -0.067295 | -0.034504 | 0.07006 | -0.036267 | -0.028522 | -0.079953 | -0.045451 | -0.04722 | -0.044375 | 0.20883 | 0.032725 | 0.038352 | 0.034492 | 0.08204 | 0.13594 | -0.007786 | 0.011272 | 0.11584 | 0.009509 | 0.017254 | -0.034177 | 0.000325 | -0.001444 | 0.001401 | 0.045449 | 0.012716 | 0.043686 | 0.010953
3840.5312 | 121.9345 | -0.10071 | 121.8979 | 0.13559 | -0.017627 | -0.021157 | -0.025017 | 0.031687 | 0.067269 | -0.071874 | -0.034504 | 0.07006 | -0.031689 | -0.028522 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.23629 | 0.083081 | 0.079551 | 0.075691 | 0.1324 | 0.16798 | 0.028834 | 0.011272 | 0.11584 | 0.014087 | 0.017254 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.050027 | 0.017294 | 0.052842 | 0.020109
3842.3125 | 121.9025 | -0.091553 | 121.8887 | 0.13559 | -0.017627 | -0.025735 | -0.029595 | 0.022531 | 0.085583 | -0.067295 | -0.039082 | 0.065481 | -0.031689 | -0.033101 | -0.08911 | -0.054607 | -0.060955 | -0.030641 | 0.22714 | 0.073926 | 0.065818 | 0.061958 | 0.11408 | 0.17714 | 0.024258 | 0.006694 | 0.11126 | 0.014087 | 0.012675 | -0.043334 | -0.008831 | -0.015179 | 0.015135 | 0.050028 | 0.021873 | 0.057421 | 0.029266
3844.0156 | 121.9254 | -0.10986 | 121.8887 | 0.12643 | -0.017627 | -0.016578 | -0.025017 | 0.027109 | 0.071848 | -0.067295 | -0.043661 | 0.07006 | -0.036267 | -0.033101 | -0.079953 | -0.050029 | -0.056376 | -0.035219 | 0.23629 | 0.092236 | 0.093285 | 0.084846 | 0.13697 | 0.18171 | 0.042568 | 0.002115 | 0.11584 | 0.009509 | 0.012675 | -0.034177 | -0.004253 | -0.0106 | 0.010557 | 0.036292 | 0.012715 | 0.043686 | 0.020109
3845.7188 | 122.0398 | -0.064087 | 121.8887 | 0.14474 | -0.022205 | -0.030314 | -0.025017 | 0.022531 | 0.067269 | -0.071874 | -0.039082 | 0.065481 | -0.031689 | -0.033101 | -0.08911 | -0.050029 | -0.04722 | -0.030641 | 0.20883 | 0.041882 | 0.033773 | 0.03907 | 0.086618 | 0.13136 | -0.007787 | 0.006694 | 0.11126 | 0.014087 | 0.012675 | -0.043334 | -0.004253 | -0.001444 | 0.015135 | 0.050028 | 0.008138 | 0.057421 | 0.015531
3847.4844 | 121.9666 | -0.11902 | 121.8887 | 0.14017 | -0.017627 | -0.016578 | -0.01586 | 0.022531 | 0.081005 | -0.067295 | -0.029925 | 0.065481 | -0.036267 | -0.033101 | -0.084531 | -0.050029 | -0.04722 | -0.030641 | 0.25918 | 0.10139 | 0.10244 | 0.10316 | 0.14155 | 0.20002 | 0.051724 | 0.015851 | 0.11126 | 0.009509 | 0.012675 | -0.038755 | -0.004253 | -0.001444 | 0.015135 | 0.054606 | 0.017295 | 0.048264 | 0.010953
3849.2656 | 121.9437 | -0.10071 | 121.8796 | 0.14474 | -0.022205 | -0.021157 | -0.029595 | 0.027109 | 0.071848 | -0.071874 | -0.034504 | 0.07006 | -0.040846 | -0.033101 | -0.08911 | -0.050029 | -0.04722 | -0.035219 | 0.24545 | 0.078503 | 0.079551 | 0.071113 | 0.12782 | 0.17256 | 0.028834 | 0.011272 | 0.11584 | 0.00493 | 0.012675 | -0.043334 | -0.004253 | -0.001444 | 0.010557 | 0.054606 | 0.012716 | 0.048264 | 0.006374
3850.9844 | 121.907 | -0.10986 | 121.907 | 0.14017 | -0.017627 | -0.025735 | -0.029595 | 0.031687 | 0.067269 | -0.071874 | -0.039082 | 0.07006 | -0.036267 | -0.023943 | -0.084531 | -0.059185 | -0.051798 | -0.035219 | 0.25003 | 0.092236 | 0.084128 | 0.080268 | 0.14155 | 0.17713 | 0.037989 | 0.006694 | 0.11584 | 0.009509 | 0.021833 | -0.038755 | -0.013409 | -0.006022 | 0.010557 | 0.045449 | 0.012716 | 0.048264 | 0.015531
3852.7656 | 121.9208 | -0.11902 | 121.8933 | 0.14017 | -0.022205 | -0.021157 | -0.025017 | 0.027109 | 0.071848 | -0.067295 | -0.034504 | 0.060902 | -0.027111 | -0.03768 | -0.084531 | -0.054607 | -0.04722 | -0.039797 | 0.25918 | 0.096814 | 0.097862 | 0.094002 | 0.14613 | 0.19087 | 0.051724 | 0.011272 | 0.10668 | 0.018665 | 0.008096 | -0.038755 | -0.008831 | -0.001444 | 0.005979 | 0.050027 | 0.012716 | 0.05742 | 0.020109
3854.5312 | 122.0535 | -0.045776 | 121.8613 | 0.14017 | -0.026784 | -0.025735 | -0.029595 | 0.022531 | 0.067269 | -0.067295 | -0.039082 | 0.065481 | -0.031689 | -0.033101 | -0.079953 | -0.045451 | -0.051798 | -0.035219 | 0.18594 | 0.018992 | 0.020041 | 0.016181 | 0.068307 | 0.11304 | -0.021519 | 0.006694 | 0.11126 | 0.014087 | 0.012675 | -0.034177 | 0.000325 | -0.006022 | 0.010557 | 0.040871 | 0.012716 | 0.048264 | 0.020109
3856.2344 | 121.9391 | -0.10986 | 121.8933 | 0.14474 | -0.017627 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.058139 | -0.039082 | 0.07006 | -0.036267 | -0.042259 | -0.079953 | -0.045451 | -0.051798 | -0.035219 | 0.25461 | 0.092236 | 0.079549 | 0.080268 | 0.13239 | 0.18171 | 0.051724 | 0.006694 | 0.11584 | 0.009509 | 0.003517 | -0.034177 | 0.000325 | -0.006022 | 0.010557 | 0.040871 | 0.012716 | 0.043686 | 0.015531
3858.0156 | 121.9528 | -0.10529 | 121.8933 | 0.14017 | -0.017627 | -0.021157 | -0.020438 | 0.022531 | 0.076426 | -0.062717 | -0.043661 | 0.074638 | -0.031689 | -0.03768 | -0.084531 | -0.054607 | -0.056376 | -0.044375 | 0.24545 | 0.087659 | 0.084129 | 0.084848 | 0.12782 | 0.18171 | 0.042569 | 0.002115 | 0.12041 | 0.014087 | 0.008096 | -0.038755 | -0.008831 | -0.0106 | 0.001401 | 0.04087 | 0.012715 | 0.052842 | 0.024687
3859.7969 | 121.9116 | -0.09613 | 121.9116 | 0.14474 | -0.017627 | -0.021157 | -0.029595 | 0.027109 | 0.071848 | -0.067295 | -0.039082 | 0.065481 | -0.027111 | -0.042259 | -0.079953 | -0.045451 | -0.04722 | -0.035219 | 0.24087 | 0.078503 | 0.074973 | 0.066535 | 0.12324 | 0.16798 | 0.028835 | 0.006694 | 0.11126 | 0.018665 | 0.003517 | -0.034177 | 0.000325 | -0.001444 | 0.010557 | 0.040871 | 0.008138 | 0.052842 | 0.020109
3861.5 | 122.0078 | -0.073242 | 121.8384 | 0.13559 | -0.013048 | -0.021157 | -0.025017 | 0.022531 | 0.076426 | -0.062717 | -0.048239 | 0.065481 | -0.031689 | -0.033101 | -0.084531 | -0.045451 | -0.051798 | -0.039797 | 0.20883 | 0.060194 | 0.052085 | 0.048225 | 0.095773 | 0.14967 | 0.010525 | -0.002463 | 0.11126 | 0.014087 | 0.012675 | -0.038755 | 0.000325 | -0.006022 | 0.005979 | 0.036292 | 0.003559 | 0.052842 | 0.020109
3863.2656 | 121.9849 | -0.082397 | 121.8842 | 0.14474 | -0.026784 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.039082 | 0.07006 | -0.027111 | -0.033101 | -0.079953 | -0.050029 | -0.04722 | -0.035219 | 0.22714 | 0.055613 | 0.056662 | 0.05738 | 0.10493 | 0.15424 | 0.015102 | 0.006694 | 0.11584 | 0.018665 | 0.012675 | -0.034177 | -0.004253 | -0.001444 | 0.010557 | 0.040871 | 0.008138 | 0.052842 | 0.020109
3865.0469 | 121.9025 | -0.09613 | 121.8979 | 0.14017 | -0.022205 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.039082 | 0.065481 | -0.036267 | -0.03768 | -0.079953 | -0.045451 | -0.042641 | -0.035219 | 0.2363 | 0.073925 | 0.070395 | 0.066535 | 0.11866 | 0.16798 | 0.028835 | 0.006694 | 0.11126 | 0.009509 | 0.008096 | -0.034177 | 0.000325 | 0.003135 | 0.010557 | 0.040871 | 0.003559 | 0.043686 | 0.006374
3866.8125 | 122.0444 | -0.050354 | 121.843 | 0.14474 | -0.026784 | -0.021157 | -0.029595 | 0.013375 | 0.062691 | -0.071874 | -0.039082 | 0.074638 | -0.031689 | -0.03768 | -0.084531 | -0.050029 | -0.04722 | -0.039797 | 0.1951 | 0.02357 | 0.029197 | 0.020759 | 0.063729 | 0.11305 | -0.02152 | 0.006694 | 0.12041 | 0.014087 | 0.008096 | -0.038755 | -0.004253 | -0.001444 | 0.005979 | 0.045449 | 0.008138 | 0.052842 | 0.015531
3868.5938 | 121.9803 | -0.09613 | 121.843 | 0.13559 | -0.022205 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.058139 | -0.034504 | 0.07006 | -0.040846 | -0.033101 | -0.079953 | -0.045451 | -0.04722 | -0.039797 | 0.23172 | 0.073925 | 0.074973 | 0.071113 | 0.11866 | 0.16798 | 0.037991 | 0.011272 | 0.11584 | 0.00493 | 0.012675 | -0.034177 | 0.000325 | -0.001444 | 0.005979 | 0.045449 | 0.012716 | 0.039107 | 0.006374
3870.3594 | 122.0261 | -0.045776 | 121.8246 | 0.14017 | -0.026784 | -0.030314 | -0.029595 | 0.017953 | 0.071848 | -0.062717 | -0.034504 | 0.074638 | -0.036267 | -0.033101 | -0.084531 | -0.050029 | -0.060955 | -0.039797 | 0.18594 | 0.018992 | 0.015462 | 0.016181 | 0.063729 | 0.11762 | -0.016941 | 0.011272 | 0.12041 | 0.009509 | 0.012675 | -0.038755 | -0.004253 | -0.015179 | 0.005979 | 0.050027 | 0.026451 | 0.048264 | 0.024688
3872.125 | 121.8887 | -0.11444 | 121.907 | 0.13559 | -0.022205 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.039082 | 0.065481 | -0.036267 | -0.042259 | -0.075375 | -0.040873 | -0.051798 | -0.039797 | 0.25003 | 0.092236 | 0.088706 | 0.089424 | 0.13697 | 0.18629 | 0.051724 | 0.006694 | 0.11126 | 0.009509 | 0.003517 | -0.029599 | 0.004903 | -0.006022 | 0.005979 | 0.036293 | 0.012716 | 0.039108 | 0.015531
3873.9062 | 121.9208 | -0.10071 | 121.8796 | 0.14932 | -0.026784 | -0.021157 | -0.029595 | 0.017953 | 0.076426 | -0.071874 | -0.039082 | 0.074638 | -0.027111 | -0.03768 | -0.084531 | -0.050029 | -0.042641 | -0.044375 | 0.25003 | 0.073924 | 0.079551 | 0.071113 | 0.11866 | 0.17713 | 0.028834 | 0.006694 | 0.12041 | 0.018665 | 0.008096 | -0.038755 | -0.004253 | 0.003135 | 0.001401 | 0.045449 | 0.003559 | 0.05742 | 0.01553
3875.6094 | 121.9299 | -0.09613 | 121.875 | 0.14017 | -0.022205 | -0.021157 | -0.020438 | 0.027109 | 0.067269 | -0.062717 | -0.043661 | 0.07006 | -0.031689 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.2363 | 0.073925 | 0.074973 | 0.075692 | 0.12324 | 0.1634 | 0.033413 | 0.002115 | 0.11584 | 0.014087 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.04087 | 0.008137 | 0.052842 | 0.020109
3877.3594 | 121.8842 | -0.10986 | 121.9025 | 0.14017 | -0.022205 | -0.016578 | -0.025017 | 0.027109 | 0.071848 | -0.071874 | -0.043661 | 0.065481 | -0.036267 | -0.03768 | -0.08911 | -0.050029 | -0.04722 | -0.044375 | 0.25003 | 0.087658 | 0.093285 | 0.084846 | 0.13697 | 0.18171 | 0.037989 | 0.002115 | 0.11126 | 0.009509 | 0.008096 | -0.043334 | -0.004253 | -0.001444 | 0.001401 | 0.045449 | 0.003559 | 0.052843 | 0.010953
3879.1406 | 121.8979 | -0.10986 | 121.8842 | 0.14017 | -0.017627 | -0.021157 | -0.029595 | 0.017953 | 0.076426 | -0.062717 | -0.043661 | 0.065481 | -0.031689 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.044375 | 0.25003 | 0.092236 | 0.088706 | 0.080268 | 0.12782 | 0.18629 | 0.047146 | 0.002115 | 0.11126 | 0.014087 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.001401 | 0.04087 | 0.008137 | 0.052842 | 0.020109
3880.8438 | 121.962 | -0.09613 | 121.8842 | 0.13559 | -0.022205 | -0.021157 | -0.025017 | 0.017953 | 0.076426 | -0.071874 | -0.029925 | 0.074638 | -0.031689 | -0.033101 | -0.084531 | -0.050029 | -0.051798 | -0.044375 | 0.23172 | 0.073925 | 0.074973 | 0.071113 | 0.11408 | 0.17256 | 0.024256 | 0.015851 | 0.12041 | 0.014087 | 0.012675 | -0.038755 | -0.004253 | -0.006022 | 0.001401 | 0.054606 | 0.021873 | 0.052842 | 0.020109
3882.625 | 121.9391 | -0.091553 | 121.9162 | 0.14474 | -0.022205 | -0.025735 | -0.025017 | 0.027109 | 0.067269 | -0.062717 | -0.039082 | 0.065481 | -0.036267 | -0.03768 | -0.075375 | -0.050029 | -0.051798 | -0.039797 | 0.2363 | 0.069348 | 0.065818 | 0.066536 | 0.11866 | 0.15882 | 0.028836 | 0.006694 | 0.11126 | 0.009509 | 0.008096 | -0.029599 | -0.004253 | -0.006022 | 0.005979 | 0.036293 | 0.012716 | 0.039108 | 0.015531
3884.3906 | 121.9849 | -0.07782 | 121.8292 | 0.13559 | -0.017627 | -0.034893 | -0.025017 | 0.022531 | 0.071848 | -0.071874 | -0.039082 | 0.065481 | -0.040846 | -0.033101 | -0.08911 | -0.054607 | -0.056376 | -0.039797 | 0.21341 | 0.060193 | 0.042927 | 0.052803 | 0.10035 | 0.14967 | 0.005946 | 0.006694 | 0.11126 | 0.00493 | 0.012675 | -0.043334 | -0.008831 | -0.0106 | 0.005979 | 0.050028 | 0.017294 | 0.048264 | 0.01553
3886.1562 | 121.9482 | -0.082397 | 121.8475 | 0.13559 | -0.022205 | -0.016578 | -0.025017 | 0.027109 | 0.067269 | -0.067295 | -0.043661 | 0.07006 | -0.036267 | -0.03768 | -0.079953 | -0.054607 | -0.056376 | -0.035219 | 0.21798 | 0.060192 | 0.065819 | 0.05738 | 0.10951 | 0.14967 | 0.015102 | 0.002115 | 0.11584 | 0.009509 | 0.008096 | -0.034177 | -0.008831 | -0.0106 | 0.010557 | 0.036292 | 0.012715 | 0.043686 | 0.020109
3887.9375 | 121.9437 | -0.09613 | 121.8796 | 0.14017 | -0.022205 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.034504 | 0.074638 | -0.031689 | -0.03768 | -0.08911 | -0.054607 | -0.051798 | -0.039797 | 0.2363 | 0.073925 | 0.070395 | 0.066535 | 0.11866 | 0.16798 | 0.028835 | 0.011272 | 0.12041 | 0.014087 | 0.008096 | -0.043334 | -0.008831 | -0.006022 | 0.005979 | 0.054606 | 0.017294 | 0.057421 | 0.020109
3889.6562 | 121.8796 | -0.086975 | 121.9025 | 0.14017 | -0.017627 | -0.012 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.043661 | 0.060902 | -0.027111 | -0.033101 | -0.079953 | -0.054607 | -0.051798 | -0.044375 | 0.22714 | 0.069348 | 0.074975 | 0.061958 | 0.10951 | 0.15882 | 0.01968 | 0.002115 | 0.10668 | 0.018665 | 0.012675 | -0.034177 | -0.008831 | -0.006022 | 0.001401 | 0.036292 | 0.008137 | 0.052842 | 0.024687
3891.4219 | 122.0078 | -0.059509 | 121.8246 | 0.14932 | -0.031363 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.039082 | 0.07006 | -0.036267 | -0.03768 | -0.08911 | -0.050029 | -0.051798 | -0.039797 | 0.20883 | 0.028146 | 0.033774 | 0.034492 | 0.08204 | 0.13136 | -0.003208 | 0.006694 | 0.11584 | 0.009509 | 0.008096 | -0.043334 | -0.004253 | -0.006022 | 0.005979 | 0.050028 | 0.012716 | 0.052843 | 0.015531
3893.125 | 121.9986 | -0.054932 | 121.8796 | 0.14017 | -0.026784 | -0.025735 | -0.029595 | 0.027109 | 0.067269 | -0.067295 | -0.043661 | 0.065481 | -0.036267 | -0.03768 | -0.084531 | -0.045451 | -0.042641 | -0.035219 | 0.1951 | 0.028148 | 0.029197 | 0.025337 | 0.082041 | 0.1222 | -0.012363 | 0.002115 | 0.11126 | 0.009509 | 0.008096 | -0.038755 | 0.000325 | 0.003135 | 0.010557 | 0.04087 | -0.00102 | 0.048264 | 0.006374
3894.8906 | 121.9025 | -0.10986 | 121.8658 | 0.14017 | -0.026784 | -0.021157 | -0.025017 | 0.017953 | 0.067269 | -0.071874 | -0.034504 | 0.065481 | -0.045424 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.25003 | 0.083079 | 0.088706 | 0.084846 | 0.12782 | 0.17713 | 0.037989 | 0.011272 | 0.11126 | 0.000352 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.050027 | 0.017294 | 0.039107 | 0.006374
3896.6562 | 121.8887 | -0.1236 | 121.8979 | 0.14474 | -0.026784 | -0.021157 | -0.025017 | 0.022531 | 0.081005 | -0.058139 | -0.039082 | 0.07006 | -0.031689 | -0.042259 | -0.084531 | -0.040873 | -0.04722 | -0.035219 | 0.26834 | 0.096812 | 0.10244 | 0.098579 | 0.14613 | 0.2046 | 0.065457 | 0.006694 | 0.11584 | 0.014087 | 0.003517 | -0.038755 | 0.004903 | -0.001444 | 0.010557 | 0.045449 | 0.008138 | 0.052842 | 0.015531
3898.4531 | 121.9528 | -0.10986 | 121.8842 | 0.14474 | -0.031363 | -0.025735 | -0.034174 | 0.031687 | 0.076426 | -0.062717 | -0.039082 | 0.07006 | -0.040846 | -0.033101 | -0.079953 | -0.054607 | -0.042641 | -0.035219 | 0.25461 | 0.0785 | 0.084128 | 0.075689 | 0.14155 | 0.18629 | 0.047146 | 0.006694 | 0.11584 | 0.00493 | 0.012675 | -0.034177 | -0.008831 | 0.003135 | 0.010557 | 0.040871 | 0.003559 | 0.039107 | 0.001795
3900.1562 | 121.9986 | -0.068665 | 121.8384 | 0.14474 | -0.017627 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.039082 | 0.065481 | -0.031689 | -0.03768 | -0.079953 | -0.045451 | -0.051798 | -0.039797 | 0.21341 | 0.051038 | 0.04293 | 0.043648 | 0.091196 | 0.14051 | 0.005948 | 0.006694 | 0.11126 | 0.014087 | 0.008096 | -0.034177 | 0.000325 | -0.006022 | 0.005979 | 0.040871 | 0.012716 | 0.048264 | 0.020109
3901.9219 | 121.8933 | -0.10529 | 121.8704 | 0.14474 | -0.022205 | -0.025735 | -0.034174 | 0.022531 | 0.067269 | -0.062717 | -0.043661 | 0.065481 | -0.036267 | -0.042259 | -0.084531 | -0.040873 | -0.04722 | -0.035219 | 0.25003 | 0.083081 | 0.079551 | 0.071112 | 0.12782 | 0.17256 | 0.042569 | 0.002115 | 0.11126 | 0.009509 | 0.003517 | -0.038755 | 0.004903 | -0.001444 | 0.010557 | 0.04087 | 0.003559 | 0.048264 | 0.010953
3903.6406 | 121.8887 | -0.10986 | 121.8521 | 0.14017 | -0.017627 | -0.021157 | -0.029595 | 0.022531 | 0.076426 | -0.067295 | -0.048239 | 0.065481 | -0.031689 | -0.03768 | -0.084531 | -0.045451 | -0.04722 | -0.035219 | 0.25003 | 0.092236 | 0.088706 | 0.080268 | 0.13239 | 0.18629 | 0.042568 | -0.002463 | 0.11126 | 0.014087 | 0.008096 | -0.038755 | 0.000325 | -0.001444 | 0.010557 | 0.036292 | -0.001019 | 0.052842 | 0.015531
3905.4062 | 121.8979 | -0.10986 | 121.875 | 0.14017 | -0.026784 | -0.021157 | -0.025017 | 0.022531 | 0.067269 | -0.067295 | -0.034504 | 0.074638 | -0.031689 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.25003 | 0.083079 | 0.088706 | 0.084846 | 0.13239 | 0.17713 | 0.042568 | 0.011272 | 0.12041 | 0.014087 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.050027 | 0.017294 | 0.052842 | 0.020109
3907.1875 | 121.8933 | -0.10071 | 121.8796 | 0.14474 | -0.022205 | -0.025735 | -0.029595 | 0.017953 | 0.076426 | -0.062717 | -0.039082 | 0.07006 | -0.036267 | -0.033101 | -0.084531 | -0.040873 | -0.051798 | -0.044375 | 0.24545 | 0.078503 | 0.074973 | 0.071113 | 0.11866 | 0.17713 | 0.037991 | 0.006694 | 0.11584 | 0.009509 | 0.012675 | -0.038755 | 0.004903 | -0.006022 | 0.001401 | 0.045449 | 0.012716 | 0.048264 | 0.015531
3908.9062 | 122.0078 | -0.045776 | 121.8292 | 0.14017 | -0.026784 | -0.025735 | -0.025017 | 0.027109 | 0.071848 | -0.071874 | -0.043661 | 0.065481 | -0.031689 | -0.03768 | -0.075375 | -0.040873 | -0.051798 | -0.039797 | 0.18594 | 0.018992 | 0.020041 | 0.020759 | 0.072885 | 0.11762 | -0.026098 | 0.002115 | 0.11126 | 0.014087 | 0.008096 | -0.029599 | 0.004903 | -0.006022 | 0.005979 | 0.031714 | 0.008137 | 0.043686 | 0.020109
3910.6875 | 122.0215 | -0.045776 | 121.8201 | 0.14474 | -0.031363 | -0.021157 | -0.029595 | 0.027109 | 0.062691 | -0.067295 | -0.043661 | 0.065481 | -0.045424 | -0.042259 | -0.075375 | -0.050029 | -0.04722 | -0.035219 | 0.19052 | 0.014413 | 0.024619 | 0.016181 | 0.072885 | 0.10847 | -0.021519 | 0.002115 | 0.11126 | 0.000352 | 0.003517 | -0.029599 | -0.004253 | -0.001444 | 0.010557 | 0.031714 | 0.003559 | 0.029951 | 0.001796
3912.3906 | 121.9986 | -0.068665 | 121.7972 | 0.14017 | -0.017627 | -0.021157 | -0.020438 | 0.017953 | 0.076426 | -0.071874 | -0.034504 | 0.065481 | -0.036267 | -0.03768 | -0.079953 | -0.050029 | -0.04722 | -0.039797 | 0.20883 | 0.051038 | 0.047508 | 0.048227 | 0.086618 | 0.14509 | -0.003209 | 0.011272 | 0.11126 | 0.009509 | 0.008096 | -0.034177 | -0.004253 | -0.001444 | 0.005979 | 0.045449 | 0.012716 | 0.043686 | 0.010953
3914.1562 | 121.9849 | -0.041199 | 121.7834 | 0.13559 | -0.026784 | -0.025735 | -0.029595 | 0.031687 | 0.071848 | -0.067295 | -0.039082 | 0.065481 | -0.036267 | -0.033101 | -0.093688 | -0.054607 | -0.04722 | -0.039797 | 0.17679 | 0.014415 | 0.015464 | 0.011604 | 0.072886 | 0.11305 | -0.026096 | 0.006694 | 0.11126 | 0.009509 | 0.012675 | -0.047912 | -0.008831 | -0.001444 | 0.005979 | 0.054606 | 0.008138 | 0.057421 | 0.010953
3915.9219 | 121.8842 | -0.091553 | 121.8475 | 0.14474 | -0.022205 | -0.016578 | -0.029595 | 0.022531 | 0.067269 | -0.076452 | -0.039082 | 0.065481 | -0.036267 | -0.03768 | -0.08911 | -0.054607 | -0.051798 | -0.035219 | 0.2363 | 0.069348 | 0.074975 | 0.061958 | 0.11408 | 0.15882 | 0.015101 | 0.006694 | 0.11126 | 0.009509 | 0.008096 | -0.043334 | -0.008831 | -0.006022 | 0.010557 | 0.050028 | 0.012716 | 0.052843 | 0.015531
3917.6406 | 122.0261 | -0.082397 | 121.8201 | 0.13559 | -0.026784 | -0.021157 | -0.025017 | 0.017953 | 0.071848 | -0.067295 | -0.039082 | 0.060902 | -0.040846 | -0.028522 | -0.08911 | -0.054607 | -0.051798 | -0.030641 | 0.21798 | 0.055613 | 0.06124 | 0.05738 | 0.10035 | 0.15424 | 0.015102 | 0.006694 | 0.10668 | 0.00493 | 0.017254 | -0.043334 | -0.008831 | -0.006022 | 0.015135 | 0.050028 | 0.012716 | 0.048264 | 0.010952
3919.4062 | 121.8567 | -0.09613 | 121.843 | 0.14474 | -0.026784 | -0.021157 | -0.020438 | 0.017953 | 0.071848 | -0.067295 | -0.048239 | 0.074638 | -0.031689 | -0.033101 | -0.08911 | -0.040873 | -0.051798 | -0.039797 | 0.24087 | 0.069346 | 0.074973 | 0.075692 | 0.11408 | 0.16798 | 0.028835 | -0.002463 | 0.12041 | 0.014087 | 0.012675 | -0.043334 | 0.004903 | -0.006022 | 0.005979 | 0.040871 | 0.003559 | 0.057421 | 0.020109
3921.1562 | 121.9574 | -0.068665 | 121.8613 | 0.14017 | -0.022205 | -0.025735 | -0.029595 | 0.017953 | 0.071848 | -0.071874 | -0.043661 | 0.056323 | -0.036267 | -0.033101 | -0.08911 | -0.054607 | -0.051798 | -0.048953 | 0.20883 | 0.04646 | 0.04293 | 0.03907 | 0.086618 | 0.14051 | -0.003209 | 0.002115 | 0.1021 | 0.009509 | 0.012675 | -0.043334 | -0.008831 | -0.006022 | -0.003177 | 0.045449 | 0.008137 | 0.052843 | 0.015531
3922.8594 | 121.8842 | -0.07782 | 121.843 | 0.14474 | -0.031363 | -0.021157 | -0.029595 | 0.022531 | 0.067269 | -0.071874 | -0.039082 | 0.065481 | -0.031689 | -0.03768 | -0.075375 | -0.045451 | -0.056376 | -0.035219 | 0.22256 | 0.046457 | 0.056663 | 0.048225 | 0.10035 | 0.14509 | 0.005946 | 0.006694 | 0.11126 | 0.014087 | 0.008096 | -0.029599 | 0.000325 | -0.0106 | 0.010557 | 0.036293 | 0.017294 | 0.043686 | 0.024687
3924.6406 | 121.962 | -0.082397 | 121.7972 | 0.13559 | -0.022205 | -0.021157 | -0.038752 | 0.022531 | 0.081005 | -0.071874 | -0.048239 | 0.065481 | -0.036267 | -0.046838 | -0.079953 | -0.050029 | -0.042641 | -0.035219 | 0.21798 | 0.060192 | 0.06124 | 0.043645 | 0.10493 | 0.1634 | 0.010523 | -0.002463 | 0.11126 | 0.009509 | -0.001062 | -0.034177 | -0.004253 | 0.003135 | 0.010557 | 0.031714 | -0.005598 | 0.043686 | 0.006374
3926.3438 | 121.8338 | -0.10071 | 121.843 | 0.13101 | -0.026784 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.048239 | 0.07006 | -0.036267 | -0.03768 | -0.093688 | -0.050029 | -0.051798 | -0.044375 | 0.23172 | 0.073924 | 0.079551 | 0.075691 | 0.12324 | 0.17256 | 0.033413 | -0.002463 | 0.11584 | 0.009509 | 0.008096 | -0.047912 | -0.004253 | -0.006022 | 0.001401 | 0.045449 | 0.003559 | 0.057421 | 0.015531
3928.1094 | 122.0123 | -0.068665 | 121.7926 | 0.13559 | -0.026784 | -0.016578 | -0.029595 | 0.027109 | 0.071848 | -0.067295 | -0.043661 | 0.074638 | -0.036267 | -0.03768 | -0.079953 | -0.050029 | -0.04722 | -0.039797 | 0.20425 | 0.041881 | 0.052087 | 0.03907 | 0.095774 | 0.14051 | 0.00137 | 0.002115 | 0.12041 | 0.009509 | 0.008096 | -0.034177 | -0.004253 | -0.001444 | 0.005979 | 0.036292 | 0.003559 | 0.043686 | 0.010953
3929.875 | 121.9757 | -0.064087 | 121.8292 | 0.13559 | -0.026784 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.043661 | 0.07006 | -0.036267 | -0.042259 | -0.079953 | -0.050029 | -0.056376 | -0.035219 | 0.19967 | 0.037303 | 0.038352 | 0.034492 | 0.086618 | 0.13594 | -0.003208 | 0.002115 | 0.11584 | 0.009509 | 0.003517 | -0.034177 | -0.004253 | -0.0106 | 0.010557 | 0.036292 | 0.012715 | 0.043686 | 0.020109
3931.5781 | 121.9803 | -0.059509 | 121.7834 | 0.14017 | -0.031363 | -0.021157 | -0.029595 | 0.013375 | 0.076426 | -0.062717 | -0.043661 | 0.060902 | -0.036267 | -0.033101 | -0.084531 | -0.045451 | -0.051798 | -0.030641 | 0.19967 | 0.028146 | 0.038352 | 0.029914 | 0.072884 | 0.13594 | -0.003208 | 0.002115 | 0.10668 | 0.009509 | 0.012675 | -0.038755 | 0.000325 | -0.006022 | 0.015135 | 0.04087 | 0.008137 | 0.048264 | 0.015531
3933.3438 | 121.8933 | -0.11444 | 121.8475 | 0.13559 | -0.022205 | -0.021157 | -0.025017 | 0.027109 | 0.076426 | -0.067295 | -0.034504 | 0.065481 | -0.036267 | -0.03768 | -0.070797 | -0.045451 | -0.04722 | -0.039797 | 0.25003 | 0.092236 | 0.093284 | 0.089424 | 0.14155 | 0.19087 | 0.047146 | 0.011272 | 0.11126 | 0.009509 | 0.008096 | -0.025021 | 0.000325 | -0.001444 | 0.005979 | 0.036293 | 0.012716 | 0.03453 | 0.010953
3935.0781 | 121.9803 | -0.041199 | 121.8063 | 0.13559 | -0.022205 | -0.025735 | -0.025017 | 0.027109 | 0.067269 | -0.071874 | -0.039082 | 0.07006 | -0.040846 | -0.03768 | -0.084531 | -0.045451 | -0.04722 | -0.039797 | 0.17679 | 0.018994 | 0.015464 | 0.016182 | 0.068308 | 0.10847 | -0.030675 | 0.006694 | 0.11584 | 0.00493 | 0.008096 | -0.038755 | 0.000325 | -0.001444 | 0.005979 | 0.045449 | 0.008138 | 0.043685 | 0.006374
3936.8438 | 121.9986 | -0.050354 | 121.7926 | 0.14017 | -0.022205 | -0.025735 | -0.029595 | 0.022531 | 0.062691 | -0.067295 | -0.039082 | 0.07006 | -0.031689 | -0.042259 | -0.079953 | -0.050029 | -0.056376 | -0.030641 | 0.19052 | 0.028149 | 0.024619 | 0.020759 | 0.072885 | 0.11305 | -0.016941 | 0.006694 | 0.11584 | 0.014087 | 0.003517 | -0.034177 | -0.004253 | -0.0106 | 0.015135 | 0.040871 | 0.017294 | 0.048264 | 0.024687
3938.5469 | 121.9437 | -0.07782 | 121.788 | 0.13559 | -0.026784 | -0.021157 | -0.034174 | 0.022531 | 0.062691 | -0.067295 | -0.034504 | 0.065481 | -0.036267 | -0.033101 | -0.084531 | -0.045451 | -0.04722 | -0.039797 | 0.21341 | 0.051036 | 0.056663 | 0.043646 | 0.10035 | 0.14051 | 0.010525 | 0.011272 | 0.11126 | 0.009509 | 0.012675 | -0.038755 | 0.000325 | -0.001444 | 0.005979 | 0.050027 | 0.012716 | 0.048264 | 0.010953
3940.3125 | 121.9803 | -0.082397 | 121.788 | 0.13559 | -0.026784 | -0.021157 | -0.025017 | 0.022531 | 0.067269 | -0.067295 | -0.043661 | 0.060902 | -0.031689 | -0.042259 | -0.08911 | -0.054607 | -0.051798 | -0.035219 | 0.21798 | 0.055613 | 0.06124 | 0.05738 | 0.10493 | 0.14967 | 0.015102 | 0.002115 | 0.10668 | 0.014087 | 0.003517 | -0.043334 | -0.008831 | -0.006022 | 0.010557 | 0.045449 | 0.008137 | 0.057421 | 0.020109
3942.0781 | 121.8979 | -0.091553 | 121.7972 | 0.14017 | -0.026784 | -0.021157 | -0.020438 | 0.017953 | 0.071848 | -0.071874 | -0.034504 | 0.07006 | -0.036267 | -0.03768 | -0.08911 | -0.050029 | -0.051798 | -0.039797 | 0.23172 | 0.064769 | 0.070396 | 0.071115 | 0.10951 | 0.1634 | 0.019679 | 0.011272 | 0.11584 | 0.009509 | 0.008096 | -0.043334 | -0.004253 | -0.006022 | 0.005979 | 0.054606 | 0.017294 | 0.052843 | 0.015531
3943.8594 | 121.9574 | -0.07782 | 121.8063 | 0.14017 | -0.022205 | -0.021157 | -0.025017 | 0.022531 | 0.076426 | -0.067295 | -0.043661 | 0.060902 | -0.027111 | -0.033101 | -0.084531 | -0.050029 | -0.04722 | -0.030641 | 0.21799 | 0.055615 | 0.056663 | 0.052803 | 0.10035 | 0.15425 | 0.010525 | 0.002115 | 0.10668 | 0.018665 | 0.012675 | -0.038755 | -0.004253 | -0.001444 | 0.015135 | 0.04087 | 0.003559 | 0.05742 | 0.020109
3945.625 | 121.843 | -0.10071 | 121.7789 | 0.14932 | -0.026784 | -0.021157 | -0.029595 | 0.022531 | 0.062691 | -0.053561 | -0.039082 | 0.07006 | -0.040846 | -0.03768 | -0.08911 | -0.054607 | -0.051798 | -0.035219 | 0.25003 | 0.073924 | 0.079551 | 0.071113 | 0.12324 | 0.1634 | 0.047147 | 0.006694 | 0.11584 | 0.00493 | 0.008096 | -0.043334 | -0.008831 | -0.006022 | 0.010557 | 0.050028 | 0.012716 | 0.048264 | 0.010952
3947.3281 | 121.9757 | -0.082397 | 121.7743 | 0.13559 | -0.022205 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.039082 | 0.060902 | -0.036267 | -0.03768 | -0.084531 | -0.054607 | -0.056376 | -0.030641 | 0.21798 | 0.060192 | 0.056662 | 0.052802 | 0.10493 | 0.15424 | 0.015102 | 0.006694 | 0.10668 | 0.009509 | 0.008096 | -0.038755 | -0.008831 | -0.0106 | 0.015135 | 0.045449 | 0.017294 | 0.048264 | 0.020109
3949.0938 | 121.994 | -0.068665 | 121.7926 | 0.13559 | -0.026784 | -0.021157 | -0.029595 | 0.022531 | 0.071848 | -0.071874 | -0.039082 | 0.060902 | -0.036267 | -0.033101 | -0.079953 | -0.054607 | -0.051798 | -0.035219 | 0.20425 | 0.041881 | 0.047508 | 0.03907 | 0.091196 | 0.14051 | -0.003209 | 0.006694 | 0.10668 | 0.009509 | 0.012675 | -0.034177 | -0.008831 | -0.006022 | 0.010557 | 0.040871 | 0.012716 | 0.043686 | 0.015531
3950.875 | 121.9116 | -0.068665 | 121.8018 | 0.13559 | -0.026784 | -0.021157 | -0.029595 | 0.022531 | 0.062691 | -0.067295 | -0.048239 | 0.065481 | -0.036267 | -0.03768 | -0.075375 | -0.050029 | -0.04722 | -0.035219 | 0.20425 | 0.041881 | 0.047508 | 0.03907 | 0.091196 | 0.13136 | 0.00137 | -0.002463 | 0.11126 | 0.009509 | 0.008096 | -0.029599 | -0.004253 | -0.001444 | 0.010557 | 0.027136 | -0.001019 | 0.039108 | 0.010953
3952.5781 | 121.9711 | -0.073242 | 121.7743 | 0.13559 | -0.026784 | -0.030314 | -0.029595 | 0.017953 | 0.067269 | -0.076452 | -0.043661 | 0.074638 | -0.036267 | -0.03768 | -0.084531 | -0.045451 | -0.051798 | -0.039797 | 0.20883 | 0.046458 | 0.042928 | 0.043647 | 0.091195 | 0.14051 | -0.00321 | 0.002115 | 0.12041 | 0.009509 | 0.008096 | -0.038755 | 0.000325 | -0.006022 | 0.005979 | 0.04087 | 0.008137 | 0.048264 | 0.015531
3954.3594 | 121.9574 | -0.054932 | 121.7651 | 0.13101 | -0.026784 | -0.021157 | -0.029595 | 0.027109 | 0.067269 | -0.071874 | -0.043661 | 0.074638 | -0.036267 | -0.03768 | -0.084531 | -0.045451 | -0.060955 | -0.039797 | 0.18594 | 0.028148 | 0.033775 | 0.025337 | 0.082041 | 0.1222 | -0.016942 | 0.002115 | 0.12041 | 0.009509 | 0.008096 | -0.038755 | 0.000325 | -0.015179 | 0.005979 | 0.04087 | 0.017294 | 0.048264 | 0.024688
3956.0625 | 121.907 | -0.068665 | 121.756 | 0.13559 | -0.022205 | -0.030314 | -0.029595 | 0.022531 | 0.067269 | -0.071874 | -0.052818 | 0.07006 | -0.036267 | -0.033101 | -0.084531 | -0.050029 | -0.04722 | -0.039797 | 0.20425 | 0.04646 | 0.038351 | 0.03907 | 0.091196 | 0.13593 | -0.003209 | -0.007042 | 0.11584 | 0.009509 | 0.012675 | -0.038755 | -0.004253 | -0.001444 | 0.005979 | 0.031713 | -0.005598 | 0.048264 | 0.010953
3957.8281 | 121.8613 | -0.09613 | 121.7834 | 0.14017 | -0.022205 | -0.025735 | -0.034174 | 0.022531 | 0.071848 | -0.067295 | -0.043661 | 0.074638 | -0.040846 | -0.033101 | -0.084531 | -0.045451 | -0.056376 | -0.035219 | 0.2363 | 0.073925 | 0.070395 | 0.061956 | 0.11866 | 0.16798 | 0.028835 | 0.002115 | 0.12041 | 0.00493 | 0.012675 | -0.038755 | 0.000325 | -0.0106 | 0.010557 | 0.04087 | 0.012715 | 0.043685 | 0.01553
3959.6094 | 121.8933 | -0.059509 | 121.7743 | 0.14017 | -0.022205 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.048239 | 0.065481 | -0.036267 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.044375 | 0.19967 | 0.037304 | 0.029195 | 0.029914 | 0.08204 | 0.13136 | -0.007786 | -0.002463 | 0.11126 | 0.009509 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.001401 | 0.036292 | 0.003559 | 0.048264 | 0.015531
3961.375 | 121.9025 | -0.086975 | 121.7377 | 0.14474 | -0.026784 | -0.016578 | -0.025017 | 0.022531 | 0.071848 | -0.071874 | -0.043661 | 0.074638 | -0.031689 | -0.03768 | -0.075375 | -0.045451 | -0.056376 | -0.026063 | 0.23172 | 0.060191 | 0.070397 | 0.061958 | 0.10951 | 0.15882 | 0.015101 | 0.002115 | 0.12041 | 0.014087 | 0.008096 | -0.029599 | 0.000325 | -0.0106 | 0.019713 | 0.031714 | 0.012715 | 0.043686 | 0.024687
3963.0938 | 121.8384 | -0.09613 | 121.8155 | 0.14017 | -0.026784 | -0.025735 | -0.020438 | 0.022531 | 0.067269 | -0.067295 | -0.039082 | 0.07006 | -0.031689 | -0.03768 | -0.08911 | -0.054607 | -0.051798 | -0.044375 | 0.2363 | 0.069346 | 0.070395 | 0.075692 | 0.11866 | 0.1634 | 0.028835 | 0.006694 | 0.11584 | 0.014087 | 0.008096 | -0.043334 | -0.008831 | -0.006022 | 0.001401 | 0.050028 | 0.012716 | 0.057421 | 0.020109
3964.875 | 121.9437 | -0.054932 | 121.7514 | 0.14017 | -0.022205 | -0.016578 | -0.029595 | 0.022531 | 0.076426 | -0.071874 | -0.039082 | 0.074638 | -0.036267 | -0.03768 | -0.084531 | -0.050029 | -0.04722 | -0.035219 | 0.1951 | 0.032727 | 0.038354 | 0.025337 | 0.077463 | 0.13136 | -0.016942 | 0.006694 | 0.12041 | 0.009509 | 0.008096 | -0.038755 | -0.004253 | -0.001444 | 0.010557 | 0.045449 | 0.008138 | 0.048264 | 0.010953
3966.5938 | 121.875 | -0.073242 | 121.7651 | 0.13559 | -0.026784 | -0.021157 | -0.029595 | 0.017953 | 0.071848 | -0.067295 | -0.043661 | 0.074638 | -0.036267 | -0.03768 | -0.08911 | -0.045451 | -0.051798 | -0.035219 | 0.20883 | 0.046458 | 0.052085 | 0.043647 | 0.091195 | 0.14509 | 0.005947 | 0.002115 | 0.12041 | 0.009509 | 0.008096 | -0.043334 | 0.000325 | -0.006022 | 0.010557 | 0.045449 | 0.008137 | 0.052843 | 0.015531
3968.375 | 121.9482 | -0.045776 | 121.7285 | 0.14017 | -0.022205 | -0.021157 | -0.029595 | 0.022531 | 0.071848 | -0.076452 | -0.043661 | 0.060902 | -0.040846 | -0.033101 | -0.084531 | -0.045451 | -0.065533 | -0.044375 | 0.18594 | 0.023571 | 0.024619 | 0.016181 | 0.068307 | 0.11762 | -0.030676 | 0.002115 | 0.10668 | 0.00493 | 0.012675 | -0.038755 | 0.000325 | -0.019757 | 0.001401 | 0.04087 | 0.021872 | 0.043685 | 0.024687
3970.0938 | 121.8201 | -0.11444 | 121.8201 | 0.13559 | -0.022205 | -0.021157 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.034504 | 0.074638 | -0.040846 | -0.03768 | -0.084531 | -0.054607 | -0.051798 | -0.039797 | 0.25003 | 0.092236 | 0.093284 | 0.084846 | 0.13697 | 0.18629 | 0.051724 | 0.011272 | 0.12041 | 0.00493 | 0.008096 | -0.038755 | -0.008831 | -0.006022 | 0.005979 | 0.050027 | 0.017294 | 0.043685 | 0.010952
3971.8594 | 121.8796 | -0.091553 | 121.7606 | 0.14017 | -0.026784 | -0.025735 | -0.025017 | 0.027109 | 0.071848 | -0.071874 | -0.034504 | 0.074638 | -0.040846 | -0.042259 | -0.079953 | -0.045451 | -0.042641 | -0.035219 | 0.23172 | 0.064769 | 0.065818 | 0.066536 | 0.11866 | 0.1634 | 0.019679 | 0.011272 | 0.12041 | 0.00493 | 0.003517 | -0.034177 | 0.000325 | 0.003135 | 0.010557 | 0.045449 | 0.008137 | 0.039107 | 0.001795
3973.5625 | 121.9437 | -0.064087 | 121.7606 | 0.13101 | -0.026784 | -0.025735 | -0.029595 | 0.022531 | 0.067269 | -0.071874 | -0.043661 | 0.065481 | -0.036267 | -0.03768 | -0.084531 | -0.045451 | -0.04722 | -0.044375 | 0.1951 | 0.037303 | 0.038352 | 0.034492 | 0.086618 | 0.13136 | -0.007787 | 0.002115 | 0.11126 | 0.009509 | 0.008096 | -0.038755 | 0.000325 | -0.001444 | 0.001401 | 0.04087 | 0.003559 | 0.048264 | 0.010953
3975.3281 | 121.7926 | -0.091553 | 121.7606 | 0.13559 | -0.031363 | -0.025735 | -0.029595 | 0.017953 | 0.067269 | -0.067295 | -0.048239 | 0.060902 | -0.036267 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.22714 | 0.06019 | 0.065818 | 0.061958 | 0.10951 | 0.15882 | 0.024258 | -0.002463 | 0.10668 | 0.009509 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.036292 | 0.003559 | 0.048264 | 0.015531
3977.0312 | 121.9437 | -0.064087 | 121.7514 | 0.14017 | -0.022205 | -0.025735 | -0.025017 | 0.027109 | 0.062691 | -0.071874 | -0.034504 | 0.065481 | -0.036267 | -0.028522 | -0.084531 | -0.045451 | -0.051798 | -0.039797 | 0.20425 | 0.041882 | 0.038352 | 0.03907 | 0.091196 | 0.12678 | -0.007787 | 0.011272 | 0.11126 | 0.009509 | 0.017254 | -0.038755 | 0.000325 | -0.006022 | 0.005979 | 0.050027 | 0.017294 | 0.048264 | 0.015531
3978.7969 | 121.9116 | -0.073242 | 121.8018 | 0.14017 | -0.026784 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.048239 | 0.065481 | -0.045424 | -0.03768 | -0.093688 | -0.054607 | -0.051798 | -0.039797 | 0.21341 | 0.046458 | 0.052085 | 0.048225 | 0.095773 | 0.14509 | 0.005947 | -0.002463 | 0.11126 | 0.000352 | 0.008096 | -0.047912 | -0.008831 | -0.006022 | 0.005979 | 0.045449 | 0.003559 | 0.048264 | 0.006374
3980.5781 | 121.9803 | -0.054932 | 121.8201 | 0.14017 | -0.026784 | -0.021157 | -0.029595 | 0.017953 | 0.071848 | -0.067295 | -0.034504 | 0.07006 | -0.040846 | -0.033101 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.1951 | 0.028148 | 0.033775 | 0.025337 | 0.072885 | 0.12678 | -0.012363 | 0.011272 | 0.11584 | 0.00493 | 0.012675 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.050027 | 0.017294 | 0.043685 | 0.010952
3982.2969 | 121.8613 | -0.10529 | 121.8384 | 0.14017 | -0.017627 | -0.021157 | -0.029595 | 0.022531 | 0.076426 | -0.062717 | -0.039082 | 0.074638 | -0.036267 | -0.033101 | -0.084531 | -0.050029 | -0.056376 | -0.039797 | 0.24545 | 0.087659 | 0.084129 | 0.075691 | 0.12782 | 0.18171 | 0.042569 | 0.006694 | 0.12041 | 0.009509 | 0.012675 | -0.038755 | -0.004253 | -0.0106 | 0.005979 | 0.045449 | 0.017294 | 0.048264 | 0.020109
3984.0625 | 121.9666 | -0.068665 | 121.8018 | 0.13559 | -0.022205 | -0.021157 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.043661 | 0.065481 | -0.036267 | -0.033101 | -0.084531 | -0.050029 | -0.04722 | -0.035219 | 0.20425 | 0.04646 | 0.047508 | 0.03907 | 0.091196 | 0.14051 | 0.005948 | 0.002115 | 0.11126 | 0.009509 | 0.012675 | -0.038755 | -0.004253 | -0.001444 | 0.010557 | 0.04087 | 0.003559 | 0.048264 | 0.010953
3985.8281 | 121.907 | -0.091553 | 121.8613 | 0.14017 | -0.026784 | -0.016578 | -0.025017 | 0.027109 | 0.076426 | -0.067295 | -0.034504 | 0.07006 | -0.040846 | -0.033101 | -0.084531 | -0.059185 | -0.051798 | -0.030641 | 0.23172 | 0.064769 | 0.074975 | 0.066536 | 0.11866 | 0.16798 | 0.024258 | 0.011272 | 0.11584 | 0.00493 | 0.012675 | -0.038755 | -0.013409 | -0.006022 | 0.015135 | 0.050027 | 0.017294 | 0.043685 | 0.010952
3987.6094 | 121.9574 | -0.064087 | 121.8201 | 0.14474 | -0.017627 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.043661 | 0.065481 | -0.031689 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.20883 | 0.04646 | 0.038352 | 0.03907 | 0.086618 | 0.13594 | 0.00137 | 0.002115 | 0.11126 | 0.014087 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.04087 | 0.008137 | 0.052842 | 0.020109
3989.3125 | 121.9208 | -0.086975 | 121.8704 | 0.14017 | -0.022205 | -0.021157 | -0.025017 | 0.027109 | 0.071848 | -0.067295 | -0.043661 | 0.07006 | -0.031689 | -0.033101 | -0.079953 | -0.054607 | -0.056376 | -0.039797 | 0.22714 | 0.06477 | 0.065818 | 0.061958 | 0.11408 | 0.15882 | 0.01968 | 0.002115 | 0.11584 | 0.014087 | 0.012675 | -0.034177 | -0.008831 | -0.0106 | 0.005979 | 0.036292 | 0.012715 | 0.048264 | 0.024687
3991.0938 | 121.8887 | -0.10529 | 121.8704 | 0.13559 | -0.026784 | -0.025735 | -0.029595 | 0.031687 | 0.076426 | -0.071874 | -0.039082 | 0.07006 | -0.036267 | -0.033101 | -0.08911 | -0.059185 | -0.051798 | -0.048953 | 0.24087 | 0.078502 | 0.079551 | 0.075691 | 0.13697 | 0.18171 | 0.033412 | 0.006694 | 0.11584 | 0.009509 | 0.012675 | -0.043334 | -0.013409 | -0.006022 | -0.003177 | 0.050028 | 0.012716 | 0.052843 | 0.015531
3992.875 | 121.9849 | -0.086975 | 121.8292 | 0.14017 | -0.026784 | -0.021157 | -0.025017 | 0.022531 | 0.076426 | -0.067295 | -0.039082 | 0.065481 | -0.036267 | -0.033101 | -0.08911 | -0.050029 | -0.056376 | -0.035219 | 0.22714 | 0.060191 | 0.065818 | 0.061958 | 0.10951 | 0.1634 | 0.01968 | 0.006694 | 0.11126 | 0.009509 | 0.012675 | -0.043334 | -0.004253 | -0.0106 | 0.010557 | 0.050028 | 0.017294 | 0.052843 | 0.020109
3994.5938 | 122.0444 | -0.050354 | 121.8384 | 0.13559 | -0.017627 | -0.025735 | -0.025017 | 0.022531 | 0.076426 | -0.067295 | -0.043661 | 0.074638 | -0.036267 | -0.03768 | -0.079953 | -0.059185 | -0.051798 | -0.044375 | 0.18594 | 0.032727 | 0.024619 | 0.025337 | 0.072885 | 0.12678 | -0.016941 | 0.002115 | 0.12041 | 0.009509 | 0.008096 | -0.034177 | -0.013409 | -0.006022 | 0.001401 | 0.036292 | 0.008137 | 0.043686 | 0.015531
3996.3594 | 122.0123 | -0.068665 | 121.8201 | 0.14017 | -0.026784 | -0.021157 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | -0.034504 | 0.074638 | -0.036267 | -0.03768 | -0.084531 | -0.059185 | -0.060955 | -0.044375 | 0.20883 | 0.041881 | 0.047508 | 0.043648 | 0.091196 | 0.13593 | 0.005948 | 0.011272 | 0.12041 | 0.009509 | 0.008096 | -0.038755 | -0.013409 | -0.015179 | 0.001401 | 0.050027 | 0.026451 | 0.048264 | 0.024688
3998.125 | 122.0352 | -0.064087 | 121.8521 | 0.13559 | -0.017627 | -0.025735 | -0.025017 | 0.022531 | 0.076426 | -0.067295 | -0.039082 | 0.065481 | -0.031689 | -0.042259 | -0.084531 | -0.054607 | -0.056376 | -0.044375 | 0.19967 | 0.04646 | 0.038352 | 0.03907 | 0.086618 | 0.14051 | -0.003208 | 0.006694 | 0.11126 | 0.014087 | 0.003517 | -0.038755 | -0.008831 | -0.0106 | 0.001401 | 0.045449 | 0.017294 | 0.052842 | 0.024687
3999.9062 | 121.9299 | -0.09613 | 121.8842 | 0.14932 | -0.017627 | -0.021157 | -0.020438 | 0.017953 | 0.081005 | -0.067295 | -0.043661 | 0.074638 | -0.040846 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.24545 | 0.078503 | 0.074973 | 0.075692 | 0.11408 | 0.17713 | 0.028835 | 0.002115 | 0.12041 | 0.00493 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.04087 | 0.008137 | 0.043685 | 0.010952
4001.6094 | 121.9116 | -0.10529 | 121.9116 | 0.14474 | -0.022205 | -0.025735 | -0.029595 | 0.022531 | 0.081005 | -0.067295 | -0.034504 | 0.07006 | -0.027111 | -0.03768 | -0.084531 | -0.054607 | -0.051798 | -0.044375 | 0.25003 | 0.083081 | 0.079551 | 0.075691 | 0.12782 | 0.18629 | 0.037991 | 0.011272 | 0.11584 | 0.018665 | 0.008096 | -0.038755 | -0.008831 | -0.006022 | 0.001401 | 0.050027 | 0.017294 | 0.05742 | 0.024687
4003.3594 | 122.0169 | -0.059509 | 121.8521 | 0.14017 | -0.026784 | -0.021157 | -0.029595 | 0.022531 | 0.071848 | -0.071874 | -0.043661 | 0.07006 | -0.036267 | -0.03768 | -0.079953 | -0.054607 | -0.051798 | -0.039797 | 0.19967 | 0.032725 | 0.038352 | 0.029914 | 0.08204 | 0.13136 | -0.012365 | 0.002115 | 0.11584 | 0.009509 | 0.008096 | -0.034177 | -0.008831 | -0.006022 | 0.005979 | 0.036292 | 0.008137 | 0.043686 | 0.015531
4005.0781 | 121.9391 | -0.091553 | 121.907 | 0.13559 | -0.022205 | -0.016578 | -0.025017 | 0.027109 | 0.076426 | -0.067295 | -0.043661 | 0.07006 | -0.036267 | -0.03768 | -0.08911 | -0.059185 | -0.051798 | -0.044375 | 0.22714 | 0.069348 | 0.074975 | 0.066536 | 0.11866 | 0.16798 | 0.024258 | 0.002115 | 0.11584 | 0.009509 | 0.008096 | -0.043334 | -0.013409 | -0.006022 | 0.001401 | 0.045449 | 0.008137 | 0.052843 | 0.015531
4006.8594 | 122.0032 | -0.073242 | 121.8842 | 0.13559 | -0.022205 | -0.021157 | -0.020438 | 0.027109 | 0.076426 | -0.067295 | -0.039082 | 0.074638 | -0.040846 | -0.033101 | -0.08911 | -0.050029 | -0.042641 | -0.039797 | 0.20883 | 0.051037 | 0.052085 | 0.052804 | 0.10035 | 0.14967 | 0.005947 | 0.006694 | 0.12041 | 0.00493 | 0.012675 | -0.043334 | -0.004253 | 0.003135 | 0.005979 | 0.050028 | 0.003559 | 0.048264 | 0.001795
4008.625 | 121.9666 | -0.09613 | 121.9116 | 0.13559 | -0.026784 | -0.016578 | -0.025017 | 0.031687 | 0.076426 | -0.067295 | -0.039082 | 0.074638 | -0.036267 | -0.042259 | -0.08911 | -0.054607 | -0.04722 | -0.039797 | 0.23172 | 0.069346 | 0.079552 | 0.071113 | 0.12782 | 0.17256 | 0.028835 | 0.006694 | 0.12041 | 0.009509 | 0.003517 | -0.043334 | -0.008831 | -0.001444 | 0.005979 | 0.050028 | 0.008138 | 0.052843 | 0.010953
4010.3281 | 121.9803 | -0.082397 | 121.9162 | 0.14474 | -0.026784 | -0.025735 | -0.01586 | 0.022531 | 0.076426 | -0.062717 | -0.039082 | 0.07006 | -0.036267 | -0.028522 | -0.08911 | -0.050029 | -0.051798 | -0.039797 | 0.22714 | 0.055613 | 0.056662 | 0.066537 | 0.10493 | 0.15882 | 0.01968 | 0.006694 | 0.11584 | 0.009509 | 0.017254 | -0.043334 | -0.004253 | -0.006022 | 0.005979 | 0.050028 | 0.012716 | 0.052843 | 0.015531
4012.0938 | 122.0078 | -0.068665 | 121.8979 | 0.13559 | -0.031363 | -0.021157 | -0.025017 | 0.017953 | 0.071848 | -0.062717 | -0.043661 | 0.074638 | -0.036267 | -0.033101 | -0.084531 | -0.054607 | -0.051798 | -0.035219 | 0.20425 | 0.037302 | 0.047508 | 0.043648 | 0.086618 | 0.14051 | 0.005948 | 0.002115 | 0.12041 | 0.009509 | 0.012675 | -0.038755 | -0.008831 | -0.006022 | 0.010557 | 0.04087 | 0.008137 | 0.048264 | 0.015531
4013.8594 | 122.0123 | -0.059509 | 121.8979 | 0.14017 | -0.017627 | -0.016578 | -0.029595 | 0.022531 | 0.076426 | -0.062717 | -0.043661 | 0.07006 | -0.036267 | -0.033101 | -0.084531 | -0.054607 | -0.051798 | -0.039797 | 0.19967 | 0.041882 | 0.042931 | 0.029914 | 0.08204 | 0.13594 | -0.003208 | 0.002115 | 0.11584 | 0.009509 | 0.012675 | -0.038755 | -0.008831 | -0.006022 | 0.005979 | 0.04087 | 0.008137 | 0.048264 | 0.015531
4015.5625 | 122.0352 | -0.068665 | 121.9025 | 0.14017 | -0.026784 | -0.021157 | -0.029595 | 0.027109 | 0.071848 | -0.071874 | -0.034504 | 0.065481 | -0.040846 | -0.03768 | -0.08911 | -0.050029 | -0.051798 | -0.039797 | 0.20883 | 0.041881 | 0.047508 | 0.03907 | 0.095774 | 0.14051 | -0.003209 | 0.011272 | 0.11126 | 0.00493 | 0.008096 | -0.043334 | -0.004253 | -0.006022 | 0.005979 | 0.054606 | 0.017294 | 0.048264 | 0.010952
4017.3281 | 121.9849 | -0.10986 | 121.907 | 0.14474 | -0.022205 | -0.021157 | -0.029595 | 0.022531 | 0.076426 | -0.067295 | -0.043661 | 0.065481 | -0.031689 | -0.033101 | -0.079953 | -0.045451 | -0.056376 | -0.039797 | 0.25461 | 0.087658 | 0.088706 | 0.080268 | 0.13239 | 0.18629 | 0.042568 | 0.002115 | 0.11126 | 0.014087 | 0.012675 | -0.034177 | 0.000325 | -0.0106 | 0.005979 | 0.036292 | 0.012715 | 0.048264 | 0.024687
4019.0938 | 122.0306 | -0.068665 | 121.9025 | 0.14017 | -0.022205 | -0.030314 | -0.020438 | 0.027109 | 0.076426 | -0.062717 | -0.043661 | 0.07006 | -0.036267 | -0.03768 | -0.079953 | -0.045451 | -0.051798 | -0.048953 | 0.20883 | 0.04646 | 0.038351 | 0.048227 | 0.095774 | 0.14509 | 0.005948 | 0.002115 | 0.11584 | 0.009509 | 0.008096 | -0.034177 | 0.000325 | -0.006022 | -0.003177 | 0.036292 | 0.008137 | 0.043686 | 0.015531
4020.8125 | 122.0306 | -0.086975 | 121.9162 | 0.13559 | -0.026784 | -0.016578 | -0.025017 | 0.027109 | 0.071848 | -0.067295 | -0.043661 | 0.060902 | -0.040846 | -0.033101 | -0.08911 | -0.050029 | -0.051798 | -0.044375 | 0.22256 | 0.060191 | 0.070397 | 0.061958 | 0.11408 | 0.15882 | 0.01968 | 0.002115 | 0.10668 | 0.00493 | 0.012675 | -0.043334 | -0.004253 | -0.006022 | 0.001401 | 0.045449 | 0.008137 | 0.048264 | 0.010952
4022.5781 | 121.9986 | -0.091553 | 121.9254 | 0.13559 | -0.022205 | -0.030314 | -0.020438 | 0.017953 | 0.067269 | -0.062717 | -0.048239 | 0.074638 | -0.036267 | -0.033101 | -0.084531 | -0.063763 | -0.051798 | -0.035219 | 0.22714 | 0.069348 | 0.061239 | 0.071115 | 0.10951 | 0.15882 | 0.028836 | -0.002463 | 0.12041 | 0.009509 | 0.012675 | -0.038755 | -0.017987 | -0.006022 | 0.010557 | 0.036292 | 0.003559 | 0.048264 | 0.015531
4024.3438 | 121.9849 | -0.10071 | 121.9437 | 0.14474 | -0.022205 | -0.016578 | -0.025017 | 0.022531 | 0.071848 | -0.071874 | -0.043661 | 0.065481 | -0.040846 | -0.03768 | -0.084531 | -0.050029 | -0.056376 | -0.035219 | 0.24545 | 0.078503 | 0.08413 | 0.075691 | 0.12324 | 0.17256 | 0.028834 | 0.002115 | 0.11126 | 0.00493 | 0.008096 | -0.038755 | -0.004253 | -0.0106 | 0.010557 | 0.04087 | 0.012715 | 0.043685 | 0.01553
4026.0625 | 121.9986 | -0.082397 | 121.907 | 0.14932 | -0.026784 | -0.021157 | -0.020438 | 0.022531 | 0.071848 | -0.062717 | -0.043661 | 0.074638 | -0.040846 | -0.033101 | -0.079953 | -0.054607 | -0.056376 | -0.044375 | 0.23172 | 0.055613 | 0.06124 | 0.061959 | 0.10493 | 0.15424 | 0.01968 | 0.002115 | 0.12041 | 0.00493 | 0.012675 | -0.034177 | -0.008831 | -0.0106 | 0.001401 | 0.036292 | 0.012715 | 0.039107 | 0.01553
4027.8438 | 122.0032 | -0.09613 | 121.9482 | 0.14017 | -0.026784 | -0.021157 | -0.025017 | 0.031687 | 0.071848 | -0.067295 | -0.034504 | 0.060902 | -0.036267 | -0.033101 | -0.08911 | -0.054607 | -0.056376 | -0.039797 | 0.2363 | 0.069346 | 0.074973 | 0.071113 | 0.12782 | 0.16798 | 0.028835 | 0.011272 | 0.10668 | 0.009509 | 0.012675 | -0.043334 | -0.008831 | -0.0106 | 0.005979 | 0.054606 | 0.021872 | 0.052843 | 0.020109
4029.5625 | 121.9711 | -0.10986 | 121.9299 | 0.14474 | -0.022205 | -0.021157 | -0.025017 | 0.031687 | 0.076426 | -0.067295 | -0.043661 | 0.060902 | -0.036267 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.25461 | 0.087658 | 0.088706 | 0.084846 | 0.14155 | 0.18629 | 0.042568 | 0.002115 | 0.10668 | 0.009509 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.04087 | 0.008137 | 0.048264 | 0.015531
4031.3438 | 121.9666 | -0.11444 | 121.9482 | 0.14017 | -0.022205 | -0.016578 | -0.020438 | 0.027109 | 0.071848 | -0.071874 | -0.039082 | 0.065481 | -0.036267 | -0.03768 | -0.08911 | -0.054607 | -0.060955 | -0.035219 | 0.25461 | 0.092236 | 0.097863 | 0.094003 | 0.14155 | 0.18629 | 0.042567 | 0.006694 | 0.11126 | 0.009509 | 0.008096 | -0.043334 | -0.008831 | -0.015179 | 0.010557 | 0.050028 | 0.021873 | 0.052843 | 0.024688
4033.125 | 122.0901 | -0.064087 | 121.8887 | 0.14017 | -0.031363 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.029925 | 0.07006 | -0.036267 | -0.03768 | -0.084531 | -0.054607 | -0.051798 | -0.039797 | 0.20425 | 0.032724 | 0.033773 | 0.034492 | 0.086618 | 0.13594 | 0.00137 | 0.015851 | 0.11584 | 0.009509 | 0.008096 | -0.038755 | -0.008831 | -0.006022 | 0.005979 | 0.054606 | 0.021873 | 0.048264 | 0.015531
4034.8438 | 122.0947 | -0.036621 | 121.9116 | 0.14474 | -0.031363 | -0.025735 | -0.020438 | 0.022531 | 0.071848 | -0.067295 | -0.039082 | 0.07006 | -0.031689 | -0.033101 | -0.08911 | -0.050029 | -0.056376 | -0.035219 | 0.18136 | 0.005258 | 0.010886 | 0.016183 | 0.059152 | 0.10847 | -0.030674 | 0.006694 | 0.11584 | 0.014087 | 0.012675 | -0.043334 | -0.004253 | -0.0106 | 0.010557 | 0.050028 | 0.017294 | 0.057421 | 0.024687
4036.625 | 122.0535 | -0.054932 | 121.9162 | 0.13559 | -0.026784 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.039082 | 0.07006 | -0.036267 | -0.028522 | -0.08911 | -0.045451 | -0.051798 | -0.039797 | 0.19052 | 0.028148 | 0.029197 | 0.029915 | 0.077463 | 0.12678 | -0.012363 | 0.006694 | 0.11584 | 0.009509 | 0.017254 | -0.043334 | 0.000325 | -0.006022 | 0.005979 | 0.050028 | 0.012716 | 0.052843 | 0.015531
4038.3281 | 122.081 | -0.050354 | 121.9025 | 0.14474 | -0.026784 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.043661 | 0.065481 | -0.031689 | -0.03768 | -0.079953 | -0.045451 | -0.04722 | -0.035219 | 0.1951 | 0.02357 | 0.024619 | 0.025337 | 0.072885 | 0.1222 | -0.016941 | 0.002115 | 0.11126 | 0.014087 | 0.008096 | -0.034177 | 0.000325 | -0.001444 | 0.010557 | 0.036292 | 0.003559 | 0.048264 | 0.015531
4040.0938 | 121.9528 | -0.11444 | 121.9345 | 0.14474 | -0.031363 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.043661 | 0.074638 | -0.036267 | -0.042259 | -0.084531 | -0.054607 | -0.051798 | -0.035219 | 0.25918 | 0.083078 | 0.093284 | 0.089424 | 0.13697 | 0.18629 | 0.051724 | 0.002115 | 0.12041 | 0.009509 | 0.003517 | -0.038755 | -0.008831 | -0.006022 | 0.010557 | 0.04087 | 0.008137 | 0.048264 | 0.015531
4041.875 | 122.0444 | -0.054932 | 121.8979 | 0.14017 | -0.026784 | -0.016578 | -0.029595 | 0.013375 | 0.067269 | -0.076452 | -0.043661 | 0.07006 | -0.031689 | -0.028522 | -0.084531 | -0.054607 | -0.051798 | -0.035219 | 0.1951 | 0.028148 | 0.038354 | 0.025337 | 0.068307 | 0.1222 | -0.02152 | 0.002115 | 0.11584 | 0.014087 | 0.017254 | -0.038755 | -0.008831 | -0.006022 | 0.010557 | 0.04087 | 0.008137 | 0.052842 | 0.020109
4043.625 | 121.962 | -0.10529 | 121.962 | 0.14017 | -0.022205 | -0.025735 | -0.020438 | 0.022531 | 0.071848 | -0.062717 | -0.039082 | 0.065481 | -0.036267 | -0.028522 | -0.084531 | -0.054607 | -0.051798 | -0.035219 | 0.24545 | 0.083081 | 0.079551 | 0.084848 | 0.12782 | 0.17713 | 0.042569 | 0.006694 | 0.11126 | 0.009509 | 0.017254 | -0.038755 | -0.008831 | -0.006022 | 0.010557 | 0.045449 | 0.012716 | 0.048264 | 0.015531
4045.3438 | 122.0123 | -0.09613 | 121.9482 | 0.14474 | -0.026784 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.048239 | 0.07006 | -0.040846 | -0.033101 | -0.08911 | -0.050029 | -0.051798 | -0.039797 | 0.24087 | 0.069346 | 0.074973 | 0.071113 | 0.11866 | 0.16798 | 0.028835 | -0.002463 | 0.11584 | 0.00493 | 0.012675 | -0.043334 | -0.004253 | -0.006022 | 0.005979 | 0.040871 | 0.003559 | 0.048264 | 0.010952
4047.1094 | 122.0581 | -0.054932 | 121.9162 | 0.13559 | -0.026784 | -0.021157 | -0.025017 | 0.017953 | 0.076426 | -0.067295 | -0.034504 | 0.065481 | -0.040846 | -0.03768 | -0.084531 | -0.045451 | -0.051798 | -0.039797 | 0.19052 | 0.028148 | 0.033775 | 0.029915 | 0.072885 | 0.13136 | -0.012363 | 0.011272 | 0.11126 | 0.00493 | 0.008096 | -0.038755 | 0.000325 | -0.006022 | 0.005979 | 0.050027 | 0.017294 | 0.043685 | 0.010952
4048.8125 | 122.0398 | -0.07782 | 121.907 | 0.14017 | -0.022205 | -0.025735 | -0.034174 | 0.027109 | 0.071848 | -0.062717 | -0.043661 | 0.065481 | -0.031689 | -0.03768 | -0.079953 | -0.059185 | -0.051798 | -0.048953 | 0.21799 | 0.055615 | 0.052085 | 0.043646 | 0.10493 | 0.14967 | 0.015103 | 0.002115 | 0.11126 | 0.014087 | 0.008096 | -0.034177 | -0.013409 | -0.006022 | -0.003177 | 0.036292 | 0.008137 | 0.048264 | 0.020109
4050.5781 | 122.049 | -0.059509 | 121.9208 | 0.13559 | -0.022205 | -0.030314 | -0.025017 | 0.017953 | 0.071848 | -0.071874 | -0.043661 | 0.07006 | -0.036267 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.1951 | 0.037304 | 0.029195 | 0.034492 | 0.077462 | 0.13136 | -0.012365 | 0.002115 | 0.11584 | 0.009509 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.04087 | 0.008137 | 0.048264 | 0.015531
4052.3594 | 122.0947 | -0.064087 | 121.9025 | 0.14474 | -0.022205 | -0.021157 | -0.029595 | 0.031687 | 0.067269 | -0.071874 | -0.039082 | 0.07006 | -0.040846 | -0.028522 | -0.075375 | -0.050029 | -0.04722 | -0.035219 | 0.20883 | 0.041882 | 0.04293 | 0.034492 | 0.095774 | 0.13136 | -0.007787 | 0.006694 | 0.11584 | 0.00493 | 0.017254 | -0.029599 | -0.004253 | -0.001444 | 0.010557 | 0.036293 | 0.008138 | 0.034529 | 0.006374
4054.0625 | 122.0718 | -0.068665 | 121.907 | 0.13559 | -0.022205 | -0.021157 | -0.025017 | 0.031687 | 0.071848 | -0.071874 | -0.043661 | 0.065481 | -0.036267 | -0.03768 | -0.08911 | -0.050029 | -0.051798 | -0.039797 | 0.20425 | 0.04646 | 0.047508 | 0.043648 | 0.10035 | 0.14051 | -0.003209 | 0.002115 | 0.11126 | 0.009509 | 0.008096 | -0.043334 | -0.004253 | -0.006022 | 0.005979 | 0.045449 | 0.008137 | 0.052843 | 0.015531
4055.8438 | 122.0398 | -0.07782 | 121.9254 | 0.13101 | -0.022205 | -0.030314 | -0.025017 | 0.022531 | 0.076426 | -0.067295 | -0.034504 | 0.060902 | -0.031689 | -0.028522 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.20883 | 0.055615 | 0.047506 | 0.052803 | 0.10035 | 0.15425 | 0.010525 | 0.011272 | 0.10668 | 0.014087 | 0.017254 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.050027 | 0.017294 | 0.052842 | 0.020109
4057.5625 | 122.0398 | -0.07782 | 121.9391 | 0.13101 | -0.022205 | -0.030314 | -0.01586 | 0.031687 | 0.076426 | -0.071874 | -0.043661 | 0.07006 | -0.031689 | -0.033101 | -0.084531 | -0.054607 | -0.04722 | -0.039797 | 0.20883 | 0.055615 | 0.047506 | 0.06196 | 0.10951 | 0.15425 | 0.005946 | 0.002115 | 0.11584 | 0.014087 | 0.012675 | -0.038755 | -0.008831 | -0.001444 | 0.005979 | 0.04087 | 0.003559 | 0.052842 | 0.015531
4059.3281 | 122.1085 | -0.068665 | 121.9025 | 0.13559 | -0.026784 | -0.016578 | -0.029595 | 0.027109 | 0.076426 | -0.058139 | -0.043661 | 0.065481 | -0.036267 | -0.033101 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.20425 | 0.041881 | 0.052087 | 0.03907 | 0.095774 | 0.14509 | 0.010526 | 0.002115 | 0.11126 | 0.009509 | 0.012675 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.04087 | 0.008137 | 0.048264 | 0.015531
4061.1094 | 121.9711 | -0.10071 | 121.9299 | 0.14017 | -0.026784 | -0.021157 | -0.025017 | 0.027109 | 0.076426 | -0.062717 | -0.043661 | 0.065481 | -0.040846 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.24087 | 0.073924 | 0.079551 | 0.075691 | 0.12782 | 0.17713 | 0.037991 | 0.002115 | 0.11126 | 0.00493 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.04087 | 0.008137 | 0.043685 | 0.010952
4062.875 | 121.9666 | -0.10529 | 121.9711 | 0.14017 | -0.026784 | -0.021157 | -0.020438 | 0.022531 | 0.076426 | -0.067295 | -0.043661 | 0.074638 | -0.036267 | -0.042259 | -0.079953 | -0.050029 | -0.04722 | -0.044375 | 0.24545 | 0.078502 | 0.084129 | 0.084848 | 0.12782 | 0.18171 | 0.037991 | 0.002115 | 0.12041 | 0.009509 | 0.003517 | -0.034177 | -0.004253 | -0.001444 | 0.001401 | 0.036292 | 0.003559 | 0.043686 | 0.010953
4064.5781 | 121.962 | -0.091553 | 121.9711 | 0.13559 | -0.026784 | -0.016578 | -0.029595 | 0.031687 | 0.076426 | -0.062717 | -0.048239 | 0.074638 | -0.031689 | -0.042259 | -0.084531 | -0.054607 | -0.056376 | -0.039797 | 0.22714 | 0.064769 | 0.074975 | 0.061958 | 0.12324 | 0.16798 | 0.028836 | -0.002463 | 0.12041 | 0.014087 | 0.003517 | -0.038755 | -0.008831 | -0.0106 | 0.005979 | 0.036292 | 0.008137 | 0.052842 | 0.024687
4066.3438 | 122.0444 | -0.082397 | 121.9482 | 0.14017 | -0.026784 | -0.021157 | -0.029595 | 0.031687 | 0.071848 | -0.067295 | -0.034504 | 0.07006 | -0.036267 | -0.03768 | -0.084531 | -0.054607 | -0.051798 | -0.035219 | 0.22256 | 0.055613 | 0.06124 | 0.052802 | 0.11408 | 0.15424 | 0.015102 | 0.011272 | 0.11584 | 0.009509 | 0.008096 | -0.038755 | -0.008831 | -0.006022 | 0.010557 | 0.050027 | 0.017294 | 0.048264 | 0.015531
4068.0469 | 122.0215 | -0.07782 | 121.9666 | 0.14017 | -0.026784 | -0.021157 | -0.029595 | 0.027109 | 0.071848 | -0.067295 | -0.043661 | 0.065481 | -0.036267 | -0.033101 | -0.079953 | -0.054607 | -0.051798 | -0.039797 | 0.21799 | 0.051036 | 0.056663 | 0.048225 | 0.10493 | 0.14967 | 0.010525 | 0.002115 | 0.11126 | 0.009509 | 0.012675 | -0.034177 | -0.008831 | -0.006022 | 0.005979 | 0.036292 | 0.008137 | 0.043686 | 0.015531
4069.8125 | 121.9803 | -0.10529 | 121.9666 | 0.14017 | -0.035942 | -0.030314 | -0.025017 | 0.017953 | 0.071848 | -0.067295 | -0.043661 | 0.07006 | -0.036267 | -0.03768 | -0.08911 | -0.050029 | -0.051798 | -0.035219 | 0.24545 | 0.069344 | 0.074972 | 0.080269 | 0.12324 | 0.17713 | 0.037991 | 0.002115 | 0.11584 | 0.009509 | 0.008096 | -0.043334 | -0.004253 | -0.006022 | 0.010557 | 0.045449 | 0.008137 | 0.052843 | 0.015531
4071.5781 | 121.9803 | -0.10986 | 121.9711 | 0.14474 | -0.022205 | -0.025735 | -0.020438 | 0.027109 | 0.076426 | -0.071874 | -0.043661 | 0.07006 | -0.040846 | -0.028522 | -0.08911 | -0.054607 | -0.051798 | -0.035219 | 0.25461 | 0.087658 | 0.084128 | 0.089425 | 0.13697 | 0.18629 | 0.037989 | 0.002115 | 0.11584 | 0.00493 | 0.017254 | -0.043334 | -0.008831 | -0.006022 | 0.010557 | 0.045449 | 0.008137 | 0.048264 | 0.010952
4073.2812 | 122.0901 | -0.036621 | 121.9162 | 0.14017 | -0.022205 | -0.025735 | -0.029595 | 0.022531 | 0.067269 | -0.067295 | -0.039082 | 0.07006 | -0.031689 | -0.042259 | -0.08911 | -0.050029 | -0.051798 | -0.030641 | 0.17679 | 0.014416 | 0.010886 | 0.007026 | 0.059152 | 0.10389 | -0.030674 | 0.006694 | 0.11584 | 0.014087 | 0.003517 | -0.043334 | -0.004253 | -0.006022 | 0.015135 | 0.050028 | 0.012716 | 0.057421 | 0.020109
4075.0469 | 122.1176 | -0.050354 | 121.9437 | 0.14017 | -0.031363 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.043661 | 0.074638 | -0.040846 | -0.028522 | -0.08911 | -0.050029 | -0.056376 | -0.035219 | 0.19052 | 0.018991 | 0.024619 | 0.020759 | 0.072885 | 0.1222 | -0.016941 | 0.002115 | 0.12041 | 0.00493 | 0.017254 | -0.043334 | -0.004253 | -0.0106 | 0.010557 | 0.045449 | 0.012715 | 0.048264 | 0.01553
4076.8125 | 122.1039 | -0.041199 | 121.9574 | 0.14017 | -0.026784 | -0.021157 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | -0.043661 | 0.065481 | -0.027111 | -0.03768 | -0.079953 | -0.050029 | -0.051798 | -0.035219 | 0.18136 | 0.014415 | 0.020042 | 0.016182 | 0.06373 | 0.10847 | -0.021518 | 0.002115 | 0.11126 | 0.018665 | 0.008096 | -0.034177 | -0.004253 | -0.006022 | 0.010557 | 0.036292 | 0.008137 | 0.052842 | 0.024687
4078.5781 | 122.081 | -0.064087 | 121.9345 | 0.14017 | -0.022205 | -0.021157 | -0.025017 | 0.022531 | 0.081005 | -0.062717 | -0.048239 | 0.074638 | -0.036267 | -0.042259 | -0.08911 | -0.045451 | -0.051798 | -0.035219 | 0.20425 | 0.041882 | 0.04293 | 0.03907 | 0.086618 | 0.14509 | 0.00137 | -0.002463 | 0.12041 | 0.009509 | 0.003517 | -0.043334 | 0.000325 | -0.006022 | 0.010557 | 0.040871 | 0.003559 | 0.052843 | 0.015531
4080.375 | 121.994 | -0.091553 | 121.9666 | 0.14017 | -0.022205 | -0.025735 | -0.034174 | 0.027109 | 0.076426 | -0.067295 | -0.039082 | 0.07006 | -0.040846 | -0.028522 | -0.084531 | -0.054607 | -0.056376 | -0.039797 | 0.23172 | 0.069348 | 0.065818 | 0.057379 | 0.11866 | 0.16798 | 0.024258 | 0.006694 | 0.11584 | 0.00493 | 0.017254 | -0.038755 | -0.008831 | -0.0106 | 0.005979 | 0.045449 | 0.017294 | 0.043685 | 0.01553
4082.1562 | 122.1451 | -0.054932 | 121.9345 | 0.13559 | -0.026784 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.048239 | 0.065481 | -0.036267 | -0.033101 | -0.079953 | -0.054607 | -0.051798 | -0.044375 | 0.19052 | 0.028148 | 0.029197 | 0.025337 | 0.077463 | 0.12678 | -0.007785 | -0.002463 | 0.11126 | 0.009509 | 0.012675 | -0.034177 | -0.008831 | -0.006022 | 0.001401 | 0.031714 | 0.003559 | 0.043686 | 0.015531
4083.8594 | 122.0856 | -0.064087 | 121.9299 | 0.14017 | -0.026784 | -0.021157 | -0.029595 | 0.017953 | 0.071848 | -0.062717 | -0.048239 | 0.065481 | -0.036267 | -0.03768 | -0.093688 | -0.054607 | -0.056376 | -0.035219 | 0.20425 | 0.037303 | 0.04293 | 0.034492 | 0.08204 | 0.13594 | 0.00137 | -0.002463 | 0.11126 | 0.009509 | 0.008096 | -0.047912 | -0.008831 | -0.0106 | 0.010557 | 0.045449 | 0.008137 | 0.057421 | 0.020109
4085.625 | 121.9666 | -0.11902 | 121.9757 | 0.14474 | -0.017627 | -0.016578 | -0.025017 | 0.027109 | 0.071848 | -0.067295 | -0.043661 | 0.07006 | -0.040846 | -0.03768 | -0.079953 | -0.054607 | -0.051798 | -0.039797 | 0.26376 | 0.10139 | 0.10244 | 0.094002 | 0.14613 | 0.19087 | 0.051724 | 0.002115 | 0.11584 | 0.00493 | 0.008096 | -0.034177 | -0.008831 | -0.006022 | 0.005979 | 0.036292 | 0.008137 | 0.039107 | 0.010952
4087.3906 | 121.994 | -0.10529 | 121.9803 | 0.14474 | -0.026784 | -0.016578 | -0.025017 | 0.022531 | 0.076426 | -0.053561 | -0.043661 | 0.07006 | -0.036267 | -0.03768 | -0.084531 | -0.054607 | -0.04722 | -0.035219 | 0.25003 | 0.078502 | 0.088708 | 0.080269 | 0.12782 | 0.18171 | 0.051725 | 0.002115 | 0.11584 | 0.009509 | 0.008096 | -0.038755 | -0.008831 | -0.001444 | 0.010557 | 0.04087 | 0.003559 | 0.048264 | 0.010953
4089.0938 | 122.1451 | -0.064087 | 121.9574 | 0.14474 | -0.026784 | -0.021157 | -0.034174 | 0.022531 | 0.067269 | -0.062717 | -0.048239 | 0.07006 | -0.036267 | -0.033101 | -0.08911 | -0.045451 | -0.051798 | -0.035219 | 0.20883 | 0.037303 | 0.04293 | 0.029913 | 0.086618 | 0.13136 | 0.00137 | -0.002463 | 0.11584 | 0.009509 | 0.012675 | -0.043334 | 0.000325 | -0.006022 | 0.010557 | 0.040871 | 0.003559 | 0.052843 | 0.015531
4090.875 | 122.0901 | -0.054932 | 121.9299 | 0.14017 | -0.026784 | -0.016578 | -0.029595 | 0.031687 | 0.076426 | -0.062717 | -0.048239 | 0.065481 | -0.036267 | -0.03768 | -0.08911 | -0.050029 | -0.060955 | -0.039797 | 0.1951 | 0.028148 | 0.038354 | 0.025337 | 0.086619 | 0.13136 | -0.007785 | -0.002463 | 0.11126 | 0.009509 | 0.008096 | -0.043334 | -0.004253 | -0.015179 | 0.005979 | 0.040871 | 0.012716 | 0.052843 | 0.024688
4092.6094 | 122.0993 | -0.059509 | 121.9162 | 0.13559 | -0.035942 | -0.030314 | -0.025017 | 0.027109 | 0.071848 | -0.067295 | -0.034504 | 0.065481 | -0.031689 | -0.03768 | -0.08911 | -0.059185 | -0.056376 | -0.035219 | 0.1951 | 0.023567 | 0.029195 | 0.034492 | 0.086618 | 0.13136 | -0.007786 | 0.011272 | 0.11126 | 0.014087 | 0.008096 | -0.043334 | -0.013409 | -0.0106 | 0.010557 | 0.054606 | 0.021872 | 0.057421 | 0.024687
4094.375 | 121.9986 | -0.1236 | 121.9666 | 0.13559 | -0.026784 | -0.025735 | -0.029595 | 0.027109 | 0.071848 | -0.067295 | -0.043661 | 0.07006 | -0.040846 | -0.033101 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.25918 | 0.096812 | 0.097861 | 0.094001 | 0.15071 | 0.19544 | 0.056301 | 0.002115 | 0.11584 | 0.00493 | 0.012675 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.04087 | 0.008137 | 0.043685 | 0.010952
4096.0781 | 121.9894 | -0.086975 | 121.9574 | 0.14017 | -0.031363 | -0.016578 | -0.034174 | 0.031687 | 0.067269 | -0.067295 | -0.043661 | 0.065481 | -0.040846 | -0.033101 | -0.079953 | -0.050029 | -0.051798 | -0.048953 | 0.22714 | 0.055612 | 0.070397 | 0.052801 | 0.11866 | 0.15424 | 0.01968 | 0.002115 | 0.11126 | 0.00493 | 0.012675 | -0.034177 | -0.004253 | -0.006022 | -0.003177 | 0.036292 | 0.008137 | 0.039107 | 0.010952
4097.8438 | 121.9894 | -0.10529 | 121.994 | 0.14474 | -0.026784 | -0.021157 | -0.025017 | 0.022531 | 0.076426 | -0.067295 | -0.048239 | 0.07006 | -0.036267 | -0.033101 | -0.08911 | -0.045451 | -0.051798 | -0.039797 | 0.25003 | 0.078502 | 0.084129 | 0.080269 | 0.12782 | 0.18171 | 0.037991 | -0.002463 | 0.11584 | 0.009509 | 0.012675 | -0.043334 | 0.000325 | -0.006022 | 0.005979 | 0.040871 | 0.003559 | 0.052843 | 0.015531
4099.5469 | 122.0627 | -0.07782 | 121.9528 | 0.14017 | -0.022205 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.052818 | 0.07006 | -0.036267 | -0.042259 | -0.075375 | -0.045451 | -0.04722 | -0.039797 | 0.21799 | 0.055615 | 0.052085 | 0.048225 | 0.10035 | 0.14967 | 0.010525 | -0.007042 | 0.11584 | 0.009509 | 0.003517 | -0.029599 | 0.000325 | -0.001444 | 0.005979 | 0.022557 | -0.005598 | 0.039108 | 0.010953
4101.3281 | 122.113 | -0.059509 | 121.9574 | 0.14932 | -0.026784 | -0.021157 | -0.025017 | 0.027109 | 0.067269 | -0.071874 | -0.039082 | 0.074638 | -0.040846 | -0.042259 | -0.079953 | -0.054607 | -0.04722 | -0.039797 | 0.20883 | 0.032725 | 0.038352 | 0.034492 | 0.086618 | 0.12678 | -0.012365 | 0.006694 | 0.12041 | 0.00493 | 0.003517 | -0.034177 | -0.008831 | -0.001444 | 0.005979 | 0.040871 | 0.008138 | 0.039107 | 0.006374
4103.0938 | 121.9894 | -0.11902 | 121.9711 | 0.13559 | -0.026784 | -0.016578 | -0.029595 | 0.027109 | 0.071848 | -0.071874 | -0.048239 | 0.060902 | -0.031689 | -0.03768 | -0.079953 | -0.050029 | -0.051798 | -0.044375 | 0.25461 | 0.092235 | 0.10244 | 0.089424 | 0.14613 | 0.19087 | 0.047145 | -0.002463 | 0.10668 | 0.014087 | 0.008096 | -0.034177 | -0.004253 | -0.006022 | 0.001401 | 0.031714 | 0.003559 | 0.048264 | 0.020109
4104.875 | 121.9849 | -0.09613 | 121.9894 | 0.13559 | -0.022205 | -0.025735 | -0.020438 | 0.022531 | 0.076426 | -0.062717 | -0.048239 | 0.07006 | -0.040846 | -0.03768 | -0.079953 | -0.050029 | -0.04722 | -0.035219 | 0.23172 | 0.073925 | 0.070395 | 0.075692 | 0.11866 | 0.17256 | 0.033413 | -0.002463 | 0.11584 | 0.00493 | 0.008096 | -0.034177 | -0.004253 | -0.001444 | 0.010557 | 0.031714 | -0.001019 | 0.039107 | 0.006374
4106.5938 | 122.0627 | -0.073242 | 121.962 | 0.14017 | -0.026784 | -0.025735 | -0.01586 | 0.027109 | 0.067269 | -0.071874 | -0.039082 | 0.065481 | -0.040846 | -0.033101 | -0.08911 | -0.050029 | -0.04722 | -0.039797 | 0.21341 | 0.046458 | 0.047507 | 0.057382 | 0.10035 | 0.14051 | 0.001368 | 0.006694 | 0.11126 | 0.00493 | 0.012675 | -0.043334 | -0.004253 | -0.001444 | 0.005979 | 0.050028 | 0.008138 | 0.048264 | 0.006374
4108.375 | 122.0078 | -0.086975 | 121.9757 | 0.13559 | -0.026784 | -0.025735 | -0.020438 | 0.027109 | 0.076426 | -0.067295 | -0.043661 | 0.07006 | -0.040846 | -0.033101 | -0.079953 | -0.050029 | -0.056376 | -0.039797 | 0.22256 | 0.060191 | 0.06124 | 0.066537 | 0.11408 | 0.1634 | 0.01968 | 0.002115 | 0.11584 | 0.00493 | 0.012675 | -0.034177 | -0.004253 | -0.0106 | 0.005979 | 0.036292 | 0.012715 | 0.039107 | 0.01553
4110.0938 | 121.9711 | -0.091553 | 121.9574 | 0.13559 | -0.022205 | -0.021157 | -0.029595 | 0.027109 | 0.071848 | -0.071874 | -0.048239 | 0.07006 | -0.036267 | -0.042259 | -0.079953 | -0.050029 | -0.051798 | -0.039797 | 0.22714 | 0.069348 | 0.070396 | 0.061958 | 0.11866 | 0.1634 | 0.019679 | -0.002463 | 0.11584 | 0.009509 | 0.003517 | -0.034177 | -0.004253 | -0.006022 | 0.005979 | 0.031714 | 0.003559 | 0.043686 | 0.015531
4111.875 | 122.1039 | -0.07782 | 121.9437 | 0.14474 | -0.026784 | -0.016578 | -0.029595 | 0.027109 | 0.076426 | -0.071874 | -0.039082 | 0.07006 | -0.040846 | -0.028522 | -0.093688 | -0.054607 | -0.051798 | -0.039797 | 0.22256 | 0.051036 | 0.061242 | 0.048225 | 0.10493 | 0.15425 | 0.005946 | 0.006694 | 0.11584 | 0.00493 | 0.017254 | -0.047912 | -0.008831 | -0.006022 | 0.005979 | 0.054606 | 0.012716 | 0.052842 | 0.010952
4113.5781 | 122.0398 | -0.10529 | 121.9803 | 0.14017 | -0.022205 | -0.021157 | -0.020438 | 0.022531 | 0.071848 | -0.062717 | -0.043661 | 0.065481 | -0.040846 | -0.03768 | -0.084531 | -0.050029 | -0.060955 | -0.039797 | 0.24545 | 0.083081 | 0.084129 | 0.084848 | 0.12782 | 0.17713 | 0.042569 | 0.002115 | 0.11126 | 0.00493 | 0.008096 | -0.038755 | -0.004253 | -0.015179 | 0.005979 | 0.04087 | 0.017294 | 0.043685 | 0.020109
4115.3438 | 121.994 | -0.10529 | 121.9894 | 0.14017 | -0.026784 | -0.021157 | -0.025017 | 0.022531 | 0.062691 | -0.067295 | -0.048239 | 0.07006 | -0.036267 | -0.03768 | -0.079953 | -0.040873 | -0.051798 | -0.044375 | 0.24545 | 0.078502 | 0.084129 | 0.080269 | 0.12782 | 0.16798 | 0.037991 | -0.002463 | 0.11584 | 0.009509 | 0.008096 | -0.034177 | 0.004903 | -0.006022 | 0.001401 | 0.031714 | 0.003559 | 0.043686 | 0.015531
4117.125 | 122.0123 | -0.091553 | 121.9803 | 0.14474 | -0.031363 | -0.030314 | -0.020438 | 0.027109 | 0.081005 | -0.071874 | -0.043661 | 0.07006 | -0.036267 | -0.03768 | -0.08911 | -0.050029 | -0.056376 | -0.035219 | 0.2363 | 0.06019 | 0.061239 | 0.071115 | 0.11866 | 0.17256 | 0.019679 | 0.002115 | 0.11584 | 0.009509 | 0.008096 | -0.043334 | -0.004253 | -0.0106 | 0.010557 | 0.045449 | 0.012715 | 0.052843 | 0.020109
4118.8906 | 122.0947 | -0.054932 | 121.9162 | 0.14017 | -0.026784 | -0.021157 | -0.025017 | 0.022531 | 0.067269 | -0.071874 | -0.048239 | 0.07006 | -0.040846 | -0.042259 | -0.084531 | -0.054607 | -0.060955 | -0.035219 | 0.1951 | 0.028148 | 0.033775 | 0.029915 | 0.077463 | 0.1222 | -0.016942 | -0.002463 | 0.11584 | 0.00493 | 0.003517 | -0.038755 | -0.008831 | -0.015179 | 0.010557 | 0.036292 | 0.012716 | 0.043685 | 0.020109
4120.6406 | 122.0032 | -0.11444 | 121.9711 | 0.14017 | -0.026784 | -0.025735 | -0.025017 | 0.031687 | 0.071848 | -0.067295 | -0.043661 | 0.07006 | -0.050002 | -0.033101 | -0.08911 | -0.040873 | -0.04722 | -0.039797 | 0.25461 | 0.087657 | 0.088706 | 0.089424 | 0.14613 | 0.18629 | 0.047146 | 0.002115 | 0.11584 | -0.004226 | 0.012675 | -0.043334 | 0.004903 | -0.001444 | 0.005979 | 0.045449 | 0.003559 | 0.039108 | -0.002782
4122.3594 | 122.0856 | -0.068665 | 121.9528 | 0.13559 | -0.031363 | -0.016578 | -0.025017 | 0.027109 | 0.067269 | -0.067295 | -0.043661 | 0.074638 | -0.036267 | -0.03768 | -0.093688 | -0.050029 | -0.051798 | -0.044375 | 0.20425 | 0.037302 | 0.052087 | 0.043648 | 0.095774 | 0.13593 | 0.00137 | 0.002115 | 0.12041 | 0.009509 | 0.008096 | -0.047912 | -0.004253 | -0.006022 | 0.001401 | 0.050027 | 0.008137 | 0.057421 | 0.015531
4124.1094 | 122.1039 | -0.059509 | 121.9345 | 0.14017 | -0.026784 | -0.016578 | -0.025017 | 0.022531 | 0.081005 | -0.062717 | -0.048239 | 0.065481 | -0.036267 | -0.042259 | -0.079953 | -0.054607 | -0.04722 | -0.030641 | 0.19967 | 0.032725 | 0.042931 | 0.034492 | 0.08204 | 0.14051 | -0.003208 | -0.002463 | 0.11126 | 0.009509 | 0.003517 | -0.034177 | -0.008831 | -0.001444 | 0.015135 | 0.031714 | -0.001019 | 0.043686 | 0.010953
4125.875 | 122.1085 | -0.082397 | 121.9162 | 0.13559 | -0.026784 | -0.016578 | -0.025017 | 0.027109 | 0.067269 | -0.071874 | -0.039082 | 0.060902 | -0.040846 | -0.042259 | -0.084531 | -0.045451 | -0.056376 | -0.039797 | 0.21798 | 0.055613 | 0.065819 | 0.05738 | 0.10951 | 0.14967 | 0.010523 | 0.006694 | 0.10668 | 0.00493 | 0.003517 | -0.038755 | 0.000325 | -0.0106 | 0.005979 | 0.045449 | 0.017294 | 0.043685 | 0.01553
4127.6094 | 121.994 | -0.10986 | 121.9849 | 0.14474 | -0.026784 | -0.016578 | -0.025017 | 0.017953 | 0.076426 | -0.071874 | -0.043661 | 0.065481 | -0.040846 | -0.033101 | -0.084531 | -0.054607 | -0.051798 | -0.044375 | 0.25461 | 0.083079 | 0.093285 | 0.084846 | 0.12782 | 0.18629 | 0.037989 | 0.002115 | 0.11126 | 0.00493 | 0.012675 | -0.038755 | -0.008831 | -0.006022 | 0.001401 | 0.04087 | 0.008137 | 0.043685 | 0.010952
4129.375 | 121.9666 | -0.09613 | 121.9803 | 0.13559 | -0.031363 | -0.021157 | -0.020438 | 0.027109 | 0.071848 | -0.062717 | -0.048239 | 0.07006 | -0.050002 | -0.033101 | -0.08911 | -0.045451 | -0.051798 | -0.039797 | 0.23172 | 0.064767 | 0.074973 | 0.075692 | 0.12324 | 0.16798 | 0.033413 | -0.002463 | 0.11584 | -0.004226 | 0.012675 | -0.043334 | 0.000325 | -0.006022 | 0.005979 | 0.040871 | 0.003559 | 0.039108 | 0.001796
4131.0781 | 122.0078 | -0.11902 | 121.9757 | 0.14017 | -0.035942 | -0.030314 | -0.029595 | 0.027109 | 0.071848 | -0.067295 | -0.043661 | 0.074638 | -0.036267 | -0.033101 | -0.079953 | -0.050029 | -0.051798 | -0.039797 | 0.25918 | 0.083077 | 0.088705 | 0.089424 | 0.14613 | 0.19087 | 0.051724 | 0.002115 | 0.12041 | 0.009509 | 0.012675 | -0.034177 | -0.004253 | -0.006022 | 0.005979 | 0.036292 | 0.008137 | 0.043686 | 0.015531
4132.8594 | 122.0993 | -0.064087 | 121.9528 | 0.13559 | -0.026784 | -0.021157 | -0.025017 | 0.027109 | 0.071848 | -0.067295 | -0.039082 | 0.065481 | -0.036267 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.19967 | 0.037303 | 0.04293 | 0.03907 | 0.091196 | 0.13594 | -0.003208 | 0.006694 | 0.11126 | 0.009509 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.045449 | 0.012716 | 0.048264 | 0.015531
4134.5625 | 122.1588 | -0.045776 | 121.9345 | 0.14474 | -0.026784 | -0.025735 | -0.020438 | 0.027109 | 0.071848 | -0.067295 | -0.048239 | 0.07006 | -0.040846 | -0.03768 | -0.075375 | -0.054607 | -0.04722 | -0.039797 | 0.19052 | 0.018992 | 0.020041 | 0.025338 | 0.072885 | 0.11762 | -0.021519 | -0.002463 | 0.11584 | 0.00493 | 0.008096 | -0.029599 | -0.008831 | -0.001444 | 0.005979 | 0.027136 | -0.001019 | 0.034529 | 0.006374
4136.3281 | 122.0627 | -0.068665 | 121.9528 | 0.13559 | -0.022205 | -0.021157 | -0.025017 | 0.022531 | 0.076426 | -0.067295 | -0.048239 | 0.060902 | -0.036267 | -0.033101 | -0.08911 | -0.050029 | -0.04722 | -0.039797 | 0.20425 | 0.04646 | 0.047508 | 0.043648 | 0.091196 | 0.14509 | 0.00137 | -0.002463 | 0.10668 | 0.009509 | 0.012675 | -0.043334 | -0.004253 | -0.001444 | 0.005979 | 0.040871 | -0.001019 | 0.052843 | 0.010953
4138.0938 | 122.1313 | -0.059509 | 121.9162 | 0.14017 | -0.022205 | -0.021157 | -0.025017 | 0.027109 | 0.071848 | -0.062717 | -0.048239 | 0.065481 | -0.036267 | -0.042259 | -0.084531 | -0.045451 | -0.051798 | -0.039797 | 0.19967 | 0.037304 | 0.038352 | 0.034492 | 0.086618 | 0.13136 | -0.003208 | -0.002463 | 0.11126 | 0.009509 | 0.003517 | -0.038755 | 0.000325 | -0.006022 | 0.005979 | 0.036292 | 0.003559 | 0.048264 | 0.015531
4139.875 | 121.9849 | -0.11444 | 121.9849 | 0.14932 | -0.026784 | -0.021157 | -0.025017 | 0.027109 | 0.071848 | -0.062717 | -0.043661 | 0.065481 | -0.040846 | -0.03768 | -0.084531 | -0.050029 | -0.04722 | -0.039797 | 0.26376 | 0.087657 | 0.093284 | 0.089424 | 0.14155 | 0.18629 | 0.051724 | 0.002115 | 0.11126 | 0.00493 | 0.008096 | -0.038755 | -0.004253 | -0.001444 | 0.005979 | 0.04087 | 0.003559 | 0.043685 | 0.006374
4141.5781 | 122.1039 | -0.050354 | 121.9299 | 0.14017 | -0.022205 | -0.021157 | -0.029595 | 0.017953 | 0.071848 | -0.067295 | -0.043661 | 0.074638 | -0.036267 | -0.042259 | -0.08911 | -0.050029 | -0.056376 | -0.035219 | 0.19052 | 0.028149 | 0.029197 | 0.020759 | 0.068307 | 0.1222 | -0.016941 | 0.002115 | 0.12041 | 0.009509 | 0.003517 | -0.043334 | -0.004253 | -0.0106 | 0.010557 | 0.045449 | 0.012715 | 0.052843 | 0.020109
4143.3594 | 122.113 | -0.064087 | 121.9299 | 0.14017 | -0.031363 | -0.021157 | -0.029595 | 0.022531 | 0.076426 | -0.076452 | -0.048239 | 0.074638 | -0.031689 | -0.03768 | -0.084531 | -0.054607 | -0.056376 | -0.039797 | 0.20425 | 0.032724 | 0.04293 | 0.034492 | 0.086618 | 0.14051 | -0.012365 | -0.002463 | 0.12041 | 0.014087 | 0.008096 | -0.038755 | -0.008831 | -0.0106 | 0.005979 | 0.036292 | 0.008137 | 0.052842 | 0.024687
4145.1406 | 122.1359 | -0.045776 | 121.9528 | 0.13559 | -0.031363 | -0.021157 | -0.029595 | 0.027109 | 0.076426 | -0.067295 | -0.043661 | 0.074638 | -0.031689 | -0.028522 | -0.08911 | -0.054607 | -0.051798 | -0.035219 | 0.18136 | 0.014413 | 0.024619 | 0.016181 | 0.072885 | 0.1222 | -0.021519 | 0.002115 | 0.12041 | 0.014087 | 0.017254 | -0.043334 | -0.008831 | -0.006022 | 0.010557 | 0.045449 | 0.008137 | 0.057421 | 0.020109
4146.8438 | 122.0947 | -0.064087 | 121.9162 | 0.14017 | -0.026784 | -0.021157 | -0.038752 | 0.017953 | 0.067269 | -0.071874 | -0.039082 | 0.065481 | -0.036267 | -0.042259 | -0.075375 | -0.054607 | -0.051798 | -0.044375 | 0.20425 | 0.037303 | 0.04293 | 0.025335 | 0.08204 | 0.13136 | -0.007787 | 0.006694 | 0.11126 | 0.009509 | 0.003517 | -0.029599 | -0.008831 | -0.006022 | 0.001401 | 0.036293 | 0.012716 | 0.039108 | 0.015531
4148.6094 | 122.1085 | -0.041199 | 121.9208 | 0.14474 | -0.022205 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.039082 | 0.07006 | -0.040846 | -0.03768 | -0.084531 | -0.045451 | -0.051798 | -0.044375 | 0.18594 | 0.018994 | 0.020042 | 0.016182 | 0.06373 | 0.11305 | -0.021518 | 0.006694 | 0.11584 | 0.00493 | 0.008096 | -0.038755 | 0.000325 | -0.006022 | 0.001401 | 0.045449 | 0.012716 | 0.043685 | 0.010952
4150.3281 | 122.1085 | -0.073242 | 121.9482 | 0.14017 | -0.026784 | -0.021157 | -0.029595 | 0.027109 | 0.071848 | -0.067295 | -0.039082 | 0.065481 | -0.036267 | -0.033101 | -0.08911 | -0.045451 | -0.051798 | -0.039797 | 0.21341 | 0.046458 | 0.052085 | 0.043647 | 0.10035 | 0.14509 | 0.005947 | 0.006694 | 0.11126 | 0.009509 | 0.012675 | -0.043334 | 0.000325 | -0.006022 | 0.005979 | 0.050028 | 0.012716 | 0.052843 | 0.015531
4152.0938 | 122.0535 | -0.045776 | 121.9391 | 0.13559 | -0.031363 | -0.016578 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.043661 | 0.065481 | -0.031689 | -0.033101 | -0.079953 | -0.050029 | -0.04722 | -0.039797 | 0.18136 | 0.014413 | 0.029198 | 0.020759 | 0.068307 | 0.11762 | -0.021519 | 0.002115 | 0.11126 | 0.014087 | 0.012675 | -0.034177 | -0.004253 | -0.001444 | 0.005979 | 0.036292 | 0.003559 | 0.048264 | 0.015531
4153.875 | 122.0764 | -0.082397 | 121.962 | 0.14474 | -0.035942 | -0.025735 | -0.025017 | 0.027109 | 0.058113 | -0.062717 | -0.039082 | 0.065481 | -0.040846 | -0.028522 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.22714 | 0.046455 | 0.056662 | 0.05738 | 0.10951 | 0.14051 | 0.01968 | 0.006694 | 0.11126 | 0.00493 | 0.017254 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.045449 | 0.012716 | 0.043685 | 0.010952
4155.6406 | 122.0215 | -0.086975 | 121.9894 | 0.13559 | -0.026784 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.043661 | 0.07006 | -0.040846 | -0.042259 | -0.093688 | -0.054607 | -0.051798 | -0.030641 | 0.22256 | 0.060191 | 0.065818 | 0.061958 | 0.10951 | 0.15882 | 0.01968 | 0.002115 | 0.11584 | 0.00493 | 0.003517 | -0.047912 | -0.008831 | -0.006022 | 0.015135 | 0.050027 | 0.008137 | 0.052842 | 0.010952
4157.3594 | 122.0947 | -0.073242 | 121.9528 | 0.14017 | -0.026784 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.034504 | 0.07006 | -0.036267 | -0.033101 | -0.079953 | -0.054607 | -0.056376 | -0.039797 | 0.21341 | 0.046458 | 0.047507 | 0.043647 | 0.095773 | 0.14509 | 0.005947 | 0.011272 | 0.11584 | 0.009509 | 0.012675 | -0.034177 | -0.008831 | -0.0106 | 0.005979 | 0.045449 | 0.021872 | 0.043686 | 0.020109
4159.0625 | 122.0581 | -0.059509 | 121.962 | 0.14017 | -0.026784 | -0.021157 | -0.025017 | 0.027109 | 0.071848 | -0.067295 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.08911 | -0.050029 | -0.056376 | -0.044375 | 0.19967 | 0.032725 | 0.038352 | 0.034492 | 0.086618 | 0.13136 | -0.007786 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.043334 | -0.004253 | -0.0106 | 0.001401 | 0.040871 | 0.008137 | 0.048264 | 0.01553
4160.8281 | 121.9849 | -0.091553 | 121.9528 | 0.14474 | -0.026784 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.043661 | 0.065481 | -0.050002 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.2363 | 0.064769 | 0.065818 | 0.066536 | 0.11408 | 0.1634 | 0.028836 | 0.002115 | 0.11126 | -0.004226 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.04087 | 0.008137 | 0.034529 | 0.001796
4162.5469 | 122.1039 | -0.068665 | 121.9116 | 0.13559 | -0.026784 | -0.025735 | -0.025017 | 0.027109 | 0.071848 | -0.067295 | -0.052818 | 0.07006 | -0.040846 | -0.042259 | -0.084531 | -0.050029 | -0.04722 | -0.039797 | 0.20425 | 0.041881 | 0.04293 | 0.043648 | 0.095774 | 0.14051 | 0.00137 | -0.007042 | 0.11584 | 0.00493 | 0.003517 | -0.038755 | -0.004253 | -0.001444 | 0.005979 | 0.031713 | -0.005598 | 0.043685 | 0.006374
4164.3125 | 122.0398 | -0.086975 | 121.9894 | 0.14474 | -0.026784 | -0.025735 | -0.020438 | 0.022531 | 0.071848 | -0.058139 | -0.039082 | 0.065481 | -0.045424 | -0.03768 | -0.084531 | -0.059185 | -0.056376 | -0.048953 | 0.23172 | 0.060191 | 0.06124 | 0.066537 | 0.10951 | 0.15882 | 0.028836 | 0.006694 | 0.11126 | 0.000352 | 0.008096 | -0.038755 | -0.013409 | -0.0106 | -0.003177 | 0.045449 | 0.017294 | 0.039107 | 0.010952
4166.0781 | 122.1405 | -0.059509 | 121.9162 | 0.14017 | -0.031363 | -0.021157 | -0.020438 | 0.017953 | 0.071848 | -0.071874 | -0.039082 | 0.065481 | -0.036267 | -0.042259 | -0.079953 | -0.050029 | -0.051798 | -0.039797 | 0.19967 | 0.028146 | 0.038352 | 0.039071 | 0.077462 | 0.13136 | -0.012365 | 0.006694 | 0.11126 | 0.009509 | 0.003517 | -0.034177 | -0.004253 | -0.006022 | 0.005979 | 0.040871 | 0.012716 | 0.043686 | 0.015531
4167.8594 | 122.1176 | -0.064087 | 121.9391 | 0.14017 | -0.026784 | -0.025735 | -0.034174 | 0.031687 | 0.067269 | -0.067295 | -0.043661 | 0.065481 | -0.036267 | -0.03768 | -0.084531 | -0.045451 | -0.056376 | -0.030641 | 0.20425 | 0.037303 | 0.038352 | 0.029913 | 0.095774 | 0.13136 | -0.003208 | 0.002115 | 0.11126 | 0.009509 | 0.008096 | -0.038755 | 0.000325 | -0.0106 | 0.015135 | 0.04087 | 0.012715 | 0.048264 | 0.020109
4169.5625 | 121.9666 | -0.10529 | 121.994 | 0.14474 | -0.026784 | -0.025735 | -0.029595 | 0.008797 | 0.081005 | -0.058139 | -0.043661 | 0.065481 | -0.040846 | -0.042259 | -0.08911 | -0.050029 | -0.051798 | -0.044375 | 0.25003 | 0.078502 | 0.079551 | 0.075691 | 0.11408 | 0.18629 | 0.047147 | 0.002115 | 0.11126 | 0.00493 | 0.003517 | -0.043334 | -0.004253 | -0.006022 | 0.001401 | 0.045449 | 0.008137 | 0.048264 | 0.010952
4171.3281 | 122.0123 | -0.091553 | 121.9528 | 0.14017 | -0.031363 | -0.025735 | -0.025017 | 0.031687 | 0.067269 | -0.071874 | -0.048239 | 0.065481 | -0.040846 | -0.033101 | -0.08911 | -0.045451 | -0.051798 | -0.044375 | 0.23172 | 0.06019 | 0.065818 | 0.066536 | 0.12324 | 0.15882 | 0.019679 | -0.002463 | 0.11126 | 0.00493 | 0.012675 | -0.043334 | 0.000325 | -0.006022 | 0.001401 | 0.040871 | 0.003559 | 0.048264 | 0.010952
4173.0938 | 122.0398 | -0.082397 | 121.9711 | 0.14474 | -0.031363 | -0.021157 | -0.025017 | 0.027109 | 0.071848 | -0.076452 | -0.048239 | 0.074638 | -0.040846 | -0.03768 | -0.079953 | -0.050029 | -0.056376 | -0.030641 | 0.22714 | 0.051034 | 0.06124 | 0.05738 | 0.10951 | 0.15424 | 0.005945 | -0.002463 | 0.12041 | 0.00493 | 0.008096 | -0.034177 | -0.004253 | -0.0106 | 0.015135 | 0.031714 | 0.008137 | 0.039107 | 0.01553
4174.8594 | 122.0306 | -0.091553 | 121.9849 | 0.14932 | -0.022205 | -0.030314 | -0.01586 | 0.027109 | 0.076426 | -0.067295 | -0.048239 | 0.074638 | -0.040846 | -0.042259 | -0.084531 | -0.045451 | -0.051798 | -0.048953 | 0.24087 | 0.069348 | 0.061239 | 0.075693 | 0.11866 | 0.16798 | 0.024258 | -0.002463 | 0.12041 | 0.00493 | 0.003517 | -0.038755 | 0.000325 | -0.006022 | -0.003177 | 0.036292 | 0.003559 | 0.043685 | 0.010952
4176.5625 | 122.0261 | -0.11902 | 121.9986 | 0.14017 | -0.026784 | -0.021157 | -0.029595 | 0.022531 | 0.076426 | -0.067295 | -0.043661 | 0.07006 | -0.036267 | -0.03768 | -0.084531 | -0.050029 | -0.060955 | -0.044375 | 0.25918 | 0.092235 | 0.097862 | 0.089424 | 0.14155 | 0.19544 | 0.051724 | 0.002115 | 0.11584 | 0.009509 | 0.008096 | -0.038755 | -0.004253 | -0.015179 | 0.001401 | 0.04087 | 0.017294 | 0.048264 | 0.024688
4178.3281 | 121.9894 | -0.10529 | 121.9666 | 0.14017 | -0.022205 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.071874 | -0.043661 | 0.07006 | -0.036267 | -0.033101 | -0.098266 | -0.050029 | -0.04722 | -0.039797 | 0.24545 | 0.083081 | 0.084129 | 0.080269 | 0.12782 | 0.17713 | 0.033412 | 0.002115 | 0.11584 | 0.009509 | 0.012675 | -0.05249 | -0.004253 | -0.001444 | 0.005979 | 0.054605 | 0.003559 | 0.061999 | 0.010953
4180.0938 | 122.1039 | -0.054932 | 121.9666 | 0.14017 | -0.031363 | -0.025735 | -0.029595 | 0.017953 | 0.071848 | -0.067295 | -0.043661 | 0.07006 | -0.040846 | -0.03768 | -0.08911 | -0.054607 | -0.04722 | -0.039797 | 0.1951 | 0.023569 | 0.029197 | 0.025337 | 0.072885 | 0.12678 | -0.012363 | 0.002115 | 0.11584 | 0.00493 | 0.008096 | -0.043334 | -0.008831 | -0.001444 | 0.005979 | 0.045449 | 0.003559 | 0.048264 | 0.006374
4181.8438 | 121.9986 | -0.086975 | 121.9849 | 0.14474 | -0.026784 | -0.021157 | -0.025017 | 0.027109 | 0.076426 | -0.058139 | -0.043661 | 0.074638 | -0.036267 | -0.042259 | -0.079953 | -0.050029 | -0.051798 | -0.039797 | 0.23172 | 0.060191 | 0.065818 | 0.061958 | 0.11408 | 0.1634 | 0.028836 | 0.002115 | 0.12041 | 0.009509 | 0.003517 | -0.034177 | -0.004253 | -0.006022 | 0.005979 | 0.036292 | 0.008137 | 0.043686 | 0.015531
4183.5625 | 122.1313 | -0.054932 | 121.9208 | 0.14474 | -0.026784 | -0.021157 | -0.029595 | 0.017953 | 0.076426 | -0.067295 | -0.048239 | 0.074638 | -0.036267 | -0.03768 | -0.08911 | -0.054607 | -0.051798 | -0.039797 | 0.19968 | 0.028148 | 0.033775 | 0.025337 | 0.072885 | 0.13136 | -0.012363 | -0.002463 | 0.12041 | 0.009509 | 0.008096 | -0.043334 | -0.008831 | -0.006022 | 0.005979 | 0.040871 | 0.003559 | 0.052843 | 0.015531
4185.3281 | 122.0078 | -0.11444 | 121.9574 | 0.14474 | -0.026784 | -0.021157 | -0.029595 | 0.022531 | 0.071848 | -0.058139 | -0.034504 | 0.065481 | -0.040846 | -0.03768 | -0.084531 | -0.050029 | -0.056376 | -0.039797 | 0.25918 | 0.087657 | 0.093284 | 0.084846 | 0.13697 | 0.18629 | 0.056302 | 0.011272 | 0.11126 | 0.00493 | 0.008096 | -0.038755 | -0.004253 | -0.0106 | 0.005979 | 0.050027 | 0.021872 | 0.043685 | 0.01553
4187.0938 | 122.113 | -0.07782 | 121.9437 | 0.14017 | -0.031363 | -0.016578 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | -0.043661 | 0.065481 | -0.040846 | -0.033101 | -0.08911 | -0.050029 | -0.056376 | -0.035219 | 0.21799 | 0.046457 | 0.061242 | 0.052803 | 0.10035 | 0.14509 | 0.015103 | 0.002115 | 0.11126 | 0.00493 | 0.012675 | -0.043334 | -0.004253 | -0.0106 | 0.010557 | 0.045449 | 0.012715 | 0.048264 | 0.01553
4188.8594 | 122.1085 | -0.059509 | 121.9299 | 0.14474 | -0.031363 | -0.021157 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.039082 | 0.07006 | -0.040846 | -0.03768 | -0.084531 | -0.054607 | -0.051798 | -0.039797 | 0.20425 | 0.028146 | 0.038352 | 0.029914 | 0.08204 | 0.13136 | -0.003208 | 0.006694 | 0.11584 | 0.00493 | 0.008096 | -0.038755 | -0.008831 | -0.006022 | 0.005979 | 0.045449 | 0.012716 | 0.043685 | 0.010952
4190.5781 | 121.9757 | -0.10986 | 121.962 | 0.14474 | -0.026784 | -0.025735 | -0.029595 | 0.022531 | 0.067269 | -0.067295 | -0.039082 | 0.07006 | -0.040846 | -0.03768 | -0.084531 | -0.050029 | -0.056376 | -0.035219 | 0.25461 | 0.083079 | 0.084128 | 0.080268 | 0.13239 | 0.17713 | 0.042568 | 0.006694 | 0.11584 | 0.00493 | 0.008096 | -0.038755 | -0.004253 | -0.0106 | 0.010557 | 0.045449 | 0.017294 | 0.043685 | 0.01553
4192.3594 | 122.0856 | -0.068665 | 121.9116 | 0.14474 | -0.031363 | -0.034893 | -0.025017 | 0.027109 | 0.076426 | -0.062717 | -0.043661 | 0.07006 | -0.040846 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.21341 | 0.037302 | 0.033772 | 0.043648 | 0.095774 | 0.14509 | 0.005948 | 0.002115 | 0.11584 | 0.00493 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.04087 | 0.008137 | 0.043685 | 0.010952
4194.1406 | 122.1176 | -0.045776 | 121.9254 | 0.14932 | -0.031363 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.058139 | -0.039082 | 0.065481 | -0.050002 | -0.042259 | -0.08911 | -0.045451 | -0.051798 | -0.039797 | 0.1951 | 0.014413 | 0.020041 | 0.016181 | 0.068307 | 0.11762 | -0.012363 | 0.006694 | 0.11126 | -0.004226 | 0.003517 | -0.043334 | 0.000325 | -0.006022 | 0.005979 | 0.050028 | 0.012716 | 0.039108 | 0.001796
4195.9062 | 122.0261 | -0.082397 | 121.9849 | 0.14474 | -0.026784 | -0.025735 | -0.025017 | 0.027109 | 0.071848 | -0.067295 | -0.039082 | 0.07006 | -0.036267 | -0.042259 | -0.084531 | -0.050029 | -0.042641 | -0.030641 | 0.22714 | 0.055613 | 0.056662 | 0.05738 | 0.10951 | 0.15424 | 0.015102 | 0.006694 | 0.11584 | 0.009509 | 0.003517 | -0.038755 | -0.004253 | 0.003135 | 0.015135 | 0.045449 | 0.003559 | 0.048264 | 0.006374
4197.625 | 121.9849 | -0.10071 | 121.9528 | 0.14474 | -0.026784 | -0.016578 | -0.025017 | 0.017953 | 0.071848 | -0.067295 | -0.039082 | 0.074638 | -0.036267 | -0.03768 | -0.084531 | -0.054607 | -0.04722 | -0.035219 | 0.24545 | 0.073924 | 0.08413 | 0.075691 | 0.11866 | 0.17256 | 0.033413 | 0.006694 | 0.12041 | 0.009509 | 0.008096 | -0.038755 | -0.008831 | -0.001444 | 0.010557 | 0.045449 | 0.008138 | 0.048264 | 0.010953
4199.4062 | 122.0856 | -0.059509 | 121.9208 | 0.14017 | -0.031363 | -0.021157 | -0.029595 | 0.022531 | 0.071848 | -0.076452 | -0.043661 | 0.07006 | -0.050002 | -0.042259 | -0.084531 | -0.050029 | -0.04722 | -0.048953 | 0.19967 | 0.028146 | 0.038352 | 0.029914 | 0.08204 | 0.13136 | -0.016943 | 0.002115 | 0.11584 | -0.004226 | 0.003517 | -0.038755 | -0.004253 | -0.001444 | -0.003177 | 0.04087 | 0.003559 | 0.034529 | -0.002782
4201.1094 | 122.0535 | -0.086975 | 121.9345 | 0.13559 | -0.031363 | -0.021157 | -0.020438 | 0.022531 | 0.067269 | -0.071874 | -0.039082 | 0.079217 | -0.045424 | -0.03768 | -0.079953 | -0.040873 | -0.04722 | -0.044375 | 0.22256 | 0.055612 | 0.065818 | 0.066537 | 0.10951 | 0.15424 | 0.015101 | 0.006694 | 0.12499 | 0.000352 | 0.008096 | -0.034177 | 0.004903 | -0.001444 | 0.001401 | 0.040871 | 0.008138 | 0.034529 | 0.001796
4202.875 | 122.0306 | -0.10986 | 121.9666 | 0.13559 | -0.035942 | -0.021157 | -0.029595 | 0.022531 | 0.071848 | -0.071874 | -0.048239 | 0.060902 | -0.036267 | -0.03768 | -0.079953 | -0.054607 | -0.051798 | -0.035219 | 0.24545 | 0.073921 | 0.088706 | 0.080268 | 0.13239 | 0.18171 | 0.037989 | -0.002463 | 0.10668 | 0.009509 | 0.008096 | -0.034177 | -0.008831 | -0.006022 | 0.010557 | 0.031714 | 0.003559 | 0.043686 | 0.015531
4204.6562 | 122.0718 | -0.086975 | 121.9574 | 0.14017 | -0.031363 | -0.021157 | -0.029595 | 0.027109 | 0.071848 | -0.062717 | -0.043661 | 0.07006 | -0.031689 | -0.03768 | -0.084531 | -0.045451 | -0.056376 | -0.044375 | 0.22714 | 0.055612 | 0.065818 | 0.05738 | 0.11408 | 0.15882 | 0.024258 | 0.002115 | 0.11584 | 0.014087 | 0.008096 | -0.038755 | 0.000325 | -0.0106 | 0.001401 | 0.04087 | 0.012715 | 0.052842 | 0.024687
4206.4219 | 122.0215 | -0.10529 | 121.9757 | 0.14017 | -0.026784 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.043661 | 0.07006 | -0.040846 | -0.03768 | -0.084531 | -0.050029 | -0.04722 | -0.035219 | 0.24545 | 0.078502 | 0.079551 | 0.080269 | 0.12782 | 0.17713 | 0.042569 | 0.002115 | 0.11584 | 0.00493 | 0.008096 | -0.038755 | -0.004253 | -0.001444 | 0.010557 | 0.04087 | 0.003559 | 0.043685 | 0.006374
4208.2031 | 122.0901 | -0.059509 | 121.9391 | 0.14474 | -0.026784 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.071874 | -0.039082 | 0.065481 | -0.031689 | -0.03768 | -0.08911 | -0.040873 | -0.04722 | -0.044375 | 0.20425 | 0.032725 | 0.033774 | 0.034492 | 0.08204 | 0.13136 | -0.012365 | 0.006694 | 0.11126 | 0.014087 | 0.008096 | -0.043334 | 0.004903 | -0.001444 | 0.001401 | 0.050028 | 0.008138 | 0.057421 | 0.015531
4209.9062 | 122.0444 | -0.068665 | 121.9345 | 0.14017 | -0.035942 | -0.025735 | -0.034174 | 0.017953 | 0.071848 | -0.071874 | -0.039082 | 0.065481 | -0.040846 | -0.03768 | -0.093688 | -0.040873 | -0.051798 | -0.044375 | 0.20883 | 0.032723 | 0.04293 | 0.034491 | 0.086618 | 0.14051 | -0.003209 | 0.006694 | 0.11126 | 0.00493 | 0.008096 | -0.047912 | 0.004903 | -0.006022 | 0.001401 | 0.054606 | 0.012716 | 0.052842 | 0.010952
4211.6719 | 121.9666 | -0.1236 | 121.9666 | 0.13559 | -0.031363 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.043661 | 0.07006 | -0.031689 | -0.03768 | -0.084531 | -0.050029 | -0.042641 | -0.044375 | 0.25918 | 0.092233 | 0.10244 | 0.098579 | 0.14613 | 0.19544 | 0.060879 | 0.002115 | 0.11584 | 0.014087 | 0.008096 | -0.038755 | -0.004253 | 0.003135 | 0.001401 | 0.04087 | -0.00102 | 0.052842 | 0.010952
4213.4531 | 122.0535 | -0.064087 | 121.9299 | 0.13101 | -0.035942 | -0.025735 | -0.020438 | 0.027109 | 0.067269 | -0.071874 | -0.043661 | 0.07006 | -0.040846 | -0.042259 | -0.08911 | -0.054607 | -0.060955 | -0.039797 | 0.1951 | 0.028145 | 0.038352 | 0.043649 | 0.091196 | 0.13136 | -0.007787 | 0.002115 | 0.11584 | 0.00493 | 0.003517 | -0.043334 | -0.008831 | -0.015179 | 0.005979 | 0.045449 | 0.017294 | 0.048264 | 0.020109
4215.1562 | 122.0673 | -0.07782 | 121.9391 | 0.14017 | -0.035942 | -0.012 | -0.025017 | 0.027109 | 0.076426 | -0.071874 | -0.043661 | 0.07006 | -0.036267 | -0.033101 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.21799 | 0.041878 | 0.06582 | 0.052803 | 0.10493 | 0.15425 | 0.005946 | 0.002115 | 0.11584 | 0.009509 | 0.012675 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.04087 | 0.008137 | 0.048264 | 0.015531
4216.9219 | 121.9894 | -0.09613 | 121.9574 | 0.14474 | -0.040521 | -0.021157 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | -0.039082 | 0.074638 | -0.040846 | -0.042259 | -0.084531 | -0.054607 | -0.051798 | -0.035219 | 0.24087 | 0.055609 | 0.074973 | 0.071113 | 0.11866 | 0.1634 | 0.033413 | 0.006694 | 0.12041 | 0.00493 | 0.003517 | -0.038755 | -0.008831 | -0.006022 | 0.010557 | 0.045449 | 0.012716 | 0.043685 | 0.010952
4218.7031 | 122.0947 | -0.059509 | 121.9254 | 0.14017 | -0.031363 | -0.016578 | -0.025017 | 0.022531 | 0.062691 | -0.067295 | -0.043661 | 0.07006 | -0.045424 | -0.03768 | -0.079953 | -0.045451 | -0.060955 | -0.044375 | 0.19967 | 0.028146 | 0.042931 | 0.034492 | 0.08204 | 0.1222 | -0.007786 | 0.002115 | 0.11584 | 0.000352 | 0.008096 | -0.034177 | 0.000325 | -0.015179 | 0.001401 | 0.036292 | 0.017294 | 0.034529 | 0.015531
4220.4688 | 122.0169 | -0.09613 | 121.9391 | 0.14017 | -0.026784 | -0.021157 | -0.020438 | 0.017953 | 0.071848 | -0.062717 | -0.048239 | 0.074638 | -0.036267 | -0.03768 | -0.084531 | -0.054607 | -0.056376 | -0.035219 | 0.2363 | 0.069346 | 0.074973 | 0.075692 | 0.11408 | 0.16798 | 0.033413 | -0.002463 | 0.12041 | 0.009509 | 0.008096 | -0.038755 | -0.008831 | -0.0106 | 0.010557 | 0.036292 | 0.008137 | 0.048264 | 0.020109
4222.1719 | 122.0123 | -0.07782 | 121.9437 | 0.13559 | -0.022205 | -0.025735 | -0.020438 | 0.022531 | 0.071848 | -0.071874 | -0.048239 | 0.065481 | -0.031689 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.21341 | 0.055615 | 0.052085 | 0.057382 | 0.10035 | 0.14967 | 0.005946 | -0.002463 | 0.11126 | 0.014087 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.036292 | 0.003559 | 0.052842 | 0.020109
4223.9375 | 121.9574 | -0.091553 | 121.9208 | 0.14017 | -0.040521 | -0.016578 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.034504 | 0.07006 | -0.045424 | -0.03768 | -0.08911 | -0.054607 | -0.056376 | -0.039797 | 0.23172 | 0.051032 | 0.074975 | 0.061958 | 0.11408 | 0.1634 | 0.024258 | 0.011272 | 0.11584 | 0.000352 | 0.008096 | -0.043334 | -0.008831 | -0.0106 | 0.005979 | 0.054606 | 0.021872 | 0.043686 | 0.010952
4225.7031 | 122.0444 | -0.091553 | 121.9254 | 0.14017 | -0.026784 | -0.016578 | -0.020438 | 0.022531 | 0.071848 | -0.071874 | -0.039082 | 0.07006 | -0.040846 | -0.042259 | -0.08911 | -0.054607 | -0.04722 | -0.035219 | 0.23172 | 0.064769 | 0.074975 | 0.071115 | 0.11408 | 0.1634 | 0.019679 | 0.006694 | 0.11584 | 0.00493 | 0.003517 | -0.043334 | -0.008831 | -0.001444 | 0.010557 | 0.050028 | 0.008138 | 0.048264 | 0.006374
4227.4844 | 122.0261 | -0.082397 | 121.9528 | 0.13559 | -0.022205 | -0.021157 | -0.025017 | 0.031687 | 0.071848 | -0.062717 | -0.039082 | 0.065481 | -0.031689 | -0.03768 | -0.08911 | -0.045451 | -0.042641 | -0.035219 | 0.21798 | 0.060192 | 0.06124 | 0.05738 | 0.11408 | 0.15424 | 0.01968 | 0.006694 | 0.11126 | 0.014087 | 0.008096 | -0.043334 | 0.000325 | 0.003135 | 0.010557 | 0.050028 | 0.003559 | 0.057421 | 0.010952
4229.2031 | 122.1039 | -0.068665 | 121.9208 | 0.14474 | -0.031363 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.071874 | -0.043661 | 0.07006 | -0.040846 | -0.03768 | -0.084531 | -0.045451 | -0.051798 | -0.035219 | 0.21341 | 0.037302 | 0.04293 | 0.03907 | 0.091196 | 0.14051 | -0.003209 | 0.002115 | 0.11584 | 0.00493 | 0.008096 | -0.038755 | 0.000325 | -0.006022 | 0.010557 | 0.04087 | 0.008137 | 0.043685 | 0.010952
4230.9844 | 122.0169 | -0.086975 | 121.962 | 0.14474 | -0.031363 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.039082 | 0.060902 | -0.031689 | -0.042259 | -0.08911 | -0.054607 | -0.056376 | -0.039797 | 0.23172 | 0.055612 | 0.06124 | 0.061958 | 0.10951 | 0.15882 | 0.01968 | 0.006694 | 0.10668 | 0.014087 | 0.003517 | -0.043334 | -0.008831 | -0.0106 | 0.005979 | 0.050028 | 0.017294 | 0.057421 | 0.024687
4232.75 | 122.0535 | -0.054932 | 121.9299 | 0.14017 | -0.040521 | -0.030314 | -0.020438 | 0.027109 | 0.062691 | -0.071874 | -0.043661 | 0.07006 | -0.040846 | -0.042259 | -0.084531 | -0.045451 | -0.04722 | -0.035219 | 0.1951 | 0.014411 | 0.024618 | 0.034494 | 0.082041 | 0.11762 | -0.016942 | 0.002115 | 0.11584 | 0.00493 | 0.003517 | -0.038755 | 0.000325 | -0.001444 | 0.010557 | 0.04087 | 0.003559 | 0.043685 | 0.006374
4234.5312 | 121.9666 | -0.10529 | 121.9482 | 0.14932 | -0.022205 | -0.016578 | -0.029595 | 0.027109 | 0.076426 | -0.067295 | -0.048239 | 0.060902 | -0.040846 | -0.03768 | -0.079953 | -0.045451 | -0.051798 | -0.044375 | 0.25461 | 0.083081 | 0.088708 | 0.075691 | 0.1324 | 0.18171 | 0.037991 | -0.002463 | 0.10668 | 0.00493 | 0.008096 | -0.034177 | 0.000325 | -0.006022 | 0.001401 | 0.031714 | 0.003559 | 0.039107 | 0.010952
4236.2969 | 122.0993 | -0.068665 | 121.907 | 0.14017 | -0.031363 | -0.016578 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | -0.043661 | 0.065481 | -0.036267 | -0.03768 | -0.079953 | -0.045451 | -0.04722 | -0.039797 | 0.20883 | 0.037302 | 0.052087 | 0.043648 | 0.091196 | 0.13593 | 0.005948 | 0.002115 | 0.11126 | 0.009509 | 0.008096 | -0.034177 | 0.000325 | -0.001444 | 0.005979 | 0.036292 | 0.003559 | 0.043686 | 0.010953
4238.0625 | 122.0078 | -0.086975 | 121.9528 | 0.14017 | -0.031363 | -0.025735 | -0.020438 | 0.022531 | 0.071848 | -0.071874 | -0.043661 | 0.065481 | -0.040846 | -0.03768 | -0.079953 | -0.050029 | -0.051798 | -0.039797 | 0.22714 | 0.055612 | 0.06124 | 0.066537 | 0.10951 | 0.15882 | 0.015101 | 0.002115 | 0.11126 | 0.00493 | 0.008096 | -0.034177 | -0.004253 | -0.006022 | 0.005979 | 0.036292 | 0.008137 | 0.039107 | 0.010952
4239.8281 | 122.0718 | -0.059509 | 121.9254 | 0.14017 | -0.035942 | -0.030314 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.039082 | 0.060902 | -0.045424 | -0.03768 | -0.084531 | -0.050029 | -0.056376 | -0.039797 | 0.19967 | 0.023567 | 0.029195 | 0.034492 | 0.08204 | 0.13136 | -0.007786 | 0.006694 | 0.10668 | 0.000352 | 0.008096 | -0.038755 | -0.004253 | -0.0106 | 0.005979 | 0.045449 | 0.017294 | 0.039107 | 0.010952
4241.5312 | 121.9711 | -0.11902 | 121.962 | 0.14017 | -0.035942 | -0.021157 | -0.025017 | 0.027109 | 0.076426 | -0.058139 | -0.043661 | 0.07006 | -0.036267 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.25918 | 0.083077 | 0.097862 | 0.094002 | 0.14613 | 0.19544 | 0.06088 | 0.002115 | 0.11584 | 0.009509 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.04087 | 0.008137 | 0.048264 | 0.015531
4243.2969 | 122.081 | -0.068665 | 121.9299 | 0.14017 | -0.026784 | -0.021157 | -0.025017 | 0.027109 | 0.071848 | -0.067295 | -0.039082 | 0.07006 | -0.036267 | -0.03768 | -0.084531 | -0.040873 | -0.051798 | -0.039797 | 0.20883 | 0.041881 | 0.047508 | 0.043648 | 0.095774 | 0.14051 | 0.00137 | 0.006694 | 0.11584 | 0.009509 | 0.008096 | -0.038755 | 0.004903 | -0.006022 | 0.005979 | 0.045449 | 0.012716 | 0.048264 | 0.015531
4245.0156 | 122.0123 | -0.082397 | 121.9528 | 0.14017 | -0.031363 | -0.025735 | -0.020438 | 0.022531 | 0.081005 | -0.067295 | -0.039082 | 0.07006 | -0.036267 | -0.03768 | -0.084531 | -0.050029 | -0.056376 | -0.030641 | 0.22256 | 0.051034 | 0.056662 | 0.061959 | 0.10493 | 0.1634 | 0.015102 | 0.006694 | 0.11584 | 0.009509 | 0.008096 | -0.038755 | -0.004253 | -0.0106 | 0.015135 | 0.045449 | 0.017294 | 0.048264 | 0.020109
4246.7812 | 122.1222 | -0.064087 | 121.907 | 0.14017 | -0.031363 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.071874 | -0.052818 | 0.065481 | -0.045424 | -0.028522 | -0.079953 | -0.050029 | -0.051798 | -0.035219 | 0.20425 | 0.032724 | 0.04293 | 0.03907 | 0.086618 | 0.13594 | -0.007787 | -0.007042 | 0.11126 | 0.000352 | 0.017254 | -0.034177 | -0.004253 | -0.006022 | 0.010557 | 0.027135 | -0.00102 | 0.034529 | 0.006374
4248.5 | 122.0306 | -0.068665 | 121.9116 | 0.14017 | -0.026784 | -0.025735 | -0.029595 | 0.022531 | 0.067269 | -0.071874 | -0.043661 | 0.079217 | -0.031689 | -0.028522 | -0.084531 | -0.050029 | -0.04722 | -0.048953 | 0.20883 | 0.041881 | 0.04293 | 0.03907 | 0.091196 | 0.13593 | -0.003209 | 0.002115 | 0.12499 | 0.014087 | 0.017254 | -0.038755 | -0.004253 | -0.001444 | -0.003177 | 0.04087 | 0.003559 | 0.052842 | 0.015531
4250.2656 | 121.9437 | -0.10986 | 121.9391 | 0.14017 | -0.040521 | -0.016578 | -0.025017 | 0.022531 | 0.067269 | -0.058139 | -0.048239 | 0.07006 | -0.040846 | -0.03768 | -0.079953 | -0.050029 | -0.04722 | -0.035219 | 0.25003 | 0.069342 | 0.093285 | 0.084846 | 0.13239 | 0.17713 | 0.051724 | -0.002463 | 0.11584 | 0.00493 | 0.008096 | -0.034177 | -0.004253 | -0.001444 | 0.010557 | 0.031714 | -0.001019 | 0.039107 | 0.006374
4252.0312 | 122.0718 | -0.059509 | 121.8704 | 0.14017 | -0.026784 | -0.021157 | -0.025017 | 0.022531 | 0.076426 | -0.062717 | -0.048239 | 0.07006 | -0.036267 | -0.033101 | -0.093688 | -0.045451 | -0.04722 | -0.039797 | 0.19967 | 0.032725 | 0.038352 | 0.034492 | 0.08204 | 0.13594 | -0.003208 | -0.002463 | 0.11584 | 0.009509 | 0.012675 | -0.047912 | 0.000325 | -0.001444 | 0.005979 | 0.045449 | -0.001019 | 0.057421 | 0.010953
4253.7969 | 121.994 | -0.09613 | 121.9437 | 0.14017 | -0.026784 | -0.030314 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | -0.043661 | 0.07006 | -0.045424 | -0.042259 | -0.079953 | -0.050029 | -0.04722 | -0.039797 | 0.2363 | 0.069346 | 0.065816 | 0.071113 | 0.11866 | 0.1634 | 0.033413 | 0.002115 | 0.11584 | 0.000352 | 0.003517 | -0.034177 | -0.004253 | -0.001444 | 0.005979 | 0.036292 | 0.003559 | 0.034529 | 0.001796
4255.5625 | 121.9437 | -0.11444 | 121.9299 | 0.14017 | -0.022205 | -0.012 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.039082 | 0.065481 | -0.036267 | -0.046838 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.25461 | 0.092236 | 0.10244 | 0.084846 | 0.13697 | 0.18629 | 0.051724 | 0.006694 | 0.11126 | 0.009509 | -0.001062 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.045449 | 0.012716 | 0.048264 | 0.015531
4257.3281 | 122.0261 | -0.07782 | 121.9345 | 0.13559 | -0.035942 | -0.025735 | -0.025017 | 0.022531 | 0.067269 | -0.067295 | -0.043661 | 0.065481 | -0.045424 | -0.042259 | -0.084531 | -0.040873 | -0.04722 | -0.044375 | 0.21341 | 0.041878 | 0.052085 | 0.052803 | 0.10035 | 0.14509 | 0.010525 | 0.002115 | 0.11126 | 0.000352 | 0.003517 | -0.038755 | 0.004903 | -0.001444 | 0.001401 | 0.04087 | 0.003559 | 0.039107 | 0.001796
4259.0312 | 121.9986 | -0.10529 | 121.9254 | 0.14017 | -0.026784 | -0.021157 | -0.025017 | 0.031687 | 0.071848 | -0.062717 | -0.043661 | 0.07006 | -0.040846 | -0.03768 | -0.079953 | -0.045451 | -0.056376 | -0.039797 | 0.24545 | 0.078502 | 0.084129 | 0.080269 | 0.13697 | 0.17713 | 0.042569 | 0.002115 | 0.11584 | 0.00493 | 0.008096 | -0.034177 | 0.000325 | -0.0106 | 0.005979 | 0.036292 | 0.012715 | 0.039107 | 0.01553
4260.7969 | 122.0306 | -0.073242 | 121.9162 | 0.13559 | -0.031363 | -0.021157 | -0.020438 | 0.022531 | 0.067269 | -0.062717 | -0.039082 | 0.065481 | -0.036267 | -0.033101 | -0.079953 | -0.050029 | -0.051798 | -0.030641 | 0.20883 | 0.041879 | 0.052085 | 0.052804 | 0.095773 | 0.14051 | 0.010525 | 0.006694 | 0.11126 | 0.009509 | 0.012675 | -0.034177 | -0.004253 | -0.006022 | 0.015135 | 0.040871 | 0.012716 | 0.043686 | 0.015531
4262.5781 | 121.9437 | -0.10529 | 121.9391 | 0.13559 | -0.035942 | -0.021157 | -0.034174 | 0.017953 | 0.076426 | -0.067295 | -0.048239 | 0.060902 | -0.050002 | -0.03768 | -0.079953 | -0.050029 | -0.060955 | -0.039797 | 0.24087 | 0.069344 | 0.084129 | 0.071112 | 0.12324 | 0.18171 | 0.037991 | -0.002463 | 0.10668 | -0.004226 | 0.008096 | -0.034177 | -0.004253 | -0.015179 | 0.005979 | 0.031714 | 0.012716 | 0.029951 | 0.010953
4264.3594 | 122.0947 | -0.068665 | 121.8933 | 0.13559 | -0.035942 | -0.025735 | -0.025017 | 0.022531 | 0.067269 | -0.067295 | -0.048239 | 0.065481 | -0.040846 | -0.042259 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.20425 | 0.032723 | 0.04293 | 0.043648 | 0.091196 | 0.13593 | 0.00137 | -0.002463 | 0.11126 | 0.00493 | 0.003517 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.036292 | 0.003559 | 0.043685 | 0.010952
4266.1406 | 121.9116 | -0.10071 | 121.9482 | 0.14017 | -0.031363 | -0.034893 | -0.020438 | 0.017953 | 0.067269 | -0.067295 | -0.048239 | 0.065481 | -0.036267 | -0.03768 | -0.084531 | -0.050029 | -0.056376 | -0.035219 | 0.24087 | 0.069345 | 0.065815 | 0.08027 | 0.11866 | 0.16798 | 0.033413 | -0.002463 | 0.11126 | 0.009509 | 0.008096 | -0.038755 | -0.004253 | -0.0106 | 0.010557 | 0.036292 | 0.008137 | 0.048264 | 0.020109
4267.9219 | 122.1039 | -0.045776 | 121.8887 | 0.13101 | -0.031363 | -0.021157 | -0.029595 | 0.022531 | 0.067269 | -0.071874 | -0.048239 | 0.074638 | -0.045424 | -0.03768 | -0.079953 | -0.054607 | -0.056376 | -0.030641 | 0.17678 | 0.014413 | 0.024619 | 0.016181 | 0.068307 | 0.11304 | -0.026098 | -0.002463 | 0.12041 | 0.000352 | 0.008096 | -0.034177 | -0.008831 | -0.0106 | 0.015135 | 0.031714 | 0.008137 | 0.034529 | 0.010952
4269.6406 | 122.049 | -0.07782 | 121.8979 | 0.14474 | -0.035942 | -0.030314 | -0.01586 | 0.022531 | 0.071848 | -0.071874 | -0.048239 | 0.079217 | -0.036267 | -0.028522 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.22256 | 0.041878 | 0.047506 | 0.06196 | 0.10035 | 0.14967 | 0.005946 | -0.002463 | 0.12499 | 0.009509 | 0.017254 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.036292 | 0.003559 | 0.048264 | 0.015531
4271.4062 | 121.9803 | -0.082397 | 121.9025 | 0.14474 | -0.040521 | -0.016578 | -0.020438 | 0.027109 | 0.071848 | -0.067295 | -0.043661 | 0.065481 | -0.027111 | -0.03768 | -0.084531 | -0.040873 | -0.051798 | -0.035219 | 0.22714 | 0.041876 | 0.065819 | 0.061959 | 0.10951 | 0.15424 | 0.015102 | 0.002115 | 0.11126 | 0.018665 | 0.008096 | -0.038755 | 0.004903 | -0.006022 | 0.010557 | 0.04087 | 0.008137 | 0.05742 | 0.024687
4273.125 | 121.9986 | -0.091553 | 121.9345 | 0.13559 | -0.035942 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.039082 | 0.065481 | -0.036267 | -0.033101 | -0.084531 | -0.050029 | -0.056376 | -0.039797 | 0.22714 | 0.055611 | 0.065818 | 0.066536 | 0.11408 | 0.1634 | 0.024258 | 0.006694 | 0.11126 | 0.009509 | 0.012675 | -0.038755 | -0.004253 | -0.0106 | 0.005979 | 0.045449 | 0.017294 | 0.048264 | 0.020109
4274.9062 | 121.9849 | -0.068665 | 121.907 | 0.14474 | -0.031363 | -0.021157 | -0.025017 | 0.027109 | 0.071848 | -0.062717 | -0.043661 | 0.074638 | -0.045424 | -0.03768 | -0.079953 | -0.045451 | -0.060955 | -0.039797 | 0.21341 | 0.037302 | 0.047508 | 0.043648 | 0.095774 | 0.14051 | 0.005948 | 0.002115 | 0.12041 | 0.000352 | 0.008096 | -0.034177 | 0.000325 | -0.015179 | 0.005979 | 0.036292 | 0.017294 | 0.034529 | 0.015531
4276.6719 | 122.0764 | -0.050354 | 121.9025 | 0.13559 | -0.035942 | -0.021157 | -0.029595 | 0.027109 | 0.062691 | -0.062717 | -0.048239 | 0.065481 | -0.045424 | -0.042259 | -0.08911 | -0.054607 | -0.060955 | -0.044375 | 0.18594 | 0.014412 | 0.029197 | 0.020759 | 0.077463 | 0.11305 | -0.012363 | -0.002463 | 0.11126 | 0.000352 | 0.003517 | -0.043334 | -0.008831 | -0.015179 | 0.001401 | 0.040871 | 0.012716 | 0.043686 | 0.015531
4278.4375 | 121.9528 | -0.11444 | 121.9391 | 0.14017 | -0.031363 | -0.021157 | -0.029595 | 0.027109 | 0.062691 | -0.067295 | -0.048239 | 0.07006 | -0.045424 | -0.042259 | -0.079953 | -0.050029 | -0.051798 | -0.044375 | 0.25461 | 0.083078 | 0.093284 | 0.084846 | 0.14155 | 0.17713 | 0.047146 | -0.002463 | 0.11584 | 0.000352 | 0.003517 | -0.034177 | -0.004253 | -0.006022 | 0.001401 | 0.031714 | 0.003559 | 0.034529 | 0.006374
4280.1562 | 121.9757 | -0.10529 | 121.9208 | 0.14474 | -0.026784 | -0.025735 | -0.020438 | 0.027109 | 0.071848 | -0.062717 | -0.043661 | 0.065481 | -0.040846 | -0.03768 | -0.079953 | -0.050029 | -0.056376 | -0.030641 | 0.25003 | 0.078502 | 0.079551 | 0.084848 | 0.1324 | 0.17713 | 0.042569 | 0.002115 | 0.11126 | 0.00493 | 0.008096 | -0.034177 | -0.004253 | -0.0106 | 0.015135 | 0.036292 | 0.012715 | 0.039107 | 0.01553
4281.9219 | 122.0627 | -0.059509 | 121.8796 | 0.13559 | -0.035942 | -0.025735 | -0.029595 | 0.027109 | 0.071848 | -0.071874 | -0.034504 | 0.079217 | -0.036267 | -0.042259 | -0.079953 | -0.050029 | -0.056376 | -0.039797 | 0.1951 | 0.023567 | 0.033774 | 0.029914 | 0.086618 | 0.13136 | -0.012365 | 0.011272 | 0.12499 | 0.009509 | 0.003517 | -0.034177 | -0.004253 | -0.0106 | 0.005979 | 0.045449 | 0.021872 | 0.043686 | 0.020109
4283.6719 | 122.0856 | -0.073242 | 121.9208 | 0.14474 | -0.035942 | -0.021157 | -0.029595 | 0.017953 | 0.071848 | -0.067295 | -0.052818 | 0.065481 | -0.036267 | -0.033101 | -0.075375 | -0.040873 | -0.056376 | -0.035219 | 0.21799 | 0.0373 | 0.052085 | 0.043647 | 0.091195 | 0.14509 | 0.005947 | -0.007042 | 0.11126 | 0.009509 | 0.012675 | -0.029599 | 0.004903 | -0.0106 | 0.010557 | 0.022557 | 0.003558 | 0.039108 | 0.020109
4285.375 | 121.994 | -0.09613 | 121.9208 | 0.13559 | -0.031363 | -0.016578 | -0.029595 | 0.027109 | 0.076426 | -0.067295 | -0.039082 | 0.07006 | -0.040846 | -0.042259 | -0.084531 | -0.054607 | -0.051798 | -0.039797 | 0.23172 | 0.064767 | 0.079552 | 0.066535 | 0.12324 | 0.17256 | 0.028835 | 0.006694 | 0.11584 | 0.00493 | 0.003517 | -0.038755 | -0.008831 | -0.006022 | 0.005979 | 0.045449 | 0.012716 | 0.043685 | 0.010952
4287.1406 | 122.0215 | -0.064087 | 121.8887 | 0.13559 | -0.031363 | -0.025735 | -0.025017 | 0.013375 | 0.067269 | -0.067295 | -0.043661 | 0.060902 | -0.040846 | -0.042259 | -0.075375 | -0.054607 | -0.056376 | -0.035219 | 0.19967 | 0.032724 | 0.038352 | 0.03907 | 0.077462 | 0.13136 | -0.003208 | 0.002115 | 0.10668 | 0.00493 | 0.003517 | -0.029599 | -0.008831 | -0.0106 | 0.010557 | 0.031714 | 0.012715 | 0.034529 | 0.01553
4288.9062 | 121.9894 | -0.082397 | 121.9162 | 0.14474 | -0.035942 | -0.021157 | -0.034174 | 0.022531 | 0.076426 | -0.071874 | -0.052818 | 0.060902 | -0.040846 | -0.03768 | -0.08911 | -0.054607 | -0.051798 | -0.035219 | 0.22714 | 0.046455 | 0.06124 | 0.048223 | 0.10493 | 0.15882 | 0.010523 | -0.007042 | 0.10668 | 0.00493 | 0.008096 | -0.043334 | -0.008831 | -0.006022 | 0.010557 | 0.036292 | -0.00102 | 0.048264 | 0.010952
4290.6094 | 121.9299 | -0.1236 | 121.962 | 0.14474 | -0.035942 | -0.030314 | -0.025017 | 0.031687 | 0.071848 | -0.071874 | -0.043661 | 0.074638 | -0.036267 | -0.042259 | -0.079953 | -0.050029 | -0.04722 | -0.039797 | 0.26834 | 0.087654 | 0.093282 | 0.098579 | 0.15528 | 0.19544 | 0.051722 | 0.002115 | 0.12041 | 0.009509 | 0.003517 | -0.034177 | -0.004253 | -0.001444 | 0.005979 | 0.036292 | 0.003559 | 0.043686 | 0.010953
4292.375 | 122.0398 | -0.059509 | 121.9116 | 0.13559 | -0.035942 | -0.021157 | -0.029595 | 0.027109 | 0.076426 | -0.071874 | -0.043661 | 0.074638 | -0.040846 | -0.03768 | -0.084531 | -0.045451 | -0.051798 | -0.039797 | 0.1951 | 0.023567 | 0.038352 | 0.029914 | 0.086618 | 0.13594 | -0.012365 | 0.002115 | 0.12041 | 0.00493 | 0.008096 | -0.038755 | 0.000325 | -0.006022 | 0.005979 | 0.04087 | 0.008137 | 0.043685 | 0.010952
4294.1406 | 122.0306 | -0.073242 | 121.8979 | 0.13559 | -0.031363 | -0.025735 | -0.025017 | 0.017953 | 0.076426 | -0.062717 | -0.039082 | 0.074638 | -0.036267 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.20883 | 0.041879 | 0.047507 | 0.048225 | 0.091195 | 0.14967 | 0.010525 | 0.006694 | 0.12041 | 0.009509 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.045449 | 0.012716 | 0.048264 | 0.015531
4295.9062 | 122.0673 | -0.059509 | 121.8613 | 0.14474 | -0.035942 | -0.030314 | -0.029595 | 0.027109 | 0.076426 | -0.062717 | -0.043661 | 0.074638 | -0.036267 | -0.046838 | -0.084531 | -0.050029 | -0.04722 | -0.044375 | 0.20425 | 0.023567 | 0.029195 | 0.029914 | 0.086618 | 0.13594 | -0.003208 | 0.002115 | 0.12041 | 0.009509 | -0.001062 | -0.038755 | -0.004253 | -0.001444 | 0.001401 | 0.04087 | 0.003559 | 0.048264 | 0.010953
4297.6719 | 121.9711 | -0.086975 | 121.9299 | 0.14932 | -0.026784 | -0.021157 | -0.029595 | 0.022531 | 0.076426 | -0.062717 | -0.043661 | 0.07006 | -0.045424 | -0.042259 | -0.084531 | -0.054607 | -0.051798 | -0.035219 | 0.2363 | 0.060191 | 0.065818 | 0.05738 | 0.10951 | 0.1634 | 0.024258 | 0.002115 | 0.11584 | 0.000352 | 0.003517 | -0.038755 | -0.008831 | -0.006022 | 0.010557 | 0.04087 | 0.008137 | 0.039107 | 0.006374
4299.3906 | 121.9849 | -0.091553 | 121.8796 | 0.13559 | -0.035942 | -0.025735 | -0.034174 | 0.017953 | 0.076426 | -0.062717 | -0.048239 | 0.07006 | -0.045424 | -0.03768 | -0.079953 | -0.045451 | -0.051798 | -0.039797 | 0.22714 | 0.055611 | 0.065818 | 0.057379 | 0.10951 | 0.16798 | 0.028836 | -0.002463 | 0.11584 | 0.000352 | 0.008096 | -0.034177 | 0.000325 | -0.006022 | 0.005979 | 0.031714 | 0.003559 | 0.034529 | 0.006374
4301.1562 | 122.0764 | -0.064087 | 121.8658 | 0.14474 | -0.026784 | -0.025735 | -0.025017 | 0.031687 | 0.071848 | -0.062717 | -0.043661 | 0.065481 | -0.040846 | -0.042259 | -0.084531 | -0.045451 | -0.04722 | -0.039797 | 0.20883 | 0.037303 | 0.038352 | 0.03907 | 0.095774 | 0.13594 | 0.00137 | 0.002115 | 0.11126 | 0.00493 | 0.003517 | -0.038755 | 0.000325 | -0.001444 | 0.005979 | 0.04087 | 0.003559 | 0.043685 | 0.006374
4302.9219 | 121.9391 | -0.10529 | 121.8979 | 0.14017 | -0.026784 | -0.025735 | -0.034174 | 0.022531 | 0.071848 | -0.062717 | -0.043661 | 0.074638 | -0.040846 | -0.042259 | -0.079953 | -0.045451 | -0.051798 | -0.035219 | 0.24545 | 0.078502 | 0.079551 | 0.071112 | 0.12782 | 0.17713 | 0.042569 | 0.002115 | 0.12041 | 0.00493 | 0.003517 | -0.034177 | 0.000325 | -0.006022 | 0.010557 | 0.036292 | 0.008137 | 0.039107 | 0.010952
4304.6875 | 121.9666 | -0.10071 | 121.9162 | 0.14474 | -0.031363 | -0.016578 | -0.034174 | 0.022531 | 0.081005 | -0.058139 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.079953 | -0.050029 | -0.056376 | -0.039797 | 0.24545 | 0.069345 | 0.08413 | 0.066534 | 0.12324 | 0.18171 | 0.042569 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.034177 | -0.004253 | -0.0106 | 0.005979 | 0.031714 | 0.008137 | 0.039107 | 0.01553
4306.3906 | 122.0261 | -0.082397 | 121.875 | 0.14017 | -0.035942 | -0.025735 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.084531 | -0.054607 | -0.04722 | -0.035219 | 0.22256 | 0.046455 | 0.056662 | 0.05738 | 0.10493 | 0.14967 | 0.01968 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.038755 | -0.008831 | -0.001444 | 0.010557 | 0.036292 | -0.001019 | 0.043685 | 0.006374
4308.1562 | 121.9437 | -0.10529 | 121.907 | 0.14017 | -0.031363 | -0.025735 | -0.029595 | 0.031687 | 0.067269 | -0.067295 | -0.048239 | 0.07006 | -0.040846 | -0.03768 | -0.079953 | -0.050029 | -0.051798 | -0.044375 | 0.24545 | 0.073923 | 0.079551 | 0.075691 | 0.13697 | 0.17256 | 0.037991 | -0.002463 | 0.11584 | 0.00493 | 0.008096 | -0.034177 | -0.004253 | -0.006022 | 0.001401 | 0.031714 | 0.003559 | 0.039107 | 0.010952
4309.9219 | 122.0169 | -0.073242 | 121.8842 | 0.14474 | -0.026784 | -0.021157 | -0.025017 | 0.031687 | 0.067269 | -0.062717 | -0.039082 | 0.065481 | -0.036267 | -0.03768 | -0.084531 | -0.050029 | -0.04722 | -0.039797 | 0.21799 | 0.046458 | 0.052085 | 0.048225 | 0.10493 | 0.14051 | 0.010525 | 0.006694 | 0.11126 | 0.009509 | 0.008096 | -0.038755 | -0.004253 | -0.001444 | 0.005979 | 0.045449 | 0.008138 | 0.048264 | 0.010953
4311.625 | 122.0581 | -0.054932 | 121.8796 | 0.14017 | -0.031363 | -0.025735 | -0.029595 | 0.022531 | 0.076426 | -0.062717 | -0.048239 | 0.079217 | -0.045424 | -0.033101 | -0.08911 | -0.054607 | -0.04722 | -0.035219 | 0.1951 | 0.023569 | 0.029197 | 0.025337 | 0.077463 | 0.13136 | -0.007785 | -0.002463 | 0.12499 | 0.000352 | 0.012675 | -0.043334 | -0.008831 | -0.001444 | 0.010557 | 0.040871 | -0.001019 | 0.043686 | 0.001796
4313.3906 | 121.9666 | -0.10529 | 121.9116 | 0.14017 | -0.031363 | -0.025735 | -0.025017 | 0.022531 | 0.081005 | -0.067295 | -0.043661 | 0.074638 | -0.036267 | -0.042259 | -0.084531 | -0.045451 | -0.051798 | -0.039797 | 0.24545 | 0.073923 | 0.079551 | 0.080269 | 0.12782 | 0.18629 | 0.037991 | 0.002115 | 0.12041 | 0.009509 | 0.003517 | -0.038755 | 0.000325 | -0.006022 | 0.005979 | 0.04087 | 0.008137 | 0.048264 | 0.015531
4315.1094 | 122.0398 | -0.073242 | 121.875 | 0.13559 | -0.031363 | -0.021157 | -0.025017 | 0.027109 | 0.071848 | -0.067295 | -0.043661 | 0.079217 | -0.040846 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.20883 | 0.041879 | 0.052085 | 0.048225 | 0.10035 | 0.14509 | 0.005947 | 0.002115 | 0.12499 | 0.00493 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.04087 | 0.008137 | 0.043685 | 0.010952
4316.875 | 122.0215 | -0.07782 | 121.8796 | 0.14017 | -0.031363 | -0.021157 | -0.029595 | 0.027109 | 0.071848 | -0.067295 | -0.039082 | 0.065481 | -0.040846 | -0.042259 | -0.079953 | -0.050029 | -0.051798 | -0.039797 | 0.21799 | 0.046457 | 0.056663 | 0.048225 | 0.10493 | 0.14967 | 0.010525 | 0.006694 | 0.11126 | 0.00493 | 0.003517 | -0.034177 | -0.004253 | -0.006022 | 0.005979 | 0.040871 | 0.012716 | 0.039107 | 0.010952
4318.5781 | 121.9116 | -0.11444 | 121.9162 | 0.13559 | -0.031363 | -0.021157 | -0.029595 | 0.027109 | 0.071848 | -0.062717 | -0.048239 | 0.056323 | -0.040846 | -0.033101 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.25003 | 0.083078 | 0.093284 | 0.084846 | 0.14155 | 0.18629 | 0.051724 | -0.002463 | 0.1021 | 0.00493 | 0.012675 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.036292 | 0.003559 | 0.043685 | 0.010952
4320.2969 | 122.0078 | -0.082397 | 121.8933 | 0.13559 | -0.035942 | -0.025735 | -0.029595 | 0.022531 | 0.076426 | -0.062717 | -0.043661 | 0.056323 | -0.040846 | -0.033101 | -0.079953 | -0.050029 | -0.042641 | -0.039797 | 0.21798 | 0.046455 | 0.056662 | 0.052802 | 0.10493 | 0.15882 | 0.01968 | 0.002115 | 0.1021 | 0.00493 | 0.012675 | -0.034177 | -0.004253 | 0.003135 | 0.005979 | 0.036292 | -0.00102 | 0.039107 | 0.001795
4322.0625 | 121.9345 | -0.10986 | 121.9437 | 0.14474 | -0.035942 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.048239 | 0.074638 | -0.040846 | -0.033101 | -0.079953 | -0.054607 | -0.042641 | -0.044375 | 0.25461 | 0.073921 | 0.088706 | 0.084846 | 0.13239 | 0.18171 | 0.042568 | -0.002463 | 0.12041 | 0.00493 | 0.012675 | -0.034177 | -0.008831 | 0.003135 | 0.001401 | 0.031714 | -0.005598 | 0.039107 | 0.001795
4323.8438 | 122.0581 | -0.073242 | 121.8658 | 0.14932 | -0.040521 | -0.025735 | -0.020438 | 0.022531 | 0.076426 | -0.071874 | -0.043661 | 0.07006 | -0.036267 | -0.03768 | -0.075375 | -0.040873 | -0.051798 | -0.035219 | 0.22256 | 0.032721 | 0.047507 | 0.052804 | 0.095773 | 0.14967 | 0.001368 | 0.002115 | 0.11584 | 0.009509 | 0.008096 | -0.029599 | 0.004903 | -0.006022 | 0.010557 | 0.031714 | 0.008137 | 0.039108 | 0.015531
4325.5625 | 121.9528 | -0.10529 | 121.8933 | 0.13559 | -0.035942 | -0.016578 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | -0.043661 | 0.07006 | -0.040846 | -0.03768 | -0.079953 | -0.050029 | -0.04722 | -0.039797 | 0.24087 | 0.069344 | 0.088708 | 0.080269 | 0.12782 | 0.17256 | 0.042569 | 0.002115 | 0.11584 | 0.00493 | 0.008096 | -0.034177 | -0.004253 | -0.001444 | 0.005979 | 0.036292 | 0.003559 | 0.039107 | 0.006374
4327.3281 | 122.0169 | -0.050354 | 121.8704 | 0.14474 | -0.031363 | -0.025735 | -0.029595 | 0.017953 | 0.067269 | -0.067295 | -0.039082 | 0.07006 | -0.040846 | -0.03768 | -0.084531 | -0.045451 | -0.051798 | -0.035219 | 0.1951 | 0.018991 | 0.024619 | 0.020759 | 0.068307 | 0.11762 | -0.016941 | 0.006694 | 0.11584 | 0.00493 | 0.008096 | -0.038755 | 0.000325 | -0.006022 | 0.010557 | 0.045449 | 0.012716 | 0.043685 | 0.010952
4329.0938 | 121.8887 | -0.11444 | 121.8704 | 0.14017 | -0.031363 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.057396 | 0.065481 | -0.036267 | -0.042259 | -0.084531 | -0.059185 | -0.051798 | -0.035219 | 0.25461 | 0.083078 | 0.093284 | 0.089424 | 0.13697 | 0.18629 | 0.047146 | -0.01162 | 0.11126 | 0.009509 | 0.003517 | -0.038755 | -0.013409 | -0.006022 | 0.010557 | 0.027135 | -0.005598 | 0.048264 | 0.015531
4330.7969 | 121.9482 | -0.082397 | 121.8704 | 0.13559 | -0.035942 | -0.021157 | -0.025017 | 0.022531 | 0.081005 | -0.067295 | -0.052818 | 0.060902 | -0.045424 | -0.03768 | -0.079953 | -0.050029 | -0.056376 | -0.035219 | 0.21798 | 0.046455 | 0.06124 | 0.05738 | 0.10493 | 0.1634 | 0.015102 | -0.007042 | 0.10668 | 0.000352 | 0.008096 | -0.034177 | -0.004253 | -0.0106 | 0.010557 | 0.027135 | 0.003558 | 0.034529 | 0.010952
4332.5156 | 121.9849 | -0.073242 | 121.8338 | 0.14474 | -0.040521 | -0.030314 | -0.034174 | 0.022531 | 0.067269 | -0.076452 | -0.048239 | 0.065481 | -0.045424 | -0.033101 | -0.079953 | -0.050029 | -0.056376 | -0.044375 | 0.21799 | 0.032721 | 0.042928 | 0.039068 | 0.095773 | 0.14051 | -0.00321 | -0.002463 | 0.11126 | 0.000352 | 0.012675 | -0.034177 | -0.004253 | -0.0106 | 0.001401 | 0.031714 | 0.008137 | 0.034529 | 0.010952
4334.2812 | 121.9437 | -0.09613 | 121.8796 | 0.14017 | -0.035942 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.043661 | 0.07006 | -0.040846 | -0.042259 | -0.084531 | -0.045451 | -0.056376 | -0.030641 | 0.2363 | 0.060188 | 0.065816 | 0.066535 | 0.11866 | 0.16798 | 0.028835 | 0.002115 | 0.11584 | 0.00493 | 0.003517 | -0.038755 | 0.000325 | -0.0106 | 0.015135 | 0.04087 | 0.012715 | 0.043685 | 0.01553
4336.0625 | 121.9528 | -0.09613 | 121.8887 | 0.13559 | -0.035942 | -0.016578 | -0.029595 | 0.027109 | 0.081005 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.084531 | -0.050029 | -0.04722 | -0.035219 | 0.23172 | 0.060188 | 0.079552 | 0.066535 | 0.12324 | 0.17713 | 0.033413 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.038755 | -0.004253 | -0.001444 | 0.010557 | 0.036292 | -0.001019 | 0.043685 | 0.006374
4337.7812 | 121.9162 | -0.11902 | 121.8933 | 0.13559 | -0.040521 | -0.016578 | -0.025017 | 0.022531 | 0.076426 | -0.062717 | -0.043661 | 0.065481 | -0.045424 | -0.042259 | -0.079953 | -0.050029 | -0.051798 | -0.035219 | 0.25461 | 0.078498 | 0.10244 | 0.094002 | 0.14155 | 0.19544 | 0.056302 | 0.002115 | 0.11126 | 0.000352 | 0.003517 | -0.034177 | -0.004253 | -0.006022 | 0.010557 | 0.036292 | 0.008137 | 0.034529 | 0.006374
4339.5625 | 121.9894 | -0.059509 | 121.8842 | 0.13559 | -0.026784 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.043661 | 0.065481 | -0.040846 | -0.03768 | -0.079953 | -0.045451 | -0.051798 | -0.044375 | 0.1951 | 0.032725 | 0.038352 | 0.034492 | 0.08204 | 0.13136 | -0.007786 | 0.002115 | 0.11126 | 0.00493 | 0.008096 | -0.034177 | 0.000325 | -0.006022 | 0.001401 | 0.036292 | 0.008137 | 0.039107 | 0.010952
4341.3438 | 122.049 | -0.050354 | 121.8384 | 0.13101 | -0.031363 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.048239 | 0.07006 | -0.040846 | -0.03768 | -0.084531 | -0.050029 | -0.056376 | -0.039797 | 0.18136 | 0.018991 | 0.02004 | 0.020759 | 0.072885 | 0.1222 | -0.016941 | -0.002463 | 0.11584 | 0.00493 | 0.008096 | -0.038755 | -0.004253 | -0.0106 | 0.005979 | 0.036292 | 0.008137 | 0.043685 | 0.01553
4343.0469 | 122.0306 | -0.050354 | 121.843 | 0.13559 | -0.035942 | -0.021157 | -0.034174 | 0.022531 | 0.081005 | -0.067295 | -0.052818 | 0.060902 | -0.040846 | -0.03768 | -0.084531 | -0.050029 | -0.056376 | -0.035219 | 0.18594 | 0.014412 | 0.029197 | 0.01618 | 0.072885 | 0.13136 | -0.016941 | -0.007042 | 0.10668 | 0.00493 | 0.008096 | -0.038755 | -0.004253 | -0.0106 | 0.010557 | 0.031713 | 0.003558 | 0.043685 | 0.01553
4344.8125 | 121.9162 | -0.091553 | 121.8658 | 0.13559 | -0.031363 | -0.021157 | -0.025017 | 0.017953 | 0.067269 | -0.067295 | -0.052818 | 0.07006 | -0.050002 | -0.042259 | -0.084531 | -0.045451 | -0.051798 | -0.030641 | 0.22714 | 0.06019 | 0.070396 | 0.066536 | 0.10951 | 0.15882 | 0.024258 | -0.007042 | 0.11584 | -0.004226 | 0.003517 | -0.038755 | 0.000325 | -0.006022 | 0.015135 | 0.031713 | -0.00102 | 0.034529 | 0.001796
4346.5312 | 122.0306 | -0.059509 | 121.8246 | 0.13559 | -0.040521 | -0.021157 | -0.029595 | 0.013375 | 0.067269 | -0.067295 | -0.052818 | 0.074638 | -0.040846 | -0.042259 | -0.08911 | -0.050029 | -0.056376 | -0.035219 | 0.1951 | 0.018988 | 0.038352 | 0.029914 | 0.072884 | 0.12678 | -0.007786 | -0.007042 | 0.12041 | 0.00493 | 0.003517 | -0.043334 | -0.004253 | -0.0106 | 0.010557 | 0.036292 | 0.003558 | 0.048264 | 0.01553
4348.2969 | 121.9116 | -0.10986 | 121.8521 | 0.14474 | -0.035942 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.052818 | 0.07006 | -0.040846 | -0.03768 | -0.084531 | -0.050029 | -0.04722 | -0.039797 | 0.25461 | 0.073921 | 0.088706 | 0.084846 | 0.13239 | 0.18171 | 0.047146 | -0.007042 | 0.11584 | 0.00493 | 0.008096 | -0.038755 | -0.004253 | -0.001444 | 0.005979 | 0.031713 | -0.005598 | 0.043685 | 0.006374
4350 | 121.9345 | -0.091553 | 121.8842 | 0.14017 | -0.040521 | -0.025735 | -0.025017 | 0.017953 | 0.067269 | -0.067295 | -0.039082 | 0.074638 | -0.040846 | -0.042259 | -0.08911 | -0.054607 | -0.04722 | -0.035219 | 0.23172 | 0.051032 | 0.065818 | 0.066536 | 0.10951 | 0.15882 | 0.024258 | 0.006694 | 0.12041 | 0.00493 | 0.003517 | -0.043334 | -0.008831 | -0.001444 | 0.010557 | 0.050028 | 0.008138 | 0.048264 | 0.006374
4351.7656 | 122.0169 | -0.041199 | 121.8613 | 0.13559 | -0.035942 | -0.025735 | -0.029595 | 0.031687 | 0.071848 | -0.067295 | -0.043661 | 0.074638 | -0.036267 | -0.03768 | -0.084531 | -0.059185 | -0.060955 | -0.039797 | 0.17679 | 0.005257 | 0.015464 | 0.011604 | 0.072886 | 0.11305 | -0.026096 | 0.002115 | 0.12041 | 0.009509 | 0.008096 | -0.038755 | -0.013409 | -0.015179 | 0.005979 | 0.04087 | 0.017294 | 0.048264 | 0.024688
4353.5312 | 121.9299 | -0.086975 | 121.875 | 0.14474 | -0.031363 | -0.021157 | -0.020438 | 0.022531 | 0.067269 | -0.067295 | -0.043661 | 0.074638 | -0.045424 | -0.033101 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.23172 | 0.055612 | 0.065818 | 0.066537 | 0.10951 | 0.15424 | 0.01968 | 0.002115 | 0.12041 | 0.000352 | 0.012675 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.04087 | 0.008137 | 0.039107 | 0.006374
4355.2969 | 121.994 | -0.045776 | 121.8338 | 0.14017 | -0.031363 | -0.025735 | -0.025017 | 0.027109 | 0.071848 | -0.067295 | -0.048239 | 0.07006 | -0.050002 | -0.03768 | -0.084531 | -0.040873 | -0.04722 | -0.035219 | 0.18594 | 0.014413 | 0.020041 | 0.020759 | 0.072885 | 0.11762 | -0.021519 | -0.002463 | 0.11584 | -0.004226 | 0.008096 | -0.038755 | 0.004903 | -0.001444 | 0.010557 | 0.036292 | -0.001019 | 0.034529 | -0.002782
4357.0156 | 122.0032 | -0.059509 | 121.8292 | 0.14474 | -0.040521 | -0.021157 | -0.025017 | 0.022531 | 0.067269 | -0.067295 | -0.039082 | 0.065481 | -0.045424 | -0.03768 | -0.084531 | -0.050029 | -0.04722 | -0.035219 | 0.20425 | 0.018988 | 0.038352 | 0.034492 | 0.08204 | 0.12678 | -0.007786 | 0.006694 | 0.11126 | 0.000352 | 0.008096 | -0.038755 | -0.004253 | -0.001444 | 0.010557 | 0.045449 | 0.008138 | 0.039107 | 0.001796
4358.7969 | 121.962 | -0.07782 | 121.8155 | 0.13559 | -0.035942 | -0.016578 | -0.034174 | 0.027109 | 0.067269 | -0.067295 | -0.048239 | 0.074638 | -0.045424 | -0.03768 | -0.08911 | -0.050029 | -0.051798 | -0.030641 | 0.21341 | 0.041878 | 0.061242 | 0.043646 | 0.10493 | 0.14509 | 0.010525 | -0.002463 | 0.12041 | 0.000352 | 0.008096 | -0.043334 | -0.004253 | -0.006022 | 0.015135 | 0.040871 | 0.003559 | 0.043686 | 0.006374
4360.5156 | 121.994 | -0.050354 | 121.7972 | 0.14474 | -0.031363 | -0.021157 | -0.020438 | 0.017953 | 0.067269 | -0.067295 | -0.043661 | 0.074638 | -0.045424 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.1951 | 0.018991 | 0.029197 | 0.029916 | 0.068307 | 0.11762 | -0.016941 | 0.002115 | 0.12041 | 0.000352 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.04087 | 0.008137 | 0.039107 | 0.006374
4362.2969 | 121.9986 | -0.054932 | 121.8201 | 0.14474 | -0.040521 | -0.025735 | -0.034174 | 0.022531 | 0.076426 | -0.058139 | -0.052818 | 0.07006 | -0.040846 | -0.03768 | -0.079953 | -0.050029 | -0.051798 | -0.035219 | 0.19968 | 0.014411 | 0.029197 | 0.020758 | 0.077463 | 0.13136 | -0.003207 | -0.007042 | 0.11584 | 0.00493 | 0.008096 | -0.034177 | -0.004253 | -0.006022 | 0.010557 | 0.027135 | -0.00102 | 0.039107 | 0.010952
4364.0625 | 121.9025 | -0.10986 | 121.8887 | 0.14017 | -0.035942 | -0.025735 | -0.025017 | 0.022531 | 0.076426 | -0.067295 | -0.048239 | 0.074638 | -0.045424 | -0.042259 | -0.075375 | -0.050029 | -0.056376 | -0.035219 | 0.25003 | 0.073921 | 0.084128 | 0.084846 | 0.13239 | 0.18629 | 0.042568 | -0.002463 | 0.12041 | 0.000352 | 0.003517 | -0.029599 | -0.004253 | -0.0106 | 0.010557 | 0.027136 | 0.008137 | 0.029951 | 0.010952
4365.7656 | 122.0261 | -0.073242 | 121.8658 | 0.14474 | -0.031363 | -0.021157 | -0.025017 | 0.017953 | 0.071848 | -0.067295 | -0.048239 | 0.065481 | -0.036267 | -0.042259 | -0.084531 | -0.045451 | -0.051798 | -0.035219 | 0.21799 | 0.041879 | 0.052085 | 0.048225 | 0.091195 | 0.14509 | 0.005947 | -0.002463 | 0.11126 | 0.009509 | 0.003517 | -0.038755 | 0.000325 | -0.006022 | 0.010557 | 0.036292 | 0.003559 | 0.048264 | 0.015531
4367.5469 | 122.0627 | -0.041199 | 121.8842 | 0.13559 | -0.0451 | -0.021157 | -0.020438 | 0.022531 | 0.067269 | -0.067295 | -0.043661 | 0.065481 | -0.040846 | -0.033101 | -0.079953 | -0.045451 | -0.04722 | -0.039797 | 0.17679 | -0.003901 | 0.020042 | 0.020761 | 0.06373 | 0.10847 | -0.026096 | 0.002115 | 0.11126 | 0.00493 | 0.012675 | -0.034177 | 0.000325 | -0.001444 | 0.005979 | 0.036292 | 0.003559 | 0.039107 | 0.006374
4369.25 | 121.9757 | -0.086975 | 121.9345 | 0.14474 | -0.035942 | -0.025735 | -0.029595 | 0.022531 | 0.067269 | -0.071874 | -0.034504 | 0.065481 | -0.040846 | -0.042259 | -0.079953 | -0.045451 | -0.051798 | -0.035219 | 0.23172 | 0.051033 | 0.06124 | 0.05738 | 0.10951 | 0.15424 | 0.015101 | 0.011272 | 0.11126 | 0.00493 | 0.003517 | -0.034177 | 0.000325 | -0.006022 | 0.010557 | 0.045449 | 0.017294 | 0.039107 | 0.010952
4371.0156 | 121.9803 | -0.11444 | 121.9162 | 0.14017 | -0.031363 | -0.021157 | -0.029595 | 0.022531 | 0.071848 | -0.058139 | -0.048239 | 0.07006 | -0.040846 | -0.042259 | -0.079953 | -0.059185 | -0.056376 | -0.035219 | 0.25461 | 0.083078 | 0.093284 | 0.084846 | 0.13697 | 0.18629 | 0.056302 | -0.002463 | 0.11584 | 0.00493 | 0.003517 | -0.034177 | -0.013409 | -0.0106 | 0.010557 | 0.031714 | 0.008137 | 0.039107 | 0.01553
4372.7188 | 121.994 | -0.073242 | 121.9299 | 0.13101 | -0.026784 | -0.016578 | -0.025017 | 0.027109 | 0.076426 | -0.067295 | -0.048239 | 0.065481 | -0.040846 | -0.033101 | -0.08911 | -0.054607 | -0.051798 | -0.035219 | 0.20425 | 0.046458 | 0.056664 | 0.048225 | 0.10035 | 0.14967 | 0.005947 | -0.002463 | 0.11126 | 0.00493 | 0.012675 | -0.043334 | -0.008831 | -0.006022 | 0.010557 | 0.040871 | 0.003559 | 0.048264 | 0.010952
4374.4844 | 122.049 | -0.059509 | 121.9025 | 0.14017 | -0.035942 | -0.030314 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.039082 | 0.074638 | -0.036267 | -0.03768 | -0.084531 | -0.054607 | -0.051798 | -0.039797 | 0.19967 | 0.023567 | 0.029195 | 0.034492 | 0.08204 | 0.13136 | -0.007786 | 0.006694 | 0.12041 | 0.009509 | 0.008096 | -0.038755 | -0.008831 | -0.006022 | 0.005979 | 0.045449 | 0.012716 | 0.048264 | 0.015531
4376.2031 | 122.0306 | -0.073242 | 121.9162 | 0.14474 | -0.026784 | -0.021157 | -0.025017 | 0.027109 | 0.076426 | -0.071874 | -0.048239 | 0.074638 | -0.036267 | -0.042259 | -0.084531 | -0.054607 | -0.056376 | -0.039797 | 0.21799 | 0.046458 | 0.052085 | 0.048225 | 0.10035 | 0.14967 | 0.001368 | -0.002463 | 0.12041 | 0.009509 | 0.003517 | -0.038755 | -0.008831 | -0.0106 | 0.005979 | 0.036292 | 0.008137 | 0.048264 | 0.020109
4377.9688 | 121.962 | -0.13275 | 121.9482 | 0.14474 | -0.026784 | -0.025735 | -0.020438 | 0.022531 | 0.076426 | -0.062717 | -0.043661 | 0.074638 | -0.040846 | -0.033101 | -0.084531 | -0.045451 | -0.065533 | -0.035219 | 0.27749 | 0.10597 | 0.10702 | 0.11231 | 0.15528 | 0.20918 | 0.070034 | 0.002115 | 0.12041 | 0.00493 | 0.012675 | -0.038755 | 0.000325 | -0.019757 | 0.010557 | 0.04087 | 0.021872 | 0.043685 | 0.024687
4379.75 | 121.9711 | -0.10986 | 121.9803 | 0.14932 | -0.026784 | -0.021157 | -0.020438 | 0.027109 | 0.076426 | -0.062717 | -0.043661 | 0.060902 | -0.040846 | -0.03768 | -0.079953 | -0.059185 | -0.051798 | -0.044375 | 0.25918 | 0.083079 | 0.088706 | 0.089425 | 0.13697 | 0.18629 | 0.047146 | 0.002115 | 0.10668 | 0.00493 | 0.008096 | -0.034177 | -0.013409 | -0.006022 | 0.001401 | 0.036292 | 0.008137 | 0.039107 | 0.010952
4381.4531 | 122.0032 | -0.10071 | 121.9666 | 0.14474 | -0.022205 | -0.021157 | -0.029595 | 0.022531 | 0.067269 | -0.062717 | -0.043661 | 0.065481 | -0.045424 | -0.046838 | -0.079953 | -0.050029 | -0.04722 | -0.035219 | 0.24545 | 0.078503 | 0.079551 | 0.071113 | 0.12324 | 0.16798 | 0.037991 | 0.002115 | 0.11126 | 0.000352 | -0.001062 | -0.034177 | -0.004253 | -0.001444 | 0.010557 | 0.036292 | 0.003559 | 0.034529 | 0.001796
4383.2188 | 122.0718 | -0.059509 | 121.9254 | 0.13559 | -0.026784 | -0.016578 | -0.029595 | 0.027109 | 0.067269 | -0.067295 | -0.048239 | 0.060902 | -0.036267 | -0.033101 | -0.075375 | -0.050029 | -0.056376 | -0.035219 | 0.1951 | 0.032725 | 0.042931 | 0.029914 | 0.086618 | 0.12678 | -0.007786 | -0.002463 | 0.10668 | 0.009509 | 0.012675 | -0.029599 | -0.004253 | -0.0106 | 0.010557 | 0.027136 | 0.008137 | 0.039108 | 0.020109
4384.9844 | 122.0306 | -0.091553 | 121.9666 | 0.14474 | -0.026784 | -0.016578 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.048239 | 0.074638 | -0.045424 | -0.03768 | -0.084531 | -0.054607 | -0.04722 | -0.044375 | 0.2363 | 0.064769 | 0.074975 | 0.061958 | 0.11408 | 0.1634 | 0.028836 | -0.002463 | 0.12041 | 0.000352 | 0.008096 | -0.038755 | -0.008831 | -0.001444 | 0.001401 | 0.036292 | -0.001019 | 0.039107 | 0.001796
4386.7656 | 122.0627 | -0.073242 | 121.9666 | 0.14474 | -0.035942 | -0.021157 | -0.020438 | 0.022531 | 0.076426 | -0.071874 | -0.043661 | 0.074638 | -0.045424 | -0.042259 | -0.084531 | -0.054607 | -0.051798 | -0.035219 | 0.21799 | 0.0373 | 0.052085 | 0.052804 | 0.095773 | 0.14967 | 0.001368 | 0.002115 | 0.12041 | 0.000352 | 0.003517 | -0.038755 | -0.008831 | -0.006022 | 0.010557 | 0.04087 | 0.008137 | 0.039107 | 0.006374
4388.5 | 122.0901 | -0.082397 | 121.9757 | 0.14017 | -0.031363 | -0.025735 | -0.025017 | 0.027109 | 0.076426 | -0.067295 | -0.048239 | 0.074638 | -0.045424 | -0.042259 | -0.075375 | -0.050029 | -0.04722 | -0.039797 | 0.22256 | 0.051034 | 0.056662 | 0.05738 | 0.10951 | 0.15882 | 0.015102 | -0.002463 | 0.12041 | 0.000352 | 0.003517 | -0.029599 | -0.004253 | -0.001444 | 0.005979 | 0.027136 | -0.001019 | 0.029951 | 0.001796
4390.2656 | 121.9894 | -0.09613 | 121.9803 | 0.14474 | -0.022205 | -0.016578 | -0.020438 | 0.022531 | 0.071848 | -0.067295 | -0.043661 | 0.07006 | -0.036267 | -0.042259 | -0.08911 | -0.050029 | -0.04722 | -0.039797 | 0.24087 | 0.073925 | 0.079552 | 0.075692 | 0.11866 | 0.16798 | 0.028835 | 0.002115 | 0.11584 | 0.009509 | 0.003517 | -0.043334 | -0.004253 | -0.001444 | 0.005979 | 0.045449 | 0.003559 | 0.052843 | 0.010953
4392.0312 | 122.1222 | -0.073242 | 121.9482 | 0.14017 | -0.026784 | -0.030314 | -0.029595 | 0.017953 | 0.071848 | -0.067295 | -0.048239 | 0.07006 | -0.031689 | -0.03768 | -0.084531 | -0.040873 | -0.051798 | -0.035219 | 0.21341 | 0.046458 | 0.042928 | 0.043647 | 0.091195 | 0.14509 | 0.005947 | -0.002463 | 0.11584 | 0.014087 | 0.008096 | -0.038755 | 0.004903 | -0.006022 | 0.010557 | 0.036292 | 0.003559 | 0.052842 | 0.020109
4393.7344 | 122.1268 | -0.050354 | 121.9437 | 0.14017 | -0.031363 | -0.025735 | -0.029595 | 0.017953 | 0.076426 | -0.071874 | -0.043661 | 0.07006 | -0.040846 | -0.03768 | -0.08911 | -0.050029 | -0.04722 | -0.039797 | 0.19052 | 0.018991 | 0.024619 | 0.020759 | 0.068307 | 0.12678 | -0.02152 | 0.002115 | 0.11584 | 0.00493 | 0.008096 | -0.043334 | -0.004253 | -0.001444 | 0.005979 | 0.045449 | 0.003559 | 0.048264 | 0.006374
4395.4844 | 122.049 | -0.11902 | 121.994 | 0.13559 | -0.031363 | -0.030314 | -0.025017 | 0.031687 | 0.071848 | -0.071874 | -0.043661 | 0.07006 | -0.040846 | -0.03768 | -0.075375 | -0.054607 | -0.056376 | -0.039797 | 0.25461 | 0.087656 | 0.088705 | 0.094002 | 0.15071 | 0.19087 | 0.047145 | 0.002115 | 0.11584 | 0.00493 | 0.008096 | -0.029599 | -0.008831 | -0.0106 | 0.005979 | 0.031714 | 0.012715 | 0.034529 | 0.01553
4397.2031 | 122.0169 | -0.10529 | 121.994 | 0.14474 | -0.031363 | -0.021157 | -0.029595 | 0.027109 | 0.067269 | -0.071874 | -0.048239 | 0.07006 | -0.040846 | -0.03768 | -0.079953 | -0.045451 | -0.056376 | -0.044375 | 0.25003 | 0.073923 | 0.084129 | 0.075691 | 0.1324 | 0.17256 | 0.033412 | -0.002463 | 0.11584 | 0.00493 | 0.008096 | -0.034177 | 0.000325 | -0.0106 | 0.001401 | 0.031714 | 0.008137 | 0.039107 | 0.01553
4398.9688 | 122.1405 | -0.054932 | 121.962 | 0.13559 | -0.026784 | -0.021157 | -0.025017 | 0.017953 | 0.067269 | -0.076452 | -0.039082 | 0.065481 | -0.045424 | -0.046838 | -0.08911 | -0.050029 | -0.04722 | -0.030641 | 0.19052 | 0.028148 | 0.033775 | 0.029915 | 0.072885 | 0.1222 | -0.02152 | 0.006694 | 0.11126 | 0.000352 | -0.001062 | -0.043334 | -0.004253 | -0.001444 | 0.015135 | 0.050028 | 0.008138 | 0.043686 | 0.001796
4400.75 | 122.0718 | -0.10071 | 121.9803 | 0.14017 | -0.022205 | -0.016578 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.043661 | 0.065481 | -0.036267 | -0.03768 | -0.08911 | -0.054607 | -0.051798 | -0.039797 | 0.24087 | 0.078503 | 0.08413 | 0.071113 | 0.12324 | 0.17256 | 0.037991 | 0.002115 | 0.11126 | 0.009509 | 0.008096 | -0.043334 | -0.008831 | -0.006022 | 0.005979 | 0.045449 | 0.008137 | 0.052843 | 0.015531
4402.4688 | 122.1085 | -0.041199 | 121.962 | 0.14017 | -0.022205 | -0.021157 | -0.034174 | 0.027109 | 0.067269 | -0.071874 | -0.048239 | 0.065481 | -0.045424 | -0.03768 | -0.075375 | -0.045451 | -0.051798 | -0.039797 | 0.18136 | 0.018994 | 0.020042 | 0.007025 | 0.068308 | 0.10847 | -0.030675 | -0.002463 | 0.11126 | 0.000352 | 0.008096 | -0.029599 | 0.000325 | -0.006022 | 0.005979 | 0.027136 | 0.003559 | 0.029951 | 0.006374
4404.2344 | 122.0581 | -0.10071 | 122.0032 | 0.14017 | -0.031363 | -0.016578 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.043661 | 0.065481 | -0.040846 | -0.03768 | -0.079953 | -0.054607 | -0.051798 | -0.039797 | 0.24087 | 0.069345 | 0.08413 | 0.075691 | 0.12324 | 0.17256 | 0.033413 | 0.002115 | 0.11126 | 0.00493 | 0.008096 | -0.034177 | -0.008831 | -0.006022 | 0.005979 | 0.036292 | 0.008137 | 0.039107 | 0.010952
4406 | 122.1176 | -0.073242 | 122.0078 | 0.14017 | -0.031363 | -0.021157 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | -0.043661 | 0.074638 | -0.040846 | -0.03768 | -0.084531 | -0.050029 | -0.04722 | -0.039797 | 0.21341 | 0.041879 | 0.052085 | 0.048225 | 0.095773 | 0.14051 | 0.010525 | 0.002115 | 0.12041 | 0.00493 | 0.008096 | -0.038755 | -0.004253 | -0.001444 | 0.005979 | 0.04087 | 0.003559 | 0.043685 | 0.006374
4407.7188 | 122.1588 | -0.050354 | 121.962 | 0.14017 | -0.031363 | -0.025735 | -0.020438 | 0.027109 | 0.071848 | -0.067295 | -0.039082 | 0.07006 | -0.031689 | -0.03768 | -0.079953 | -0.050029 | -0.056376 | -0.035219 | 0.19052 | 0.018991 | 0.024619 | 0.029916 | 0.077463 | 0.1222 | -0.016941 | 0.006694 | 0.11584 | 0.014087 | 0.008096 | -0.034177 | -0.004253 | -0.0106 | 0.010557 | 0.040871 | 0.017294 | 0.048264 | 0.024687
4409.4844 | 122.0764 | -0.086975 | 122.0169 | 0.13101 | -0.022205 | -0.021157 | -0.029595 | 0.027109 | 0.076426 | -0.062717 | -0.039082 | 0.065481 | -0.040846 | -0.042259 | -0.075375 | -0.054607 | -0.051798 | -0.039797 | 0.21798 | 0.06477 | 0.065818 | 0.05738 | 0.11408 | 0.1634 | 0.024258 | 0.006694 | 0.11126 | 0.00493 | 0.003517 | -0.029599 | -0.008831 | -0.006022 | 0.005979 | 0.036293 | 0.012716 | 0.034529 | 0.010952
4411.2031 | 122.0444 | -0.10071 | 121.9849 | 0.13559 | -0.031363 | -0.021157 | -0.025017 | 0.022531 | 0.081005 | -0.071874 | -0.043661 | 0.07006 | -0.045424 | -0.03768 | -0.08911 | -0.050029 | -0.051798 | -0.035219 | 0.23629 | 0.069345 | 0.079551 | 0.075691 | 0.12324 | 0.18171 | 0.028834 | 0.002115 | 0.11584 | 0.000352 | 0.008096 | -0.043334 | -0.004253 | -0.006022 | 0.010557 | 0.045449 | 0.008137 | 0.043686 | 0.006374
4412.9688 | 122.1451 | -0.054932 | 121.9574 | 0.14474 | -0.031363 | -0.025735 | -0.034174 | 0.022531 | 0.067269 | -0.067295 | -0.043661 | 0.060902 | -0.045424 | -0.042259 | -0.079953 | -0.054607 | -0.042641 | -0.035219 | 0.19968 | 0.023569 | 0.029197 | 0.020758 | 0.077463 | 0.1222 | -0.012363 | 0.002115 | 0.10668 | 0.000352 | 0.003517 | -0.034177 | -0.008831 | 0.003135 | 0.010557 | 0.036292 | -0.00102 | 0.034529 | -0.002783
4414.7344 | 122.1313 | -0.068665 | 121.9757 | 0.14017 | -0.031363 | -0.021157 | -0.025017 | 0.017953 | 0.076426 | -0.067295 | -0.043661 | 0.065481 | -0.040846 | -0.033101 | -0.084531 | -0.059185 | -0.04722 | -0.044375 | 0.20883 | 0.037302 | 0.047508 | 0.043648 | 0.086618 | 0.14509 | 0.00137 | 0.002115 | 0.11126 | 0.00493 | 0.012675 | -0.038755 | -0.013409 | -0.001444 | 0.001401 | 0.04087 | 0.003559 | 0.043685 | 0.006374
4416.4375 | 122.113 | -0.059509 | 121.9574 | 0.14017 | -0.035942 | -0.021157 | -0.020438 | 0.022531 | 0.076426 | -0.071874 | -0.039082 | 0.065481 | -0.040846 | -0.033101 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.19967 | 0.023567 | 0.038352 | 0.039071 | 0.08204 | 0.13594 | -0.012365 | 0.006694 | 0.11126 | 0.00493 | 0.012675 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.045449 | 0.012716 | 0.043685 | 0.010952
4418.2188 | 122.1542 | -0.068665 | 121.962 | 0.13559 | -0.026784 | -0.021157 | -0.029595 | 0.017953 | 0.076426 | -0.067295 | -0.043661 | 0.07006 | -0.040846 | -0.033101 | -0.079953 | -0.045451 | -0.04722 | -0.044375 | 0.20425 | 0.041881 | 0.047508 | 0.03907 | 0.086618 | 0.14509 | 0.00137 | 0.002115 | 0.11584 | 0.00493 | 0.012675 | -0.034177 | 0.000325 | -0.001444 | 0.001401 | 0.036292 | 0.003559 | 0.039107 | 0.006374
4419.9844 | 122.0535 | -0.10529 | 121.9849 | 0.14474 | -0.026784 | -0.021157 | -0.025017 | 0.031687 | 0.076426 | -0.067295 | -0.043661 | 0.065481 | -0.036267 | -0.042259 | -0.084531 | -0.050029 | -0.056376 | -0.030641 | 0.25003 | 0.078502 | 0.084129 | 0.080269 | 0.13697 | 0.18171 | 0.037991 | 0.002115 | 0.11126 | 0.009509 | 0.003517 | -0.038755 | -0.004253 | -0.0106 | 0.015135 | 0.04087 | 0.012715 | 0.048264 | 0.020109
4421.6875 | 122.0764 | -0.11444 | 122.0032 | 0.14017 | -0.035942 | -0.016578 | -0.020438 | 0.017953 | 0.076426 | -0.062717 | -0.043661 | 0.074638 | -0.040846 | -0.042259 | -0.075375 | -0.063763 | -0.051798 | -0.030641 | 0.25461 | 0.078499 | 0.097863 | 0.094003 | 0.13239 | 0.19087 | 0.051724 | 0.002115 | 0.12041 | 0.00493 | 0.003517 | -0.029599 | -0.017987 | -0.006022 | 0.015135 | 0.031714 | 0.008137 | 0.034529 | 0.010952
4423.4531 | 122.1771 | -0.068665 | 121.9574 | 0.14017 | -0.035942 | -0.016578 | -0.025017 | 0.027109 | 0.076426 | -0.067295 | -0.043661 | 0.065481 | -0.040846 | -0.03768 | -0.084531 | -0.054607 | -0.056376 | -0.044375 | 0.20883 | 0.032723 | 0.052087 | 0.043648 | 0.095774 | 0.14509 | 0.00137 | 0.002115 | 0.11126 | 0.00493 | 0.008096 | -0.038755 | -0.008831 | -0.0106 | 0.001401 | 0.04087 | 0.012715 | 0.043685 | 0.01553
4425.2188 | 122.0627 | -0.10071 | 122.0169 | 0.14017 | -0.031363 | -0.025735 | -0.029595 | 0.017953 | 0.067269 | -0.067295 | -0.043661 | 0.07006 | -0.040846 | -0.042259 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.24087 | 0.069345 | 0.074973 | 0.071113 | 0.11866 | 0.16798 | 0.033413 | 0.002115 | 0.11584 | 0.00493 | 0.003517 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.04087 | 0.008137 | 0.043685 | 0.010952
4427 | 122.0352 | -0.12817 | 122.0398 | 0.13559 | -0.031363 | -0.030314 | -0.029595 | 0.022531 | 0.067269 | -0.062717 | -0.048239 | 0.07006 | -0.045424 | -0.03768 | -0.084531 | -0.045451 | -0.060955 | -0.044375 | 0.26376 | 0.096811 | 0.09786 | 0.098579 | 0.15071 | 0.19544 | 0.065457 | -0.002463 | 0.11584 | 0.000352 | 0.008096 | -0.038755 | 0.000325 | -0.015179 | 0.001401 | 0.036292 | 0.012716 | 0.039107 | 0.015531
4428.7188 | 122.2046 | -0.059509 | 121.9757 | 0.14017 | -0.022205 | -0.025735 | -0.029595 | 0.027109 | 0.067269 | -0.062717 | -0.039082 | 0.07006 | -0.036267 | -0.042259 | -0.084531 | -0.045451 | -0.051798 | -0.035219 | 0.19967 | 0.037304 | 0.033774 | 0.029914 | 0.086618 | 0.12678 | -0.003208 | 0.006694 | 0.11584 | 0.009509 | 0.003517 | -0.038755 | 0.000325 | -0.006022 | 0.010557 | 0.045449 | 0.012716 | 0.048264 | 0.015531
4430.4844 | 122.0261 | -0.09613 | 122.0398 | 0.14017 | -0.035942 | -0.025735 | -0.020438 | 0.027109 | 0.067269 | -0.071874 | -0.043661 | 0.07006 | -0.040846 | -0.042259 | -0.084531 | -0.045451 | -0.056376 | -0.039797 | 0.2363 | 0.060188 | 0.070395 | 0.075692 | 0.12324 | 0.1634 | 0.024256 | 0.002115 | 0.11584 | 0.00493 | 0.003517 | -0.038755 | 0.000325 | -0.0106 | 0.005979 | 0.04087 | 0.012715 | 0.043685 | 0.01553
4432.2031 | 122.0078 | -0.09613 | 122.0352 | 0.14474 | -0.026784 | -0.025735 | -0.034174 | 0.022531 | 0.071848 | -0.067295 | -0.048239 | 0.065481 | -0.031689 | -0.03768 | -0.079953 | -0.050029 | -0.051798 | -0.035219 | 0.24087 | 0.069346 | 0.070395 | 0.061956 | 0.11866 | 0.16798 | 0.028835 | -0.002463 | 0.11126 | 0.014087 | 0.008096 | -0.034177 | -0.004253 | -0.006022 | 0.010557 | 0.031714 | 0.003559 | 0.048264 | 0.020109
4433.9688 | 122.1039 | -0.091553 | 122.0123 | 0.14017 | -0.022205 | -0.025735 | -0.029595 | 0.031687 | 0.067269 | -0.058139 | -0.039082 | 0.07006 | -0.040846 | -0.042259 | -0.084531 | -0.050029 | -0.04722 | -0.035219 | 0.23172 | 0.069348 | 0.065818 | 0.061958 | 0.12324 | 0.15882 | 0.033414 | 0.006694 | 0.11584 | 0.00493 | 0.003517 | -0.038755 | -0.004253 | -0.001444 | 0.010557 | 0.045449 | 0.008138 | 0.043685 | 0.006374
4435.7344 | 122.1359 | -0.059509 | 121.9757 | 0.14474 | -0.031363 | -0.030314 | -0.025017 | 0.027109 | 0.076426 | -0.062717 | -0.034504 | 0.065481 | -0.036267 | -0.042259 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.20425 | 0.028146 | 0.029195 | 0.034492 | 0.086618 | 0.13594 | -0.003208 | 0.011272 | 0.11126 | 0.009509 | 0.003517 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.050027 | 0.017294 | 0.048264 | 0.015531
4437.4375 | 122.0673 | -0.09613 | 122.0398 | 0.14474 | -0.031363 | -0.030314 | -0.025017 | 0.031687 | 0.062691 | -0.058139 | -0.043661 | 0.065481 | -0.040846 | -0.042259 | -0.079953 | -0.054607 | -0.051798 | -0.039797 | 0.24087 | 0.064767 | 0.065816 | 0.071113 | 0.12782 | 0.15882 | 0.037991 | 0.002115 | 0.11126 | 0.00493 | 0.003517 | -0.034177 | -0.008831 | -0.006022 | 0.005979 | 0.036292 | 0.008137 | 0.039107 | 0.010952
4439.2031 | 122.1954 | -0.054932 | 121.9986 | 0.14474 | -0.031363 | -0.034893 | -0.025017 | 0.022531 | 0.067269 | -0.071874 | -0.034504 | 0.065481 | -0.040846 | -0.033101 | -0.084531 | -0.050029 | -0.04722 | -0.030641 | 0.19968 | 0.023569 | 0.020039 | 0.029915 | 0.077463 | 0.1222 | -0.016942 | 0.011272 | 0.11126 | 0.00493 | 0.012675 | -0.038755 | -0.004253 | -0.001444 | 0.015135 | 0.050027 | 0.012716 | 0.043685 | 0.006374
4440.9688 | 122.0673 | -0.10529 | 122.0306 | 0.14474 | -0.026784 | -0.016578 | -0.025017 | 0.017953 | 0.071848 | -0.062717 | -0.043661 | 0.07006 | -0.040846 | -0.042259 | -0.084531 | -0.054607 | -0.051798 | -0.044375 | 0.25003 | 0.078502 | 0.088708 | 0.080269 | 0.12324 | 0.17713 | 0.042569 | 0.002115 | 0.11584 | 0.00493 | 0.003517 | -0.038755 | -0.008831 | -0.006022 | 0.001401 | 0.04087 | 0.008137 | 0.043685 | 0.010952
4442.7031 | 122.0856 | -0.10529 | 122.0627 | 0.14474 | -0.026784 | -0.030314 | -0.029595 | 0.027109 | 0.067269 | -0.062717 | -0.039082 | 0.07006 | -0.040846 | -0.042259 | -0.079953 | -0.045451 | -0.051798 | -0.039797 | 0.25003 | 0.078502 | 0.074972 | 0.075691 | 0.1324 | 0.17256 | 0.042569 | 0.006694 | 0.11584 | 0.00493 | 0.003517 | -0.034177 | 0.000325 | -0.006022 | 0.005979 | 0.040871 | 0.012716 | 0.039107 | 0.010952
4444.4688 | 122.0627 | -0.10529 | 122.0352 | 0.14017 | -0.031363 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.039082 | 0.065481 | -0.045424 | -0.03768 | -0.079953 | -0.050029 | -0.042641 | -0.039797 | 0.24545 | 0.073923 | 0.084129 | 0.080269 | 0.12782 | 0.17713 | 0.037991 | 0.006694 | 0.11126 | 0.000352 | 0.008096 | -0.034177 | -0.004253 | 0.003135 | 0.005979 | 0.040871 | 0.003559 | 0.034529 | -0.002783
4446.2344 | 122.1725 | -0.064087 | 122.0032 | 0.14474 | -0.026784 | -0.030314 | -0.025017 | 0.022531 | 0.071848 | -0.071874 | -0.043661 | 0.065481 | -0.036267 | -0.033101 | -0.075375 | -0.050029 | -0.051798 | -0.035219 | 0.20883 | 0.037303 | 0.033773 | 0.03907 | 0.086618 | 0.13594 | -0.007787 | 0.002115 | 0.11126 | 0.009509 | 0.012675 | -0.029599 | -0.004253 | -0.006022 | 0.010557 | 0.031714 | 0.008137 | 0.039108 | 0.015531
4448 | 122.2 | -0.064087 | 121.9894 | 0.14017 | -0.026784 | -0.021157 | -0.025017 | 0.022531 | 0.067269 | -0.071874 | -0.039082 | 0.065481 | -0.040846 | -0.03768 | -0.084531 | -0.045451 | -0.04722 | -0.048953 | 0.20425 | 0.037303 | 0.04293 | 0.03907 | 0.086618 | 0.13136 | -0.007787 | 0.006694 | 0.11126 | 0.00493 | 0.008096 | -0.038755 | 0.000325 | -0.001444 | -0.003177 | 0.045449 | 0.008138 | 0.043685 | 0.006374
4449.7031 | 122.1909 | -0.032043 | 122.0032 | 0.14017 | -0.031363 | -0.021157 | -0.025017 | 0.017953 | 0.071848 | -0.071874 | -0.043661 | 0.07006 | -0.040846 | -0.042259 | -0.08911 | -0.045451 | -0.051798 | -0.039797 | 0.17221 | 0.00068 | 0.010886 | 0.007026 | 0.049996 | 0.10389 | -0.039831 | 0.002115 | 0.11584 | 0.00493 | 0.003517 | -0.043334 | 0.000325 | -0.006022 | 0.005979 | 0.045449 | 0.008137 | 0.048264 | 0.010952
4451.4688 | 122.1634 | -0.054932 | 122.0078 | 0.14017 | -0.026784 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.058139 | -0.043661 | 0.060902 | -0.045424 | -0.042259 | -0.079953 | -0.050029 | -0.04722 | -0.044375 | 0.1951 | 0.028148 | 0.024618 | 0.025337 | 0.077463 | 0.12678 | -0.003207 | 0.002115 | 0.10668 | 0.000352 | 0.003517 | -0.034177 | -0.004253 | -0.001444 | 0.001401 | 0.036292 | 0.003559 | 0.034529 | 0.001796
4453.1719 | 122.1863 | -0.045776 | 122.0078 | 0.14017 | -0.031363 | -0.021157 | -0.025017 | 0.017953 | 0.071848 | -0.058139 | -0.043661 | 0.07006 | -0.040846 | -0.028522 | -0.079953 | -0.054607 | -0.04722 | -0.044375 | 0.18594 | 0.014413 | 0.024619 | 0.020759 | 0.063729 | 0.11762 | -0.012363 | 0.002115 | 0.11584 | 0.00493 | 0.017254 | -0.034177 | -0.008831 | -0.001444 | 0.001401 | 0.036292 | 0.003559 | 0.039107 | 0.006374
4454.9688 | 122.0856 | -0.091553 | 122.0352 | 0.14474 | -0.026784 | -0.030314 | -0.020438 | 0.022531 | 0.076426 | -0.062717 | -0.043661 | 0.060902 | -0.040846 | -0.033101 | -0.084531 | -0.050029 | -0.051798 | -0.044375 | 0.2363 | 0.064769 | 0.061239 | 0.071115 | 0.11408 | 0.16798 | 0.028836 | 0.002115 | 0.10668 | 0.00493 | 0.012675 | -0.038755 | -0.004253 | -0.006022 | 0.001401 | 0.04087 | 0.008137 | 0.043685 | 0.010952
4456.7344 | 122.0673 | -0.11902 | 122.0627 | 0.14017 | -0.035942 | -0.021157 | -0.025017 | 0.027109 | 0.071848 | -0.062717 | -0.048239 | 0.07006 | -0.045424 | -0.03768 | -0.08911 | -0.050029 | -0.04722 | -0.035219 | 0.25918 | 0.083077 | 0.097862 | 0.094002 | 0.14613 | 0.19087 | 0.056302 | -0.002463 | 0.11584 | 0.000352 | 0.008096 | -0.043334 | -0.004253 | -0.001444 | 0.010557 | 0.040871 | -0.001019 | 0.043686 | 0.001796
4458.4531 | 122.1863 | -0.050354 | 122.0169 | 0.14474 | -0.031363 | -0.030314 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | -0.043661 | 0.07006 | -0.031689 | -0.03768 | -0.070797 | -0.054607 | -0.060955 | -0.039797 | 0.1951 | 0.018991 | 0.02004 | 0.025337 | 0.072885 | 0.11762 | -0.012363 | 0.002115 | 0.11584 | 0.014087 | 0.008096 | -0.025021 | -0.008831 | -0.015179 | 0.005979 | 0.027136 | 0.017294 | 0.039108 | 0.029266
4460.2188 | 122.0764 | -0.1236 | 122.0352 | 0.14474 | -0.031363 | -0.021157 | -0.029595 | 0.027109 | 0.071848 | -0.067295 | -0.048239 | 0.07006 | -0.050002 | -0.033101 | -0.084531 | -0.054607 | -0.051798 | -0.044375 | 0.26834 | 0.092233 | 0.10244 | 0.094001 | 0.15071 | 0.19544 | 0.056301 | -0.002463 | 0.11584 | -0.004226 | 0.012675 | -0.038755 | -0.008831 | -0.006022 | 0.001401 | 0.036292 | 0.003559 | 0.034529 | 0.001796
4461.9219 | 122.1725 | -0.054932 | 122.0123 | 0.13101 | -0.026784 | -0.025735 | -0.025017 | 0.022531 | 0.062691 | -0.067295 | -0.039082 | 0.07006 | -0.036267 | -0.046838 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.18594 | 0.028148 | 0.029197 | 0.029915 | 0.077463 | 0.11762 | -0.012363 | 0.006694 | 0.11584 | 0.009509 | -0.001062 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.045449 | 0.012716 | 0.048264 | 0.015531
4463.6875 | 122.1451 | -0.068665 | 122.0078 | 0.14017 | -0.031363 | -0.030314 | -0.029595 | 0.027109 | 0.062691 | -0.067295 | -0.048239 | 0.07006 | -0.040846 | -0.03768 | -0.079953 | -0.054607 | -0.051798 | -0.035219 | 0.20883 | 0.037302 | 0.038351 | 0.03907 | 0.095774 | 0.13136 | 0.00137 | -0.002463 | 0.11584 | 0.00493 | 0.008096 | -0.034177 | -0.008831 | -0.006022 | 0.010557 | 0.031714 | 0.003559 | 0.039107 | 0.010952
4465.4531 | 122.1863 | -0.064087 | 122.0032 | 0.14474 | -0.026784 | -0.025735 | -0.025017 | 0.027109 | 0.071848 | -0.062717 | -0.048239 | 0.07006 | -0.045424 | -0.03768 | -0.084531 | -0.059185 | -0.051798 | -0.030641 | 0.20883 | 0.037303 | 0.038352 | 0.03907 | 0.091196 | 0.13594 | 0.00137 | -0.002463 | 0.11584 | 0.000352 | 0.008096 | -0.038755 | -0.013409 | -0.006022 | 0.015135 | 0.036292 | 0.003559 | 0.039107 | 0.006374
4467.2188 | 122.0993 | -0.10986 | 122.0444 | 0.13559 | -0.031363 | -0.025735 | -0.029595 | 0.022531 | 0.081005 | -0.067295 | -0.048239 | 0.065481 | -0.040846 | -0.033101 | -0.079953 | -0.040873 | -0.056376 | -0.039797 | 0.24545 | 0.0785 | 0.084128 | 0.080268 | 0.13239 | 0.19087 | 0.042568 | -0.002463 | 0.11126 | 0.00493 | 0.012675 | -0.034177 | 0.004903 | -0.0106 | 0.005979 | 0.031714 | 0.008137 | 0.039107 | 0.01553
4468.9844 | 122.1313 | -0.091553 | 122.0398 | 0.13559 | -0.031363 | -0.021157 | -0.020438 | 0.017953 | 0.071848 | -0.062717 | -0.043661 | 0.065481 | -0.036267 | -0.03768 | -0.08911 | -0.054607 | -0.04722 | -0.039797 | 0.22714 | 0.06019 | 0.070396 | 0.071115 | 0.10951 | 0.1634 | 0.028836 | 0.002115 | 0.11126 | 0.009509 | 0.008096 | -0.043334 | -0.008831 | -0.001444 | 0.005979 | 0.045449 | 0.003559 | 0.052843 | 0.010953
4470.6875 | 122.1039 | -0.09613 | 122.0261 | 0.14017 | -0.026784 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.048239 | 0.07006 | -0.036267 | -0.03768 | -0.084531 | -0.045451 | -0.051798 | -0.044375 | 0.2363 | 0.069346 | 0.070395 | 0.066535 | 0.11866 | 0.16798 | 0.028835 | -0.002463 | 0.11584 | 0.009509 | 0.008096 | -0.038755 | 0.000325 | -0.006022 | 0.001401 | 0.036292 | 0.003559 | 0.048264 | 0.015531
4472.4531 | 122.1634 | -0.068665 | 122.0306 | 0.14017 | -0.035942 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.052818 | 0.065481 | -0.040846 | -0.03768 | -0.070797 | -0.050029 | -0.04722 | -0.039797 | 0.20883 | 0.032723 | 0.047508 | 0.043648 | 0.091196 | 0.14051 | 0.005948 | -0.007042 | 0.11126 | 0.00493 | 0.008096 | -0.025021 | -0.004253 | -0.001444 | 0.005979 | 0.017979 | -0.005598 | 0.029951 | 0.006374
4474.1562 | 122.1405 | -0.07782 | 122.0169 | 0.14017 | -0.031363 | -0.025735 | -0.029595 | 0.022531 | 0.067269 | -0.071874 | -0.043661 | 0.065481 | -0.040846 | -0.042259 | -0.084531 | -0.054607 | -0.051798 | -0.039797 | 0.21799 | 0.046457 | 0.052085 | 0.048225 | 0.10035 | 0.14509 | 0.005946 | 0.002115 | 0.11126 | 0.00493 | 0.003517 | -0.038755 | -0.008831 | -0.006022 | 0.005979 | 0.04087 | 0.008137 | 0.043685 | 0.010952
4475.9219 | 122.1085 | -0.082397 | 122.0261 | 0.14474 | -0.040521 | -0.034893 | -0.025017 | 0.022531 | 0.076426 | -0.062717 | -0.043661 | 0.07006 | -0.045424 | -0.03768 | -0.08911 | -0.040873 | -0.056376 | -0.039797 | 0.22714 | 0.041876 | 0.047504 | 0.05738 | 0.10493 | 0.15882 | 0.01968 | 0.002115 | 0.11584 | 0.000352 | 0.008096 | -0.043334 | 0.004903 | -0.0106 | 0.005979 | 0.045449 | 0.012715 | 0.043686 | 0.010952
4477.6875 | 122.0627 | -0.10529 | 122.0398 | 0.14017 | -0.031363 | -0.016578 | -0.020438 | 0.022531 | 0.071848 | -0.062717 | -0.048239 | 0.074638 | -0.040846 | -0.03768 | -0.084531 | -0.045451 | -0.051798 | -0.039797 | 0.24545 | 0.073923 | 0.088708 | 0.084848 | 0.12782 | 0.17713 | 0.042569 | -0.002463 | 0.12041 | 0.00493 | 0.008096 | -0.038755 | 0.000325 | -0.006022 | 0.005979 | 0.036292 | 0.003559 | 0.043685 | 0.010952
4479.4531 | 122.1039 | -0.086975 | 122.0215 | 0.14017 | -0.035942 | -0.021157 | -0.029595 | 0.022531 | 0.067269 | -0.067295 | -0.048239 | 0.074638 | -0.040846 | -0.042259 | -0.079953 | -0.045451 | -0.051798 | -0.035219 | 0.22714 | 0.051033 | 0.065818 | 0.05738 | 0.10951 | 0.15424 | 0.01968 | -0.002463 | 0.12041 | 0.00493 | 0.003517 | -0.034177 | 0.000325 | -0.006022 | 0.010557 | 0.031714 | 0.003559 | 0.039107 | 0.010952
4481.1562 | 122.1222 | -0.091553 | 122.0261 | 0.14474 | -0.035942 | -0.021157 | -0.034174 | 0.013375 | 0.067269 | -0.067295 | -0.048239 | 0.074638 | -0.040846 | -0.033101 | -0.084531 | -0.040873 | -0.051798 | -0.035219 | 0.2363 | 0.055611 | 0.070396 | 0.057379 | 0.10493 | 0.15882 | 0.024258 | -0.002463 | 0.12041 | 0.00493 | 0.012675 | -0.038755 | 0.004903 | -0.006022 | 0.010557 | 0.036292 | 0.003559 | 0.043685 | 0.010952
4482.9219 | 122.1359 | -0.073242 | 122.0032 | 0.14474 | -0.031363 | -0.025735 | -0.029595 | 0.022531 | 0.058113 | -0.076452 | -0.043661 | 0.065481 | -0.036267 | -0.03768 | -0.079953 | -0.045451 | -0.051798 | -0.030641 | 0.21799 | 0.041879 | 0.047507 | 0.043647 | 0.095773 | 0.13135 | -0.00321 | 0.002115 | 0.11126 | 0.009509 | 0.008096 | -0.034177 | 0.000325 | -0.006022 | 0.015135 | 0.036292 | 0.008137 | 0.043686 | 0.015531
4484.6562 | 122.0718 | -0.10529 | 122.0352 | 0.14474 | -0.026784 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.048239 | 0.060902 | -0.036267 | -0.033101 | -0.079953 | -0.054607 | -0.051798 | -0.039797 | 0.25003 | 0.078502 | 0.079551 | 0.075691 | 0.12782 | 0.17713 | 0.037991 | -0.002463 | 0.10668 | 0.009509 | 0.012675 | -0.034177 | -0.008831 | -0.006022 | 0.005979 | 0.031714 | 0.003559 | 0.043686 | 0.015531
4486.4219 | 122.0581 | -0.10071 | 122.0398 | 0.13559 | -0.022205 | -0.030314 | -0.025017 | 0.027109 | 0.076426 | -0.071874 | -0.043661 | 0.07006 | -0.045424 | -0.03768 | -0.079953 | -0.050029 | -0.051798 | -0.035219 | 0.23629 | 0.078503 | 0.070394 | 0.075691 | 0.12782 | 0.17713 | 0.028834 | 0.002115 | 0.11584 | 0.000352 | 0.008096 | -0.034177 | -0.004253 | -0.006022 | 0.010557 | 0.036292 | 0.008137 | 0.034529 | 0.006374
4488.1406 | 122.1909 | -0.086975 | 122.049 | 0.14017 | -0.031363 | -0.030314 | -0.029595 | 0.017953 | 0.067269 | -0.071874 | -0.043661 | 0.065481 | -0.050002 | -0.03768 | -0.079953 | -0.050029 | -0.051798 | -0.044375 | 0.22714 | 0.055612 | 0.056661 | 0.05738 | 0.10493 | 0.15424 | 0.015101 | 0.002115 | 0.11126 | -0.004226 | 0.008096 | -0.034177 | -0.004253 | -0.006022 | 0.001401 | 0.036292 | 0.008137 | 0.029951 | 0.001796
4489.9062 | 122.1268 | -0.091553 | 122.0535 | 0.14474 | -0.026784 | -0.016578 | -0.020438 | 0.027109 | 0.076426 | -0.062717 | -0.048239 | 0.065481 | -0.036267 | -0.03768 | -0.08911 | -0.045451 | -0.04722 | -0.044375 | 0.2363 | 0.064769 | 0.074975 | 0.071115 | 0.11866 | 0.16798 | 0.028836 | -0.002463 | 0.11126 | 0.009509 | 0.008096 | -0.043334 | 0.000325 | -0.001444 | 0.001401 | 0.040871 | -0.001019 | 0.052843 | 0.010953
4491.6719 | 121.9666 | -0.10986 | 121.9528 | 0.13559 | -0.031363 | -0.025735 | -0.029595 | 0.031687 | 0.062691 | -0.071874 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.079953 | -0.040873 | -0.051798 | -0.030641 | 0.24545 | 0.0785 | 0.084128 | 0.080268 | 0.14155 | 0.17255 | 0.037989 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.034177 | 0.004903 | -0.006022 | 0.015135 | 0.031714 | 0.003559 | 0.039107 | 0.010952
4493.375 | 122.0398 | -0.11902 | 121.9894 | 0.13559 | -0.031363 | -0.025735 | -0.029595 | 0.022531 | 0.076426 | -0.067295 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.075375 | -0.045451 | -0.051798 | -0.030641 | 0.25461 | 0.087656 | 0.093284 | 0.089424 | 0.14155 | 0.19544 | 0.051724 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.029599 | 0.000325 | -0.006022 | 0.015135 | 0.027136 | 0.003559 | 0.034529 | 0.010952
4495.1406 | 122.0535 | -0.1236 | 122.0535 | 0.13559 | -0.031363 | -0.025735 | -0.025017 | 0.027109 | 0.076426 | -0.062717 | -0.048239 | 0.07006 | -0.045424 | -0.046838 | -0.079953 | -0.045451 | -0.056376 | -0.044375 | 0.25918 | 0.092233 | 0.097861 | 0.098579 | 0.15071 | 0.20002 | 0.060879 | -0.002463 | 0.11584 | 0.000352 | -0.001062 | -0.034177 | 0.000325 | -0.0106 | 0.001401 | 0.031714 | 0.008137 | 0.034529 | 0.010952
4496.8438 | 122.1817 | -0.064087 | 122.0078 | 0.13559 | -0.040521 | -0.025735 | -0.025017 | 0.013375 | 0.067269 | -0.062717 | -0.043661 | 0.07006 | -0.040846 | -0.033101 | -0.075375 | -0.040873 | -0.051798 | -0.035219 | 0.19967 | 0.023566 | 0.038352 | 0.03907 | 0.077462 | 0.13136 | 0.00137 | 0.002115 | 0.11584 | 0.00493 | 0.012675 | -0.029599 | 0.004903 | -0.006022 | 0.010557 | 0.031714 | 0.008137 | 0.034529 | 0.010952
4498.625 | 122.0535 | -0.10529 | 122.0398 | 0.14474 | -0.035942 | -0.021157 | -0.029595 | 0.017953 | 0.076426 | -0.071874 | -0.048239 | 0.07006 | -0.040846 | -0.042259 | -0.079953 | -0.045451 | -0.051798 | -0.035219 | 0.25003 | 0.069344 | 0.084129 | 0.075691 | 0.12324 | 0.18171 | 0.033412 | -0.002463 | 0.11584 | 0.00493 | 0.003517 | -0.034177 | 0.000325 | -0.006022 | 0.010557 | 0.031714 | 0.003559 | 0.039107 | 0.010952
4500.3281 | 122.1222 | -0.10071 | 122.0535 | 0.14017 | -0.035942 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.058139 | -0.048239 | 0.07006 | -0.040846 | -0.042259 | -0.079953 | -0.045451 | -0.056376 | -0.039797 | 0.24087 | 0.064766 | 0.079551 | 0.075691 | 0.12324 | 0.17256 | 0.042569 | -0.002463 | 0.11584 | 0.00493 | 0.003517 | -0.034177 | 0.000325 | -0.0106 | 0.005979 | 0.031714 | 0.008137 | 0.039107 | 0.01553
4502.0938 | 122.2321 | -0.086975 | 122.0352 | 0.14017 | -0.035942 | -0.025735 | -0.029595 | 0.022531 | 0.067269 | -0.071874 | -0.052818 | 0.065481 | -0.040846 | -0.033101 | -0.079953 | -0.045451 | -0.051798 | -0.030641 | 0.22714 | 0.051033 | 0.06124 | 0.05738 | 0.10951 | 0.15424 | 0.015101 | -0.007042 | 0.11126 | 0.00493 | 0.012675 | -0.034177 | 0.000325 | -0.006022 | 0.015135 | 0.027135 | -0.00102 | 0.039107 | 0.010952
4503.8125 | 122.0764 | -0.091553 | 122.081 | 0.13559 | -0.040521 | -0.030314 | -0.034174 | 0.022531 | 0.071848 | -0.062717 | -0.052818 | 0.065481 | -0.040846 | -0.03768 | -0.079953 | -0.040873 | -0.04722 | -0.044375 | 0.22714 | 0.051032 | 0.061239 | 0.057379 | 0.11408 | 0.1634 | 0.028836 | -0.007042 | 0.11126 | 0.00493 | 0.008096 | -0.034177 | 0.004903 | -0.001444 | 0.001401 | 0.027135 | -0.005598 | 0.039107 | 0.006374
4505.5781 | 122.1771 | -0.059509 | 122.0627 | 0.14017 | -0.031363 | -0.030314 | -0.025017 | 0.027109 | 0.067269 | -0.053561 | -0.043661 | 0.07006 | -0.040846 | -0.03768 | -0.079953 | -0.040873 | -0.051798 | -0.035219 | 0.19967 | 0.028146 | 0.029195 | 0.034492 | 0.086618 | 0.12678 | 0.005948 | 0.002115 | 0.11584 | 0.00493 | 0.008096 | -0.034177 | 0.004903 | -0.006022 | 0.010557 | 0.036292 | 0.008137 | 0.039107 | 0.010952
4507.3594 | 122.1817 | -0.086975 | 122.0581 | 0.13101 | -0.031363 | -0.030314 | -0.029595 | 0.022531 | 0.067269 | -0.062717 | -0.048239 | 0.060902 | -0.036267 | -0.03768 | -0.079953 | -0.050029 | -0.051798 | -0.039797 | 0.21798 | 0.055612 | 0.056661 | 0.05738 | 0.10951 | 0.15424 | 0.024258 | -0.002463 | 0.10668 | 0.009509 | 0.008096 | -0.034177 | -0.004253 | -0.006022 | 0.005979 | 0.031714 | 0.003559 | 0.043686 | 0.015531
4509.0781 | 122.1313 | -0.09613 | 122.081 | 0.14017 | -0.026784 | -0.025735 | -0.025017 | 0.022531 | 0.076426 | -0.067295 | -0.052818 | 0.056323 | -0.045424 | -0.03768 | -0.084531 | -0.050029 | -0.056376 | -0.035219 | 0.2363 | 0.069346 | 0.070395 | 0.071113 | 0.11866 | 0.17256 | 0.028835 | -0.007042 | 0.1021 | 0.000352 | 0.008096 | -0.038755 | -0.004253 | -0.0106 | 0.010557 | 0.031713 | 0.003558 | 0.039107 | 0.010952
4510.8438 | 122.0993 | -0.091553 | 122.0718 | 0.13559 | -0.031363 | -0.025735 | -0.034174 | 0.022531 | 0.067269 | -0.071874 | -0.057396 | 0.056323 | -0.045424 | -0.042259 | -0.079953 | -0.040873 | -0.04722 | -0.035219 | 0.22714 | 0.06019 | 0.065818 | 0.057379 | 0.11408 | 0.15882 | 0.019679 | -0.01162 | 0.1021 | 0.000352 | 0.003517 | -0.034177 | 0.004903 | -0.001444 | 0.010557 | 0.022557 | -0.010176 | 0.034529 | 0.001796
4512.6094 | 122.1497 | -0.09613 | 122.0856 | 0.14017 | -0.031363 | -0.030314 | -0.034174 | 0.027109 | 0.071848 | -0.062717 | -0.052818 | 0.07006 | -0.040846 | -0.042259 | -0.079953 | -0.050029 | -0.056376 | -0.035219 | 0.2363 | 0.064767 | 0.065816 | 0.061956 | 0.12324 | 0.16798 | 0.033413 | -0.007042 | 0.11584 | 0.00493 | 0.003517 | -0.034177 | -0.004253 | -0.0106 | 0.010557 | 0.027135 | 0.003558 | 0.039107 | 0.01553
4514.3906 | 122.2137 | -0.073242 | 122.0901 | 0.13559 | -0.031363 | -0.025735 | -0.025017 | 0.027109 | 0.067269 | -0.067295 | -0.043661 | 0.060902 | -0.040846 | -0.03768 | -0.075375 | -0.045451 | -0.056376 | -0.044375 | 0.20883 | 0.041879 | 0.047507 | 0.048225 | 0.10035 | 0.14051 | 0.005947 | 0.002115 | 0.10668 | 0.00493 | 0.008096 | -0.029599 | 0.000325 | -0.0106 | 0.001401 | 0.031714 | 0.012715 | 0.034529 | 0.01553
4516.1094 | 122.2321 | -0.073242 | 122.0581 | 0.14932 | -0.031363 | -0.025735 | -0.029595 | 0.017953 | 0.081005 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.046838 | -0.079953 | -0.050029 | -0.04722 | -0.035219 | 0.22256 | 0.041879 | 0.047507 | 0.043647 | 0.091195 | 0.15425 | 0.010525 | -0.002463 | 0.11126 | 0.00493 | -0.001062 | -0.034177 | -0.004253 | -0.001444 | 0.010557 | 0.031714 | -0.001019 | 0.039107 | 0.006374
4517.875 | 122.1451 | -0.10529 | 122.113 | 0.14474 | -0.031363 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.042259 | -0.079953 | -0.040873 | -0.051798 | -0.039797 | 0.25003 | 0.073923 | 0.079551 | 0.075691 | 0.12782 | 0.17713 | 0.042569 | -0.002463 | 0.11126 | 0.00493 | 0.003517 | -0.034177 | 0.004903 | -0.006022 | 0.005979 | 0.031714 | 0.003559 | 0.039107 | 0.010952
4519.6562 | 122.168 | -0.10986 | 122.1039 | 0.13559 | -0.031363 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.052818 | 0.065481 | -0.040846 | -0.03768 | -0.075375 | -0.050029 | -0.056376 | -0.044375 | 0.24545 | 0.0785 | 0.088706 | 0.084846 | 0.13239 | 0.18171 | 0.047146 | -0.007042 | 0.11126 | 0.00493 | 0.008096 | -0.029599 | -0.004253 | -0.0106 | 0.001401 | 0.022557 | 0.003558 | 0.034529 | 0.01553
4521.4219 | 122.1359 | -0.10071 | 122.1039 | 0.14017 | -0.035942 | -0.021157 | -0.034174 | 0.027109 | 0.067269 | -0.058139 | -0.048239 | 0.07006 | -0.040846 | -0.03768 | -0.075375 | -0.045451 | -0.056376 | -0.035219 | 0.24087 | 0.064766 | 0.079551 | 0.066534 | 0.12782 | 0.16798 | 0.042569 | -0.002463 | 0.11584 | 0.00493 | 0.008096 | -0.029599 | 0.000325 | -0.0106 | 0.010557 | 0.027136 | 0.008137 | 0.034529 | 0.01553
4523.125 | 122.1313 | -0.10529 | 122.1039 | 0.14474 | -0.031363 | -0.016578 | -0.034174 | 0.027109 | 0.067269 | -0.062717 | -0.057396 | 0.065481 | -0.036267 | -0.042259 | -0.075375 | -0.045451 | -0.051798 | -0.035219 | 0.25003 | 0.073923 | 0.088708 | 0.071112 | 0.1324 | 0.17256 | 0.042569 | -0.01162 | 0.11126 | 0.009509 | 0.003517 | -0.029599 | 0.000325 | -0.006022 | 0.010557 | 0.017979 | -0.005598 | 0.039108 | 0.015531
4524.9062 | 122.1451 | -0.09613 | 122.1085 | 0.14017 | -0.026784 | -0.021157 | -0.029595 | 0.027109 | 0.071848 | -0.067295 | -0.052818 | 0.060902 | -0.036267 | -0.033101 | -0.084531 | -0.045451 | -0.056376 | -0.035219 | 0.2363 | 0.069346 | 0.074973 | 0.066535 | 0.12324 | 0.16798 | 0.028835 | -0.007042 | 0.10668 | 0.009509 | 0.012675 | -0.038755 | 0.000325 | -0.0106 | 0.010557 | 0.031713 | 0.003558 | 0.048264 | 0.020109
4526.6094 | 122.1176 | -0.10986 | 122.1268 | 0.14017 | -0.031363 | -0.025735 | -0.025017 | 0.027109 | 0.076426 | -0.062717 | -0.043661 | 0.060902 | -0.045424 | -0.042259 | -0.075375 | -0.045451 | -0.04722 | -0.030641 | 0.25003 | 0.0785 | 0.084128 | 0.084846 | 0.13697 | 0.18629 | 0.047146 | 0.002115 | 0.10668 | 0.000352 | 0.003517 | -0.029599 | 0.000325 | -0.001444 | 0.015135 | 0.031714 | 0.003559 | 0.029951 | 0.001796
4528.375 | 122.2183 | -0.059509 | 122.0901 | 0.13559 | -0.040521 | -0.025735 | -0.025017 | 0.022531 | 0.062691 | -0.071874 | -0.057396 | 0.065481 | -0.036267 | -0.03768 | -0.075375 | -0.045451 | -0.051798 | -0.035219 | 0.1951 | 0.018988 | 0.033774 | 0.034492 | 0.08204 | 0.1222 | -0.012365 | -0.01162 | 0.11126 | 0.009509 | 0.008096 | -0.029599 | 0.000325 | -0.006022 | 0.010557 | 0.017979 | -0.005598 | 0.039108 | 0.015531
4530.0938 | 122.1771 | -0.086975 | 122.1268 | 0.13559 | -0.035942 | -0.025735 | -0.025017 | 0.027109 | 0.071848 | -0.067295 | -0.043661 | 0.07006 | -0.040846 | -0.046838 | -0.079953 | -0.054607 | -0.04722 | -0.035219 | 0.22256 | 0.051033 | 0.06124 | 0.061958 | 0.11408 | 0.15882 | 0.01968 | 0.002115 | 0.11584 | 0.00493 | -0.001062 | -0.034177 | -0.008831 | -0.001444 | 0.010557 | 0.036292 | 0.003559 | 0.039107 | 0.006374
4531.8594 | 122.2549 | -0.07782 | 122.0764 | 0.14017 | -0.031363 | -0.034893 | -0.029595 | 0.022531 | 0.071848 | -0.071874 | -0.048239 | 0.065481 | -0.045424 | -0.042259 | -0.08911 | -0.045451 | -0.056376 | -0.044375 | 0.21799 | 0.046457 | 0.042927 | 0.048225 | 0.10035 | 0.14967 | 0.005946 | -0.002463 | 0.11126 | 0.000352 | 0.003517 | -0.043334 | 0.000325 | -0.0106 | 0.001401 | 0.040871 | 0.008137 | 0.043686 | 0.010952
4533.6406 | 122.2412 | -0.045776 | 122.0901 | 0.13559 | -0.031363 | -0.030314 | -0.029595 | 0.017953 | 0.067269 | -0.062717 | -0.048239 | 0.060902 | -0.045424 | -0.03768 | -0.079953 | -0.050029 | -0.056376 | -0.030641 | 0.18136 | 0.014413 | 0.015462 | 0.016181 | 0.063729 | 0.11304 | -0.016941 | -0.002463 | 0.10668 | 0.000352 | 0.008096 | -0.034177 | -0.004253 | -0.0106 | 0.015135 | 0.031714 | 0.008137 | 0.034529 | 0.010952
4535.4062 | 122.2 | -0.091553 | 122.1268 | 0.14017 | -0.031363 | -0.025735 | -0.025017 | 0.027109 | 0.076426 | -0.071874 | -0.043661 | 0.07006 | -0.050002 | -0.042259 | -0.070797 | -0.045451 | -0.051798 | -0.026063 | 0.23172 | 0.06019 | 0.065818 | 0.066536 | 0.11866 | 0.16798 | 0.019679 | 0.002115 | 0.11584 | -0.004226 | 0.003517 | -0.025021 | 0.000325 | -0.006022 | 0.019713 | 0.027136 | 0.008137 | 0.020795 | 0.001796
4537.1094 | 122.1451 | -0.11444 | 122.168 | 0.14017 | -0.040521 | -0.030314 | -0.029595 | 0.027109 | 0.067269 | -0.058139 | -0.052818 | 0.065481 | -0.040846 | -0.042259 | -0.084531 | -0.040873 | -0.051798 | -0.035219 | 0.25461 | 0.07392 | 0.084127 | 0.084846 | 0.14155 | 0.18171 | 0.056302 | -0.007042 | 0.11126 | 0.00493 | 0.003517 | -0.038755 | 0.004903 | -0.006022 | 0.010557 | 0.031713 | -0.00102 | 0.043685 | 0.010952
4538.875 | 122.1451 | -0.10986 | 122.1634 | 0.13559 | -0.026784 | -0.025735 | -0.029595 | 0.027109 | 0.067269 | -0.062717 | -0.048239 | 0.060902 | -0.036267 | -0.042259 | -0.079953 | -0.050029 | -0.051798 | -0.039797 | 0.24545 | 0.083079 | 0.084128 | 0.080268 | 0.13697 | 0.17713 | 0.047146 | -0.002463 | 0.10668 | 0.009509 | 0.003517 | -0.034177 | -0.004253 | -0.006022 | 0.005979 | 0.031714 | 0.003559 | 0.043686 | 0.015531
4540.6406 | 122.1542 | -0.1236 | 122.1725 | 0.14474 | -0.040521 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.048239 | 0.065481 | -0.045424 | -0.042259 | -0.079953 | -0.040873 | -0.056376 | -0.035219 | 0.26834 | 0.083075 | 0.097861 | 0.094001 | 0.14613 | 0.19544 | 0.060879 | -0.002463 | 0.11126 | 0.000352 | 0.003517 | -0.034177 | 0.004903 | -0.0106 | 0.010557 | 0.031714 | 0.008137 | 0.034529 | 0.010952
4542.3438 | 122.2321 | -0.068665 | 122.1176 | 0.13559 | -0.026784 | -0.021157 | -0.029595 | 0.022531 | 0.067269 | -0.067295 | -0.052818 | 0.074638 | -0.040846 | -0.042259 | -0.075375 | -0.050029 | -0.051798 | -0.035219 | 0.20425 | 0.041881 | 0.047508 | 0.03907 | 0.091196 | 0.13593 | 0.00137 | -0.007042 | 0.12041 | 0.00493 | 0.003517 | -0.029599 | -0.004253 | -0.006022 | 0.010557 | 0.022557 | -0.00102 | 0.034529 | 0.010952
4544.1094 | 122.1588 | -0.09613 | 122.1359 | 0.13559 | -0.035942 | -0.021157 | -0.025017 | 0.027109 | 0.067269 | -0.071874 | -0.057396 | 0.060902 | -0.045424 | -0.03768 | -0.084531 | -0.040873 | -0.056376 | -0.039797 | 0.23172 | 0.060188 | 0.074973 | 0.071113 | 0.12324 | 0.1634 | 0.024256 | -0.01162 | 0.10668 | 0.000352 | 0.008096 | -0.038755 | 0.004903 | -0.0106 | 0.005979 | 0.027135 | -0.00102 | 0.039107 | 0.010952
4545.875 | 122.2458 | -0.068665 | 122.0718 | 0.13559 | -0.035942 | -0.025735 | -0.034174 | 0.027109 | 0.076426 | -0.071874 | -0.048239 | 0.065481 | -0.045424 | -0.03768 | -0.084531 | -0.040873 | -0.056376 | -0.039797 | 0.20425 | 0.032723 | 0.04293 | 0.034491 | 0.095774 | 0.14509 | -0.003209 | -0.002463 | 0.11126 | 0.000352 | 0.008096 | -0.038755 | 0.004903 | -0.0106 | 0.005979 | 0.036292 | 0.008137 | 0.039107 | 0.010952
4547.6562 | 122.1542 | -0.086975 | 122.168 | 0.13559 | -0.026784 | -0.025735 | -0.020438 | 0.027109 | 0.076426 | -0.062717 | -0.043661 | 0.074638 | -0.045424 | -0.042259 | -0.079953 | -0.045451 | -0.051798 | -0.035219 | 0.22256 | 0.060191 | 0.06124 | 0.066537 | 0.11408 | 0.1634 | 0.024258 | 0.002115 | 0.12041 | 0.000352 | 0.003517 | -0.034177 | 0.000325 | -0.006022 | 0.010557 | 0.036292 | 0.008137 | 0.034529 | 0.006374
4549.4219 | 122.2183 | -0.10071 | 122.1542 | 0.14474 | -0.026784 | -0.025735 | -0.025017 | 0.031687 | 0.071848 | -0.067295 | -0.043661 | 0.065481 | -0.045424 | -0.033101 | -0.084531 | -0.036295 | -0.051798 | -0.035219 | 0.24545 | 0.073924 | 0.074973 | 0.075691 | 0.1324 | 0.17256 | 0.033413 | 0.002115 | 0.11126 | 0.000352 | 0.012675 | -0.038755 | 0.009481 | -0.006022 | 0.010557 | 0.04087 | 0.008137 | 0.039107 | 0.006374
4551.125 | 122.1863 | -0.10529 | 122.1542 | 0.13559 | -0.031363 | -0.025735 | -0.029595 | 0.031687 | 0.071848 | -0.058139 | -0.052818 | 0.065481 | -0.045424 | -0.03768 | -0.079953 | -0.050029 | -0.051798 | -0.039797 | 0.24087 | 0.073923 | 0.079551 | 0.075691 | 0.13697 | 0.17713 | 0.047147 | -0.007042 | 0.11126 | 0.000352 | 0.008096 | -0.034177 | -0.004253 | -0.006022 | 0.005979 | 0.027135 | -0.00102 | 0.034529 | 0.006374
4552.8906 | 122.2687 | -0.068665 | 122.0947 | 0.13559 | -0.031363 | -0.021157 | -0.025017 | 0.022531 | 0.067269 | -0.067295 | -0.043661 | 0.056323 | -0.045424 | -0.042259 | -0.079953 | -0.045451 | -0.056376 | -0.048953 | 0.20425 | 0.037302 | 0.047508 | 0.043648 | 0.091196 | 0.13593 | 0.00137 | 0.002115 | 0.1021 | 0.000352 | 0.003517 | -0.034177 | 0.000325 | -0.0106 | -0.003177 | 0.036292 | 0.012715 | 0.034529 | 0.010952
4554.6562 | 122.287 | -0.054932 | 122.113 | 0.13559 | -0.031363 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.076452 | -0.043661 | 0.060902 | -0.045424 | -0.042259 | -0.075375 | -0.050029 | -0.051798 | -0.039797 | 0.19052 | 0.023569 | 0.029197 | 0.025337 | 0.077463 | 0.12678 | -0.02152 | 0.002115 | 0.10668 | 0.000352 | 0.003517 | -0.029599 | -0.004253 | -0.006022 | 0.005979 | 0.031714 | 0.008137 | 0.029951 | 0.006374
4556.3594 | 122.1771 | -0.11444 | 122.1725 | 0.14017 | -0.031363 | -0.025735 | -0.025017 | 0.017953 | 0.067269 | -0.062717 | -0.043661 | 0.065481 | -0.045424 | -0.042259 | -0.084531 | -0.045451 | -0.04722 | -0.035219 | 0.25461 | 0.083078 | 0.088706 | 0.089424 | 0.13239 | 0.18171 | 0.051724 | 0.002115 | 0.11126 | 0.000352 | 0.003517 | -0.038755 | 0.000325 | -0.001444 | 0.010557 | 0.04087 | 0.003559 | 0.039107 | 0.001796
4558.125 | 122.2641 | -0.073242 | 122.1176 | 0.13559 | -0.031363 | -0.030314 | -0.020438 | 0.022531 | 0.071848 | -0.067295 | -0.048239 | 0.060902 | -0.040846 | -0.03768 | -0.084531 | -0.050029 | -0.04722 | -0.039797 | 0.20883 | 0.041879 | 0.042928 | 0.052804 | 0.095773 | 0.14509 | 0.005947 | -0.002463 | 0.10668 | 0.00493 | 0.008096 | -0.038755 | -0.004253 | -0.001444 | 0.005979 | 0.036292 | -0.001019 | 0.043685 | 0.006374
4559.8438 | 122.1771 | -0.091553 | 122.1542 | 0.14474 | -0.035942 | -0.030314 | -0.029595 | 0.017953 | 0.071848 | -0.067295 | -0.052818 | 0.060902 | -0.040846 | -0.03768 | -0.079953 | -0.050029 | -0.051798 | -0.030641 | 0.2363 | 0.055611 | 0.061239 | 0.061958 | 0.10951 | 0.1634 | 0.024258 | -0.007042 | 0.10668 | 0.00493 | 0.008096 | -0.034177 | -0.004253 | -0.006022 | 0.015135 | 0.027135 | -0.00102 | 0.039107 | 0.010952
4561.6094 | 122.2458 | -0.064087 | 122.1268 | 0.13559 | -0.031363 | -0.030314 | -0.029595 | 0.017953 | 0.071848 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.042259 | -0.075375 | -0.050029 | -0.04722 | -0.030641 | 0.19967 | 0.032724 | 0.033773 | 0.034492 | 0.08204 | 0.13594 | 0.00137 | -0.002463 | 0.11126 | 0.00493 | 0.003517 | -0.029599 | -0.004253 | -0.001444 | 0.015135 | 0.027136 | -0.001019 | 0.034529 | 0.006374
4563.3906 | 122.3099 | -0.050354 | 122.113 | 0.14017 | -0.031363 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.052818 | 0.07006 | -0.045424 | -0.03768 | -0.079953 | -0.040873 | -0.04722 | -0.035219 | 0.19052 | 0.018991 | 0.024619 | 0.020759 | 0.072885 | 0.1222 | -0.016941 | -0.007042 | 0.11584 | 0.000352 | 0.008096 | -0.034177 | 0.004903 | -0.001444 | 0.010557 | 0.027135 | -0.005598 | 0.034529 | 0.001796
4565.1719 | 122.3007 | -0.064087 | 122.0993 | 0.14017 | -0.026784 | -0.025735 | -0.029595 | 0.013375 | 0.071848 | -0.071874 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.075375 | -0.040873 | -0.051798 | -0.030641 | 0.20425 | 0.037303 | 0.038352 | 0.034492 | 0.077462 | 0.13594 | -0.007787 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.029599 | 0.004903 | -0.006022 | 0.015135 | 0.027136 | 0.003559 | 0.034529 | 0.010952
4566.9531 | 122.1954 | -0.11902 | 122.1634 | 0.14474 | -0.031363 | -0.030314 | -0.034174 | 0.022531 | 0.071848 | -0.076452 | -0.043661 | 0.060902 | -0.045424 | -0.042259 | -0.079953 | -0.040873 | -0.056376 | -0.035219 | 0.26376 | 0.087656 | 0.088705 | 0.084845 | 0.14155 | 0.19087 | 0.042567 | 0.002115 | 0.10668 | 0.000352 | 0.003517 | -0.034177 | 0.004903 | -0.0106 | 0.010557 | 0.036292 | 0.012715 | 0.034529 | 0.010952
4568.6562 | 122.1909 | -0.11444 | 122.1542 | 0.14017 | -0.026784 | -0.021157 | -0.034174 | 0.022531 | 0.067269 | -0.067295 | -0.048239 | 0.060902 | -0.045424 | -0.046838 | -0.075375 | -0.045451 | -0.04722 | -0.035219 | 0.25461 | 0.087657 | 0.093284 | 0.080267 | 0.13697 | 0.18171 | 0.047146 | -0.002463 | 0.10668 | 0.000352 | -0.001062 | -0.029599 | 0.000325 | -0.001444 | 0.010557 | 0.027136 | -0.001019 | 0.029951 | 0.001796
4570.4375 | 122.2275 | -0.091553 | 122.1634 | 0.14017 | -0.026784 | -0.021157 | -0.029595 | 0.017953 | 0.067269 | -0.062717 | -0.052818 | 0.060902 | -0.045424 | -0.03768 | -0.084531 | -0.045451 | -0.051798 | -0.039797 | 0.23172 | 0.064769 | 0.070396 | 0.061958 | 0.10951 | 0.15882 | 0.028836 | -0.007042 | 0.10668 | 0.000352 | 0.008096 | -0.038755 | 0.000325 | -0.006022 | 0.005979 | 0.031713 | -0.00102 | 0.039107 | 0.006374
4572.2031 | 122.3099 | -0.07782 | 122.1313 | 0.13559 | -0.035942 | -0.025735 | -0.029595 | 0.017953 | 0.076426 | -0.067295 | -0.052818 | 0.060902 | -0.050002 | -0.046838 | -0.070797 | -0.045451 | -0.060955 | -0.035219 | 0.21341 | 0.041878 | 0.052085 | 0.048225 | 0.095773 | 0.15425 | 0.010525 | -0.007042 | 0.10668 | -0.004226 | -0.001062 | -0.025021 | 0.000325 | -0.015179 | 0.010557 | 0.017979 | 0.008137 | 0.020795 | 0.010953
4573.9688 | 122.1863 | -0.10529 | 122.1817 | 0.13559 | -0.031363 | -0.021157 | -0.025017 | 0.017953 | 0.071848 | -0.062717 | -0.052818 | 0.07006 | -0.045424 | -0.033101 | -0.079953 | -0.040873 | -0.051798 | -0.039797 | 0.24087 | 0.073923 | 0.084129 | 0.080269 | 0.12324 | 0.17713 | 0.042569 | -0.007042 | 0.11584 | 0.000352 | 0.012675 | -0.034177 | 0.004903 | -0.006022 | 0.005979 | 0.027135 | -0.00102 | 0.034529 | 0.006374
4575.6875 | 122.3236 | -0.064087 | 122.168 | 0.13559 | -0.026784 | -0.025735 | -0.025017 | 0.022531 | 0.067269 | -0.071874 | -0.048239 | 0.060902 | -0.040846 | -0.03768 | -0.084531 | -0.036295 | -0.060955 | -0.035219 | 0.19967 | 0.037303 | 0.038352 | 0.03907 | 0.086618 | 0.13136 | -0.007787 | -0.002463 | 0.10668 | 0.00493 | 0.008096 | -0.038755 | 0.009481 | -0.015179 | 0.010557 | 0.036292 | 0.012716 | 0.043685 | 0.020109
4577.4531 | 122.2046 | -0.11444 | 122.1771 | 0.14474 | -0.035942 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.043661 | 0.065481 | -0.040846 | -0.042259 | -0.079953 | -0.045451 | -0.051798 | -0.035219 | 0.25918 | 0.078499 | 0.088706 | 0.089424 | 0.13697 | 0.18629 | 0.047146 | 0.002115 | 0.11126 | 0.00493 | 0.003517 | -0.034177 | 0.000325 | -0.006022 | 0.010557 | 0.036292 | 0.008137 | 0.039107 | 0.010952
4579.1562 | 122.2 | -0.12817 | 122.1725 | 0.13559 | -0.031363 | -0.025735 | -0.029595 | 0.022531 | 0.067269 | -0.067295 | -0.048239 | 0.065481 | -0.036267 | -0.042259 | -0.075375 | -0.050029 | -0.04722 | -0.035219 | 0.26376 | 0.096811 | 0.10244 | 0.098579 | 0.15071 | 0.19544 | 0.060879 | -0.002463 | 0.11126 | 0.009509 | 0.003517 | -0.029599 | -0.004253 | -0.001444 | 0.010557 | 0.027136 | -0.001019 | 0.039108 | 0.010953
4580.9219 | 122.2504 | -0.086975 | 122.168 | 0.13559 | -0.026784 | -0.025735 | -0.020438 | 0.022531 | 0.071848 | -0.062717 | -0.052818 | 0.07006 | -0.050002 | -0.042259 | -0.075375 | -0.054607 | -0.051798 | -0.030641 | 0.22256 | 0.060191 | 0.06124 | 0.066537 | 0.10951 | 0.15882 | 0.024258 | -0.007042 | 0.11584 | -0.004226 | 0.003517 | -0.029599 | -0.008831 | -0.006022 | 0.015135 | 0.022557 | -0.00102 | 0.025373 | 0.001796
4582.7031 | 122.3328 | -0.064087 | 122.1405 | 0.14017 | -0.031363 | -0.030314 | -0.034174 | 0.022531 | 0.067269 | -0.071874 | -0.052818 | 0.060902 | -0.036267 | -0.03768 | -0.079953 | -0.050029 | -0.051798 | -0.039797 | 0.20425 | 0.032724 | 0.033773 | 0.029913 | 0.086618 | 0.13136 | -0.007787 | -0.007042 | 0.10668 | 0.009509 | 0.008096 | -0.034177 | -0.004253 | -0.006022 | 0.005979 | 0.027135 | -0.00102 | 0.043686 | 0.015531
4584.4688 | 122.3282 | -0.054932 | 122.1542 | 0.14017 | -0.031363 | -0.021157 | -0.029595 | 0.013375 | 0.071848 | -0.067295 | -0.043661 | 0.065481 | -0.036267 | -0.042259 | -0.070797 | -0.045451 | -0.056376 | -0.030641 | 0.1951 | 0.023569 | 0.033775 | 0.025337 | 0.068307 | 0.12678 | -0.012363 | 0.002115 | 0.11126 | 0.009509 | 0.003517 | -0.025021 | 0.000325 | -0.0106 | 0.015135 | 0.027136 | 0.012715 | 0.03453 | 0.020109
4586.1719 | 122.2092 | -0.11902 | 122.1954 | 0.13101 | -0.026784 | -0.025735 | -0.025017 | 0.017953 | 0.058113 | -0.062717 | -0.048239 | 0.065481 | -0.045424 | -0.03768 | -0.075375 | -0.045451 | -0.04722 | -0.039797 | 0.25003 | 0.092235 | 0.093284 | 0.094002 | 0.13697 | 0.17713 | 0.056302 | -0.002463 | 0.11126 | 0.000352 | 0.008096 | -0.029599 | 0.000325 | -0.001444 | 0.005979 | 0.027136 | -0.001019 | 0.029951 | 0.001796
4587.9375 | 122.3373 | -0.054932 | 122.1451 | 0.14017 | -0.022205 | -0.025735 | -0.029595 | 0.022531 | 0.067269 | -0.067295 | -0.048239 | 0.051744 | -0.045424 | -0.033101 | -0.070797 | -0.045451 | -0.04722 | -0.030641 | 0.1951 | 0.032727 | 0.029197 | 0.025337 | 0.077463 | 0.1222 | -0.012363 | -0.002463 | 0.09752 | 0.000352 | 0.012675 | -0.025021 | 0.000325 | -0.001444 | 0.015135 | 0.022558 | -0.001019 | 0.025373 | 0.001796
4589.7188 | 122.2046 | -0.10529 | 122.1817 | 0.14017 | -0.035942 | -0.025735 | -0.020438 | 0.022531 | 0.067269 | -0.071874 | -0.057396 | 0.060902 | -0.045424 | -0.03768 | -0.079953 | -0.045451 | -0.04722 | -0.044375 | 0.24545 | 0.069344 | 0.079551 | 0.084848 | 0.12782 | 0.17256 | 0.033412 | -0.01162 | 0.10668 | 0.000352 | 0.008096 | -0.034177 | 0.000325 | -0.001444 | 0.001401 | 0.022557 | -0.010176 | 0.034529 | 0.001796
4591.5 | 122.2961 | -0.073242 | 122.1725 | 0.14474 | -0.026784 | -0.025735 | -0.029595 | 0.022531 | 0.067269 | -0.067295 | -0.048239 | 0.060902 | -0.031689 | -0.046838 | -0.079953 | -0.036295 | -0.04722 | -0.044375 | 0.21799 | 0.046458 | 0.047507 | 0.043647 | 0.095773 | 0.14051 | 0.005947 | -0.002463 | 0.10668 | 0.014087 | -0.001062 | -0.034177 | 0.009481 | -0.001444 | 0.001401 | 0.031714 | -0.001019 | 0.048264 | 0.015531
4593.2031 | 122.2961 | -0.082397 | 122.1497 | 0.13101 | -0.026784 | -0.025735 | -0.034174 | 0.027109 | 0.062691 | -0.067295 | -0.043661 | 0.060902 | -0.045424 | -0.042259 | -0.075375 | -0.040873 | -0.04722 | -0.039797 | 0.21341 | 0.055613 | 0.056662 | 0.048223 | 0.10951 | 0.14509 | 0.015102 | 0.002115 | 0.10668 | 0.000352 | 0.003517 | -0.029599 | 0.004903 | -0.001444 | 0.005979 | 0.031714 | 0.003559 | 0.029951 | 0.001796
4594.9844 | 122.1771 | -0.10986 | 122.2 | 0.14474 | -0.031363 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.052818 | 0.07006 | -0.040846 | -0.042259 | -0.079953 | -0.045451 | -0.04722 | -0.035219 | 0.25461 | 0.0785 | 0.084128 | 0.084846 | 0.13239 | 0.18171 | 0.042568 | -0.007042 | 0.11584 | 0.00493 | 0.003517 | -0.034177 | 0.000325 | -0.001444 | 0.010557 | 0.027135 | -0.005598 | 0.039107 | 0.006374
4596.7031 | 122.2092 | -0.10986 | 122.2046 | 0.13101 | -0.040521 | -0.025735 | -0.029595 | 0.017953 | 0.067269 | -0.071874 | -0.052818 | 0.056323 | -0.036267 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.24087 | 0.069342 | 0.084128 | 0.080268 | 0.12782 | 0.17713 | 0.037989 | -0.007042 | 0.1021 | 0.009509 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.031713 | -0.00102 | 0.048264 | 0.015531
4598.4688 | 122.287 | -0.10071 | 122.1634 | 0.13101 | -0.026784 | -0.025735 | -0.025017 | 0.027109 | 0.076426 | -0.067295 | -0.057396 | 0.065481 | -0.040846 | -0.03768 | -0.093688 | -0.050029 | -0.051798 | -0.039797 | 0.23172 | 0.073924 | 0.074973 | 0.075691 | 0.12782 | 0.17713 | 0.033413 | -0.01162 | 0.11126 | 0.00493 | 0.008096 | -0.047912 | -0.004253 | -0.006022 | 0.005979 | 0.036292 | -0.005598 | 0.052842 | 0.010952
4600.1875 | 122.2321 | -0.09613 | 122.2046 | 0.13101 | -0.031363 | -0.025735 | -0.029595 | 0.022531 | 0.058113 | -0.067295 | -0.057396 | 0.060902 | -0.045424 | -0.033101 | -0.075375 | -0.045451 | -0.056376 | -0.030641 | 0.22714 | 0.064767 | 0.070395 | 0.066535 | 0.11866 | 0.15424 | 0.028835 | -0.01162 | 0.10668 | 0.000352 | 0.012675 | -0.029599 | 0.000325 | -0.0106 | 0.015135 | 0.017979 | -0.00102 | 0.029951 | 0.010952
4601.9531 | 122.3419 | -0.07782 | 122.1542 | 0.13559 | -0.026784 | -0.025735 | -0.029595 | 0.017953 | 0.071848 | -0.071874 | -0.057396 | 0.060902 | -0.045424 | -0.042259 | -0.084531 | -0.040873 | -0.051798 | -0.035219 | 0.21341 | 0.051036 | 0.052085 | 0.048225 | 0.095773 | 0.14967 | 0.005946 | -0.01162 | 0.10668 | 0.000352 | 0.003517 | -0.038755 | 0.004903 | -0.006022 | 0.010557 | 0.027135 | -0.005598 | 0.039107 | 0.006374
4603.6562 | 122.3648 | -0.054932 | 122.1451 | 0.13101 | -0.031363 | -0.030314 | -0.034174 | 0.013375 | 0.067269 | -0.067295 | -0.048239 | 0.07006 | -0.040846 | -0.03768 | -0.084531 | -0.040873 | -0.051798 | -0.030641 | 0.18594 | 0.023569 | 0.024618 | 0.020758 | 0.068307 | 0.1222 | -0.012363 | -0.002463 | 0.11584 | 0.00493 | 0.008096 | -0.038755 | 0.004903 | -0.006022 | 0.015135 | 0.036292 | 0.003559 | 0.043685 | 0.010952
4605.4219 | 122.3145 | -0.050354 | 122.1771 | 0.13559 | -0.035942 | -0.030314 | -0.034174 | 0.017953 | 0.067269 | -0.067295 | -0.048239 | 0.065481 | -0.036267 | -0.03768 | -0.079953 | -0.040873 | -0.051798 | -0.035219 | 0.18594 | 0.014412 | 0.02004 | 0.01618 | 0.068307 | 0.11762 | -0.016941 | -0.002463 | 0.11126 | 0.009509 | 0.008096 | -0.034177 | 0.004903 | -0.006022 | 0.010557 | 0.031714 | 0.003559 | 0.043686 | 0.015531
4607.125 | 122.3419 | -0.073242 | 122.1588 | 0.13101 | -0.040521 | -0.025735 | -0.034174 | 0.017953 | 0.062691 | -0.071874 | -0.057396 | 0.056323 | -0.045424 | -0.042259 | -0.075375 | -0.050029 | -0.051798 | -0.035219 | 0.20425 | 0.032721 | 0.047507 | 0.039068 | 0.091195 | 0.13593 | 0.001368 | -0.01162 | 0.1021 | 0.000352 | 0.003517 | -0.029599 | -0.004253 | -0.006022 | 0.010557 | 0.017979 | -0.005598 | 0.029951 | 0.006374
4608.9062 | 122.2595 | -0.11444 | 122.2183 | 0.13559 | -0.035942 | -0.016578 | -0.029595 | 0.031687 | 0.067269 | -0.071874 | -0.048239 | 0.056323 | -0.045424 | -0.046838 | -0.079953 | -0.050029 | -0.056376 | -0.035219 | 0.25003 | 0.078499 | 0.097863 | 0.084846 | 0.14613 | 0.18171 | 0.042567 | -0.002463 | 0.1021 | 0.000352 | -0.001062 | -0.034177 | -0.004253 | -0.0106 | 0.010557 | 0.031714 | 0.008137 | 0.034529 | 0.010952
4610.625 | 122.2549 | -0.10986 | 122.2092 | 0.13101 | -0.035942 | -0.025735 | -0.020438 | 0.017953 | 0.067269 | -0.067295 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.079953 | -0.045451 | -0.04722 | -0.026063 | 0.24087 | 0.073921 | 0.084128 | 0.089425 | 0.12782 | 0.17713 | 0.042568 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.034177 | 0.000325 | -0.001444 | 0.019713 | 0.031714 | -0.001019 | 0.039107 | 0.006374
4612.4062 | 122.2595 | -0.10071 | 122.2046 | 0.14017 | -0.040521 | -0.021157 | -0.020438 | 0.017953 | 0.071848 | -0.062717 | -0.043661 | 0.060902 | -0.031689 | -0.03768 | -0.084531 | -0.045451 | -0.051798 | -0.039797 | 0.24087 | 0.060187 | 0.079551 | 0.08027 | 0.11866 | 0.17256 | 0.037991 | 0.002115 | 0.10668 | 0.014087 | 0.008096 | -0.038755 | 0.000325 | -0.006022 | 0.005979 | 0.04087 | 0.008137 | 0.052842 | 0.020109
4614.125 | 122.2549 | -0.10529 | 122.1954 | 0.13101 | -0.031363 | -0.030314 | -0.029595 | 0.027109 | 0.071848 | -0.067295 | -0.057396 | 0.060902 | -0.045424 | -0.046838 | -0.079953 | -0.045451 | -0.04722 | -0.035219 | 0.23629 | 0.073923 | 0.074972 | 0.075691 | 0.1324 | 0.17713 | 0.037991 | -0.01162 | 0.10668 | 0.000352 | -0.001062 | -0.034177 | 0.000325 | -0.001444 | 0.010557 | 0.022557 | -0.010176 | 0.034529 | 0.001796
4615.9062 | 122.2366 | -0.11444 | 122.2321 | 0.13101 | -0.026784 | -0.030314 | -0.025017 | 0.013375 | 0.062691 | -0.062717 | -0.052818 | 0.056323 | -0.036267 | -0.03768 | -0.079953 | -0.045451 | -0.051798 | -0.039797 | 0.24545 | 0.087657 | 0.084127 | 0.089424 | 0.12782 | 0.17713 | 0.051724 | -0.007042 | 0.1021 | 0.009509 | 0.008096 | -0.034177 | 0.000325 | -0.006022 | 0.005979 | 0.027135 | -0.00102 | 0.043686 | 0.015531
4617.6875 | 122.2641 | -0.091553 | 122.2137 | 0.13101 | -0.031363 | -0.021157 | -0.034174 | 0.027109 | 0.076426 | -0.076452 | -0.052818 | 0.065481 | -0.031689 | -0.051417 | -0.075375 | -0.050029 | -0.042641 | -0.035219 | 0.22256 | 0.06019 | 0.070396 | 0.057379 | 0.11866 | 0.16798 | 0.015101 | -0.007042 | 0.11126 | 0.014087 | -0.005641 | -0.029599 | -0.004253 | 0.003135 | 0.010557 | 0.022557 | -0.010177 | 0.043686 | 0.010952
4619.4531 | 122.3282 | -0.07782 | 122.2092 | 0.13101 | -0.031363 | -0.025735 | -0.038752 | 0.022531 | 0.067269 | -0.071874 | -0.052818 | 0.060902 | -0.040846 | -0.033101 | -0.084531 | -0.045451 | -0.051798 | -0.039797 | 0.20883 | 0.046457 | 0.052085 | 0.039068 | 0.10035 | 0.14509 | 0.005946 | -0.007042 | 0.10668 | 0.00493 | 0.012675 | -0.038755 | 0.000325 | -0.006022 | 0.005979 | 0.031713 | -0.00102 | 0.043685 | 0.010952
4621.2344 | 122.319 | -0.064087 | 122.1863 | 0.13559 | -0.040521 | -0.030314 | -0.034174 | 0.022531 | 0.067269 | -0.067295 | -0.057396 | 0.060902 | -0.040846 | -0.046838 | -0.075375 | -0.045451 | -0.051798 | -0.035219 | 0.19967 | 0.023566 | 0.033773 | 0.029913 | 0.086618 | 0.13136 | -0.003208 | -0.01162 | 0.10668 | 0.00493 | -0.001062 | -0.029599 | 0.000325 | -0.006022 | 0.010557 | 0.017979 | -0.005598 | 0.034529 | 0.010952
4622.9531 | 122.3282 | -0.068665 | 122.168 | 0.13101 | -0.031363 | -0.021157 | -0.029595 | 0.013375 | 0.071848 | -0.067295 | -0.043661 | 0.060902 | -0.045424 | -0.042259 | -0.084531 | -0.050029 | -0.056376 | -0.035219 | 0.19967 | 0.037302 | 0.047508 | 0.03907 | 0.08204 | 0.14051 | 0.00137 | 0.002115 | 0.10668 | 0.000352 | 0.003517 | -0.038755 | -0.004253 | -0.0106 | 0.010557 | 0.04087 | 0.012715 | 0.039107 | 0.010952
4624.7188 | 122.2321 | -0.10529 | 122.2229 | 0.13559 | -0.035942 | -0.025735 | -0.029595 | 0.027109 | 0.071848 | -0.062717 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.075375 | -0.040873 | -0.051798 | -0.030641 | 0.24087 | 0.069344 | 0.079551 | 0.075691 | 0.1324 | 0.17713 | 0.042569 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.029599 | 0.004903 | -0.006022 | 0.015135 | 0.027136 | 0.003559 | 0.034529 | 0.010952
4626.4844 | 122.2229 | -0.10986 | 122.2183 | 0.13559 | -0.031363 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.052818 | 0.065481 | -0.036267 | -0.03768 | -0.079953 | -0.050029 | -0.051798 | -0.035219 | 0.24545 | 0.0785 | 0.079549 | 0.080268 | 0.13239 | 0.18171 | 0.042568 | -0.007042 | 0.11126 | 0.009509 | 0.008096 | -0.034177 | -0.004253 | -0.006022 | 0.010557 | 0.027135 | -0.00102 | 0.043686 | 0.015531
4628.1875 | 122.2733 | -0.11902 | 122.2412 | 0.13559 | -0.031363 | -0.030314 | -0.029595 | 0.017953 | 0.071848 | -0.062717 | -0.048239 | 0.056323 | -0.040846 | -0.046838 | -0.084531 | -0.036295 | -0.051798 | -0.035219 | 0.25461 | 0.087656 | 0.088705 | 0.089424 | 0.13697 | 0.19087 | 0.056302 | -0.002463 | 0.1021 | 0.00493 | -0.001062 | -0.038755 | 0.009481 | -0.006022 | 0.010557 | 0.036292 | 0.003559 | 0.043685 | 0.010952
4629.9531 | 122.3877 | -0.050354 | 122.1817 | 0.13559 | -0.035942 | -0.021157 | -0.029595 | 0.017953 | 0.067269 | -0.08103 | -0.048239 | 0.065481 | -0.045424 | -0.03768 | -0.070797 | -0.045451 | -0.04722 | -0.035219 | 0.18594 | 0.014412 | 0.029197 | 0.020759 | 0.068307 | 0.11762 | -0.030676 | -0.002463 | 0.11126 | 0.000352 | 0.008096 | -0.025021 | 0.000325 | -0.001444 | 0.010557 | 0.022558 | -0.001019 | 0.025373 | 0.001796
4631.6719 | 122.2275 | -0.10986 | 122.2412 | 0.13559 | -0.035942 | -0.030314 | -0.029595 | 0.022531 | 0.076426 | -0.062717 | -0.048239 | 0.056323 | -0.045424 | -0.042259 | -0.084531 | -0.050029 | -0.042641 | -0.035219 | 0.24545 | 0.073921 | 0.079549 | 0.080268 | 0.13239 | 0.18629 | 0.047146 | -0.002463 | 0.1021 | 0.000352 | 0.003517 | -0.038755 | -0.004253 | 0.003135 | 0.010557 | 0.036292 | -0.005598 | 0.039107 | -0.002783
4633.4375 | 122.374 | -0.073242 | 122.2092 | 0.13559 | -0.031363 | -0.021157 | -0.025017 | 0.017953 | 0.067269 | -0.067295 | -0.052818 | 0.065481 | -0.036267 | -0.042259 | -0.075375 | -0.040873 | -0.051798 | -0.039797 | 0.20883 | 0.041879 | 0.052085 | 0.048225 | 0.091195 | 0.14051 | 0.005947 | -0.007042 | 0.11126 | 0.009509 | 0.003517 | -0.029599 | 0.004903 | -0.006022 | 0.005979 | 0.022557 | -0.00102 | 0.039108 | 0.015531
4635.2188 | 122.3831 | -0.050354 | 122.2137 | 0.12643 | -0.031363 | -0.021157 | -0.029595 | 0.027109 | 0.071848 | -0.071874 | -0.048239 | 0.056323 | -0.050002 | -0.042259 | -0.084531 | -0.040873 | -0.056376 | -0.035219 | 0.17678 | 0.018991 | 0.029197 | 0.020759 | 0.077463 | 0.1222 | -0.02152 | -0.002463 | 0.1021 | -0.004226 | 0.003517 | -0.038755 | 0.004903 | -0.0106 | 0.010557 | 0.036292 | 0.008137 | 0.034529 | 0.006374
4636.9375 | 122.3465 | -0.073242 | 122.1863 | 0.13101 | -0.031363 | -0.025735 | -0.043331 | 0.017953 | 0.076426 | -0.067295 | -0.052818 | 0.060902 | -0.040846 | -0.042259 | -0.070797 | -0.050029 | -0.04722 | -0.039797 | 0.20425 | 0.041879 | 0.047507 | 0.029911 | 0.091195 | 0.14967 | 0.005947 | -0.007042 | 0.10668 | 0.00493 | 0.003517 | -0.025021 | -0.004253 | -0.001444 | 0.005979 | 0.017979 | -0.005598 | 0.029951 | 0.006374
4638.6875 | 122.2458 | -0.1236 | 122.2275 | 0.13559 | -0.035942 | -0.030314 | -0.029595 | 0.017953 | 0.071848 | -0.062717 | -0.057396 | 0.056323 | -0.040846 | -0.042259 | -0.070797 | -0.050029 | -0.056376 | -0.030641 | 0.25918 | 0.087654 | 0.093282 | 0.094001 | 0.14155 | 0.19544 | 0.060879 | -0.01162 | 0.1021 | 0.00493 | 0.003517 | -0.025021 | -0.004253 | -0.0106 | 0.015135 | 0.013401 | -0.00102 | 0.029951 | 0.01553
4640.3906 | 122.3145 | -0.082397 | 122.2137 | 0.13101 | -0.035942 | -0.025735 | -0.029595 | 0.027109 | 0.067269 | -0.067295 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.075375 | -0.054607 | -0.051798 | -0.039797 | 0.21341 | 0.046455 | 0.056662 | 0.052802 | 0.10951 | 0.14967 | 0.015102 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.029599 | -0.008831 | -0.006022 | 0.005979 | 0.027136 | 0.003559 | 0.034529 | 0.010952
4642.1719 | 122.2458 | -0.10529 | 122.2549 | 0.13101 | -0.040521 | -0.034893 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.052818 | 0.056323 | -0.045424 | -0.046838 | -0.079953 | -0.045451 | -0.04722 | -0.039797 | 0.23629 | 0.064765 | 0.070393 | 0.080269 | 0.12782 | 0.17713 | 0.042569 | -0.007042 | 0.1021 | 0.000352 | -0.001062 | -0.034177 | 0.000325 | -0.001444 | 0.005979 | 0.027135 | -0.005598 | 0.034529 | 0.001796
4643.9375 | 122.3053 | -0.09613 | 122.2458 | 0.12643 | -0.040521 | -0.021157 | -0.025017 | 0.017953 | 0.062691 | -0.067295 | -0.057396 | 0.056323 | -0.040846 | -0.042259 | -0.070797 | -0.045451 | -0.051798 | -0.035219 | 0.22256 | 0.055609 | 0.074973 | 0.071113 | 0.11408 | 0.15882 | 0.028835 | -0.01162 | 0.1021 | 0.00493 | 0.003517 | -0.025021 | 0.000325 | -0.006022 | 0.010557 | 0.013401 | -0.005598 | 0.029951 | 0.010952
4645.7188 | 122.2504 | -0.10071 | 122.2458 | 0.14017 | -0.035942 | -0.025735 | -0.025017 | 0.017953 | 0.071848 | -0.062717 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.075375 | -0.045451 | -0.051798 | -0.035219 | 0.24087 | 0.064766 | 0.074973 | 0.075691 | 0.11866 | 0.17256 | 0.037991 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.029599 | 0.000325 | -0.006022 | 0.010557 | 0.027136 | 0.003559 | 0.034529 | 0.010952
4647.4375 | 122.3923 | -0.054932 | 122.2229 | 0.13559 | -0.035942 | -0.030314 | -0.025017 | 0.027109 | 0.067269 | -0.067295 | -0.052818 | 0.056323 | -0.045424 | -0.046838 | -0.075375 | -0.050029 | -0.042641 | -0.039797 | 0.19052 | 0.01899 | 0.024618 | 0.029915 | 0.082041 | 0.1222 | -0.012363 | -0.007042 | 0.1021 | 0.000352 | -0.001062 | -0.029599 | -0.004253 | 0.003135 | 0.005979 | 0.022557 | -0.010177 | 0.029951 | -0.002783
4649.1875 | 122.287 | -0.10529 | 122.2458 | 0.13559 | -0.035942 | -0.030314 | -0.025017 | 0.022531 | 0.076426 | -0.071874 | -0.057396 | 0.065481 | -0.036267 | -0.03768 | -0.075375 | -0.045451 | -0.04722 | -0.039797 | 0.24087 | 0.069344 | 0.074972 | 0.080269 | 0.12782 | 0.18171 | 0.033412 | -0.01162 | 0.11126 | 0.009509 | 0.008096 | -0.029599 | 0.000325 | -0.001444 | 0.005979 | 0.017979 | -0.010176 | 0.039108 | 0.010953
4650.9531 | 122.3419 | -0.054932 | 122.2275 | 0.13101 | -0.040521 | -0.021157 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.048239 | 0.056323 | -0.040846 | -0.03768 | -0.075375 | -0.045451 | -0.051798 | -0.039797 | 0.18594 | 0.014411 | 0.033775 | 0.025337 | 0.077463 | 0.12678 | -0.007785 | -0.002463 | 0.1021 | 0.00493 | 0.008096 | -0.029599 | 0.000325 | -0.006022 | 0.005979 | 0.027136 | 0.003559 | 0.034529 | 0.010952
4652.7344 | 122.3236 | -0.09613 | 122.2504 | 0.13101 | -0.031363 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.052818 | 0.065481 | -0.045424 | -0.051417 | -0.070797 | -0.050029 | -0.051798 | -0.039797 | 0.22714 | 0.064767 | 0.070395 | 0.071113 | 0.11866 | 0.16798 | 0.033413 | -0.007042 | 0.11126 | 0.000352 | -0.005641 | -0.025021 | -0.004253 | -0.006022 | 0.005979 | 0.017979 | -0.00102 | 0.025373 | 0.006374
4654.5156 | 122.2687 | -0.11444 | 122.2687 | 0.12185 | -0.026784 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.052818 | 0.065481 | -0.045424 | -0.042259 | -0.075375 | -0.040873 | -0.051798 | -0.039797 | 0.23629 | 0.087657 | 0.084127 | 0.084846 | 0.13697 | 0.18629 | 0.047146 | -0.007042 | 0.11126 | 0.000352 | 0.003517 | -0.029599 | 0.004903 | -0.006022 | 0.005979 | 0.022557 | -0.00102 | 0.029951 | 0.006374
4656.2969 | 122.287 | -0.10529 | 122.2458 | 0.13101 | -0.035942 | -0.021157 | -0.025017 | 0.027109 | 0.067269 | -0.071874 | -0.048239 | 0.060902 | -0.040846 | -0.028522 | -0.075375 | -0.045451 | -0.051798 | -0.026063 | 0.23629 | 0.069344 | 0.084129 | 0.080269 | 0.1324 | 0.17256 | 0.033412 | -0.002463 | 0.10668 | 0.00493 | 0.017254 | -0.029599 | 0.000325 | -0.006022 | 0.019713 | 0.027136 | 0.003559 | 0.034529 | 0.010952
4658.0625 | 122.2733 | -0.1236 | 122.2595 | 0.13559 | -0.031363 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.052818 | 0.060902 | -0.040846 | -0.042259 | -0.084531 | -0.040873 | -0.051798 | -0.035219 | 0.25918 | 0.092233 | 0.097861 | 0.094001 | 0.14613 | 0.19544 | 0.056301 | -0.007042 | 0.10668 | 0.00493 | 0.003517 | -0.038755 | 0.004903 | -0.006022 | 0.010557 | 0.031713 | -0.00102 | 0.043685 | 0.010952
4659.7656 | 122.4152 | -0.068665 | 122.2229 | 0.12643 | -0.035942 | -0.030314 | -0.029595 | 0.022531 | 0.067269 | -0.071874 | -0.048239 | 0.060902 | -0.036267 | -0.03768 | -0.079953 | -0.040873 | -0.060955 | -0.030641 | 0.19509 | 0.032723 | 0.038351 | 0.03907 | 0.091196 | 0.13593 | -0.003209 | -0.002463 | 0.10668 | 0.009509 | 0.008096 | -0.034177 | 0.004903 | -0.015179 | 0.015135 | 0.031714 | 0.012716 | 0.043686 | 0.024688
4661.5469 | 122.3328 | -0.082397 | 122.2549 | 0.13101 | -0.026784 | -0.025735 | -0.034174 | 0.017953 | 0.071848 | -0.067295 | -0.057396 | 0.060902 | -0.036267 | -0.042259 | -0.079953 | -0.050029 | -0.051798 | -0.035219 | 0.21341 | 0.055613 | 0.056662 | 0.048223 | 0.10035 | 0.15424 | 0.015102 | -0.01162 | 0.10668 | 0.009509 | 0.003517 | -0.034177 | -0.004253 | -0.006022 | 0.010557 | 0.022557 | -0.005598 | 0.043686 | 0.015531
4663.3125 | 122.4152 | -0.068665 | 122.2229 | 0.13101 | -0.031363 | -0.025735 | -0.029595 | 0.017953 | 0.067269 | -0.071874 | -0.057396 | 0.060902 | -0.045424 | -0.03768 | -0.079953 | -0.045451 | -0.04722 | -0.035219 | 0.19967 | 0.037302 | 0.04293 | 0.03907 | 0.086618 | 0.13593 | -0.003209 | -0.01162 | 0.10668 | 0.000352 | 0.008096 | -0.034177 | 0.000325 | -0.001444 | 0.010557 | 0.022557 | -0.010176 | 0.034529 | 0.001796
4665.0156 | 122.3831 | -0.064087 | 122.2046 | 0.13559 | -0.040521 | -0.025735 | -0.029595 | 0.013375 | 0.067269 | -0.058139 | -0.057396 | 0.051744 | -0.045424 | -0.046838 | -0.075375 | -0.040873 | -0.04722 | -0.039797 | 0.19967 | 0.023566 | 0.038352 | 0.034492 | 0.077462 | 0.13136 | 0.005948 | -0.01162 | 0.09752 | 0.000352 | -0.001062 | -0.029599 | 0.004903 | -0.001444 | 0.005979 | 0.017979 | -0.010176 | 0.029951 | 0.001796
4666.7969 | 122.3053 | -0.11444 | 122.2733 | 0.13101 | -0.035942 | -0.021157 | -0.034174 | 0.017953 | 0.067269 | -0.067295 | -0.052818 | 0.060902 | -0.040846 | -0.03768 | -0.079953 | -0.045451 | -0.060955 | -0.030641 | 0.24545 | 0.078499 | 0.093284 | 0.080267 | 0.13239 | 0.18171 | 0.047146 | -0.007042 | 0.10668 | 0.00493 | 0.008096 | -0.034177 | 0.000325 | -0.015179 | 0.015135 | 0.027135 | 0.008137 | 0.039107 | 0.020109
4668.5625 | 122.3969 | -0.050354 | 122.2046 | 0.13101 | -0.031363 | -0.030314 | -0.020438 | 0.027109 | 0.062691 | -0.067295 | -0.052818 | 0.060902 | -0.045424 | -0.046838 | -0.075375 | -0.045451 | -0.051798 | -0.039797 | 0.18136 | 0.018991 | 0.02004 | 0.029916 | 0.077463 | 0.11305 | -0.016941 | -0.007042 | 0.10668 | 0.000352 | -0.001062 | -0.029599 | 0.000325 | -0.006022 | 0.005979 | 0.022557 | -0.00102 | 0.029951 | 0.006374
4670.2656 | 122.3877 | -0.068665 | 122.2275 | 0.12185 | -0.035942 | -0.030314 | -0.029595 | 0.022531 | 0.062691 | -0.067295 | -0.052818 | 0.060902 | -0.036267 | -0.042259 | -0.079953 | -0.045451 | -0.042641 | -0.035219 | 0.19052 | 0.032723 | 0.038351 | 0.03907 | 0.091196 | 0.13136 | 0.00137 | -0.007042 | 0.10668 | 0.009509 | 0.003517 | -0.034177 | 0.000325 | 0.003135 | 0.010557 | 0.027135 | -0.010177 | 0.043686 | 0.006374
4672.0469 | 122.3785 | -0.073242 | 122.2595 | 0.13101 | -0.035942 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.084531 | -0.050029 | -0.04722 | -0.044375 | 0.20425 | 0.0373 | 0.047507 | 0.048225 | 0.095773 | 0.14509 | 0.005947 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.038755 | -0.004253 | -0.001444 | 0.001401 | 0.036292 | -0.001019 | 0.043685 | 0.006374
4673.8281 | 122.4106 | -0.064087 | 122.2595 | 0.13559 | -0.035942 | -0.025735 | -0.025017 | 0.022531 | 0.067269 | -0.067295 | -0.052818 | 0.060902 | -0.045424 | -0.046838 | -0.066219 | -0.040873 | -0.060955 | -0.035219 | 0.19967 | 0.028145 | 0.038352 | 0.03907 | 0.086618 | 0.13136 | -0.003208 | -0.007042 | 0.10668 | 0.000352 | -0.001062 | -0.020443 | 0.004903 | -0.015179 | 0.010557 | 0.013401 | 0.008137 | 0.020795 | 0.015531
4675.5469 | 122.438 | -0.082397 | 122.2183 | 0.13101 | -0.035942 | -0.025735 | -0.029595 | 0.027109 | 0.067269 | -0.067295 | -0.057396 | 0.056323 | -0.040846 | -0.033101 | -0.075375 | -0.045451 | -0.042641 | -0.035219 | 0.21341 | 0.046455 | 0.056662 | 0.052802 | 0.10951 | 0.14967 | 0.015102 | -0.01162 | 0.1021 | 0.00493 | 0.012675 | -0.029599 | 0.000325 | 0.003135 | 0.010557 | 0.017979 | -0.014755 | 0.034529 | 0.001795
4677.3281 | 122.4472 | -0.054932 | 122.2458 | 0.13101 | -0.031363 | -0.025735 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | -0.057396 | 0.060902 | -0.040846 | -0.03768 | -0.075375 | -0.045451 | -0.051798 | -0.035219 | 0.18594 | 0.023569 | 0.029197 | 0.029915 | 0.077463 | 0.1222 | -0.007785 | -0.01162 | 0.10668 | 0.00493 | 0.008096 | -0.029599 | 0.000325 | -0.006022 | 0.010557 | 0.017979 | -0.005598 | 0.034529 | 0.010952
4679.1094 | 122.374 | -0.068665 | 122.2412 | 0.13101 | -0.035942 | -0.025735 | -0.034174 | 0.013375 | 0.071848 | -0.067295 | -0.057396 | 0.060902 | -0.040846 | -0.042259 | -0.079953 | -0.040873 | -0.051798 | -0.035219 | 0.19967 | 0.032723 | 0.04293 | 0.034491 | 0.08204 | 0.14051 | 0.00137 | -0.01162 | 0.10668 | 0.00493 | 0.003517 | -0.034177 | 0.004903 | -0.006022 | 0.010557 | 0.022557 | -0.005598 | 0.039107 | 0.010952
4680.8281 | 122.4152 | -0.054932 | 122.2321 | 0.13101 | -0.031363 | -0.025735 | -0.029595 | 0.022531 | 0.067269 | -0.067295 | -0.052818 | 0.060902 | -0.045424 | -0.042259 | -0.075375 | -0.050029 | -0.056376 | -0.035219 | 0.18594 | 0.023569 | 0.029197 | 0.025337 | 0.077463 | 0.1222 | -0.012363 | -0.007042 | 0.10668 | 0.000352 | 0.003517 | -0.029599 | -0.004253 | -0.0106 | 0.010557 | 0.022557 | 0.003558 | 0.029951 | 0.010952
4682.6094 | 122.2961 | -0.12817 | 122.2687 | 0.13559 | -0.031363 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.052818 | 0.056323 | -0.040846 | -0.042259 | -0.075375 | -0.045451 | -0.042641 | -0.035219 | 0.26376 | 0.096811 | 0.10244 | 0.10316 | 0.15071 | 0.20002 | 0.065457 | -0.007042 | 0.1021 | 0.00493 | 0.003517 | -0.029599 | 0.000325 | 0.003135 | 0.010557 | 0.022557 | -0.010177 | 0.034529 | 0.001795
4684.3906 | 122.3465 | -0.11444 | 122.2595 | 0.12643 | -0.040521 | -0.021157 | -0.029595 | 0.013375 | 0.067269 | -0.062717 | -0.048239 | 0.065481 | -0.050002 | -0.046838 | -0.070797 | -0.040873 | -0.051798 | -0.039797 | 0.24087 | 0.07392 | 0.093284 | 0.084846 | 0.12782 | 0.18171 | 0.051724 | -0.002463 | 0.11126 | -0.004226 | -0.001062 | -0.025021 | 0.004903 | -0.006022 | 0.005979 | 0.022558 | 0.003559 | 0.020795 | 0.001796
4686.1719 | 122.2778 | -0.10529 | 122.2549 | 0.13101 | -0.026784 | -0.030314 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.057396 | 0.060902 | -0.040846 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.035219 | 0.23629 | 0.078502 | 0.074972 | 0.080269 | 0.12782 | 0.17713 | 0.037991 | -0.01162 | 0.10668 | 0.00493 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.010557 | 0.027135 | -0.005598 | 0.043685 | 0.010952
4687.9531 | 122.4289 | -0.068665 | 122.2458 | 0.12643 | -0.026784 | -0.025735 | -0.029595 | 0.022531 | 0.062691 | -0.062717 | -0.052818 | 0.056323 | -0.040846 | -0.042259 | -0.075375 | -0.045451 | -0.051798 | -0.035219 | 0.19509 | 0.041881 | 0.04293 | 0.03907 | 0.091196 | 0.13136 | 0.005948 | -0.007042 | 0.1021 | 0.00493 | 0.003517 | -0.029599 | 0.000325 | -0.006022 | 0.010557 | 0.022557 | -0.00102 | 0.034529 | 0.010952
4689.6719 | 122.3007 | -0.10529 | 122.287 | 0.13101 | -0.031363 | -0.021157 | -0.025017 | 0.017953 | 0.071848 | -0.062717 | -0.043661 | 0.056323 | -0.045424 | -0.046838 | -0.079953 | -0.050029 | -0.051798 | -0.035219 | 0.23629 | 0.073923 | 0.084129 | 0.080269 | 0.12324 | 0.17713 | 0.042569 | 0.002115 | 0.1021 | 0.000352 | -0.001062 | -0.034177 | -0.004253 | -0.006022 | 0.010557 | 0.036292 | 0.008137 | 0.034529 | 0.006374
4691.375 | 122.4243 | -0.064087 | 122.2504 | 0.13101 | -0.031363 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.052818 | 0.060902 | -0.040846 | -0.042259 | -0.079953 | -0.045451 | -0.04722 | -0.039797 | 0.1951 | 0.032724 | 0.038352 | 0.034492 | 0.086618 | 0.13594 | -0.003208 | -0.007042 | 0.10668 | 0.00493 | 0.003517 | -0.034177 | 0.000325 | -0.001444 | 0.005979 | 0.027135 | -0.005598 | 0.039107 | 0.006374
4693.1562 | 122.3145 | -0.10071 | 122.2778 | 0.13559 | -0.031363 | -0.021157 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | -0.061975 | 0.051744 | -0.045424 | -0.03768 | -0.079953 | -0.050029 | -0.056376 | -0.035219 | 0.23629 | 0.069345 | 0.079551 | 0.075691 | 0.12324 | 0.16798 | 0.037991 | -0.016199 | 0.09752 | 0.000352 | 0.008096 | -0.034177 | -0.004253 | -0.0106 | 0.010557 | 0.017978 | -0.005599 | 0.034529 | 0.010952
4694.875 | 122.4335 | -0.054932 | 122.2412 | 0.13559 | -0.031363 | -0.030314 | -0.029595 | 0.013375 | 0.067269 | -0.067295 | -0.052818 | 0.060902 | -0.040846 | -0.046838 | -0.079953 | -0.045451 | -0.056376 | -0.035219 | 0.19052 | 0.023569 | 0.024618 | 0.025337 | 0.068307 | 0.1222 | -0.012363 | -0.007042 | 0.10668 | 0.00493 | -0.001062 | -0.034177 | 0.000325 | -0.0106 | 0.010557 | 0.027135 | 0.003558 | 0.039107 | 0.01553
4696.6406 | 122.4014 | -0.10071 | 122.2366 | 0.13101 | -0.031363 | -0.025735 | -0.025017 | 0.017953 | 0.062691 | -0.067295 | -0.052818 | 0.060902 | -0.050002 | -0.042259 | -0.075375 | -0.045451 | -0.051798 | -0.039797 | 0.23172 | 0.069345 | 0.074973 | 0.075691 | 0.11866 | 0.1634 | 0.033413 | -0.007042 | 0.10668 | -0.004226 | 0.003517 | -0.029599 | 0.000325 | -0.006022 | 0.005979 | 0.022557 | -0.00102 | 0.025373 | 0.001796
4698.4062 | 122.4243 | -0.068665 | 122.2504 | 0.13559 | -0.031363 | -0.025735 | -0.025017 | 0.013375 | 0.071848 | -0.062717 | -0.052818 | 0.056323 | -0.045424 | -0.03768 | -0.070797 | -0.045451 | -0.042641 | -0.030641 | 0.20425 | 0.037302 | 0.04293 | 0.043648 | 0.08204 | 0.14051 | 0.005948 | -0.007042 | 0.1021 | 0.000352 | 0.008096 | -0.025021 | 0.000325 | 0.003135 | 0.015135 | 0.017979 | -0.010177 | 0.025373 | -0.002783
4700.1094 | 122.3465 | -0.10529 | 122.2778 | 0.13101 | -0.035942 | -0.021157 | -0.025017 | 0.022531 | 0.067269 | -0.067295 | -0.052818 | 0.060902 | -0.031689 | -0.03768 | -0.079953 | -0.045451 | -0.056376 | -0.026063 | 0.23629 | 0.069344 | 0.084129 | 0.080269 | 0.12782 | 0.17256 | 0.037991 | -0.007042 | 0.10668 | 0.014087 | 0.008096 | -0.034177 | 0.000325 | -0.0106 | 0.019713 | 0.027135 | 0.003558 | 0.048264 | 0.024687
4701.875 | 122.2961 | -0.11902 | 122.287 | 0.13559 | -0.031363 | -0.030314 | -0.025017 | 0.017953 | 0.071848 | -0.067295 | -0.048239 | 0.060902 | -0.045424 | -0.042259 | -0.079953 | -0.040873 | -0.04722 | -0.030641 | 0.25461 | 0.087656 | 0.088705 | 0.094002 | 0.13697 | 0.19087 | 0.051724 | -0.002463 | 0.10668 | 0.000352 | 0.003517 | -0.034177 | 0.004903 | -0.001444 | 0.015135 | 0.031714 | -0.001019 | 0.034529 | 0.001796
4703.6406 | 122.406 | -0.068665 | 122.2458 | 0.12643 | -0.040521 | -0.034893 | -0.029595 | 0.022531 | 0.067269 | -0.062717 | -0.057396 | 0.060902 | -0.040846 | -0.051417 | -0.075375 | -0.054607 | -0.04722 | -0.026063 | 0.19509 | 0.028144 | 0.033772 | 0.03907 | 0.091196 | 0.13593 | 0.005948 | -0.01162 | 0.10668 | 0.00493 | -0.005641 | -0.029599 | -0.008831 | -0.001444 | 0.019713 | 0.017979 | -0.010176 | 0.034529 | 0.006374
4705.3438 | 122.4014 | -0.064087 | 122.2824 | 0.13101 | -0.031363 | -0.030314 | -0.029595 | 0.022531 | 0.067269 | -0.067295 | -0.057396 | 0.056323 | -0.045424 | -0.033101 | -0.075375 | -0.040873 | -0.051798 | -0.035219 | 0.1951 | 0.032724 | 0.033773 | 0.034492 | 0.086618 | 0.13136 | -0.003208 | -0.01162 | 0.1021 | 0.000352 | 0.012675 | -0.029599 | 0.004903 | -0.006022 | 0.010557 | 0.017979 | -0.005598 | 0.029951 | 0.006374
4707.125 | 122.438 | -0.045776 | 122.2549 | 0.13101 | -0.031363 | -0.030314 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.048239 | 0.056323 | -0.040846 | -0.042259 | -0.075375 | -0.045451 | -0.04722 | -0.030641 | 0.17678 | 0.014413 | 0.015462 | 0.020759 | 0.068307 | 0.11762 | -0.021519 | -0.002463 | 0.1021 | 0.00493 | 0.003517 | -0.029599 | 0.000325 | -0.001444 | 0.015135 | 0.027136 | -0.001019 | 0.034529 | 0.006374
4708.8438 | 122.3145 | -0.11902 | 122.2916 | 0.12643 | -0.035942 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.052818 | 0.060902 | -0.045424 | -0.042259 | -0.070797 | -0.045451 | -0.056376 | -0.035219 | 0.24545 | 0.083077 | 0.093284 | 0.094002 | 0.14155 | 0.19087 | 0.051724 | -0.007042 | 0.10668 | 0.000352 | 0.003517 | -0.025021 | 0.000325 | -0.0106 | 0.010557 | 0.017979 | 0.003558 | 0.025373 | 0.010952
4710.625 | 122.3648 | -0.10071 | 122.2916 | 0.12643 | -0.031363 | -0.025735 | -0.025017 | 0.017953 | 0.076426 | -0.071874 | -0.052818 | 0.060902 | -0.040846 | -0.03768 | -0.084531 | -0.045451 | -0.04722 | -0.035219 | 0.22714 | 0.069345 | 0.074973 | 0.075691 | 0.11866 | 0.17713 | 0.028834 | -0.007042 | 0.10668 | 0.00493 | 0.008096 | -0.038755 | 0.000325 | -0.001444 | 0.010557 | 0.031713 | -0.005598 | 0.043685 | 0.006374
4712.3438 | 122.3511 | -0.10529 | 122.3145 | 0.13559 | -0.031363 | -0.021157 | -0.025017 | 0.013375 | 0.076426 | -0.067295 | -0.048239 | 0.051744 | -0.040846 | -0.042259 | -0.070797 | -0.050029 | -0.04722 | -0.030641 | 0.24087 | 0.073923 | 0.084129 | 0.080269 | 0.11866 | 0.18171 | 0.037991 | -0.002463 | 0.09752 | 0.00493 | 0.003517 | -0.025021 | -0.004253 | -0.001444 | 0.015135 | 0.022558 | -0.001019 | 0.029951 | 0.006374
4714.1094 | 122.3328 | -0.10071 | 122.3053 | 0.13559 | -0.031363 | -0.021157 | -0.029595 | 0.022531 | 0.067269 | -0.067295 | -0.061975 | 0.060902 | -0.045424 | -0.046838 | -0.070797 | -0.054607 | -0.051798 | -0.035219 | 0.23629 | 0.069345 | 0.079551 | 0.071113 | 0.12324 | 0.16798 | 0.033413 | -0.016199 | 0.10668 | 0.000352 | -0.001062 | -0.025021 | -0.008831 | -0.006022 | 0.010557 | 0.008822 | -0.010177 | 0.025373 | 0.006374
4715.875 | 122.4152 | -0.073242 | 122.2961 | 0.13101 | -0.035942 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.048239 | 0.056323 | -0.045424 | -0.03768 | -0.079953 | -0.040873 | -0.04722 | -0.035219 | 0.20425 | 0.0373 | 0.047507 | 0.043647 | 0.095773 | 0.14509 | 0.005947 | -0.002463 | 0.1021 | 0.000352 | 0.008096 | -0.034177 | 0.004903 | -0.001444 | 0.010557 | 0.031714 | -0.001019 | 0.034529 | 0.001796
4717.6562 | 122.319 | -0.11444 | 122.2916 | 0.13559 | -0.035942 | -0.025735 | -0.029595 | 0.008797 | 0.067269 | -0.076452 | -0.057396 | 0.065481 | -0.040846 | -0.03768 | -0.075375 | -0.045451 | -0.04722 | -0.039797 | 0.25003 | 0.078499 | 0.088706 | 0.084846 | 0.12324 | 0.18171 | 0.037989 | -0.01162 | 0.11126 | 0.00493 | 0.008096 | -0.029599 | 0.000325 | -0.001444 | 0.005979 | 0.017979 | -0.010176 | 0.034529 | 0.006374
4719.375 | 122.3785 | -0.10529 | 122.3145 | 0.12643 | -0.026784 | -0.030314 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.043661 | 0.060902 | -0.040846 | -0.042259 | -0.079953 | -0.045451 | -0.04722 | -0.035219 | 0.23172 | 0.078502 | 0.074972 | 0.080269 | 0.12782 | 0.17713 | 0.037991 | 0.002115 | 0.10668 | 0.00493 | 0.003517 | -0.034177 | 0.000325 | -0.001444 | 0.010557 | 0.036292 | 0.003559 | 0.039107 | 0.006374
4721.1406 | 122.4426 | -0.068665 | 122.2961 | 0.13101 | -0.040521 | -0.025735 | -0.025017 | 0.017953 | 0.076426 | -0.067295 | -0.043661 | 0.060902 | -0.040846 | -0.042259 | -0.079953 | -0.040873 | -0.051798 | -0.035219 | 0.19967 | 0.028144 | 0.04293 | 0.043648 | 0.086618 | 0.14509 | 0.00137 | 0.002115 | 0.10668 | 0.00493 | 0.003517 | -0.034177 | 0.004903 | -0.006022 | 0.010557 | 0.036292 | 0.008137 | 0.039107 | 0.010952
4722.9219 | 122.4518 | -0.064087 | 122.2824 | 0.13559 | -0.031363 | -0.030314 | -0.029595 | 0.013375 | 0.071848 | -0.058139 | -0.052818 | 0.060902 | -0.040846 | -0.03768 | -0.084531 | -0.031717 | -0.04722 | -0.030641 | 0.19967 | 0.032724 | 0.033773 | 0.034492 | 0.077462 | 0.13594 | 0.005948 | -0.007042 | 0.10668 | 0.00493 | 0.008096 | -0.038755 | 0.014059 | -0.001444 | 0.015135 | 0.031713 | -0.005598 | 0.043685 | 0.006374
4724.6406 | 122.3419 | -0.11444 | 122.3099 | 0.13559 | -0.031363 | -0.030314 | -0.034174 | 0.027109 | 0.071848 | -0.067295 | -0.052818 | 0.060902 | -0.045424 | -0.03768 | -0.084531 | -0.050029 | -0.051798 | -0.039797 | 0.25003 | 0.083078 | 0.084127 | 0.080267 | 0.14155 | 0.18629 | 0.047146 | -0.007042 | 0.10668 | 0.000352 | 0.008096 | -0.038755 | -0.004253 | -0.006022 | 0.005979 | 0.031713 | -0.00102 | 0.039107 | 0.006374
4726.4062 | 122.4655 | -0.068665 | 122.2733 | 0.12643 | -0.031363 | -0.030314 | -0.029595 | 0.017953 | 0.067269 | -0.067295 | -0.052818 | 0.060902 | -0.045424 | -0.042259 | -0.079953 | -0.045451 | -0.042641 | -0.039797 | 0.19509 | 0.037302 | 0.038351 | 0.03907 | 0.086618 | 0.13593 | 0.00137 | -0.007042 | 0.10668 | 0.000352 | 0.003517 | -0.034177 | 0.000325 | 0.003135 | 0.005979 | 0.027135 | -0.010177 | 0.034529 | -0.002783
4728.1875 | 122.3465 | -0.10986 | 122.287 | 0.12643 | -0.040521 | -0.030314 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | -0.048239 | 0.060902 | -0.040846 | -0.046838 | -0.079953 | -0.045451 | -0.04722 | -0.035219 | 0.23629 | 0.069342 | 0.079549 | 0.084846 | 0.13239 | 0.17713 | 0.047146 | -0.002463 | 0.10668 | 0.00493 | -0.001062 | -0.034177 | 0.000325 | -0.001444 | 0.010557 | 0.031714 | -0.001019 | 0.039107 | 0.006374
4729.9062 | 122.4426 | -0.064087 | 122.2778 | 0.13101 | -0.031363 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.048239 | 0.060902 | -0.050002 | -0.046838 | -0.079953 | -0.040873 | -0.042641 | -0.030641 | 0.1951 | 0.032724 | 0.033773 | 0.034492 | 0.086618 | 0.13594 | -0.003208 | -0.002463 | 0.10668 | -0.004226 | -0.001062 | -0.034177 | 0.004903 | 0.003135 | 0.015135 | 0.031714 | -0.005598 | 0.029951 | -0.007361
4731.6719 | 122.4152 | -0.086975 | 122.287 | 0.12643 | -0.035942 | -0.030314 | -0.034174 | 0.013375 | 0.071848 | -0.071874 | -0.043661 | 0.051744 | -0.045424 | -0.042259 | -0.075375 | -0.045451 | -0.056376 | -0.039797 | 0.2134 | 0.051033 | 0.056661 | 0.052801 | 0.10035 | 0.15882 | 0.015101 | 0.002115 | 0.09752 | 0.000352 | 0.003517 | -0.029599 | 0.000325 | -0.0106 | 0.005979 | 0.031714 | 0.012715 | 0.029951 | 0.010952
4733.4375 | 122.4197 | -0.07782 | 122.319 | 0.13101 | -0.0451 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.052818 | 0.056323 | -0.045424 | -0.051417 | -0.079953 | -0.045451 | -0.04722 | -0.030641 | 0.20883 | 0.03272 | 0.052085 | 0.052803 | 0.10035 | 0.14967 | 0.010525 | -0.007042 | 0.1021 | 0.000352 | -0.005641 | -0.034177 | 0.000325 | -0.001444 | 0.015135 | 0.027135 | -0.005598 | 0.034529 | 0.001796
4735.2031 | 122.3099 | -0.10071 | 122.3282 | 0.13559 | -0.035942 | -0.030314 | -0.029595 | 0.017953 | 0.067269 | -0.067295 | -0.057396 | 0.056323 | -0.040846 | -0.03768 | -0.084531 | -0.045451 | -0.051798 | -0.044375 | 0.23629 | 0.064766 | 0.070394 | 0.071113 | 0.11866 | 0.16798 | 0.033413 | -0.01162 | 0.1021 | 0.00493 | 0.008096 | -0.038755 | 0.000325 | -0.006022 | 0.001401 | 0.027135 | -0.005598 | 0.043685 | 0.010952
4736.9688 | 122.4747 | -0.054932 | 122.2824 | 0.13101 | -0.035942 | -0.025735 | -0.029595 | 0.022531 | 0.062691 | -0.062717 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.084531 | -0.040873 | -0.051798 | -0.039797 | 0.18594 | 0.01899 | 0.029197 | 0.025337 | 0.077463 | 0.11762 | -0.007785 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.038755 | 0.004903 | -0.006022 | 0.005979 | 0.036292 | 0.003559 | 0.043685 | 0.010952
4738.75 | 122.4609 | -0.068665 | 122.2778 | 0.13101 | -0.035942 | -0.030314 | -0.034174 | 0.022531 | 0.062691 | -0.067295 | -0.052818 | 0.060902 | -0.040846 | -0.042259 | -0.075375 | -0.045451 | -0.042641 | -0.035219 | 0.19967 | 0.032723 | 0.038351 | 0.034491 | 0.091196 | 0.13136 | 0.00137 | -0.007042 | 0.10668 | 0.00493 | 0.003517 | -0.029599 | 0.000325 | 0.003135 | 0.010557 | 0.022557 | -0.010177 | 0.034529 | 0.001795
4740.4531 | 122.4747 | -0.059509 | 122.2824 | 0.13101 | -0.035942 | -0.030314 | -0.034174 | 0.022531 | 0.067269 | -0.062717 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.070797 | -0.040873 | -0.04722 | -0.030641 | 0.19052 | 0.023567 | 0.029195 | 0.025335 | 0.08204 | 0.12678 | -0.003208 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.025021 | 0.004903 | -0.001444 | 0.015135 | 0.022558 | -0.001019 | 0.029951 | 0.006374
4742.2188 | 122.4197 | -0.082397 | 122.2961 | 0.12643 | -0.035942 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.048239 | 0.056323 | -0.045424 | -0.046838 | -0.079953 | -0.045451 | -0.051798 | -0.035219 | 0.20883 | 0.046455 | 0.052083 | 0.052802 | 0.10493 | 0.15424 | 0.015102 | -0.002463 | 0.1021 | 0.000352 | -0.001062 | -0.034177 | 0.000325 | -0.006022 | 0.010557 | 0.031714 | 0.003559 | 0.034529 | 0.006374
4743.9375 | 122.4701 | -0.050354 | 122.2916 | 0.13101 | -0.040521 | -0.034893 | -0.034174 | 0.017953 | 0.067269 | -0.071874 | -0.057396 | 0.056323 | -0.040846 | -0.033101 | -0.075375 | -0.045451 | -0.051798 | -0.044375 | 0.18136 | 0.009833 | 0.015461 | 0.01618 | 0.068307 | 0.11762 | -0.02152 | -0.01162 | 0.1021 | 0.00493 | 0.012675 | -0.029599 | 0.000325 | -0.006022 | 0.001401 | 0.017979 | -0.005598 | 0.034529 | 0.010952
4745.7031 | 122.4518 | -0.068665 | 122.2961 | 0.14017 | -0.035942 | -0.025735 | -0.025017 | 0.027109 | 0.067269 | -0.067295 | -0.048239 | 0.060902 | -0.050002 | -0.042259 | -0.079953 | -0.050029 | -0.042641 | -0.035219 | 0.20883 | 0.032723 | 0.04293 | 0.043648 | 0.095774 | 0.13593 | 0.00137 | -0.002463 | 0.10668 | -0.004226 | 0.003517 | -0.034177 | -0.004253 | 0.003135 | 0.010557 | 0.031714 | -0.005598 | 0.029951 | -0.007361
4747.4688 | 122.3923 | -0.10986 | 122.3465 | 0.12643 | -0.040521 | -0.030314 | -0.034174 | 0.022531 | 0.062691 | -0.067295 | -0.052818 | 0.060902 | -0.050002 | -0.046838 | -0.075375 | -0.045451 | -0.04722 | -0.035219 | 0.23629 | 0.069342 | 0.079549 | 0.075689 | 0.13239 | 0.17255 | 0.042568 | -0.007042 | 0.10668 | -0.004226 | -0.001062 | -0.029599 | 0.000325 | -0.001444 | 0.010557 | 0.022557 | -0.005598 | 0.025373 | -0.002782
4749.1875 | 122.4747 | -0.064087 | 122.2916 | 0.13101 | -0.035942 | -0.030314 | -0.029595 | 0.017953 | 0.062691 | -0.067295 | -0.048239 | 0.051744 | -0.045424 | -0.042259 | -0.070797 | -0.045451 | -0.04722 | -0.039797 | 0.1951 | 0.028145 | 0.033773 | 0.034492 | 0.08204 | 0.12678 | -0.003208 | -0.002463 | 0.09752 | 0.000352 | 0.003517 | -0.025021 | 0.000325 | -0.001444 | 0.005979 | 0.022558 | -0.001019 | 0.025373 | 0.001796
4750.9688 | 122.4426 | -0.07782 | 122.3007 | 0.13101 | -0.040521 | -0.025735 | -0.025017 | 0.017953 | 0.062691 | -0.067295 | -0.052818 | 0.060902 | -0.045424 | -0.042259 | -0.075375 | -0.045451 | -0.04722 | -0.035219 | 0.20883 | 0.037299 | 0.052085 | 0.052803 | 0.095773 | 0.14051 | 0.010525 | -0.007042 | 0.10668 | 0.000352 | 0.003517 | -0.029599 | 0.000325 | -0.001444 | 0.010557 | 0.022557 | -0.005598 | 0.029951 | 0.001796
4752.6719 | 122.4197 | -0.086975 | 122.2961 | 0.13101 | -0.040521 | -0.030314 | -0.025017 | 0.017953 | 0.071848 | -0.062717 | -0.052818 | 0.056323 | -0.040846 | -0.03768 | -0.075375 | -0.045451 | -0.056376 | -0.044375 | 0.21798 | 0.046454 | 0.056661 | 0.061958 | 0.10493 | 0.15882 | 0.024258 | -0.007042 | 0.1021 | 0.00493 | 0.008096 | -0.029599 | 0.000325 | -0.0106 | 0.001401 | 0.022557 | 0.003558 | 0.034529 | 0.01553
4754.4375 | 122.4152 | -0.07782 | 122.2961 | 0.12643 | -0.035942 | -0.030314 | -0.029595 | 0.008797 | 0.067269 | -0.076452 | -0.057396 | 0.060902 | -0.050002 | -0.042259 | -0.075375 | -0.045451 | -0.04722 | -0.039797 | 0.20425 | 0.041878 | 0.047506 | 0.048225 | 0.086617 | 0.14509 | 0.001368 | -0.01162 | 0.10668 | -0.004226 | 0.003517 | -0.029599 | 0.000325 | -0.001444 | 0.005979 | 0.017979 | -0.010176 | 0.025373 | -0.002782
4756.1562 | 122.3557 | -0.10986 | 122.3328 | 0.13101 | -0.035942 | -0.025735 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | -0.057396 | 0.060902 | -0.040846 | -0.033101 | -0.075375 | -0.045451 | -0.04722 | -0.030641 | 0.24087 | 0.073921 | 0.084128 | 0.084846 | 0.13239 | 0.17713 | 0.047146 | -0.01162 | 0.10668 | 0.00493 | 0.012675 | -0.029599 | 0.000325 | -0.001444 | 0.015135 | 0.017979 | -0.010176 | 0.034529 | 0.006374
4757.9219 | 122.5159 | -0.068665 | 122.2961 | 0.13101 | -0.0451 | -0.034893 | -0.025017 | 0.022531 | 0.071848 | -0.058139 | -0.057396 | 0.065481 | -0.045424 | -0.03768 | -0.079953 | -0.040873 | -0.056376 | -0.039797 | 0.19967 | 0.023565 | 0.033772 | 0.043648 | 0.091196 | 0.14051 | 0.010526 | -0.01162 | 0.11126 | 0.000352 | 0.008096 | -0.034177 | 0.004903 | -0.0106 | 0.005979 | 0.022557 | -0.00102 | 0.034529 | 0.010952
4759.6406 | 122.3694 | -0.10986 | 122.3373 | 0.13101 | -0.035942 | -0.030314 | -0.025017 | 0.017953 | 0.067269 | -0.067295 | -0.052818 | 0.065481 | -0.045424 | -0.042259 | -0.079953 | -0.040873 | -0.056376 | -0.030641 | 0.24087 | 0.073921 | 0.079549 | 0.084846 | 0.12782 | 0.17713 | 0.042568 | -0.007042 | 0.11126 | 0.000352 | 0.003517 | -0.034177 | 0.004903 | -0.0106 | 0.015135 | 0.027135 | 0.003558 | 0.034529 | 0.010952
4761.4062 | 122.4884 | -0.068665 | 122.3007 | 0.12643 | -0.026784 | -0.021157 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.052818 | 0.056323 | -0.05458 | -0.03768 | -0.079953 | -0.040873 | -0.051798 | -0.030641 | 0.19509 | 0.041881 | 0.047508 | 0.03907 | 0.091196 | 0.14051 | 0.00137 | -0.007042 | 0.1021 | -0.008804 | 0.008096 | -0.034177 | 0.004903 | -0.006022 | 0.015135 | 0.027135 | -0.00102 | 0.025373 | -0.002782
4763.1719 | 122.4609 | -0.073242 | 122.3053 | 0.12643 | -0.035942 | -0.025735 | -0.029595 | 0.022531 | 0.067269 | -0.062717 | -0.061975 | 0.056323 | -0.045424 | -0.03768 | -0.070797 | -0.045451 | -0.051798 | -0.035219 | 0.19967 | 0.0373 | 0.047507 | 0.043647 | 0.095773 | 0.14051 | 0.010525 | -0.016199 | 0.1021 | 0.000352 | 0.008096 | -0.025021 | 0.000325 | -0.006022 | 0.010557 | 0.008822 | -0.010177 | 0.025373 | 0.006374
4764.9375 | 122.493 | -0.050354 | 122.3099 | 0.13101 | -0.035942 | -0.030314 | -0.025017 | 0.017953 | 0.071848 | -0.067295 | -0.043661 | 0.056323 | -0.040846 | -0.03768 | -0.075375 | -0.045451 | -0.056376 | -0.030641 | 0.18136 | 0.014412 | 0.02004 | 0.025337 | 0.068307 | 0.1222 | -0.016941 | 0.002115 | 0.1021 | 0.00493 | 0.008096 | -0.029599 | 0.000325 | -0.0106 | 0.015135 | 0.031714 | 0.012715 | 0.034529 | 0.01553
4766.6562 | 122.3648 | -0.10986 | 122.3465 | 0.12643 | -0.040521 | -0.034893 | -0.025017 | 0.022531 | 0.067269 | -0.067295 | -0.052818 | 0.060902 | -0.040846 | -0.042259 | -0.079953 | -0.054607 | -0.04722 | -0.035219 | 0.23629 | 0.069342 | 0.07497 | 0.084846 | 0.13239 | 0.17713 | 0.042568 | -0.007042 | 0.10668 | 0.00493 | 0.003517 | -0.034177 | -0.008831 | -0.001444 | 0.010557 | 0.027135 | -0.005598 | 0.039107 | 0.006374
4768.4375 | 122.374 | -0.10986 | 122.3282 | 0.13559 | -0.026784 | -0.030314 | -0.025017 | 0.017953 | 0.071848 | -0.067295 | -0.061975 | 0.060902 | -0.040846 | -0.03768 | -0.070797 | -0.045451 | -0.056376 | -0.030641 | 0.24545 | 0.083079 | 0.079549 | 0.084846 | 0.12782 | 0.18171 | 0.042568 | -0.016199 | 0.10668 | 0.00493 | 0.008096 | -0.025021 | 0.000325 | -0.0106 | 0.015135 | 0.008822 | -0.005599 | 0.029951 | 0.01553
4770.2031 | 122.4518 | -0.073242 | 122.2961 | 0.13559 | -0.040521 | -0.030314 | -0.029595 | 0.027109 | 0.062691 | -0.062717 | -0.052818 | 0.051744 | -0.045424 | -0.046838 | -0.079953 | -0.045451 | -0.04722 | -0.035219 | 0.20883 | 0.032721 | 0.042928 | 0.043647 | 0.10035 | 0.13593 | 0.010525 | -0.007042 | 0.09752 | 0.000352 | -0.001062 | -0.034177 | 0.000325 | -0.001444 | 0.010557 | 0.027135 | -0.005598 | 0.034529 | 0.001796
4771.9844 | 122.438 | -0.086975 | 122.3328 | 0.13101 | -0.040521 | -0.030314 | -0.034174 | 0.013375 | 0.062691 | -0.067295 | -0.048239 | 0.056323 | -0.040846 | -0.042259 | -0.079953 | -0.040873 | -0.042641 | -0.030641 | 0.21798 | 0.046454 | 0.056661 | 0.052801 | 0.10035 | 0.14967 | 0.01968 | -0.002463 | 0.1021 | 0.00493 | 0.003517 | -0.034177 | 0.004903 | 0.003135 | 0.015135 | 0.031714 | -0.005598 | 0.039107 | 0.001795
4773.7656 | 122.4609 | -0.059509 | 122.319 | 0.13101 | -0.040521 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.071874 | -0.043661 | 0.056323 | -0.05458 | -0.042259 | -0.075375 | -0.040873 | -0.04722 | -0.035219 | 0.19052 | 0.018988 | 0.029195 | 0.029914 | 0.08204 | 0.13136 | -0.012365 | 0.002115 | 0.1021 | -0.008804 | 0.003517 | -0.029599 | 0.004903 | -0.001444 | 0.010557 | 0.031714 | 0.003559 | 0.020795 | -0.00736
4775.4688 | 122.4976 | -0.064087 | 122.3145 | 0.13559 | -0.026784 | -0.030314 | -0.029595 | 0.017953 | 0.062691 | -0.067295 | -0.057396 | 0.060902 | -0.040846 | -0.046838 | -0.075375 | -0.036295 | -0.056376 | -0.044375 | 0.19967 | 0.037303 | 0.033773 | 0.034492 | 0.08204 | 0.12678 | -0.003208 | -0.01162 | 0.10668 | 0.00493 | -0.001062 | -0.029599 | 0.009481 | -0.0106 | 0.001401 | 0.017979 | -0.00102 | 0.034529 | 0.01553
4777.2344 | 122.4106 | -0.10529 | 122.3373 | 0.14017 | -0.040521 | -0.030314 | -0.020438 | 0.022531 | 0.076426 | -0.067295 | -0.052818 | 0.056323 | -0.040846 | -0.042259 | -0.075375 | -0.050029 | -0.04722 | -0.039797 | 0.24545 | 0.064765 | 0.074972 | 0.084848 | 0.12782 | 0.18171 | 0.037991 | -0.007042 | 0.1021 | 0.00493 | 0.003517 | -0.029599 | -0.004253 | -0.001444 | 0.005979 | 0.022557 | -0.005598 | 0.034529 | 0.006374
4778.9531 | 122.4518 | -0.07782 | 122.3145 | 0.13101 | -0.035942 | -0.025735 | -0.029595 | 0.013375 | 0.071848 | -0.062717 | -0.052818 | 0.060902 | -0.040846 | -0.042259 | -0.079953 | -0.045451 | -0.051798 | -0.039797 | 0.20883 | 0.041878 | 0.052085 | 0.048225 | 0.091195 | 0.14967 | 0.015103 | -0.007042 | 0.10668 | 0.00493 | 0.003517 | -0.034177 | 0.000325 | -0.006022 | 0.005979 | 0.027135 | -0.00102 | 0.039107 | 0.010952
4780.7188 | 122.3785 | -0.11444 | 122.3557 | 0.13101 | -0.040521 | -0.030314 | -0.025017 | 0.017953 | 0.071848 | -0.067295 | -0.052818 | 0.051744 | -0.045424 | -0.042259 | -0.079953 | -0.045451 | -0.04722 | -0.035219 | 0.24545 | 0.07392 | 0.084127 | 0.089424 | 0.13239 | 0.18629 | 0.047146 | -0.007042 | 0.09752 | 0.000352 | 0.003517 | -0.034177 | 0.000325 | -0.001444 | 0.010557 | 0.027135 | -0.005598 | 0.034529 | 0.001796
4782.4844 | 122.3557 | -0.11444 | 122.3648 | 0.12643 | -0.035942 | -0.025735 | -0.029595 | 0.017953 | 0.062691 | -0.062717 | -0.048239 | 0.056323 | -0.040846 | -0.03768 | -0.075375 | -0.045451 | -0.051798 | -0.039797 | 0.24087 | 0.078499 | 0.088706 | 0.084846 | 0.13239 | 0.17713 | 0.051724 | -0.002463 | 0.1021 | 0.00493 | 0.008096 | -0.029599 | 0.000325 | -0.006022 | 0.005979 | 0.027136 | 0.003559 | 0.034529 | 0.010952
4784.25 | 122.4609 | -0.09613 | 122.3282 | 0.13101 | -0.0451 | -0.025735 | -0.029595 | 0.027109 | 0.067269 | -0.067295 | -0.043661 | 0.065481 | -0.045424 | -0.03768 | -0.075375 | -0.045451 | -0.051798 | -0.035219 | 0.22714 | 0.05103 | 0.070395 | 0.066535 | 0.12324 | 0.1634 | 0.028835 | 0.002115 | 0.11126 | 0.000352 | 0.008096 | -0.029599 | 0.000325 | -0.006022 | 0.010557 | 0.031714 | 0.008137 | 0.029951 | 0.006374
4785.9531 | 122.4655 | -0.073242 | 122.3419 | 0.12643 | -0.040521 | -0.030314 | -0.020438 | 0.017953 | 0.067269 | -0.058139 | -0.057396 | 0.056323 | -0.036267 | -0.042259 | -0.075375 | -0.045451 | -0.056376 | -0.035219 | 0.19967 | 0.032721 | 0.042928 | 0.052804 | 0.091195 | 0.14051 | 0.015103 | -0.01162 | 0.1021 | 0.009509 | 0.003517 | -0.029599 | 0.000325 | -0.0106 | 0.010557 | 0.017979 | -0.00102 | 0.039108 | 0.020109
4787.7188 | 122.4884 | -0.10071 | 122.3236 | 0.13559 | -0.040521 | -0.021157 | -0.029595 | 0.013375 | 0.067269 | -0.071874 | -0.057396 | 0.065481 | -0.045424 | -0.03768 | -0.075375 | -0.045451 | -0.051798 | -0.035219 | 0.23629 | 0.060187 | 0.079551 | 0.071113 | 0.11408 | 0.16798 | 0.028834 | -0.01162 | 0.11126 | 0.000352 | 0.008096 | -0.029599 | 0.000325 | -0.006022 | 0.010557 | 0.017979 | -0.005598 | 0.029951 | 0.006374
4789.4844 | 122.5342 | -0.068665 | 122.3099 | 0.12643 | -0.040521 | -0.021157 | -0.025017 | 0.017953 | 0.067269 | -0.067295 | -0.052818 | 0.056323 | -0.040846 | -0.03768 | -0.075375 | -0.040873 | -0.051798 | -0.035219 | 0.19509 | 0.028144 | 0.047508 | 0.043648 | 0.086618 | 0.13593 | 0.00137 | -0.007042 | 0.1021 | 0.00493 | 0.008096 | -0.029599 | 0.004903 | -0.006022 | 0.010557 | 0.022557 | -0.00102 | 0.034529 | 0.010952
4791.2656 | 122.4335 | -0.10071 | 122.3648 | 0.13559 | -0.040521 | -0.025735 | -0.020438 | 0.017953 | 0.071848 | -0.067295 | -0.057396 | 0.056323 | -0.045424 | -0.042259 | -0.075375 | -0.045451 | -0.042641 | -0.035219 | 0.23629 | 0.060187 | 0.074973 | 0.08027 | 0.11866 | 0.17256 | 0.033413 | -0.01162 | 0.1021 | 0.000352 | 0.003517 | -0.029599 | 0.000325 | 0.003135 | 0.010557 | 0.017979 | -0.014755 | 0.029951 | -0.002783
4793.0469 | 122.4197 | -0.09613 | 122.3648 | 0.13101 | -0.040521 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.052818 | 0.056323 | -0.045424 | -0.046838 | -0.075375 | -0.036295 | -0.056376 | -0.035219 | 0.22714 | 0.055609 | 0.070395 | 0.071113 | 0.11866 | 0.16798 | 0.033413 | -0.007042 | 0.1021 | 0.000352 | -0.001062 | -0.029599 | 0.009481 | -0.0106 | 0.010557 | 0.022557 | 0.003558 | 0.029951 | 0.010952
4794.75 | 122.5067 | -0.073242 | 122.3145 | 0.12643 | -0.035942 | -0.030314 | -0.025017 | 0.017953 | 0.071848 | -0.062717 | -0.052818 | 0.056323 | -0.040846 | -0.03768 | -0.075375 | -0.040873 | -0.051798 | -0.039797 | 0.19967 | 0.0373 | 0.042928 | 0.048225 | 0.091195 | 0.14509 | 0.010525 | -0.007042 | 0.1021 | 0.00493 | 0.008096 | -0.029599 | 0.004903 | -0.006022 | 0.005979 | 0.022557 | -0.00102 | 0.034529 | 0.010952
4796.5312 | 122.4518 | -0.07782 | 122.3373 | 0.13101 | -0.035942 | -0.030314 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.048239 | 0.060902 | -0.050002 | -0.03768 | -0.075375 | -0.045451 | -0.051798 | -0.035219 | 0.20883 | 0.041878 | 0.047506 | 0.052803 | 0.10035 | 0.14967 | 0.010525 | -0.002463 | 0.10668 | -0.004226 | 0.008096 | -0.029599 | 0.000325 | -0.006022 | 0.010557 | 0.027136 | 0.003559 | 0.025373 | 0.001796
4798.2344 | 122.4655 | -0.073242 | 122.3099 | 0.12643 | -0.035942 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.057396 | 0.051744 | -0.045424 | -0.042259 | -0.075375 | -0.036295 | -0.04722 | -0.030641 | 0.19967 | 0.0373 | 0.042928 | 0.043647 | 0.095773 | 0.14509 | 0.005947 | -0.01162 | 0.09752 | 0.000352 | 0.003517 | -0.029599 | 0.009481 | -0.001444 | 0.015135 | 0.017979 | -0.010176 | 0.029951 | 0.001796
4800.0156 | 122.5159 | -0.064087 | 122.3328 | 0.13559 | -0.035942 | -0.030314 | -0.020438 | 0.013375 | 0.067269 | -0.071874 | -0.057396 | 0.060902 | -0.045424 | -0.042259 | -0.079953 | -0.040873 | -0.04722 | -0.035219 | 0.19967 | 0.028145 | 0.033773 | 0.043649 | 0.077462 | 0.13136 | -0.007787 | -0.01162 | 0.10668 | 0.000352 | 0.003517 | -0.034177 | 0.004903 | -0.001444 | 0.010557 | 0.022557 | -0.010176 | 0.034529 | 0.001796
4801.7344 | 122.4106 | -0.091553 | 122.3694 | 0.13101 | -0.040521 | -0.030314 | -0.025017 | 0.013375 | 0.071848 | -0.062717 | -0.052818 | 0.051744 | -0.036267 | -0.042259 | -0.079953 | -0.045451 | -0.042641 | -0.035219 | 0.22256 | 0.051032 | 0.061239 | 0.066536 | 0.10493 | 0.1634 | 0.028836 | -0.007042 | 0.09752 | 0.009509 | 0.003517 | -0.034177 | 0.000325 | 0.003135 | 0.010557 | 0.027135 | -0.010177 | 0.043686 | 0.006374
4803.5 | 122.4976 | -0.059509 | 122.3373 | 0.13101 | -0.026784 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.048239 | 0.060902 | -0.045424 | -0.033101 | -0.079953 | -0.045451 | -0.056376 | -0.039797 | 0.19052 | 0.032725 | 0.033774 | 0.034492 | 0.08204 | 0.13136 | -0.007786 | -0.002463 | 0.10668 | 0.000352 | 0.012675 | -0.034177 | 0.000325 | -0.0106 | 0.005979 | 0.031714 | 0.008137 | 0.034529 | 0.010952
4805.2812 | 122.3877 | -0.11902 | 122.3557 | 0.13101 | -0.0451 | -0.025735 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | -0.061975 | 0.056323 | -0.045424 | -0.033101 | -0.070797 | -0.050029 | -0.051798 | -0.035219 | 0.25003 | 0.073919 | 0.093284 | 0.094002 | 0.14155 | 0.18629 | 0.056302 | -0.016199 | 0.1021 | 0.000352 | 0.012675 | -0.025021 | -0.004253 | -0.006022 | 0.010557 | 0.008822 | -0.010177 | 0.025373 | 0.006374
4807.0625 | 122.406 | -0.09613 | 122.3602 | 0.13101 | -0.040521 | -0.030314 | -0.020438 | 0.022531 | 0.067269 | -0.067295 | -0.057396 | 0.060902 | -0.036267 | -0.03768 | -0.084531 | -0.045451 | -0.051798 | -0.039797 | 0.22714 | 0.055609 | 0.065816 | 0.075692 | 0.11866 | 0.1634 | 0.028835 | -0.01162 | 0.10668 | 0.009509 | 0.008096 | -0.038755 | 0.000325 | -0.006022 | 0.005979 | 0.027135 | -0.005598 | 0.048264 | 0.015531
4808.7656 | 122.5388 | -0.064087 | 122.3465 | 0.13559 | -0.035942 | -0.030314 | -0.029595 | 0.013375 | 0.067269 | -0.067295 | -0.052818 | 0.065481 | -0.040846 | -0.033101 | -0.079953 | -0.045451 | -0.042641 | -0.035219 | 0.19967 | 0.028145 | 0.033773 | 0.034492 | 0.077462 | 0.13136 | -0.003208 | -0.007042 | 0.11126 | 0.00493 | 0.012675 | -0.034177 | 0.000325 | 0.003135 | 0.010557 | 0.027135 | -0.010177 | 0.039107 | 0.001795
4810.5312 | 122.5204 | -0.050354 | 122.3511 | 0.13101 | -0.040521 | -0.025735 | -0.029595 | 0.017953 | 0.062691 | -0.067295 | -0.048239 | 0.060902 | -0.045424 | -0.03768 | -0.075375 | -0.045451 | -0.056376 | -0.026063 | 0.18136 | 0.009833 | 0.024619 | 0.020759 | 0.068307 | 0.11305 | -0.016941 | -0.002463 | 0.10668 | 0.000352 | 0.008096 | -0.029599 | 0.000325 | -0.0106 | 0.019713 | 0.027136 | 0.008137 | 0.029951 | 0.010952
4812.2969 | 122.5159 | -0.054932 | 122.3236 | 0.13101 | -0.035942 | -0.030314 | -0.029595 | 0.013375 | 0.062691 | -0.071874 | -0.057396 | 0.060902 | -0.045424 | -0.03768 | -0.070797 | -0.045451 | -0.051798 | -0.035219 | 0.18594 | 0.01899 | 0.024618 | 0.025337 | 0.068307 | 0.11762 | -0.016942 | -0.01162 | 0.10668 | 0.000352 | 0.008096 | -0.025021 | 0.000325 | -0.006022 | 0.010557 | 0.013401 | -0.005598 | 0.025373 | 0.006374
4814.0156 | 122.4014 | -0.10986 | 122.3694 | 0.13559 | -0.035942 | -0.025735 | -0.034174 | 0.022531 | 0.067269 | -0.067295 | -0.052818 | 0.056323 | -0.045424 | -0.042259 | -0.079953 | -0.045451 | -0.051798 | -0.039797 | 0.24545 | 0.073921 | 0.084128 | 0.075689 | 0.13239 | 0.17713 | 0.042568 | -0.007042 | 0.1021 | 0.000352 | 0.003517 | -0.034177 | 0.000325 | -0.006022 | 0.005979 | 0.027135 | -0.00102 | 0.034529 | 0.006374
4815.7812 | 122.4884 | -0.073242 | 122.3511 | 0.12643 | -0.040521 | -0.030314 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.048239 | 0.056323 | -0.045424 | -0.042259 | -0.079953 | -0.040873 | -0.042641 | -0.044375 | 0.19967 | 0.032721 | 0.042928 | 0.048225 | 0.095773 | 0.14509 | 0.010525 | -0.002463 | 0.1021 | 0.000352 | 0.003517 | -0.034177 | 0.004903 | 0.003135 | 0.001401 | 0.031714 | -0.005598 | 0.034529 | -0.002783
4817.5469 | 122.3923 | -0.11444 | 122.3785 | 0.13559 | -0.035942 | -0.030314 | -0.020438 | 0.013375 | 0.076426 | -0.071874 | -0.057396 | 0.060902 | -0.036267 | -0.03768 | -0.075375 | -0.040873 | -0.051798 | -0.044375 | 0.25003 | 0.078499 | 0.084127 | 0.094003 | 0.12782 | 0.19087 | 0.042567 | -0.01162 | 0.10668 | 0.009509 | 0.008096 | -0.029599 | 0.004903 | -0.006022 | 0.001401 | 0.017979 | -0.005598 | 0.039108 | 0.015531
4819.3281 | 122.4701 | -0.073242 | 122.3511 | 0.12643 | -0.035942 | -0.025735 | -0.029595 | 0.013375 | 0.062691 | -0.067295 | -0.052818 | 0.056323 | -0.040846 | -0.042259 | -0.079953 | -0.040873 | -0.042641 | -0.039797 | 0.19967 | 0.0373 | 0.047507 | 0.043647 | 0.086617 | 0.13593 | 0.005947 | -0.007042 | 0.1021 | 0.00493 | 0.003517 | -0.034177 | 0.004903 | 0.003135 | 0.005979 | 0.027135 | -0.010177 | 0.039107 | 0.001795
4821.1094 | 122.5388 | -0.054932 | 122.3373 | 0.13559 | -0.040521 | -0.030314 | -0.029595 | 0.017953 | 0.071848 | -0.067295 | -0.057396 | 0.060902 | -0.036267 | -0.042259 | -0.079953 | -0.054607 | -0.051798 | -0.035219 | 0.19052 | 0.014411 | 0.024618 | 0.025337 | 0.072885 | 0.12678 | -0.012363 | -0.01162 | 0.10668 | 0.009509 | 0.003517 | -0.034177 | -0.008831 | -0.006022 | 0.010557 | 0.022557 | -0.005598 | 0.043686 | 0.015531
4822.8281 | 122.4701 | -0.073242 | 122.3831 | 0.12643 | -0.0451 | -0.030314 | -0.025017 | 0.022531 | 0.067269 | -0.076452 | -0.057396 | 0.060902 | -0.040846 | -0.046838 | -0.079953 | -0.040873 | -0.051798 | -0.039797 | 0.19967 | 0.028142 | 0.042928 | 0.048225 | 0.095773 | 0.14051 | -0.00321 | -0.01162 | 0.10668 | 0.00493 | -0.001062 | -0.034177 | 0.004903 | -0.006022 | 0.005979 | 0.022557 | -0.005598 | 0.039107 | 0.010952
4824.6094 | 122.4609 | -0.091553 | 122.374 | 0.12643 | -0.040521 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.057396 | 0.060902 | -0.045424 | -0.042259 | -0.079953 | -0.040873 | -0.051798 | -0.035219 | 0.21798 | 0.051032 | 0.061239 | 0.061958 | 0.11408 | 0.1634 | 0.024258 | -0.01162 | 0.10668 | 0.000352 | 0.003517 | -0.034177 | 0.004903 | -0.006022 | 0.010557 | 0.022557 | -0.005598 | 0.034529 | 0.006374
4826.375 | 122.4243 | -0.09613 | 122.3969 | 0.13101 | -0.040521 | -0.016578 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.057396 | 0.060902 | -0.040846 | -0.042259 | -0.079953 | -0.040873 | -0.04722 | -0.035219 | 0.22714 | 0.055609 | 0.079552 | 0.066535 | 0.11866 | 0.16798 | 0.028835 | -0.01162 | 0.10668 | 0.00493 | 0.003517 | -0.034177 | 0.004903 | -0.001444 | 0.010557 | 0.022557 | -0.010176 | 0.039107 | 0.006374
4828.0781 | 122.4014 | -0.10071 | 122.374 | 0.13101 | -0.035942 | -0.025735 | -0.025017 | 0.022531 | 0.062691 | -0.067295 | -0.048239 | 0.060902 | -0.045424 | -0.03768 | -0.075375 | -0.050029 | -0.056376 | -0.039797 | 0.23172 | 0.064766 | 0.074973 | 0.075691 | 0.12324 | 0.1634 | 0.033413 | -0.002463 | 0.10668 | 0.000352 | 0.008096 | -0.029599 | -0.004253 | -0.0106 | 0.005979 | 0.027136 | 0.008137 | 0.029951 | 0.010952
4829.8438 | 122.3923 | -0.11444 | 122.4014 | 0.13559 | -0.040521 | -0.025735 | -0.025017 | 0.013375 | 0.076426 | -0.067295 | -0.052818 | 0.056323 | -0.040846 | -0.046838 | -0.075375 | -0.040873 | -0.051798 | -0.035219 | 0.25003 | 0.07392 | 0.088706 | 0.089424 | 0.12782 | 0.19087 | 0.047146 | -0.007042 | 0.1021 | 0.00493 | -0.001062 | -0.029599 | 0.004903 | -0.006022 | 0.010557 | 0.022557 | -0.00102 | 0.034529 | 0.010952
4831.625 | 122.4838 | -0.073242 | 122.3419 | 0.13559 | -0.0451 | -0.025735 | -0.025017 | 0.017953 | 0.062691 | -0.067295 | -0.057396 | 0.060902 | -0.045424 | -0.046838 | -0.084531 | -0.040873 | -0.04722 | -0.030641 | 0.20883 | 0.028142 | 0.047507 | 0.048225 | 0.091195 | 0.13593 | 0.005947 | -0.01162 | 0.10668 | 0.000352 | -0.001062 | -0.038755 | 0.004903 | -0.001444 | 0.015135 | 0.027135 | -0.010176 | 0.039107 | 0.001796
4833.3906 | 122.4655 | -0.10071 | 122.3694 | 0.13559 | -0.035942 | -0.021157 | -0.020438 | 0.022531 | 0.071848 | -0.071874 | -0.061975 | 0.056323 | -0.045424 | -0.042259 | -0.079953 | -0.045451 | -0.04722 | -0.035219 | 0.23629 | 0.064766 | 0.079551 | 0.08027 | 0.12324 | 0.17256 | 0.028834 | -0.016199 | 0.1021 | 0.000352 | 0.003517 | -0.034177 | 0.000325 | -0.001444 | 0.010557 | 0.017978 | -0.014755 | 0.034529 | 0.001796
4835.1094 | 122.5433 | -0.064087 | 122.3465 | 0.13559 | -0.035942 | -0.030314 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.057396 | 0.060902 | -0.050002 | -0.03768 | -0.084531 | -0.045451 | -0.04722 | -0.039797 | 0.19967 | 0.028145 | 0.033773 | 0.03907 | 0.086618 | 0.13594 | 0.00137 | -0.01162 | 0.10668 | -0.004226 | 0.008096 | -0.038755 | 0.000325 | -0.001444 | 0.005979 | 0.027135 | -0.010176 | 0.034529 | -0.002782
4836.875 | 122.4472 | -0.11444 | 122.3969 | 0.13101 | -0.040521 | -0.025735 | -0.025017 | 0.017953 | 0.071848 | -0.062717 | -0.052818 | 0.056323 | -0.050002 | -0.046838 | -0.066219 | -0.040873 | -0.056376 | -0.035219 | 0.24545 | 0.07392 | 0.088706 | 0.089424 | 0.13239 | 0.18629 | 0.051724 | -0.007042 | 0.1021 | -0.004226 | -0.001062 | -0.020443 | 0.004903 | -0.0106 | 0.010557 | 0.013401 | 0.003558 | 0.016217 | 0.006374
4838.5781 | 122.5342 | -0.054932 | 122.3694 | 0.12643 | -0.035942 | -0.025735 | -0.025017 | 0.017953 | 0.067269 | -0.067295 | -0.052818 | 0.056323 | -0.045424 | -0.042259 | -0.079953 | -0.050029 | -0.051798 | -0.035219 | 0.18136 | 0.01899 | 0.029197 | 0.029915 | 0.072885 | 0.1222 | -0.012363 | -0.007042 | 0.1021 | 0.000352 | 0.003517 | -0.034177 | -0.004253 | -0.006022 | 0.010557 | 0.027135 | -0.00102 | 0.034529 | 0.006374
4840.3594 | 122.5571 | -0.064087 | 122.3557 | 0.13559 | -0.035942 | -0.021157 | -0.020438 | 0.022531 | 0.071848 | -0.067295 | -0.052818 | 0.051744 | -0.036267 | -0.042259 | -0.075375 | -0.040873 | -0.051798 | -0.035219 | 0.19967 | 0.028145 | 0.04293 | 0.043649 | 0.086618 | 0.13594 | -0.003208 | -0.007042 | 0.09752 | 0.009509 | 0.003517 | -0.029599 | 0.004903 | -0.006022 | 0.010557 | 0.022557 | -0.00102 | 0.039108 | 0.015531
4842.0781 | 122.4197 | -0.11902 | 122.3648 | 0.13559 | -0.035942 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.052818 | 0.047165 | -0.050002 | -0.03768 | -0.075375 | -0.040873 | -0.04722 | -0.035219 | 0.25461 | 0.083077 | 0.088705 | 0.089424 | 0.14155 | 0.19087 | 0.056302 | -0.007042 | 0.092941 | -0.004226 | 0.008096 | -0.029599 | 0.004903 | -0.001444 | 0.010557 | 0.022557 | -0.005598 | 0.025373 | -0.002782
4843.875 | 122.4335 | -0.10529 | 122.4014 | 0.13559 | -0.040521 | -0.039471 | -0.025017 | 0.022531 | 0.081005 | -0.071874 | -0.052818 | 0.07006 | -0.040846 | -0.03768 | -0.084531 | -0.045451 | -0.051798 | -0.035219 | 0.24087 | 0.064765 | 0.065815 | 0.080269 | 0.12782 | 0.18629 | 0.033412 | -0.007042 | 0.11584 | 0.00493 | 0.008096 | -0.038755 | 0.000325 | -0.006022 | 0.010557 | 0.031713 | -0.00102 | 0.043685 | 0.010952
4845.6406 | 122.4014 | -0.11902 | 122.3877 | 0.12643 | -0.0451 | -0.030314 | -0.029595 | 0.022531 | 0.067269 | -0.067295 | -0.057396 | 0.060902 | -0.040846 | -0.042259 | -0.079953 | -0.040873 | -0.04722 | -0.035219 | 0.24545 | 0.073919 | 0.088705 | 0.089424 | 0.14155 | 0.18629 | 0.051724 | -0.01162 | 0.10668 | 0.00493 | 0.003517 | -0.034177 | 0.004903 | -0.001444 | 0.010557 | 0.022557 | -0.010176 | 0.039107 | 0.006374
4847.3594 | 122.4518 | -0.091553 | 122.3831 | 0.13559 | -0.040521 | -0.034893 | -0.020438 | 0.022531 | 0.076426 | -0.062717 | -0.048239 | 0.060902 | -0.045424 | -0.03768 | -0.075375 | -0.050029 | -0.04722 | -0.030641 | 0.22714 | 0.051032 | 0.05666 | 0.071115 | 0.11408 | 0.16798 | 0.028836 | -0.002463 | 0.10668 | 0.000352 | 0.008096 | -0.029599 | -0.004253 | -0.001444 | 0.015135 | 0.027136 | -0.001019 | 0.029951 | 0.001796
4849.1562 | 122.5525 | -0.073242 | 122.3373 | 0.13559 | -0.035942 | -0.021157 | -0.034174 | 0.022531 | 0.076426 | -0.067295 | -0.057396 | 0.051744 | -0.040846 | -0.03768 | -0.079953 | -0.045451 | -0.051798 | -0.030641 | 0.20883 | 0.0373 | 0.052085 | 0.039068 | 0.095773 | 0.14967 | 0.005947 | -0.01162 | 0.09752 | 0.00493 | 0.008096 | -0.034177 | 0.000325 | -0.006022 | 0.015135 | 0.022557 | -0.005598 | 0.039107 | 0.010952
4850.9219 | 122.5296 | -0.059509 | 122.3557 | 0.12643 | -0.035942 | -0.030314 | -0.034174 | 0.022531 | 0.062691 | -0.071874 | -0.052818 | 0.060902 | -0.036267 | -0.042259 | -0.070797 | -0.036295 | -0.051798 | -0.039797 | 0.18594 | 0.023567 | 0.029195 | 0.025335 | 0.08204 | 0.1222 | -0.012365 | -0.007042 | 0.10668 | 0.009509 | 0.003517 | -0.025021 | 0.009481 | -0.006022 | 0.005979 | 0.017979 | -0.00102 | 0.03453 | 0.015531
4852.6875 | 122.4289 | -0.10986 | 122.4152 | 0.13101 | -0.040521 | -0.030314 | -0.029595 | 0.017953 | 0.067269 | -0.067295 | -0.052818 | 0.060902 | -0.050002 | -0.042259 | -0.075375 | -0.050029 | -0.042641 | -0.035219 | 0.24087 | 0.069342 | 0.079549 | 0.080268 | 0.12782 | 0.17713 | 0.042568 | -0.007042 | 0.10668 | -0.004226 | 0.003517 | -0.029599 | -0.004253 | 0.003135 | 0.010557 | 0.022557 | -0.010177 | 0.025373 | -0.007361
4854.4531 | 122.4747 | -0.10529 | 122.3785 | 0.12643 | -0.031363 | -0.021157 | -0.025017 | 0.022531 | 0.067269 | -0.062717 | -0.057396 | 0.051744 | -0.050002 | -0.046838 | -0.075375 | -0.045451 | -0.051798 | -0.030641 | 0.23172 | 0.073923 | 0.084129 | 0.080269 | 0.12782 | 0.17256 | 0.042569 | -0.01162 | 0.09752 | -0.004226 | -0.001062 | -0.029599 | 0.000325 | -0.006022 | 0.015135 | 0.017979 | -0.005598 | 0.025373 | 0.001796
4856.1719 | 122.4792 | -0.09613 | 122.374 | 0.12643 | -0.035942 | -0.025735 | -0.029595 | 0.013375 | 0.062691 | -0.062717 | -0.052818 | 0.056323 | -0.045424 | -0.046838 | -0.070797 | -0.031717 | -0.04722 | -0.035219 | 0.22256 | 0.060188 | 0.070395 | 0.066535 | 0.1095 | 0.15882 | 0.033413 | -0.007042 | 0.1021 | 0.000352 | -0.001062 | -0.025021 | 0.014059 | -0.001444 | 0.010557 | 0.017979 | -0.005598 | 0.025373 | 0.001796
4857.9375 | 122.5021 | -0.073242 | 122.3877 | 0.12643 | -0.040521 | -0.025735 | -0.029595 | 0.013375 | 0.062691 | -0.067295 | -0.061975 | 0.060902 | -0.045424 | -0.046838 | -0.075375 | -0.045451 | -0.051798 | -0.035219 | 0.19967 | 0.032721 | 0.047507 | 0.043647 | 0.086617 | 0.13593 | 0.005947 | -0.016199 | 0.10668 | 0.000352 | -0.001062 | -0.029599 | 0.000325 | -0.006022 | 0.010557 | 0.0134 | -0.010177 | 0.029951 | 0.006374
4859.7188 | 122.5571 | -0.041199 | 122.3648 | 0.13559 | -0.035942 | -0.025735 | -0.01586 | 0.027109 | 0.067269 | -0.067295 | -0.057396 | 0.060902 | -0.045424 | -0.046838 | -0.075375 | -0.045451 | -0.04722 | -0.035219 | 0.17679 | 0.005257 | 0.015464 | 0.025339 | 0.068308 | 0.10847 | -0.026096 | -0.01162 | 0.10668 | 0.000352 | -0.001062 | -0.029599 | 0.000325 | -0.001444 | 0.010557 | 0.017979 | -0.010176 | 0.029951 | 0.001796
4861.4844 | 122.4747 | -0.09613 | 122.3923 | 0.13559 | -0.031363 | -0.021157 | -0.020438 | 0.017953 | 0.067269 | -0.071874 | -0.052818 | 0.060902 | -0.040846 | -0.046838 | -0.070797 | -0.040873 | -0.04722 | -0.035219 | 0.23172 | 0.064767 | 0.074973 | 0.075692 | 0.11408 | 0.1634 | 0.024256 | -0.007042 | 0.10668 | 0.00493 | -0.001062 | -0.025021 | 0.004903 | -0.001444 | 0.010557 | 0.017979 | -0.005598 | 0.029951 | 0.006374
4863.1875 | 122.5021 | -0.064087 | 122.3557 | 0.13559 | -0.040521 | -0.034893 | -0.029595 | 0.027109 | 0.071848 | -0.067295 | -0.061975 | 0.060902 | -0.040846 | -0.042259 | -0.075375 | -0.040873 | -0.051798 | -0.026063 | 0.19967 | 0.023566 | 0.029194 | 0.034492 | 0.091196 | 0.13594 | -0.003208 | -0.016199 | 0.10668 | 0.00493 | 0.003517 | -0.029599 | 0.004903 | -0.006022 | 0.019713 | 0.0134 | -0.010177 | 0.034529 | 0.010952
4864.9688 | 122.4701 | -0.073242 | 122.3969 | 0.13559 | -0.035942 | -0.025735 | -0.029595 | 0.013375 | 0.071848 | -0.058139 | -0.052818 | 0.060902 | -0.040846 | -0.033101 | -0.079953 | -0.045451 | -0.04722 | -0.035219 | 0.20883 | 0.0373 | 0.047507 | 0.043647 | 0.086617 | 0.14509 | 0.015103 | -0.007042 | 0.10668 | 0.00493 | 0.012675 | -0.034177 | 0.000325 | -0.001444 | 0.010557 | 0.027135 | -0.005598 | 0.039107 | 0.006374
4866.7344 | 122.4792 | -0.086975 | 122.4014 | 0.14017 | -0.040521 | -0.030314 | -0.034174 | 0.022531 | 0.067269 | -0.067295 | -0.048239 | 0.060902 | -0.045424 | -0.03768 | -0.079953 | -0.040873 | -0.051798 | -0.035219 | 0.22714 | 0.046454 | 0.056661 | 0.052801 | 0.10951 | 0.15424 | 0.01968 | -0.002463 | 0.10668 | 0.000352 | 0.008096 | -0.034177 | 0.004903 | -0.006022 | 0.010557 | 0.031714 | 0.003559 | 0.034529 | 0.006374
4868.4375 | 122.5159 | -0.050354 | 122.3877 | 0.13559 | -0.035942 | -0.034893 | -0.020438 | 0.022531 | 0.071848 | -0.071874 | -0.048239 | 0.065481 | -0.040846 | -0.046838 | -0.079953 | -0.036295 | -0.051798 | -0.039797 | 0.18594 | 0.014412 | 0.015461 | 0.029916 | 0.072885 | 0.1222 | -0.02152 | -0.002463 | 0.11126 | 0.00493 | -0.001062 | -0.034177 | 0.009481 | -0.006022 | 0.005979 | 0.031714 | 0.003559 | 0.039107 | 0.010952
4870.2188 | 122.4426 | -0.10986 | 122.4106 | 0.12643 | -0.031363 | -0.034893 | -0.025017 | 0.022531 | 0.067269 | -0.058139 | -0.048239 | 0.060902 | -0.050002 | -0.042259 | -0.079953 | -0.045451 | -0.051798 | -0.039797 | 0.23629 | 0.0785 | 0.07497 | 0.084846 | 0.13239 | 0.17713 | 0.051724 | -0.002463 | 0.10668 | -0.004226 | 0.003517 | -0.034177 | 0.000325 | -0.006022 | 0.005979 | 0.031714 | 0.003559 | 0.029951 | 0.001796
4871.9375 | 122.4243 | -0.10986 | 122.4014 | 0.13559 | -0.040521 | -0.030314 | -0.020438 | 0.017953 | 0.076426 | -0.067295 | -0.052818 | 0.060902 | -0.036267 | -0.03768 | -0.070797 | -0.040873 | -0.04722 | -0.035219 | 0.24545 | 0.069342 | 0.079549 | 0.089425 | 0.12782 | 0.18629 | 0.042568 | -0.007042 | 0.10668 | 0.009509 | 0.008096 | -0.025021 | 0.004903 | -0.001444 | 0.010557 | 0.017979 | -0.005598 | 0.03453 | 0.010953
4873.7188 | 122.4197 | -0.10986 | 122.4152 | 0.13101 | -0.040521 | -0.030314 | -0.029595 | 0.022531 | 0.067269 | -0.067295 | -0.057396 | 0.060902 | -0.050002 | -0.03768 | -0.075375 | -0.045451 | -0.04722 | -0.039797 | 0.24087 | 0.069342 | 0.079549 | 0.080268 | 0.13239 | 0.17713 | 0.042568 | -0.01162 | 0.10668 | -0.004226 | 0.008096 | -0.029599 | 0.000325 | -0.001444 | 0.005979 | 0.017979 | -0.010176 | 0.025373 | -0.002782
4875.4219 | 122.5159 | -0.082397 | 122.4014 | 0.13101 | -0.035942 | -0.034893 | -0.029595 | 0.017953 | 0.067269 | -0.071874 | -0.057396 | 0.060902 | -0.040846 | -0.042259 | -0.075375 | -0.040873 | -0.051798 | -0.039797 | 0.21341 | 0.046455 | 0.047504 | 0.052802 | 0.10035 | 0.14967 | 0.010523 | -0.01162 | 0.10668 | 0.00493 | 0.003517 | -0.029599 | 0.004903 | -0.006022 | 0.005979 | 0.017979 | -0.005598 | 0.034529 | 0.010952
4877.1875 | 122.4838 | -0.10529 | 122.3969 | 0.13101 | -0.0451 | -0.021157 | -0.025017 | 0.017953 | 0.071848 | -0.062717 | -0.057396 | 0.065481 | -0.040846 | -0.042259 | -0.079953 | -0.040873 | -0.056376 | -0.030641 | 0.23629 | 0.060186 | 0.084129 | 0.080269 | 0.12324 | 0.17713 | 0.042569 | -0.01162 | 0.11126 | 0.00493 | 0.003517 | -0.034177 | 0.004903 | -0.0106 | 0.015135 | 0.022557 | -0.00102 | 0.039107 | 0.01553
4878.9688 | 122.5662 | -0.054932 | 122.3923 | 0.14017 | -0.035942 | -0.034893 | -0.025017 | 0.013375 | 0.062691 | -0.071874 | -0.052818 | 0.056323 | -0.036267 | -0.046838 | -0.084531 | -0.036295 | -0.051798 | -0.030641 | 0.1951 | 0.01899 | 0.020039 | 0.029915 | 0.068307 | 0.11762 | -0.016942 | -0.007042 | 0.1021 | 0.009509 | -0.001062 | -0.038755 | 0.009481 | -0.006022 | 0.015135 | 0.031713 | -0.00102 | 0.048264 | 0.015531
4880.6875 | 122.4335 | -0.11902 | 122.4197 | 0.14017 | -0.040521 | -0.034893 | -0.020438 | 0.022531 | 0.071848 | -0.067295 | -0.057396 | 0.060902 | -0.040846 | -0.042259 | -0.079953 | -0.045451 | -0.051798 | -0.035219 | 0.25918 | 0.078498 | 0.084126 | 0.098581 | 0.14155 | 0.19087 | 0.051724 | -0.01162 | 0.10668 | 0.00493 | 0.003517 | -0.034177 | 0.000325 | -0.006022 | 0.010557 | 0.022557 | -0.005598 | 0.039107 | 0.010952
4882.4531 | 122.525 | -0.068665 | 122.3877 | 0.13101 | -0.035942 | -0.034893 | -0.034174 | 0.022531 | 0.062691 | -0.067295 | -0.052818 | 0.056323 | -0.040846 | -0.03768 | -0.070797 | -0.045451 | -0.051798 | -0.035219 | 0.19967 | 0.032723 | 0.033772 | 0.034491 | 0.091196 | 0.13136 | 0.00137 | -0.007042 | 0.1021 | 0.00493 | 0.008096 | -0.025021 | 0.000325 | -0.006022 | 0.010557 | 0.017979 | -0.00102 | 0.029951 | 0.010952
4884.2344 | 122.5113 | -0.054932 | 122.4014 | 0.13559 | -0.040521 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.058139 | -0.052818 | 0.056323 | -0.036267 | -0.03768 | -0.079953 | -0.045451 | -0.042641 | -0.044375 | 0.19052 | 0.014411 | 0.024618 | 0.025337 | 0.077463 | 0.12678 | -0.003207 | -0.007042 | 0.1021 | 0.009509 | 0.008096 | -0.034177 | 0.000325 | 0.003135 | 0.001401 | 0.027135 | -0.010177 | 0.043686 | 0.006374
4886.0156 | 122.5845 | -0.054932 | 122.3831 | 0.13101 | -0.040521 | -0.030314 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.048239 | 0.060902 | -0.05458 | -0.042259 | -0.070797 | -0.040873 | -0.051798 | -0.039797 | 0.18594 | 0.014411 | 0.024618 | 0.029915 | 0.077463 | 0.12678 | -0.007785 | -0.002463 | 0.10668 | -0.008804 | 0.003517 | -0.025021 | 0.004903 | -0.006022 | 0.005979 | 0.022558 | 0.003559 | 0.016217 | -0.002782
4887.7344 | 122.5845 | -0.068665 | 122.3877 | 0.13101 | -0.040521 | -0.034893 | -0.029595 | 0.022531 | 0.067269 | -0.071874 | -0.048239 | 0.060902 | -0.045424 | -0.042259 | -0.070797 | -0.040873 | -0.051798 | -0.035219 | 0.19967 | 0.028144 | 0.033772 | 0.03907 | 0.091196 | 0.13593 | -0.003209 | -0.002463 | 0.10668 | 0.000352 | 0.003517 | -0.025021 | 0.004903 | -0.006022 | 0.010557 | 0.022558 | 0.003559 | 0.025373 | 0.006374
4889.4531 | 122.58 | -0.064087 | 122.3694 | 0.13101 | -0.035942 | -0.025735 | -0.025017 | 0.013375 | 0.067269 | -0.071874 | -0.048239 | 0.060902 | -0.040846 | -0.033101 | -0.070797 | -0.040873 | -0.051798 | -0.044375 | 0.1951 | 0.028145 | 0.038352 | 0.03907 | 0.077462 | 0.13136 | -0.007787 | -0.002463 | 0.10668 | 0.00493 | 0.012675 | -0.025021 | 0.004903 | -0.006022 | 0.001401 | 0.022558 | 0.003559 | 0.029951 | 0.010952
4891.2344 | 122.4289 | -0.091553 | 122.4289 | 0.13101 | -0.040521 | -0.025735 | -0.029595 | 0.013375 | 0.067269 | -0.062717 | -0.048239 | 0.056323 | -0.045424 | -0.042259 | -0.075375 | -0.036295 | -0.051798 | -0.039797 | 0.22256 | 0.051032 | 0.065818 | 0.061958 | 0.10493 | 0.15882 | 0.028836 | -0.002463 | 0.1021 | 0.000352 | 0.003517 | -0.029599 | 0.009481 | -0.006022 | 0.005979 | 0.027136 | 0.003559 | 0.029951 | 0.006374
4893 | 122.4838 | -0.10071 | 122.4335 | 0.13559 | -0.031363 | -0.030314 | -0.029595 | 0.027109 | 0.081005 | -0.067295 | -0.043661 | 0.056323 | -0.040846 | -0.042259 | -0.079953 | -0.045451 | -0.051798 | -0.035219 | 0.23629 | 0.069345 | 0.070394 | 0.071113 | 0.12782 | 0.18171 | 0.033413 | 0.002115 | 0.1021 | 0.00493 | 0.003517 | -0.034177 | 0.000325 | -0.006022 | 0.010557 | 0.036292 | 0.008137 | 0.039107 | 0.010952
4894.7656 | 122.438 | -0.09613 | 122.4518 | 0.12643 | -0.031363 | -0.025735 | -0.025017 | 0.027109 | 0.067269 | -0.062717 | -0.052818 | 0.065481 | -0.036267 | -0.03768 | -0.075375 | -0.045451 | -0.051798 | -0.035219 | 0.22256 | 0.064767 | 0.070395 | 0.071113 | 0.12324 | 0.1634 | 0.033413 | -0.007042 | 0.11126 | 0.009509 | 0.008096 | -0.029599 | 0.000325 | -0.006022 | 0.010557 | 0.022557 | -0.00102 | 0.039108 | 0.015531
4896.4844 | 122.5754 | -0.07782 | 122.3602 | 0.13101 | -0.040521 | -0.025735 | -0.029595 | 0.013375 | 0.062691 | -0.067295 | -0.057396 | 0.060902 | -0.045424 | -0.033101 | -0.079953 | -0.040873 | -0.056376 | -0.035219 | 0.20883 | 0.037299 | 0.052085 | 0.048225 | 0.091195 | 0.14051 | 0.010525 | -0.01162 | 0.10668 | 0.000352 | 0.012675 | -0.034177 | 0.004903 | -0.0106 | 0.010557 | 0.022557 | -0.00102 | 0.034529 | 0.010952
4898.25 | 122.5433 | -0.054932 | 122.3923 | 0.13559 | -0.035942 | -0.030314 | -0.029595 | 0.017953 | 0.067269 | -0.062717 | -0.052818 | 0.056323 | -0.040846 | -0.03768 | -0.075375 | -0.040873 | -0.051798 | -0.035219 | 0.19052 | 0.01899 | 0.024618 | 0.025337 | 0.072885 | 0.1222 | -0.007785 | -0.007042 | 0.1021 | 0.00493 | 0.008096 | -0.029599 | 0.004903 | -0.006022 | 0.010557 | 0.022557 | -0.00102 | 0.034529 | 0.010952
4899.9531 | 122.5616 | -0.07782 | 122.4152 | 0.13559 | -0.035942 | -0.034893 | -0.025017 | 0.013375 | 0.067269 | -0.067295 | -0.052818 | 0.060902 | -0.045424 | -0.042259 | -0.075375 | -0.036295 | -0.051798 | -0.035219 | 0.21341 | 0.041878 | 0.042927 | 0.052803 | 0.091195 | 0.14509 | 0.010525 | -0.007042 | 0.10668 | 0.000352 | 0.003517 | -0.029599 | 0.009481 | -0.006022 | 0.010557 | 0.022557 | -0.00102 | 0.029951 | 0.006374
4901.7344 | 122.5296 | -0.068665 | 122.4197 | 0.12643 | -0.040521 | -0.034893 | -0.029595 | 0.008797 | 0.067269 | -0.067295 | -0.057396 | 0.056323 | -0.045424 | -0.042259 | -0.075375 | -0.045451 | -0.051798 | -0.039797 | 0.19509 | 0.028144 | 0.033772 | 0.03907 | 0.077462 | 0.13593 | 0.00137 | -0.01162 | 0.1021 | 0.000352 | 0.003517 | -0.029599 | 0.000325 | -0.006022 | 0.005979 | 0.017979 | -0.005598 | 0.029951 | 0.006374
4903.5 | 122.58 | -0.059509 | 122.4289 | 0.13101 | -0.035942 | -0.025735 | -0.034174 | 0.017953 | 0.067269 | -0.067295 | -0.052818 | 0.056323 | -0.036267 | -0.042259 | -0.084531 | -0.040873 | -0.056376 | -0.039797 | 0.19052 | 0.023567 | 0.033774 | 0.025335 | 0.077462 | 0.12678 | -0.007786 | -0.007042 | 0.1021 | 0.009509 | 0.003517 | -0.038755 | 0.004903 | -0.0106 | 0.005979 | 0.031713 | 0.003558 | 0.048264 | 0.020109
4905.2031 | 122.5342 | -0.09613 | 122.3969 | 0.13101 | -0.035942 | -0.025735 | -0.034174 | 0.022531 | 0.067269 | -0.067295 | -0.057396 | 0.056323 | -0.040846 | -0.03768 | -0.075375 | -0.045451 | -0.04722 | -0.030641 | 0.22714 | 0.060188 | 0.070395 | 0.061956 | 0.11866 | 0.1634 | 0.028835 | -0.01162 | 0.1021 | 0.00493 | 0.008096 | -0.029599 | 0.000325 | -0.001444 | 0.015135 | 0.017979 | -0.010176 | 0.034529 | 0.006374
4906.9688 | 122.5342 | -0.082397 | 122.4014 | 0.13559 | -0.031363 | -0.030314 | -0.020438 | 0.022531 | 0.071848 | -0.067295 | -0.048239 | 0.056323 | -0.045424 | -0.042259 | -0.075375 | -0.040873 | -0.056376 | -0.039797 | 0.21798 | 0.051034 | 0.052083 | 0.061959 | 0.10493 | 0.15424 | 0.015102 | -0.002463 | 0.1021 | 0.000352 | 0.003517 | -0.029599 | 0.004903 | -0.0106 | 0.005979 | 0.027136 | 0.008137 | 0.029951 | 0.010952
4908.75 | 122.5525 | -0.082397 | 122.4289 | 0.13101 | -0.035942 | -0.030314 | -0.025017 | 0.017953 | 0.062691 | -0.067295 | -0.066553 | 0.060902 | -0.045424 | -0.042259 | -0.079953 | -0.045451 | -0.04722 | -0.030641 | 0.21341 | 0.046455 | 0.052083 | 0.05738 | 0.10035 | 0.14509 | 0.015102 | -0.020777 | 0.10668 | 0.000352 | 0.003517 | -0.034177 | 0.000325 | -0.001444 | 0.015135 | 0.0134 | -0.019333 | 0.034529 | 0.001796
4910.4688 | 122.5937 | -0.059509 | 122.4014 | 0.13101 | -0.026784 | -0.034893 | -0.020438 | 0.022531 | 0.071848 | -0.071874 | -0.048239 | 0.056323 | -0.036267 | -0.046838 | -0.079953 | -0.036295 | -0.051798 | -0.039797 | 0.19052 | 0.032725 | 0.024616 | 0.039071 | 0.08204 | 0.13136 | -0.012365 | -0.002463 | 0.1021 | 0.009509 | -0.001062 | -0.034177 | 0.009481 | -0.006022 | 0.005979 | 0.031714 | 0.003559 | 0.043686 | 0.015531
4912.2344 | 122.4564 | -0.11444 | 122.4426 | 0.14017 | -0.035942 | -0.025735 | -0.020438 | 0.017953 | 0.071848 | -0.058139 | -0.048239 | 0.056323 | -0.040846 | -0.042259 | -0.084531 | -0.045451 | -0.04722 | -0.030641 | 0.25461 | 0.078499 | 0.088706 | 0.094003 | 0.13239 | 0.18629 | 0.056302 | -0.002463 | 0.1021 | 0.00493 | 0.003517 | -0.038755 | 0.000325 | -0.001444 | 0.015135 | 0.036292 | -0.001019 | 0.043685 | 0.006374
4914 | 122.5113 | -0.09613 | 122.4518 | 0.13101 | -0.031363 | -0.021157 | -0.025017 | 0.022531 | 0.067269 | -0.067295 | -0.061975 | 0.056323 | -0.036267 | -0.042259 | -0.075375 | -0.045451 | -0.051798 | -0.039797 | 0.22714 | 0.064767 | 0.074973 | 0.071113 | 0.11866 | 0.1634 | 0.028835 | -0.016199 | 0.1021 | 0.009509 | 0.003517 | -0.029599 | 0.000325 | -0.006022 | 0.005979 | 0.0134 | -0.010177 | 0.039108 | 0.015531
4915.7188 | 122.4976 | -0.091553 | 122.4243 | 0.13101 | -0.031363 | -0.034893 | -0.025017 | 0.017953 | 0.071848 | -0.071874 | -0.061975 | 0.060902 | -0.050002 | -0.03768 | -0.070797 | -0.045451 | -0.04722 | -0.030641 | 0.22256 | 0.06019 | 0.05666 | 0.066536 | 0.10951 | 0.1634 | 0.019679 | -0.016199 | 0.10668 | -0.004226 | 0.008096 | -0.025021 | 0.000325 | -0.001444 | 0.015135 | 0.008822 | -0.014755 | 0.020795 | -0.002782
4917.4844 | 122.5204 | -0.082397 | 122.4014 | 0.13101 | -0.040521 | -0.025735 | -0.029595 | 0.013375 | 0.067269 | -0.071874 | -0.057396 | 0.060902 | -0.040846 | -0.03768 | -0.070797 | -0.040873 | -0.04722 | -0.035219 | 0.21341 | 0.041876 | 0.056662 | 0.052802 | 0.095772 | 0.14967 | 0.010523 | -0.01162 | 0.10668 | 0.00493 | 0.008096 | -0.025021 | 0.004903 | -0.001444 | 0.010557 | 0.013401 | -0.010176 | 0.029951 | 0.006374
4919.2031 | 122.5479 | -0.064087 | 122.3877 | 0.12643 | -0.040521 | -0.021157 | -0.029595 | 0.008797 | 0.067269 | -0.067295 | -0.052818 | 0.056323 | -0.050002 | -0.046838 | -0.079953 | -0.036295 | -0.051798 | -0.035219 | 0.19052 | 0.023566 | 0.04293 | 0.034492 | 0.072884 | 0.13136 | -0.003208 | -0.007042 | 0.1021 | -0.004226 | -0.001062 | -0.034177 | 0.009481 | -0.006022 | 0.010557 | 0.027135 | -0.00102 | 0.029951 | 0.001796
4920.9688 | 122.5433 | -0.068665 | 122.4197 | 0.13101 | -0.031363 | -0.025735 | -0.025017 | 0.017953 | 0.076426 | -0.067295 | -0.052818 | 0.060902 | -0.040846 | -0.03768 | -0.070797 | -0.036295 | -0.051798 | -0.035219 | 0.19967 | 0.037302 | 0.04293 | 0.043648 | 0.086618 | 0.14509 | 0.00137 | -0.007042 | 0.10668 | 0.00493 | 0.008096 | -0.025021 | 0.009481 | -0.006022 | 0.010557 | 0.017979 | -0.00102 | 0.029951 | 0.010952
4922.75 | 122.4884 | -0.10071 | 122.406 | 0.12643 | -0.040521 | -0.025735 | -0.025017 | 0.022531 | 0.076426 | -0.067295 | -0.057396 | 0.056323 | -0.040846 | -0.042259 | -0.075375 | -0.050029 | -0.04722 | -0.030641 | 0.22714 | 0.060187 | 0.074973 | 0.075691 | 0.12324 | 0.17713 | 0.033413 | -0.01162 | 0.1021 | 0.00493 | 0.003517 | -0.029599 | -0.004253 | -0.001444 | 0.015135 | 0.017979 | -0.010176 | 0.034529 | 0.006374
4924.4531 | 122.5891 | -0.045776 | 122.3969 | 0.13101 | -0.031363 | -0.030314 | -0.029595 | 0.027109 | 0.071848 | -0.062717 | -0.043661 | 0.060902 | -0.040846 | -0.046838 | -0.075375 | -0.040873 | -0.051798 | -0.039797 | 0.17678 | 0.014413 | 0.015462 | 0.016181 | 0.072885 | 0.11762 | -0.016941 | 0.002115 | 0.10668 | 0.00493 | -0.001062 | -0.029599 | 0.004903 | -0.006022 | 0.005979 | 0.031714 | 0.008137 | 0.034529 | 0.010952
4926.2344 | 122.5891 | -0.064087 | 122.4152 | 0.13559 | -0.031363 | -0.025735 | -0.029595 | 0.017953 | 0.071848 | -0.062717 | -0.057396 | 0.056323 | -0.040846 | -0.042259 | -0.079953 | -0.036295 | -0.051798 | -0.039797 | 0.19967 | 0.032724 | 0.038352 | 0.034492 | 0.08204 | 0.13594 | 0.00137 | -0.01162 | 0.1021 | 0.00493 | 0.003517 | -0.034177 | 0.009481 | -0.006022 | 0.005979 | 0.022557 | -0.005598 | 0.039107 | 0.010952
4928 | 122.6074 | -0.059509 | 122.4426 | 0.12643 | -0.031363 | -0.030314 | -0.034174 | 0.017953 | 0.062691 | -0.062717 | -0.052818 | 0.056323 | -0.040846 | -0.046838 | -0.084531 | -0.040873 | -0.042641 | -0.039797 | 0.18594 | 0.028146 | 0.029195 | 0.025335 | 0.077462 | 0.1222 | -0.003208 | -0.007042 | 0.1021 | 0.00493 | -0.001062 | -0.038755 | 0.004903 | 0.003135 | 0.005979 | 0.031713 | -0.010177 | 0.043685 | 0.001795
4929.7656 | 122.5433 | -0.086975 | 122.4197 | 0.13559 | -0.031363 | -0.021157 | -0.029595 | 0.022531 | 0.076426 | -0.062717 | -0.061975 | 0.060902 | -0.045424 | -0.03768 | -0.079953 | -0.045451 | -0.051798 | -0.035219 | 0.22256 | 0.055612 | 0.065818 | 0.05738 | 0.10951 | 0.1634 | 0.024258 | -0.016199 | 0.10668 | 0.000352 | 0.008096 | -0.034177 | 0.000325 | -0.006022 | 0.010557 | 0.017978 | -0.010177 | 0.034529 | 0.006374
4931.5469 | 122.4792 | -0.10986 | 122.4564 | 0.13101 | -0.035942 | -0.025735 | -0.025017 | 0.013375 | 0.067269 | -0.067295 | -0.057396 | 0.056323 | -0.040846 | -0.042259 | -0.079953 | -0.045451 | -0.051798 | -0.030641 | 0.24087 | 0.073921 | 0.084128 | 0.084846 | 0.12324 | 0.17713 | 0.042568 | -0.01162 | 0.1021 | 0.00493 | 0.003517 | -0.034177 | 0.000325 | -0.006022 | 0.015135 | 0.022557 | -0.005598 | 0.039107 | 0.010952
4933.3125 | 122.5983 | -0.064087 | 122.4014 | 0.13101 | -0.031363 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.052818 | 0.060902 | -0.05458 | -0.03768 | -0.079953 | -0.040873 | -0.051798 | -0.035219 | 0.1951 | 0.032724 | 0.033773 | 0.034492 | 0.086618 | 0.13594 | -0.003208 | -0.007042 | 0.10668 | -0.008804 | 0.008096 | -0.034177 | 0.004903 | -0.006022 | 0.010557 | 0.027135 | -0.00102 | 0.025373 | -0.002782
4935.0312 | 122.4838 | -0.10986 | 122.438 | 0.13559 | -0.035942 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.052818 | 0.060902 | -0.040846 | -0.042259 | -0.079953 | -0.045451 | -0.04722 | -0.035219 | 0.24545 | 0.073921 | 0.079549 | 0.080268 | 0.13239 | 0.18171 | 0.047146 | -0.007042 | 0.10668 | 0.00493 | 0.003517 | -0.034177 | 0.000325 | -0.001444 | 0.010557 | 0.027135 | -0.005598 | 0.039107 | 0.006374
4936.8281 | 122.5525 | -0.073242 | 122.4106 | 0.12643 | -0.035942 | -0.025735 | -0.034174 | 0.022531 | 0.067269 | -0.071874 | -0.057396 | 0.060902 | -0.040846 | -0.042259 | -0.075375 | -0.050029 | -0.060955 | -0.035219 | 0.19967 | 0.0373 | 0.047507 | 0.039068 | 0.095773 | 0.14051 | 0.001368 | -0.01162 | 0.10668 | 0.00493 | 0.003517 | -0.029599 | -0.004253 | -0.015179 | 0.010557 | 0.017979 | 0.003559 | 0.034529 | 0.020109
4938.5469 | 122.5845 | -0.068665 | 122.4243 | 0.12643 | -0.035942 | -0.025735 | -0.034174 | 0.017953 | 0.067269 | -0.067295 | -0.052818 | 0.060902 | -0.036267 | -0.03768 | -0.08911 | -0.045451 | -0.042641 | -0.035219 | 0.19509 | 0.032723 | 0.04293 | 0.034491 | 0.086618 | 0.13593 | 0.00137 | -0.007042 | 0.10668 | 0.009509 | 0.008096 | -0.043334 | 0.000325 | 0.003135 | 0.010557 | 0.036292 | -0.010177 | 0.052843 | 0.006374
4940.3125 | 122.493 | -0.09613 | 122.4747 | 0.13559 | -0.035942 | -0.025735 | -0.034174 | 0.022531 | 0.067269 | -0.062717 | -0.048239 | 0.056323 | -0.040846 | -0.03768 | -0.075375 | -0.045451 | -0.042641 | -0.026063 | 0.23172 | 0.060188 | 0.070395 | 0.061956 | 0.11866 | 0.1634 | 0.033413 | -0.002463 | 0.1021 | 0.00493 | 0.008096 | -0.029599 | 0.000325 | 0.003135 | 0.019713 | 0.027136 | -0.005598 | 0.034529 | 0.001795
4942.0938 | 122.438 | -0.12817 | 122.4518 | 0.13559 | -0.031363 | -0.030314 | -0.034174 | 0.017953 | 0.062691 | -0.058139 | -0.057396 | 0.056323 | -0.045424 | -0.042259 | -0.084531 | -0.045451 | -0.04722 | -0.039797 | 0.26376 | 0.096811 | 0.09786 | 0.094 | 0.14613 | 0.19087 | 0.070035 | -0.01162 | 0.1021 | 0.000352 | 0.003517 | -0.038755 | 0.000325 | -0.001444 | 0.005979 | 0.027135 | -0.010176 | 0.039107 | 0.001796
4943.875 | 122.4701 | -0.10986 | 122.4335 | 0.12643 | -0.035942 | -0.025735 | -0.025017 | 0.017953 | 0.067269 | -0.067295 | -0.052818 | 0.056323 | -0.036267 | -0.042259 | -0.079953 | -0.040873 | -0.051798 | -0.039797 | 0.23629 | 0.073921 | 0.084128 | 0.084846 | 0.12782 | 0.17713 | 0.042568 | -0.007042 | 0.1021 | 0.009509 | 0.003517 | -0.034177 | 0.004903 | -0.006022 | 0.005979 | 0.027135 | -0.00102 | 0.043686 | 0.015531
4945.5938 | 122.4884 | -0.10071 | 122.4426 | 0.13101 | -0.040521 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.061975 | 0.051744 | -0.040846 | -0.042259 | -0.075375 | -0.045451 | -0.04722 | -0.035219 | 0.23172 | 0.060187 | 0.074973 | 0.075691 | 0.12324 | 0.17256 | 0.033413 | -0.016199 | 0.09752 | 0.00493 | 0.003517 | -0.029599 | 0.000325 | -0.001444 | 0.010557 | 0.0134 | -0.014755 | 0.034529 | 0.006374
4947.3594 | 122.5113 | -0.091553 | 122.4655 | 0.13101 | -0.035942 | -0.030314 | -0.034174 | 0.022531 | 0.067269 | -0.058139 | -0.057396 | 0.060902 | -0.040846 | -0.046838 | -0.079953 | -0.040873 | -0.051798 | -0.035219 | 0.22256 | 0.055611 | 0.061239 | 0.057379 | 0.11408 | 0.15882 | 0.033414 | -0.01162 | 0.10668 | 0.00493 | -0.001062 | -0.034177 | 0.004903 | -0.006022 | 0.010557 | 0.022557 | -0.005598 | 0.039107 | 0.010952
4949.1406 | 122.493 | -0.10071 | 122.4701 | 0.13559 | -0.040521 | -0.034893 | -0.038752 | 0.017953 | 0.071848 | -0.062717 | -0.061975 | 0.060902 | -0.040846 | -0.03768 | -0.075375 | -0.045451 | -0.051798 | -0.030641 | 0.23629 | 0.060187 | 0.065815 | 0.061956 | 0.11866 | 0.17256 | 0.037991 | -0.016199 | 0.10668 | 0.00493 | 0.008096 | -0.029599 | 0.000325 | -0.006022 | 0.015135 | 0.0134 | -0.010177 | 0.034529 | 0.010952
4950.9219 | 122.4838 | -0.10986 | 122.4564 | 0.13559 | -0.040521 | -0.030314 | -0.034174 | 0.017953 | 0.067269 | -0.062717 | -0.052818 | 0.056323 | -0.050002 | -0.042259 | -0.079953 | -0.045451 | -0.056376 | -0.039797 | 0.24545 | 0.069342 | 0.079549 | 0.075689 | 0.12782 | 0.17713 | 0.047146 | -0.007042 | 0.1021 | -0.004226 | 0.003517 | -0.034177 | 0.000325 | -0.0106 | 0.005979 | 0.027135 | 0.003558 | 0.029951 | 0.006374
4952.7031 | 122.5296 | -0.091553 | 122.4884 | 0.13559 | -0.035942 | -0.025735 | -0.029595 | 0.027109 | 0.071848 | -0.062717 | -0.061975 | 0.051744 | -0.040846 | -0.046838 | -0.075375 | -0.045451 | -0.04722 | -0.035219 | 0.22714 | 0.055611 | 0.065818 | 0.061958 | 0.11866 | 0.1634 | 0.028836 | -0.016199 | 0.09752 | 0.00493 | -0.001062 | -0.029599 | 0.000325 | -0.001444 | 0.010557 | 0.0134 | -0.014755 | 0.034529 | 0.006374
4954.4219 | 122.5296 | -0.10071 | 122.4472 | 0.13101 | -0.040521 | -0.025735 | -0.029595 | 0.017953 | 0.062691 | -0.067295 | -0.052818 | 0.060902 | -0.036267 | -0.03768 | -0.084531 | -0.040873 | -0.051798 | -0.035219 | 0.23172 | 0.060187 | 0.074973 | 0.071113 | 0.11866 | 0.1634 | 0.033413 | -0.007042 | 0.10668 | 0.009509 | 0.008096 | -0.038755 | 0.004903 | -0.006022 | 0.010557 | 0.031713 | -0.00102 | 0.048264 | 0.015531
4956.2031 | 122.5662 | -0.091553 | 122.4518 | 0.13559 | -0.035942 | -0.025735 | -0.029595 | 0.022531 | 0.067269 | -0.067295 | -0.052818 | 0.060902 | -0.036267 | -0.03768 | -0.075375 | -0.040873 | -0.042641 | -0.035219 | 0.22714 | 0.055611 | 0.065818 | 0.061958 | 0.11408 | 0.15882 | 0.024258 | -0.007042 | 0.10668 | 0.009509 | 0.008096 | -0.029599 | 0.004903 | 0.003135 | 0.010557 | 0.022557 | -0.010177 | 0.039108 | 0.006374
4957.9688 | 122.6166 | -0.059509 | 122.4152 | 0.14017 | -0.035942 | -0.034893 | -0.029595 | 0.027109 | 0.067269 | -0.058139 | -0.061975 | 0.056323 | -0.040846 | -0.042259 | -0.084531 | -0.036295 | -0.051798 | -0.044375 | 0.19967 | 0.023567 | 0.024616 | 0.029914 | 0.086618 | 0.12678 | 0.00137 | -0.016199 | 0.1021 | 0.00493 | 0.003517 | -0.038755 | 0.009481 | -0.006022 | 0.001401 | 0.022556 | -0.010177 | 0.043685 | 0.010952
4959.7031 | 122.5708 | -0.082397 | 122.4564 | 0.13559 | -0.0451 | -0.039471 | -0.029595 | 0.017953 | 0.067269 | -0.062717 | -0.061975 | 0.051744 | -0.036267 | -0.042259 | -0.075375 | -0.045451 | -0.051798 | -0.039797 | 0.21798 | 0.037297 | 0.042926 | 0.052802 | 0.10035 | 0.14967 | 0.01968 | -0.016199 | 0.09752 | 0.009509 | 0.003517 | -0.029599 | 0.000325 | -0.006022 | 0.005979 | 0.0134 | -0.010177 | 0.039108 | 0.015531
4961.5156 | 122.5433 | -0.082397 | 122.4564 | 0.13559 | -0.040521 | -0.025735 | -0.025017 | 0.013375 | 0.067269 | -0.071874 | -0.057396 | 0.060902 | -0.040846 | -0.033101 | -0.075375 | -0.040873 | -0.051798 | -0.035219 | 0.21798 | 0.041876 | 0.056662 | 0.05738 | 0.095772 | 0.14967 | 0.010523 | -0.01162 | 0.10668 | 0.00493 | 0.012675 | -0.029599 | 0.004903 | -0.006022 | 0.010557 | 0.017979 | -0.005598 | 0.034529 | 0.010952
4963.2188 | 122.5021 | -0.10986 | 122.4655 | 0.13101 | -0.040521 | -0.025735 | -0.020438 | 0.017953 | 0.071848 | -0.071874 | -0.057396 | 0.060902 | -0.045424 | -0.042259 | -0.075375 | -0.045451 | -0.051798 | -0.030641 | 0.24087 | 0.069342 | 0.084128 | 0.089425 | 0.12782 | 0.18171 | 0.037989 | -0.01162 | 0.10668 | 0.000352 | 0.003517 | -0.029599 | 0.000325 | -0.006022 | 0.015135 | 0.017979 | -0.005598 | 0.029951 | 0.006374
4964.9531 | 122.6486 | -0.059509 | 122.438 | 0.13559 | -0.040521 | -0.025735 | -0.029595 | 0.022531 | 0.062691 | -0.071874 | -0.057396 | 0.060902 | -0.045424 | -0.042259 | -0.075375 | -0.040873 | -0.04722 | -0.030641 | 0.1951 | 0.018988 | 0.033774 | 0.029914 | 0.08204 | 0.1222 | -0.012365 | -0.01162 | 0.10668 | 0.000352 | 0.003517 | -0.029599 | 0.004903 | -0.001444 | 0.015135 | 0.017979 | -0.010176 | 0.029951 | 0.001796
4966.7031 | 122.4747 | -0.10529 | 122.4701 | 0.13101 | -0.035942 | -0.025735 | -0.029595 | 0.017953 | 0.062691 | -0.062717 | -0.052818 | 0.056323 | -0.040846 | -0.03768 | -0.079953 | -0.045451 | -0.051798 | -0.035219 | 0.23629 | 0.069344 | 0.079551 | 0.075691 | 0.12324 | 0.16798 | 0.042569 | -0.007042 | 0.1021 | 0.00493 | 0.008096 | -0.034177 | 0.000325 | -0.006022 | 0.010557 | 0.027135 | -0.00102 | 0.039107 | 0.010952
4968.4062 | 122.5479 | -0.10071 | 122.4884 | 0.13559 | -0.0451 | -0.030314 | -0.029595 | 0.013375 | 0.067269 | -0.058139 | -0.052818 | 0.056323 | -0.045424 | -0.042259 | -0.075375 | -0.045451 | -0.051798 | -0.026063 | 0.23629 | 0.055608 | 0.070394 | 0.071113 | 0.11408 | 0.16798 | 0.042569 | -0.007042 | 0.1021 | 0.000352 | 0.003517 | -0.029599 | 0.000325 | -0.006022 | 0.019713 | 0.022557 | -0.00102 | 0.029951 | 0.006374
4970.1719 | 122.5067 | -0.10071 | 122.4564 | 0.13101 | -0.040521 | -0.025735 | -0.025017 | 0.022531 | 0.062691 | -0.058139 | -0.061975 | 0.060902 | -0.031689 | -0.03768 | -0.070797 | -0.045451 | -0.042641 | -0.044375 | 0.23172 | 0.060187 | 0.074973 | 0.075691 | 0.12324 | 0.1634 | 0.042569 | -0.016199 | 0.10668 | 0.014087 | 0.008096 | -0.025021 | 0.000325 | 0.003135 | 0.001401 | 0.008822 | -0.019334 | 0.039108 | 0.010952
4971.9375 | 122.5067 | -0.10529 | 122.4564 | 0.13101 | -0.031363 | -0.025735 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.057396 | 0.051744 | -0.040846 | -0.042259 | -0.066219 | -0.045451 | -0.051798 | -0.039797 | 0.23629 | 0.073923 | 0.079551 | 0.080269 | 0.12782 | 0.17713 | 0.037991 | -0.01162 | 0.09752 | 0.00493 | 0.003517 | -0.020443 | 0.000325 | -0.006022 | 0.005979 | 0.008823 | -0.005598 | 0.025373 | 0.010952
4973.7344 | 122.58 | -0.082397 | 122.4564 | 0.13101 | -0.040521 | -0.025735 | -0.034174 | 0.017953 | 0.062691 | -0.062717 | -0.057396 | 0.056323 | -0.040846 | -0.042259 | -0.075375 | -0.036295 | -0.04722 | -0.035219 | 0.21341 | 0.041876 | 0.056662 | 0.048223 | 0.10035 | 0.14509 | 0.01968 | -0.01162 | 0.1021 | 0.00493 | 0.003517 | -0.029599 | 0.009481 | -0.001444 | 0.010557 | 0.017979 | -0.010176 | 0.034529 | 0.006374
4975.4531 | 122.5204 | -0.10986 | 122.4884 | 0.14017 | -0.035942 | -0.021157 | -0.034174 | 0.017953 | 0.067269 | -0.062717 | -0.057396 | 0.051744 | -0.040846 | -0.03768 | -0.070797 | -0.040873 | -0.056376 | -0.030641 | 0.25003 | 0.073921 | 0.088706 | 0.075689 | 0.12782 | 0.17713 | 0.047146 | -0.01162 | 0.09752 | 0.00493 | 0.008096 | -0.025021 | 0.004903 | -0.0106 | 0.015135 | 0.013401 | -0.00102 | 0.029951 | 0.01553
4977.1562 | 122.5159 | -0.09613 | 122.493 | 0.13559 | -0.0451 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.052818 | 0.056323 | -0.040846 | -0.03768 | -0.070797 | -0.036295 | -0.056376 | -0.030641 | 0.23172 | 0.05103 | 0.065816 | 0.066535 | 0.11866 | 0.16798 | 0.033413 | -0.007042 | 0.1021 | 0.00493 | 0.008096 | -0.025021 | 0.009481 | -0.0106 | 0.015135 | 0.017979 | 0.003558 | 0.029951 | 0.01553
4978.875 | 122.4655 | -0.11902 | 122.4747 | 0.13559 | -0.0451 | -0.025735 | -0.029595 | 0.017953 | 0.067269 | -0.062717 | -0.052818 | 0.056323 | -0.040846 | -0.042259 | -0.079953 | -0.036295 | -0.042641 | -0.035219 | 0.25461 | 0.073919 | 0.093284 | 0.089424 | 0.13697 | 0.18629 | 0.056302 | -0.007042 | 0.1021 | 0.00493 | 0.003517 | -0.034177 | 0.009481 | 0.003135 | 0.010557 | 0.027135 | -0.010177 | 0.039107 | 0.001795
4980.6094 | 122.6349 | -0.073242 | 122.4289 | 0.12643 | -0.035942 | -0.025735 | -0.020438 | 0.022531 | 0.067269 | -0.062717 | -0.057396 | 0.051744 | -0.040846 | -0.03768 | -0.075375 | -0.040873 | -0.051798 | -0.035219 | 0.19967 | 0.0373 | 0.047507 | 0.052804 | 0.095773 | 0.14051 | 0.010525 | -0.01162 | 0.09752 | 0.00493 | 0.008096 | -0.029599 | 0.004903 | -0.006022 | 0.010557 | 0.017979 | -0.005598 | 0.034529 | 0.010952
4982.375 | 122.5708 | -0.082397 | 122.4426 | 0.13101 | -0.031363 | -0.030314 | -0.025017 | 0.017953 | 0.071848 | -0.071874 | -0.048239 | 0.051744 | -0.050002 | -0.033101 | -0.070797 | -0.045451 | -0.051798 | -0.021484 | 0.21341 | 0.051034 | 0.052083 | 0.05738 | 0.10035 | 0.15424 | 0.010523 | -0.002463 | 0.09752 | -0.004226 | 0.012675 | -0.025021 | 0.000325 | -0.006022 | 0.024292 | 0.022558 | 0.003559 | 0.020795 | 0.001796
4984.0938 | 122.5479 | -0.07782 | 122.4884 | 0.13101 | -0.035942 | -0.025735 | -0.029595 | 0.022531 | 0.067269 | -0.067295 | -0.052818 | 0.056323 | -0.040846 | -0.033101 | -0.070797 | -0.045451 | -0.051798 | -0.030641 | 0.20883 | 0.041878 | 0.052085 | 0.048225 | 0.10035 | 0.14509 | 0.010525 | -0.007042 | 0.1021 | 0.00493 | 0.012675 | -0.025021 | 0.000325 | -0.006022 | 0.015135 | 0.017979 | -0.00102 | 0.029951 | 0.010952
4985.8438 | 122.4976 | -0.1236 | 122.4792 | 0.13101 | -0.031363 | -0.030314 | -0.025017 | 0.022531 | 0.067269 | -0.067295 | -0.052818 | 0.056323 | -0.045424 | -0.03768 | -0.075375 | -0.040873 | -0.051798 | -0.030641 | 0.2546 | 0.092233 | 0.093282 | 0.098579 | 0.14613 | 0.19087 | 0.056301 | -0.007042 | 0.1021 | 0.000352 | 0.008096 | -0.029599 | 0.004903 | -0.006022 | 0.015135 | 0.022557 | -0.00102 | 0.029951 | 0.006374
4987.5625 | 122.5845 | -0.059509 | 122.4701 | 0.13559 | -0.035942 | -0.025735 | -0.034174 | 0.027109 | 0.062691 | -0.067295 | -0.052818 | 0.056323 | -0.040846 | -0.042259 | -0.075375 | -0.040873 | -0.051798 | -0.035219 | 0.1951 | 0.023567 | 0.033774 | 0.025335 | 0.086618 | 0.1222 | -0.007786 | -0.007042 | 0.1021 | 0.00493 | 0.003517 | -0.029599 | 0.004903 | -0.006022 | 0.010557 | 0.022557 | -0.00102 | 0.034529 | 0.010952
4989.3438 | 122.5388 | -0.091553 | 122.493 | 0.14017 | -0.040521 | -0.025735 | -0.029595 | 0.022531 | 0.076426 | -0.067295 | -0.052818 | 0.056323 | -0.045424 | -0.03768 | -0.066219 | -0.036295 | -0.051798 | -0.030641 | 0.23172 | 0.051032 | 0.065818 | 0.061958 | 0.11408 | 0.16798 | 0.024258 | -0.007042 | 0.1021 | 0.000352 | 0.008096 | -0.020443 | 0.009481 | -0.006022 | 0.015135 | 0.013401 | -0.00102 | 0.020795 | 0.006374
4991.0781 | 122.6486 | -0.050354 | 122.438 | 0.13101 | -0.035942 | -0.030314 | -0.038752 | 0.013375 | 0.062691 | -0.067295 | -0.052818 | 0.060902 | -0.050002 | -0.03768 | -0.070797 | -0.040873 | -0.04722 | -0.035219 | 0.18136 | 0.014412 | 0.02004 | 0.011602 | 0.063729 | 0.11305 | -0.016941 | -0.007042 | 0.10668 | -0.004226 | 0.008096 | -0.025021 | 0.004903 | -0.001444 | 0.010557 | 0.017979 | -0.005598 | 0.020795 | -0.002782
4992.7969 | 122.5845 | -0.068665 | 122.4518 | 0.13101 | -0.040521 | -0.034893 | -0.025017 | 0.017953 | 0.071848 | -0.062717 | -0.057396 | 0.060902 | -0.045424 | -0.046838 | -0.075375 | -0.040873 | -0.051798 | -0.035219 | 0.19967 | 0.028144 | 0.033772 | 0.043648 | 0.086618 | 0.14051 | 0.005948 | -0.01162 | 0.10668 | 0.000352 | -0.001062 | -0.029599 | 0.004903 | -0.006022 | 0.010557 | 0.017979 | -0.005598 | 0.029951 | 0.006374
4994.5938 | 122.5479 | -0.10529 | 122.4747 | 0.13101 | -0.031363 | -0.030314 | -0.029595 | 0.027109 | 0.071848 | -0.067295 | -0.052818 | 0.056323 | -0.045424 | -0.046838 | -0.075375 | -0.040873 | -0.04722 | -0.035219 | 0.23629 | 0.073923 | 0.074972 | 0.075691 | 0.1324 | 0.17713 | 0.037991 | -0.007042 | 0.1021 | 0.000352 | -0.001062 | -0.029599 | 0.004903 | -0.001444 | 0.010557 | 0.022557 | -0.005598 | 0.029951 | 0.001796
4996.4062 | 122.5342 | -0.10071 | 122.5067 | 0.13101 | -0.035942 | -0.025735 | -0.034174 | 0.017953 | 0.071848 | -0.067295 | -0.052818 | 0.065481 | -0.045424 | -0.042259 | -0.079953 | -0.036295 | -0.04722 | -0.035219 | 0.23172 | 0.064766 | 0.074973 | 0.066534 | 0.11866 | 0.17256 | 0.033413 | -0.007042 | 0.11126 | 0.000352 | 0.003517 | -0.034177 | 0.009481 | -0.001444 | 0.010557 | 0.027135 | -0.005598 | 0.034529 | 0.001796
4998.125 | 122.6486 | -0.064087 | 122.4472 | 0.13559 | -0.040521 | -0.030314 | -0.025017 | 0.017953 | 0.067269 | -0.067295 | -0.057396 | 0.056323 | -0.040846 | -0.042259 | -0.070797 | -0.045451 | -0.056376 | -0.039797 | 0.19967 | 0.023566 | 0.033773 | 0.03907 | 0.08204 | 0.13136 | -0.003208 | -0.01162 | 0.1021 | 0.00493 | 0.003517 | -0.025021 | 0.000325 | -0.0106 | 0.005979 | 0.013401 | -0.00102 | 0.029951 | 0.01553
4999.8906 | 122.6395 | -0.054932 | 122.4289 | 0.14017 | -0.035942 | -0.030314 | -0.034174 | 0.022531 | 0.067269 | -0.058139 | -0.052818 | 0.060902 | -0.045424 | -0.042259 | -0.075375 | -0.036295 | -0.051798 | -0.035219 | 0.1951 | 0.01899 | 0.024618 | 0.020758 | 0.077463 | 0.1222 | -0.003207 | -0.007042 | 0.10668 | 0.000352 | 0.003517 | -0.029599 | 0.009481 | -0.006022 | 0.010557 | 0.022557 | -0.00102 | 0.029951 | 0.006374
5001.6719 | 122.5159 | -0.09613 | 122.4701 | 0.13101 | -0.040521 | -0.030314 | -0.029595 | 0.008797 | 0.071848 | -0.067295 | -0.052818 | 0.060902 | -0.045424 | -0.03768 | -0.084531 | -0.045451 | -0.04722 | -0.039797 | 0.22714 | 0.055609 | 0.065816 | 0.066535 | 0.10493 | 0.16798 | 0.028835 | -0.007042 | 0.10668 | 0.000352 | 0.008096 | -0.038755 | 0.000325 | -0.001444 | 0.005979 | 0.031713 | -0.005598 | 0.039107 | 0.001796
5003.375 | 122.6257 | -0.068665 | 122.438 | 0.13559 | -0.031363 | -0.030314 | -0.029595 | 0.013375 | 0.076426 | -0.071874 | -0.057396 | 0.060902 | -0.036267 | -0.046838 | -0.075375 | -0.036295 | -0.051798 | -0.039797 | 0.20425 | 0.037302 | 0.038351 | 0.03907 | 0.08204 | 0.14509 | -0.003209 | -0.01162 | 0.10668 | 0.009509 | -0.001062 | -0.029599 | 0.009481 | -0.006022 | 0.005979 | 0.017979 | -0.005598 | 0.039108 | 0.015531
5005.1094 | 122.6212 | -0.082397 | 122.4747 | 0.13101 | -0.035942 | -0.025735 | -0.034174 | 0.013375 | 0.071848 | -0.067295 | -0.052818 | 0.065481 | -0.045424 | -0.03768 | -0.070797 | -0.045451 | -0.04722 | -0.039797 | 0.21341 | 0.046455 | 0.056662 | 0.048223 | 0.095772 | 0.15424 | 0.015102 | -0.007042 | 0.11126 | 0.000352 | 0.008096 | -0.025021 | 0.000325 | -0.001444 | 0.005979 | 0.017979 | -0.005598 | 0.025373 | 0.001796
5006.8594 | 122.5433 | -0.086975 | 122.5021 | 0.13559 | -0.031363 | -0.025735 | -0.034174 | 0.017953 | 0.062691 | -0.071874 | -0.057396 | 0.056323 | -0.045424 | -0.046838 | -0.084531 | -0.045451 | -0.051798 | -0.044375 | 0.22256 | 0.055612 | 0.06124 | 0.052801 | 0.10493 | 0.14967 | 0.015101 | -0.01162 | 0.1021 | 0.000352 | -0.001062 | -0.038755 | 0.000325 | -0.006022 | 0.001401 | 0.027135 | -0.005598 | 0.039107 | 0.006374
5008.5781 | 122.644 | -0.07782 | 122.4609 | 0.13101 | -0.031363 | -0.030314 | -0.034174 | 0.022531 | 0.067269 | -0.067295 | -0.057396 | 0.051744 | -0.040846 | -0.046838 | -0.070797 | -0.036295 | -0.042641 | -0.035219 | 0.20883 | 0.046457 | 0.047506 | 0.043646 | 0.10035 | 0.14509 | 0.010525 | -0.01162 | 0.09752 | 0.00493 | -0.001062 | -0.025021 | 0.009481 | 0.003135 | 0.010557 | 0.013401 | -0.014755 | 0.029951 | 0.001795
5010.3594 | 122.5616 | -0.091553 | 122.493 | 0.13101 | -0.031363 | -0.025735 | -0.029595 | 0.022531 | 0.067269 | -0.062717 | -0.061975 | 0.060902 | -0.040846 | -0.042259 | -0.066219 | -0.040873 | -0.04722 | -0.039797 | 0.22256 | 0.06019 | 0.065818 | 0.061958 | 0.11408 | 0.15882 | 0.028836 | -0.016199 | 0.10668 | 0.00493 | 0.003517 | -0.020443 | 0.004903 | -0.001444 | 0.005979 | 0.004244 | -0.014755 | 0.025373 | 0.006374
5012.0781 | 122.5113 | -0.09613 | 122.4792 | 0.13101 | -0.035942 | -0.030314 | -0.029595 | 0.017953 | 0.071848 | -0.062717 | -0.052818 | 0.056323 | -0.036267 | -0.03768 | -0.075375 | -0.050029 | -0.04722 | -0.035219 | 0.22714 | 0.060188 | 0.065816 | 0.066535 | 0.11408 | 0.16798 | 0.033413 | -0.007042 | 0.1021 | 0.009509 | 0.008096 | -0.029599 | -0.004253 | -0.001444 | 0.010557 | 0.022557 | -0.005598 | 0.039108 | 0.010953
5013.8281 | 122.6028 | -0.086975 | 122.4655 | 0.13101 | -0.035942 | -0.025735 | -0.034174 | 0.027109 | 0.071848 | -0.062717 | -0.052818 | 0.060902 | -0.040846 | -0.046838 | -0.075375 | -0.045451 | -0.04722 | -0.030641 | 0.21798 | 0.051033 | 0.06124 | 0.052801 | 0.11408 | 0.15882 | 0.024258 | -0.007042 | 0.10668 | 0.00493 | -0.001062 | -0.029599 | 0.000325 | -0.001444 | 0.015135 | 0.022557 | -0.005598 | 0.034529 | 0.006374
5015.5469 | 122.5296 | -0.10986 | 122.5067 | 0.13559 | -0.040521 | -0.021157 | -0.029595 | 0.017953 | 0.071848 | -0.071874 | -0.057396 | 0.056323 | -0.045424 | -0.03768 | -0.079953 | -0.040873 | -0.051798 | -0.035219 | 0.24545 | 0.069342 | 0.088706 | 0.080268 | 0.12782 | 0.18171 | 0.037989 | -0.01162 | 0.1021 | 0.000352 | 0.008096 | -0.034177 | 0.004903 | -0.006022 | 0.010557 | 0.022557 | -0.005598 | 0.034529 | 0.006374
5017.2969 | 122.5571 | -0.086975 | 122.4655 | 0.13101 | -0.026784 | -0.034893 | -0.029595 | 0.017953 | 0.071848 | -0.067295 | -0.061975 | 0.056323 | -0.045424 | -0.03768 | -0.075375 | -0.040873 | -0.051798 | -0.039797 | 0.21798 | 0.060191 | 0.052082 | 0.05738 | 0.10493 | 0.15882 | 0.01968 | -0.016199 | 0.1021 | 0.000352 | 0.008096 | -0.029599 | 0.004903 | -0.006022 | 0.005979 | 0.0134 | -0.010177 | 0.029951 | 0.006374
5019.0156 | 122.5983 | -0.07782 | 122.4518 | 0.13101 | -0.035942 | -0.025735 | -0.020438 | 0.017953 | 0.071848 | -0.067295 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.079953 | -0.040873 | -0.04722 | -0.035219 | 0.20883 | 0.041878 | 0.052085 | 0.057382 | 0.095773 | 0.14967 | 0.010525 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.034177 | 0.004903 | -0.001444 | 0.010557 | 0.031714 | -0.001019 | 0.039107 | 0.006374
5020.7812 | 122.5845 | -0.10071 | 122.4747 | 0.13101 | -0.040521 | -0.034893 | -0.029595 | 0.013375 | 0.067269 | -0.067295 | -0.043661 | 0.060902 | -0.045424 | -0.042259 | -0.075375 | -0.045451 | -0.056376 | -0.030641 | 0.23172 | 0.060187 | 0.065815 | 0.071113 | 0.11408 | 0.16798 | 0.033413 | 0.002115 | 0.10668 | 0.000352 | 0.003517 | -0.029599 | 0.000325 | -0.0106 | 0.015135 | 0.031714 | 0.012715 | 0.029951 | 0.010952
5022.4844 | 122.5983 | -0.064087 | 122.4609 | 0.13101 | -0.035942 | -0.025735 | -0.029595 | 0.022531 | 0.067269 | -0.067295 | -0.061975 | 0.056323 | -0.045424 | -0.042259 | -0.079953 | -0.050029 | -0.051798 | -0.030641 | 0.1951 | 0.028145 | 0.038352 | 0.034492 | 0.086618 | 0.13136 | -0.003208 | -0.016199 | 0.1021 | 0.000352 | 0.003517 | -0.034177 | -0.004253 | -0.006022 | 0.015135 | 0.017978 | -0.010177 | 0.034529 | 0.006374
5024.2031 | 122.6624 | -0.054932 | 122.4518 | 0.14017 | -0.040521 | -0.034893 | -0.029595 | 0.013375 | 0.062691 | -0.062717 | -0.052818 | 0.056323 | -0.040846 | -0.046838 | -0.066219 | -0.036295 | -0.051798 | -0.035219 | 0.1951 | 0.014411 | 0.020039 | 0.025337 | 0.068307 | 0.11762 | -0.007785 | -0.007042 | 0.1021 | 0.00493 | -0.001062 | -0.020443 | 0.009481 | -0.006022 | 0.010557 | 0.013401 | -0.00102 | 0.025373 | 0.010952
5025.9219 | 122.6624 | -0.068665 | 122.4838 | 0.14474 | -0.040521 | -0.021157 | -0.025017 | 0.022531 | 0.071848 | -0.062717 | -0.052818 | 0.065481 | -0.040846 | -0.051417 | -0.066219 | -0.036295 | -0.051798 | -0.035219 | 0.21341 | 0.028144 | 0.047508 | 0.043648 | 0.091196 | 0.14051 | 0.005948 | -0.007042 | 0.11126 | 0.00493 | -0.005641 | -0.020443 | 0.009481 | -0.006022 | 0.010557 | 0.013401 | -0.00102 | 0.025373 | 0.010952
5027.6562 | 122.5525 | -0.11444 | 122.4976 | 0.13559 | -0.035942 | -0.030314 | -0.029595 | 0.017953 | 0.071848 | -0.062717 | -0.057396 | 0.060902 | -0.036267 | -0.03768 | -0.079953 | -0.050029 | -0.056376 | -0.035219 | 0.25003 | 0.078499 | 0.084127 | 0.084846 | 0.13239 | 0.18629 | 0.051724 | -0.01162 | 0.10668 | 0.009509 | 0.008096 | -0.034177 | -0.004253 | -0.0106 | 0.010557 | 0.022557 | -0.00102 | 0.043686 | 0.020109
5029.375 | 122.5204 | -0.10529 | 122.5067 | 0.13101 | -0.031363 | -0.034893 | -0.034174 | 0.013375 | 0.062691 | -0.067295 | -0.057396 | 0.056323 | -0.045424 | -0.03768 | -0.075375 | -0.040873 | -0.056376 | -0.035219 | 0.23629 | 0.073923 | 0.070393 | 0.071112 | 0.11866 | 0.16798 | 0.037991 | -0.01162 | 0.1021 | 0.000352 | 0.008096 | -0.029599 | 0.004903 | -0.0106 | 0.010557 | 0.017979 | -0.00102 | 0.029951 | 0.010952
5031.0781 | 122.644 | -0.050354 | 122.4792 | 0.13101 | -0.0451 | -0.030314 | -0.025017 | 0.017953 | 0.071848 | -0.067295 | -0.057396 | 0.065481 | -0.045424 | -0.03768 | -0.070797 | -0.045451 | -0.056376 | -0.035219 | 0.18136 | 0.005254 | 0.02004 | 0.025337 | 0.068307 | 0.1222 | -0.016941 | -0.01162 | 0.11126 | 0.000352 | 0.008096 | -0.025021 | 0.000325 | -0.0106 | 0.010557 | 0.013401 | -0.00102 | 0.025373 | 0.010952
5032.7969 | 122.6028 | -0.086975 | 122.4747 | 0.14017 | -0.035942 | -0.034893 | -0.025017 | 0.017953 | 0.062691 | -0.062717 | -0.057396 | 0.051744 | -0.045424 | -0.03768 | -0.070797 | -0.040873 | -0.04722 | -0.035219 | 0.22714 | 0.051033 | 0.052082 | 0.061958 | 0.10493 | 0.14967 | 0.024258 | -0.01162 | 0.09752 | 0.000352 | 0.008096 | -0.025021 | 0.004903 | -0.001444 | 0.010557 | 0.013401 | -0.010176 | 0.025373 | 0.001796
5034.5156 | 122.6349 | -0.068665 | 122.4701 | 0.13101 | -0.035942 | -0.034893 | -0.029595 | 0.022531 | 0.067269 | -0.071874 | -0.052818 | 0.060902 | -0.036267 | -0.046838 | -0.070797 | -0.050029 | -0.056376 | -0.035219 | 0.19967 | 0.032723 | 0.033772 | 0.03907 | 0.091196 | 0.13593 | -0.003209 | -0.007042 | 0.10668 | 0.009509 | -0.001062 | -0.025021 | -0.004253 | -0.0106 | 0.010557 | 0.017979 | 0.003558 | 0.03453 | 0.020109
5036.3906 | 122.6532 | -0.059509 | 122.493 | 0.13101 | -0.031363 | -0.034893 | -0.034174 | 0.013375 | 0.062691 | -0.067295 | -0.052818 | 0.060902 | -0.036267 | -0.03768 | -0.075375 | -0.040873 | -0.051798 | -0.035219 | 0.19052 | 0.028146 | 0.024616 | 0.025335 | 0.072884 | 0.1222 | -0.007786 | -0.007042 | 0.10668 | 0.009509 | 0.008096 | -0.029599 | 0.004903 | -0.006022 | 0.010557 | 0.022557 | -0.00102 | 0.039108 | 0.015531
5038.1406 | 122.5067 | -0.10071 | 122.5159 | 0.13101 | -0.035942 | -0.021157 | -0.025017 | 0.017953 | 0.067269 | -0.071874 | -0.057396 | 0.056323 | -0.045424 | -0.042259 | -0.070797 | -0.040873 | -0.056376 | -0.035219 | 0.23172 | 0.064766 | 0.079551 | 0.075691 | 0.11866 | 0.16798 | 0.028834 | -0.01162 | 0.1021 | 0.000352 | 0.003517 | -0.025021 | 0.004903 | -0.0106 | 0.010557 | 0.013401 | -0.00102 | 0.025373 | 0.010952
5039.9219 | 122.5525 | -0.11902 | 122.5021 | 0.13559 | -0.035942 | -0.025735 | -0.034174 | 0.013375 | 0.067269 | -0.067295 | -0.052818 | 0.056323 | -0.050002 | -0.042259 | -0.070797 | -0.036295 | -0.051798 | -0.035219 | 0.25461 | 0.083077 | 0.093284 | 0.084845 | 0.13239 | 0.18629 | 0.051724 | -0.007042 | 0.1021 | -0.004226 | 0.003517 | -0.025021 | 0.009481 | -0.006022 | 0.010557 | 0.017979 | -0.00102 | 0.020795 | 0.001796
5041.6562 | 122.612 | -0.068665 | 122.4838 | 0.14017 | -0.035942 | -0.030314 | -0.034174 | 0.017953 | 0.062691 | -0.071874 | -0.048239 | 0.056323 | -0.045424 | -0.042259 | -0.075375 | -0.045451 | -0.051798 | -0.035219 | 0.20883 | 0.032723 | 0.038351 | 0.034491 | 0.086618 | 0.13136 | -0.003209 | -0.002463 | 0.1021 | 0.000352 | 0.003517 | -0.029599 | 0.000325 | -0.006022 | 0.010557 | 0.027136 | 0.003559 | 0.029951 | 0.006374
5043.4375 | 122.5754 | -0.082397 | 122.4792 | 0.13101 | -0.035942 | -0.025735 | -0.038752 | 0.013375 | 0.071848 | -0.071874 | -0.052818 | 0.056323 | -0.045424 | -0.042259 | -0.066219 | -0.045451 | -0.04722 | -0.030641 | 0.21341 | 0.046455 | 0.056662 | 0.043645 | 0.095772 | 0.15424 | 0.010523 | -0.007042 | 0.1021 | 0.000352 | 0.003517 | -0.020443 | 0.000325 | -0.001444 | 0.015135 | 0.013401 | -0.005598 | 0.020795 | 0.001796
5045.2188 | 122.5204 | -0.12817 | 122.5113 | 0.13101 | -0.031363 | -0.025735 | -0.01586 | 0.017953 | 0.071848 | -0.058139 | -0.057396 | 0.060902 | -0.045424 | -0.03768 | -0.075375 | -0.050029 | -0.051798 | -0.035219 | 0.25918 | 0.096811 | 0.10244 | 0.11231 | 0.14613 | 0.20002 | 0.070035 | -0.01162 | 0.10668 | 0.000352 | 0.008096 | -0.029599 | -0.004253 | -0.006022 | 0.010557 | 0.017979 | -0.005598 | 0.029951 | 0.006374
5047 | 122.5388 | -0.10071 | 122.5021 | 0.13101 | -0.031363 | -0.025735 | -0.034174 | 0.022531 | 0.062691 | -0.067295 | -0.061975 | 0.051744 | -0.050002 | -0.042259 | -0.070797 | -0.045451 | -0.04722 | -0.039797 | 0.23172 | 0.069345 | 0.074973 | 0.066534 | 0.12324 | 0.1634 | 0.033413 | -0.016199 | 0.09752 | -0.004226 | 0.003517 | -0.025021 | 0.000325 | -0.001444 | 0.005979 | 0.008822 | -0.014755 | 0.020795 | -0.002782
5048.7188 | 122.58 | -0.12817 | 122.5296 | 0.13101 | -0.035942 | -0.034893 | -0.025017 | 0.017953 | 0.071848 | -0.062717 | -0.048239 | 0.056323 | -0.045424 | -0.042259 | -0.075375 | -0.045451 | -0.051798 | -0.044375 | 0.25918 | 0.092232 | 0.093281 | 0.10316 | 0.14613 | 0.20002 | 0.065457 | -0.002463 | 0.1021 | 0.000352 | 0.003517 | -0.029599 | 0.000325 | -0.006022 | 0.001401 | 0.027136 | 0.003559 | 0.029951 | 0.006374
5050.4844 | 122.5891 | -0.086975 | 122.5113 | 0.13559 | -0.031363 | -0.034893 | -0.029595 | 0.017953 | 0.062691 | -0.067295 | -0.057396 | 0.060902 | -0.040846 | -0.046838 | -0.079953 | -0.040873 | -0.04722 | -0.044375 | 0.22256 | 0.055612 | 0.052082 | 0.05738 | 0.10493 | 0.14967 | 0.01968 | -0.01162 | 0.10668 | 0.00493 | -0.001062 | -0.034177 | 0.004903 | -0.001444 | 0.001401 | 0.022557 | -0.010176 | 0.039107 | 0.006374
5052.2656 | 122.5845 | -0.10529 | 122.4792 | 0.13101 | -0.031363 | -0.034893 | -0.025017 | 0.022531 | 0.071848 | -0.071874 | -0.052818 | 0.056323 | -0.045424 | -0.03768 | -0.084531 | -0.040873 | -0.04722 | -0.030641 | 0.23629 | 0.073923 | 0.070393 | 0.080269 | 0.12782 | 0.17713 | 0.033412 | -0.007042 | 0.1021 | 0.000352 | 0.008096 | -0.038755 | 0.004903 | -0.001444 | 0.015135 | 0.031713 | -0.005598 | 0.039107 | 0.001796
5054.0625 | 122.6074 | -0.086975 | 122.4838 | 0.13101 | -0.026784 | -0.030314 | -0.029595 | 0.027109 | 0.062691 | -0.062717 | -0.057396 | 0.060902 | -0.050002 | -0.03768 | -0.075375 | -0.040873 | -0.051798 | -0.035219 | 0.21798 | 0.060191 | 0.056661 | 0.05738 | 0.11408 | 0.14967 | 0.024258 | -0.01162 | 0.10668 | -0.004226 | 0.008096 | -0.029599 | 0.004903 | -0.006022 | 0.010557 | 0.017979 | -0.005598 | 0.025373 | 0.001796
5055.8438 | 122.5891 | -0.10071 | 122.5296 | 0.13101 | -0.031363 | -0.021157 | -0.029595 | 0.013375 | 0.076426 | -0.067295 | -0.057396 | 0.056323 | -0.040846 | -0.03768 | -0.070797 | -0.045451 | -0.051798 | -0.035219 | 0.23172 | 0.069345 | 0.079551 | 0.071113 | 0.11408 | 0.17713 | 0.033413 | -0.01162 | 0.1021 | 0.00493 | 0.008096 | -0.025021 | 0.000325 | -0.006022 | 0.010557 | 0.013401 | -0.005598 | 0.029951 | 0.010952
5057.5469 | 122.6624 | -0.059509 | 122.4564 | 0.13101 | -0.031363 | -0.034893 | -0.029595 | 0.022531 | 0.067269 | -0.067295 | -0.057396 | 0.047165 | -0.045424 | -0.042259 | -0.070797 | -0.036295 | -0.051798 | -0.039797 | 0.19052 | 0.028146 | 0.024616 | 0.029914 | 0.08204 | 0.12678 | -0.007786 | -0.01162 | 0.092941 | 0.000352 | 0.003517 | -0.025021 | 0.009481 | -0.006022 | 0.005979 | 0.013401 | -0.005598 | 0.025373 | 0.006374
5059.3281 | 122.5342 | -0.1236 | 122.5159 | 0.14017 | -0.040521 | -0.030314 | -0.029595 | 0.017953 | 0.067269 | -0.067295 | -0.048239 | 0.051744 | -0.045424 | -0.042259 | -0.070797 | -0.040873 | -0.04722 | -0.039797 | 0.26376 | 0.083075 | 0.093282 | 0.094001 | 0.14155 | 0.19087 | 0.056301 | -0.002463 | 0.09752 | 0.000352 | 0.003517 | -0.025021 | 0.004903 | -0.001444 | 0.005979 | 0.022558 | -0.001019 | 0.025373 | 0.001796
5061.0469 | 122.5204 | -0.10071 | 122.5067 | 0.13559 | -0.031363 | -0.030314 | -0.034174 | 0.013375 | 0.062691 | -0.067295 | -0.057396 | 0.060902 | -0.040846 | -0.03768 | -0.079953 | -0.040873 | -0.051798 | -0.039797 | 0.23629 | 0.069345 | 0.070394 | 0.066534 | 0.11408 | 0.1634 | 0.033413 | -0.01162 | 0.10668 | 0.00493 | 0.008096 | -0.034177 | 0.004903 | -0.006022 | 0.005979 | 0.022557 | -0.005598 | 0.039107 | 0.010952
5062.8125 | 122.5571 | -0.09613 | 122.5296 | 0.13101 | -0.031363 | -0.025735 | -0.025017 | 0.013375 | 0.076426 | -0.062717 | -0.052818 | 0.056323 | -0.040846 | -0.046838 | -0.075375 | -0.040873 | -0.051798 | -0.030641 | 0.22714 | 0.064767 | 0.070395 | 0.071113 | 0.1095 | 0.17256 | 0.033413 | -0.007042 | 0.1021 | 0.00493 | -0.001062 | -0.029599 | 0.004903 | -0.006022 | 0.015135 | 0.022557 | -0.00102 | 0.034529 | 0.010952
5064.5312 | 122.5479 | -0.10529 | 122.5204 | 0.12643 | -0.031363 | -0.025735 | -0.025017 | 0.013375 | 0.071848 | -0.062717 | -0.052818 | 0.060902 | -0.040846 | -0.046838 | -0.066219 | -0.040873 | -0.051798 | -0.030641 | 0.23172 | 0.073923 | 0.079551 | 0.080269 | 0.11866 | 0.17713 | 0.042569 | -0.007042 | 0.10668 | 0.00493 | -0.001062 | -0.020443 | 0.004903 | -0.006022 | 0.015135 | 0.013401 | -0.00102 | 0.025373 | 0.010952
5066.3125 | 122.5525 | -0.09613 | 122.5204 | 0.13101 | -0.035942 | -0.025735 | -0.029595 | 0.017953 | 0.062691 | -0.071874 | -0.048239 | 0.060902 | -0.040846 | -0.046838 | -0.079953 | -0.031717 | -0.051798 | -0.030641 | 0.22714 | 0.060188 | 0.070395 | 0.066535 | 0.11408 | 0.15882 | 0.024256 | -0.002463 | 0.10668 | 0.00493 | -0.001062 | -0.034177 | 0.014059 | -0.006022 | 0.015135 | 0.031714 | 0.003559 | 0.039107 | 0.010952
5068.0312 | 122.5296 | -0.11902 | 122.5067 | 0.13559 | -0.035942 | -0.030314 | -0.025017 | 0.013375 | 0.067269 | -0.062717 | -0.052818 | 0.060902 | -0.040846 | -0.03768 | -0.079953 | -0.040873 | -0.051798 | -0.039797 | 0.25461 | 0.083077 | 0.088705 | 0.094002 | 0.13239 | 0.18629 | 0.056302 | -0.007042 | 0.10668 | 0.00493 | 0.008096 | -0.034177 | 0.004903 | -0.006022 | 0.005979 | 0.027135 | -0.00102 | 0.039107 | 0.010952
5069.8281 | 122.6166 | -0.073242 | 122.4976 | 0.14017 | -0.031363 | -0.030314 | -0.025017 | 0.013375 | 0.058113 | -0.062717 | -0.057396 | 0.060902 | -0.050002 | -0.03768 | -0.079953 | -0.040873 | -0.060955 | -0.035219 | 0.21341 | 0.041879 | 0.042928 | 0.048225 | 0.086617 | 0.13135 | 0.010525 | -0.01162 | 0.10668 | -0.004226 | 0.008096 | -0.034177 | 0.004903 | -0.015179 | 0.010557 | 0.022557 | 0.003559 | 0.029951 | 0.010953
5071.5469 | 122.5296 | -0.11444 | 122.5433 | 0.12643 | -0.031363 | -0.021157 | -0.025017 | 0.017953 | 0.062691 | -0.062717 | -0.052818 | 0.056323 | -0.050002 | -0.03768 | -0.079953 | -0.036295 | -0.04722 | -0.035219 | 0.24087 | 0.083078 | 0.093284 | 0.089424 | 0.13239 | 0.17713 | 0.051724 | -0.007042 | 0.1021 | -0.004226 | 0.008096 | -0.034177 | 0.009481 | -0.001444 | 0.010557 | 0.027135 | -0.005598 | 0.029951 | -0.002782
5073.3281 | 122.6898 | -0.059509 | 122.5021 | 0.13559 | -0.031363 | -0.021157 | -0.029595 | 0.013375 | 0.071848 | -0.067295 | -0.052818 | 0.056323 | -0.050002 | -0.042259 | -0.070797 | -0.040873 | -0.051798 | -0.030641 | 0.1951 | 0.028146 | 0.038352 | 0.029914 | 0.072884 | 0.13136 | -0.007786 | -0.007042 | 0.1021 | -0.004226 | 0.003517 | -0.025021 | 0.004903 | -0.006022 | 0.015135 | 0.017979 | -0.00102 | 0.020795 | 0.001796
5075.1094 | 122.5342 | -0.11444 | 122.5342 | 0.13101 | -0.026784 | -0.025735 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.061975 | 0.056323 | -0.040846 | -0.042259 | -0.070797 | -0.036295 | -0.042641 | -0.030641 | 0.24545 | 0.087657 | 0.088706 | 0.084846 | 0.13697 | 0.18629 | 0.051724 | -0.016199 | 0.1021 | 0.00493 | 0.003517 | -0.025021 | 0.009481 | 0.003135 | 0.015135 | 0.008822 | -0.019334 | 0.029951 | 0.001795
5076.875 | 122.5571 | -0.10529 | 122.5296 | 0.13101 | -0.035942 | -0.025735 | -0.025017 | 0.013375 | 0.067269 | -0.062717 | -0.052818 | 0.060902 | -0.045424 | -0.042259 | -0.075375 | -0.040873 | -0.042641 | -0.039797 | 0.23629 | 0.069344 | 0.079551 | 0.080269 | 0.11866 | 0.17256 | 0.042569 | -0.007042 | 0.10668 | 0.000352 | 0.003517 | -0.029599 | 0.004903 | 0.003135 | 0.005979 | 0.022557 | -0.010177 | 0.029951 | -0.002783
5078.5938 | 122.6761 | -0.050354 | 122.5021 | 0.13559 | -0.035942 | -0.030314 | -0.034174 | 0.008797 | 0.062691 | -0.071874 | -0.052818 | 0.060902 | -0.040846 | -0.03768 | -0.066219 | -0.031717 | -0.04722 | -0.035219 | 0.18594 | 0.014412 | 0.02004 | 0.01618 | 0.059151 | 0.11305 | -0.02152 | -0.007042 | 0.10668 | 0.00493 | 0.008096 | -0.020443 | 0.014059 | -0.001444 | 0.010557 | 0.013401 | -0.005598 | 0.025373 | 0.006374
5080.3125 | 122.5342 | -0.091553 | 122.5296 | 0.12643 | -0.031363 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.048239 | 0.060902 | -0.045424 | -0.042259 | -0.079953 | -0.045451 | -0.042641 | -0.044375 | 0.21798 | 0.06019 | 0.061239 | 0.061958 | 0.11408 | 0.1634 | 0.028836 | -0.002463 | 0.10668 | 0.000352 | 0.003517 | -0.034177 | 0.000325 | 0.003135 | 0.001401 | 0.031714 | -0.005598 | 0.034529 | -0.002783
5082.0781 | 122.6349 | -0.059509 | 122.5113 | 0.13559 | -0.040521 | -0.034893 | -0.029595 | 0.017953 | 0.062691 | -0.071874 | -0.048239 | 0.056323 | -0.036267 | -0.042259 | -0.070797 | -0.040873 | -0.042641 | -0.035219 | 0.1951 | 0.018988 | 0.024616 | 0.029914 | 0.077462 | 0.1222 | -0.012365 | -0.002463 | 0.1021 | 0.009509 | 0.003517 | -0.025021 | 0.004903 | 0.003135 | 0.010557 | 0.022558 | -0.005598 | 0.03453 | 0.006374
5083.7969 | 122.5433 | -0.11444 | 122.5342 | 0.13101 | -0.035942 | -0.030314 | -0.029595 | 0.013375 | 0.067269 | -0.062717 | -0.052818 | 0.056323 | -0.050002 | -0.03768 | -0.066219 | -0.040873 | -0.051798 | -0.035219 | 0.24545 | 0.078499 | 0.084127 | 0.084846 | 0.12782 | 0.18171 | 0.051724 | -0.007042 | 0.1021 | -0.004226 | 0.008096 | -0.020443 | 0.004903 | -0.006022 | 0.010557 | 0.013401 | -0.00102 | 0.016217 | 0.001796
5085.5625 | 122.5433 | -0.10071 | 122.5388 | 0.13559 | -0.040521 | -0.030314 | -0.025017 | 0.013375 | 0.067269 | -0.067295 | -0.052818 | 0.07006 | -0.036267 | -0.042259 | -0.075375 | -0.040873 | -0.04722 | -0.030641 | 0.23629 | 0.060187 | 0.070394 | 0.075691 | 0.11408 | 0.16798 | 0.033413 | -0.007042 | 0.11584 | 0.009509 | 0.003517 | -0.029599 | 0.004903 | -0.001444 | 0.015135 | 0.022557 | -0.005598 | 0.039108 | 0.010953
5087.3281 | 122.5296 | -0.10071 | 122.5433 | 0.12643 | -0.035942 | -0.025735 | -0.034174 | 0.022531 | 0.067269 | -0.067295 | -0.052818 | 0.060902 | -0.045424 | -0.042259 | -0.075375 | -0.040873 | -0.04722 | -0.030641 | 0.22714 | 0.064766 | 0.074973 | 0.066534 | 0.12324 | 0.16798 | 0.033413 | -0.007042 | 0.10668 | 0.000352 | 0.003517 | -0.029599 | 0.004903 | -0.001444 | 0.015135 | 0.022557 | -0.005598 | 0.029951 | 0.001796
5089.0625 | 122.5571 | -0.10986 | 122.5342 | 0.14017 | -0.035942 | -0.030314 | -0.034174 | 0.017953 | 0.071848 | -0.067295 | -0.048239 | 0.051744 | -0.050002 | -0.051417 | -0.070797 | -0.036295 | -0.042641 | -0.035219 | 0.25003 | 0.073921 | 0.079549 | 0.075689 | 0.12782 | 0.18171 | 0.042568 | -0.002463 | 0.09752 | -0.004226 | -0.005641 | -0.025021 | 0.009481 | 0.003135 | 0.010557 | 0.022558 | -0.005598 | 0.020795 | -0.007361
5090.8438 | 122.6028 | -0.07782 | 122.5067 | 0.13559 | -0.035942 | -0.030314 | -0.034174 | 0.022531 | 0.076426 | -0.067295 | -0.057396 | 0.056323 | -0.045424 | -0.042259 | -0.066219 | -0.036295 | -0.04722 | -0.026063 | 0.21341 | 0.041878 | 0.047506 | 0.043646 | 0.10035 | 0.15425 | 0.010525 | -0.01162 | 0.1021 | 0.000352 | 0.003517 | -0.020443 | 0.009481 | -0.001444 | 0.019713 | 0.008823 | -0.010176 | 0.020795 | 0.001796
5092.5469 | 122.6624 | -0.064087 | 122.5113 | 0.13101 | -0.035942 | -0.039471 | -0.029595 | 0.013375 | 0.062691 | -0.071874 | -0.052818 | 0.060902 | -0.036267 | -0.042259 | -0.075375 | -0.045451 | -0.051798 | -0.030641 | 0.1951 | 0.028145 | 0.024616 | 0.034492 | 0.077462 | 0.12678 | -0.007787 | -0.007042 | 0.10668 | 0.009509 | 0.003517 | -0.029599 | 0.000325 | -0.006022 | 0.015135 | 0.022557 | -0.00102 | 0.039108 | 0.015531
5094.3281 | 122.5983 | -0.091553 | 122.5159 | 0.12185 | -0.026784 | -0.025735 | -0.029595 | 0.008797 | 0.071848 | -0.058139 | -0.057396 | 0.065481 | -0.040846 | -0.042259 | -0.070797 | -0.040873 | -0.04722 | -0.035219 | 0.2134 | 0.064769 | 0.065818 | 0.061958 | 0.10035 | 0.1634 | 0.033414 | -0.01162 | 0.11126 | 0.00493 | 0.003517 | -0.025021 | 0.004903 | -0.001444 | 0.010557 | 0.013401 | -0.010176 | 0.029951 | 0.006374
5096.0312 | 122.5662 | -0.11444 | 122.5296 | 0.13559 | -0.040521 | -0.025735 | -0.025017 | 0.017953 | 0.058113 | -0.067295 | -0.048239 | 0.060902 | -0.045424 | -0.046838 | -0.079953 | -0.040873 | -0.04722 | -0.026063 | 0.25003 | 0.07392 | 0.088706 | 0.089424 | 0.13239 | 0.17255 | 0.047146 | -0.002463 | 0.10668 | 0.000352 | -0.001062 | -0.034177 | 0.004903 | -0.001444 | 0.019713 | 0.031714 | -0.001019 | 0.034529 | 0.001796
5097.7969 | 122.5571 | -0.10071 | 122.5342 | 0.13559 | -0.026784 | -0.021157 | -0.025017 | 0.017953 | 0.071848 | -0.062717 | -0.066553 | 0.056323 | -0.040846 | -0.03768 | -0.070797 | -0.045451 | -0.051798 | -0.030641 | 0.23629 | 0.073924 | 0.079551 | 0.075691 | 0.11866 | 0.17256 | 0.037991 | -0.020777 | 0.1021 | 0.00493 | 0.008096 | -0.025021 | 0.000325 | -0.006022 | 0.015135 | 0.004244 | -0.014755 | 0.029951 | 0.010952
5099.5781 | 122.644 | -0.073242 | 122.4976 | 0.13101 | -0.031363 | -0.034893 | -0.029595 | 0.013375 | 0.058113 | -0.076452 | -0.057396 | 0.060902 | -0.050002 | -0.051417 | -0.075375 | -0.036295 | -0.04722 | -0.035219 | 0.20425 | 0.041879 | 0.038349 | 0.043647 | 0.086617 | 0.13135 | -0.00321 | -0.01162 | 0.10668 | -0.004226 | -0.005641 | -0.029599 | 0.009481 | -0.001444 | 0.010557 | 0.017979 | -0.010176 | 0.025373 | -0.002782
5101.3594 | 122.6852 | -0.064087 | 122.4884 | 0.13559 | -0.035942 | -0.030314 | -0.025017 | 0.017953 | 0.062691 | -0.067295 | -0.052818 | 0.060902 | -0.036267 | -0.042259 | -0.079953 | -0.040873 | -0.051798 | -0.039797 | 0.19967 | 0.028145 | 0.033773 | 0.03907 | 0.08204 | 0.12678 | -0.003208 | -0.007042 | 0.10668 | 0.009509 | 0.003517 | -0.034177 | 0.004903 | -0.006022 | 0.005979 | 0.027135 | -0.00102 | 0.043686 | 0.015531
5103.0781 | 122.5662 | -0.10529 | 122.525 | 0.13101 | -0.026784 | -0.039471 | -0.025017 | 0.013375 | 0.067269 | -0.062717 | -0.061975 | 0.060902 | -0.045424 | -0.033101 | -0.075375 | -0.040873 | -0.04722 | -0.030641 | 0.23629 | 0.078502 | 0.065815 | 0.080269 | 0.11866 | 0.17256 | 0.042569 | -0.016199 | 0.10668 | 0.000352 | 0.012675 | -0.029599 | 0.004903 | -0.001444 | 0.015135 | 0.0134 | -0.014755 | 0.029951 | 0.001796
5104.875 | 122.6166 | -0.082397 | 122.5113 | 0.13559 | -0.035942 | -0.034893 | -0.029595 | 0.022531 | 0.067269 | -0.071874 | -0.057396 | 0.060902 | -0.040846 | -0.042259 | -0.070797 | -0.045451 | -0.051798 | -0.030641 | 0.21798 | 0.046455 | 0.047504 | 0.052802 | 0.10493 | 0.14967 | 0.010523 | -0.01162 | 0.10668 | 0.00493 | 0.003517 | -0.025021 | 0.000325 | -0.006022 | 0.015135 | 0.013401 | -0.005598 | 0.029951 | 0.010952
5106.6562 | 122.5479 | -0.1236 | 122.5433 | 0.13559 | -0.022205 | -0.025735 | -0.034174 | 0.013375 | 0.067269 | -0.062717 | -0.052818 | 0.056323 | -0.040846 | -0.03768 | -0.079953 | -0.036295 | -0.04722 | -0.026063 | 0.25918 | 0.10139 | 0.097861 | 0.089422 | 0.13697 | 0.19087 | 0.060879 | -0.007042 | 0.1021 | 0.00493 | 0.008096 | -0.034177 | 0.009481 | -0.001444 | 0.019713 | 0.027135 | -0.005598 | 0.039107 | 0.006374
5108.3594 | 122.5433 | -0.11444 | 122.5525 | 0.13559 | -0.031363 | -0.021157 | -0.029595 | 0.008797 | 0.067269 | -0.071874 | -0.048239 | 0.065481 | -0.040846 | -0.042259 | -0.075375 | -0.040873 | -0.051798 | -0.039797 | 0.25003 | 0.083078 | 0.093284 | 0.084846 | 0.12324 | 0.18171 | 0.042567 | -0.002463 | 0.11126 | 0.00493 | 0.003517 | -0.029599 | 0.004903 | -0.006022 | 0.005979 | 0.027136 | 0.003559 | 0.034529 | 0.010952
5110.1406 | 122.6898 | -0.050354 | 122.4747 | 0.13559 | -0.035942 | -0.034893 | -0.025017 | 0.017953 | 0.071848 | -0.071874 | -0.052818 | 0.060902 | -0.040846 | -0.046838 | -0.075375 | -0.045451 | -0.042641 | -0.030641 | 0.18594 | 0.014412 | 0.015461 | 0.025337 | 0.068307 | 0.1222 | -0.02152 | -0.007042 | 0.10668 | 0.00493 | -0.001062 | -0.029599 | 0.000325 | 0.003135 | 0.015135 | 0.022557 | -0.010177 | 0.034529 | 0.001795
5111.8594 | 122.6852 | -0.064087 | 122.5113 | 0.13559 | -0.031363 | -0.021157 | -0.029595 | 0.022531 | 0.067269 | -0.067295 | -0.052818 | 0.056323 | -0.040846 | -0.042259 | -0.070797 | -0.036295 | -0.04722 | -0.035219 | 0.19967 | 0.032724 | 0.04293 | 0.034492 | 0.086618 | 0.13136 | -0.003208 | -0.007042 | 0.1021 | 0.00493 | 0.003517 | -0.025021 | 0.009481 | -0.001444 | 0.010557 | 0.017979 | -0.005598 | 0.029951 | 0.006374
5113.6406 | 122.6898 | -0.064087 | 122.5067 | 0.13559 | -0.035942 | -0.030314 | -0.034174 | 0.017953 | 0.067269 | -0.062717 | -0.052818 | 0.060902 | -0.040846 | -0.03768 | -0.070797 | -0.040873 | -0.051798 | -0.030641 | 0.19967 | 0.028145 | 0.033773 | 0.029913 | 0.08204 | 0.13136 | 0.00137 | -0.007042 | 0.10668 | 0.00493 | 0.008096 | -0.025021 | 0.004903 | -0.006022 | 0.015135 | 0.017979 | -0.00102 | 0.029951 | 0.010952
5115.4219 | 122.699 | -0.068665 | 122.5204 | 0.13101 | -0.035942 | -0.025735 | -0.034174 | 0.022531 | 0.071848 | -0.067295 | -0.052818 | 0.065481 | -0.050002 | -0.03768 | -0.070797 | -0.045451 | -0.04722 | -0.030641 | 0.19967 | 0.032723 | 0.04293 | 0.034491 | 0.091196 | 0.14051 | 0.00137 | -0.007042 | 0.11126 | -0.004226 | 0.008096 | -0.025021 | 0.000325 | -0.001444 | 0.015135 | 0.017979 | -0.005598 | 0.020795 | -0.002782
5117.125 | 122.5571 | -0.11444 | 122.5388 | 0.13559 | -0.026784 | -0.030314 | -0.029595 | 0.017953 | 0.067269 | -0.062717 | -0.052818 | 0.060902 | -0.050002 | -0.042259 | -0.075375 | -0.036295 | -0.042641 | -0.026063 | 0.25003 | 0.087657 | 0.084127 | 0.084846 | 0.13239 | 0.18171 | 0.051724 | -0.007042 | 0.10668 | -0.004226 | 0.003517 | -0.029599 | 0.009481 | 0.003135 | 0.019713 | 0.022557 | -0.010177 | 0.025373 | -0.007361
5118.8906 | 122.5616 | -0.10986 | 122.5433 | 0.13101 | -0.040521 | -0.034893 | -0.025017 | 0.017953 | 0.067269 | -0.067295 | -0.052818 | 0.065481 | -0.045424 | -0.042259 | -0.079953 | -0.036295 | -0.04722 | -0.039797 | 0.24087 | 0.069342 | 0.07497 | 0.084846 | 0.12782 | 0.17713 | 0.042568 | -0.007042 | 0.11126 | 0.000352 | 0.003517 | -0.034177 | 0.009481 | -0.001444 | 0.005979 | 0.027135 | -0.005598 | 0.034529 | 0.001796
5120.6562 | 122.5708 | -0.12817 | 122.5159 | 0.12643 | -0.035942 | -0.034893 | -0.025017 | 0.013375 | 0.071848 | -0.067295 | -0.057396 | 0.065481 | -0.036267 | -0.042259 | -0.075375 | -0.045451 | -0.042641 | -0.030641 | 0.2546 | 0.092232 | 0.093281 | 0.10316 | 0.14155 | 0.20002 | 0.060879 | -0.01162 | 0.11126 | 0.009509 | 0.003517 | -0.029599 | 0.000325 | 0.003135 | 0.015135 | 0.017979 | -0.014755 | 0.039108 | 0.006374
5122.375 | 122.6395 | -0.091553 | 122.5296 | 0.13101 | -0.040521 | -0.030314 | -0.034174 | 0.013375 | 0.067269 | -0.062717 | -0.052818 | 0.065481 | -0.045424 | -0.03768 | -0.079953 | -0.045451 | -0.042641 | -0.030641 | 0.22256 | 0.051032 | 0.061239 | 0.057379 | 0.10493 | 0.15882 | 0.028836 | -0.007042 | 0.11126 | 0.000352 | 0.008096 | -0.034177 | 0.000325 | 0.003135 | 0.015135 | 0.027135 | -0.010177 | 0.034529 | -0.002783
5124.1562 | 122.612 | -0.10529 | 122.5388 | 0.12643 | -0.026784 | -0.030314 | -0.029595 | 0.017953 | 0.062691 | -0.067295 | -0.048239 | 0.051744 | -0.05458 | -0.03768 | -0.070797 | -0.045451 | -0.051798 | -0.039797 | 0.23172 | 0.078502 | 0.074972 | 0.075691 | 0.12324 | 0.16798 | 0.037991 | -0.002463 | 0.09752 | -0.008804 | 0.008096 | -0.025021 | 0.000325 | -0.006022 | 0.005979 | 0.022558 | 0.003559 | 0.016217 | -0.002782
5125.9375 | 122.6028 | -0.10986 | 122.5296 | 0.13101 | -0.031363 | -0.030314 | -0.034174 | 0.013375 | 0.058113 | -0.067295 | -0.057396 | 0.056323 | -0.040846 | -0.03768 | -0.070797 | -0.036295 | -0.051798 | -0.035219 | 0.24087 | 0.0785 | 0.079549 | 0.075689 | 0.12324 | 0.16798 | 0.042568 | -0.01162 | 0.1021 | 0.00493 | 0.008096 | -0.025021 | 0.009481 | -0.006022 | 0.010557 | 0.013401 | -0.005598 | 0.029951 | 0.010952
5127.7188 | 122.5616 | -0.1236 | 122.5616 | 0.13559 | -0.031363 | -0.016578 | -0.034174 | 0.022531 | 0.067269 | -0.062717 | -0.048239 | 0.065481 | -0.045424 | -0.042259 | -0.070797 | -0.040873 | -0.042641 | -0.035219 | 0.25918 | 0.092233 | 0.10702 | 0.089422 | 0.14613 | 0.19087 | 0.060879 | -0.002463 | 0.11126 | 0.000352 | 0.003517 | -0.025021 | 0.004903 | 0.003135 | 0.010557 | 0.022558 | -0.005598 | 0.025373 | -0.002783
5129.5 | 122.5754 | -0.10529 | 122.5342 | 0.14017 | -0.035942 | -0.030314 | -0.029595 | 0.008797 | 0.067269 | -0.067295 | -0.052818 | 0.056323 | -0.045424 | -0.042259 | -0.070797 | -0.036295 | -0.042641 | -0.030641 | 0.24545 | 0.069344 | 0.074972 | 0.075691 | 0.11408 | 0.17256 | 0.037991 | -0.007042 | 0.1021 | 0.000352 | 0.003517 | -0.025021 | 0.009481 | 0.003135 | 0.015135 | 0.017979 | -0.010177 | 0.025373 | -0.002783
5131.2188 | 122.5891 | -0.10986 | 122.525 | 0.14017 | -0.022205 | -0.030314 | -0.029595 | 0.013375 | 0.067269 | -0.062717 | -0.043661 | 0.060902 | -0.040846 | -0.042259 | -0.070797 | -0.036295 | -0.051798 | -0.044375 | 0.25003 | 0.087658 | 0.079549 | 0.080268 | 0.12324 | 0.17713 | 0.047146 | 0.002115 | 0.10668 | 0.00493 | 0.003517 | -0.025021 | 0.009481 | -0.006022 | 0.001401 | 0.027136 | 0.008137 | 0.029951 | 0.010952
5132.9844 | 122.644 | -0.082397 | 122.5296 | 0.13101 | -0.031363 | -0.025735 | -0.034174 | 0.008797 | 0.062691 | -0.053561 | -0.048239 | 0.056323 | -0.040846 | -0.03768 | -0.070797 | -0.045451 | -0.04722 | -0.030641 | 0.21341 | 0.051034 | 0.056662 | 0.048223 | 0.091194 | 0.14509 | 0.028836 | -0.002463 | 0.1021 | 0.00493 | 0.008096 | -0.025021 | 0.000325 | -0.001444 | 0.015135 | 0.022558 | -0.001019 | 0.029951 | 0.006374
5134.7812 | 122.612 | -0.086975 | 122.5616 | 0.12643 | -0.040521 | -0.030314 | -0.034174 | 0.008797 | 0.062691 | -0.062717 | -0.057396 | 0.065481 | -0.045424 | -0.042259 | -0.075375 | -0.036295 | -0.051798 | -0.039797 | 0.2134 | 0.046454 | 0.056661 | 0.052801 | 0.095772 | 0.14967 | 0.024258 | -0.01162 | 0.11126 | 0.000352 | 0.003517 | -0.029599 | 0.009481 | -0.006022 | 0.005979 | 0.017979 | -0.005598 | 0.029951 | 0.006374
5136.5625 | 122.6303 | -0.091553 | 122.5616 | 0.13101 | -0.040521 | -0.034893 | -0.025017 | 0.017953 | 0.067269 | -0.058139 | -0.061975 | 0.065481 | -0.040846 | -0.03768 | -0.070797 | -0.040873 | -0.051798 | -0.035219 | 0.22256 | 0.051032 | 0.05666 | 0.066536 | 0.10951 | 0.15882 | 0.033414 | -0.016199 | 0.11126 | 0.00493 | 0.008096 | -0.025021 | 0.004903 | -0.006022 | 0.010557 | 0.008822 | -0.010177 | 0.029951 | 0.010952
5138.2812 | 122.6761 | -0.059509 | 122.5204 | 0.13559 | -0.031363 | -0.030314 | -0.029595 | 0.013375 | 0.062691 | -0.062717 | -0.057396 | 0.056323 | -0.040846 | -0.042259 | -0.075375 | -0.045451 | -0.04722 | -0.039797 | 0.1951 | 0.028146 | 0.029195 | 0.029914 | 0.072884 | 0.1222 | -0.003208 | -0.01162 | 0.1021 | 0.00493 | 0.003517 | -0.029599 | 0.000325 | -0.001444 | 0.005979 | 0.017979 | -0.010176 | 0.034529 | 0.006374
5140.0781 | 122.6349 | -0.10529 | 122.5708 | 0.13559 | -0.040521 | -0.025735 | -0.029595 | 0.013375 | 0.062691 | -0.062717 | -0.057396 | 0.065481 | -0.050002 | -0.042259 | -0.075375 | -0.031717 | -0.042641 | -0.035219 | 0.24087 | 0.064765 | 0.079551 | 0.075691 | 0.11866 | 0.16798 | 0.042569 | -0.01162 | 0.11126 | -0.004226 | 0.003517 | -0.029599 | 0.014059 | 0.003135 | 0.010557 | 0.017979 | -0.014755 | 0.025373 | -0.007361
5141.7969 | 122.6852 | -0.050354 | 122.5388 | 0.13101 | -0.031363 | -0.025735 | -0.029595 | 0.022531 | 0.067269 | -0.067295 | -0.052818 | 0.060902 | -0.050002 | -0.042259 | -0.075375 | -0.040873 | -0.051798 | -0.035219 | 0.18136 | 0.018991 | 0.024619 | 0.020759 | 0.072885 | 0.11762 | -0.016941 | -0.007042 | 0.10668 | -0.004226 | 0.003517 | -0.029599 | 0.004903 | -0.006022 | 0.010557 | 0.022557 | -0.00102 | 0.025373 | 0.001796
5143.5781 | 122.6807 | -0.086975 | 122.5296 | 0.13559 | -0.035942 | -0.030314 | -0.029595 | 0.017953 | 0.058113 | -0.067295 | -0.043661 | 0.056323 | -0.045424 | -0.042259 | -0.070797 | -0.040873 | -0.042641 | -0.035219 | 0.22256 | 0.051033 | 0.056661 | 0.05738 | 0.10493 | 0.14509 | 0.01968 | 0.002115 | 0.1021 | 0.000352 | 0.003517 | -0.025021 | 0.004903 | 0.003135 | 0.010557 | 0.027136 | -0.00102 | 0.025373 | -0.002783
5145.3594 | 122.6166 | -0.10071 | 122.5571 | 0.12185 | -0.040521 | -0.025735 | -0.038752 | 0.013375 | 0.058113 | -0.067295 | -0.057396 | 0.060902 | -0.040846 | -0.046838 | -0.075375 | -0.040873 | -0.051798 | -0.035219 | 0.22256 | 0.060187 | 0.074973 | 0.061956 | 0.11408 | 0.15882 | 0.033413 | -0.01162 | 0.10668 | 0.00493 | -0.001062 | -0.029599 | 0.004903 | -0.006022 | 0.010557 | 0.017979 | -0.005598 | 0.034529 | 0.010952
5147.1562 | 122.5479 | -0.11444 | 122.5525 | 0.13559 | -0.031363 | -0.030314 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.048239 | 0.051744 | -0.040846 | -0.03768 | -0.070797 | -0.036295 | -0.04722 | -0.030641 | 0.25003 | 0.083078 | 0.084127 | 0.084846 | 0.13697 | 0.18629 | 0.051724 | -0.002463 | 0.09752 | 0.00493 | 0.008096 | -0.025021 | 0.009481 | -0.001444 | 0.015135 | 0.022558 | -0.001019 | 0.029951 | 0.006374
5148.9375 | 122.7219 | -0.050354 | 122.5296 | 0.13101 | -0.040521 | -0.030314 | -0.025017 | 0.017953 | 0.071848 | -0.062717 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.079953 | -0.040873 | -0.04722 | -0.035219 | 0.18136 | 0.009833 | 0.02004 | 0.025337 | 0.068307 | 0.1222 | -0.012363 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.034177 | 0.004903 | -0.001444 | 0.010557 | 0.031714 | -0.001019 | 0.039107 | 0.006374
5150.7188 | 122.7036 | -0.050354 | 122.5433 | 0.14017 | -0.031363 | -0.030314 | -0.029595 | 0.008797 | 0.062691 | -0.067295 | -0.048239 | 0.056323 | -0.045424 | -0.042259 | -0.079953 | -0.040873 | -0.04722 | -0.039797 | 0.19052 | 0.018991 | 0.02004 | 0.020759 | 0.059151 | 0.11305 | -0.016941 | -0.002463 | 0.1021 | 0.000352 | 0.003517 | -0.034177 | 0.004903 | -0.001444 | 0.005979 | 0.031714 | -0.001019 | 0.034529 | 0.001796
5152.4375 | 122.612 | -0.11444 | 122.5662 | 0.13559 | -0.035942 | -0.025735 | -0.025017 | 0.013375 | 0.067269 | -0.062717 | -0.048239 | 0.051744 | -0.040846 | -0.046838 | -0.070797 | -0.040873 | -0.04722 | -0.035219 | 0.25003 | 0.078499 | 0.088706 | 0.089424 | 0.12782 | 0.18171 | 0.051724 | -0.002463 | 0.09752 | 0.00493 | -0.001062 | -0.025021 | 0.004903 | -0.001444 | 0.010557 | 0.022558 | -0.001019 | 0.029951 | 0.006374
5154.2188 | 122.6212 | -0.09613 | 122.5388 | 0.13559 | -0.035942 | -0.025735 | -0.029595 | 0.013375 | 0.067269 | -0.067295 | -0.048239 | 0.065481 | -0.040846 | -0.042259 | -0.061641 | -0.040873 | -0.04722 | -0.030641 | 0.23172 | 0.060188 | 0.070395 | 0.066535 | 0.1095 | 0.1634 | 0.028835 | -0.002463 | 0.11126 | 0.00493 | 0.003517 | -0.015865 | 0.004903 | -0.001444 | 0.015135 | 0.013402 | -0.001019 | 0.020795 | 0.006374
5155.9375 | 122.6303 | -0.082397 | 122.5662 | 0.13101 | -0.031363 | -0.025735 | -0.025017 | 0.008797 | 0.067269 | -0.067295 | -0.057396 | 0.060902 | -0.045424 | -0.042259 | -0.075375 | -0.040873 | -0.051798 | -0.035219 | 0.21341 | 0.051034 | 0.056662 | 0.05738 | 0.091194 | 0.14967 | 0.015102 | -0.01162 | 0.10668 | 0.000352 | 0.003517 | -0.029599 | 0.004903 | -0.006022 | 0.010557 | 0.017979 | -0.005598 | 0.029951 | 0.006374
5157.7188 | 122.6578 | -0.082397 | 122.5525 | 0.13559 | -0.035942 | -0.025735 | -0.025017 | 0.013375 | 0.071848 | -0.071874 | -0.057396 | 0.056323 | -0.040846 | -0.03768 | -0.070797 | -0.040873 | -0.051798 | -0.030641 | 0.21798 | 0.046455 | 0.056662 | 0.05738 | 0.095772 | 0.15424 | 0.010523 | -0.01162 | 0.1021 | 0.00493 | 0.008096 | -0.025021 | 0.004903 | -0.006022 | 0.015135 | 0.013401 | -0.005598 | 0.029951 | 0.010952
5159.5 | 122.7081 | -0.054932 | 122.5296 | 0.13101 | -0.035942 | -0.025735 | -0.029595 | 0.013375 | 0.067269 | -0.071874 | -0.048239 | 0.065481 | -0.040846 | -0.046838 | -0.075375 | -0.040873 | -0.051798 | -0.039797 | 0.18594 | 0.01899 | 0.029197 | 0.025337 | 0.068307 | 0.1222 | -0.016942 | -0.002463 | 0.11126 | 0.00493 | -0.001062 | -0.029599 | 0.004903 | -0.006022 | 0.005979 | 0.027136 | 0.003559 | 0.034529 | 0.010952
5161.2812 | 122.7219 | -0.054932 | 122.4792 | 0.13559 | -0.035942 | -0.034893 | -0.029595 | 0.017953 | 0.071848 | -0.067295 | -0.061975 | 0.060902 | -0.040846 | -0.03768 | -0.070797 | -0.036295 | -0.04722 | -0.030641 | 0.19052 | 0.01899 | 0.020039 | 0.025337 | 0.072885 | 0.12678 | -0.012363 | -0.016199 | 0.10668 | 0.00493 | 0.008096 | -0.025021 | 0.009481 | -0.001444 | 0.015135 | 0.008822 | -0.014755 | 0.029951 | 0.006374
5163.0625 | 122.6166 | -0.086975 | 122.5342 | 0.13101 | -0.031363 | -0.021157 | -0.025017 | 0.013375 | 0.071848 | -0.071874 | -0.057396 | 0.065481 | -0.040846 | -0.042259 | -0.070797 | -0.040873 | -0.051798 | -0.039797 | 0.21798 | 0.055612 | 0.065818 | 0.061958 | 0.10035 | 0.15882 | 0.015101 | -0.01162 | 0.11126 | 0.00493 | 0.003517 | -0.025021 | 0.004903 | -0.006022 | 0.005979 | 0.013401 | -0.005598 | 0.029951 | 0.010952
5164.8438 | 122.7219 | -0.064087 | 122.525 | 0.12643 | -0.035942 | -0.034893 | -0.025017 | 0.013375 | 0.067269 | -0.076452 | -0.061975 | 0.060902 | -0.045424 | -0.033101 | -0.079953 | -0.040873 | -0.051798 | -0.035219 | 0.19052 | 0.028145 | 0.029194 | 0.03907 | 0.077462 | 0.13136 | -0.012365 | -0.016199 | 0.10668 | 0.000352 | 0.012675 | -0.034177 | 0.004903 | -0.006022 | 0.010557 | 0.017978 | -0.010177 | 0.034529 | 0.006374
5166.5781 | 122.6898 | -0.086975 | 122.5479 | 0.13101 | -0.035942 | -0.030314 | -0.038752 | 0.013375 | 0.067269 | -0.058139 | -0.057396 | 0.065481 | -0.045424 | -0.042259 | -0.070797 | -0.040873 | -0.04722 | -0.035219 | 0.21798 | 0.051033 | 0.056661 | 0.048223 | 0.10035 | 0.15424 | 0.028836 | -0.01162 | 0.11126 | 0.000352 | 0.003517 | -0.025021 | 0.004903 | -0.001444 | 0.010557 | 0.013401 | -0.010176 | 0.025373 | 0.001796
5168.3594 | 122.6349 | -0.082397 | 122.5433 | 0.12643 | -0.035942 | -0.034893 | -0.034174 | 0.017953 | 0.067269 | -0.067295 | -0.061975 | 0.065481 | -0.040846 | -0.051417 | -0.070797 | -0.045451 | -0.056376 | -0.030641 | 0.20883 | 0.046455 | 0.047504 | 0.048223 | 0.10035 | 0.14967 | 0.015102 | -0.016199 | 0.11126 | 0.00493 | -0.005641 | -0.025021 | 0.000325 | -0.0106 | 0.015135 | 0.008822 | -0.005599 | 0.029951 | 0.01553
5170.0781 | 122.7036 | -0.07782 | 122.5433 | 0.13559 | -0.035942 | -0.025735 | -0.029595 | 0.017953 | 0.067269 | -0.062717 | -0.057396 | 0.065481 | -0.040846 | -0.042259 | -0.066219 | -0.040873 | -0.04722 | -0.039797 | 0.21341 | 0.041878 | 0.052085 | 0.048225 | 0.095773 | 0.14509 | 0.015103 | -0.01162 | 0.11126 | 0.00493 | 0.003517 | -0.020443 | 0.004903 | -0.001444 | 0.005979 | 0.008823 | -0.010176 | 0.025373 | 0.006374
5171.8594 | 122.699 | -0.07782 | 122.5754 | 0.13559 | -0.040521 | -0.025735 | -0.029595 | 0.013375 | 0.067269 | -0.062717 | -0.057396 | 0.056323 | -0.045424 | -0.051417 | -0.066219 | -0.040873 | -0.051798 | -0.035219 | 0.21341 | 0.037299 | 0.052085 | 0.048225 | 0.091195 | 0.14509 | 0.015103 | -0.01162 | 0.1021 | 0.000352 | -0.005641 | -0.020443 | 0.004903 | -0.006022 | 0.010557 | 0.008823 | -0.005598 | 0.020795 | 0.006374
5173.625 | 122.6852 | -0.068665 | 122.5433 | 0.13101 | -0.040521 | -0.030314 | -0.029595 | 0.017953 | 0.062691 | -0.067295 | -0.052818 | 0.065481 | -0.040846 | -0.042259 | -0.070797 | -0.045451 | -0.051798 | -0.030641 | 0.19967 | 0.028144 | 0.038351 | 0.03907 | 0.086618 | 0.13136 | 0.00137 | -0.007042 | 0.11126 | 0.00493 | 0.003517 | -0.025021 | 0.000325 | -0.006022 | 0.015135 | 0.017979 | -0.00102 | 0.029951 | 0.010952
5175.3281 | 122.6166 | -0.091553 | 122.5754 | 0.13101 | -0.031363 | -0.021157 | -0.029595 | 0.022531 | 0.071848 | -0.067295 | -0.048239 | 0.056323 | -0.045424 | -0.03768 | -0.070797 | -0.036295 | -0.051798 | -0.030641 | 0.22256 | 0.06019 | 0.070396 | 0.061958 | 0.11408 | 0.1634 | 0.024258 | -0.002463 | 0.1021 | 0.000352 | 0.008096 | -0.025021 | 0.009481 | -0.006022 | 0.015135 | 0.022558 | 0.003559 | 0.025373 | 0.006374
5177.1094 | 122.7036 | -0.068665 | 122.5342 | 0.13559 | -0.040521 | -0.039471 | -0.029595 | 0.017953 | 0.067269 | -0.071874 | -0.052818 | 0.060902 | -0.040846 | -0.042259 | -0.070797 | -0.036295 | -0.051798 | -0.030641 | 0.20425 | 0.028144 | 0.029194 | 0.03907 | 0.086618 | 0.13593 | -0.003209 | -0.007042 | 0.10668 | 0.00493 | 0.003517 | -0.025021 | 0.009481 | -0.006022 | 0.015135 | 0.017979 | -0.00102 | 0.029951 | 0.010952
5178.8281 | 122.7264 | -0.064087 | 122.5159 | 0.13101 | -0.035942 | -0.030314 | -0.029595 | 0.013375 | 0.067269 | -0.058139 | -0.048239 | 0.065481 | -0.036267 | -0.042259 | -0.066219 | -0.040873 | -0.051798 | -0.035219 | 0.1951 | 0.028145 | 0.033773 | 0.034492 | 0.077462 | 0.13136 | 0.005948 | -0.002463 | 0.11126 | 0.009509 | 0.003517 | -0.020443 | 0.004903 | -0.006022 | 0.010557 | 0.01798 | 0.003559 | 0.029952 | 0.015531
5180.625 | 122.612 | -0.10529 | 122.5937 | 0.13101 | -0.035942 | -0.025735 | -0.029595 | 0.008797 | 0.071848 | -0.076452 | -0.048239 | 0.051744 | -0.045424 | -0.042259 | -0.070797 | -0.045451 | -0.056376 | -0.035219 | 0.23629 | 0.069344 | 0.079551 | 0.075691 | 0.11408 | 0.17713 | 0.028834 | -0.002463 | 0.09752 | 0.000352 | 0.003517 | -0.025021 | 0.000325 | -0.0106 | 0.010557 | 0.022558 | 0.008137 | 0.025373 | 0.010952
5182.4062 | 122.6074 | -0.10071 | 122.6028 | 0.13559 | -0.035942 | -0.025735 | -0.034174 | 0.013375 | 0.076426 | -0.067295 | -0.057396 | 0.060902 | -0.050002 | -0.042259 | -0.070797 | -0.031717 | -0.04722 | -0.035219 | 0.23629 | 0.064766 | 0.074973 | 0.066534 | 0.11408 | 0.17713 | 0.033413 | -0.01162 | 0.10668 | -0.004226 | 0.003517 | -0.025021 | 0.014059 | -0.001444 | 0.010557 | 0.013401 | -0.010176 | 0.020795 | -0.002782
5184.125 | 122.7219 | -0.041199 | 122.5433 | 0.13101 | -0.035942 | -0.030314 | -0.034174 | 0.017953 | 0.067269 | -0.067295 | -0.048239 | 0.060902 | -0.036267 | -0.042259 | -0.066219 | -0.036295 | -0.051798 | -0.035219 | 0.17221 | 0.005257 | 0.010885 | 0.007025 | 0.059152 | 0.10847 | -0.026096 | -0.002463 | 0.10668 | 0.009509 | 0.003517 | -0.020443 | 0.009481 | -0.006022 | 0.010557 | 0.01798 | 0.003559 | 0.029952 | 0.015531
5185.8906 | 122.6349 | -0.12817 | 122.5754 | 0.13559 | -0.040521 | -0.034893 | -0.029595 | 0.017953 | 0.071848 | -0.058139 | -0.048239 | 0.060902 | -0.036267 | -0.046838 | -0.066219 | -0.040873 | -0.04722 | -0.039797 | 0.26376 | 0.087653 | 0.093281 | 0.098579 | 0.14613 | 0.20002 | 0.070035 | -0.002463 | 0.10668 | 0.009509 | -0.001062 | -0.020443 | 0.004903 | -0.001444 | 0.005979 | 0.01798 | -0.001019 | 0.029952 | 0.010953
5187.5938 | 122.5845 | -0.10986 | 122.5479 | 0.13559 | -0.035942 | -0.025735 | -0.034174 | 0.008797 | 0.062691 | -0.067295 | -0.052818 | 0.060902 | -0.040846 | -0.042259 | -0.070797 | -0.045451 | -0.051798 | -0.035219 | 0.24545 | 0.073921 | 0.084128 | 0.075689 | 0.11866 | 0.17255 | 0.042568 | -0.007042 | 0.10668 | 0.00493 | 0.003517 | -0.025021 | 0.000325 | -0.006022 | 0.010557 | 0.017979 | -0.00102 | 0.029951 | 0.010952
5189.3594 | 122.6486 | -0.10529 | 122.5479 | 0.13559 | -0.035942 | -0.025735 | -0.025017 | 0.017953 | 0.062691 | -0.062717 | -0.057396 | 0.060902 | -0.050002 | -0.03768 | -0.070797 | -0.040873 | -0.051798 | -0.044375 | 0.24087 | 0.069344 | 0.079551 | 0.080269 | 0.12324 | 0.16798 | 0.042569 | -0.01162 | 0.10668 | -0.004226 | 0.008096 | -0.025021 | 0.004903 | -0.006022 | 0.001401 | 0.013401 | -0.005598 | 0.020795 | 0.001796
5191.1406 | 122.7264 | -0.068665 | 122.5342 | 0.13101 | -0.031363 | -0.021157 | -0.025017 | 0.013375 | 0.067269 | -0.067295 | -0.048239 | 0.060902 | -0.045424 | -0.033101 | -0.070797 | -0.040873 | -0.04722 | -0.030641 | 0.19967 | 0.037302 | 0.047508 | 0.043648 | 0.08204 | 0.13593 | 0.00137 | -0.002463 | 0.10668 | 0.000352 | 0.012675 | -0.025021 | 0.004903 | -0.001444 | 0.015135 | 0.022558 | -0.001019 | 0.025373 | 0.001796
5192.9062 | 122.6074 | -0.11902 | 122.5937 | 0.13559 | -0.040521 | -0.030314 | -0.025017 | 0.017953 | 0.067269 | -0.062717 | -0.052818 | 0.060902 | -0.045424 | -0.042259 | -0.070797 | -0.040873 | -0.056376 | -0.035219 | 0.25461 | 0.078498 | 0.088705 | 0.094002 | 0.13697 | 0.18629 | 0.056302 | -0.007042 | 0.10668 | 0.000352 | 0.003517 | -0.025021 | 0.004903 | -0.0106 | 0.010557 | 0.017979 | 0.003558 | 0.025373 | 0.010952
5194.625 | 122.6852 | -0.073242 | 122.5662 | 0.13101 | -0.035942 | -0.030314 | -0.034174 | 0.013375 | 0.071848 | -0.071874 | -0.052818 | 0.060902 | -0.040846 | -0.042259 | -0.075375 | -0.036295 | -0.051798 | -0.035219 | 0.20425 | 0.0373 | 0.042928 | 0.039068 | 0.086617 | 0.14509 | 0.001368 | -0.007042 | 0.10668 | 0.00493 | 0.003517 | -0.029599 | 0.009481 | -0.006022 | 0.010557 | 0.022557 | -0.00102 | 0.034529 | 0.010952
5196.4062 | 122.6303 | -0.086975 | 122.6074 | 0.12643 | -0.035942 | -0.030314 | -0.025017 | 0.017953 | 0.067269 | -0.062717 | -0.057396 | 0.056323 | -0.040846 | -0.042259 | -0.075375 | -0.045451 | -0.04722 | -0.026063 | 0.2134 | 0.051033 | 0.056661 | 0.061958 | 0.10493 | 0.15424 | 0.024258 | -0.01162 | 0.1021 | 0.00493 | 0.003517 | -0.029599 | 0.000325 | -0.001444 | 0.019713 | 0.017979 | -0.010176 | 0.034529 | 0.006374
5198.1719 | 122.6028 | -0.10986 | 122.5983 | 0.13101 | -0.035942 | -0.030314 | -0.025017 | 0.013375 | 0.071848 | -0.071874 | -0.052818 | 0.060902 | -0.040846 | -0.03768 | -0.075375 | -0.036295 | -0.056376 | -0.035219 | 0.24087 | 0.073921 | 0.079549 | 0.084846 | 0.12324 | 0.18171 | 0.037989 | -0.007042 | 0.10668 | 0.00493 | 0.008096 | -0.029599 | 0.009481 | -0.0106 | 0.010557 | 0.022557 | 0.003558 | 0.034529 | 0.01553
5199.875 | 122.5708 | -0.10071 | 122.58 | 0.13101 | -0.040521 | -0.021157 | -0.029595 | 0.017953 | 0.067269 | -0.071874 | -0.052818 | 0.056323 | -0.036267 | -0.046838 | -0.061641 | -0.050029 | -0.051798 | -0.035219 | 0.23172 | 0.060187 | 0.079551 | 0.071113 | 0.11866 | 0.16798 | 0.028834 | -0.007042 | 0.1021 | 0.009509 | -0.001062 | -0.015865 | -0.004253 | -0.006022 | 0.010557 | 0.008823 | -0.00102 | 0.025374 | 0.015531
5201.6719 | 122.6898 | -0.064087 | 122.5571 | 0.13101 | -0.031363 | -0.034893 | -0.025017 | 0.008797 | 0.062691 | -0.067295 | -0.057396 | 0.07006 | -0.045424 | -0.033101 | -0.070797 | -0.040873 | -0.04722 | -0.035219 | 0.1951 | 0.032724 | 0.029194 | 0.03907 | 0.072884 | 0.12678 | -0.003208 | -0.01162 | 0.11584 | 0.000352 | 0.012675 | -0.025021 | 0.004903 | -0.001444 | 0.010557 | 0.013401 | -0.010176 | 0.025373 | 0.001796
5203.3906 | 122.6807 | -0.064087 | 122.5616 | 0.12185 | -0.031363 | -0.034893 | -0.029595 | 0.013375 | 0.062691 | -0.062717 | -0.052818 | 0.056323 | -0.050002 | -0.046838 | -0.070797 | -0.040873 | -0.056376 | -0.035219 | 0.18594 | 0.032724 | 0.029194 | 0.034492 | 0.077462 | 0.12678 | 0.00137 | -0.007042 | 0.1021 | -0.004226 | -0.001062 | -0.025021 | 0.004903 | -0.0106 | 0.010557 | 0.017979 | 0.003558 | 0.020795 | 0.006374
5205.1719 | 122.5983 | -0.09613 | 122.5983 | 0.13559 | -0.040521 | -0.030314 | -0.025017 | 0.017953 | 0.062691 | -0.062717 | -0.057396 | 0.056323 | -0.040846 | -0.046838 | -0.070797 | -0.040873 | -0.04722 | -0.030641 | 0.23172 | 0.055609 | 0.065816 | 0.071113 | 0.11408 | 0.15882 | 0.033413 | -0.01162 | 0.1021 | 0.00493 | -0.001062 | -0.025021 | 0.004903 | -0.001444 | 0.015135 | 0.013401 | -0.010176 | 0.029951 | 0.006374
5206.9531 | 122.7219 | -0.054932 | 122.5662 | 0.13101 | -0.035942 | -0.030314 | -0.029595 | 0.013375 | 0.062691 | -0.067295 | -0.052818 | 0.060902 | -0.040846 | -0.03768 | -0.066219 | -0.040873 | -0.056376 | -0.035219 | 0.18594 | 0.01899 | 0.024618 | 0.025337 | 0.068307 | 0.11762 | -0.012363 | -0.007042 | 0.10668 | 0.00493 | 0.008096 | -0.020443 | 0.004903 | -0.0106 | 0.010557 | 0.013401 | 0.003558 | 0.025373 | 0.01553
5208.6719 | 122.6349 | -0.11902 | 122.5662 | 0.13559 | -0.035942 | -0.025735 | -0.025017 | 0.013375 | 0.067269 | -0.062717 | -0.048239 | 0.056323 | -0.040846 | -0.046838 | -0.066219 | -0.031717 | -0.051798 | -0.035219 | 0.25461 | 0.083077 | 0.093284 | 0.094002 | 0.13239 | 0.18629 | 0.056302 | -0.002463 | 0.1021 | 0.00493 | -0.001062 | -0.020443 | 0.014059 | -0.006022 | 0.010557 | 0.01798 | 0.003559 | 0.025373 | 0.010952
5210.4375 | 122.7539 | -0.07782 | 122.5433 | 0.13559 | -0.035942 | -0.030314 | -0.029595 | 0.013375 | 0.062691 | -0.071874 | -0.048239 | 0.060902 | -0.05458 | -0.042259 | -0.075375 | -0.040873 | -0.04722 | -0.035219 | 0.21341 | 0.041878 | 0.047506 | 0.048225 | 0.091195 | 0.14051 | 0.005946 | -0.002463 | 0.10668 | -0.008804 | 0.003517 | -0.029599 | 0.004903 | -0.001444 | 0.010557 | 0.027136 | -0.001019 | 0.020795 | -0.00736
5212.2031 | 122.6074 | -0.13733 | 122.5891 | 0.13101 | -0.035942 | -0.030314 | -0.034174 | 0.017953 | 0.062691 | -0.067295 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.079953 | -0.045451 | -0.042641 | -0.039797 | 0.26834 | 0.10139 | 0.10701 | 0.10315 | 0.15528 | 0.20002 | 0.070034 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.034177 | 0.000325 | 0.003135 | 0.005979 | 0.031714 | -0.005598 | 0.039107 | 0.001795
5213.9219 | 122.6212 | -0.10529 | 122.5891 | 0.13559 | -0.035942 | -0.021157 | -0.034174 | 0.008797 | 0.067269 | -0.071874 | -0.052818 | 0.060902 | -0.036267 | -0.03768 | -0.079953 | -0.045451 | -0.04722 | -0.030641 | 0.24087 | 0.069344 | 0.084129 | 0.071112 | 0.11408 | 0.17256 | 0.033412 | -0.007042 | 0.10668 | 0.009509 | 0.008096 | -0.034177 | 0.000325 | -0.001444 | 0.015135 | 0.027135 | -0.005598 | 0.043686 | 0.010953
5215.7031 | 122.731 | -0.045776 | 122.5571 | 0.13101 | -0.0451 | -0.030314 | -0.029595 | 0.017953 | 0.071848 | -0.067295 | -0.048239 | 0.065481 | -0.031689 | -0.042259 | -0.070797 | -0.036295 | -0.042641 | -0.030641 | 0.17678 | 0.000676 | 0.015462 | 0.016181 | 0.063729 | 0.11762 | -0.021519 | -0.002463 | 0.11126 | 0.014087 | 0.003517 | -0.025021 | 0.009481 | 0.003135 | 0.015135 | 0.022558 | -0.005598 | 0.039108 | 0.010952
5217.4844 | 122.699 | -0.064087 | 122.5525 | 0.13101 | -0.035942 | -0.030314 | -0.029595 | 0.017953 | 0.067269 | -0.062717 | -0.052818 | 0.056323 | -0.040846 | -0.033101 | -0.070797 | -0.040873 | -0.04722 | -0.035219 | 0.1951 | 0.028145 | 0.033773 | 0.034492 | 0.08204 | 0.13136 | 0.00137 | -0.007042 | 0.1021 | 0.00493 | 0.012675 | -0.025021 | 0.004903 | -0.001444 | 0.010557 | 0.017979 | -0.005598 | 0.029951 | 0.006374
5219.2031 | 122.6074 | -0.10986 | 122.6166 | 0.13101 | -0.035942 | -0.030314 | -0.034174 | 0.013375 | 0.076426 | -0.062717 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.070797 | -0.045451 | -0.04722 | -0.030641 | 0.24087 | 0.073921 | 0.079549 | 0.075689 | 0.12324 | 0.18629 | 0.047146 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.025021 | 0.000325 | -0.001444 | 0.015135 | 0.022558 | -0.001019 | 0.029951 | 0.006374
5220.9688 | 122.612 | -0.11444 | 122.5937 | 0.14017 | -0.035942 | -0.025735 | -0.029595 | 0.013375 | 0.067269 | -0.062717 | -0.057396 | 0.060902 | -0.045424 | -0.042259 | -0.070797 | -0.036295 | -0.04722 | -0.035219 | 0.25461 | 0.078499 | 0.088706 | 0.084846 | 0.12782 | 0.18171 | 0.051724 | -0.01162 | 0.10668 | 0.000352 | 0.003517 | -0.025021 | 0.009481 | -0.001444 | 0.010557 | 0.013401 | -0.010176 | 0.025373 | 0.001796
5222.75 | 122.58 | -0.10071 | 122.6028 | 0.13101 | -0.040521 | -0.034893 | -0.029595 | 0.004219 | 0.067269 | -0.067295 | -0.052818 | 0.056323 | -0.040846 | -0.042259 | -0.070797 | -0.045451 | -0.04722 | -0.030641 | 0.23172 | 0.060187 | 0.065815 | 0.071113 | 0.10493 | 0.16798 | 0.033413 | -0.007042 | 0.1021 | 0.00493 | 0.003517 | -0.025021 | 0.000325 | -0.001444 | 0.015135 | 0.017979 | -0.005598 | 0.029951 | 0.006374
5224.5312 | 122.6852 | -0.091553 | 122.5525 | 0.13101 | -0.031363 | -0.034893 | -0.034174 | 0.022531 | 0.067269 | -0.062717 | -0.048239 | 0.060902 | -0.045424 | -0.042259 | -0.079953 | -0.045451 | -0.056376 | -0.035219 | 0.22256 | 0.06019 | 0.05666 | 0.057379 | 0.11408 | 0.15882 | 0.028836 | -0.002463 | 0.10668 | 0.000352 | 0.003517 | -0.034177 | 0.000325 | -0.0106 | 0.010557 | 0.031714 | 0.008137 | 0.034529 | 0.010952
5226.25 | 122.6578 | -0.082397 | 122.6028 | 0.13101 | -0.026784 | -0.039471 | -0.034174 | 0.013375 | 0.062691 | -0.071874 | -0.048239 | 0.07006 | -0.040846 | -0.046838 | -0.070797 | -0.045451 | -0.051798 | -0.039797 | 0.21341 | 0.055613 | 0.042926 | 0.048223 | 0.095772 | 0.14509 | 0.010523 | -0.002463 | 0.11584 | 0.00493 | -0.001062 | -0.025021 | 0.000325 | -0.006022 | 0.005979 | 0.022558 | 0.003559 | 0.029951 | 0.010952
5228.0312 | 122.6852 | -0.068665 | 122.5616 | 0.13101 | -0.031363 | -0.030314 | -0.029595 | 0.008797 | 0.062691 | -0.071874 | -0.052818 | 0.051744 | -0.045424 | -0.046838 | -0.070797 | -0.040873 | -0.051798 | -0.030641 | 0.19967 | 0.037302 | 0.038351 | 0.03907 | 0.077462 | 0.13136 | -0.003209 | -0.007042 | 0.09752 | 0.000352 | -0.001062 | -0.025021 | 0.004903 | -0.006022 | 0.015135 | 0.017979 | -0.00102 | 0.025373 | 0.006374
5229.7344 | 122.612 | -0.10529 | 122.612 | 0.13101 | -0.031363 | -0.030314 | -0.034174 | 0.017953 | 0.062691 | -0.062717 | -0.048239 | 0.056323 | -0.036267 | -0.03768 | -0.070797 | -0.036295 | -0.056376 | -0.039797 | 0.23629 | 0.073923 | 0.074972 | 0.071112 | 0.12324 | 0.16798 | 0.042569 | -0.002463 | 0.1021 | 0.009509 | 0.008096 | -0.025021 | 0.009481 | -0.0106 | 0.005979 | 0.022558 | 0.008137 | 0.03453 | 0.020109
5231.5156 | 122.6944 | -0.082397 | 122.58 | 0.13101 | -0.040521 | -0.030314 | -0.029595 | 0.017953 | 0.067269 | -0.071874 | -0.048239 | 0.065481 | -0.050002 | -0.046838 | -0.070797 | -0.040873 | -0.042641 | -0.044375 | 0.21341 | 0.041876 | 0.052083 | 0.052802 | 0.10035 | 0.14967 | 0.010523 | -0.002463 | 0.11126 | -0.004226 | -0.001062 | -0.025021 | 0.004903 | 0.003135 | 0.001401 | 0.022558 | -0.005598 | 0.020795 | -0.007361
5233.2188 | 122.7722 | -0.068665 | 122.58 | 0.13559 | -0.040521 | -0.025735 | -0.020438 | 0.022531 | 0.067269 | -0.062717 | -0.057396 | 0.056323 | -0.040846 | -0.042259 | -0.070797 | -0.040873 | -0.042641 | -0.030641 | 0.20425 | 0.028144 | 0.04293 | 0.048227 | 0.091196 | 0.13593 | 0.005948 | -0.01162 | 0.1021 | 0.00493 | 0.003517 | -0.025021 | 0.004903 | 0.003135 | 0.015135 | 0.013401 | -0.014755 | 0.029951 | 0.001795
5234.9844 | 122.6212 | -0.1236 | 122.6028 | 0.13101 | -0.035942 | -0.034893 | -0.038752 | 0.022531 | 0.071848 | -0.062717 | -0.048239 | 0.056323 | -0.045424 | -0.03768 | -0.070797 | -0.045451 | -0.04722 | -0.039797 | 0.2546 | 0.087654 | 0.088703 | 0.084844 | 0.14613 | 0.19544 | 0.060879 | -0.002463 | 0.1021 | 0.000352 | 0.008096 | -0.025021 | 0.000325 | -0.001444 | 0.005979 | 0.022558 | -0.001019 | 0.025373 | 0.001796
5236.7188 | 122.7264 | -0.064087 | 122.5479 | 0.14017 | -0.031363 | -0.039471 | -0.034174 | 0.013375 | 0.062691 | -0.062717 | -0.057396 | 0.060902 | -0.045424 | -0.042259 | -0.066219 | -0.040873 | -0.04722 | -0.039797 | 0.20425 | 0.032724 | 0.024616 | 0.029913 | 0.077462 | 0.12678 | 0.00137 | -0.01162 | 0.10668 | 0.000352 | 0.003517 | -0.020443 | 0.004903 | -0.001444 | 0.005979 | 0.008823 | -0.010176 | 0.020795 | 0.001796
5238.5 | 122.731 | -0.082397 | 122.5708 | 0.14017 | -0.035942 | -0.030314 | -0.029595 | 0.017953 | 0.058113 | -0.071874 | -0.052818 | 0.060902 | -0.045424 | -0.03768 | -0.066219 | -0.040873 | -0.051798 | -0.030641 | 0.22256 | 0.046455 | 0.052083 | 0.052802 | 0.10035 | 0.14051 | 0.010523 | -0.007042 | 0.10668 | 0.000352 | 0.008096 | -0.020443 | 0.004903 | -0.006022 | 0.015135 | 0.013401 | -0.00102 | 0.020795 | 0.006374
5240.2031 | 122.6578 | -0.068665 | 122.6028 | 0.13101 | -0.0451 | -0.030314 | -0.034174 | 0.008797 | 0.062691 | -0.058139 | -0.052818 | 0.056323 | -0.036267 | -0.042259 | -0.070797 | -0.040873 | -0.051798 | -0.026063 | 0.19967 | 0.023565 | 0.038351 | 0.034491 | 0.077462 | 0.13136 | 0.010526 | -0.007042 | 0.1021 | 0.009509 | 0.003517 | -0.025021 | 0.004903 | -0.006022 | 0.019713 | 0.017979 | -0.00102 | 0.03453 | 0.015531
5241.9844 | 122.6486 | -0.10071 | 122.58 | 0.13101 | -0.035942 | -0.030314 | -0.034174 | 0.017953 | 0.062691 | -0.071874 | -0.057396 | 0.056323 | -0.036267 | -0.03768 | -0.070797 | -0.031717 | -0.04722 | -0.026063 | 0.23172 | 0.064766 | 0.070394 | 0.066534 | 0.11866 | 0.1634 | 0.028834 | -0.01162 | 0.1021 | 0.009509 | 0.008096 | -0.025021 | 0.014059 | -0.001444 | 0.019713 | 0.013401 | -0.010176 | 0.03453 | 0.010953
5243.7656 | 122.7493 | -0.068665 | 122.5845 | 0.13559 | -0.026784 | -0.034893 | -0.029595 | 0.017953 | 0.058113 | -0.062717 | -0.052818 | 0.060902 | -0.040846 | -0.046838 | -0.075375 | -0.036295 | -0.042641 | -0.035219 | 0.20425 | 0.041881 | 0.033772 | 0.03907 | 0.086618 | 0.12678 | 0.005948 | -0.007042 | 0.10668 | 0.00493 | -0.001062 | -0.029599 | 0.009481 | 0.003135 | 0.010557 | 0.022557 | -0.010177 | 0.034529 | 0.001795
5245.4688 | 122.6898 | -0.07782 | 122.5891 | 0.13101 | -0.031363 | -0.030314 | -0.034174 | 0.013375 | 0.071848 | -0.058139 | -0.048239 | 0.060902 | -0.045424 | -0.03768 | -0.070797 | -0.040873 | -0.051798 | -0.035219 | 0.20883 | 0.046457 | 0.047506 | 0.043646 | 0.091195 | 0.14967 | 0.019681 | -0.002463 | 0.10668 | 0.000352 | 0.008096 | -0.025021 | 0.004903 | -0.006022 | 0.010557 | 0.022558 | 0.003559 | 0.025373 | 0.006374
5247.25 | 122.7081 | -0.068665 | 122.5891 | 0.13101 | -0.035942 | -0.025735 | -0.034174 | 0.022531 | 0.062691 | -0.067295 | -0.052818 | 0.056323 | -0.040846 | -0.042259 | -0.075375 | -0.036295 | -0.051798 | -0.021484 | 0.19967 | 0.032723 | 0.04293 | 0.034491 | 0.091196 | 0.13136 | 0.00137 | -0.007042 | 0.1021 | 0.00493 | 0.003517 | -0.029599 | 0.009481 | -0.006022 | 0.024292 | 0.022557 | -0.00102 | 0.034529 | 0.010952
5248.9688 | 122.6624 | -0.11902 | 122.5937 | 0.14017 | -0.026784 | -0.030314 | -0.025017 | 0.008797 | 0.062691 | -0.058139 | -0.048239 | 0.051744 | -0.050002 | -0.042259 | -0.070797 | -0.036295 | -0.042641 | -0.039797 | 0.25918 | 0.092235 | 0.088705 | 0.094002 | 0.12782 | 0.18171 | 0.06088 | -0.002463 | 0.09752 | -0.004226 | 0.003517 | -0.025021 | 0.009481 | 0.003135 | 0.005979 | 0.022558 | -0.005598 | 0.020795 | -0.007361
5250.75 | 122.7722 | -0.050354 | 122.5708 | 0.13101 | -0.035942 | -0.030314 | -0.025017 | 0.008797 | 0.062691 | -0.067295 | -0.052818 | 0.056323 | -0.040846 | -0.042259 | -0.070797 | -0.031717 | -0.051798 | -0.035219 | 0.18136 | 0.014412 | 0.02004 | 0.025337 | 0.059151 | 0.11305 | -0.016941 | -0.007042 | 0.1021 | 0.00493 | 0.003517 | -0.025021 | 0.014059 | -0.006022 | 0.010557 | 0.017979 | -0.00102 | 0.029951 | 0.010952
5252.4688 | 122.6166 | -0.12817 | 122.6166 | 0.13559 | -0.040521 | -0.021157 | -0.034174 | 0.017953 | 0.071848 | -0.067295 | -0.043661 | 0.065481 | -0.045424 | -0.046838 | -0.070797 | -0.040873 | -0.04722 | -0.035219 | 0.26376 | 0.087653 | 0.10702 | 0.094 | 0.14613 | 0.20002 | 0.060879 | 0.002115 | 0.11126 | 0.000352 | -0.001062 | -0.025021 | 0.004903 | -0.001444 | 0.010557 | 0.027136 | 0.003559 | 0.025373 | 0.001796
5254.25 | 122.6532 | -0.07782 | 122.5845 | 0.13101 | -0.026784 | -0.034893 | -0.034174 | 0.013375 | 0.067269 | -0.067295 | -0.057396 | 0.060902 | -0.036267 | -0.042259 | -0.075375 | -0.036295 | -0.04722 | -0.030641 | 0.20883 | 0.051036 | 0.042927 | 0.043646 | 0.091195 | 0.14509 | 0.010525 | -0.01162 | 0.10668 | 0.009509 | 0.003517 | -0.029599 | 0.009481 | -0.001444 | 0.015135 | 0.017979 | -0.010176 | 0.039108 | 0.010953
5256.0312 | 122.6486 | -0.10529 | 122.5983 | 0.14017 | -0.026784 | -0.025735 | -0.025017 | 0.022531 | 0.067269 | -0.067295 | -0.043661 | 0.060902 | -0.050002 | -0.042259 | -0.075375 | -0.036295 | -0.051798 | -0.039797 | 0.24545 | 0.078502 | 0.079551 | 0.080269 | 0.12782 | 0.17256 | 0.037991 | 0.002115 | 0.10668 | -0.004226 | 0.003517 | -0.029599 | 0.009481 | -0.006022 | 0.005979 | 0.031714 | 0.008137 | 0.025373 | 0.001796
5257.75 | 122.6898 | -0.091553 | 122.5983 | 0.13101 | -0.031363 | -0.030314 | -0.034174 | 0.013375 | 0.067269 | -0.067295 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.070797 | -0.036295 | -0.04722 | -0.035219 | 0.22256 | 0.06019 | 0.061239 | 0.057379 | 0.10493 | 0.15882 | 0.024258 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.025021 | 0.009481 | -0.001444 | 0.010557 | 0.022558 | -0.001019 | 0.029951 | 0.006374
5259.5156 | 122.7448 | -0.054932 | 122.5571 | 0.13559 | -0.035942 | -0.025735 | -0.029595 | 0.017953 | 0.067269 | -0.071874 | -0.052818 | 0.060902 | -0.040846 | -0.03768 | -0.066219 | -0.045451 | -0.042641 | -0.026063 | 0.19052 | 0.01899 | 0.029197 | 0.025337 | 0.072885 | 0.1222 | -0.016942 | -0.007042 | 0.10668 | 0.00493 | 0.008096 | -0.020443 | 0.000325 | 0.003135 | 0.019713 | 0.013401 | -0.010177 | 0.025373 | 0.001795
5261.2344 | 122.6486 | -0.091553 | 122.5937 | 0.13101 | -0.031363 | -0.030314 | -0.034174 | 0.008797 | 0.076426 | -0.067295 | -0.057396 | 0.065481 | -0.050002 | -0.03768 | -0.070797 | -0.036295 | -0.04722 | -0.039797 | 0.22256 | 0.06019 | 0.061239 | 0.057379 | 0.10035 | 0.16798 | 0.024258 | -0.01162 | 0.11126 | -0.004226 | 0.008096 | -0.025021 | 0.009481 | -0.001444 | 0.005979 | 0.013401 | -0.010176 | 0.020795 | -0.002782
5263.0156 | 122.644 | -0.10529 | 122.6074 | 0.14017 | -0.035942 | -0.021157 | -0.029595 | 0.017953 | 0.062691 | -0.067295 | -0.052818 | 0.065481 | -0.036267 | -0.042259 | -0.070797 | -0.040873 | -0.042641 | -0.030641 | 0.24545 | 0.069344 | 0.084129 | 0.075691 | 0.12324 | 0.16798 | 0.037991 | -0.007042 | 0.11126 | 0.009509 | 0.003517 | -0.025021 | 0.004903 | 0.003135 | 0.015135 | 0.017979 | -0.010177 | 0.03453 | 0.006374
5264.7969 | 122.7173 | -0.086975 | 122.5983 | 0.13101 | -0.040521 | -0.030314 | -0.029595 | 0.008797 | 0.062691 | -0.071874 | -0.048239 | 0.060902 | -0.040846 | -0.046838 | -0.075375 | -0.040873 | -0.056376 | -0.030641 | 0.21798 | 0.046454 | 0.056661 | 0.05738 | 0.095772 | 0.14967 | 0.015101 | -0.002463 | 0.10668 | 0.00493 | -0.001062 | -0.029599 | 0.004903 | -0.0106 | 0.015135 | 0.027136 | 0.008137 | 0.034529 | 0.01553
5266.5156 | 122.6715 | -0.11444 | 122.5754 | 0.13559 | -0.035942 | -0.025735 | -0.029595 | 0.008797 | 0.062691 | -0.067295 | -0.057396 | 0.07006 | -0.050002 | -0.042259 | -0.075375 | -0.040873 | -0.051798 | -0.026063 | 0.25003 | 0.078499 | 0.088706 | 0.084846 | 0.12324 | 0.17713 | 0.047146 | -0.01162 | 0.11584 | -0.004226 | 0.003517 | -0.029599 | 0.004903 | -0.006022 | 0.019713 | 0.017979 | -0.005598 | 0.025373 | 0.001796
5268.3125 | 122.7676 | -0.068665 | 122.5479 | 0.13101 | -0.040521 | -0.034893 | -0.034174 | 0.013375 | 0.058113 | -0.067295 | -0.057396 | 0.065481 | -0.045424 | -0.042259 | -0.070797 | -0.036295 | -0.051798 | -0.035219 | 0.19967 | 0.028144 | 0.033772 | 0.034491 | 0.08204 | 0.12678 | 0.00137 | -0.01162 | 0.11126 | 0.000352 | 0.003517 | -0.025021 | 0.009481 | -0.006022 | 0.010557 | 0.013401 | -0.005598 | 0.025373 | 0.006374
5270.1094 | 122.6578 | -0.11902 | 122.6166 | 0.13101 | -0.040521 | -0.025735 | -0.029595 | 0.013375 | 0.067269 | -0.058139 | -0.052818 | 0.056323 | -0.040846 | -0.042259 | -0.070797 | -0.045451 | -0.042641 | -0.035219 | 0.25003 | 0.078498 | 0.093284 | 0.089424 | 0.13239 | 0.18629 | 0.06088 | -0.007042 | 0.1021 | 0.00493 | 0.003517 | -0.025021 | 0.000325 | 0.003135 | 0.010557 | 0.017979 | -0.010177 | 0.029951 | 0.001795
5271.8438 | 122.7539 | -0.086975 | 122.58 | 0.13559 | -0.031363 | -0.034893 | -0.029595 | 0.013375 | 0.071848 | -0.071874 | -0.052818 | 0.060902 | -0.045424 | -0.042259 | -0.070797 | -0.040873 | -0.056376 | -0.030641 | 0.22256 | 0.055612 | 0.052082 | 0.05738 | 0.10035 | 0.15882 | 0.015101 | -0.007042 | 0.10668 | 0.000352 | 0.003517 | -0.025021 | 0.004903 | -0.0106 | 0.015135 | 0.017979 | 0.003558 | 0.025373 | 0.010952
5273.5781 | 122.7264 | -0.068665 | 122.6257 | 0.13559 | -0.040521 | -0.021157 | -0.029595 | 0.017953 | 0.071848 | -0.067295 | -0.052818 | 0.060902 | -0.045424 | -0.033101 | -0.075375 | -0.040873 | -0.04722 | -0.030641 | 0.20425 | 0.028144 | 0.047508 | 0.03907 | 0.086618 | 0.14051 | 0.00137 | -0.007042 | 0.10668 | 0.000352 | 0.012675 | -0.029599 | 0.004903 | -0.001444 | 0.015135 | 0.022557 | -0.005598 | 0.029951 | 0.001796
5275.2969 | 122.699 | -0.054932 | 122.5937 | 0.13559 | -0.040521 | -0.030314 | -0.034174 | 0.017953 | 0.062691 | -0.071874 | -0.043661 | 0.065481 | -0.045424 | -0.03768 | -0.070797 | -0.040873 | -0.042641 | -0.039797 | 0.19052 | 0.014411 | 0.024618 | 0.020758 | 0.072885 | 0.11762 | -0.016942 | 0.002115 | 0.11126 | 0.000352 | 0.008096 | -0.025021 | 0.004903 | 0.003135 | 0.005979 | 0.027136 | -0.00102 | 0.025373 | -0.002783
5277.0625 | 122.7859 | -0.064087 | 122.5845 | 0.14017 | -0.0451 | -0.030314 | -0.034174 | 0.008797 | 0.067269 | -0.062717 | -0.052818 | 0.060902 | -0.040846 | -0.042259 | -0.070797 | -0.040873 | -0.051798 | -0.030641 | 0.20425 | 0.018987 | 0.033773 | 0.029913 | 0.072884 | 0.13136 | 0.00137 | -0.007042 | 0.10668 | 0.00493 | 0.003517 | -0.025021 | 0.004903 | -0.006022 | 0.015135 | 0.017979 | -0.00102 | 0.029951 | 0.010952
5278.7969 | 122.6669 | -0.09613 | 122.5983 | 0.13559 | -0.035942 | -0.034893 | -0.025017 | 0.008797 | 0.062691 | -0.062717 | -0.048239 | 0.060902 | -0.040846 | -0.03768 | -0.070797 | -0.040873 | -0.051798 | -0.035219 | 0.23172 | 0.060188 | 0.061237 | 0.071113 | 0.10493 | 0.15882 | 0.033413 | -0.002463 | 0.10668 | 0.00493 | 0.008096 | -0.025021 | 0.004903 | -0.006022 | 0.010557 | 0.022558 | 0.003559 | 0.029951 | 0.010952
5280.5625 | 122.6303 | -0.10071 | 122.6166 | 0.12643 | -0.031363 | -0.025735 | -0.029595 | 0.004219 | 0.071848 | -0.062717 | -0.052818 | 0.056323 | -0.045424 | -0.042259 | -0.075375 | -0.036295 | -0.04722 | -0.035219 | 0.22714 | 0.069345 | 0.074973 | 0.071113 | 0.10493 | 0.17256 | 0.037991 | -0.007042 | 0.1021 | 0.000352 | 0.003517 | -0.029599 | 0.009481 | -0.001444 | 0.010557 | 0.022557 | -0.005598 | 0.029951 | 0.001796
5282.3438 | 122.699 | -0.082397 | 122.5616 | 0.13559 | -0.040521 | -0.030314 | -0.029595 | 0.013375 | 0.071848 | -0.067295 | -0.048239 | 0.060902 | -0.045424 | -0.03768 | -0.070797 | -0.040873 | -0.04722 | -0.026063 | 0.21798 | 0.041876 | 0.052083 | 0.052802 | 0.095772 | 0.15424 | 0.015102 | -0.002463 | 0.10668 | 0.000352 | 0.008096 | -0.025021 | 0.004903 | -0.001444 | 0.019713 | 0.022558 | -0.001019 | 0.025373 | 0.001796
5284.0781 | 122.7585 | -0.059509 | 122.5616 | 0.13101 | -0.035942 | -0.021157 | -0.029595 | 0.013375 | 0.067269 | -0.067295 | -0.052818 | 0.065481 | -0.045424 | -0.042259 | -0.070797 | -0.036295 | -0.042641 | -0.030641 | 0.19052 | 0.023567 | 0.038352 | 0.029914 | 0.072884 | 0.12678 | -0.007786 | -0.007042 | 0.11126 | 0.000352 | 0.003517 | -0.025021 | 0.009481 | 0.003135 | 0.015135 | 0.017979 | -0.010177 | 0.025373 | -0.002783
5285.8438 | 122.6257 | -0.1236 | 122.5983 | 0.13559 | -0.040521 | -0.021157 | -0.034174 | 0.017953 | 0.067269 | -0.067295 | -0.052818 | 0.060902 | -0.045424 | -0.03768 | -0.070797 | -0.040873 | -0.051798 | -0.026063 | 0.25918 | 0.083075 | 0.10244 | 0.089422 | 0.14155 | 0.19087 | 0.056301 | -0.007042 | 0.10668 | 0.000352 | 0.008096 | -0.025021 | 0.004903 | -0.006022 | 0.019713 | 0.017979 | -0.00102 | 0.025373 | 0.006374
5287.5625 | 122.6761 | -0.09613 | 122.6212 | 0.14017 | -0.035942 | -0.030314 | -0.029595 | 0.013375 | 0.058113 | -0.062717 | -0.052818 | 0.060902 | -0.040846 | -0.042259 | -0.075375 | -0.040873 | -0.051798 | -0.030641 | 0.2363 | 0.060188 | 0.065816 | 0.066535 | 0.1095 | 0.15424 | 0.033413 | -0.007042 | 0.10668 | 0.00493 | 0.003517 | -0.029599 | 0.004903 | -0.006022 | 0.015135 | 0.022557 | -0.00102 | 0.034529 | 0.010952
5289.2812 | 122.7585 | -0.073242 | 122.5937 | 0.13101 | -0.049678 | -0.030314 | -0.025017 | 0.008797 | 0.071848 | -0.076452 | -0.048239 | 0.065481 | -0.031689 | -0.03768 | -0.066219 | -0.040873 | -0.051798 | -0.030641 | 0.20425 | 0.023564 | 0.042928 | 0.048225 | 0.082039 | 0.14509 | -0.00321 | -0.002463 | 0.11126 | 0.014087 | 0.008096 | -0.020443 | 0.004903 | -0.006022 | 0.015135 | 0.01798 | 0.003559 | 0.03453 | 0.020109
5291.0156 | 122.7036 | -0.091553 | 122.6166 | 0.13559 | -0.0451 | -0.025735 | -0.034174 | 0.017953 | 0.071848 | -0.062717 | -0.048239 | 0.060902 | -0.050002 | -0.042259 | -0.070797 | -0.040873 | -0.056376 | -0.035219 | 0.22714 | 0.046453 | 0.065818 | 0.057379 | 0.10951 | 0.1634 | 0.028836 | -0.002463 | 0.10668 | -0.004226 | 0.003517 | -0.025021 | 0.004903 | -0.0106 | 0.010557 | 0.022558 | 0.008137 | 0.020795 | 0.006374
5292.7344 | 122.7402 | -0.068665 | 122.6166 | 0.13101 | -0.031363 | -0.034893 | -0.029595 | 0.008797 | 0.062691 | -0.062717 | -0.052818 | 0.065481 | -0.040846 | -0.03768 | -0.070797 | -0.036295 | -0.04722 | -0.030641 | 0.19967 | 0.037302 | 0.033772 | 0.03907 | 0.077462 | 0.13136 | 0.005948 | -0.007042 | 0.11126 | 0.00493 | 0.008096 | -0.025021 | 0.009481 | -0.001444 | 0.015135 | 0.017979 | -0.005598 | 0.029951 | 0.006374
5294.4375 | 122.6852 | -0.086975 | 122.612 | 0.13559 | -0.040521 | -0.030314 | -0.034174 | 0.017953 | 0.071848 | -0.062717 | -0.048239 | 0.060902 | -0.045424 | -0.03768 | -0.066219 | -0.036295 | -0.051798 | -0.030641 | 0.22256 | 0.046454 | 0.056661 | 0.052801 | 0.10493 | 0.15882 | 0.024258 | -0.002463 | 0.10668 | 0.000352 | 0.008096 | -0.020443 | 0.009481 | -0.006022 | 0.015135 | 0.01798 | 0.003559 | 0.020795 | 0.006374
5296.1562 | 122.6303 | -0.11444 | 122.6212 | 0.13559 | -0.031363 | -0.034893 | -0.029595 | 0.013375 | 0.067269 | -0.071874 | -0.052818 | 0.065481 | -0.050002 | -0.03768 | -0.070797 | -0.040873 | -0.04722 | -0.030641 | 0.25003 | 0.083078 | 0.079548 | 0.084846 | 0.12782 | 0.18171 | 0.042567 | -0.007042 | 0.11126 | -0.004226 | 0.008096 | -0.025021 | 0.004903 | -0.001444 | 0.015135 | 0.017979 | -0.005598 | 0.020795 | -0.002782
5297.8906 | 122.7676 | -0.068665 | 122.5937 | 0.13101 | -0.035942 | -0.025735 | -0.029595 | 0.008797 | 0.062691 | -0.062717 | -0.048239 | 0.056323 | -0.045424 | -0.03768 | -0.070797 | -0.045451 | -0.04722 | -0.035219 | 0.19967 | 0.032723 | 0.04293 | 0.03907 | 0.077462 | 0.13136 | 0.005948 | -0.002463 | 0.1021 | 0.000352 | 0.008096 | -0.025021 | 0.000325 | -0.001444 | 0.010557 | 0.022558 | -0.001019 | 0.025373 | 0.001796
5299.6094 | 122.6761 | -0.10071 | 122.6212 | 0.12643 | -0.035942 | -0.030314 | -0.034174 | 0.013375 | 0.067269 | -0.062717 | -0.057396 | 0.060902 | -0.040846 | -0.046838 | -0.066219 | -0.040873 | -0.042641 | -0.035219 | 0.22714 | 0.064766 | 0.070394 | 0.066534 | 0.11408 | 0.16798 | 0.037991 | -0.01162 | 0.10668 | 0.00493 | -0.001062 | -0.020443 | 0.004903 | 0.003135 | 0.010557 | 0.008823 | -0.014755 | 0.025373 | 0.001795
5301.375 | 122.7356 | -0.073242 | 122.5983 | 0.13101 | -0.040521 | -0.030314 | -0.029595 | 0.017953 | 0.071848 | -0.067295 | -0.048239 | 0.060902 | -0.040846 | -0.046838 | -0.066219 | -0.031717 | -0.04722 | -0.039797 | 0.20425 | 0.032721 | 0.042928 | 0.043647 | 0.091195 | 0.14509 | 0.005947 | -0.002463 | 0.10668 | 0.00493 | -0.001062 | -0.020443 | 0.014059 | -0.001444 | 0.005979 | 0.01798 | -0.001019 | 0.025373 | 0.006374
5303.0938 | 122.7814 | -0.068665 | 122.58 | 0.13101 | -0.035942 | -0.030314 | -0.034174 | 0.013375 | 0.058113 | -0.062717 | -0.048239 | 0.060902 | -0.045424 | -0.042259 | -0.075375 | -0.031717 | -0.04722 | -0.030641 | 0.19967 | 0.032723 | 0.038351 | 0.034491 | 0.08204 | 0.12678 | 0.005948 | -0.002463 | 0.10668 | 0.000352 | 0.003517 | -0.029599 | 0.014059 | -0.001444 | 0.015135 | 0.027136 | -0.001019 | 0.029951 | 0.001796
5304.875 | 122.7859 | -0.073242 | 122.5937 | 0.13101 | -0.035942 | -0.034893 | -0.034174 | 0.013375 | 0.067269 | -0.067295 | -0.048239 | 0.060902 | -0.036267 | -0.046838 | -0.070797 | -0.040873 | -0.04722 | -0.035219 | 0.20425 | 0.0373 | 0.038349 | 0.039068 | 0.086617 | 0.14051 | 0.005947 | -0.002463 | 0.10668 | 0.009509 | -0.001062 | -0.025021 | 0.004903 | -0.001444 | 0.010557 | 0.022558 | -0.001019 | 0.03453 | 0.010953
5306.6094 | 122.6349 | -0.10071 | 122.612 | 0.13559 | -0.040521 | -0.030314 | -0.034174 | 0.008797 | 0.071848 | -0.067295 | -0.052818 | 0.056323 | -0.045424 | -0.042259 | -0.075375 | -0.045451 | -0.051798 | -0.035219 | 0.23629 | 0.060187 | 0.070394 | 0.066534 | 0.10951 | 0.17256 | 0.033413 | -0.007042 | 0.1021 | 0.000352 | 0.003517 | -0.029599 | 0.000325 | -0.006022 | 0.010557 | 0.022557 | -0.00102 | 0.029951 | 0.006374
5308.3125 | 122.7448 | -0.064087 | 122.58 | 0.13559 | -0.049678 | -0.034893 | -0.034174 | 0.008797 | 0.062691 | -0.067295 | -0.057396 | 0.065481 | -0.05458 | -0.03768 | -0.075375 | -0.036295 | -0.04722 | -0.030641 | 0.19967 | 0.014409 | 0.029194 | 0.029913 | 0.072884 | 0.12678 | -0.003208 | -0.01162 | 0.11126 | -0.008804 | 0.008096 | -0.029599 | 0.009481 | -0.001444 | 0.015135 | 0.017979 | -0.010176 | 0.020795 | -0.00736
5310.0312 | 122.7173 | -0.068665 | 122.6074 | 0.13101 | -0.040521 | -0.025735 | -0.029595 | 0.022531 | 0.062691 | -0.067295 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.075375 | -0.031717 | -0.042641 | -0.030641 | 0.19967 | 0.028144 | 0.04293 | 0.03907 | 0.091196 | 0.13136 | 0.00137 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.029599 | 0.014059 | 0.003135 | 0.015135 | 0.027136 | -0.005598 | 0.034529 | 0.001795
5311.75 | 122.6395 | -0.11902 | 122.6486 | 0.13559 | -0.040521 | -0.030314 | -0.029595 | 0.017953 | 0.062691 | -0.067295 | -0.052818 | 0.074638 | -0.040846 | -0.046838 | -0.061641 | -0.040873 | -0.060955 | -0.039797 | 0.25461 | 0.078498 | 0.088705 | 0.089424 | 0.13697 | 0.18171 | 0.051724 | -0.007042 | 0.12041 | 0.00493 | -0.001062 | -0.015865 | 0.004903 | -0.015179 | 0.005979 | 0.008823 | 0.008137 | 0.020795 | 0.020109
5313.4688 | 122.6898 | -0.10529 | 122.5937 | 0.12643 | -0.035942 | -0.030314 | -0.043331 | 0.004219 | 0.062691 | -0.067295 | -0.048239 | 0.065481 | -0.045424 | -0.042259 | -0.066219 | -0.040873 | -0.051798 | -0.030641 | 0.23172 | 0.069344 | 0.074972 | 0.061955 | 0.10951 | 0.16798 | 0.037991 | -0.002463 | 0.11126 | 0.000352 | 0.003517 | -0.020443 | 0.004903 | -0.006022 | 0.015135 | 0.01798 | 0.003559 | 0.020795 | 0.006374
5315.1719 | 122.6944 | -0.10529 | 122.6212 | 0.14017 | -0.0451 | -0.030314 | -0.025017 | 0.017953 | 0.067269 | -0.067295 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.070797 | -0.036295 | -0.04722 | -0.035219 | 0.24545 | 0.060186 | 0.074972 | 0.080269 | 0.12324 | 0.17256 | 0.037991 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.025021 | 0.009481 | -0.001444 | 0.010557 | 0.022558 | -0.001019 | 0.029951 | 0.006374
5316.8906 | 122.7127 | -0.086975 | 122.612 | 0.13101 | -0.040521 | -0.030314 | -0.034174 | 0.008797 | 0.058113 | -0.071874 | -0.052818 | 0.065481 | -0.045424 | -0.046838 | -0.070797 | -0.040873 | -0.04722 | -0.035219 | 0.21798 | 0.046454 | 0.056661 | 0.052801 | 0.095772 | 0.14509 | 0.015101 | -0.007042 | 0.11126 | 0.000352 | -0.001062 | -0.025021 | 0.004903 | -0.001444 | 0.010557 | 0.017979 | -0.005598 | 0.025373 | 0.001796
5318.6094 | 122.7356 | -0.050354 | 122.6074 | 0.13559 | -0.049678 | -0.034893 | -0.029595 | 0.017953 | 0.062691 | -0.062717 | -0.039082 | 0.056323 | -0.045424 | -0.046838 | -0.079953 | -0.045451 | -0.051798 | -0.030641 | 0.18594 | 0.000676 | 0.015461 | 0.020759 | 0.068307 | 0.11305 | -0.012363 | 0.006694 | 0.1021 | 0.000352 | -0.001062 | -0.034177 | 0.000325 | -0.006022 | 0.015135 | 0.040871 | 0.012716 | 0.034529 | 0.006374
5320.3594 | 122.7905 | -0.059509 | 122.5937 | 0.13101 | -0.0451 | -0.025735 | -0.029595 | 0.013375 | 0.062691 | -0.067295 | -0.048239 | 0.07006 | -0.050002 | -0.03768 | -0.070797 | -0.027139 | -0.04722 | -0.039797 | 0.19052 | 0.014409 | 0.033774 | 0.029914 | 0.072884 | 0.1222 | -0.007786 | -0.002463 | 0.11584 | -0.004226 | 0.008096 | -0.025021 | 0.018637 | -0.001444 | 0.005979 | 0.022558 | -0.001019 | 0.020795 | -0.002782
5322.0781 | 122.644 | -0.10986 | 122.6257 | 0.14017 | -0.035942 | -0.025735 | -0.029595 | 0.008797 | 0.067269 | -0.067295 | -0.052818 | 0.065481 | -0.036267 | -0.046838 | -0.070797 | -0.036295 | -0.051798 | -0.035219 | 0.25003 | 0.073921 | 0.084128 | 0.080268 | 0.11866 | 0.17713 | 0.042568 | -0.007042 | 0.11126 | 0.009509 | -0.001062 | -0.025021 | 0.009481 | -0.006022 | 0.010557 | 0.017979 | -0.00102 | 0.03453 | 0.015531
5323.7969 | 122.7493 | -0.073242 | 122.5891 | 0.14017 | -0.040521 | -0.034893 | -0.038752 | 0.017953 | 0.067269 | -0.067295 | -0.057396 | 0.065481 | -0.040846 | -0.03768 | -0.066219 | -0.036295 | -0.04722 | -0.030641 | 0.21341 | 0.032721 | 0.038349 | 0.03449 | 0.091195 | 0.14051 | 0.005947 | -0.01162 | 0.11126 | 0.00493 | 0.008096 | -0.020443 | 0.009481 | -0.001444 | 0.015135 | 0.008823 | -0.010176 | 0.025373 | 0.006374
5325.5 | 122.6486 | -0.10986 | 122.6303 | 0.13559 | -0.040521 | -0.034893 | -0.025017 | 0.017953 | 0.062691 | -0.067295 | -0.057396 | 0.065481 | -0.040846 | -0.03768 | -0.070797 | -0.036295 | -0.051798 | -0.035219 | 0.24545 | 0.069342 | 0.07497 | 0.084846 | 0.12782 | 0.17255 | 0.042568 | -0.01162 | 0.11126 | 0.00493 | 0.008096 | -0.025021 | 0.009481 | -0.006022 | 0.010557 | 0.013401 | -0.005598 | 0.029951 | 0.010952
5327.2344 | 122.7402 | -0.082397 | 122.6166 | 0.13559 | -0.040521 | -0.034893 | -0.038752 | 0.013375 | 0.062691 | -0.067295 | -0.043661 | 0.074638 | -0.045424 | -0.042259 | -0.070797 | -0.036295 | -0.051798 | -0.030641 | 0.21798 | 0.041876 | 0.047504 | 0.043645 | 0.095772 | 0.14509 | 0.015102 | 0.002115 | 0.12041 | 0.000352 | 0.003517 | -0.025021 | 0.009481 | -0.006022 | 0.015135 | 0.027136 | 0.008137 | 0.025373 | 0.006374
5328.9531 | 122.699 | -0.07782 | 122.6074 | 0.13559 | -0.0451 | -0.025735 | -0.025017 | 0.017953 | 0.067269 | -0.062717 | -0.052818 | 0.065481 | -0.040846 | -0.03768 | -0.070797 | -0.040873 | -0.051798 | -0.030641 | 0.21341 | 0.03272 | 0.052085 | 0.052803 | 0.095773 | 0.14509 | 0.015103 | -0.007042 | 0.11126 | 0.00493 | 0.008096 | -0.025021 | 0.004903 | -0.006022 | 0.015135 | 0.017979 | -0.00102 | 0.029951 | 0.010952
5330.6719 | 122.731 | -0.086975 | 122.5937 | 0.13101 | -0.0451 | -0.030314 | -0.025017 | 0.008797 | 0.062691 | -0.062717 | -0.052818 | 0.065481 | -0.036267 | -0.03768 | -0.066219 | -0.036295 | -0.04722 | -0.030641 | 0.21798 | 0.041875 | 0.056661 | 0.061958 | 0.095772 | 0.14967 | 0.024258 | -0.007042 | 0.11126 | 0.009509 | 0.008096 | -0.020443 | 0.009481 | -0.001444 | 0.015135 | 0.013401 | -0.005598 | 0.029952 | 0.010953
5332.4062 | 122.7356 | -0.09613 | 122.5983 | 0.13101 | -0.049678 | -0.030314 | -0.029595 | 0.013375 | 0.067269 | -0.062717 | -0.052818 | 0.065481 | -0.036267 | -0.046838 | -0.061641 | -0.031717 | -0.04722 | -0.030641 | 0.22714 | 0.046452 | 0.065816 | 0.066535 | 0.1095 | 0.1634 | 0.033413 | -0.007042 | 0.11126 | 0.009509 | -0.001062 | -0.015865 | 0.014059 | -0.001444 | 0.015135 | 0.008823 | -0.005598 | 0.025374 | 0.010953
5334.1094 | 122.7539 | -0.045776 | 122.612 | 0.13559 | -0.0451 | -0.034893 | -0.029595 | 0.013375 | 0.062691 | -0.062717 | -0.052818 | 0.065481 | -0.040846 | -0.042259 | -0.070797 | -0.040873 | -0.04722 | -0.030641 | 0.18136 | 0.000676 | 0.010883 | 0.016181 | 0.059151 | 0.10847 | -0.016941 | -0.007042 | 0.11126 | 0.00493 | 0.003517 | -0.025021 | 0.004903 | -0.001444 | 0.015135 | 0.017979 | -0.005598 | 0.029951 | 0.006374
5335.8438 | 122.7814 | -0.050354 | 122.5891 | 0.12643 | -0.049678 | -0.034893 | -0.034174 | 0.013375 | 0.062691 | -0.067295 | -0.048239 | 0.060902 | -0.045424 | -0.042259 | -0.061641 | -0.040873 | -0.04722 | -0.035219 | 0.17678 | 0.000676 | 0.015461 | 0.01618 | 0.063729 | 0.11305 | -0.016941 | -0.002463 | 0.10668 | 0.000352 | 0.003517 | -0.015865 | 0.004903 | -0.001444 | 0.010557 | 0.013402 | -0.001019 | 0.016217 | 0.001796
5337.5625 | 122.6532 | -0.1236 | 122.6532 | 0.13101 | -0.040521 | -0.025735 | -0.020438 | 0.013375 | 0.067269 | -0.067295 | -0.052818 | 0.07006 | -0.040846 | -0.046838 | -0.070797 | -0.045451 | -0.051798 | -0.035219 | 0.2546 | 0.083075 | 0.097861 | 0.10316 | 0.13697 | 0.19087 | 0.056301 | -0.007042 | 0.11584 | 0.00493 | -0.001062 | -0.025021 | 0.000325 | -0.006022 | 0.010557 | 0.017979 | -0.00102 | 0.029951 | 0.010952
5339.3281 | 122.7402 | -0.082397 | 122.58 | 0.12643 | -0.040521 | -0.034893 | -0.025017 | 0.013375 | 0.058113 | -0.067295 | -0.048239 | 0.065481 | -0.045424 | -0.046838 | -0.070797 | -0.040873 | -0.051798 | -0.035219 | 0.20883 | 0.041876 | 0.047504 | 0.05738 | 0.095772 | 0.14051 | 0.015102 | -0.002463 | 0.11126 | 0.000352 | -0.001062 | -0.025021 | 0.004903 | -0.006022 | 0.010557 | 0.022558 | 0.003559 | 0.025373 | 0.006374
5341.0469 | 122.7539 | -0.064087 | 122.6028 | 0.13559 | -0.0451 | -0.034893 | -0.034174 | 0.008797 | 0.067269 | -0.067295 | -0.043661 | 0.060902 | -0.045424 | -0.042259 | -0.066219 | -0.040873 | -0.042641 | -0.035219 | 0.19967 | 0.018987 | 0.029194 | 0.029913 | 0.072884 | 0.13136 | -0.003208 | 0.002115 | 0.10668 | 0.000352 | 0.003517 | -0.020443 | 0.004903 | 0.003135 | 0.010557 | 0.022558 | -0.00102 | 0.020795 | -0.002783
5342.7969 | 122.7676 | -0.07782 | 122.6212 | 0.13559 | -0.0451 | -0.030314 | -0.029595 | 0.008797 | 0.067269 | -0.062717 | -0.048239 | 0.060902 | -0.036267 | -0.042259 | -0.070797 | -0.036295 | -0.042641 | -0.030641 | 0.21341 | 0.03272 | 0.047506 | 0.048225 | 0.086617 | 0.14509 | 0.015103 | -0.002463 | 0.10668 | 0.009509 | 0.003517 | -0.025021 | 0.009481 | 0.003135 | 0.015135 | 0.022558 | -0.005598 | 0.03453 | 0.006374
5344.5156 | 122.7402 | -0.082397 | 122.6212 | 0.13101 | -0.049678 | -0.030314 | -0.029595 | 0.008797 | 0.067269 | -0.062717 | -0.052818 | 0.060902 | -0.040846 | -0.042259 | -0.061641 | -0.036295 | -0.042641 | -0.035219 | 0.21341 | 0.032719 | 0.052083 | 0.052802 | 0.091194 | 0.14967 | 0.01968 | -0.007042 | 0.10668 | 0.00493 | 0.003517 | -0.015865 | 0.009481 | 0.003135 | 0.010557 | 0.008823 | -0.010177 | 0.020795 | 0.001795
5346.2344 | 122.7951 | -0.064087 | 122.5891 | 0.13559 | -0.040521 | -0.034893 | -0.029595 | 0.013375 | 0.067269 | -0.067295 | -0.057396 | 0.065481 | -0.045424 | -0.03768 | -0.066219 | -0.036295 | -0.042641 | -0.026063 | 0.19967 | 0.023566 | 0.029194 | 0.034492 | 0.077462 | 0.13136 | -0.003208 | -0.01162 | 0.11126 | 0.000352 | 0.008096 | -0.020443 | 0.009481 | 0.003135 | 0.019713 | 0.008823 | -0.014755 | 0.020795 | -0.002783
5347.9688 | 122.6715 | -0.10071 | 122.6257 | 0.13101 | -0.0451 | -0.030314 | -0.025017 | 0.013375 | 0.071848 | -0.062717 | -0.048239 | 0.07006 | -0.040846 | -0.042259 | -0.066219 | -0.036295 | -0.051798 | -0.035219 | 0.23172 | 0.055608 | 0.070394 | 0.075691 | 0.11408 | 0.17256 | 0.037991 | -0.002463 | 0.11584 | 0.00493 | 0.003517 | -0.020443 | 0.009481 | -0.006022 | 0.010557 | 0.01798 | 0.003559 | 0.025373 | 0.010952
5349.6875 | 122.6761 | -0.1236 | 122.6257 | 0.13559 | -0.040521 | -0.030314 | -0.029595 | 0.017953 | 0.071848 | -0.062717 | -0.048239 | 0.060902 | -0.040846 | -0.03768 | -0.066219 | -0.036295 | -0.04722 | -0.035219 | 0.25918 | 0.083075 | 0.093282 | 0.094001 | 0.14155 | 0.19544 | 0.060879 | -0.002463 | 0.10668 | 0.00493 | 0.008096 | -0.020443 | 0.009481 | -0.001444 | 0.010557 | 0.01798 | -0.001019 | 0.025373 | 0.006374
5351.4062 | 122.7356 | -0.09613 | 122.6303 | 0.13101 | -0.049678 | -0.034893 | -0.029595 | 0.013375 | 0.067269 | -0.062717 | -0.052818 | 0.060902 | -0.045424 | -0.03768 | -0.070797 | -0.036295 | -0.056376 | -0.039797 | 0.22714 | 0.046452 | 0.061237 | 0.066535 | 0.1095 | 0.1634 | 0.033413 | -0.007042 | 0.10668 | 0.000352 | 0.008096 | -0.025021 | 0.009481 | -0.0106 | 0.005979 | 0.017979 | 0.003558 | 0.025373 | 0.010952
5353.1562 | 122.6532 | -0.11902 | 122.6349 | 0.13559 | -0.0451 | -0.030314 | -0.029595 | 0.017953 | 0.067269 | -0.058139 | -0.052818 | 0.065481 | -0.040846 | -0.042259 | -0.066219 | -0.040873 | -0.051798 | -0.030641 | 0.25461 | 0.073919 | 0.088705 | 0.089424 | 0.13697 | 0.18629 | 0.06088 | -0.007042 | 0.11126 | 0.00493 | 0.003517 | -0.020443 | 0.004903 | -0.006022 | 0.015135 | 0.013401 | -0.00102 | 0.025373 | 0.010952
5354.875 | 122.6578 | -0.09613 | 122.6349 | 0.13559 | -0.049678 | -0.021157 | -0.034174 | 0.013375 | 0.071848 | -0.062717 | -0.052818 | 0.056323 | -0.040846 | -0.033101 | -0.070797 | -0.040873 | -0.051798 | -0.035219 | 0.23172 | 0.046452 | 0.074973 | 0.061956 | 0.1095 | 0.16798 | 0.033413 | -0.007042 | 0.1021 | 0.00493 | 0.012675 | -0.025021 | 0.004903 | -0.006022 | 0.010557 | 0.017979 | -0.00102 | 0.029951 | 0.010952
5356.5938 | 122.6532 | -0.11902 | 122.6669 | 0.13101 | -0.040521 | -0.025735 | -0.029595 | 0.013375 | 0.067269 | -0.062717 | -0.052818 | 0.065481 | -0.045424 | -0.046838 | -0.066219 | -0.036295 | -0.04722 | -0.035219 | 0.25003 | 0.078498 | 0.093284 | 0.089424 | 0.13239 | 0.18629 | 0.056302 | -0.007042 | 0.11126 | 0.000352 | -0.001062 | -0.020443 | 0.009481 | -0.001444 | 0.010557 | 0.013401 | -0.005598 | 0.020795 | 0.001796
5358.3594 | 122.7356 | -0.082397 | 122.6349 | 0.13559 | -0.0451 | -0.025735 | -0.025017 | 0.013375 | 0.058113 | -0.067295 | -0.052818 | 0.07006 | -0.040846 | -0.046838 | -0.061641 | -0.031717 | -0.04722 | -0.026063 | 0.21798 | 0.037297 | 0.056662 | 0.05738 | 0.095772 | 0.14051 | 0.015102 | -0.007042 | 0.11584 | 0.00493 | -0.001062 | -0.015865 | 0.014059 | -0.001444 | 0.019713 | 0.008823 | -0.005598 | 0.020795 | 0.006374
5360.0625 | 122.6578 | -0.10986 | 122.6166 | 0.14017 | -0.049678 | -0.025735 | -0.029595 | 0.017953 | 0.071848 | -0.058139 | -0.052818 | 0.065481 | -0.040846 | -0.03768 | -0.079953 | -0.036295 | -0.04722 | -0.030641 | 0.25003 | 0.060185 | 0.084128 | 0.080268 | 0.12782 | 0.18171 | 0.051724 | -0.007042 | 0.11126 | 0.00493 | 0.008096 | -0.034177 | 0.009481 | -0.001444 | 0.015135 | 0.027135 | -0.005598 | 0.039107 | 0.006374
5361.8281 | 122.6807 | -0.09613 | 122.6532 | 0.12643 | -0.049678 | -0.034893 | -0.025017 | 0.013375 | 0.062691 | -0.071874 | -0.048239 | 0.065481 | -0.036267 | -0.042259 | -0.070797 | -0.040873 | -0.042641 | -0.035219 | 0.22256 | 0.046452 | 0.061237 | 0.071113 | 0.1095 | 0.15882 | 0.024256 | -0.002463 | 0.11126 | 0.009509 | 0.003517 | -0.025021 | 0.004903 | 0.003135 | 0.010557 | 0.022558 | -0.005598 | 0.03453 | 0.006374
5363.5469 | 122.6852 | -0.086975 | 122.6257 | 0.13101 | -0.054257 | -0.025735 | -0.029595 | 0.008797 | 0.062691 | -0.062717 | -0.052818 | 0.07006 | -0.050002 | -0.042259 | -0.070797 | -0.040873 | -0.056376 | -0.026063 | 0.21798 | 0.032718 | 0.06124 | 0.05738 | 0.095772 | 0.14967 | 0.024258 | -0.007042 | 0.11584 | -0.004226 | 0.003517 | -0.025021 | 0.004903 | -0.0106 | 0.019713 | 0.017979 | 0.003558 | 0.020795 | 0.006374
5365.2812 | 122.6486 | -0.11902 | 122.6303 | 0.13101 | -0.040521 | -0.034893 | -0.025017 | 0.013375 | 0.062691 | -0.062717 | -0.057396 | 0.074638 | -0.040846 | -0.042259 | -0.070797 | -0.036295 | -0.04722 | -0.035219 | 0.25003 | 0.078498 | 0.084126 | 0.094002 | 0.13239 | 0.18171 | 0.056302 | -0.01162 | 0.12041 | 0.00493 | 0.003517 | -0.025021 | 0.009481 | -0.001444 | 0.010557 | 0.013401 | -0.010176 | 0.029951 | 0.006374
5367 | 122.6532 | -0.1236 | 122.644 | 0.12643 | -0.049678 | -0.030314 | -0.029595 | 0.013375 | 0.071848 | -0.062717 | -0.048239 | 0.060902 | -0.045424 | -0.03768 | -0.066219 | -0.045451 | -0.042641 | -0.030641 | 0.25002 | 0.073918 | 0.093282 | 0.094001 | 0.13697 | 0.19544 | 0.060879 | -0.002463 | 0.10668 | 0.000352 | 0.008096 | -0.020443 | 0.000325 | 0.003135 | 0.015135 | 0.01798 | -0.005598 | 0.020795 | -0.002783
5368.7188 | 122.7951 | -0.064087 | 122.5983 | 0.13101 | -0.049678 | -0.025735 | -0.025017 | 0.013375 | 0.067269 | -0.067295 | -0.048239 | 0.07006 | -0.045424 | -0.042259 | -0.066219 | -0.045451 | -0.051798 | -0.030641 | 0.1951 | 0.014409 | 0.038352 | 0.03907 | 0.077462 | 0.13136 | -0.003208 | -0.002463 | 0.11584 | 0.000352 | 0.003517 | -0.020443 | 0.000325 | -0.006022 | 0.015135 | 0.01798 | 0.003559 | 0.020795 | 0.006374
5370.4375 | 122.699 | -0.082397 | 122.6303 | 0.13101 | -0.054257 | -0.025735 | -0.034174 | 0.013375 | 0.062691 | -0.062717 | -0.048239 | 0.065481 | -0.045424 | -0.03768 | -0.066219 | -0.045451 | -0.038063 | -0.035219 | 0.21341 | 0.02814 | 0.056662 | 0.048223 | 0.095772 | 0.14509 | 0.01968 | -0.002463 | 0.11126 | 0.000352 | 0.008096 | -0.020443 | 0.000325 | 0.007713 | 0.010557 | 0.01798 | -0.010176 | 0.020795 | -0.007361
5372.1562 | 122.7036 | -0.10986 | 122.6532 | 0.14474 | -0.040521 | -0.030314 | -0.025017 | 0.022531 | 0.071848 | -0.067295 | -0.043661 | 0.065481 | -0.036267 | -0.051417 | -0.066219 | -0.040873 | -0.051798 | -0.035219 | 0.25461 | 0.069342 | 0.079549 | 0.084846 | 0.13239 | 0.18171 | 0.042568 | 0.002115 | 0.11126 | 0.009509 | -0.005641 | -0.020443 | 0.004903 | -0.006022 | 0.010557 | 0.022558 | 0.008137 | 0.029952 | 0.015531
5373.8906 | 122.6486 | -0.10529 | 122.644 | 0.14017 | -0.049678 | -0.030314 | -0.034174 | 0.017953 | 0.067269 | -0.071874 | -0.039082 | 0.065481 | -0.040846 | -0.042259 | -0.070797 | -0.040873 | -0.04722 | -0.035219 | 0.24545 | 0.055608 | 0.074972 | 0.071112 | 0.12324 | 0.17256 | 0.033412 | 0.006694 | 0.11126 | 0.00493 | 0.003517 | -0.025021 | 0.004903 | -0.001444 | 0.010557 | 0.031715 | 0.008138 | 0.029951 | 0.006374
5375.625 | 122.7173 | -0.11444 | 122.6257 | 0.13559 | -0.049678 | -0.025735 | -0.029595 | 0.004219 | 0.067269 | -0.058139 | -0.057396 | 0.060902 | -0.045424 | -0.042259 | -0.066219 | -0.027139 | -0.04722 | -0.026063 | 0.25003 | 0.064763 | 0.088706 | 0.084846 | 0.11866 | 0.18171 | 0.056302 | -0.01162 | 0.10668 | 0.000352 | 0.003517 | -0.020443 | 0.018637 | -0.001444 | 0.019713 | 0.008823 | -0.010176 | 0.020795 | 0.001796
5377.3281 | 122.6898 | -0.09613 | 122.6532 | 0.14017 | -0.054257 | -0.030314 | -0.029595 | 0.013375 | 0.067269 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.046838 | -0.061641 | -0.040873 | -0.04722 | -0.026063 | 0.2363 | 0.041873 | 0.065816 | 0.066535 | 0.1095 | 0.1634 | 0.033413 | -0.002463 | 0.11126 | 0.00493 | -0.001062 | -0.015865 | 0.004903 | -0.001444 | 0.019713 | 0.013402 | -0.001019 | 0.020795 | 0.006374
5379.0312 | 122.7539 | -0.064087 | 122.6257 | 0.13559 | -0.049678 | -0.034893 | -0.034174 | 0.013375 | 0.062691 | -0.062717 | -0.048239 | 0.065481 | -0.045424 | -0.042259 | -0.066219 | -0.031717 | -0.051798 | -0.026063 | 0.19967 | 0.014409 | 0.029194 | 0.029913 | 0.077462 | 0.12678 | 0.00137 | -0.002463 | 0.11126 | 0.000352 | 0.003517 | -0.020443 | 0.014059 | -0.006022 | 0.019713 | 0.01798 | 0.003559 | 0.020795 | 0.006374
5380.8281 | 122.7036 | -0.091553 | 122.6395 | 0.13559 | -0.049678 | -0.034893 | -0.034174 | 0.013375 | 0.062691 | -0.062717 | -0.043661 | 0.065481 | -0.040846 | -0.046838 | -0.070797 | -0.031717 | -0.051798 | -0.030641 | 0.22714 | 0.041875 | 0.05666 | 0.057379 | 0.10493 | 0.15424 | 0.028836 | 0.002115 | 0.11126 | 0.00493 | -0.001062 | -0.025021 | 0.014059 | -0.006022 | 0.015135 | 0.027136 | 0.008137 | 0.029951 | 0.010952
5382.5469 | 122.8088 | -0.054932 | 122.6074 | 0.13559 | -0.049678 | -0.030314 | -0.029595 | 0.013375 | 0.062691 | -0.067295 | -0.048239 | 0.056323 | -0.045424 | -0.046838 | -0.066219 | -0.036295 | -0.051798 | -0.026063 | 0.19052 | 0.005254 | 0.024618 | 0.025337 | 0.068307 | 0.11762 | -0.012363 | -0.002463 | 0.1021 | 0.000352 | -0.001062 | -0.020443 | 0.009481 | -0.006022 | 0.019713 | 0.01798 | 0.003559 | 0.020795 | 0.006374
5384.2656 | 122.7356 | -0.073242 | 122.6257 | 0.14017 | -0.049678 | -0.034893 | -0.034174 | 0.008797 | 0.062691 | -0.067295 | -0.052818 | 0.060902 | -0.040846 | -0.03768 | -0.070797 | -0.040873 | -0.051798 | -0.035219 | 0.21341 | 0.023564 | 0.038349 | 0.039068 | 0.082039 | 0.13593 | 0.005947 | -0.007042 | 0.10668 | 0.00493 | 0.008096 | -0.025021 | 0.004903 | -0.006022 | 0.010557 | 0.017979 | -0.00102 | 0.029951 | 0.010952
5386 | 122.8134 | -0.073242 | 122.6349 | 0.13101 | -0.049678 | -0.034893 | -0.034174 | 0.013375 | 0.062691 | -0.067295 | -0.039082 | 0.065481 | -0.045424 | -0.03768 | -0.061641 | -0.036295 | -0.042641 | -0.035219 | 0.20425 | 0.023564 | 0.038349 | 0.039068 | 0.086617 | 0.13593 | 0.005947 | 0.006694 | 0.11126 | 0.000352 | 0.008096 | -0.015865 | 0.009481 | 0.003135 | 0.010557 | 0.022559 | 0.003559 | 0.016217 | -0.002783
5387.7031 | 122.8088 | -0.068665 | 122.612 | 0.13101 | -0.054257 | -0.025735 | -0.034174 | 0.013375 | 0.071848 | -0.062717 | -0.043661 | 0.065481 | -0.045424 | -0.042259 | -0.066219 | -0.036295 | -0.042641 | -0.030641 | 0.19967 | 0.014408 | 0.04293 | 0.034491 | 0.08204 | 0.14051 | 0.005948 | 0.002115 | 0.11126 | 0.000352 | 0.003517 | -0.020443 | 0.009481 | 0.003135 | 0.015135 | 0.022558 | -0.00102 | 0.020795 | -0.002783
5389.4062 | 122.7814 | -0.082397 | 122.6257 | 0.12185 | -0.054257 | -0.025735 | -0.034174 | 0.013375 | 0.067269 | -0.067295 | -0.048239 | 0.060902 | -0.050002 | -0.046838 | -0.070797 | -0.045451 | -0.042641 | -0.030641 | 0.20425 | 0.02814 | 0.056662 | 0.048223 | 0.095772 | 0.14967 | 0.015102 | -0.002463 | 0.10668 | -0.004226 | -0.001062 | -0.025021 | 0.000325 | 0.003135 | 0.015135 | 0.022558 | -0.005598 | 0.020795 | -0.007361
5391.1094 | 122.6624 | -0.11902 | 122.644 | 0.13559 | -0.0451 | -0.030314 | -0.029595 | 0.013375 | 0.067269 | -0.062717 | -0.052818 | 0.07006 | -0.045424 | -0.042259 | -0.070797 | -0.040873 | -0.056376 | -0.030641 | 0.25461 | 0.073919 | 0.088705 | 0.089424 | 0.13239 | 0.18629 | 0.056302 | -0.007042 | 0.11584 | 0.000352 | 0.003517 | -0.025021 | 0.004903 | -0.0106 | 0.015135 | 0.017979 | 0.003558 | 0.025373 | 0.010952
5392.875 | 122.8088 | -0.068665 | 122.6028 | 0.13559 | -0.054257 | -0.034893 | -0.034174 | 0.008797 | 0.067269 | -0.067295 | -0.043661 | 0.07006 | -0.040846 | -0.051417 | -0.070797 | -0.036295 | -0.04722 | -0.030641 | 0.20425 | 0.014408 | 0.033772 | 0.034491 | 0.077462 | 0.13593 | 0.00137 | 0.002115 | 0.11584 | 0.00493 | -0.005641 | -0.025021 | 0.009481 | -0.001444 | 0.015135 | 0.027136 | 0.003559 | 0.029951 | 0.006374
5394.5938 | 122.7539 | -0.07782 | 122.6074 | 0.14017 | -0.049678 | -0.030314 | -0.029595 | 0.008797 | 0.067269 | -0.062717 | -0.048239 | 0.065481 | -0.045424 | -0.03768 | -0.061641 | -0.040873 | -0.051798 | -0.030641 | 0.21799 | 0.028142 | 0.047506 | 0.048225 | 0.086617 | 0.14509 | 0.015103 | -0.002463 | 0.11126 | 0.000352 | 0.008096 | -0.015865 | 0.004903 | -0.006022 | 0.015135 | 0.013402 | 0.003559 | 0.016217 | 0.006374
5396.3594 | 122.7173 | -0.10071 | 122.6303 | 0.13559 | -0.049678 | -0.025735 | -0.025017 | 0.017953 | 0.058113 | -0.067295 | -0.052818 | 0.065481 | -0.040846 | -0.03768 | -0.070797 | -0.031717 | -0.051798 | -0.039797 | 0.23629 | 0.05103 | 0.074973 | 0.075691 | 0.11866 | 0.15882 | 0.033413 | -0.007042 | 0.11126 | 0.00493 | 0.008096 | -0.025021 | 0.014059 | -0.006022 | 0.005979 | 0.017979 | -0.00102 | 0.029951 | 0.010952
5398.0625 | 122.7859 | -0.054932 | 122.5983 | 0.13101 | -0.054257 | -0.030314 | -0.025017 | 0.008797 | 0.062691 | -0.062717 | -0.057396 | 0.056323 | -0.040846 | -0.042259 | -0.070797 | -0.045451 | -0.051798 | -0.035219 | 0.18594 | 0.000675 | 0.024618 | 0.029915 | 0.063729 | 0.11762 | -0.007785 | -0.01162 | 0.1021 | 0.00493 | 0.003517 | -0.025021 | 0.000325 | -0.006022 | 0.010557 | 0.013401 | -0.005598 | 0.029951 | 0.010952
5399.7812 | 122.6944 | -0.10071 | 122.6486 | 0.13559 | -0.0451 | -0.034893 | -0.034174 | 0.013375 | 0.062691 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.051417 | -0.066219 | -0.036295 | -0.04722 | -0.030641 | 0.23629 | 0.055608 | 0.065815 | 0.066534 | 0.11408 | 0.1634 | 0.037991 | -0.002463 | 0.11126 | 0.00493 | -0.005641 | -0.020443 | 0.009481 | -0.001444 | 0.015135 | 0.01798 | -0.001019 | 0.025373 | 0.006374
5401.5156 | 122.7814 | -0.059509 | 122.612 | 0.13101 | -0.040521 | -0.034893 | -0.034174 | 0.013375 | 0.062691 | -0.067295 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.070797 | -0.031717 | -0.056376 | -0.035219 | 0.19052 | 0.018988 | 0.024616 | 0.025335 | 0.072884 | 0.1222 | -0.007786 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.025021 | 0.014059 | -0.0106 | 0.010557 | 0.022558 | 0.008137 | 0.029951 | 0.01553
5403.2812 | 122.7036 | -0.1236 | 122.6669 | 0.12643 | -0.049678 | -0.030314 | -0.029595 | 0.017953 | 0.062691 | -0.067295 | -0.043661 | 0.060902 | -0.040846 | -0.042259 | -0.070797 | -0.040873 | -0.051798 | -0.039797 | 0.25002 | 0.073918 | 0.093282 | 0.094001 | 0.14155 | 0.18629 | 0.056301 | 0.002115 | 0.10668 | 0.00493 | 0.003517 | -0.025021 | 0.004903 | -0.006022 | 0.005979 | 0.027136 | 0.008137 | 0.029951 | 0.010952
5405 | 122.6715 | -0.091553 | 122.6807 | 0.13559 | -0.058836 | -0.025735 | -0.025017 | 0.013375 | 0.062691 | -0.062717 | -0.052818 | 0.065481 | -0.045424 | -0.046838 | -0.066219 | -0.036295 | -0.051798 | -0.035219 | 0.22714 | 0.032717 | 0.065818 | 0.066536 | 0.10493 | 0.15424 | 0.028836 | -0.007042 | 0.11126 | 0.000352 | -0.001062 | -0.020443 | 0.009481 | -0.006022 | 0.010557 | 0.013401 | -0.00102 | 0.020795 | 0.006374
5406.7188 | 122.6807 | -0.10071 | 122.6578 | 0.13101 | -0.049678 | -0.034893 | -0.029595 | 0.013375 | 0.067269 | -0.062717 | -0.052818 | 0.060902 | -0.036267 | -0.03768 | -0.070797 | -0.040873 | -0.04722 | -0.039797 | 0.23172 | 0.05103 | 0.065815 | 0.071113 | 0.11408 | 0.16798 | 0.037991 | -0.007042 | 0.10668 | 0.009509 | 0.008096 | -0.025021 | 0.004903 | -0.001444 | 0.005979 | 0.017979 | -0.005598 | 0.03453 | 0.010953
5408.4375 | 122.7951 | -0.054932 | 122.6257 | 0.13101 | -0.054257 | -0.021157 | -0.029595 | 0.013375 | 0.062691 | -0.067295 | -0.048239 | 0.060902 | -0.045424 | -0.042259 | -0.066219 | -0.036295 | -0.056376 | -0.030641 | 0.18594 | 0.000675 | 0.033775 | 0.025337 | 0.068307 | 0.11762 | -0.012363 | -0.002463 | 0.10668 | 0.000352 | 0.003517 | -0.020443 | 0.009481 | -0.0106 | 0.015135 | 0.01798 | 0.008137 | 0.020795 | 0.010952
5410.1562 | 122.7722 | -0.059509 | 122.644 | 0.14474 | -0.054257 | -0.030314 | -0.034174 | 0.008797 | 0.071848 | -0.067295 | -0.043661 | 0.074638 | -0.040846 | -0.03768 | -0.066219 | -0.036295 | -0.04722 | -0.026063 | 0.20425 | 0.005252 | 0.029195 | 0.025335 | 0.068306 | 0.13136 | -0.007786 | 0.002115 | 0.12041 | 0.00493 | 0.008096 | -0.020443 | 0.009481 | -0.001444 | 0.019713 | 0.022558 | 0.003559 | 0.025373 | 0.006374
5411.875 | 122.818 | -0.050354 | 122.6486 | 0.14017 | -0.049678 | -0.030314 | -0.034174 | 0.004219 | 0.062691 | -0.062717 | -0.043661 | 0.065481 | -0.040846 | -0.046838 | -0.066219 | -0.031717 | -0.051798 | -0.035219 | 0.19052 | 0.000676 | 0.02004 | 0.01618 | 0.054573 | 0.11305 | -0.012363 | 0.002115 | 0.11126 | 0.00493 | -0.001062 | -0.020443 | 0.014059 | -0.006022 | 0.010557 | 0.022558 | 0.008137 | 0.025373 | 0.010952
5413.5938 | 122.818 | -0.045776 | 122.5983 | 0.13559 | -0.049678 | -0.039471 | -0.034174 | 0.013375 | 0.062691 | -0.067295 | -0.052818 | 0.060902 | -0.040846 | -0.03768 | -0.066219 | -0.040873 | -0.04722 | -0.035219 | 0.18136 | -0.003902 | 0.006305 | 0.011602 | 0.059151 | 0.10847 | -0.021519 | -0.007042 | 0.10668 | 0.00493 | 0.008096 | -0.020443 | 0.004903 | -0.001444 | 0.010557 | 0.013401 | -0.005598 | 0.025373 | 0.006374
5415.3438 | 122.8134 | -0.054932 | 122.6257 | 0.12185 | -0.049678 | -0.034893 | -0.029595 | 0.008797 | 0.067269 | -0.071874 | -0.048239 | 0.074638 | -0.036267 | -0.042259 | -0.066219 | -0.036295 | -0.051798 | -0.035219 | 0.17678 | 0.005254 | 0.020039 | 0.025337 | 0.063729 | 0.1222 | -0.016942 | -0.002463 | 0.12041 | 0.009509 | 0.003517 | -0.020443 | 0.009481 | -0.006022 | 0.010557 | 0.01798 | 0.003559 | 0.029952 | 0.015531
5417.0469 | 122.8043 | -0.073242 | 122.644 | 0.13101 | -0.054257 | -0.034893 | -0.025017 | 0.017953 | 0.062691 | -0.067295 | -0.048239 | 0.065481 | -0.045424 | -0.03768 | -0.066219 | -0.036295 | -0.042641 | -0.039797 | 0.20425 | 0.018985 | 0.038349 | 0.048225 | 0.091195 | 0.13593 | 0.005947 | -0.002463 | 0.11126 | 0.000352 | 0.008096 | -0.020443 | 0.009481 | 0.003135 | 0.005979 | 0.01798 | -0.005598 | 0.020795 | -0.002783
5418.7812 | 122.8226 | -0.073242 | 122.6166 | 0.12643 | -0.054257 | -0.030314 | -0.029595 | 0.008797 | 0.062691 | -0.067295 | -0.048239 | 0.065481 | -0.045424 | -0.03768 | -0.066219 | -0.031717 | -0.051798 | -0.030641 | 0.19967 | 0.018985 | 0.042928 | 0.043647 | 0.082039 | 0.13593 | 0.005947 | -0.002463 | 0.11126 | 0.000352 | 0.008096 | -0.020443 | 0.014059 | -0.006022 | 0.015135 | 0.01798 | 0.003559 | 0.020795 | 0.006374
5420.5 | 122.7814 | -0.086975 | 122.644 | 0.13101 | -0.054257 | -0.030314 | -0.038752 | 0.004219 | 0.053534 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.061641 | -0.036295 | -0.04722 | -0.035219 | 0.21798 | 0.032718 | 0.056661 | 0.048223 | 0.091194 | 0.14051 | 0.024258 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.015865 | 0.009481 | -0.001444 | 0.010557 | 0.013402 | -0.001019 | 0.020795 | 0.006374
5422.25 | 122.6852 | -0.11902 | 122.6898 | 0.12643 | -0.049678 | -0.021157 | -0.025017 | 0.013375 | 0.067269 | -0.071874 | -0.048239 | 0.065481 | -0.045424 | -0.03768 | -0.070797 | -0.045451 | -0.042641 | -0.030641 | 0.24545 | 0.069341 | 0.097862 | 0.094002 | 0.13239 | 0.18629 | 0.047145 | -0.002463 | 0.11126 | 0.000352 | 0.008096 | -0.025021 | 0.000325 | 0.003135 | 0.015135 | 0.022558 | -0.005598 | 0.025373 | -0.002783
5423.9531 | 122.6761 | -0.11444 | 122.6624 | 0.13101 | -0.049678 | -0.030314 | -0.029595 | 0.017953 | 0.062691 | -0.062717 | -0.043661 | 0.07006 | -0.040846 | -0.033101 | -0.070797 | -0.040873 | -0.04722 | -0.035219 | 0.24545 | 0.064763 | 0.084127 | 0.084846 | 0.13239 | 0.17713 | 0.051724 | 0.002115 | 0.11584 | 0.00493 | 0.012675 | -0.025021 | 0.004903 | -0.001444 | 0.010557 | 0.027136 | 0.003559 | 0.029951 | 0.006374
5425.6719 | 122.7722 | -0.07782 | 122.6212 | 0.13559 | -0.054257 | -0.025735 | -0.029595 | 0.017953 | 0.062691 | -0.067295 | -0.043661 | 0.060902 | -0.036267 | -0.042259 | -0.070797 | -0.040873 | -0.051798 | -0.030641 | 0.21341 | 0.023563 | 0.052085 | 0.048225 | 0.095773 | 0.14051 | 0.010525 | 0.002115 | 0.10668 | 0.009509 | 0.003517 | -0.025021 | 0.004903 | -0.006022 | 0.015135 | 0.027136 | 0.008137 | 0.03453 | 0.015531
5427.3906 | 122.7539 | -0.082397 | 122.644 | 0.13559 | -0.054257 | -0.030314 | -0.034174 | 0.008797 | 0.058113 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.042259 | -0.066219 | -0.036295 | -0.051798 | -0.039797 | 0.21798 | 0.02814 | 0.052083 | 0.048223 | 0.091194 | 0.14051 | 0.01968 | -0.002463 | 0.11126 | 0.00493 | 0.003517 | -0.020443 | 0.009481 | -0.006022 | 0.005979 | 0.01798 | 0.003559 | 0.025373 | 0.010952
5429.0938 | 122.8088 | -0.059509 | 122.6395 | 0.13101 | -0.054257 | -0.025735 | -0.029595 | 0.008797 | 0.067269 | -0.058139 | -0.043661 | 0.07006 | -0.040846 | -0.042259 | -0.061641 | -0.031717 | -0.051798 | -0.026063 | 0.19052 | 0.005252 | 0.033774 | 0.029914 | 0.068306 | 0.12678 | 0.00137 | 0.002115 | 0.11584 | 0.00493 | 0.003517 | -0.015865 | 0.014059 | -0.006022 | 0.019713 | 0.01798 | 0.008137 | 0.020795 | 0.010952
5430.8125 | 122.7356 | -0.09613 | 122.6669 | 0.13559 | -0.054257 | -0.025735 | -0.034174 | 0.017953 | 0.067269 | -0.058139 | -0.052818 | 0.065481 | -0.045424 | -0.042259 | -0.070797 | -0.045451 | -0.04722 | -0.039797 | 0.23172 | 0.041873 | 0.070395 | 0.061956 | 0.11408 | 0.1634 | 0.037991 | -0.007042 | 0.11126 | 0.000352 | 0.003517 | -0.025021 | 0.000325 | -0.001444 | 0.005979 | 0.017979 | -0.005598 | 0.025373 | 0.001796
5432.5312 | 122.6944 | -0.10986 | 122.6761 | 0.13101 | -0.049678 | -0.030314 | -0.034174 | 0.008797 | 0.067269 | -0.067295 | -0.052818 | 0.065481 | -0.045424 | -0.03768 | -0.070797 | -0.036295 | -0.04722 | -0.021484 | 0.24087 | 0.060185 | 0.079549 | 0.075689 | 0.11866 | 0.17713 | 0.042568 | -0.007042 | 0.11126 | 0.000352 | 0.008096 | -0.025021 | 0.009481 | -0.001444 | 0.024292 | 0.017979 | -0.005598 | 0.025373 | 0.001796
5434.2969 | 122.6807 | -0.10071 | 122.6761 | 0.13101 | -0.049678 | -0.030314 | -0.034174 | 0.013375 | 0.062691 | -0.067295 | -0.048239 | 0.056323 | -0.036267 | -0.046838 | -0.061641 | -0.036295 | -0.04722 | -0.026063 | 0.23172 | 0.05103 | 0.070394 | 0.066534 | 0.11408 | 0.1634 | 0.033413 | -0.002463 | 0.1021 | 0.009509 | -0.001062 | -0.015865 | 0.009481 | -0.001444 | 0.019713 | 0.013402 | -0.001019 | 0.025374 | 0.010953
5436.0156 | 122.7219 | -0.10529 | 122.6532 | 0.14017 | -0.054257 | -0.030314 | -0.029595 | 0.008797 | 0.076426 | -0.071874 | -0.052818 | 0.065481 | -0.050002 | -0.042259 | -0.066219 | -0.040873 | -0.04722 | -0.026063 | 0.24545 | 0.051029 | 0.074972 | 0.075691 | 0.11408 | 0.18171 | 0.033412 | -0.007042 | 0.11126 | -0.004226 | 0.003517 | -0.020443 | 0.004903 | -0.001444 | 0.019713 | 0.013401 | -0.005598 | 0.016217 | -0.002782
5437.7969 | 122.7036 | -0.1236 | 122.6624 | 0.12643 | -0.049678 | -0.025735 | -0.029595 | 0.013375 | 0.071848 | -0.062717 | -0.048239 | 0.065481 | -0.050002 | -0.03768 | -0.066219 | -0.036295 | -0.051798 | -0.035219 | 0.25002 | 0.073918 | 0.097861 | 0.094001 | 0.13697 | 0.19544 | 0.060879 | -0.002463 | 0.11126 | -0.004226 | 0.008096 | -0.020443 | 0.009481 | -0.006022 | 0.010557 | 0.01798 | 0.003559 | 0.016217 | 0.001796
5439.5 | 122.699 | -0.11444 | 122.6532 | 0.13101 | -0.049678 | -0.030314 | -0.034174 | 0.017953 | 0.062691 | -0.062717 | -0.052818 | 0.065481 | -0.036267 | -0.033101 | -0.075375 | -0.036295 | -0.042641 | -0.035219 | 0.24545 | 0.064763 | 0.084127 | 0.080267 | 0.13239 | 0.17713 | 0.051724 | -0.007042 | 0.11126 | 0.009509 | 0.012675 | -0.029599 | 0.009481 | 0.003135 | 0.010557 | 0.022557 | -0.010177 | 0.039108 | 0.006374
5441.2344 | 122.6715 | -0.09613 | 122.644 | 0.13101 | -0.0451 | -0.034893 | -0.034174 | 0.022531 | 0.067269 | -0.071874 | -0.039082 | 0.065481 | -0.031689 | -0.042259 | -0.066219 | -0.040873 | -0.051798 | -0.035219 | 0.22714 | 0.05103 | 0.061237 | 0.061956 | 0.11866 | 0.1634 | 0.024256 | 0.006694 | 0.11126 | 0.014087 | 0.003517 | -0.020443 | 0.004903 | -0.006022 | 0.010557 | 0.027137 | 0.012716 | 0.03453 | 0.020109
5442.9531 | 122.7997 | -0.059509 | 122.6395 | 0.13559 | -0.054257 | -0.034893 | -0.029595 | 0.017953 | 0.058113 | -0.062717 | -0.043661 | 0.065481 | -0.050002 | -0.042259 | -0.079953 | -0.040873 | -0.051798 | -0.021484 | 0.1951 | 0.005252 | 0.024616 | 0.029914 | 0.077462 | 0.11762 | -0.003208 | 0.002115 | 0.11126 | -0.004226 | 0.003517 | -0.034177 | 0.004903 | -0.006022 | 0.024292 | 0.036292 | 0.008137 | 0.029951 | 0.001796
5444.6875 | 122.7036 | -0.12817 | 122.6944 | 0.13559 | -0.054257 | -0.030314 | -0.025017 | 0.013375 | 0.062691 | -0.067295 | -0.048239 | 0.074638 | -0.045424 | -0.042259 | -0.075375 | -0.036295 | -0.04722 | -0.035219 | 0.26376 | 0.073917 | 0.09786 | 0.10316 | 0.14155 | 0.19087 | 0.060879 | -0.002463 | 0.12041 | 0.000352 | 0.003517 | -0.029599 | 0.009481 | -0.001444 | 0.010557 | 0.027136 | -0.001019 | 0.029951 | 0.001796
5446.3906 | 122.6807 | -0.11902 | 122.6807 | 0.14017 | -0.054257 | -0.025735 | -0.029595 | 0.017953 | 0.062691 | -0.062717 | -0.043661 | 0.074638 | -0.045424 | -0.046838 | -0.066219 | -0.036295 | -0.04722 | -0.035219 | 0.25918 | 0.064762 | 0.093284 | 0.089424 | 0.13697 | 0.18171 | 0.056302 | 0.002115 | 0.12041 | 0.000352 | -0.001062 | -0.020443 | 0.009481 | -0.001444 | 0.010557 | 0.022558 | 0.003559 | 0.020795 | 0.001796
5448.125 | 122.7081 | -0.10529 | 122.644 | 0.13101 | -0.054257 | -0.030314 | -0.034174 | 0.013375 | 0.062691 | -0.071874 | -0.048239 | 0.07006 | -0.045424 | -0.042259 | -0.066219 | -0.040873 | -0.04722 | -0.035219 | 0.23629 | 0.051029 | 0.074972 | 0.071112 | 0.11866 | 0.16798 | 0.033412 | -0.002463 | 0.11584 | 0.000352 | 0.003517 | -0.020443 | 0.004903 | -0.001444 | 0.010557 | 0.01798 | -0.001019 | 0.020795 | 0.001796
5449.8438 | 122.7448 | -0.10529 | 122.6715 | 0.13101 | -0.049678 | -0.030314 | -0.029595 | 0.017953 | 0.058113 | -0.058139 | -0.052818 | 0.07006 | -0.045424 | -0.033101 | -0.066219 | -0.040873 | -0.056376 | -0.030641 | 0.23629 | 0.055608 | 0.074972 | 0.075691 | 0.12324 | 0.1634 | 0.047147 | -0.007042 | 0.11584 | 0.000352 | 0.012675 | -0.020443 | 0.004903 | -0.0106 | 0.015135 | 0.013401 | 0.003558 | 0.020795 | 0.010952
5451.5625 | 122.8271 | -0.07782 | 122.644 | 0.13101 | -0.058836 | -0.030314 | -0.034174 | 0.008797 | 0.067269 | -0.071874 | -0.043661 | 0.065481 | -0.040846 | -0.03768 | -0.066219 | -0.027139 | -0.04722 | -0.035219 | 0.20883 | 0.018984 | 0.047506 | 0.043646 | 0.086617 | 0.14509 | 0.005946 | 0.002115 | 0.11126 | 0.00493 | 0.008096 | -0.020443 | 0.018637 | -0.001444 | 0.010557 | 0.022558 | 0.003559 | 0.025373 | 0.006374
5453.2969 | 122.7081 | -0.10529 | 122.699 | 0.13559 | -0.049678 | -0.030314 | -0.029595 | 0.017953 | 0.062691 | -0.062717 | -0.048239 | 0.07006 | -0.045424 | -0.03768 | -0.057062 | -0.036295 | -0.042641 | -0.030641 | 0.24087 | 0.055608 | 0.074972 | 0.075691 | 0.12324 | 0.16798 | 0.042569 | -0.002463 | 0.11584 | 0.000352 | 0.008096 | -0.011286 | 0.009481 | 0.003135 | 0.015135 | 0.008823 | -0.005598 | 0.011638 | -0.002783
5455.0312 | 122.8088 | -0.068665 | 122.6395 | 0.13101 | -0.054257 | -0.034893 | -0.025017 | 0.022531 | 0.058113 | -0.067295 | -0.048239 | 0.065481 | -0.040846 | -0.042259 | -0.075375 | -0.036295 | -0.051798 | -0.035219 | 0.19967 | 0.014408 | 0.033772 | 0.043648 | 0.091196 | 0.12678 | 0.00137 | -0.002463 | 0.11126 | 0.00493 | 0.003517 | -0.029599 | 0.009481 | -0.006022 | 0.010557 | 0.027136 | 0.003559 | 0.034529 | 0.010952
5456.7656 | 122.8088 | -0.07782 | 122.6715 | 0.13101 | -0.054257 | -0.025735 | -0.038752 | 0.008797 | 0.067269 | -0.062717 | -0.043661 | 0.065481 | -0.040846 | -0.042259 | -0.066219 | -0.045451 | -0.04722 | -0.030641 | 0.20883 | 0.023563 | 0.052085 | 0.039068 | 0.086617 | 0.14509 | 0.015103 | 0.002115 | 0.11126 | 0.00493 | 0.003517 | -0.020443 | 0.000325 | -0.001444 | 0.015135 | 0.022558 | 0.003559 | 0.025373 | 0.006374
5458.4688 | 122.7448 | -0.091553 | 122.6669 | 0.12643 | -0.0451 | -0.030314 | -0.020438 | 0.013375 | 0.067269 | -0.067295 | -0.057396 | 0.065481 | -0.040846 | -0.046838 | -0.066219 | -0.040873 | -0.042641 | -0.035219 | 0.21798 | 0.046453 | 0.061239 | 0.071115 | 0.10493 | 0.15882 | 0.024258 | -0.01162 | 0.11126 | 0.00493 | -0.001062 | -0.020443 | 0.004903 | 0.003135 | 0.010557 | 0.008823 | -0.014755 | 0.025373 | 0.001795
5460.1719 | 122.6898 | -0.10986 | 122.6624 | 0.13101 | -0.058836 | -0.030314 | -0.029595 | 0.013375 | 0.067269 | -0.058139 | -0.048239 | 0.065481 | -0.040846 | -0.033101 | -0.066219 | -0.040873 | -0.04722 | -0.039797 | 0.24087 | 0.051027 | 0.079549 | 0.080268 | 0.12324 | 0.17713 | 0.051724 | -0.002463 | 0.11126 | 0.00493 | 0.012675 | -0.020443 | 0.004903 | -0.001444 | 0.005979 | 0.01798 | -0.001019 | 0.025373 | 0.006374
5461.8906 | 122.7814 | -0.050354 | 122.6212 | 0.13559 | -0.058836 | -0.030314 | -0.034174 | 0.008797 | 0.067269 | -0.067295 | -0.052818 | 0.065481 | -0.045424 | -0.042259 | -0.066219 | -0.036295 | -0.056376 | -0.030641 | 0.18594 | -0.008482 | 0.02004 | 0.01618 | 0.059151 | 0.11762 | -0.016941 | -0.007042 | 0.11126 | 0.000352 | 0.003517 | -0.020443 | 0.009481 | -0.0106 | 0.015135 | 0.013401 | 0.003558 | 0.020795 | 0.010952
5463.6094 | 122.8088 | -0.073242 | 122.6532 | 0.13101 | -0.054257 | -0.025735 | -0.029595 | 0.013375 | 0.062691 | -0.062717 | -0.043661 | 0.07006 | -0.040846 | -0.03768 | -0.061641 | -0.040873 | -0.04722 | -0.026063 | 0.20425 | 0.018985 | 0.047507 | 0.043647 | 0.086617 | 0.13593 | 0.010525 | 0.002115 | 0.11584 | 0.00493 | 0.008096 | -0.015865 | 0.004903 | -0.001444 | 0.019713 | 0.01798 | 0.003559 | 0.020795 | 0.006374
5465.3281 | 122.8455 | -0.064087 | 122.6532 | 0.13101 | -0.058836 | -0.030314 | -0.029595 | 0.013375 | 0.058113 | -0.058139 | -0.043661 | 0.07006 | -0.040846 | -0.03768 | -0.066219 | -0.040873 | -0.051798 | -0.030641 | 0.1951 | 0.005251 | 0.033773 | 0.034492 | 0.077462 | 0.1222 | 0.005948 | 0.002115 | 0.11584 | 0.00493 | 0.008096 | -0.020443 | 0.004903 | -0.006022 | 0.015135 | 0.022558 | 0.008137 | 0.025373 | 0.010952
5467.0469 | 122.7676 | -0.091553 | 122.6578 | 0.13559 | -0.054257 | -0.034893 | -0.029595 | 0.017953 | 0.062691 | -0.062717 | -0.052818 | 0.065481 | -0.036267 | -0.042259 | -0.066219 | -0.045451 | -0.04722 | -0.035219 | 0.22714 | 0.037296 | 0.05666 | 0.061958 | 0.10951 | 0.15424 | 0.028836 | -0.007042 | 0.11126 | 0.009509 | 0.003517 | -0.020443 | 0.000325 | -0.001444 | 0.010557 | 0.013401 | -0.005598 | 0.029952 | 0.010953
5468.7656 | 122.7722 | -0.086975 | 122.6715 | 0.13559 | -0.049678 | -0.030314 | -0.025017 | 0.017953 | 0.071848 | -0.067295 | -0.048239 | 0.074638 | -0.045424 | -0.042259 | -0.066219 | -0.036295 | -0.051798 | -0.030641 | 0.22256 | 0.037297 | 0.056661 | 0.061958 | 0.10493 | 0.15882 | 0.01968 | -0.002463 | 0.12041 | 0.000352 | 0.003517 | -0.020443 | 0.009481 | -0.006022 | 0.015135 | 0.01798 | 0.003559 | 0.020795 | 0.006374
5470.4688 | 122.8043 | -0.082397 | 122.6578 | 0.13101 | -0.054257 | -0.030314 | -0.034174 | 0.017953 | 0.058113 | -0.067295 | -0.052818 | 0.056323 | -0.050002 | -0.042259 | -0.070797 | -0.040873 | -0.04722 | -0.039797 | 0.21341 | 0.02814 | 0.052083 | 0.048223 | 0.10035 | 0.14051 | 0.015102 | -0.007042 | 0.1021 | -0.004226 | 0.003517 | -0.025021 | 0.004903 | -0.001444 | 0.005979 | 0.017979 | -0.005598 | 0.020795 | -0.002782
5472.1719 | 122.7219 | -0.10529 | 122.6807 | 0.12643 | -0.054257 | -0.025735 | -0.029595 | 0.013375 | 0.067269 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.066219 | -0.040873 | -0.051798 | -0.030641 | 0.23172 | 0.051029 | 0.079551 | 0.075691 | 0.11866 | 0.17256 | 0.042569 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.020443 | 0.004903 | -0.006022 | 0.015135 | 0.01798 | 0.003559 | 0.025373 | 0.010952
5473.9219 | 122.7036 | -0.09613 | 122.6807 | 0.13101 | -0.058836 | -0.025735 | -0.029595 | 0.027109 | 0.071848 | -0.067295 | -0.048239 | 0.065481 | -0.050002 | -0.03768 | -0.070797 | -0.040873 | -0.042641 | -0.035219 | 0.22714 | 0.037294 | 0.070395 | 0.066535 | 0.12324 | 0.16798 | 0.028835 | -0.002463 | 0.11126 | -0.004226 | 0.008096 | -0.025021 | 0.004903 | 0.003135 | 0.010557 | 0.022558 | -0.005598 | 0.020795 | -0.007361
5475.625 | 122.8317 | -0.041199 | 122.6303 | 0.12643 | -0.054257 | -0.034893 | -0.029595 | 0.027109 | 0.062691 | -0.071874 | -0.039082 | 0.065481 | -0.040846 | -0.042259 | -0.066219 | -0.031717 | -0.056376 | -0.035219 | 0.16763 | -0.013058 | 0.006306 | 0.011604 | 0.068308 | 0.10389 | -0.030675 | 0.006694 | 0.11126 | 0.00493 | 0.003517 | -0.020443 | 0.014059 | -0.0106 | 0.010557 | 0.027137 | 0.017294 | 0.025373 | 0.01553
5477.375 | 122.7814 | -0.07782 | 122.644 | 0.13101 | -0.049678 | -0.030314 | -0.034174 | 0.013375 | 0.062691 | -0.067295 | -0.052818 | 0.060902 | -0.045424 | -0.042259 | -0.057062 | -0.031717 | -0.056376 | -0.035219 | 0.20883 | 0.028142 | 0.047506 | 0.043646 | 0.091195 | 0.14051 | 0.010525 | -0.007042 | 0.10668 | 0.000352 | 0.003517 | -0.011286 | 0.014059 | -0.0106 | 0.010557 | 0.004244 | 0.003558 | 0.011638 | 0.010952
5479.1406 | 122.8271 | -0.07782 | 122.6395 | 0.13101 | -0.0451 | -0.030314 | -0.029595 | 0.013375 | 0.058113 | -0.058139 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.070797 | -0.036295 | -0.056376 | -0.039797 | 0.20883 | 0.03272 | 0.047506 | 0.048225 | 0.091195 | 0.13593 | 0.019681 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.025021 | 0.009481 | -0.0106 | 0.005979 | 0.022558 | 0.008137 | 0.029951 | 0.01553
5480.8594 | 122.7036 | -0.10529 | 122.6807 | 0.12643 | -0.049678 | -0.034893 | -0.034174 | 0.013375 | 0.058113 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.042259 | -0.066219 | -0.040873 | -0.04722 | -0.030641 | 0.23172 | 0.055608 | 0.070393 | 0.071112 | 0.11866 | 0.1634 | 0.042569 | -0.002463 | 0.11126 | 0.00493 | 0.003517 | -0.020443 | 0.004903 | -0.001444 | 0.015135 | 0.01798 | -0.001019 | 0.025373 | 0.006374
5482.5625 | 122.8226 | -0.050354 | 122.6624 | 0.12643 | -0.054257 | -0.034893 | -0.034174 | 0.017953 | 0.062691 | -0.062717 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.061641 | -0.031717 | -0.04722 | -0.035219 | 0.17678 | -0.003903 | 0.015461 | 0.01618 | 0.068307 | 0.11305 | -0.012363 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.015865 | 0.014059 | -0.001444 | 0.010557 | 0.013402 | -0.001019 | 0.020795 | 0.006374
5484.2656 | 122.8546 | -0.07782 | 122.6486 | 0.13559 | -0.058836 | -0.025735 | -0.025017 | 0.017953 | 0.062691 | -0.067295 | -0.048239 | 0.065481 | -0.040846 | -0.042259 | -0.070797 | -0.040873 | -0.042641 | -0.035219 | 0.21341 | 0.018984 | 0.052085 | 0.052803 | 0.095773 | 0.14051 | 0.010525 | -0.002463 | 0.11126 | 0.00493 | 0.003517 | -0.025021 | 0.004903 | 0.003135 | 0.010557 | 0.022558 | -0.005598 | 0.029951 | 0.001795
5485.9688 | 122.7539 | -0.10986 | 122.699 | 0.13101 | -0.054257 | -0.025735 | -0.025017 | 0.017953 | 0.062691 | -0.067295 | -0.043661 | 0.065481 | -0.045424 | -0.046838 | -0.066219 | -0.036295 | -0.051798 | -0.030641 | 0.24087 | 0.055606 | 0.084128 | 0.084846 | 0.12782 | 0.17255 | 0.042568 | 0.002115 | 0.11126 | 0.000352 | -0.001062 | -0.020443 | 0.009481 | -0.006022 | 0.015135 | 0.022558 | 0.008137 | 0.020795 | 0.006374
5487.6875 | 122.7356 | -0.082397 | 122.6761 | 0.13101 | -0.054257 | -0.025735 | -0.029595 | 0.017953 | 0.062691 | -0.067295 | -0.052818 | 0.060902 | -0.05458 | -0.042259 | -0.066219 | -0.040873 | -0.04722 | -0.030641 | 0.21341 | 0.02814 | 0.056662 | 0.052802 | 0.10035 | 0.14509 | 0.015102 | -0.007042 | 0.10668 | -0.008804 | 0.003517 | -0.020443 | 0.004903 | -0.001444 | 0.015135 | 0.013401 | -0.005598 | 0.011639 | -0.00736
5489.4062 | 122.8363 | -0.068665 | 122.6303 | 0.13559 | -0.049678 | -0.030314 | -0.029595 | 0.017953 | 0.062691 | -0.062717 | -0.043661 | 0.07006 | -0.045424 | -0.03768 | -0.066219 | -0.036295 | -0.051798 | -0.035219 | 0.20425 | 0.018987 | 0.038351 | 0.03907 | 0.086618 | 0.13136 | 0.005948 | 0.002115 | 0.11584 | 0.000352 | 0.008096 | -0.020443 | 0.009481 | -0.006022 | 0.010557 | 0.022558 | 0.008137 | 0.020795 | 0.006374
5491.125 | 122.7448 | -0.10529 | 122.6807 | 0.14017 | -0.054257 | -0.025735 | -0.025017 | 0.017953 | 0.067269 | -0.062717 | -0.052818 | 0.065481 | -0.045424 | -0.03768 | -0.061641 | -0.027139 | -0.051798 | -0.035219 | 0.24545 | 0.051029 | 0.079551 | 0.080269 | 0.12324 | 0.17256 | 0.042569 | -0.007042 | 0.11126 | 0.000352 | 0.008096 | -0.015865 | 0.018637 | -0.006022 | 0.010557 | 0.008823 | -0.00102 | 0.016217 | 0.006374
5492.8281 | 122.8043 | -0.07782 | 122.6578 | 0.14017 | -0.054257 | -0.030314 | -0.034174 | 0.017953 | 0.062691 | -0.062717 | -0.052818 | 0.060902 | -0.050002 | -0.042259 | -0.066219 | -0.036295 | -0.051798 | -0.030641 | 0.21799 | 0.023563 | 0.047506 | 0.043646 | 0.095773 | 0.14051 | 0.015103 | -0.007042 | 0.10668 | -0.004226 | 0.003517 | -0.020443 | 0.009481 | -0.006022 | 0.015135 | 0.013401 | -0.00102 | 0.016217 | 0.001796
5494.5312 | 122.8317 | -0.064087 | 122.6761 | 0.13101 | -0.054257 | -0.030314 | -0.029595 | 0.013375 | 0.058113 | -0.067295 | -0.052818 | 0.07006 | -0.040846 | -0.03768 | -0.070797 | -0.031717 | -0.038063 | -0.026063 | 0.1951 | 0.00983 | 0.033773 | 0.034492 | 0.077462 | 0.1222 | -0.003208 | -0.007042 | 0.11584 | 0.00493 | 0.008096 | -0.025021 | 0.014059 | 0.007713 | 0.019713 | 0.017979 | -0.014755 | 0.029951 | -0.002783
5496.25 | 122.7585 | -0.10529 | 122.6761 | 0.13101 | -0.049678 | -0.025735 | -0.029595 | 0.008797 | 0.067269 | -0.071874 | -0.043661 | 0.065481 | -0.045424 | -0.03768 | -0.061641 | -0.036295 | -0.04722 | -0.030641 | 0.23629 | 0.055608 | 0.079551 | 0.075691 | 0.11408 | 0.17256 | 0.033412 | 0.002115 | 0.11126 | 0.000352 | 0.008096 | -0.015865 | 0.009481 | -0.001444 | 0.015135 | 0.01798 | 0.003559 | 0.016217 | 0.001796
5497.9688 | 122.7768 | -0.073242 | 122.6532 | 0.13559 | -0.054257 | -0.030314 | -0.029595 | 0.013375 | 0.058113 | -0.062717 | -0.048239 | 0.065481 | -0.036267 | -0.042259 | -0.066219 | -0.040873 | -0.051798 | -0.030641 | 0.20883 | 0.018985 | 0.042928 | 0.043647 | 0.086617 | 0.13135 | 0.010525 | -0.002463 | 0.11126 | 0.009509 | 0.003517 | -0.020443 | 0.004903 | -0.006022 | 0.015135 | 0.01798 | 0.003559 | 0.029952 | 0.015531
5499.6719 | 122.7585 | -0.10529 | 122.6807 | 0.13559 | -0.054257 | -0.025735 | -0.020438 | 0.013375 | 0.067269 | -0.062717 | -0.052818 | 0.074638 | -0.045424 | -0.042259 | -0.070797 | -0.036295 | -0.042641 | -0.026063 | 0.24087 | 0.051029 | 0.079551 | 0.084848 | 0.11866 | 0.17256 | 0.042569 | -0.007042 | 0.12041 | 0.000352 | 0.003517 | -0.025021 | 0.009481 | 0.003135 | 0.019713 | 0.017979 | -0.010177 | 0.025373 | -0.002783
5501.3906 | 122.8409 | -0.050354 | 122.6532 | 0.13101 | -0.058836 | -0.030314 | -0.029595 | 0.017953 | 0.067269 | -0.062717 | -0.048239 | 0.060902 | -0.036267 | -0.042259 | -0.066219 | -0.040873 | -0.04722 | -0.039797 | 0.18136 | -0.008482 | 0.02004 | 0.020759 | 0.068307 | 0.11762 | -0.012363 | -0.002463 | 0.10668 | 0.009509 | 0.003517 | -0.020443 | 0.004903 | -0.001444 | 0.005979 | 0.01798 | -0.001019 | 0.029952 | 0.010953
5503.1094 | 122.7585 | -0.09613 | 122.6669 | 0.13101 | -0.049678 | -0.030314 | -0.025017 | 0.017953 | 0.067269 | -0.067295 | -0.048239 | 0.07006 | -0.045424 | -0.03768 | -0.066219 | -0.031717 | -0.04722 | -0.035219 | 0.22714 | 0.046452 | 0.065816 | 0.071113 | 0.11408 | 0.1634 | 0.028835 | -0.002463 | 0.11584 | 0.000352 | 0.008096 | -0.020443 | 0.014059 | -0.001444 | 0.010557 | 0.01798 | -0.001019 | 0.020795 | 0.001796
5504.8438 | 122.7951 | -0.07782 | 122.6624 | 0.13101 | -0.054257 | -0.025735 | -0.029595 | 0.013375 | 0.067269 | -0.067295 | -0.048239 | 0.060902 | -0.040846 | -0.046838 | -0.070797 | -0.036295 | -0.04722 | -0.035219 | 0.20883 | 0.023563 | 0.052085 | 0.048225 | 0.091195 | 0.14509 | 0.010525 | -0.002463 | 0.10668 | 0.00493 | -0.001062 | -0.025021 | 0.009481 | -0.001444 | 0.010557 | 0.022558 | -0.001019 | 0.029951 | 0.006374
5506.5625 | 122.7127 | -0.13275 | 122.6669 | 0.13101 | -0.054257 | -0.025735 | -0.025017 | 0.017953 | 0.062691 | -0.071874 | -0.043661 | 0.07006 | -0.040846 | -0.03768 | -0.066219 | -0.027139 | -0.04722 | -0.035219 | 0.26376 | 0.078494 | 0.10702 | 0.10773 | 0.1507 | 0.19544 | 0.060877 | 0.002115 | 0.11584 | 0.00493 | 0.008096 | -0.020443 | 0.018637 | -0.001444 | 0.010557 | 0.022558 | 0.003559 | 0.025373 | 0.006374
5508.2812 | 122.7402 | -0.086975 | 122.6898 | 0.12185 | -0.054257 | -0.030314 | -0.034174 | 0.004219 | 0.067269 | -0.058139 | -0.048239 | 0.065481 | -0.040846 | -0.033101 | -0.070797 | -0.036295 | -0.051798 | -0.030641 | 0.20883 | 0.032718 | 0.056661 | 0.052801 | 0.091194 | 0.15424 | 0.028836 | -0.002463 | 0.11126 | 0.00493 | 0.012675 | -0.025021 | 0.009481 | -0.006022 | 0.015135 | 0.022558 | 0.003559 | 0.029951 | 0.010952
5510 | 122.7448 | -0.11902 | 122.7036 | 0.13559 | -0.0451 | -0.025735 | -0.034174 | 0.017953 | 0.062691 | -0.067295 | -0.057396 | 0.060902 | -0.040846 | -0.046838 | -0.066219 | -0.036295 | -0.04722 | -0.030641 | 0.25461 | 0.073919 | 0.093284 | 0.084845 | 0.13697 | 0.18171 | 0.051724 | -0.01162 | 0.10668 | 0.00493 | -0.001062 | -0.020443 | 0.009481 | -0.001444 | 0.015135 | 0.008823 | -0.010176 | 0.025373 | 0.006374
5511.75 | 122.8043 | -0.086975 | 122.6532 | 0.14017 | -0.049678 | -0.034893 | -0.029595 | 0.022531 | 0.062691 | -0.062717 | -0.048239 | 0.056323 | -0.036267 | -0.046838 | -0.070797 | -0.036295 | -0.04722 | -0.035219 | 0.22714 | 0.037297 | 0.052082 | 0.05738 | 0.10951 | 0.14967 | 0.024258 | -0.002463 | 0.1021 | 0.009509 | -0.001062 | -0.025021 | 0.009481 | -0.001444 | 0.010557 | 0.022558 | -0.001019 | 0.03453 | 0.010953
5513.4844 | 122.8043 | -0.09613 | 122.6944 | 0.12643 | -0.054257 | -0.030314 | -0.034174 | 0.013375 | 0.058113 | -0.071874 | -0.043661 | 0.060902 | -0.036267 | -0.033101 | -0.070797 | -0.036295 | -0.051798 | -0.030641 | 0.22256 | 0.041873 | 0.065816 | 0.061956 | 0.1095 | 0.15424 | 0.024256 | 0.002115 | 0.10668 | 0.009509 | 0.012675 | -0.025021 | 0.009481 | -0.006022 | 0.015135 | 0.027136 | 0.008137 | 0.03453 | 0.015531
5515.2031 | 122.7997 | -0.082397 | 122.7219 | 0.14017 | -0.054257 | -0.025735 | -0.029595 | 0.008797 | 0.053534 | -0.067295 | -0.057396 | 0.065481 | -0.040846 | -0.042259 | -0.061641 | -0.036295 | -0.051798 | -0.035219 | 0.22256 | 0.02814 | 0.056662 | 0.052802 | 0.091194 | 0.13593 | 0.015102 | -0.01162 | 0.11126 | 0.00493 | 0.003517 | -0.015865 | 0.009481 | -0.006022 | 0.010557 | 0.004245 | -0.005598 | 0.020795 | 0.010952
5516.9375 | 122.8592 | -0.064087 | 122.6715 | 0.13559 | -0.058836 | -0.034893 | -0.025017 | 0.013375 | 0.062691 | -0.067295 | -0.052818 | 0.056323 | -0.050002 | -0.046838 | -0.066219 | -0.031717 | -0.056376 | -0.030641 | 0.19967 | 0.005251 | 0.029194 | 0.03907 | 0.077462 | 0.12678 | -0.003208 | -0.007042 | 0.1021 | -0.004226 | -0.001062 | -0.020443 | 0.014059 | -0.0106 | 0.015135 | 0.013401 | 0.003558 | 0.016217 | 0.006374
5518.6406 | 122.7036 | -0.11444 | 122.699 | 0.13101 | -0.054257 | -0.030314 | -0.034174 | 0.017953 | 0.062691 | -0.071874 | -0.048239 | 0.07006 | -0.045424 | -0.042259 | -0.066219 | -0.031717 | -0.04722 | -0.039797 | 0.24545 | 0.060184 | 0.084127 | 0.080267 | 0.13239 | 0.17713 | 0.042567 | -0.002463 | 0.11584 | 0.000352 | 0.003517 | -0.020443 | 0.014059 | -0.001444 | 0.005979 | 0.01798 | -0.001019 | 0.020795 | 0.001796
5520.3594 | 122.8088 | -0.073242 | 122.6807 | 0.13559 | -0.058836 | -0.034893 | -0.029595 | 0.017953 | 0.058113 | -0.067295 | -0.043661 | 0.065481 | -0.040846 | -0.042259 | -0.070797 | -0.040873 | -0.051798 | -0.030641 | 0.20883 | 0.014406 | 0.038349 | 0.043647 | 0.091195 | 0.13135 | 0.005947 | 0.002115 | 0.11126 | 0.00493 | 0.003517 | -0.025021 | 0.004903 | -0.006022 | 0.015135 | 0.027136 | 0.008137 | 0.029951 | 0.010952
5522.0781 | 122.7127 | -0.10529 | 122.7036 | 0.13101 | -0.054257 | -0.025735 | -0.034174 | 0.008797 | 0.062691 | -0.067295 | -0.048239 | 0.065481 | -0.040846 | -0.051417 | -0.070797 | -0.040873 | -0.04722 | -0.030641 | 0.23629 | 0.051029 | 0.079551 | 0.071112 | 0.11408 | 0.16798 | 0.037991 | -0.002463 | 0.11126 | 0.00493 | -0.005641 | -0.025021 | 0.004903 | -0.001444 | 0.015135 | 0.022558 | -0.001019 | 0.029951 | 0.006374
5523.8438 | 122.7264 | -0.10071 | 122.6852 | 0.13559 | -0.063415 | -0.030314 | -0.029595 | 0.017953 | 0.067269 | -0.062717 | -0.048239 | 0.060902 | -0.050002 | -0.046838 | -0.070797 | -0.040873 | -0.051798 | -0.035219 | 0.23629 | 0.037293 | 0.070394 | 0.071113 | 0.11866 | 0.16798 | 0.037991 | -0.002463 | 0.10668 | -0.004226 | -0.001062 | -0.025021 | 0.004903 | -0.006022 | 0.010557 | 0.022558 | 0.003559 | 0.020795 | 0.001796
5525.5469 | 122.8546 | -0.064087 | 122.644 | 0.13101 | -0.058836 | -0.025735 | -0.029595 | 0.008797 | 0.067269 | -0.071874 | -0.048239 | 0.065481 | -0.050002 | -0.042259 | -0.075375 | -0.036295 | -0.042641 | -0.030641 | 0.1951 | 0.005251 | 0.038352 | 0.034492 | 0.072884 | 0.13136 | -0.007787 | -0.002463 | 0.11126 | -0.004226 | 0.003517 | -0.029599 | 0.009481 | 0.003135 | 0.015135 | 0.027136 | -0.005598 | 0.025373 | -0.007361
5527.2656 | 122.818 | -0.068665 | 122.6852 | 0.14017 | -0.058836 | -0.034893 | -0.029595 | 0.017953 | 0.062691 | -0.067295 | -0.048239 | 0.07006 | -0.040846 | -0.042259 | -0.066219 | -0.040873 | -0.04722 | -0.026063 | 0.20883 | 0.009829 | 0.033772 | 0.03907 | 0.086618 | 0.13136 | 0.00137 | -0.002463 | 0.11584 | 0.00493 | 0.003517 | -0.020443 | 0.004903 | -0.001444 | 0.019713 | 0.01798 | -0.001019 | 0.025373 | 0.006374
5528.9844 | 122.8455 | -0.064087 | 122.6669 | 0.13101 | -0.049678 | -0.034893 | -0.034174 | 0.013375 | 0.062691 | -0.071874 | -0.043661 | 0.060902 | -0.045424 | -0.033101 | -0.066219 | -0.031717 | -0.042641 | -0.030641 | 0.1951 | 0.014409 | 0.029194 | 0.029913 | 0.077462 | 0.12678 | -0.007787 | 0.002115 | 0.10668 | 0.000352 | 0.012675 | -0.020443 | 0.014059 | 0.003135 | 0.015135 | 0.022558 | -0.00102 | 0.020795 | -0.002783
5530.6875 | 122.731 | -0.09613 | 122.6898 | 0.14017 | -0.049678 | -0.021157 | -0.029595 | 0.013375 | 0.058113 | -0.062717 | -0.043661 | 0.060902 | -0.045424 | -0.03768 | -0.066219 | -0.036295 | -0.04722 | -0.016906 | 0.2363 | 0.046452 | 0.074973 | 0.066535 | 0.1095 | 0.15424 | 0.033413 | 0.002115 | 0.10668 | 0.000352 | 0.008096 | -0.020443 | 0.009481 | -0.001444 | 0.02887 | 0.022558 | 0.003559 | 0.020795 | 0.001796
5532.4219 | 122.7859 | -0.07782 | 122.699 | 0.13101 | -0.049678 | -0.030314 | -0.034174 | 0.013375 | 0.067269 | -0.058139 | -0.052818 | 0.07006 | -0.036267 | -0.03768 | -0.070797 | -0.036295 | -0.04722 | -0.030641 | 0.20883 | 0.028142 | 0.047506 | 0.043646 | 0.091195 | 0.14509 | 0.019681 | -0.007042 | 0.11584 | 0.009509 | 0.008096 | -0.025021 | 0.009481 | -0.001444 | 0.015135 | 0.017979 | -0.005598 | 0.03453 | 0.010953
5534.125 | 122.7081 | -0.10529 | 122.6898 | 0.12643 | -0.054257 | -0.030314 | -0.025017 | 0.013375 | 0.062691 | -0.067295 | -0.048239 | 0.07006 | -0.040846 | -0.042259 | -0.066219 | -0.040873 | -0.051798 | -0.039797 | 0.23172 | 0.051029 | 0.074972 | 0.080269 | 0.11866 | 0.16798 | 0.037991 | -0.002463 | 0.11584 | 0.00493 | 0.003517 | -0.020443 | 0.004903 | -0.006022 | 0.005979 | 0.01798 | 0.003559 | 0.025373 | 0.010952
5535.8281 | 122.8271 | -0.07782 | 122.6761 | 0.13559 | -0.049678 | -0.030314 | -0.034174 | 0.008797 | 0.062691 | -0.053561 | -0.039082 | 0.074638 | -0.036267 | -0.042259 | -0.066219 | -0.031717 | -0.051798 | -0.026063 | 0.21341 | 0.028142 | 0.047506 | 0.043646 | 0.086617 | 0.14051 | 0.024259 | 0.006694 | 0.12041 | 0.009509 | 0.003517 | -0.020443 | 0.014059 | -0.006022 | 0.019713 | 0.027137 | 0.012716 | 0.029952 | 0.015531
5537.5469 | 122.7264 | -0.11902 | 122.7219 | 0.13101 | -0.054257 | -0.030314 | -0.029595 | 0.017953 | 0.062691 | -0.062717 | -0.043661 | 0.065481 | -0.045424 | -0.042259 | -0.070797 | -0.031717 | -0.04722 | -0.030641 | 0.25003 | 0.064762 | 0.088705 | 0.089424 | 0.13697 | 0.18171 | 0.056302 | 0.002115 | 0.11126 | 0.000352 | 0.003517 | -0.025021 | 0.014059 | -0.001444 | 0.015135 | 0.027136 | 0.003559 | 0.025373 | 0.001796
5539.3125 | 122.8683 | -0.07782 | 122.6395 | 0.13101 | -0.054257 | -0.030314 | -0.034174 | 0.004219 | 0.067269 | -0.062717 | -0.052818 | 0.074638 | -0.050002 | -0.042259 | -0.075375 | -0.045451 | -0.04722 | -0.030641 | 0.20883 | 0.023563 | 0.047506 | 0.043646 | 0.082039 | 0.14509 | 0.015103 | -0.007042 | 0.12041 | -0.004226 | 0.003517 | -0.029599 | 0.000325 | -0.001444 | 0.015135 | 0.022557 | -0.005598 | 0.025373 | -0.002782
5541.0156 | 122.731 | -0.10986 | 122.6898 | 0.13101 | -0.058836 | -0.034893 | -0.025017 | 0.017953 | 0.067269 | -0.062717 | -0.048239 | 0.065481 | -0.045424 | -0.042259 | -0.066219 | -0.036295 | -0.04722 | -0.026063 | 0.24087 | 0.051027 | 0.07497 | 0.084846 | 0.12782 | 0.17713 | 0.047146 | -0.002463 | 0.11126 | 0.000352 | 0.003517 | -0.020443 | 0.009481 | -0.001444 | 0.019713 | 0.01798 | -0.001019 | 0.020795 | 0.001796
5542.7344 | 122.7585 | -0.09613 | 122.6944 | 0.13101 | -0.058836 | -0.030314 | -0.034174 | 0.013375 | 0.067269 | -0.062717 | -0.052818 | 0.07006 | -0.045424 | -0.046838 | -0.070797 | -0.031717 | -0.051798 | -0.035219 | 0.22714 | 0.037294 | 0.065816 | 0.061956 | 0.1095 | 0.1634 | 0.033413 | -0.007042 | 0.11584 | 0.000352 | -0.001062 | -0.025021 | 0.014059 | -0.006022 | 0.010557 | 0.017979 | -0.00102 | 0.025373 | 0.006374
5544.4688 | 122.7448 | -0.091553 | 122.699 | 0.13101 | -0.058836 | -0.034893 | -0.034174 | 0.013375 | 0.062691 | -0.067295 | -0.043661 | 0.060902 | -0.040846 | -0.03768 | -0.066219 | -0.040873 | -0.051798 | -0.035219 | 0.22256 | 0.032717 | 0.05666 | 0.057379 | 0.10493 | 0.15424 | 0.024258 | 0.002115 | 0.10668 | 0.00493 | 0.008096 | -0.020443 | 0.004903 | -0.006022 | 0.010557 | 0.022558 | 0.008137 | 0.025373 | 0.010952
5546.1875 | 122.7448 | -0.11444 | 122.7036 | 0.13101 | -0.054257 | -0.030314 | -0.029595 | 0.017953 | 0.062691 | -0.062717 | -0.048239 | 0.07006 | -0.050002 | -0.042259 | -0.066219 | -0.036295 | -0.04722 | -0.030641 | 0.24545 | 0.060184 | 0.084127 | 0.084846 | 0.13239 | 0.17713 | 0.051724 | -0.002463 | 0.11584 | -0.004226 | 0.003517 | -0.020443 | 0.009481 | -0.001444 | 0.015135 | 0.01798 | -0.001019 | 0.016217 | -0.002782
5547.9219 | 122.7356 | -0.10986 | 122.7127 | 0.12643 | -0.054257 | -0.030314 | -0.029595 | 0.013375 | 0.062691 | -0.062717 | -0.048239 | 0.07006 | -0.040846 | -0.03768 | -0.066219 | -0.031717 | -0.042641 | -0.030641 | 0.23629 | 0.055606 | 0.079549 | 0.080268 | 0.12324 | 0.17255 | 0.047146 | -0.002463 | 0.11584 | 0.00493 | 0.008096 | -0.020443 | 0.014059 | 0.003135 | 0.015135 | 0.01798 | -0.005598 | 0.025373 | 0.001795
5549.6562 | 122.8455 | -0.059509 | 122.6669 | 0.13101 | -0.054257 | -0.034893 | -0.029595 | 0.008797 | 0.062691 | -0.062717 | -0.043661 | 0.056323 | -0.045424 | -0.033101 | -0.061641 | -0.031717 | -0.04722 | -0.030641 | 0.19052 | 0.005252 | 0.024616 | 0.029914 | 0.068306 | 0.1222 | -0.003208 | 0.002115 | 0.1021 | 0.000352 | 0.012675 | -0.015865 | 0.014059 | -0.001444 | 0.015135 | 0.01798 | 0.003559 | 0.016217 | 0.001796
5551.3906 | 122.7859 | -0.09613 | 122.7081 | 0.13101 | -0.058836 | -0.025735 | -0.029595 | 0.013375 | 0.062691 | -0.062717 | -0.048239 | 0.060902 | -0.040846 | -0.046838 | -0.070797 | -0.022561 | -0.04722 | -0.030641 | 0.22714 | 0.037294 | 0.070395 | 0.066535 | 0.1095 | 0.15882 | 0.033413 | -0.002463 | 0.10668 | 0.00493 | -0.001062 | -0.025021 | 0.023215 | -0.001444 | 0.015135 | 0.022558 | -0.001019 | 0.029951 | 0.006374
5553.0938 | 122.8638 | -0.054932 | 122.6761 | 0.13101 | -0.054257 | -0.021157 | -0.034174 | 0.008797 | 0.062691 | -0.062717 | -0.052818 | 0.060902 | -0.045424 | -0.03768 | -0.070797 | -0.031717 | -0.04722 | -0.030641 | 0.18594 | 0.000675 | 0.033775 | 0.020758 | 0.063729 | 0.11762 | -0.007785 | -0.007042 | 0.10668 | 0.000352 | 0.008096 | -0.025021 | 0.014059 | -0.001444 | 0.015135 | 0.017979 | -0.005598 | 0.025373 | 0.001796
5554.8125 | 122.7356 | -0.13275 | 122.6944 | 0.12643 | -0.054257 | -0.034893 | -0.025017 | 0.013375 | 0.062691 | -0.058139 | -0.043661 | 0.060902 | -0.031689 | -0.03768 | -0.066219 | -0.036295 | -0.04722 | -0.030641 | 0.25918 | 0.078494 | 0.097858 | 0.10773 | 0.14613 | 0.19544 | 0.074612 | 0.002115 | 0.10668 | 0.014087 | 0.008096 | -0.020443 | 0.009481 | -0.001444 | 0.015135 | 0.022558 | 0.003559 | 0.03453 | 0.015531
5556.5469 | 122.8729 | -0.064087 | 122.6624 | 0.13559 | -0.054257 | -0.030314 | -0.029595 | 0.017953 | 0.062691 | -0.071874 | -0.052818 | 0.065481 | -0.040846 | -0.03768 | -0.061641 | -0.036295 | -0.042641 | -0.030641 | 0.19967 | 0.00983 | 0.033773 | 0.034492 | 0.08204 | 0.12678 | -0.007787 | -0.007042 | 0.11126 | 0.00493 | 0.008096 | -0.015865 | 0.009481 | 0.003135 | 0.015135 | 0.008823 | -0.010177 | 0.020795 | 0.001795
5558.3125 | 122.7859 | -0.091553 | 122.699 | 0.13101 | -0.049678 | -0.030314 | -0.029595 | 0.013375 | 0.067269 | -0.071874 | -0.048239 | 0.060902 | -0.036267 | -0.046838 | -0.066219 | -0.036295 | -0.04722 | -0.030641 | 0.22256 | 0.041875 | 0.061239 | 0.061958 | 0.10493 | 0.15882 | 0.019679 | -0.002463 | 0.10668 | 0.009509 | -0.001062 | -0.020443 | 0.009481 | -0.001444 | 0.015135 | 0.01798 | -0.001019 | 0.029952 | 0.010953
5560.0312 | 122.7493 | -0.10529 | 122.6944 | 0.13101 | -0.049678 | -0.025735 | -0.029595 | 0.013375 | 0.058113 | -0.067295 | -0.048239 | 0.07006 | -0.045424 | -0.03768 | -0.070797 | -0.036295 | -0.042641 | -0.030641 | 0.23629 | 0.055608 | 0.079551 | 0.075691 | 0.11866 | 0.1634 | 0.037991 | -0.002463 | 0.11584 | 0.000352 | 0.008096 | -0.025021 | 0.009481 | 0.003135 | 0.015135 | 0.022558 | -0.005598 | 0.025373 | -0.002783
5561.7656 | 122.7722 | -0.10071 | 122.6898 | 0.13559 | -0.054257 | -0.030314 | -0.034174 | 0.013375 | 0.062691 | -0.062717 | -0.052818 | 0.07006 | -0.05458 | -0.046838 | -0.066219 | -0.036295 | -0.051798 | -0.030641 | 0.23629 | 0.046451 | 0.070394 | 0.066534 | 0.11408 | 0.1634 | 0.037991 | -0.007042 | 0.11584 | -0.008804 | -0.001062 | -0.020443 | 0.009481 | -0.006022 | 0.015135 | 0.013401 | -0.00102 | 0.011639 | -0.002782
5563.4844 | 122.818 | -0.07782 | 122.6715 | 0.13559 | -0.054257 | -0.025735 | -0.034174 | 0.013375 | 0.062691 | -0.062717 | -0.048239 | 0.060902 | -0.045424 | -0.03768 | -0.070797 | -0.031717 | -0.056376 | -0.035219 | 0.21341 | 0.023563 | 0.052085 | 0.043646 | 0.091195 | 0.14051 | 0.015103 | -0.002463 | 0.10668 | 0.000352 | 0.008096 | -0.025021 | 0.014059 | -0.0106 | 0.010557 | 0.022558 | 0.008137 | 0.025373 | 0.010952
5565.2031 | 122.8226 | -0.064087 | 122.6852 | 0.14017 | -0.054257 | -0.034893 | -0.034174 | 0.004219 | 0.062691 | -0.071874 | -0.048239 | 0.060902 | -0.040846 | -0.03768 | -0.070797 | -0.040873 | -0.042641 | -0.035219 | 0.20425 | 0.00983 | 0.029194 | 0.029913 | 0.068306 | 0.12678 | -0.007787 | -0.002463 | 0.10668 | 0.00493 | 0.008096 | -0.025021 | 0.004903 | 0.003135 | 0.010557 | 0.022558 | -0.005598 | 0.029951 | 0.001795
5566.9375 | 122.7631 | -0.10986 | 122.7081 | 0.13101 | -0.063415 | -0.030314 | -0.038752 | 0.008797 | 0.062691 | -0.062717 | -0.043661 | 0.07006 | -0.050002 | -0.03768 | -0.070797 | -0.036295 | -0.04722 | -0.030641 | 0.24087 | 0.046448 | 0.079549 | 0.071111 | 0.11866 | 0.17255 | 0.047146 | 0.002115 | 0.11584 | -0.004226 | 0.008096 | -0.025021 | 0.009481 | -0.001444 | 0.015135 | 0.027136 | 0.003559 | 0.020795 | -0.002782
5568.6562 | 122.8317 | -0.059509 | 122.7127 | 0.13101 | -0.058836 | -0.030314 | -0.029595 | 0.013375 | 0.062691 | -0.062717 | -0.043661 | 0.060902 | -0.050002 | -0.03768 | -0.070797 | -0.031717 | -0.051798 | -0.026063 | 0.19052 | 0.000673 | 0.029195 | 0.029914 | 0.072884 | 0.1222 | -0.003208 | 0.002115 | 0.10668 | -0.004226 | 0.008096 | -0.025021 | 0.014059 | -0.006022 | 0.019713 | 0.027136 | 0.008137 | 0.020795 | 0.001796
5570.375 | 122.8455 | -0.068665 | 122.6898 | 0.13101 | -0.054257 | -0.034893 | -0.025017 | 0.017953 | 0.071848 | -0.062717 | -0.048239 | 0.07006 | -0.040846 | -0.042259 | -0.066219 | -0.040873 | -0.04722 | -0.030641 | 0.19967 | 0.014408 | 0.033772 | 0.043648 | 0.086618 | 0.14051 | 0.005948 | -0.002463 | 0.11584 | 0.00493 | 0.003517 | -0.020443 | 0.004903 | -0.001444 | 0.015135 | 0.01798 | -0.001019 | 0.025373 | 0.006374
5572.0938 | 122.7173 | -0.09613 | 122.7448 | 0.13559 | -0.049678 | -0.030314 | -0.038752 | 0.013375 | 0.062691 | -0.062717 | -0.052818 | 0.065481 | -0.040846 | -0.042259 | -0.066219 | -0.036295 | -0.04722 | -0.026063 | 0.23172 | 0.046452 | 0.065816 | 0.057378 | 0.1095 | 0.15882 | 0.033413 | -0.007042 | 0.11126 | 0.00493 | 0.003517 | -0.020443 | 0.009481 | -0.001444 | 0.019713 | 0.013401 | -0.005598 | 0.025373 | 0.006374
5573.8281 | 122.8409 | -0.07782 | 122.7127 | 0.13559 | -0.054257 | -0.034893 | -0.034174 | 0.013375 | 0.058113 | -0.067295 | -0.048239 | 0.060902 | -0.050002 | -0.03768 | -0.066219 | -0.036295 | -0.051798 | -0.026063 | 0.21341 | 0.023563 | 0.042927 | 0.043646 | 0.091195 | 0.13593 | 0.010525 | -0.002463 | 0.10668 | -0.004226 | 0.008096 | -0.020443 | 0.009481 | -0.006022 | 0.019713 | 0.01798 | 0.003559 | 0.016217 | 0.001796
5575.5469 | 122.8088 | -0.059509 | 122.6807 | 0.13101 | -0.054257 | -0.030314 | -0.029595 | 0.013375 | 0.067269 | -0.062717 | -0.043661 | 0.065481 | -0.036267 | -0.03768 | -0.066219 | -0.027139 | -0.04722 | -0.030641 | 0.19052 | 0.005252 | 0.029195 | 0.029914 | 0.072884 | 0.12678 | -0.003208 | 0.002115 | 0.11126 | 0.009509 | 0.008096 | -0.020443 | 0.018637 | -0.001444 | 0.015135 | 0.022558 | 0.003559 | 0.029952 | 0.010953
5577.3125 | 122.7356 | -0.10529 | 122.7219 | 0.13559 | -0.054257 | -0.025735 | -0.029595 | 0.013375 | 0.053534 | -0.067295 | -0.052818 | 0.07006 | -0.045424 | -0.042259 | -0.066219 | -0.040873 | -0.042641 | -0.035219 | 0.24087 | 0.051029 | 0.079551 | 0.075691 | 0.11866 | 0.15882 | 0.037991 | -0.007042 | 0.11584 | 0.000352 | 0.003517 | -0.020443 | 0.004903 | 0.003135 | 0.010557 | 0.013401 | -0.010177 | 0.020795 | -0.002783
5579.0312 | 122.7905 | -0.09613 | 122.7127 | 0.13101 | -0.0451 | -0.025735 | -0.025017 | 0.004219 | 0.062691 | -0.062717 | -0.043661 | 0.065481 | -0.045424 | -0.046838 | -0.070797 | -0.036295 | -0.042641 | -0.030641 | 0.22714 | 0.05103 | 0.070395 | 0.071113 | 0.10035 | 0.15882 | 0.033413 | 0.002115 | 0.11126 | 0.000352 | -0.001062 | -0.025021 | 0.009481 | 0.003135 | 0.015135 | 0.027136 | -0.00102 | 0.025373 | -0.002783
5580.7656 | 122.7402 | -0.12817 | 122.7036 | 0.13559 | -0.058836 | -0.025735 | -0.025017 | 0.013375 | 0.071848 | -0.062717 | -0.052818 | 0.07006 | -0.045424 | -0.042259 | -0.070797 | -0.036295 | -0.056376 | -0.035219 | 0.26376 | 0.069338 | 0.10244 | 0.10316 | 0.14155 | 0.20002 | 0.065457 | -0.007042 | 0.11584 | 0.000352 | 0.003517 | -0.025021 | 0.009481 | -0.0106 | 0.010557 | 0.017979 | 0.003558 | 0.025373 | 0.010952
5582.4844 | 122.7585 | -0.10986 | 122.7036 | 0.12643 | -0.054257 | -0.030314 | -0.025017 | 0.013375 | 0.062691 | -0.062717 | -0.048239 | 0.060902 | -0.050002 | -0.051417 | -0.061641 | -0.036295 | -0.051798 | -0.035219 | 0.23629 | 0.055606 | 0.079549 | 0.084846 | 0.12324 | 0.17255 | 0.047146 | -0.002463 | 0.10668 | -0.004226 | -0.005641 | -0.015865 | 0.009481 | -0.006022 | 0.010557 | 0.013402 | 0.003559 | 0.011639 | 0.001796
5584.2656 | 122.7585 | -0.11444 | 122.7081 | 0.13559 | -0.054257 | -0.025735 | -0.034174 | 0.017953 | 0.071848 | -0.058139 | -0.043661 | 0.079217 | -0.05458 | -0.042259 | -0.070797 | -0.040873 | -0.042641 | -0.039797 | 0.25003 | 0.060184 | 0.088706 | 0.080267 | 0.13239 | 0.18629 | 0.056302 | 0.002115 | 0.12499 | -0.008804 | 0.003517 | -0.025021 | 0.004903 | 0.003135 | 0.005979 | 0.027136 | -0.00102 | 0.016217 | -0.011939
5585.9844 | 122.8683 | -0.054932 | 122.6898 | 0.13559 | -0.058836 | -0.025735 | -0.034174 | 0.008797 | 0.058113 | -0.067295 | -0.052818 | 0.065481 | -0.040846 | -0.046838 | -0.066219 | -0.036295 | -0.042641 | -0.035219 | 0.19052 | -0.003904 | 0.029197 | 0.020758 | 0.063729 | 0.11305 | -0.012363 | -0.007042 | 0.11126 | 0.00493 | -0.001062 | -0.020443 | 0.009481 | 0.003135 | 0.010557 | 0.013401 | -0.010177 | 0.025373 | 0.001795
5587.75 | 122.7768 | -0.09613 | 122.7264 | 0.13101 | -0.049678 | -0.034893 | -0.029595 | 0.008797 | 0.062691 | -0.058139 | -0.048239 | 0.07006 | -0.045424 | -0.033101 | -0.066219 | -0.031717 | -0.04722 | -0.030641 | 0.22714 | 0.046452 | 0.061237 | 0.066535 | 0.10493 | 0.15882 | 0.037991 | -0.002463 | 0.11584 | 0.000352 | 0.012675 | -0.020443 | 0.014059 | -0.001444 | 0.015135 | 0.01798 | -0.001019 | 0.020795 | 0.001796
5589.4531 | 122.7951 | -0.10071 | 122.7127 | 0.13101 | -0.054257 | -0.025735 | -0.025017 | 0.013375 | 0.062691 | -0.062717 | -0.048239 | 0.07006 | -0.036267 | -0.042259 | -0.070797 | -0.031717 | -0.051798 | -0.030641 | 0.23172 | 0.046451 | 0.074973 | 0.075691 | 0.11408 | 0.1634 | 0.037991 | -0.002463 | 0.11584 | 0.009509 | 0.003517 | -0.025021 | 0.014059 | -0.006022 | 0.015135 | 0.022558 | 0.003559 | 0.03453 | 0.015531
5591.1719 | 122.7905 | -0.10529 | 122.6898 | 0.13559 | -0.058836 | -0.030314 | -0.025017 | 0.017953 | 0.067269 | -0.067295 | -0.052818 | 0.060902 | -0.036267 | -0.033101 | -0.066219 | -0.031717 | -0.051798 | -0.035219 | 0.24087 | 0.04645 | 0.074972 | 0.080269 | 0.12324 | 0.17256 | 0.037991 | -0.007042 | 0.10668 | 0.009509 | 0.012675 | -0.020443 | 0.014059 | -0.006022 | 0.010557 | 0.013401 | -0.00102 | 0.029952 | 0.015531
5592.8906 | 122.7814 | -0.11902 | 122.7173 | 0.13101 | -0.058836 | -0.025735 | -0.029595 | 0.013375 | 0.062691 | -0.058139 | -0.048239 | 0.060902 | -0.040846 | -0.03768 | -0.070797 | -0.031717 | -0.042641 | -0.035219 | 0.25003 | 0.060183 | 0.093284 | 0.089424 | 0.13239 | 0.18171 | 0.06088 | -0.002463 | 0.10668 | 0.00493 | 0.008096 | -0.025021 | 0.014059 | 0.003135 | 0.010557 | 0.022558 | -0.005598 | 0.029951 | 0.001795
5594.625 | 122.7081 | -0.11902 | 122.7356 | 0.13101 | -0.049678 | -0.030314 | -0.025017 | 0.008797 | 0.058113 | -0.071874 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.061641 | -0.031717 | -0.051798 | -0.026063 | 0.25003 | 0.069341 | 0.088705 | 0.094002 | 0.12782 | 0.17713 | 0.047145 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.015865 | 0.014059 | -0.006022 | 0.019713 | 0.013402 | 0.003559 | 0.020795 | 0.010952
5596.375 | 122.8134 | -0.059509 | 122.6898 | 0.12643 | -0.058836 | -0.034893 | -0.029595 | 0.022531 | 0.058113 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.061641 | -0.031717 | -0.04722 | -0.039797 | 0.18594 | 0.000673 | 0.024616 | 0.029914 | 0.08204 | 0.11762 | -0.003208 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.015865 | 0.014059 | -0.001444 | 0.005979 | 0.013402 | -0.001019 | 0.020795 | 0.006374
5598.0938 | 122.7219 | -0.11444 | 122.7173 | 0.13101 | -0.054257 | -0.030314 | -0.025017 | 0.008797 | 0.058113 | -0.067295 | -0.048239 | 0.060902 | -0.050002 | -0.046838 | -0.070797 | -0.031717 | -0.051798 | -0.035219 | 0.24545 | 0.060184 | 0.084127 | 0.089424 | 0.12324 | 0.17255 | 0.047146 | -0.002463 | 0.10668 | -0.004226 | -0.001062 | -0.025021 | 0.014059 | -0.006022 | 0.010557 | 0.022558 | 0.003559 | 0.020795 | 0.001796
5599.7969 | 122.8043 | -0.073242 | 122.699 | 0.13559 | -0.058836 | -0.039471 | -0.034174 | 0.013375 | 0.067269 | -0.062717 | -0.043661 | 0.07006 | -0.050002 | -0.042259 | -0.061641 | -0.036295 | -0.042641 | -0.030641 | 0.20883 | 0.014406 | 0.033771 | 0.039068 | 0.086617 | 0.14051 | 0.010525 | 0.002115 | 0.11584 | -0.004226 | 0.003517 | -0.015865 | 0.009481 | 0.003135 | 0.015135 | 0.01798 | -0.00102 | 0.011639 | -0.007361
5601.5469 | 122.8271 | -0.082397 | 122.7219 | 0.12643 | -0.054257 | -0.034893 | -0.029595 | 0.004219 | 0.062691 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.046838 | -0.070797 | -0.027139 | -0.04722 | -0.030641 | 0.20883 | 0.02814 | 0.047504 | 0.052802 | 0.086616 | 0.14509 | 0.01968 | -0.002463 | 0.11126 | 0.00493 | -0.001062 | -0.025021 | 0.018637 | -0.001444 | 0.015135 | 0.022558 | -0.001019 | 0.029951 | 0.006374
5603.25 | 122.8638 | -0.059509 | 122.7127 | 0.13559 | -0.049678 | -0.030314 | -0.029595 | 0.017953 | 0.067269 | -0.062717 | -0.052818 | 0.07006 | -0.050002 | -0.042259 | -0.066219 | -0.040873 | -0.042641 | -0.035219 | 0.1951 | 0.009831 | 0.029195 | 0.029914 | 0.077462 | 0.12678 | -0.003208 | -0.007042 | 0.11584 | -0.004226 | 0.003517 | -0.020443 | 0.004903 | 0.003135 | 0.010557 | 0.013401 | -0.010177 | 0.016217 | -0.007361
5604.9844 | 122.7585 | -0.10071 | 122.7264 | 0.13101 | -0.054257 | -0.025735 | -0.034174 | 0.013375 | 0.071848 | -0.067295 | -0.048239 | 0.065481 | -0.045424 | -0.042259 | -0.061641 | -0.031717 | -0.04722 | -0.026063 | 0.23172 | 0.046451 | 0.074973 | 0.066534 | 0.11408 | 0.17256 | 0.033413 | -0.002463 | 0.11126 | 0.000352 | 0.003517 | -0.015865 | 0.014059 | -0.001444 | 0.019713 | 0.013402 | -0.001019 | 0.016217 | 0.001796
5606.7188 | 122.731 | -0.10071 | 122.7448 | 0.13559 | -0.058836 | -0.04405 | -0.029595 | 0.008797 | 0.067269 | -0.067295 | -0.048239 | 0.074638 | -0.040846 | -0.042259 | -0.070797 | -0.031717 | -0.04722 | -0.026063 | 0.23629 | 0.041872 | 0.056658 | 0.071113 | 0.10951 | 0.16798 | 0.033413 | -0.002463 | 0.12041 | 0.00493 | 0.003517 | -0.025021 | 0.014059 | -0.001444 | 0.019713 | 0.022558 | -0.001019 | 0.029951 | 0.006374
5608.4531 | 122.7585 | -0.09613 | 122.7127 | 0.13559 | -0.054257 | -0.030314 | -0.025017 | 0.013375 | 0.062691 | -0.062717 | -0.052818 | 0.060902 | -0.045424 | -0.042259 | -0.066219 | -0.036295 | -0.04722 | -0.035219 | 0.23172 | 0.041873 | 0.065816 | 0.071113 | 0.1095 | 0.15882 | 0.033413 | -0.007042 | 0.10668 | 0.000352 | 0.003517 | -0.020443 | 0.009481 | -0.001444 | 0.010557 | 0.013401 | -0.005598 | 0.020795 | 0.001796
5610.1719 | 122.7768 | -0.10071 | 122.7127 | 0.14017 | -0.054257 | -0.021157 | -0.038752 | 0.013375 | 0.062691 | -0.067295 | -0.052818 | 0.065481 | -0.050002 | -0.042259 | -0.070797 | -0.036295 | -0.04722 | -0.030641 | 0.24087 | 0.046451 | 0.079551 | 0.061956 | 0.11408 | 0.1634 | 0.033413 | -0.007042 | 0.11126 | -0.004226 | 0.003517 | -0.025021 | 0.009481 | -0.001444 | 0.015135 | 0.017979 | -0.005598 | 0.020795 | -0.002782
5611.875 | 122.7722 | -0.10986 | 122.699 | 0.13101 | -0.063415 | -0.025735 | -0.025017 | 0.017953 | 0.062691 | -0.062717 | -0.048239 | 0.074638 | -0.040846 | -0.03768 | -0.066219 | -0.031717 | -0.04722 | -0.035219 | 0.24087 | 0.046448 | 0.084128 | 0.084846 | 0.12782 | 0.17255 | 0.047146 | -0.002463 | 0.12041 | 0.00493 | 0.008096 | -0.020443 | 0.014059 | -0.001444 | 0.010557 | 0.01798 | -0.001019 | 0.025373 | 0.006374
5613.5938 | 122.7402 | -0.10529 | 122.7264 | 0.12643 | -0.054257 | -0.025735 | -0.029595 | 0.017953 | 0.067269 | -0.067295 | -0.043661 | 0.065481 | -0.040846 | -0.042259 | -0.061641 | -0.036295 | -0.042641 | -0.030641 | 0.23172 | 0.051029 | 0.079551 | 0.075691 | 0.12324 | 0.17256 | 0.037991 | 0.002115 | 0.11126 | 0.00493 | 0.003517 | -0.015865 | 0.009481 | 0.003135 | 0.015135 | 0.01798 | -0.00102 | 0.020795 | 0.001795
5615.3438 | 122.85 | -0.064087 | 122.7081 | 0.13101 | -0.058836 | -0.030314 | -0.029595 | 0.008797 | 0.062691 | -0.062717 | -0.052818 | 0.074638 | -0.045424 | -0.042259 | -0.066219 | -0.031717 | -0.051798 | -0.035219 | 0.1951 | 0.005251 | 0.033773 | 0.034492 | 0.072884 | 0.12678 | 0.00137 | -0.007042 | 0.12041 | 0.000352 | 0.003517 | -0.020443 | 0.014059 | -0.006022 | 0.010557 | 0.013401 | -0.00102 | 0.020795 | 0.006374
5617.0625 | 122.7448 | -0.1236 | 122.7219 | 0.13559 | -0.054257 | -0.030314 | -0.025017 | 0.017953 | 0.062691 | -0.071874 | -0.048239 | 0.065481 | -0.045424 | -0.03768 | -0.066219 | -0.031717 | -0.04722 | -0.030641 | 0.25918 | 0.069339 | 0.093282 | 0.098579 | 0.14155 | 0.18629 | 0.051722 | -0.002463 | 0.11126 | 0.000352 | 0.008096 | -0.020443 | 0.014059 | -0.001444 | 0.015135 | 0.01798 | -0.001019 | 0.020795 | 0.001796
5618.7969 | 122.9141 | -0.068665 | 122.6898 | 0.13101 | -0.049678 | -0.030314 | -0.034174 | 0.004219 | 0.062691 | -0.062717 | -0.043661 | 0.060902 | -0.040846 | -0.03768 | -0.057062 | -0.031717 | -0.04722 | -0.035219 | 0.19967 | 0.018987 | 0.038351 | 0.034491 | 0.072884 | 0.13136 | 0.005948 | 0.002115 | 0.10668 | 0.00493 | 0.008096 | -0.011286 | 0.014059 | -0.001444 | 0.010557 | 0.013401 | 0.003559 | 0.016216 | 0.006374
5620.5156 | 122.7951 | -0.11444 | 122.7448 | 0.13559 | -0.049678 | -0.034893 | -0.029595 | 0.013375 | 0.053534 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.033101 | -0.066219 | -0.040873 | -0.051798 | -0.026063 | 0.25003 | 0.064763 | 0.079548 | 0.084846 | 0.12782 | 0.16797 | 0.051724 | -0.002463 | 0.11126 | 0.00493 | 0.012675 | -0.020443 | 0.004903 | -0.006022 | 0.019713 | 0.01798 | 0.003559 | 0.025373 | 0.010952
5622.2969 | 122.818 | -0.073242 | 122.7081 | 0.13559 | -0.058836 | -0.030314 | -0.029595 | 0.013375 | 0.062691 | -0.071874 | -0.048239 | 0.07006 | -0.040846 | -0.042259 | -0.057062 | -0.031717 | -0.04722 | -0.030641 | 0.20883 | 0.014406 | 0.042928 | 0.043647 | 0.086617 | 0.13593 | 0.001368 | -0.002463 | 0.11584 | 0.00493 | 0.003517 | -0.011286 | 0.014059 | -0.001444 | 0.015135 | 0.008823 | -0.001019 | 0.016216 | 0.006374
5624.0156 | 122.8455 | -0.068665 | 122.7402 | 0.13559 | -0.058836 | -0.034893 | -0.025017 | 0.013375 | 0.071848 | -0.062717 | -0.048239 | 0.07006 | -0.045424 | -0.042259 | -0.070797 | -0.036295 | -0.042641 | -0.030641 | 0.20425 | 0.009829 | 0.033772 | 0.043648 | 0.08204 | 0.14051 | 0.005948 | -0.002463 | 0.11584 | 0.000352 | 0.003517 | -0.025021 | 0.009481 | 0.003135 | 0.015135 | 0.022558 | -0.005598 | 0.025373 | -0.002783
5625.7344 | 122.7585 | -0.1236 | 122.731 | 0.13559 | -0.054257 | -0.039471 | -0.029595 | 0.013375 | 0.071848 | -0.062717 | -0.048239 | 0.065481 | -0.045424 | -0.046838 | -0.070797 | -0.036295 | -0.051798 | -0.030641 | 0.25918 | 0.069339 | 0.084125 | 0.094001 | 0.13697 | 0.19544 | 0.060879 | -0.002463 | 0.11126 | 0.000352 | -0.001062 | -0.025021 | 0.009481 | -0.006022 | 0.015135 | 0.022558 | 0.003559 | 0.025373 | 0.006374
5627.4531 | 122.7676 | -0.11902 | 122.7264 | 0.13101 | -0.054257 | -0.021157 | -0.038752 | 0.008797 | 0.062691 | -0.062717 | -0.043661 | 0.065481 | -0.045424 | -0.033101 | -0.066219 | -0.040873 | -0.051798 | -0.035219 | 0.25003 | 0.064762 | 0.097862 | 0.080267 | 0.12782 | 0.18171 | 0.056302 | 0.002115 | 0.11126 | 0.000352 | 0.012675 | -0.020443 | 0.004903 | -0.006022 | 0.010557 | 0.022558 | 0.008137 | 0.020795 | 0.006374
5629.1719 | 122.7859 | -0.091553 | 122.7264 | 0.13559 | -0.063415 | -0.034893 | -0.029595 | 0.017953 | 0.058113 | -0.058139 | -0.048239 | 0.065481 | -0.040846 | -0.042259 | -0.066219 | -0.036295 | -0.04722 | -0.035219 | 0.22714 | 0.028138 | 0.05666 | 0.061958 | 0.10951 | 0.14967 | 0.033414 | -0.002463 | 0.11126 | 0.00493 | 0.003517 | -0.020443 | 0.009481 | -0.001444 | 0.010557 | 0.01798 | -0.001019 | 0.025373 | 0.006374
5630.9062 | 122.7997 | -0.10529 | 122.7219 | 0.14017 | -0.049678 | -0.030314 | -0.034174 | 0.017953 | 0.062691 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.061641 | -0.031717 | -0.042641 | -0.030641 | 0.24545 | 0.055608 | 0.074972 | 0.071112 | 0.12324 | 0.16798 | 0.042569 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.015865 | 0.014059 | 0.003135 | 0.015135 | 0.013402 | -0.005598 | 0.020795 | 0.001795
5632.6406 | 122.8592 | -0.064087 | 122.6898 | 0.13101 | -0.063415 | -0.030314 | -0.034174 | 0.013375 | 0.062691 | -0.062717 | -0.052818 | 0.065481 | -0.05458 | -0.042259 | -0.066219 | -0.031717 | -0.04722 | -0.030641 | 0.1951 | 0.000672 | 0.033773 | 0.029913 | 0.077462 | 0.12678 | 0.00137 | -0.007042 | 0.11126 | -0.008804 | 0.003517 | -0.020443 | 0.014059 | -0.001444 | 0.015135 | 0.013401 | -0.005598 | 0.011639 | -0.00736
5634.3906 | 122.818 | -0.091553 | 122.6898 | 0.13559 | -0.054257 | -0.034893 | -0.025017 | 0.013375 | 0.062691 | -0.058139 | -0.052818 | 0.065481 | -0.040846 | -0.042259 | -0.061641 | -0.031717 | -0.051798 | -0.035219 | 0.22714 | 0.037296 | 0.05666 | 0.066536 | 0.10493 | 0.15424 | 0.033414 | -0.007042 | 0.11126 | 0.00493 | 0.003517 | -0.015865 | 0.014059 | -0.006022 | 0.010557 | 0.008823 | -0.00102 | 0.020795 | 0.010952
5636.0938 | 122.7859 | -0.10986 | 122.7356 | 0.14017 | -0.049678 | -0.030314 | -0.034174 | 0.017953 | 0.062691 | -0.067295 | -0.043661 | 0.07006 | -0.050002 | -0.03768 | -0.061641 | -0.040873 | -0.051798 | -0.026063 | 0.25003 | 0.060185 | 0.079549 | 0.075689 | 0.12782 | 0.17255 | 0.042568 | 0.002115 | 0.11584 | -0.004226 | 0.008096 | -0.015865 | 0.004903 | -0.006022 | 0.019713 | 0.01798 | 0.008137 | 0.011639 | 0.001796
5637.7969 | 122.8409 | -0.09613 | 122.6944 | 0.12643 | -0.054257 | -0.030314 | -0.029595 | 0.013375 | 0.058113 | -0.067295 | -0.048239 | 0.060902 | -0.045424 | -0.042259 | -0.066219 | -0.031717 | -0.04722 | -0.030641 | 0.22256 | 0.041873 | 0.065816 | 0.066535 | 0.1095 | 0.15424 | 0.028835 | -0.002463 | 0.10668 | 0.000352 | 0.003517 | -0.020443 | 0.014059 | -0.001444 | 0.015135 | 0.01798 | -0.001019 | 0.020795 | 0.001796
5639.5156 | 122.8867 | -0.07782 | 122.6807 | 0.13101 | -0.054257 | -0.025735 | -0.025017 | 0.017953 | 0.058113 | -0.062717 | -0.043661 | 0.065481 | -0.045424 | -0.028522 | -0.070797 | -0.031717 | -0.04722 | -0.030641 | 0.20883 | 0.023563 | 0.052085 | 0.052803 | 0.095773 | 0.13593 | 0.015103 | 0.002115 | 0.11126 | 0.000352 | 0.017254 | -0.025021 | 0.014059 | -0.001444 | 0.015135 | 0.027136 | 0.003559 | 0.025373 | 0.001796
5641.2812 | 122.7493 | -0.10986 | 122.731 | 0.13101 | -0.058836 | -0.030314 | -0.029595 | 0.008797 | 0.062691 | -0.067295 | -0.043661 | 0.07006 | -0.05458 | -0.042259 | -0.061641 | -0.031717 | -0.04722 | -0.030641 | 0.24087 | 0.051027 | 0.079549 | 0.080268 | 0.11866 | 0.17255 | 0.042568 | 0.002115 | 0.11584 | -0.008804 | 0.003517 | -0.015865 | 0.014059 | -0.001444 | 0.015135 | 0.01798 | 0.003559 | 0.007061 | -0.00736
5642.9844 | 122.8409 | -0.054932 | 122.7219 | 0.13101 | -0.049678 | -0.030314 | -0.034174 | 0.008797 | 0.053534 | -0.058139 | -0.043661 | 0.060902 | -0.036267 | -0.03768 | -0.066219 | -0.031717 | -0.051798 | -0.035219 | 0.18594 | 0.005254 | 0.024618 | 0.020758 | 0.063729 | 0.10847 | -0.003207 | 0.002115 | 0.10668 | 0.009509 | 0.008096 | -0.020443 | 0.014059 | -0.006022 | 0.010557 | 0.022558 | 0.008137 | 0.029952 | 0.015531
5644.7031 | 122.8683 | -0.068665 | 122.7173 | 0.13101 | -0.054257 | -0.025735 | -0.029595 | 0.008797 | 0.067269 | -0.067295 | -0.048239 | 0.060902 | -0.045424 | -0.042259 | -0.066219 | -0.036295 | -0.04722 | -0.039797 | 0.19967 | 0.014408 | 0.04293 | 0.03907 | 0.077462 | 0.13593 | 0.00137 | -0.002463 | 0.10668 | 0.000352 | 0.003517 | -0.020443 | 0.009481 | -0.001444 | 0.005979 | 0.01798 | -0.001019 | 0.020795 | 0.001796
5646.4219 | 122.7997 | -0.10529 | 122.7219 | 0.13101 | -0.058836 | -0.025735 | -0.029595 | 0.022531 | 0.062691 | -0.062717 | -0.057396 | 0.065481 | -0.040846 | -0.03768 | -0.066219 | -0.036295 | -0.04722 | -0.035219 | 0.23629 | 0.04645 | 0.079551 | 0.075691 | 0.12782 | 0.16798 | 0.042569 | -0.01162 | 0.11126 | 0.00493 | 0.008096 | -0.020443 | 0.009481 | -0.001444 | 0.010557 | 0.008823 | -0.010176 | 0.025373 | 0.006374
5648.1406 | 122.7402 | -0.10529 | 122.7219 | 0.13101 | -0.058836 | -0.025735 | -0.034174 | 0.013375 | 0.067269 | -0.067295 | -0.048239 | 0.074638 | -0.045424 | -0.046838 | -0.061641 | -0.040873 | -0.051798 | -0.035219 | 0.23629 | 0.04645 | 0.079551 | 0.071112 | 0.11866 | 0.17256 | 0.037991 | -0.002463 | 0.12041 | 0.000352 | -0.001062 | -0.015865 | 0.004903 | -0.006022 | 0.010557 | 0.013402 | 0.003559 | 0.016217 | 0.006374
5649.8594 | 122.8546 | -0.073242 | 122.7036 | 0.13559 | -0.054257 | -0.030314 | -0.029595 | 0.017953 | 0.058113 | -0.058139 | -0.052818 | 0.065481 | -0.040846 | -0.042259 | -0.066219 | -0.036295 | -0.051798 | -0.026063 | 0.20883 | 0.018985 | 0.042928 | 0.043647 | 0.091195 | 0.13135 | 0.015103 | -0.007042 | 0.11126 | 0.00493 | 0.003517 | -0.020443 | 0.009481 | -0.006022 | 0.019713 | 0.013401 | -0.00102 | 0.025373 | 0.010952
5651.5781 | 122.8134 | -0.09613 | 122.7173 | 0.12643 | -0.049678 | -0.030314 | -0.034174 | 0.017953 | 0.062691 | -0.062717 | -0.052818 | 0.07006 | -0.040846 | -0.03768 | -0.066219 | -0.031717 | -0.051798 | -0.030641 | 0.22256 | 0.046452 | 0.065816 | 0.061956 | 0.11408 | 0.15882 | 0.033413 | -0.007042 | 0.11584 | 0.00493 | 0.008096 | -0.020443 | 0.014059 | -0.006022 | 0.015135 | 0.013401 | -0.00102 | 0.025373 | 0.010952
5653.3594 | 122.7951 | -0.10071 | 122.7448 | 0.13101 | -0.049678 | -0.030314 | -0.029595 | 0.013375 | 0.062691 | -0.067295 | -0.052818 | 0.060902 | -0.045424 | -0.042259 | -0.066219 | -0.036295 | -0.04722 | -0.044375 | 0.23172 | 0.05103 | 0.070394 | 0.071113 | 0.11408 | 0.1634 | 0.033413 | -0.007042 | 0.10668 | 0.000352 | 0.003517 | -0.020443 | 0.009481 | -0.001444 | 0.001401 | 0.013401 | -0.005598 | 0.020795 | 0.001796
5655.0781 | 122.8455 | -0.086975 | 122.7356 | 0.12643 | -0.058836 | -0.030314 | -0.034174 | 0.008797 | 0.067269 | -0.062717 | -0.048239 | 0.060902 | -0.040846 | -0.03768 | -0.061641 | -0.031717 | -0.042641 | -0.035219 | 0.2134 | 0.028139 | 0.056661 | 0.052801 | 0.095772 | 0.15424 | 0.024258 | -0.002463 | 0.10668 | 0.00493 | 0.008096 | -0.015865 | 0.014059 | 0.003135 | 0.010557 | 0.013402 | -0.005598 | 0.020795 | 0.001795
5656.7812 | 122.7585 | -0.10986 | 122.7448 | 0.13101 | -0.058836 | -0.030314 | -0.025017 | 0.008797 | 0.062691 | -0.062717 | -0.057396 | 0.07006 | -0.040846 | -0.03768 | -0.057062 | -0.040873 | -0.051798 | -0.035219 | 0.24087 | 0.051027 | 0.079549 | 0.084846 | 0.11866 | 0.17255 | 0.047146 | -0.01162 | 0.11584 | 0.00493 | 0.008096 | -0.011286 | 0.004903 | -0.006022 | 0.010557 | -0.000334 | -0.005598 | 0.016216 | 0.010952
5658.5156 | 122.7722 | -0.1236 | 122.7402 | 0.12643 | -0.058836 | -0.025735 | -0.029595 | 0.004219 | 0.058113 | -0.067295 | -0.052818 | 0.060902 | -0.050002 | -0.046838 | -0.066219 | -0.022561 | -0.042641 | -0.026063 | 0.25002 | 0.06476 | 0.097861 | 0.094001 | 0.12781 | 0.18171 | 0.056301 | -0.007042 | 0.10668 | -0.004226 | -0.001062 | -0.020443 | 0.023215 | 0.003135 | 0.019713 | 0.013401 | -0.010177 | 0.016217 | -0.007361
5660.2812 | 122.8775 | -0.054932 | 122.699 | 0.13101 | -0.063415 | -0.030314 | -0.034174 | 0.013375 | 0.058113 | -0.067295 | -0.052818 | 0.065481 | -0.045424 | -0.033101 | -0.057062 | -0.031717 | -0.051798 | -0.039797 | 0.18594 | -0.008483 | 0.024618 | 0.020758 | 0.068307 | 0.11305 | -0.012363 | -0.007042 | 0.11126 | 0.000352 | 0.012675 | -0.011286 | 0.014059 | -0.006022 | 0.005979 | 0.004244 | -0.00102 | 0.011638 | 0.006374
5661.9844 | 122.818 | -0.10071 | 122.7219 | 0.13559 | -0.049678 | -0.034893 | -0.029595 | 0.008797 | 0.062691 | -0.062717 | -0.043661 | 0.07006 | -0.050002 | -0.042259 | -0.061641 | -0.031717 | -0.04722 | -0.030641 | 0.23629 | 0.05103 | 0.065815 | 0.071113 | 0.10951 | 0.1634 | 0.037991 | 0.002115 | 0.11584 | -0.004226 | 0.003517 | -0.015865 | 0.014059 | -0.001444 | 0.015135 | 0.01798 | 0.003559 | 0.011639 | -0.002782
5663.6875 | 122.8912 | -0.073242 | 122.7036 | 0.13559 | -0.054257 | -0.025735 | -0.034174 | 0.013375 | 0.058113 | -0.071874 | -0.048239 | 0.074638 | -0.045424 | -0.042259 | -0.070797 | -0.036295 | -0.04722 | -0.026063 | 0.20883 | 0.018985 | 0.047507 | 0.039068 | 0.086617 | 0.13135 | 0.001368 | -0.002463 | 0.12041 | 0.000352 | 0.003517 | -0.025021 | 0.009481 | -0.001444 | 0.019713 | 0.022558 | -0.001019 | 0.025373 | 0.001796
5665.4062 | 122.8226 | -0.073242 | 122.7264 | 0.13101 | -0.0451 | -0.034893 | -0.029595 | 0.013375 | 0.062691 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.061641 | -0.036295 | -0.04722 | -0.030641 | 0.20425 | 0.028142 | 0.038349 | 0.043647 | 0.086617 | 0.13593 | 0.010525 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.015865 | 0.009481 | -0.001444 | 0.015135 | 0.013402 | -0.001019 | 0.020795 | 0.006374
5667.125 | 122.7951 | -0.11444 | 122.7448 | 0.13559 | -0.049678 | -0.034893 | -0.029595 | 0.013375 | 0.067269 | -0.067295 | -0.052818 | 0.065481 | -0.040846 | -0.046838 | -0.066219 | -0.045451 | -0.060955 | -0.035219 | 0.25003 | 0.064763 | 0.079548 | 0.084846 | 0.12782 | 0.18171 | 0.047146 | -0.007042 | 0.11126 | 0.00493 | -0.001062 | -0.020443 | 0.000325 | -0.015179 | 0.010557 | 0.013401 | 0.008137 | 0.025373 | 0.020109
5668.8906 | 122.8546 | -0.07782 | 122.7173 | 0.13101 | -0.040521 | -0.030314 | -0.029595 | 0.013375 | 0.062691 | -0.067295 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.061641 | -0.031717 | -0.04722 | -0.026063 | 0.20883 | 0.037299 | 0.047506 | 0.048225 | 0.091195 | 0.14051 | 0.010525 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.015865 | 0.014059 | -0.001444 | 0.019713 | 0.013402 | -0.001019 | 0.020795 | 0.006374
5670.6094 | 122.7539 | -0.11444 | 122.7264 | 0.13559 | -0.054257 | -0.025735 | -0.038752 | 0.013375 | 0.062691 | -0.067295 | -0.052818 | 0.065481 | -0.045424 | -0.033101 | -0.066219 | -0.036295 | -0.051798 | -0.035219 | 0.25003 | 0.060184 | 0.088706 | 0.075689 | 0.12782 | 0.17713 | 0.047146 | -0.007042 | 0.11126 | 0.000352 | 0.012675 | -0.020443 | 0.009481 | -0.006022 | 0.010557 | 0.013401 | -0.00102 | 0.020795 | 0.006374
5672.375 | 122.7676 | -0.1236 | 122.7402 | 0.12643 | -0.049678 | -0.034893 | -0.034174 | 0.008797 | 0.071848 | -0.058139 | -0.048239 | 0.07006 | -0.040846 | -0.042259 | -0.066219 | -0.040873 | -0.04722 | -0.026063 | 0.25002 | 0.073918 | 0.088703 | 0.089422 | 0.13239 | 0.19544 | 0.065457 | -0.002463 | 0.11584 | 0.00493 | 0.003517 | -0.020443 | 0.004903 | -0.001444 | 0.019713 | 0.01798 | -0.001019 | 0.025373 | 0.006374
5674.0938 | 122.8592 | -0.086975 | 122.731 | 0.13559 | -0.058836 | -0.030314 | -0.038752 | 0.013375 | 0.062691 | -0.062717 | -0.043661 | 0.060902 | -0.036267 | -0.03768 | -0.066219 | -0.036295 | -0.04722 | -0.039797 | 0.22256 | 0.028139 | 0.056661 | 0.048223 | 0.10035 | 0.14967 | 0.024258 | 0.002115 | 0.10668 | 0.009509 | 0.008096 | -0.020443 | 0.009481 | -0.001444 | 0.005979 | 0.022558 | 0.003559 | 0.029952 | 0.010953
5675.8281 | 122.7631 | -0.11444 | 122.7585 | 0.13559 | -0.049678 | -0.025735 | -0.029595 | 0.017953 | 0.062691 | -0.062717 | -0.048239 | 0.056323 | -0.040846 | -0.03768 | -0.070797 | -0.031717 | -0.04722 | -0.035219 | 0.25003 | 0.064763 | 0.088706 | 0.084846 | 0.13239 | 0.17713 | 0.051724 | -0.002463 | 0.1021 | 0.00493 | 0.008096 | -0.025021 | 0.014059 | -0.001444 | 0.010557 | 0.022558 | -0.001019 | 0.029951 | 0.006374
5677.5469 | 122.8683 | -0.091553 | 122.7493 | 0.12643 | -0.054257 | -0.025735 | -0.029595 | 0.013375 | 0.058113 | -0.062717 | -0.052818 | 0.060902 | -0.045424 | -0.042259 | -0.066219 | -0.036295 | -0.04722 | -0.030641 | 0.21798 | 0.037296 | 0.065818 | 0.061958 | 0.10493 | 0.14967 | 0.028836 | -0.007042 | 0.10668 | 0.000352 | 0.003517 | -0.020443 | 0.009481 | -0.001444 | 0.015135 | 0.013401 | -0.005598 | 0.020795 | 0.001796
5679.3125 | 122.7631 | -0.10529 | 122.7539 | 0.12643 | -0.054257 | -0.025735 | -0.029595 | 0.017953 | 0.062691 | -0.071874 | -0.048239 | 0.07006 | -0.040846 | -0.042259 | -0.070797 | -0.036295 | -0.04722 | -0.030641 | 0.23172 | 0.051029 | 0.079551 | 0.075691 | 0.12324 | 0.16798 | 0.033412 | -0.002463 | 0.11584 | 0.00493 | 0.003517 | -0.025021 | 0.009481 | -0.001444 | 0.015135 | 0.022558 | -0.001019 | 0.029951 | 0.006374
5681.0312 | 122.8867 | -0.064087 | 122.7036 | 0.13101 | -0.054257 | -0.039471 | -0.034174 | 0.008797 | 0.058113 | -0.067295 | -0.043661 | 0.065481 | -0.045424 | -0.042259 | -0.061641 | -0.031717 | -0.04722 | -0.030641 | 0.1951 | 0.00983 | 0.024616 | 0.029913 | 0.072884 | 0.1222 | -0.003208 | 0.002115 | 0.11126 | 0.000352 | 0.003517 | -0.015865 | 0.014059 | -0.001444 | 0.015135 | 0.01798 | 0.003559 | 0.016217 | 0.001796
5682.7656 | 122.8638 | -0.059509 | 122.7264 | 0.13559 | -0.054257 | -0.030314 | -0.038752 | 0.013375 | 0.062691 | -0.067295 | -0.039082 | 0.060902 | -0.045424 | -0.03768 | -0.061641 | -0.036295 | -0.04722 | -0.035219 | 0.1951 | 0.005252 | 0.029195 | 0.020757 | 0.072884 | 0.1222 | -0.007786 | 0.006694 | 0.10668 | 0.000352 | 0.008096 | -0.015865 | 0.009481 | -0.001444 | 0.010557 | 0.022559 | 0.008138 | 0.016217 | 0.001796
5684.5312 | 122.8134 | -0.091553 | 122.7402 | 0.12643 | -0.049678 | -0.030314 | -0.034174 | 0.013375 | 0.058113 | -0.067295 | -0.048239 | 0.065481 | -0.050002 | -0.042259 | -0.061641 | -0.036295 | -0.04722 | -0.030641 | 0.21798 | 0.041875 | 0.061239 | 0.057379 | 0.10493 | 0.14967 | 0.024258 | -0.002463 | 0.11126 | -0.004226 | 0.003517 | -0.015865 | 0.009481 | -0.001444 | 0.015135 | 0.013402 | -0.001019 | 0.011639 | -0.002782
5686.25 | 122.8317 | -0.091553 | 122.7356 | 0.13559 | -0.054257 | -0.025735 | -0.025017 | 0.013375 | 0.067269 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.042259 | -0.066219 | -0.036295 | -0.056376 | -0.026063 | 0.22714 | 0.037296 | 0.065818 | 0.066536 | 0.10493 | 0.15882 | 0.028836 | -0.002463 | 0.11126 | 0.00493 | 0.003517 | -0.020443 | 0.009481 | -0.0106 | 0.019713 | 0.01798 | 0.008137 | 0.025373 | 0.01553
5687.9688 | 122.7631 | -0.11902 | 122.7448 | 0.13101 | -0.058836 | -0.030314 | -0.038752 | 0.013375 | 0.062691 | -0.067295 | -0.052818 | 0.065481 | -0.045424 | -0.042259 | -0.061641 | -0.031717 | -0.051798 | -0.026063 | 0.25003 | 0.060183 | 0.088705 | 0.080267 | 0.13239 | 0.18171 | 0.051724 | -0.007042 | 0.11126 | 0.000352 | 0.003517 | -0.015865 | 0.014059 | -0.006022 | 0.019713 | 0.008823 | -0.00102 | 0.016217 | 0.006374
5689.6875 | 122.7676 | -0.10071 | 122.7264 | 0.13101 | -0.049678 | -0.034893 | -0.029595 | 0.008797 | 0.062691 | -0.071874 | -0.048239 | 0.065481 | -0.045424 | -0.033101 | -0.066219 | -0.031717 | -0.051798 | -0.035219 | 0.23172 | 0.05103 | 0.065815 | 0.071113 | 0.10951 | 0.1634 | 0.028834 | -0.002463 | 0.11126 | 0.000352 | 0.012675 | -0.020443 | 0.014059 | -0.006022 | 0.010557 | 0.01798 | 0.003559 | 0.020795 | 0.006374
5691.4062 | 122.8363 | -0.07782 | 122.7081 | 0.13101 | -0.0451 | -0.030314 | -0.034174 | 0.013375 | 0.067269 | -0.067295 | -0.043661 | 0.065481 | -0.045424 | -0.03768 | -0.066219 | -0.036295 | -0.04722 | -0.030641 | 0.20883 | 0.03272 | 0.047506 | 0.043646 | 0.091195 | 0.14509 | 0.010525 | 0.002115 | 0.11126 | 0.000352 | 0.008096 | -0.020443 | 0.009481 | -0.001444 | 0.015135 | 0.022558 | 0.003559 | 0.020795 | 0.001796
5693.1562 | 122.8317 | -0.10529 | 122.7402 | 0.13559 | -0.054257 | -0.034893 | -0.029595 | 0.008797 | 0.067269 | -0.067295 | -0.043661 | 0.065481 | -0.045424 | -0.042259 | -0.061641 | -0.031717 | -0.051798 | -0.030641 | 0.24087 | 0.051029 | 0.070393 | 0.075691 | 0.11408 | 0.17256 | 0.037991 | 0.002115 | 0.11126 | 0.000352 | 0.003517 | -0.015865 | 0.014059 | -0.006022 | 0.015135 | 0.01798 | 0.008137 | 0.016217 | 0.006374
5694.8594 | 122.9004 | -0.082397 | 122.7173 | 0.13101 | -0.054257 | -0.030314 | -0.029595 | 0.008797 | 0.062691 | -0.067295 | -0.048239 | 0.065481 | -0.045424 | -0.042259 | -0.066219 | -0.031717 | -0.056376 | -0.026063 | 0.21341 | 0.02814 | 0.052083 | 0.052802 | 0.091194 | 0.14509 | 0.015102 | -0.002463 | 0.11126 | 0.000352 | 0.003517 | -0.020443 | 0.014059 | -0.0106 | 0.019713 | 0.01798 | 0.008137 | 0.020795 | 0.010952
5696.5625 | 122.8729 | -0.07782 | 122.7219 | 0.13101 | -0.054257 | -0.025735 | -0.034174 | 0.008797 | 0.058113 | -0.058139 | -0.048239 | 0.065481 | -0.040846 | -0.042259 | -0.070797 | -0.031717 | -0.042641 | -0.030641 | 0.20883 | 0.023563 | 0.052085 | 0.043646 | 0.086617 | 0.13593 | 0.019681 | -0.002463 | 0.11126 | 0.00493 | 0.003517 | -0.025021 | 0.014059 | 0.003135 | 0.015135 | 0.022558 | -0.005598 | 0.029951 | 0.001795
5698.3281 | 122.8409 | -0.082397 | 122.7219 | 0.13101 | -0.049678 | -0.034893 | -0.034174 | 0.013375 | 0.062691 | -0.058139 | -0.052818 | 0.060902 | -0.040846 | -0.033101 | -0.066219 | -0.036295 | -0.04722 | -0.039797 | 0.21341 | 0.032719 | 0.047504 | 0.048223 | 0.095772 | 0.14509 | 0.024258 | -0.007042 | 0.10668 | 0.00493 | 0.012675 | -0.020443 | 0.009481 | -0.001444 | 0.005979 | 0.013401 | -0.005598 | 0.025373 | 0.006374
5700.0312 | 122.8134 | -0.11444 | 122.7448 | 0.13101 | -0.049678 | -0.025735 | -0.029595 | 0.008797 | 0.062691 | -0.071874 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.066219 | -0.036295 | -0.042641 | -0.035219 | 0.24545 | 0.064763 | 0.088706 | 0.084846 | 0.12324 | 0.17713 | 0.042567 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.020443 | 0.009481 | 0.003135 | 0.010557 | 0.01798 | -0.005598 | 0.025373 | 0.001795
5701.75 | 122.7676 | -0.10986 | 122.7631 | 0.13101 | -0.058836 | -0.030314 | -0.029595 | 0.017953 | 0.071848 | -0.071874 | -0.043661 | 0.060902 | -0.045424 | -0.03768 | -0.070797 | -0.036295 | -0.042641 | -0.030641 | 0.24087 | 0.051027 | 0.079549 | 0.080268 | 0.12782 | 0.18171 | 0.037989 | 0.002115 | 0.10668 | 0.000352 | 0.008096 | -0.025021 | 0.009481 | 0.003135 | 0.015135 | 0.027136 | -0.00102 | 0.025373 | -0.002783
5703.4844 | 122.818 | -0.10529 | 122.7081 | 0.13101 | -0.049678 | -0.030314 | -0.025017 | 0.013375 | 0.076426 | -0.067295 | -0.048239 | 0.065481 | -0.045424 | -0.03768 | -0.066219 | -0.036295 | -0.04722 | -0.035219 | 0.23629 | 0.055608 | 0.074972 | 0.080269 | 0.11866 | 0.18171 | 0.037991 | -0.002463 | 0.11126 | 0.000352 | 0.008096 | -0.020443 | 0.009481 | -0.001444 | 0.010557 | 0.01798 | -0.001019 | 0.020795 | 0.001796
5705.25 | 122.7676 | -0.11444 | 122.7768 | 0.13559 | -0.054257 | -0.030314 | -0.025017 | 0.008797 | 0.062691 | -0.067295 | -0.048239 | 0.060902 | -0.050002 | -0.046838 | -0.066219 | -0.031717 | -0.051798 | -0.030641 | 0.25003 | 0.060184 | 0.084127 | 0.089424 | 0.12324 | 0.17713 | 0.047146 | -0.002463 | 0.10668 | -0.004226 | -0.001062 | -0.020443 | 0.014059 | -0.006022 | 0.015135 | 0.01798 | 0.003559 | 0.016217 | 0.001796
5706.9531 | 122.7585 | -0.09613 | 122.7448 | 0.13101 | -0.049678 | -0.034893 | -0.034174 | 0.013375 | 0.062691 | -0.067295 | -0.052818 | 0.07006 | -0.036267 | -0.03768 | -0.061641 | -0.031717 | -0.051798 | -0.026063 | 0.22714 | 0.046452 | 0.061237 | 0.061956 | 0.1095 | 0.15882 | 0.028835 | -0.007042 | 0.11584 | 0.009509 | 0.008096 | -0.015865 | 0.014059 | -0.006022 | 0.019713 | 0.008823 | -0.00102 | 0.025374 | 0.015531
5708.6719 | 122.7585 | -0.11444 | 122.7859 | 0.13559 | -0.054257 | -0.034893 | -0.029595 | 0.017953 | 0.062691 | -0.062717 | -0.057396 | 0.065481 | -0.05458 | -0.03768 | -0.070797 | -0.031717 | -0.042641 | -0.035219 | 0.25003 | 0.060184 | 0.079548 | 0.084846 | 0.13239 | 0.17713 | 0.051724 | -0.01162 | 0.11126 | -0.008804 | 0.008096 | -0.025021 | 0.014059 | 0.003135 | 0.010557 | 0.013401 | -0.014755 | 0.016217 | -0.011939
5710.375 | 122.7905 | -0.11902 | 122.731 | 0.13101 | -0.049678 | -0.034893 | -0.034174 | 0.013375 | 0.062691 | -0.076452 | -0.043661 | 0.065481 | -0.045424 | -0.042259 | -0.057062 | -0.040873 | -0.042641 | -0.030641 | 0.25003 | 0.069341 | 0.084126 | 0.084845 | 0.13239 | 0.18171 | 0.042567 | 0.002115 | 0.11126 | 0.000352 | 0.003517 | -0.011286 | 0.004903 | 0.003135 | 0.015135 | 0.013401 | -0.00102 | 0.011638 | -0.002783
5712.0938 | 122.8592 | -0.07782 | 122.7356 | 0.12643 | -0.049678 | -0.034893 | -0.034174 | 0.017953 | 0.058113 | -0.076452 | -0.048239 | 0.065481 | -0.045424 | -0.03768 | -0.061641 | -0.036295 | -0.051798 | -0.039797 | 0.20425 | 0.028142 | 0.042927 | 0.043646 | 0.095773 | 0.13593 | 0.001368 | -0.002463 | 0.11126 | 0.000352 | 0.008096 | -0.015865 | 0.009481 | -0.006022 | 0.005979 | 0.013402 | 0.003559 | 0.016217 | 0.006374
5713.8125 | 122.8226 | -0.086975 | 122.7585 | 0.13559 | -0.049678 | -0.021157 | -0.025017 | 0.013375 | 0.062691 | -0.067295 | -0.043661 | 0.065481 | -0.045424 | -0.03768 | -0.061641 | -0.036295 | -0.042641 | -0.026063 | 0.22256 | 0.037297 | 0.065818 | 0.061958 | 0.10035 | 0.14967 | 0.01968 | 0.002115 | 0.11126 | 0.000352 | 0.008096 | -0.015865 | 0.009481 | 0.003135 | 0.019713 | 0.01798 | -0.00102 | 0.016217 | -0.002783
5715.5312 | 122.8226 | -0.10529 | 122.7356 | 0.13101 | -0.054257 | -0.025735 | -0.029595 | 0.022531 | 0.062691 | -0.062717 | -0.048239 | 0.065481 | -0.045424 | -0.03768 | -0.066219 | -0.031717 | -0.04722 | -0.030641 | 0.23629 | 0.051029 | 0.079551 | 0.075691 | 0.12782 | 0.16798 | 0.042569 | -0.002463 | 0.11126 | 0.000352 | 0.008096 | -0.020443 | 0.014059 | -0.001444 | 0.015135 | 0.01798 | -0.001019 | 0.020795 | 0.001796
5717.2969 | 122.8409 | -0.082397 | 122.7356 | 0.13559 | -0.049678 | -0.039471 | -0.025017 | 0.013375 | 0.067269 | -0.067295 | -0.052818 | 0.060902 | -0.05458 | -0.042259 | -0.061641 | -0.036295 | -0.056376 | -0.026063 | 0.21798 | 0.032719 | 0.042926 | 0.05738 | 0.095772 | 0.14967 | 0.015102 | -0.007042 | 0.10668 | -0.008804 | 0.003517 | -0.015865 | 0.009481 | -0.0106 | 0.019713 | 0.008823 | 0.003558 | 0.007061 | 0.001796
5719.0156 | 122.9141 | -0.07782 | 122.7219 | 0.13559 | -0.049678 | -0.034893 | -0.029595 | 0.013375 | 0.058113 | -0.062717 | -0.048239 | 0.056323 | -0.045424 | -0.03768 | -0.061641 | -0.036295 | -0.04722 | -0.035219 | 0.21341 | 0.028142 | 0.042927 | 0.048225 | 0.091195 | 0.13593 | 0.015103 | -0.002463 | 0.1021 | 0.000352 | 0.008096 | -0.015865 | 0.009481 | -0.001444 | 0.010557 | 0.013402 | -0.001019 | 0.016217 | 0.001796
5720.75 | 122.7905 | -0.11902 | 122.7448 | 0.13101 | -0.049678 | -0.030314 | -0.034174 | 0.008797 | 0.062691 | -0.071874 | -0.048239 | 0.065481 | -0.045424 | -0.03768 | -0.066219 | -0.036295 | -0.04722 | -0.035219 | 0.25003 | 0.069341 | 0.088705 | 0.084845 | 0.12782 | 0.18171 | 0.047145 | -0.002463 | 0.11126 | 0.000352 | 0.008096 | -0.020443 | 0.009481 | -0.001444 | 0.010557 | 0.01798 | -0.001019 | 0.020795 | 0.001796
5722.4688 | 122.905 | -0.064087 | 122.731 | 0.13559 | -0.0451 | -0.025735 | -0.025017 | 0.004219 | 0.058113 | -0.062717 | -0.043661 | 0.060902 | -0.040846 | -0.03768 | -0.061641 | -0.040873 | -0.038063 | -0.035219 | 0.19967 | 0.018987 | 0.038352 | 0.03907 | 0.068306 | 0.1222 | 0.00137 | 0.002115 | 0.10668 | 0.00493 | 0.008096 | -0.015865 | 0.004903 | 0.007713 | 0.010557 | 0.01798 | -0.005598 | 0.020795 | -0.002783
5724.1719 | 122.7722 | -0.11444 | 122.7631 | 0.12643 | -0.0451 | -0.030314 | -0.029595 | 0.017953 | 0.067269 | -0.062717 | -0.048239 | 0.065481 | -0.045424 | -0.03768 | -0.066219 | -0.036295 | -0.042641 | -0.030641 | 0.24087 | 0.069341 | 0.084127 | 0.084846 | 0.13239 | 0.18171 | 0.051724 | -0.002463 | 0.11126 | 0.000352 | 0.008096 | -0.020443 | 0.009481 | 0.003135 | 0.015135 | 0.01798 | -0.005598 | 0.020795 | -0.002783
5725.8906 | 122.7676 | -0.09613 | 122.7448 | 0.13101 | -0.049678 | -0.025735 | -0.038752 | 0.008797 | 0.062691 | -0.062717 | -0.052818 | 0.065481 | -0.040846 | -0.042259 | -0.061641 | -0.036295 | -0.042641 | -0.030641 | 0.22714 | 0.046452 | 0.070395 | 0.057378 | 0.10493 | 0.15882 | 0.033413 | -0.007042 | 0.11126 | 0.00493 | 0.003517 | -0.015865 | 0.009481 | 0.003135 | 0.015135 | 0.008823 | -0.010177 | 0.020795 | 0.001795
5727.6094 | 122.905 | -0.073242 | 122.6944 | 0.13559 | -0.0451 | -0.030314 | -0.034174 | 0.008797 | 0.067269 | -0.067295 | -0.048239 | 0.060902 | -0.045424 | -0.03768 | -0.066219 | -0.031717 | -0.04722 | -0.026063 | 0.20883 | 0.028142 | 0.042928 | 0.039068 | 0.082039 | 0.14051 | 0.005947 | -0.002463 | 0.10668 | 0.000352 | 0.008096 | -0.020443 | 0.014059 | -0.001444 | 0.019713 | 0.01798 | -0.001019 | 0.020795 | 0.001796
5729.3281 | 122.8043 | -0.11902 | 122.7493 | 0.13559 | -0.054257 | -0.025735 | -0.029595 | 0.013375 | 0.062691 | -0.067295 | -0.048239 | 0.065481 | -0.045424 | -0.046838 | -0.070797 | -0.031717 | -0.04722 | -0.035219 | 0.25461 | 0.064762 | 0.093284 | 0.089424 | 0.13239 | 0.18171 | 0.051724 | -0.002463 | 0.11126 | 0.000352 | -0.001062 | -0.025021 | 0.014059 | -0.001444 | 0.010557 | 0.022558 | -0.001019 | 0.025373 | 0.001796
5731.0625 | 122.8775 | -0.07782 | 122.6944 | 0.12643 | -0.0451 | -0.030314 | -0.029595 | 0.008797 | 0.067269 | -0.067295 | -0.048239 | 0.056323 | -0.045424 | -0.03768 | -0.066219 | -0.036295 | -0.042641 | -0.035219 | 0.20425 | 0.03272 | 0.047506 | 0.048225 | 0.086617 | 0.14509 | 0.010525 | -0.002463 | 0.1021 | 0.000352 | 0.008096 | -0.020443 | 0.009481 | 0.003135 | 0.010557 | 0.01798 | -0.005598 | 0.020795 | -0.002783
5732.7812 | 122.8134 | -0.09613 | 122.7539 | 0.14017 | -0.0451 | -0.021157 | -0.034174 | 0.013375 | 0.062691 | -0.062717 | -0.052818 | 0.060902 | -0.036267 | -0.03768 | -0.066219 | -0.040873 | -0.042641 | -0.035219 | 0.2363 | 0.05103 | 0.074973 | 0.061956 | 0.1095 | 0.15882 | 0.033413 | -0.007042 | 0.10668 | 0.009509 | 0.008096 | -0.020443 | 0.004903 | 0.003135 | 0.010557 | 0.013401 | -0.010177 | 0.029952 | 0.006374
5734.4844 | 122.9004 | -0.068665 | 122.7356 | 0.13559 | -0.054257 | -0.030314 | -0.034174 | 0.013375 | 0.062691 | -0.067295 | -0.048239 | 0.060902 | -0.040846 | -0.051417 | -0.061641 | -0.040873 | -0.04722 | -0.030641 | 0.20425 | 0.014408 | 0.038351 | 0.034491 | 0.08204 | 0.13136 | 0.00137 | -0.002463 | 0.10668 | 0.00493 | -0.005641 | -0.015865 | 0.004903 | -0.001444 | 0.015135 | 0.013402 | -0.001019 | 0.020795 | 0.006374
5736.25 | 122.8958 | -0.050354 | 122.731 | 0.13559 | -0.049678 | -0.030314 | -0.038752 | 0.017953 | 0.058113 | -0.067295 | -0.052818 | 0.065481 | -0.045424 | -0.03768 | -0.061641 | -0.036295 | -0.056376 | -0.035219 | 0.18594 | 0.000676 | 0.02004 | 0.011602 | 0.068307 | 0.10847 | -0.016941 | -0.007042 | 0.11126 | 0.000352 | 0.008096 | -0.015865 | 0.009481 | -0.0106 | 0.010557 | 0.008823 | 0.003558 | 0.016217 | 0.010952
5737.9531 | 122.9004 | -0.068665 | 122.7631 | 0.13101 | -0.054257 | -0.034893 | -0.029595 | 0.008797 | 0.058113 | -0.071874 | -0.048239 | 0.060902 | -0.027111 | -0.03768 | -0.061641 | -0.031717 | -0.042641 | -0.035219 | 0.19967 | 0.014408 | 0.033772 | 0.03907 | 0.077462 | 0.12678 | -0.003209 | -0.002463 | 0.10668 | 0.018665 | 0.008096 | -0.015865 | 0.014059 | 0.003135 | 0.010557 | 0.013402 | -0.005598 | 0.03453 | 0.01553
5739.6719 | 122.7768 | -0.11902 | 122.7676 | 0.13559 | -0.0451 | -0.034893 | -0.025017 | 0.013375 | 0.067269 | -0.067295 | -0.052818 | 0.065481 | -0.040846 | -0.03768 | -0.066219 | -0.036295 | -0.051798 | -0.035219 | 0.25461 | 0.073919 | 0.084126 | 0.094002 | 0.13239 | 0.18629 | 0.051724 | -0.007042 | 0.11126 | 0.00493 | 0.008096 | -0.020443 | 0.009481 | -0.006022 | 0.010557 | 0.013401 | -0.00102 | 0.025373 | 0.010952
5741.3906 | 122.8546 | -0.054932 | 122.7402 | 0.12643 | -0.0451 | -0.025735 | -0.029595 | 0.017953 | 0.058113 | -0.067295 | -0.048239 | 0.065481 | -0.050002 | -0.046838 | -0.070797 | -0.027139 | -0.04722 | -0.035219 | 0.18136 | 0.009832 | 0.029197 | 0.025337 | 0.072885 | 0.11305 | -0.012363 | -0.002463 | 0.11126 | -0.004226 | -0.001062 | -0.025021 | 0.018637 | -0.001444 | 0.010557 | 0.022558 | -0.001019 | 0.020795 | -0.002782
5743.1406 | 122.905 | -0.050354 | 122.7356 | 0.12643 | -0.049678 | -0.034893 | -0.029595 | 0.004219 | 0.067269 | -0.062717 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.061641 | -0.036295 | -0.042641 | -0.030641 | 0.17678 | 0.000676 | 0.015461 | 0.020759 | 0.054573 | 0.11762 | -0.012363 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.015865 | 0.009481 | 0.003135 | 0.015135 | 0.013402 | -0.005598 | 0.020795 | 0.001795
5744.8438 | 122.7905 | -0.09613 | 122.7676 | 0.13559 | -0.040521 | -0.034893 | -0.029595 | 0.017953 | 0.058113 | -0.058139 | -0.043661 | 0.065481 | -0.036267 | -0.042259 | -0.066219 | -0.027139 | -0.051798 | -0.035219 | 0.23172 | 0.055609 | 0.061237 | 0.066535 | 0.11408 | 0.15424 | 0.037991 | 0.002115 | 0.11126 | 0.009509 | 0.003517 | -0.020443 | 0.018637 | -0.006022 | 0.010557 | 0.022558 | 0.008137 | 0.029952 | 0.015531
5746.5625 | 122.85 | -0.082397 | 122.7219 | 0.13559 | -0.0451 | -0.030314 | -0.034174 | 0.004219 | 0.058113 | -0.067295 | -0.043661 | 0.065481 | -0.036267 | -0.042259 | -0.070797 | -0.036295 | -0.04722 | -0.035219 | 0.21798 | 0.037297 | 0.052083 | 0.048223 | 0.086616 | 0.14051 | 0.015102 | 0.002115 | 0.11126 | 0.009509 | 0.003517 | -0.025021 | 0.009481 | -0.001444 | 0.010557 | 0.027136 | 0.003559 | 0.03453 | 0.010953
5748.3438 | 122.7676 | -0.10529 | 122.7997 | 0.12643 | -0.040521 | -0.025735 | -0.025017 | 0.013375 | 0.062691 | -0.062717 | -0.052818 | 0.065481 | -0.040846 | -0.046838 | -0.061641 | -0.036295 | -0.042641 | -0.030641 | 0.23172 | 0.064765 | 0.079551 | 0.080269 | 0.11866 | 0.16798 | 0.042569 | -0.007042 | 0.11126 | 0.00493 | -0.001062 | -0.015865 | 0.009481 | 0.003135 | 0.015135 | 0.008823 | -0.010177 | 0.020795 | 0.001795
5750.0469 | 122.7539 | -0.11902 | 122.7356 | 0.13101 | -0.049678 | -0.034893 | -0.025017 | 0.013375 | 0.067269 | -0.071874 | -0.043661 | 0.065481 | -0.040846 | -0.042259 | -0.061641 | -0.031717 | -0.04722 | -0.030641 | 0.25003 | 0.069341 | 0.084126 | 0.094002 | 0.13239 | 0.18629 | 0.047145 | 0.002115 | 0.11126 | 0.00493 | 0.003517 | -0.015865 | 0.014059 | -0.001444 | 0.015135 | 0.01798 | 0.003559 | 0.020795 | 0.006374
5751.7656 | 122.8638 | -0.082397 | 122.7356 | 0.12643 | -0.040521 | -0.030314 | -0.029595 | 0.008797 | 0.062691 | -0.067295 | -0.057396 | 0.065481 | -0.040846 | -0.042259 | -0.066219 | -0.031717 | -0.056376 | -0.026063 | 0.20883 | 0.041876 | 0.052083 | 0.052802 | 0.091194 | 0.14509 | 0.015102 | -0.01162 | 0.11126 | 0.00493 | 0.003517 | -0.020443 | 0.014059 | -0.0106 | 0.019713 | 0.008823 | -0.00102 | 0.025373 | 0.01553
5753.4688 | 122.8821 | -0.064087 | 122.7173 | 0.13559 | -0.0451 | -0.034893 | -0.029595 | 0.017953 | 0.062691 | -0.067295 | -0.048239 | 0.07006 | -0.045424 | -0.042259 | -0.066219 | -0.040873 | -0.051798 | -0.026063 | 0.19967 | 0.018987 | 0.029194 | 0.034492 | 0.08204 | 0.12678 | -0.003208 | -0.002463 | 0.11584 | 0.000352 | 0.003517 | -0.020443 | 0.004903 | -0.006022 | 0.019713 | 0.01798 | 0.003559 | 0.020795 | 0.006374
5755.1719 | 122.8821 | -0.086975 | 122.7493 | 0.14017 | -0.0451 | -0.034893 | -0.020438 | 0.017953 | 0.058113 | -0.062717 | -0.048239 | 0.060902 | -0.036267 | -0.042259 | -0.066219 | -0.031717 | -0.042641 | -0.030641 | 0.22714 | 0.041875 | 0.052082 | 0.066537 | 0.10493 | 0.14509 | 0.024258 | -0.002463 | 0.10668 | 0.009509 | 0.003517 | -0.020443 | 0.014059 | 0.003135 | 0.015135 | 0.01798 | -0.005598 | 0.029952 | 0.006374
5756.9062 | 122.8134 | -0.10071 | 122.7219 | 0.13101 | -0.0451 | -0.025735 | -0.025017 | 0.017953 | 0.071848 | -0.062717 | -0.048239 | 0.07006 | -0.050002 | -0.042259 | -0.061641 | -0.031717 | -0.04722 | -0.030641 | 0.23172 | 0.055608 | 0.074973 | 0.075691 | 0.11866 | 0.17256 | 0.037991 | -0.002463 | 0.11584 | -0.004226 | 0.003517 | -0.015865 | 0.014059 | -0.001444 | 0.015135 | 0.013402 | -0.001019 | 0.011639 | -0.002782
5758.6406 | 122.9004 | -0.086975 | 122.7402 | 0.13559 | -0.049678 | -0.034893 | -0.029595 | 0.008797 | 0.058113 | -0.067295 | -0.043661 | 0.065481 | -0.040846 | -0.03768 | -0.061641 | -0.036295 | -0.042641 | -0.035219 | 0.22256 | 0.037297 | 0.052082 | 0.05738 | 0.095772 | 0.14509 | 0.01968 | 0.002115 | 0.11126 | 0.00493 | 0.008096 | -0.015865 | 0.009481 | 0.003135 | 0.010557 | 0.01798 | -0.00102 | 0.020795 | 0.001795
5760.375 | 122.7859 | -0.11444 | 122.7631 | 0.13559 | -0.040521 | -0.030314 | -0.034174 | 0.017953 | 0.062691 | -0.062717 | -0.043661 | 0.060902 | -0.045424 | -0.03768 | -0.057062 | -0.027139 | -0.042641 | -0.030641 | 0.25003 | 0.07392 | 0.084127 | 0.080267 | 0.13239 | 0.17713 | 0.051724 | 0.002115 | 0.10668 | 0.000352 | 0.008096 | -0.011286 | 0.018637 | 0.003135 | 0.015135 | 0.013401 | -0.00102 | 0.011638 | -0.002783
5762.1094 | 122.7997 | -0.091553 | 122.7585 | 0.13101 | -0.049678 | -0.025735 | -0.034174 | 0.008797 | 0.062691 | -0.067295 | -0.048239 | 0.056323 | -0.040846 | -0.03768 | -0.070797 | -0.036295 | -0.051798 | -0.030641 | 0.22256 | 0.041875 | 0.065818 | 0.057379 | 0.10035 | 0.15424 | 0.024258 | -0.002463 | 0.1021 | 0.00493 | 0.008096 | -0.025021 | 0.009481 | -0.006022 | 0.015135 | 0.022558 | 0.003559 | 0.029951 | 0.010952
5763.8594 | 122.8226 | -0.10986 | 122.7585 | 0.14017 | -0.040521 | -0.030314 | -0.029595 | 0.013375 | 0.062691 | -0.067295 | -0.043661 | 0.060902 | -0.040846 | -0.042259 | -0.057062 | -0.031717 | -0.04722 | -0.035219 | 0.25003 | 0.069342 | 0.079549 | 0.080268 | 0.12324 | 0.17255 | 0.042568 | 0.002115 | 0.10668 | 0.00493 | 0.003517 | -0.011286 | 0.014059 | -0.001444 | 0.010557 | 0.013401 | 0.003559 | 0.016216 | 0.006374
5765.5781 | 122.8134 | -0.11902 | 122.7539 | 0.12643 | -0.0451 | -0.030314 | -0.034174 | 0.017953 | 0.062691 | -0.062717 | -0.043661 | 0.065481 | -0.036267 | -0.03768 | -0.066219 | -0.040873 | -0.04722 | -0.030641 | 0.24545 | 0.073919 | 0.088705 | 0.084845 | 0.13697 | 0.18171 | 0.056302 | 0.002115 | 0.11126 | 0.009509 | 0.008096 | -0.020443 | 0.004903 | -0.001444 | 0.015135 | 0.022558 | 0.003559 | 0.029952 | 0.010953
5767.3438 | 122.9141 | -0.064087 | 122.7356 | 0.13101 | -0.058836 | -0.034893 | -0.029595 | 0.013375 | 0.058113 | -0.067295 | -0.043661 | 0.056323 | -0.05458 | -0.03768 | -0.066219 | -0.036295 | -0.056376 | -0.021484 | 0.1951 | 0.005251 | 0.029194 | 0.034492 | 0.077462 | 0.1222 | -0.003208 | 0.002115 | 0.1021 | -0.008804 | 0.008096 | -0.020443 | 0.009481 | -0.0106 | 0.024292 | 0.022558 | 0.012715 | 0.011639 | 0.001796
5769.0625 | 122.8867 | -0.082397 | 122.7264 | 0.12643 | -0.040521 | -0.034893 | -0.034174 | 0.008797 | 0.058113 | -0.071874 | -0.048239 | 0.060902 | -0.045424 | -0.046838 | -0.070797 | -0.027139 | -0.051798 | -0.035219 | 0.20883 | 0.041876 | 0.047504 | 0.048223 | 0.091194 | 0.14051 | 0.010523 | -0.002463 | 0.10668 | 0.000352 | -0.001062 | -0.025021 | 0.018637 | -0.006022 | 0.010557 | 0.022558 | 0.003559 | 0.025373 | 0.006374
5770.7812 | 122.85 | -0.091553 | 122.7356 | 0.13101 | -0.035942 | -0.021157 | -0.034174 | 0.013375 | 0.058113 | -0.062717 | -0.043661 | 0.065481 | -0.045424 | -0.042259 | -0.066219 | -0.031717 | -0.04722 | -0.030641 | 0.22256 | 0.055611 | 0.070396 | 0.057379 | 0.10493 | 0.14967 | 0.028836 | 0.002115 | 0.11126 | 0.000352 | 0.003517 | -0.020443 | 0.014059 | -0.001444 | 0.015135 | 0.022558 | 0.003559 | 0.020795 | 0.001796
5772.5156 | 122.7905 | -0.11444 | 122.7859 | 0.13101 | -0.054257 | -0.021157 | -0.029595 | 0.017953 | 0.058113 | -0.067295 | -0.052818 | 0.065481 | -0.045424 | -0.042259 | -0.066219 | -0.036295 | -0.04722 | -0.035219 | 0.24545 | 0.060184 | 0.093284 | 0.084846 | 0.13239 | 0.17255 | 0.047146 | -0.007042 | 0.11126 | 0.000352 | 0.003517 | -0.020443 | 0.009481 | -0.001444 | 0.010557 | 0.013401 | -0.005598 | 0.020795 | 0.001796
5774.2969 | 122.8317 | -0.07782 | 122.7722 | 0.13101 | -0.0451 | -0.030314 | -0.029595 | 0.013375 | 0.062691 | -0.062717 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.061641 | -0.036295 | -0.051798 | -0.035219 | 0.20883 | 0.03272 | 0.047506 | 0.048225 | 0.091195 | 0.14051 | 0.015103 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.015865 | 0.009481 | -0.006022 | 0.010557 | 0.013402 | 0.003559 | 0.020795 | 0.010952
5776.0312 | 122.8958 | -0.082397 | 122.7127 | 0.13101 | -0.049678 | -0.030314 | -0.034174 | 0.008797 | 0.058113 | -0.067295 | -0.057396 | 0.065481 | -0.040846 | -0.042259 | -0.066219 | -0.027139 | -0.051798 | -0.030641 | 0.21341 | 0.032719 | 0.052083 | 0.048223 | 0.091194 | 0.14051 | 0.015102 | -0.01162 | 0.11126 | 0.00493 | 0.003517 | -0.020443 | 0.018637 | -0.006022 | 0.015135 | 0.008823 | -0.005598 | 0.025373 | 0.010952
5777.7344 | 122.8363 | -0.10071 | 122.7631 | 0.13101 | -0.0451 | -0.030314 | -0.029595 | 0.017953 | 0.062691 | -0.062717 | -0.052818 | 0.065481 | -0.050002 | -0.042259 | -0.066219 | -0.040873 | -0.038063 | -0.035219 | 0.23172 | 0.055608 | 0.070394 | 0.071113 | 0.11866 | 0.1634 | 0.037991 | -0.007042 | 0.11126 | -0.004226 | 0.003517 | -0.020443 | 0.004903 | 0.007713 | 0.010557 | 0.013401 | -0.014755 | 0.016217 | -0.011939
5779.4531 | 122.7539 | -0.1236 | 122.7676 | 0.13101 | -0.054257 | -0.030314 | -0.034174 | 0.013375 | 0.062691 | -0.062717 | -0.048239 | 0.060902 | -0.045424 | -0.042259 | -0.057062 | -0.036295 | -0.051798 | -0.026063 | 0.2546 | 0.069339 | 0.093282 | 0.089422 | 0.13697 | 0.18629 | 0.060879 | -0.002463 | 0.10668 | 0.000352 | 0.003517 | -0.011286 | 0.009481 | -0.006022 | 0.019713 | 0.008823 | 0.003559 | 0.011638 | 0.006374
5781.1719 | 122.9279 | -0.07782 | 122.7127 | 0.12643 | -0.049678 | -0.030314 | -0.038752 | 0.017953 | 0.062691 | -0.067295 | -0.048239 | 0.07006 | -0.040846 | -0.046838 | -0.061641 | -0.031717 | -0.04722 | -0.035219 | 0.20425 | 0.028142 | 0.047506 | 0.039068 | 0.095773 | 0.14051 | 0.010525 | -0.002463 | 0.11584 | 0.00493 | -0.001062 | -0.015865 | 0.014059 | -0.001444 | 0.010557 | 0.013402 | -0.001019 | 0.020795 | 0.006374
5782.8906 | 122.8683 | -0.082397 | 122.7859 | 0.13559 | -0.0451 | -0.025735 | -0.025017 | 0.017953 | 0.058113 | -0.071874 | -0.057396 | 0.065481 | -0.045424 | -0.042259 | -0.066219 | -0.031717 | -0.04722 | -0.030641 | 0.21798 | 0.037297 | 0.056662 | 0.05738 | 0.10035 | 0.14051 | 0.010523 | -0.01162 | 0.11126 | 0.000352 | 0.003517 | -0.020443 | 0.014059 | -0.001444 | 0.015135 | 0.008823 | -0.010176 | 0.020795 | 0.001796
5784.6094 | 122.9095 | -0.073242 | 122.7356 | 0.12643 | -0.049678 | -0.025735 | -0.034174 | 0.017953 | 0.071848 | -0.062717 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.066219 | -0.036295 | -0.04722 | -0.030641 | 0.19967 | 0.023564 | 0.047507 | 0.039068 | 0.091195 | 0.14509 | 0.010525 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.020443 | 0.009481 | -0.001444 | 0.015135 | 0.01798 | -0.001019 | 0.025373 | 0.006374
5786.3594 | 122.8638 | -0.07782 | 122.7356 | 0.13559 | -0.0451 | -0.034893 | -0.029595 | 0.013375 | 0.053534 | -0.071874 | -0.052818 | 0.065481 | -0.045424 | -0.042259 | -0.070797 | -0.031717 | -0.04722 | -0.030641 | 0.21341 | 0.03272 | 0.042927 | 0.048225 | 0.091195 | 0.13135 | 0.005946 | -0.007042 | 0.11126 | 0.000352 | 0.003517 | -0.025021 | 0.014059 | -0.001444 | 0.015135 | 0.017979 | -0.005598 | 0.025373 | 0.001796
5788.0781 | 122.818 | -0.10986 | 122.7905 | 0.14017 | -0.049678 | -0.034893 | -0.029595 | 0.013375 | 0.071848 | -0.062717 | -0.048239 | 0.060902 | -0.040846 | -0.03768 | -0.061641 | -0.027139 | -0.042641 | -0.039797 | 0.25003 | 0.060185 | 0.07497 | 0.080268 | 0.12324 | 0.18171 | 0.047146 | -0.002463 | 0.10668 | 0.00493 | 0.008096 | -0.015865 | 0.018637 | 0.003135 | 0.005979 | 0.013402 | -0.005598 | 0.020795 | 0.001795
5789.7969 | 122.9095 | -0.073242 | 122.7448 | 0.13559 | -0.049678 | -0.034893 | -0.034174 | 0.013375 | 0.062691 | -0.067295 | -0.039082 | 0.060902 | -0.040846 | -0.03768 | -0.061641 | -0.031717 | -0.04722 | -0.035219 | 0.20883 | 0.023564 | 0.038349 | 0.039068 | 0.086617 | 0.13593 | 0.005947 | 0.006694 | 0.10668 | 0.00493 | 0.008096 | -0.015865 | 0.014059 | -0.001444 | 0.010557 | 0.022559 | 0.008138 | 0.020795 | 0.006374
5791.5 | 122.8363 | -0.10071 | 122.7356 | 0.13559 | -0.049678 | -0.030314 | -0.034174 | 0.013375 | 0.067269 | -0.071874 | -0.048239 | 0.065481 | -0.050002 | -0.046838 | -0.061641 | -0.036295 | -0.04722 | -0.035219 | 0.23629 | 0.05103 | 0.070394 | 0.066534 | 0.11408 | 0.16798 | 0.028834 | -0.002463 | 0.11126 | -0.004226 | -0.001062 | -0.015865 | 0.009481 | -0.001444 | 0.010557 | 0.013402 | -0.001019 | 0.011639 | -0.002782
5793.2812 | 122.8134 | -0.10986 | 122.7768 | 0.13559 | -0.0451 | -0.030314 | -0.029595 | 0.017953 | 0.071848 | -0.067295 | -0.043661 | 0.065481 | -0.040846 | -0.042259 | -0.061641 | -0.036295 | -0.04722 | -0.030641 | 0.24545 | 0.064763 | 0.079549 | 0.080268 | 0.12782 | 0.18171 | 0.042568 | 0.002115 | 0.11126 | 0.00493 | 0.003517 | -0.015865 | 0.009481 | -0.001444 | 0.015135 | 0.01798 | 0.003559 | 0.020795 | 0.006374
5795 | 122.9095 | -0.073242 | 122.7585 | 0.13559 | -0.049678 | -0.034893 | -0.043331 | 0.013375 | 0.067269 | -0.071874 | -0.048239 | 0.07006 | -0.045424 | -0.033101 | -0.066219 | -0.036295 | -0.051798 | -0.030641 | 0.20883 | 0.023564 | 0.038349 | 0.029911 | 0.086617 | 0.14051 | 0.001368 | -0.002463 | 0.11584 | 0.000352 | 0.012675 | -0.020443 | 0.009481 | -0.006022 | 0.015135 | 0.01798 | 0.003559 | 0.020795 | 0.006374
5796.7031 | 122.8867 | -0.068665 | 122.7402 | 0.13559 | -0.054257 | -0.034893 | -0.034174 | 0.013375 | 0.062691 | -0.058139 | -0.043661 | 0.065481 | -0.040846 | -0.03768 | -0.066219 | -0.027139 | -0.042641 | -0.026063 | 0.20425 | 0.014408 | 0.033772 | 0.034491 | 0.08204 | 0.13136 | 0.010526 | 0.002115 | 0.11126 | 0.00493 | 0.008096 | -0.020443 | 0.018637 | 0.003135 | 0.019713 | 0.022558 | -0.00102 | 0.025373 | 0.001795
5798.4219 | 122.8088 | -0.1236 | 122.7585 | 0.13101 | -0.0451 | -0.034893 | -0.034174 | 0.017953 | 0.067269 | -0.062717 | -0.057396 | 0.056323 | -0.036267 | -0.033101 | -0.061641 | -0.036295 | -0.051798 | -0.039797 | 0.2546 | 0.078496 | 0.088703 | 0.089422 | 0.14155 | 0.19087 | 0.060879 | -0.01162 | 0.1021 | 0.009509 | 0.012675 | -0.015865 | 0.009481 | -0.006022 | 0.005979 | 0.004245 | -0.005598 | 0.025374 | 0.015531
5800.1406 | 122.9141 | -0.068665 | 122.7173 | 0.13559 | -0.054257 | -0.034893 | -0.038752 | 0.013375 | 0.062691 | -0.062717 | -0.052818 | 0.060902 | -0.045424 | -0.042259 | -0.066219 | -0.031717 | -0.042641 | -0.030641 | 0.20425 | 0.014408 | 0.033772 | 0.029913 | 0.08204 | 0.13136 | 0.005948 | -0.007042 | 0.10668 | 0.000352 | 0.003517 | -0.020443 | 0.014059 | 0.003135 | 0.015135 | 0.013401 | -0.010177 | 0.020795 | -0.002783
5801.8594 | 122.7905 | -0.10529 | 122.7905 | 0.13101 | -0.058836 | -0.034893 | -0.034174 | 0.013375 | 0.062691 | -0.067295 | -0.043661 | 0.060902 | -0.050002 | -0.046838 | -0.070797 | -0.031717 | -0.042641 | -0.030641 | 0.23629 | 0.04645 | 0.070393 | 0.071112 | 0.11866 | 0.16798 | 0.037991 | 0.002115 | 0.10668 | -0.004226 | -0.001062 | -0.025021 | 0.014059 | 0.003135 | 0.015135 | 0.027136 | -0.00102 | 0.020795 | -0.007361
5803.5625 | 122.9095 | -0.054932 | 122.7173 | 0.13101 | -0.049678 | -0.034893 | -0.034174 | 0.013375 | 0.062691 | -0.067295 | -0.043661 | 0.060902 | -0.050002 | -0.03768 | -0.061641 | -0.036295 | -0.051798 | -0.035219 | 0.18594 | 0.005254 | 0.020039 | 0.020758 | 0.068307 | 0.11762 | -0.012363 | 0.002115 | 0.10668 | -0.004226 | 0.008096 | -0.015865 | 0.009481 | -0.006022 | 0.010557 | 0.01798 | 0.008137 | 0.011639 | 0.001796
5805.3281 | 122.7814 | -0.11444 | 122.7814 | 0.13101 | -0.058836 | -0.030314 | -0.029595 | 0.008797 | 0.058113 | -0.062717 | -0.043661 | 0.060902 | -0.050002 | -0.042259 | -0.057062 | -0.031717 | -0.056376 | -0.030641 | 0.24545 | 0.055605 | 0.084127 | 0.084846 | 0.12324 | 0.17255 | 0.051724 | 0.002115 | 0.10668 | -0.004226 | 0.003517 | -0.011286 | 0.014059 | -0.0106 | 0.015135 | 0.013401 | 0.012715 | 0.00706 | 0.006374
5807.0469 | 122.8821 | -0.07782 | 122.7722 | 0.13101 | -0.049678 | -0.025735 | -0.029595 | 0.017953 | 0.062691 | -0.071874 | -0.043661 | 0.065481 | -0.045424 | -0.03768 | -0.066219 | -0.031717 | -0.04722 | -0.026063 | 0.20883 | 0.028142 | 0.052085 | 0.048225 | 0.095773 | 0.14051 | 0.005946 | 0.002115 | 0.11126 | 0.000352 | 0.008096 | -0.020443 | 0.014059 | -0.001444 | 0.019713 | 0.022558 | 0.003559 | 0.020795 | 0.001796
5808.7812 | 122.818 | -0.12817 | 122.8088 | 0.13101 | -0.049678 | -0.034893 | -0.025017 | 0.008797 | 0.067269 | -0.062717 | -0.052818 | 0.065481 | -0.045424 | -0.046838 | -0.066219 | -0.031717 | -0.056376 | -0.035219 | 0.25918 | 0.078496 | 0.093281 | 0.10316 | 0.13697 | 0.19544 | 0.065457 | -0.007042 | 0.11126 | 0.000352 | -0.001062 | -0.020443 | 0.014059 | -0.0106 | 0.010557 | 0.013401 | 0.003558 | 0.020795 | 0.010952
5810.5312 | 122.8043 | -0.1236 | 122.7859 | 0.13101 | -0.054257 | -0.030314 | -0.034174 | 0.017953 | 0.058113 | -0.067295 | -0.048239 | 0.065481 | -0.050002 | -0.03768 | -0.066219 | -0.031717 | -0.042641 | -0.030641 | 0.2546 | 0.069339 | 0.093282 | 0.089422 | 0.14155 | 0.18171 | 0.056301 | -0.002463 | 0.11126 | -0.004226 | 0.008096 | -0.020443 | 0.014059 | 0.003135 | 0.015135 | 0.01798 | -0.005598 | 0.016217 | -0.007361
5812.3125 | 122.8775 | -0.068665 | 122.7448 | 0.13559 | -0.0451 | -0.039471 | -0.029595 | 0.017953 | 0.058113 | -0.062717 | -0.052818 | 0.065481 | -0.045424 | -0.03768 | -0.061641 | -0.027139 | -0.051798 | -0.030641 | 0.20425 | 0.023565 | 0.029194 | 0.03907 | 0.086618 | 0.12678 | 0.005948 | -0.007042 | 0.11126 | 0.000352 | 0.008096 | -0.015865 | 0.018637 | -0.006022 | 0.015135 | 0.008823 | -0.00102 | 0.016217 | 0.006374
5814.0312 | 122.8638 | -0.09613 | 122.7631 | 0.13101 | -0.049678 | -0.030314 | -0.025017 | 0.017953 | 0.062691 | -0.058139 | -0.048239 | 0.074638 | -0.040846 | -0.042259 | -0.066219 | -0.027139 | -0.04722 | -0.030641 | 0.22714 | 0.046452 | 0.065816 | 0.071113 | 0.11408 | 0.15882 | 0.037991 | -0.002463 | 0.12041 | 0.00493 | 0.003517 | -0.020443 | 0.018637 | -0.001444 | 0.015135 | 0.01798 | -0.001019 | 0.025373 | 0.006374
5815.8125 | 122.9324 | -0.064087 | 122.731 | 0.13101 | -0.058836 | -0.034893 | -0.034174 | 0.013375 | 0.058113 | -0.071874 | -0.043661 | 0.07006 | -0.040846 | -0.042259 | -0.061641 | -0.031717 | -0.04722 | -0.030641 | 0.1951 | 0.005251 | 0.029194 | 0.029913 | 0.077462 | 0.1222 | -0.007787 | 0.002115 | 0.11584 | 0.00493 | 0.003517 | -0.015865 | 0.014059 | -0.001444 | 0.015135 | 0.01798 | 0.003559 | 0.020795 | 0.006374
5817.5312 | 122.905 | -0.073242 | 122.7402 | 0.13559 | -0.058836 | -0.034893 | -0.029595 | 0.017953 | 0.067269 | -0.067295 | -0.048239 | 0.07006 | -0.045424 | -0.042259 | -0.066219 | -0.036295 | -0.051798 | -0.026063 | 0.20883 | 0.014406 | 0.038349 | 0.043647 | 0.091195 | 0.14051 | 0.005947 | -0.002463 | 0.11584 | 0.000352 | 0.003517 | -0.020443 | 0.009481 | -0.006022 | 0.019713 | 0.01798 | 0.003559 | 0.020795 | 0.006374
5819.25 | 122.8134 | -0.11902 | 122.7631 | 0.13101 | -0.0451 | -0.025735 | -0.034174 | 0.013375 | 0.062691 | -0.067295 | -0.052818 | 0.056323 | -0.045424 | -0.042259 | -0.066219 | -0.036295 | -0.038063 | -0.030641 | 0.25003 | 0.073919 | 0.093284 | 0.084845 | 0.13239 | 0.18171 | 0.051724 | -0.007042 | 0.1021 | 0.000352 | 0.003517 | -0.020443 | 0.009481 | 0.007713 | 0.015135 | 0.013401 | -0.014755 | 0.020795 | -0.007361
5820.9688 | 122.7951 | -0.10529 | 122.7951 | 0.13101 | -0.049678 | -0.030314 | -0.020438 | 0.013375 | 0.058113 | -0.062717 | -0.048239 | 0.065481 | -0.045424 | -0.046838 | -0.066219 | -0.031717 | -0.04722 | -0.039797 | 0.23629 | 0.055608 | 0.074972 | 0.084848 | 0.11866 | 0.1634 | 0.042569 | -0.002463 | 0.11126 | 0.000352 | -0.001062 | -0.020443 | 0.014059 | -0.001444 | 0.005979 | 0.01798 | -0.001019 | 0.020795 | 0.001796
5822.8125 | 122.9324 | -0.059509 | 122.7493 | 0.13101 | -0.049678 | -0.034893 | -0.034174 | 0.008797 | 0.053534 | -0.062717 | -0.048239 | 0.060902 | -0.036267 | -0.03768 | -0.066219 | -0.027139 | -0.051798 | -0.030641 | 0.19052 | 0.009831 | 0.024616 | 0.025335 | 0.068306 | 0.11304 | -0.003208 | -0.002463 | 0.10668 | 0.009509 | 0.008096 | -0.020443 | 0.018637 | -0.006022 | 0.015135 | 0.01798 | 0.003559 | 0.029952 | 0.015531
5824.6094 | 122.8271 | -0.10071 | 122.7722 | 0.12643 | -0.0451 | -0.025735 | -0.043331 | 0.013375 | 0.062691 | -0.067295 | -0.048239 | 0.07006 | -0.045424 | -0.033101 | -0.066219 | -0.036295 | -0.042641 | -0.026063 | 0.22714 | 0.055608 | 0.074973 | 0.057377 | 0.11408 | 0.1634 | 0.033413 | -0.002463 | 0.11584 | 0.000352 | 0.012675 | -0.020443 | 0.009481 | 0.003135 | 0.019713 | 0.01798 | -0.005598 | 0.020795 | -0.002783
5826.3438 | 122.9004 | -0.07782 | 122.7722 | 0.13101 | -0.054257 | -0.030314 | -0.029595 | 0.013375 | 0.062691 | -0.067295 | -0.052818 | 0.060902 | -0.050002 | -0.03768 | -0.061641 | -0.031717 | -0.042641 | -0.030641 | 0.20883 | 0.023563 | 0.047506 | 0.048225 | 0.091195 | 0.14051 | 0.010525 | -0.007042 | 0.10668 | -0.004226 | 0.008096 | -0.015865 | 0.014059 | 0.003135 | 0.015135 | 0.008823 | -0.010177 | 0.011639 | -0.007361
5828.125 | 122.8088 | -0.10986 | 122.7722 | 0.13101 | -0.049678 | -0.034893 | -0.038752 | 0.017953 | 0.062691 | -0.067295 | -0.057396 | 0.060902 | -0.050002 | -0.042259 | -0.070797 | -0.036295 | -0.051798 | -0.039797 | 0.24087 | 0.060185 | 0.07497 | 0.071111 | 0.12782 | 0.17255 | 0.042568 | -0.01162 | 0.10668 | -0.004226 | 0.003517 | -0.025021 | 0.009481 | -0.006022 | 0.005979 | 0.013401 | -0.005598 | 0.020795 | 0.001796
5829.9062 | 122.8546 | -0.10986 | 122.7448 | 0.13559 | -0.054257 | -0.039471 | -0.034174 | 0.017953 | 0.058113 | -0.062717 | -0.052818 | 0.065481 | -0.040846 | -0.046838 | -0.066219 | -0.027139 | -0.051798 | -0.030641 | 0.24545 | 0.055606 | 0.070392 | 0.075689 | 0.12782 | 0.16798 | 0.047146 | -0.007042 | 0.11126 | 0.00493 | -0.001062 | -0.020443 | 0.018637 | -0.006022 | 0.015135 | 0.013401 | -0.00102 | 0.025373 | 0.010952
5831.625 | 122.8455 | -0.09613 | 122.7814 | 0.13559 | -0.054257 | -0.025735 | -0.038752 | 0.017953 | 0.062691 | -0.062717 | -0.048239 | 0.065481 | -0.050002 | -0.03768 | -0.066219 | -0.040873 | -0.04722 | -0.035219 | 0.23172 | 0.041873 | 0.070395 | 0.057378 | 0.11408 | 0.15882 | 0.033413 | -0.002463 | 0.11126 | -0.004226 | 0.008096 | -0.020443 | 0.004903 | -0.001444 | 0.010557 | 0.01798 | -0.001019 | 0.016217 | -0.002782
5833.4062 | 122.7905 | -0.10529 | 122.7631 | 0.13101 | -0.049678 | -0.030314 | -0.025017 | 0.017953 | 0.058113 | -0.062717 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.070797 | -0.031717 | -0.04722 | -0.026063 | 0.23629 | 0.055608 | 0.074972 | 0.080269 | 0.12324 | 0.1634 | 0.042569 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.025021 | 0.014059 | -0.001444 | 0.019713 | 0.022558 | -0.001019 | 0.029951 | 0.006374
5835.125 | 122.9095 | -0.07782 | 122.7448 | 0.12185 | -0.054257 | -0.030314 | -0.043331 | 0.008797 | 0.058113 | -0.062717 | -0.043661 | 0.060902 | -0.036267 | -0.03768 | -0.061641 | -0.031717 | -0.04722 | -0.035219 | 0.19967 | 0.023563 | 0.047506 | 0.034489 | 0.086617 | 0.13593 | 0.015103 | 0.002115 | 0.10668 | 0.009509 | 0.008096 | -0.015865 | 0.014059 | -0.001444 | 0.010557 | 0.01798 | 0.003559 | 0.025374 | 0.010953
5836.9062 | 122.8317 | -0.10986 | 122.8043 | 0.12643 | -0.049678 | -0.025735 | -0.025017 | 0.008797 | 0.062691 | -0.071874 | -0.052818 | 0.065481 | -0.040846 | -0.042259 | -0.061641 | -0.036295 | -0.056376 | -0.030641 | 0.23629 | 0.060185 | 0.084128 | 0.084846 | 0.11866 | 0.17255 | 0.037989 | -0.007042 | 0.11126 | 0.00493 | 0.003517 | -0.015865 | 0.009481 | -0.0106 | 0.015135 | 0.008823 | 0.003558 | 0.020795 | 0.01553
5838.6875 | 122.8455 | -0.10071 | 122.7814 | 0.13101 | -0.0451 | -0.025735 | -0.034174 | 0.022531 | 0.058113 | -0.067295 | -0.052818 | 0.060902 | -0.045424 | -0.042259 | -0.066219 | -0.031717 | -0.04722 | -0.035219 | 0.23172 | 0.055608 | 0.074973 | 0.066534 | 0.12324 | 0.15882 | 0.033413 | -0.007042 | 0.10668 | 0.000352 | 0.003517 | -0.020443 | 0.014059 | -0.001444 | 0.010557 | 0.013401 | -0.005598 | 0.020795 | 0.001796
5840.4219 | 122.8546 | -0.10529 | 122.8088 | 0.13559 | -0.058836 | -0.030314 | -0.038752 | 0.004219 | 0.058113 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.066219 | -0.031717 | -0.033484 | -0.026063 | 0.24087 | 0.04645 | 0.074972 | 0.066534 | 0.10951 | 0.1634 | 0.042569 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.020443 | 0.014059 | 0.012292 | 0.019713 | 0.01798 | -0.014755 | 0.025373 | -0.007362
5842.2031 | 122.9279 | -0.091553 | 122.7356 | 0.13101 | -0.058836 | -0.030314 | -0.029595 | 0.013375 | 0.062691 | -0.067295 | -0.048239 | 0.065481 | -0.050002 | -0.03768 | -0.066219 | -0.027139 | -0.038063 | -0.035219 | 0.22256 | 0.032717 | 0.061239 | 0.061958 | 0.10493 | 0.15424 | 0.024258 | -0.002463 | 0.11126 | -0.004226 | 0.008096 | -0.020443 | 0.018637 | 0.007713 | 0.010557 | 0.01798 | -0.010176 | 0.016217 | -0.011939
5843.9844 | 122.937 | -0.07782 | 122.7493 | 0.12643 | -0.058836 | -0.030314 | -0.034174 | 0.013375 | 0.062691 | -0.062717 | -0.048239 | 0.065481 | -0.045424 | -0.03768 | -0.066219 | -0.031717 | -0.042641 | -0.030641 | 0.20425 | 0.018984 | 0.047506 | 0.043646 | 0.091195 | 0.14051 | 0.015103 | -0.002463 | 0.11126 | 0.000352 | 0.008096 | -0.020443 | 0.014059 | 0.003135 | 0.015135 | 0.01798 | -0.005598 | 0.020795 | -0.002783
5845.7656 | 122.7997 | -0.10071 | 122.7768 | 0.13101 | -0.058836 | -0.034893 | -0.029595 | 0.017953 | 0.062691 | -0.058139 | -0.052818 | 0.065481 | -0.040846 | -0.03768 | -0.066219 | -0.036295 | -0.056376 | -0.030641 | 0.23172 | 0.041872 | 0.065815 | 0.071113 | 0.11866 | 0.1634 | 0.042569 | -0.007042 | 0.11126 | 0.00493 | 0.008096 | -0.020443 | 0.009481 | -0.0106 | 0.015135 | 0.013401 | 0.003558 | 0.025373 | 0.01553
5847.4844 | 122.8226 | -0.10529 | 122.7905 | 0.12643 | -0.058836 | -0.025735 | -0.038752 | 0.008797 | 0.067269 | -0.067295 | -0.057396 | 0.065481 | -0.040846 | -0.042259 | -0.061641 | -0.031717 | -0.056376 | -0.035219 | 0.23172 | 0.04645 | 0.079551 | 0.066534 | 0.11408 | 0.17256 | 0.037991 | -0.01162 | 0.11126 | 0.00493 | 0.003517 | -0.015865 | 0.014059 | -0.0106 | 0.010557 | 0.004245 | -0.00102 | 0.020795 | 0.01553
5849.25 | 122.85 | -0.082397 | 122.7722 | 0.14017 | -0.058836 | -0.030314 | -0.029595 | 0.008797 | 0.058113 | -0.067295 | -0.052818 | 0.065481 | -0.040846 | -0.03768 | -0.061641 | -0.031717 | -0.042641 | -0.030641 | 0.22256 | 0.023561 | 0.052083 | 0.052802 | 0.091194 | 0.14051 | 0.015102 | -0.007042 | 0.11126 | 0.00493 | 0.008096 | -0.015865 | 0.014059 | 0.003135 | 0.015135 | 0.008823 | -0.010177 | 0.020795 | 0.001795
5851.0312 | 122.8043 | -0.11902 | 122.7951 | 0.13101 | -0.054257 | -0.034893 | -0.029595 | 0.013375 | 0.071848 | -0.058139 | -0.052818 | 0.065481 | -0.045424 | -0.03768 | -0.066219 | -0.031717 | -0.056376 | -0.030641 | 0.25003 | 0.064762 | 0.084126 | 0.089424 | 0.13239 | 0.19087 | 0.06088 | -0.007042 | 0.11126 | 0.000352 | 0.008096 | -0.020443 | 0.014059 | -0.0106 | 0.015135 | 0.013401 | 0.003558 | 0.020795 | 0.010952
5852.8281 | 122.8226 | -0.10986 | 122.7768 | 0.12643 | -0.058836 | -0.021157 | -0.038752 | 0.004219 | 0.067269 | -0.062717 | -0.039082 | 0.065481 | -0.040846 | -0.033101 | -0.066219 | -0.031717 | -0.051798 | -0.039797 | 0.23629 | 0.051027 | 0.088706 | 0.071111 | 0.11408 | 0.17713 | 0.047146 | 0.006694 | 0.11126 | 0.00493 | 0.012675 | -0.020443 | 0.014059 | -0.006022 | 0.005979 | 0.027137 | 0.012716 | 0.025373 | 0.010952
5854.5469 | 122.818 | -0.10986 | 122.7859 | 0.13559 | -0.049678 | -0.025735 | -0.038752 | 0.008797 | 0.062691 | -0.067295 | -0.043661 | 0.060902 | -0.036267 | -0.033101 | -0.070797 | -0.031717 | -0.051798 | -0.026063 | 0.24545 | 0.060185 | 0.084128 | 0.071111 | 0.11866 | 0.17255 | 0.042568 | 0.002115 | 0.10668 | 0.009509 | 0.012675 | -0.025021 | 0.014059 | -0.006022 | 0.019713 | 0.027136 | 0.008137 | 0.03453 | 0.015531
5856.3125 | 122.8638 | -0.10071 | 122.7951 | 0.13559 | -0.054257 | -0.030314 | -0.034174 | 0.013375 | 0.062691 | -0.071874 | -0.048239 | 0.060902 | -0.045424 | -0.042259 | -0.066219 | -0.040873 | -0.051798 | -0.035219 | 0.23629 | 0.046451 | 0.070394 | 0.066534 | 0.11408 | 0.1634 | 0.028834 | -0.002463 | 0.10668 | 0.000352 | 0.003517 | -0.020443 | 0.004903 | -0.006022 | 0.010557 | 0.01798 | 0.003559 | 0.020795 | 0.006374
5858.0938 | 122.8043 | -0.10529 | 122.7814 | 0.13559 | -0.058836 | -0.034893 | -0.038752 | 0.017953 | 0.067269 | -0.067295 | -0.052818 | 0.060902 | -0.040846 | -0.042259 | -0.066219 | -0.031717 | -0.042641 | -0.035219 | 0.24087 | 0.04645 | 0.070393 | 0.066534 | 0.12324 | 0.17256 | 0.037991 | -0.007042 | 0.10668 | 0.00493 | 0.003517 | -0.020443 | 0.014059 | 0.003135 | 0.010557 | 0.013401 | -0.010177 | 0.025373 | 0.001795
5859.875 | 122.8775 | -0.068665 | 122.7631 | 0.13101 | -0.058836 | -0.034893 | -0.034174 | 0.013375 | 0.067269 | -0.062717 | -0.052818 | 0.065481 | -0.045424 | -0.03768 | -0.057062 | -0.031717 | -0.042641 | -0.026063 | 0.19967 | 0.009829 | 0.033772 | 0.034491 | 0.08204 | 0.13593 | 0.005948 | -0.007042 | 0.11126 | 0.000352 | 0.008096 | -0.011286 | 0.014059 | 0.003135 | 0.019713 | 0.004244 | -0.010177 | 0.011638 | -0.002783
5861.5781 | 122.8317 | -0.11902 | 122.7905 | 0.13559 | -0.058836 | -0.030314 | -0.034174 | 0.017953 | 0.058113 | -0.067295 | -0.052818 | 0.07006 | -0.040846 | -0.042259 | -0.061641 | -0.031717 | -0.04722 | -0.030641 | 0.25461 | 0.060183 | 0.088705 | 0.084845 | 0.13697 | 0.17713 | 0.051724 | -0.007042 | 0.11584 | 0.00493 | 0.003517 | -0.015865 | 0.014059 | -0.001444 | 0.015135 | 0.008823 | -0.005598 | 0.020795 | 0.006374
5863.3438 | 122.8546 | -0.09613 | 122.7905 | 0.13559 | -0.054257 | -0.034893 | -0.029595 | 0.008797 | 0.067269 | -0.067295 | -0.048239 | 0.060902 | -0.040846 | -0.033101 | -0.066219 | -0.022561 | -0.042641 | -0.026063 | 0.23172 | 0.041873 | 0.061237 | 0.066535 | 0.10493 | 0.1634 | 0.028835 | -0.002463 | 0.10668 | 0.00493 | 0.012675 | -0.020443 | 0.023215 | 0.003135 | 0.019713 | 0.01798 | -0.005598 | 0.025373 | 0.001795
5865.0625 | 122.8134 | -0.10071 | 122.7905 | 0.13101 | -0.054257 | -0.034893 | -0.034174 | 0.017953 | 0.058113 | -0.058139 | -0.043661 | 0.07006 | -0.040846 | -0.03768 | -0.061641 | -0.022561 | -0.042641 | -0.030641 | 0.23172 | 0.046451 | 0.065815 | 0.066534 | 0.11866 | 0.15882 | 0.042569 | 0.002115 | 0.11584 | 0.00493 | 0.008096 | -0.015865 | 0.023215 | 0.003135 | 0.015135 | 0.01798 | -0.00102 | 0.020795 | 0.001795
5866.8281 | 122.8088 | -0.11902 | 122.7951 | 0.13101 | -0.054257 | -0.030314 | -0.034174 | 0.013375 | 0.062691 | -0.062717 | -0.048239 | 0.065481 | -0.050002 | -0.03768 | -0.057062 | -0.027139 | -0.04722 | -0.030641 | 0.25003 | 0.064762 | 0.088705 | 0.084845 | 0.13239 | 0.18171 | 0.056302 | -0.002463 | 0.11126 | -0.004226 | 0.008096 | -0.011286 | 0.018637 | -0.001444 | 0.015135 | 0.008823 | -0.001019 | 0.00706 | -0.002782
5868.6094 | 122.818 | -0.11444 | 122.7997 | 0.13559 | -0.049678 | -0.025735 | -0.034174 | 0.013375 | 0.053534 | -0.062717 | -0.048239 | 0.060902 | -0.036267 | -0.03768 | -0.070797 | -0.031717 | -0.042641 | -0.030641 | 0.25003 | 0.064763 | 0.088706 | 0.080267 | 0.12782 | 0.16797 | 0.051724 | -0.002463 | 0.10668 | 0.009509 | 0.008096 | -0.025021 | 0.014059 | 0.003135 | 0.015135 | 0.022558 | -0.005598 | 0.03453 | 0.006374
5870.3438 | 122.8363 | -0.10071 | 122.8043 | 0.13101 | -0.058836 | -0.030314 | -0.029595 | 0.013375 | 0.058113 | -0.067295 | -0.048239 | 0.060902 | -0.040846 | -0.033101 | -0.061641 | -0.027139 | -0.04722 | -0.035219 | 0.23172 | 0.041872 | 0.070394 | 0.071113 | 0.11408 | 0.15882 | 0.033413 | -0.002463 | 0.10668 | 0.00493 | 0.012675 | -0.015865 | 0.018637 | -0.001444 | 0.010557 | 0.013402 | -0.001019 | 0.020795 | 0.006374
5872.125 | 122.8363 | -0.10529 | 122.7768 | 0.13559 | -0.058836 | -0.034893 | -0.034174 | 0.017953 | 0.062691 | -0.071874 | -0.048239 | 0.060902 | -0.045424 | -0.03768 | -0.066219 | -0.036295 | -0.04722 | -0.035219 | 0.24087 | 0.04645 | 0.070393 | 0.071112 | 0.12324 | 0.16798 | 0.033412 | -0.002463 | 0.10668 | 0.000352 | 0.008096 | -0.020443 | 0.009481 | -0.001444 | 0.010557 | 0.01798 | -0.001019 | 0.020795 | 0.001796
5873.9062 | 122.8226 | -0.11444 | 122.7814 | 0.14017 | -0.054257 | -0.034893 | -0.029595 | 0.022531 | 0.058113 | -0.071874 | -0.043661 | 0.060902 | -0.050002 | -0.042259 | -0.061641 | -0.027139 | -0.04722 | -0.035219 | 0.25461 | 0.060184 | 0.079548 | 0.084846 | 0.13697 | 0.17255 | 0.042567 | 0.002115 | 0.10668 | -0.004226 | 0.003517 | -0.015865 | 0.018637 | -0.001444 | 0.010557 | 0.01798 | 0.003559 | 0.011639 | -0.002782
5875.6875 | 122.905 | -0.082397 | 122.7448 | 0.13101 | -0.054257 | -0.034893 | -0.029595 | 0.013375 | 0.053534 | -0.076452 | -0.043661 | 0.060902 | -0.045424 | -0.03768 | -0.061641 | -0.027139 | -0.038063 | -0.035219 | 0.21341 | 0.02814 | 0.047504 | 0.052802 | 0.095772 | 0.13593 | 0.005945 | 0.002115 | 0.10668 | 0.000352 | 0.008096 | -0.015865 | 0.018637 | 0.007713 | 0.010557 | 0.01798 | -0.005598 | 0.016217 | -0.007361
5877.4688 | 122.9324 | -0.059509 | 122.7722 | 0.12643 | -0.054257 | -0.034893 | -0.034174 | 0.013375 | 0.062691 | -0.067295 | -0.048239 | 0.065481 | -0.045424 | -0.046838 | -0.061641 | -0.027139 | -0.042641 | -0.026063 | 0.18594 | 0.005252 | 0.024616 | 0.025335 | 0.072884 | 0.1222 | -0.007786 | -0.002463 | 0.11126 | 0.000352 | -0.001062 | -0.015865 | 0.018637 | 0.003135 | 0.019713 | 0.013402 | -0.005598 | 0.016217 | -0.002783
5879.1875 | 122.8683 | -0.086975 | 122.7768 | 0.13559 | -0.054257 | -0.034893 | -0.029595 | 0.022531 | 0.071848 | -0.062717 | -0.043661 | 0.065481 | -0.045424 | -0.03768 | -0.057062 | -0.036295 | -0.04722 | -0.030641 | 0.22256 | 0.032718 | 0.052082 | 0.05738 | 0.10951 | 0.15882 | 0.024258 | 0.002115 | 0.11126 | 0.000352 | 0.008096 | -0.011286 | 0.009481 | -0.001444 | 0.015135 | 0.013401 | 0.003559 | 0.011638 | 0.001796
5880.9688 | 122.8455 | -0.073242 | 122.7814 | 0.13101 | -0.058836 | -0.030314 | -0.025017 | 0.017953 | 0.067269 | -0.062717 | -0.048239 | 0.060902 | -0.036267 | -0.03768 | -0.061641 | -0.027139 | -0.04722 | -0.030641 | 0.20425 | 0.014406 | 0.042928 | 0.048225 | 0.091195 | 0.14051 | 0.010525 | -0.002463 | 0.10668 | 0.009509 | 0.008096 | -0.015865 | 0.018637 | -0.001444 | 0.015135 | 0.013402 | -0.001019 | 0.025374 | 0.010953
5882.7656 | 122.8592 | -0.091553 | 122.7539 | 0.12643 | -0.054257 | -0.034893 | -0.029595 | 0.008797 | 0.058113 | -0.071874 | -0.052818 | 0.065481 | -0.050002 | -0.03768 | -0.061641 | -0.027139 | -0.04722 | -0.035219 | 0.21798 | 0.037296 | 0.05666 | 0.061958 | 0.10035 | 0.14967 | 0.019679 | -0.007042 | 0.11126 | -0.004226 | 0.008096 | -0.015865 | 0.018637 | -0.001444 | 0.010557 | 0.008823 | -0.005598 | 0.011639 | -0.002782
5884.4844 | 122.9324 | -0.054932 | 122.7448 | 0.13101 | -0.054257 | -0.034893 | -0.029595 | 0.008797 | 0.053534 | -0.058139 | -0.052818 | 0.07006 | -0.031689 | -0.046838 | -0.061641 | -0.031717 | -0.042641 | -0.026063 | 0.18594 | 0.000675 | 0.020039 | 0.025337 | 0.063729 | 0.10847 | -0.003207 | -0.007042 | 0.11584 | 0.014087 | -0.001062 | -0.015865 | 0.014059 | 0.003135 | 0.019713 | 0.008823 | -0.010177 | 0.029952 | 0.010952
5886.2656 | 122.9279 | -0.059509 | 122.7631 | 0.13101 | -0.058836 | -0.030314 | -0.029595 | 0.013375 | 0.062691 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.066219 | -0.036295 | -0.051798 | -0.035219 | 0.19052 | 0.000673 | 0.029195 | 0.029914 | 0.072884 | 0.1222 | -0.003208 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.020443 | 0.009481 | -0.006022 | 0.010557 | 0.01798 | 0.003559 | 0.025373 | 0.010952
5888.0469 | 122.8592 | -0.086975 | 122.7814 | 0.13101 | -0.063415 | -0.030314 | -0.034174 | 0.013375 | 0.067269 | -0.062717 | -0.052818 | 0.07006 | -0.045424 | -0.042259 | -0.066219 | -0.031717 | -0.051798 | -0.026063 | 0.21798 | 0.02356 | 0.056661 | 0.052801 | 0.10035 | 0.15424 | 0.024258 | -0.007042 | 0.11584 | 0.000352 | 0.003517 | -0.020443 | 0.014059 | -0.006022 | 0.019713 | 0.013401 | -0.00102 | 0.020795 | 0.006374
5889.7656 | 122.9553 | -0.07782 | 122.7356 | 0.13101 | -0.054257 | -0.030314 | -0.038752 | 0.008797 | 0.058113 | -0.071874 | -0.043661 | 0.07006 | -0.050002 | -0.03768 | -0.061641 | -0.036295 | -0.04722 | -0.035219 | 0.20883 | 0.023563 | 0.047506 | 0.039068 | 0.086617 | 0.13593 | 0.005946 | 0.002115 | 0.11584 | -0.004226 | 0.008096 | -0.015865 | 0.009481 | -0.001444 | 0.010557 | 0.01798 | 0.003559 | 0.011639 | -0.002782
5891.5469 | 122.9736 | -0.068665 | 122.7676 | 0.13101 | -0.058836 | -0.034893 | -0.029595 | 0.017953 | 0.071848 | -0.067295 | -0.048239 | 0.065481 | -0.045424 | -0.03768 | -0.066219 | -0.036295 | -0.042641 | -0.030641 | 0.19967 | 0.009829 | 0.033772 | 0.03907 | 0.086618 | 0.14051 | 0.00137 | -0.002463 | 0.11126 | 0.000352 | 0.008096 | -0.020443 | 0.009481 | 0.003135 | 0.015135 | 0.01798 | -0.005598 | 0.020795 | -0.002783
5893.3281 | 122.8546 | -0.11902 | 122.8134 | 0.13101 | -0.058836 | -0.034893 | -0.029595 | 0.017953 | 0.062691 | -0.058139 | -0.048239 | 0.060902 | -0.045424 | -0.03768 | -0.066219 | -0.031717 | -0.04722 | -0.035219 | 0.25003 | 0.060183 | 0.084126 | 0.089424 | 0.13697 | 0.18171 | 0.06088 | -0.002463 | 0.10668 | 0.000352 | 0.008096 | -0.020443 | 0.014059 | -0.001444 | 0.010557 | 0.01798 | -0.001019 | 0.020795 | 0.001796
5895.1094 | 122.9553 | -0.073242 | 122.7539 | 0.13101 | -0.058836 | -0.034893 | -0.029595 | 0.013375 | 0.062691 | -0.062717 | -0.048239 | 0.07006 | -0.040846 | -0.042259 | -0.057062 | -0.031717 | -0.042641 | -0.035219 | 0.20425 | 0.014406 | 0.038349 | 0.043647 | 0.086617 | 0.13593 | 0.010525 | -0.002463 | 0.11584 | 0.00493 | 0.003517 | -0.011286 | 0.014059 | 0.003135 | 0.010557 | 0.008823 | -0.005598 | 0.016216 | 0.001795
5896.875 | 122.8867 | -0.086975 | 122.7585 | 0.13559 | -0.058836 | -0.030314 | -0.025017 | 0.017953 | 0.058113 | -0.062717 | -0.048239 | 0.07006 | -0.045424 | -0.046838 | -0.061641 | -0.031717 | -0.04722 | -0.030641 | 0.22256 | 0.028139 | 0.056661 | 0.061958 | 0.10493 | 0.14509 | 0.024258 | -0.002463 | 0.11584 | 0.000352 | -0.001062 | -0.015865 | 0.014059 | -0.001444 | 0.015135 | 0.013402 | -0.001019 | 0.016217 | 0.001796
5898.5938 | 122.8271 | -0.10071 | 122.7905 | 0.13101 | -0.054257 | -0.030314 | -0.029595 | 0.013375 | 0.048956 | -0.062717 | -0.052818 | 0.060902 | -0.036267 | -0.051417 | -0.061641 | -0.031717 | -0.04722 | -0.035219 | 0.23172 | 0.046451 | 0.070394 | 0.071113 | 0.11408 | 0.14966 | 0.037991 | -0.007042 | 0.10668 | 0.009509 | -0.005641 | -0.015865 | 0.014059 | -0.001444 | 0.010557 | 0.008823 | -0.005598 | 0.025374 | 0.010953
5900.3906 | 122.818 | -0.10986 | 122.8043 | 0.13101 | -0.058836 | -0.030314 | -0.029595 | 0.022531 | 0.058113 | -0.058139 | -0.048239 | 0.065481 | -0.050002 | -0.03768 | -0.061641 | -0.040873 | -0.051798 | -0.030641 | 0.24087 | 0.051027 | 0.079549 | 0.080268 | 0.13239 | 0.16798 | 0.051724 | -0.002463 | 0.11126 | -0.004226 | 0.008096 | -0.015865 | 0.004903 | -0.006022 | 0.015135 | 0.013402 | 0.003559 | 0.011639 | 0.001796
5902.1719 | 122.9004 | -0.07782 | 122.7631 | 0.13559 | -0.049678 | -0.034893 | -0.038752 | 0.013375 | 0.058113 | -0.062717 | -0.043661 | 0.060902 | -0.036267 | -0.046838 | -0.061641 | -0.031717 | -0.042641 | -0.035219 | 0.21341 | 0.028142 | 0.042927 | 0.039068 | 0.091195 | 0.13593 | 0.015103 | 0.002115 | 0.10668 | 0.009509 | -0.001062 | -0.015865 | 0.014059 | 0.003135 | 0.010557 | 0.01798 | -0.00102 | 0.025374 | 0.006374
5903.8906 | 122.9736 | -0.064087 | 122.7722 | 0.12643 | -0.054257 | -0.025735 | -0.029595 | 0.013375 | 0.062691 | -0.071874 | -0.052818 | 0.060902 | -0.031689 | -0.03768 | -0.061641 | -0.027139 | -0.042641 | -0.030641 | 0.19052 | 0.00983 | 0.038352 | 0.034492 | 0.077462 | 0.12678 | -0.007787 | -0.007042 | 0.10668 | 0.014087 | 0.008096 | -0.015865 | 0.018637 | 0.003135 | 0.015135 | 0.008823 | -0.010177 | 0.029952 | 0.010952
5905.6719 | 122.8592 | -0.10529 | 122.8226 | 0.13101 | -0.054257 | -0.034893 | -0.034174 | 0.017953 | 0.067269 | -0.062717 | -0.043661 | 0.065481 | -0.045424 | -0.028522 | -0.061641 | -0.031717 | -0.042641 | -0.026063 | 0.23629 | 0.051029 | 0.070393 | 0.071112 | 0.12324 | 0.17256 | 0.042569 | 0.002115 | 0.11126 | 0.000352 | 0.017254 | -0.015865 | 0.014059 | 0.003135 | 0.019713 | 0.01798 | -0.00102 | 0.016217 | -0.002783
5907.4531 | 122.8271 | -0.10071 | 122.7997 | 0.12643 | -0.058836 | -0.030314 | -0.025017 | 0.017953 | 0.067269 | -0.067295 | -0.048239 | 0.065481 | -0.045424 | -0.046838 | -0.066219 | -0.031717 | -0.04722 | -0.026063 | 0.22714 | 0.041872 | 0.070394 | 0.075691 | 0.11866 | 0.16798 | 0.033413 | -0.002463 | 0.11126 | 0.000352 | -0.001062 | -0.020443 | 0.014059 | -0.001444 | 0.019713 | 0.01798 | -0.001019 | 0.020795 | 0.001796
5909.1719 | 122.8226 | -0.1236 | 122.8134 | 0.13101 | -0.058836 | -0.025735 | -0.038752 | 0.017953 | 0.067269 | -0.067295 | -0.052818 | 0.065481 | -0.045424 | -0.03768 | -0.066219 | -0.027139 | -0.04722 | -0.035219 | 0.2546 | 0.06476 | 0.097861 | 0.084844 | 0.14155 | 0.19087 | 0.056301 | -0.007042 | 0.11126 | 0.000352 | 0.008096 | -0.020443 | 0.018637 | -0.001444 | 0.010557 | 0.013401 | -0.005598 | 0.020795 | 0.001796
5910.9531 | 122.9553 | -0.07782 | 122.7493 | 0.12643 | -0.058836 | -0.030314 | -0.034174 | 0.008797 | 0.062691 | -0.067295 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.061641 | -0.027139 | -0.051798 | -0.030641 | 0.20425 | 0.018984 | 0.047506 | 0.043646 | 0.086617 | 0.14051 | 0.010525 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.015865 | 0.018637 | -0.006022 | 0.015135 | 0.013402 | 0.003559 | 0.020795 | 0.010952
5912.7344 | 122.818 | -0.10071 | 122.8271 | 0.13101 | -0.058836 | -0.030314 | -0.025017 | 0.008797 | 0.067269 | -0.062717 | -0.043661 | 0.065481 | -0.045424 | -0.042259 | -0.066219 | -0.036295 | -0.056376 | -0.030641 | 0.23172 | 0.041872 | 0.070394 | 0.075691 | 0.10951 | 0.16798 | 0.037991 | 0.002115 | 0.11126 | 0.000352 | 0.003517 | -0.020443 | 0.009481 | -0.0106 | 0.015135 | 0.022558 | 0.012715 | 0.020795 | 0.010952
5914.4531 | 122.8683 | -0.082397 | 122.7539 | 0.13559 | -0.049678 | -0.034893 | -0.029595 | 0.017953 | 0.062691 | -0.071874 | -0.043661 | 0.065481 | -0.040846 | -0.042259 | -0.061641 | -0.036295 | -0.04722 | -0.030641 | 0.21798 | 0.032719 | 0.047504 | 0.052802 | 0.10035 | 0.14509 | 0.010523 | 0.002115 | 0.11126 | 0.00493 | 0.003517 | -0.015865 | 0.009481 | -0.001444 | 0.015135 | 0.01798 | 0.003559 | 0.020795 | 0.006374
5916.2344 | 122.9507 | -0.07782 | 122.7448 | 0.12643 | -0.063415 | -0.034893 | -0.029595 | 0.004219 | 0.058113 | -0.067295 | -0.043661 | 0.065481 | -0.040846 | -0.046838 | -0.061641 | -0.040873 | -0.04722 | -0.035219 | 0.20425 | 0.014405 | 0.042927 | 0.048225 | 0.082039 | 0.13593 | 0.010525 | 0.002115 | 0.11126 | 0.00493 | -0.001062 | -0.015865 | 0.004903 | -0.001444 | 0.010557 | 0.01798 | 0.003559 | 0.020795 | 0.006374
5917.9531 | 122.8683 | -0.11902 | 122.7997 | 0.13559 | -0.054257 | -0.030314 | -0.029595 | 0.017953 | 0.062691 | -0.058139 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.057062 | -0.036295 | -0.051798 | -0.030641 | 0.25461 | 0.064762 | 0.088705 | 0.089424 | 0.13697 | 0.18171 | 0.06088 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.011286 | 0.009481 | -0.006022 | 0.015135 | 0.008823 | 0.003559 | 0.016216 | 0.010952
5919.75 | 122.9645 | -0.068665 | 122.7722 | 0.12643 | -0.058836 | -0.030314 | -0.029595 | 0.008797 | 0.058113 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.042259 | -0.066219 | -0.031717 | -0.04722 | -0.035219 | 0.19509 | 0.009829 | 0.038351 | 0.03907 | 0.077462 | 0.12678 | 0.005948 | -0.002463 | 0.11126 | 0.00493 | 0.003517 | -0.020443 | 0.014059 | -0.001444 | 0.010557 | 0.01798 | -0.001019 | 0.025373 | 0.006374
5921.5312 | 122.9141 | -0.068665 | 122.8043 | 0.13101 | -0.058836 | -0.025735 | -0.034174 | 0.008797 | 0.058113 | -0.067295 | -0.052818 | 0.060902 | -0.040846 | -0.042259 | -0.057062 | -0.040873 | -0.04722 | -0.026063 | 0.19967 | 0.009829 | 0.04293 | 0.034491 | 0.077462 | 0.12678 | 0.00137 | -0.007042 | 0.10668 | 0.00493 | 0.003517 | -0.011286 | 0.004903 | -0.001444 | 0.019713 | 0.004244 | -0.005598 | 0.016216 | 0.006374
5923.25 | 122.818 | -0.1236 | 122.7997 | 0.13101 | -0.054257 | -0.030314 | -0.034174 | 0.022531 | 0.058113 | -0.058139 | -0.048239 | 0.065481 | -0.045424 | -0.033101 | -0.057062 | -0.036295 | -0.04722 | -0.035219 | 0.2546 | 0.069339 | 0.093282 | 0.089422 | 0.14613 | 0.18171 | 0.065457 | -0.002463 | 0.11126 | 0.000352 | 0.012675 | -0.011286 | 0.009481 | -0.001444 | 0.010557 | 0.008823 | -0.001019 | 0.011638 | 0.001796
5925.0312 | 122.9095 | -0.068665 | 122.7768 | 0.12643 | -0.049678 | -0.030314 | -0.038752 | 0.013375 | 0.053534 | -0.076452 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.061641 | -0.036295 | -0.042641 | -0.030641 | 0.19509 | 0.018987 | 0.038351 | 0.029913 | 0.08204 | 0.1222 | -0.007787 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.015865 | 0.009481 | 0.003135 | 0.015135 | 0.013402 | -0.005598 | 0.020795 | 0.001795
5926.8125 | 122.8638 | -0.10071 | 122.7768 | 0.12643 | -0.063415 | -0.034893 | -0.029595 | 0.013375 | 0.067269 | -0.067295 | -0.052818 | 0.060902 | -0.045424 | -0.042259 | -0.057062 | -0.040873 | -0.051798 | -0.035219 | 0.22714 | 0.037293 | 0.065815 | 0.071113 | 0.11408 | 0.16798 | 0.033413 | -0.007042 | 0.10668 | 0.000352 | 0.003517 | -0.011286 | 0.004903 | -0.006022 | 0.010557 | 0.004244 | -0.00102 | 0.011638 | 0.006374
5928.5312 | 122.8638 | -0.11444 | 122.7997 | 0.14017 | -0.054257 | -0.021157 | -0.029595 | 0.013375 | 0.067269 | -0.067295 | -0.048239 | 0.060902 | -0.045424 | -0.042259 | -0.066219 | -0.027139 | -0.04722 | -0.026063 | 0.25461 | 0.060184 | 0.093284 | 0.084846 | 0.12782 | 0.18171 | 0.047146 | -0.002463 | 0.10668 | 0.000352 | 0.003517 | -0.020443 | 0.018637 | -0.001444 | 0.019713 | 0.01798 | -0.001019 | 0.020795 | 0.001796
5930.3125 | 122.9462 | -0.059509 | 122.7631 | 0.13559 | -0.054257 | -0.030314 | -0.038752 | 0.008797 | 0.067269 | -0.067295 | -0.048239 | 0.07006 | -0.036267 | -0.03768 | -0.057062 | -0.040873 | -0.051798 | -0.030641 | 0.1951 | 0.005252 | 0.029195 | 0.020757 | 0.068306 | 0.12678 | -0.007786 | -0.002463 | 0.11584 | 0.009509 | 0.008096 | -0.011286 | 0.004903 | -0.006022 | 0.015135 | 0.008823 | 0.003559 | 0.020795 | 0.015531
5932.0938 | 122.905 | -0.073242 | 122.7722 | 0.12643 | -0.054257 | -0.025735 | -0.025017 | 0.013375 | 0.071848 | -0.058139 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.070797 | -0.036295 | -0.04722 | -0.030641 | 0.19967 | 0.018985 | 0.047507 | 0.048225 | 0.086617 | 0.14509 | 0.015103 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.025021 | 0.009481 | -0.001444 | 0.015135 | 0.022558 | -0.001019 | 0.029951 | 0.006374
5933.8906 | 122.8317 | -0.10071 | 122.8134 | 0.13101 | -0.054257 | -0.034893 | -0.029595 | 0.017953 | 0.053534 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.042259 | -0.061641 | -0.036295 | -0.051798 | -0.035219 | 0.23172 | 0.046451 | 0.065815 | 0.071113 | 0.11866 | 0.15424 | 0.037991 | -0.002463 | 0.11126 | 0.00493 | 0.003517 | -0.015865 | 0.009481 | -0.006022 | 0.010557 | 0.013402 | 0.003559 | 0.020795 | 0.010952
5935.6094 | 122.9691 | -0.054932 | 122.7814 | 0.13559 | -0.058836 | -0.030314 | -0.034174 | 0.013375 | 0.067269 | -0.067295 | -0.043661 | 0.056323 | -0.045424 | -0.03768 | -0.061641 | -0.036295 | -0.04722 | -0.030641 | 0.19052 | -0.003904 | 0.024618 | 0.020758 | 0.068307 | 0.1222 | -0.012363 | 0.002115 | 0.1021 | 0.000352 | 0.008096 | -0.015865 | 0.009481 | -0.001444 | 0.015135 | 0.01798 | 0.003559 | 0.016217 | 0.001796
5937.375 | 122.8455 | -0.10986 | 122.7814 | 0.12643 | -0.054257 | -0.030314 | -0.029595 | 0.013375 | 0.062691 | -0.062717 | -0.043661 | 0.060902 | -0.040846 | -0.042259 | -0.057062 | -0.027139 | -0.042641 | -0.030641 | 0.23629 | 0.055606 | 0.079549 | 0.080268 | 0.12324 | 0.17255 | 0.047146 | 0.002115 | 0.10668 | 0.00493 | 0.003517 | -0.011286 | 0.018637 | 0.003135 | 0.015135 | 0.013401 | -0.00102 | 0.016216 | 0.001795
5939.1094 | 122.8088 | -0.13275 | 122.8317 | 0.13101 | -0.058836 | -0.030314 | -0.025017 | 0.013375 | 0.062691 | -0.058139 | -0.052818 | 0.065481 | -0.036267 | -0.051417 | -0.070797 | -0.031717 | -0.042641 | -0.030641 | 0.26376 | 0.073915 | 0.10244 | 0.10773 | 0.14613 | 0.19544 | 0.074612 | -0.007042 | 0.11126 | 0.009509 | -0.005641 | -0.025021 | 0.014059 | 0.003135 | 0.015135 | 0.017979 | -0.010177 | 0.03453 | 0.006374
5940.8906 | 122.8638 | -0.10071 | 122.8271 | 0.13559 | -0.054257 | -0.030314 | -0.029595 | 0.017953 | 0.058113 | -0.062717 | -0.039082 | 0.060902 | -0.040846 | -0.03768 | -0.057062 | -0.040873 | -0.051798 | -0.035219 | 0.23629 | 0.046451 | 0.070394 | 0.071113 | 0.11866 | 0.15882 | 0.037991 | 0.006694 | 0.10668 | 0.00493 | 0.008096 | -0.011286 | 0.004903 | -0.006022 | 0.010557 | 0.01798 | 0.012716 | 0.016216 | 0.010952
5942.6719 | 122.9095 | -0.091553 | 122.7905 | 0.13559 | -0.054257 | -0.034893 | -0.029595 | 0.008797 | 0.062691 | -0.062717 | -0.043661 | 0.060902 | -0.040846 | -0.03768 | -0.057062 | -0.027139 | -0.042641 | -0.035219 | 0.22714 | 0.037296 | 0.05666 | 0.061958 | 0.10035 | 0.15424 | 0.028836 | 0.002115 | 0.10668 | 0.00493 | 0.008096 | -0.011286 | 0.018637 | 0.003135 | 0.010557 | 0.013401 | -0.00102 | 0.016216 | 0.001795
5944.3906 | 122.8043 | -0.11444 | 122.7951 | 0.13559 | -0.058836 | -0.034893 | -0.034174 | 0.013375 | 0.058113 | -0.062717 | -0.052818 | 0.065481 | -0.040846 | -0.042259 | -0.061641 | -0.031717 | -0.056376 | -0.035219 | 0.25003 | 0.055605 | 0.079548 | 0.080267 | 0.12782 | 0.17255 | 0.051724 | -0.007042 | 0.11126 | 0.00493 | 0.003517 | -0.015865 | 0.014059 | -0.0106 | 0.010557 | 0.008823 | 0.003558 | 0.020795 | 0.01553
5946.1719 | 122.8912 | -0.10071 | 122.8043 | 0.13101 | -0.058836 | -0.030314 | -0.029595 | 0.013375 | 0.058113 | -0.062717 | -0.048239 | 0.07006 | -0.036267 | -0.042259 | -0.057062 | -0.031717 | -0.04722 | -0.030641 | 0.23172 | 0.041872 | 0.070394 | 0.071113 | 0.11408 | 0.15882 | 0.037991 | -0.002463 | 0.11584 | 0.009509 | 0.003517 | -0.011286 | 0.014059 | -0.001444 | 0.015135 | 0.008823 | -0.001019 | 0.020795 | 0.010953
5947.9531 | 122.8455 | -0.11902 | 122.7859 | 0.13101 | -0.063415 | -0.030314 | -0.029595 | 0.013375 | 0.058113 | -0.067295 | -0.048239 | 0.060902 | -0.036267 | -0.051417 | -0.057062 | -0.036295 | -0.04722 | -0.026063 | 0.25003 | 0.055604 | 0.088705 | 0.089424 | 0.13239 | 0.17713 | 0.051724 | -0.002463 | 0.10668 | 0.009509 | -0.005641 | -0.011286 | 0.009481 | -0.001444 | 0.019713 | 0.008823 | -0.001019 | 0.020795 | 0.010953
5949.6875 | 122.9599 | -0.073242 | 122.7722 | 0.13101 | -0.0451 | -0.030314 | -0.029595 | 0.013375 | 0.062691 | -0.067295 | -0.052818 | 0.07006 | -0.045424 | -0.042259 | -0.061641 | -0.031717 | -0.04722 | -0.035219 | 0.20425 | 0.028142 | 0.042928 | 0.043647 | 0.086617 | 0.13593 | 0.005947 | -0.007042 | 0.11584 | 0.000352 | 0.003517 | -0.015865 | 0.014059 | -0.001444 | 0.010557 | 0.008823 | -0.005598 | 0.016217 | 0.001796
5951.4531 | 122.9553 | -0.073242 | 122.7905 | 0.13101 | -0.063415 | -0.034893 | -0.034174 | 0.013375 | 0.058113 | -0.062717 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.057062 | -0.031717 | -0.04722 | -0.026063 | 0.20425 | 0.009827 | 0.038349 | 0.039068 | 0.086617 | 0.13135 | 0.010525 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.011286 | 0.014059 | -0.001444 | 0.019713 | 0.008823 | -0.001019 | 0.016216 | 0.006374
5953.2344 | 122.9004 | -0.10071 | 122.8134 | 0.13559 | -0.054257 | -0.030314 | -0.029595 | 0.013375 | 0.062691 | -0.067295 | -0.052818 | 0.060902 | -0.050002 | -0.03768 | -0.057062 | -0.027139 | -0.04722 | -0.035219 | 0.23629 | 0.046451 | 0.070394 | 0.071113 | 0.11408 | 0.1634 | 0.033413 | -0.007042 | 0.10668 | -0.004226 | 0.008096 | -0.011286 | 0.018637 | -0.001444 | 0.010557 | 0.004244 | -0.005598 | 0.00706 | -0.002782
5954.9531 | 122.8317 | -0.1236 | 122.7814 | 0.13559 | -0.054257 | -0.034893 | -0.034174 | 0.008797 | 0.062691 | -0.067295 | -0.052818 | 0.065481 | -0.050002 | -0.042259 | -0.066219 | -0.031717 | -0.04722 | -0.030641 | 0.25918 | 0.069339 | 0.088703 | 0.089422 | 0.13239 | 0.18629 | 0.056301 | -0.007042 | 0.11126 | -0.004226 | 0.003517 | -0.020443 | 0.014059 | -0.001444 | 0.015135 | 0.013401 | -0.005598 | 0.016217 | -0.002782
5956.6719 | 122.8775 | -0.09613 | 122.7814 | 0.13559 | -0.058836 | -0.030314 | -0.034174 | 0.008797 | 0.062691 | -0.067295 | -0.052818 | 0.07006 | -0.050002 | -0.03768 | -0.061641 | -0.036295 | -0.042641 | -0.035219 | 0.23172 | 0.037294 | 0.065816 | 0.061956 | 0.10493 | 0.15882 | 0.028835 | -0.007042 | 0.11584 | -0.004226 | 0.008096 | -0.015865 | 0.009481 | 0.003135 | 0.010557 | 0.008823 | -0.010177 | 0.011639 | -0.007361
5958.4375 | 122.9645 | -0.059509 | 122.7951 | 0.13559 | -0.063415 | -0.030314 | -0.034174 | 0.013375 | 0.058113 | -0.062717 | -0.048239 | 0.065481 | -0.036267 | -0.03768 | -0.066219 | -0.031717 | -0.033484 | -0.026063 | 0.1951 | -0.003906 | 0.029195 | 0.025335 | 0.072884 | 0.11762 | -0.003208 | -0.002463 | 0.11126 | 0.009509 | 0.008096 | -0.020443 | 0.014059 | 0.012292 | 0.019713 | 0.01798 | -0.014755 | 0.029952 | -0.002783
5960.2188 | 122.8775 | -0.086975 | 122.8043 | 0.13101 | -0.063415 | -0.030314 | -0.025017 | 0.013375 | 0.058113 | -0.067295 | -0.043661 | 0.060902 | -0.045424 | -0.03768 | -0.057062 | -0.031717 | -0.038063 | -0.035219 | 0.21798 | 0.02356 | 0.056661 | 0.061958 | 0.10035 | 0.14509 | 0.01968 | 0.002115 | 0.10668 | 0.000352 | 0.008096 | -0.011286 | 0.014059 | 0.007713 | 0.010557 | 0.013401 | -0.005598 | 0.011638 | -0.007361
5961.9844 | 122.9004 | -0.091553 | 122.7905 | 0.13559 | -0.054257 | -0.030314 | -0.034174 | -0.000359 | 0.058113 | -0.067295 | -0.048239 | 0.060902 | -0.040846 | -0.03768 | -0.057062 | -0.040873 | -0.051798 | -0.030641 | 0.22714 | 0.037296 | 0.061239 | 0.057379 | 0.091194 | 0.14967 | 0.024258 | -0.002463 | 0.10668 | 0.00493 | 0.008096 | -0.011286 | 0.004903 | -0.006022 | 0.015135 | 0.008823 | 0.003559 | 0.016216 | 0.010952
5963.7031 | 122.9736 | -0.054932 | 122.7814 | 0.13101 | -0.054257 | -0.025735 | -0.034174 | 0.013375 | 0.058113 | -0.062717 | -0.052818 | 0.060902 | -0.045424 | -0.03768 | -0.061641 | -0.027139 | -0.042641 | -0.026063 | 0.18594 | 0.000675 | 0.029197 | 0.020758 | 0.068307 | 0.11305 | -0.007785 | -0.007042 | 0.10668 | 0.000352 | 0.008096 | -0.015865 | 0.018637 | 0.003135 | 0.019713 | 0.008823 | -0.010177 | 0.016217 | -0.002783
5965.5 | 122.9324 | -0.073242 | 122.7814 | 0.12643 | -0.063415 | -0.021157 | -0.034174 | 0.004219 | 0.058113 | -0.067295 | -0.048239 | 0.065481 | -0.040846 | -0.033101 | -0.066219 | -0.040873 | -0.04722 | -0.026063 | 0.19967 | 0.009827 | 0.052085 | 0.039068 | 0.077461 | 0.13135 | 0.005947 | -0.002463 | 0.11126 | 0.00493 | 0.012675 | -0.020443 | 0.004903 | -0.001444 | 0.019713 | 0.01798 | -0.001019 | 0.025373 | 0.006374
5967.2188 | 122.8455 | -0.11902 | 122.8134 | 0.13101 | -0.058836 | -0.034893 | -0.034174 | 0.008797 | 0.067269 | -0.058139 | -0.043661 | 0.065481 | -0.045424 | -0.042259 | -0.061641 | -0.036295 | -0.04722 | -0.030641 | 0.25003 | 0.060183 | 0.084126 | 0.084845 | 0.12782 | 0.18629 | 0.06088 | 0.002115 | 0.11126 | 0.000352 | 0.003517 | -0.015865 | 0.009481 | -0.001444 | 0.015135 | 0.01798 | 0.003559 | 0.016217 | 0.001796
5968.9844 | 122.8271 | -0.10529 | 122.8088 | 0.13559 | -0.063415 | -0.030314 | -0.038752 | 0.013375 | 0.058113 | -0.067295 | -0.048239 | 0.07006 | -0.040846 | -0.042259 | -0.066219 | -0.036295 | -0.042641 | -0.030641 | 0.24087 | 0.041871 | 0.074972 | 0.066534 | 0.11866 | 0.1634 | 0.037991 | -0.002463 | 0.11584 | 0.00493 | 0.003517 | -0.020443 | 0.009481 | 0.003135 | 0.015135 | 0.01798 | -0.005598 | 0.025373 | 0.001795
5970.7031 | 122.9324 | -0.082397 | 122.7859 | 0.13101 | -0.054257 | -0.030314 | -0.029595 | 0.017953 | 0.062691 | -0.071874 | -0.043661 | 0.065481 | -0.040846 | -0.03768 | -0.061641 | -0.027139 | -0.04722 | -0.026063 | 0.21341 | 0.02814 | 0.052083 | 0.052802 | 0.10035 | 0.14509 | 0.010523 | 0.002115 | 0.11126 | 0.00493 | 0.008096 | -0.015865 | 0.018637 | -0.001444 | 0.019713 | 0.01798 | 0.003559 | 0.020795 | 0.006374
5972.4844 | 122.85 | -0.10529 | 122.8134 | 0.13559 | -0.054257 | -0.034893 | -0.034174 | 0.013375 | 0.062691 | -0.062717 | -0.039082 | 0.060902 | -0.045424 | -0.028522 | -0.057062 | -0.031717 | -0.04722 | -0.044375 | 0.24087 | 0.051029 | 0.070393 | 0.071112 | 0.11866 | 0.16798 | 0.042569 | 0.006694 | 0.10668 | 0.000352 | 0.017254 | -0.011286 | 0.014059 | -0.001444 | 0.001401 | 0.01798 | 0.008138 | 0.011638 | 0.001796
5974.2031 | 122.8592 | -0.086975 | 122.8043 | 0.13101 | -0.058836 | -0.034893 | -0.038752 | 0.017953 | 0.071848 | -0.067295 | -0.052818 | 0.065481 | -0.040846 | -0.03768 | -0.066219 | -0.031717 | -0.042641 | -0.030641 | 0.21798 | 0.028139 | 0.052082 | 0.048223 | 0.10493 | 0.15882 | 0.01968 | -0.007042 | 0.11126 | 0.00493 | 0.008096 | -0.020443 | 0.014059 | 0.003135 | 0.015135 | 0.013401 | -0.010177 | 0.025373 | 0.001795
5976 | 122.9874 | -0.07782 | 122.8043 | 0.14017 | -0.058836 | -0.034893 | -0.029595 | 0.013375 | 0.058113 | -0.058139 | -0.048239 | 0.060902 | -0.031689 | -0.03768 | -0.057062 | -0.031717 | -0.04722 | -0.030641 | 0.21799 | 0.018984 | 0.042927 | 0.048225 | 0.091195 | 0.13593 | 0.019681 | -0.002463 | 0.10668 | 0.014087 | 0.008096 | -0.011286 | 0.014059 | -0.001444 | 0.015135 | 0.008823 | -0.001019 | 0.025373 | 0.015531
5977.7344 | 122.9279 | -0.068665 | 122.7951 | 0.13101 | -0.063415 | -0.025735 | -0.034174 | 0.013375 | 0.062691 | -0.058139 | -0.048239 | 0.060902 | -0.045424 | -0.03768 | -0.057062 | -0.027139 | -0.051798 | -0.035219 | 0.19967 | 0.00525 | 0.04293 | 0.034491 | 0.08204 | 0.13136 | 0.010526 | -0.002463 | 0.10668 | 0.000352 | 0.008096 | -0.011286 | 0.018637 | -0.006022 | 0.010557 | 0.008823 | 0.003559 | 0.011638 | 0.006374
5979.5156 | 122.905 | -0.073242 | 122.7997 | 0.13559 | -0.058836 | -0.030314 | -0.029595 | 0.017953 | 0.062691 | -0.062717 | -0.052818 | 0.07006 | -0.040846 | -0.033101 | -0.061641 | -0.036295 | -0.051798 | -0.039797 | 0.20883 | 0.014406 | 0.042928 | 0.043647 | 0.091195 | 0.13593 | 0.010525 | -0.007042 | 0.11584 | 0.00493 | 0.012675 | -0.015865 | 0.009481 | -0.006022 | 0.005979 | 0.008823 | -0.00102 | 0.020795 | 0.010952
5981.2969 | 122.937 | -0.064087 | 122.7814 | 0.13101 | -0.054257 | -0.030314 | -0.029595 | 0.013375 | 0.071848 | -0.067295 | -0.048239 | 0.060902 | -0.040846 | -0.03768 | -0.057062 | -0.031717 | -0.042641 | -0.026063 | 0.1951 | 0.00983 | 0.033773 | 0.034492 | 0.077462 | 0.13594 | -0.003208 | -0.002463 | 0.10668 | 0.00493 | 0.008096 | -0.011286 | 0.014059 | 0.003135 | 0.019713 | 0.008823 | -0.005598 | 0.016216 | 0.001795
5983.0781 | 122.8958 | -0.10071 | 122.8409 | 0.14017 | -0.058836 | -0.030314 | -0.034174 | 0.013375 | 0.053534 | -0.062717 | -0.048239 | 0.065481 | -0.05458 | -0.03768 | -0.066219 | -0.036295 | -0.060955 | -0.035219 | 0.24087 | 0.041872 | 0.070394 | 0.066534 | 0.11408 | 0.15424 | 0.037991 | -0.002463 | 0.11126 | -0.008804 | 0.008096 | -0.020443 | 0.009481 | -0.015179 | 0.010557 | 0.01798 | 0.012716 | 0.011639 | 0.006375
5984.7969 | 122.8363 | -0.1236 | 122.85 | 0.13101 | -0.049678 | -0.025735 | -0.034174 | 0.013375 | 0.058113 | -0.067295 | -0.043661 | 0.065481 | -0.045424 | -0.033101 | -0.057062 | -0.031717 | -0.04722 | -0.035219 | 0.2546 | 0.073918 | 0.097861 | 0.089422 | 0.13697 | 0.18171 | 0.056301 | 0.002115 | 0.11126 | 0.000352 | 0.012675 | -0.011286 | 0.014059 | -0.001444 | 0.010557 | 0.013401 | 0.003559 | 0.011638 | 0.001796
5986.5781 | 122.8867 | -0.10529 | 122.8271 | 0.13559 | -0.058836 | -0.034893 | -0.025017 | 0.013375 | 0.053534 | -0.062717 | -0.043661 | 0.065481 | -0.045424 | -0.042259 | -0.066219 | -0.031717 | -0.04722 | -0.026063 | 0.24087 | 0.04645 | 0.070393 | 0.080269 | 0.11866 | 0.15882 | 0.042569 | 0.002115 | 0.11126 | 0.000352 | 0.003517 | -0.020443 | 0.014059 | -0.001444 | 0.019713 | 0.022558 | 0.003559 | 0.020795 | 0.001796
5988.2969 | 122.9416 | -0.073242 | 122.8134 | 0.12643 | -0.049678 | -0.034893 | -0.034174 | 0.008797 | 0.053534 | -0.067295 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.066219 | -0.040873 | -0.042641 | -0.030641 | 0.19967 | 0.023564 | 0.038349 | 0.039068 | 0.082039 | 0.12678 | 0.005947 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.020443 | 0.004903 | 0.003135 | 0.015135 | 0.01798 | -0.005598 | 0.025373 | 0.001795
5990.0938 | 122.8729 | -0.11444 | 122.8088 | 0.12643 | -0.063415 | -0.025735 | -0.029595 | 0.017953 | 0.067269 | -0.062717 | -0.052818 | 0.060902 | -0.040846 | -0.028522 | -0.066219 | -0.031717 | -0.04722 | -0.026063 | 0.24087 | 0.051026 | 0.088706 | 0.084846 | 0.13239 | 0.18171 | 0.051724 | -0.007042 | 0.10668 | 0.00493 | 0.017254 | -0.020443 | 0.014059 | -0.001444 | 0.019713 | 0.013401 | -0.005598 | 0.025373 | 0.006374
5991.875 | 122.9141 | -0.086975 | 122.8088 | 0.13101 | -0.058836 | -0.025735 | -0.034174 | 0.017953 | 0.067269 | -0.071874 | -0.057396 | 0.060902 | -0.036267 | -0.042259 | -0.061641 | -0.027139 | -0.042641 | -0.035219 | 0.21798 | 0.028139 | 0.06124 | 0.052801 | 0.10493 | 0.15424 | 0.015101 | -0.01162 | 0.10668 | 0.009509 | 0.003517 | -0.015865 | 0.018637 | 0.003135 | 0.010557 | 0.004245 | -0.014755 | 0.025374 | 0.006374
5993.5938 | 122.8683 | -0.09613 | 122.8088 | 0.13101 | -0.058836 | -0.034893 | -0.034174 | 0.008797 | 0.058113 | -0.062717 | -0.043661 | 0.060902 | -0.036267 | -0.042259 | -0.061641 | -0.031717 | -0.051798 | -0.026063 | 0.22714 | 0.037294 | 0.061237 | 0.061956 | 0.10493 | 0.15424 | 0.033413 | 0.002115 | 0.10668 | 0.009509 | 0.003517 | -0.015865 | 0.014059 | -0.006022 | 0.019713 | 0.01798 | 0.008137 | 0.025374 | 0.015531
5995.375 | 122.9782 | -0.068665 | 122.7539 | 0.13559 | -0.063415 | -0.039471 | -0.029595 | 0.004219 | 0.048956 | -0.067295 | -0.052818 | 0.07006 | -0.036267 | -0.03768 | -0.061641 | -0.027139 | -0.042641 | -0.030641 | 0.20425 | 0.00525 | 0.029194 | 0.03907 | 0.072884 | 0.11762 | 0.00137 | -0.007042 | 0.11584 | 0.009509 | 0.008096 | -0.015865 | 0.018637 | 0.003135 | 0.015135 | 0.008823 | -0.010177 | 0.025374 | 0.006374
5997.1562 | 122.9004 | -0.10529 | 122.8271 | 0.13101 | -0.049678 | -0.030314 | -0.025017 | 0.013375 | 0.062691 | -0.067295 | -0.048239 | 0.056323 | -0.040846 | -0.042259 | -0.061641 | -0.027139 | -0.042641 | -0.021484 | 0.23629 | 0.055608 | 0.074972 | 0.080269 | 0.11866 | 0.16798 | 0.037991 | -0.002463 | 0.1021 | 0.00493 | 0.003517 | -0.015865 | 0.018637 | 0.003135 | 0.024292 | 0.013402 | -0.005598 | 0.020795 | 0.001795
5998.9375 | 122.85 | -0.11444 | 122.8226 | 0.13101 | -0.058836 | -0.030314 | -0.034174 | 0.013375 | 0.062691 | -0.062717 | -0.048239 | 0.060902 | -0.045424 | -0.046838 | -0.057062 | -0.031717 | -0.042641 | -0.035219 | 0.24545 | 0.055605 | 0.084127 | 0.080267 | 0.12782 | 0.17713 | 0.051724 | -0.002463 | 0.10668 | 0.000352 | -0.001062 | -0.011286 | 0.014059 | 0.003135 | 0.010557 | 0.008823 | -0.005598 | 0.011638 | -0.002783
6000.6562 | 122.9691 | -0.068665 | 122.7768 | 0.13101 | -0.063415 | -0.034893 | -0.038752 | 0.013375 | 0.062691 | -0.071874 | -0.048239 | 0.060902 | -0.040846 | -0.042259 | -0.057062 | -0.027139 | -0.04722 | -0.030641 | 0.19967 | 0.00525 | 0.033772 | 0.029913 | 0.08204 | 0.13136 | -0.003209 | -0.002463 | 0.10668 | 0.00493 | 0.003517 | -0.011286 | 0.018637 | -0.001444 | 0.015135 | 0.008823 | -0.001019 | 0.016216 | 0.006374
6002.4219 | 122.8912 | -0.10071 | 122.8088 | 0.12643 | -0.063415 | -0.025735 | -0.034174 | 0.013375 | 0.058113 | -0.062717 | -0.043661 | 0.065481 | -0.040846 | -0.042259 | -0.061641 | -0.031717 | -0.04722 | -0.021484 | 0.22714 | 0.037293 | 0.074973 | 0.066534 | 0.11408 | 0.15882 | 0.037991 | 0.002115 | 0.11126 | 0.00493 | 0.003517 | -0.015865 | 0.014059 | -0.001444 | 0.024292 | 0.01798 | 0.003559 | 0.020795 | 0.006374
6004.125 | 122.8775 | -0.09613 | 122.8455 | 0.13559 | -0.049678 | -0.030314 | -0.029595 | 0.017953 | 0.058113 | -0.067295 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.061641 | -0.027139 | -0.038063 | -0.026063 | 0.23172 | 0.046452 | 0.065816 | 0.066535 | 0.11408 | 0.15424 | 0.028835 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.015865 | 0.018637 | 0.007713 | 0.019713 | 0.013402 | -0.010176 | 0.020795 | -0.002783
6005.9062 | 122.9233 | -0.091553 | 122.8043 | 0.13101 | -0.058836 | -0.025735 | -0.029595 | 0.013375 | 0.058113 | -0.067295 | -0.048239 | 0.065481 | -0.045424 | -0.042259 | -0.057062 | -0.031717 | -0.042641 | -0.026063 | 0.22256 | 0.032717 | 0.065818 | 0.061958 | 0.10493 | 0.14967 | 0.024258 | -0.002463 | 0.11126 | 0.000352 | 0.003517 | -0.011286 | 0.014059 | 0.003135 | 0.019713 | 0.008823 | -0.005598 | 0.011638 | -0.002783
6007.625 | 122.9416 | -0.07782 | 122.7997 | 0.13101 | -0.063415 | -0.039471 | -0.038752 | 0.022531 | 0.062691 | -0.062717 | -0.039082 | 0.056323 | -0.036267 | -0.042259 | -0.061641 | -0.022561 | -0.04722 | -0.035219 | 0.20883 | 0.014405 | 0.038349 | 0.039068 | 0.10035 | 0.14051 | 0.015103 | 0.006694 | 0.1021 | 0.009509 | 0.003517 | -0.015865 | 0.023215 | -0.001444 | 0.010557 | 0.022559 | 0.008138 | 0.025374 | 0.010953
6009.3906 | 122.8867 | -0.11444 | 122.7997 | 0.13559 | -0.058836 | -0.025735 | -0.038752 | 0.013375 | 0.058113 | -0.067295 | -0.048239 | 0.065481 | -0.045424 | -0.033101 | -0.061641 | -0.027139 | -0.051798 | -0.030641 | 0.25003 | 0.055605 | 0.088706 | 0.075689 | 0.12782 | 0.17255 | 0.047146 | -0.002463 | 0.11126 | 0.000352 | 0.012675 | -0.015865 | 0.018637 | -0.006022 | 0.015135 | 0.013402 | 0.003559 | 0.016217 | 0.006374
6011.1719 | 122.9004 | -0.09613 | 122.7814 | 0.13101 | -0.058836 | -0.030314 | -0.034174 | 0.013375 | 0.062691 | -0.062717 | -0.048239 | 0.060902 | -0.045424 | -0.042259 | -0.061641 | -0.031717 | -0.04722 | -0.035219 | 0.22714 | 0.037294 | 0.065816 | 0.061956 | 0.1095 | 0.15882 | 0.033413 | -0.002463 | 0.10668 | 0.000352 | 0.003517 | -0.015865 | 0.014059 | -0.001444 | 0.010557 | 0.013402 | -0.001019 | 0.016217 | 0.001796
6012.9531 | 122.8867 | -0.10071 | 122.7905 | 0.13101 | -0.058836 | -0.025735 | -0.029595 | 0.013375 | 0.058113 | -0.067295 | -0.048239 | 0.07006 | -0.05458 | -0.03768 | -0.061641 | -0.027139 | -0.042641 | -0.035219 | 0.23172 | 0.041872 | 0.074973 | 0.071113 | 0.11408 | 0.15882 | 0.033413 | -0.002463 | 0.11584 | -0.008804 | 0.008096 | -0.015865 | 0.018637 | 0.003135 | 0.010557 | 0.013402 | -0.005598 | 0.007061 | -0.011939
6014.7188 | 122.8775 | -0.10071 | 122.818 | 0.12643 | -0.058836 | -0.030314 | -0.038752 | 0.008797 | 0.062691 | -0.062717 | -0.052818 | 0.065481 | -0.040846 | -0.042259 | -0.057062 | -0.027139 | -0.04722 | -0.030641 | 0.22714 | 0.041872 | 0.070394 | 0.061956 | 0.10951 | 0.1634 | 0.037991 | -0.007042 | 0.11126 | 0.00493 | 0.003517 | -0.011286 | 0.018637 | -0.001444 | 0.015135 | 0.004244 | -0.005598 | 0.016216 | 0.006374
6016.4375 | 122.8546 | -0.10529 | 122.818 | 0.12643 | -0.058836 | -0.034893 | -0.038752 | 0.017953 | 0.067269 | -0.067295 | -0.043661 | 0.07006 | -0.040846 | -0.03768 | -0.066219 | -0.031717 | -0.051798 | -0.035219 | 0.23172 | 0.04645 | 0.070393 | 0.066534 | 0.12324 | 0.17256 | 0.037991 | 0.002115 | 0.11584 | 0.00493 | 0.008096 | -0.020443 | 0.014059 | -0.006022 | 0.010557 | 0.022558 | 0.008137 | 0.025373 | 0.010952
6018.2031 | 122.85 | -0.14191 | 122.8226 | 0.13559 | -0.058836 | -0.025735 | -0.029595 | 0.017953 | 0.062691 | -0.071874 | -0.048239 | 0.056323 | -0.045424 | -0.042259 | -0.057062 | -0.040873 | -0.042641 | -0.035219 | 0.27749 | 0.083071 | 0.11617 | 0.11231 | 0.15986 | 0.2046 | 0.070033 | -0.002463 | 0.1021 | 0.000352 | 0.003517 | -0.011286 | 0.004903 | 0.003135 | 0.010557 | 0.008823 | -0.005598 | 0.011638 | -0.002783
6019.9844 | 122.937 | -0.059509 | 122.7448 | 0.14017 | -0.058836 | -0.030314 | -0.029595 | 0.008797 | 0.062691 | -0.067295 | -0.052818 | 0.060902 | -0.045424 | -0.03768 | -0.061641 | -0.036295 | -0.051798 | -0.026063 | 0.19967 | 0.000673 | 0.029195 | 0.029914 | 0.068306 | 0.1222 | -0.007786 | -0.007042 | 0.10668 | 0.000352 | 0.008096 | -0.015865 | 0.009481 | -0.006022 | 0.019713 | 0.008823 | -0.00102 | 0.016217 | 0.006374
6021.7031 | 122.8546 | -0.10071 | 122.8271 | 0.13559 | -0.054257 | -0.030314 | -0.034174 | 0.013375 | 0.062691 | -0.067295 | -0.048239 | 0.065481 | -0.045424 | -0.046838 | -0.057062 | -0.036295 | -0.04722 | -0.026063 | 0.23629 | 0.046451 | 0.070394 | 0.066534 | 0.11408 | 0.1634 | 0.033413 | -0.002463 | 0.11126 | 0.000352 | -0.001062 | -0.011286 | 0.009481 | -0.001444 | 0.019713 | 0.008823 | -0.001019 | 0.011638 | 0.001796
6023.4844 | 122.9324 | -0.091553 | 122.7997 | 0.13101 | -0.063415 | -0.025735 | -0.034174 | 0.013375 | 0.058113 | -0.062717 | -0.048239 | 0.07006 | -0.045424 | -0.03768 | -0.057062 | -0.031717 | -0.051798 | -0.030641 | 0.22256 | 0.028138 | 0.065818 | 0.057379 | 0.10493 | 0.14967 | 0.028836 | -0.002463 | 0.11584 | 0.000352 | 0.008096 | -0.011286 | 0.014059 | -0.006022 | 0.015135 | 0.008823 | 0.003559 | 0.011638 | 0.006374
6025.2188 | 122.9141 | -0.07782 | 122.8088 | 0.12643 | -0.054257 | -0.030314 | -0.034174 | 0.022531 | 0.053534 | -0.058139 | -0.048239 | 0.065481 | -0.036267 | -0.03768 | -0.057062 | -0.036295 | -0.04722 | -0.030641 | 0.20425 | 0.023563 | 0.047506 | 0.043646 | 0.10035 | 0.13135 | 0.019681 | -0.002463 | 0.11126 | 0.009509 | 0.008096 | -0.011286 | 0.009481 | -0.001444 | 0.015135 | 0.008823 | -0.001019 | 0.020795 | 0.010953
6026.9844 | 122.9324 | -0.07782 | 122.8271 | 0.12643 | -0.067994 | -0.030314 | -0.025017 | 0.013375 | 0.058113 | -0.058139 | -0.048239 | 0.060902 | -0.040846 | -0.03768 | -0.061641 | -0.031717 | -0.051798 | -0.021484 | 0.20425 | 0.009826 | 0.047506 | 0.052803 | 0.091195 | 0.13593 | 0.019681 | -0.002463 | 0.10668 | 0.00493 | 0.008096 | -0.015865 | 0.014059 | -0.006022 | 0.024292 | 0.013402 | 0.003559 | 0.020795 | 0.010952
6028.7031 | 122.9507 | -0.059509 | 122.8043 | 0.13559 | -0.058836 | -0.030314 | -0.034174 | 0.017953 | 0.058113 | -0.058139 | -0.048239 | 0.065481 | -0.036267 | -0.03768 | -0.061641 | -0.027139 | -0.038063 | -0.030641 | 0.1951 | 0.000673 | 0.029195 | 0.025335 | 0.077462 | 0.11762 | 0.00137 | -0.002463 | 0.11126 | 0.009509 | 0.008096 | -0.015865 | 0.018637 | 0.007713 | 0.015135 | 0.013402 | -0.010176 | 0.025374 | 0.001796
6030.4844 | 122.8867 | -0.10529 | 122.8271 | 0.12643 | -0.058836 | -0.039471 | -0.038752 | 0.017953 | 0.058113 | -0.067295 | -0.043661 | 0.060902 | -0.040846 | -0.03768 | -0.052484 | -0.031717 | -0.051798 | -0.030641 | 0.23172 | 0.04645 | 0.065815 | 0.066534 | 0.12324 | 0.1634 | 0.037991 | 0.002115 | 0.10668 | 0.00493 | 0.008096 | -0.006708 | 0.014059 | -0.006022 | 0.015135 | 0.008823 | 0.008137 | 0.011638 | 0.010952
6032.2031 | 122.9691 | -0.064087 | 122.7859 | 0.12185 | -0.058836 | -0.030314 | -0.034174 | 0.008797 | 0.058113 | -0.062717 | -0.052818 | 0.065481 | -0.045424 | -0.042259 | -0.052484 | -0.031717 | -0.04722 | -0.026063 | 0.18594 | 0.005251 | 0.033773 | 0.029913 | 0.072884 | 0.1222 | 0.00137 | -0.007042 | 0.11126 | 0.000352 | 0.003517 | -0.006708 | 0.014059 | -0.001444 | 0.019713 | -0.000334 | -0.005598 | 0.00706 | 0.001796
6033.9844 | 122.9553 | -0.09613 | 122.7722 | 0.12643 | -0.058836 | -0.034893 | -0.034174 | 0.017953 | 0.058113 | -0.067295 | -0.048239 | 0.065481 | -0.040846 | -0.033101 | -0.061641 | -0.027139 | -0.04722 | -0.035219 | 0.22256 | 0.037294 | 0.061237 | 0.061956 | 0.11408 | 0.15424 | 0.028835 | -0.002463 | 0.11126 | 0.00493 | 0.012675 | -0.015865 | 0.018637 | -0.001444 | 0.010557 | 0.013402 | -0.001019 | 0.020795 | 0.006374
6035.7656 | 122.8867 | -0.10071 | 122.8363 | 0.12643 | -0.063415 | -0.034893 | -0.034174 | 0.017953 | 0.062691 | -0.058139 | -0.048239 | 0.060902 | -0.036267 | -0.042259 | -0.057062 | -0.031717 | -0.042641 | -0.026063 | 0.22714 | 0.037293 | 0.065815 | 0.066534 | 0.11866 | 0.1634 | 0.042569 | -0.002463 | 0.10668 | 0.009509 | 0.003517 | -0.011286 | 0.014059 | 0.003135 | 0.019713 | 0.008823 | -0.005598 | 0.020795 | 0.006374
6037.4844 | 122.9507 | -0.07782 | 122.7768 | 0.12185 | -0.054257 | -0.034893 | -0.025017 | 0.008797 | 0.058113 | -0.067295 | -0.052818 | 0.065481 | -0.040846 | -0.046838 | -0.061641 | -0.027139 | -0.038063 | -0.030641 | 0.19967 | 0.023563 | 0.042927 | 0.052803 | 0.086617 | 0.13593 | 0.010525 | -0.007042 | 0.11126 | 0.00493 | -0.001062 | -0.015865 | 0.018637 | 0.007713 | 0.015135 | 0.008823 | -0.014755 | 0.020795 | -0.002783
6039.2656 | 122.9691 | -0.073242 | 122.818 | 0.13559 | -0.054257 | -0.025735 | -0.025017 | 0.013375 | 0.062691 | -0.067295 | -0.048239 | 0.065481 | -0.036267 | -0.03768 | -0.057062 | -0.031717 | -0.042641 | -0.026063 | 0.20883 | 0.018985 | 0.047507 | 0.048225 | 0.086617 | 0.13593 | 0.005947 | -0.002463 | 0.11126 | 0.009509 | 0.008096 | -0.011286 | 0.014059 | 0.003135 | 0.019713 | 0.008823 | -0.005598 | 0.020795 | 0.006374
6041.0625 | 122.9874 | -0.054932 | 122.7768 | 0.13101 | -0.058836 | -0.030314 | -0.029595 | 0.017953 | 0.058113 | -0.062717 | -0.043661 | 0.07006 | -0.050002 | -0.042259 | -0.061641 | -0.027139 | -0.042641 | -0.035219 | 0.18594 | -0.003904 | 0.024618 | 0.025337 | 0.072885 | 0.11305 | -0.007785 | 0.002115 | 0.11584 | -0.004226 | 0.003517 | -0.015865 | 0.018637 | 0.003135 | 0.010557 | 0.01798 | -0.00102 | 0.011639 | -0.007361
6042.8438 | 122.8729 | -0.10071 | 122.818 | 0.12643 | -0.058836 | -0.030314 | -0.034174 | 0.013375 | 0.053534 | -0.062717 | -0.048239 | 0.065481 | -0.045424 | -0.042259 | -0.061641 | -0.031717 | -0.051798 | -0.030641 | 0.22714 | 0.041872 | 0.070394 | 0.066534 | 0.11408 | 0.15424 | 0.037991 | -0.002463 | 0.11126 | 0.000352 | 0.003517 | -0.015865 | 0.014059 | -0.006022 | 0.015135 | 0.013402 | 0.003559 | 0.016217 | 0.006374
6044.5625 | 122.9233 | -0.086975 | 122.7951 | 0.13559 | -0.054257 | -0.030314 | -0.029595 | 0.013375 | 0.053534 | -0.067295 | -0.039082 | 0.065481 | -0.045424 | -0.03768 | -0.061641 | -0.031717 | -0.042641 | -0.035219 | 0.22256 | 0.032718 | 0.056661 | 0.05738 | 0.10035 | 0.14051 | 0.01968 | 0.006694 | 0.11126 | 0.000352 | 0.008096 | -0.015865 | 0.014059 | 0.003135 | 0.010557 | 0.022559 | 0.003559 | 0.016217 | -0.002783
6046.6562 | 122.85 | -0.10986 | 122.8043 | 0.12643 | -0.054257 | -0.030314 | -0.034174 | 0.008797 | 0.058113 | -0.062717 | -0.048239 | 0.065481 | -0.040846 | -0.03768 | -0.057062 | -0.031717 | -0.051798 | -0.026063 | 0.23629 | 0.055606 | 0.079549 | 0.075689 | 0.11866 | 0.16798 | 0.047146 | -0.002463 | 0.11126 | 0.00493 | 0.008096 | -0.011286 | 0.014059 | -0.006022 | 0.019713 | 0.008823 | 0.003559 | 0.016216 | 0.010952
6050.3594 | 122.9919 | -0.073242 | 122.7859 | 0.12643 | -0.063415 | -0.034893 | -0.034174 | 0.017953 | 0.058113 | -0.062717 | -0.052818 | 0.060902 | -0.050002 | -0.042259 | -0.061641 | -0.031717 | -0.04722 | -0.035219 | 0.19967 | 0.009827 | 0.038349 | 0.039068 | 0.091195 | 0.13135 | 0.010525 | -0.007042 | 0.10668 | -0.004226 | 0.003517 | -0.015865 | 0.014059 | -0.001444 | 0.010557 | 0.008823 | -0.005598 | 0.011639 | -0.002782
6053.8281 | 122.8683 | -0.10529 | 122.8271 | 0.13101 | -0.058836 | -0.030314 | -0.029595 | 0.013375 | 0.067269 | -0.062717 | -0.052818 | 0.056323 | -0.045424 | -0.046838 | -0.066219 | -0.031717 | -0.051798 | -0.035219 | 0.23629 | 0.04645 | 0.074972 | 0.075691 | 0.11866 | 0.17256 | 0.042569 | -0.007042 | 0.1021 | 0.000352 | -0.001062 | -0.020443 | 0.014059 | -0.006022 | 0.010557 | 0.013401 | -0.00102 | 0.020795 | 0.006374
6059.5 | 122.9462 | -0.086975 | 122.7951 | 0.12643 | -0.054257 | -0.025735 | -0.029595 | 0.013375 | 0.067269 | -0.071874 | -0.048239 | 0.07006 | -0.040846 | -0.03768 | -0.061641 | -0.031717 | -0.042641 | -0.026063 | 0.2134 | 0.032718 | 0.06124 | 0.05738 | 0.10035 | 0.15424 | 0.015101 | -0.002463 | 0.11584 | 0.00493 | 0.008096 | -0.015865 | 0.014059 | 0.003135 | 0.019713 | 0.013402 | -0.005598 | 0.020795 | 0.001795
6061.2969 | 122.9736 | -0.086975 | 122.8043 | 0.12643 | -0.054257 | -0.030314 | -0.029595 | 0.022531 | 0.062691 | -0.067295 | -0.048239 | 0.065481 | -0.040846 | -0.042259 | -0.057062 | -0.036295 | -0.042641 | -0.035219 | 0.2134 | 0.032718 | 0.056661 | 0.05738 | 0.10951 | 0.14967 | 0.01968 | -0.002463 | 0.11126 | 0.00493 | 0.003517 | -0.011286 | 0.009481 | 0.003135 | 0.010557 | 0.008823 | -0.005598 | 0.016216 | 0.001795

## Thermal Data
Fire Time | D Position - 3' | D Position - Middle | D Position - 7'
-0.4021 | 4.4465 | 4.0403 | 3.9583
0.5979 | 4.456 | 4.0438 | 3.9568
1.5979 | 4.4496 | 4.0373 | 3.9542
2.5979 | 4.4527 | 4.0311 | 3.9619
3.5979 | 4.448 | 4.036 | 3.9607
4.5979 | 4.4532 | 4.0637 | 3.9475
5.5979 | 4.4631 | 4.0643 | 3.9517
6.5979 | 4.4683 | 4.2126 | 4.0459
7.5979 | 6.2282 | 6.4143 | 5.9619
8.5979 | 9.3559 | 10.0432 | 9.2055
9.5979 | 10.9719 | 16.2924 | 11.9942
10.5979 | 13.151 | 19.042 | 14.5121
11.5979 | 15.2621 | 22.2896 | 16.0224
12.5979 | 16.7143 | 24.4799 | 18.2209
13.5979 | 18.7654 | 26.0265 | 20.8845
14.5979 | 22.0938 | 30.0212 | 24.0345
15.5979 | 24.3321 | 33.5253 | 25.904
16.5979 | 26.598 | 39.8493 | 30.0026
17.5979 | 29.7675 | 44.3208 | 32.007
18.5979 | 33.3942 | 49.2564 | 34.5893
19.5979 | 36.71 | 54.2831 | 38.3551
20.5979 | 39.1417 | 63.1136 | 41.0464
21.5979 | 41.989 | 68.9458 | 46.7874
22.5979 | 46.0552 | 76.2016 | 50.0346
23.5979 | 49.4796 | 81.7077 | 53.0973
24.5979 | 53.0126 | 89.0341 | 60.6173
25.5979 | 60.071 | 96.8203 | 64.3694
26.5979 | 62.9546 | 101.3487 | 66.623
27.5979 | 65.3139 | 104.2754 | 69.4663
28.5979 | 67.0381 | 107.4444 | 72.9033
29.5979 | 70.5882 | 112.3509 | 76.8962
30.5979 | 73.094 | 116.1986 | 81.5337
31.5979 | 76.386 | 119.0537 | 85.7821
32.5979 | 78.7019 | 121.593 | 88.9686
33.5979 | 81.916 | 123.4359 | 92.1737
34.5979 | 85.1189 | 127.4009 | 95.4064
35.5979 | 88.2907 | 133.456 | 101.6747
36.5979 | 91.2816 | 138.9252 | 104.1034
37.5979 | 93.3992 | 142.5176 | 108.321
38.5979 | 95.7396 | 148.3298 | 112.9403
39.5979 | 99.4015 | 152.7438 | 115.4908
40.5979 | 103.3453 | 158.1122 | 118.823
41.5979 | 107.1313 | 159.937 | 121.9613
42.5979 | 110.1087 | 163.3371 | 125.862
43.5979 | 113.6195 | 168.1937 | 129.8509
44.5979 | 116.3859 | 170.8767 | 131.4686
45.5979 | 119.8076 | 172.436 | 132.3019
46.5979 | 121.5641 | 174.975 | 134.3352
47.5979 | 123.1093 | 176.7422 | 137.4763
48.5979 | 125.1943 | 178.6856 | 140.4238
49.5979 | 126.2728 | 180.8093 | 142.237
50.5979 | 127.5145 | 182.2897 | 145.0172
51.5979 | 129.5031 | 183.0984 | 147.5443
52.5979 | 132.2719 | 185.902 | 150.9663
53.5979 | 134.2957 | 187.8395 | 153.6165
54.5979 | 135.2245 | 188.7471 | 156.3171
55.5979 | 138.8127 | 192.3614 | 158.538
56.5979 | 139.9999 | 196.5027 | 159.913
57.5979 | 140.5609 | 197.7791 | 160.6962
58.5979 | 141.4802 | 199.8823 | 162.2102
59.5979 | 142.0185 | 201.0837 | 164.412
60.5979 | 141.9602 | 201.0427 | 165.0497
61.5979 | 142.4248 | 201.7379 | 165.7845
62.5979 | 143.6606 | 202.2445 | 165.7353
63.5979 | 143.9486 | 202.5955 | 166.5045
64.5979 | 145.4475 | 203.5962 | 168.4542
65.5979 | 146.2083 | 202.8163 | 170.2435
66.5979 | 146.0785 | 202.3181 | 172.5806
67.5979 | 146.5985 | 200.6794 | 173.2987
68.5979 | 147.3094 | 201.642 | 173.5963
69.5979 | 146.8797 | 200.3605 | 172.6641
70.5979 | 146.6076 | 198.6553 | 171.9551
71.5979 | 147.6849 | 199.3791 | 170.9823
72.5979 | 147.0135 | 197.1838 | 170.7804
73.5979 | 147.2184 | 196.5464 | 169.7144
74.5979 | 147.3355 | 195.3455 | 169.5416
75.5979 | 147.6726 | 195.834 | 171.4732
76.5979 | 148.5439 | 197.0952 | 173.0236
77.5979 | 149.5182 | 195.829 | 173.0224
78.5979 | 148.9624 | 196.5017 | 175.1297
79.5979 | 150.5218 | 196.2153 | 175.8146
80.5979 | 153.0041 | 200.7427 | 176.6767
81.5979 | 153.4126 | 200.9664 | 177.7112
82.5979 | 153.0786 | 200.3622 | 179.5409
83.5979 | 153.8105 | 200.0535 | 180.0926
84.6292 | 153.4436 | 199.5125 | 179.4416
85.5979 | 154.2641 | 198.5694 | 179.085
86.5979 | 154.2159 | 198.3213 | 180.8328
87.5979 | 154.7618 | 197.366 | 180.8721
88.5979 | 155.257 | 198.3203 | 179.956
89.5979 | 156.3788 | 199.3672 | 179.936
90.5979 | 156.7136 | 200.3507 | 180.2635
91.5979 | 156.3542 | 200.0999 | 180.9451
92.5979 | 155.8773 | 201.3938 | 181.9632
93.5979 | 155.6803 | 201.5409 | 183.1522
94.5979 | 155.6397 | 200.5194 | 183.1789
95.6135 | 154.7396 | 201.1229 | 182.4611
96.5979 | 155.7665 | 203.3289 | 183.819
97.5979 | 156.5178 | 203.9228 | 185.8198
98.5979 | 157.1097 | 205.4672 | 185.8777
99.5979 | 157.7105 | 205.3234 | 186.8042
100.5979 | 158.3979 | 204.6604 | 187.4766
101.5979 | 157.5819 | 205.209 | 188.061
102.5979 | 156.9256 | 204.6122 | 188.3779
103.5979 | 158.3417 | 204.1216 | 187.1707
104.5979 | 159.7611 | 203.6615 | 188.4787
105.5979 | 160.0721 | 205.3526 | 189.9722
106.5979 | 159.296 | 204.7178 | 189.2276
107.5979 | 161.3148 | 205.5713 | 188.8927
108.5979 | 160.3711 | 204.8819 | 188.4455
109.5979 | 160.8988 | 205.9427 | 188.5403
110.5979 | 161.0158 | 206.4526 | 188.7768
111.5979 | 160.9409 | 204.7009 | 187.0413
112.5979 | 161.0523 | 205.4571 | 187.2537
113.5979 | 160.4713 | 205.4577 | 187.2195
114.5979 | 160.6366 | 206.5191 | 187.2634
115.5979 | 160.6635 | 207.2185 | 187.5093
116.5979 | 160.6375 | 207.0199 | 186.4787
117.5979 | 160.4079 | 207.421 | 186.3132
118.5979 | 160.072 | 207.8519 | 185.5308
119.5979 | 160.7363 | 208.5713 | 186.547
120.5979 | 160.8924 | 209.1262 | 187.4468
121.5979 | 161.5486 | 210.0865 | 186.0729
122.5979 | 162.2236 | 209.9237 | 186.2256
123.5979 | 161.9066 | 210.7662 | 187.2558
124.5979 | 163.1841 | 211.7569 | 187.0414
125.5979 | 163.8122 | 213.4604 | 186.8237
126.5979 | 163.846 | 215.4932 | 187.1039
127.5979 | 164.273 | 214.9584 | 186.6111
128.5979 | 163.1526 | 214.7741 | 186.2371
129.5979 | 162.9252 | 214.1929 | 185.4895
130.5979 | 162.1357 | 212.4148 | 185.4646
131.5979 | 162.2436 | 211.6348 | 187.2686
132.5979 | 162.4901 | 211.7875 | 186.8712
133.5979 | 162.0648 | 211.2801 | 187.0172
134.5979 | 161.6822 | 211.7891 | 187.8308
135.5979 | 163.3594 | 212.4636 | 188.7375
136.5979 | 163.4623 | 211.8894 | 188.6249
137.5979 | 163.1555 | 212.7363 | 188.7428
138.5979 | 162.8456 | 212.1925 | 188.3396
139.5979 | 162.7803 | 212.3053 | 187.9574
140.5979 | 162.8154 | 212.8103 | 189.4367
141.5979 | 162.7589 | 212.3888 | 189.2602
142.5979 | 162.1863 | 212.2782 | 188.4435
143.5979 | 162.8188 | 213.1414 | 187.9459
144.5979 | 162.1877 | 212.7191 | 188.2574
145.5979 | 161.8519 | 211.1419 | 188.6471
146.5979 | 160.7134 | 208.897 | 188.3273
147.5979 | 160.2684 | 209.1568 | 188.4616
148.5979 | 161.254 | 209.4146 | 189.3124
149.5979 | 161.6559 | 207.7167 | 189.4396
150.5979 | 161.0319 | 206.8836 | 188.6622
151.5979 | 161.3635 | 206.362 | 189.2535
152.5979 | 161.4628 | 206.6894 | 189.6389
153.5979 | 162.3332 | 209.4748 | 189.3033
154.5979 | 163.9524 | 210.5466 | 188.1439
155.5979 | 165.4553 | 210.5994 | 187.8346
156.5979 | 165.6288 | 212.888 | 188.5861
157.5979 | 168.4527 | 215.7072 | 189.2203
158.5979 | 169.2773 | 216.0584 | 189.2461
159.5979 | 169.0677 | 215.1505 | 189.8869
160.5979 | 169.3525 | 214.9382 | 190.019
161.5979 | 169.5367 | 214.4476 | 189.0355
162.5979 | 170.3115 | 215.0413 | 188.6335
163.5979 | 169.0821 | 213.0583 | 188.9882
164.5979 | 168.1592 | 213.0396 | 189.6351
165.5979 | 169.4825 | 212.3441 | 189.2297
166.5979 | 169.9506 | 211.4437 | 188.2479
167.5979 | 168.8206 | 210.6499 | 187.577
168.5979 | 168.3322 | 210.5067 | 187.8091
169.5979 | 167.1595 | 207.965 | 187.685
170.5979 | 166.189 | 207.9125 | 187.3555
171.5979 | 165.6101 | 207.5929 | 187.4318
172.5979 | 165.6825 | 205.9616 | 186.5993
173.5979 | 164.9762 | 205.1337 | 185.8371
174.5979 | 165.0248 | 204.8412 | 185.5305
175.5979 | 165.0069 | 204.0594 | 185.5743
176.5979 | 164.0775 | 204.9276 | 186.4936
177.5979 | 163.5848 | 204.0858 | 185.8587
178.5979 | 162.6124 | 203.4837 | 185.6019
179.5979 | 161.93 | 202.7321 | 186.122
180.5979 | 161.2258 | 201.5861 | 185.4782
181.5979 | 160.5375 | 202.672 | 187.0497
182.5979 | 161.831 | 204.3105 | 188.3874
183.5979 | 164.3695 | 206.7822 | 188.5195
184.5979 | 164.1571 | 206.3755 | 188.2997
185.5979 | 164.3508 | 206.7224 | 188.493
186.5979 | 164.0782 | 204.0685 | 186.5732
187.5979 | 163.7665 | 204.2247 | 186.0726
188.5979 | 163.6471 | 205.3536 | 186.8128
189.5979 | 164.2804 | 204.6489 | 187.1577
190.5979 | 163.6128 | 202.9354 | 186.1734
191.5979 | 163.1419 | 202.6034 | 186.2631
192.5979 | 163.4052 | 204.9849 | 187.5312
193.5979 | 163.078 | 203.3984 | 186.4573
194.5979 | 162.8272 | 202.6613 | 185.4843
195.5979 | 163.322 | 203.0364 | 184.8991
196.5979 | 165.2597 | 203.8194 | 185.5039
197.5979 | 166.127 | 204.6724 | 185.7387
198.5979 | 166.9873 | 206.6831 | 185.3034
199.5979 | 166.7871 | 205.0986 | 185.3272
200.5979 | 165.9562 | 203.6005 | 183.8934
201.5979 | 166.7729 | 202.7171 | 182.9772
202.5979 | 166.5372 | 202.4072 | 181.8505
203.5979 | 168.337 | 204.1212 | 181.6212
204.5979 | 167.6087 | 203.3993 | 180.1285
205.5979 | 167.5234 | 203.2849 | 180.4642
206.5979 | 168.159 | 204.5434 | 181.9
207.5979 | 168.0442 | 206.8782 | 183.0842
208.5979 | 168.2498 | 207.0646 | 185.4526
209.5979 | 168.6682 | 207.8266 | 186.8912
210.5979 | 168.9738 | 208.8848 | 188.0463
211.5979 | 169.9319 | 209.2643 | 189.4395
212.5979 | 170.4272 | 210.0326 | 189.6481
213.5979 | 169.5806 | 209.6813 | 190.5633
214.5979 | 169.7286 | 210.4387 | 191.0537
215.5979 | 171.0514 | 210.5335 | 191.0972
216.5979 | 171.3085 | 211.9249 | 193.2949
217.5979 | 171.6601 | 213.5971 | 193.6058
218.5979 | 172.178 | 213.1347 | 193.2848
219.5979 | 172.6539 | 213.3437 | 193.2171
220.5979 | 173.3911 | 214.1125 | 194.69
221.5979 | 174.5102 | 214.2833 | 195.3503
222.5979 | 175.7345 | 214.1796 | 194.6841
223.5979 | 177.3287 | 215.1952 | 193.9377
224.5979 | 178.7868 | 216.0314 | 193.9272
225.5979 | 179.017 | 215.738 | 195.0235
226.5979 | 179.2735 | 216.8853 | 196.5656
227.5979 | 178.6004 | 215.333 | 196.7414
228.5979 | 177.574 | 216.7202 | 195.8499
229.5979 | 177.0379 | 215.038 | 195.9253
230.5979 | 176.4615 | 215.421 | 196.6164
231.5979 | 176.2182 | 216.3021 | 196.0935
232.5979 | 177.1087 | 216.3573 | 196.4123
233.5979 | 177.0786 | 216.5398 | 197.6692
234.5979 | 176.6881 | 215.8184 | 197.023
235.5979 | 177.2433 | 216.5922 | 196.6686
236.5979 | 176.8283 | 215.5676 | 197.3124
237.5979 | 176.589 | 214.8669 | 197.9743
238.5979 | 175.668 | 214.8853 | 197.6484
239.5979 | 176.2152 | 217.3103 | 198.0563
240.5979 | 178.1782 | 219.1497 | 198.4691
241.5979 | 178.6986 | 220.1381 | 199.0428
242.5979 | 179.5738 | 221.3881 | 199.8494
243.5979 | 181.021 | 223.0265 | 199.0798
244.5979 | 181.8565 | 224.5494 | 201.2552
245.5979 | 181.3112 | 223.9368 | 201.4485
246.5979 | 179.9505 | 224.3982 | 201.6732
247.5979 | 180.9178 | 226.3424 | 202.1961
248.5979 | 182.068 | 226.953 | 204.2282
249.5979 | 181.7206 | 227.3741 | 203.5529
250.5979 | 182.0466 | 226.3013 | 203.1518
251.5979 | 182.5512 | 228.5196 | 204.3395
252.5979 | 182.5908 | 228.138 | 205.1541
253.5979 | 181.7264 | 227.9794 | 206.6289
254.5979 | 183.2925 | 228.3583 | 207.1933
255.5979 | 182.6265 | 229.2348 | 209.0355
256.5979 | 181.6939 | 228.4077 | 207.1137
257.5979 | 181.6867 | 227.016 | 207.5777
258.5979 | 180.7955 | 227.0302 | 206.6031
259.5979 | 180.7064 | 225.4377 | 206.64
260.5979 | 180.1055 | 225.6602 | 206.5303
261.5979 | 180.2958 | 227.038 | 206.2416
262.5979 | 179.6691 | 225.2691 | 204.754
263.5979 | 179.4952 | 224.6057 | 203.9792
264.5979 | 179.6883 | 224.8372 | 202.4156
265.6135 | 179.9943 | 224.2187 | 202.6049
266.5979 | 180.3956 | 224.1606 | 203.5324
267.5979 | 180.468 | 223.5573 | 202.5285
268.5979 | 180.6262 | 223.7082 | 203.6713
269.5979 | 180.8267 | 225.0659 | 203.9083
270.5979 | 181.6809 | 225.4651 | 203.3672
271.5979 | 181.9465 | 226.6633 | 203.9042
272.5979 | 182.517 | 227.5327 | 205.1084
273.5979 | 182.7106 | 229.7568 | 204.7572
274.5979 | 183.7979 | 229.9052 | 204.1976
275.5979 | 183.7042 | 230.974 | 205.284
276.5979 | 183.938 | 230.8308 | 206.9099
277.5979 | 184.1343 | 229.6958 | 207.2383
278.5979 | 183.7949 | 228.9194 | 207.5127
279.5979 | 183.1056 | 229.072 | 207.2285
280.5979 | 183.0805 | 229.9462 | 207.4239
281.5979 | 183.5167 | 230.8831 | 208.1021
282.5979 | 184.4623 | 230.5242 | 208.1782
283.5979 | 185.7993 | 230.7846 | 207.9431
284.5979 | 186.7741 | 231.6295 | 209.5836
285.5979 | 186.7519 | 231.5988 | 210.2102
286.5979 | 187.1717 | 231.5934 | 212.7638
287.5979 | 186.7044 | 231.3861 | 213.4185
288.5979 | 187.4271 | 231.7975 | 213.2355
289.5979 | 188.9277 | 231.7014 | 213.1252
290.5979 | 189.9202 | 232.9583 | 213.6241
291.5979 | 189.6315 | 231.9931 | 214.3234
292.5979 | 189.4925 | 232.0642 | 215.2031
293.5979 | 188.6334 | 233.2624 | 215.4524
294.5979 | 188.5607 | 232.0374 | 216.1251
295.5979 | 189.0375 | 233.659 | 216.3132
296.5979 | 191.3849 | 233.6848 | 217.0218
297.5979 | 190.2207 | 232.8016 | 216.7932
298.5979 | 189.8572 | 232.5629 | 216.9693
299.5979 | 190.0414 | 233.1299 | 216.6428
300.5979 | 190.4366 | 234.9582 | 216.0514
301.5979 | 190.4649 | 234.3333 | 216.5661
302.5979 | 190.6162 | 235.2255 | 217.9876
303.5979 | 189.3404 | 236.0688 | 217.8644
304.5979 | 189.078 | 236.8583 | 217.3299
305.5979 | 189.8459 | 237.3598 | 217.2585
306.5979 | 191.4633 | 241.0436 | 218.9023
307.5979 | 191.7672 | 241.7953 | 218.0987
308.5979 | 191.5132 | 242.9074 | 216.6856
309.5979 | 192.6027 | 244.411 | 216.3685
310.5979 | 192.418 | 243.8926 | 216.2553
311.5979 | 191.7027 | 245.0202 | 217.3339
312.5979 | 192.4673 | 245.8296 | 217.8319
313.5979 | 193.7068 | 245.7892 | 219.075
314.5979 | 194.3856 | 244.8719 | 218.6098
315.5979 | 194.5547 | 242.3947 | 218.5484
316.5979 | 195.1184 | 242.5611 | 218.6856
317.5979 | 194.5274 | 242.3727 | 218.4813
318.5979 | 194.9619 | 241.2942 | 219.3794
319.5979 | 195.5267 | 241.8195 | 219.0867
320.5979 | 196.0251 | 241.3613 | 219.3873
321.5979 | 196.9615 | 241.1918 | 220.7677
322.5979 | 197.1717 | 241.0617 | 219.5945
323.5979 | 198.5018 | 239.9405 | 220.0178
324.6135 | 197.5268 | 238.4861 | 220.3114
325.5979 | 197.5027 | 238.7366 | 221.5899
326.5979 | 196.4817 | 238.1974 | 222.7989
327.5979 | 195.8377 | 238.0258 | 222.7314
328.5979 | 196.5732 | 237.1429 | 223.2101
329.5979 | 197.4516 | 238.3887 | 224.1138
330.5979 | 196.7365 | 238.4966 | 223.5358
331.6135 | 196.4309 | 238.7173 | 224.5946
332.5979 | 196.8374 | 239.2236 | 225.0408
333.5979 | 197.3084 | 239.7327 | 225.6562
334.5979 | 199.0957 | 239.895 | 225.0199
335.5979 | 199.4252 | 240.0712 | 225.2203
336.5979 | 198.603 | 240.9586 | 225.6572
337.5979 | 197.9432 | 239.3449 | 225.9343
338.5979 | 197.3941 | 239.5029 | 225.7682
339.5979 | 197.0209 | 239.9596 | 226.0028
340.5979 | 197.7563 | 241.7635 | 226.2255
341.5979 | 197.6114 | 242.2247 | 226.8689
342.5979 | 198.2807 | 242.5638 | 228.1519
343.5979 | 198.0354 | 242.0259 | 227.598
344.5979 | 199.1133 | 241.896 | 228.1383
345.5979 | 201.7482 | 242.6282 | 227.7107
346.5979 | 202.1269 | 243.0118 | 228.0137
347.5979 | 201.7696 | 242.4848 | 227.842
348.5979 | 202.5052 | 242.9091 | 227.5908
349.5979 | 203.7448 | 243.7396 | 227.6333
350.5979 | 203.644 | 243.6426 | 228.7932
351.5979 | 204.0907 | 244.7625 | 228.6773
352.5979 | 204.2416 | 245.3058 | 229.4088
353.5979 | 203.0127 | 245.3223 | 229.6246
354.5979 | 203.9795 | 246.6183 | 229.3116
355.5979 | 203.904 | 246.5384 | 229.0768
356.5979 | 204.4258 | 246.7023 | 228.2105
357.5979 | 206.0202 | 247.5893 | 228.7507
358.5979 | 206.3584 | 248.1789 | 229.847
359.5979 | 207.7877 | 248.3776 | 229.6677
360.5979 | 207.7067 | 251.2553 | 230.9571
361.5979 | 208.0651 | 254.1165 | 231.2241
362.5979 | 207.5772 | 253.879 | 231.3911
363.5979 | 207.9432 | 253.7058 | 231.4726
364.5979 | 207.9139 | 253.6773 | 231.6943
365.5979 | 207.4241 | 254.4198 | 232.1206
366.5979 | 207.0111 | 255.2953 | 232.8286
367.5979 | 208.3987 | 255.8615 | 234.9906
368.5979 | 208.2869 | 256.1353 | 234.3749
369.5979 | 208.9497 | 255.6395 | 235.949
370.5979 | 208.5446 | 255.9068 | 235.9284
371.5979 | 208.91 | 255.4456 | 235.3947
372.5979 | 208.5122 | 256.3824 | 237.4708
373.5979 | 209.0815 | 256.6086 | 238.7415
374.5979 | 208.3759 | 255.6082 | 238.981
375.5979 | 208.191 | 256.4028 | 240.0683
376.5979 | 208.3969 | 257.0643 | 240.2856
377.5979 | 209.1291 | 256.2451 | 241.34
378.5979 | 208.4016 | 256.3856 | 241.2146
379.5979 | 208.1321 | 258.2445 | 242.2496
380.5979 | 207.4224 | 255.7213 | 242
381.5979 | 207.06 | 255.1549 | 242.069
382.5979 | 206.7531 | 255.0542 | 241.9162
383.5979 | 206.704 | 256.0538 | 242.1303
384.5979 | 206.6008 | 255.9066 | 241.7085
385.5979 | 207.2044 | 257.2467 | 243.1616
386.5979 | 207.2187 | 260.0004 | 243.5767
387.5979 | 207.7273 | 261.568 | 243.8444
388.5979 | 206.9036 | 262.0132 | 244.6625
389.5979 | 206.0485 | 261.8064 | 244.9272
390.5979 | 206.4426 | 263.8308 | 244.8764
391.5979 | 205.5091 | 263.763 | 245.5481
392.5979 | 207.8365 | 263.1219 | 244.9519
393.5979 | 208.4602 | 263.6105 | 245.2672
394.5979 | 210.0814 | 266.1069 | 244.4549
395.5979 | 209.72 | 267.0041 | 246.2332
396.5979 | 209.5615 | 266.439 | 245.6461
397.5979 | 209.3948 | 265.9904 | 245.3158
398.5979 | 210.0506 | 267.0607 | 244.8059
399.5979 | 210.456 | 268.2356 | 245.2758
400.5979 | 210.2402 | 269.5084 | 243.9282
401.5979 | 210.4159 | 270.2549 | 242.871
402.5979 | 210.6808 | 271.3678 | 243.2253
403.5979 | 210.7011 | 271.7764 | 244.525
404.5979 | 210.2115 | 271.9849 | 245.4184
405.5979 | 211.4184 | 269.9458 | 246.42
406.5979 | 212.6487 | 268.8335 | 245.6993
407.5979 | 211.8477 | 270.0121 | 244.2936
408.5979 | 211.8347 | 270.7662 | 243.6961
409.5979 | 211.1061 | 269.4344 | 243.0091
410.5979 | 210.0158 | 269.6643 | 242.9318
411.5979 | 209.4307 | 269.9076 | 242.3274
412.5979 | 209.7016 | 271.7471 | 242.317
413.5979 | 209.8131 | 270.9 | 242.1007
414.5979 | 209.7779 | 271.1372 | 240.999
415.5979 | 210.9314 | 270.538 | 240.5766
416.5979 | 210.3207 | 270.2738 | 240.0086
417.5979 | 210.7949 | 269.8674 | 241.0262
418.5979 | 210.9264 | 270.1227 | 241.2721
419.5979 | 212.1741 | 269.5811 | 241.425
420.5979 | 212.918 | 269.8416 | 241.2633
421.5979 | 213.3618 | 269.0321 | 241.1981
422.5979 | 213.7431 | 269.8393 | 241.5596
423.5979 | 213.665 | 270.5587 | 242.302
424.5979 | 215.1936 | 270.565 | 242.2482
425.5979 | 215.6655 | 271.3392 | 243.4708
426.5979 | 216.6589 | 270.8499 | 244.4142
427.5979 | 217.1632 | 271.4574 | 244.3682
428.5979 | 218.0247 | 272.0785 | 243.8918
429.5979 | 217.9013 | 272.7119 | 245.4179
430.5979 | 217.4133 | 271.5982 | 246.0664
431.5979 | 217.5267 | 270.7982 | 245.9037
432.5979 | 216.749 | 271.7483 | 246.9143
433.5979 | 217.6621 | 270.5511 | 246.3376
434.5979 | 217.1191 | 270.6091 | 245.8316
435.5979 | 216.1943 | 269.2044 | 245.3868
436.5979 | 215.2134 | 269.6724 | 244.8477
437.5979 | 216.7216 | 269.3837 | 244.6486
438.5979 | 216.5794 | 269.5736 | 245.8723
439.5979 | 216.449 | 269.7977 | 246.7298
440.5979 | 215.7114 | 270.4752 | 245.5857
441.5979 | 215.7119 | 270.6689 | 244.7967
442.5979 | 216.4197 | 270.9646 | 244.4571
443.5979 | 216.9408 | 269.2764 | 241.831
444.5979 | 217.1699 | 269.7767 | 241.5691
445.5979 | 217.6232 | 270.7269 | 241.4589
446.5979 | 217.8528 | 271.4397 | 241.3936
447.5979 | 217.6647 | 270.6105 | 240.4559
448.5979 | 218.1333 | 270.8277 | 239.6518
449.5979 | 217.2789 | 271.0171 | 238.749
450.5979 | 216.7679 | 270.8522 | 238.3554
451.6135 | 216.632 | 269.419 | 239.2941
452.5979 | 216.7144 | 268.6994 | 239.1882
453.5979 | 215.7319 | 268.7115 | 238.8388
454.5979 | 216.2942 | 268.8231 | 238.4742
455.5979 | 215.7278 | 270.483 | 239.8732
456.5979 | 215.0038 | 269.0542 | 239.4243
457.5979 | 215.2401 | 268.9939 | 238.3069
458.5979 | 215.8091 | 269.251 | 237.5507
459.5979 | 215.9328 | 270.1404 | 235.9473
460.5979 | 215.4041 | 271.5413 | 234.285
461.5979 | 216.0155 | 271.5592 | 232.7579
462.5979 | 216.8974 | 272.7278 | 232.5981
463.5979 | 217.5711 | 273.1131 | 233.6191
464.5979 | 218.3394 | 273.2604 | 233.8701
465.5979 | 218.3427 | 273.3796 | 233.847
466.5979 | 218.3195 | 273.5895 | 233.8062
467.5979 | 217.5828 | 272.9297 | 233.7386
468.5979 | 218.6287 | 272.8691 | 234.7765
469.5979 | 218.9378 | 274.1349 | 233.9912
470.5979 | 220.1141 | 274.1451 | 235.0647
471.5979 | 219.8071 | 275.5706 | 235.1421
472.5979 | 219.6645 | 275.6609 | 235.2672
473.5979 | 218.2872 | 276.9489 | 235.0127
474.5979 | 217.2593 | 277.579 | 234.9736
475.5979 | 217.5165 | 279.2889 | 234.35
476.5979 | 217.0276 | 279.7388 | 234.5882
477.5979 | 215.9349 | 280.8094 | 233.5411
478.5979 | 215.2303 | 279.8107 | 231.9745
479.5979 | 215.9866 | 279.0572 | 230.5176
480.5979 | 215.7647 | 279.387 | 231.2119
481.5979 | 216.3129 | 279.9791 | 231.2419
482.5979 | 216.1432 | 280.1514 | 232.21
483.5979 | 216.2421 | 279.3395 | 232.5968
484.5979 | 215.5656 | 279.2961 | 232.0973
485.5979 | 214.9488 | 279.3728 | 232.5776
486.5979 | 214.6922 | 279.2721 | 232.8536
487.5979 | 213.8001 | 280.0068 | 233.3669
488.5979 | 213.6423 | 280.229 | 233.6061
489.5979 | 214.6628 | 279.5489 | 232.6092
490.5979 | 216.5099 | 280.0096 | 231.2726
491.5979 | 217.4734 | 281.3382 | 230.6707
492.5979 | 220.2328 | 281.3538 | 230.5143
493.5979 | 221.2503 | 281.4165 | 230.3289
494.5979 | 221.8562 | 280.3583 | 230.2492
495.5979 | 223.6045 | 280.2318 | 231.413
496.5979 | 223.8377 | 279.4796 | 231.6869
497.5979 | 223.7273 | 278.0793 | 232.7024
498.5979 | 223.8223 | 277.6749 | 232.4348
499.5979 | 223.8204 | 277.4598 | 232.3565
500.5979 | 223.7036 | 275.3901 | 231.5728
501.5979 | 223.0513 | 274.6869 | 231.7408
502.5979 | 223.6357 | 274.4153 | 230.8722
503.5979 | 224.1322 | 275.9584 | 231.1035
504.5979 | 224.5055 | 275.8693 | 232.0636
505.5979 | 225.3213 | 274.9089 | 233.01
506.5979 | 225.904 | 276.3965 | 233.2314
507.5979 | 225.9858 | 274.8279 | 232.8588
508.5979 | 225.8117 | 273.1537 | 233.9122
509.5979 | 225.2779 | 273.1564 | 235.2649
510.5979 | 224.5695 | 272.2755 | 235.0036
511.5979 | 223.5197 | 271.3071 | 233.599
512.5979 | 223.3358 | 271.4917 | 234.7039
513.5979 | 224.1734 | 271.1075 | 235.581
514.5979 | 224.4626 | 270.2194 | 234.9852
515.5979 | 224.3954 | 269.749 | 234.3644
516.5979 | 224.2403 | 270.4222 | 235.2406
517.5979 | 223.5321 | 271.7708 | 236.1809
518.5979 | 222.5804 | 271.496 | 235.7254
519.5979 | 221.8647 | 271.3528 | 235.4044
520.5979 | 222.386 | 270.7518 | 234.1907
521.5979 | 223.8911 | 270.3812 | 234.1957
522.5979 | 225.4886 | 271.393 | 235.324
523.5979 | 226.6816 | 272.0127 | 235.6417
524.5979 | 225.3729 | 272.4127 | 235.71
525.5979 | 224.492 | 271.8921 | 236.2692
526.5979 | 225.5173 | 271.7361 | 236.5675
527.5979 | 227.2961 | 272.5937 | 235.2224
528.5979 | 227.0422 | 272.8183 | 234.704
529.5979 | 226.6654 | 274.1803 | 234.9233
530.5979 | 225.3476 | 275.1078 | 233.7729
531.5979 | 224.9829 | 275.7074 | 233.0751
532.5979 | 225.2885 | 275.4187 | 232.1746
533.5979 | 224.7732 | 274.1608 | 230.9485
534.5979 | 225.6295 | 274.7727 | 230.2463
535.5979 | 226.0436 | 274.6652 | 229.951
536.5979 | 226.9968 | 275.2712 | 230.1426
537.5979 | 228.1904 | 275.4214 | 229.6646
538.5979 | 230.3845 | 276.0482 | 229.5386
539.5979 | 230.0636 | 276.4196 | 229.0646
540.5979 | 229.5124 | 276.1843 | 229.2361
541.5979 | 228.5432 | 276.0668 | 230.2764
542.5979 | 228.5076 | 276.5634 | 230.0387
543.5979 | 228.3881 | 276.5745 | 230.4265
544.5979 | 227.452 | 275.9623 | 229.2708
545.5979 | 227.3971 | 276.1052 | 227.8303
546.5979 | 226.7071 | 275.2306 | 227.6761
547.5979 | 225.9655 | 275.4522 | 228.022
548.5979 | 226.5017 | 274.8541 | 228.4531
549.5979 | 226.3078 | 274.396 | 228.0663
550.5979 | 225.7727 | 274.338 | 227.7226
551.5979 | 226.5119 | 275.2774 | 227.9058
552.5979 | 226.1354 | 274.9029 | 228.1506
553.5979 | 225.8506 | 276.8028 | 229.1079
554.5979 | 225.2891 | 278.9844 | 229.7222
555.5979 | 224.8824 | 278.4899 | 230.7752
556.5979 | 224.562 | 280.1163 | 230.6863
557.5979 | 224.7157 | 281.0453 | 230.0429
558.5979 | 226.4036 | 280.8487 | 227.9694
559.5979 | 228.8342 | 280.5137 | 226.7373
560.5979 | 231.0264 | 279.812 | 226.5835
561.5979 | 232.6605 | 280.3807 | 226.2325
562.5979 | 233.3339 | 281.1489 | 227.043
563.5979 | 233.7326 | 281.8998 | 227.3244
564.6135 | 233.6515 | 282.0705 | 226.8412
565.5979 | 233.4245 | 282.6896 | 226.0987
566.5979 | 233.3728 | 284.0991 | 226.1352
567.5979 | 235.1388 | 284.2498 | 225.5306
568.5979 | 235.3364 | 284.8764 | 226.1349
569.5979 | 236.3712 | 285.4483 | 226.3442
570.5979 | 235.9268 | 286.3688 | 227.0737
571.5979 | 235.6418 | 286.2878 | 226.8911
572.5979 | 235.6933 | 285.4563 | 225.0934
573.5979 | 236.2751 | 285.0666 | 224.3005
574.5979 | 238.0982 | 285.429 | 223.4651
575.5979 | 238.4009 | 285.3757 | 223.2455
576.5979 | 239.433 | 285.6898 | 223.8913
577.5979 | 239.5899 | 283.6367 | 223.9596
578.5979 | 238.9477 | 284.8627 | 224.5038
579.5979 | 239.2719 | 284.9252 | 224.0452
580.5979 | 239.0772 | 285.8426 | 225.6913
581.5979 | 238.8594 | 286.2974 | 225.889
582.5979 | 240.37 | 287.5469 | 226.7438
583.5979 | 238.9844 | 286.9819 | 226.7161
584.5979 | 239.3838 | 286.4157 | 226.7461
585.5979 | 240.4324 | 286.6223 | 227.4776
586.5979 | 239.6491 | 286.363 | 227.5802
587.5979 | 241.2905 | 287.4047 | 228.4642
588.5979 | 241.6386 | 288.598 | 230.617
589.5979 | 239.9067 | 287.9614 | 230.8121
590.5979 | 238.8751 | 287.5516 | 230.0465
591.5979 | 238.7023 | 287.6239 | 230.5099
592.5979 | 237.5627 | 286.6107 | 230.4867
593.5979 | 237.7624 | 285.955 | 231.327
594.5979 | 238.2778 | 286.446 | 231.661
595.5979 | 239.4752 | 286.1146 | 231.0598
596.5979 | 238.3143 | 285.6066 | 231.5317
597.5979 | 237.8948 | 285.2858 | 233.0777
598.5979 | 237.9141 | 285.6443 | 234.4793
599.5979 | 237.6805 | 285.7044 | 235.773
600.5979 | 238.237 | 284.3032 | 236.0033
601.5979 | 237.4167 | 285.5876 | 236.7454
602.5979 | 236.3565 | 284.5256 | 237.6071
603.5979 | 239.0343 | 284.6729 | 236.5628
604.5979 | 239.683 | 284.771 | 237.2889
605.5979 | 240.0154 | 284.3011 | 238.4609
606.5979 | 239.5222 | 283.5994 | 239.8348
607.5979 | 239.2173 | 284.8993 | 240.1513
608.5979 | 239.3864 | 285.9436 | 241.8611
609.5979 | 240.5204 | 285.6346 | 241.2665
610.5979 | 241.0422 | 287.0414 | 241.4766
611.5979 | 241.3608 | 287.3849 | 241.8953
612.5979 | 240.983 | 287.8662 | 242.0752
613.5979 | 240.3236 | 288.756 | 240.415
614.5979 | 242.0683 | 289.1498 | 239.5492
615.5979 | 242.0966 | 289.6525 | 240.5113
616.5979 | 241.766 | 290.8243 | 240.7709
617.5979 | 241.942 | 290.7665 | 241.2315
618.5979 | 241.6079 | 290.6221 | 242.2081
619.5979 | 242.5183 | 290.4694 | 242.5526
620.5979 | 243.264 | 290.1767 | 242.4556
621.5979 | 241.7565 | 291.04 | 242.4072
622.5979 | 240.9398 | 290.797 | 244.0077
623.5979 | 240.6242 | 290.1105 | 244.5955
624.5979 | 239.8686 | 291.7375 | 245.6204
625.5979 | 239.1254 | 293.427 | 244.4082
626.5979 | 239.4444 | 293.3678 | 242.5153
627.5979 | 240.0292 | 292.0764 | 241.2644
628.5979 | 240.0258 | 292.0117 | 240.8794
629.5979 | 240.1084 | 293.1472 | 240.5328
630.5979 | 240.0444 | 293.0534 | 241.1675
631.5979 | 239.6127 | 292.5833 | 240.9959
632.5979 | 238.6254 | 293.2107 | 242.88
633.5979 | 238.5454 | 293.4381 | 242.3532
634.5979 | 238.0218 | 292.6954 | 242.2549
635.5979 | 237.2639 | 293.8762 | 242.4952
636.5979 | 236.8687 | 295.6066 | 242.0634
637.5979 | 237.8848 | 295.9032 | 241.7097
638.5979 | 238.3521 | 295.3179 | 241.3335
639.5979 | 237.782 | 295.247 | 241.2211
640.5979 | 238.4248 | 295.6977 | 239.7097
641.5979 | 239.2235 | 295.9618 | 238.992
642.5979 | 239.255 | 295.4163 | 238.8437
643.5979 | 239.8398 | 296.2096 | 238.2247
644.5979 | 239.7115 | 296.4686 | 238.2913
645.5979 | 241.0594 | 296.2435 | 237.7953
646.5979 | 241.2501 | 296.8721 | 238.0224
647.5979 | 241.2085 | 297.4399 | 237.9966
648.5979 | 240.7408 | 299.0035 | 237.9159
649.5979 | 240.8582 | 300.3323 | 237.5411
650.5979 | 241.7364 | 299.6701 | 237.249
651.5979 | 242.5931 | 299.3644 | 236.4897
652.5979 | 244.4603 | 299.3392 | 235.6387
653.5979 | 244.6931 | 300.0689 | 235.5646
654.6135 | 245.7864 | 302.1052 | 235.4205
655.5979 | 246.0429 | 302.3712 | 234.7178
656.5979 | 247.0023 | 302.2682 | 234.4544
657.5979 | 247.532 | 302.1025 | 234.2212
658.5979 | 248.6268 | 303.2989 | 233.6428
659.5979 | 248.242 | 302.8478 | 232.3041
660.5979 | 248.6812 | 302.5135 | 231.8806
661.5979 | 248.5136 | 302.9171 | 230.8765
662.5979 | 248.2402 | 303.5585 | 230.3386
663.5979 | 249.16 | 304.689 | 230.5601
664.5979 | 249.0814 | 305.0428 | 230.576
665.5979 | 249.4575 | 303.992 | 229.6204
666.5979 | 250.1203 | 304.3309 | 228.7594
667.5979 | 249.6803 | 304.0724 | 228.1979
668.5979 | 250.5489 | 304.62 | 228.3982
669.5979 | 251.3379 | 304.8008 | 229.3706
670.5979 | 252.8331 | 304.1297 | 229.7809
671.5979 | 252.6304 | 302.7222 | 229.7683
672.5979 | 251.7643 | 302.0283 | 231.3428
673.5979 | 251.6296 | 301.1277 | 231.6486
674.5979 | 250.8298 | 300.7061 | 232.3436
675.5979 | 250.6456 | 299.5427 | 232.2171
676.5979 | 250.7517 | 299.2684 | 232.5537
677.5979 | 252.4103 | 299.1097 | 233.0731
678.5979 | 253.9556 | 298.4039 | 233.0384
679.5979 | 253.1579 | 297.6016 | 232.3414
680.5979 | 252.9336 | 297.5554 | 233.0709
681.5979 | 252.8586 | 297.418 | 234.3616
682.5979 | 252.3258 | 297.9552 | 234.5059
683.5979 | 253.1967 | 300.1349 | 235.1774
684.5979 | 252.0733 | 300.894 | 235.8793
685.5979 | 250.9859 | 300.4958 | 236.0138
686.5979 | 251.5235 | 300.2868 | 235.3757
687.5979 | 252.508 | 300.6929 | 234.6532
688.5979 | 251.9099 | 300.6762 | 234.6911
689.5979 | 251.6388 | 300.2164 | 235.5986
690.5979 | 252.2339 | 300.8832 | 235.7115
691.5979 | 251.8024 | 300.6273 | 235.7937
692.5979 | 253.6787 | 299.8442 | 235.3559
693.5979 | 254.8478 | 300.2173 | 235.1912
694.5979 | 255.8845 | 301.4079 | 235.69
695.5979 | 256.9348 | 301.3799 | 235.8363
696.5979 | 256.3731 | 301.3885 | 235.0679
697.5979 | 255.6513 | 301.0321 | 234.7736
698.5979 | 254.8761 | 299.4359 | 234.5073
699.5979 | 255.3698 | 298.7686 | 234.5997
700.5979 | 255.5237 | 298.0477 | 234.6286
701.5979 | 255.7936 | 298.3403 | 234.7453
702.5979 | 254.8653 | 297.5451 | 234.3901
703.5979 | 255.233 | 298.2261 | 234.6477
704.5979 | 254.3134 | 298.0837 | 235.4665
705.5979 | 255.36 | 296.4929 | 234.4331
706.5979 | 256.2506 | 296.7242 | 234.4304
707.5979 | 255.9089 | 296.5922 | 234.9814
708.5979 | 254.2527 | 295.467 | 234.438
709.5979 | 252.8121 | 294.3562 | 235.8998
710.5979 | 251.7592 | 293.84 | 236.8421
711.5979 | 251.6846 | 293.3469 | 238.6693
712.5979 | 251.8558 | 293.9391 | 239.204
713.5979 | 252.5881 | 295.2989 | 239.2224
714.5979 | 254.4361 | 295.231 | 239.2437
715.5979 | 254.8694 | 295.1318 | 238.6722
716.5979 | 254.7046 | 294.544 | 238.0755
717.5979 | 254.6685 | 294.4256 | 238.1777
718.5979 | 255.341 | 294.2584 | 238.7415
719.5979 | 255.0063 | 296.0653 | 240.1725
720.5979 | 255.3807 | 296.7147 | 240.294
721.5979 | 254.5383 | 297.3496 | 241.2102
722.5979 | 254.0771 | 297.8835 | 241.55
723.5979 | 252.8896 | 297.4264 | 241.0534
724.5979 | 252.5631 | 298.1974 | 239.8879
725.5979 | 252.8579 | 299.6171 | 238.676
726.5979 | 252.7227 | 300.6424 | 237.7722
727.5979 | 252.2235 | 301.2856 | 237.6173
728.5979 | 252.1916 | 302.3378 | 237.7215
729.5979 | 251.7571 | 302.7347 | 237.9901
730.5979 | 250.7336 | 302.8635 | 237.0868
731.5979 | 251.0261 | 301.9475 | 237.254
732.5979 | 252.1344 | 302.9063 | 238.3403
733.5979 | 251.8732 | 303.9265 | 237.8864
734.5979 | 251.2873 | 306.1607 | 237.5864
735.5979 | 250.2296 | 306.792 | 237.5021
736.5979 | 249.7757 | 306.889 | 237.9565
737.5979 | 248.8358 | 306.1226 | 237.3409
738.5979 | 248.0317 | 306.4432 | 236.5149
739.5979 | 247.3135 | 306.6078 | 235.615
740.5979 | 247.3799 | 305.746 | 234.4474
741.5979 | 248.506 | 305.3784 | 233.9286
742.5979 | 249.7929 | 305.3979 | 232.985
743.5979 | 250.183 | 304.0062 | 232.5611
744.5979 | 250.9056 | 303.7162 | 231.0762
745.5979 | 251.5559 | 303.5089 | 231.5501
746.5979 | 253.0616 | 303.7687 | 232.7436
747.5979 | 253.4597 | 302.3967 | 232.257
748.5979 | 255.0079 | 300.9809 | 232.8216
749.5979 | 254.9534 | 299.8781 | 232.3347
750.6135 | 255.2034 | 299.4015 | 231.4364
751.5979 | 257.0888 | 298.5648 | 232.123
752.6135 | 256.8669 | 297.5588 | 231.1427
753.5979 | 256.7898 | 295.8532 | 229.9597
754.6135 | 256.1681 | 293.6806 | 229.0746
755.5979 | 256.2105 | 292.8542 | 228.9905
756.6135 | 256.2198 | 292.6376 | 229.4554
757.5979 | 256.8069 | 292.7205 | 230.6353
758.5979 | 256.6661 | 291.3645 | 231.3088
759.5979 | 255.7905 | 290.7988 | 230.9413
760.5979 | 254.9679 | 291.1848 | 231.9558
761.5979 | 254.8334 | 291.6065 | 232.8212
762.5979 | 256.4134 | 292.2342 | 232.6215
763.5979 | 256.1712 | 291.4864 | 232.355
764.5979 | 256.4232 | 290.8438 | 231.9766
765.5979 | 256.7189 | 290.2538 | 231.6831
766.5979 | 256.6908 | 290.7753 | 232.1462
767.5979 | 256.0124 | 289.7607 | 232.2531
768.5979 | 255.7178 | 289.6089 | 232.8571
769.5979 | 255.3812 | 290.3227 | 232.7272
770.5979 | 255.9269 | 289.8707 | 232.7545
771.5979 | 255.6176 | 288.9515 | 232.693
772.5979 | 254.8063 | 287.6873 | 232.827
773.5979 | 255.055 | 286.7368 | 232.4853
774.5979 | 254.2281 | 285.1843 | 230.9705
775.5979 | 253.8072 | 284.2911 | 230.4213
776.6135 | 253.4103 | 283.7506 | 231.8968
777.5979 | 252.2298 | 283.7837 | 233.1437
778.5979 | 252.0024 | 284.2268 | 233.9144
779.5979 | 252.542 | 284.9728 | 234.6038
780.5979 | 253.0047 | 285.4089 | 233.8716
781.6292 | 252.7718 | 285.5265 | 234.8061
782.5979 | 253.5349 | 285.6472 | 233.8168
783.5979 | 253.5763 | 286.6226 | 234.169
784.5979 | 251.9567 | 285.1434 | 235.1886
785.5979 | 250.9919 | 284.2509 | 235.5421
786.5979 | 250.3153 | 284.129 | 236.5104
787.5979 | 250.5242 | 284.1746 | 236.4317
788.5979 | 251.9825 | 284.9042 | 236.8456
789.5979 | 253.0396 | 285.757 | 236.9001
790.5979 | 254.3141 | 287.0486 | 238.0713
791.5979 | 255.742 | 286.4715 | 237.9106
792.5979 | 255.8662 | 285.3517 | 236.8569
793.5979 | 256.0459 | 285.1057 | 236.7441
794.5979 | 256.2591 | 285.4781 | 236.0417
795.5979 | 257.4462 | 284.9493 | 235.1748
796.5979 | 257.6417 | 285.3598 | 234.5054
797.5979 | 257.8869 | 286.0407 | 234.1836
798.5979 | 257.8359 | 287.0885 | 233.3477
799.5979 | 258.4067 | 287.6984 | 232.3397
800.5979 | 258.6332 | 287.1521 | 232.1502
801.5979 | 257.7019 | 285.6484 | 230.9582
802.5979 | 256.5955 | 285.3088 | 230.669
803.5979 | 256.2267 | 285.8839 | 231.0505
804.5979 | 256.1946 | 285.342 | 230.8082
805.5979 | 256.2813 | 286.6336 | 230.3204
806.5979 | 257.0142 | 287.6781 | 230.5165
807.5979 | 257.9676 | 288.3242 | 231.2463
808.5979 | 258.1387 | 288.4676 | 231.2742
809.5979 | 258.8756 | 287.4002 | 230.9585
810.5979 | 258.7481 | 286.5128 | 230.4918
811.5979 | 259.0486 | 286.622 | 230.8356
812.5979 | 259.2146 | 286.6567 | 231.0728
813.5979 | 259.447 | 286.1267 | 231.3254
814.5979 | 259.1439 | 285.5258 | 231.5274
815.5979 | 259.5943 | 286.5762 | 232.3325
816.5979 | 259.6763 | 287.2744 | 232.9369
817.5979 | 260.9252 | 289.3181 | 234.2514
818.5979 | 261.5731 | 290.0839 | 234.506
819.5979 | 261.2875 | 289.8935 | 234.1705
820.5979 | 260.9584 | 289.9312 | 233.6815
821.5979 | 261.3578 | 290.0056 | 233.7918
822.5979 | 262.119 | 289.916 | 234.3846
823.5979 | 261.5792 | 289.714 | 235.3208
824.5979 | 260.2613 | 289.7919 | 235.3008
825.5979 | 258.7735 | 289.8436 | 234.2418
826.5979 | 258.2908 | 289.5278 | 233.0326
827.5979 | 257.7991 | 290.8663 | 234.055
828.5979 | 257.4905 | 292.2053 | 233.4873
829.5979 | 257.4225 | 293.6373 | 233.7102
830.5979 | 257.9847 | 294.7143 | 233.0689
831.5979 | 257.9455 | 294.4249 | 232.2158
832.5979 | 257.9634 | 295.0861 | 232.1391
833.5979 | 257.7524 | 294.1303 | 231.3265
834.5979 | 258.1741 | 294.5122 | 230.5068
835.5979 | 259.0181 | 294.2657 | 229.9977
836.5979 | 259.5235 | 293.8582 | 228.7985
837.5979 | 260.3416 | 293.8303 | 228.2283
838.5979 | 260.7003 | 294.9393 | 228.2758
839.5979 | 260.8024 | 294.5108 | 227.3797
840.5979 | 261.1199 | 294.7925 | 226.5544
841.5979 | 260.4308 | 297.3175 | 227.1761
842.5979 | 260.7282 | 298.9372 | 227.2818
843.5979 | 260.5018 | 299.6899 | 226.2886
844.5979 | 261.0207 | 297.9763 | 225.3408
845.5979 | 261.2085 | 297.0417 | 224.8129
846.5979 | 261.1156 | 295.7513 | 224.8566
847.5979 | 261.7691 | 297.1081 | 224.9373
848.5979 | 261.8361 | 295.9106 | 224.7519
849.5979 | 262.0781 | 295.7779 | 224.0952
850.5979 | 262.5825 | 295.7994 | 223.0763
851.5979 | 261.9287 | 297.3254 | 223.2502
852.5979 | 262.0232 | 298.357 | 223.9428
853.5979 | 261.8897 | 299.1141 | 225.0737
854.5979 | 261.4947 | 299.5779 | 225.4524
855.5979 | 261.852 | 300.7454 | 225.458
856.5979 | 261.7022 | 301.4097 | 225.2795
857.5979 | 261.0606 | 300.6942 | 224.4793
858.5979 | 261.7783 | 301.1049 | 224.6461
859.5979 | 261.2563 | 300.3195 | 226.16
860.5979 | 260.6241 | 300.2196 | 227.9788
861.5979 | 260.4126 | 300.1592 | 228.7052
862.5979 | 260.0488 | 299.8667 | 229.1976
863.5979 | 259.9031 | 300.1486 | 228.6283
864.5979 | 259.6067 | 301.2933 | 228.8137
865.5979 | 260.6893 | 305.612 | 228.5751
866.5979 | 261.4179 | 306.7605 | 228.4084
867.5979 | 262.265 | 307.592 | 227.6966
868.5979 | 262.661 | 306.1169 | 227.0703
869.5979 | 261.9781 | 304.4311 | 226.8002
870.5979 | 262.3127 | 303.0259 | 226.5205
871.5979 | 262.6347 | 303.1769 | 226.4497
872.5979 | 262.1179 | 302.0457 | 226.1069
873.5979 | 262.157 | 301.9785 | 225.5785
874.5979 | 263.0577 | 302.2583 | 225.405
875.5979 | 263.1044 | 302.686 | 225.1278
876.5979 | 263.5909 | 301.2106 | 224.5247
877.5979 | 263.6897 | 299.7319 | 224.5119
878.5979 | 263.6928 | 299.2709 | 224.0862
879.5979 | 264.8322 | 298.903 | 224.2416
880.5979 | 265.512 | 299.8346 | 224.6042
881.5979 | 266.5825 | 299.5874 | 225.2566
882.5979 | 267.1505 | 299.547 | 224.9677
883.5979 | 266.968 | 299.5811 | 224.3379
884.5979 | 267.4954 | 299.5525 | 224.2771
885.5979 | 266.8308 | 298.792 | 223.8825
886.5979 | 266.453 | 299.7077 | 223.3874
887.5979 | 267.1265 | 301.5227 | 223.8279
888.5979 | 266.6772 | 301.7781 | 225.0549
889.5979 | 267.2822 | 301.7202 | 225.2646
890.5979 | 267.9147 | 304.154 | 225.2344
891.5979 | 267.517 | 306.0656 | 224.6299
892.5979 | 269.0143 | 308.0042 | 224.6371
893.5979 | 269.3484 | 309.3417 | 225.3288
894.5979 | 269.3156 | 309.2504 | 225.0964
895.5979 | 268.871 | 308.5181 | 224.492
896.5979 | 268.8023 | 306.8095 | 224.0617
897.5979 | 267.9993 | 306.3467 | 224.4425
898.5979 | 268.3458 | 309.7388 | 224.3552
899.5979 | 268.7756 | 308.2016 | 224.3603
900.5979 | 268.4894 | 307.5702 | 225.2374
901.5979 | 270.5836 | 308.9062 | 228.3378
902.5979 | 270.7821 | 309.2183 | 228.7258
903.5979 | 270.7288 | 309.1263 | 229.7987
904.5979 | 271.7025 | 309.3877 | 230.032
905.5979 | 271.1869 | 309.4378 | 230.1358
906.5979 | 271.9612 | 308.8605 | 231.2776
907.5979 | 271.1244 | 308.09 | 231.2918
908.5979 | 270.6215 | 308.6067 | 231.1636
909.5979 | 271.2231 | 309.2634 | 232.1523
910.5979 | 271.0213 | 309.944 | 232.5854
911.5979 | 270.6492 | 312.0845 | 233.5603
912.5979 | 272.6918 | 311.2507 | 233.2867
913.5979 | 271.9136 | 309.6775 | 232.1084
914.5979 | 271.5999 | 308.6679 | 232.1817
915.5979 | 271.907 | 309.0358 | 233.3255
916.5979 | 272.2946 | 309.8717 | 234.4852
917.5979 | 273.2422 | 310.2859 | 235.134
918.5979 | 274.5136 | 311.2203 | 235.3872
919.5979 | 275.6843 | 312.9734 | 235.8336
920.5979 | 276.8852 | 314.0169 | 236.1076
921.5979 | 276.7287 | 315.2043 | 236.5768
922.5979 | 277.6121 | 316.3535 | 239.8078
923.5979 | 279.2201 | 318.4573 | 243.2784
924.5979 | 279.9219 | 318.5539 | 243.6314
925.5979 | 280.0638 | 322.3904 | 244.5788
926.5979 | 282.0676 | 323.2601 | 245.1187
927.5979 | 281.3813 | 323.2041 | 244.5941
928.5979 | 281.7811 | 322.4862 | 244.6229
929.5979 | 283.3567 | 322.4424 | 244.3567
930.5979 | 283.3105 | 321.5235 | 243.1802
931.5979 | 283.7052 | 320.7673 | 242.1685
932.5979 | 283.4802 | 321.7912 | 242.9187
933.5979 | 285.2684 | 322.38 | 242.2365
934.5979 | 285.2262 | 323.0942 | 241.878
935.5979 | 286.7331 | 322.7503 | 241.1696
936.5979 | 287.1972 | 323.9782 | 239.9989
937.5979 | 287.7369 | 324.3577 | 238.9904
938.5979 | 288.4498 | 324.2028 | 238.1481
939.5979 | 288.597 | 324.6656 | 237.9993
940.5979 | 291.1663 | 326.1563 | 237.4639
941.5979 | 294.5828 | 330.1764 | 237.8598
942.5979 | 296.6327 | 330.9787 | 238.1779
943.5979 | 296.5959 | 330.1101 | 238.5107
944.5979 | 297.0725 | 330.3593 | 238.2124
945.5979 | 297.779 | 330.4627 | 240.4156
946.5979 | 297.6969 | 329.7316 | 241.1854
947.5979 | 297.3974 | 329.8626 | 241.9747
948.5979 | 296.4255 | 329.1171 | 242.054
949.5979 | 296.4567 | 328.1638 | 241.8692
950.5979 | 295.8963 | 328.3887 | 241.3541
951.5979 | 295.2242 | 327.6983 | 241.4376
952.5979 | 294.0125 | 328.0703 | 241.5692
953.5979 | 293.6787 | 328.3908 | 242.3861
954.5979 | 294.303 | 329.1942 | 242.2913
955.5979 | 294.2814 | 328.3516 | 241.6253
956.5979 | 295.3164 | 328.7686 | 242.2992
957.5979 | 295.0352 | 327.8159 | 241.9309
958.5979 | 294.5419 | 328.133 | 241.3917
959.5979 | 295.4409 | 328.7956 | 242.6965
960.5979 | 295.5367 | 328.7296 | 242.4404
961.5979 | 296.1511 | 328.2557 | 242.2864
962.5979 | 297.1218 | 328.3396 | 241.4782
963.5979 | 297.9332 | 328.2774 | 240.9797
964.5979 | 298.5608 | 329.5213 | 241.9332
965.5979 | 299.4114 | 329.9166 | 241.9037
966.5979 | 300.4402 | 331.427 | 242.3797
967.5979 | 301.3638 | 332.0284 | 243.106
968.5979 | 303.8987 | 333.6195 | 243.5909
969.5979 | 304.9028 | 333.7871 | 243.7077
970.5979 | 304.9394 | 333.1071 | 243.3592
971.5979 | 305.7074 | 333.3638 | 243.0518
972.5979 | 307.4512 | 334.6 | 243.9085
973.5979 | 311.2846 | 336.6163 | 246.1723
974.5979 | 309.9564 | 338.7586 | 247.0996
975.5979 | 309.0757 | 338.7046 | 247.7684
976.5979 | 308.6459 | 337.3791 | 247.0368
977.5979 | 311.6722 | 337.871 | 249.3912
978.5979 | 311.4999 | 337.707 | 250.1729
979.5979 | 311.5191 | 336.8375 | 250.3687
980.5979 | 312.0236 | 337.5917 | 250.7103
981.5979 | 313.5725 | 337.9486 | 251.7077
982.5979 | 314.2984 | 338.4713 | 252.5901
983.5979 | 313.5679 | 340.6844 | 253.8618
984.5979 | 312.4456 | 341.4337 | 253.8412
985.5979 | 310.5249 | 340.2121 | 252.5477
986.6135 | 312.2002 | 340.8175 | 253.492
987.5979 | 312.5054 | 341.6748 | 254.2823
988.5979 | 312.0835 | 342.6418 | 254.8249
989.5979 | 311.3992 | 341.7608 | 253.7886
990.5979 | 311.7314 | 342.1289 | 254.6876
991.5979 | 312.3598 | 341.5433 | 254.2137
992.5979 | 312.995 | 340.903 | 254.0613
993.5979 | 314.3662 | 340.2509 | 254.9635
994.5979 | 313.4797 | 340.8663 | 255.8455
995.5979 | 313.2436 | 341.7592 | 256.8341
996.5979 | 313.2012 | 342.4352 | 256.9166
997.5979 | 312.5088 | 342.0335 | 256.3442
998.5979 | 311.7032 | 342.193 | 255.7587
999.5979 | 311.6518 | 342.0765 | 256.8063
1000.5979 | 312.6205 | 343.0779 | 256.5657
1001.5979 | 313.4202 | 343.663 | 257.9497
1002.5979 | 312.9332 | 345.5926 | 257.6131
1003.5979 | 313.0622 | 345.5171 | 257.0117
1004.5979 | 313.1442 | 344.8819 | 256.7008
1005.5979 | 313.6593 | 345.5322 | 255.7339
1006.5979 | 314.0816 | 344.5933 | 255.2702
1007.5979 | 313.2389 | 343.6824 | 254.6584
1008.5979 | 312.4127 | 344.1989 | 255.0577
1009.5979 | 311.4683 | 344.1993 | 254.517
1010.5979 | 311.2377 | 344.5877 | 253.8624
1011.5979 | 311.658 | 345.4345 | 254.2069
1012.5979 | 311.0838 | 344.4319 | 253.8446
1013.5979 | 310.1213 | 343.5133 | 253.9245
1014.5979 | 311.1681 | 343.2556 | 253.5751
1015.5979 | 312.1513 | 343.3016 | 254.4135
1016.5979 | 311.7169 | 343.6023 | 254.9977
1017.5979 | 311.7009 | 343.8654 | 254.8469
1018.5979 | 311.119 | 343.7574 | 255.1087
1019.5979 | 310.6815 | 343.6268 | 254.8515
1020.5979 | 311.6349 | 344.5452 | 254.6276
1021.5979 | 313.1304 | 345.6937 | 254.9949
1022.5979 | 313.0616 | 347.1039 | 254.5067
1023.5979 | 312.7584 | 347.1134 | 254.0586
1024.5979 | 312.5684 | 347.1577 | 253.5358
1025.5979 | 313.2539 | 346.6124 | 252.9877
1026.5979 | 314.0631 | 345.9615 | 253.3826
1027.5979 | 313.997 | 344.9658 | 252.2818
1028.5979 | 312.9933 | 344.9922 | 251.432
1029.5979 | 313.2317 | 344.4865 | 252.1094
1030.5979 | 312.738 | 343.9261 | 252.2315
1031.5979 | 314.1983 | 344.391 | 254.5501
1032.5979 | 314.288 | 343.2068 | 255.9137
1033.5979 | 314.9053 | 344.2502 | 255.8153
1034.5979 | 315.5728 | 345.331 | 257.9621
1035.5979 | 315.7723 | 346.2918 | 257.1371
1036.5979 | 315.9581 | 347.6226 | 257.6276
1037.5979 | 315.4685 | 348.8786 | 256.8586
1038.5979 | 315.4706 | 348.8279 | 256.6499
1039.5979 | 315.4976 | 347.1443 | 255.8237
1040.5979 | 316.0248 | 346.489 | 254.8058
1041.5979 | 315.6059 | 346.3143 | 254.1585
1042.5979 | 315.1759 | 345.8103 | 254.0818
1043.5979 | 315.2458 | 347.1914 | 254.0951
1044.5979 | 314.3218 | 346.3721 | 254.6365
1045.5979 | 314.9809 | 345.85 | 254.5693
1046.5979 | 316.2978 | 345.0863 | 254.8692
1047.5979 | 316.6372 | 345.775 | 255.7364
1048.5979 | 316.1889 | 345.148 | 256.4349
1049.5979 | 314.7349 | 344.4264 | 257.1453
1050.5979 | 314.795 | 343.9043 | 256.6947
1051.5979 | 316.6429 | 344.1011 | 256.8002
1052.5979 | 317.1477 | 345.5109 | 256.6366
1053.5979 | 317.4548 | 346.46 | 257.3822
1054.5979 | 317.1362 | 346.279 | 257.4419
1055.5979 | 316.1414 | 344.7764 | 257.9368
1056.5979 | 316.4817 | 345.2471 | 258.8936
1057.5979 | 316.4981 | 345.6281 | 258.4849
1058.5979 | 315.787 | 346.459 | 258.0584
1059.5979 | 316.8004 | 347.9976 | 257.6184
1060.5979 | 318.241 | 349.2851 | 257.4157
1061.5979 | 318.7258 | 348.5687 | 257.5338
1062.5979 | 320.0473 | 348.5214 | 259.2295
1063.5979 | 319.8304 | 349.225 | 258.5394
1064.5979 | 319.1093 | 348.8722 | 258.0366
1065.5979 | 319.574 | 348.5912 | 257.4941
1066.5979 | 320.4001 | 348.6584 | 257.9398
1067.5979 | 322.0294 | 350.3955 | 257.9407
1068.5979 | 322.2108 | 351.6185 | 257.6026
1069.5979 | 322.2816 | 351.467 | 258.5892
1070.5979 | 321.7205 | 351.1277 | 259.4472
1071.5979 | 321.1627 | 351.1178 | 260.1456
1072.5979 | 321.1008 | 351.5853 | 260.5943
1073.5979 | 320.4431 | 350.6037 | 261.1456
1074.5979 | 320.5597 | 350.3974 | 260.4025
1075.5979 | 321.3048 | 350.0923 | 261.9732
1076.5979 | 321.4471 | 350.3211 | 262.2023
1077.5979 | 321.3824 | 350.3368 | 262.8935
1078.5979 | 321.48 | 350.4134 | 261.7731
1079.5979 | 321.0166 | 349.4674 | 262.9963
1080.5979 | 321.231 | 351.2491 | 262.4009
1081.5979 | 322.5115 | 352.1382 | 262.0071
1082.5979 | 322.0737 | 352.7981 | 262.9614
1083.5979 | 322.6344 | 355.0698 | 264.0435
1084.5979 | 323.3459 | 356.2444 | 265.1232
1085.5979 | 323.5446 | 356.8859 | 266.7075
1086.5979 | 324.2052 | 356.3433 | 265.9891
1087.5979 | 323.7341 | 354.9336 | 266.0676
1088.5979 | 324.4715 | 354.8265 | 267.4338
1089.5979 | 323.0541 | 352.8772 | 266.6003
1090.5979 | 321.9912 | 352.7767 | 266.9361
1091.6135 | 321.8842 | 353.1877 | 267.1071
1092.5979 | 322.7819 | 355.5196 | 268.5644
1093.5979 | 322.9315 | 355.9531 | 269.3072
1094.5979 | 323.0062 | 355.4836 | 270.3211
1095.5979 | 324.2193 | 357.9787 | 270.2491
1096.5979 | 324.295 | 360.5865 | 271.931
1097.5979 | 324.8125 | 360.8155 | 272.3259
1098.5979 | 324.5807 | 360.3738 | 271.8862
1099.5979 | 325.3669 | 359.8157 | 270.9659
1100.5979 | 324.8274 | 358.6602 | 270.8578
1101.5979 | 326.5016 | 361.2905 | 271.9706
1102.5979 | 327.1594 | 363.8431 | 274.0682
1103.5979 | 327.6128 | 364.5485 | 273.1262
1104.5979 | 327.9842 | 364.4947 | 272.425
1105.5979 | 328.7668 | 369.6473 | 272.2665
1106.5979 | 329.1003 | 372.8203 | 271.017
1107.5979 | 329.8942 | 374.7706 | 270.5452
1108.5979 | 330.5571 | 374.2998 | 270.2077
1109.5979 | 330.7718 | 374.7097 | 271.2773
1110.5979 | 330.8357 | 375.1508 | 272.5374
1111.5979 | 331.0452 | 376.3267 | 274.313
1112.5979 | 333.5885 | 378.6159 | 275.8273
1113.5979 | 334.2142 | 378.003 | 275.8528
1114.5979 | 334.4731 | 376.7083 | 275.5987
1115.5979 | 335.2843 | 377.3446 | 275.5951
1116.5979 | 335.5248 | 377.3605 | 275.2868
1117.5979 | 336.5787 | 380.7427 | 274.8019
1118.5979 | 337.9921 | 383.1685 | 275.8453
1119.5979 | 339.7468 | 386.6587 | 275.654
1120.5979 | 341.5844 | 390.4696 | 274.8903
1121.5979 | 342.3125 | 389.5944 | 275.9283
1122.5979 | 342.8384 | 390.6859 | 277.0144
1123.5979 | 342.4992 | 393.5438 | 276.6922
1124.5979 | 342.2346 | 391.4406 | 275.6984
1125.5979 | 342.1584 | 390.1348 | 274.8136
1126.6135 | 343.9898 | 393.7865 | 275.4709
1127.5979 | 345.4751 | 393.2689 | 275.7795
1128.5979 | 345.5289 | 395.4967 | 275.522
1129.5979 | 345.0785 | 394.3242 | 275.3548
1130.5979 | 344.867 | 395.3411 | 275.1869
1131.5979 | 347.191 | 395.4319 | 275.4418
1132.5979 | 353.9593 | 397.6255 | 275.1048
1133.5979 | 354.3119 | 397.398 | 276.3634
1134.5979 | 353.8055 | 397.1889 | 277.2958
1135.5979 | 353.9928 | 397.1499 | 278.312
1136.5979 | 353.5765 | 396.7609 | 277.9009
1137.5979 | 353.3188 | 398.3329 | 277.987
1138.5979 | 352.7494 | 396.6071 | 277.6548
1139.5979 | 355.897 | 399.0725 | 280.0408
1140.5979 | 356.995 | 398.5706 | 279.3341
1141.5979 | 359.0376 | 399.679 | 278.4959
1142.5979 | 362.1887 | 406.5791 | 278.7261
1143.5979 | 369.4944 | 409.6668 | 278.2535
1144.5979 | 373.826 | 414.7291 | 280.5958
1145.5979 | 380.9661 | 419.0432 | 281.7251
1146.5979 | 384.667 | 424.5245 | 283.9592
1147.5979 | 386.1252 | 430.9077 | 284.4168
1148.5979 | 387.9395 | 433.3974 | 283.9887
1149.5979 | 391.5333 | 438.4662 | 283.8157
1150.5979 | 392.4432 | 435.0433 | 284.9641
1151.5979 | 391.7053 | 439.1698 | 283.667
1152.5979 | 395.4862 | 438.9602 | 283.1143
1153.5979 | 394.6411 | 446.6037 | 282.0819
1154.5979 | 400.6244 | 447.4721 | 281.9353
1155.5979 | 406.9921 | 447.1415 | 282.2663
1156.5979 | 410.5729 | 448.4344 | 281.8931
1157.5979 | 411.892 | 447.4394 | 283.5498
1158.5979 | 417.8844 | 444.4387 | 284.9988
1159.5979 | 423.3575 | 444.0222 | 286.4584
1160.5979 | 424.9183 | 440.9348 | 287.8509
1161.5979 | 428.8492 | 437.3173 | 287.6384
1162.5979 | 432.5498 | 434.8462 | 289.3289
1163.5979 | 436.2053 | 435.9005 | 289.8279
1164.5979 | 439.0981 | 439.03 | 291.0787
1165.5979 | 445.0419 | 440.2144 | 292.1061
1166.5979 | 448.5054 | 444.1365 | 293.1663
1167.5979 | 449.733 | 446.7556 | 293.8054
1168.5979 | 457.5307 | 453.5636 | 295.344
1169.5979 | 457.5307 | 454.6112 | 297.9156
1170.5979 | 464.0977 | 456.6194 | 298.6043
1171.5979 | 466.0442 | 458.291 | 299.1456
1172.5979 | 465.4595 | 457.2525 | 298.8578
1173.5979 | 470.8047 | 457.16 | 299.546
1174.5979 | 465.98 | 454.0297 | 298.809
1175.5979 | 460.5309 | 453.3427 | 298.6915
1176.5979 | 455.0805 | 451.333 | 299.3494
1177.5979 | 459.6655 | 457.335 | 302.669
1178.5979 | 459.0592 | 457.6389 | 301.6269
1179.5979 | 460.1827 | 457.555 | 300.0383
1180.5979 | 460.99 | 460.5955 | 298.9019
1181.6135 | 465.3365 | 460.0513 | 298.1126
1182.5979 | 467.8101 | 459.9134 | 298.4242
1183.5979 | 477.0555 | 462.5623 | 299.9486
1184.5979 | 475.4183 | 462.5204 | 301.6864
1185.5979 | 470.3931 | 459.8977 | 302.3654
1186.5979 | 464.4464 | 457.5854 | 302.222
1187.5979 | 461.5683 | 458.1837 | 303.8768
1188.5979 | 463.4766 | 459.2437 | 304.219
1189.5979 | 459.8879 | 460.8502 | 304.8407
1190.5979 | 455.5958 | 459.41 | 305.3077
1191.5979 | 451.0333 | 457.533 | 305.4073
1192.5979 | 449.236 | 457.5087 | 305.456
1193.5979 | 449.0427 | 461.6553 | 304.3476
1194.5979 | 446.2059 | 460.0377 | 305.3683
1195.5979 | 451.7924 | 457.8216 | 303.4504
1196.5979 | 457.9832 | 457.0061 | 302.2587
1197.5979 | 457.6247 | 454.436 | 301.3298
1198.5979 | 459.5377 | 452.7934 | 300.3587
1199.5979 | 459.2056 | 457.1375 | 300.3634
1200.5979 | 460.608 | 458.5445 | 300.462
1201.5979 | 462.4273 | 459.6214 | 300.7329
1202.5979 | 458.6425 | 458.6739 | 301.0715
1203.5979 | 455.9913 | 456.1477 | 299.721
1204.5979 | 455.3363 | 454.6328 | 299.2742
1205.5979 | 451.3147 | 453.1721 | 299.359
1206.5979 | 448.7181 | 452.5718 | 300.5269
1207.5979 | 450.4 | 453.058 | 301.1404
1208.5979 | 453.5899 | 451.0349 | 301.1877
1209.5979 | 449.7585 | 449.1952 | 301.4486
1210.5979 | 446.3957 | 449.6247 | 302.2283
1211.5979 | 444.2525 | 452.0451 | 302.3885
1212.5979 | 444.7803 | 453.538 | 303.659
1213.5979 | 453.2422 | 458.9782 | 304.1433
1214.5979 | 455.6815 | 460.7998 | 305.5113
1215.5979 | 452.6063 | 460.1905 | 304.5294
1216.5979 | 450.2272 | 461.3049 | 303.3354
1217.5979 | 452.908 | 460.7705 | 302.1508
1218.5979 | 458.2396 | 457.4306 | 301.5523
1219.5979 | 465.5795 | 458.3971 | 301.3668
1220.5979 | 475.6043 | 462.5136 | 301.4277
1221.5979 | 480.8505 | 461.9966 | 301.3341
1222.5979 | 483.1996 | 461.8437 | 301.8202
1223.5979 | 485.4184 | 461.6914 | 305.2877
1224.5979 | 490.9986 | 459.764 | 306.2655
1225.5979 | 495.5449 | 458.9098 | 306.6389
1226.5979 | 507.0449 | 462.5736 | 307.4401
1227.5979 | 508.9856 | 466.0501 | 307.0118
1228.5979 | 512.1481 | 462.4353 | 306.0589
1229.5979 | 514.0428 | 462.3236 | 307.3066
1230.5979 | 518.3883 | 463.0515 | 307.1885
1231.5979 | 521.1956 | 463.262 | 307.658
1232.5979 | 527.41 | 462.3525 | 307.0362
1233.5979 | 523.7544 | 458.9923 | 305.6019
1234.5979 | 518.7687 | 455.9495 | 305.3973
1235.5979 | 519.7166 | 454.3423 | 306.8441
1236.5979 | 522.9939 | 454.0258 | 306.9442
1237.5979 | 529.3012 | 455.351 | 309.4212
1238.5979 | 528.9491 | 455.1058 | 309.832
1239.5979 | 525.9453 | 455.1089 | 309.7182
1240.5979 | 538.1894 | 457.1169 | 309.5945
1241.6135 | 537.0569 | 455.3123 | 309.5764
1242.5979 | 534.1335 | 454.2185 | 309.4549
1243.5979 | 536.2093 | 453.5736 | 308.8616
1244.5979 | 530.8876 | 453.4783 | 307.8735
1245.5979 | 529.8127 | 451.0362 | 306.449
1246.5979 | 524.8576 | 450.696 | 307.7619
1247.5979 | 520.4248 | 449.5581 | 308.4036
1248.5979 | 516.805 | 447.6909 | 308.4458
1249.5979 | 518.4878 | 448.8649 | 308.8807
1250.5979 | 518.189 | 450.0799 | 307.8278
1251.5979 | 527.3583 | 449.6999 | 307.1274
1252.5979 | 523.2778 | 447.1616 | 306.0521
1253.5979 | 518.669 | 445.3072 | 306.5408
1254.5979 | 511.1923 | 444.3252 | 307.9728
1255.5979 | 506.8696 | 445.2849 | 308.5503
1256.5979 | 508.5186 | 448.7228 | 308.488
1257.5979 | 513.381 | 451.5858 | 309.3987
1258.5979 | 513.0526 | 450.8467 | 309.3181
1259.5979 | 513.1574 | 454.3255 | 308.4027
1260.5979 | 517.3144 | 457.1758 | 309.3087
1261.5979 | 516.8384 | 460.4282 | 311.0759
1262.5979 | 518.5776 | 462.9 | 311.3073
1263.5979 | 517.3162 | 462.0336 | 311.7089
1264.5979 | 516.4157 | 462.3956 | 314.4548
1265.5979 | 512.9882 | 460.8492 | 314.9936
1266.5979 | 517.1448 | 458.7445 | 316.5109
1267.5979 | 520.7618 | 460.8947 | 316.974
1268.5979 | 519.6505 | 459.8918 | 317.179
1269.5979 | 513.742 | 458.0911 | 316.0519
1270.5979 | 519.1796 | 458.2553 | 317.151
1271.5979 | 518.3788 | 458.1024 | 316.573
1272.5979 | 520.314 | 459.453 | 317.0449
1273.5979 | 523.5823 | 463.5456 | 317.2319
1274.5979 | 525.8854 | 460.1273 | 316.9195
1275.5979 | 526.2383 | 456.6339 | 316.6731
1276.5979 | 528.463 | 454.1275 | 316.4257
1277.5979 | 525.1994 | 450.4319 | 315.1743
1278.5979 | 529.4506 | 450.012 | 315.6229
1279.5979 | 531.7386 | 453.5895 | 316.6388
1280.5979 | 531.9055 | 456.2886 | 318.9815
1281.5979 | 532.242 | 457.9231 | 319.821
1282.5979 | 533.7366 | 455.0009 | 318.7958
1283.5979 | 531.4513 | 452.2737 | 318.0972
1284.5979 | 536.6249 | 451.2084 | 318.7124
1285.5979 | 536.8384 | 454.6972 | 318.4523
1286.5979 | 537.641 | 456.6132 | 320.2368
1287.5979 | 539.9813 | 455.5273 | 321.4503
1288.5979 | 540.3026 | 456.0864 | 321.9853
1289.5979 | 540.1103 | 454.8785 | 321.906
1290.5979 | 545.3813 | 458.0045 | 322.1227
1291.5979 | 552.1663 | 459.9307 | 320.6507
1292.5979 | 554.3604 | 461.5554 | 320.4031
1293.5979 | 556.5787 | 460.9729 | 320.4293
1294.5979 | 559.3609 | 461.2124 | 320.5164
1295.5979 | 560.9257 | 463.6923 | 319.7873
1296.5979 | 561.1293 | 463.1037 | 318.5992
1297.5979 | 557.5537 | 463.6158 | 318.6795
1298.5979 | 558.1959 | 463.0158 | 319.2659
1299.5979 | 556.2387 | 463.6489 | 318.7945
1300.5979 | 560.1816 | 461.464 | 318.5012
1301.6135 | 559.0141 | 458.6624 | 317.1237
1302.5979 | 558.908 | 455.8168 | 316.2532
1303.5979 | 556.3403 | 453.3018 | 317.0708
1304.5979 | 546.3577 | 455.1133 | 319.5668
1305.5979 | 545.2111 | 459.4487 | 322.4184
1306.5979 | 545.203 | 461.2996 | 322.8441
1307.5979 | 553.0986 | 461.5232 | 321.9404
1308.5979 | 555.8304 | 463.0684 | 321.2128
1309.5979 | 557.4072 | 465.4186 | 320.7392
1310.5979 | 556.6172 | 467.9421 | 320.3621
1311.5979 | 561.0027 | 472.3823 | 320.9824
1312.5979 | 562.3497 | 474.7755 | 321.6782
1313.5979 | 564.4738 | 476.4627 | 321.6402
1314.5979 | 564.7189 | 475.4278 | 321.3995
1315.5979 | 565.914 | 474.9577 | 321.5431
1316.5979 | 563.0126 | 474.6206 | 321.5098
1317.5979 | 564.3955 | 474.6121 | 321.6354
1318.5979 | 566.466 | 475.6611 | 321.9963
1319.5979 | 559.8449 | 474.59 | 322.5012
1320.5979 | 564.6263 | 473.9434 | 322.2871
1321.5979 | 565.403 | 473.367 | 322.0148
1322.6135 | 561.8337 | 473.2209 | 323.0065
1323.5979 | 559.9185 | 474.1953 | 323.3598
1324.5979 | 556.8391 | 472.2 | 325.1274
1325.5979 | 553.3119 | 473.6197 | 326.6483
1326.5979 | 550.213 | 473.8094 | 326.2415
1327.5979 | 549.051 | 472.9454 | 326.5169
1328.5979 | 553.121 | 475.039 | 325.6696
1329.5979 | 550.0639 | 474.4133 | 325.1692
1330.5979 | 545.305 | 471.1761 | 324.7471
1331.5979 | 546.383 | 469.7581 | 326.2191
1332.5979 | 545.8212 | 469.6265 | 326.1598
1333.5979 | 544.7242 | 469.5906 | 326.6941
1334.5979 | 544.7349 | 468.2094 | 327.3602
1335.5979 | 547.1476 | 470.329 | 327.7853
1336.5979 | 545.5425 | 469.3463 | 327.3461
1337.5979 | 543.9742 | 472.3636 | 327.5628
1338.5979 | 548.5032 | 472.7313 | 327.9648
1339.5979 | 550.8612 | 471.2475 | 328.6796
1340.5979 | 552.4363 | 471.7119 | 330.4175
1341.5979 | 550.1834 | 468.7827 | 329.7708
1342.5979 | 558.6143 | 470.2201 | 330.0646
1343.5979 | 554.8259 | 469.4571 | 330.1042
1344.5979 | 554.2671 | 468.6692 | 328.8955
1345.5979 | 548.5351 | 468.9893 | 330.3804
1346.5979 | 545.6811 | 468.9493 | 331.1136
1347.5979 | 545.5294 | 469.0708 | 332.2231
1348.5979 | 548.7135 | 473.1115 | 334.2445
1349.5979 | 545.9995 | 474.6906 | 335.5362
1350.5979 | 544.8253 | 476.2175 | 336.3599
1351.5979 | 546.8443 | 475.4796 | 337.4892
1352.6135 | 544.9817 | 479.9848 | 339.0543
1353.5979 | 545.6995 | 479.7416 | 339.1684
1354.5979 | 546.2106 | 483.4069 | 341.8662
1355.5979 | 546.8772 | 487.4626 | 341.7448
1356.5979 | 550.0952 | 488.2064 | 339.9672
1357.5979 | 558.5663 | 489.3947 | 339.6523
1358.5979 | 556.9449 | 489.3491 | 339.6322
1359.6135 | 551.6675 | 489.6091 | 341.0465
1360.6135 | 551.309 | 491.6171 | 341.7535
1361.6135 | 547.6008 | 491.1596 | 341.2511
1362.5979 | 546.538 | 493.0922 | 339.7195
1363.5979 | 554.85 | 499.5639 | 338.8152
1364.5979 | 552.8476 | 501.492 | 337.6183
1365.5979 | 554.2307 | 503.2965 | 336.861
1366.5979 | 557.3819 | 503.5426 | 335.9223
1367.5979 | 553.681 | 502.6208 | 334.7303
1368.5979 | 562.331 | 503.6994 | 333.8735
1369.5979 | 562.3621 | 503.0795 | 332.5696
1370.5979 | 562.5135 | 502.9552 | 333.2533
1371.5979 | 561.4066 | 499.229 | 333.3147
1372.5979 | 556.5569 | 499.0758 | 334.4123
1373.5979 | 553.3603 | 496.0559 | 334.796
1374.5979 | 550.8316 | 492.9364 | 335.2069
1375.5979 | 552.1301 | 491.8478 | 336.5847
1376.5979 | 556.9313 | 493.2808 | 336.6419
1377.5979 | 557.8092 | 489.3219 | 335.4942
1378.5979 | 554.6632 | 486.6224 | 334.3003
1379.5979 | 555.8015 | 485.571 | 334.8903
1380.5979 | 550.5757 | 483.7451 | 334.5825
1381.5979 | 547.8525 | 482.3053 | 336.4959
1382.5979 | 549.151 | 483.0521 | 337.5292
1383.5979 | 558.877 | 483.9913 | 337.5095
1384.5979 | 559.0206 | 484.5719 | 339.177
1385.5979 | 555.8311 | 485.5614 | 340.1164
1386.5979 | 552.2975 | 484.1208 | 339.7962
1387.5979 | 559.8611 | 486.4243 | 338.2641
1388.5979 | 556.442 | 483.2972 | 337.3647
1389.5979 | 553.9902 | 484.0909 | 336.9083
1390.5979 | 553.5818 | 484.2604 | 338.5675
1391.5979 | 554.1761 | 483.2694 | 339.5634
1392.5979 | 555.2576 | 484.1881 | 339.8265
1393.5979 | 555.1197 | 486.7842 | 341.8705
1394.5979 | 552.5538 | 487.9784 | 341.1646
1395.5979 | 549.393 | 488.0886 | 341.8324
1396.5979 | 552.5337 | 490.9112 | 343.8151
1397.5979 | 552.2765 | 488.1163 | 343.1465
1398.5979 | 559.4244 | 487.6998 | 343.024
1399.5979 | 560.3854 | 492.4336 | 343.5541
1400.5979 | 557.5357 | 492.5637 | 343.7602
1401.5979 | 558.3248 | 493.7703 | 344.7796
1402.5979 | 553.9588 | 496.6667 | 345.2877
1403.5979 | 550.3005 | 502.0835 | 344.3593
1404.5979 | 550.8569 | 508.2903 | 343.6499
1405.5979 | 551.6608 | 512.811 | 344.1183
1406.5979 | 553.1867 | 512.0878 | 343.5105
1407.5979 | 552.5918 | 514.6456 | 343.1854
1408.5979 | 551.8392 | 517.7069 | 343.3139
1409.5979 | 550.1058 | 518.1768 | 344.7015
1410.5979 | 550.4509 | 520.2122 | 344.0578
1411.5979 | 551.9902 | 519.6203 | 344.6864
1412.6135 | 559.1442 | 514.9172 | 344.6971
1413.5979 | 561.4445 | 512.5023 | 344.7828
1414.5979 | 560.1065 | 513.8773 | 345.6015
1415.5979 | 566.5232 | 514.1125 | 345.7047
1416.5979 | 564.2452 | 517.3515 | 345.9017
1417.5979 | 564.1186 | 514.8421 | 347.8565
1418.5979 | 566.4082 | 512.7111 | 348.3579
1419.5979 | 566.9186 | 509.4995 | 347.7551
1420.5979 | 568.9937 | 507.4635 | 346.5479
1421.5979 | 573.5712 | 502.9749 | 347.3325
1422.5979 | 572.1387 | 502.5227 | 346.832
1423.5979 | 575.4752 | 502.1005 | 346.9812
1424.5979 | 578.8569 | 503.6731 | 347.6747
1425.5979 | 579.5385 | 504.9017 | 346.3599
1426.5979 | 575.733 | 502.8833 | 345.5498
1427.5979 | 574.5592 | 501.9271 | 347.1141
1428.5979 | 571.1748 | 500.0675 | 349.2352
1429.5979 | 571.3082 | 496.7796 | 348.3173
1430.5979 | 565.9711 | 495.5762 | 350.5768
1431.5979 | 566.8168 | 496.7658 | 353.5751
1432.5979 | 564.1753 | 494.9597 | 352.2949
1433.5979 | 561.9309 | 494.3858 | 351.5551
1434.5979 | 563.035 | 492.5914 | 351.8595
1435.5979 | 564.1348 | 489.2024 | 353.6052
1436.5979 | 566.3166 | 489.068 | 352.6393
1437.5979 | 566.9368 | 487.3612 | 352.8034
1438.5979 | 565.0694 | 488.9015 | 352.9418
1439.5979 | 562.3394 | 489.914 | 352.157
1440.5979 | 563.3697 | 491.122 | 353.4365
1441.5979 | 564.5976 | 491.7207 | 353.1198
1442.5979 | 566.4353 | 494.6915 | 353.7536
1443.5979 | 568.0588 | 495.7706 | 354.7952
1444.5979 | 563.5712 | 494.5831 | 356.1247
1445.5979 | 557.6443 | 491.0087 | 354.7212
1446.5979 | 555.5385 | 492.9944 | 353.8572
1447.5979 | 556.8849 | 494.1235 | 352.9507
1448.5979 | 558.006 | 495.6292 | 351.6862
1449.5979 | 558.5725 | 493.4676 | 351.5289
1450.5979 | 559.7784 | 491.884 | 349.9551
1451.5979 | 559.7703 | 491.2791 | 348.4665
1452.5979 | 566.4236 | 491.7911 | 347.9199
1453.5979 | 568.9187 | 489.5285 | 347.4635
1454.5979 | 569.6646 | 486.5725 | 346.4761
1455.5979 | 572.6342 | 490.4035 | 346.4033
1456.5979 | 575.9135 | 490.3794 | 347.9857
1457.5979 | 584.2325 | 490.0895 | 348.2458
1458.5979 | 583.1707 | 491.31 | 350.5721
1459.5979 | 576.3343 | 490.0935 | 350.2338
1460.5979 | 571.9601 | 486.5719 | 348.3349
1461.5979 | 574.5251 | 483.6945 | 347.0745
1462.5979 | 580.6632 | 484.1904 | 346.8295
1463.5979 | 575.1392 | 483.897 | 345.9751
1464.5979 | 578.9026 | 483.6428 | 345.8411
1465.5979 | 579.2523 | 482.6259 | 344.8326
1466.5979 | 580.8603 | 482.0944 | 344.0323
1467.5979 | 574.9048 | 478.5393 | 343.3109
1468.5979 | 568.3242 | 476.8968 | 342.7788
1469.5979 | 559.9582 | 477.1367 | 342.1889
1470.5979 | 553.3174 | 474.545 | 341.8332
1471.5979 | 548.3154 | 471.5714 | 341.1971
1472.5979 | 546.2054 | 468.7345 | 341.7943
1473.5979 | 542.3999 | 466.1708 | 341.8518
1474.5979 | 546.1959 | 467.5129 | 342.5373
1475.5979 | 550.0455 | 468.5364 | 341.8206
1476.5979 | 548.757 | 470.2184 | 342.8008
1477.5979 | 556.3016 | 472.6623 | 344.2792
1478.5979 | 557.1179 | 475.4519 | 345.9857
1479.5979 | 561.4744 | 476.4699 | 348.8548
1480.5979 | 563.2432 | 478.4595 | 348.2582
1481.6135 | 565.1767 | 479.8882 | 348.2252
1482.5979 | 563.864 | 480.6558 | 350.4032
1483.5979 | 575.4374 | 483.5004 | 350.4391
1484.5979 | 578.8347 | 486.7669 | 352.6893
1485.5979 | 588.972 | 483.8223 | 352.8218
1486.5979 | 594.1767 | 484.6608 | 351.9479
1487.5979 | 594.4515 | 484.7146 | 352.2957
1488.5979 | 591.2878 | 487.5382 | 353.2401
1489.5979 | 593.2111 | 490.5787 | 353.5502
1490.5979 | 589.663 | 489.6738 | 352.5675
1491.5979 | 579.6612 | 488.0831 | 353.3618
1492.5979 | 581.2654 | 488.5416 | 356.4973
1493.5979 | 584.9934 | 487.1217 | 355.9562
1494.5979 | 591.9852 | 489.5129 | 356.7955
1495.5979 | 590.5993 | 490.512 | 356.5383
1496.5979 | 587.8959 | 485.9069 | 354.537
1497.5979 | 583.1569 | 485.0221 | 355.0776
1498.5979 | 577.7782 | 482.9642 | 355.3758
1499.5979 | 580.3899 | 484.7204 | 355.2196
1500.6135 | 583.9801 | 484.8212 | 354.9383
1501.5979 | 585.3125 | 482.2458 | 355.8784
1502.5979 | 591.0098 | 480.4602 | 353.9896
1503.5979 | 589.7988 | 481.3794 | 352.9314
1504.5979 | 588.6036 | 481.0951 | 353.9777
1505.5979 | 587.6697 | 481.2671 | 354.3495
1506.5979 | 588.0637 | 483.4607 | 356.5938
1507.5979 | 585.397 | 486.6458 | 356.301
1508.5979 | 591.2705 | 487.1677 | 355.132
1509.5979 | 590.0875 | 489.1857 | 355.8573
1510.5979 | 592.4509 | 487.8303 | 354.654
1511.5979 | 589.0091 | 489.2016 | 356.3874
1512.5979 | 586.5347 | 490.9041 | 356.5716
1513.5979 | 587.7079 | 491.2665 | 356.8233
1514.5979 | 585.4104 | 490.6872 | 355.2253
1515.5979 | 585.3066 | 490.5397 | 354.9405
1516.5979 | 584.8031 | 490.3137 | 356.0804
1517.5979 | 585.8275 | 490.9235 | 356.889
1518.5979 | 589.0953 | 492.9234 | 357.3773
1519.5979 | 589.7734 | 495.469 | 358.1041
1520.5979 | 589.3249 | 491.9573 | 357.1687
1521.5979 | 590.8359 | 488.9745 | 357.053
1522.5979 | 596.3209 | 487.2939 | 355.8119
1523.5979 | 601.6909 | 488.0118 | 355.1277
1524.5979 | 601.4383 | 488.2727 | 356.1512
1525.5979 | 607.5676 | 488.3223 | 356.2804
1526.5979 | 610.5745 | 485.6824 | 356.3863
1527.5979 | 610.8915 | 487.1756 | 356.2299
1528.5979 | 611.7099 | 486.8776 | 357.3301
1529.5979 | 610.9783 | 488.5428 | 359.0575
1530.5979 | 607.5468 | 490.8518 | 360.4685
1531.5979 | 607.6584 | 494.2681 | 363.1793
1532.6135 | 611.3098 | 497.2975 | 364.3776
1533.5979 | 612.2255 | 498.6731 | 365.1766
1534.5979 | 618.6856 | 499.2451 | 365.3423
1535.5979 | 616.426 | 498.8114 | 365.0703
1536.5979 | 618.2637 | 497.2804 | 364.2155
1537.5979 | 620.0024 | 496.3815 | 364.5327
1538.5979 | 618.0121 | 497.9312 | 368.2009
1539.5979 | 614.1125 | 497.2755 | 368.0239
1540.5979 | 615.9324 | 497.7401 | 368.2681
1541.5979 | 622.3223 | 504.1413 | 370.2113
1542.5979 | 625.0673 | 505.553 | 370.06
1543.5979 | 631.5071 | 505.6387 | 369.3523
1544.5979 | 629.4383 | 505.468 | 369.8546
1545.5979 | 630.2911 | 505.6566 | 369.5921
1546.5979 | 629.64 | 506.3237 | 370.7044
1547.5979 | 626.7398 | 507.2651 | 372.1943
1548.5979 | 628.4977 | 507.0113 | 371.9203
1549.5979 | 625.4173 | 505.9411 | 371.8169
1550.5979 | 624.4867 | 505.007 | 371.4019
1551.5979 | 624.6892 | 505.4097 | 371.7371
1552.5979 | 625.6768 | 503.4974 | 372.3834
1553.5979 | 623.1908 | 502.5285 | 373.5777
1554.5979 | 622.1882 | 502.8672 | 374.1487
1555.5979 | 621.5061 | 502.6052 | 373.0404
1556.5979 | 623.8045 | 503.5877 | 373.5313
1557.5979 | 625.1802 | 502.966 | 374.3078
1558.5979 | 628.088 | 506.4798 | 375.1963
1559.5979 | 626.0112 | 507.669 | 378.0273
1560.5979 | 627.0099 | 511.4477 | 379.6464
1561.5979 | 627.5471 | 511.4772 | 378.088
1562.6135 | 627.9968 | 514.6083 | 377.4249
1563.5979 | 629.1378 | 517.9288 | 376.121
1564.5979 | 628.1086 | 519.0578 | 378.0819
1565.5979 | 628.3 | 520.1915 | 379.2123
1566.5979 | 628.3781 | 521.8893 | 378.9164
1567.5979 | 631.0884 | 521.1693 | 378.6117
1568.5979 | 628.7692 | 522.961 | 377.9574
1569.5979 | 628.4119 | 523.8648 | 379.4936
1570.5979 | 627.0635 | 524.0288 | 378.5976
1571.5979 | 626.4554 | 524.1107 | 380.2021
1572.5979 | 625.9568 | 523.5112 | 380.2207
1573.5979 | 628.2923 | 524.563 | 381.3397
1574.5979 | 628.5472 | 524.6604 | 382.6683
1575.5979 | 631.589 | 524.8466 | 382.3324
1576.5979 | 635.7096 | 528.704 | 381.7267
1577.5979 | 635.865 | 529.5382 | 381.3732
1578.5979 | 633.9229 | 525.7139 | 383.1555
1579.5979 | 630.9363 | 524.9156 | 383.172
1580.5979 | 630.9924 | 530.8728 | 383.5928
1581.5979 | 633.2857 | 529.4204 | 383.9791
1582.5979 | 635.4992 | 532.4478 | 384.1678
1583.5979 | 639.2824 | 536.823 | 383.4485
1584.5979 | 641.7455 | 534.5486 | 382.185
1585.5979 | 642.8091 | 536.752 | 381.853
1586.5979 | 640.3181 | 537.4048 | 383.2554
1587.5979 | 642.8239 | 537.9403 | 383.4561
1588.5979 | 644.0367 | 539.0338 | 382.4701
1589.5979 | 645.0053 | 539.9706 | 380.9552
1590.5979 | 645.6796 | 540.6063 | 379.8107
1591.5979 | 650.5831 | 544.4451 | 379.214
1592.5979 | 653.2049 | 544.9735 | 379.6697
1593.5979 | 650.9367 | 545.3261 | 380.4434
1594.5979 | 650.0124 | 546.3214 | 381.4102
1595.5979 | 653.6702 | 543.8428 | 381.6036
1596.5979 | 651.1669 | 542.9608 | 381.1936
1597.5979 | 648.9712 | 540.5604 | 383.4332
1598.5979 | 648.5255 | 541.0348 | 385.0149
1599.5979 | 645.7047 | 540.0619 | 384.5522
1600.5979 | 645.8839 | 537.4554 | 384.1445
1601.5979 | 645.5657 | 538.0489 | 383.8387
1602.6135 | 647.1354 | 537.5831 | 383.1876
1603.5979 | 648.6353 | 538.8289 | 383.7571
1604.5979 | 642.9645 | 538.3204 | 385.1703
1605.5979 | 637.3038 | 539.9346 | 386.5379
1606.5979 | 636.1366 | 540.4063 | 386.6678
1607.5979 | 643.0231 | 539.7613 | 385.7147
1608.5979 | 642.9179 | 539.7384 | 384.1616
1609.5979 | 642.7407 | 539.9405 | 383.2468
1610.5979 | 643.0071 | 539.9822 | 383.9867
1611.5979 | 648.022 | 541.3611 | 383.0882
1612.5979 | 653.0552 | 543.4128 | 383.783
1613.5979 | 651.2882 | 545.3566 | 384.9302
1614.5979 | 650.8704 | 549.3417 | 385.1217
1615.5979 | 650.4578 | 548.6783 | 385.5149
1616.5979 | 646.3916 | 547.2758 | 385.9689
1617.5979 | 643.8835 | 545.385 | 386.0405
1618.5979 | 654.5443 | 545.636 | 386.9127
1619.5979 | 653.3009 | 546.8901 | 389.6628
1620.5979 | 651.902 | 547.0446 | 390.4146
1621.5979 | 651.55 | 544.4317 | 390.0051
1622.6135 | 650.3584 | 540.5625 | 391.2953
1623.5979 | 648.7798 | 542.3559 | 392.1413
1624.5979 | 648.7074 | 543.8773 | 390.0138
1625.5979 | 650.646 | 543.641 | 390.2752
1626.5979 | 647.3066 | 541.8561 | 390.008
1627.6135 | 652.4507 | 542.3004 | 389.5862
1628.6135 | 651.714 | 541.0717 | 389.4491
1629.5979 | 647.9764 | 537.2712 | 389.0572
1630.6135 | 646.2451 | 537.7878 | 388.4947
1631.6135 | 647.3705 | 537.116 | 388.2952
1632.5979 | 644.2393 | 537.1847 | 389.6077
1633.5979 | 642.6293 | 538.5134 | 390.7021
1634.5979 | 644.4719 | 540.0557 | 392.1865
1635.5979 | 643.7891 | 541.6485 | 391.1464
1636.5979 | 640.9589 | 539.1521 | 391.0429
1637.5979 | 634.6911 | 540.1519 | 393.0533
1638.5979 | 630.8062 | 543.8646 | 394.746
1639.5979 | 632.8939 | 547.9087 | 395.7059
1640.5979 | 635.6192 | 551.0155 | 394.6731
1641.5979 | 634.9303 | 550.5816 | 393.9218
1642.5979 | 633.0488 | 550.711 | 392.9699
1643.5979 | 636.0266 | 555.3863 | 391.9771
1644.5979 | 637.8392 | 559.6987 | 392.9411
1645.5979 | 639.0321 | 559.27 | 392.8169
1646.5979 | 640.0758 | 556.0465 | 392.6706
1647.5979 | 639.2627 | 556.6307 | 391.4881
1648.5979 | 640.4906 | 557.9672 | 391.0069
1649.5979 | 643.0816 | 557.4943 | 392.1138
1650.5979 | 639.4381 | 553.0229 | 391.5954
1651.5979 | 636.3064 | 548.1362 | 391.8133
1652.5979 | 636.0045 | 546.7919 | 392.6277
1653.5979 | 634.9375 | 548.1253 | 393.2734
1654.5979 | 637.1612 | 547.8401 | 392.6186
1655.5979 | 635.724 | 546.0988 | 391.7534
1656.5979 | 633.1096 | 543.9462 | 392.5331
1657.5979 | 631.5425 | 543.6011 | 392.5828
1658.5979 | 632.6133 | 542.968 | 393.7254
1659.5979 | 632.3167 | 540.6412 | 393.6849
1660.5979 | 634.2947 | 541.1274 | 394.1671
1661.6135 | 632.7589 | 537.6972 | 394.1365
1662.5979 | 638.8913 | 536.6523 | 393.3411
1663.5979 | 634.3475 | 536.3693 | 394.7524
1664.5979 | 630.7635 | 532.9005 | 393.7262
1665.5979 | 631.6222 | 531.2181 | 393.6238
1666.5979 | 630.4007 | 529.4724 | 393.6826
1667.5979 | 628.5298 | 530.7163 | 392.5479
1668.5979 | 628.2337 | 532.5276 | 391.618
1669.5979 | 627.2547 | 531.363 | 391.2993
1670.5979 | 635.0528 | 533.4109 | 390.6645
1671.5979 | 634.7883 | 532.7458 | 389.9792
1672.5979 | 638.8177 | 535.154 | 390.0763
1673.5979 | 636.1748 | 536.3685 | 389.082
1674.5979 | 638.6317 | 536.2783 | 388.8769
1675.5979 | 636.152 | 534.4002 | 388.1002
1676.5979 | 633.6764 | 533.2746 | 387.4863
1677.5979 | 630.2998 | 532.5951 | 387.1285
1678.5979 | 630.5306 | 531.5491 | 386.3548
1679.5979 | 629.3552 | 531.6281 | 387.6653
1680.5979 | 629.4321 | 532.5915 | 388.4684
1681.5979 | 627.2323 | 532.7544 | 388.5021
1682.5979 | 624.9756 | 532.4961 | 388.2691
1683.5979 | 623.1666 | 529.7947 | 387.8614
1684.5979 | 623.8164 | 530.5816 | 388.1563
1685.5979 | 623.812 | 528.2107 | 387.3409
1686.5979 | 624.2963 | 527.3064 | 386.5808
1687.5979 | 623.1874 | 525.3289 | 386.5121
1688.5979 | 620.2888 | 521.6233 | 385.8402
1689.5979 | 620.5423 | 519.8096 | 384.8874
1690.5979 | 619.6645 | 519.0506 | 384.872
1691.5979 | 623.0552 | 519.1488 | 385.6482
1692.5979 | 627.4152 | 520.6374 | 384.8514
1693.5979 | 624.6995 | 521.7997 | 384.7966
1694.5979 | 623.2873 | 518.8444 | 385.4377
1695.5979 | 620.8745 | 518.1169 | 385.8347
1696.5979 | 618.4422 | 515.6092 | 385.617
1697.5979 | 617.7546 | 513.8865 | 386.5816
1698.5979 | 615.5789 | 513.8849 | 386.8442
1699.5979 | 623.7559 | 516.4117 | 386.4706
1700.5979 | 626.9527 | 514.0484 | 385.6572
1701.5979 | 624.0832 | 515.169 | 386.2779
1702.5979 | 617.3048 | 515.1274 | 386.5961
1703.5979 | 617.4911 | 512.9384 | 385.7288
1704.5979 | 616.6691 | 509.7746 | 385.5443
1705.5979 | 619.5722 | 511.5748 | 385.0042
1706.5979 | 619.5359 | 510.4159 | 384.0284
1707.5979 | 614.5207 | 509.1564 | 383.6473
1708.5979 | 620.1173 | 513.3236 | 384.2463
1709.5979 | 621.0706 | 515.9048 | 383.3504
1710.5979 | 617.5639 | 516.1091 | 383.1209
1711.5979 | 614.8393 | 513.9497 | 383.4221
1712.6135 | 611.8001 | 513.0984 | 383.8953
1713.5979 | 611.3593 | 513.6198 | 383.1935
1714.5979 | 612.4877 | 514.1159 | 382.8625
1715.5979 | 613.5902 | 512.7235 | 382.2549
1716.5979 | 618.0757 | 515.548 | 380.7781
1717.5979 | 617.1738 | 519.2057 | 380.5286
1718.5979 | 616.2641 | 520.5526 | 381.5661
1719.5979 | 617.729 | 520.0473 | 382.433
1720.5979 | 617.4754 | 518.908 | 382.8677
1721.5979 | 618.496 | 520.6663 | 382.7545
1722.5979 | 619.1904 | 522.7097 | 382.3185
1723.5979 | 619.1198 | 521.5286 | 382.3414
1724.5979 | 618.4391 | 519.5035 | 381.8317
1725.5979 | 616.3349 | 520.1146 | 382.1295
1726.5979 | 612.4051 | 519.0425 | 382.3126
1727.5979 | 612.5734 | 520.0559 | 386.1305
1728.5979 | 612.0336 | 520.624 | 387.4856
1729.5979 | 612.12 | 520.5575 | 387.2742
1730.5979 | 614.4446 | 520.5862 | 388.0197
1731.5979 | 613.2676 | 519.1477 | 386.5409
1732.5979 | 612.8144 | 518.7275 | 386.8838
1733.5979 | 612.8043 | 521.2456 | 388.1693
1734.5979 | 616.3962 | 523.0873 | 388.3382
1735.5979 | 618.1367 | 523.8313 | 387.4377
1736.5979 | 616.1343 | 523.4943 | 386.9498
1737.5979 | 615.2486 | 520.6592 | 387.0367
1738.5979 | 613.0777 | 518.7719 | 386.2193
1739.6135 | 610.1074 | 516.9444 | 385.7798
1740.5979 | 604.657 | 514.5414 | 386.2265
1741.5979 | 604.9117 | 514.8171 | 387.473
1742.6135 | 605.6717 | 515.554 | 387.5083
1743.5979 | 604.0116 | 513.4799 | 387.3994
1744.5979 | 602.2932 | 512.4596 | 387.2103
1745.5979 | 601.6322 | 513.8525 | 387.8212
1746.6135 | 600.759 | 512.9561 | 387.0002
1747.5979 | 602.7359 | 509.7525 | 385.9814
1748.5979 | 599.6622 | 507.0505 | 385.1796
1749.5979 | 599.7981 | 503.9742 | 385.3612
1750.5979 | 603.3496 | 503.6398 | 385.3281
1751.5979 | 600.9039 | 502.4263 | 385.3453
1752.5979 | 604.3469 | 501.8861 | 384.7757
1753.5979 | 604.1807 | 500.6005 | 384.8521
1754.6135 | 601.7882 | 502.188 | 384.2912
1755.5979 | 601.2051 | 504.8122 | 384.419
1756.5979 | 601.8624 | 506.8542 | 383.7082
1757.5979 | 602.525 | 506.6526 | 382.7847
1758.5979 | 600.9355 | 506.0216 | 382.3664
1759.5979 | 596.3419 | 502.9312 | 382.716
1760.5979 | 591.4813 | 501.7407 | 382.566
1761.5979 | 591.5197 | 501.2354 | 384.0229
1762.5979 | 590.7592 | 503.9 | 385.3665
1763.5979 | 589.6412 | 502.7232 | 385.4467
1764.5979 | 593.6465 | 501.1015 | 386.5515
1765.5979 | 587.7815 | 501.5226 | 387.5834
1766.5979 | 583.7751 | 501.1282 | 386.9362
1767.5979 | 581.8082 | 500.1822 | 387.7024
1768.5979 | 580.3579 | 499.5572 | 387.4439
1769.5979 | 578.7 | 498.4447 | 386.9988
1770.5979 | 574.4492 | 496.7073 | 388.1935
1771.5979 | 573.8433 | 496.7802 | 388.0591
1772.5979 | 575.0534 | 496.1109 | 387.7517
1773.5979 | 576.1295 | 496.7615 | 387.382
1774.5979 | 575.1606 | 496.3968 | 387.8173
1775.5979 | 575.9371 | 499.832 | 387.6985
1776.5979 | 580.7882 | 500.966 | 387.4341
1777.5979 | 581.8232 | 500.7034 | 386.2152
1778.5979 | 578.1873 | 498.3772 | 386.0823
1779.5979 | 572.4071 | 496.1819 | 386.864
1780.5979 | 570.9023 | 495.4208 | 385.8723
1781.5979 | 580.1695 | 493.5082 | 385.6075
1782.5979 | 579.9582 | 496.8424 | 385.2723
1783.5979 | 576.156 | 497.7498 | 385.2869
1784.5979 | 574.2497 | 495.6743 | 385.013
1785.5979 | 571.5836 | 492.9894 | 383.449
1786.5979 | 576.2206 | 493.4184 | 382.6573
1787.5979 | 573.9028 | 494.505 | 383.3953
1788.5979 | 571.3757 | 494.3426 | 382.7641
1789.5979 | 567.6749 | 491.9994 | 381.2494
1790.5979 | 570.3327 | 492.5798 | 380.6697
1791.5979 | 567.3082 | 492.9645 | 380.8373
1792.5979 | 564.2371 | 492.0823 | 382.8144
1793.5979 | 564.5462 | 489.508 | 382.6397
1794.5979 | 562.8854 | 487.7654 | 382.5297
1795.5979 | 565.522 | 488.2365 | 381.6541
1796.5979 | 565.4711 | 487.7994 | 382.252
1797.5979 | 562.4669 | 486.3754 | 382.9867
1798.5979 | 559.9546 | 485.1128 | 383.5562
1799.5979 | 557.0149 | 484.0143 | 382.7
1800.5979 | 556.4741 | 484.2795 | 382.8049
1801.5979 | 554.8435 | 482.2915 | 382.64
1802.5979 | 552.1269 | 481.5027 | 383.7699
1803.5979 | 550.0372 | 484.2956 | 385.0047
1804.5979 | 547.5392 | 488.2772 | 385.1227
1805.5979 | 551.6067 | 490.7582 | 385.0989
1806.5979 | 553.8364 | 490.6702 | 384.8503
1807.5979 | 557.1567 | 494.3368 | 384.7318
1808.5979 | 564.9111 | 496.3619 | 384.1459
1809.5979 | 565.7641 | 496.9275 | 382.6996
1810.5979 | 564.248 | 496.2888 | 381.6495
1811.5979 | 566.673 | 499.4627 | 380.7245
1812.5979 | 567.4307 | 499.5075 | 379.8462
1813.5979 | 567.9951 | 499.6154 | 378.881
1814.5979 | 566.3793 | 497.3118 | 378.6411
1815.5979 | 562.9337 | 498.1991 | 378.5398
1816.5979 | 559.8049 | 496.5591 | 378.5681
1817.5979 | 559.5514 | 496.8632 | 378.6641
1818.5979 | 560.6425 | 496.2846 | 377.9667
1819.5979 | 562.2192 | 499.7849 | 378.5006
1820.5979 | 562.2852 | 498.7379 | 378.178
1821.5979 | 562.4815 | 496.8309 | 377.1672
1822.5979 | 562.6861 | 497.0152 | 376.7711
1823.5979 | 561.7531 | 497.5067 | 376.2334
1824.5979 | 561.873 | 496.4832 | 375.6832
1825.5979 | 561.3176 | 495.2184 | 375.5988
1826.5979 | 558.1356 | 494.7524 | 374.9601
1827.5979 | 556.5613 | 494.5322 | 374.8997
1828.5979 | 556.1753 | 492.7658 | 374.4075
1829.5979 | 554.5485 | 490.3144 | 374.1767
1830.5979 | 552.8877 | 488.8486 | 373.7076
1831.5979 | 559.2752 | 487.6373 | 373.9173
1832.5979 | 556.6239 | 486.7549 | 374.5936
1833.5979 | 556.2615 | 486.9237 | 374.6409
1834.5979 | 554.6103 | 485.8955 | 374.5836
1835.5979 | 552.8074 | 485.1772 | 374.2612
1836.5979 | 550.9487 | 484.4927 | 373.7284
1837.5979 | 549.9939 | 482.9009 | 374.0235
1838.5979 | 548.7929 | 482.8775 | 374.5935
1839.5979 | 548.7138 | 482.5424 | 375.192
1840.5979 | 547.9496 | 480.6883 | 374.8539
1841.5979 | 548.8207 | 479.7634 | 374.5903
1842.5979 | 546.0742 | 477.6968 | 374.3442
1843.5979 | 544.0138 | 476.1797 | 373.9328
1844.5979 | 544.0091 | 475.5682 | 374.1967
1845.5979 | 542.0888 | 475.4241 | 373.9649
1846.5979 | 540.8466 | 475.2011 | 373.8139
1847.5979 | 537.7134 | 475.8759 | 373.8389
1848.5979 | 535.9729 | 474.8787 | 374.3419
1849.5979 | 534.135 | 475.0951 | 374.2478
1850.5979 | 537.0739 | 476.8065 | 373.9263
1851.5979 | 539.8539 | 477.0996 | 373.1951
1852.5979 | 536.2199 | 474.9856 | 373.2815
1853.5979 | 533.5807 | 475.0741 | 374.0163
1854.5979 | 531.7818 | 476.6473 | 374.3232
1855.5979 | 528.7056 | 476.6945 | 373.6403
1856.5979 | 530.3722 | 475.4991 | 373.6686
1857.5979 | 530.8884 | 474.4303 | 373.9909
1858.5979 | 528.5475 | 471.3632 | 373.4071
1859.5979 | 526.3602 | 470.5095 | 373.2311
1860.5979 | 524.8077 | 469.0891 | 373.0549
1861.5979 | 524.1252 | 467.6868 | 372.5702
1862.5979 | 526.5912 | 467.3585 | 372.1439
1863.5979 | 527.1164 | 467.6806 | 371.9794
1864.5979 | 525.2136 | 467.6155 | 372.1782
1865.5979 | 523.3829 | 468.1263 | 373.2249
1866.5979 | 522.9679 | 469.8163 | 373.3319
1867.5979 | 525.4241 | 470.3009 | 373.5428
1868.5979 | 523.8935 | 469.0631 | 374.3165
1869.5979 | 522.0454 | 469.5513 | 373.6683
1870.5979 | 522.3056 | 470.0538 | 373.8743
1871.5979 | 525.097 | 469.5338 | 373.004
1872.5979 | 524.9721 | 469.7741 | 372.5406
1873.5979 | 523.7877 | 468.2774 | 372.2538
1874.5979 | 519.9441 | 467.1486 | 372.4489
1875.5979 | 515.6707 | 465.7447 | 372.4098
1876.5979 | 512.9031 | 464.8212 | 372.9726
1877.5979 | 511.1485 | 463.4299 | 373.0092
1878.5979 | 510.5989 | 462.8012 | 373.7526
1879.5979 | 510.1021 | 463.9026 | 373.807
1880.5979 | 509.3721 | 463.01 | 373.7489
1881.5979 | 506.2142 | 461.4151 | 374.0889
1882.5979 | 503.4511 | 459.7203 | 373.8352
1883.5979 | 503.5399 | 458.4854 | 373.2809
1884.5979 | 504.8288 | 458.123 | 373.3544
1885.5979 | 503.9427 | 458.7726 | 373.982
1886.5979 | 502.2132 | 457.6056 | 374.2498
1887.5979 | 501.295 | 457.0158 | 373.5538
1888.5979 | 505.567 | 457.4064 | 372.843
1889.5979 | 508.2248 | 459.4331 | 373.0255
1890.5979 | 511.7947 | 461.7068 | 372.6369
1891.5979 | 511.3656 | 460.9933 | 372.7487
1892.5979 | 508.6703 | 460.7584 | 371.9769
1893.5979 | 508.0205 | 460.8466 | 372.0948
1894.5979 | 509.5408 | 460.3398 | 372.5617
1895.5979 | 508.1512 | 459.5639 | 372.5238
1896.5979 | 508.6479 | 459.9768 | 372.7704
1897.5979 | 510.0867 | 459.1461 | 372.0373
1898.5979 | 508.4376 | 456.7595 | 371.6228
1899.5979 | 505.9285 | 459.7821 | 370.7225
1900.5979 | 504.7594 | 460.435 | 371.155
1901.6135 | 502.8746 | 460.4453 | 371.4793
1902.5979 | 502.3311 | 459.8843 | 372.2547
1903.5979 | 501.9251 | 461.3961 | 373.2768
1904.5979 | 505.8223 | 465.6026 | 375.1769
1905.5979 | 508.3338 | 469.0341 | 375.321
1906.5979 | 508.5533 | 469.998 | 376.419
1907.5979 | 508.8672 | 472.3882 | 377.5162
1908.5979 | 509.512 | 475.4539 | 378.7587
1909.5979 | 510.4677 | 478.3276 | 380.9573
1910.5979 | 509.9563 | 478.2342 | 381.9682
1911.5979 | 508.1791 | 477.7302 | 381.786
1912.5979 | 504.8921 | 475.1494 | 382.1413
1913.5979 | 501.9007 | 472.5043 | 381.4164
1914.5979 | 499.9831 | 473.1839 | 380.3414
1915.5979 | 501.9846 | 474.7042 | 379.1373
1916.5979 | 503.7127 | 475.2796 | 378.4962
1917.5979 | 504.6206 | 475.4077 | 377.2771
1918.5979 | 511.2571 | 477.4185 | 377.512
1919.5979 | 518.1154 | 482.1011 | 378.2012
1920.5979 | 523.185 | 488.2429 | 380.0269
1921.5979 | 524.9052 | 495.3735 | 382.9863
1922.5979 | 530.0018 | 507.363 | 389.2889
1923.5979 | 534.9623 | 515.5894 | 393.9062
1924.5979 | 537.1373 | 523.3603 | 397.853
1925.5979 | 536.576 | 524.0329 | 399.0115
1926.5979 | 535.3751 | 523.7762 | 399.6855
1927.5979 | 534.7302 | 522.7814 | 399.4447
1928.5979 | 534.3299 | 527.0276 | 399.6237
1929.5979 | 537.4487 | 536.3402 | 401.2228
1930.5979 | 537.685 | 540.7604 | 401.3518
1931.5979 | 539.2605 | 547.8466 | 402.1033
1932.5979 | 542.1296 | 555.2284 | 402.9799
1933.5979 | 543.3225 | 559.7047 | 403.9094
1934.5979 | 543.9336 | 558.9125 | 403.5848
1935.5979 | 546.4284 | 559.5265 | 404.3545
1936.5979 | 548.4051 | 559.0078 | 405.0456
1937.5979 | 549.3085 | 559.6089 | 406.8514
1938.5979 | 549.1164 | 559.3661 | 407.1198
1939.5979 | 550.5533 | 559.4729 | 407.7925
1940.5979 | 552.1787 | 560.9061 | 408.4041
1941.5979 | 550.9131 | 560.0706 | 408.1261
1942.5979 | 549.9996 | 557.5654 | 407.1924
1943.5979 | 548.2298 | 556.4924 | 407.4174
1944.5979 | 547.3078 | 555.8683 | 408.066
1945.5979 | 547.9376 | 555.4535 | 408.471
1946.5979 | 545.6423 | 553.6382 | 409.2701
1947.5979 | 544.9322 | 554.7888 | 410.4727
1948.5979 | 544.5123 | 554.8068 | 411.7555
1949.5979 | 543.0351 | 554.9698 | 413.0704
1950.5979 | 542.3952 | 556.0662 | 415.4225
1951.5979 | 541.2991 | 557.2799 | 416.9854
1952.5979 | 539.8541 | 555.9648 | 417.7439
1953.5979 | 539.2148 | 555.3014 | 417.3999
1954.5979 | 538.7544 | 557.4678 | 418.5323
1955.5979 | 537.1278 | 556.3487 | 419.7634
1956.5979 | 536.5455 | 552.6967 | 419.0385
1957.5979 | 535.8783 | 549.0517 | 418.2669
1958.5979 | 535.1866 | 547.1869 | 418.7164
1959.5979 | 537.7964 | 554.6217 | 417.9679
1960.5979 | 538.2046 | 554.059 | 417.972
1961.5979 | 537.686 | 555.8079 | 417.8473
1962.5979 | 537.5894 | 561.7238 | 419.1135
1963.5979 | 539.3736 | 562.8302 | 422.0675
1964.5979 | 538.7664 | 559.8544 | 422.6672
1965.5979 | 539.0182 | 559.3666 | 423.5611
1966.5979 | 537.0535 | 555.524 | 423.3106
1967.5979 | 536.019 | 552.5755 | 422.5179
1968.5979 | 535.2317 | 552.1715 | 423.2811
1969.5979 | 534.6168 | 552.3039 | 424.6265
1970.5979 | 535.1719 | 555.354 | 423.9556
1971.5979 | 535.484 | 559.0635 | 424.5786
1972.5979 | 538.5869 | 562.6452 | 425.0312
1973.5979 | 540.719 | 562.4404 | 425.7414
1974.5979 | 541.8428 | 565.0417 | 428.4525
1975.5979 | 539.4776 | 561.2934 | 428.7139
1976.5979 | 537.7835 | 559.2312 | 428.6454
1977.5979 | 537.5733 | 558.6691 | 429.6308
1978.5979 | 535.5664 | 557.642 | 430.2506
1979.5979 | 535.2898 | 559.2046 | 431.1487
1980.5979 | 536.8412 | 563.6449 | 431.3785
1981.5979 | 536.5281 | 561.9134 | 431.4191
1982.5979 | 537.1371 | 561.6425 | 431.5309
1983.5979 | 535.9373 | 560.4749 | 432.3305
1984.5979 | 536.2936 | 560.0874 | 433.4004
1985.5979 | 537.4314 | 563.0718 | 433.0349
1986.5979 | 537.756 | 565.9628 | 432.037
1987.5979 | 538.7434 | 564.7767 | 433.199
1988.5979 | 538.0643 | 564.1063 | 435.7435
1989.5979 | 536.8622 | 563.2747 | 437.575
1990.5979 | 534.9205 | 562.3689 | 439.6118
1991.5979 | 532.2287 | 560.1626 | 440.4152
1992.5979 | 529.269 | 555.7438 | 439.7832
1993.5979 | 527.2033 | 553.0088 | 438.0714
1994.5979 | 527.338 | 552.833 | 437.3627
1995.5979 | 527.9061 | 554.6845 | 438.121
1996.5979 | 527.3355 | 557.3787 | 438.179
1997.5979 | 528.047 | 558.0257 | 438.9991
1998.5979 | 527.9458 | 559.0012 | 440.182
1999.5979 | 527.4646 | 556.7374 | 440.4931
2000.5979 | 527.6583 | 555.3794 | 438.9083
2001.5979 | 528.8724 | 556.3464 | 437.4872
2002.5979 | 528.1064 | 553.6222 | 438.0558
2003.5979 | 528.0677 | 552.1777 | 437.0665
2004.5979 | 526.9294 | 551.3309 | 436.509
2005.5979 | 526.9068 | 557.1317 | 437.6817
2006.5979 | 527.269 | 558.4762 | 438.6058
2007.5979 | 528.3241 | 557.8042 | 439.1201
2008.5979 | 530.276 | 558.5862 | 439.5973
2009.5979 | 529.397 | 557.2616 | 439.908
2010.5979 | 528.7126 | 558.413 | 442.2173
2011.5979 | 528.1022 | 559.781 | 442.5392
2012.5979 | 529.3091 | 561.9671 | 442.2992
2013.5979 | 529.1154 | 560.7572 | 442.0162
2014.5979 | 527.5646 | 556.9441 | 441.0851
2015.5979 | 525.8804 | 554.9866 | 440.8535
2016.5979 | 524.4445 | 553.3394 | 441.0498
2017.5979 | 523.9784 | 553.6629 | 442.1514
2018.5979 | 523.1619 | 551.9093 | 442.8656
2019.5979 | 523.1727 | 549.9453 | 441.7695
2020.5979 | 522.9033 | 552.6324 | 440.1698
2021.5979 | 523.7411 | 555.8105 | 440.9364
2022.5979 | 523.9695 | 555.622 | 443.4409
2023.5979 | 522.9345 | 555.1397 | 444.327
2024.5979 | 522.6395 | 553.3655 | 443.8846
2025.5979 | 522.3688 | 550.3149 | 444.8719
2026.5979 | 522.3893 | 551.0993 | 444.093
2027.5979 | 522.0702 | 551.2791 | 445.2599
2028.5979 | 522.0564 | 550.7521 | 446.0638
2029.5979 | 521.6383 | 548.4746 | 445.7927
2030.5979 | 521.5375 | 555.4565 | 446.3356
2031.5979 | 523.3304 | 558.4795 | 449.1459
2032.5979 | 523.7196 | 563.7424 | 450.0343
2033.5979 | 525.5357 | 565.1352 | 451.3669
2034.5979 | 526.1975 | 567.1764 | 451.5306
2035.5979 | 527.0001 | 569.0323 | 452.1146
2036.5979 | 528.0031 | 571.6629 | 456.3147
2037.5979 | 527.0853 | 570.3525 | 457.4251
2038.5979 | 525.5706 | 569.3291 | 457.9582
2039.5979 | 524.8796 | 568.4095 | 457.5566
2040.5979 | 524.8743 | 568.52 | 456.2985
2041.5979 | 525.3371 | 570.7031 | 454.9897
2042.5979 | 526.4201 | 571.55 | 453.9998
2043.5979 | 527.8639 | 572.8278 | 454.7801
2044.5979 | 528.4412 | 569.255 | 455.8179
2045.5979 | 529.7026 | 566.513 | 455.2365
2046.5979 | 528.2309 | 564.1566 | 453.7528
2047.5979 | 529.2116 | 566.1262 | 453.2572
2048.5979 | 533.3443 | 569.1622 | 454.5278
2049.5979 | 532.8005 | 571.3275 | 456.0263
2050.5979 | 533.7918 | 571.6985 | 458.5014
2051.5979 | 533.2685 | 570.4861 | 459.8078
2052.5979 | 532.7482 | 569.1436 | 459.4156
2053.5979 | 534.0644 | 570.1969 | 457.8766
2054.5979 | 536.5148 | 570.9017 | 458.4354
2055.5979 | 536.9715 | 571.3798 | 459.513
2056.5979 | 535.8047 | 570.6494 | 459.3716
2057.5979 | 535.6115 | 575.351 | 459.6709
2058.5979 | 535.5598 | 577.535 | 461.7083
2059.5979 | 535.0608 | 577.6964 | 460.8503
2060.5979 | 536.3174 | 578.7764 | 460.8759
2061.5979 | 534.9904 | 575.222 | 460.4049
2062.5979 | 533.132 | 570.3623 | 459.8827
2063.5979 | 531.0206 | 568.0099 | 459.2875
2064.5979 | 530.721 | 565.9656 | 457.7631
2065.5979 | 530.4565 | 569.0108 | 457.432
2066.5979 | 529.4913 | 573.6786 | 458.5346
2067.5979 | 532.4151 | 574.168 | 460.0554
2068.5979 | 531.3451 | 573.2419 | 459.4376
2069.5979 | 533.3188 | 584.9165 | 460.6651
2070.5979 | 535.1864 | 586.2158 | 461.3227
2071.5979 | 537.9232 | 588.2477 | 461.1197
2072.5979 | 539.7828 | 586.8329 | 461.5688
2073.5979 | 540.1662 | 583.9934 | 460.5912
2074.5979 | 539.7271 | 581.1624 | 461.5525
2075.5979 | 539.5044 | 580.8758 | 461.9173
2076.5979 | 538.6892 | 579.6418 | 464.7797
2077.5979 | 538.3969 | 582.8364 | 466.4979
2078.5979 | 538.3258 | 583.4811 | 467.8994
2079.5979 | 537.5224 | 581.8402 | 466.5416
2080.5979 | 536.6846 | 579.4287 | 466.4503
2081.5979 | 535.4123 | 576.0236 | 465.1172
2082.5979 | 536.3513 | 576.9486 | 463.4781
2083.5979 | 534.9325 | 573.9771 | 463.0781
2084.5979 | 536.5181 | 576.836 | 462.5562
2085.5979 | 535.6578 | 574.0697 | 461.833
2086.5979 | 533.8843 | 572.2151 | 461.4443
2087.5979 | 534.0344 | 574.2862 | 461.1679
2088.5979 | 533.1343 | 574.3596 | 461.576
2089.5979 | 531.1469 | 572.0328 | 461.8304
2090.5979 | 529.9768 | 570.3669 | 460.2571
2091.5979 | 528.844 | 569.7216 | 461.0465
2092.5979 | 531.3329 | 571.6908 | 462.8264
2093.5979 | 530.629 | 570.4339 | 463.1498
2094.5979 | 532.6992 | 570.8757 | 464.3229
2095.5979 | 533.0766 | 572.8735 | 464.8307
2096.5979 | 535.5052 | 577.6973 | 464.609
2097.5979 | 537.8067 | 583.0114 | 465.3352
2098.5979 | 536.9018 | 581.7989 | 466.0607
2099.5979 | 534.9334 | 579.8121 | 465.2622
2100.5979 | 535.9769 | 582.1223 | 465.0433
2101.5979 | 536.4678 | 582.9091 | 465.2134
2102.5979 | 536.3412 | 580.8342 | 466.2008
2103.5979 | 536.0421 | 576.7023 | 465.3603
2104.5979 | 535.207 | 574.1415 | 463.2249
2105.5979 | 536.5816 | 571.5237 | 462.9489
2106.5979 | 536.212 | 569.964 | 462.3146
2107.5979 | 534.9386 | 569.7637 | 462.0754
2108.5979 | 534.052 | 569.6333 | 461.8931
2109.5979 | 533.9566 | 572.019 | 462.008
2110.5979 | 535.2414 | 573.4429 | 464.9934
2111.5979 | 533.8393 | 570.6789 | 463.9536
2112.5979 | 533.9953 | 574.9306 | 465.4811
2113.5979 | 535.6862 | 578.4479 | 469.1547
2114.5979 | 537.6828 | 580.5614 | 470.4721
2115.5979 | 537.5552 | 580.2449 | 470.5239
2116.5979 | 536.403 | 577.6628 | 468.6994
2117.5979 | 536.3007 | 577.6499 | 468.534
2118.5979 | 535.6308 | 580.593 | 469.7217
2119.5979 | 535.9406 | 583.8768 | 469.8329
2120.5979 | 536.7824 | 584.7702 | 468.4308
2121.5979 | 538.1387 | 585.3845 | 469.1953
2122.5979 | 539.937 | 587.2845 | 471.3186
2123.5979 | 539.1614 | 587.6762 | 471.9507
2124.5979 | 538.1861 | 587.7231 | 471.7682
2125.5979 | 536.6993 | 585.9931 | 471.6103
2126.5979 | 536.1122 | 584.1799 | 473.0883
2127.5979 | 535.3431 | 581.0189 | 473.1294
2128.5979 | 534.5795 | 579.966 | 472.5654
2129.5979 | 534.5691 | 582.1489 | 472.1776
2130.5979 | 535.6659 | 581.9851 | 471.1254
2131.5979 | 535.1897 | 580.0143 | 472.1666
2132.5979 | 536.7924 | 583.5016 | 472.0554
2133.5979 | 536.0796 | 580.983 | 472.7437
2134.5979 | 534.5371 | 575.9516 | 471.6021
2135.5979 | 532.9978 | 574.6078 | 471.6394
2136.5979 | 532.8156 | 570.691 | 471.6338
2137.5979 | 532.4197 | 573.2931 | 472.0628
2138.5979 | 533.7627 | 573.0554 | 470.9777
2139.5979 | 533.772 | 571.4534 | 471.879
2140.5979 | 535.3334 | 574.5723 | 472.1897
2141.5979 | 535.5462 | 576.5519 | 473.3288
2142.5979 | 534.1068 | 575.086 | 474.3304
2143.5979 | 532.3769 | 573.4142 | 473.6904
2144.5979 | 531.0948 | 571.2949 | 472.6556
2145.5979 | 530.1672 | 577.4983 | 472.8677
2146.5979 | 530.7639 | 577.6086 | 473.1668
2147.5979 | 529.9904 | 576.908 | 472.4822
2148.5979 | 531.2059 | 577.8825 | 471.7842
2149.5979 | 532.796 | 579.8047 | 471.8032
2150.5979 | 534.8566 | 581.8882 | 472.295
2151.5979 | 534.9253 | 582.1294 | 474.9323
2152.5979 | 533.9571 | 581.0325 | 474.9226
2153.5979 | 534.0497 | 583.0194 | 473.8511
2154.5979 | 535.2278 | 585.1251 | 474.3375
2155.5979 | 535.7452 | 583.0263 | 473.594
2156.5979 | 535.495 | 583.5993 | 476.3377
2157.6135 | 535.0913 | 581.9868 | 480.1409
2158.5979 | 533.1129 | 579.3614 | 481.6815
2159.5979 | 533.0482 | 579.9996 | 481.3788
2160.5979 | 533.9399 | 583.9249 | 480.1709
2161.5979 | 535.6245 | 586.893 | 481.9776
2162.5979 | 536.9635 | 590.8746 | 482.9754
2163.5979 | 537.7398 | 591.7477 | 485.7985
2164.5979 | 535.9205 | 588.9927 | 486.3548
2165.5979 | 535.4445 | 589.2709 | 486.8339
2166.5979 | 534.9184 | 587.3688 | 488.1989
2167.5979 | 534.0185 | 582.1016 | 489.0076
2168.5979 | 534.5405 | 580.635 | 491.2877
2169.5979 | 534.4862 | 583.4028 | 493.325
2170.5979 | 535.6758 | 584.1678 | 494.59
2171.5979 | 535.3739 | 583.3804 | 495.5867
2172.5979 | 536.9149 | 584.7106 | 494.3653
2173.5979 | 538.3728 | 588.7792 | 493.131
2174.5979 | 538.223 | 587.8433 | 493.1157
2175.5979 | 538.732 | 590.4182 | 497.1603
2176.5979 | 538.3647 | 590.1735 | 499.8665
2177.5979 | 537.3961 | 589.6401 | 499.9799
2178.5979 | 538.4164 | 592.3486 | 501.1348
2179.5979 | 538.6714 | 593.2579 | 503.2548
2180.5979 | 537.3131 | 590.7614 | 503.8468
2181.5979 | 538.7433 | 593.7355 | 504.8867
2182.5979 | 538.6834 | 592.5498 | 505.0172
2183.5979 | 539.5055 | 591.065 | 505.397
2184.5979 | 540.6466 | 592.1773 | 503.9918
2185.5979 | 541.9789 | 591.7815 | 503.1146
2186.5979 | 541.2464 | 590.0456 | 504.5737
2187.5979 | 541.4202 | 588.4053 | 506.046
2188.5979 | 540.5876 | 591.1434 | 505.7294
2189.5979 | 540.4358 | 589.2355 | 505.4998
2190.5979 | 540.7121 | 589.7019 | 506.7116
2191.5979 | 540.1327 | 587.4048 | 509.2234
2192.5979 | 540.5222 | 586.8262 | 511.9659
2193.5979 | 540.7961 | 587.6964 | 512.9387
2194.5979 | 539.3214 | 584.5964 | 510.4265
2195.5979 | 539.752 | 583.111 | 510.6919
2196.5979 | 539.8616 | 581.541 | 511.0158
2197.5979 | 538.9199 | 579.6636 | 511.8689
2198.5979 | 538.9701 | 578.4096 | 511.8464
2199.5979 | 538.623 | 581.1698 | 512.9202
2200.5979 | 537.2709 | 580.0787 | 514.1552
2201.6135 | 536.6632 | 585.9988 | 517.4005
2202.5979 | 537.3766 | 584.5331 | 519.2725
2203.5979 | 534.9939 | 579.3789 | 517.1435
2204.5979 | 535.8641 | 583.0297 | 515.0594
2205.5979 | 537.8313 | 586.9094 | 516.2126
2206.5979 | 537.9873 | 588.3358 | 516.7456
2207.5979 | 537.8324 | 590.1641 | 517.4728
2208.5979 | 537.6673 | 589.6935 | 520.9233
2209.5979 | 537.8672 | 591.5076 | 519.9155
2210.5979 | 537.0038 | 587.692 | 519.4402
2211.5979 | 537.8347 | 585.7496 | 519.65
2212.5979 | 535.6382 | 581.9635 | 519.8693
2213.5979 | 534.8741 | 580.0271 | 517.6767
2214.5979 | 535.6337 | 581.0477 | 515.4683
2215.5979 | 535.1218 | 582.4536 | 515.299
2216.5979 | 535.4034 | 582.8213 | 515.6959
2217.5979 | 534.2569 | 583.372 | 514.6068
2218.5979 | 533.9071 | 586.766 | 519.8324
2219.5979 | 534.5724 | 587.112 | 520.7452
2220.5979 | 535.2444 | 588.3188 | 520.5975
2221.5979 | 535.809 | 586.3847 | 520.4506
2222.5979 | 535.5274 | 590.921 | 521.1694
2223.5979 | 535.4095 | 588.915 | 523.2591
2224.5979 | 534.2628 | 587.6674 | 525.4869
2225.5979 | 533.2397 | 584.5744 | 524.6123
2226.5979 | 530.6756 | 579.0377 | 522.2318
2227.5979 | 529.6228 | 575.6932 | 519.8839
2228.5979 | 530.8635 | 574.568 | 518.4437
2229.5979 | 530.8703 | 577.9787 | 517.7383
2230.5979 | 531.7039 | 577.6826 | 517.2755
2231.5979 | 532.6147 | 579.4919 | 517.0935
2232.5979 | 532.1557 | 582.3642 | 519.0281
2233.5979 | 532.7484 | 584.7717 | 518.1261
2234.5979 | 532.203 | 583.3244 | 519.8158
2235.5979 | 531.6799 | 584.9696 | 520.2764
2236.5979 | 533.6569 | 586.2433 | 519.2375
2237.5979 | 536.5443 | 588.807 | 520.137
2238.5979 | 535.7438 | 589.774 | 520.1557
2239.5979 | 535.6723 | 587.1926 | 519.0499
2240.5979 | 535.9067 | 584.5667 | 517.4833
2241.5979 | 536.0044 | 584.8556 | 515.91
2242.5979 | 537.6332 | 583.8079 | 514.0377
2243.5979 | 539.6153 | 583.0027 | 513.0726
2244.5979 | 540.3234 | 582.1838 | 514.2897
2245.5979 | 542.896 | 581.5419 | 515.0326
2246.5979 | 543.3394 | 581.0955 | 514.9434
2247.5979 | 542.3944 | 582.1685 | 515.1487
2248.5979 | 542.704 | 579.587 | 516.3078
2249.5979 | 541.7647 | 581.1594 | 515.449
2250.5979 | 543.5554 | 581.6004 | 514.2729
2251.5979 | 545.8461 | 584.5577 | 515.0051
2252.5979 | 544.7777 | 582.8717 | 515.6932
2253.5979 | 543.4318 | 580.7581 | 515.5989
2254.5979 | 544.5476 | 583.0912 | 516.4549
2255.5979 | 546.1639 | 589.3384 | 516.7633
2256.5979 | 547.3686 | 592.0612 | 517.5539
2257.5979 | 547.4322 | 590.8598 | 518.3953
2258.5979 | 546.7653 | 593.2498 | 518.5098
2259.5979 | 547.3265 | 595.3269 | 518.4467
2260.5979 | 547.7192 | 594.1491 | 519.1474
2261.5979 | 550.0498 | 595.4795 | 520.3275
2262.5979 | 550.2271 | 595.3054 | 519.5472
2263.5979 | 548.9122 | 593.3725 | 520.0308
2264.5979 | 547.7826 | 590.7988 | 519.9526
2265.5979 | 546.8364 | 586.1081 | 519.1261
2266.5979 | 544.8572 | 580.6213 | 517.5361
2267.5979 | 543.6213 | 579.059 | 516.1662
2268.5979 | 543.2895 | 577.5702 | 516.7276
2269.5979 | 543.8019 | 578.6435 | 517.9849
2270.5979 | 543.3382 | 576.5391 | 517.6453
2271.5979 | 543.5376 | 579.3032 | 517.3928
2272.5979 | 543.6938 | 581.8362 | 517.0546
2273.5979 | 544.0243 | 580.7509 | 515.7883
2274.5979 | 544.0068 | 583.4157 | 515.7181
2275.5979 | 544.7192 | 583.4232 | 515.58
2276.5979 | 546.1447 | 586.1481 | 518.187
2277.5979 | 546.8094 | 585.9346 | 520.3072
2278.5979 | 545.9084 | 585.9492 | 520.0371
2279.5979 | 545.6599 | 588.8473 | 521.5606
2280.5979 | 545.8327 | 587.3482 | 521.9853
2281.5979 | 544.4731 | 587.3815 | 521.3534
2282.5979 | 544.0554 | 590.3601 | 522.8013
2283.5979 | 543.7249 | 589.9317 | 522.4361
2284.5979 | 543.6922 | 590.5363 | 524.5365
2285.5979 | 541.7903 | 588.4673 | 523.2726
2286.5979 | 542.2207 | 589.0979 | 522.7819
2287.5979 | 542.2989 | 587.6847 | 521.3223
2288.5979 | 543.264 | 591.4319 | 519.7444
2289.5979 | 544.2603 | 592.7079 | 520.4447
2290.5979 | 542.7288 | 591.0597 | 521.317
2291.5979 | 541.6025 | 587.358 | 521.1433
2292.5979 | 539.6643 | 584.5177 | 520.2606
2293.5979 | 539.4138 | 587.3106 | 518.7563
2294.5979 | 541.4651 | 587.2282 | 518.3537
2295.5979 | 542.3745 | 590.2605 | 520.3768
2296.5979 | 541.5781 | 586.647 | 520.9808
2297.5979 | 539.7128 | 583.2156 | 520.0704
2298.5979 | 539.1087 | 582.1214 | 518.4636
2299.5979 | 539.6221 | 582.0637 | 518.8333
2300.5979 | 539.5384 | 583.2458 | 519.4219
2301.5979 | 538.4547 | 582.3282 | 520.2061
2302.6135 | 538.9122 | 584.0418 | 522.2083
2303.5979 | 538.0013 | 584.4431 | 522.6524
2304.6135 | 540.7522 | 587.32 | 526.2372
2305.5979 | 540.6596 | 586.3031 | 526.7161
2306.5979 | 540.3813 | 589.0243 | 526.7527
2307.5979 | 540.7157 | 589.1343 | 526.8948
2308.5979 | 540.7911 | 592.0042 | 524.6629
2309.5979 | 540.2374 | 594.4402 | 523.1718
2310.5979 | 540.694 | 593.1436 | 523.2066
2311.5979 | 540.1018 | 588.6619 | 522.1455
2312.5979 | 541.0232 | 589.5898 | 521.9168
2313.5979 | 540.2334 | 588.6922 | 524.5092
2314.5979 | 539.1283 | 586.7722 | 524.1469
2315.5979 | 540.3929 | 588.7665 | 524.1102
2316.5979 | 543.0303 | 592.6247 | 527.07
2317.5979 | 541.6729 | 592.1233 | 525.7297
2318.5979 | 542.4865 | 592.8413 | 526.2117
2319.5979 | 542.3933 | 593.1036 | 526.9775
2320.5979 | 543.4222 | 598.4454 | 527.1497
2321.5979 | 543.8635 | 597.2166 | 526.5689
2322.5979 | 543.9153 | 595.2225 | 526.9509
2323.5979 | 543.6645 | 592.8375 | 527.26
2324.5979 | 543.6262 | 593.3666 | 526.3111
2325.5979 | 544.1434 | 598.375 | 525.4523
2326.5979 | 544.4854 | 595.3741 | 525.0457
2327.5979 | 545.2795 | 595.0283 | 526.9734
2328.5979 | 547.2459 | 593.9008 | 527.1886
2329.5979 | 548.9223 | 595.7268 | 527.2058
2330.5979 | 549.3745 | 593.7639 | 526.9822
2331.5979 | 548.6596 | 596.3853 | 528.0589
2332.5979 | 548.7128 | 595.7683 | 527.8089
2333.5979 | 548.4443 | 594.5581 | 528.2212
2334.5979 | 547.5534 | 592.8453 | 528.072
2335.5979 | 547.0416 | 593.0673 | 529.1948
2336.5979 | 545.6079 | 590.3556 | 527.6658
2337.5979 | 544.5063 | 590.3487 | 528.6796
2338.5979 | 545.2777 | 593.2782 | 527.7868
2339.5979 | 545.9874 | 595.8862 | 528.2283
2340.5979 | 546.875 | 596.5893 | 527.007
2341.5979 | 546.6096 | 594.0219 | 527.7058
2342.5979 | 545.7897 | 592.047 | 528.4262
2343.5979 | 543.8913 | 586.7887 | 528.3757
2344.5979 | 544.1343 | 585.5372 | 527.3768
2345.5979 | 544.978 | 588.8351 | 526.5915
2346.5979 | 546.266 | 589.4852 | 526.7833
2347.5979 | 544.91 | 587.6584 | 527.2615
2348.5979 | 544.183 | 586.4925 | 527.8336
2349.5979 | 544.1046 | 587.0797 | 527.7224
2350.5979 | 543.7819 | 590.6425 | 527.737
2351.5979 | 544.7955 | 593.1073 | 529.7866
2352.5979 | 544.4066 | 589.1838 | 529.5242
2353.5979 | 544.2441 | 590.9548 | 530.2454
2354.5979 | 546.154 | 591.0494 | 531.0148
2355.5979 | 545.9013 | 590.7198 | 529.5579
2356.5979 | 544.1421 | 590.9352 | 529.0496
2357.5979 | 544.362 | 590.7407 | 531.5503
2358.5979 | 545.0234 | 589.1003 | 531.4899
2359.5979 | 544.6358 | 588.8485 | 531.8235
2360.5979 | 545.2656 | 589.6397 | 532.939
2361.5979 | 547.3604 | 593.8269 | 533.3945
2362.5979 | 547.9569 | 593.7359 | 532.0731
2363.5979 | 548.5235 | 593.8712 | 531.0062
2364.6135 | 547.2408 | 591.9077 | 531.8928
2365.5979 | 546.6401 | 590.0331 | 532.2603
2366.6135 | 545.364 | 587.6097 | 530.9495
2367.5979 | 545.6699 | 587.8428 | 529.112
2368.6135 | 545.5803 | 585.1668 | 529.5122
2369.5979 | 544.0474 | 582.6984 | 528.6264
2370.5979 | 544.9767 | 582.9871 | 528.5852
2371.5979 | 544.8977 | 582.4238 | 528.6459
2372.5979 | 545.0215 | 579.6428 | 527.3589
2373.5979 | 544.9282 | 579.8537 | 525.9367
2374.5979 | 545.198 | 580.4764 | 526.8703
2375.5979 | 544.8133 | 582.2568 | 528.0366
2376.5979 | 543.6416 | 583.8357 | 527.8966
2377.5979 | 544.0074 | 585.5223 | 527.5573
2378.5979 | 544.1373 | 583.3301 | 525.2995
2379.5979 | 545.1629 | 583.0991 | 524.9295
2380.5979 | 546.1146 | 581.1231 | 524.7179
2381.5979 | 545.3864 | 579.3432 | 525.688
2382.5979 | 546.0641 | 579.8857 | 527.8706
2383.5979 | 546.6643 | 577.7437 | 529.8232
2384.5979 | 546.0483 | 578.6424 | 531.061
2385.5979 | 545.812 | 579.6561 | 532.3275
2386.5979 | 545.4577 | 577.2368 | 532.6747
2387.5979 | 545.2529 | 574.4544 | 531.7946
2388.5979 | 544.3419 | 571.9541 | 531.5799
2389.5979 | 543.4691 | 571.9397 | 530.5612
2390.5979 | 542.0992 | 570.064 | 528.9238
2391.5979 | 543.3067 | 573.9792 | 531.8779
2392.5979 | 544.2621 | 575.747 | 531.5635
2393.5979 | 544.3229 | 576.5266 | 531.0241
2394.5979 | 545.7167 | 575.5313 | 530.8787
2395.5979 | 545.8399 | 574.9173 | 530.8107
2396.5979 | 544.6411 | 573.6145 | 532.4707
2397.5979 | 544.8087 | 572.2006 | 532.7144
2398.5979 | 545.0168 | 573.7089 | 532.0252
2399.5979 | 545.516 | 574.4629 | 533.0522
2400.5979 | 545.0419 | 572.8719 | 534.8732
2401.5979 | 544.2453 | 572.8708 | 534.6868
2402.5979 | 543.3907 | 574.5017 | 535.5996
2403.5979 | 542.0237 | 574.3427 | 534.4372
2404.5979 | 541.2972 | 574.3393 | 533.7041
2405.5979 | 542.2148 | 573.5702 | 532.8989
2406.5979 | 542.4165 | 571.6864 | 532.5845
2407.5979 | 541.8129 | 572.3168 | 533.4727
2408.5979 | 541.6406 | 573.2375 | 534.577
2409.5979 | 541.4241 | 574.8687 | 534.2162
2410.5979 | 540.0846 | 573.2048 | 534.5743
2411.5979 | 541.5007 | 576.4195 | 535.2768
2412.5979 | 542.1295 | 579.0043 | 536.5225
2413.5979 | 541.463 | 580.8788 | 535.6547
2414.5979 | 541.6489 | 582.3729 | 536.9165
2415.5979 | 541.2221 | 581.3978 | 535.7701
2416.5979 | 542.1419 | 581.0812 | 536.1193
2417.5979 | 540.7986 | 580.404 | 535.2484
2418.5979 | 541.2775 | 580.311 | 535.8692
2419.5979 | 541.6863 | 579.8612 | 536.9891
2420.5979 | 541.7879 | 578.3025 | 536.1013
2421.5979 | 541.3931 | 576.2459 | 534.7512
2422.5979 | 540.2002 | 576.4925 | 533.9114
2423.5979 | 540.3826 | 576.9025 | 533.8425
2424.5979 | 541.228 | 578.7464 | 533.3697
2425.5979 | 541.9958 | 580.3943 | 534.3053
2426.5979 | 544.1502 | 581.8533 | 535.3927
2427.5979 | 545.1798 | 583.0232 | 537.4287
2428.5979 | 543.3943 | 579.8389 | 535.9656
2429.5979 | 541.6965 | 576.3633 | 533.6445
2430.5979 | 543.4486 | 579.071 | 534.8557
2431.5979 | 543.276 | 578.9039 | 536.3127
2432.5979 | 544.2449 | 580.1353 | 537.5158
2433.5979 | 543.7639 | 581.5622 | 536.9843
2434.6135 | 543.6398 | 582.71 | 536.5098
2435.5979 | 543.1665 | 580.0949 | 536.368
2436.5979 | 541.3449 | 576.0795 | 535.3946
2437.5979 | 540.5434 | 574.9575 | 534.6559
2438.5979 | 539.2409 | 573.7005 | 535.1187
2439.5979 | 540.0867 | 576.6977 | 535.1959
2440.5979 | 540.347 | 578.2523 | 534.7994
2441.5979 | 540.0782 | 577.1243 | 533.0135
2442.5979 | 540.9823 | 577.2502 | 531.6951
2443.5979 | 542.4265 | 577.1617 | 531.3538
2444.5979 | 541.0345 | 575.1117 | 533.0837
2445.5979 | 539.7491 | 573.5247 | 533.4308
2446.5979 | 539.6987 | 571.6444 | 534.0458
2447.5979 | 540.3786 | 571.3749 | 533.6533
2448.5979 | 540.8167 | 572.4902 | 535.3991
2449.5979 | 539.5074 | 572.4996 | 535.4713
2450.5979 | 537.6299 | 571.7669 | 536.3871
2451.5979 | 536.7851 | 571.2242 | 535.4457
2452.5979 | 536.9042 | 572.0502 | 535.633
2453.5979 | 536.7 | 574.0025 | 537.1397
2454.5979 | 535.8937 | 572.6101 | 537.1321
2455.5979 | 537.627 | 574.4424 | 536.2528
2456.5979 | 537.5955 | 576.921 | 535.4224
2457.5979 | 539.1832 | 577.9451 | 535.845
2458.5979 | 539.5029 | 579.449 | 536.5305
2459.5979 | 540.3281 | 581.3623 | 537.2568
2460.5979 | 539.9418 | 581.1277 | 538.0817
2461.5979 | 540.6579 | 578.8877 | 537.7554
2462.5979 | 538.652 | 575.2589 | 536.6741
2463.5979 | 537.8266 | 571.8907 | 535.0011
2464.5979 | 537.919 | 571.2657 | 534.8831
2465.5979 | 537.8236 | 569.9209 | 534.2096
2466.5979 | 537.011 | 567.0817 | 533.8408
2467.5979 | 536.0949 | 564.2328 | 533.0976
2468.5979 | 535.2869 | 562.3721 | 531.2241
2469.5979 | 535.3192 | 561.5764 | 531.519
2470.5979 | 535.7746 | 561.5551 | 533.0347
2471.5979 | 535.0708 | 559.7509 | 532.7481
2472.5979 | 536.2472 | 560.7529 | 533.9702
2473.5979 | 535.5674 | 561.5441 | 534.7588
2474.5979 | 534.6684 | 560.8079 | 534.37
2475.5979 | 534.6842 | 561.0095 | 533.1326
2476.5979 | 534.7311 | 561.0534 | 533.4748
2477.5979 | 534.6242 | 562.5063 | 535.8219
2478.5979 | 533.3498 | 561.0398 | 535.2938
2479.5979 | 533.963 | 560.3935 | 534.0053
2480.5979 | 534.0844 | 560.7151 | 532.6718
2481.5979 | 535.7247 | 563.4423 | 534.2004
2482.5979 | 537.3297 | 564.2306 | 535.1363
2483.5979 | 537.7974 | 564.0677 | 534.5327
2484.6135 | 538.9904 | 562.1843 | 533.162
2485.5979 | 538.4542 | 560.6011 | 532.1912
2486.6135 | 536.7881 | 559.0439 | 533.053
2487.5979 | 537.0844 | 559.8021 | 534.7499
2488.5979 | 536.8561 | 559.3681 | 534.6559
2489.5979 | 536.2379 | 558.8704 | 533.7438
2490.5979 | 536.6151 | 562.4017 | 533.2552
2491.5979 | 538.1999 | 564.5365 | 532.9468
2492.5979 | 539.5732 | 565.7305 | 532.7435
2493.5979 | 539.2375 | 565.1492 | 531.8687
2494.5979 | 538.8158 | 564.935 | 531.4327
2495.5979 | 538.6111 | 564.6898 | 530.5079
2496.5979 | 538.8438 | 562.4862 | 529.8152
2497.5979 | 538.7595 | 563.4104 | 530.0299
2498.5979 | 539.131 | 564.3023 | 531.9133
2499.5979 | 538.025 | 563.5429 | 531.8899
2500.5979 | 537.2438 | 561.2888 | 530.3882
2501.5979 | 536.4546 | 559.0673 | 528.5229
2502.5979 | 536.6171 | 560.634 | 528.5171
2503.5979 | 536.9269 | 564.1426 | 528.1826
2504.5979 | 537.9138 | 566.1182 | 529.8894
2505.5979 | 537.2947 | 564.3044 | 529.3154
2506.5979 | 537.8403 | 564.3187 | 528.8807
2507.5979 | 539.5832 | 565.8536 | 528.8206
2508.5979 | 541.6323 | 570.5557 | 529.3917
2509.5979 | 542.5902 | 572.873 | 533.2374
2510.5979 | 544.7193 | 573.2568 | 534.6126
2511.5979 | 545.367 | 571.4043 | 533.7975
2512.5979 | 545.0243 | 573.0273 | 533.7243
2513.5979 | 545.25 | 575.3864 | 534.9126
2514.5979 | 544.2957 | 573.6028 | 534.2855
2515.5979 | 544.4737 | 575.8436 | 534.0081
2516.5979 | 545.9045 | 576.2587 | 535.4369
2517.5979 | 545.0948 | 574.826 | 534.5975
2518.5979 | 545.9155 | 573.1363 | 533.823
2519.5979 | 546.1461 | 572.3876 | 532.6916
2520.5979 | 546.2175 | 575.9538 | 533.2475
2521.5979 | 546.7375 | 576.1621 | 534.0347
2522.5979 | 547.9033 | 577.5972 | 534.7005
2523.5979 | 547.9866 | 576.9265 | 535.2915
2524.5979 | 549.2114 | 576.4272 | 534.2582
2525.5979 | 551.3059 | 577.4434 | 534.7963
2526.5979 | 552.8942 | 577.9647 | 535.436
2527.5979 | 554.1546 | 577.7963 | 535.0134
2528.5979 | 552.2543 | 575.6762 | 537.3221
2529.5979 | 551.3344 | 573.9823 | 537.6807
2530.5979 | 551.5302 | 576.1168 | 536.4542
2531.5979 | 550.0188 | 574.8471 | 535.3449
2532.5979 | 549.2231 | 575.1409 | 537.3828
2533.5979 | 549.7988 | 575.5894 | 538.5736
2534.5979 | 549.7694 | 576.5589 | 538.987
2535.5979 | 551.3211 | 581.0471 | 539.9434
2536.5979 | 551.2012 | 578.4086 | 539.805
2537.5979 | 551.4808 | 577.6497 | 539.7909
2538.5979 | 552.4825 | 578.9872 | 542.9509
2539.5979 | 553.9385 | 578.2527 | 541.8289
2540.5979 | 552.9471 | 576.702 | 541.7715
2541.5979 | 552.4246 | 597.1949 | 542.6375
2542.5979 | 550.9407 | 597.4502 | 543.5761
2543.5979 | 550.0467 | 591.2565 | 543.7859
2544.5979 | 549.5239 | 585.2198 | 544.0919
2545.5979 | 549.1974 | 581.3918 | 544.7225
2546.5979 | 549.4302 | 578.9734 | 544.2596
2547.5979 | 550.191 | 577.7446 | 544.2733
2548.5979 | 549.2659 | 576.7392 | 543.4921
2549.5979 | 547.4432 | 573.2398 | 541.8005
2550.5979 | 546.3804 | 573.1612 | 541.1304
2551.5979 | 545.5685 | 572.2457 | 541.924
2552.5979 | 546.3694 | 573.1334 | 541.1947
2553.5979 | 547.078 | 570.0611 | 539.3449
2554.5979 | 547.404 | 570.1961 | 539.3257
2555.6135 | 548.5823 | 573.0071 | 540.7091
2556.6135 | 549.1329 | 573.3704 | 540.3777
2557.6135 | 547.1261 | 569.8983 | 537.4584
2558.5979 | 545.9486 | 567.6578 | 536.4579
2559.5979 | 545.7677 | 568.0221 | 536.8584
2560.5979 | 545.9003 | 569.555 | 536.5101
2561.5979 | 546.7227 | 571.0285 | 536.3018
2562.5979 | 548.0782 | 570.4194 | 535.6057
2563.5979 | 548.1407 | 570.3014 | 534.0955
2564.5979 | 548.5892 | 569.5082 | 535.7687
2565.5979 | 548.789 | 570.1287 | 535.7341
2566.5979 | 549.7999 | 568.605 | 536.1756
2567.5979 | 550.3202 | 567.0604 | 535.5415
2568.5979 | 549.5411 | 565.4908 | 534.7121
2569.5979 | 549.2285 | 565.9687 | 535.0311
2570.5979 | 548.187 | 564.0991 | 534.4713
2571.5979 | 547.9973 | 564.5474 | 533.5647
2572.5979 | 549.5319 | 567.4874 | 532.9874
2573.5979 | 549.5586 | 568.1854 | 533.8223
2574.5979 | 548.6274 | 566.5014 | 533.5838
2575.5979 | 547.9219 | 564.0777 | 534.0497
2576.5979 | 547.3861 | 565.1004 | 532.9054
2577.5979 | 548.6261 | 565.156 | 532.8706
2578.5979 | 550.2943 | 568.893 | 533.9993
2579.5979 | 550.4225 | 568.9104 | 535.2698
2580.5979 | 549.2749 | 567.8916 | 535.2876
2581.5979 | 550.6143 | 567.4721 | 535.2237
2582.5979 | 549.4121 | 565.3634 | 533.4506
2583.5979 | 549.1866 | 565.9066 | 533.3071
2584.5979 | 549.2612 | 565.8024 | 533.2758
2585.5979 | 547.5396 | 565.4224 | 532.5125
2586.5979 | 547.0721 | 567.1752 | 532.4987
2587.5979 | 547.6908 | 568.6436 | 532.2084
2588.5979 | 548.7049 | 567.6924 | 532.0323
2589.5979 | 548.4438 | 566.6794 | 531.5257
2590.5979 | 547.6674 | 566.9213 | 535.4231
2591.5979 | 549.4807 | 567.1435 | 537.0429
2592.5979 | 550.4667 | 569.0748 | 539.1563
2593.5979 | 552.3227 | 571.5854 | 540.8108
2594.5979 | 551.4722 | 569.968 | 539.5338
2595.5979 | 550.4207 | 569.5546 | 537.3737
2596.5979 | 550.9736 | 567.5399 | 538.0598
2597.5979 | 550.3977 | 565.9355 | 537.9329
2598.5979 | 550.9851 | 566.9973 | 537.3112
2599.5979 | 551.4757 | 567.357 | 536.4698
2600.5979 | 552.3144 | 566.2258 | 536.2873
2601.5979 | 549.8375 | 565.0268 | 536.8741
2602.5979 | 548.2026 | 562.5696 | 536.1676
2603.5979 | 548.3932 | 564.9547 | 536.3282
2604.5979 | 547.9149 | 565.9125 | 535.9936
2605.5979 | 548.0443 | 563.9349 | 535.1864
2606.5979 | 548.9352 | 563.4802 | 535.6004
2607.5979 | 548.5193 | 563.9361 | 535.1708
2608.5979 | 549.9715 | 567.9979 | 537.9317
2609.5979 | 550.4515 | 568.2644 | 537.606
2610.5979 | 551.1025 | 567.1509 | 536.4251
2611.5979 | 550.2719 | 565.2539 | 534.9939
2612.5979 | 549.8324 | 565.6588 | 534.4199
2613.5979 | 549.214 | 566.3402 | 533.9141
2614.5979 | 548.3596 | 566.8228 | 534.6736
2615.5979 | 548.1781 | 567.338 | 534.6056
2616.5979 | 548.0357 | 568.5979 | 534.2902
2617.5979 | 548.9198 | 568.119 | 534.435
2618.5979 | 549.6483 | 568.8131 | 535.3889
2619.5979 | 550.3125 | 569.4464 | 536.7394
2620.5979 | 550.3916 | 570.8337 | 538.4084
2621.5979 | 548.9139 | 569.9598 | 539.5473
2622.5979 | 549.7813 | 571.0398 | 539.8107
2623.5979 | 550.9731 | 571.0457 | 539.1243
2624.5979 | 553.2195 | 572.1593 | 538.4874
2625.5979 | 555.4558 | 573.8253 | 540.3589
2626.5979 | 555.045 | 574.9186 | 541.7898
2627.5979 | 556.7711 | 576.0071 | 542.2729
2628.5979 | 556.7986 | 575.4919 | 541.894
2629.5979 | 555.9948 | 574.9935 | 541.1486
2630.5979 | 555.4632 | 574.1724 | 541.039
2631.5979 | 554.6184 | 572.6478 | 541.513
2632.5979 | 555.4391 | 570.5127 | 540.5652
2633.5979 | 554.1831 | 569.8419 | 541.0326
2634.5979 | 553.8149 | 570.4175 | 542.0206
2635.5979 | 553.7425 | 568.8512 | 541.1392
2636.5979 | 552.4779 | 567.1985 | 539.8218
2637.5979 | 552.6269 | 567.7705 | 541.1724
2638.5979 | 553.1199 | 568.5556 | 542.1047
2639.5979 | 553.289 | 568.9999 | 542.4221
2640.5979 | 552.9403 | 569.0462 | 541.6051
2641.5979 | 553.9112 | 569.318 | 541.6466
2642.5979 | 554.564 | 569.0992 | 540.9274
2643.5979 | 556.5688 | 567.9355 | 539.8628
2644.5979 | 556.5096 | 567.8351 | 538.7352
2645.5979 | 555.5189 | 565.4989 | 537.5871
2646.5979 | 555.2465 | 564.9253 | 536.7178
2647.5979 | 554.902 | 564.5827 | 538.8355
2648.5979 | 554.563 | 563.3508 | 539.0859
2649.5979 | 554.045 | 561.3501 | 538.4168
2650.5979 | 554.4443 | 563.0599 | 537.5877
2651.5979 | 555.5033 | 564.984 | 536.8836
2652.5979 | 555.9837 | 565.5004 | 537.0782
2653.5979 | 554.4664 | 564.4293 | 536.9013
2654.5979 | 552.0426 | 562.2664 | 535.9315
2655.5979 | 553.8282 | 562.8006 | 535.7649
2656.5979 | 554.3679 | 562.0074 | 534.9438
2657.5979 | 555.8908 | 565.1477 | 535.5596
2658.5979 | 555.9568 | 565.813 | 537.1315
2659.5979 | 555.7212 | 564.2092 | 536.3189
2660.5979 | 555.5507 | 563.9428 | 537.3225
2661.5979 | 554.7244 | 563.5945 | 537.1895
2662.5979 | 554.2449 | 563.4136 | 537.7569
2663.5979 | 554.4065 | 565.1403 | 539.2698
2664.5979 | 554.5374 | 567.706 | 540.7643
2665.5979 | 554.0746 | 568.1235 | 540.9227
2666.5979 | 554.7291 | 569.1916 | 540.9598
2667.5979 | 555.0481 | 568.5252 | 541.0075
2668.5979 | 555.6242 | 568.5759 | 541.2838
2669.5979 | 555.1917 | 568.7276 | 543.1119
2670.5979 | 554.097 | 567.1954 | 543.4927
2671.5979 | 553.2543 | 564.1595 | 543.8668
2672.5979 | 552.6608 | 562.4983 | 544.7512
2673.5979 | 552.1103 | 560.2833 | 542.8218
2674.5979 | 551.9128 | 558.2004 | 541.552
2675.5979 | 552.0445 | 557.2142 | 541.7792
2676.5979 | 552.6627 | 557.5357 | 542.3589
2677.5979 | 552.1293 | 556.0106 | 541.7926
2678.5979 | 550.5665 | 554.0587 | 542.3942
2679.5979 | 549.5926 | 552.8659 | 543.3896
2680.5979 | 550.651 | 553.1057 | 545.313
2681.5979 | 550.6688 | 554.6777 | 546.6165
2682.5979 | 551.7721 | 555.79 | 547.5907
2683.5979 | 552.9393 | 555.735 | 546.9869
2684.5979 | 551.0991 | 554.1833 | 545.5129
2685.5979 | 552.1649 | 554.1687 | 543.8579
2686.5979 | 552.2396 | 553.4449 | 542.1493
2687.5979 | 551.2442 | 552.733 | 541.6689
2688.5979 | 550.7785 | 551.767 | 540.6159
2689.5979 | 548.3043 | 550.7761 | 539.4923
2690.5979 | 548.4551 | 550.2883 | 537.9993
2691.5979 | 549.8703 | 552.2556 | 537.7497
2692.5979 | 550.7561 | 554.9582 | 536.7787
2693.5979 | 549.7484 | 553.8206 | 534.9451
2694.5979 | 549.6404 | 555.8948 | 534.1248
2695.5979 | 550.0082 | 556.1729 | 533.4558
2696.5979 | 550.6732 | 558.3022 | 534.9735
2697.5979 | 551.69 | 559.5293 | 537.6022
2698.5979 | 551.2429 | 561.1812 | 540.8623
2699.5979 | 552.0523 | 565.284 | 542.4781
2700.5979 | 554.1805 | 569.8565 | 543.5422
2701.5979 | 557.1818 | 572.6725 | 544.5409
2702.5979 | 558.2415 | 572.0149 | 544.1759
2703.6135 | 558.6035 | 574.8891 | 544.2727
2704.5979 | 560.3667 | 576.2896 | 543.9334
2705.5979 | 560.8797 | 574.6705 | 543.722
2706.5979 | 561.1987 | 573.6596 | 543.0486
2707.5979 | 561.9723 | 575.0157 | 542.5026
2708.5979 | 563.0749 | 579.8102 | 544.5662
2709.5979 | 565.4136 | 583.2252 | 544.8156
2710.5979 | 566.0206 | 581.2867 | 544.0523
2711.5979 | 564.749 | 580.4168 | 544.3415
2712.5979 | 564.3432 | 578.7535 | 545.3938
2713.5979 | 562.2863 | 577.6022 | 548.4489
2714.5979 | 559.6073 | 576.1862 | 547.5467
2715.5979 | 557.4607 | 572.8786 | 545.0327
2716.5979 | 558.1344 | 570.8617 | 543.1871
2717.5979 | 558.8374 | 571.8563 | 543.7755
2718.6135 | 557.9302 | 572.9992 | 543.6023
2719.5979 | 557.2716 | 572.9467 | 543.9315
2720.5979 | 558.7665 | 574.1161 | 543.5185
2721.5979 | 562.8356 | 576.7049 | 544.4369
2722.5979 | 567.1485 | 578.1207 | 544.5316
2723.5979 | 571.9397 | 579.3147 | 546.0021
2724.5979 | 573.6336 | 579.619 | 546.295
2725.5979 | 574.5039 | 580.6892 | 548.7146
2726.5979 | 575.423 | 580.3901 | 550.1986
2727.5979 | 574.6927 | 580.9804 | 550.7946
2728.5979 | 574.0359 | 580.8527 | 552.8385
2729.5979 | 576.9312 | 581.8157 | 553.3273
2730.5979 | 576.2053 | 582.5309 | 553.0827
2731.5979 | 576.8736 | 583.6472 | 553.9648
2732.5979 | 578.2769 | 584.496 | 555.0901
2733.6135 | 579.8243 | 586.9839 | 556.5254
2734.5979 | 581.1412 | 587.1065 | 556.6118
2735.5979 | 579.4942 | 588.439 | 556.6257
2736.5979 | 577.9004 | 589.7303 | 557.1012
2737.5979 | 578.3555 | 590.57 | 556.832
2738.5979 | 579.4713 | 592.3613 | 557.1342
2739.5979 | 581.573 | 593.1563 | 559.0724
2740.5979 | 581.7334 | 594.7526 | 558.5283
2741.5979 | 583.2838 | 596.1982 | 558.5553
2742.5979 | 582.8321 | 596.6379 | 558.9882
2743.5979 | 581.3865 | 595.0857 | 557.6083
2744.5979 | 580.6271 | 593.539 | 556.6245
2745.5979 | 578.6367 | 594.4851 | 557.2368
2746.5979 | 580.8473 | 596.2297 | 556.7944
2747.5979 | 581.8764 | 596.0295 | 556.793
2748.5979 | 581.412 | 595.5309 | 558.8754
2749.5979 | 578.3142 | 594.2453 | 560.1623
2750.5979 | 578.3847 | 596.7672 | 559.8911
2751.5979 | 577.4682 | 595.3743 | 561.8609
2752.5979 | 578.7722 | 595.2753 | 563.152
2753.5979 | 576.6922 | 597.401 | 565.1796
2754.5979 | 579.3933 | 599.7936 | 566.1614
2755.5979 | 581.7647 | 601.5139 | 566.1624
2756.5979 | 582.9937 | 599.493 | 567.3825
2757.5979 | 582.5331 | 597.2511 | 568.6349
2758.5979 | 581.9527 | 593.5099 | 568.3116
2759.5979 | 581.3725 | 590.8905 | 567.6833
2760.5979 | 580.0266 | 589.5887 | 567.1092
2761.5979 | 578.2158 | 589.9149 | 566.4329
2762.5979 | 579.9717 | 591.0489 | 565.473
2763.5979 | 578.5246 | 591.7804 | 565.0556
2764.5979 | 578.7658 | 591.1174 | 562.9354
2765.5979 | 579.0592 | 588.117 | 561.4384
2766.5979 | 575.2134 | 584.5954 | 560.5627
2767.5979 | 576.9329 | 582.6348 | 559.7991
2768.5979 | 573.6795 | 580.9906 | 560.2952
2769.5979 | 574.809 | 581.0661 | 559.3593
2770.5979 | 577.1092 | 582.5795 | 560.6684
2771.5979 | 579.647 | 582.4167 | 562.2607
2772.5979 | 585.3826 | 582.0271 | 561.987
2773.5979 | 584.2195 | 583.1646 | 562.7446
2774.5979 | 583.4914 | 585.4048 | 563.4301
2775.5979 | 583.7503 | 584.7508 | 561.987
2776.5979 | 584.8871 | 584.928 | 560.7002
2777.5979 | 585.4614 | 587.9556 | 562.6042
2778.5979 | 584.7488 | 586.2134 | 562.522
2779.5979 | 582.7546 | 586.0789 | 563.1771
2780.5979 | 583.7391 | 585.9047 | 563.4677
2781.5979 | 581.159 | 586.3639 | 562.7902
2782.5979 | 579.1141 | 586.2018 | 562.9012
2783.5979 | 579.3635 | 585.7214 | 562.1724
2784.5979 | 579.2242 | 585.6031 | 561.1472
2785.5979 | 579.4276 | 586.6233 | 562.1469
2786.5979 | 578.449 | 587.1192 | 562.5856
2787.5979 | 577.4562 | 585.0983 | 562.5088
2788.5979 | 577.4702 | 583.6017 | 561.5217
2789.5979 | 576.1891 | 583.1422 | 561.3276
2790.5979 | 575.5615 | 583.0913 | 561.3193
2791.5979 | 575.8128 | 586.2559 | 563.9752
2792.5979 | 575.2127 | 584.7968 | 563.6383
2793.5979 | 576.0936 | 586.6121 | 564.0555
2794.5979 | 578.2811 | 588.8189 | 563.6385
2795.5979 | 576.1381 | 589.0347 | 564.191
2796.5979 | 575.5259 | 589.3855 | 564.4649
2797.5979 | 574.6514 | 593.4706 | 565.0288
2798.5979 | 574.8309 | 592.7136 | 564.133
2799.5979 | 573.951 | 592.0621 | 563.3737
2800.5979 | 573.6165 | 593.1972 | 563.4807
2801.5979 | 574.5437 | 593.998 | 562.6808
2802.5979 | 572.3678 | 591.8685 | 562.2947
2803.5979 | 572.0736 | 592.4756 | 562.7039
2804.5979 | 570.3463 | 590.7703 | 563.2672
2805.5979 | 570.0529 | 591.819 | 564.0319
2806.5979 | 569.5863 | 593.8083 | 562.9559
2807.5979 | 568.8057 | 592.5562 | 561.8889
2808.5979 | 567.5631 | 592.8057 | 562.6461
2809.5979 | 568.8556 | 593.9503 | 564.8234
2810.5979 | 569.105 | 595.2385 | 564.8889
2811.5979 | 570.0926 | 596.5836 | 566.9593
2812.5979 | 569.4249 | 595.5971 | 567.212
2813.5979 | 569.4235 | 597.0711 | 569.2291
2814.5979 | 570.0686 | 595.4102 | 569.1625
2815.5979 | 569.6708 | 594.325 | 568.6432
2816.5979 | 569.3952 | 595.2385 | 569.3239
2817.5979 | 568.717 | 596.2047 | 570.5978
2818.5979 | 569.3925 | 595.6454 | 571.3806
2819.5979 | 568.7456 | 595.6264 | 570.4609
2820.5979 | 570.1852 | 594.5556 | 569.9359
2821.5979 | 569.9264 | 597.616 | 569.5804
2822.5979 | 569.9412 | 597.8423 | 568.6892
2823.5979 | 572.3632 | 599.8435 | 568.7533
2824.5979 | 574.3296 | 597.6062 | 567.7471
2825.5979 | 574.0645 | 596.2131 | 567.1132
2826.5979 | 574.0494 | 593.4876 | 566.517
2827.5979 | 573.392 | 591.7116 | 566.7099
2828.5979 | 573.517 | 592.1904 | 566.8066
2829.5979 | 573.5437 | 591.1941 | 567.7262
2830.5979 | 571.5479 | 589.9149 | 567.1156
2831.5979 | 570.4961 | 590.304 | 566.9114
2832.5979 | 570.8943 | 592.2053 | 568.5006
2833.5979 | 569.4887 | 589.3108 | 567.972
2834.5979 | 568.7319 | 588.3556 | 567.081
2835.5979 | 567.9534 | 589.545 | 570.4297
2836.5979 | 569.1843 | 588.9463 | 570.964
2837.5979 | 570.3339 | 589.9909 | 570.6667
2838.5979 | 569.5091 | 591.23 | 576.1758
2839.5979 | 568.7692 | 590.6921 | 575.6872
2840.5979 | 570.5975 | 591.244 | 575.533
2841.5979 | 569.2958 | 587.4367 | 574.582
2842.5979 | 568.0717 | 585.2349 | 573.8598
2843.5979 | 567.6837 | 584.3582 | 574.538
2844.5979 | 567.5167 | 584.8066 | 574.9753
2845.6135 | 566.6841 | 585.8755 | 575.4985
2846.5979 | 567.3195 | 586.0861 | 575.2108
2847.5979 | 567.037 | 586.1047 | 575.7967
2848.5979 | 567.2498 | 586.3079 | 574.7168
2849.5979 | 566.5004 | 585.8303 | 575.6089
2850.5979 | 565.4825 | 584.8093 | 575.7725
2851.5979 | 565.6825 | 586.327 | 575.6757
2852.5979 | 568.0032 | 587.6832 | 576.3532
2853.5979 | 569.1123 | 587.7408 | 575.0307
2854.5979 | 569.2874 | 585.6081 | 575.1851
2855.6135 | 569.6957 | 584.7423 | 576.8864
2856.5979 | 569.9807 | 585.244 | 579.8961
2857.5979 | 569.4159 | 584.1237 | 578.8906
2858.5979 | 569.3484 | 584.2557 | 577.7856
2859.5979 | 569.8966 | 585.4459 | 577.6971
2860.5979 | 568.9028 | 584.903 | 578.3455
2861.5979 | 568.3069 | 583.9676 | 578.142
2862.5979 | 567.1421 | 581.9874 | 576.4639
2863.5979 | 566.8027 | 582.0823 | 576.3622
2864.5979 | 567.0573 | 581.6746 | 575.9086
2865.5979 | 566.5417 | 581.1742 | 576.0066
2866.5979 | 567.4089 | 585.0908 | 577.6681
2867.5979 | 567.5298 | 584.2382 | 579.1652
2868.5979 | 567.7914 | 584.2018 | 579.1632
2869.5979 | 567.0011 | 582.2226 | 579.1492
2870.5979 | 568.0331 | 581.1711 | 578.7902
2871.5979 | 570.3622 | 581.4275 | 577.4398
2872.5979 | 571.0735 | 579.2868 | 575.9109
2873.5979 | 571.3578 | 577.4702 | 577.2915
2874.5979 | 571.615 | 575.5863 | 579.2684
2875.5979 | 570.8845 | 573.113 | 580.0194
2876.5979 | 569.8972 | 571.9571 | 578.8066
2877.5979 | 568.8711 | 569.9491 | 579.0886
2878.5979 | 567.2461 | 568.1957 | 577.9252
2879.5979 | 568.1202 | 568.2697 | 578.4331
2880.5979 | 568.5022 | 567.9703 | 578.0996
2881.5979 | 568.9029 | 566.4536 | 580.7008
2882.5979 | 570.6657 | 567.3818 | 580.1602
2883.5979 | 571.9261 | 568.3628 | 582.2817
2884.5979 | 571.6373 | 568.8445 | 583.8657
2885.5979 | 569.9984 | 568.1943 | 584.0402
2886.5979 | 568.3637 | 566.2018 | 583.6739
2887.5979 | 565.5479 | 562.9941 | 582.2359
2888.5979 | 564.9368 | 562.8159 | 582.2516
2889.5979 | 564.7574 | 561.3589 | 582.5847
2890.5979 | 562.4808 | 559.5694 | 581.0721
2891.5979 | 562.7587 | 560.1587 | 582.5101
2892.5979 | 561.5714 | 559.1134 | 583.4674
2893.5979 | 562.38 | 559.7578 | 583.3811
2894.5979 | 562.419 | 559.3184 | 582.8014
2895.6135 | 561.6826 | 559.5175 | 583.6537
2896.5979 | 561.5625 | 561.3875 | 585.3118
2897.5979 | 561.6167 | 561.9226 | 585.5547
2898.5979 | 561.9705 | 561.8578 | 585.7531
2899.5979 | 562.0775 | 561.7612 | 584.3707
2900.5979 | 563.754 | 563.0249 | 583.9023
2901.5979 | 564.0796 | 563.3117 | 584.2415
2902.5979 | 564.6377 | 565.6178 | 584.4228
2903.5979 | 568.4106 | 568.5199 | 584.3422
2904.5979 | 573.4182 | 572.3578 | 585.2482
2905.5979 | 574.9276 | 570.1701 | 588.553
2906.5979 | 574.7761 | 568.7081 | 587.1102
2907.5979 | 573.1835 | 567.2692 | 587.1472
2908.5979 | 571.8825 | 567.4952 | 590.8249
2909.5979 | 570.0673 | 566.9969 | 588.7557
2910.5979 | 569.9281 | 566.2041 | 586.5891
2911.5979 | 570.2914 | 564.3308 | 585.5636
2912.5979 | 570.3801 | 562.7999 | 586.0931
2913.5979 | 568.4989 | 560.259 | 585.7442
2914.5979 | 567.854 | 560.4236 | 585.9437
2915.5979 | 567.1229 | 560.7465 | 586.1823
2916.5979 | 568.3667 | 562.0395 | 586.4033
2917.5979 | 569.9604 | 560.4159 | 586.0254
2918.5979 | 571.9441 | 559.9833 | 584.688
2919.5979 | 570.8097 | 559.9159 | 586.0823
2920.5979 | 568.5574 | 556.1401 | 585.7622
2921.5979 | 569.7796 | 556.2947 | 585.7636
2922.5979 | 570.325 | 556.1046 | 586.4426
2923.5979 | 569.0041 | 553.4718 | 587.8216
2924.5979 | 567.6284 | 551.1118 | 585.0037
2925.5979 | 566.4838 | 550.4243 | 583.7995
2926.5979 | 566.0115 | 550.1147 | 582.6771
2927.5979 | 566.1882 | 548.6219 | 581.6887
2928.5979 | 565.8581 | 546.9211 | 580.1568
2929.5979 | 564.7611 | 545.5986 | 578.5094
2930.5979 | 563.3878 | 543.4903 | 578.6027
2931.5979 | 562.7716 | 545.1746 | 579.4954
2932.5979 | 563.5872 | 550.3496 | 581.0135
2933.5979 | 563.9343 | 552.1909 | 580.556
2934.5979 | 563.6315 | 551.8115 | 579.9409
2935.5979 | 563.9095 | 549.702 | 583.8182
2936.5979 | 562.9567 | 549.4296 | 583.363
2937.5979 | 563.5561 | 550.7353 | 583.5323
2938.5979 | 562.7627 | 549.282 | 583.6753
2939.5979 | 562.6232 | 547.0033 | 582.19
2940.5979 | 561.4018 | 546.0133 | 580.9895
2941.5979 | 560.6606 | 544.417 | 580.7359
2942.5979 | 558.9593 | 543.4892 | 580.5075
2943.5979 | 558.1903 | 541.9865 | 579.3717
2944.5979 | 558.7818 | 540.7436 | 578.5441
2945.5979 | 558.7199 | 540.3064 | 578.2531
2946.5979 | 558.6622 | 540.8178 | 578.6933
2947.5979 | 558.4186 | 543.6126 | 579.8833
2948.5979 | 560.8664 | 544.4146 | 579.8251
2949.5979 | 562.4103 | 542.4524 | 578.9035
2950.5979 | 561.3879 | 540.0289 | 583.2388
2951.5979 | 560.3267 | 539.4464 | 589.0792
2952.5979 | 561.0684 | 540.6939 | 593.8359
2953.5979 | 562.5857 | 539.6117 | 595.6204
2954.5979 | 561.0632 | 538.1143 | 595.7556
2955.5979 | 560.3125 | 537.0761 | 596.0183
2956.5979 | 559.6159 | 537.822 | 594.9778
2957.5979 | 560.4966 | 538.1285 | 594.427
2958.5979 | 560.4428 | 538.1938 | 593.4865
2959.5979 | 560.2717 | 537.1644 | 592.0443
2960.5979 | 560.0434 | 535.605 | 590.9734
2961.5979 | 558.3877 | 534.9716 | 589.3982
2962.5979 | 557.9726 | 532.8483 | 589.2114
2963.5979 | 557.6794 | 532.9378 | 587.0706
2964.5979 | 557.1434 | 531.7432 | 585.5128
2965.5979 | 556.1132 | 531.026 | 583.5124
2966.5979 | 556.5242 | 533.0899 | 582.5604
2967.5979 | 556.3082 | 535.0144 | 582.8692
2968.5979 | 555.2509 | 534.1538 | 582.5582
2969.5979 | 555.8923 | 531.4222 | 580.788
2970.5979 | 555.1038 | 529.7746 | 580.3366
2971.5979 | 555.2606 | 529.1769 | 582.0013
2972.5979 | 554.52 | 530.6724 | 582.6292
2973.5979 | 554.1446 | 530.9586 | 581.8698
2974.5979 | 554.4541 | 531.9102 | 581.0748
2975.5979 | 554.3042 | 531.6504 | 580.4528
2976.5979 | 554.299 | 533.1382 | 580.5585
2977.5979 | 554.7358 | 533.6758 | 579.6917
2978.5979 | 555.4775 | 532.5134 | 579.5904
2979.5979 | 554.506 | 531.7927 | 579.5034
2980.5979 | 553.0187 | 529.9932 | 579.4258
2981.5979 | 552.7152 | 529.748 | 578.4253
2982.5979 | 552.2598 | 529.4865 | 576.892
2983.5979 | 552.6362 | 528.2791 | 576.5649
2984.5979 | 553.2266 | 526.2487 | 575.7187
2985.5979 | 552.4035 | 522.8041 | 574.317
2986.5979 | 551.1975 | 520.7755 | 573.3643
2987.5979 | 549.5184 | 517.2431 | 573.4475
2988.5979 | 549.4045 | 515.5843 | 573.6418
2989.5979 | 548.9029 | 514.2601 | 572.4788
2990.5979 | 549.3878 | 514.6816 | 572.3124
2991.5979 | 549.96 | 513.8692 | 572.717
2992.5979 | 550.853 | 512.8369 | 572.2713
2993.5979 | 549.8281 | 511.6964 | 571.3575
2994.5979 | 550.6716 | 511.9885 | 570.7896
2995.5979 | 549.9549 | 510.8304 | 569.8642
2996.6135 | 549.8393 | 510.5479 | 570.964
2997.5979 | 550.9261 | 512.6342 | 571.9158
2998.6135 | 552.4962 | 514.5281 | 571.9633
2999.5979 | 551.4278 | 512.8742 | 571.5136
3000.5979 | 550.9515 | 514.3964 | 572.1475
3001.5979 | 550.9668 | 515.4854 | 573.3644
3002.5979 | 549.2619 | 513.9833 | 574.2715
3003.5979 | 548.1319 | 513.7121 | 574.5665
3004.5979 | 548.3525 | 514.8171 | 574.9418
3005.5979 | 548.7833 | 513.0848 | 574.4014
3006.5979 | 547.3551 | 510.9528 | 575.6343
3007.5979 | 545.836 | 510.8739 | 575.4669
3008.5979 | 545.8577 | 513.4767 | 576.05
3009.5979 | 545.5918 | 512.6036 | 576.9452
3010.5979 | 546.0357 | 511.1477 | 577.3137
3011.5979 | 552.588 | 511.0355 | 576.4099
3012.5979 | 550.6139 | 508.5758 | 575.6002
3013.5979 | 549.7158 | 509.5831 | 575.0972
3014.5979 | 548.1656 | 508.3172 | 574.1794
3015.5979 | 546.6218 | 507.565 | 573.9386
3016.5979 | 547.1779 | 506.6979 | 573.2796
3017.5979 | 546.0089 | 507.9489 | 573.2015
3018.5979 | 544.5664 | 505.7283 | 572.7214
3019.5979 | 544.3502 | 506.2522 | 571.6914
3020.5979 | 543.9964 | 505.1946 | 570.999
3021.5979 | 544.1793 | 505.4811 | 570.8222
3022.5979 | 544.4753 | 565.8734 | 570.3991
3023.5979 | 545.767 | 566.94 | 570.3714
3024.5979 | 545.3781 | 567.8945 | 571.1919
3025.5979 | 544.7657 | 568.7945 | 575.9209
3026.5979 | 543.7348 | 567.075 | 575.1503
3027.5979 | 542.9864 | 565.6955 | 574.2934
3028.5979 | 543.4993 | 565.4613 | 573.9669
3029.5979 | 542.5187 | 564.557 | 574.5509
3030.5979 | 541.834 | 564.0938 | 573.3715
3031.5979 | 540.1888 | 562.9965 | 572.4805
3032.5979 | 541.0831 | 562.7975 | 571.8511
3033.5979 | 541.0912 | 561.3637 | 571.3016
3034.5979 | 540.9496 | 562.4052 | 571.4245
3035.5979 | 541.1224 | 562.3 | 571.2902
3036.5979 | 540.984 | 562.8797 | 570.3954
3037.5979 | 540.2521 | 562.6386 | 569.6256
3038.5979 | 541.3246 | 566.0584 | 569.1494
3039.5979 | 541.5734 | 565.6526 | 569.4215
3040.5979 | 540.6584 | 565.0799 | 569.1775
3041.5979 | 541.9392 | 565.2829 | 569.6491
3042.5979 | 542.3233 | 565.272 | 570.7392
3043.5979 | 541.9877 | 564.0291 | 569.1261
3044.5979 | 542.299 | 563.0289 | 567.9077
3045.5979 | 542.0384 | 562.3641 | 566.7375
3046.5979 | 542.7137 | 563.0385 | 568.6531
3047.5979 | 541.3805 | 563.5184 | 568.4869
3048.5979 | 541.3828 | 562.6847 | 567.8145
3049.5979 | 540.9038 | 561.9752 | 567.2666
3050.5979 | 541.9023 | 562.8753 | 566.8663
3051.5979 | 541.5907 | 562.4397 | 566.7583
3052.5979 | 540.1629 | 560.4309 | 565.6147
3053.5979 | 540.3463 | 559.2188 | 565.9395
3054.5979 | 540.7453 | 558.7784 | 566.0731
3055.5979 | 540.7485 | 558.4346 | 565.7327
3056.5979 | 539.7126 | 556.4768 | 565.3224
3057.5979 | 539.4071 | 556.6487 | 564.4797
3058.5979 | 539.571 | 556.9723 | 564.5539
3059.5979 | 539.4094 | 556.3749 | 564.5899
3060.5979 | 539.39 | 555.2015 | 563.8706
3061.5979 | 538.8705 | 555.9969 | 563.8532
3062.5979 | 538.1545 | 555.1448 | 563.0064
3063.5979 | 537.9265 | 554.4274 | 562.088
3064.5979 | 537.4557 | 553.0858 | 561.6426
3065.5979 | 535.0318 | 551.7075 | 561.4312
3066.5979 | 534.4362 | 551.0787 | 559.9379
3067.5979 | 534.5122 | 549.9874 | 559.8674
3068.5979 | 533.1236 | 548.0773 | 559.5373
3069.5979 | 533.1026 | 548.5264 | 559.209
3070.5979 | 532.2669 | 548.5413 | 558.5966
3071.5979 | 530.4784 | 547.697 | 558.3279
3072.5979 | 530.7744 | 546.7621 | 558.9928
3073.5979 | 529.5475 | 547.5437 | 558.6667
3074.5979 | 530.2883 | 549.3697 | 559.4282
3075.5979 | 531.64 | 549.363 | 559.2714
3076.5979 | 532.0479 | 549.6777 | 558.7066
3077.5979 | 531.1881 | 549.8697 | 560.329
3078.5979 | 531.8333 | 551.2982 | 561.0752
3079.5979 | 534.083 | 552.4998 | 561.1852
3080.5979 | 533.0062 | 551.6905 | 560.8694
3081.5979 | 532.938 | 551.386 | 560.3062
3082.5979 | 533.2984 | 551.8378 | 561.7898
3083.5979 | 532.2575 | 551.5147 | 562.1332
3084.5979 | 531.3707 | 550.7588 | 560.7953
3085.5979 | 531.0391 | 551.5301 | 560.6249
3086.5979 | 531.4828 | 551.9935 | 561.2349
3087.5979 | 531.5152 | 554.1062 | 561.6472
3088.5979 | 531.9913 | 555.1532 | 562.9767
3089.5979 | 532.4011 | 556.4272 | 563.129
3090.5979 | 532.3732 | 557.7069 | 563.0722
3091.5979 | 532.8752 | 559.7596 | 564.2943
3092.5979 | 533.8518 | 560.1155 | 563.9494
3093.5979 | 533.1584 | 561.0492 | 563.9595
3094.5979 | 533.3302 | 560.0818 | 563.6916
3095.5979 | 532.4371 | 559.2647 | 563.3542
3096.5979 | 531.3716 | 558.8487 | 563.4885
3097.5979 | 529.7601 | 558.0599 | 564.2705
3098.5979 | 530.6389 | 558.6563 | 563.7045
3099.5979 | 529.7803 | 559.8824 | 564.3171
3100.5979 | 530.5662 | 561.7681 | 565.1736
3101.5979 | 531.9191 | 561.0979 | 564.1536
3102.5979 | 531.4319 | 561.6416 | 563.5886
3103.5979 | 532.0042 | 561.5232 | 563.4389
3104.5979 | 533.156 | 562.3995 | 563.8978
3105.5979 | 534.6287 | 562.2897 | 563.3079
3106.5979 | 534.0603 | 562.0682 | 562.7835
3107.5979 | 534.104 | 562.2138 | 562.9798
3108.5979 | 532.6281 | 562.9376 | 563.593
3109.5979 | 532.2161 | 562.4566 | 565.0055
3110.5979 | 533.3009 | 561.6282 | 565.1399
3111.5979 | 532.8433 | 560.5184 | 564.6703
3112.5979 | 531.488 | 559.1897 | 564.1806
3113.5979 | 530.4875 | 559.2056 | 563.9877
3114.5979 | 529.9262 | 559.2243 | 563.5778
3115.5979 | 529.4835 | 558.513 | 563.242
3116.5979 | 530.2399 | 558.0755 | 561.941
3117.5979 | 529.6261 | 557.9833 | 562.1473
3118.5979 | 530.1353 | 559.075 | 561.8875
3119.5979 | 529.9825 | 560.2829 | 562.4891
3120.5979 | 529.4329 | 558.7882 | 562.7982
3121.5979 | 529.7766 | 557.9401 | 561.643
3122.5979 | 530.1068 | 557.6142 | 560.6061
3123.5979 | 531.3084 | 557.1578 | 560.3232
3124.5979 | 531.3528 | 558.2139 | 560.3163
3125.5979 | 531.6754 | 558.2714 | 559.8657
3126.5979 | 531.4761 | 558.2084 | 559.2215
3127.5979 | 531.0545 | 558.2544 | 558.3784
3128.5979 | 530.28 | 560.718 | 558.2218
3129.5979 | 531.1608 | 560.2477 | 557.5829
3130.6135 | 531.0607 | 560.4361 | 558.2829
3131.5979 | 530.0691 | 560.0021 | 558.5018
3132.5979 | 529.2334 | 561.1265 | 559.1142
3133.5979 | 528.7945 | 562.7294 | 558.8572
3134.5979 | 529.3876 | 563.5108 | 558.5518
3135.6135 | 529.4556 | 564.4858 | 558.4912
3136.6135 | 530.4335 | 565.8085 | 558.6932
3137.6135 | 529.5075 | 566.8357 | 559.6154
3138.5979 | 530.1822 | 568.0359 | 559.3314
3139.5979 | 530.7549 | 567.5722 | 559.2057
3140.5979 | 530.2545 | 569.1779 | 559.1007
3141.5979 | 528.836 | 570.6795 | 561.4492
3142.5979 | 527.7018 | 571.0945 | 561.432
3143.5979 | 527.0139 | 570.6702 | 560.5623
3144.5979 | 526.0798 | 571.2184 | 559.4147
3145.5979 | 527.7909 | 572.5003 | 559.4928
3146.5979 | 528.8799 | 573.5536 | 559.5712
3147.5979 | 529.023 | 573.8029 | 558.8588
3148.5979 | 528.404 | 573.2317 | 559.347
3149.5979 | 528.2035 | 576.4152 | 560.0616
3150.5979 | 528.2278 | 578.3977 | 561.7163
3151.5979 | 526.9278 | 579.1601 | 562.3248
3152.5979 | 527.028 | 579.1626 | 562.1441
3153.5979 | 527.2914 | 578.8628 | 561.425
3154.5979 | 527.9818 | 578.534 | 561.1181
3155.5979 | 526.8537 | 578.2891 | 560.7133
3156.5979 | 526.9799 | 576.8462 | 561.1036
3157.5979 | 525.6689 | 576.9019 | 560.7165
3158.5979 | 524.2866 | 575.8093 | 559.5787
3159.5979 | 523.6684 | 574.8408 | 558.4273
3160.5979 | 524.7115 | 575.2628 | 557.242
3161.5979 | 524.6029 | 575.4094 | 556.2702
3162.5979 | 523.429 | 575.2559 | 556.2789
3163.5979 | 523.8582 | 575.8402 | 556.2087
3164.5979 | 523.797 | 574.7407 | 556.1513
3165.5979 | 522.6222 | 575.6313 | 556.0888
3166.5979 | 521.8506 | 575.0228 | 556.14
3167.5979 | 521.9619 | 574.1882 | 555.1133
3168.5979 | 521.6965 | 574.2108 | 553.9846
3169.5979 | 520.9672 | 575.2453 | 553.6012
3170.5979 | 521.721 | 575.0528 | 554.1254
3171.5979 | 520.6232 | 574.5981 | 553.9543
3172.5979 | 520.2034 | 575.3052 | 553.3679
3173.5979 | 519.7397 | 574.7115 | 553.5471
3174.5979 | 519.2051 | 574.1139 | 553.8497
3175.5979 | 518.5242 | 573.2254 | 553.0284
3176.5979 | 518.4253 | 571.7044 | 552.6028
3177.5979 | 518.563 | 571.3042 | 552.0675
3178.5979 | 520.3749 | 571.712 | 552.4559
3179.5979 | 521.2332 | 571.7711 | 551.9311
3180.5979 | 521.217 | 572.2418 | 551.6149
3181.5979 | 521.1825 | 574.0086 | 552.5248
3182.5979 | 520.6833 | 574.4128 | 551.7358
3183.5979 | 520.827 | 574.2438 | 551.5824
3184.5979 | 520.3885 | 573.5817 | 551.7318
3185.5979 | 520.4155 | 573.8383 | 551.655
3186.5979 | 521.3951 | 576.1166 | 551.8384
3187.5979 | 524.0459 | 577.4268 | 551.7794
3188.5979 | 525.4463 | 579.1872 | 551.1072
3189.5979 | 526.5756 | 581.7928 | 551.306
3190.5979 | 524.9328 | 582.2647 | 551.0274
3191.5979 | 525.7505 | 584.3434 | 550.6543
3192.5979 | 525.7731 | 585.9064 | 550.4552
3193.5979 | 524.7443 | 588.0635 | 550.1721
3194.5979 | 523.3909 | 589.486 | 550.86
3195.5979 | 524.1739 | 591.4061 | 550.9566
3196.5979 | 524.8399 | 593.1354 | 551.3709
3197.5979 | 523.7346 | 598.072 | 551.4488
3198.5979 | 523.4462 | 605.1736 | 551.1067
3199.5979 | 522.3789 | 625.0453 | 551.1387
3200.5979 | 522.1995 | 652.8838 | 549.5406
3201.5979 | 520.9649 | 725.4915 | 549.6326
3202.5979 | 521.5906 | 857.3743 | 549.104
3203.5979 | 522.0258 | 1038.3662 | 550.1551
3204.5979 | 522.4405 | 1243.441 | 551.7876
3205.5979 | 523.0578 | 136.2185 | 551.5097
3206.5979 | -5.8935 | 1243.4419 | 536.3677
3207.5979 | 522.1794 | 634.1775 | 550.9324
3208.5979 | 523.1873 | 606.8784 | 551.8478
3209.5979 | 522.7893 | 597.5879 | 551.1883
3210.5979 | 522.1736 | 591.898 | 550.3346
3211.5979 | 522.2078 | 588.2419 | 550.4485
3212.5979 | 522.0385 | 587.2618 | 550.9797
3213.5979 | 523.019 | 578.9248 | 550.7488
3214.5979 | 523.1649 | 579.0663 | 550.6403
3215.5979 | 522.9849 | 577.6442 | 552.4439
3216.5979 | 523.3433 | 576.964 | 552.0156
3217.5979 | 521.3905 | 580.1384 | 551.3378
3218.5979 | 522.6572 | 578.4694 | 552.335
3219.5979 | 520.0184 | 577.9476 | 550.9738
3220.5979 | 520.4992 | 577.849 | 550.218
3221.5979 | 519.2667 | 577.3704 | 550.378
3222.5979 | 519.6377 | 578.277 | 550.3058
3223.5979 | 518.5793 | 578.4193 | 550.7118
3224.5979 | 520.6958 | 579.5582 | 552.4929
3225.5979 | 519.5004 | 580.781 | 555.2215
3226.5979 | 518.6856 | 579.7888 | 554.0651
3227.5979 | 518.6676 | 580.3004 | 553.5196
3228.5979 | 518.2902 | 580.5112 | 552.9255
3229.5979 | 519.099 | 579.9276 | 551.9404
3230.5979 | 520.0449 | 580.6056 | 552.0967
3231.5979 | 517.6117 | 580.9299 | 551.0795
3232.5979 | 519.0676 | 581.711 | 550.6783
3233.5979 | 517.3794 | 581.5345 | 549.5577
3234.5979 | 517.878 | 582.3186 | 549.7175
3235.5979 | 517.5308 | 582.5113 | 549.001
3236.5979 | 516.675 | 582.4569 | 549.1684
3237.5979 | 516.516 | 581.9809 | 548.2251
3238.5979 | 517.3688 | 582.516 | 547.6233
3239.5979 | 515.8745 | 582.2624 | 547.7965
3240.5979 | 517.5849 | 582.757 | 547.5207
3241.5979 | 516.5912 | 583.0219 | 547.0933
3242.5979 | 515.9501 | 583.2451 | 545.839
3243.5979 | 516.3674 | 583.593 | 545.2884
3244.5979 | 519.1455 | 583.5476 | 544.4282
3245.5979 | 518.942 | 583.5706 | 543.9119
3246.5979 | 518.4058 | 583.9522 | 544.2161
3247.5979 | 515.6343 | 583.4332 | 544.2731
3248.5979 | 515.3042 | 583.0222 | 544.0287
3249.5979 | 516.8701 | 583.7071 | 543.4919
3250.5979 | 518.1061 | 582.4664 | 543.4166
3251.5979 | 517.0787 | 582.5993 | 543.4391
3252.5979 | 516.087 | 583.1636 | 542.7342
3253.5979 | 516.7253 | 583.7248 | 542.0389
3254.5979 | 515.79 | 583.0705 | 541.4404
3255.5979 | 514.7027 | 582.4699 | 540.2799
3256.5979 | 515.611 | 582.5793 | 540.2971
3257.5979 | 515.2193 | 582.7154 | 539.7795
3258.5979 | 515.7239 | 583.2674 | 539.4004
3259.5979 | 514.904 | 583.1317 | 538.8833
3260.5979 | 515.0152 | 584.4037 | 538.4539
3261.5979 | 514.8794 | 584.961 | 538.6189
3262.5979 | 515.0711 | 584.6732 | 538.0091
3263.5979 | 514.0348 | 584.0257 | 537.0427
3264.5979 | 514.5817 | 584.7644 | 536.9117
3265.5979 | 513.3081 | 587.483 | 537.4654
3266.5979 | 513.4473 | 590.3037 | 537.014
3267.5979 | 512.9936 | 590.7358 | 536.3851
3268.5979 | 513.5429 | 591.919 | 535.9963
3269.5979 | 513.6203 | 593.7499 | 536.4866
3270.5979 | 514.519 | 592.7503 | 536.3635
3271.5979 | 515.1739 | 591.5486 | 535.6573
3272.5979 | 512.4586 | 591.6782 | 535.2201
3273.5979 | 512.3715 | 591.0731 | 535.1309
3274.5979 | 512.4764 | 592.0794 | 535.6393
3275.5979 | 513.5375 | 592.4145 | 535.0601
3276.5979 | 513.5357 | 592.4015 | 533.9404
3277.5979 | 514.7217 | 590.2046 | 533.1529
3278.5979 | 512.6017 | 590.5205 | 532.4683
3279.5979 | 513.1167 | 590.5586 | 532.1473
3280.5979 | 512.8156 | 588.8393 | 531.4046
3281.5979 | 513.4872 | 587.8634 | 532.7993
3282.5979 | 512.4522 | 588.2701 | 533.2735
3283.5979 | 512.0326 | 587.4611 | 534.6573
3284.5979 | 512.3168 | 586.0633 | 536.1489
3285.5979 | 510.5974 | 584.628 | 536.9988
3286.5979 | 509.943 | 584.4537 | 536.9748
3287.5979 | 510.8645 | 584.1666 | 537.4126
3288.5979 | 509.5063 | 582.8429 | 537.5965
3289.5979 | 510.2489 | 581.8018 | 537.2037
3290.5979 | 509.7852 | 581.9835 | 537.1468
3291.5979 | 510.4531 | 583.1425 | 538.6925
3292.5979 | 511.5332 | 583.4528 | 539.506
3293.5979 | 512.1396 | 582.4746 | 541.435
3294.5979 | 511.9093 | 582.2824 | 542.3564
3295.5979 | 510.969 | 581.7943 | 544.5505
3296.5979 | 510.578 | 581.4778 | 544.8593
3297.5979 | 510.2741 | 580.4303 | 544.5588
3298.5979 | 510.5669 | 578.4682 | 543.9812
3299.5979 | 510.2022 | 576.0327 | 544.42
3300.5979 | 511.2019 | 573.3839 | 543.9143
3301.5979 | 510.5183 | 572.7977 | 542.0253
3302.5979 | 509.8438 | 569.8678 | 540.1539
3303.5979 | 509.5737 | 567.4627 | 538.7831
3304.5979 | 508.8332 | 565.4082 | 537.5448
3305.5979 | 508.1423 | 562.8995 | 536.4273
3306.5979 | 506.1029 | 560.8195 | 535.5548
3307.5979 | 505.2781 | 560.0379 | 538.199
3308.5979 | 504.5393 | 559.3086 | 539.8118
3309.5979 | 506.0739 | 558.1629 | 539.3526
3310.5979 | 504.9157 | 557.7618 | 539.3115
3311.5979 | 505.731 | 557.0005 | 538.6397
3312.5979 | 506.4977 | 555.3869 | 536.8705
3313.5979 | 505.4717 | 554.4592 | 536.1094
3314.5979 | 504.0184 | 553.3293 | 535.3586
3315.5979 | 505.1851 | 552.0204 | 534.6846
3316.5979 | 506.0454 | 549.6826 | 532.9627
3317.5979 | 505.386 | 547.0242 | 531.7773
3318.5979 | 503.9891 | 545.7672 | 530.7796
3319.5979 | 504.1012 | 544.9022 | 529.5127
3320.5979 | 506.4676 | 544.5163 | 529.0558
3321.5979 | 506.5039 | 543.4393 | 528.3228
3322.5979 | 505.09 | 541.8258 | 527.3013
3323.6135 | 505.577 | 539.7887 | 526.6038
3324.5979 | 507.9711 | 538.0995 | 525.432
3325.5979 | 506.3522 | 536.3219 | 524.9912
3326.5979 | 505.9763 | 532.9099 | 523.8876
3327.5979 | 504.6955 | 530.7693 | 523.1066
3328.5979 | 505.7623 | 529.1189 | 521.6488
3329.5979 | 504.7136 | 527.9763 | 520.5304
3330.5979 | 506.4939 | 527.7547 | 520.3828
3331.5979 | 507.1689 | 526.9605 | 519.5455
3332.5979 | 505.9433 | 525.8759 | 519.0895
3333.5979 | 506.5532 | 523.7741 | 518.8085
3334.5979 | 504.1067 | 521.3416 | 518.6115
3335.5979 | 504.9567 | 519.0863 | 518.6283
3336.5979 | 503.6617 | 518.2062 | 518.3812
3337.5979 | 503.5325 | 517.0483 | 517.6385
3338.5979 | 502.6933 | 515.0651 | 517.3773
3339.5979 | 503.154 | 513.5817 | 516.2571
3340.5979 | 502.067 | 513.2673 | 515.7815
3341.5979 | 502.2806 | 513.1444 | 515.7359
3342.5979 | 503.4584 | 512.3223 | 515.7321
3343.5979 | 502.0399 | 511.8524 | 515.6969
3344.5979 | 502.8903 | 510.9255 | 515.5659
3345.5979 | 502.4798 | 509.8265 | 515.8377
3346.5979 | 501.0894 | 508.9687 | 515.4997
3347.5979 | 501.1069 | 508.2017 | 515.1047
3348.5979 | 501.1559 | 508.3387 | 515.9488
3349.5979 | 500.5566 | 508.9036 | 517.5253
3350.5979 | 501.465 | 510.0459 | 518.4537
3351.5979 | 499.566 | 509.6837 | 520.2857
3352.5979 | 499.0378 | 509.4156 | 522.8793
3353.5979 | 497.8926 | 509.4596 | 523.6837
3354.5979 | 498.8256 | 510.1833 | 523.4258
3355.5979 | 499.1469 | 510.7914 | 525.2851
3356.5979 | 498.1353 | 508.7958 | 524.6684
3357.5979 | 498.1884 | 509.3307 | 523.8984
3358.5979 | 498.073 | 508.2051 | 523.7633
3359.5979 | 497.2215 | 506.784 | 522.6852
3360.5979 | 496.0625 | 505.1126 | 521.7869
3361.5979 | 496.8218 | 504.4295 | 520.6595
3362.5979 | 500.0347 | 503.7756 | 519.1577
3363.5979 | 498.3687 | 501.5124 | 518.2605
3364.5979 | 498.0903 | 500.7931 | 517.7996
3365.5979 | 496.8998 | 500.5382 | 516.4751
3366.5979 | 496.5523 | 500.9675 | 514.9895
3367.5979 | 496.1675 | 500.0134 | 513.6667
3368.5979 | 496.8935 | 499.1574 | 512.0289
3369.5979 | 496.0425 | 498.6475 | 511.3557
3370.5979 | 494.9369 | 499.0763 | 511.076
3371.5979 | 495.8209 | 500.3357 | 511.739
3372.5979 | 498.6379 | 501.0302 | 512.2614
3373.5979 | 498.9197 | 501.5283 | 513.4018
3374.5979 | 498.4878 | 501.4193 | 513.9816
3375.5979 | 496.8899 | 499.4923 | 514.2042
3376.5979 | 496.7065 | 498.4707 | 516.2418
3377.5979 | 496.9635 | 498.2455 | 516.8232
3378.5979 | 495.2407 | 497.5616 | 516.5424
3379.5979 | 495.9034 | 496.5865 | 514.3862
3380.5979 | 495.2849 | 496.3258 | 512.5238
3381.5979 | 493.4442 | 496.1002 | 510.9833
3382.5979 | 496.2792 | 495.4674 | 509.514
3383.5979 | 494.9581 | 494.4766 | 508.0335
3384.5979 | 494.8036 | 493.7478 | 506.4555
3385.5979 | 493.5452 | 493.5594 | 505.3225
3386.5979 | 493.888 | 493.8617 | 504.6917
3387.5979 | 493.8142 | 493.6111 | 504.7138
3388.5979 | 492.3565 | 492.5641 | 503.9156
3389.5979 | 492.2015 | 491.7399 | 503.5549
3390.5979 | 492.3443 | 491.1087 | 504.0385
3391.5979 | 491.9811 | 490.6765 | 504.3754
3392.5979 | 491.589 | 489.7661 | 504.2332
3393.5979 | 492.1084 | 489.6921 | 504.0254
3394.5979 | 491.7435 | 489.7373 | 504.8862
3395.5979 | 490.776 | 489.8483 | 505.4965
3396.5979 | 489.8168 | 488.3941 | 505.3624
3397.5979 | 489.5626 | 486.9181 | 505.3476
3398.5979 | 489.1025 | 485.638 | 507.3366
3399.5979 | 487.8916 | 484.7006 | 506.649
3400.5979 | 487.8355 | 484.1009 | 505.253
3401.5979 | 486.3426 | 484.5064 | 504.4146
3402.5979 | 486.3176 | 484.3365 | 503.2665
3403.5979 | 485.5854 | 484.5793 | 501.8019
3404.5979 | 485.2987 | 484.0634 | 500.6597
3405.5979 | 485.2013 | 483.9136 | 499.7052
3406.5979 | 485.544 | 484.5415 | 499.009
3407.5979 | 485.6257 | 484.489 | 498.1776
3408.5979 | 485.5497 | 484.1997 | 497.0144
3409.5979 | 486.0006 | 485.4963 | 496.0925
3410.5979 | 486.2204 | 486.1175 | 495.9872
3411.5979 | 485.7355 | 484.9938 | 495.6916
3412.5979 | 485.9526 | 484.0826 | 494.8516
3413.5979 | 485.6438 | 483.6477 | 495.4341
3414.5979 | 485.9266 | 484.4975 | 495.2726
3415.5979 | 487.187 | 484.8674 | 495.1436
3416.5979 | 487.394 | 484.8806 | 494.3256
3417.5979 | 488.1414 | 484.3555 | 493.7821
3418.5979 | 487.874 | 484.6803 | 493.2684
3419.5979 | 488.5071 | 484.8096 | 492.9583
3420.5979 | 488.2589 | 484.9841 | 492.2667
3421.5979 | 489.1822 | 484.6467 | 491.6326
3422.5979 | 490.0635 | 484.2408 | 491.3211
3423.5979 | 488.4948 | 483.6055 | 491.4238
3424.5979 | 489.1203 | 483.2082 | 490.4146
3425.5979 | 488.574 | 483.3654 | 489.9907
3426.5979 | 487.6946 | 482.6131 | 489.7384
3427.5979 | 488.5398 | 482.3593 | 489.1977
3428.5979 | 487.8781 | 481.9776 | 488.7063
3429.5979 | 487.5309 | 482.1269 | 488.1409
3430.5979 | 487.5012 | 482.3593 | 487.9166
3431.5979 | 486.5398 | 481.9013 | 487.5208
3432.5979 | 486.9658 | 481.7283 | 487.2329
3433.5979 | 486.7592 | 481.5476 | 486.8976
3434.5979 | 486.4322 | 481.4364 | 486.4173
3435.5979 | 486.9403 | 480.2827 | 485.9592
3436.5979 | 486.3986 | 480.0292 | 485.5094
3437.5979 | 485.9359 | 480.1196 | 485.3722
3438.5979 | 485.6023 | 480.0625 | 485.1307
3439.5979 | 486.4763 | 479.9876 | 485.0391
3440.5979 | 485.7565 | 480.0944 | 484.4397
3441.5979 | 485.3816 | 480.5052 | 483.8706
3442.5979 | 485.292 | 481.3782 | 483.6961
3443.5979 | 485.0054 | 480.9989 | 483.2636
3444.5979 | 484.1144 | 480.3527 | 482.4244
3445.5979 | 484.8817 | 481.3126 | 481.8169
3446.5979 | 487.0766 | 480.7663 | 480.8809
3447.5979 | 487.5251 | 480.0768 | 480.1668
3448.5979 | 486.9167 | 480.6348 | 479.6576
3449.5979 | 486.923 | 479.0681 | 480.0546
3450.5979 | 489.0985 | 480.9841 | 480.1081
3451.5979 | 489.1288 | 481.4475 | 479.6745
3452.5979 | 488.0427 | 481.6441 | 479.1906
3453.5979 | 487.2395 | 481.0434 | 478.7672
3454.5979 | 487.4329 | 480.8594 | 478.813
3455.5979 | 487.4215 | 479.972 | 478.5662
3456.5979 | 487.2614 | 479.567 | 477.98
3457.5979 | 486.2576 | 478.6823 | 477.3163
3458.5979 | 485.6658 | 478.0626 | 477.2384
3459.5979 | 485.3152 | 477.1859 | 476.9763
3460.5979 | 485.9666 | 475.0367 | 476.5916
3461.5979 | 484.0621 | 472.6553 | 475.6742
3462.5979 | 482.5829 | 470.4311 | 475.0765
3463.5979 | 481.92 | 468.3695 | 473.9928
3464.5979 | 481.2541 | 467.1165 | 474.6062
3465.5979 | 482.3371 | 464.964 | 474.1424
3466.5979 | 481.7603 | 463.0089 | 473.7364
3467.5979 | 480.0099 | 460.8652 | 473.2201
3468.5979 | 478.2541 | 458.6025 | 472.7223
3469.5979 | 477.3342 | 456.8321 | 471.5641
3470.5979 | 475.3049 | 455.1804 | 471.1599
3471.5979 | 473.4614 | 453.5256 | 470.6
3472.5979 | 474.1655 | 452.6806 | 469.4766
3473.5979 | 474.1715 | 452.5837 | 468.3831
3474.5979 | 472.4431 | 453.2463 | 467.4156
3475.5979 | 471.3658 | 452.4486 | 466.9853
3476.5979 | 470.2061 | 450.9994 | 466.7496
3477.5979 | 470.2263 | 449.2404 | 467.8078
3478.5979 | 470.7373 | 447.7776 | 470.3421
3479.5979 | 470.6514 | 448.1838 | 471.6683
3480.5979 | 470.3787 | 452.5692 | 472.7129
3481.5979 | 470.3081 | 453.9798 | 482.0335
3482.5979 | 470.6651 | 453.8087 | 485.4967
3483.5979 | 469.209 | 451.8748 | 486.7309
3484.5979 | 469.2225 | 451.8607 | 491.514
3485.5979 | 470.5487 | 452.8086 | 490.9493
3486.5979 | 470.7287 | 455.3634 | 490.9252
3487.5979 | 471.4889 | 460.7891 | 493.692
3488.5979 | 470.2596 | 459.0934 | 493.4134
3489.5979 | 468.3791 | 456.2334 | 492.3674
3490.5979 | 470.9114 | 454.5061 | 490.7956
3491.5979 | 472.3307 | 452.2565 | 489.9278
3492.5979 | 473.5774 | 450.7783 | 489.3534
3493.5979 | 476.919 | 452.9235 | 488.8976
3494.5979 | 475.3232 | 454.066 | 488.7379
3495.5979 | 474.908 | 452.5747 | 488.7735
3496.5979 | 475.6104 | 463.2284 | 488.1504
3497.5979 | 475.1269 | 471.9133 | 490.4946
3498.5979 | 474.3419 | 470.7157 | 492.5847
3499.5979 | 475.1513 | 472.8608 | 493.6065
3500.5979 | 473.8413 | 472.1564 | 495.1351
3501.5979 | 472.8108 | 473.4821 | 494.979
3502.5979 | 471.5189 | 473.918 | 493.4852
3503.5979 | 473.4842 | 474.5923 | 493.3926
3504.5979 | 472.4019 | 473.7768 | 493.3134
3505.5979 | 472.0024 | 471.5889 | 493.4962
3506.5979 | 473.5686 | 471.0539 | 493.1987
3507.5979 | 476.642 | 471.1772 | 492.0802
3508.5979 | 475.6442 | 468.4912 | 491.2833
3509.5979 | 477.3987 | 465.2761 | 491.4051
3510.5979 | 474.2494 | 463.732 | 489.2868
3511.5979 | 473.148 | 466.1789 | 487.4517
3512.5979 | 474.8459 | 469.4709 | 489.0931
3513.5979 | 474.3012 | 467.1576 | 490.0488
3514.5979 | 472.3608 | 468.1404 | 489.3912
3515.5979 | 470.6197 | 470.3768 | 492.0548
3516.5979 | 471.7008 | 472.2152 | 491.4669
3517.5979 | 472.7138 | 471.8289 | 492.1937
3518.5979 | 471.8922 | 474.3025 | 493.9726
3519.5979 | 471.6939 | 475.6871 | 495.3277
3520.5979 | 471.3943 | 472.5233 | 496.3446
3521.5979 | 470.6709 | 470.1726 | 494.5393
3522.5979 | 470.6754 | 468.6256 | 493.5293
3523.5979 | 470.6023 | 466.9416 | 493.3527
3524.5979 | 471.3862 | 466.6298 | 493.6919
3525.5979 | 471.0971 | 463.926 | 493.7444
3526.5979 | 470.5056 | 462.6404 | 493.8766
3527.5979 | 473.14 | 464.4952 | 494.0213
3528.5979 | 473.4701 | 463.6529 | 493.6355
3529.5979 | 472.7553 | 462.4866 | 494.1419
3530.5979 | 472.4371 | 461.0523 | 493.0296
3531.5979 | 471.4772 | 464.5656 | 492.3054
3532.5979 | 471.166 | 467.9475 | 492.9445
3533.5979 | 471.019 | 467.8799 | 494.3787
3534.5979 | 469.7556 | 467.2761 | 493.7848
3535.5979 | 469.6459 | 466.4085 | 495.2863
3536.5979 | 469.6433 | 465.6743 | 494.6322
3537.5979 | 469.6075 | 463.9907 | 494.3026
3538.5979 | 468.4781 | 462.6236 | 493.4669
3539.5979 | 468.0571 | 460.9586 | 492.6657
3540.5979 | 467.1566 | 459.2213 | 491.7094
3541.5979 | 467.3872 | 458.8056 | 490.9862
3542.5979 | 466.4636 | 459.0106 | 492.8079
3543.5979 | 467.6513 | 459.4409 | 495.5967
3544.5979 | 467.2872 | 458.9618 | 494.9481
3545.5979 | 468.2922 | 459.6524 | 493.8151
3546.5979 | 468.0391 | 458.2942 | 492.8728
3547.6135 | 470.5288 | 457.9493 | 491.5942
3548.5979 | 469.0713 | 457.6391 | 490.6593
3549.5979 | 468.7383 | 457.7356 | 489.8653
3550.5979 | 469.9935 | 458.5551 | 488.4647
3551.5979 | 469.256 | 460.0994 | 488.3257
3552.5979 | 469.6589 | 461.7288 | 489.0781
3553.5979 | 469.4265 | 461.4498 | 489.4713
3554.5979 | 468.1797 | 462.5046 | 488.7838
3555.5979 | 468.178 | 463.1761 | 490.7631
3556.5979 | 466.6554 | 464.5076 | 490.7483
3557.5979 | 466.4674 | 464.7556 | 490.3397
3558.5979 | 465.1155 | 463.9141 | 490.2825
3559.5979 | 465.7986 | 462.933 | 493.3637
3560.5979 | 465.7456 | 462.8691 | 494.9656
3561.5979 | 465.7617 | 461.9196 | 494.51
3562.5979 | 467.0931 | 462.1273 | 493.1804
3563.5979 | 468.3979 | 461.6797 | 492.1795
3564.5979 | 468.1081 | 460.456 | 491.2787
3565.5979 | 467.5234 | 460.1256 | 491.3307
3566.5979 | 467.6519 | 461.1913 | 492.1626
3567.5979 | 468.5137 | 461.6077 | 493.5353
3568.5979 | 467.7526 | 460.8347 | 493.0975
3569.5979 | 466.7284 | 460.6363 | 493.332
3570.5979 | 466.0885 | 460.4694 | 493.0958
3571.5979 | 466.6427 | 461.7259 | 493.705
3572.5979 | 465.891 | 461.2736 | 494.987
3573.5979 | 465.7571 | 460.5617 | 495.9429
3574.6135 | 469.0992 | 459.5217 | 496.2408
3575.5979 | 470.1326 | 460.3543 | 496.2602
3576.5979 | 476.2184 | 461.7008 | 496.5183
3577.5979 | 481.3994 | 461.9895 | 496.5566
3578.5979 | 479.7446 | 461.1477 | 496.107
3579.5979 | 476.1713 | 463.0331 | 495.183
3580.5979 | 475.5342 | 465.8316 | 493.5163
3581.5979 | 478.8968 | 465.7042 | 495.7835
3582.5979 | 479.1991 | 467.8053 | 494.5208
3583.5979 | 478.2248 | 468.3166 | 494.5962
3584.5979 | 477.9933 | 471.6161 | 494.9201
3585.5979 | 477.4242 | 472.3817 | 495.9528
3586.5979 | 479.4676 | 471.2921 | 496.3392
3587.5979 | 479.3264 | 473.8844 | 496.2845
3588.5979 | 480.4418 | 477.1836 | 496.0889
3589.5979 | 479.0452 | 477.7385 | 496.6705
3590.5979 | 477.5627 | 475.7629 | 496.2724
3591.5979 | 477.2991 | 475.3389 | 497.8783
3592.5979 | 476.2263 | 475.948 | 499.8263
3593.5979 | 477.7678 | 479.0682 | 498.575
3594.5979 | 477.4061 | 484.0304 | 497.9988
3595.5979 | 477.0769 | 493.0448 | 497.4984
3596.5979 | 476.6927 | 491.1559 | 496.8823
3597.5979 | 475.079 | 492.175 | 495.7542
3598.5979 | 473.8222 | 491.3956 | 496.3262
3599.5979 | 473.2937 | 497.9008 | 497.6167
3600.5979 | 472.0566 | 498.3263 | 496.9209
3601.5979 | 470.4237 | 502.2848 | 497.0901
3602.5979 | 470.1141 | 499.7532 | 496.3295
3603.5979 | 470.7324 | 496.1704 | 496.7668
3604.6135 | 470.1724 | 490.8334 | 499.6132
3605.5979 | 469.7154 | 487.9358 | 499.2481
3606.5979 | 469.6098 | 485.6905 | 499.5171
3607.5979 | 469.654 | 482.0585 | 499.0421
3608.5979 | 473.5228 | 482.2407 | 499.9658
3609.5979 | 474.9495 | 481.8936 | 500.7604
3610.5979 | 476.2598 | 479.2839 | 503.4718
3611.5979 | 476.6719 | 478.5403 | 504.8731
3612.5979 | 476.0797 | 481.68 | 503.6903
3613.5979 | 474.6171 | 482.8022 | 502.7851
3614.5979 | 473.2148 | 480.1968 | 500.8478
3615.5979 | 474.5465 | 481.6098 | 500.9293
3616.5979 | 475.1534 | 479.4742 | 502.0226
3617.5979 | 477.1985 | 482.617 | 501.7594
3618.5979 | 479.0375 | 479.4313 | 503.1404
3619.5979 | 478.439 | 478.2442 | 501.072
3620.5979 | 483.5003 | 476.2147 | 500.1462
3621.5979 | 490.3832 | 477.5834 | 499.8846
3622.5979 | 490.3914 | 475.0769 | 500.4195
3623.5979 | 487.2848 | 472.9216 | 498.6207
3624.5979 | 487.0179 | 475.5417 | 498.5723
3625.5979 | 484.7016 | 472.5823 | 499.905
3626.5979 | 481.2527 | 470.1464 | 503.6974
3627.5979 | 479.5398 | 468.3696 | 502.6968
3628.5979 | 478.6276 | 466.66 | 501.6273
3629.5979 | 477.1252 | 469.9186 | 500.7777
3630.5979 | 478.314 | 468.6752 | 500.0702
3631.5979 | 485.1184 | 466.7691 | 498.435
3632.5979 | 482.366 | 465.1985 | 498.5396
3633.5979 | 486.1503 | 464.7709 | 498.8966
3634.5979 | 485.8676 | 463.6465 | 498.0509
3635.5979 | 484.7582 | 468.7765 | 495.9977
3636.5979 | 483.7926 | 469.3373 | 497.9979
3637.5979 | 486.1939 | 469.1229 | 500.3692
3638.5979 | 490.3706 | 469.2159 | 500.6982
3639.5979 | 488.2246 | 469.2363 | 499.8631
3640.5979 | 485.8233 | 477.5218 | 500.043
3641.5979 | 484.7792 | 473.0538 | 500.8373
3642.5979 | 481.0159 | 472.2603 | 501.8279
3643.5979 | 480.2432 | 478.0695 | 501.3132
3644.5979 | 480.2216 | 476.4301 | 500.2541
3645.5979 | 478.6692 | 482.0706 | 499.6683
3646.5979 | 479.4892 | 483.5512 | 499.5387
3647.5979 | 479.0009 | 483.8315 | 500.1167
3648.5979 | 481.6297 | 485.5469 | 500.911
3649.5979 | 482.9514 | 487.074 | 499.9548
3650.5979 | 483.9009 | 493.4714 | 498.7191
3651.5979 | 483.2698 | 491.4758 | 497.9057
3652.5979 | 483.7747 | 489.4264 | 496.4594
3653.5979 | 492.3798 | 490.0027 | 495.6667
3654.5979 | 488.3728 | 485.8506 | 494.7133
3655.5979 | 485.0813 | 485.89 | 492.5412
3656.5979 | 484.6875 | 483.4338 | 492.2344
3657.6135 | 483.1076 | 480.3117 | 493.1437
3658.5979 | 481.7769 | 481.1491 | 497.5187
3659.5979 | 483.7794 | 481.4146 | 499.4782
3660.5979 | 481.0946 | 484.5592 | 498.5623
3661.5979 | 477.6829 | 481.3106 | 498.2603
3662.5979 | 475.5952 | 481.0618 | 497.488
3663.5979 | 481.7 | 481.4987 | 500.247
3664.5979 | 481.6186 | 479.1423 | 500.2177
3665.5979 | 483.5596 | 488.2338 | 500.1956
3666.5979 | 484.3636 | 484.7202 | 501.6389
3667.5979 | 483.7583 | 483.706 | 501.796
3668.5979 | 487.368 | 484.6876 | 502.5145
3669.5979 | 488.2131 | 484.6233 | 501.3328
3670.5979 | 488.5408 | 484.5923 | 501.3076
3671.5979 | 488.1685 | 491.1083 | 501.936
3672.5979 | 485.5565 | 492.6341 | 502.4454
3673.5979 | 484.1598 | 498.8588 | 501.6233
3674.5979 | 481.5167 | 496.4734 | 500.3061
3675.5979 | 481.0306 | 496.7868 | 500.3514
3676.5979 | 480.5274 | 494.3691 | 502.4474
3677.5979 | 482.378 | 490.9519 | 503.0844
3678.5979 | 484.518 | 491.4331 | 504.9451
3679.5979 | 485.1347 | 492.9414 | 504.7115
3680.5979 | 485.7917 | 489.787 | 503.3485
3681.5979 | 483.7729 | 490.0615 | 501.493
3682.5979 | 484.886 | 489.7601 | 501.6304
3683.5979 | 485.6661 | 490.4004 | 501.6451
3684.5979 | 483.885 | 491.8032 | 500.5436
3685.6135 | 487.4206 | 488.1229 | 501.1018
3686.5979 | 488.6484 | 488.2681 | 503.8819
3687.5979 | 490.1002 | 487.85 | 503.6319
3688.5979 | 487.7293 | 484.5387 | 503.6842
3689.5979 | 487.5076 | 485.8338 | 503.041
3690.5979 | 489.3049 | 489.3383 | 505.832
3691.5979 | 494.9646 | 486.1125 | 507.189
3692.5979 | 492.951 | 484.8341 | 507.1749
3693.5979 | 491.6088 | 483.6012 | 506.8703
3694.6135 | 492.41 | 483.9803 | 503.2835
3695.5979 | 490.6382 | 483.9948 | 501.9976
3696.5979 | 490.6819 | 486.3523 | 501.6079
3697.5979 | 494.938 | 486.1554 | 502.9493
3698.5979 | 494.6394 | 484.9553 | 503.8428
3699.5979 | 495.6372 | 482.496 | 503.8368
3700.5979 | 491.4079 | 480.299 | 502.5991
3701.5979 | 488.6689 | 483.0666 | 506.0187
3702.5979 | 486.5602 | 480.8316 | 505.9014
3703.5979 | 485.5668 | 480.1522 | 504.2121
3704.5979 | 483.1767 | 482.5988 | 502.8858
3705.5979 | 481.7211 | 479.9842 | 505.7094
3706.5979 | 491.4944 | 478.7106 | 504.026
3707.5979 | 492.9485 | 477.7133 | 506.2839
3708.5979 | 492.3178 | 478.6228 | 507.1039
3709.5979 | 494.2786 | 481.8191 | 508.8011
3710.5979 | 496.6345 | 479.1148 | 509.3348
3711.5979 | 492.2216 | 483.8379 | 513.5717
3712.5979 | 488.3592 | 488.7084 | 513.5662
3713.5979 | 490.7024 | 489.1837 | 512.7897
3714.5979 | 491.4179 | 486.6494 | 510.3041
3715.5979 | 489.1584 | 486.0515 | 507.5659
3716.5979 | 488.4412 | 491.4928 | 504.6475
3717.5979 | 489.3893 | 495.7131 | 501.4863
3718.5979 | 487.482 | 495.0481 | 500.8501
3719.5979 | 488.5907 | 495.2838 | 502.1588
3720.5979 | 487.8755 | 489.9215 | 501.5222
3721.5979 | 489.3533 | 490.7234 | 500.226
3722.5979 | 487.3923 | 490.2364 | 499.8607
3723.5979 | 495.9271 | 489.3674 | 498.3093
3724.5979 | 498.2655 | 493.4933 | 499.5499
3725.5979 | 501.9687 | 495.1138 | 499.0762
3726.5979 | 503.8159 | 495.0872 | 498.4407
3727.5979 | 503.5612 | 499.6224 | 497.9775
3728.5979 | 501.0935 | 508.5102 | 498.3351
3729.5979 | 498.6501 | 505.0016 | 501.7839
3730.5979 | 498.8649 | 503.0657 | 500.4706
3731.5979 | 494.7461 | 505.4572 | 498.7555
3732.5979 | 493.6728 | 509.7451 | 498.5489
3733.5979 | 496.5305 | 504.9677 | 498.3612
3734.5979 | 495.0112 | 501.9648 | 497.4893
3735.5979 | 496.7369 | 502.0576 | 498.1489
3736.5979 | 496.1786 | 506.5583 | 498.1217
3737.5979 | 496.9514 | 505.5113 | 498.1159
3738.5979 | 497.3427 | 506.6802 | 499.8601
3739.5979 | 499.8037 | 501.1128 | 498.0801
3740.5979 | 501.4577 | 500.1246 | 497.8153
3741.5979 | 502.3612 | 502.5401 | 496.9282
3742.5979 | 506.5255 | 506.7808 | 496.0647
3743.5979 | 505.1591 | 503.2561 | 494.4753
3744.5979 | 503.4628 | 503.0319 | 493.913
3745.5979 | 511.9294 | 503.907 | 497.0527
3746.5979 | 509.8385 | 502.5719 | 505.6432
3747.5979 | 505.0435 | 501.7918 | 503.1426
3748.5979 | 506.1156 | 500.2038 | 500.2446
3749.5979 | 501.5773 | 500.8418 | 497.4628
3750.5979 | 498.6516 | 504.421 | 495.1602
3751.5979 | 496.0898 | 502.3587 | 493.9442
3752.5979 | 494.1756 | 499.0663 | 493.6009
3753.5979 | 497.7358 | 499.3744 | 492.7987
3754.5979 | 495.7765 | 505.4278 | 492.7585
3755.5979 | 496.1809 | 512.0159 | 493.9403
3756.5979 | 494.7133 | 514.3929 | 494.6525
3757.5979 | 500.7731 | 513.7567 | 493.0215
3758.5979 | 496.2978 | 514.5065 | 494.9462
3759.5979 | 494.1025 | 511.8938 | 494.5784
3760.5979 | 492.3038 | 509.857 | 495.0546
3761.5979 | 493.081 | 506.8999 | 495.8481
3762.5979 | 490.6993 | 507.8192 | 493.9561
3763.5979 | 493.4474 | 507.6732 | 492.7806
3764.5979 | 492.2029 | 505.4208 | 491.8561
3765.5979 | 493.3932 | 501.3885 | 491.9825
3766.5979 | 492.0999 | 502.837 | 493.1645
3767.5979 | 489.8595 | 502.3222 | 492.1508
3768.5979 | 489.7118 | 502.0447 | 491.9565
3769.5979 | 490.0255 | 505.5774 | 493.1981
3770.5979 | 491.6735 | 500.3973 | 496.1969
3771.5979 | 490.9936 | 497.3061 | 495.9463
3772.5979 | 488.8629 | 503.2627 | 498.302
3773.5979 | 489.985 | 507.1286 | 499.8393
3774.5979 | 490.7742 | 507.5945 | 497.5691
3775.5979 | 495.5071 | 506.6436 | 497.0241
3776.5979 | 497.162 | 506.5591 | 497.149
3777.5979 | 497.5443 | 506.8911 | 497.1215
3778.5979 | 499.1062 | 507.6469 | 497.6155
3779.5979 | 500.2344 | 508.8743 | 498.6023
3780.5979 | 503.8712 | 508.375 | 498.714
3781.5979 | 503.1916 | 507.462 | 501.1462
3782.5979 | 503.3388 | 504.5857 | 500.7371
3783.5979 | 502.0074 | 506.0734 | 498.3516
3784.5979 | 499.5333 | 507.5964 | 497.7685
3785.5979 | 500.9369 | 509.927 | 497.3706
3786.5979 | 502.8643 | 508.3409 | 496.0866
3787.5979 | 499.8425 | 504.7669 | 500.6706
3788.5979 | 496.9448 | 502.3048 | 501.7308
3789.5979 | 495.9377 | 505.1925 | 502.7559
3790.5979 | 495.8846 | 502.9376 | 501.9324
3791.5979 | 493.3622 | 498.5254 | 501.5233
3792.5979 | 491.3629 | 494.3695 | 501.3284
3793.5979 | 494.2271 | 493.8602 | 500.5305
3794.5979 | 491.846 | 492.0513 | 498.8367
3795.5979 | 492.0867 | 497.3372 | 497.1723
3796.5979 | 492.3292 | 494.1718 | 496.3776
3797.5979 | 489.9888 | 492.7521 | 497.3996
3798.5979 | 490.2458 | 497.2128 | 497.3894
3799.5979 | 494.6851 | 496.8338 | 496.4656
3800.5979 | 491.9442 | 499.5947 | 494.9388
3801.5979 | 491.2531 | 499.8705 | 491.8255
3802.5979 | 489.9114 | 499.5054 | 491.5158
3803.5979 | 488.9323 | 499.0934 | 491.3238
3804.5979 | 491.1161 | 495.8277 | 491.7015
3805.5979 | 491.962 | 497.3221 | 489.9637
3806.5979 | 491.476 | 496.6957 | 488.882
3807.5979 | 493.7345 | 499.2218 | 488.5389
3808.5979 | 499.9469 | 496.8709 | 489.1118
3809.5979 | 499.7375 | 495.5748 | 489.9737
3810.5979 | 503.3559 | 495.5894 | 487.8637
3811.5979 | 499.966 | 497.2362 | 485.6398
3812.5979 | 502.1021 | 502.611 | 485.2995
3813.5979 | 500.9043 | 507.8948 | 486.7657
3814.5979 | 497.5276 | 506.4576 | 490.3395
3815.5979 | 496.851 | 507.3115 | 490.6023
3816.5979 | 496.4058 | 504.432 | 490.9292
3817.5979 | 500.73 | 504.8953 | 493.8831
3818.5979 | 502.7535 | 500.9264 | 494.2531
3819.5979 | 504.9988 | 497.8784 | 501.3631
3820.5979 | 503.9896 | 504.4942 | 501.8635
3821.5979 | 502.3627 | 503.4645 | 499.9685
3822.5979 | 497.9129 | 502.8537 | 499.314
3823.5979 | 497.7675 | 498.0667 | 499.0466
3824.5979 | 497.8262 | 498.3749 | 498.0551
3825.5979 | 497.9395 | 500.7351 | 498.6299
3826.5979 | 497.3159 | 505.1975 | 496.1481
3827.5979 | 500.0647 | 507.778 | 492.315
3828.5979 | 501.6197 | 509.5304 | 491.9432
3829.5979 | 502.8347 | 506.7961 | 492.0246
3830.5979 | 504.128 | 500.7002 | 491.4199
3831.5979 | 503.3523 | 499.058 | 490.137
3832.5979 | 497.911 | 499.5651 | 490.1208
3833.5979 | 498.8888 | 507.1023 | 489.1175
3834.5979 | 500.954 | 505.1299 | 491.9974
3835.5979 | 499.9034 | 501.5617 | 492.7025
3836.5979 | 497.6821 | 501.669 | 491.673
3837.5979 | 496.6763 | 507.1155 | 491.4999
3838.5979 | 496.7547 | 511.4103 | 490.0838
3839.5979 | 494.6307 | 513.3586 | 488.493
3840.5979 | 495.3109 | 505.6417 | 486.9841
3841.5979 | 493.3851 | 506.3936 | 488.2154
3842.5979 | 497.7889 | 512.5367 | 488.4575
3843.5979 | 496.8046 | 509.4805 | 488.711
3844.5979 | 496.0151 | 508.8401 | 490.1093
3845.5979 | 496.5293 | 506.4968 | 489.4376
3846.5979 | 499.8507 | 509.1625 | 489.8261
3847.5979 | 497.1086 | 509.3306 | 489.7348
3848.5979 | 497.6284 | 508.6319 | 490.5044
3849.5979 | 495.3312 | 507.1378 | 494.9698
3850.5979 | 496.1532 | 507.6848 | 495.6513
3851.5979 | 499.529 | 502.2032 | 496.7339
3852.5979 | 496.917 | 501.5155 | 495.4734
3853.5979 | 495.1708 | 500.7834 | 494.8746
3854.5979 | 496.0953 | 498.9059 | 494.6069
3855.5979 | 493.7781 | 500.0846 | 492.7787
3856.5979 | 493.731 | 502.1356 | 494.8511
3857.5979 | 490.9877 | 502.5119 | 496.6436
3858.5979 | 493.9304 | 504.9562 | 494.9064
3859.5979 | 494.9096 | 502.3711 | 491.1119
3860.5979 | 492.7899 | 503.8897 | 493.1519
3861.5979 | 491.739 | 504.0871 | 493.5708
3862.5979 | 489.6776 | 503.178 | 494.547
3863.5979 | 487.9286 | 499.879 | 493.2856
3864.5979 | 488.4378 | 495.6181 | 491.0911
3865.5979 | 488.7559 | 495.4691 | 491.4275
3866.5979 | 491.5465 | 493.7029 | 490.0644
3867.5979 | 493.0206 | 497.5886 | 488.589
3868.5979 | 491.5199 | 494.5742 | 486.4988
3869.5979 | 489.0276 | 493.2278 | 486.6087
3870.5979 | 494.2763 | 497.8787 | 487.2107
3871.5979 | 496.6446 | 498.231 | 487.9955
3872.5979 | 493.9487 | 496.3208 | 491.3879
3873.5979 | 492.2677 | 496.0987 | 492.2357
3874.5979 | 493.4334 | 494.4011 | 491.3687
3875.5979 | 496.5697 | 493.2086 | 487.4779
3876.5979 | 495.62 | 494.7624 | 487.8766
3877.5979 | 494.642 | 491.4482 | 488.1301
3878.5979 | 493.7951 | 491.9604 | 485.0721
3879.5979 | 490.078 | 488.3636 | 482.553
3880.5979 | 489.2567 | 486.7494 | 482.6579
3881.5979 | 486.3602 | 484.682 | 483.972
3882.5979 | 484.1402 | 488.1178 | 485.38
3883.5979 | 484.2753 | 483.7734 | 486.0951
3884.5979 | 488.3327 | 480.5093 | 489.6857
3885.5979 | 484.319 | 476.5263 | 490.9607
3886.5979 | 484.3578 | 474.8782 | 493.5787
3887.5979 | 485.1961 | 473.4578 | 494.3331
3888.5979 | 484.6644 | 473.4369 | 494.8916
3889.5979 | 485.8967 | 474.1959 | 496.256
3890.5979 | 488.4935 | 475.4005 | 496.1269
3891.5979 | 485.3755 | 473.2783 | 496.0527
3892.5979 | 484.6536 | 472.2214 | 493.4336
3893.5979 | 486.2299 | 476.7774 | 492.8594
3894.5979 | 483.2473 | 476.2704 | 492.4307
3895.5979 | 481.73 | 477.5153 | 492.7756
3896.5979 | 480.6257 | 476.0017 | 493.5824
3897.5979 | 479.4543 | 475.8953 | 493.3077
3898.5979 | 476.8295 | 475.6309 | 491.4475
3899.5979 | 473.592 | 476.5279 | 491.5198
3900.5979 | 471.4475 | 479.4259 | 489.2213
3901.5979 | 474.3372 | 480.6998 | 486.5819
3902.5979 | 473.8605 | 480.4848 | 486.7781
3903.5979 | 474.9757 | 479.919 | 488.4674
3904.5979 | 477.9264 | 478.1136 | 490.1134
3905.5979 | 483.3825 | 477.9652 | 488.3462
3906.5979 | 482.9238 | 478.3716 | 487.7873
3907.5979 | 481.9274 | 481.7035 | 489.0042
3908.5979 | 480.0752 | 484.9326 | 487.1798
3909.5979 | 479.2966 | 483.473 | 488.6554
3910.5979 | 476.7635 | 487.7842 | 488.4565
3911.5979 | 482.3182 | 484.315 | 487.7248
3912.5979 | 481.348 | 480.3619 | 486.9081
3913.5979 | 480.2753 | 477.6624 | 486.8707
3914.5979 | 479.4688 | 476.1081 | 488.265
3915.5979 | 479.6301 | 482.9051 | 491.8604
3916.5979 | 479.7036 | 483.3932 | 490.6673
3917.5979 | 476.9524 | 483.7267 | 492.1301
3918.5979 | 477.7776 | 483.1511 | 496.4051
3919.5979 | 480.6595 | 482.1125 | 493.6183
3920.5979 | 480.2948 | 481.0264 | 491.1648
3921.5979 | 480.5652 | 481.3865 | 488.902
3922.5979 | 478.5687 | 480.8727 | 488.2785
3923.5979 | 479.1232 | 483.7026 | 486.7461
3924.5979 | 480.5049 | 482.2275 | 485.6071
3925.5979 | 479.6553 | 484.9539 | 485.0402
3926.5979 | 478.3222 | 483.7535 | 487.8944
3927.5979 | 480.2843 | 482.6621 | 487.506
3928.5979 | 480.3967 | 485.6997 | 488.3419
3929.5979 | 478.4428 | 482.7922 | 486.5175
3930.5979 | 480.4816 | 481.9982 | 487.1669
3931.5979 | 480.0826 | 482.8141 | 486.2633
3932.5979 | 478.1628 | 479.4175 | 485.9251
3933.5979 | 477.2141 | 482.6796 | 484.4291
3934.5979 | 479.6826 | 484.7449 | 483.5682
3935.5979 | 475.5552 | 481.6841 | 481.918
3936.5979 | 477.4992 | 477.7067 | 481.5846
3937.5979 | 475.6548 | 476.8736 | 481.5925
3938.5979 | 477.6983 | 477.9678 | 482.3621
3939.5979 | 478.681 | 478.3046 | 481.983
3940.5979 | 479.5761 | 477.6596 | 481.1437
3941.5979 | 478.8463 | 478.7706 | 480.5884
3942.5979 | 477.6456 | 484.286 | 480.5629
3943.5979 | 479.6255 | 484.2475 | 480.6408
3944.5979 | 479.3251 | 484.131 | 482.817
3945.5979 | 478.9806 | 483.2943 | 483.1048
3946.5979 | 480.0673 | 482.5504 | 481.7868
3947.5979 | 479.2456 | 481.3962 | 480.4592
3948.5979 | 478.9005 | 479.2196 | 483.9361
3949.5979 | 483.1133 | 477.2359 | 485.9056
3950.5979 | 480.4038 | 478.3639 | 484.4868
3951.5979 | 477.8368 | 479.0508 | 486.0874
3952.5979 | 475.2003 | 480.8285 | 489.9455
3953.5979 | 472.7948 | 476.3532 | 488.5702
3954.5979 | 475.1652 | 479.7175 | 488.6784
3955.5979 | 474.7148 | 478.5021 | 488.7348
3956.5979 | 471.9124 | 475.9778 | 487.9035
3957.5979 | 474.8147 | 474.6444 | 486.9939
3958.5979 | 475.6936 | 472.9915 | 484.711
3959.5979 | 472.0064 | 472.9332 | 483.8666
3960.5979 | 470.3886 | 469.7372 | 485.7642
3961.5979 | 474.9014 | 474.1074 | 487.2965
3962.5979 | 472.5019 | 472.0196 | 486.771
3963.5979 | 471.438 | 471.8792 | 485.4496
3964.6135 | 470.3837 | 471.8382 | 484.8289
3965.5979 | 470.9403 | 475.3904 | 486.7244
3966.5979 | 468.4941 | 475.422 | 487.9188
3967.5979 | 466.9348 | 474.8297 | 486.5886
3968.5979 | 470.1161 | 474.5791 | 483.4612
3969.5979 | 469.2056 | 478.6413 | 484.5473
3970.5979 | 469.3968 | 477.7754 | 485.0619
3971.5979 | 469.8561 | 479.1166 | 483.592
3972.5979 | 469.3696 | 483.5334 | 480.5826
3973.5979 | 471.1873 | 483.5065 | 481.3171
3974.5979 | 472.6681 | 482.6801 | 479.4468
3975.5979 | 471.6271 | 482.5729 | 478.1375
3976.5979 | 469.9481 | 482.7533 | 478.616
3977.5979 | 469.0815 | 482.2595 | 476.3658
3978.5979 | 467.4135 | 482.7955 | 475.7251
3979.5979 | 468.5932 | 483.5446 | 474.3287
3980.5979 | 471.5683 | 481.8562 | 473.997
3981.5979 | 470.8266 | 479.3242 | 475.1053
3982.5979 | 472.3252 | 480.668 | 477.9283
3983.5979 | 471.0392 | 480.0257 | 479.9018
3984.5979 | 474.587 | 481.2077 | 479.9841
3985.5979 | 474.3873 | 479.3868 | 479.3009
3986.5979 | 474.3745 | 476.5085 | 479.7843
3987.5979 | 473.1096 | 473.7584 | 478.8205
3988.5979 | 468.8616 | 470.5976 | 477.671
3989.5979 | 471.2678 | 470.5277 | 476.875
3990.5979 | 467.9192 | 468.1606 | 478.9183
3991.5979 | 467.1157 | 465.7156 | 483.0264
3992.5979 | 466.2282 | 466.6306 | 483.5265
3993.5979 | 466.906 | 465.1214 | 483.3468
3994.5979 | 465.2826 | 463.9775 | 480.6462
3995.5979 | 466.7356 | 463.6521 | 480.2513
3996.5979 | 464.3811 | 466.2518 | 478.3203
3997.5979 | 464.0153 | 466.6642 | 478.8487
3998.5979 | 465.4998 | 464.7655 | 479.4777
3999.5979 | 461.7099 | 462.3445 | 479.5348
4000.5979 | 462.9598 | 464.2246 | 478.5325
4001.5979 | 461.4155 | 462.9558 | 479.3411
4002.5979 | 457.5261 | 465.8236 | 475.4176
4003.5979 | 457.9135 | 463.0276 | 476.5295
4004.5979 | 460.4453 | 460.5159 | 475.1506
4005.5979 | 459.7123 | 458.9349 | 474.9818
4006.5979 | 461.2502 | 457.5678 | 477.2007
4007.5979 | 459.3895 | 457.4413 | 474.8428
4008.5979 | 463.7646 | 456.0223 | 471.1188
4009.5979 | 461.2726 | 456.3727 | 469.4187
4010.5979 | 461.1033 | 454.588 | 468.9431
4011.5979 | 459.5135 | 454.8676 | 475.2161
4012.5979 | 460.4843 | 456.0641 | 479.1835
4013.5979 | 458.8078 | 457.5251 | 482.4744
4014.5979 | 458.3848 | 459.8527 | 481.4896
4015.5979 | 466.1366 | 461.1212 | 479.5445
4016.5979 | 461.7903 | 462.0893 | 479.1673
4017.5979 | 461.1223 | 464.1666 | 476.8829
4018.5979 | 461.7602 | 462.917 | 476.5527
4019.5979 | 462.6779 | 463.6872 | 474.8123
4020.5979 | 463.6178 | 464.4637 | 472.7492
4021.5979 | 462.5155 | 464.7866 | 474.4252
4022.5979 | 461.4687 | 464.3189 | 473.484
4023.5979 | 462.0301 | 465.1103 | 474.8729
4024.5979 | 461.4896 | 462.4015 | 475.2844
4025.5979 | 458.1412 | 461.9745 | 474.517
4026.5979 | 454.874 | 462.201 | 474.2003
4027.5979 | 459.9252 | 462.5411 | 472.5219
4028.5979 | 460.3106 | 463.6387 | 470.1023
4029.5979 | 461.0505 | 465.2869 | 468.8853
4030.5979 | 458.7141 | 466.5099 | 468.2742
4031.5979 | 457.6829 | 467.4836 | 468.2074
4032.5979 | 457.0129 | 468.2844 | 467.8231
4033.5979 | 454.7419 | 466.5498 | 468.0295
4034.5979 | 455.9443 | 468.2038 | 470.8493
4035.5979 | 460.0365 | 465.6036 | 471.7141
4036.5979 | 457.0382 | 468.1991 | 475.9954
4037.5979 | 456.7768 | 469.5878 | 475.4062
4038.5979 | 458.2455 | 468.9866 | 472.2874
4039.5979 | 452.0481 | 470.8716 | 470.653
4040.5979 | 454.5974 | 467.0406 | 479.7674
4041.5979 | 455.2206 | 463.9677 | 481.4882
4042.5979 | 454.1177 | 461.9931 | 481.3236
4043.5979 | 452.4072 | 459.8202 | 479.3093
4044.5979 | 452.4634 | 456.203 | 477.0912
4045.5979 | 455.1354 | 453.5575 | 476.6245
4046.5979 | 454.0661 | 452.2682 | 478.245
4047.5979 | 452.3681 | 456.2216 | 481.299
4048.5979 | 453.9725 | 458.2535 | 480.5713
4049.5979 | 450.2831 | 458.4284 | 481.3859
4050.5979 | 453.1024 | 460.8072 | 480.4452
4051.5979 | 451.9861 | 459.4682 | 477.1971
4052.5979 | 452.7615 | 456.446 | 475.237
4053.5979 | 452.6051 | 455.4167 | 473.6362
4054.5979 | 448.8789 | 455.0178 | 475.4592
4055.5979 | 451.5433 | 456.1688 | 473.9722
4056.5979 | 451.3833 | 454.889 | 475.9644
4057.5979 | 455.3296 | 454.7038 | 478.6196
4058.5979 | 457.0497 | 456.4759 | 480.2718
4059.5979 | 454.4382 | 454.3182 | 485.5452
4060.5979 | 452.093 | 454.3094 | 481.1662
4061.5979 | 453.3162 | 454.7793 | 478.5146
4062.5979 | 454.2755 | 456.2199 | 476.9027
4063.5979 | 456.0878 | 457.5533 | 476.6855
4064.5979 | 454.7305 | 458.4724 | 477.4891
4065.5979 | 457.8082 | 458.7056 | 476.7018
4066.5979 | 462.7035 | 460.7002 | 477.0675
4067.5979 | 460.846 | 461.1163 | 482.942
4068.5979 | 458.4565 | 461.2875 | 491.6697
4069.5979 | 457.76 | 459.3983 | 488.4264
4070.5979 | 459.5694 | 455.7221 | 486.8914
4071.5979 | 460.4924 | 453.6265 | 496.3009
4072.5979 | 461.4212 | 451.6935 | 491.6696
4073.5979 | 456.2428 | 451.1791 | 494.2726
4074.5979 | 456.4979 | 450.39 | 490.1025
4075.5979 | 452.9684 | 449.909 | 487.9497
4076.5979 | 452.8444 | 448.1293 | 485.9721
4077.5979 | 452.6544 | 447.1908 | 484.1623
4078.5979 | 449.9331 | 448.0688 | 481.8594
4079.5979 | 449.5661 | 446.5268 | 478.2538
4080.5979 | 451.9956 | 446.8347 | 475.9736
4081.5979 | 451.3674 | 449.0981 | 480.6829
4082.5979 | 450.0899 | 449.274 | 481.1022
4083.5979 | 449.4003 | 447.8254 | 480.4156
4084.5979 | 447.4053 | 446.5368 | 479.9206
4085.5979 | 449.4697 | 447.8298 | 480.5937
4086.5979 | 450.8973 | 445.9898 | 481.5038
4087.5979 | 453.36 | 447.4422 | 483.9651
4088.5979 | 454.6945 | 445.6011 | 483.1982
4089.5979 | 448.582 | 448.6215 | 481.1907
4090.5979 | 453.7462 | 448.3743 | 480.9188
4091.5979 | 454.4787 | 446.2651 | 477.2038
4092.5979 | 454.4915 | 447.545 | 477.1886
4093.5979 | 456.3685 | 446.628 | 479.8212
4094.5979 | 453.5607 | 444.6184 | 477.7402
4095.5979 | 452.035 | 447.8145 | 478.2473
4096.5979 | 449.9101 | 446.2226 | 484.4681
4097.5979 | 450.1908 | 446.4894 | 483.856
4098.5979 | 451.6123 | 446.7502 | 482.0001
4099.5979 | 450.1887 | 445.4441 | 484.2815
4100.5979 | 446.2535 | 445.5815 | 488.2111
4101.5979 | 448.3748 | 444.5026 | 488.5785
4102.5979 | 447.6743 | 445.2848 | 491.9031
4103.5979 | 446.3677 | 446.4344 | 497.5496
4104.5979 | 443.6102 | 445.4562 | 500.7312
4105.5979 | 446.4821 | 444.729 | 499.1969
4106.5979 | 446.488 | 444.9704 | 495.9443
4107.5979 | 443.1703 | 444.126 | 492.9024
4108.5979 | 443.323 | 444.3097 | 494.8248
4109.5979 | 450.5628 | 445.0789 | 492.8453
4110.5979 | 447.9163 | 447.1521 | 491.1654
4111.5979 | 447.6642 | 446.611 | 493.6429
4112.5979 | 446.923 | 446.0159 | 498.0555
4113.5979 | 448.4843 | 445.1732 | 497.1697
4114.5979 | 451.0153 | 446.0528 | 493.7873
4115.5979 | 451.3476 | 445.2816 | 494.2488
4116.5979 | 448.7883 | 444.7018 | 492.2699
4117.5979 | 448.911 | 443.4729 | 489.7281
4118.5979 | 447.1669 | 444.0815 | 487.742
4119.5979 | 446.1248 | 445.3292 | 484.6916
4120.5979 | 451.4422 | 443.6863 | 485.4649
4121.5979 | 448.5225 | 447.2014 | 485.8784
4122.5979 | 451.6772 | 444.1119 | 484.3017
4123.5979 | 448.422 | 441.7781 | 481.0168
4124.5979 | 443.7503 | 446.1421 | 480.182
4125.5979 | 438.5091 | 445.8373 | 479.4461
4126.5979 | 445.2608 | 442.7903 | 479.1443
4127.5979 | 443.5615 | 442.8164 | 490.4917
4128.5979 | 446.0566 | 442.3878 | 491.75
4129.5979 | 443.1176 | 441.9925 | 488.8757
4130.5979 | 437.5028 | 442.0334 | 487.016
4131.5979 | 443.1615 | 440.236 | 487.3579
4132.5979 | 445.0949 | 441.3233 | 486.6686
4133.5979 | 443.7543 | 439.2576 | 493.7302
4134.5979 | 444.4672 | 437.352 | 493.1235
4135.5979 | 441.3668 | 436.2842 | 490.9636
4136.5979 | 444.0184 | 434.4948 | 489.4761
4137.5979 | 436.9393 | 432.6371 | 493.3262
4138.5979 | 438.7728 | 431.8342 | 491.3895
4139.5979 | 441.0011 | 432.4745 | 489.6863
4140.5979 | 441.5055 | 432.3712 | 487.1531
4141.5979 | 448.5838 | 432.0365 | 485.7817
4142.5979 | 445.5725 | 433.3944 | 486.7298
4143.5979 | 445.175 | 433.1559 | 484.7041
4144.5979 | 448.2719 | 433.8588 | 482.0344
4145.5979 | 446.8415 | 433.9089 | 479.4395
4146.5979 | 448.2461 | 433.3192 | 478.6208
4147.5979 | 446.9785 | 432.4223 | 480.1531
4148.5979 | 443.2678 | 431.8215 | 480.5907
4149.5979 | 439.5718 | 431.9411 | 479.6847
4150.5979 | 439.8117 | 430.9947 | 476.3006
4151.5979 | 439.1798 | 430.5283 | 475.4726
4152.5979 | 441.2033 | 430.8941 | 475.1095
4153.5979 | 446.953 | 431.9781 | 475.4453
4154.5979 | 445.4129 | 432.4461 | 479.7648
4155.5979 | 442.661 | 432.2397 | 477.6892
4156.5979 | 441.4274 | 432.4428 | 481.9342
4157.5979 | 441.1024 | 431.8477 | 488.835
4158.5979 | 435.1109 | 432.7022 | 490.0115
4159.5979 | 444.5339 | 432.4886 | 486.9545
4160.5979 | 437.0191 | 431.9114 | 487.1729
4161.5979 | 442.1991 | 432.6566 | 488.5205
4162.5979 | 441.3103 | 432.299 | 488.1992
4163.5979 | 440.7675 | 432.0506 | 488.8781
4164.5979 | 440.414 | 431.4654 | 491.1886
4165.5979 | 437.4791 | 430.0595 | 487.7903
4166.5979 | 439.3075 | 429.2113 | 487.5329
4167.5979 | 439.5398 | 428.498 | 486.7055
4168.5979 | 437.4072 | 427.3358 | 492.8122
4169.5979 | 433.3591 | 426.5851 | 499.3568
4170.5979 | 442.162 | 426.1034 | 496.6017
4171.5979 | 444.2796 | 424.2674 | 500.1409
4172.5979 | 443.9976 | 423.6027 | 497.24
4173.5979 | 437.5656 | 422.2547 | 493.1814
4174.5979 | 435.4796 | 423.0631 | 489.7994
4175.5979 | 430.7883 | 421.884 | 489.7023
4176.5979 | 441.429 | 420.5794 | 484.7233
4177.5979 | 439.6796 | 419.3066 | 483.8831
4178.5979 | 438.8447 | 419.0788 | 482.2636
4179.5979 | 433.9672 | 418.6294 | 481.0438
4180.5979 | 439.4577 | 419.5538 | 479.9326
4181.5979 | 437.1117 | 420.2389 | 481.0739
4182.5979 | 439.516 | 419.8907 | 482.5829
4183.5979 | 434.2913 | 420.2726 | 482.045
4184.5979 | 434.0568 | 420.935 | 481.1882
4185.5979 | 431.5709 | 421.4866 | 481.5175
4186.5979 | 431.4895 | 420.8506 | 481.3757
4187.5979 | 433.7747 | 419.3696 | 481.2201
4188.5979 | 435.585 | 418.355 | 489.2682
4189.5979 | 434.3798 | 418.0684 | 486.629
4190.5979 | 433.6415 | 417.1832 | 486.9373
4191.5979 | 434.813 | 416.6466 | 486.5968
4192.5979 | 432.5881 | 415.6258 | 486.2273
4193.5979 | 431.07 | 415.0338 | 486.576
4194.5979 | 434.0363 | 415.2639 | 486.6433
4195.5979 | 432.7019 | 414.8625 | 486.6198
4196.5979 | 437.952 | 413.972 | 494.7164
4197.5979 | 435.5246 | 413.5245 | 493.8281
4198.5979 | 431.4626 | 412.5939 | 495.8907
4199.5979 | 424.568 | 411.3109 | 495.6083
4200.5979 | 429.7574 | 412.4929 | 490.0431
4201.5979 | 426.5484 | 412.3221 | 492.1393
4202.5979 | 429.3679 | 413.2629 | 491.2597
4203.5979 | 429.3967 | 412.8643 | 488.5581
4204.5979 | 433.993 | 412.1779 | 487.1083
4205.5979 | 436.0297 | 411.9138 | 486.6202
4206.5979 | 432.7163 | 411.8147 | 482.0055
4207.5979 | 437.1405 | 410.9251 | 480.6691
4208.5979 | 431.6876 | 410.2907 | 483.7599
4209.5979 | 431.1011 | 410.0367 | 481.3819
4210.5979 | 426.7634 | 410.0826 | 481.8513
4211.5979 | 433.5241 | 409.1968 | 480.1919
4212.5979 | 432.5919 | 408.4111 | 479.1517
4213.5979 | 428.9789 | 407.4944 | 481.5489
4214.5979 | 426.5526 | 407.0663 | 484.8902
4215.5979 | 428.7184 | 407.6141 | 484.6142
4216.5979 | 429.7432 | 407.6338 | 481.5138
4217.5979 | 436.6723 | 408.2439 | 478.9591
4218.5979 | 436.2167 | 408.7594 | 478.0116
4219.5979 | 433.9785 | 408.4069 | 476.8613
4220.5979 | 430.2538 | 408.8145 | 476.7837
4221.5979 | 433.8372 | 408.7612 | 475.7303
4222.5979 | 430.4704 | 408.9489 | 475.3974
4223.5979 | 431.8394 | 408.5879 | 476.1083
4224.5979 | 428.2156 | 408.5358 | 476.8909
4225.5979 | 432.7568 | 408.425 | 476.0646
4226.5979 | 430.932 | 408.0763 | 477.8493
4227.5979 | 429.1238 | 407.6393 | 478.6334
4228.5979 | 431.0396 | 407.9168 | 480.9974
4229.5979 | 429.9194 | 408.3986 | 479.4002
4230.5979 | 429.501 | 408.8525 | 479.2691
4231.5979 | 428.8605 | 408.5339 | 480.5918
4232.5979 | 434.7516 | 409.2343 | 482.0368
4233.5979 | 430.7863 | 410.3919 | 481.4195
4234.5979 | 433.2932 | 411.1415 | 483.4469
4235.5979 | 427.6637 | 410.8606 | 482.7253
4236.5979 | 425.6576 | 410.5184 | 481.8706
4237.5979 | 428.8803 | 410.981 | 479.3521
4238.5979 | 426.2207 | 410.1988 | 476.8867
4239.5979 | 423.1451 | 409.7884 | 474.3212
4240.5979 | 428.0497 | 411.0645 | 475.3154
4241.5979 | 429.3628 | 411.553 | 478.02
4242.5979 | 427.2261 | 411.4118 | 476.0353
4243.5979 | 427.1891 | 411.3529 | 477.7541
4244.5979 | 425.7991 | 410.7698 | 477.6935
4245.5979 | 420.2177 | 411.6708 | 478.9141
4246.5979 | 428.7499 | 411.598 | 479.3125
4247.5979 | 423.8516 | 410.3547 | 477.7432
4248.5979 | 420.3939 | 409.3977 | 478.4455
4249.5979 | 422.0162 | 409.4123 | 478.2971
4250.5979 | 422.4426 | 409.4166 | 479.2166
4251.5979 | 416.8571 | 409.2315 | 478.8828
4252.5979 | 423.8225 | 408.6458 | 478.2358
4253.5979 | 421.1291 | 407.9622 | 479.6945
4254.5979 | 421.2673 | 408.5697 | 480.984
4255.5979 | 417.9116 | 408.6564 | 480.738
4256.5979 | 418.9113 | 408.4835 | 482.0298
4257.5979 | 422.8811 | 408.5138 | 485.006
4258.5979 | 418.7712 | 408.357 | 482.1223
4259.5979 | 419.4963 | 408.6609 | 480.7143
4260.5979 | 413.1361 | 408.789 | 479.589
4261.5979 | 420.2796 | 409.7059 | 476.9718
4262.5979 | 418.0858 | 408.9309 | 475.0188
4263.5979 | 416.2101 | 408.8325 | 474.5842
4264.5979 | 415.491 | 408.8958 | 473.07
4265.5979 | 420.2508 | 408.8758 | 473.4587
4266.5979 | 418.2637 | 407.9233 | 471.9724
4267.5979 | 416.6466 | 407.1331 | 472.5779
4268.5979 | 415.4382 | 406.9907 | 473.1856
4269.5979 | 411.3106 | 407.2494 | 477.9279
4270.5979 | 413.4991 | 407.5726 | 477.4969
4271.5979 | 413.3448 | 408.2448 | 477.6439
4272.5979 | 414.8428 | 407.4506 | 477.783
4273.5979 | 417.0754 | 406.9316 | 476.4126
4274.5979 | 415.0535 | 406.6404 | 480.6939
4275.5979 | 408.5978 | 405.7355 | 479.1702
4276.5979 | 408.097 | 404.1147 | 479.5237
4277.5979 | 410.5962 | 403.6121 | 480.0809
4278.5979 | 413.6551 | 402.8939 | 481.8189
4279.5979 | 407.3742 | 401.8576 | 482.4094
4280.5979 | 414.0234 | 401.5231 | 478.4411
4281.5979 | 407.7253 | 401.0265 | 476.1988
4282.5979 | 408.5912 | 400.8554 | 476.808
4283.5979 | 405.0808 | 400.7344 | 476.9825
4284.5979 | 406.6139 | 400.2756 | 478.889
4285.5979 | 405.4128 | 399.8035 | 477.6561
4286.5979 | 404.8632 | 399.7575 | 477.943
4287.5979 | 405.3865 | 399.4206 | 479.2368
4288.5979 | 410.9016 | 398.3193 | 480.8086
4289.5979 | 411.88 | 398.6035 | 478.3067
4290.5979 | 411.8506 | 398.9027 | 478.0629
4291.5979 | 412.4166 | 398.3044 | 475.9591
4292.5979 | 410.5314 | 397.6035 | 479.0346
4293.5979 | 412.5225 | 397.2469 | 478.6273
4294.5979 | 412.2136 | 398.0854 | 479.9695
4295.5979 | 411.5216 | 397.7548 | 481.6225
4296.5979 | 410.493 | 398.0095 | 482.0588
4297.5979 | 406.9443 | 397.9954 | 485.211
4298.5979 | 413.521 | 397.9917 | 484.8558
4299.5979 | 412.5625 | 398.8699 | 484.2134
4300.5979 | 411.8414 | 399.4471 | 481.7119
4301.5979 | 406.3982 | 399.2317 | 482.4299
4302.5979 | 410.0024 | 398.9175 | 485.5723
4303.5979 | 409.6929 | 399.3809 | 485.098
4304.5979 | 410.8204 | 399.7969 | 482.9756
4305.5979 | 413.6787 | 399.7351 | 480.629
4306.5979 | 411.9145 | 399.0381 | 479.3908
4307.5979 | 414.3502 | 398.6509 | 478.8072
4308.5979 | 411.2563 | 398.6237 | 480.8653
4309.5979 | 411.0807 | 398.0403 | 481.2834
4310.5979 | 411.3888 | 397.9638 | 480.2164
4311.5979 | 408.3311 | 396.984 | 483.6327
4312.5979 | 410.8855 | 396.4167 | 479.6
4313.5979 | 412.2242 | 396.5311 | 478.7404
4314.5979 | 412.088 | 396.4927 | 479.6703
4315.5979 | 410.7031 | 395.7457 | 479.3597
4316.5979 | 410.795 | 396.6944 | 479.0169
4317.5979 | 408.5919 | 396.8926 | 477.997
4318.5979 | 408.1374 | 397.1452 | 478.3506
4319.5979 | 406.6341 | 398.5869 | 481.8649
4320.5979 | 404.2555 | 398.3092 | 481.9246
4321.5979 | 404.3385 | 397.7607 | 482.2003
4322.5979 | 400.9589 | 398.5325 | 482.2269
4323.5979 | 401.018 | 399.3539 | 482.192
4324.5979 | 406.6354 | 399.9321 | 483.3509
4325.5979 | 404.1334 | 399.9496 | 483.8807
4326.5979 | 401.7574 | 400.6277 | 483.6453
4327.5979 | 403.8538 | 400.9377 | 483.9976
4328.5979 | 407.2929 | 399.6786 | 481.2132
4329.5979 | 408.7982 | 398.0958 | 481.744
4330.5979 | 408.5392 | 397.1917 | 482.8283
4331.5979 | 403.0265 | 396.5022 | 477.5835
4332.5979 | 402.9533 | 395.5029 | 474.0256
4333.5979 | 404.3194 | 394.9643 | 472.937
4334.5979 | 406.1625 | 394.7497 | 470.7706
4335.5979 | 405.0593 | 394.3469 | 468.2654
4336.5979 | 406.1775 | 393.7822 | 465.7857
4337.5979 | 405.093 | 393.4395 | 465.1225
4338.5979 | 405.5315 | 393.5509 | 464.0223
4339.5979 | 404.6719 | 394.0116 | 464.4214
4340.5979 | 403.8628 | 393.2271 | 464.4131
4341.5979 | 401.5162 | 393.3778 | 463.6202
4342.5979 | 403.4027 | 392.9406 | 465.1021
4343.5979 | 399.424 | 392.85 | 464.4993
4344.5979 | 397.9324 | 392.4662 | 465.0356
4345.5979 | 392.8743 | 391.8442 | 465.41
4346.5979 | 393.9491 | 391.2323 | 465.9121
4347.5979 | 400.1519 | 390.5021 | 462.6907
4348.5979 | 400.8622 | 389.7324 | 462.36
4349.5979 | 397.9758 | 389.6007 | 464.2077
4350.5979 | 393.1609 | 388.7705 | 463.7265
4351.5979 | 397.348 | 389.1062 | 464.9158
4352.5979 | 394.5876 | 389.834 | 467.1685
4353.5979 | 390.2989 | 389.6381 | 466.776
4354.5979 | 394.1527 | 389.7194 | 465.6155
4355.5979 | 396.5995 | 389.7256 | 465.6207
4356.5979 | 397.5826 | 389.3807 | 467.1658
4357.5979 | 389.2308 | 389.4157 | 468.1948
4358.5979 | 394.9193 | 390.0354 | 468.7811
4359.5979 | 389.3998 | 390.2571 | 468.2539
4360.5979 | 393.6562 | 390.1064 | 468.9341
4361.5979 | 396.7507 | 390.2678 | 470.8725
4362.5979 | 397.2923 | 390.8937 | 470.4013
4363.5979 | 393.4693 | 391.1003 | 471.1951
4364.5979 | 392.9601 | 389.8517 | 471.5279
4365.5979 | 392.3351 | 389.3165 | 471.8036
4366.5979 | 397.9943 | 388.8732 | 471.0317
4367.5979 | 397.0941 | 388.4077 | 471.4551
4368.5979 | 397.7636 | 388.434 | 472.2701
4369.5979 | 396.8441 | 388.5965 | 470.9347
4370.5979 | 391.4144 | 387.9757 | 470.0747
4371.5979 | 396.503 | 388.069 | 471.1706
4372.5979 | 391.4013 | 387.4149 | 471.3758
4373.5979 | 393.7189 | 387.1204 | 471.4858
4374.5979 | 394.2761 | 386.3959 | 472.4624
4375.5979 | 389.3015 | 385.7661 | 471.5873
4376.5979 | 394.2915 | 386.0124 | 470.4013
4377.5979 | 394.4406 | 385.9575 | 470.5445
4378.5979 | 394.0877 | 385.8249 | 470.2086
4379.5979 | 395.1119 | 385.579 | 467.8687
4380.5979 | 391.3001 | 385.339 | 467.8829
4381.5979 | 392.0938 | 385.0783 | 465.9285
4382.5979 | 388.6712 | 385.3596 | 465.5584
4383.5979 | 391.3256 | 385.5985 | 467.2933
4384.5979 | 396.1947 | 386.0885 | 466.7727
4385.5979 | 395.9949 | 386.1592 | 467.0596
4386.5979 | 395.4494 | 385.4209 | 466.803
4387.5979 | 392.2913 | 384.4635 | 467.1106
4388.5979 | 395.4332 | 384.5655 | 467.4916
4389.5979 | 391.8772 | 384.0032 | 466.5366
4390.5979 | 394.636 | 384.1059 | 465.182
4391.5979 | 394.7393 | 383.4443 | 466.3249
4392.5979 | 391.9821 | 383.0276 | 469.5136
4393.5979 | 391.6839 | 383.4858 | 468.1432
4394.5979 | 388.2842 | 382.8877 | 468.279
4395.5979 | 392.0921 | 382.1755 | 467.5097
4396.5979 | 389.9522 | 381.5193 | 467.3807
4397.5979 | 387.891 | 381.4343 | 466.1162
4398.5979 | 382.5479 | 380.8936 | 466.833
4399.5979 | 389.4808 | 380.4434 | 465.471
4400.5979 | 385.9683 | 380.8042 | 462.7088
4401.5979 | 392.7603 | 381.2462 | 463.1587
4402.5979 | 393.0177 | 380.6303 | 464.7079
4403.5979 | 391.2217 | 380.3448 | 464.092
4404.5979 | 392.0655 | 380.6107 | 462.9852
4405.5979 | 392.3371 | 381.7094 | 462.7701
4406.5979 | 390.6956 | 382.3634 | 463.8045
4407.5979 | 394.222 | 382.1904 | 463.1662
4408.5979 | 390.1849 | 382.4408 | 463.9437
4409.5979 | 389.7591 | 382.3842 | 466.6744
4410.5979 | 390.8351 | 382.3908 | 465.4717
4411.5979 | 392.3998 | 382.5032 | 464.6915
4412.5979 | 391.1535 | 382.4952 | 463.6296
4413.5979 | 391.8279 | 382.1899 | 463.3372
4414.5979 | 392.4542 | 381.1717 | 464.9546
4415.5979 | 391.5266 | 380.2025 | 463.4737
4416.5979 | 392.2741 | 380.0215 | 460.3587
4417.5979 | 390.5974 | 380.3464 | 461.7474
4418.5979 | 391.5954 | 380.339 | 462.4027
4419.5979 | 390.6656 | 380.4412 | 461.4978
4420.5979 | 390.0155 | 380.8026 | 460.822
4421.5979 | 388.4512 | 380.7553 | 460.8169
4422.5979 | 387.7979 | 380.2578 | 460.7173
4423.5979 | 384.7877 | 380.0604 | 459.5612
4424.5979 | 389.6034 | 380.1729 | 456.9968
4425.5979 | 384.541 | 379.1794 | 457.0817
4426.5979 | 387.9869 | 379.6947 | 457.8425
4427.5979 | 388.9615 | 379.7862 | 458.0826
4428.5979 | 387.7277 | 379.8668 | 458.714
4429.5979 | 390.3919 | 380.1221 | 459.0567
4430.5979 | 390.2882 | 379.7399 | 458.448
4431.5979 | 387.4746 | 379.4994 | 457.0998
4432.5979 | 388.4654 | 379.6743 | 455.6387
4433.5979 | 384.7843 | 379.5132 | 454.7821
4434.5979 | 383.1026 | 379.4882 | 454.4132
4435.5979 | 383.5747 | 380.0319 | 457.0194
4436.5979 | 376.4239 | 379.6516 | 457.3387
4437.5979 | 386.0692 | 380.1147 | 457.3644
4438.5979 | 385.8299 | 379.7865 | 457.8568
4439.5979 | 384.7977 | 379.2403 | 457.5908
4440.5979 | 384.1609 | 379.2149 | 458.3304
4441.5979 | 383.7603 | 379.2809 | 459.4266
4442.5979 | 381.2338 | 379.1816 | 458.7253
4443.5979 | 379.9718 | 379.6539 | 458.7169
4444.5979 | 383.2047 | 379.7386 | 460.1665
4445.5979 | 382.0381 | 379.3692 | 459.3322
4446.5979 | 382.2501 | 379.0645 | 457.6737
4447.5979 | 385.7786 | 378.3228 | 455.7849
4448.5979 | 379.2352 | 377.7529 | 452.9918
4449.5979 | 384.3032 | 377.1037 | 452.1575
4450.5979 | 380.0531 | 377.022 | 454.6674
4451.5979 | 381.947 | 376.0809 | 452.9235
4452.5979 | 376.4853 | 375.627 | 449.9371
4453.5979 | 383.3119 | 375.1362 | 448.9121
4454.5979 | 382.0534 | 374.5953 | 448.6063
4455.5979 | 381.7873 | 374.8968 | 447.7171
4456.5979 | 381.0183 | 374.5467 | 446.8942
4457.5979 | 375.7138 | 374.0229 | 444.4078
4458.5979 | 380.723 | 374.1659 | 445.1219
4459.5979 | 381.3571 | 374.2301 | 445.8819
4460.5979 | 381.1403 | 374.4093 | 445.9232
4461.5979 | 379.7095 | 374.3016 | 445.0905
4462.5979 | 382.7599 | 374.5186 | 445.6171
4463.5979 | 382.3502 | 374.471 | 446.8784
4464.5979 | 380.2803 | 374.1331 | 446.7444
4465.5979 | 380.0507 | 374.4125 | 447.89
4466.5979 | 381.3449 | 374.3325 | 446.79
4467.5979 | 376.9086 | 374.024 | 447.9092
4468.5979 | 373.4309 | 373.821 | 447.1858
4469.5979 | 378.4489 | 373.4268 | 447.4836
4470.5979 | 376.0583 | 373.1715 | 446.7494
4471.5979 | 378.8557 | 373.0637 | 447.098
4472.5979 | 373.8891 | 372.8444 | 447.9289
4473.5979 | 373.2107 | 371.9605 | 445.4683
4474.5979 | 370.8699 | 371.5933 | 443.6833
4475.5979 | 378.726 | 372.2314 | 444.8526
4476.5979 | 379.3558 | 372.0997 | 444.4147
4477.5979 | 379.9098 | 372.0082 | 442.0746
4478.5979 | 376.7276 | 372.0699 | 440.2413
4479.5979 | 372.323 | 371.6602 | 439.9498
4480.5979 | 372.4207 | 371.3028 | 439.2909
4481.5979 | 376.2542 | 370.8118 | 438.2041
4482.5979 | 377.4528 | 370.8589 | 438.7541
4483.5979 | 375.8768 | 370.0243 | 438.8175
4484.5979 | 374.5149 | 368.9007 | 437.9653
4485.5979 | 375.9634 | 369.0885 | 434.7326
4486.5979 | 376.022 | 369.1661 | 432.7771
4487.5979 | 370.9155 | 369.2117 | 433.8318
4488.5979 | 372.2247 | 369.3312 | 435.6978
4489.5979 | 376.8465 | 369.1026 | 437.5584
4490.5979 | 377.5796 | 368.8806 | 438.1809
4491.5979 | 377.0171 | 369.0607 | 438.5025
4492.5979 | 377.0299 | 369.458 | 439.5591
4493.5979 | 375.897 | 369.4331 | 439.121
4494.5979 | 376.4555 | 369.1389 | 439.0266
4495.5979 | 377.8007 | 369.2822 | 440.2196
4496.5979 | 374.0689 | 369.2589 | 439.5496
4497.5979 | 375.2534 | 369.5599 | 442.4594
4498.5979 | 375.1826 | 368.9295 | 440.7143
4499.5979 | 378.9629 | 368.6489 | 438.8398
4500.5979 | 376.1961 | 369.1397 | 438.9728
4501.5979 | 377.4621 | 369.1081 | 439.8655
4502.5979 | 374.0185 | 369.0112 | 442.3565
4503.5979 | 374.3952 | 368.5841 | 441.7079
4504.5979 | 368.0229 | 368.7114 | 440.5493
4505.5979 | 373.3076 | 368.661 | 440.517
4506.5979 | 374.6193 | 368.8315 | 439.463
4507.5979 | 372.2772 | 368.7512 | 438.6208
4508.5979 | 372.1836 | 368.6226 | 436.1745
4509.5979 | 371.5996 | 368.8706 | 433.9418
4510.5979 | 368.6712 | 368.3278 | 432.2931
4511.5979 | 369.7899 | 367.3539 | 432.5148
4512.5979 | 369.4021 | 366.742 | 432.2447
4513.5979 | 367.4272 | 366.4612 | 432.2468
4514.5979 | 371.5195 | 366.1053 | 431.6224
4515.5979 | 371.1519 | 366.5677 | 431.2756
4516.5979 | 368.2079 | 367.3866 | 431.746
4517.5979 | 366.3656 | 367.9328 | 432.6579
4518.5979 | 367.9053 | 368.422 | 434.0131
4519.5979 | 371.4347 | 368.8481 | 435.0003
4520.5979 | 369.328 | 369.5011 | 437.2144
4521.5979 | 372.131 | 369.2284 | 437.3471
4522.5979 | 369.7706 | 368.4613 | 437.3413
4523.5979 | 373.2697 | 368.2467 | 435.9051
4524.5979 | 371.216 | 367.6305 | 434.7966
4525.5979 | 370.5918 | 367.3741 | 432.2906
4526.5979 | 369.688 | 367.4569 | 431.6418
4527.5979 | 368.6653 | 368.1548 | 431.8207
4528.5979 | 366.4429 | 367.6563 | 433.0684
4529.5979 | 369.4722 | 367.6337 | 432.65
4530.5979 | 369.1953 | 367.71 | 431.9374
4531.5979 | 370.4458 | 367.4533 | 432.4417
4532.5979 | 369.0284 | 366.8393 | 432.3994
4533.5979 | 367.9125 | 366.6693 | 432.3334
4534.5979 | 366.596 | 366.433 | 432.0513
4535.5979 | 369.5263 | 366.8126 | 433.218
4536.5979 | 365.2029 | 367.1323 | 434.8941
4537.5979 | 364.0806 | 366.8494 | 435.5132
4538.5979 | 362.1883 | 367.1839 | 435.7778
4539.5979 | 362.7437 | 367.4751 | 436.7131
4540.5979 | 363.2855 | 366.9758 | 437.1725
4541.5979 | 366.1565 | 366.7066 | 437.5668
4542.5979 | 366.5097 | 366.4187 | 437.8009
4543.5979 | 366.3533 | 366.1043 | 437.3275
4544.5979 | 366.6641 | 366.3866 | 437.041
4545.5979 | 365.0964 | 365.8097 | 435.9293
4546.5979 | 363.2391 | 365.4931 | 436.4422
4547.5979 | 366.3355 | 366.0586 | 439.1512
4548.5979 | 365.9742 | 365.9902 | 441.7651
4549.5979 | 366.1761 | 366.3435 | 442.4063
4550.5979 | 365.8804 | 366.2387 | 440.8563
4551.5979 | 365.5661 | 365.584 | 440.415
4552.5979 | 365.6809 | 365.0869 | 439.3838
4553.5979 | 366.4299 | 364.8015 | 437.9222
4554.5979 | 365.9106 | 365.1371 | 436.6611
4555.5979 | 366.587 | 364.8749 | 434.4034
4556.5979 | 365.6478 | 364.8914 | 432.6433
4557.5979 | 365.301 | 364.8188 | 430.7574
4558.5979 | 364.416 | 364.4254 | 429.4548
4559.5979 | 363.9484 | 364.0811 | 428.5803
4560.5979 | 362.4489 | 363.4542 | 427.8952
4561.5979 | 364.5292 | 362.8644 | 427.4289
4562.5979 | 362.6312 | 363.1286 | 426.2995
4563.5979 | 365.2465 | 363.789 | 427.3462
4564.5979 | 365.1923 | 362.9758 | 427.9036
4565.6135 | 363.6409 | 362.7296 | 425.3987
4566.5979 | 365.5327 | 362.8961 | 425.0885
4567.5979 | 364.0173 | 363.1405 | 426.215
4568.5979 | 365.66 | 362.8922 | 427.0337
4569.5979 | 364.0182 | 362.8133 | 427.075
4570.5979 | 364.9418 | 362.1346 | 427.9127
4571.5979 | 363.6945 | 361.5871 | 429.5597
4572.5979 | 362.5221 | 361.8158 | 430.8486
4573.5979 | 363.2584 | 361.9528 | 430.6033
4574.5979 | 362.2122 | 361.9705 | 430.9911
4575.5979 | 363.3405 | 362.2041 | 431.3891
4576.5979 | 361.7006 | 362.543 | 433.1048
4577.5979 | 359.276 | 362.6817 | 432.5965
4578.5979 | 356.8209 | 362.2446 | 433.9363
4579.5979 | 361.4718 | 362.0159 | 432.5968
4580.5979 | 362.0332 | 362.4047 | 432.4706
4581.5979 | 359.2104 | 363.0715 | 432.0302
4582.5979 | 361.2104 | 363.906 | 431.5068
4583.5979 | 361.3395 | 363.8424 | 430.3713
4584.5979 | 358.9023 | 363.7466 | 430.3502
4585.5979 | 359.9896 | 362.8364 | 429.9859
4586.5979 | 362.0476 | 362.615 | 429.0602
4587.5979 | 363.216 | 362.8189 | 428.8027
4588.5979 | 362.5195 | 362.6831 | 427.6899
4589.5979 | 363.5114 | 362.22 | 425.6097
4590.5979 | 362.5398 | 361.8147 | 425.2942
4591.5979 | 363.0569 | 361.8252 | 423.9181
4592.5979 | 362.9156 | 361.414 | 421.7571
4593.5979 | 361.7455 | 361.6148 | 422.3032
4594.5979 | 361.9607 | 360.9282 | 422.7228
4595.6135 | 362.074 | 360.0948 | 421.0596
4596.5979 | 362.431 | 360.0785 | 421.7175
4597.5979 | 362.811 | 360.2365 | 423.0422
4598.5979 | 360.927 | 360.3283 | 422.8313
4599.5979 | 361.2233 | 360.2903 | 422.4586
4600.5979 | 360.4707 | 360.5968 | 424.306
4601.5979 | 361.5577 | 360.077 | 424.5712
4602.6135 | 362.7636 | 359.6642 | 423.1916
4603.5979 | 361.9225 | 359.9536 | 423.1886
4604.5979 | 360.1081 | 359.9232 | 422.3035
4605.5979 | 360.3512 | 359.8713 | 422.4656
4606.5979 | 359.4521 | 359.4715 | 423.071
4607.5979 | 360.349 | 359.4031 | 422.9132
4608.5979 | 359.8023 | 359.6236 | 424.0412
4609.5979 | 359.8782 | 359.4621 | 423.5189
4610.5979 | 357.0767 | 359.6845 | 421.8903
4611.5979 | 357.8474 | 359.7188 | 420.8655
4612.5979 | 359.687 | 359.9816 | 419.5776
4613.5979 | 360.2179 | 360.0611 | 418.8125
4614.5979 | 358.6409 | 360.0764 | 418.9788
4615.5979 | 355.3904 | 359.5931 | 417.5149
4616.5979 | 355.6606 | 359.1078 | 417.4381
4617.5979 | 356.6757 | 358.7522 | 418.035
4618.5979 | 359.0596 | 358.4459 | 417.9613
4619.5979 | 359.52 | 358.7434 | 418.7933
4620.5979 | 358.4983 | 358.5598 | 417.8051
4621.5979 | 356.0723 | 358.1553 | 417.1887
4622.5979 | 356.6836 | 357.3881 | 416.7709
4623.5979 | 356.5556 | 357.1961 | 417.2318
4624.5979 | 354.9475 | 356.9482 | 417.8056
4625.5979 | 355.2817 | 356.7287 | 417.1528
4626.5979 | 356.2439 | 356.5533 | 417.3797
4627.5979 | 355.5286 | 356.1925 | 417.7101
4628.5979 | 352.8158 | 355.4444 | 418.7658
4629.5979 | 355.5993 | 355.6793 | 417.9206
4630.5979 | 356.0783 | 355.4558 | 415.7032
4631.5979 | 354.8455 | 355.5048 | 416.6877
4632.5979 | 354.379 | 355.6086 | 415.9781
4633.5979 | 356.0668 | 355.6069 | 415.1838
4634.5979 | 352.8354 | 355.363 | 415.8408
4635.5979 | 352.0746 | 355.4061 | 415.4115
4636.5979 | 351.3344 | 355.7709 | 416.1002
4637.5979 | 351.932 | 356.0358 | 414.5026
4638.5979 | 351.5943 | 356.0002 | 415.446
4639.5979 | 349.4852 | 356.3686 | 416.201
4640.5979 | 351.1751 | 356.9062 | 416.7681
4641.5979 | 350.9972 | 357.2898 | 417.2676
4642.5979 | 351.0789 | 357.4503 | 417.5631
4643.5979 | 350.7149 | 357.8253 | 417.3147
4644.5979 | 350.0844 | 357.9438 | 417.1626
4645.5979 | 349.8185 | 358.0104 | 419.2918
4646.5979 | 351.2755 | 358.8974 | 418.6222
4647.5979 | 350.146 | 358.1565 | 416.665
4648.5979 | 351.5686 | 358.2843 | 416.2355
4649.5979 | 350.7927 | 357.7197 | 414.4433
4650.5979 | 350.9641 | 357.3529 | 413.8258
4651.5979 | 350.6692 | 356.6491 | 413.0342
4652.5979 | 350.9002 | 356.8402 | 413.1753
4653.5979 | 352.2692 | 357.422 | 414.6294
4654.5979 | 350.8784 | 357.7433 | 414.77
4655.5979 | 351.5053 | 357.9105 | 414.7018
4656.5979 | 351.0087 | 357.8949 | 414.5721
4657.5979 | 350.1728 | 357.8699 | 414.2703
4658.5979 | 350.7757 | 358.6525 | 414.1363
4659.5979 | 350.0957 | 358.6217 | 413.7241
4660.5979 | 351.189 | 358.3304 | 413.8136
4661.5979 | 350.6989 | 357.9546 | 411.9436
4662.5979 | 349.7856 | 357.3977 | 413.0137
4663.5979 | 350.2126 | 356.6967 | 412.8239
4664.5979 | 349.6862 | 356.1566 | 411.473
4665.5979 | 348.5872 | 354.7626 | 410.9571
4666.5979 | 349.3463 | 354.1534 | 409.116
4667.5979 | 349.3068 | 353.8424 | 408.1859
4668.5979 | 349.2794 | 353.6291 | 408.2666
4669.5979 | 349.0115 | 354.0301 | 409.9814
4670.5979 | 347.7588 | 353.7684 | 409.5496
4671.5979 | 346.2866 | 353.8143 | 408.9554
4672.5979 | 348.7672 | 353.6496 | 408.2445
4673.5979 | 348.7325 | 353.5386 | 407.6908
4674.5979 | 348.5377 | 353.0412 | 406.5805
4675.5979 | 348.3213 | 352.9871 | 405.4336
4676.5979 | 348.906 | 352.6681 | 406.1851
4677.5979 | 347.1277 | 352.2486 | 407.0311
4678.5979 | 347.2863 | 351.637 | 406.3889
4679.5979 | 348.6148 | 351.4436 | 405.7901
4680.5979 | 348.7843 | 351.7092 | 406.4614
4681.5979 | 348.3388 | 351.6622 | 406.6473
4682.5979 | 348.6405 | 351.559 | 408.3356
4683.5979 | 349.2793 | 351.0595 | 407.8417
4684.5979 | 348.3856 | 350.9201 | 407.796
4685.5979 | 347.9398 | 350.9876 | 407.7729
4686.5979 | 346.7851 | 351.0417 | 406.6481
4687.5979 | 347.2311 | 350.9197 | 405.0186
4688.5979 | 347.5572 | 351.404 | 403.7171
4689.5979 | 347.5198 | 351.0344 | 403.3009
4690.5979 | 347.2844 | 351.5604 | 404.1995
4691.5979 | 347.7886 | 351.0419 | 403.284
4692.5979 | 347.3238 | 350.9448 | 401.7668
4693.5979 | 345.8827 | 350.8829 | 401.5638
4694.5979 | 345.4143 | 351.5828 | 402.0843
4695.5979 | 345.3749 | 351.5867 | 401.7422
4696.5979 | 345.2789 | 351.2203 | 401.7599
4697.5979 | 343.5565 | 350.9057 | 401.3325
4698.5979 | 344.911 | 350.6978 | 400.6213
4699.5979 | 344.8201 | 350.5963 | 399.7913
4700.5979 | 342.9824 | 350.5791 | 399.9104
4701.5979 | 344.012 | 350.4586 | 400.016
4702.5979 | 343.8468 | 350.7401 | 399.8436
4703.5979 | 344.373 | 350.5733 | 400.0226
4704.5979 | 343.4546 | 350.023 | 399.0549
4705.5979 | 344.8702 | 349.8098 | 398.6114
4706.5979 | 345.0693 | 350.2423 | 398.6631
4707.5979 | 344.7959 | 350.4437 | 397.932
4708.5979 | 345.2715 | 350.5904 | 398.1969
4709.5979 | 344.413 | 350.0217 | 398.1987
4710.5979 | 344.4407 | 349.6032 | 397.5447
4711.5979 | 344.3547 | 349.6894 | 397.4492
4712.5979 | 344.5174 | 349.6185 | 396.6454
4713.5979 | 345.0326 | 349.8145 | 396.03
4714.5979 | 343.253 | 349.5503 | 395.3619
4715.5979 | 342.5887 | 348.7719 | 394.3115
4716.5979 | 343.8714 | 349.0422 | 393.7732
4717.5979 | 343.5138 | 348.8186 | 392.8225
4718.5979 | 342.8606 | 349.1191 | 393.3465
4719.5979 | 343.6346 | 349.5478 | 395.0782
4720.5979 | 344.0397 | 349.1427 | 396.5102
4721.5979 | 343.6941 | 348.9096 | 396.1801
4722.5979 | 342.6851 | 349.0576 | 395.3481
4723.5979 | 341.7489 | 348.8678 | 394.9045
4724.5979 | 342.0922 | 348.848 | 394.6666
4725.5979 | 341.9447 | 348.5544 | 394.4625
4726.5979 | 341.4242 | 348.9431 | 392.7745
4727.5979 | 340.9663 | 349.0001 | 393.8949
4728.5979 | 339.0057 | 348.7317 | 394.2892
4729.5979 | 337.5993 | 348.8336 | 393.5227
4730.5979 | 338.0599 | 349.1874 | 394.6828
4731.5979 | 338.5968 | 349.2185 | 394.2864
4732.5979 | 336.419 | 348.8079 | 393.5537
4733.5979 | 336.7997 | 348.3136 | 394.7164
4734.5979 | 338.2664 | 347.9448 | 395.1133
4735.5979 | 337.4562 | 347.8306 | 394.8709
4736.5979 | 338.9281 | 347.4456 | 395.1152
4737.5979 | 339.3099 | 347.0582 | 394.6705
4738.5979 | 339.3282 | 347.4855 | 393.9812
4739.5979 | 339.2927 | 347.3348 | 393.3432
4740.5979 | 339.2693 | 346.902 | 392.5483
4741.5979 | 339.1839 | 346.5959 | 391.5467
4742.5979 | 339.538 | 346.5757 | 391.2461
4743.5979 | 339.8272 | 346.4582 | 391.0167
4744.5979 | 340.0694 | 346.6397 | 389.2416
4745.5979 | 339.7448 | 346.3363 | 389.6073
4746.5979 | 340.0968 | 346.1453 | 389.6463
4747.5979 | 339.5641 | 345.9658 | 389.5544
4748.5979 | 339.2405 | 345.8158 | 389.0015
4749.5979 | 338.8914 | 346.1245 | 389.0763
4750.5979 | 338.1521 | 345.8521 | 388.5109
4751.5979 | 337.4842 | 346.1212 | 388.6774
4752.5979 | 337.0304 | 345.8863 | 389.2962
4753.5979 | 335.8605 | 346.3972 | 389.336
4754.5979 | 336.4731 | 346.4821 | 389.5421
4755.5979 | 333.7158 | 346.0301 | 389.2804
4756.5979 | 332.4 | 346.6465 | 390.0483
4757.5979 | 333.8887 | 346.5131 | 389.6977
4758.5979 | 333.3675 | 346.3152 | 390.2883
4759.5979 | 333.6575 | 346.6049 | 391.7643
4760.5979 | 335.0962 | 346.3637 | 392.5006
4761.5979 | 335.4988 | 346.6669 | 392.9435
4762.5979 | 336.4424 | 346.829 | 392.8621
4763.5979 | 337.0446 | 346.4458 | 392.4204
4764.5979 | 337.9046 | 345.8974 | 391.2506
4765.5979 | 337.1581 | 345.5903 | 391.101
4766.5979 | 336.865 | 345.3862 | 390.2105
4767.5979 | 336.7994 | 345.4714 | 389.7336
4768.5979 | 336.8585 | 345.65 | 388.826
4769.5979 | 336.7736 | 345.3486 | 388.9785
4770.5979 | 337.5151 | 345.3031 | 389.4011
4771.5979 | 335.3917 | 345.3261 | 390.0997
4772.5979 | 336.1597 | 345.5563 | 390.6237
4773.5979 | 336.8943 | 345.7117 | 390.5303
4774.5979 | 337.476 | 345.9162 | 390.9962
4775.5979 | 337.5476 | 345.6909 | 390.5178
4776.5979 | 333.9601 | 345.2175 | 390.6408
4777.5979 | 334.053 | 345.1885 | 390.8842
4778.5979 | 334.9951 | 345.1727 | 390.4289
4779.5979 | 335.2336 | 344.8718 | 390.2288
4780.5979 | 336.0019 | 345.0935 | 388.7585
4781.5979 | 335.9097 | 345.0634 | 388.1243
4782.6135 | 336.1077 | 344.7971 | 388.4131
4783.5979 | 334.9938 | 344.2954 | 388.4092
4784.5979 | 335.5901 | 344.0407 | 387.3615
4785.5979 | 335.5867 | 343.9771 | 386.6447
4786.5979 | 335.9209 | 343.998 | 386.9924
4787.5979 | 335.4 | 343.8336 | 387.4147
4788.5979 | 333.8157 | 343.7987 | 388.2081
4789.5979 | 334.5446 | 343.3727 | 386.8641
4790.5979 | 333.6107 | 343.0345 | 385.7491
4791.5979 | 334.5418 | 342.9939 | 385.0781
4792.5979 | 334.2012 | 342.6792 | 383.6059
4793.5979 | 333.914 | 343.6952 | 383.9923
4794.5979 | 334.1704 | 344.2394 | 383.5923
4795.6135 | 334.4548 | 343.8684 | 384.1431
4796.5979 | 333.5645 | 343.7759 | 383.9626
4797.5979 | 333.1428 | 343.8121 | 383.0687
4798.5979 | 333.5142 | 343.6769 | 383.4671
4799.5979 | 333.4249 | 343.2519 | 382.8477
4800.5979 | 333.1886 | 342.468 | 383.6712
4801.5979 | 331.3906 | 341.7992 | 383.4725
4802.5979 | 332.6421 | 341.5807 | 382.6446
4803.5979 | 333.8064 | 342.0511 | 381.3911
4804.5979 | 334.1006 | 342.2224 | 380.9541
4805.6135 | 333.7789 | 342.4051 | 380.1097
4806.5979 | 333.7239 | 342.2169 | 379.5844
4807.5979 | 333.7132 | 341.8732 | 379.6278
4808.5979 | 333.0025 | 341.9728 | 380.3189
4809.5979 | 332.9308 | 342.1984 | 380.1843
4810.5979 | 331.6909 | 342.0273 | 380.6165
4811.5979 | 333.1782 | 341.4574 | 380.0843
4812.5979 | 333.1178 | 341.5485 | 380.2874
4813.5979 | 332.5921 | 341.1381 | 379.4462
4814.5979 | 331.3776 | 341.0334 | 379.5536
4815.5979 | 330.6918 | 340.4214 | 379.2617
4816.5979 | 330.7774 | 340.4229 | 379.2322
4817.5979 | 331.2948 | 340.147 | 378.8236
4818.5979 | 330.4842 | 339.5578 | 379.0081
4819.5979 | 330.1555 | 339.3948 | 378.8136
4820.5979 | 331.3128 | 339.6474 | 378.2378
4821.5979 | 331.6332 | 339.6586 | 377.7351
4822.5979 | 331.207 | 339.8309 | 377.1914
4823.5979 | 330.9021 | 338.9358 | 376.7503
4824.5979 | 329.8299 | 338.7274 | 376.0707
4825.5979 | 330.7371 | 339.2451 | 375.9112
4826.5979 | 330.5664 | 339.4426 | 376.2118
4827.5979 | 330.6144 | 339.1983 | 376.1794
4828.5979 | 330.7134 | 339.0082 | 375.6248
4829.5979 | 329.9864 | 339.2534 | 375.3257
4830.5979 | 330.8931 | 339.2886 | 375.2991
4831.5979 | 330.6971 | 339.3394 | 375.7814
4832.5979 | 330.2728 | 339.4942 | 375.426
4833.5979 | 330.2251 | 339.3154 | 375.0595
4834.5979 | 329.9447 | 339.1822 | 376.009
4835.5979 | 330.3995 | 338.6595 | 376.0447
4836.5979 | 330.2154 | 338.5227 | 374.9874
4837.5979 | 330.2665 | 338.4246 | 375.0455
4838.5979 | 330.1366 | 338.2821 | 374.5901
4839.5979 | 329.7638 | 337.9741 | 373.2722
4840.5979 | 329.1114 | 337.6419 | 372.4695
4841.5979 | 329.9458 | 337.7822 | 372.203
4842.5979 | 329.6695 | 337.5937 | 371.9326
4843.5979 | 329.5478 | 337.3728 | 371.6432
4844.5979 | 329.8598 | 337.4711 | 370.9564
4845.5979 | 329.9511 | 336.8775 | 370.9844
4846.5979 | 329.8777 | 336.759 | 370.8951
4847.5979 | 329.6045 | 336.8599 | 370.4416
4848.5979 | 328.5203 | 336.6518 | 371.0066
4849.5979 | 327.6553 | 336.6449 | 370.9498
4850.5979 | 327.4706 | 336.2044 | 371.3988
4851.5979 | 328.2328 | 335.9456 | 371.5785
4852.5979 | 326.923 | 336.0066 | 371.2528
4853.5979 | 328.143 | 336.1328 | 371.2092
4854.5979 | 328.3499 | 336.2018 | 371.645
4855.5979 | 327.5468 | 336.1858 | 371.3558
4856.5979 | 326.9413 | 335.691 | 372.4966
4857.5979 | 326.8517 | 335.7431 | 373.1163
4858.5979 | 326.6875 | 335.9327 | 373.7613
4859.5979 | 326.4926 | 336.4138 | 374.6483
4860.5979 | 326.6376 | 336.2467 | 373.9415
4861.5979 | 327.086 | 336.1976 | 373.0737
4862.5979 | 326.2499 | 335.7569 | 372.0645
4863.5979 | 325.9399 | 335.7975 | 371.4235
4864.5979 | 326.0991 | 335.9265 | 371.3796
4865.5979 | 326.1514 | 336.0928 | 371.0575
4866.5979 | 325.4295 | 335.7167 | 371.8738
4867.5979 | 325.6591 | 335.9549 | 372.1054
4868.5979 | 325.2667 | 335.4053 | 372.1217
4869.5979 | 325.2448 | 335.0556 | 372.3813
4870.5979 | 325.2104 | 335.5556 | 372.7193
4871.5979 | 325.5416 | 335.4875 | 371.9591
4872.5979 | 325.5453 | 335.1843 | 371.8143
4873.5979 | 325.4454 | 334.6449 | 371.1458
4874.5979 | 324.7772 | 334.4361 | 371.8714
4875.5979 | 324.3223 | 334.3007 | 370.9757
4876.5979 | 323.9169 | 334.3304 | 371.328
4877.5979 | 324.156 | 334.504 | 372.2324
4878.5979 | 324.3975 | 334.6035 | 372.3277
4879.5979 | 324.2897 | 334.6406 | 372.4855
4880.5979 | 323.4584 | 336.0824 | 372.449
4881.5979 | 323.34 | 336.0339 | 372.3673
4882.5979 | 323.0536 | 335.4506 | 371.9938
4883.5979 | 322.5155 | 335.2661 | 371.7902
4884.5979 | 322.5408 | 335.2446 | 371.5531
4885.5979 | 322.5361 | 335.0861 | 371.0599
4886.5979 | 322.8388 | 335.2194 | 371.4147
4887.5979 | 323.2893 | 334.9665 | 370.2759
4888.5979 | 322.5737 | 334.9308 | 369.3643
4889.5979 | 322.1579 | 335.1518 | 368.1656
4890.5979 | 322.3552 | 334.9148 | 367.8664
4891.5979 | 322.1693 | 334.8627 | 366.8523
4892.5979 | 321.7766 | 334.8859 | 368.2014
4893.5979 | 321.7321 | 334.5486 | 368.2966
4894.5979 | 322.2664 | 334.1981 | 367.9545
4895.5979 | 322.1044 | 333.882 | 367.9284
4896.5979 | 321.9735 | 334.3281 | 368.5302
4897.5979 | 321.979 | 334.5754 | 367.6952
4898.5979 | 322.1945 | 334.9195 | 367.3988
4899.5979 | 321.6028 | 334.9697 | 367.7962
4900.5979 | 321.3997 | 335.3116 | 367.4391
4901.5979 | 321.5454 | 335.2748 | 367.0637
4902.5979 | 321.5902 | 334.8875 | 367.2049
4903.5979 | 321.1036 | 334.5363 | 367.1354
4904.5979 | 320.9096 | 334.5338 | 366.5189
4905.5979 | 321.2752 | 334.282 | 366.7427
4906.5979 | 321.2909 | 334.0558 | 366.8963
4907.5979 | 320.9502 | 333.9468 | 366.905
4908.5979 | 321.0555 | 334.1598 | 366.7084
4909.5979 | 320.8739 | 334.2635 | 366.0016
4910.5979 | 320.6305 | 333.8031 | 365.9177
4911.5979 | 320.8246 | 333.8478 | 366.3451
4912.5979 | 320.4659 | 333.5125 | 365.5131
4913.5979 | 320.0441 | 333.2496 | 365.1246
4914.5979 | 320.1318 | 332.9815 | 364.7345
4915.5979 | 319.9887 | 332.3731 | 364.2024
4916.5979 | 319.4746 | 331.813 | 364.8975
4917.5979 | 319.5164 | 331.6475 | 364.9855
4918.5979 | 319.6918 | 331.1947 | 365.064
4919.5979 | 319.2405 | 331.0305 | 364.619
4920.5979 | 319.1599 | 331.1804 | 364.6057
4921.5979 | 319.423 | 331.4787 | 364.2044
4922.5979 | 319.335 | 331.6 | 364.0519
4923.5979 | 319.3875 | 331.3051 | 364.0515
4924.5979 | 319.358 | 331.0901 | 363.4839
4925.5979 | 319.2881 | 330.7717 | 363.1409
4926.5979 | 318.8105 | 331.0514 | 362.5916
4927.5979 | 318.8472 | 330.9233 | 361.6284
4928.5979 | 318.8093 | 331.0888 | 361.4593
4929.5979 | 318.4774 | 331.0056 | 361.4996
4930.5979 | 318.0706 | 330.7741 | 360.6609
4931.5979 | 318.1619 | 330.8136 | 360.502
4932.5979 | 318.3584 | 330.3859 | 359.115
4933.5979 | 317.9923 | 330.676 | 358.6611
4934.5979 | 318.3299 | 330.9569 | 359.0056
4935.5979 | 318.4926 | 330.5721 | 359.4517
4936.5979 | 317.8963 | 330.3704 | 359.531
4937.5979 | 317.973 | 330.4097 | 359.4499
4938.5979 | 317.8332 | 330.3438 | 359.7902
4939.5979 | 317.0525 | 329.9232 | 359.7014
4940.5979 | 316.9805 | 329.6439 | 360.356
4941.5979 | 316.9227 | 329.5777 | 360.2266
4942.5979 | 316.7557 | 329.4327 | 360.2204
4943.5979 | 316.8935 | 329.788 | 360.1372
4944.5979 | 317.0041 | 329.8725 | 359.8851
4945.5979 | 317.0006 | 329.5536 | 359.2083
4946.5979 | 317.0341 | 329.4397 | 359.5102
4947.5979 | 316.9979 | 329.0968 | 359.2559
4948.5979 | 316.7391 | 328.567 | 359.3603
4949.5979 | 316.6352 | 328.1156 | 358.0188
4950.5979 | 316.2265 | 328.11 | 357.5601
4951.5979 | 316.041 | 327.9426 | 356.7766
4952.5979 | 316.3798 | 328.2535 | 356.118
4953.5979 | 317.0451 | 328.3223 | 356.3114
4954.5979 | 317.3603 | 328.5282 | 355.6078
4955.5979 | 317.0876 | 328.6729 | 354.3769
4956.5979 | 317.1066 | 328.5343 | 354.3814
4957.5979 | 316.6706 | 327.9488 | 354.077
4958.5979 | 316.5162 | 328.4107 | 354.6229
4959.5979 | 316.8444 | 328.682 | 355.3383
4960.5979 | 316.9161 | 328.3386 | 355.1732
4961.5979 | 316.4068 | 327.7389 | 354.8671
4962.5979 | 315.7197 | 327.5438 | 355.1609
4963.5979 | 315.2954 | 327.3948 | 354.8941
4964.5979 | 315.1942 | 327.6148 | 354.7044
4965.5979 | 315.0209 | 327.449 | 353.4772
4966.5979 | 315.1961 | 327.1554 | 353.5561
4967.5979 | 315.595 | 326.939 | 353.6876
4968.5979 | 315.767 | 326.7652 | 353.756
4969.5979 | 315.7295 | 326.8085 | 354.0884
4970.5979 | 315.8493 | 327.169 | 353.7162
4971.5979 | 315.7802 | 327.1435 | 353.5377
4972.5979 | 315.6082 | 327.3714 | 352.7607
4973.5979 | 315.2876 | 327.0211 | 352.3952
4974.5979 | 315.1863 | 326.8974 | 353.1678
4975.5979 | 314.9662 | 327.3712 | 353.2639
4976.5979 | 315.057 | 327.522 | 352.9463
4977.5979 | 314.7217 | 326.4821 | 353.0123
4978.5979 | 314.0561 | 326.6028 | 353.0494
4979.5979 | 313.7091 | 326.4244 | 352.5514
4980.5979 | 313.2026 | 326.0712 | 352.5498
4981.5979 | 312.5262 | 325.9462 | 352.6142
4982.5979 | 311.9449 | 325.8393 | 352.6335
4983.5979 | 312.1524 | 325.2564 | 353.3269
4984.5979 | 312.2057 | 325.1881 | 353.716
4985.5979 | 312.5369 | 324.9927 | 353.1505
4986.5979 | 312.5223 | 325.2719 | 352.7017
4987.5979 | 312.2486 | 324.6571 | 351.9525
4988.5979 | 312.2636 | 324.6273 | 351.0934
4989.5979 | 312.3067 | 325.047 | 351.014
4990.5979 | 312.2907 | 324.9866 | 350.9416
4991.5979 | 312.1694 | 324.949 | 350.9155
4992.5979 | 311.842 | 324.3855 | 350.68
4993.5979 | 311.4896 | 324.4339 | 350.6369
4994.5979 | 311.6325 | 324.4079 | 351.6794
4995.5979 | 311.4757 | 324.9856 | 352.1735
4996.5979 | 311.4713 | 325.8441 | 352.4572
4997.5979 | 311.5702 | 326.2562 | 352.8934
4998.5979 | 311.997 | 326.4057 | 352.1146
4999.5979 | 312.2876 | 326.7169 | 352.6481
5000.5979 | 312.7003 | 326.8901 | 352.3917
5001.5979 | 312.7646 | 327.1063 | 352.5608
5002.5979 | 312.687 | 326.7071 | 352.1692
5003.5979 | 312.8333 | 326.0773 | 352.0964
5004.5979 | 312.994 | 326.3459 | 351.5044
5005.5979 | 313.0892 | 326.3771 | 350.8523
5006.5979 | 313.3393 | 326.1543 | 350.1636
5007.5979 | 313.132 | 326.0109 | 350.1111
5008.5979 | 312.9425 | 325.9703 | 349.2666
5009.5979 | 312.573 | 325.4829 | 349.0124
5010.5979 | 312.4591 | 325.0101 | 348.261
5011.5979 | 312.5383 | 325.2216 | 347.7971
5012.5979 | 312.6417 | 325.382 | 347.9913
5013.5979 | 312.7011 | 325.7594 | 347.3376
5014.5979 | 312.6079 | 326.1109 | 347.3093
5015.5979 | 312.606 | 326.5152 | 347.1042
5016.5979 | 312.1683 | 326.3677 | 346.5913
5017.5979 | 311.7168 | 326.0875 | 347.3528
5018.5979 | 311.2847 | 325.5706 | 347.5889
5019.5979 | 310.9008 | 325.1729 | 347.6764
5020.5979 | 310.9598 | 324.6145 | 347.2548
5021.5979 | 310.9156 | 323.7813 | 347.573
5022.5979 | 310.6172 | 323.1845 | 347.453
5023.5979 | 310.9658 | 323.425 | 347.3057
5024.5979 | 311.094 | 323.484 | 347.1886
5025.5979 | 311.252 | 323.3837 | 346.9218
5026.5979 | 311.4575 | 323.4414 | 346.1346
5027.5979 | 311.5209 | 323.3363 | 345.8337
5028.5979 | 311.6336 | 322.8879 | 345.5002
5029.5979 | 311.5574 | 322.712 | 345.6774
5030.5979 | 311.7073 | 322.5415 | 346.4842
5031.5979 | 311.3276 | 322.184 | 346.0811
5032.5979 | 310.8617 | 322.21 | 346.2887
5033.5979 | 310.422 | 322.2312 | 346.7507
5034.5979 | 310.4623 | 322.0348 | 346.6321
5035.5979 | 310.0762 | 321.9328 | 346.8991
5036.5979 | 309.8241 | 321.9727 | 347.1084
5037.5979 | 309.7826 | 321.7323 | 346.8873
5038.5979 | 309.9866 | 321.6228 | 346.5189
5039.5979 | 310.1183 | 321.2684 | 346.3745
5040.5979 | 310.0131 | 320.7401 | 346.0749
5041.5979 | 310.0577 | 321.0465 | 346.4988
5042.5979 | 309.8919 | 321.7907 | 346.3844
5043.5979 | 309.833 | 322.492 | 345.6069
5044.5979 | 309.4244 | 322.6941 | 344.8619
5045.5979 | 309.2249 | 322.9484 | 345.4945
5046.5979 | 309.0614 | 322.8803 | 345.946
5047.5979 | 309.1939 | 322.9097 | 346.3499
5048.5979 | 309.2664 | 322.7441 | 345.9474
5049.5979 | 309.0287 | 322.258 | 345.5396
5050.5979 | 309.1117 | 322.144 | 344.45
5051.5979 | 309.0942 | 322.0414 | 344.48
5052.5979 | 308.7273 | 321.7563 | 344.2564
5053.5979 | 308.5864 | 321.7956 | 343.7484
5054.5979 | 308.0866 | 321.3113 | 344.1568
5055.5979 | 308.078 | 320.9129 | 343.8524
5056.5979 | 308.3907 | 321.0866 | 343.5303
5057.5979 | 308.4991 | 320.5998 | 343.4148
5058.5979 | 307.9185 | 320.2711 | 343.1053
5059.5979 | 308.1032 | 320.4352 | 342.727
5060.5979 | 308.3603 | 320.1656 | 342.882
5061.5979 | 308.5547 | 319.8923 | 342.7587
5062.5979 | 308.5224 | 319.9277 | 342.8697
5063.5979 | 308.0378 | 320.1885 | 342.3164
5064.5979 | 308.2268 | 320.7869 | 343.189
5065.5979 | 308.1181 | 320.8909 | 343.8298
5066.5979 | 307.5452 | 321.0738 | 344.2698
5067.5979 | 307.0522 | 320.9695 | 344.2752
5068.5979 | 306.3712 | 320.4462 | 343.8398
5069.5979 | 306.1196 | 319.7342 | 344.2938
5070.5979 | 306.457 | 319.8293 | 343.4998
5071.5979 | 306.2561 | 319.7896 | 343.118
5072.5979 | 306.2182 | 319.5363 | 343.0847
5073.5979 | 306.8163 | 319.4821 | 343.2158
5074.5979 | 307.0631 | 319.2646 | 343.3572
5075.5979 | 306.6886 | 319.4807 | 343.1258
5076.5979 | 306.6057 | 319.6423 | 342.3944
5077.5979 | 306.8437 | 319.6426 | 342.7151
5078.5979 | 307.3718 | 319.7565 | 343.2591
5079.5979 | 307.2659 | 319.6519 | 343.5311
5080.5979 | 307.2364 | 319.8712 | 343.4802
5081.5979 | 307.6357 | 320.3016 | 343.4367
5082.5979 | 307.5675 | 320.1827 | 343.3522
5083.5979 | 307.5749 | 320.0253 | 343.6017
5084.5979 | 307.3217 | 320.0162 | 343.0351
5085.5979 | 307.2766 | 319.7251 | 342.8942
5086.5979 | 307.0629 | 319.7569 | 343.5717
5087.5979 | 307.0879 | 319.739 | 342.8906
5088.5979 | 307.228 | 319.8052 | 342.9579
5089.5979 | 307.3366 | 319.9663 | 342.8535
5090.5979 | 307.4697 | 319.3064 | 342.8372
5091.5979 | 307.4596 | 319.1719 | 342.719
5092.5979 | 307.6589 | 319.1531 | 343.2823
5093.5979 | 307.4369 | 319.412 | 343.3508
5094.5979 | 307.221 | 319.668 | 342.9325
5095.5979 | 307.1004 | 319.9666 | 341.9364
5096.5979 | 307.0959 | 319.6575 | 341.519
5097.5979 | 307.0192 | 319.5504 | 341.2341
5098.5979 | 307.1218 | 319.3375 | 340.4677
5099.5979 | 307.2504 | 319.114 | 339.8918
5100.5979 | 307.4355 | 319.1222 | 339.4367
5101.5979 | 307.5249 | 319.1198 | 339.1886
5102.5979 | 307.201 | 319.2938 | 338.8587
5103.5979 | 306.9076 | 319.1735 | 338.9537
5104.5979 | 306.833 | 318.9211 | 338.5153
5105.5979 | 306.4073 | 318.8701 | 337.9528
5106.5979 | 306.5428 | 318.8294 | 337.5285
5107.5979 | 307.0467 | 318.6525 | 337.1572
5108.5979 | 307.0889 | 318.4551 | 337.2737
5109.5979 | 306.8457 | 318.5066 | 337.7702
5110.5979 | 305.9852 | 318.5712 | 337.9478
5111.5979 | 305.7877 | 318.6579 | 338.204
5112.5979 | 305.3638 | 318.1557 | 338.2488
5113.5979 | 305.5487 | 318.1035 | 338.1601
5114.5979 | 305.6112 | 318.1342 | 337.8139
5115.5979 | 305.6229 | 317.5082 | 338.8988
5116.5979 | 305.3943 | 317.4242 | 338.8343
5117.5979 | 305.5285 | 317.8771 | 339.1193
5118.5979 | 305.541 | 318.2163 | 339.6331
5119.5979 | 305.3367 | 318.514 | 339.685
5120.5979 | 305.8799 | 318.2497 | 339.6053
5121.5979 | 306.1891 | 317.9059 | 339.9942
5122.5979 | 305.9109 | 318.2079 | 339.7783
5123.5979 | 305.9763 | 318.1742 | 339.0271
5124.5979 | 306.137 | 317.9499 | 339.0796
5125.5979 | 306.2912 | 317.9397 | 338.8158
5126.5979 | 305.7237 | 317.3443 | 338.4822
5127.5979 | 305.5567 | 317.3583 | 337.9688
5128.5979 | 304.7866 | 317.3541 | 337.5489
5129.5979 | 304.2801 | 317.4494 | 336.7562
5130.5979 | 304.3287 | 317.2636 | 336.6373
5131.5979 | 304.341 | 317.0535 | 337.5305
5132.5979 | 304.2928 | 317.4469 | 337.3574
5133.5979 | 304.3359 | 317.1068 | 337.5352
5134.5979 | 304.0925 | 317.0195 | 337.9732
5135.5979 | 304.306 | 316.9156 | 338.0537
5136.5979 | 304.2584 | 316.7294 | 337.9292
5137.5979 | 304.091 | 316.6182 | 337.5891
5138.5979 | 304.1249 | 316.4342 | 337.1318
5139.5979 | 304.2552 | 316.4637 | 336.3622
5140.5979 | 304.3414 | 316.5897 | 335.8996
5141.5979 | 304.1723 | 316.9781 | 335.4605
5142.5979 | 304.2733 | 317.2869 | 335.3149
5143.5979 | 304.3711 | 317.0599 | 335.9004
5144.5979 | 304.1133 | 317.1573 | 335.8368
5145.5979 | 303.9842 | 317.2274 | 335.3349
5146.5979 | 303.7281 | 316.8825 | 334.9599
5147.5979 | 303.9006 | 316.3719 | 334.396
5148.5979 | 303.9545 | 315.8908 | 333.9146
5149.5979 | 304.2236 | 315.6808 | 333.6454
5150.5979 | 303.5541 | 315.7557 | 333.1851
5151.5979 | 303.407 | 315.744 | 333.2859
5152.5979 | 303.2954 | 315.8195 | 333.3902
5153.5979 | 303.0355 | 315.4005 | 332.7355
5154.5979 | 302.9774 | 315.3448 | 332.6071
5155.5979 | 303.0428 | 315.1111 | 332.9141
5156.5979 | 303.3275 | 314.9015 | 332.6572
5157.5979 | 303.0665 | 314.663 | 332.8993
5158.5979 | 302.9889 | 314.4165 | 332.6102
5159.5979 | 302.4136 | 314.1062 | 332.9564
5160.5979 | 302.0184 | 313.9897 | 332.8935
5161.5979 | 301.848 | 313.9429 | 333.1405
5162.5979 | 301.9472 | 313.915 | 332.1878
5163.5979 | 302.2093 | 313.6638 | 330.9498
5164.5979 | 302.3342 | 313.436 | 330.7119
5165.5979 | 302.1943 | 313.3556 | 330.9557
5166.5979 | 302.1857 | 313.4215 | 331.3887
5167.5979 | 302.4621 | 313.3316 | 331.5364
5168.5979 | 302.301 | 313.0995 | 331.1068
5169.5979 | 302.0831 | 313.1697 | 331.1884
5170.5979 | 301.9799 | 312.9608 | 332.0387
5171.5979 | 301.5904 | 312.8357 | 332.4352
5172.5979 | 301.6444 | 312.8036 | 332.7348
5173.5979 | 301.3355 | 312.9754 | 332.7991
5174.5979 | 301.0027 | 312.7508 | 332.5301
5175.5979 | 300.6558 | 312.4973 | 332.0345
5176.5979 | 300.4134 | 312.5337 | 331.4163
5177.5979 | 300.2199 | 312.0907 | 330.6356
5178.5979 | 300.4026 | 311.9353 | 330.6583
5179.5979 | 300.2471 | 311.6731 | 330.6118
5180.5979 | 300.5344 | 311.5439 | 330.7115
5181.5979 | 300.8868 | 311.4877 | 330.7265
5182.5979 | 301.2261 | 311.3962 | 329.9737
5183.5979 | 301.2176 | 311.1174 | 330.0758
5184.5979 | 300.9304 | 311.0799 | 329.8217
5185.5979 | 300.6601 | 311.0866 | 329.9805
5186.5979 | 300.3462 | 311.1261 | 330.377
5187.5979 | 300.2123 | 311.229 | 329.9444
5188.5979 | 300.3545 | 311.1291 | 329.43
5189.5979 | 300.4698 | 311.2188 | 329.1062
5190.5979 | 300.2022 | 311.4763 | 329.0671
5191.5979 | 300.1535 | 311.5866 | 328.8344
5192.5979 | 299.9547 | 311.3083 | 328.9098
5193.5979 | 299.7422 | 311.3992 | 328.481
5194.5979 | 300.1179 | 312.0501 | 328.0949
5195.5979 | 300.0405 | 312.0864 | 328.5505
5196.5979 | 300.1687 | 312.2219 | 328.3399
5197.5979 | 299.9649 | 311.9396 | 327.6929
5198.5979 | 299.7714 | 311.866 | 327.8338
5199.5979 | 299.7621 | 311.7371 | 327.7323
5200.5979 | 300.1357 | 311.637 | 327.2301
5201.5979 | 300.0974 | 311.7337 | 327.3885
5202.5979 | 300.1972 | 312.0145 | 327.6209
5203.5979 | 300.2752 | 311.7784 | 327.3291
5204.5979 | 300.0908 | 311.6031 | 327.8764
5205.5979 | 300.0417 | 311.6181 | 327.9185
5206.5979 | 300.1691 | 311.241 | 328.1832
5207.5979 | 300.0353 | 311.199 | 327.3779
5208.5979 | 299.8701 | 311.4664 | 327.5478
5209.5979 | 299.6237 | 311.0388 | 328.1057
5210.5979 | 299.6418 | 310.9169 | 328.1794
5211.5979 | 299.5354 | 310.7489 | 328.4048
5212.5979 | 299.4915 | 310.591 | 328.3459
5213.5979 | 299.2694 | 310.0777 | 328.2899
5214.5979 | 298.8511 | 309.9221 | 328.2931
5215.5979 | 298.9183 | 309.5998 | 328.2008
5216.5979 | 298.7174 | 309.5578 | 327.7286
5217.5979 | 298.8309 | 309.5092 | 327.3444
5218.5979 | 298.8713 | 309.1237 | 327.7639
5219.5979 | 298.9974 | 309.0646 | 327.3725
5220.5979 | 299.1652 | 308.9741 | 327.0247
5221.5979 | 299.4575 | 308.6703 | 327.2554
5222.5979 | 299.4205 | 308.8379 | 326.8168
5223.5979 | 299.554 | 308.752 | 326.679
5224.5979 | 299.3393 | 308.5549 | 326.2035
5225.5979 | 299.042 | 308.5557 | 326.0542
5226.5979 | 299.3128 | 308.5597 | 325.9315
5227.5979 | 299.3273 | 308.5474 | 325.6813
5228.5979 | 298.9857 | 308.7686 | 325.7069
5229.5979 | 298.9244 | 308.481 | 325.4397
5230.5979 | 298.7614 | 308.1987 | 325.4526
5231.5979 | 298.5964 | 308.4197 | 325.553
5232.5979 | 298.5078 | 308.9821 | 325.2228
5233.5979 | 298.6217 | 308.8423 | 325.1295
5234.5979 | 298.4901 | 308.7807 | 325.78
5235.5979 | 298.6681 | 308.9283 | 325.9757
5236.5979 | 298.7482 | 308.9561 | 326.5545
5237.5979 | 298.8087 | 308.5966 | 326.3287
5238.5979 | 298.8328 | 308.2731 | 327.2572
5239.5979 | 298.6812 | 308.0432 | 327.5015
5240.5979 | 298.754 | 307.8362 | 327.2071
5241.5979 | 298.9066 | 307.5408 | 326.8488
5242.5979 | 299.0125 | 307.5294 | 326.8614
5243.5979 | 298.8027 | 307.6268 | 326.0643
5244.5979 | 299.0585 | 307.758 | 325.6626
5245.5979 | 298.8304 | 308.0396 | 324.4634
5246.5979 | 298.6086 | 308.0784 | 324.678
5247.5979 | 298.7696 | 308.4106 | 324.5372
5248.5979 | 298.478 | 308.7845 | 324.6881
5249.5979 | 298.4493 | 309.0392 | 324.5542
5250.5979 | 298.1637 | 309.2394 | 324.7081
5251.5979 | 298.1699 | 309.0536 | 324.3131
5252.5979 | 298.0468 | 308.5722 | 324.5635
5253.5979 | 297.8088 | 308.1716 | 324.1729
5254.5979 | 297.7875 | 308.0664 | 324.1622
5255.5979 | 297.8311 | 308.4213 | 324.1519
5256.5979 | 298.2003 | 308.6903 | 324.1224
5257.5979 | 298.02 | 309.0969 | 324.2978
5258.5979 | 298.0275 | 309.1004 | 324.2732
5259.5979 | 298.0301 | 309.193 | 324.2434
5260.5979 | 298.2021 | 308.6494 | 324.3969
5261.5979 | 297.7736 | 308.7859 | 324.5782
5262.5979 | 297.5471 | 308.8221 | 324.6526
5263.5979 | 297.4054 | 308.7346 | 324.4968
5264.5979 | 297.2589 | 309.1266 | 324.4422
5265.5979 | 297.1936 | 309.4062 | 323.8875
5266.5979 | 297.1694 | 309.5245 | 323.9665
5267.5979 | 296.8481 | 309.8604 | 323.1679
5268.5979 | 296.5022 | 309.3661 | 322.8241
5269.5979 | 296.2749 | 308.6478 | 322.5451
5270.5979 | 296.1725 | 308.1102 | 322.5397
5271.5979 | 296.1248 | 308.1992 | 322.3307
5272.5979 | 296.0901 | 308.0345 | 322.6187
5273.5979 | 295.8068 | 307.8561 | 322.1523
5274.5979 | 296.1222 | 307.4517 | 321.9455
5275.5979 | 296.1426 | 307.4279 | 322.2249
5276.5979 | 296.1679 | 306.6905 | 321.9701
5277.5979 | 296.4183 | 306.3151 | 320.7501
5278.5979 | 296.5897 | 306.0235 | 321.1306
5279.5979 | 296.7497 | 305.7805 | 321.9263
5280.5979 | 296.4607 | 305.6354 | 322.4471
5281.5979 | 296.1967 | 305.6386 | 321.624
5282.5979 | 295.773 | 305.6719 | 321.2681
5283.5979 | 295.6385 | 305.5827 | 322.0417
5284.5979 | 295.5529 | 305.7238 | 322.3568
5285.5979 | 295.8922 | 305.6807 | 322.4024
5286.5979 | 295.8892 | 305.5431 | 321.7423
5287.5979 | 295.841 | 305.5266 | 321.192
5288.5979 | 295.559 | 305.4111 | 320.9822
5289.5979 | 295.4399 | 305.0834 | 321.3492
5290.5979 | 294.89 | 304.4666 | 321.4729
5291.5979 | 294.5895 | 304.4506 | 321.4956
5292.5979 | 294.1574 | 304.6703 | 321.822
5293.5979 | 294.1409 | 304.8601 | 321.5575
5294.5979 | 294.3478 | 304.5141 | 321.1644
5295.5979 | 294.1837 | 304.1867 | 321.2482
5296.5979 | 294.1058 | 303.662 | 321.4237
5297.5979 | 294.2774 | 303.2997 | 320.5078
5298.5979 | 294.5379 | 302.5603 | 319.8005
5299.5979 | 294.4874 | 302.3759 | 319.2154
5300.5979 | 294.3702 | 302.2286 | 319.0309
5301.5979 | 294.4363 | 302.2006 | 318.9786
5302.5979 | 294.4591 | 301.9664 | 319.1921
5303.5979 | 294.1217 | 302.0747 | 319.0395
5304.5979 | 294.0495 | 302.2851 | 319.208
5305.5979 | 294.0689 | 302.1975 | 319.1615
5306.5979 | 293.9356 | 302.0742 | 319.1633
5307.5979 | 293.471 | 302.1103 | 319.3368
5308.5979 | 293.4029 | 301.8746 | 319.6404
5309.5979 | 293.4488 | 301.8881 | 319.3966
5310.5979 | 293.5142 | 302.3 | 319.292
5311.5979 | 293.5331 | 302.606 | 319.2986
5312.5979 | 293.347 | 302.9806 | 318.5642
5313.5979 | 293.3136 | 303.1451 | 318.2678
5314.5979 | 293.3985 | 302.6938 | 318.4192
5315.5979 | 293.0296 | 302.7688 | 318.1941
5316.5979 | 292.8467 | 302.5253 | 318.6135
5317.5979 | 293.0513 | 302.6159 | 318.413
5318.5979 | 292.9182 | 302.8973 | 318.009
5319.5979 | 292.4587 | 302.5681 | 317.8947
5320.5979 | 292.5843 | 302.3923 | 317.5365
5321.5979 | 292.2717 | 302.2064 | 317.6441
5322.5979 | 292.0417 | 302.1658 | 318.4809
5323.5979 | 292.1267 | 302.3181 | 319.2022
5324.5979 | 292.1422 | 302.4857 | 319.7759
5325.5979 | 292.3157 | 301.8727 | 319.5524
5326.5979 | 292.3917 | 301.2883 | 319.8816
5327.5979 | 292.331 | 301.0425 | 320.2174
5328.5979 | 292.5505 | 301.2749 | 320.3082
5329.5979 | 292.1569 | 301.7576 | 319.9397
5330.5979 | 292.1254 | 301.7865 | 319.4069
5331.5979 | 291.584 | 301.7004 | 318.8294
5332.5979 | 291.2938 | 301.6753 | 319.1397
5333.5979 | 290.6933 | 301.2713 | 319.0079
5334.5979 | 290.5467 | 301.2442 | 319.3832
5335.5979 | 290.7754 | 300.8806 | 319.982
5336.5979 | 291.0438 | 301.3858 | 320.1717
5337.5979 | 291.0242 | 301.7824 | 319.7056
5338.5979 | 290.8433 | 302.4663 | 318.8895
5339.5979 | 290.7092 | 302.7206 | 318.7667
5340.5979 | 290.8808 | 303.2035 | 318.6956
5341.5979 | 290.895 | 303.2992 | 319.1809
5342.5979 | 291.2944 | 303.1048 | 319.6095
5343.5979 | 291.3203 | 303.2043 | 319.0765
5344.5979 | 291.4455 | 303.0571 | 319.1412
5345.5979 | 291.4365 | 303.0227 | 319.4973
5346.5979 | 291.432 | 303.1782 | 319.2251
5347.5979 | 291.5521 | 303.0461 | 319.1893
5348.5979 | 291.5884 | 303.3947 | 319.2523
5349.5979 | 291.724 | 302.9628 | 318.8531
5350.5979 | 292.0235 | 302.857 | 319.0719
5351.5979 | 292.0228 | 303.051 | 319.0827
5352.5979 | 292.0771 | 302.7397 | 319.3851
5353.5979 | 291.9804 | 302.2905 | 319.3828
5354.5979 | 291.9936 | 302.1104 | 319.043
5355.5979 | 291.8772 | 301.8468 | 318.6421
5356.5979 | 291.5493 | 301.9823 | 318.4438
5357.5979 | 291.3309 | 301.5095 | 318.4322
5358.5979 | 291.0895 | 301.3447 | 318.5325
5359.5979 | 291.0266 | 300.9943 | 319.0464
5360.5979 | 290.7516 | 301.2032 | 318.9256
5361.5979 | 290.6791 | 301.4789 | 318.3019
5362.5979 | 290.4565 | 300.9271 | 317.5957
5363.5979 | 290.3498 | 300.4696 | 317.3186
5364.5979 | 290.1131 | 300.2786 | 317.6735
5365.5979 | 290.1145 | 300.249 | 317.7562
5366.5979 | 290.1851 | 300.1355 | 317.5807
5367.5979 | 290.143 | 300.4807 | 316.7764
5368.5979 | 290.113 | 300.3755 | 316.5412
5369.5979 | 290.2132 | 300.2056 | 316.4102
5370.5979 | 290.0435 | 299.977 | 316.7388
5371.5979 | 290.3254 | 299.8587 | 316.6003
5372.5979 | 290.4141 | 299.6614 | 316.0961
5373.5979 | 290.7955 | 299.4934 | 316.0952
5374.5979 | 290.6218 | 299.4024 | 316.2488
5375.5979 | 290.4561 | 299.5853 | 315.7851
5376.5979 | 290.2339 | 299.7807 | 315.6175
5377.5979 | 290.31 | 299.7435 | 315.8529
5378.5979 | 290.1317 | 300.1053 | 316.4535
5379.5979 | 290.182 | 299.7803 | 315.7477
5380.5979 | 289.4481 | 300.0932 | 315.8055
5381.5979 | 288.9748 | 300.0035 | 315.4125
5382.5979 | 288.8792 | 300.0803 | 315.0611
5383.5979 | 288.5175 | 299.4316 | 315.0441
5384.5979 | 288.1652 | 299.4619 | 315.1687
5385.5979 | 287.8857 | 299.4118 | 315.3964
5386.5979 | 287.8281 | 299.4476 | 315.1856
5387.5979 | 288.1826 | 299.6467 | 315.3822
5388.5979 | 288.2628 | 299.6081 | 315.484
5389.5979 | 288.4422 | 299.9881 | 315.4464
5390.5979 | 288.6112 | 299.8546 | 315.4834
5391.5979 | 288.7158 | 300.019 | 315.528
5392.5979 | 288.2076 | 299.618 | 315.8191
5393.5979 | 287.9258 | 299.4765 | 315.5442
5394.5979 | 288.0198 | 299.5329 | 315.1995
5395.5979 | 288.181 | 299.3219 | 315.0187
5396.5979 | 288.2161 | 299.2282 | 315.371
5397.5979 | 287.8015 | 299.2398 | 314.7627
5398.5979 | 287.9082 | 299.2009 | 314.5977
5399.5979 | 287.9462 | 298.9889 | 315.0888
5400.5979 | 288.2005 | 298.9469 | 315.277
5401.5979 | 288.3121 | 298.6209 | 315.2933
5402.5979 | 287.7762 | 298.2918 | 315.6589
5403.5979 | 287.3937 | 298.0572 | 315.8129
5404.5979 | 287.5871 | 297.5699 | 315.812
5405.5979 | 287.8798 | 297.3245 | 315.4918
5406.5979 | 288.2409 | 296.8477 | 314.9803
5407.5979 | 287.996 | 296.6925 | 314.518
5408.5979 | 287.765 | 296.7305 | 314.6612
5409.5979 | 287.3404 | 296.857 | 313.9206
5410.5979 | 287.314 | 296.9345 | 314.5451
5411.5979 | 287.4184 | 297.2697 | 313.7498
5412.5979 | 287.2483 | 297.4729 | 313.6136
5413.5979 | 286.8736 | 297.328 | 313.0534
5414.5979 | 286.6823 | 297.2774 | 313.2077
5415.5979 | 286.5293 | 297.2896 | 313.2237
5416.5979 | 286.7408 | 297.2445 | 313.3594
5417.5979 | 286.7417 | 297.1359 | 313.6459
5418.5979 | 287.0164 | 296.7865 | 314.0117
5419.5979 | 287.0277 | 296.4878 | 314.0183
5420.5979 | 287.0409 | 296.518 | 314.3738
5421.5979 | 287.0861 | 296.0843 | 314.526
5422.5979 | 286.7952 | 295.757 | 314.1483
5423.5979 | 286.5867 | 295.6644 | 313.9732
5424.5979 | 286.3011 | 295.7525 | 314.0049
5425.5979 | 286.3228 | 295.6856 | 313.6084
5426.5979 | 286.5684 | 295.4368 | 313.4842
5427.5979 | 286.5934 | 295.0235 | 313.0215
5428.5979 | 286.7373 | 294.7801 | 312.8811
5429.5979 | 286.4609 | 294.959 | 312.9467
5430.5979 | 286.5934 | 294.8194 | 312.5812
5431.5979 | 286.5748 | 294.7076 | 312.8786
5432.5979 | 286.7633 | 294.2286 | 312.7687
5433.5979 | 286.7883 | 293.9825 | 312.5365
5434.5979 | 286.5693 | 293.8729 | 312.83
5435.5979 | 285.9443 | 293.7948 | 312.5166
5436.5979 | 285.5833 | 293.8105 | 312.7432
5437.5979 | 285.7261 | 293.8359 | 312.5425
5438.5979 | 285.45 | 293.7757 | 312.0833
5439.5979 | 285.7639 | 293.7159 | 311.4211
5440.5979 | 285.5736 | 294.0448 | 311.0559
5441.5979 | 285.3253 | 294.4251 | 310.8498
5442.5979 | 284.7429 | 294.6094 | 311.4394
5443.5979 | 284.4372 | 294.3237 | 311.2868
5444.5979 | 284.557 | 294.7239 | 311.7752
5445.5979 | 284.8829 | 295.2804 | 311.7624
5446.5979 | 284.8565 | 295.2904 | 311.2358
5447.5979 | 285.0046 | 295.1603 | 311.1062
5448.5979 | 285.0535 | 294.9796 | 311.1418
5449.5979 | 285.0168 | 294.8921 | 310.5824
5450.5979 | 285.0193 | 294.7454 | 310.3166
5451.5979 | 285.0413 | 294.7414 | 310.4402
5452.5979 | 285.0214 | 295.1752 | 310.0299
5453.5979 | 285.181 | 294.617 | 309.9845
5454.5979 | 285.2632 | 294.4766 | 309.4972
5455.5979 | 284.74 | 294.3044 | 309.1961
5456.5979 | 284.4885 | 294.3453 | 309.3752
5457.5979 | 284.3043 | 294.3593 | 309.5568
5458.5979 | 283.9085 | 294.649 | 309.6534
5459.5979 | 284.0378 | 294.7726 | 309.5304
5460.5979 | 283.7688 | 294.9812 | 309.4924
5461.5979 | 283.8808 | 295.1575 | 309.9686
5462.5979 | 284.0822 | 295.5147 | 310.2224
5463.5979 | 284.2272 | 295.4291 | 310.2125
5464.5979 | 284.2916 | 296.1005 | 310.2519
5465.5979 | 284.2933 | 295.7173 | 310.4854
5466.5979 | 284.7106 | 295.6772 | 310.0758
5467.5979 | 284.5826 | 295.3122 | 309.9064
5468.5979 | 284.3684 | 294.7268 | 310.6805
5469.5979 | 284.3005 | 294.7511 | 311.6424
5470.5979 | 284.343 | 294.2728 | 312.1277
5471.5979 | 284.3366 | 293.8609 | 312.0702
5472.5979 | 284.2732 | 293.5433 | 312.0982
5473.5979 | 283.9443 | 293.414 | 311.2667
5474.5979 | 283.9024 | 293.4313 | 311.4237
5475.5979 | 283.6538 | 293.4331 | 311.6467
5476.5979 | 283.1094 | 293.3229 | 312.149
5477.5979 | 283.0151 | 293.7103 | 311.8298
5478.5979 | 283.0892 | 293.4951 | 311.6254
5479.5979 | 282.9926 | 293.4441 | 311.5582
5480.5979 | 282.7296 | 293.418 | 311.2669
5481.5979 | 282.9817 | 293.2393 | 310.5559
5482.5979 | 282.9278 | 293.2191 | 310.2218
5483.5979 | 282.8616 | 293.0241 | 309.8243
5484.5979 | 282.6812 | 292.9456 | 309.2959
5485.5979 | 282.4884 | 292.6147 | 309.4565
5486.5979 | 282.5785 | 292.8135 | 309.9461
5487.5979 | 282.751 | 293.6089 | 309.7448
5488.5979 | 282.7913 | 293.8095 | 309.5613
5489.5979 | 283.0118 | 293.8453 | 308.9989
5490.5979 | 283.6062 | 293.8524 | 309.1854
5491.5979 | 283.3493 | 293.3194 | 309.2619
5492.5979 | 282.6268 | 292.7722 | 310.0806
5493.5979 | 282.3333 | 292.7577 | 310.2604
5494.5979 | 282.1738 | 292.6841 | 310.3549
5495.5979 | 281.8607 | 292.3889 | 310.3151
5496.5979 | 281.813 | 292.2005 | 309.7615
5497.5979 | 281.8955 | 292.2333 | 309.3011
5498.5979 | 281.9898 | 291.8522 | 309.5371
5499.5979 | 281.5015 | 291.4639 | 308.8501
5500.5979 | 281.415 | 291.356 | 308.0824
5501.5979 | 281.512 | 291.3384 | 308.7623
5502.5979 | 281.5861 | 291.3714 | 308.4349
5503.5979 | 281.6448 | 291.6556 | 308.319
5504.5979 | 281.3457 | 291.927 | 307.9237
5505.5979 | 281.0067 | 292.2301 | 308.1513
5506.5979 | 280.6643 | 292.4924 | 308.055
5507.5979 | 280.7545 | 292.7084 | 307.7669
5508.5979 | 281.0392 | 292.6731 | 307.419
5509.5979 | 280.9479 | 292.5725 | 307.0461
5510.5979 | 280.6857 | 292.5458 | 307.0801
5511.5979 | 280.7858 | 292.6661 | 307.0003
5512.5979 | 280.9987 | 292.4089 | 307.291
5513.5979 | 280.7862 | 292.3253 | 307.5406
5514.5979 | 281.0492 | 292.2348 | 307.5032
5515.5979 | 281.0173 | 292.2344 | 307.2098
5516.5979 | 281.1429 | 291.8086 | 306.7836
5517.5979 | 281.0471 | 291.4075 | 306.4788
5518.5979 | 280.9135 | 291.1556 | 307.2602
5519.5979 | 281.0646 | 291.0102 | 307.3372
5520.5979 | 281.1044 | 290.8062 | 306.9116
5521.5979 | 280.7829 | 290.895 | 307.3337
5522.5979 | 280.6556 | 290.6761 | 307.1669
5523.5979 | 280.2953 | 290.518 | 306.6405
5524.5979 | 280.5155 | 290.385 | 306.3105
5525.5979 | 280.2315 | 290.074 | 306.7167
5526.5979 | 279.8097 | 289.6407 | 306.9147
5527.5979 | 279.5502 | 289.6312 | 306.9303
5528.5979 | 279.6224 | 289.1812 | 306.6032
5529.5979 | 279.526 | 289.1644 | 306.9334
5530.5979 | 279.6459 | 289.4304 | 307.1114
5531.5979 | 279.8806 | 289.7383 | 307.1862
5532.5979 | 279.9547 | 289.9475 | 306.624
5533.5979 | 279.4671 | 290.0712 | 306.7215
5534.5979 | 279.2701 | 290.1695 | 306.5486
5535.5979 | 279.4089 | 289.443 | 307.0509
5536.5979 | 279.4477 | 289.4935 | 306.2564
5537.5979 | 279.6809 | 289.336 | 306.3449
5538.5979 | 279.7802 | 289.6689 | 305.3037
5539.5979 | 280.0068 | 289.6567 | 305.2745
5540.5979 | 280.1941 | 289.6626 | 304.706
5541.5979 | 280.2999 | 289.8792 | 304.1061
5542.5979 | 280.5393 | 289.8445 | 304.2495
5543.5979 | 280.3377 | 289.8652 | 304.4969
5544.5979 | 280.5138 | 289.4413 | 304.5983
5545.5979 | 280.5216 | 289.458 | 304.9023
5546.5979 | 280.459 | 289.1085 | 304.8687
5547.5979 | 280.251 | 289.1533 | 305.1182
5548.5979 | 280.1255 | 289.3092 | 305.4152
5549.5979 | 279.6205 | 289.3732 | 305.2398
5550.5979 | 279.2816 | 289.2651 | 304.9958
5551.5979 | 279.0229 | 289.0848 | 304.6538
5552.5979 | 279.1494 | 288.8426 | 304.498
5553.5979 | 278.6545 | 288.738 | 304.4804
5554.5979 | 278.5848 | 288.5155 | 304.7218
5555.5979 | 278.3974 | 288.4034 | 304.5132
5556.5979 | 278.6531 | 288.5671 | 304.7061
5557.5979 | 278.3007 | 288.2579 | 304.7672
5558.5979 | 278.1456 | 288.2531 | 304.5788
5559.5979 | 278.2723 | 288.3701 | 305.0007
5560.5979 | 278.2259 | 288.6423 | 305.4246
5561.5979 | 278.1514 | 288.4778 | 305.4178
5562.5979 | 278.5423 | 288.1769 | 305.6117
5563.5979 | 278.5729 | 288.215 | 304.9714
5564.5979 | 278.3708 | 288.0823 | 304.7827
5565.5979 | 278.4146 | 288.3441 | 304.8306
5566.5979 | 278.0868 | 288.2979 | 304.5812
5567.5979 | 278.0048 | 288.2375 | 305.0129
5568.5979 | 278.243 | 287.9176 | 304.8256
5569.5979 | 278.0961 | 287.9678 | 304.6236
5570.5979 | 278.0131 | 288.298 | 304.5246
5571.5979 | 278.0252 | 288.0865 | 304.7005
5572.5979 | 278.413 | 288.2855 | 304.7484
5573.5979 | 278.6496 | 288.7955 | 304.2038
5574.5979 | 278.7157 | 288.7789 | 304.348
5575.5979 | 278.7929 | 288.7671 | 304.5679
5576.5979 | 278.5338 | 288.9017 | 304.2153
5577.5979 | 278.4355 | 288.8916 | 303.927
5578.5979 | 278.6095 | 288.7557 | 303.5067
5579.5979 | 278.2821 | 288.5976 | 303.3918
5580.5979 | 278.7292 | 288.4561 | 303.2756
5581.5979 | 278.7313 | 288.3467 | 304.0051
5582.5979 | 278.7013 | 288.5336 | 303.5216
5583.5979 | 278.3857 | 288.5737 | 303.9812
5584.5979 | 277.9078 | 288.4206 | 304.1983
5585.5979 | 278.0685 | 288.6899 | 303.8189
5586.5979 | 278.0179 | 288.5799 | 303.6621
5587.5979 | 277.9965 | 288.4293 | 303.9924
5588.5979 | 278.1033 | 288.1629 | 303.1729
5589.5979 | 277.9309 | 288.1397 | 303.2349
5590.5979 | 277.6947 | 288.3924 | 303.4163
5591.5979 | 277.2251 | 288.2866 | 303.4782
5592.5979 | 277.1218 | 287.7969 | 303.8705
5593.5979 | 276.9636 | 287.667 | 304.0494
5594.5979 | 277.0316 | 287.5185 | 303.8321
5595.5979 | 277.4114 | 287.3456 | 303.028
5596.5979 | 277.4544 | 287.3598 | 303.2326
5597.5979 | 277.2301 | 287.2403 | 303.3399
5598.5979 | 277.1798 | 287.309 | 302.9776
5599.5979 | 276.9958 | 287.2817 | 303.0265
5600.5979 | 277.0384 | 287.1239 | 302.4475
5601.5979 | 277.2166 | 286.9902 | 302.0054
5602.5979 | 276.9064 | 286.9947 | 301.662
5603.5979 | 276.8148 | 286.9553 | 302.254
5604.5979 | 276.3398 | 286.5287 | 302.9784
5605.5979 | 276.4845 | 286.1894 | 302.7278
5606.5979 | 276.5277 | 285.5976 | 301.933
5607.5979 | 276.3433 | 285.4524 | 301.9459
5608.5979 | 276.0048 | 285.4825 | 301.4853
5609.5979 | 275.8901 | 285.5278 | 301.5754
5610.5979 | 275.589 | 285.3511 | 301.7254
5611.5979 | 275.3248 | 284.983 | 301.1676
5612.5979 | 275.5529 | 284.7545 | 301.0059
5613.5979 | 275.7623 | 284.6445 | 300.2974
5614.5979 | 275.3067 | 284.4299 | 300.478
5615.5979 | 275.568 | 284.4788 | 300.4689
5616.5979 | 276.0347 | 284.5156 | 300.6587
5617.5979 | 276.1403 | 283.9773 | 300.835
5618.5979 | 275.9589 | 283.4942 | 300.926
5619.5979 | 275.9533 | 283.4012 | 300.4067
5620.5979 | 275.8031 | 283.4469 | 300.3066
5621.5979 | 275.7768 | 283.5963 | 299.7308
5622.5979 | 275.8778 | 283.6763 | 299.9289
5623.5979 | 275.8417 | 283.9457 | 300.8075
5624.5979 | 275.6991 | 283.8038 | 300.7624
5625.5979 | 275.4713 | 283.6131 | 301.1982
5626.5979 | 275.3832 | 283.6449 | 301.0394
5627.5979 | 275.3223 | 283.6145 | 301.0966
5628.5979 | 275.1211 | 283.3515 | 301.2693
5629.5979 | 275.0373 | 283.4499 | 301.5066
5630.5979 | 275.1765 | 283.4061 | 301.0932
5631.5979 | 274.98 | 283.6532 | 300.305
5632.5979 | 274.8897 | 283.4904 | 300.0091
5633.5979 | 275.0092 | 283.2366 | 299.7955
5634.5979 | 274.4805 | 283.2391 | 299.7692
5635.5979 | 274.3583 | 283.3808 | 300.0235
5636.5979 | 274.3349 | 283.106 | 299.7682
5637.5979 | 273.9355 | 283.2251 | 300.0338
5638.5979 | 274.2987 | 283.2479 | 299.9066
5639.5979 | 274.637 | 283.2026 | 300.1814
5640.5979 | 274.5914 | 282.817 | 299.6417
5641.5979 | 274.4312 | 283.1851 | 299.5435
5642.5979 | 274.3587 | 283.4809 | 299.1371
5643.5979 | 274.5398 | 283.5279 | 298.211
5644.5979 | 274.5143 | 283.3072 | 298.1118
5645.6135 | 274.2476 | 282.9777 | 298.5142
5646.5979 | 273.8478 | 282.964 | 299.2115
5647.5979 | 273.7871 | 283.08 | 299.2575
5648.5979 | 274.0356 | 283.1445 | 299.2606
5649.5979 | 274.0578 | 282.927 | 299.2014
5650.5979 | 274.0262 | 283.0875 | 298.0557
5651.5979 | 273.779 | 282.6671 | 298.0016
5652.5979 | 273.588 | 282.7916 | 298.2155
5653.5979 | 273.7209 | 282.626 | 298.5948
5654.5979 | 273.7896 | 282.8183 | 298.8501
5655.5979 | 274.0186 | 282.9492 | 299.7666
5656.5979 | 273.9178 | 283.2713 | 299.746
5657.5979 | 274.1132 | 283.4388 | 299.6419
5658.5979 | 273.8042 | 283.7947 | 299.3188
5659.5979 | 273.6949 | 284.4035 | 299.0203
5660.5979 | 273.7354 | 284.4415 | 298.4272
5661.5979 | 273.6637 | 284.5652 | 298.1448
5662.5979 | 273.551 | 284.1871 | 298.2783
5663.5979 | 273.4714 | 284.3079 | 298.0332
5664.5979 | 273.6038 | 284.4189 | 298.3469
5665.5979 | 273.4559 | 284.8188 | 298.5244
5666.5979 | 273.7092 | 284.7507 | 297.8222
5667.5979 | 273.8119 | 284.7709 | 297.8982
5668.5979 | 273.9716 | 284.4233 | 297.5105
5669.5979 | 274.2912 | 284.3523 | 296.5866
5670.5979 | 274.1481 | 283.8802 | 296.7524
5671.5979 | 273.7285 | 283.4031 | 296.8404
5672.5979 | 273.7758 | 283.5073 | 296.7198
5673.5979 | 273.5741 | 283.3145 | 296.4285
5674.5979 | 273.3404 | 283.2119 | 296.3503
5675.5979 | 272.9893 | 283.1185 | 296.5051
5676.6135 | 272.9422 | 283.1207 | 296.4928
5677.5979 | 272.9421 | 283.1981 | 296.3456
5678.5979 | 272.5511 | 283.4369 | 295.9041
5679.5979 | 272.0134 | 283.797 | 295.194
5680.5979 | 271.9779 | 283.5724 | 295.314
5681.5979 | 271.684 | 283.1476 | 295.3059
5682.5979 | 271.4662 | 282.7414 | 295.3803
5683.5979 | 271.3367 | 282.6719 | 295.2209
5684.5979 | 271.2564 | 282.5441 | 295.125
5685.5979 | 270.6035 | 282.129 | 293.9869
5686.5979 | 270.4101 | 282.106 | 294.7693
5687.5979 | 270.4648 | 281.7362 | 294.8126
5688.5979 | 270.2553 | 281.6834 | 294.9253
5689.5979 | 270.142 | 281.7524 | 295.0016
5690.5979 | 270.0137 | 281.4358 | 295.0205
5691.5979 | 269.9736 | 281.4596 | 294.3083
5692.5979 | 269.7555 | 281.5889 | 294.9208
5693.5979 | 269.6717 | 281.3474 | 295.3299
5694.5979 | 269.5563 | 281.1418 | 294.8644
5695.5979 | 269.3876 | 280.9911 | 294.3655
5696.5979 | 269.5072 | 281.1302 | 295.0625
5697.5979 | 269.4858 | 281.1404 | 295.7528
5698.5979 | 269.9435 | 281.2256 | 295.5725
5699.5979 | 269.8331 | 281.2906 | 295.3547
5700.5979 | 269.7584 | 280.838 | 294.5521
5701.5979 | 269.4425 | 281.0064 | 295.1254
5702.5979 | 269.3977 | 280.7458 | 295.1326
5703.5979 | 269.5693 | 280.9197 | 295.2416
5704.5979 | 269.5074 | 280.7292 | 295.5747
5705.5979 | 269.2388 | 280.7226 | 295.5954
5706.5979 | 269.0471 | 280.3718 | 295.7389
5707.5979 | 268.9121 | 280.3737 | 296.0715
5708.5979 | 269.0021 | 280.031 | 295.7793
5709.5979 | 268.8662 | 279.7125 | 296.0552
5710.5979 | 269.025 | 279.9978 | 295.5858
5711.5979 | 269.1368 | 279.6083 | 295.2007
5712.5979 | 269.1551 | 279.7453 | 294.6374
5713.5979 | 269.1004 | 279.5327 | 294.7791
5714.5979 | 269.3084 | 279.7856 | 294.5364
5715.5979 | 269.5293 | 280.1518 | 295.0094
5716.5979 | 269.6303 | 279.797 | 295.1597
5717.5979 | 269.6847 | 279.7286 | 295.0716
5718.5979 | 269.6195 | 279.9672 | 294.9163
5719.5979 | 269.7454 | 279.9019 | 294.9581
5720.5979 | 269.8419 | 279.8291 | 295.324
5721.5979 | 269.822 | 279.9288 | 295.6874
5722.5979 | 269.8727 | 279.9075 | 295.864
5723.5979 | 270.2761 | 279.9523 | 296.0849
5724.5979 | 270.3954 | 280.0776 | 295.774
5725.5979 | 270.113 | 279.9204 | 295.3409
5726.5979 | 270.2718 | 279.6151 | 295.8294
5727.5979 | 270.2781 | 279.1871 | 296.4201
5728.5979 | 270.1711 | 278.9482 | 295.8236
5729.5979 | 270.0703 | 279.1994 | 295.3961
5730.5979 | 270.3403 | 278.8638 | 295.1164
5731.5979 | 270.6027 | 278.8127 | 294.7449
5732.5979 | 270.4846 | 279.0377 | 294.2228
5733.5979 | 270.0798 | 278.9625 | 294.2778
5734.5979 | 270.3424 | 278.7655 | 294.0699
5735.5979 | 270.1406 | 278.7787 | 293.7617
5736.5979 | 270.0933 | 278.7869 | 293.8421
5737.5979 | 270.1905 | 278.6828 | 293.756
5738.5979 | 270.1925 | 278.7868 | 293.7161
5739.5979 | 270.5004 | 278.8933 | 293.4049
5740.5979 | 270.4896 | 278.9088 | 293.3497
5741.5979 | 270.4301 | 278.7332 | 293.7725
5742.5979 | 270.344 | 278.83 | 293.2884
5743.5979 | 270.4255 | 278.8245 | 293.229
5744.5979 | 270.6183 | 278.4748 | 293.2021
5745.5979 | 270.3833 | 278.5287 | 293.423
5746.5979 | 270.0903 | 278.5672 | 293.0047
5747.5979 | 269.7557 | 278.5236 | 293.6258
5748.5979 | 270.1433 | 278.4041 | 294.1675
5749.5979 | 270.085 | 278.3253 | 294.1285
5750.5979 | 270.0906 | 278.0498 | 294.2602
5751.5979 | 269.5829 | 278.262 | 294.4138
5752.5979 | 269.8476 | 278.5139 | 294.1395
5753.5979 | 269.3637 | 278.3762 | 293.6427
5754.5979 | 269.5812 | 278.2359 | 292.932
5755.5979 | 269.5861 | 278.083 | 293.4721
5756.5979 | 269.2445 | 277.9701 | 292.9966
5757.5979 | 269.2405 | 277.8521 | 293.2234
5758.5979 | 269.4006 | 277.7614 | 293.0702
5759.5979 | 269.87 | 277.5446 | 293.4489
5760.5979 | 269.6449 | 277.5397 | 292.8879
5761.5979 | 269.3115 | 277.4327 | 292.7635
5762.5979 | 268.8348 | 277.2478 | 292.7542
5763.5979 | 268.4603 | 277.4549 | 292.8134
5764.5979 | 268.3831 | 277.2084 | 292.4743
5765.5979 | 268.3663 | 276.7884 | 292.7078
5766.5979 | 268.3292 | 276.8963 | 292.8489
5767.5979 | 267.9871 | 276.7802 | 292.6102
5768.5979 | 268.0654 | 276.6592 | 292.6739
5769.5979 | 267.8292 | 276.4619 | 292.7288
5770.5979 | 268.0163 | 276.4365 | 293.2933
5771.5979 | 267.9998 | 276.5193 | 293.7478
5772.5979 | 268.1423 | 276.3176 | 294.2129
5773.5979 | 268.1245 | 276.1619 | 293.8598
5774.5979 | 268.0217 | 275.9881 | 294.2292
5775.5979 | 268.2249 | 275.9366 | 293.9661
5776.5979 | 268.3919 | 275.9712 | 294.8288
5777.5979 | 268.0658 | 275.596 | 295.063
5778.5979 | 268.0636 | 275.4691 | 295.0411
5779.5979 | 267.9851 | 275.7863 | 295.025
5780.5979 | 268.1626 | 275.7497 | 294.7238
5781.5979 | 268.1412 | 275.9302 | 295.0205
5782.5979 | 267.9383 | 275.7672 | 294.5778
5783.5979 | 268.0053 | 275.9883 | 295.0149
5784.5979 | 267.8298 | 275.4132 | 295.0916
5785.5979 | 267.2939 | 275.3773 | 294.906
5786.5979 | 267.1668 | 275.3173 | 294.5278
5787.5979 | 267.1752 | 275.3076 | 294.4396
5788.5979 | 266.9699 | 275.6642 | 294.0957
5789.5979 | 267.0168 | 275.8688 | 293.9328
5790.5979 | 267.0864 | 275.64 | 293.535
5791.5979 | 267.1082 | 275.6045 | 292.7261
5792.5979 | 266.8457 | 275.6077 | 292.4393
5793.5979 | 266.777 | 275.3522 | 292.9402
5794.5979 | 266.6567 | 275.2656 | 293.116
5795.5979 | 266.4578 | 275.2918 | 292.9881
5796.5979 | 266.3411 | 275.3065 | 292.7198
5797.5979 | 266.243 | 275.3294 | 292.032
5798.5979 | 266.5952 | 275.2403 | 291.8714
5799.5979 | 266.4584 | 275.3916 | 292.3645
5800.5979 | 266.4085 | 275.0214 | 293.0044
5801.5979 | 266.2845 | 275.0868 | 292.3826
5802.5979 | 266.227 | 274.3965 | 291.6917
5803.5979 | 266.0459 | 274.0232 | 291.3806
5804.5979 | 266.1608 | 274.069 | 291.1034
5805.5979 | 266.2587 | 274.1456 | 291.6797
5806.5979 | 266.1656 | 274.0484 | 291.3113
5807.5979 | 266.3593 | 273.9898 | 290.773
5808.5979 | 266.1927 | 274.0475 | 290.6814
5809.5979 | 265.8802 | 273.9999 | 290.3881
5810.5979 | 265.5216 | 273.932 | 289.8007
5811.5979 | 265.4904 | 274.2893 | 289.0095
5812.5979 | 265.7196 | 274.5457 | 288.7199
5813.5979 | 265.9576 | 274.3185 | 289.3481
5814.5979 | 265.7451 | 273.941 | 289.4084
5815.5979 | 265.7747 | 273.9396 | 289.424
5816.5979 | 265.4462 | 273.9423 | 289.8052
5817.5979 | 265.5884 | 273.8954 | 289.7208
5818.5979 | 265.5823 | 273.6717 | 290.3458
5819.5979 | 265.7702 | 273.8056 | 289.5244
5820.5979 | 265.9381 | 273.8227 | 288.6958
5821.5979 | 265.9476 | 273.8205 | 289.0944
5822.5979 | 266.1188 | 273.9287 | 289.0369
5823.5979 | 265.9875 | 273.9256 | 289.2028
5824.5979 | 265.6318 | 273.8653 | 288.3464
5825.5979 | 265.8803 | 273.9687 | 287.6133
5826.5979 | 265.7123 | 273.8059 | 288.0054
5827.5979 | 265.7678 | 273.6275 | 287.8051
5828.5979 | 265.6987 | 273.4893 | 287.5975
5829.5979 | 265.2968 | 273.2234 | 288.1247
5830.5979 | 265.0223 | 272.8855 | 288.5508
5831.5979 | 264.4557 | 272.7317 | 289.3314
5832.5979 | 264.5423 | 272.8119 | 289.4333
5833.5979 | 264.6586 | 272.6123 | 289.1999
5834.5979 | 265 | 272.2626 | 288.9415
5835.5979 | 264.7653 | 272.3903 | 289.0871
5836.5979 | 264.9725 | 272.3748 | 288.7418
5837.5979 | 265.1038 | 272.2779 | 288.3113
5838.5979 | 265.1038 | 272.0758 | 287.5534
5839.5979 | 264.8225 | 271.9623 | 287.3973
5840.5979 | 264.0874 | 271.9983 | 287.0211
5841.5979 | 263.5295 | 271.9386 | 287.0394
5842.5979 | 263.5626 | 271.8126 | 287.7422
5843.5979 | 263.7313 | 271.8822 | 287.1348
5844.5979 | 263.4349 | 271.7529 | 286.7974
5845.5979 | 263.4423 | 271.899 | 286.9369
5846.5979 | 263.4923 | 271.9513 | 286.7357
5847.5979 | 263.229 | 271.8761 | 286.9874
5848.5979 | 263.309 | 271.9879 | 287.4101
5849.5979 | 263.1751 | 272.3803 | 287.2061
5850.5979 | 262.9561 | 272.1984 | 287.2177
5851.5979 | 262.9504 | 271.8384 | 287.5638
5852.5979 | 262.3827 | 271.8496 | 287.6678
5853.5979 | 262.147 | 271.9519 | 288.2523
5854.5979 | 262.5018 | 271.7714 | 288.1192
5855.5979 | 262.485 | 271.4658 | 288.0194
5856.6135 | 262.5932 | 271.5409 | 288.5886
5857.5979 | 262.685 | 271.5488 | 288.6966
5858.5979 | 262.7315 | 271.7565 | 288.4549
5859.5979 | 262.8264 | 271.835 | 288.3313
5860.5979 | 263.0465 | 271.7027 | 288.8648
5861.5979 | 262.9965 | 271.6601 | 289.1304
5862.5979 | 262.9025 | 271.3672 | 288.4664
5863.5979 | 263.0586 | 271.3689 | 287.9021
5864.5979 | 263.3486 | 271.585 | 286.9045
5865.5979 | 263.2566 | 271.045 | 286.5118
5866.5979 | 263.2151 | 271.1236 | 286.3782
5867.5979 | 262.9344 | 270.8972 | 286.0408
5868.5979 | 263.1152 | 270.7923 | 285.5234
5869.5979 | 262.9559 | 270.8338 | 285.3915
5870.5979 | 263.1823 | 270.6213 | 285.6895
5871.5979 | 263.1201 | 270.5643 | 285.7871
5872.5979 | 263.2238 | 270.8215 | 285.6252
5873.5979 | 263.1075 | 270.6587 | 285.5662
5874.5979 | 263.3235 | 270.6463 | 285.6556
5875.5979 | 263.3198 | 270.5807 | 285.9461
5876.5979 | 263.6254 | 270.6954 | 285.5914
5877.5979 | 263.5763 | 270.8815 | 284.8478
5878.5979 | 263.3476 | 270.5388 | 284.7318
5879.5979 | 263.0764 | 270.5826 | 284.921
5880.5979 | 262.8654 | 270.5574 | 285.5697
5881.5979 | 262.7891 | 270.5023 | 286.0217
5882.5979 | 262.7674 | 270.6825 | 286.4726
5883.5979 | 262.7821 | 271.0676 | 286.3591
5884.5979 | 263.0975 | 271.1708 | 286.4457
5885.5979 | 262.677 | 271.095 | 286.7948
5886.5979 | 262.1668 | 270.7604 | 287.1581
5887.5979 | 262.4375 | 270.6499 | 287.2811
5888.5979 | 261.821 | 270.3088 | 287.7104
5889.5979 | 261.6412 | 270.1525 | 287.9363
5890.5979 | 261.8507 | 269.8172 | 288.0523
5891.5979 | 261.4908 | 269.7313 | 287.6616
5892.5979 | 261.6461 | 269.6888 | 287.7256
5893.5979 | 261.5314 | 269.8345 | 286.8903
5894.5979 | 261.6355 | 269.9061 | 285.9996
5895.5979 | 261.6971 | 269.6284 | 284.9179
5896.5979 | 261.8079 | 269.534 | 284.6133
5897.5979 | 261.7861 | 269.2076 | 284.812
5898.5979 | 261.7251 | 269.0689 | 284.956
5899.5979 | 261.6633 | 268.9315 | 283.8879
5900.5979 | 261.4704 | 269.0596 | 283.7153
5901.5979 | 261.2179 | 268.6311 | 283.3647
5902.5979 | 260.8606 | 268.7586 | 282.9497
5903.5979 | 260.2603 | 268.4668 | 282.405
5904.5979 | 259.9934 | 268.8341 | 282.4454
5905.5979 | 259.9537 | 269.1591 | 282.5567
5906.5979 | 259.8206 | 268.9839 | 282.3385
5907.5979 | 259.9667 | 269.1256 | 281.8895
5908.5979 | 260.2513 | 269.3943 | 282.3152
5909.5979 | 260.6453 | 269.405 | 282.5694
5910.5979 | 260.9182 | 269.1888 | 282.5753
5911.5979 | 260.6677 | 269.24 | 283.0048
5912.5979 | 260.8989 | 269.0929 | 283.3073
5913.5979 | 260.6236 | 268.9572 | 283.5418
5914.5979 | 260.15 | 268.9698 | 283.7886
5915.5979 | 259.9538 | 268.5891 | 284.034
5916.5979 | 260.4367 | 268.371 | 284.3599
5917.5979 | 260.7809 | 268.3932 | 284.4585
5918.5979 | 260.355 | 268.1892 | 284.4186
5919.5979 | 260.1757 | 268.308 | 284.4118
5920.5979 | 260.1308 | 268.1711 | 284.3454
5921.5979 | 260.2966 | 267.9039 | 284.9229
5922.5979 | 260.757 | 268.0511 | 285.2498
5923.5979 | 261.0041 | 268.1409 | 285.5378
5924.5979 | 260.8657 | 268.5292 | 285.3306
5925.5979 | 260.678 | 268.7073 | 285.1575
5926.5979 | 260.492 | 268.4242 | 285.1294
5927.5979 | 260.2422 | 268.3569 | 285.2699
5928.5979 | 260.5051 | 268.488 | 285.0733
5929.5979 | 260.5657 | 268.7199 | 284.578
5930.5979 | 260.3422 | 268.5176 | 284.7384
5931.5979 | 260.0951 | 268.5715 | 284.0113
5932.5979 | 260.3923 | 268.6535 | 284.1964
5933.5979 | 260.249 | 268.6868 | 284.3548
5934.5979 | 260.1278 | 268.2855 | 284.1329
5935.5979 | 260.0799 | 267.9337 | 283.9976
5936.5979 | 260.0257 | 267.715 | 284.0573
5937.5979 | 260.13 | 267.5417 | 284.1307
5938.5979 | 260.1317 | 267.4605 | 284.1169
5939.5979 | 260.2067 | 267.058 | 283.6299
5940.5979 | 260.6747 | 266.8311 | 283.3902
5941.5979 | 260.8474 | 266.5164 | 283.7294
5942.5979 | 260.6115 | 266.2317 | 283.6632
5943.5979 | 260.5363 | 265.9151 | 283.7233
5944.5979 | 260.1642 | 265.6689 | 282.6169
5945.5979 | 259.8907 | 265.8104 | 283.1054
5946.6135 | 259.978 | 266.1889 | 282.6799
5947.5979 | 259.7985 | 266.1747 | 282.7813
5948.5979 | 259.7183 | 266.2194 | 282.7255
5949.5979 | 259.5228 | 266.0057 | 282.7522
5950.5979 | 259.4663 | 265.6591 | 282.8397
5951.5979 | 259.6198 | 265.5363 | 282.4811
5952.5979 | 259.5386 | 265.5772 | 282.9263
5953.5979 | 259.5583 | 265.2177 | 283.1966
5954.5979 | 259.4208 | 264.9016 | 282.8689
5955.5979 | 259.6859 | 265.1494 | 282.4354
5956.5979 | 259.8512 | 265.1624 | 282.623
5957.5979 | 259.7353 | 265.3001 | 283.357
5958.5979 | 259.641 | 265.6588 | 283.6127
5959.5979 | 259.789 | 265.5161 | 283.7647
5960.5979 | 259.6497 | 266.0444 | 283.126
5961.5979 | 259.5204 | 266.3506 | 283.255
5962.5979 | 259.2534 | 266.1976 | 282.7256
5963.5979 | 259.2326 | 266.6402 | 281.4891
5964.5979 | 259.2559 | 266.8518 | 281.9034
5965.5979 | 259.0253 | 266.6851 | 281.9978
5966.5979 | 259.0454 | 266.4017 | 281.9171
5967.5979 | 259.1216 | 266.3516 | 281.9356
5968.5979 | 259.2134 | 266.2042 | 281.8416
5969.5979 | 259.1204 | 265.8519 | 281.5495
5970.5979 | 259.1508 | 265.6414 | 281.3445
5971.5979 | 259.2508 | 265.5936 | 281.4132
5972.5979 | 259.1302 | 265.669 | 281.2303
5973.5979 | 258.8547 | 266.0239 | 281.3016
5974.5979 | 258.5812 | 265.6001 | 281.6898
5975.5979 | 258.5518 | 265.1179 | 281.9561
5976.5979 | 258.5132 | 265.0295 | 282.2052
5977.5979 | 258.2516 | 264.998 | 282.022
5978.5979 | 258.077 | 265.1211 | 282.0713
5979.5979 | 257.6722 | 265.2364 | 281.5996
5980.5979 | 257.6731 | 265.5461 | 280.9317
5981.5979 | 257.5361 | 265.5384 | 280.5024
5982.5979 | 257.677 | 265.2251 | 280.8485
5983.5979 | 257.7442 | 265.1903 | 280.8771
5984.5979 | 257.506 | 265.2689 | 281.1068
5985.5979 | 257.3664 | 265.128 | 281.0397
5986.5979 | 257.4312 | 265.1937 | 281.258
5987.5979 | 257.4479 | 265.4964 | 281.2968
5988.5979 | 257.3122 | 264.7808 | 281.4428
5989.5979 | 256.9734 | 264.548 | 281.2801
5990.5979 | 256.5593 | 264.858 | 281.5589
5991.5979 | 256.6568 | 265.2749 | 281.5952
5992.5979 | 256.2351 | 265.3256 | 281.3268
5993.5979 | 255.8914 | 265.3282 | 280.6686
5994.5979 | 256.0513 | 265.4492 | 280.1394
5995.5979 | 256.4203 | 265.458 | 280.3897
5996.5979 | 256.4545 | 265.058 | 280.929
5997.5979 | 256.4546 | 265.0606 | 280.9689
5998.5979 | 256.0463 | 265.0448 | 281.0622
5999.5979 | 255.6717 | 265.1377 | 280.5678
6000.5979 | 255.7978 | 264.829 | 280.4232
6001.5979 | 255.7573 | 264.8059 | 280.8413
6002.5979 | 255.4807 | 264.5464 | 280.4705
6003.5979 | 255.743 | 264.5675 | 280.227
6004.5979 | 255.7024 | 264.7686 | 280.8184
6005.5979 | 255.8641 | 264.8794 | 281.1928
6006.5979 | 255.9605 | 264.7487 | 281.1098
6007.5979 | 255.9887 | 264.7546 | 280.4688
6008.5979 | 255.8947 | 265.3888 | 279.9183
6009.5979 | 255.7259 | 265.4756 | 280.3423
6010.5979 | 255.693 | 265.2889 | 279.8123
6011.5979 | 255.5375 | 265.2807 | 279.5672
6012.5979 | 255.5332 | 265.0421 | 278.7022
6013.5979 | 255.3712 | 264.7392 | 278.3592
6014.5979 | 255.5429 | 264.711 | 278.75
6015.5979 | 255.6737 | 264.5821 | 279.2034
6016.5979 | 255.6909 | 264.5039 | 279.362
6017.5979 | 255.7209 | 264.9709 | 279.1473
6018.5979 | 255.7362 | 265.2252 | 279.2493
6019.5979 | 255.7659 | 264.9145 | 278.5984
6020.5979 | 255.8047 | 264.667 | 278.2202
6021.5979 | 256.0515 | 264.6356 | 278.32
6022.5979 | 256.0868 | 264.5058 | 277.3422
6023.5979 | 256.042 | 264.4942 | 277.3203
6024.5979 | 256.0967 | 264.5986 | 277.5489
6025.5979 | 256.3643 | 264.5334 | 277.1145
6026.5979 | 256.6578 | 264.486 | 276.9189
6027.5979 | 256.6072 | 264.627 | 276.8275
6028.5979 | 256.7161 | 264.9047 | 277.1455
6029.5979 | 256.7554 | 264.5065 | 276.9982
6030.5979 | 256.7419 | 264.2824 | 276.5751
6031.5979 | 256.7658 | 264.081 | 276.1101
6032.5979 | 256.8426 | 263.6187 | 275.9747
6033.5979 | 256.494 | 263.3444 | 276.5244
6034.5979 | 256.1999 | 262.9842 | 276.9933
6035.5979 | 256.1736 | 263.4778 | 276.8107
6036.5979 | 256.2116 | 263.3187 | 277.0314
6037.5979 | 256.2348 | 263.4157 | 277.4539
6038.5979 | 256.2136 | 263.7657 | 276.8717
6039.5979 | 256.1958 | 264.1041 | 276.2416
6040.5979 | 256.3684 | 263.674 | 276.4533
6041.5979 | 256.3422 | 263.4934 | 276.2311
6042.5979 | 256.0799 | 263.2564 | 276.0126
6043.5979 | 256.1342 | 263.2369 | 276.2945
6044.5979 | 256.2112 | 263.1641 | 276.3603
6045.5979 | 256.0305 | 262.9562 | 276.1369
6046.5979 | 255.8707 | 263.0381 | 276.768
6047.5979 | 255.8894 | 263.1358 | 277.0576
6048.5979 | 255.7986 | 263.3877 | 277.1754
6049.5979 | 255.5133 | 263.2732 | 276.8919
6050.5979 | 255.2511 | 263.1344 | 276.9702
6051.5979 | 255.2761 | 262.9755 | 276.809
6052.5979 | 255.3414 | 262.8682 | 277.1094
6053.5979 | 255.6103 | 263.0846 | 276.8607
6054.5979 | 255.6421 | 263.1356 | 277.0771
6055.5979 | 255.7494 | 263.2132 | 277.0821
6056.5979 | 255.6668 | 263.1922 | 276.9745
6057.5979 | 255.7271 | 263.715 | 276.8075
6058.5979 | 255.575 | 263.7724 | 276.7366
6059.5979 | 255.5873 | 264.0117 | 276.8109
6060.5979 | 255.4398 | 263.9571 | 276.6054