## Test Conditions
DESIREE-FIRE Intermediate Scale Test Number 2 - Circuit Simulator Data Only
Test Date: | 2009-12-02
DCSim DAQ Start Time | 12:25
DCSim Time for Synchronization | 12:27
Heat Source Synchronization | 0:01 | hour:minutes:seconds
Heat Source DAQ Start Time | 12:26
Fire Time | 13:59
Offset | 1:34 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 5640 | seconds
Heat Source Offset | 1:33 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 5605 | seconds
Heat Source Stop Time | 15:40
Test Duration | 1:41 | hour:minutes:seconds
| 6060 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 2, 3, and 4 represents the air temperature 3', 5', and 7' down the cable tray located in C-Position. These are labeled as "C-Position - 3'", "C-Position - Middle", " C-Position - 7'", respectively.
MOV 2 | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 0 which is defined as "A Position - Middle" in the Temperature Data File respresents the temperature in the center of the cable tray.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-0.85938 | 121.7651 | -61.528 | 60.1135 | -0.0045011 | 0.0014056 | 0.057059 | 0.057715 | 0.00015814 | -0.0053576 | 0.0001816 | -0.0084228 | 0.0022367 | 0.066561 | 0.064189 | -0.0071051 | 0.019265 | -0.0049069 | -0.027466 | 60.0082 | -61.5692 | 60.1318 | -61.3312 | -61.7569 | -61.7844 | 0.018311 | 59.9762 | -61.6013 | 60.0769 | -61.4914 | -61.6287 | -61.7249 | -0.041199 | -0.10529 | 0.018311 | 0.19684 | -0.25635 | -0.22888 | -0.21515 | -0.18768 | -0.073242 | -0.13733 | -0.036621 | 0.036621 | -0.19684 | -0.10071 | -0.1236 | -0.027466 | 0.23804 | 121.7011 | 0.10986 | 121.6782 | 121.5775 | 121.5775 | 121.5363 | 121.5042 | -121.6827 | -121.7148 | 121.6599 | 121.6049 | 61.5005 | 61.5463
0.875 | 121.7743 | -61.5372 | 60.1089 | -0.0045011 | 0.00012398 | 0.057059 | 0.054937 | -0.0062507 | -0.0045032 | 0.001677 | -0.005371 | 0.0030911 | 0.063784 | 0.060131 | -0.0079597 | 0.020333 | -0.0023435 | 0.018311 | 59.9579 | -61.5372 | 60.1547 | -61.29 | -61.7386 | -61.7615 | 0.036621 | 59.9579 | -61.5692 | 60.0723 | -61.4868 | -61.6104 | -61.7386 | 0 | -0.15106 | 0.045776 | 0.24719 | -0.2243 | -0.20142 | -0.2243 | -0.20142 | -0.032044 | -0.15106 | -0.036621 | 0.050354 | -0.20142 | -0.073243 | -0.16937 | -0.041199 | 0.24719 | 121.6919 | 0.082398 | 121.6415 | 121.4951 | 121.5271 | 121.4951 | 121.4951 | -121.6461 | -121.6782 | 121.6919 | 121.6095 | 61.5555 | 61.5738
2.5469 | 121.7606 | -61.6058 | 60.0311 | 0.0031279 | 0.001192 | 0.058768 | 0.058569 | 0.0040033 | -0.0062122 | 0.0014634 | -0.005371 | 0.0048001 | 0.070833 | 0.061626 | -0.0071051 | 0.021614 | -0.0061887 | -0.09613 | 59.9304 | -61.6333 | 60.0174 | -61.4594 | -61.9034 | -61.908 | -0.091553 | 59.8801 | -61.6791 | 60.0082 | -61.5967 | -61.7523 | -61.7935 | -0.027466 | -0.10071 | -0.013733 | 0.14648 | -0.30212 | -0.29755 | -0.27466 | -0.27008 | -0.073242 | -0.15106 | -0.022888 | 0.009155 | -0.18768 | -0.14648 | -0.11444 | -0.073242 | 0.17395 | 121.6507 | 0.082397 | 121.6873 | 121.5637 | 121.5591 | 121.5363 | 121.4859 | -121.6644 | -121.7102 | 121.6232 | 121.6141 | 61.5097 | 61.5143
4.2812 | 121.8613 | -61.5509 | 60.0174 | -0.012131 | 0.0039692 | 0.058554 | 0.055578 | 0.0012261 | -0.0062122 | -0.0030228 | -0.005371 | 0.00010048 | 0.06592 | 0.062694 | -0.0079597 | 0.019692 | -0.0031979 | -0.064087 | 59.8709 | -61.5555 | 60.141 | -61.2808 | -61.7706 | -61.7615 | 0.041199 | 59.8251 | -61.6196 | 60.1089 | -61.4914 | -61.6104 | -61.6882 | -0.004578 | -0.14648 | 0.1236 | 0.27008 | -0.21057 | -0.21973 | -0.20599 | -0.21515 | -0.068665 | -0.19226 | 0.091553 | 0.059509 | -0.13733 | -0.05951 | -0.068664 | 0.009155 | 0.27466 | 121.6965 | 0.12817 | 121.7285 | 121.4264 | 121.4447 | 121.4218 | 121.376 | -121.5729 | -121.637 | 121.6919 | 121.6599 | 61.4868 | 61.5921
6.0156 | 121.8979 | -61.5646 | 59.9945 | -0.012131 | 0.0039692 | 0.059409 | 0.05686 | 0.0010125 | -0.005144 | -3.1996e-05 | -0.005371 | 0.0013821 | 0.06592 | 0.056926 | -0.0077459 | 0.020333 | -0.0010617 | -0.068665 | 59.8663 | -61.5784 | 60.1776 | -61.29 | -61.7706 | -61.7752 | 0.073242 | 59.8297 | -61.6333 | 60.1181 | -61.4594 | -61.5921 | -61.6928 | -0.013733 | -0.12817 | 0.18311 | 0.27466 | -0.21057 | -0.20599 | -0.19684 | -0.19226 | -0.068665 | -0.16479 | 0.1236 | 0.10529 | -0.12817 | -0.027466 | -0.059509 | 0.041199 | 0.28839 | 121.756 | 0.17395 | 121.7514 | 121.4447 | 121.463 | 121.431 | 121.3943 | -121.5729 | -121.6278 | 121.7422 | 121.6827 | 61.496 | 61.6379
7.7031 | 121.8338 | -61.5143 | 60.0952 | -0.01976 | 0.00012398 | 0.057913 | 0.054937 | -0.00026906 | -0.0066394 | 0.0012496 | -0.0023192 | 0.0011685 | 0.064638 | 0.059917 | -0.0068915 | 0.019265 | -0.0040525 | 0.032043 | 59.9304 | -61.5555 | 60.2188 | -61.2122 | -61.6608 | -61.7065 | 0.10986 | 59.9487 | -61.5921 | 60.1227 | -61.4182 | -61.5555 | -61.6745 | -0.041199 | -0.1648 | 0.1236 | 0.30212 | -0.19226 | -0.14648 | -0.15106 | -0.10529 | -0.07782 | -0.14649 | 0.027466 | 0.09613 | -0.16022 | -0.041199 | -0.082398 | 0.036621 | 0.34332 | 121.7743 | 0.17395 | 121.7148 | 121.4859 | 121.5408 | 121.4447 | 121.463 | -121.6507 | -121.6873 | 121.7331 | 121.637 | 61.5463 | 61.6241
9.4375 | 121.8658 | -61.5601 | 59.9899 | -0.0045011 | 0.0035418 | 0.060263 | 0.05451 | 0.0050713 | -0.0059986 | -0.002382 | -0.005371 | 0.0026639 | 0.065279 | 0.057994 | -0.0090277 | 0.02076 | 6.346e-06 | -0.054932 | 59.848 | -61.5829 | 60.1318 | -61.2946 | -61.7477 | -61.7661 | 0.045776 | 59.8251 | -61.6241 | 60.0815 | -61.4822 | -61.6013 | -61.6974 | -0.022888 | -0.14191 | 0.14191 | 0.2655 | -0.20599 | -0.18768 | -0.18311 | -0.1648 | -0.064087 | -0.16479 | 0.091553 | 0.07782 | -0.13733 | -0.041198 | -0.073242 | 0.022889 | 0.28839 | 121.7148 | 0.14191 | 121.7056 | 121.431 | 121.4493 | 121.4081 | 121.3852 | -121.5729 | -121.6141 | 121.6919 | 121.6415 | 61.5051 | 61.6058
11.1094 | 121.9025 | -61.5601 | 59.9716 | -0.012131 | 0.001192 | 0.060477 | 0.055578 | -0.00048286 | -0.0055712 | -0.0032364 | -0.005371 | 0.00074128 | 0.066988 | 0.057567 | -0.0086005 | 0.020119 | -0.0034117 | -0.068665 | 59.8572 | -61.6104 | 60.1639 | -61.2808 | -61.7569 | -61.7661 | 0.064087 | 59.8297 | -61.6516 | 60.1044 | -61.4639 | -61.5921 | -61.6791 | -0.050354 | -0.11444 | 0.19226 | 0.27924 | -0.20599 | -0.19684 | -0.15564 | -0.14648 | -0.091552 | -0.14191 | 0.13275 | 0.096131 | -0.11902 | -0.032043 | -0.027466 | 0.059509 | 0.32959 | 121.7743 | 0.18768 | 121.756 | 121.4676 | 121.4813 | 121.4172 | 121.3898 | -121.582 | -121.6232 | 121.7239 | 121.6644 | 61.4914 | 61.6241
12.8594 | 121.7743 | -61.5463 | 60.1273 | -0.0045011 | 0.00076478 | 0.057059 | 0.054083 | -0.0013373 | -0.0087756 | 0.0008224 | -0.0084228 | 0.00052768 | 0.066347 | 0.062908 | -0.0098823 | 0.016701 | -0.0027707 | -0.032043 | 60.0037 | -61.5372 | 60.1135 | -61.3129 | -61.7477 | -61.7844 | 0.027466 | 59.9625 | -61.5784 | 60.054 | -61.4868 | -61.6287 | -61.7111 | 0.009156 | -0.1236 | -0.013733 | 0.23346 | -0.23804 | -0.20142 | -0.24719 | -0.21057 | -0.032043 | -0.16479 | -0.073242 | 0.05951 | -0.16479 | -0.082397 | -0.13275 | -0.050354 | 0.2243 | 121.6507 | 0.091553 | 121.6324 | 121.5408 | 121.5408 | 121.55 | 121.5088 | -121.6644 | -121.7056 | 121.6599 | 121.6003 | 61.5143 | 61.5738
14.5312 | 121.8155 | -61.5463 | 60.0632 | -0.01976 | 0.0031146 | 0.058554 | 0.057928 | -0.0041145 | -0.005144 | 0.0014634 | -0.0023192 | 0.0039457 | 0.067202 | 0.056285 | -0.0062507 | 0.020333 | -0.00063445 | 0 | 59.9945 | -61.5738 | 60.1547 | -61.322 | -61.7523 | -61.7844 | 0.054932 | 59.9487 | -61.6104 | 60.0998 | -61.4639 | -61.6196 | -61.6974 | -0.027466 | -0.068664 | 0.091553 | 0.22431 | -0.23804 | -0.20599 | -0.21057 | -0.17853 | -0.064087 | -0.11444 | 0.036621 | 0.082398 | -0.15106 | -0.073242 | -0.086975 | -0.009155 | 0.25177 | 121.7285 | 0.14648 | 121.7102 | 121.5683 | 121.5591 | 121.5408 | 121.4951 | -121.637 | -121.6736 | 121.7011 | 121.6461 | 61.5463 | 61.6013
16.25 | 121.8475 | -61.5601 | 60.0403 | 0.0031279 | 0.0026874 | 0.057486 | 0.057287 | 0.00079894 | -0.0055712 | -0.0013138 | -0.005371 | 0.00031408 | 0.06357 | 0.049022 | -0.0090277 | 0.019692 | -0.00084805 | -0.082397 | 59.9075 | -61.5601 | 60.1273 | -61.3129 | -61.7661 | -61.7661 | 0 | 59.8618 | -61.6196 | 60.0723 | -61.4777 | -61.6241 | -61.7065 | 0 | -0.13275 | 0.086975 | 0.24719 | -0.20599 | -0.20599 | -0.20599 | -0.20599 | -0.059509 | -0.17853 | 0.032044 | 0.082398 | -0.14648 | -0.064087 | -0.086975 | -0.004578 | 0.24719 | 121.6873 | 0.14191 | 121.6919 | 121.4676 | 121.4813 | 121.4676 | 121.4218 | -121.6003 | -121.6599 | 121.6873 | 121.6324 | 61.4777 | 61.5601
18 | 121.9116 | -61.5143 | 60.0403 | 0.0031279 | 0.00012398 | 0.0577 | 0.053442 | -0.0030463 | -0.0074938 | -0.0013138 | -0.0023192 | 0.00074128 | 0.065706 | 0.059917 | -0.0096685 | 0.020546 | -0.0059751 | 0.041199 | 59.9396 | -61.5646 | 60.2371 | -61.1847 | -61.647 | -61.6653 | 0.15106 | 59.8984 | -61.5784 | 60.1822 | -61.3632 | -61.4777 | -61.6104 | -0.050354 | -0.10071 | 0.19684 | 0.32959 | -0.15106 | -0.13275 | -0.10071 | -0.082398 | -0.064087 | -0.14191 | 0.14191 | 0.15106 | -0.096131 | 0.036621 | -0.032044 | 0.10071 | 0.37994 | 121.8018 | 0.21515 | 121.7606 | 121.5042 | 121.4767 | 121.4539 | 121.4127 | -121.6049 | -121.6187 | 121.7514 | 121.6965 | 61.5555 | 61.6653
19.75 | 121.8063 | -61.5326 | 60.0815 | 0.0031279 | 0.00012398 | 0.05834 | 0.05686 | -0.0021919 | -0.0064258 | -0.0030228 | -0.005371 | 0.00031408 | 0.064424 | 0.06483 | -0.0088141 | 0.021187 | 0.00021995 | 0.036621 | 59.9808 | -61.5189 | 60.1822 | -61.2488 | -61.6928 | -61.7203 | 0.064087 | 59.9487 | -61.5692 | 60.0723 | -61.441 | -61.6196 | -61.7111 | 0.013733 | -0.10071 | 0.10071 | 0.28381 | -0.18768 | -0.16022 | -0.20142 | -0.17395 | -0.036621 | -0.13275 | -0.009155 | 0.091553 | -0.17853 | -0.086975 | -0.14191 | -0.050354 | 0.27008 | 121.701 | 0.12817 | 121.6415 | 121.4996 | 121.5179 | 121.5134 | 121.4813 | -121.6003 | -121.6507 | 121.7148 | 121.6049 | 61.5692 | 61.5967
21.4219 | 121.9025 | -61.4914 | 60.054 | -0.012131 | 0.001833 | 0.059409 | 0.055365 | -0.0028327 | -0.0074938 | -0.001741 | -0.0084228 | 0.0011685 | 0.065493 | 0.058635 | -0.0094549 | 0.019051 | -0.0038389 | 0.032043 | 59.9304 | -61.5326 | 60.2463 | -61.1755 | -61.615 | -61.6608 | 0.16022 | 59.8938 | -61.5463 | 60.1685 | -61.3678 | -61.4914 | -61.6104 | -0.041199 | -0.1236 | 0.19226 | 0.31586 | -0.16937 | -0.1236 | -0.12817 | -0.082397 | -0.054932 | -0.16022 | 0.11444 | 0.1236 | -0.11902 | 0 | -0.064087 | 0.054932 | 0.35706 | 121.7789 | 0.17853 | 121.7148 | 121.463 | 121.4401 | 121.4218 | 121.3852 | -121.5866 | -121.6003 | 121.7377 | 121.6599 | 61.5234 | 61.6516
23.1562 | 121.7697 | -61.5234 | 60.1135 | -0.0045011 | 0.00097838 | 0.055136 | 0.056219 | -0.0011237 | -0.0059986 | -0.0013138 | -0.005371 | 0.0018095 | 0.066347 | 0.056285 | -0.010096 | 0.019051 | -0.00042085 | -0.027466 | 59.9762 | -61.5509 | 60.1318 | -61.3266 | -61.7432 | -61.7706 | 0.018311 | 59.9716 | -61.6104 | 60.0677 | -61.4731 | -61.6196 | -61.7203 | -0.027466 | -0.13733 | 0.018311 | 0.19684 | -0.24719 | -0.21973 | -0.21973 | -0.19226 | -0.086976 | -0.14191 | -0.045776 | 0.050354 | -0.19684 | -0.096131 | -0.10986 | -0.009155 | 0.2243 | 121.6827 | 0.13733 | 121.6782 | 121.5271 | 121.582 | 121.4996 | 121.4951 | -121.6644 | -121.7239 | 121.6553 | 121.5912 | 61.496 | 61.5417
24.8906 | 121.8887 | -61.5143 | 60.022 | -0.012131 | 0.00012398 | 0.057913 | 0.055578 | 0.0031487 | -0.0066394 | -0.0021682 | -0.0023192 | 0.00074128 | 0.06592 | 0.05479 | -0.0081733 | 0.020974 | -0.0021299 | -0.050354 | 59.935 | -61.5601 | 60.1547 | -61.2808 | -61.7157 | -61.734 | 0.059509 | 59.8892 | -61.6058 | 60.1547 | -61.4273 | -61.5189 | -61.6425 | -0.045777 | -0.086975 | 0.13275 | 0.23346 | -0.21973 | -0.20142 | -0.17395 | -0.15564 | -0.091553 | -0.13275 | 0.13275 | 0.086975 | -0.12817 | -0.004578 | -0.036621 | 0.086975 | 0.27924 | 121.7148 | 0.17853 | 121.7606 | 121.4951 | 121.4951 | 121.4493 | 121.4035 | -121.582 | -121.6278 | 121.669 | 121.669 | 61.4639 | 61.5738
26.5625 | 121.8109 | -61.5189 | 60.0632 | -0.01976 | 0.0024738 | 0.059195 | 0.059424 | -0.00069646 | -0.0040758 | -0.0015274 | -0.005371 | 0.0048001 | 0.066561 | 0.064189 | -0.0071051 | 0.018624 | -0.0042661 | 0.022888 | 59.9716 | -61.5509 | 60.141 | -61.322 | -61.7477 | -61.7752 | 0.073242 | 59.9442 | -61.6104 | 60.0906 | -61.4731 | -61.615 | -61.6974 | -0.032043 | -0.091552 | 0.07782 | 0.19684 | -0.25635 | -0.22888 | -0.22431 | -0.19684 | -0.091553 | -0.11902 | 0.027466 | 0.045777 | -0.17853 | -0.09613 | -0.086975 | -0.004577 | 0.22888 | 121.6919 | 0.13733 | 121.7011 | 121.5225 | 121.5546 | 121.4905 | 121.463 | -121.6141 | -121.6736 | 121.6599 | 121.6095 | 61.5417 | 61.5921
28.2969 | 121.7972 | -61.5326 | 60.1044 | -0.0045011 | -0.00073062 | 0.057059 | 0.055578 | -0.0019781 | -0.0062122 | 0.0001816 | -0.005371 | 0.0011685 | 0.066988 | 0.062694 | -0.0079597 | 0.020546 | -0.0049069 | 0.004578 | 59.9899 | -61.5372 | 60.1501 | -61.2671 | -61.7157 | -61.7706 | 0.041199 | 59.935 | -61.5875 | 60.0677 | -61.4731 | -61.6104 | -61.734 | -0.004577 | -0.11444 | 0.045776 | 0.2655 | -0.23804 | -0.18311 | -0.23346 | -0.17853 | -0.054931 | -0.16937 | -0.036621 | 0.05951 | -0.20142 | -0.07782 | -0.14648 | -0.022889 | 0.27008 | 121.6873 | 0.11444 | 121.6553 | 121.5271 | 121.5225 | 121.5225 | 121.4676 | -121.6415 | -121.6919 | 121.6827 | 121.6003 | 61.5372 | 61.5738
30.0469 | 121.8475 | -61.5326 | 60.0723 | -0.01976 | 0.00055118 | 0.057272 | 0.054297 | -0.0045417 | -0.006853 | -0.0025956 | -0.005371 | 0.0018095 | 0.066988 | 0.056499 | -0.0090277 | 0.020119 | -0.0025571 | 0.032043 | 59.935 | -61.5463 | 60.2234 | -61.2076 | -61.6516 | -61.6837 | 0.10986 | 59.9167 | -61.5646 | 60.1318 | -61.3998 | -61.5417 | -61.6516 | -0.013733 | -0.13733 | 0.15106 | 0.32501 | -0.15106 | -0.11902 | -0.13733 | -0.10529 | -0.032043 | -0.15564 | 0.059509 | 0.13275 | -0.11902 | -0.009155 | -0.086975 | 0.022888 | 0.33875 | 121.7697 | 0.16479 | 121.6965 | 121.4813 | 121.4813 | 121.4676 | 121.4493 | -121.6187 | -121.637 | 121.756 | 121.6644 | 61.5646 | 61.6425
31.7344 | 121.7926 | -61.5967 | 60.0357 | -0.0045011 | 0.0033282 | 0.058127 | 0.058783 | 0.0040033 | -0.0070666 | -0.0030228 | -0.005371 | 0.0030911 | 0.066347 | 0.057781 | -0.0071051 | 0.020333 | -0.0061887 | 0.013733 | 59.9625 | -61.6058 | 60.141 | -61.3129 | -61.7798 | -61.8073 | 0.036621 | 59.9075 | -61.6379 | 60.0723 | -61.5097 | -61.6608 | -61.734 | -0.009155 | -0.073243 | 0.10529 | 0.28381 | -0.21057 | -0.1831 | -0.20142 | -0.17395 | -0.041198 | -0.12817 | 0.036621 | 0.086975 | -0.13733 | -0.064087 | -0.096131 | -0.022889 | 0.29297 | 121.7468 | 0.12817 | 121.7102 | 121.5683 | 121.5454 | 121.5591 | 121.5042 | -121.6415 | -121.6736 | 121.7377 | 121.669 | 61.6104 | 61.6333
33.4844 | 121.8018 | -61.5417 | 60.1044 | -0.012131 | -0.00051702 | 0.056204 | 0.056646 | -0.00091006 | -0.0040758 | -0.002382 | -0.0084228 | 0.0039457 | 0.066347 | 0.058422 | -0.0090277 | 0.019905 | -0.0036253 | -0.027466 | 60.0357 | -61.5784 | 60.0998 | -61.3449 | -61.7706 | -61.7889 | -0.009155 | 59.967 | -61.5967 | 60.0861 | -61.4822 | -61.6241 | -61.702 | -0.036621 | -0.068664 | -0.004578 | 0.19684 | -0.24719 | -0.22888 | -0.21057 | -0.19226 | -0.054932 | -0.13733 | -0.01831 | 0.059509 | -0.16022 | -0.082398 | -0.10529 | -0.027466 | 0.23346 | 121.6782 | 0.11444 | 121.6827 | 121.6141 | 121.5637 | 121.5775 | 121.5088 | -121.6827 | -121.7011 | 121.6415 | 121.6278 | 61.5143 | 61.5326
35.1562 | 121.756 | -61.615 | 60.0449 | -0.012131 | 0.0054644 | 0.060049 | 0.05921 | -0.0015509 | -0.0042896 | -0.0047318 | -0.011475 | 0.0013821 | 0.066988 | 0.063335 | -0.0049689 | 0.020333 | -0.0049069 | -0.068665 | 59.9487 | -61.6013 | 60.0586 | -61.4136 | -61.8576 | -61.8759 | -0.086975 | 59.903 | -61.6562 | 59.9991 | -61.5967 | -61.7477 | -61.7844 | 0.013733 | -0.096131 | 0.013733 | 0.20142 | -0.26093 | -0.24262 | -0.27466 | -0.25635 | -0.041199 | -0.14191 | -0.045777 | 0.01831 | -0.16937 | -0.13275 | -0.12817 | -0.091553 | 0.18768 | 121.6599 | 0.059509 | 121.6553 | 121.55 | 121.5591 | 121.5637 | 121.5179 | -121.6461 | -121.701 | 121.6736 | 121.6141 | 61.5463 | 61.528
36.9062 | 121.8796 | -61.5005 | 60.0952 | -0.0045011 | 0.001192 | 0.058768 | 0.055578 | 0.00058534 | -0.0057848 | -0.0021682 | -0.0023192 | -0.00011332 | 0.066774 | 0.054576 | -0.0079597 | 0.021187 | -0.0012753 | 0.036621 | 59.9396 | -61.5326 | 60.2371 | -61.203 | -61.647 | -61.6928 | 0.12817 | 59.8938 | -61.5646 | 60.1456 | -61.3861 | -61.5143 | -61.6333 | -0.032044 | -0.15564 | 0.14191 | 0.29755 | -0.19226 | -0.14648 | -0.16022 | -0.11444 | -0.064087 | -0.20142 | 0.050354 | 0.11444 | -0.13275 | -0.013733 | -0.068665 | 0.050354 | 0.32959 | 121.7697 | 0.17853 | 121.7102 | 121.4722 | 121.4584 | 121.4401 | 121.3943 | -121.6278 | -121.6599 | 121.7377 | 121.6461 | 61.5372 | 61.6287
38.6406 | 121.8796 | -61.6013 | 60.0082 | -0.012131 | 0.0043964 | 0.057913 | 0.057501 | 0.0014397 | -0.0055712 | -0.0047318 | -0.005371 | 0.0018095 | 0.066133 | 0.054576 | -0.0056097 | 0.021828 | -0.0034117 | -0.11444 | 59.9167 | -61.615 | 60.0677 | -61.3724 | -61.8393 | -61.8439 | -0.022888 | 59.8389 | -61.647 | 60.0815 | -61.4868 | -61.6425 | -61.702 | -0.013733 | -0.091553 | 0.059509 | 0.22888 | -0.24262 | -0.23804 | -0.22888 | -0.2243 | -0.045777 | -0.16937 | 0.073242 | 0.11444 | -0.10071 | -0.041199 | -0.054931 | 0.004578 | 0.24262 | 121.6827 | 0.16022 | 121.7285 | 121.5317 | 121.4859 | 121.5179 | 121.4401 | -121.6232 | -121.6553 | 121.669 | 121.6827 | 61.4868 | 61.5784
40.3125 | 121.8567 | -61.5646 | 60.0266 | -0.01976 | 0.0031146 | 0.058127 | 0.054724 | -0.0021919 | -0.0062122 | -0.0011002 | -0.005371 | 0.00052768 | 0.067202 | 0.05244 | -0.011591 | 0.020333 | -0.0021299 | -0.082397 | 59.8892 | -61.5829 | 60.1318 | -61.3083 | -61.7615 | -61.7615 | 0.009155 | 59.8663 | -61.5967 | 60.0723 | -61.4868 | -61.5967 | -61.6974 | -0.018311 | -0.13733 | 0.10529 | 0.25635 | -0.19684 | -0.19684 | -0.17853 | -0.17853 | -0.032044 | -0.16022 | 0.045777 | 0.07782 | -0.13275 | -0.032044 | -0.10071 | 0 | 0.27466 | 121.7148 | 0.10986 | 121.669 | 121.4722 | 121.463 | 121.4539 | 121.431 | -121.6095 | -121.6232 | 121.6965 | 121.637 | 61.4822 | 61.5738
42.0469 | 121.8979 | -61.5646 | 59.9579 | -0.01976 | 0.002901 | 0.05834 | 0.057501 | 0.0044305 | -0.0042896 | -0.0032364 | 0.00073235 | 0.0013821 | 0.068911 | 0.059276 | -0.0083869 | 0.020119 | -0.0044797 | -0.064087 | 59.903 | -61.6058 | 60.1501 | -61.2991 | -61.7569 | -61.7706 | 0.050354 | 59.8526 | -61.6287 | 60.1044 | -61.4777 | -61.6058 | -61.6791 | -0.041199 | -0.054932 | 0.19226 | 0.2655 | -0.20599 | -0.19226 | -0.16479 | -0.15106 | -0.064087 | -0.10529 | 0.14648 | 0.086975 | -0.11444 | -0.041199 | -0.050354 | 0.022888 | 0.3067 | 121.756 | 0.15106 | 121.7331 | 121.5088 | 121.4813 | 121.4676 | 121.4172 | -121.5637 | -121.5866 | 121.7148 | 121.669 | 61.5005 | 61.615
43.7969 | 121.8521 | -61.5463 | 60.0357 | -0.012131 | 0.0014056 | 0.058768 | 0.055365 | -0.00048286 | -0.0045032 | -0.0038772 | -0.0084228 | -0.00075412 | 0.065065 | 0.054363 | -0.0086005 | 0.021828 | -0.0019163 | -0.09613 | 59.8938 | -61.5692 | 60.1318 | -61.2946 | -61.7706 | -61.7706 | 0.013733 | 59.848 | -61.6241 | 60.0998 | -61.5005 | -61.5967 | -61.702 | -0.022888 | -0.14191 | 0.09613 | 0.25177 | -0.2243 | -0.2243 | -0.20142 | -0.20142 | -0.07782 | -0.18768 | 0.064086 | 0.045777 | -0.15564 | -0.050354 | -0.077819 | 0.027466 | 0.27466 | 121.7011 | 0.1236 | 121.7239 | 121.463 | 121.4722 | 121.4401 | 121.3943 | -121.6049 | -121.6599 | 121.6782 | 121.6461 | 61.4502 | 61.5601
45.4688 | 121.875 | -61.5738 | 59.9716 | -0.012131 | 0.0024738 | 0.059195 | 0.055365 | 0.0010125 | -0.0049304 | -0.0004592 | -0.005371 | 0.0022367 | 0.065279 | 0.056713 | -0.0086005 | 0.019478 | -0.0042661 | -0.073242 | 59.8709 | -61.5967 | 60.1822 | -61.2717 | -61.7523 | -61.7386 | 0.064087 | 59.8251 | -61.6287 | 60.0861 | -61.4868 | -61.6058 | -61.6882 | -0.022888 | -0.10071 | 0.21057 | 0.30212 | -0.16479 | -0.17853 | -0.14191 | -0.15564 | -0.054931 | -0.14648 | 0.11444 | 0.086976 | -0.11444 | -0.032043 | -0.059509 | 0.022888 | 0.32501 | 121.7789 | 0.14191 | 121.7148 | 121.4676 | 121.4539 | 121.4447 | 121.3989 | -121.5683 | -121.6003 | 121.756 | 121.6599 | 61.5005 | 61.6379
47.2031 | 121.7651 | -61.6196 | 60.0494 | -0.01976 | 0.0069598 | 0.056631 | 0.060278 | -0.00091006 | -0.0055712 | 0.0001816 | -0.005371 | 0.0050137 | 0.064852 | 0.06184 | -0.0071051 | 0.017769 | -0.0055479 | -0.082397 | 59.9304 | -61.6013 | 60.0815 | -61.3861 | -61.8622 | -61.8576 | -0.054932 | 59.8938 | -61.6516 | 60.0128 | -61.5921 | -61.7249 | -61.7844 | 0.018311 | -0.11902 | 0.032044 | 0.23346 | -0.23804 | -0.24262 | -0.25635 | -0.26093 | -0.032043 | -0.15564 | -0.036621 | 0.027466 | -0.16479 | -0.10529 | -0.13275 | -0.073243 | 0.21515 | 121.6827 | 0.059509 | 121.6644 | 121.5317 | 121.5454 | 121.55 | 121.5134 | -121.6507 | -121.701 | 121.7011 | 121.6324 | 61.5372 | 61.5646
48.8906 | 121.907 | -61.5051 | 60.054 | -0.0045011 | -0.00051702 | 0.055563 | 0.053869 | -0.0041145 | -0.0055712 | -0.0008866 | -0.0084228 | 0.00095488 | 0.06592 | 0.055431 | -0.010737 | 0.021187 | -0.0040525 | 0 | 59.9167 | -61.5372 | 60.2463 | -61.1572 | -61.6379 | -61.647 | 0.15106 | 59.903 | -61.5829 | 60.173 | -61.3495 | -61.4822 | -61.6058 | -0.032043 | -0.13733 | 0.19226 | 0.3479 | -0.14191 | -0.13275 | -0.10986 | -0.10071 | -0.07782 | -0.15106 | 0.11902 | 0.15564 | -0.10071 | 0.022888 | -0.022888 | 0.10071 | 0.37994 | 121.7834 | 0.23346 | 121.756 | 121.4539 | 121.4859 | 121.4218 | 121.4081 | -121.5912 | -121.637 | 121.7514 | 121.6782 | 61.5051 | 61.6562
50.625 | 121.8704 | -61.5509 | 60.0357 | -0.0045011 | 0.0024738 | 0.057272 | 0.05451 | 0.0010125 | -0.0066394 | -0.001741 | -0.0023192 | 0.00052768 | 0.065706 | 0.047527 | -0.0094549 | 0.01841 | -0.0014891 | -0.073242 | 59.9213 | -61.5692 | 60.1227 | -61.3129 | -61.7569 | -61.7523 | 0.022888 | 59.8755 | -61.6013 | 60.0998 | -61.4594 | -61.5738 | -61.6791 | -0.018311 | -0.11444 | 0.086975 | 0.23804 | -0.20142 | -0.20599 | -0.1831 | -0.18768 | -0.050354 | -0.16022 | 0.064086 | 0.091552 | -0.12817 | -0.022889 | -0.07782 | 0.027465 | 0.25635 | 121.6919 | 0.14191 | 121.701 | 121.4905 | 121.4767 | 121.4722 | 121.4264 | -121.6049 | -121.637 | 121.6736 | 121.6507 | 61.4777 | 61.5738
52.3594 | 121.9116 | -61.5234 | 60.0266 | -0.0045011 | 0.00012398 | 0.057913 | 0.056219 | -0.0013373 | -0.0055712 | 0.0012496 | -0.005371 | 0.00095488 | 0.064424 | 0.066326 | -0.0086005 | 0.019692 | -0.0034117 | -0.032043 | 59.9396 | -61.5646 | 60.1913 | -61.2396 | -61.6837 | -61.702 | 0.10529 | 59.8892 | -61.5829 | 60.1639 | -61.377 | -61.5051 | -61.6196 | -0.041199 | -0.086975 | 0.16479 | 0.28381 | -0.17853 | -0.16022 | -0.13733 | -0.11902 | -0.05951 | -0.13733 | 0.13733 | 0.14648 | -0.096131 | 0.01831 | -0.036621 | 0.07782 | 0.32501 | 121.756 | 0.20599 | 121.7468 | 121.5042 | 121.4722 | 121.463 | 121.4127 | -121.5912 | -121.6095 | 121.7148 | 121.6873 | 61.4914 | 61.6287
54.0469 | 121.907 | -61.4914 | 60.0769 | -0.0045011 | -0.00030342 | 0.057059 | 0.054083 | -0.0011237 | -0.0077074 | -0.0015274 | -0.011475 | 0.0015957 | 0.066133 | 0.055431 | -0.0083869 | 0.019692 | -0.0034117 | 0.009155 | 59.9213 | -61.5372 | 60.2417 | -61.1664 | -61.6241 | -61.6516 | 0.17395 | 59.8801 | -61.5692 | 60.1776 | -61.3678 | -61.5097 | -61.5921 | -0.045776 | -0.15564 | 0.16479 | 0.32501 | -0.16022 | -0.13275 | -0.11444 | -0.086976 | -0.07782 | -0.19684 | 0.10071 | 0.1236 | -0.10071 | -0.018311 | -0.022888 | 0.059509 | 0.37079 | 121.7789 | 0.20142 | 121.7468 | 121.4584 | 121.4493 | 121.4127 | 121.3715 | -121.6141 | -121.6461 | 121.7331 | 121.669 | 61.5005 | 61.6653
55.7812 | 121.7743 | -61.6104 | 60.0174 | 0.0031279 | 0.0035418 | 0.058554 | 0.05921 | 0.0059259 | -0.0057848 | -0.00345 | 0.00073235 | 0.0035183 | 0.066988 | 0.061199 | -0.0075323 | 0.017983 | -0.0044797 | -0.09613 | 59.9304 | -61.6104 | 60.0311 | -61.441 | -61.8668 | -61.8896 | -0.082397 | 59.903 | -61.6608 | 59.9945 | -61.6058 | -61.7432 | -61.7889 | 0 | -0.086975 | 0.013733 | 0.16937 | -0.27923 | -0.25635 | -0.27923 | -0.25635 | -0.050354 | -0.11444 | -0.022888 | 0.004578 | -0.17853 | -0.13275 | -0.12817 | -0.082397 | 0.16937 | 121.6415 | 0.054932 | 121.6553 | 121.5408 | 121.5637 | 121.5408 | 121.5134 | -121.6278 | -121.6782 | 121.6415 | 121.6049 | 61.5143 | 61.528
57.4531 | 121.7834 | -61.5921 | 60.0128 | -0.0045011 | 0.0043964 | 0.059195 | 0.054937 | 0.0025079 | -0.005144 | 0.0001816 | -0.0023192 | 0.0024503 | 0.066133 | 0.057353 | -0.0071051 | 0.020546 | -0.0023435 | -0.11902 | 59.9258 | -61.6333 | 60.0403 | -61.4273 | -61.8713 | -61.8805 | -0.086975 | 59.8846 | -61.6425 | 60.0174 | -61.5967 | -61.7294 | -61.7706 | -0.041199 | -0.086975 | 0.027466 | 0.16479 | -0.28839 | -0.27924 | -0.24719 | -0.23804 | -0.050354 | -0.12817 | 0.004578 | -0.004578 | -0.17853 | -0.13733 | -0.12817 | -0.086975 | 0.20599 | 121.6736 | 0.045776 | 121.6599 | 121.5591 | 121.5271 | 121.5179 | 121.4767 | -121.6461 | -121.6553 | 121.6324 | 121.6095 | 61.4731 | 61.5051
59.2031 | 121.8842 | -61.5097 | 60.0311 | -0.0045011 | 0.00012398 | 0.059195 | 0.053442 | -0.0047553 | -0.0053576 | -0.0019546 | -0.0084228 | 0.0020231 | 0.064852 | 0.05244 | -0.0088141 | 0.02076 | -0.0017027 | -0.064087 | 59.8938 | -61.5875 | 60.1456 | -61.2762 | -61.7157 | -61.7249 | 0.045776 | 59.8618 | -61.5784 | 60.1318 | -61.3998 | -61.5234 | -61.6379 | -0.077819 | -0.13733 | 0.11444 | 0.23346 | -0.21515 | -0.20599 | -0.13733 | -0.12817 | -0.068664 | -0.16937 | 0.10071 | 0.10986 | -0.12817 | -0.013732 | -0.059509 | 0.054932 | 0.31128 | 121.7331 | 0.17853 | 121.7102 | 121.4813 | 121.4401 | 121.4035 | 121.3715 | -121.6187 | -121.6095 | 121.6553 | 121.6415 | 61.4456 | 61.5555
60.9531 | 121.7743 | -61.5189 | 60.0998 | -0.012131 | 0.00055118 | 0.057059 | 0.056006 | -0.0026191 | -0.0062122 | -0.0002456 | -0.0084228 | 0.0015957 | 0.065706 | 0.052867 | -0.0088141 | 0.02076 | -0.0031979 | -0.013733 | 59.9899 | -61.5875 | 60.1227 | -61.2991 | -61.7523 | -61.7706 | 0.018311 | 59.9625 | -61.5738 | 60.0632 | -61.4685 | -61.6196 | -61.7294 | -0.068664 | -0.10986 | 0.022889 | 0.21973 | -0.25177 | -0.23346 | -0.18311 | -0.16479 | -0.054932 | -0.13733 | -0.036621 | 0.050354 | -0.21057 | -0.10071 | -0.15564 | -0.045776 | 0.28839 | 121.7102 | 0.10529 | 121.637 | 121.5775 | 121.5363 | 121.5088 | 121.4813 | -121.6873 | -121.6736 | 121.6415 | 121.582 | 61.5051 | 61.5372
62.6406 | 121.788 | -61.528 | 60.0952 | 0.0031279 | 0.0014056 | 0.057272 | 0.056433 | -0.00069646 | -0.0064258 | 0.0012496 | -0.0023192 | 0.0024503 | 0.066774 | 0.056285 | -0.0077459 | 0.018837 | -0.0059751 | -0.013733 | 59.9899 | -61.5463 | 60.0998 | -61.3358 | -61.7569 | -61.7981 | -0.009155 | 59.967 | -61.5692 | 60.0632 | -61.4868 | -61.6379 | -61.6974 | -0.018311 | -0.10529 | 0.004577 | 0.19226 | -0.27008 | -0.22888 | -0.25177 | -0.21057 | -0.041199 | -0.12817 | -0.032044 | 0.041199 | -0.16937 | -0.10986 | -0.12817 | -0.068664 | 0.21057 | 121.6461 | 0.082398 | 121.6324 | 121.5363 | 121.5363 | 121.5179 | 121.4951 | -121.6415 | -121.6644 | 121.6278 | 121.5912 | 61.5143 | 61.5189
64.3906 | 121.7606 | -61.5875 | 60.0494 | -0.0045011 | 0.0043964 | 0.056845 | 0.057501 | 0.0016535 | -0.0070666 | 0.0012496 | -0.0023192 | 0.0030911 | 0.067842 | 0.063335 | -0.0062507 | 0.020974 | 0.00086095 | -0.068665 | 59.9487 | -61.6104 | 60.054 | -61.4044 | -61.8713 | -61.8759 | -0.086975 | 59.9075 | -61.6516 | 59.9991 | -61.5829 | -61.7294 | -61.7889 | -0.022889 | -0.10071 | 0.004578 | 0.18311 | -0.28839 | -0.28381 | -0.2655 | -0.26093 | -0.064087 | -0.14191 | -0.050354 | 0.004577 | -0.20142 | -0.14191 | -0.13733 | -0.07782 | 0.20599 | 121.6644 | 0.068664 | 121.6507 | 121.5591 | 121.5591 | 121.5363 | 121.4951 | -121.6599 | -121.701 | 121.6415 | 121.5866 | 61.5189 | 61.5005
66.0781 | 121.8018 | -61.5326 | 60.0403 | -0.01976 | 0.0035418 | 0.058127 | 0.056433 | 0.0012261 | -0.0053576 | -0.0013138 | 0.00073235 | 0.0041593 | 0.067202 | 0.05479 | -0.0079597 | 0.017983 | -0.0010617 | -0.004578 | 59.9625 | -61.5829 | 60.1501 | -61.29 | -61.7615 | -61.7752 | 0.059509 | 59.9213 | -61.615 | 60.0861 | -61.4822 | -61.6241 | -61.7065 | -0.050354 | -0.07782 | 0.10986 | 0.24262 | -0.24262 | -0.22888 | -0.19226 | -0.17853 | -0.082397 | -0.11902 | 0.045777 | 0.050354 | -0.17395 | -0.091553 | -0.091553 | -0.009156 | 0.29297 | 121.7331 | 0.13275 | 121.7011 | 121.5454 | 121.5363 | 121.4951 | 121.4539 | -121.6232 | -121.6553 | 121.6827 | 121.6187 | 61.528 | 61.5921
67.8125 | 121.8109 | -61.5601 | 60.1044 | -0.0045011 | 0.001192 | 0.057913 | 0.052588 | -0.0015509 | -0.0074938 | 0.001677 | -0.0084228 | 0.0015957 | 0.065706 | 0.061412 | -0.0086005 | 0.020974 | -0.0025571 | -0.022888 | 59.9854 | -61.5738 | 60.1089 | -61.322 | -61.7523 | -61.7844 | 0.009155 | 59.9533 | -61.6013 | 60.0861 | -61.4594 | -61.6241 | -61.6974 | -0.013733 | -0.11902 | 0.004578 | 0.23804 | -0.2243 | -0.19226 | -0.21057 | -0.17853 | -0.041198 | -0.15106 | -0.01831 | 0.10071 | -0.13733 | -0.064087 | -0.096131 | -0.022889 | 0.25177 | 121.6827 | 0.14191 | 121.6873 | 121.5591 | 121.5546 | 121.5454 | 121.5134 | -121.6782 | -121.7056 | 121.669 | 121.6461 | 61.5372 | 61.5692
69.5 | 121.8613 | -61.5601 | 60.0174 | -0.0045011 | 0.001192 | 0.058554 | 0.054297 | 0.0022943 | -0.005144 | -0.0013138 | -0.005371 | -0.00011332 | 0.066133 | 0.056285 | -0.0090277 | 0.022469 | -0.0031979 | -0.091553 | 59.8892 | -61.5784 | 60.1135 | -61.2991 | -61.7661 | -61.7752 | 0.004578 | 59.8618 | -61.6425 | 60.0906 | -61.4731 | -61.6058 | -61.6882 | -0.01831 | -0.12817 | 0.09613 | 0.26093 | -0.21515 | -0.20599 | -0.19684 | -0.18768 | -0.082397 | -0.15564 | 0.073242 | 0.086976 | -0.12817 | -0.045776 | -0.045776 | 0.036621 | 0.27924 | 121.6919 | 0.16937 | 121.7331 | 121.4676 | 121.5042 | 121.4493 | 121.4218 | -121.5958 | -121.6599 | 121.6736 | 121.6507 | 61.4685 | 61.5646
71.2344 | 121.8109 | -61.5555 | 60.0906 | -0.0045011 | 0.0026874 | 0.058554 | 0.057501 | -0.00069646 | -0.0055712 | -3.1996e-05 | 0.00073235 | 0.0041593 | 0.064638 | 0.056713 | -0.0075323 | 0.019692 | -0.0019163 | -0.013733 | 59.9625 | -61.5784 | 60.141 | -61.29 | -61.7569 | -61.7752 | 0.073242 | 59.9304 | -61.6013 | 60.0861 | -61.4685 | -61.6104 | -61.6837 | -0.022888 | -0.12817 | 0.050354 | 0.2655 | -0.21973 | -0.20142 | -0.19684 | -0.17853 | -0.045776 | -0.16022 | -0.004577 | 0.086975 | -0.12817 | -0.054932 | -0.082398 | -0.009156 | 0.28839 | 121.7194 | 0.13275 | 121.6873 | 121.5408 | 121.5317 | 121.5179 | 121.4859 | -121.669 | -121.6919 | 121.6965 | 121.6415 | 61.5417 | 61.6287
72.9062 | 121.8933 | -61.5738 | 59.9991 | -0.0045011 | 0.0041828 | 0.060477 | 0.054724 | 0.0061395 | -0.0059986 | 0.0001816 | -0.005371 | 0.00010048 | 0.066988 | 0.053508 | -0.0064643 | 0.020119 | -0.0019163 | -0.059509 | 59.8526 | -61.5784 | 60.1364 | -61.2946 | -61.7523 | -61.7661 | 0.054932 | 59.8022 | -61.6287 | 60.1135 | -61.4456 | -61.5875 | -61.6699 | -0.004577 | -0.14648 | 0.13733 | 0.27924 | -0.19226 | -0.17853 | -0.18768 | -0.17395 | -0.054931 | -0.19684 | 0.11444 | 0.12817 | -0.09613 | -0.013732 | -0.041199 | 0.041199 | 0.28381 | 121.7148 | 0.1831 | 121.7422 | 121.431 | 121.431 | 121.4264 | 121.376 | -121.5775 | -121.6278 | 121.7102 | 121.6873 | 61.5143 | 61.6287
74.6562 | 121.788 | -61.5784 | 60.0403 | -0.012131 | 0.0033282 | 0.060049 | 0.056006 | 0.0014397 | -0.0040758 | -0.000673 | -0.005371 | 0.0052273 | 0.067842 | 0.05949 | -0.0073187 | 0.019692 | -0.00020725 | -0.1236 | 59.9396 | -61.6287 | 60.022 | -61.4136 | -61.8668 | -61.8851 | -0.059509 | 59.8846 | -61.6516 | 60.0174 | -61.5784 | -61.7065 | -61.7706 | -0.050354 | -0.10071 | -0.01831 | 0.1648 | -0.3067 | -0.28839 | -0.25635 | -0.23804 | -0.073242 | -0.15564 | -0.022888 | 0 | -0.19226 | -0.12817 | -0.11902 | -0.054932 | 0.21515 | 121.6507 | 0.073242 | 121.669 | 121.5683 | 121.5363 | 121.5179 | 121.463 | -121.669 | -121.6919 | 121.6003 | 121.5958 | 61.4548 | 61.5189
76.3906 | 121.8704 | -61.5189 | 60.0677 | -0.0045011 | 0.0014056 | 0.056845 | 0.054937 | 0.00037174 | -0.0047168 | -0.0002456 | -0.0084228 | 0.0028775 | 0.065706 | 0.053081 | -0.011164 | 0.020333 | -0.00084805 | 0.036621 | 59.9258 | -61.5326 | 60.2234 | -61.1801 | -61.6608 | -61.6699 | 0.13733 | 59.9075 | -61.5692 | 60.1593 | -61.377 | -61.5051 | -61.6241 | -0.013733 | -0.14191 | 0.15564 | 0.33874 | -0.15106 | -0.14191 | -0.13733 | -0.12817 | -0.050354 | -0.16022 | 0.091553 | 0.14191 | -0.10529 | 0.013733 | -0.054932 | 0.064087 | 0.35248 | 121.756 | 0.19226 | 121.7285 | 121.4584 | 121.4767 | 121.4447 | 121.4264 | -121.6003 | -121.637 | 121.7422 | 121.6782 | 61.5555 | 61.6562
78.125 | 121.8887 | -61.5097 | 60.0449 | -0.01976 | 0.0016192 | 0.059622 | 0.051733 | -0.0036871 | -0.0059986 | -0.000673 | -0.005371 | 0.00052768 | 0.067202 | 0.054149 | -0.0098823 | 0.020333 | -0.00042085 | 0.027466 | 59.9213 | -61.5326 | 60.2234 | -61.171 | -61.6379 | -61.6516 | 0.16022 | 59.8892 | -61.5463 | 60.1685 | -61.3678 | -61.4914 | -61.6058 | -0.022888 | -0.1236 | 0.17853 | 0.33875 | -0.14191 | -0.12817 | -0.11902 | -0.10529 | -0.036621 | -0.15564 | 0.1236 | 0.14191 | -0.09613 | 0.018311 | -0.059509 | 0.054932 | 0.36163 | 121.756 | 0.17853 | 121.7148 | 121.4539 | 121.4355 | 121.431 | 121.3989 | -121.5775 | -121.5912 | 121.7331 | 121.6782 | 61.5372 | 61.6699
79.7969 | 121.7926 | -61.6013 | 60.0311 | -0.0045011 | 0.0026874 | 0.05834 | 0.057715 | -0.00048286 | -0.0047168 | -0.0064408 | -0.0084228 | 0.0024503 | 0.065279 | 0.063121 | -0.0094549 | 0.020974 | -0.00084805 | -0.013733 | 59.9579 | -61.5692 | 60.1273 | -61.3312 | -61.7798 | -61.8027 | 0.022888 | 59.9121 | -61.647 | 60.0403 | -61.5234 | -61.6882 | -61.7569 | 0.032043 | -0.073242 | 0.09613 | 0.27008 | -0.20142 | -0.17853 | -0.23346 | -0.21057 | -0.045777 | -0.11902 | 0.009155 | 0.07782 | -0.15564 | -0.086975 | -0.10986 | -0.041198 | 0.23804 | 121.6965 | 0.1236 | 121.6873 | 121.5271 | 121.5591 | 121.5591 | 121.5134 | -121.6003 | -121.6782 | 121.7285 | 121.6415 | 61.5875 | 61.6241
81.5469 | 121.7926 | -61.5692 | 60.054 | -0.0045011 | 0.0052508 | 0.05834 | 0.060064 | 0.0031487 | -0.0079212 | 0.0003952 | -0.0084228 | 0.0048001 | 0.067842 | 0.05479 | -0.0071051 | 0.020974 | -0.00042085 | -0.004578 | 59.9442 | -61.5784 | 60.1273 | -61.3174 | -61.7798 | -61.7935 | 0.027466 | 59.9258 | -61.6241 | 60.0494 | -61.5234 | -61.6653 | -61.7386 | -0.009155 | -0.10986 | 0.073242 | 0.25177 | -0.2243 | -0.21057 | -0.21515 | -0.20142 | -0.054932 | -0.12817 | -0.004578 | 0.045777 | -0.16937 | -0.09613 | -0.11444 | -0.041198 | 0.26093 | 121.7056 | 0.10071 | 121.6736 | 121.5225 | 121.55 | 121.5134 | 121.4951 | -121.6324 | -121.6782 | 121.6965 | 121.6187 | 61.5646 | 61.5967
83.2188 | 121.8475 | -61.5326 | 60.0952 | -0.0045011 | -0.00030342 | 0.057059 | 0.054724 | 0.0020807 | -0.0062122 | -0.0030228 | -0.005371 | 0.0028775 | 0.065279 | 0.058208 | -0.0096685 | 0.020974 | -0.0053343 | 0.013733 | 59.8984 | -61.528 | 60.2142 | -61.1984 | -61.6608 | -61.6928 | 0.11902 | 59.903 | -61.5555 | 60.141 | -61.3907 | -61.5097 | -61.6104 | 0.004578 | -0.19684 | 0.11902 | 0.33417 | -0.16022 | -0.12817 | -0.16479 | -0.13275 | -0.022888 | -0.19226 | 0.045776 | 0.14191 | -0.07782 | 0.022888 | -0.054932 | 0.045776 | 0.32959 | 121.7422 | 0.16479 | 121.6965 | 121.4264 | 121.4584 | 121.431 | 121.4355 | -121.6232 | -121.6507 | 121.7468 | 121.6736 | 61.5463 | 61.6516
84.9688 | 121.8658 | -61.5463 | 60.022 | 0.0031279 | -0.00073062 | 0.056845 | 0.053015 | -0.0026191 | -0.0074938 | -0.0011002 | -0.005371 | -0.00032692 | 0.064638 | 0.05009 | -0.0094549 | 0.020333 | -0.0040525 | -0.073242 | 59.8984 | -61.5646 | 60.1227 | -61.2946 | -61.7477 | -61.7432 | 0.027466 | 59.8572 | -61.6013 | 60.1181 | -61.4182 | -61.5372 | -61.6516 | -0.01831 | -0.1236 | 0.10071 | 0.25177 | -0.19684 | -0.20142 | -0.17853 | -0.18311 | -0.054931 | -0.1648 | 0.09613 | 0.12817 | -0.10529 | 0.009156 | -0.050354 | 0.064087 | 0.27008 | 121.6873 | 0.1831 | 121.7194 | 121.463 | 121.4584 | 121.4447 | 121.4035 | -121.5866 | -121.6232 | 121.669 | 121.6644 | 61.4731 | 61.5738
86.7188 | 121.8521 | -61.5143 | 60.0952 | -0.0045011 | 0.0020466 | 0.0577 | 0.055365 | 0.0012261 | -0.0055712 | -0.000673 | -0.005371 | 0.0011685 | 0.063784 | 0.058849 | -0.0083869 | 0.02076 | -0.0019163 | 0.032043 | 59.9487 | -61.5326 | 60.2142 | -61.2213 | -61.6425 | -61.6699 | 0.11902 | 59.9213 | -61.5601 | 60.1364 | -61.4044 | -61.5326 | -61.647 | -0.018311 | -0.14649 | 0.11902 | 0.29297 | -0.15564 | -0.12817 | -0.13733 | -0.10986 | -0.045777 | -0.17395 | 0.041199 | 0.10986 | -0.13275 | -0.018311 | -0.086975 | 0.027466 | 0.31128 | 121.7468 | 0.15564 | 121.6965 | 121.4813 | 121.4813 | 121.463 | 121.4355 | -121.6278 | -121.6553 | 121.7285 | 121.6507 | 61.5463 | 61.6333
88.4688 | 121.7743 | -61.6013 | 60.0266 | -0.0045011 | 0.0039692 | 0.058127 | 0.059424 | -0.00091006 | -0.006853 | -0.001741 | -0.0084228 | 0.0041593 | 0.065279 | 0.056926 | -0.0071051 | 0.020333 | -0.0017027 | -0.13275 | 59.9121 | -61.6196 | 60.0082 | -61.4365 | -61.8805 | -61.8805 | -0.07782 | 59.8755 | -61.6562 | 60.0128 | -61.5875 | -61.7249 | -61.7798 | -0.018311 | -0.11444 | -0.01831 | 0.16479 | -0.27924 | -0.27924 | -0.26093 | -0.26093 | -0.054932 | -0.15106 | -0.013733 | 0.013733 | -0.17853 | -0.1236 | -0.1236 | -0.068665 | 0.18311 | 121.6278 | 0.068665 | 121.669 | 121.5317 | 121.5317 | 121.5134 | 121.4767 | -121.6461 | -121.6827 | 121.6095 | 121.6141 | 61.4685 | 61.5234
90.2031 | 121.756 | -61.5326 | 60.1181 | -0.012131 | 0.0020466 | 0.056204 | 0.055151 | -5.5462e-05 | -0.0066394 | 0.002745 | -0.005371 | 0.0022367 | 0.067842 | 0.056499 | -0.0079597 | 0.021187 | -0.0059751 | -0.041199 | 59.9854 | -61.5555 | 60.1089 | -61.3312 | -61.7523 | -61.7752 | 0.004578 | 59.9716 | -61.5738 | 60.054 | -61.496 | -61.6287 | -61.7157 | -0.022888 | -0.13275 | -0.009155 | 0.20142 | -0.24262 | -0.21973 | -0.21973 | -0.19684 | -0.041199 | -0.14648 | -0.064087 | 0.036621 | -0.18311 | -0.09613 | -0.14191 | -0.054931 | 0.2243 | 121.6644 | 0.07782 | 121.6278 | 121.5408 | 121.5454 | 121.5179 | 121.5042 | -121.6736 | -121.6919 | 121.6415 | 121.5866 | 61.4914 | 61.5372
91.9062 | 121.8567 | -61.5097 | 60.0952 | 0.0031279 | 0.00097838 | 0.056845 | 0.054937 | -0.0043281 | -0.0079212 | -0.0004592 | -0.0023192 | -0.00054052 | 0.069551 | 0.060131 | -0.0079597 | 0.02076 | -0.00042085 | 0.018311 | 59.935 | -61.5555 | 60.2142 | -61.203 | -61.6608 | -61.6745 | 0.11902 | 59.8892 | -61.5555 | 60.1318 | -61.3953 | -61.5143 | -61.6241 | -0.045776 | -0.16022 | 0.11902 | 0.3067 | -0.1648 | -0.15106 | -0.11902 | -0.10529 | -0.045776 | -0.20599 | 0.036621 | 0.11444 | -0.11444 | -0.004577 | -0.068665 | 0.041199 | 0.35248 | 121.7697 | 0.16022 | 121.6873 | 121.4905 | 121.4447 | 121.4447 | 121.3989 | -121.6507 | -121.6507 | 121.7239 | 121.6415 | 61.528 | 61.6287
93.6406 | 121.9025 | -61.5051 | 60.0403 | -0.012131 | -0.00094422 | 0.058127 | 0.055578 | -0.0019781 | -0.0064258 | -0.0015274 | -0.0023192 | 0.00052768 | 0.063784 | 0.058422 | -0.0096685 | 0.022042 | -0.0027707 | 0.004578 | 59.9213 | -61.5234 | 60.2554 | -61.1526 | -61.6379 | -61.6516 | 0.16022 | 59.8846 | -61.5555 | 60.173 | -61.3541 | -61.4822 | -61.6104 | -0.01831 | -0.11902 | 0.21515 | 0.35248 | -0.14648 | -0.13275 | -0.12817 | -0.11444 | -0.050354 | -0.15564 | 0.13275 | 0.15106 | -0.10529 | 0.022888 | -0.054932 | 0.073242 | 0.37079 | 121.7789 | 0.20142 | 121.7285 | 121.4447 | 121.4401 | 121.4264 | 121.3898 | -121.5637 | -121.5958 | 121.7606 | 121.6782 | 61.5097 | 61.6653
95.3125 | 121.9025 | -61.4822 | 60.054 | -0.0045011 | 0.001192 | 0.054922 | 0.05152 | -0.0045417 | -0.0062122 | -0.000673 | -0.0084228 | 0.0024503 | 0.067842 | 0.058849 | -0.010523 | 0.019905 | -0.0021299 | 0.013733 | 59.9533 | -61.5509 | 60.228 | -61.1755 | -61.6425 | -61.6653 | 0.17395 | 59.9258 | -61.5738 | 60.1685 | -61.3586 | -61.496 | -61.5967 | -0.068664 | -0.10071 | 0.17395 | 0.3067 | -0.1831 | -0.16022 | -0.11444 | -0.091553 | -0.091553 | -0.12817 | 0.11444 | 0.1236 | -0.11444 | -0.013733 | -0.022888 | 0.07782 | 0.37537 | 121.7789 | 0.21515 | 121.7422 | 121.5042 | 121.4996 | 121.4355 | 121.4081 | -121.6049 | -121.6278 | 121.7102 | 121.6507 | 61.496 | 61.6562
97.0469 | 121.8613 | -61.5921 | 59.9854 | -0.01976 | 0.00461 | 0.05834 | 0.057928 | 0.0037897 | -0.0077074 | -0.0025956 | -0.005371 | 0.0022367 | 0.066347 | 0.058422 | -0.0096685 | 0.022469 | -0.0025571 | -0.10986 | 59.9121 | -61.5921 | 60.0494 | -61.3953 | -61.8439 | -61.8439 | -0.027466 | 59.8663 | -61.6516 | 60.0723 | -61.5005 | -61.6608 | -61.7065 | 0 | -0.073243 | 0.064086 | 0.19684 | -0.25177 | -0.25177 | -0.25177 | -0.25177 | -0.059509 | -0.11902 | 0.086975 | 0.091553 | -0.11444 | -0.068665 | -0.054932 | -0.009156 | 0.19684 | 121.6415 | 0.15106 | 121.7239 | 121.5042 | 121.5179 | 121.5042 | 121.4584 | -121.5775 | -121.637 | 121.6415 | 121.6644 | 61.4822 | 61.5646
98.7969 | 121.8658 | -61.5784 | 59.9899 | -0.012131 | 0.00461 | 0.057913 | 0.058569 | 0.0025079 | -0.0064258 | -0.0025956 | -0.005371 | 0.0041593 | 0.066133 | 0.058635 | -0.0077459 | 0.020546 | -0.00084805 | -0.12817 | 59.903 | -61.6104 | 60.0586 | -61.3861 | -61.8484 | -61.8393 | -0.013733 | 59.8572 | -61.6425 | 60.0815 | -61.496 | -61.6562 | -61.6928 | -0.032044 | -0.086975 | 0.068665 | 0.19226 | -0.26093 | -0.27008 | -0.22888 | -0.23804 | -0.064087 | -0.13275 | 0.091553 | 0.082397 | -0.11444 | -0.07782 | -0.050354 | -0.013733 | 0.22431 | 121.669 | 0.14648 | 121.7239 | 121.5134 | 121.4996 | 121.4813 | 121.4355 | -121.6003 | -121.6324 | 121.637 | 121.6599 | 61.4502 | 61.5646
100.5469 | 121.8979 | -61.5738 | 59.9579 | -0.012131 | 0.0014056 | 0.058554 | 0.055578 | -0.0024055 | -0.0049304 | -0.002382 | -0.005371 | 0.0022367 | 0.064424 | 0.055217 | -0.0062507 | 0.022042 | -0.0031979 | -0.050354 | 59.8618 | -61.5829 | 60.1501 | -61.29 | -61.7706 | -61.7752 | 0.050354 | 59.8114 | -61.647 | 60.1089 | -61.4548 | -61.6058 | -61.6653 | -0.009155 | -0.096131 | 0.19226 | 0.28381 | -0.20142 | -0.19684 | -0.19226 | -0.18768 | -0.073242 | -0.14649 | 0.15106 | 0.11902 | -0.091552 | -0.032043 | -0.01831 | 0.041199 | 0.29297 | 121.7331 | 0.19226 | 121.756 | 121.4447 | 121.4584 | 121.4355 | 121.3852 | -121.5408 | -121.6049 | 121.7239 | 121.6827 | 61.5234 | 61.6241
102.2969 | 121.8201 | -61.5417 | 60.0586 | -0.0045011 | 0.0035418 | 0.059622 | 0.058142 | 0.0029351 | -0.008562 | 0.0008224 | -0.005371 | 0.0018095 | 0.064852 | 0.059276 | -0.0086005 | 0.019905 | -0.00063445 | 0 | 59.9808 | -61.5463 | 60.1456 | -61.3037 | -61.7569 | -61.7798 | 0.068665 | 59.9075 | -61.5967 | 60.0861 | -61.4639 | -61.6333 | -61.6974 | -0.004578 | -0.07782 | 0.086975 | 0.23804 | -0.23804 | -0.21515 | -0.23346 | -0.21057 | -0.054932 | -0.15106 | 0.027466 | 0.07782 | -0.15564 | -0.091553 | -0.10071 | -0.036621 | 0.24262 | 121.6919 | 0.13275 | 121.6827 | 121.5271 | 121.5042 | 121.5225 | 121.4493 | -121.6049 | -121.6553 | 121.6873 | 121.6278 | 61.5417 | 61.6104
103.9688 | 121.843 | -61.5555 | 60.0128 | -0.012131 | 0.0043964 | 0.058981 | 0.052588 | 0.0048577 | -0.0055712 | -0.0002456 | 0.00073235 | 0.0015957 | 0.065493 | 0.056072 | -0.0094549 | 0.021401 | -0.0023435 | -0.10529 | 59.903 | -61.5692 | 60.1181 | -61.3129 | -61.7477 | -61.7706 | 0 | 59.8709 | -61.6241 | 60.0677 | -61.4777 | -61.6058 | -61.6974 | -0.013733 | -0.10986 | 0.10529 | 0.24262 | -0.21515 | -0.19226 | -0.20142 | -0.17853 | -0.068665 | -0.14191 | 0.054932 | 0.07782 | -0.14191 | -0.050354 | -0.073242 | 0.018311 | 0.25635 | 121.6873 | 0.14649 | 121.6919 | 121.4722 | 121.4951 | 121.4584 | 121.4264 | -121.582 | -121.637 | 121.6736 | 121.6232 | 61.4502 | 61.5555
105.7031 | 121.8613 | -61.5463 | 60.0357 | -0.012131 | 0.0033282 | 0.059409 | 0.055792 | 0.0010125 | -0.0049304 | -0.0021682 | -0.0084228 | 0.0015957 | 0.064638 | 0.065257 | -0.0096685 | 0.022896 | 0.00086095 | -0.086975 | 59.8938 | -61.6013 | 60.1135 | -61.29 | -61.7661 | -61.7615 | 0.032043 | 59.8618 | -61.5921 | 60.0952 | -61.4777 | -61.6013 | -61.6791 | -0.054931 | -0.14191 | 0.077819 | 0.25635 | -0.21515 | -0.21973 | -0.16022 | -0.1648 | -0.045776 | -0.17395 | 0.059509 | 0.068665 | -0.13275 | -0.054931 | -0.086975 | -0.009155 | 0.31128 | 121.7148 | 0.11444 | 121.6873 | 121.4951 | 121.4539 | 121.4401 | 121.4081 | -121.637 | -121.6278 | 121.6599 | 121.6415 | 61.4594 | 61.5784
107.375 | 121.8842 | -61.5692 | 59.9808 | -0.0045011 | 0.001833 | 0.058768 | 0.056433 | 0.0010125 | -0.005144 | -0.0019546 | -0.005371 | -0.00011332 | 0.065065 | 0.056713 | -0.0064643 | 0.018837 | -0.0017027 | -0.07782 | 59.8663 | -61.5967 | 60.1501 | -61.3037 | -61.7523 | -61.7706 | 0.054932 | 59.8343 | -61.6562 | 60.0906 | -61.4639 | -61.6287 | -61.6608 | -0.027466 | -0.11444 | 0.16937 | 0.2655 | -0.20142 | -0.1831 | -0.17395 | -0.15564 | -0.086975 | -0.14648 | 0.10986 | 0.10529 | -0.091553 | -0.059509 | -0.004578 | 0.027466 | 0.29297 | 121.7468 | 0.19226 | 121.7468 | 121.463 | 121.4905 | 121.4355 | 121.4035 | -121.5775 | -121.637 | 121.7194 | 121.6599 | 61.4914 | 61.6241
109.125 | 121.8842 | -61.5601 | 59.9762 | 0.0031279 | 0.0022602 | 0.057913 | 0.05451 | 0.00015814 | -0.0036486 | -0.0038772 | -0.005371 | 0.0018095 | 0.064638 | 0.059703 | -0.0081733 | 0.021828 | -0.0012753 | -0.07782 | 59.8434 | -61.6058 | 60.141 | -61.2671 | -61.7569 | -61.7661 | 0.07782 | 59.816 | -61.6516 | 60.1089 | -61.4502 | -61.5921 | -61.6791 | -0.045776 | -0.13275 | 0.16479 | 0.29297 | -0.20599 | -0.19684 | -0.16022 | -0.15106 | -0.091552 | -0.16022 | 0.13275 | 0.10986 | -0.11902 | -0.032043 | -0.027466 | 0.059509 | 0.33874 | 121.7468 | 0.20142 | 121.7606 | 121.4493 | 121.4676 | 121.4035 | 121.376 | -121.582 | -121.6278 | 121.7011 | 121.669 | 61.4822 | 61.6379
110.875 | 121.7834 | -61.5738 | 60.0311 | -0.0045011 | 0.002901 | 0.058981 | 0.057715 | -5.5462e-05 | -0.0055712 | -0.0013138 | -0.005371 | 0.0026639 | 0.065493 | 0.060771 | -0.0081733 | 0.019478 | -0.00042085 | -0.009155 | 59.9716 | -61.5784 | 60.1089 | -61.3358 | -61.7981 | -61.821 | 0.009155 | 59.9075 | -61.615 | 60.0449 | -61.5509 | -61.6928 | -61.7661 | -0.004577 | -0.059509 | 0.07782 | 0.23804 | -0.24719 | -0.2243 | -0.24262 | -0.21973 | -0.041198 | -0.1236 | 0.013733 | 0.022889 | -0.19226 | -0.11902 | -0.15106 | -0.07782 | 0.24262 | 121.6873 | 0.064087 | 121.6599 | 121.55 | 121.5225 | 121.5454 | 121.4813 | -121.6095 | -121.6461 | 121.6827 | 121.6187 | 61.5646 | 61.5829
112.625 | 121.8796 | -61.5097 | 60.0586 | 0.0031279 | 0.0026874 | 0.058768 | 0.055151 | 0.0010125 | -0.0087756 | -0.0040908 | -0.0084228 | 0.00052768 | 0.065706 | 0.061412 | -0.0090277 | 0.020333 | -0.00084805 | 0.036621 | 59.935 | -61.5372 | 60.228 | -61.1847 | -61.647 | -61.6699 | 0.14191 | 59.9167 | -61.5646 | 60.1547 | -61.3861 | -61.496 | -61.615 | -0.027465 | -0.1236 | 0.16937 | 0.32501 | -0.16022 | -0.13733 | -0.13275 | -0.10986 | -0.054931 | -0.14191 | 0.09613 | 0.1236 | -0.10529 | 0.013733 | -0.050354 | 0.068664 | 0.35248 | 121.7651 | 0.17853 | 121.7194 | 121.4722 | 121.4813 | 121.4447 | 121.4264 | -121.5958 | -121.6232 | 121.7377 | 121.6644 | 61.5463 | 61.6516
114.375 | 121.7514 | -61.615 | 60.0357 | -0.012131 | 0.0065326 | 0.058127 | 0.060278 | 0.0044305 | -0.0038622 | 0.0003952 | -0.0084228 | 0.0033047 | 0.066133 | 0.05714 | -0.0064643 | 0.020119 | -0.0031979 | -0.086975 | 59.9258 | -61.6013 | 60.0357 | -61.4227 | -61.8805 | -61.8851 | -0.082397 | 59.903 | -61.6425 | 59.9808 | -61.6058 | -61.7523 | -61.7798 | 0.013733 | -0.10986 | 0 | 0.19226 | -0.27008 | -0.2655 | -0.28381 | -0.27924 | -0.027466 | -0.13275 | -0.054932 | 0.009155 | -0.16479 | -0.13733 | -0.13733 | -0.10986 | 0.17853 | 121.637 | 0.036621 | 121.6232 | 121.5271 | 121.5454 | 121.5408 | 121.5179 | -121.637 | -121.6782 | 121.6507 | 121.5958 | 61.528 | 61.5326
116.0469 | 121.907 | -61.5738 | 59.9625 | -0.012131 | 0.00461 | 0.061331 | 0.055578 | 0.00015814 | -0.0053576 | 0.0003952 | -0.005371 | 0.0024503 | 0.06592 | 0.056926 | -0.0068915 | 0.020974 | -0.00084805 | -0.068665 | 59.8892 | -61.6013 | 60.1318 | -61.2854 | -61.7706 | -61.7706 | 0.041199 | 59.816 | -61.6653 | 60.1181 | -61.4548 | -61.5967 | -61.6745 | -0.027465 | -0.073242 | 0.16937 | 0.28839 | -0.19684 | -0.19684 | -0.16937 | -0.16937 | -0.091552 | -0.14648 | 0.15564 | 0.11902 | -0.10071 | -0.022888 | -0.009156 | 0.068664 | 0.31586 | 121.7331 | 0.21057 | 121.7834 | 121.4905 | 121.4813 | 121.463 | 121.3898 | -121.5637 | -121.6278 | 121.7056 | 121.6919 | 61.5051 | 61.615
117.7812 | 121.8567 | -61.5509 | 60.022 | -0.012131 | 0.0024738 | 0.058554 | 0.055365 | 0.0014397 | -0.005144 | -0.0028092 | -0.0084228 | 0.0011685 | 0.064424 | 0.054363 | -0.0075323 | 0.019905 | -0.0027707 | -0.082397 | 59.8846 | -61.6104 | 60.1273 | -61.29 | -61.7569 | -61.7752 | 0.045776 | 59.848 | -61.6241 | 60.0861 | -61.4685 | -61.6013 | -61.6837 | -0.05951 | -0.13733 | 0.10528 | 0.26093 | -0.22431 | -0.20599 | -0.16479 | -0.14648 | -0.073243 | -0.17395 | 0.064087 | 0.082397 | -0.13275 | -0.050354 | -0.059509 | 0.022889 | 0.32044 | 121.7377 | 0.15564 | 121.7102 | 121.4951 | 121.4722 | 121.4355 | 121.3989 | -121.6324 | -121.6461 | 121.6782 | 121.637 | 61.4685 | 61.5967
119.5312 | 121.7743 | -61.5921 | 60.0082 | -0.012131 | 0.0037556 | 0.06069 | 0.058142 | 0.0042169 | -0.0049304 | -0.0002456 | -0.0023192 | 0.0028775 | 0.065279 | 0.063549 | -0.0064643 | 0.01841 | -0.0053343 | -0.086975 | 59.9258 | -61.6058 | 60.0494 | -61.3998 | -61.8622 | -61.8668 | -0.07782 | 59.8892 | -61.6379 | 60.0082 | -61.5829 | -61.7294 | -61.7844 | -0.013733 | -0.082398 | 0.041198 | 0.19226 | -0.27466 | -0.27008 | -0.26093 | -0.25635 | -0.045776 | -0.11902 | 0 | 0.009155 | -0.19226 | -0.13733 | -0.14648 | -0.091553 | 0.20599 | 121.6553 | 0.054931 | 121.6461 | 121.5317 | 121.5271 | 121.5179 | 121.4813 | -121.6141 | -121.6461 | 121.6415 | 121.6003 | 61.5051 | 61.5143
121.2031 | 121.8155 | -61.5509 | 60.0586 | 0.0031279 | 0.0033282 | 0.057272 | 0.056006 | 0.0022943 | -0.0074938 | 0.0003952 | -0.0023192 | 0.0011685 | 0.066774 | 0.059062 | -0.0096685 | 0.018837 | -0.0046933 | -0.009155 | 59.9716 | -61.5646 | 60.1318 | -61.3037 | -61.7432 | -61.7889 | 0.068665 | 59.9258 | -61.5967 | 60.0861 | -61.4685 | -61.6287 | -61.6928 | -0.013733 | -0.086975 | 0.073242 | 0.24719 | -0.23804 | -0.19226 | -0.2243 | -0.17853 | -0.045777 | -0.13275 | 0.027466 | 0.082397 | -0.14191 | -0.07782 | -0.09613 | -0.032043 | 0.26093 | 121.6965 | 0.12817 | 121.6827 | 121.5363 | 121.5225 | 121.5225 | 121.4767 | -121.6232 | -121.6553 | 121.6827 | 121.637 | 61.5417 | 61.6196
122.9531 | 121.8155 | -61.5509 | 60.0586 | -0.0045011 | 0.0033282 | 0.059622 | 0.055792 | 0.0035761 | -0.0062122 | -0.000673 | -0.005371 | 0.0026639 | 0.066347 | 0.058849 | -0.0056097 | 0.021187 | -0.00020725 | -0.018311 | 59.967 | -61.5601 | 60.1364 | -61.2854 | -61.7569 | -61.7844 | 0.059509 | 59.9075 | -61.6058 | 60.0906 | -61.4914 | -61.6425 | -61.7111 | -0.009156 | -0.091553 | 0.07782 | 0.2655 | -0.23346 | -0.20599 | -0.2243 | -0.19684 | -0.054932 | -0.15106 | 0.032043 | 0.059509 | -0.16022 | -0.091553 | -0.10529 | -0.036621 | 0.27466 | 121.6965 | 0.11444 | 121.6965 | 121.5271 | 121.5134 | 121.5179 | 121.4584 | -121.6187 | -121.6644 | 121.6873 | 121.6415 | 61.5326 | 61.6104
124.7031 | 121.7926 | -61.5234 | 60.0952 | -0.012131 | -0.00094422 | 0.055563 | 0.053015 | 0.00015814 | -0.0059986 | -0.0011002 | -0.011475 | 0.00074128 | 0.068056 | 0.053081 | -0.0079597 | 0.020333 | -0.0042661 | 0.004578 | 59.967 | -61.5417 | 60.173 | -61.2534 | -61.6928 | -61.734 | 0.050354 | 59.935 | -61.5738 | 60.0769 | -61.4685 | -61.5967 | -61.7065 | -0.018311 | -0.12817 | 0.07782 | 0.27008 | -0.21057 | -0.16937 | -0.19226 | -0.15106 | -0.050355 | -0.16022 | -0.018311 | 0.054931 | -0.18311 | -0.073243 | -0.13275 | -0.022888 | 0.28839 | 121.7148 | 0.10529 | 121.6507 | 121.5088 | 121.5088 | 121.4905 | 121.4584 | -121.637 | -121.669 | 121.6965 | 121.6003 | 61.528 | 61.5738
126.375 | 121.8201 | -61.5372 | 60.0403 | -0.012131 | 0.0024738 | 0.058981 | 0.055365 | -0.0017645 | -0.0062122 | -0.0002456 | -0.005371 | 0.0037321 | 0.067629 | 0.056926 | -0.0092413 | 0.020546 | 0.00021995 | 0.009155 | 59.9442 | -61.5692 | 60.1318 | -61.2946 | -61.7523 | -61.7889 | 0.059509 | 59.9258 | -61.615 | 60.0815 | -61.4594 | -61.6241 | -61.6882 | -0.032044 | -0.09613 | 0.091553 | 0.24261 | -0.25177 | -0.21515 | -0.21973 | -0.1831 | -0.07782 | -0.11444 | 0.041199 | 0.077819 | -0.15106 | -0.086976 | -0.073242 | -0.009156 | 0.27466 | 121.7011 | 0.15564 | 121.6965 | 121.5134 | 121.5408 | 121.4813 | 121.463 | -121.6095 | -121.6553 | 121.669 | 121.6187 | 61.5463 | 61.5967
128.1094 | 121.788 | -61.5234 | 60.1318 | -0.01976 | 0.0014056 | 0.057913 | 0.056219 | -0.00091006 | -0.006853 | -0.0021682 | -0.005371 | 0.0024503 | 0.068483 | 0.061412 | -0.0088141 | 0.022042 | 0.0017153 | -0.032043 | 59.9991 | -61.5417 | 60.0998 | -61.3358 | -61.7706 | -61.7935 | 0.004578 | 59.9487 | -61.6058 | 60.0677 | -61.4822 | -61.6196 | -61.6928 | -0.018311 | -0.13275 | -0.032044 | 0.18768 | -0.27008 | -0.24719 | -0.25177 | -0.22888 | -0.082398 | -0.18311 | -0.064087 | 0.041198 | -0.16937 | -0.096131 | -0.086975 | -0.013733 | 0.20599 | 121.6415 | 0.1236 | 121.6736 | 121.5408 | 121.5546 | 121.5225 | 121.4722 | -121.6736 | -121.7377 | 121.6232 | 121.5912 | 61.4914 | 61.528
129.8438 | 121.7606 | -61.5875 | 60.022 | -0.012131 | 0.0041828 | 0.056418 | 0.057287 | 0.00015814 | -0.0038622 | -0.0025956 | -0.0023192 | 0.0041593 | 0.065279 | 0.058849 | -0.0079597 | 0.021401 | -0.0036253 | -0.07782 | 59.9442 | -61.5921 | 60.0677 | -61.3861 | -61.8576 | -61.8713 | -0.07782 | 59.8984 | -61.6425 | 60.0037 | -61.5692 | -61.7294 | -61.7844 | -0.004578 | -0.07782 | 0.045776 | 0.20142 | -0.28381 | -0.27008 | -0.27924 | -0.2655 | -0.054932 | -0.1236 | -0.018311 | 0.01831 | -0.19684 | -0.14191 | -0.14191 | -0.086975 | 0.20599 | 121.6599 | 0.073242 | 121.6461 | 121.5363 | 121.5408 | 121.5317 | 121.4859 | -121.6141 | -121.6644 | 121.6553 | 121.5912 | 61.5097 | 61.5097
131.5781 | 121.8018 | -61.5692 | 60.0677 | -0.0045011 | 0.0031146 | 0.061118 | 0.058355 | -5.5462e-05 | -0.0055712 | -0.0025956 | -0.005371 | 0.0026639 | 0.067202 | 0.058422 | -0.0079597 | 0.022255 | -0.0012753 | -0.004578 | 59.9625 | -61.5921 | 60.1318 | -61.2991 | -61.7706 | -61.7935 | 0.064087 | 59.9213 | -61.5829 | 60.0723 | -61.4868 | -61.6425 | -61.7111 | -0.022888 | -0.10529 | 0.064087 | 0.27008 | -0.2243 | -0.20142 | -0.20142 | -0.17853 | -0.013733 | -0.14648 | 0.004578 | 0.082398 | -0.14191 | -0.073242 | -0.12817 | -0.059509 | 0.29297 | 121.7239 | 0.096131 | 121.6553 | 121.5546 | 121.5042 | 121.5317 | 121.4905 | -121.6599 | -121.6507 | 121.7011 | 121.6415 | 61.5646 | 61.6333
133.3125 | 121.7834 | -61.5417 | 60.0815 | 0.0031279 | -0.00051702 | 0.058768 | 0.056006 | -0.0034735 | -0.0081348 | -0.00345 | -0.005371 | 0.0020231 | 0.065065 | 0.049449 | -0.0083869 | 0.019265 | -0.0038389 | 0.018311 | 59.9716 | -61.5463 | 60.1364 | -61.2854 | -61.7111 | -61.7477 | 0.036621 | 59.9533 | -61.5784 | 60.0677 | -61.4639 | -61.6104 | -61.7065 | -0.004578 | -0.10986 | 0.054932 | 0.25635 | -0.20599 | -0.16937 | -0.20142 | -0.16479 | -0.036621 | -0.12817 | -0.013733 | 0.07782 | -0.1648 | -0.068665 | -0.12817 | -0.032044 | 0.26093 | 121.6827 | 0.11444 | 121.6461 | 121.5179 | 121.5317 | 121.5134 | 121.4951 | -121.6278 | -121.6599 | 121.6782 | 121.6095 | 61.5601 | 61.5784
135 | 121.8979 | -61.5509 | 59.9762 | -0.012131 | 0.0026874 | 0.05834 | 0.053228 | 0.0020807 | -0.0040758 | -0.0019546 | -0.0084228 | 0.0041593 | 0.066347 | 0.059276 | -0.0092413 | 0.021401 | -0.0036253 | -0.050354 | 59.8709 | -61.6104 | 60.1273 | -61.3037 | -61.7523 | -61.7615 | 0.064087 | 59.7839 | -61.6196 | 60.1044 | -61.4594 | -61.6104 | -61.6653 | -0.05951 | -0.10529 | 0.15106 | 0.24719 | -0.21057 | -0.20142 | -0.15106 | -0.14191 | -0.068665 | -0.19226 | 0.12817 | 0.091552 | -0.11444 | -0.05951 | -0.045776 | 0.009155 | 0.3067 | 121.7377 | 0.16022 | 121.7239 | 121.4813 | 121.4035 | 121.4218 | 121.3348 | -121.5866 | -121.5958 | 121.6782 | 121.6553 | 61.5005 | 61.615
136.7344 | 121.756 | -61.6013 | 60.0357 | -0.0045011 | 0.0037556 | 0.059195 | 0.057074 | -0.00091006 | -0.0064258 | -0.0021682 | -0.0084228 | 0.0022367 | 0.066347 | 0.053081 | -0.0086005 | 0.019692 | -0.0010617 | -0.091553 | 59.9213 | -61.5921 | 60.0174 | -61.4639 | -61.8851 | -61.8988 | -0.09613 | 59.8892 | -61.6562 | 59.9808 | -61.5967 | -61.7432 | -61.7661 | 0.009155 | -0.11444 | -0.018311 | 0.13733 | -0.29755 | -0.28381 | -0.3067 | -0.29297 | -0.054932 | -0.14648 | -0.054932 | 0.004577 | -0.1648 | -0.14191 | -0.10986 | -0.086975 | 0.12817 | 121.6095 | 0.059509 | 121.637 | 121.5134 | 121.5454 | 121.5225 | 121.4905 | -121.6278 | -121.6919 | 121.6187 | 121.582 | 61.5097 | 61.5051
138.4844 | 121.756 | -61.5189 | 60.141 | -0.0045011 | 0.001192 | 0.057486 | 0.055365 | -0.0030463 | -0.0072802 | 0.0008224 | -0.005371 | 0.0030911 | 0.069124 | 0.05714 | -0.0086005 | 0.018624 | -0.0036253 | -0.036621 | 59.9945 | -61.5692 | 60.1044 | -61.3174 | -61.7432 | -61.7661 | 0.027466 | 59.9396 | -61.5555 | 60.054 | -61.4822 | -61.6333 | -61.6974 | -0.050354 | -0.14648 | -0.036621 | 0.20142 | -0.24719 | -0.2243 | -0.19684 | -0.17395 | -0.036621 | -0.20142 | -0.086975 | 0.036621 | -0.17853 | -0.11444 | -0.14191 | -0.07782 | 0.25177 | 121.6736 | 0.073242 | 121.6095 | 121.5637 | 121.4951 | 121.5134 | 121.4584 | -121.7102 | -121.6965 | 121.6232 | 121.5729 | 61.4822 | 61.5463
140.1719 | 121.9208 | -61.5692 | 59.9762 | -0.012131 | 0.0024738 | 0.057913 | 0.057074 | -0.00048286 | -0.0055712 | -0.0019546 | -0.0084228 | 0.00052768 | 0.063997 | 0.061412 | -0.0096685 | 0.020333 | -0.00020725 | -0.07782 | 59.8618 | -61.5921 | 60.141 | -61.2946 | -61.7706 | -61.7798 | 0.045776 | 59.8022 | -61.6241 | 60.1181 | -61.4502 | -61.5829 | -61.6562 | -0.022888 | -0.11444 | 0.16479 | 0.27466 | -0.21057 | -0.20142 | -0.18768 | -0.17853 | -0.054932 | -0.17395 | 0.14191 | 0.11902 | -0.086975 | -0.013733 | -0.032043 | 0.041199 | 0.29755 | 121.7331 | 0.17395 | 121.7422 | 121.4539 | 121.4264 | 121.431 | 121.3715 | -121.5683 | -121.6003 | 121.7102 | 121.6873 | 61.4914 | 61.615
141.9219 | 121.756 | -61.5829 | 60.0449 | -0.012131 | 0.0073872 | 0.05834 | 0.057501 | 0.00058534 | -0.0083484 | -0.0008866 | -0.0023192 | 0.0035183 | 0.065279 | 0.061199 | -0.0062507 | 0.019265 | -0.0036253 | -0.041199 | 59.9442 | -61.5967 | 60.0677 | -61.3632 | -61.8439 | -61.8484 | -0.022888 | 59.9121 | -61.6104 | 60.0037 | -61.5601 | -61.7157 | -61.7661 | -0.013733 | -0.10071 | 0.022888 | 0.21973 | -0.2655 | -0.26093 | -0.25177 | -0.24719 | -0.027466 | -0.13275 | -0.041199 | 0.022888 | -0.18311 | -0.13275 | -0.15564 | -0.10529 | 0.23346 | 121.6644 | 0.050354 | 121.6141 | 121.5408 | 121.5225 | 121.5271 | 121.4951 | -121.6415 | -121.6553 | 121.6507 | 121.5866 | 61.5417 | 61.5601
143.6562 | 121.9162 | -61.5189 | 60.0403 | -0.012131 | -0.0017986 | 0.060049 | 0.053869 | 0.0014397 | -0.0062122 | -0.0043046 | -0.005371 | -0.00011332 | 0.066774 | 0.050945 | -0.0088141 | 0.019051 | -0.00084805 | 0.004578 | 59.903 | -61.5417 | 60.2051 | -61.1664 | -61.6379 | -61.6608 | 0.18768 | 59.8663 | -61.5829 | 60.1685 | -61.3358 | -61.4594 | -61.5692 | -0.022888 | -0.13733 | 0.16479 | 0.35248 | -0.14191 | -0.11902 | -0.11902 | -0.09613 | -0.064087 | -0.17395 | 0.12817 | 0.18311 | -0.050354 | 0.059509 | 0.013733 | 0.1236 | 0.37537 | 121.7468 | 0.24719 | 121.7514 | 121.4447 | 121.4493 | 121.4218 | 121.3852 | -121.582 | -121.6232 | 121.7239 | 121.6873 | 61.5234 | 61.7065
145.3906 | 121.8979 | -61.5692 | 59.9579 | -0.012131 | 0.0058918 | 0.058554 | 0.057715 | 0.00015814 | -0.0066394 | -0.000673 | -0.005371 | 0.0022367 | 0.065065 | 0.065471 | -0.010737 | 0.018837 | -0.0017027 | -0.064087 | 59.8846 | -61.6241 | 60.1364 | -61.3037 | -61.7569 | -61.7706 | 0.050354 | 59.8068 | -61.6196 | 60.1044 | -61.4685 | -61.615 | -61.6562 | -0.054932 | -0.073242 | 0.17853 | 0.2655 | -0.20142 | -0.18768 | -0.14648 | -0.13275 | -0.050354 | -0.15106 | 0.14648 | 0.10071 | -0.086975 | -0.045776 | -0.036621 | 0.004578 | 0.32044 | 121.7606 | 0.15106 | 121.7239 | 121.5088 | 121.4264 | 121.4539 | 121.376 | -121.582 | -121.5775 | 121.7056 | 121.6736 | 61.5051 | 61.6196
147.125 | 121.7789 | -61.6013 | 60.022 | -0.01976 | 0.0026874 | 0.058127 | 0.056646 | 0.0046441 | -0.0066394 | -0.0002456 | 0.00073235 | 0.0033047 | 0.066988 | 0.067607 | -0.0092413 | 0.019265 | -0.00063445 | -0.11902 | 59.935 | -61.6196 | 60.0128 | -61.4273 | -61.8668 | -61.8713 | -0.064087 | 59.8846 | -61.6608 | 60.0174 | -61.5646 | -61.7111 | -61.7523 | -0.018311 | -0.086975 | -0.009156 | 0.17395 | -0.27008 | -0.2655 | -0.25177 | -0.24719 | -0.05951 | -0.13733 | -0.004578 | 0.036621 | -0.15106 | -0.10986 | -0.091552 | -0.050354 | 0.19226 | 121.6324 | 0.096131 | 121.6782 | 121.5546 | 121.5454 | 121.5363 | 121.4859 | -121.6415 | -121.6827 | 121.6141 | 121.6187 | 61.4822 | 61.5372
148.7969 | 121.8521 | -61.5555 | 60.0037 | -0.012131 | 0.0037556 | 0.058768 | 0.055151 | -0.00026906 | -0.0047168 | -0.0013138 | -0.005371 | 0.00095488 | 0.067629 | 0.051799 | -0.0098823 | 0.019051 | -0.00042085 | -0.082397 | 59.8984 | -61.5601 | 60.1135 | -61.3037 | -61.7752 | -61.7615 | 0.041199 | 59.8526 | -61.6196 | 60.0769 | -61.4777 | -61.6013 | -61.6791 | -0.004578 | -0.10529 | 0.10986 | 0.25177 | -0.20599 | -0.21973 | -0.20142 | -0.21515 | -0.064087 | -0.15106 | 0.073242 | 0.07782 | -0.1236 | -0.045776 | -0.059509 | 0.018311 | 0.25635 | 121.6736 | 0.14191 | 121.6965 | 121.4584 | 121.4722 | 121.4539 | 121.4081 | -121.5637 | -121.6232 | 121.669 | 121.6324 | 61.4731 | 61.5967
150.5469 | 121.7834 | -61.5326 | 60.0952 | -0.012131 | 0.0024738 | 0.057913 | 0.055151 | 0.0012261 | -0.0059986 | -0.0030228 | -0.005371 | 0.00052768 | 0.067415 | 0.055004 | -0.011378 | 0.019478 | 0.00021995 | 0.009155 | 59.9579 | -61.5372 | 60.1639 | -61.2534 | -61.6928 | -61.7203 | 0.073242 | 59.9533 | -61.5463 | 60.0769 | -61.4639 | -61.5967 | -61.7065 | -0.004577 | -0.13733 | 0.068664 | 0.27924 | -0.18768 | -0.16022 | -0.18311 | -0.15564 | -0.013733 | -0.14191 | -0.018311 | 0.068665 | -0.17395 | -0.064087 | -0.16022 | -0.050354 | 0.28381 | 121.701 | 0.082398 | 121.6232 | 121.4951 | 121.4996 | 121.4905 | 121.4859 | -121.6324 | -121.6415 | 121.6965 | 121.6095 | 61.5417 | 61.6058
152.2969 | 121.9116 | -61.5051 | 60.0449 | -0.012131 | 0.00012398 | 0.058554 | 0.054937 | -0.0030463 | -0.0072802 | -0.0013138 | -0.005371 | 0.0020231 | 0.066988 | 0.061199 | -0.0083869 | 0.021187 | -0.0034117 | 0.004578 | 59.9121 | -61.5417 | 60.1959 | -61.1984 | -61.6608 | -61.6562 | 0.16479 | 59.8572 | -61.5555 | 60.1685 | -61.3541 | -61.4868 | -61.6058 | -0.036621 | -0.13275 | 0.15106 | 0.3067 | -0.15106 | -0.15564 | -0.11444 | -0.11902 | -0.050354 | -0.18768 | 0.1236 | 0.15106 | -0.10071 | 0.018311 | -0.050354 | 0.068665 | 0.34332 | 121.7377 | 0.20142 | 121.7239 | 121.4539 | 121.4127 | 121.4172 | 121.3623 | -121.5866 | -121.6003 | 121.7011 | 121.6736 | 61.5097 | 61.6699
154.0469 | 121.7651 | -61.5326 | 60.1089 | -0.01976 | 0.0014056 | 0.056631 | 0.05451 | 0.0031487 | -0.0089892 | -0.0002456 | -0.005371 | 0.0018095 | 0.065493 | 0.065044 | -0.0094549 | 0.020333 | -0.0012753 | -0.045776 | 59.967 | -61.5646 | 60.1089 | -61.3174 | -61.7432 | -61.7752 | 0.013733 | 59.9762 | -61.5875 | 60.0586 | -61.4777 | -61.6104 | -61.7065 | -0.032043 | -0.14191 | 0 | 0.21515 | -0.24262 | -0.21057 | -0.21057 | -0.17853 | -0.054931 | -0.13275 | -0.050354 | 0.054932 | -0.17395 | -0.07782 | -0.11902 | -0.022889 | 0.24719 | 121.6736 | 0.10986 | 121.6461 | 121.5317 | 121.5637 | 121.4996 | 121.5088 | -121.6736 | -121.6965 | 121.6415 | 121.5912 | 61.4868 | 61.5463
155.7344 | 121.8338 | -61.6013 | 59.9991 | -0.012131 | 0.0024738 | 0.057272 | 0.055578 | -0.0013373 | -0.005144 | -0.0030228 | -0.005371 | 0.0028775 | 0.065279 | 0.060985 | -0.0081733 | 0.019905 | -0.00084805 | -0.11444 | 59.9213 | -61.6196 | 60.0449 | -61.3953 | -61.8668 | -61.8759 | -0.054932 | 59.8526 | -61.6516 | 60.0494 | -61.528 | -61.6653 | -61.7249 | -0.018311 | -0.077819 | 0.045777 | 0.20599 | -0.27466 | -0.2655 | -0.25635 | -0.24719 | -0.050354 | -0.14648 | 0.050354 | 0.073242 | -0.1236 | -0.064087 | -0.073243 | -0.013733 | 0.2243 | 121.6644 | 0.1236 | 121.701 | 121.5408 | 121.5042 | 121.5225 | 121.4539 | -121.6187 | -121.6507 | 121.6461 | 121.6507 | 61.4868 | 61.5463
157.4688 | 121.7651 | -61.5509 | 60.1227 | -0.012131 | 0.00012398 | 0.0577 | 0.055792 | 0.00015814 | -0.0079212 | -0.0013138 | -0.0023192 | 0.0015957 | 0.066561 | 0.055858 | -0.0092413 | 0.018837 | -0.0042661 | 0.004578 | 59.9579 | -61.5417 | 60.1364 | -61.3083 | -61.7432 | -61.7615 | 0.018311 | 59.9716 | -61.5829 | 60.0632 | -61.4731 | -61.6241 | -61.7065 | 0.009155 | -0.16479 | 0.013733 | 0.24261 | -0.21057 | -0.19226 | -0.21973 | -0.20142 | -0.032044 | -0.15106 | -0.05951 | 0.07782 | -0.15564 | -0.073243 | -0.1236 | -0.041199 | 0.23346 | 121.6782 | 0.10986 | 121.6461 | 121.4996 | 121.5546 | 121.5088 | 121.5225 | -121.6644 | -121.7056 | 121.6873 | 121.6141 | 61.5555 | 61.5692
159.1562 | 121.8155 | -61.5417 | 60.0769 | -0.012131 | 0.0026874 | 0.057272 | 0.056006 | -0.0013373 | -0.0059986 | -0.00345 | -0.0084228 | 0.0022367 | 0.066133 | 0.05949 | -0.0081733 | 0.020546 | 0.00043375 | 0.009155 | 59.9991 | -61.5509 | 60.1181 | -61.3266 | -61.7432 | -61.7752 | 0.027466 | 59.9442 | -61.5921 | 60.0815 | -61.4731 | -61.6287 | -61.6882 | -0.009155 | -0.07782 | 0.041199 | 0.21515 | -0.23346 | -0.20142 | -0.22431 | -0.19226 | -0.050354 | -0.13275 | 0.004578 | 0.068665 | -0.14648 | -0.086975 | -0.09613 | -0.036621 | 0.2243 | 121.669 | 0.11902 | 121.6736 | 121.55 | 121.5363 | 121.5408 | 121.4859 | -121.6278 | -121.669 | 121.6599 | 121.6232 | 61.5509 | 61.5692
160.9062 | 121.8658 | -61.5875 | 59.9945 | -0.0045011 | 0.0026874 | 0.058554 | 0.056646 | 0.0033623 | -0.0070666 | -0.0002456 | -0.0084228 | 0.00095488 | 0.065279 | 0.051586 | -0.0086005 | 0.022255 | -0.0029843 | -0.11902 | 59.9075 | -61.6058 | 60.054 | -61.3861 | -61.8347 | -61.8484 | -0.022888 | 59.8389 | -61.6562 | 60.0632 | -61.4914 | -61.647 | -61.6837 | -0.018311 | -0.086975 | 0.059509 | 0.20142 | -0.26093 | -0.24719 | -0.24262 | -0.22888 | -0.068665 | -0.15564 | 0.068664 | 0.09613 | -0.096131 | -0.05951 | -0.027466 | 0.009155 | 0.21973 | 121.6599 | 0.16479 | 121.7194 | 121.5134 | 121.4951 | 121.4951 | 121.4264 | -121.6003 | -121.6507 | 121.6415 | 121.6507 | 61.4685 | 61.5646
162.6562 | 121.9025 | -61.5692 | 59.967 | -0.0045011 | 0.00461 | 0.059409 | 0.056433 | -5.5462e-05 | -0.0066394 | -0.0002456 | -0.0084228 | 0.00074128 | 0.065065 | 0.060344 | -0.0075323 | 0.022896 | -0.0027707 | -0.064087 | 59.848 | -61.5921 | 60.1318 | -61.2762 | -61.7752 | -61.7523 | 0.064087 | 59.8068 | -61.6425 | 60.1089 | -61.441 | -61.5875 | -61.6562 | -0.022888 | -0.11902 | 0.16479 | 0.29297 | -0.1831 | -0.20599 | -0.16022 | -0.18311 | -0.073242 | -0.16022 | 0.14191 | 0.12817 | -0.086975 | -0.01831 | -0.013733 | 0.054932 | 0.31586 | 121.7239 | 0.20142 | 121.7514 | 121.4401 | 121.4493 | 121.4172 | 121.376 | -121.5591 | -121.6095 | 121.7011 | 121.6782 | 61.5051 | 61.6333
164.3438 | 121.875 | -61.5005 | 60.0494 | -0.0045011 | 0.00076478 | 0.056418 | 0.053869 | 0.0010125 | -0.0066394 | 0.0006088 | -0.0023192 | 0.0011685 | 0.064424 | 0.050731 | -0.0088141 | 0.022683 | -0.0029843 | 0.032043 | 59.9442 | -61.5372 | 60.2188 | -61.1893 | -61.6379 | -61.6608 | 0.13733 | 59.9121 | -61.5601 | 60.1501 | -61.377 | -61.5005 | -61.6104 | -0.036621 | -0.10529 | 0.16937 | 0.31128 | -0.16022 | -0.13733 | -0.1236 | -0.10071 | -0.05951 | -0.13733 | 0.10071 | 0.1236 | -0.10986 | 0 | -0.050354 | 0.05951 | 0.3479 | 121.756 | 0.18311 | 121.7102 | 121.4813 | 121.4722 | 121.4447 | 121.4127 | -121.5866 | -121.6095 | 121.7194 | 121.6507 | 61.5326 | 61.6379
166.0781 | 121.7651 | -61.5051 | 60.0906 | -0.01976 | 0.00097838 | 0.057486 | 0.055365 | -0.0019781 | -0.0083484 | -0.001741 | -0.0084228 | 0.0022367 | 0.06592 | 0.054149 | -0.01095 | 0.020546 | 0.00064735 | 0.022888 | 59.9625 | -61.528 | 60.173 | -61.2442 | -61.6974 | -61.702 | 0.073242 | 59.9625 | -61.5692 | 60.0861 | -61.4456 | -61.5829 | -61.6882 | -0.022888 | -0.12817 | 0.082398 | 0.26093 | -0.19684 | -0.19226 | -0.17395 | -0.16937 | -0.064087 | -0.12817 | -0.004577 | 0.059509 | -0.1831 | -0.07782 | -0.11902 | -0.013733 | 0.28381 | 121.7011 | 0.1236 | 121.6553 | 121.4905 | 121.5317 | 121.4676 | 121.4676 | -121.6187 | -121.6599 | 121.6782 | 121.5912 | 61.528 | 61.5784
167.8125 | 121.907 | -61.5097 | 60.0357 | -0.0045011 | -0.00030342 | 0.0577 | 0.05451 | -0.0041145 | -0.0064258 | -0.0013138 | 0.00073235 | 0.00052768 | 0.063997 | 0.055004 | -0.0088141 | 0.02076 | -0.0051205 | -0.009155 | 59.9213 | -61.5646 | 60.1959 | -61.1847 | -61.6425 | -61.6608 | 0.15564 | 59.8892 | -61.5646 | 60.1685 | -61.3541 | -61.4731 | -61.5875 | -0.054931 | -0.11444 | 0.16022 | 0.32501 | -0.15106 | -0.13275 | -0.096131 | -0.07782 | -0.054931 | -0.14648 | 0.13275 | 0.15564 | -0.077819 | 0.036622 | -0.022888 | 0.091553 | 0.37994 | 121.7606 | 0.21057 | 121.7331 | 121.4859 | 121.4539 | 121.431 | 121.3989 | -121.6003 | -121.6003 | 121.7056 | 121.6782 | 61.5005 | 61.6653
169.5781 | 121.843 | -61.5875 | 59.9762 | -0.012131 | 0.0035418 | 0.058768 | 0.05921 | 0.0016535 | -0.0053576 | -0.0019546 | -0.0023192 | 0.0050137 | 0.064638 | 0.063549 | -0.0073187 | 0.02076 | -0.0029843 | -0.10986 | 59.935 | -61.6058 | 60.0494 | -61.3907 | -61.8759 | -61.8713 | -0.022888 | 59.8251 | -61.6241 | 60.0586 | -61.5143 | -61.6608 | -61.7157 | -0.018311 | -0.041198 | 0.073242 | 0.19684 | -0.28381 | -0.28839 | -0.2655 | -0.27008 | -0.036622 | -0.15106 | 0.082398 | 0.073242 | -0.12817 | -0.073243 | -0.091552 | -0.036621 | 0.21515 | 121.6553 | 0.10986 | 121.6827 | 121.5408 | 121.4493 | 121.5225 | 121.4127 | -121.582 | -121.6003 | 121.637 | 121.6461 | 61.4777 | 61.5646
171.25 | 121.7377 | -61.5738 | 60.0449 | -0.01976 | 0.0043964 | 0.058554 | 0.056646 | 0.0025079 | -0.0057848 | -0.0028092 | -0.0023192 | 0.0045865 | 0.066347 | 0.060985 | -0.0073187 | 0.017983 | -0.00084805 | -0.091553 | 59.9258 | -61.6104 | 60.0357 | -61.4227 | -61.8622 | -61.8851 | -0.086975 | 59.9167 | -61.647 | 59.9854 | -61.5967 | -61.7569 | -61.7935 | -0.036621 | -0.11902 | -0.009155 | 0.15106 | -0.31128 | -0.28839 | -0.27466 | -0.25177 | -0.073242 | -0.12817 | -0.059509 | -0.022888 | -0.21973 | -0.18311 | -0.14648 | -0.10986 | 0.18768 | 121.6461 | 0.050354 | 121.6324 | 121.5363 | 121.5637 | 121.4996 | 121.4905 | -121.6553 | -121.6919 | 121.6095 | 121.5591 | 61.4822 | 61.4868
172.9844 | 121.8338 | -61.5005 | 60.0952 | -0.01976 | 0.0016192 | 0.058981 | 0.055578 | 0.00058534 | -0.0064258 | -0.0013138 | -0.0023192 | -0.0011813 | 0.065279 | 0.052226 | -0.010096 | 0.022042 | -0.0031979 | 0.022888 | 59.9258 | -61.5509 | 60.2142 | -61.2076 | -61.6379 | -61.6837 | 0.1236 | 59.9487 | -61.5601 | 60.1273 | -61.3998 | -61.528 | -61.647 | -0.050354 | -0.16937 | 0.11902 | 0.29297 | -0.18311 | -0.13733 | -0.13275 | -0.086975 | -0.05951 | -0.14649 | 0.032043 | 0.10071 | -0.14648 | -0.027466 | -0.086975 | 0.032044 | 0.34332 | 121.7651 | 0.16022 | 121.6873 | 121.4767 | 121.5088 | 121.4264 | 121.4493 | -121.6461 | -121.6553 | 121.7148 | 121.6278 | 61.5234 | 61.6241
174.7344 | 121.8018 | -61.5234 | 60.0677 | -0.0045011 | 0.0031146 | 0.058768 | 0.056433 | 0.0033623 | -0.0087756 | -0.0040908 | -0.0084228 | 0.0039457 | 0.066988 | 0.060558 | -0.0066779 | 0.019051 | -0.0031979 | 0.004578 | 59.9808 | -61.5601 | 60.1273 | -61.3037 | -61.7432 | -61.7798 | 0.064087 | 59.903 | -61.6196 | 60.0861 | -61.4777 | -61.6196 | -61.6882 | -0.036622 | -0.086975 | 0.059509 | 0.21973 | -0.25635 | -0.21973 | -0.21973 | -0.1831 | -0.096131 | -0.16479 | 0.018311 | 0.045776 | -0.16479 | -0.096131 | -0.068664 | 0 | 0.25635 | 121.6873 | 0.14191 | 121.7056 | 121.5408 | 121.5225 | 121.5042 | 121.4264 | -121.6278 | -121.6873 | 121.6507 | 121.6095 | 61.528 | 61.5875
176.4688 | 121.9162 | -61.5005 | 60.054 | -0.0045011 | -0.00051702 | 0.05834 | 0.05216 | -0.00091006 | -0.0059986 | -0.0055862 | -0.0023192 | 0.0015957 | 0.065279 | 0.055858 | -0.0090277 | 0.02311 | -0.0023435 | 0.004578 | 59.9167 | -61.5417 | 60.2097 | -61.1893 | -61.647 | -61.6608 | 0.15106 | 59.8709 | -61.5875 | 60.1868 | -61.3358 | -61.4777 | -61.5829 | -0.041199 | -0.13733 | 0.15564 | 0.31128 | -0.16022 | -0.14648 | -0.11902 | -0.10529 | -0.086975 | -0.1831 | 0.13275 | 0.16479 | -0.082398 | 0.022888 | 0.004577 | 0.10986 | 0.35248 | 121.7514 | 0.25177 | 121.7743 | 121.4584 | 121.4584 | 121.4172 | 121.3715 | -121.5958 | -121.6415 | 121.7102 | 121.6873 | 61.5051 | 61.6516
178.1406 | 121.9299 | -61.4914 | 60.0494 | -0.0045011 | 0.001833 | 0.058127 | 0.052588 | 0.0027215 | -0.0072802 | -0.0019546 | -0.0084228 | 0.0020231 | 0.066133 | 0.059276 | -0.011164 | 0.018624 | -0.0014891 | -0.009155 | 59.8984 | -61.5372 | 60.2097 | -61.171 | -61.6287 | -61.6608 | 0.15564 | 59.8846 | -61.5555 | 60.1913 | -61.3449 | -61.4731 | -61.5875 | -0.045776 | -0.15106 | 0.16022 | 0.32043 | -0.16937 | -0.13733 | -0.1236 | -0.091553 | -0.064087 | -0.16479 | 0.14191 | 0.14648 | -0.09613 | 0.018311 | -0.032043 | 0.082398 | 0.36621 | 121.7468 | 0.21057 | 121.7468 | 121.4355 | 121.4401 | 121.3898 | 121.376 | -121.5866 | -121.6049 | 121.7011 | 121.6827 | 61.4822 | 61.647
179.875 | 121.7834 | -61.5417 | 60.1089 | -0.0045011 | 0.00076478 | 0.057059 | 0.054724 | -0.00026906 | -0.0077074 | -0.0008866 | -0.0023192 | 0.0022367 | 0.064852 | 0.05949 | -0.010096 | 0.019478 | 0.0015017 | 0.018311 | 59.9625 | -61.5326 | 60.173 | -61.2534 | -61.6928 | -61.7111 | 0.059509 | 59.9487 | -61.5646 | 60.0861 | -61.4548 | -61.6013 | -61.702 | 0.009155 | -0.14648 | 0.064087 | 0.28839 | -0.16937 | -0.15106 | -0.17853 | -0.16022 | -0.022888 | -0.16022 | -0.022888 | 0.086975 | -0.16022 | -0.059509 | -0.13733 | -0.036621 | 0.27924 | 121.7056 | 0.10986 | 121.6507 | 121.4951 | 121.5134 | 121.5042 | 121.4905 | -121.6415 | -121.6736 | 121.7148 | 121.6278 | 61.5601 | 61.6013
181.6094 | 121.8155 | -61.5738 | 60.0586 | -0.012131 | 0.0024738 | 0.059622 | 0.058569 | 0.0027215 | -0.0062122 | -0.0008866 | 0.00073235 | 0.0043729 | 0.065065 | 0.060558 | -0.0064643 | 0.019905 | -0.0036253 | -0.004578 | 59.9487 | -61.5829 | 60.1273 | -61.3129 | -61.7844 | -61.7889 | 0.045776 | 59.9075 | -61.6104 | 60.0586 | -61.4868 | -61.6562 | -61.7386 | -0.009155 | -0.10986 | 0.068664 | 0.26093 | -0.21515 | -0.21057 | -0.20599 | -0.20142 | -0.036621 | -0.15106 | 0 | 0.086976 | -0.16479 | -0.082397 | -0.12817 | -0.045776 | 0.27008 | 121.7102 | 0.1236 | 121.669 | 121.5317 | 121.5179 | 121.5225 | 121.4813 | -121.6415 | -121.669 | 121.701 | 121.6324 | 61.5692 | 61.6196
183.3438 | 121.9025 | -61.5738 | 59.967 | -0.012131 | 0.0037556 | 0.058127 | 0.056006 | 0.0018671 | -0.0045032 | -0.0015274 | -0.0023192 | 0.00031408 | 0.066561 | 0.050945 | -0.0081733 | 0.018837 | -0.0023435 | -0.068665 | 59.8801 | -61.6058 | 60.1364 | -61.2991 | -61.7661 | -61.7752 | 0.054932 | 59.848 | -61.6287 | 60.1044 | -61.4731 | -61.6241 | -61.6653 | -0.032043 | -0.086975 | 0.16937 | 0.27466 | -0.20142 | -0.19226 | -0.16937 | -0.16022 | -0.054931 | -0.11902 | 0.13733 | 0.10071 | -0.091552 | -0.050354 | -0.036621 | 0.004577 | 0.3067 | 121.7422 | 0.15564 | 121.7331 | 121.4859 | 121.4767 | 121.4539 | 121.4218 | -121.5729 | -121.5958 | 121.7102 | 121.6782 | 61.5051 | 61.6287
185.0312 | 121.8018 | -61.5463 | 60.0632 | -0.0045011 | 0.00055118 | 0.05834 | 0.057928 | -0.0028327 | -0.006853 | -3.1996e-05 | -0.005371 | 0.0050137 | 0.065065 | 0.057994 | -0.0075323 | 0.021187 | -0.0055479 | -0.009155 | 59.9945 | -61.5646 | 60.1227 | -61.3083 | -61.7249 | -61.7752 | 0.036621 | 59.9213 | -61.5875 | 60.0815 | -61.4639 | -61.6196 | -61.6837 | -0.01831 | -0.068664 | 0.05951 | 0.23804 | -0.22888 | -0.17853 | -0.21057 | -0.16022 | -0.041198 | -0.14191 | 0.018311 | 0.082398 | -0.13733 | -0.073242 | -0.096131 | -0.032044 | 0.25635 | 121.6873 | 0.1236 | 121.669 | 121.5591 | 121.5088 | 121.5408 | 121.4676 | -121.6278 | -121.6507 | 121.669 | 121.6278 | 61.5372 | 61.5829
186.7656 | 121.875 | -61.5646 | 59.9945 | -0.012131 | 0.002901 | 0.060477 | 0.055578 | 0.0020807 | -0.005144 | -0.0028092 | -0.0023192 | 0.00052768 | 0.066988 | 0.060771 | -0.0096685 | 0.020333 | -0.0051205 | -0.073242 | 59.8709 | -61.5829 | 60.1456 | -61.2579 | -61.734 | -61.7615 | 0.073242 | 59.8526 | -61.6379 | 60.0906 | -61.4594 | -61.6013 | -61.6745 | -0.018311 | -0.1236 | 0.15106 | 0.3067 | -0.19684 | -0.16937 | -0.17853 | -0.15106 | -0.073242 | -0.14191 | 0.09613 | 0.10529 | -0.10986 | -0.036621 | -0.036622 | 0.036621 | 0.32501 | 121.7285 | 0.17853 | 121.7285 | 121.4539 | 121.4905 | 121.4355 | 121.4172 | -121.5775 | -121.6324 | 121.7102 | 121.6553 | 61.4914 | 61.6379
188.4375 | 121.9025 | -61.4639 | 60.0494 | -0.012131 | 0.00055118 | 0.056631 | 0.054937 | -0.0019781 | -0.005144 | -0.000673 | -0.0084228 | 0.00052768 | 0.065279 | 0.059703 | -0.010096 | 0.019051 | -0.0027707 | 0.022888 | 59.8938 | -61.5189 | 60.2371 | -61.1572 | -61.6196 | -61.6379 | 0.17853 | 59.8984 | -61.5738 | 60.173 | -61.3495 | -61.4777 | -61.5967 | -0.054932 | -0.15564 | 0.18768 | 0.3067 | -0.17395 | -0.15564 | -0.11902 | -0.10071 | -0.10986 | -0.15106 | 0.1236 | 0.11444 | -0.13275 | -0.013733 | -0.022888 | 0.096131 | 0.36163 | 121.756 | 0.2243 | 121.7468 | 121.4127 | 121.4722 | 121.3577 | 121.3623 | -121.5683 | -121.6232 | 121.7011 | 121.637 | 61.4868 | 61.6425
190.1719 | 121.8155 | -61.5097 | 60.0815 | -0.012131 | 0.001192 | 0.056631 | 0.055792 | 0.0025079 | -0.0077074 | -0.0004592 | -0.005371 | 0.0039457 | 0.066774 | 0.051158 | -0.010523 | 0.020546 | -0.0023435 | 0.036621 | 59.935 | -61.5417 | 60.2005 | -61.203 | -61.6699 | -61.6837 | 0.091553 | 59.9258 | -61.5601 | 60.0906 | -61.4319 | -61.5509 | -61.6516 | -0.032043 | -0.14648 | 0.11902 | 0.3067 | -0.17395 | -0.16022 | -0.14191 | -0.12817 | -0.050354 | -0.15564 | 0.009155 | 0.07782 | -0.14191 | -0.041198 | -0.091552 | 0.009156 | 0.33874 | 121.7422 | 0.12817 | 121.6507 | 121.4767 | 121.4859 | 121.4447 | 121.4355 | -121.6232 | -121.6415 | 121.7102 | 121.6003 | 61.5463 | 61.6013
191.9062 | 121.7743 | -61.5326 | 60.0952 | -0.012131 | 0.00076478 | 0.056418 | 0.055578 | 0.0022943 | -0.0079212 | -0.00345 | -0.005371 | 0.0033047 | 0.065706 | 0.065044 | -0.0090277 | 0.017983 | -0.0019163 | -0.022888 | 59.9854 | -61.5417 | 60.0952 | -61.322 | -61.7615 | -61.7844 | 0.022888 | 59.9854 | -61.5829 | 60.0632 | -61.4868 | -61.6287 | -61.7065 | -0.009155 | -0.10986 | 0 | 0.21057 | -0.25177 | -0.22888 | -0.24262 | -0.21973 | -0.050354 | -0.10986 | -0.032044 | 0.045777 | -0.17395 | -0.09613 | -0.1236 | -0.045776 | 0.21973 | 121.637 | 0.096131 | 121.6461 | 121.5271 | 121.5683 | 121.5179 | 121.5179 | -121.637 | -121.6782 | 121.6278 | 121.5958 | 61.5097 | 61.5555
193.5781 | 121.7651 | -61.5967 | 60.0449 | -0.012131 | 0.0048236 | 0.05834 | 0.055578 | 0.0022943 | -0.0064258 | -0.0015274 | -0.005371 | 0.0037321 | 0.064424 | 0.059062 | -0.0083869 | 0.020119 | -0.0029843 | -0.11444 | 59.9396 | -61.615 | 60.0266 | -61.4319 | -61.9034 | -61.8896 | -0.082397 | 59.8709 | -61.6699 | 59.9899 | -61.5921 | -61.734 | -61.7661 | -0.01831 | -0.10529 | -0.018311 | 0.16479 | -0.29297 | -0.3067 | -0.27466 | -0.28839 | -0.073242 | -0.17395 | -0.054932 | 0.004578 | -0.16937 | -0.13733 | -0.09613 | -0.064087 | 0.1831 | 121.6415 | 0.07782 | 121.6599 | 121.5546 | 121.5408 | 121.5363 | 121.4676 | -121.6599 | -121.7148 | 121.6232 | 121.5866 | 61.4822 | 61.5143
195.3281 | 121.8796 | -61.5738 | 59.9716 | -0.0045011 | 0.00461 | 0.058981 | 0.056646 | 0.00015814 | -0.0053576 | -0.0032364 | -0.005371 | -0.0013949 | 0.064424 | 0.055644 | -0.0092413 | 0.021614 | -0.0051205 | -0.082397 | 59.8526 | -61.6104 | 60.1318 | -61.2854 | -61.7615 | -61.7661 | 0.054932 | 59.8068 | -61.6516 | 60.1044 | -61.4365 | -61.5967 | -61.6562 | -0.036621 | -0.11902 | 0.16022 | 0.28839 | -0.19226 | -0.18768 | -0.15564 | -0.15106 | -0.077819 | -0.16479 | 0.13275 | 0.13733 | -0.082397 | -0.022888 | -0.004578 | 0.054931 | 0.32501 | 121.7422 | 0.21515 | 121.756 | 121.463 | 121.4584 | 121.4264 | 121.3806 | -121.582 | -121.6232 | 121.7056 | 121.6782 | 61.4914 | 61.6287
197.0156 | 121.7606 | -61.615 | 60.0266 | -0.01976 | 0.0054644 | 0.059195 | 0.058783 | 0.00058534 | -0.0077074 | -0.0030228 | -0.005371 | 0.0026639 | 0.06592 | 0.056713 | -0.0092413 | 0.020119 | 0.0012881 | -0.13733 | 59.935 | -61.6425 | 60.0037 | -61.4548 | -61.8851 | -61.8805 | -0.09613 | 59.8755 | -61.6516 | 59.9899 | -61.5967 | -61.7294 | -61.7889 | -0.027466 | -0.091552 | -0.022888 | 0.16022 | -0.2655 | -0.27008 | -0.23804 | -0.24262 | -0.036621 | -0.15106 | -0.036621 | 0.01831 | -0.17395 | -0.11444 | -0.13733 | -0.07782 | 0.18768 | 121.6461 | 0.054931 | 121.6415 | 121.5775 | 121.5271 | 121.55 | 121.4905 | -121.669 | -121.6782 | 121.6187 | 121.6049 | 61.4777 | 61.5189
198.75 | 121.7834 | -61.5417 | 60.1364 | -0.012131 | -0.00030342 | 0.058127 | 0.054724 | 0.0040033 | -0.0066394 | -0.0021682 | -0.0023192 | 0.0024503 | 0.068911 | 0.060985 | -0.0083869 | 0.02076 | -0.0036253 | -0.004578 | 59.9762 | -61.5372 | 60.1227 | -61.3083 | -61.7432 | -61.7752 | 0.018311 | 59.9487 | -61.5692 | 60.054 | -61.4822 | -61.6013 | -61.702 | 0.004578 | -0.16022 | -0.013733 | 0.23346 | -0.23346 | -0.20142 | -0.23804 | -0.20599 | -0.027466 | -0.18768 | -0.082398 | 0.059509 | -0.16022 | -0.059509 | -0.13275 | -0.032043 | 0.22888 | 121.6599 | 0.086975 | 121.6232 | 121.5134 | 121.5179 | 121.5179 | 121.4905 | -121.6736 | -121.7056 | 121.6644 | 121.5958 | 61.5372 | 61.5601
200.4375 | 121.8842 | -61.5143 | 60.0449 | -0.0045011 | -0.00073062 | 0.0577 | 0.052801 | -0.0060371 | -0.0070666 | -0.0013138 | -0.005371 | 0.00074128 | 0.06357 | 0.056072 | -0.0096685 | 0.021828 | -0.0049069 | -0.022888 | 59.9167 | -61.5372 | 60.1959 | -61.2259 | -61.6516 | -61.6653 | 0.12817 | 59.903 | -61.5601 | 60.1639 | -61.3632 | -61.496 | -61.6013 | -0.022888 | -0.12817 | 0.15106 | 0.28839 | -0.15106 | -0.13733 | -0.12817 | -0.11444 | -0.045777 | -0.14191 | 0.11902 | 0.15106 | -0.086975 | 0.01831 | -0.041198 | 0.064087 | 0.31128 | 121.7331 | 0.19684 | 121.7239 | 121.4539 | 121.463 | 121.431 | 121.4172 | -121.582 | -121.6049 | 121.7102 | 121.6782 | 61.4914 | 61.6425
202.1719 | 121.8887 | -61.5189 | 60.0311 | -0.012131 | 0.001192 | 0.055563 | 0.053656 | 0.00015814 | -0.0066394 | -0.0021682 | -0.0023192 | 0.00010048 | 0.063356 | 0.053081 | -0.011591 | 0.02076 | -0.0034117 | -0.027466 | 59.8755 | -61.5372 | 60.1822 | -61.2488 | -61.6699 | -61.6928 | 0.10529 | 59.8801 | -61.5784 | 60.1501 | -61.377 | -61.5051 | -61.6104 | -0.01831 | -0.15564 | 0.15106 | 0.27008 | -0.17395 | -0.15106 | -0.15564 | -0.13275 | -0.059509 | -0.15106 | 0.11902 | 0.14191 | -0.091553 | 0.013733 | -0.032044 | 0.073242 | 0.28839 | 121.7194 | 0.20142 | 121.7285 | 121.4127 | 121.4584 | 121.3943 | 121.3989 | -121.5683 | -121.6095 | 121.701 | 121.669 | 61.4914 | 61.6241
203.9062 | 121.8933 | -61.5646 | 59.9808 | -0.01976 | 0.0039692 | 0.058127 | 0.054937 | 0.0029351 | -0.0057848 | -0.0013138 | -0.0084228 | 0.0030911 | 0.065279 | 0.063762 | -0.0096685 | 0.022042 | -0.0049069 | -0.086975 | 59.8709 | -61.6287 | 60.1273 | -61.3174 | -61.7889 | -61.7615 | 0.036621 | 59.8343 | -61.6379 | 60.0906 | -61.4594 | -61.5921 | -61.6562 | -0.064087 | -0.10986 | 0.14648 | 0.24719 | -0.19684 | -0.2243 | -0.13275 | -0.16022 | -0.073242 | -0.14648 | 0.10986 | 0.10529 | -0.091553 | -0.027466 | -0.018311 | 0.045776 | 0.31128 | 121.756 | 0.17853 | 121.7285 | 121.4996 | 121.4722 | 121.4355 | 121.3989 | -121.6095 | -121.6187 | 121.6919 | 121.6553 | 61.4777 | 61.6013
205.5938 | 121.8796 | -61.5005 | 60.0906 | -0.0045011 | 0.00033758 | 0.056418 | 0.054083 | -0.0043281 | -0.005144 | 0.0006088 | -0.005371 | 0.0024503 | 0.065493 | 0.065257 | -0.010737 | 0.020333 | -0.0019163 | 0.041199 | 59.9121 | -61.5051 | 60.2371 | -61.1801 | -61.647 | -61.6562 | 0.13733 | 59.9258 | -61.5555 | 60.1593 | -61.3815 | -61.4914 | -61.6013 | -0.004578 | -0.17853 | 0.14648 | 0.32043 | -0.15564 | -0.14648 | -0.15106 | -0.14191 | -0.054932 | -0.16479 | 0.068665 | 0.11902 | -0.10071 | 0.009155 | -0.045776 | 0.064087 | 0.32501 | 121.7422 | 0.17395 | 121.7148 | 121.4172 | 121.4813 | 121.4127 | 121.4264 | -121.5958 | -121.6461 | 121.7377 | 121.6599 | 61.5417 | 61.6379
207.3281 | 121.756 | -61.6013 | 60.0403 | -0.012131 | 0.0037556 | 0.059195 | 0.057287 | 0.0020807 | -0.0081348 | -0.0004592 | -0.0023192 | 0.0052273 | 0.067842 | 0.070384 | -0.0073187 | 0.020546 | 0.00021995 | -0.10529 | 59.9167 | -61.6241 | 60.0082 | -61.4548 | -61.8851 | -61.8988 | -0.091553 | 59.8755 | -61.6608 | 60.0037 | -61.6013 | -61.734 | -61.7661 | -0.022889 | -0.1236 | -0.032043 | 0.14648 | -0.29755 | -0.28381 | -0.27466 | -0.26093 | -0.05951 | -0.1648 | -0.036621 | 0 | -0.1648 | -0.13275 | -0.10529 | -0.073242 | 0.16937 | 121.6324 | 0.05951 | 121.6644 | 121.5408 | 121.5363 | 121.5179 | 121.4767 | -121.6644 | -121.7011 | 121.6095 | 121.6049 | 61.496 | 61.5097
209.0625 | 121.9162 | -61.5005 | 60.0357 | 0.0031279 | -0.0017986 | 0.059622 | 0.053015 | -0.0030463 | -0.0074938 | -0.0008866 | -0.0084228 | 0.0011685 | 0.065706 | 0.05479 | -0.010523 | 0.020119 | -0.0044797 | -0.009155 | 59.9167 | -61.528 | 60.2051 | -61.1938 | -61.6287 | -61.647 | 0.15564 | 59.8846 | -61.5646 | 60.1822 | -61.3449 | -61.4685 | -61.5738 | -0.027466 | -0.11902 | 0.16937 | 0.3067 | -0.14648 | -0.12817 | -0.11902 | -0.10071 | -0.064087 | -0.15106 | 0.14648 | 0.15564 | -0.073243 | 0.032043 | -0.009156 | 0.09613 | 0.33417 | 121.7331 | 0.21973 | 121.7468 | 121.4447 | 121.4493 | 121.4172 | 121.3852 | -121.5637 | -121.6003 | 121.7056 | 121.6827 | 61.4914 | 61.6562
210.8125 | 121.9116 | -61.496 | 60.0449 | -0.0045011 | 0.001833 | 0.056418 | 0.053656 | -0.0039007 | -0.0094164 | -0.0021682 | -0.005371 | -0.00075412 | 0.066347 | 0.05244 | -0.0098823 | 0.020119 | -0.0027707 | 0 | 59.8846 | -61.5509 | 60.2188 | -61.171 | -61.6287 | -61.6516 | 0.16022 | 59.8938 | -61.5829 | 60.1868 | -61.3266 | -61.4594 | -61.5692 | -0.054931 | -0.16022 | 0.17395 | 0.32501 | -0.15564 | -0.13275 | -0.10071 | -0.07782 | -0.086975 | -0.15106 | 0.14191 | 0.16937 | -0.073242 | 0.036621 | 0.013733 | 0.1236 | 0.37994 | 121.7697 | 0.25635 | 121.7697 | 121.4355 | 121.4767 | 121.3806 | 121.3898 | -121.5958 | -121.6278 | 121.7148 | 121.6827 | 61.496 | 61.6562
212.4844 | 121.7651 | -61.5234 | 60.1044 | -0.012131 | 0.001192 | 0.06069 | 0.054724 | -0.0015509 | -0.0094164 | -3.1996e-05 | -0.0084228 | 0.0043729 | 0.066347 | 0.060771 | -0.010096 | 0.019265 | -0.0025571 | -0.032043 | 59.9991 | -61.5372 | 60.1135 | -61.322 | -61.7477 | -61.7661 | 0.022888 | 59.9762 | -61.5601 | 60.0632 | -61.4822 | -61.6104 | -61.7157 | -0.013733 | -0.10529 | 0.009155 | 0.20142 | -0.24262 | -0.22431 | -0.22888 | -0.21057 | -0.036622 | -0.12817 | -0.041199 | 0.041198 | -0.19226 | -0.086976 | -0.15564 | -0.050354 | 0.21515 | 121.6507 | 0.07782 | 121.6232 | 121.5363 | 121.5363 | 121.5225 | 121.4996 | -121.6415 | -121.6644 | 121.637 | 121.5866 | 61.4914 | 61.5463
214.2188 | 121.8063 | -61.5143 | 60.0403 | -0.0045011 | 0.0022602 | 0.058554 | 0.057928 | 0.0022943 | -0.0077074 | -0.0021682 | -0.0023192 | 0.0041593 | 0.064852 | 0.056926 | -0.0079597 | 0.020333 | -0.0038389 | -0.013733 | 59.9213 | -61.5646 | 60.1318 | -61.2854 | -61.7615 | -61.7661 | 0.064087 | 59.9258 | -61.6058 | 60.1044 | -61.4777 | -61.6104 | -61.6837 | -0.050354 | -0.11902 | 0.091553 | 0.22888 | -0.25177 | -0.24719 | -0.20142 | -0.19684 | -0.091553 | -0.11444 | 0.064087 | 0.036621 | -0.16937 | -0.096131 | -0.07782 | -0.004578 | 0.27924 | 121.6965 | 0.12817 | 121.7102 | 121.4859 | 121.5317 | 121.4355 | 121.4401 | -121.6049 | -121.6461 | 121.6461 | 121.6187 | 61.5005 | 61.5784
215.9062 | 121.8613 | -61.528 | 60.0174 | -0.01976 | 0.001192 | 0.059195 | 0.055792 | -0.0030463 | -0.0066394 | -0.0030228 | -0.005371 | 0.0018095 | 0.065279 | 0.063121 | -0.0081733 | 0.020974 | -0.0034117 | -0.073242 | 59.8755 | -61.5784 | 60.1135 | -61.2991 | -61.7706 | -61.7615 | -0.004578 | 59.848 | -61.5967 | 60.0815 | -61.4548 | -61.5646 | -61.6653 | -0.050354 | -0.14191 | 0.09613 | 0.22888 | -0.23346 | -0.24261 | -0.18311 | -0.19226 | -0.068665 | -0.16937 | 0.064087 | 0.073242 | -0.13733 | -0.036621 | -0.068664 | 0.032044 | 0.27924 | 121.6919 | 0.14191 | 121.6782 | 121.4539 | 121.4447 | 121.4035 | 121.376 | -121.5958 | -121.6141 | 121.6415 | 121.6095 | 61.4548 | 61.5234
217.6562 | 121.8475 | -61.5372 | 60.0174 | 0.0031279 | 0.0014056 | 0.056845 | 0.053015 | -0.0041145 | -0.0079212 | -0.000673 | -0.005371 | 0.0024503 | 0.065065 | 0.045391 | -0.0081733 | 0.022469 | -0.0014891 | -0.086975 | 59.8801 | -61.5738 | 60.1135 | -61.3174 | -61.7615 | -61.7615 | 0 | 59.8663 | -61.6196 | 60.0815 | -61.4685 | -61.6013 | -61.6928 | -0.036622 | -0.13733 | 0.09613 | 0.21973 | -0.2243 | -0.2243 | -0.18768 | -0.18768 | -0.082398 | -0.15106 | 0.064087 | 0.068664 | -0.15564 | -0.064087 | -0.073242 | 0.018311 | 0.25635 | 121.6873 | 0.15106 | 121.7011 | 121.4539 | 121.4859 | 121.4172 | 121.4035 | -121.5912 | -121.637 | 121.6507 | 121.6187 | 61.4502 | 61.5372
219.4062 | 121.8796 | -61.5555 | 59.9854 | -0.012131 | 0.0031146 | 0.057272 | 0.055578 | -0.00026906 | -0.0059986 | -0.00345 | -0.0023192 | 0.0026639 | 0.064638 | 0.056285 | -0.0083869 | 0.019051 | 0.00021995 | -0.059509 | 59.8434 | -61.5875 | 60.1273 | -61.29 | -61.7752 | -61.7798 | 0.041199 | 59.8114 | -61.6379 | 60.1135 | -61.4319 | -61.5738 | -61.6516 | -0.032043 | -0.14191 | 0.14191 | 0.2655 | -0.2243 | -0.21973 | -0.19226 | -0.18768 | -0.082397 | -0.17395 | 0.12817 | 0.1236 | -0.09613 | -0.018311 | -0.013733 | 0.064086 | 0.29755 | 121.7148 | 0.20599 | 121.7514 | 121.431 | 121.4493 | 121.3989 | 121.3669 | -121.5729 | -121.6232 | 121.6827 | 121.669 | 61.496 | 61.5967
221.1719 | 121.7651 | -61.5921 | 60.0037 | -0.0045011 | 0.0052508 | 0.059195 | 0.060064 | 0.0033623 | -0.006853 | -0.0015274 | -0.005371 | 0.0050137 | 0.065493 | 0.063121 | -0.0077459 | 0.018837 | -0.0021299 | -0.09613 | 59.9487 | -61.6104 | 60.0128 | -61.4319 | -61.8805 | -61.8759 | -0.10529 | 59.9121 | -61.6425 | 59.9945 | -61.5967 | -61.7294 | -61.7844 | -0.018311 | -0.054932 | 0.009155 | 0.16022 | -0.28381 | -0.28839 | -0.2655 | -0.27008 | -0.050354 | -0.091553 | -0.009155 | -0.004578 | -0.19226 | -0.13733 | -0.14191 | -0.086975 | 0.17853 | 121.6232 | 0.045776 | 121.637 | 121.5591 | 121.5546 | 121.5408 | 121.5042 | -121.6141 | -121.6461 | 121.6049 | 121.5866 | 61.496 | 61.4868
222.8906 | 121.7606 | -61.5097 | 60.1044 | -0.012131 | 0.0014056 | 0.0577 | 0.057074 | 0.0029351 | -0.0072802 | -0.0025956 | -0.005371 | 0.0033047 | 0.067842 | 0.054363 | -0.0092413 | 0.022469 | -0.0036253 | -0.013733 | 59.9991 | -61.5555 | 60.0998 | -61.3403 | -61.7523 | -61.7935 | -0.004578 | 59.9487 | -61.5921 | 60.0723 | -61.4868 | -61.6241 | -61.6974 | -0.045776 | -0.10529 | -0.004578 | 0.16937 | -0.28381 | -0.24261 | -0.23804 | -0.19684 | -0.082397 | -0.15564 | -0.032043 | 0.022889 | -0.18768 | -0.11444 | -0.10529 | -0.032044 | 0.21515 | 121.6553 | 0.10529 | 121.6644 | 121.5546 | 121.5408 | 121.5088 | 121.4584 | -121.6599 | -121.6965 | 121.6095 | 121.582 | 61.496 | 61.5051
224.5625 | 121.7468 | -61.528 | 60.1135 | -0.012131 | -8.9824e-05 | 0.0577 | 0.056219 | 0.0012261 | -0.0081348 | -0.0011002 | -0.005371 | 0.0026639 | 0.068911 | 0.051586 | -0.0098823 | 0.021187 | -0.0031979 | 0.009155 | 59.9533 | -61.5326 | 60.141 | -61.2808 | -61.7203 | -61.734 | 0.027466 | 59.9579 | -61.5784 | 60.0815 | -61.4685 | -61.6104 | -61.7065 | -0.004578 | -0.16022 | 0.027466 | 0.24719 | -0.20599 | -0.19226 | -0.20142 | -0.18768 | -0.050354 | -0.15564 | -0.032043 | 0.059509 | -0.17853 | -0.082398 | -0.12817 | -0.032044 | 0.25177 | 121.6736 | 0.10986 | 121.6599 | 121.4859 | 121.5363 | 121.4813 | 121.4859 | -121.6461 | -121.6919 | 121.669 | 121.6095 | 61.5372 | 61.5555
226.2969 | 121.8613 | -61.5601 | 59.9716 | -0.012131 | 0.0026874 | 0.058127 | 0.054724 | 0.0020807 | -0.003435 | -0.001741 | -0.005371 | 0.0013821 | 0.065493 | 0.058208 | -0.0098823 | 0.020119 | -0.0057615 | -0.059509 | 59.8663 | -61.5784 | 60.141 | -61.2534 | -61.7386 | -61.7386 | 0.054932 | 59.8434 | -61.6241 | 60.0952 | -61.4685 | -61.6013 | -61.6562 | -0.01831 | -0.10529 | 0.16937 | 0.3067 | -0.17853 | -0.17853 | -0.16022 | -0.16022 | -0.064087 | -0.12817 | 0.1236 | 0.091553 | -0.09613 | -0.041198 | -0.032043 | 0.022889 | 0.32501 | 121.7194 | 0.15564 | 121.7194 | 121.4447 | 121.4676 | 121.4264 | 121.4035 | -121.55 | -121.5958 | 121.7011 | 121.6553 | 61.5006 | 61.615
227.9688 | 121.8658 | -61.4822 | 60.0677 | -0.012131 | -0.00030342 | 0.05834 | 0.054937 | -0.0030463 | -0.0070666 | -0.000673 | -0.0084228 | 0.0015957 | 0.067415 | 0.051372 | -0.0086005 | 0.021187 | -0.0014891 | 0.027466 | 59.9121 | -61.5372 | 60.2234 | -61.1938 | -61.6379 | -61.6608 | 0.14191 | 59.903 | -61.5601 | 60.1639 | -61.3724 | -61.4868 | -61.6104 | -0.054931 | -0.15564 | 0.15564 | 0.28839 | -0.17853 | -0.15564 | -0.1236 | -0.10071 | -0.07782 | -0.16479 | 0.09613 | 0.10986 | -0.12817 | -0.004577 | -0.050354 | 0.073243 | 0.34332 | 121.7606 | 0.18768 | 121.7239 | 121.4493 | 121.463 | 121.3943 | 121.3852 | -121.6049 | -121.6278 | 121.7056 | 121.6461 | 61.5097 | 61.6241
229.6562 | 121.756 | -61.5784 | 60.0494 | 0.0031279 | 0.002901 | 0.057913 | 0.058996 | -0.0034735 | -0.0081348 | -0.0013138 | -0.0084228 | 0.0050137 | 0.066988 | 0.055431 | -0.0090277 | 0.021828 | -0.0014891 | -0.064087 | 59.9442 | -61.615 | 60.0449 | -61.3815 | -61.8668 | -61.8668 | -0.054932 | 59.9258 | -61.6425 | 59.9991 | -61.5646 | -61.7157 | -61.7661 | -0.036621 | -0.10529 | -0.004577 | 0.19684 | -0.28839 | -0.28839 | -0.25177 | -0.25177 | -0.064087 | -0.1236 | -0.050354 | 0.013733 | -0.18768 | -0.13733 | -0.1236 | -0.073242 | 0.23346 | 121.6599 | 0.07782 | 121.6415 | 121.5591 | 121.5683 | 121.5225 | 121.5042 | -121.6644 | -121.6919 | 121.6232 | 121.5775 | 61.5143 | 61.5234
231.3281 | 121.788 | -61.528 | 60.1135 | -0.01976 | -0.00073062 | 0.058127 | 0.056646 | 0.0022943 | -0.0049304 | -0.0021682 | -0.005371 | 0.0041593 | 0.066347 | 0.05479 | -0.0075323 | 0.020974 | -0.0027707 | -0.027466 | 59.9899 | -61.5738 | 60.0861 | -61.3358 | -61.7752 | -61.7935 | -0.009155 | 59.9487 | -61.5738 | 60.0632 | -61.4731 | -61.6058 | -61.6745 | -0.045777 | -0.1236 | -0.027465 | 0.19226 | -0.2655 | -0.24719 | -0.21973 | -0.20142 | -0.045777 | -0.1648 | -0.050354 | 0.054932 | -0.14648 | -0.07782 | -0.10071 | -0.032043 | 0.23804 | 121.6599 | 0.10071 | 121.637 | 121.5637 | 121.5225 | 121.5179 | 121.4767 | -121.6873 | -121.6873 | 121.6141 | 121.5912 | 61.5005 | 61.5189
233.0625 | 121.8155 | -61.5372 | 60.0632 | 0.0031279 | 0.002901 | 0.060263 | 0.057501 | -0.00069646 | -0.0062122 | -0.000673 | -0.005371 | 0.00074128 | 0.065706 | 0.050731 | -0.0068915 | 0.019692 | -0.0014891 | 0.009155 | 59.9762 | -61.5509 | 60.1364 | -61.2854 | -61.7615 | -61.7889 | 0.07782 | 59.9075 | -61.6058 | 60.0906 | -61.4639 | -61.615 | -61.6745 | -0.013733 | -0.086975 | 0.073243 | 0.25177 | -0.25177 | -0.2243 | -0.23804 | -0.21057 | -0.068665 | -0.15564 | 0.027466 | 0.073242 | -0.13733 | -0.07782 | -0.068665 | -0.009155 | 0.2655 | 121.6873 | 0.14191 | 121.6965 | 121.5271 | 121.5134 | 121.5134 | 121.4447 | -121.6141 | -121.669 | 121.6736 | 121.6278 | 61.5463 | 61.615
234.75 | 121.8063 | -61.5555 | 60.054 | -0.012131 | 0.0020466 | 0.058981 | 0.056219 | -0.0021919 | -0.0053576 | -0.000673 | -0.005371 | 0.0054409 | 0.068056 | 0.060558 | -0.0060369 | 0.022042 | -0.0017027 | -0.013733 | 59.935 | -61.5601 | 60.1273 | -61.2854 | -61.7432 | -61.7798 | 0.064087 | 59.8938 | -61.6104 | 60.0815 | -61.4685 | -61.6287 | -61.6837 | -0.004578 | -0.11902 | 0.073242 | 0.27008 | -0.2243 | -0.18768 | -0.21973 | -0.1831 | -0.054932 | -0.16022 | 0.027466 | 0.086975 | -0.12817 | -0.073242 | -0.073242 | -0.01831 | 0.27466 | 121.6873 | 0.14191 | 121.6919 | 121.4951 | 121.5042 | 121.4905 | 121.4493 | -121.6141 | -121.6644 | 121.6827 | 121.637 | 61.5417 | 61.6196
236.4219 | 121.7514 | -61.5829 | 60.0449 | -0.0045011 | 0.0037556 | 0.056845 | 0.05686 | -0.00048286 | -0.0057848 | -0.0008866 | -0.0023192 | 0.0035183 | 0.066133 | 0.061626 | -0.0075323 | 0.022255 | -0.0036253 | -0.054932 | 59.9533 | -61.5967 | 60.0677 | -61.3724 | -61.8484 | -61.8393 | -0.045776 | 59.8984 | -61.647 | 60.0128 | -61.5601 | -61.7249 | -61.7569 | -0.013733 | -0.091553 | 0.022888 | 0.21057 | -0.25635 | -0.2655 | -0.24261 | -0.25177 | -0.064087 | -0.14648 | -0.032044 | 0.022888 | -0.17395 | -0.14191 | -0.10986 | -0.07782 | 0.22431 | 121.6644 | 0.086975 | 121.6599 | 121.55 | 121.5454 | 121.5363 | 121.4813 | -121.6415 | -121.6919 | 121.6507 | 121.5958 | 61.528 | 61.5372
238.0938 | 121.8704 | -61.5555 | 59.9808 | -0.0045011 | 0.002901 | 0.058554 | 0.058142 | -0.0024055 | -0.0077074 | 0.0001816 | -0.0023192 | 0.00074128 | 0.065065 | 0.059703 | -0.0081733 | 0.022255 | -0.0023435 | -0.11902 | 59.903 | -61.6013 | 60.1044 | -61.322 | -61.7661 | -61.7935 | 0.013733 | 59.8343 | -61.6425 | 60.0906 | -61.4685 | -61.5967 | -61.6608 | -0.045776 | -0.07782 | 0.1236 | 0.23346 | -0.23804 | -0.21057 | -0.19226 | -0.1648 | -0.086975 | -0.14648 | 0.10986 | 0.086975 | -0.10529 | -0.041199 | -0.018311 | 0.045776 | 0.27924 | 121.7056 | 0.17395 | 121.7331 | 121.5042 | 121.4767 | 121.4584 | 121.3898 | -121.582 | -121.6232 | 121.6599 | 121.6461 | 61.4365 | 61.5692
239.7656 | 121.8521 | -61.5738 | 59.9854 | -0.01976 | 0.0016192 | 0.057272 | 0.057501 | 0.00015814 | -0.005144 | -0.0025956 | -0.0084228 | 0.0022367 | 0.065065 | 0.058208 | -0.0090277 | 0.020119 | 0.00086095 | -0.11902 | 59.903 | -61.6196 | 60.0632 | -61.377 | -61.8301 | -61.8393 | -0.027466 | 59.8389 | -61.6333 | 60.0632 | -61.4914 | -61.6196 | -61.6699 | -0.045776 | -0.082398 | 0.077819 | 0.19684 | -0.2655 | -0.25635 | -0.21973 | -0.21057 | -0.059509 | -0.14648 | 0.077819 | 0.082398 | -0.09613 | -0.045776 | -0.036621 | 0.013733 | 0.24262 | 121.6827 | 0.14191 | 121.6965 | 121.5225 | 121.4722 | 121.4767 | 121.4127 | -121.6049 | -121.6187 | 121.637 | 121.637 | 61.4548 | 61.5463
241.4375 | 121.7743 | -61.615 | 60.0357 | -0.01976 | 0.006319 | 0.057913 | 0.05686 | 0.0010125 | -0.0047168 | -0.0002456 | -0.005371 | 0.0035183 | 0.065065 | 0.057353 | -0.0088141 | 0.021828 | -0.0038389 | -0.1236 | 59.9213 | -61.6333 | 60.0037 | -61.441 | -61.8713 | -61.8896 | -0.10529 | 59.8755 | -61.6516 | 59.9991 | -61.5692 | -61.734 | -61.7661 | -0.018311 | -0.11444 | -0.032044 | 0.17395 | -0.27466 | -0.25635 | -0.25635 | -0.23804 | -0.036621 | -0.16022 | -0.036622 | 0.045776 | -0.15106 | -0.11902 | -0.11444 | -0.082398 | 0.19226 | 121.637 | 0.082397 | 121.6507 | 121.5546 | 121.5271 | 121.5363 | 121.4905 | -121.669 | -121.6873 | 121.6187 | 121.6141 | 61.4914 | 61.5097
243.1406 | 121.7651 | -61.615 | 60.0357 | -0.0045011 | 0.0052508 | 0.057486 | 0.058569 | -0.0026191 | -0.0059986 | -0.0008866 | -0.0023192 | 0.0028775 | 0.065706 | 0.061199 | -0.0079597 | 0.022896 | 0.00043375 | -0.11902 | 59.9304 | -61.6333 | 60.0037 | -61.4502 | -61.8896 | -61.8759 | -0.091553 | 59.8938 | -61.6516 | 59.9945 | -61.5921 | -61.734 | -61.7615 | -0.018311 | -0.10529 | -0.032044 | 0.16479 | -0.26093 | -0.27466 | -0.24261 | -0.25635 | -0.036621 | -0.14191 | -0.041199 | 0.022888 | -0.14648 | -0.11902 | -0.10986 | -0.082398 | 0.18311 | 121.637 | 0.059509 | 121.6461 | 121.5637 | 121.5454 | 121.5454 | 121.5088 | -121.669 | -121.6873 | 121.6187 | 121.6095 | 61.496 | 61.5234
244.8594 | 121.8109 | -61.5509 | 60.0815 | -0.01976 | 0.0033282 | 0.057059 | 0.054724 | 0.0027215 | -0.0057848 | -0.0002456 | -0.0023192 | 0.0039457 | 0.06827 | 0.056926 | -0.0079597 | 0.020546 | -0.0059751 | 0.009155 | 59.9808 | -61.5646 | 60.1227 | -61.3083 | -61.734 | -61.7661 | 0.050354 | 59.9213 | -61.5967 | 60.0861 | -61.4639 | -61.6058 | -61.6837 | -0.013733 | -0.10071 | 0.041199 | 0.24261 | -0.21515 | -0.18311 | -0.20142 | -0.16937 | -0.045777 | -0.16022 | 0.004578 | 0.086975 | -0.13275 | -0.054932 | -0.086975 | -0.009155 | 0.25635 | 121.6873 | 0.13275 | 121.6827 | 121.5454 | 121.5179 | 121.5317 | 121.4722 | -121.6461 | -121.6782 | 121.6736 | 121.637 | 61.5601 | 61.6013
246.5469 | 121.7743 | -61.5784 | 60.0266 | -0.0045011 | 0.0043964 | 0.057272 | 0.057074 | -0.00048286 | -0.0070666 | -0.001741 | -0.005371 | -0.00096772 | 0.066774 | 0.055217 | -0.0086005 | 0.022683 | -0.0021299 | -0.10986 | 59.9121 | -61.615 | 60.0128 | -61.4227 | -61.8805 | -61.8942 | -0.09613 | 59.8709 | -61.6608 | 59.9854 | -61.5967 | -61.7386 | -61.7706 | -0.036621 | -0.11444 | -0.013733 | 0.15564 | -0.31586 | -0.30212 | -0.27924 | -0.2655 | -0.082398 | -0.15564 | -0.041198 | -0.018311 | -0.19226 | -0.16022 | -0.10986 | -0.077819 | 0.19226 | 121.6278 | 0.064087 | 121.6461 | 121.5271 | 121.5317 | 121.4905 | 121.4493 | -121.6415 | -121.6873 | 121.5912 | 121.5637 | 61.4685 | 61.4822
248.25 | 121.7926 | -61.5509 | 60.0586 | 0.0031279 | 0.0014056 | 0.059195 | 0.055365 | 0.0027215 | -0.0072802 | -0.002382 | -0.005371 | 0.0026639 | 0.066347 | 0.068248 | -0.0071051 | 0.021187 | -0.0042661 | -0.022888 | 59.9396 | -61.5829 | 60.1227 | -61.3083 | -61.7661 | -61.7889 | 0.022888 | 59.9258 | -61.615 | 60.054 | -61.5143 | -61.6699 | -61.7111 | -0.032044 | -0.11902 | 0.064087 | 0.24261 | -0.23804 | -0.21515 | -0.20599 | -0.18311 | -0.064087 | -0.13275 | -0.004578 | 0.036621 | -0.16022 | -0.11902 | -0.096131 | -0.054932 | 0.27466 | 121.7056 | 0.10071 | 121.669 | 121.5225 | 121.5408 | 121.4905 | 121.4767 | -121.6415 | -121.6736 | 121.6736 | 121.6049 | 61.528 | 61.5738
249.9688 | 121.7789 | -61.5875 | 60.0357 | -0.0045011 | 0.0065326 | 0.058127 | 0.055792 | 0.0050713 | -0.005144 | -0.0015274 | -0.0084228 | 0.0043729 | 0.066774 | 0.051586 | -0.0083869 | 0.022042 | -0.0010617 | -0.11444 | 59.9396 | -61.6379 | 59.9991 | -61.4273 | -61.8759 | -61.8805 | -0.091553 | 59.8618 | -61.6608 | 59.9945 | -61.5738 | -61.7203 | -61.7569 | -0.050354 | -0.096131 | -0.036622 | 0.16022 | -0.29297 | -0.28839 | -0.24262 | -0.23804 | -0.073243 | -0.17395 | -0.041199 | 0.013732 | -0.16937 | -0.13275 | -0.09613 | -0.059509 | 0.21057 | 121.637 | 0.086975 | 121.6553 | 121.5775 | 121.5225 | 121.5271 | 121.4493 | -121.6736 | -121.6965 | 121.5866 | 121.582 | 61.4731 | 61.496
251.6719 | 121.9025 | -61.5189 | 60.0494 | -0.012131 | -0.0026532 | 0.056204 | 0.053015 | -0.0021919 | -0.0070666 | -0.0015274 | -0.0084228 | -0.00032692 | 0.065706 | 0.053081 | -0.010737 | 0.020546 | 0.0021425 | -0.032043 | 59.9075 | -61.5646 | 60.173 | -61.2167 | -61.6516 | -61.6791 | 0.12817 | 59.8938 | -61.5829 | 60.1639 | -61.3632 | -61.4822 | -61.5829 | -0.045776 | -0.14191 | 0.1236 | 0.30212 | -0.16022 | -0.13275 | -0.11444 | -0.086975 | -0.064087 | -0.15564 | 0.11444 | 0.15564 | -0.064087 | 0.036621 | 0 | 0.10071 | 0.3479 | 121.7377 | 0.21973 | 121.7468 | 121.4722 | 121.4767 | 121.4264 | 121.4127 | -121.6141 | -121.6324 | 121.6919 | 121.6827 | 61.4868 | 61.647
253.3438 | 121.875 | -61.4685 | 60.0723 | 0.0031279 | 0.00055118 | 0.058554 | 0.053869 | -0.0028327 | -0.0077074 | -0.0025956 | -0.0084228 | -0.00011332 | 0.066988 | 0.057567 | -0.010523 | 0.021401 | -0.00063445 | 0.022888 | 59.9213 | -61.5326 | 60.2234 | -61.1572 | -61.6287 | -61.6516 | 0.15106 | 59.8801 | -61.5463 | 60.1593 | -61.377 | -61.4822 | -61.6058 | -0.064087 | -0.15106 | 0.15106 | 0.31128 | -0.18311 | -0.16022 | -0.11902 | -0.09613 | -0.07782 | -0.19226 | 0.086975 | 0.091553 | -0.13733 | -0.013733 | -0.059509 | 0.064087 | 0.37537 | 121.756 | 0.16937 | 121.7056 | 121.4539 | 121.4264 | 121.3898 | 121.3486 | -121.6049 | -121.6187 | 121.6919 | 121.6278 | 61.4914 | 61.6196
255.0156 | 121.8063 | -61.5417 | 60.0586 | -0.012131 | 0.0035418 | 0.0577 | 0.057074 | -0.0019781 | -0.0070666 | -3.1996e-05 | -0.0023192 | 0.0022367 | 0.065279 | 0.06248 | -0.0071051 | 0.020333 | 6.346e-06 | -0.013733 | 59.9487 | -61.5692 | 60.1273 | -61.2946 | -61.7294 | -61.7661 | 0.068665 | 59.8984 | -61.5784 | 60.0723 | -61.4594 | -61.615 | -61.6745 | -0.027466 | -0.10986 | 0.068664 | 0.24719 | -0.2243 | -0.18768 | -0.19684 | -0.16022 | -0.036621 | -0.16022 | 0.013733 | 0.082397 | -0.13275 | -0.073242 | -0.096131 | -0.036621 | 0.27466 | 121.6965 | 0.11902 | 121.6507 | 121.5179 | 121.4767 | 121.4905 | 121.4401 | -121.6278 | -121.637 | 121.669 | 121.6141 | 61.528 | 61.6104
256.7344 | 121.8475 | -61.4914 | 60.0723 | -0.0045011 | 0.0014056 | 0.057059 | 0.053656 | -5.5462e-05 | -0.0081348 | -0.0015274 | -0.0023192 | 0.0011685 | 0.065493 | 0.060344 | -0.011378 | 0.023537 | -0.0057615 | 0.013733 | 59.9213 | -61.528 | 60.2142 | -61.2122 | -61.647 | -61.6791 | 0.11902 | 59.9075 | -61.5326 | 60.1456 | -61.3724 | -61.496 | -61.6058 | -0.036621 | -0.15106 | 0.14191 | 0.27924 | -0.18768 | -0.15564 | -0.15106 | -0.11902 | -0.041199 | -0.16479 | 0.073242 | 0.11902 | -0.11444 | -0.004578 | -0.073242 | 0.036621 | 0.31586 | 121.7422 | 0.16022 | 121.6782 | 121.4493 | 121.4401 | 121.4127 | 121.3989 | -121.6003 | -121.6049 | 121.7056 | 121.637 | 61.5051 | 61.6104
258.4531 | 121.8109 | -61.5372 | 60.0449 | -0.0045011 | 0.0024738 | 0.06069 | 0.057928 | -0.0017645 | -0.006853 | -0.00345 | -0.011475 | 0.0045865 | 0.066774 | 0.059917 | -0.0083869 | 0.017556 | -0.0061887 | -0.004578 | 59.9625 | -61.5738 | 60.1318 | -61.2991 | -61.7523 | -61.7706 | 0.054932 | 59.9167 | -61.5967 | 60.0815 | -61.4639 | -61.6196 | -61.6928 | -0.036622 | -0.082398 | 0.086975 | 0.23804 | -0.23346 | -0.21515 | -0.19684 | -0.17853 | -0.05951 | -0.12817 | 0.036621 | 0.073242 | -0.15564 | -0.082398 | -0.09613 | -0.022888 | 0.27466 | 121.7056 | 0.13275 | 121.6782 | 121.5363 | 121.5134 | 121.4996 | 121.4539 | -121.6187 | -121.6415 | 121.669 | 121.6187 | 61.5326 | 61.5921
260.1406 | 121.8979 | -61.4914 | 60.0494 | -0.0045011 | -0.00051702 | 0.057486 | 0.052374 | -5.5462e-05 | -0.0055712 | -0.0036636 | -0.0023192 | 0.00074128 | 0.066561 | 0.058849 | -0.0096685 | 0.018624 | -0.0036253 | 0.009155 | 59.9167 | -61.5326 | 60.2188 | -61.1664 | -61.6287 | -61.6608 | 0.16022 | 59.9167 | -61.5738 | 60.1593 | -61.3541 | -61.496 | -61.6013 | -0.041199 | -0.13275 | 0.16937 | 0.32501 | -0.16937 | -0.13733 | -0.12817 | -0.09613 | -0.082398 | -0.13275 | 0.10986 | 0.13733 | -0.10986 | -0.004578 | -0.027465 | 0.07782 | 0.36621 | 121.7514 | 0.21973 | 121.7331 | 121.4493 | 121.4905 | 121.4081 | 121.4081 | -121.582 | -121.6232 | 121.7102 | 121.6507 | 61.5005 | 61.6516
261.8281 | 121.7743 | -61.5829 | 59.9899 | -0.01976 | 0.0056782 | 0.058981 | 0.056219 | 0.00037174 | -0.0070666 | -0.0028092 | 0.00073235 | 0.0041593 | 0.065493 | 0.064617 | -0.0098823 | 0.019692 | -0.0025571 | -0.10986 | 59.9213 | -61.6058 | 59.9945 | -61.4319 | -61.8759 | -61.8988 | -0.086975 | 59.8709 | -61.6379 | 59.9854 | -61.5784 | -61.7203 | -61.7661 | -0.022888 | -0.068664 | 0.004578 | 0.15106 | -0.31586 | -0.29297 | -0.29297 | -0.27008 | -0.054931 | -0.11902 | -0.004577 | 0.004578 | -0.18311 | -0.13733 | -0.12817 | -0.082398 | 0.17395 | 121.6003 | 0.059509 | 121.6232 | 121.5271 | 121.5088 | 121.5042 | 121.4539 | -121.5958 | -121.6278 | 121.5775 | 121.5683 | 61.4731 | 61.496
263.5156 | 121.8842 | -61.5738 | 59.9579 | -0.012131 | 0.0024738 | 0.059622 | 0.056433 | -0.0013373 | -0.0083484 | -0.0032364 | 0.00073235 | 0.0026639 | 0.065279 | 0.063121 | -0.010523 | 0.021614 | -0.0025571 | -0.10529 | 59.8755 | -61.6058 | 60.1044 | -61.2991 | -61.7798 | -61.7661 | 0.041199 | 59.8389 | -61.6333 | 60.0952 | -61.4548 | -61.6104 | -61.6516 | -0.032043 | -0.082398 | 0.14648 | 0.27466 | -0.19226 | -0.20599 | -0.16022 | -0.17395 | -0.059509 | -0.11902 | 0.13733 | 0.11902 | -0.077819 | -0.036621 | -0.01831 | 0.022888 | 0.3067 | 121.7102 | 0.17853 | 121.7285 | 121.4813 | 121.4722 | 121.4493 | 121.4127 | -121.5637 | -121.5912 | 121.6782 | 121.669 | 61.4685 | 61.615
265.1875 | 121.7834 | -61.5921 | 59.9991 | -0.0045011 | 0.0054644 | 0.057913 | 0.057074 | 0.00079894 | -0.0087756 | -0.001741 | -0.0023192 | 0.0028775 | 0.066988 | 0.056072 | -0.0062507 | 0.020333 | -0.0051205 | -0.1236 | 59.9121 | -61.6058 | 60.0128 | -61.4227 | -61.8759 | -61.8668 | -0.073242 | 59.8663 | -61.6699 | 60.0037 | -61.5738 | -61.7157 | -61.7569 | -0.013733 | -0.086975 | 0.013733 | 0.16937 | -0.27466 | -0.28381 | -0.26093 | -0.27008 | -0.07782 | -0.13275 | 0.004578 | 0.01831 | -0.1648 | -0.1236 | -0.086975 | -0.045776 | 0.18311 | 121.6187 | 0.09613 | 121.6736 | 121.5179 | 121.5363 | 121.5042 | 121.4584 | -121.6049 | -121.669 | 121.6049 | 121.5958 | 61.4685 | 61.5189
266.875 | 121.8521 | -61.5051 | 60.0677 | -0.012131 | -0.0017986 | 0.05834 | 0.05451 | 0.0018671 | -0.006853 | -0.00345 | -0.005371 | 0.00095488 | 0.066774 | 0.057781 | -0.011164 | 0.021401 | 0.0040651 | 0.027466 | 59.9304 | -61.5509 | 60.2234 | -61.203 | -61.6562 | -61.6608 | 0.12817 | 59.9075 | -61.5509 | 60.1318 | -61.3632 | -61.5097 | -61.615 | -0.045776 | -0.13733 | 0.15564 | 0.30212 | -0.15564 | -0.15106 | -0.10986 | -0.10529 | -0.045776 | -0.16022 | 0.064087 | 0.14191 | -0.10986 | -0.004578 | -0.064087 | 0.041198 | 0.3479 | 121.7743 | 0.18768 | 121.6827 | 121.4813 | 121.4584 | 121.4355 | 121.4127 | -121.6187 | -121.6187 | 121.7285 | 121.637 | 61.5326 | 61.6333
268.5781 | 121.8842 | -61.5097 | 60.0632 | -0.0045011 | 0.00055118 | 0.057272 | 0.05152 | -0.00069646 | -0.0053576 | -0.002382 | -0.011475 | 0.0024503 | 0.063784 | 0.051586 | -0.01031 | 0.020119 | -0.0049069 | 0.018311 | 59.9487 | -61.5326 | 60.2325 | -61.1618 | -61.6196 | -61.6562 | 0.16479 | 59.8938 | -61.528 | 60.1685 | -61.3541 | -61.4777 | -61.5875 | -0.022888 | -0.11444 | 0.16937 | 0.3479 | -0.14648 | -0.10986 | -0.1236 | -0.086975 | -0.01831 | -0.16937 | 0.10529 | 0.15564 | -0.077819 | 0.032044 | -0.059509 | 0.050354 | 0.37079 | 121.7651 | 0.17395 | 121.6965 | 121.4813 | 121.4218 | 121.4584 | 121.4035 | -121.5958 | -121.5912 | 121.7422 | 121.6782 | 61.528 | 61.6745
270.3125 | 121.7743 | -61.5692 | 60.0082 | -0.012131 | 0.0035418 | 0.059195 | 0.056646 | -0.00091006 | -0.0072802 | -0.001741 | -0.005371 | 0.0028775 | 0.064852 | 0.055644 | -0.0071051 | 0.018196 | -0.0064023 | -0.10071 | 59.8938 | -61.6013 | 60.0082 | -61.441 | -61.8851 | -61.8759 | -0.09613 | 59.8984 | -61.6699 | 59.9945 | -61.5784 | -61.7294 | -61.7569 | -0.032043 | -0.11444 | 0 | 0.12817 | -0.3067 | -0.31586 | -0.27466 | -0.28381 | -0.10071 | -0.10986 | -0.013733 | -0.009155 | -0.18768 | -0.16022 | -0.086975 | -0.059509 | 0.16022 | 121.6095 | 0.091553 | 121.6644 | 121.4951 | 121.5683 | 121.463 | 121.4676 | -121.6095 | -121.6782 | 121.5775 | 121.5637 | 61.4685 | 61.4731
272 | 121.8933 | -61.5509 | 59.9808 | -0.0045011 | 0.0041828 | 0.056204 | 0.055151 | 0.0037897 | -0.0040758 | -0.0015274 | -0.0023192 | 0.0020231 | 0.063143 | 0.056072 | -0.0088141 | 0.020333 | -0.0038389 | -0.064087 | 59.8709 | -61.5921 | 60.1273 | -61.29 | -61.7477 | -61.7615 | 0.064087 | 59.8251 | -61.6425 | 60.0952 | -61.4502 | -61.5921 | -61.6562 | -0.041199 | -0.10986 | 0.14648 | 0.26093 | -0.21057 | -0.19684 | -0.16937 | -0.15564 | -0.091553 | -0.15564 | 0.11444 | 0.10071 | -0.10529 | -0.041199 | -0.013733 | 0.050354 | 0.30212 | 121.7194 | 0.19226 | 121.7377 | 121.463 | 121.4676 | 121.4218 | 121.376 | -121.5729 | -121.6232 | 121.6782 | 121.6461 | 61.4868 | 61.615
273.6875 | 121.8521 | -61.5372 | 60.022 | -0.012131 | 0.002901 | 0.057272 | 0.05451 | -0.0049689 | -0.006853 | -0.0019546 | -0.0084228 | 0.00010048 | 0.06592 | 0.059917 | -0.01031 | 0.020546 | -0.0042661 | -0.09613 | 59.8938 | -61.5921 | 60.1135 | -61.3129 | -61.7615 | -61.7615 | 0 | 59.8526 | -61.6058 | 60.0677 | -61.4777 | -61.6058 | -61.6837 | -0.054932 | -0.12817 | 0.091552 | 0.2243 | -0.2243 | -0.2243 | -0.16937 | -0.16937 | -0.068665 | -0.16937 | 0.045776 | 0.059509 | -0.14648 | -0.068665 | -0.07782 | 0 | 0.27924 | 121.7056 | 0.12817 | 121.6736 | 121.4859 | 121.4584 | 121.431 | 121.3898 | -121.6141 | -121.6278 | 121.6507 | 121.6049 | 61.441 | 61.5372
275.4531 | 121.8155 | -61.5005 | 60.0815 | -0.012131 | 0.00033758 | 0.060049 | 0.056433 | -0.0017645 | -0.0098438 | -0.0030228 | -0.005371 | 0.0026639 | 0.066561 | 0.059062 | -0.0088141 | 0.019051 | -0.0027707 | 0.027466 | 59.935 | -61.496 | 60.2005 | -61.2213 | -61.6608 | -61.6699 | 0.11444 | 59.935 | -61.5601 | 60.1135 | -61.4182 | -61.5509 | -61.6379 | 0.004577 | -0.14648 | 0.11902 | 0.27924 | -0.16937 | -0.16022 | -0.17395 | -0.16479 | -0.05951 | -0.14648 | 0.032043 | 0.082397 | -0.13733 | -0.050354 | -0.077819 | 0.009156 | 0.27466 | 121.6965 | 0.14191 | 121.6736 | 121.431 | 121.4951 | 121.4355 | 121.4355 | -121.5775 | -121.6415 | 121.701 | 121.6141 | 61.528 | 61.615
277.1406 | 121.7606 | -61.5875 | 60.0174 | -0.012131 | 0.0037556 | 0.058768 | 0.05686 | 0.0010125 | -0.0070666 | -0.0013138 | -0.0084228 | 0.0035183 | 0.065279 | 0.063335 | -0.0077459 | 0.019051 | -0.0040525 | -0.036621 | 59.9304 | -61.5738 | 60.0861 | -61.3632 | -61.821 | -61.8393 | -0.013733 | 59.8938 | -61.6333 | 60.0128 | -61.5417 | -61.7157 | -61.7477 | 0.013732 | -0.086975 | 0.068665 | 0.2243 | -0.25177 | -0.23346 | -0.2655 | -0.24719 | -0.045777 | -0.1236 | -0.004578 | 0.045776 | -0.16022 | -0.12817 | -0.11444 | -0.082397 | 0.21057 | 121.6599 | 0.091553 | 121.6461 | 121.5042 | 121.5271 | 121.5179 | 121.4813 | -121.5912 | -121.6507 | 121.6736 | 121.6003 | 61.5509 | 61.5738
278.8594 | 121.8567 | -61.5234 | 60.0174 | -0.012131 | 0.0014056 | 0.058768 | 0.053228 | 0.0029351 | -0.0064258 | -0.0028092 | -0.0084228 | 0.00074128 | 0.067842 | 0.055644 | -0.011378 | 0.020974 | -0.0029843 | -0.082397 | 59.9075 | -61.5829 | 60.1089 | -61.2946 | -61.734 | -61.7569 | 0.027466 | 59.8801 | -61.6058 | 60.0861 | -61.4365 | -61.5509 | -61.6379 | -0.05951 | -0.10986 | 0.091553 | 0.22888 | -0.23346 | -0.21057 | -0.17395 | -0.15106 | -0.082398 | -0.13733 | 0.068665 | 0.086975 | -0.11444 | -0.027466 | -0.032043 | 0.054932 | 0.28839 | 121.6919 | 0.16937 | 121.6919 | 121.4905 | 121.4859 | 121.431 | 121.4035 | -121.6003 | -121.6232 | 121.6324 | 121.6095 | 61.441 | 61.5509
280.5469 | 121.7697 | -61.5601 | 60.0494 | -0.012131 | 0.0033282 | 0.05834 | 0.056219 | -0.0015509 | -0.0081348 | -0.0002456 | -0.0084228 | 0.0024503 | 0.066988 | 0.05949 | -0.0060369 | 0.019692 | -0.0066159 | -0.009155 | 59.9579 | -61.5646 | 60.1089 | -61.3083 | -61.7706 | -61.7889 | 0.054932 | 59.903 | -61.6104 | 60.0586 | -61.5097 | -61.6699 | -61.7065 | -0.004577 | -0.091552 | 0.05951 | 0.25177 | -0.22888 | -0.21057 | -0.2243 | -0.20599 | -0.050354 | -0.14648 | 0.009156 | 0.050354 | -0.14648 | -0.10986 | -0.09613 | -0.059509 | 0.25635 | 121.6736 | 0.10071 | 121.669 | 121.5225 | 121.5134 | 121.5179 | 121.463 | -121.6141 | -121.6599 | 121.669 | 121.6187 | 61.5509 | 61.615
282.3281 | 121.7468 | -61.5921 | 60.0311 | -0.012131 | 0.006319 | 0.058554 | 0.058142 | 0.0016535 | -0.0062122 | 0.0003952 | -0.0023192 | 0.0041593 | 0.064424 | 0.06248 | -0.0071051 | 0.018624 | -0.0070433 | -0.086975 | 59.9213 | -61.6333 | 60.0403 | -61.4227 | -61.8713 | -61.8622 | -0.086975 | 59.9075 | -61.647 | 59.9808 | -61.5875 | -61.7294 | -61.7844 | -0.041199 | -0.10986 | 0.009155 | 0.16937 | -0.27008 | -0.27924 | -0.22888 | -0.23804 | -0.054932 | -0.1236 | -0.050354 | 0.004578 | -0.19226 | -0.13733 | -0.13733 | -0.082397 | 0.21057 | 121.6736 | 0.05951 | 121.6278 | 121.5546 | 121.5546 | 121.5134 | 121.4996 | -121.6644 | -121.6782 | 121.6324 | 121.5729 | 61.5051 | 61.5051
284.0312 | 121.7606 | -61.6013 | 60.0357 | -0.0045011 | 0.0065326 | 0.060263 | 0.058142 | -5.5462e-05 | -0.0047168 | -0.000673 | -0.0084228 | 0.0035183 | 0.067629 | 0.058635 | -0.0064643 | 0.021828 | -0.0038389 | -0.11444 | 59.9808 | -61.6196 | 59.9854 | -61.441 | -61.8942 | -61.8805 | -0.086975 | 59.8755 | -61.6562 | 59.9854 | -61.5875 | -61.7294 | -61.7844 | -0.018311 | -0.054932 | -0.050354 | 0.16022 | -0.27924 | -0.29297 | -0.26093 | -0.27466 | -0.054932 | -0.16022 | -0.050354 | 0.013733 | -0.18311 | -0.12817 | -0.12817 | -0.073242 | 0.17853 | 121.6049 | 0.068665 | 121.6415 | 121.6003 | 121.5317 | 121.582 | 121.4767 | -121.6553 | -121.6919 | 121.5866 | 121.5866 | 61.4868 | 61.5143
285.7031 | 121.7422 | -61.5875 | 60.0494 | -0.0045011 | 0.0052508 | 0.058981 | 0.058142 | -0.00048286 | -0.0057848 | -0.0015274 | -0.005371 | 0.0041593 | 0.066133 | 0.057353 | -0.0062507 | 0.020974 | -0.00084805 | -0.12817 | 59.9304 | -61.6196 | 60.0174 | -61.4456 | -61.8851 | -61.8759 | -0.082397 | 59.8709 | -61.6653 | 59.9854 | -61.6013 | -61.7386 | -61.7706 | -0.032044 | -0.11902 | -0.032043 | 0.14191 | -0.28839 | -0.29755 | -0.25635 | -0.2655 | -0.07782 | -0.17853 | -0.064086 | -0.013733 | -0.18311 | -0.15106 | -0.10529 | -0.073242 | 0.17395 | 121.637 | 0.064087 | 121.6507 | 121.55 | 121.5363 | 121.5179 | 121.4584 | -121.669 | -121.7148 | 121.6049 | 121.5729 | 61.4594 | 61.5051
287.4062 | 121.756 | -61.5189 | 60.1089 | -0.0045011 | 0.0014056 | 0.057059 | 0.056006 | -0.00026906 | -0.0081348 | -0.001741 | -0.0084228 | 0.0054409 | 0.066347 | 0.053081 | -0.0073187 | 0.021401 | -0.0031979 | -0.032043 | 60.0037 | -61.5509 | 60.0998 | -61.3403 | -61.7477 | -61.7798 | -0.009155 | 59.9716 | -61.5692 | 60.0586 | -61.496 | -61.6241 | -61.702 | -0.032043 | -0.10529 | -0.009156 | 0.17853 | -0.26093 | -0.22888 | -0.22888 | -0.19684 | -0.050354 | -0.13733 | -0.050354 | 0.022888 | -0.18311 | -0.10529 | -0.13275 | -0.054932 | 0.21057 | 121.6507 | 0.073242 | 121.6278 | 121.5546 | 121.5408 | 121.5225 | 121.4905 | -121.6599 | -121.6782 | 121.6187 | 121.5775 | 61.4868 | 61.5097
289.125 | 121.788 | -61.5509 | 60.0266 | -0.01976 | 0.00461 | 0.060477 | 0.057928 | 0.00079894 | -0.0045032 | 0.0003952 | -0.0084228 | 0.0050137 | 0.064852 | 0.061199 | -0.0071051 | 0.019905 | -0.0025571 | -0.009155 | 59.9625 | -61.5784 | 60.1044 | -61.2946 | -61.7523 | -61.7889 | 0.036621 | 59.8938 | -61.615 | 60.0632 | -61.4868 | -61.6562 | -61.6974 | -0.027466 | -0.064087 | 0.07782 | 0.25635 | -0.23804 | -0.20142 | -0.21057 | -0.17395 | -0.064087 | -0.13275 | 0.036621 | 0.064087 | -0.14648 | -0.10529 | -0.082398 | -0.041199 | 0.28381 | 121.6827 | 0.12817 | 121.6782 | 121.5408 | 121.5088 | 121.5134 | 121.4447 | -121.6049 | -121.6415 | 121.6553 | 121.6141 | 61.5417 | 61.5875
290.8281 | 121.8887 | -61.4685 | 60.0494 | -0.012131 | 0.0024738 | 0.056845 | 0.055792 | -0.0017645 | -0.0074938 | -0.0002456 | -0.005371 | -0.0013949 | 0.066988 | 0.053935 | -0.0098823 | 0.024605 | -0.0019163 | -0.009155 | 59.9075 | -61.5326 | 60.2005 | -61.1526 | -61.615 | -61.6425 | 0.16022 | 59.8846 | -61.5463 | 60.1593 | -61.3449 | -61.4731 | -61.5875 | -0.064087 | -0.14191 | 0.15106 | 0.31586 | -0.17395 | -0.14648 | -0.10986 | -0.082397 | -0.07782 | -0.16479 | 0.10986 | 0.1236 | -0.11902 | -0.004577 | -0.041198 | 0.073243 | 0.37994 | 121.7331 | 0.20142 | 121.7056 | 121.4401 | 121.431 | 121.376 | 121.3531 | -121.582 | -121.5958 | 121.669 | 121.6278 | 61.4594 | 61.6287
292.5156 | 121.7331 | -61.6013 | 60.0266 | -0.012131 | 0.0061054 | 0.057272 | 0.055792 | 0.0014397 | -0.005144 | -0.0040908 | -0.0023192 | 0.0039457 | 0.065279 | 0.054576 | -0.0088141 | 0.020546 | 0.0023563 | -0.10071 | 59.9304 | -61.6058 | 60.0128 | -61.4273 | -61.8851 | -61.8759 | -0.10529 | 59.8846 | -61.6608 | 59.9899 | -61.5829 | -61.7294 | -61.7706 | -0.004578 | -0.09613 | -0.013733 | 0.17395 | -0.27466 | -0.28381 | -0.27008 | -0.27924 | -0.05951 | -0.14191 | -0.036621 | 0.01831 | -0.16937 | -0.12817 | -0.10986 | -0.068664 | 0.17853 | 121.6187 | 0.07782 | 121.6507 | 121.5363 | 121.5454 | 121.5317 | 121.4859 | -121.6324 | -121.6873 | 121.6141 | 121.5912 | 61.5005 | 61.496
294.2031 | 121.8887 | -61.5784 | 59.967 | -0.02739 | 0.0037556 | 0.059836 | 0.055792 | -0.0024055 | -0.0049304 | -0.0013138 | -0.0023192 | 0.0018095 | 0.066774 | 0.055004 | -0.0090277 | 0.020546 | -0.00042085 | -0.064087 | 59.8663 | -61.5692 | 60.1227 | -61.2808 | -61.7569 | -61.7844 | 0.045776 | 59.8114 | -61.6379 | 60.0861 | -61.441 | -61.5967 | -61.6562 | 0.009155 | -0.10071 | 0.15564 | 0.29755 | -0.20599 | -0.17853 | -0.21515 | -0.18768 | -0.059509 | -0.15564 | 0.11902 | 0.13733 | -0.07782 | -0.018311 | -0.018311 | 0.041198 | 0.28839 | 121.6919 | 0.19684 | 121.7239 | 121.4355 | 121.4493 | 121.4447 | 121.3898 | -121.5363 | -121.6049 | 121.7011 | 121.6644 | 61.5143 | 61.6241
295.9062 | 121.8979 | -61.5005 | 60.0586 | -0.012131 | 0.00055118 | 0.057272 | 0.054297 | -0.00091006 | -0.0077074 | -0.000673 | -0.011475 | 0.00074128 | 0.064852 | 0.056285 | -0.010737 | 0.021187 | -0.0014891 | -0.027466 | 59.9075 | -61.5417 | 60.1685 | -61.2213 | -61.6791 | -61.6837 | 0.13275 | 59.8846 | -61.5875 | 60.1456 | -61.3678 | -61.496 | -61.5921 | -0.041199 | -0.15106 | 0.10986 | 0.27924 | -0.18311 | -0.17853 | -0.14191 | -0.13733 | -0.086975 | -0.17395 | 0.086975 | 0.13275 | -0.091553 | 0.004577 | -0.004578 | 0.091552 | 0.32043 | 121.7102 | 0.21973 | 121.7331 | 121.4493 | 121.4722 | 121.4081 | 121.3852 | -121.6003 | -121.6461 | 121.669 | 121.6461 | 61.4731 | 61.6333
297.6094 | 121.8933 | -61.5005 | 60.054 | -0.012131 | -0.00030342 | 0.055136 | 0.053656 | -0.00048286 | -0.0089892 | -0.001741 | -0.0023192 | 0.0020231 | 0.06592 | 0.059062 | -0.01095 | 0.020974 | 0.00043375 | 0.027466 | 59.9304 | -61.5189 | 60.2234 | -61.171 | -61.6287 | -61.6562 | 0.16022 | 59.9213 | -61.5646 | 60.1547 | -61.3678 | -61.4914 | -61.5875 | -0.018311 | -0.1236 | 0.16937 | 0.32959 | -0.15564 | -0.12817 | -0.13733 | -0.10986 | -0.064087 | -0.13275 | 0.10071 | 0.13275 | -0.086975 | 0.009155 | -0.022888 | 0.073242 | 0.3479 | 121.7422 | 0.19684 | 121.7194 | 121.4493 | 121.4859 | 121.431 | 121.4218 | -121.5729 | -121.6187 | 121.7239 | 121.6553 | 61.528 | 61.6608
299.3438 | 121.7697 | -61.5463 | 60.0494 | -0.012131 | 0.0039692 | 0.061118 | 0.057287 | -0.0019781 | -0.0047168 | -0.0021682 | -0.0023192 | 0.0011685 | 0.063784 | 0.056926 | -0.0088141 | 0.020119 | -0.00063445 | -0.032043 | 59.9396 | -61.5738 | 60.0998 | -61.3129 | -61.7935 | -61.7889 | 0.036621 | 59.9213 | -61.5967 | 60.0266 | -61.528 | -61.6837 | -61.7249 | -0.027466 | -0.10986 | 0.050354 | 0.23346 | -0.24261 | -0.24719 | -0.21515 | -0.21973 | -0.050354 | -0.12817 | -0.022888 | 0.018311 | -0.17853 | -0.13733 | -0.12817 | -0.086975 | 0.26093 | 121.6736 | 0.068665 | 121.6232 | 121.5134 | 121.5179 | 121.4859 | 121.4676 | -121.6232 | -121.6461 | 121.6461 | 121.5729 | 61.5143 | 61.5829
301.0312 | 121.7972 | -61.5005 | 60.0861 | -0.0045011 | 0.0024738 | 0.056204 | 0.055792 | -0.0049689 | -0.0074938 | -0.0002456 | -0.0023192 | 0.0028775 | 0.065493 | 0.052226 | -0.011805 | 0.020974 | -0.0031979 | 0.018311 | 59.9396 | -61.5326 | 60.1685 | -61.2076 | -61.6653 | -61.702 | 0.091553 | 59.9442 | -61.5646 | 60.0815 | -61.4319 | -61.5692 | -61.6608 | -0.032044 | -0.14649 | 0.082397 | 0.29297 | -0.20142 | -0.16479 | -0.16937 | -0.13275 | -0.064087 | -0.14191 | -0.004578 | 0.068664 | -0.16022 | -0.068665 | -0.096131 | -0.004578 | 0.32501 | 121.701 | 0.13275 | 121.6461 | 121.4722 | 121.5088 | 121.4401 | 121.4447 | -121.6187 | -121.6507 | 121.669 | 121.582 | 61.5189 | 61.5921
302.7344 | 121.7514 | -61.5646 | 60.0174 | -0.012131 | 0.0052508 | 0.057272 | 0.057928 | -0.00091006 | -0.005144 | -3.1996e-05 | -0.005371 | 0.0026639 | 0.066561 | 0.056926 | -0.0066779 | 0.019051 | -0.0038389 | -0.10071 | 59.935 | -61.5875 | 60.0082 | -61.4502 | -61.8988 | -61.8942 | -0.09613 | 59.9121 | -61.6333 | 59.9808 | -61.5967 | -61.7432 | -61.7661 | -0.022888 | -0.082397 | -0.009155 | 0.11444 | -0.32959 | -0.33417 | -0.3067 | -0.31128 | -0.068665 | -0.10529 | -0.036621 | -0.032044 | -0.20142 | -0.17853 | -0.13275 | -0.10986 | 0.13733 | 121.5958 | 0.036621 | 121.6141 | 121.5225 | 121.5454 | 121.4996 | 121.4767 | -121.6049 | -121.6507 | 121.5729 | 121.5454 | 61.4639 | 61.4685
304.4219 | 121.8201 | -61.5097 | 60.0815 | -0.012131 | -0.0011578 | 0.057272 | 0.051733 | 0.0022943 | -0.0066394 | -0.0008866 | -0.0023192 | 0.0018095 | 0.066774 | 0.051799 | -0.011164 | 0.021401 | -0.00042085 | 0.027466 | 59.9304 | -61.5372 | 60.1822 | -61.2122 | -61.6425 | -61.6653 | 0.10071 | 59.9213 | -61.5784 | 60.1135 | -61.4136 | -61.5509 | -61.647 | -0.027465 | -0.15106 | 0.10071 | 0.29755 | -0.15564 | -0.13275 | -0.12817 | -0.10529 | -0.068664 | -0.16022 | 0.032043 | 0.096131 | -0.13733 | -0.041198 | -0.068665 | 0.027466 | 0.32501 | 121.7194 | 0.1648 | 121.6919 | 121.4676 | 121.4996 | 121.4401 | 121.431 | -121.6187 | -121.6599 | 121.6919 | 121.6232 | 61.5372 | 61.6104
306.125 | 121.875 | -61.5509 | 59.9625 | -0.02739 | 0.0037556 | 0.05834 | 0.056219 | 0.0065667 | -0.0045032 | -0.0011002 | -0.005371 | 0.00074128 | 0.066347 | 0.05949 | -0.0088141 | 0.019478 | -0.0042661 | -0.091553 | 59.8846 | -61.615 | 60.0952 | -61.3266 | -61.7706 | -61.7661 | 0.041199 | 59.8572 | -61.6241 | 60.0998 | -61.4731 | -61.5967 | -61.647 | -0.064087 | -0.077819 | 0.13275 | 0.2243 | -0.21515 | -0.21973 | -0.15106 | -0.15564 | -0.073243 | -0.10529 | 0.13733 | 0.07782 | -0.096131 | -0.045777 | -0.022888 | 0.027466 | 0.28839 | 121.7102 | 0.15106 | 121.7239 | 121.4996 | 121.4813 | 121.4355 | 121.4081 | -121.5775 | -121.5866 | 121.6461 | 121.6507 | 61.4594 | 61.5921
307.8281 | 121.8109 | -61.5372 | 60.0586 | -0.0045011 | 0.0061054 | 0.060049 | 0.056646 | 0.0012261 | -0.006853 | -0.002382 | -0.005371 | 0.0028775 | 0.066774 | 0.059917 | -0.0090277 | 0.019905 | -0.0036253 | -0.009155 | 59.9808 | -61.5646 | 60.1227 | -61.2854 | -61.7569 | -61.7661 | 0.073242 | 59.9167 | -61.6058 | 60.0861 | -61.4594 | -61.5967 | -61.6745 | -0.027466 | -0.07782 | 0.064087 | 0.25177 | -0.22888 | -0.21973 | -0.20142 | -0.19226 | -0.068665 | -0.14191 | 0.027466 | 0.077819 | -0.13733 | -0.05951 | -0.068665 | 0.009155 | 0.27924 | 121.6873 | 0.14648 | 121.6919 | 121.5454 | 121.5225 | 121.5179 | 121.4539 | -121.6232 | -121.6644 | 121.6599 | 121.6232 | 61.528 | 61.6104
309.5312 | 121.8842 | -61.496 | 60.0449 | -0.012131 | -0.00030342 | 0.057913 | 0.053015 | -0.0026191 | -0.006853 | -0.000673 | -0.0084228 | 0.00031408 | 0.066561 | 0.058208 | -0.011805 | 0.021828 | -0.0019163 | -0.004578 | 59.8892 | -61.5555 | 60.2234 | -61.1526 | -61.6196 | -61.647 | 0.13275 | 59.8846 | -61.5463 | 60.1593 | -61.3403 | -61.4731 | -61.5829 | -0.059509 | -0.15564 | 0.17853 | 0.34332 | -0.15106 | -0.1236 | -0.091553 | -0.064087 | -0.050354 | -0.16022 | 0.11444 | 0.15564 | -0.086975 | 0.022889 | -0.036621 | 0.073243 | 0.40283 | 121.7789 | 0.20599 | 121.7056 | 121.4447 | 121.431 | 121.3852 | 121.3806 | -121.6003 | -121.5912 | 121.7194 | 121.6553 | 61.4914 | 61.6287
311.2031 | 121.7468 | -61.5189 | 60.1135 | -0.0045011 | -8.9824e-05 | 0.056845 | 0.05451 | -0.0028327 | -0.0074938 | 0.0001816 | -0.0023192 | 0.0022367 | 0.065065 | 0.057353 | -0.01095 | 0.02076 | -0.00020725 | -0.032043 | 59.9991 | -61.5463 | 60.1044 | -61.3266 | -61.7706 | -61.7615 | 0.013733 | 59.9625 | -61.5921 | 60.0494 | -61.4685 | -61.6058 | -61.7111 | -0.027466 | -0.11444 | -0.009155 | 0.19226 | -0.24262 | -0.25177 | -0.21515 | -0.2243 | -0.073242 | -0.15106 | -0.064087 | 0.050354 | -0.19226 | -0.086975 | -0.11902 | -0.013733 | 0.21973 | 121.6507 | 0.1236 | 121.6415 | 121.5454 | 121.5546 | 121.5179 | 121.4813 | -121.6599 | -121.7056 | 121.6232 | 121.5683 | 61.4868 | 61.5326
312.875 | 121.8796 | -61.5555 | 59.9899 | -0.012131 | 0.0035418 | 0.05834 | 0.055365 | -0.0015509 | -0.0066394 | -0.001741 | -0.005371 | 0.0011685 | 0.06592 | 0.060131 | -0.01031 | 0.021828 | -0.00084805 | -0.068665 | 59.8343 | -61.5738 | 60.1318 | -61.29 | -61.7752 | -61.7615 | 0.054932 | 59.7885 | -61.6699 | 60.0861 | -61.4502 | -61.5921 | -61.6608 | -0.018311 | -0.15564 | 0.14191 | 0.2655 | -0.20599 | -0.21973 | -0.18768 | -0.20142 | -0.11444 | -0.20142 | 0.096131 | 0.10529 | -0.10529 | -0.036621 | 0.009155 | 0.07782 | 0.28381 | 121.7056 | 0.21973 | 121.756 | 121.4081 | 121.4584 | 121.3898 | 121.344 | -121.5637 | -121.6599 | 121.6873 | 121.6415 | 61.4868 | 61.6104
314.5625 | 121.8246 | -61.5326 | 60.0082 | -0.012131 | 0.0039692 | 0.056631 | 0.054297 | 0.0016535 | -0.0059986 | -0.00345 | -0.0023192 | 0.0013821 | 0.067842 | 0.060771 | -0.010523 | 0.020546 | -0.0029843 | -0.086975 | 59.8984 | -61.5967 | 60.1135 | -61.3083 | -61.7569 | -61.7569 | 0 | 59.8846 | -61.5967 | 60.0723 | -61.4639 | -61.5875 | -61.6837 | -0.064087 | -0.10986 | 0.10529 | 0.2243 | -0.2243 | -0.2243 | -0.16022 | -0.16022 | -0.064087 | -0.1236 | 0.064087 | 0.068665 | -0.15106 | -0.054931 | -0.086975 | 0.009156 | 0.28839 | 121.7102 | 0.13275 | 121.669 | 121.4951 | 121.4813 | 121.431 | 121.4172 | -121.6049 | -121.6049 | 121.6461 | 121.6049 | 61.4456 | 61.5326
316.2969 | 121.8246 | -61.5738 | 59.9945 | -0.0045011 | 0.002901 | 0.057913 | 0.055151 | 0.00015814 | -0.0062122 | -0.0032364 | -0.005371 | 0.00095488 | 0.064211 | 0.058849 | -0.0088141 | 0.021187 | -0.0049069 | -0.082397 | 59.8938 | -61.5784 | 60.0998 | -61.2991 | -61.7706 | -61.7523 | 0.013733 | 59.8389 | -61.6058 | 60.0723 | -61.4822 | -61.6013 | -61.6791 | -0.004577 | -0.10071 | 0.10529 | 0.27466 | -0.17853 | -0.19684 | -0.17395 | -0.19226 | -0.032043 | -0.15564 | 0.07782 | 0.091553 | -0.10529 | -0.027465 | -0.073242 | 0.004578 | 0.27924 | 121.6782 | 0.1236 | 121.6782 | 121.4722 | 121.4447 | 121.4676 | 121.4127 | -121.5729 | -121.6003 | 121.6736 | 121.6461 | 61.4914 | 61.5875
317.9844 | 121.8887 | -61.5509 | 59.9487 | -0.012131 | 0.0054644 | 0.058554 | 0.057715 | 0.00037174 | -0.0057848 | -0.0004592 | -0.0023192 | 0.00095488 | 0.063356 | 0.058422 | -0.0068915 | 0.023323 | -0.0042661 | -0.07782 | 59.8526 | -61.615 | 60.1318 | -61.2991 | -61.7523 | -61.7706 | 0.036621 | 59.8434 | -61.6333 | 60.0998 | -61.4639 | -61.5875 | -61.6516 | -0.064087 | -0.09613 | 0.18311 | 0.25177 | -0.21973 | -0.20142 | -0.15564 | -0.13733 | -0.082398 | -0.10528 | 0.15106 | 0.086975 | -0.10071 | -0.036621 | -0.01831 | 0.045777 | 0.31586 | 121.7468 | 0.16937 | 121.7331 | 121.4676 | 121.4767 | 121.4035 | 121.3943 | -121.5637 | -121.582 | 121.6827 | 121.6507 | 61.4731 | 61.5875
319.6875 | 121.756 | -61.5189 | 60.1181 | -0.012131 | 0.00033758 | 0.055991 | 0.056219 | -0.00091006 | -0.0062122 | -0.0015274 | -0.0023192 | 0.0026639 | 0.066561 | 0.058208 | -0.0086005 | 0.017983 | -0.0029843 | -0.027466 | 59.9808 | -61.5463 | 60.1089 | -61.322 | -61.7477 | -61.7661 | 0.013733 | 59.9716 | -61.5829 | 60.0494 | -61.4685 | -61.6196 | -61.6882 | -0.027466 | -0.13733 | -0.009155 | 0.19684 | -0.24719 | -0.22888 | -0.21973 | -0.20142 | -0.064087 | -0.14648 | -0.068665 | 0.050354 | -0.16937 | -0.10071 | -0.10529 | -0.036621 | 0.22431 | 121.6553 | 0.11444 | 121.6324 | 121.5271 | 121.5546 | 121.4996 | 121.4905 | -121.6644 | -121.701 | 121.6278 | 121.5683 | 61.4914 | 61.5326
321.3594 | 121.7789 | -61.5326 | 60.0952 | 0.0031279 | 0.00097838 | 0.057913 | 0.057501 | 0.0042169 | -0.0089892 | -0.0002456 | -0.005371 | 0.0022367 | 0.066347 | 0.056072 | -0.010096 | 0.019265 | -0.0046933 | -0.022888 | 59.9945 | -61.5601 | 60.0952 | -61.322 | -61.7661 | -61.7798 | 0 | 59.9762 | -61.5875 | 60.0449 | -61.4914 | -61.6287 | -61.6928 | -0.027466 | -0.10071 | 0 | 0.21057 | -0.24719 | -0.23346 | -0.21973 | -0.20599 | -0.054931 | -0.11902 | -0.050354 | 0.041199 | -0.16022 | -0.09613 | -0.10529 | -0.041199 | 0.23804 | 121.6553 | 0.09613 | 121.6324 | 121.5546 | 121.5637 | 121.5271 | 121.5088 | -121.6553 | -121.6827 | 121.6278 | 121.5775 | 61.5097 | 61.5326
323.0625 | 121.8292 | -61.5417 | 60.0403 | -0.01976 | 0.0020466 | 0.056845 | 0.054083 | -0.0015509 | -0.006853 | -0.001741 | -0.0023192 | 0.0024503 | 0.065279 | 0.057567 | -0.0086005 | 0.02076 | -0.0068295 | -0.086975 | 59.9075 | -61.5784 | 60.1135 | -61.3174 | -61.7477 | -61.7615 | 0 | 59.8755 | -61.5967 | 60.0632 | -61.4639 | -61.5875 | -61.6699 | -0.036621 | -0.13275 | 0.073242 | 0.2243 | -0.21973 | -0.20599 | -0.18311 | -0.16937 | -0.054932 | -0.1648 | 0.022888 | 0.07782 | -0.12817 | -0.045776 | -0.073242 | 0.009156 | 0.26093 | 121.6919 | 0.13275 | 121.6599 | 121.4859 | 121.4722 | 121.4493 | 121.4172 | -121.6187 | -121.637 | 121.6553 | 121.6049 | 61.4548 | 61.5417
324.75 | 121.8842 | -61.4822 | 60.0769 | -0.0045011 | -0.00073062 | 0.058127 | 0.054724 | -0.00091006 | -0.0081348 | -0.0013138 | -0.0084228 | 0.0030911 | 0.064424 | 0.055858 | -0.0081733 | 0.02076 | -0.0019163 | 0.013733 | 59.9213 | -61.5463 | 60.228 | -61.1435 | -61.6196 | -61.6425 | 0.16937 | 59.8938 | -61.5555 | 60.1593 | -61.3449 | -61.4731 | -61.5875 | -0.064087 | -0.15564 | 0.15106 | 0.33875 | -0.16022 | -0.13733 | -0.09613 | -0.073242 | -0.073242 | -0.1831 | 0.082398 | 0.13733 | -0.10529 | 0.009156 | -0.032043 | 0.082398 | 0.40283 | 121.7743 | 0.21057 | 121.7148 | 121.4676 | 121.4493 | 121.4035 | 121.376 | -121.6232 | -121.6324 | 121.7102 | 121.6415 | 61.496 | 61.6516
326.4219 | 121.8658 | -61.5509 | 59.9854 | -0.012131 | 0.0048236 | 0.05834 | 0.058569 | 0.0048577 | -0.0055712 | 0.0008224 | -0.0084228 | 0.0015957 | 0.065706 | 0.056926 | -0.0079597 | 0.019265 | -0.0017027 | -0.091553 | 59.8801 | -61.5875 | 60.0861 | -61.3403 | -61.821 | -61.8118 | 0.013733 | 59.8343 | -61.6333 | 60.0815 | -61.4731 | -61.6196 | -61.6653 | -0.036621 | -0.10529 | 0.10071 | 0.21057 | -0.26093 | -0.27008 | -0.22431 | -0.23346 | -0.082398 | -0.15106 | 0.09613 | 0.07782 | -0.11444 | -0.068665 | -0.032043 | 0.013733 | 0.24719 | 121.6736 | 0.16022 | 121.7148 | 121.4676 | 121.4676 | 121.431 | 121.3852 | -121.5729 | -121.6187 | 121.637 | 121.6324 | 61.4594 | 61.5646
328.1406 | 121.8292 | -61.5417 | 60.0082 | -0.012131 | 0.0016192 | 0.05834 | 0.054724 | 0.0020807 | -0.0079212 | -0.00345 | -0.0084228 | 0.00052768 | 0.064852 | 0.053081 | -0.0090277 | 0.019478 | 0.0015017 | -0.082397 | 59.903 | -61.5829 | 60.0998 | -61.2991 | -61.7661 | -61.7569 | 0.022888 | 59.8755 | -61.6196 | 60.0769 | -61.4731 | -61.5829 | -61.6745 | -0.041199 | -0.10529 | 0.091552 | 0.24262 | -0.21515 | -0.2243 | -0.17395 | -0.18311 | -0.07782 | -0.13275 | 0.068664 | 0.068665 | -0.13275 | -0.041199 | -0.054932 | 0.036621 | 0.28381 | 121.6827 | 0.14648 | 121.6965 | 121.4859 | 121.4951 | 121.4447 | 121.4172 | -121.5912 | -121.6278 | 121.6415 | 121.6187 | 61.4594 | 61.5646
329.875 | 121.9116 | -61.496 | 60.0586 | -0.0045011 | -0.00051702 | 0.056631 | 0.054297 | -0.0030463 | -0.0094164 | -0.0004592 | -0.005371 | 0.0015957 | 0.066561 | 0.056072 | -0.0096685 | 0.02076 | -0.0053343 | -0.004578 | 59.9075 | -61.5326 | 60.1913 | -61.1893 | -61.6516 | -61.647 | 0.15106 | 59.8892 | -61.5555 | 60.1776 | -61.3358 | -61.4685 | -61.5784 | -0.036621 | -0.15106 | 0.13275 | 0.3067 | -0.15106 | -0.15564 | -0.11444 | -0.11902 | -0.059509 | -0.16937 | 0.11902 | 0.16022 | -0.082397 | 0.027466 | -0.022888 | 0.086975 | 0.34332 | 121.7239 | 0.21973 | 121.7331 | 121.4401 | 121.4447 | 121.4035 | 121.3852 | -121.5912 | -121.6141 | 121.6873 | 121.6736 | 61.4914 | 61.647
331.5625 | 121.7377 | -61.6058 | 60.0266 | -0.012131 | 0.0056782 | 0.058554 | 0.057501 | 0.00079894 | -0.0047168 | -0.002382 | -0.0084228 | 0.0039457 | 0.063997 | 0.068035 | -0.0058233 | 0.020333 | -0.0066159 | -0.086975 | 59.9258 | -61.6058 | 60.0266 | -61.409 | -61.8622 | -61.8713 | -0.082397 | 59.9121 | -61.6745 | 59.9945 | -61.6104 | -61.7432 | -61.7752 | 0 | -0.10071 | 0 | 0.19684 | -0.2655 | -0.25635 | -0.2655 | -0.25635 | -0.068665 | -0.11444 | -0.032043 | -0.004578 | -0.16937 | -0.13733 | -0.10071 | -0.068664 | 0.19684 | 121.6324 | 0.064087 | 121.669 | 121.5317 | 121.5866 | 121.5317 | 121.5179 | -121.6324 | -121.7011 | 121.6324 | 121.6003 | 61.5189 | 61.5234
333.2812 | 121.8796 | -61.4868 | 60.0311 | -0.0045011 | 0.0024738 | 0.057486 | 0.050024 | -0.0019781 | -0.0047168 | -0.0036636 | -0.005371 | 0.00052768 | 0.065065 | 0.054576 | -0.01095 | 0.019692 | -0.0025571 | -0.022888 | 59.8984 | -61.5509 | 60.1822 | -61.2122 | -61.6562 | -61.6974 | 0.10529 | 59.8801 | -61.5875 | 60.1685 | -61.3678 | -61.4914 | -61.5921 | -0.064087 | -0.13275 | 0.15106 | 0.27466 | -0.21057 | -0.16937 | -0.14648 | -0.10529 | -0.10071 | -0.15106 | 0.13733 | 0.11902 | -0.10529 | -0.004578 | -0.004578 | 0.09613 | 0.33874 | 121.7331 | 0.21973 | 121.756 | 121.4493 | 121.4676 | 121.3852 | 121.3669 | -121.582 | -121.6187 | 121.669 | 121.6553 | 61.4639 | 61.5921
335.0312 | 121.8933 | -61.5738 | 59.9899 | -0.012131 | 0.0026874 | 0.059195 | 0.056646 | 0.0044305 | -0.0066394 | -0.0040908 | -0.005371 | 0.0033047 | 0.065706 | 0.056499 | -0.0075323 | 0.018837 | -0.0010617 | -0.082397 | 59.8618 | -61.5875 | 60.1273 | -61.3037 | -61.7661 | -61.7661 | 0.050354 | 59.8434 | -61.6379 | 60.0906 | -61.4594 | -61.6104 | -61.6379 | -0.013732 | -0.12817 | 0.13733 | 0.27008 | -0.19226 | -0.19226 | -0.17853 | -0.17853 | -0.064086 | -0.14648 | 0.10071 | 0.11444 | -0.064086 | -0.036621 | 0 | 0.027465 | 0.28381 | 121.7148 | 0.17853 | 121.7285 | 121.4493 | 121.4813 | 121.4355 | 121.4172 | -121.5775 | -121.6278 | 121.701 | 121.6644 | 61.4914 | 61.6241
336.7188 | 121.788 | -61.5875 | 60.0403 | -0.01976 | 0.0039692 | 0.059409 | 0.058783 | -0.0036871 | -0.0045032 | -0.0011002 | -0.0023192 | 0.0041593 | 0.065706 | 0.064403 | -0.010096 | 0.02076 | -0.0061887 | -0.11902 | 59.9121 | -61.6104 | 60.0174 | -61.4044 | -61.8713 | -61.8713 | -0.068665 | 59.8755 | -61.6608 | 60.0128 | -61.5555 | -61.7111 | -61.7615 | -0.022889 | -0.12817 | -0.022888 | 0.18311 | -0.28381 | -0.28381 | -0.26093 | -0.26093 | -0.073243 | -0.1648 | -0.027466 | 0.032043 | -0.17395 | -0.1236 | -0.10071 | -0.050354 | 0.20599 | 121.6278 | 0.10529 | 121.6736 | 121.5225 | 121.5363 | 121.4996 | 121.463 | -121.6507 | -121.7011 | 121.6049 | 121.6003 | 61.4685 | 61.5189
338.4062 | 121.843 | -61.5601 | 60.0037 | -0.0045011 | 0.0033282 | 0.058554 | 0.05451 | 0.0044305 | -0.0062122 | -0.001741 | -0.0023192 | 0.00052768 | 0.068056 | 0.061412 | -0.0083869 | 0.021401 | -0.0036253 | -0.073242 | 59.8755 | -61.5829 | 60.1135 | -61.2946 | -61.7661 | -61.7706 | 0.036621 | 59.8297 | -61.6241 | 60.0952 | -61.4777 | -61.5967 | -61.6699 | -0.022888 | -0.12817 | 0.10986 | 0.2655 | -0.21057 | -0.20599 | -0.18768 | -0.18311 | -0.064087 | -0.17395 | 0.091553 | 0.082398 | -0.10986 | -0.036621 | -0.045776 | 0.027466 | 0.28839 | 121.6965 | 0.14649 | 121.7194 | 121.4584 | 121.4539 | 121.4355 | 121.3898 | -121.5866 | -121.6278 | 121.6736 | 121.6553 | 61.4868 | 61.5967
340.1094 | 121.8933 | -61.4777 | 60.0403 | -0.0045011 | -0.00030342 | 0.055563 | 0.054083 | -0.0019781 | -0.010698 | -3.1996e-05 | -0.005371 | 0.00074128 | 0.065706 | 0.057994 | -0.0094549 | 0.020546 | 6.346e-06 | -0.027466 | 59.9213 | -61.5646 | 60.1868 | -61.2167 | -61.6562 | -61.6928 | 0.11902 | 59.8846 | -61.5601 | 60.1547 | -61.3632 | -61.4822 | -61.5875 | -0.086975 | -0.11902 | 0.14648 | 0.26093 | -0.21515 | -0.17853 | -0.12817 | -0.091553 | -0.082398 | -0.15564 | 0.11444 | 0.11444 | -0.10986 | -0.004578 | -0.027465 | 0.07782 | 0.3479 | 121.7514 | 0.19684 | 121.7148 | 121.4859 | 121.4447 | 121.3989 | 121.3623 | -121.6049 | -121.6003 | 121.6644 | 121.6324 | 61.4502 | 61.5967
341.8281 | 121.8338 | -61.528 | 59.9991 | -0.01976 | 0.0020466 | 0.0577 | 0.054937 | -0.0051825 | -0.00963 | -0.0028092 | -0.005371 | 0.0022367 | 0.064211 | 0.059062 | -0.0098823 | 0.02076 | -0.0040525 | -0.07782 | 59.8663 | -61.5829 | 60.0998 | -61.2946 | -61.7798 | -61.7569 | 0.022888 | 59.8572 | -61.6104 | 60.0861 | -61.4639 | -61.5967 | -61.6745 | -0.054932 | -0.13275 | 0.10071 | 0.23346 | -0.22888 | -0.25177 | -0.17395 | -0.19684 | -0.082398 | -0.14191 | 0.086976 | 0.064087 | -0.14648 | -0.068665 | -0.064087 | 0.013733 | 0.28839 | 121.6827 | 0.14648 | 121.6965 | 121.4493 | 121.4676 | 121.3943 | 121.3852 | -121.582 | -121.6095 | 121.6278 | 121.6141 | 61.4502 | 61.5509
343.5156 | 121.8292 | -61.5555 | 60.0037 | -0.012131 | 0.0024738 | 0.058768 | 0.054937 | 0.0027215 | -0.0066394 | -0.0002456 | -0.0084228 | 0.0028775 | 0.067202 | 0.053935 | -0.0081733 | 0.021187 | -0.0010617 | -0.073242 | 59.8434 | -61.5692 | 60.1181 | -61.2991 | -61.7844 | -61.7752 | 0.022888 | 59.8663 | -61.6333 | 60.0815 | -61.4731 | -61.5967 | -61.6745 | -0.013733 | -0.16022 | 0.11444 | 0.25635 | -0.21973 | -0.22888 | -0.20599 | -0.21515 | -0.07782 | -0.13733 | 0.07782 | 0.082398 | -0.11902 | -0.041199 | -0.041199 | 0.036621 | 0.27008 | 121.6873 | 0.16022 | 121.7148 | 121.4127 | 121.4996 | 121.3989 | 121.4218 | -121.5729 | -121.637 | 121.6736 | 121.637 | 61.4822 | 61.5784
345.25 | 121.7789 | -61.5143 | 60.1044 | -0.012131 | 0.0022602 | 0.059409 | 0.057715 | 0.0022943 | -0.0062122 | -0.0015274 | -0.0023192 | 0.0026639 | 0.06592 | 0.06184 | -0.0079597 | 0.019265 | -0.0055479 | -0.036621 | 59.9762 | -61.5417 | 60.0861 | -61.3449 | -61.7706 | -61.7844 | 0.009155 | 59.967 | -61.5921 | 60.054 | -61.4868 | -61.6196 | -61.6745 | -0.027466 | -0.12817 | -0.01831 | 0.16937 | -0.27008 | -0.25635 | -0.24262 | -0.22888 | -0.07782 | -0.13733 | -0.050354 | 0.027466 | -0.16022 | -0.10529 | -0.082398 | -0.027466 | 0.19684 | 121.6278 | 0.10529 | 121.6461 | 121.5179 | 121.5591 | 121.4905 | 121.4813 | -121.6461 | -121.6965 | 121.6003 | 121.5683 | 61.4777 | 61.5234
346.9375 | 121.8887 | -61.4914 | 60.0494 | -0.012131 | 0.00076478 | 0.0577 | 0.054724 | 0.0025079 | -0.0057848 | -0.000673 | -0.005371 | 0.0015957 | 0.066774 | 0.055431 | -0.0090277 | 0.01841 | -0.00042085 | 0.018311 | 59.9442 | -61.528 | 60.2142 | -61.171 | -61.6333 | -61.6425 | 0.1831 | 59.8801 | -61.5555 | 60.1547 | -61.3403 | -61.4685 | -61.5829 | -0.036621 | -0.10529 | 0.16479 | 0.32043 | -0.15106 | -0.14191 | -0.11444 | -0.10529 | -0.064087 | -0.16937 | 0.10529 | 0.15106 | -0.091553 | 0.022888 | -0.027466 | 0.086975 | 0.35706 | 121.7422 | 0.21515 | 121.7102 | 121.4722 | 121.4355 | 121.4355 | 121.3715 | -121.5775 | -121.6049 | 121.7056 | 121.6461 | 61.5097 | 61.6745
348.625 | 121.8704 | -61.5234 | 60.0311 | -0.0045011 | 0.0014056 | 0.05834 | 0.05451 | -0.0049689 | -0.0049304 | -0.00345 | -0.0023192 | 0.00010048 | 0.064638 | 0.054149 | -0.0094549 | 0.022469 | 0.00043375 | -0.068665 | 59.8984 | -61.5646 | 60.1501 | -61.2717 | -61.7157 | -61.734 | 0.054932 | 59.8938 | -61.5875 | 60.1227 | -61.3953 | -61.5097 | -61.6013 | -0.041199 | -0.13275 | 0.11902 | 0.25177 | -0.21057 | -0.19226 | -0.16937 | -0.15106 | -0.064087 | -0.13733 | 0.091553 | 0.12817 | -0.07782 | 0.013732 | -0.013733 | 0.077819 | 0.29297 | 121.7148 | 0.19226 | 121.7102 | 121.463 | 121.4813 | 121.4218 | 121.4172 | -121.5958 | -121.6187 | 121.6736 | 121.6461 | 61.4548 | 61.5784
350.3438 | 121.756 | -61.5784 | 60.0311 | -0.012131 | 0.00461 | 0.057486 | 0.058569 | -0.0028327 | -0.0049304 | 0.001036 | -0.0084228 | 0.0045865 | 0.067415 | 0.069744 | -0.0060369 | 0.022255 | -0.0055479 | -0.032043 | 59.9579 | -61.5875 | 60.0861 | -61.3358 | -61.7935 | -61.8118 | 0 | 59.9213 | -61.6196 | 60.0174 | -61.5372 | -61.702 | -61.734 | -0.009155 | -0.073242 | 0.054932 | 0.24262 | -0.23346 | -0.21515 | -0.22431 | -0.20599 | -0.041199 | -0.10986 | -0.013733 | 0.041199 | -0.15564 | -0.1236 | -0.11444 | -0.082397 | 0.25177 | 121.6736 | 0.082398 | 121.637 | 121.5454 | 121.5408 | 121.5363 | 121.4996 | -121.6187 | -121.6507 | 121.6644 | 121.5958 | 61.5463 | 61.5784
352.0469 | 121.7789 | -61.528 | 60.0952 | -0.012131 | -0.00094422 | 0.058768 | 0.05451 | -0.0045417 | -0.0059986 | -0.002382 | -0.0084228 | 0.0011685 | 0.063784 | 0.056285 | -0.0075323 | 0.020546 | -0.0042661 | 0.013733 | 59.9487 | -61.5372 | 60.1593 | -61.2442 | -61.6837 | -61.7157 | 0.050354 | 59.9579 | -61.5692 | 60.0677 | -61.4502 | -61.5967 | -61.6928 | -0.009155 | -0.14649 | 0.064087 | 0.28381 | -0.18768 | -0.15564 | -0.17853 | -0.14648 | -0.041199 | -0.13733 | -0.027466 | 0.07782 | -0.16479 | -0.068665 | -0.1236 | -0.027466 | 0.29297 | 121.6965 | 0.11902 | 121.637 | 121.4859 | 121.5271 | 121.4767 | 121.4859 | -121.6324 | -121.6644 | 121.6873 | 121.5958 | 61.5417 | 61.5784
353.7344 | 121.8475 | -61.5509 | 59.9945 | -0.01976 | 0.00055118 | 0.05834 | 0.053656 | 0.00058534 | -0.006853 | -0.002382 | -0.005371 | -0.00075412 | 0.063143 | 0.054149 | -0.0092413 | 0.021401 | -0.0034117 | -0.10071 | 59.8618 | -61.6013 | 60.0998 | -61.3037 | -61.7661 | -61.7523 | 0.009155 | 59.8618 | -61.6287 | 60.0723 | -61.4639 | -61.5829 | -61.6562 | -0.050354 | -0.13275 | 0.10529 | 0.24719 | -0.20142 | -0.21515 | -0.15106 | -0.1648 | -0.07782 | -0.13275 | 0.07782 | 0.086975 | -0.10529 | -0.032044 | -0.027466 | 0.045776 | 0.29755 | 121.701 | 0.16479 | 121.7011 | 121.463 | 121.4905 | 121.4127 | 121.4127 | -121.5958 | -121.6232 | 121.6507 | 121.6232 | 61.4502 | 61.5601
355.4375 | 121.8933 | -61.4685 | 60.0174 | -0.012131 | 0.00097838 | 0.058554 | 0.054297 | -0.00091006 | -0.0059986 | -0.002382 | -0.005371 | 0.0020231 | 0.066133 | 0.058208 | -0.011805 | 0.020546 | -0.0042661 | -0.032043 | 59.903 | -61.5326 | 60.173 | -61.2213 | -61.6791 | -61.6928 | 0.11444 | 59.8984 | -61.5784 | 60.1501 | -61.3678 | -61.4731 | -61.5921 | -0.064087 | -0.11444 | 0.15564 | 0.24719 | -0.2243 | -0.21057 | -0.16022 | -0.14648 | -0.10986 | -0.11902 | 0.13275 | 0.10071 | -0.1236 | -0.004577 | -0.013733 | 0.10529 | 0.31128 | 121.7056 | 0.21057 | 121.7285 | 121.4355 | 121.4767 | 121.3715 | 121.3669 | -121.55 | -121.5958 | 121.6415 | 121.6187 | 61.4365 | 61.5829
357.1562 | 121.8292 | -61.5463 | 59.9945 | 0.0031279 | 0.0020466 | 0.05834 | 0.056646 | 0.0044305 | -0.0057848 | 0.0006088 | -0.005371 | 0.0024503 | 0.06357 | 0.06184 | -0.010523 | 0.020119 | -0.0023435 | -0.086975 | 59.8526 | -61.5875 | 60.1227 | -61.2854 | -61.7798 | -61.7523 | 0.032043 | 59.8526 | -61.6013 | 60.0677 | -61.4731 | -61.5921 | -61.6653 | -0.041198 | -0.14191 | 0.12817 | 0.26093 | -0.20599 | -0.23346 | -0.16479 | -0.19226 | -0.054931 | -0.14191 | 0.073242 | 0.073243 | -0.11902 | -0.045776 | -0.064087 | 0.009155 | 0.30212 | 121.7102 | 0.12817 | 121.669 | 121.4401 | 121.4539 | 121.3989 | 121.3989 | -121.582 | -121.5958 | 121.669 | 121.6141 | 61.4594 | 61.5784
358.9219 | 121.8109 | -61.5417 | 60.0769 | -0.01976 | 0.0033282 | 0.057059 | 0.055151 | 0.00015814 | -0.0062122 | -0.0025956 | -0.0023192 | 0.0045865 | 0.065279 | 0.066539 | -0.0075323 | 0.021187 | -0.0051205 | 0.013733 | 59.9625 | -61.5967 | 60.1273 | -61.2991 | -61.7615 | -61.7798 | 0.059509 | 59.903 | -61.6104 | 60.0952 | -61.4548 | -61.6013 | -61.6699 | -0.054932 | -0.11444 | 0.050354 | 0.24262 | -0.23804 | -0.21973 | -0.1831 | -0.16479 | -0.068665 | -0.17395 | 0.018311 | 0.086975 | -0.12817 | -0.059509 | -0.059509 | 0.009156 | 0.29755 | 121.7239 | 0.15564 | 121.7056 | 121.5591 | 121.5134 | 121.5042 | 121.4447 | -121.6736 | -121.6873 | 121.669 | 121.637 | 61.5555 | 61.6013
360.6406 | 121.7514 | -61.5234 | 60.1135 | -0.01976 | -0.00073062 | 0.055563 | 0.054724 | -0.0013373 | -0.0089892 | 0.0025314 | -0.005371 | 0.0020231 | 0.06827 | 0.055431 | -0.0083869 | 0.019692 | -0.0057615 | -0.036621 | 59.9762 | -61.5509 | 60.0998 | -61.3129 | -61.7432 | -61.7615 | 0.022888 | 59.967 | -61.5646 | 60.0586 | -61.4685 | -61.6196 | -61.6974 | -0.027466 | -0.13733 | -0.013733 | 0.21057 | -0.23804 | -0.21973 | -0.21057 | -0.19226 | -0.041199 | -0.14648 | -0.054931 | 0.054931 | -0.17395 | -0.096131 | -0.13275 | -0.054932 | 0.23804 | 121.6507 | 0.09613 | 121.6232 | 121.5271 | 121.5317 | 121.4996 | 121.4905 | -121.6644 | -121.6782 | 121.6232 | 121.582 | 61.4868 | 61.5463
362.4219 | 121.7422 | -61.5829 | 60.0128 | -0.012131 | 0.0039692 | 0.058768 | 0.057074 | -0.0015509 | -0.0064258 | -0.0002456 | -0.0084228 | 0.0026639 | 0.064852 | 0.064403 | -0.0047553 | 0.02311 | -0.0040525 | -0.10529 | 59.9487 | -61.6013 | 60.0037 | -61.441 | -61.8988 | -61.8942 | -0.07782 | 59.8572 | -61.647 | 59.9808 | -61.5829 | -61.7432 | -61.7706 | -0.01831 | -0.064087 | -0.009155 | 0.14191 | -0.31128 | -0.31586 | -0.29297 | -0.29755 | -0.064087 | -0.15564 | -0.032043 | 0 | -0.18768 | -0.16022 | -0.1236 | -0.09613 | 0.16022 | 121.6049 | 0.064087 | 121.6278 | 121.55 | 121.5042 | 121.5317 | 121.4401 | -121.6141 | -121.6599 | 121.5866 | 121.5637 | 61.4777 | 61.5051
364.1094 | 121.788 | -61.5326 | 60.0494 | -0.012131 | 0.0039692 | 0.059836 | 0.056219 | 0.0042169 | -0.0055712 | -0.0028092 | -0.005371 | 0.0026639 | 0.067842 | 0.061626 | -0.0062507 | 0.021828 | -0.00042085 | -0.013733 | 59.9579 | -61.5784 | 60.1364 | -61.2854 | -61.7432 | -61.7752 | 0.073242 | 59.9075 | -61.5967 | 60.0861 | -61.4731 | -61.6287 | -61.6928 | -0.045776 | -0.091552 | 0.086976 | 0.24719 | -0.24262 | -0.21057 | -0.19684 | -0.16479 | -0.064087 | -0.14191 | 0.036622 | 0.05951 | -0.16022 | -0.09613 | -0.09613 | -0.032043 | 0.29297 | 121.7148 | 0.1236 | 121.6827 | 121.5363 | 121.5042 | 121.4905 | 121.4401 | -121.6278 | -121.6461 | 121.669 | 121.6187 | 61.5189 | 61.6058
365.8594 | 121.8246 | -61.5372 | 60.0174 | -0.01976 | 0.00055118 | 0.05834 | 0.051733 | -0.0036871 | -0.0057848 | -0.0030228 | -0.0084228 | 0.00052768 | 0.067629 | 0.055431 | -0.010523 | 0.022683 | -0.0055479 | -0.091553 | 59.8846 | -61.5738 | 60.1044 | -61.3083 | -61.7523 | -61.7615 | 0.004578 | 59.8526 | -61.6196 | 60.0677 | -61.4502 | -61.5875 | -61.6699 | -0.036622 | -0.13275 | 0.086975 | 0.22888 | -0.2243 | -0.21515 | -0.18768 | -0.17853 | -0.082398 | -0.16479 | 0.050354 | 0.086975 | -0.13275 | -0.050354 | -0.050354 | 0.032044 | 0.2655 | 121.6782 | 0.16937 | 121.6873 | 121.4584 | 121.4722 | 121.4218 | 121.3898 | -121.5912 | -121.637 | 121.6415 | 121.6049 | 61.4456 | 61.5417
367.5469 | 121.8246 | -61.5509 | 60.0128 | -0.0045011 | 0.001192 | 0.056204 | 0.052801 | -0.00048286 | -0.0079212 | 0.0003952 | -0.0084228 | -0.00032692 | 0.067415 | 0.053295 | -0.0098823 | 0.021187 | -0.0040525 | -0.07782 | 59.8846 | -61.5738 | 60.1089 | -61.3129 | -61.7523 | -61.7615 | 0 | 59.8663 | -61.615 | 60.0723 | -61.4548 | -61.5875 | -61.6653 | -0.022889 | -0.12817 | 0.096131 | 0.23804 | -0.21057 | -0.20142 | -0.18768 | -0.17853 | -0.064087 | -0.14648 | 0.05951 | 0.09613 | -0.11444 | -0.036621 | -0.050354 | 0.027466 | 0.26093 | 121.6827 | 0.16022 | 121.6873 | 121.4584 | 121.4813 | 121.4355 | 121.4172 | -121.5866 | -121.6278 | 121.6599 | 121.6232 | 61.4731 | 61.5509
369.3125 | 121.875 | -61.5738 | 59.9808 | -0.0045011 | 0.0039692 | 0.061118 | 0.057074 | -0.0015509 | -0.0036486 | -0.0019546 | -0.0084228 | 0.0045865 | 0.068483 | 0.054576 | -0.0086005 | 0.02076 | -0.0019163 | -0.10986 | 59.903 | -61.5967 | 60.0769 | -61.3358 | -61.7935 | -61.7889 | 0.018311 | 59.816 | -61.6516 | 60.0906 | -61.4731 | -61.5967 | -61.6379 | -0.022888 | -0.07782 | 0.09613 | 0.23804 | -0.21515 | -0.21973 | -0.19226 | -0.19684 | -0.077819 | -0.16479 | 0.10986 | 0.10071 | -0.064086 | -0.022888 | 0.013733 | 0.054931 | 0.26093 | 121.6736 | 0.17853 | 121.7422 | 121.4996 | 121.4676 | 121.4767 | 121.3898 | -121.5775 | -121.6324 | 121.6507 | 121.6644 | 61.4639 | 61.5921
371.0781 | 121.7743 | -61.5509 | 60.0357 | -0.0045011 | 0.006319 | 0.05834 | 0.056219 | -0.0034735 | -0.0055712 | -0.0028092 | -0.005371 | 0.0024503 | 0.065065 | 0.055431 | -0.0071051 | 0.019051 | -0.00020725 | -0.009155 | 59.9487 | -61.5784 | 60.1227 | -61.2991 | -61.7798 | -61.7981 | 0.022888 | 59.903 | -61.615 | 60.054 | -61.5097 | -61.6608 | -61.7203 | -0.027466 | -0.086976 | 0.086975 | 0.25177 | -0.24719 | -0.22888 | -0.21973 | -0.20142 | -0.064087 | -0.13275 | 0.01831 | 0.041198 | -0.16937 | -0.10986 | -0.10529 | -0.045777 | 0.27924 | 121.7011 | 0.10529 | 121.669 | 121.5271 | 121.5179 | 121.4996 | 121.4539 | -121.6141 | -121.6507 | 121.6736 | 121.6049 | 61.5417 | 61.5738
372.8438 | 121.7697 | -61.5646 | 60.0357 | -0.012131 | 0.0050372 | 0.057272 | 0.057501 | 0.0018671 | -0.0064258 | -0.0032364 | -0.005371 | 0.0033047 | 0.066561 | 0.060558 | -0.0056097 | 0.021828 | 0.00021995 | -0.013733 | 59.9533 | -61.5738 | 60.0906 | -61.3174 | -61.7844 | -61.7935 | 0.027466 | 59.9167 | -61.5967 | 60.0357 | -61.5097 | -61.6699 | -61.7157 | -0.009156 | -0.082398 | 0.054931 | 0.24719 | -0.22888 | -0.21973 | -0.21973 | -0.21057 | -0.032044 | -0.11902 | 0 | 0.054931 | -0.15106 | -0.10529 | -0.11902 | -0.073242 | 0.25635 | 121.6644 | 0.086975 | 121.6324 | 121.5271 | 121.5134 | 121.5179 | 121.4813 | -121.6095 | -121.6324 | 121.6553 | 121.6003 | 61.5509 | 61.5921
374.5312 | 121.7697 | -61.5097 | 60.1044 | -0.0045011 | 0.00012398 | 0.057272 | 0.056006 | 0.0035761 | -0.0092028 | -0.0013138 | -0.0084228 | 0.00095488 | 0.06592 | 0.056285 | -0.0083869 | 0.021614 | -0.0064023 | -0.027466 | 59.9991 | -61.5646 | 60.0815 | -61.322 | -61.7523 | -61.7798 | 0.009155 | 59.9533 | -61.5738 | 60.0769 | -61.4502 | -61.6013 | -61.6699 | -0.054931 | -0.10529 | -0.022888 | 0.18768 | -0.27008 | -0.24261 | -0.21515 | -0.18768 | -0.064087 | -0.15106 | -0.027466 | 0.05951 | -0.16022 | -0.091552 | -0.09613 | -0.027465 | 0.24262 | 121.6461 | 0.1236 | 121.6507 | 121.5637 | 121.5271 | 121.5088 | 121.463 | -121.669 | -121.6782 | 121.5912 | 121.5866 | 61.4822 | 61.5189
376.2656 | 121.756 | -61.6196 | 60.0403 | -0.0045011 | 0.0054644 | 0.057913 | 0.057074 | 0.0040033 | -0.0045032 | -0.0013138 | 0.00073235 | 0.0026639 | 0.065493 | 0.064403 | -0.0075323 | 0.020546 | -0.0046933 | -0.10071 | 59.9258 | -61.6013 | 60.0037 | -61.441 | -61.8988 | -61.8942 | -0.10986 | 59.8938 | -61.6562 | 59.9899 | -61.6013 | -61.7386 | -61.7661 | 0.018311 | -0.11444 | -0.036621 | 0.17853 | -0.27466 | -0.27924 | -0.29297 | -0.29755 | -0.036621 | -0.14648 | -0.050354 | 0.018311 | -0.14648 | -0.11902 | -0.10986 | -0.082397 | 0.16022 | 121.6049 | 0.054932 | 121.6461 | 121.5271 | 121.55 | 121.5454 | 121.5134 | -121.6415 | -121.6965 | 121.6232 | 121.6095 | 61.5189 | 61.5097
378.0312 | 121.7743 | -61.5921 | 60.022 | -0.012131 | 0.0043964 | 0.05834 | 0.054937 | -0.00026906 | -0.0055712 | 0.0006088 | -0.0023192 | 0.0035183 | 0.067202 | 0.0471 | -0.0077459 | 0.021401 | -0.00084805 | -0.11902 | 59.9304 | -61.6058 | 60.0037 | -61.4044 | -61.853 | -61.8759 | -0.064087 | 59.8892 | -61.6699 | 60.0174 | -61.5463 | -61.702 | -61.7386 | -0.013733 | -0.091553 | -0.018311 | 0.18768 | -0.28381 | -0.26093 | -0.27008 | -0.24719 | -0.07782 | -0.13275 | -0.004578 | 0.045776 | -0.14648 | -0.10986 | -0.068664 | -0.032043 | 0.20142 | 121.6095 | 0.1236 | 121.6873 | 121.5363 | 121.5591 | 121.5225 | 121.4813 | -121.6278 | -121.6919 | 121.5958 | 121.6095 | 61.4731 | 61.528
379.7812 | 121.8658 | -61.4731 | 60.0586 | -0.012131 | 0.00012398 | 0.056631 | 0.053869 | 0.00037174 | -0.0074938 | -0.00345 | -0.0084228 | 0.00031408 | 0.066347 | 0.052867 | -0.0092413 | 0.022255 | -0.0021299 | 0.027466 | 59.9213 | -61.5417 | 60.2234 | -61.1847 | -61.6379 | -61.6562 | 0.13733 | 59.8984 | -61.5646 | 60.1501 | -61.3586 | -61.4914 | -61.5875 | -0.068665 | -0.13733 | 0.16479 | 0.28839 | -0.18311 | -0.16479 | -0.11444 | -0.09613 | -0.091553 | -0.16022 | 0.091552 | 0.11444 | -0.11444 | -0.018311 | -0.022888 | 0.073242 | 0.35706 | 121.7651 | 0.20599 | 121.7148 | 121.463 | 121.463 | 121.3943 | 121.3715 | -121.6003 | -121.6232 | 121.6965 | 121.6232 | 61.5005 | 61.6104
381.4531 | 121.7651 | -61.5875 | 60.022 | -0.01976 | 0.0043964 | 0.058554 | 0.056646 | -0.0019781 | -0.0049304 | -0.0040908 | -0.005371 | 0.0041593 | 0.066774 | 0.061626 | -0.0058233 | 0.022469 | -0.0010617 | -0.10529 | 59.9213 | -61.5967 | 60.0174 | -61.4456 | -61.8759 | -61.8851 | -0.10071 | 59.8709 | -61.6516 | 59.9899 | -61.5692 | -61.7432 | -61.7477 | -0.009156 | -0.10071 | -0.004578 | 0.14191 | -0.29755 | -0.28839 | -0.28839 | -0.27924 | -0.064087 | -0.15106 | -0.032044 | 0.01831 | -0.16022 | -0.15564 | -0.096131 | -0.091553 | 0.15106 | 121.6141 | 0.082397 | 121.6415 | 121.5179 | 121.5225 | 121.5088 | 121.4584 | -121.6187 | -121.6736 | 121.6049 | 121.5775 | 61.4822 | 61.4868
383.2031 | 121.7468 | -61.5646 | 60.022 | -0.01976 | 0.0031146 | 0.059195 | 0.056219 | 0.0029351 | -0.0040758 | -0.0013138 | -0.0023192 | 0.0030911 | 0.066774 | 0.063335 | -0.0090277 | 0.02076 | -0.00042085 | -0.041199 | 59.9442 | -61.5921 | 60.0586 | -61.3632 | -61.821 | -61.8439 | -0.032043 | 59.8892 | -61.6379 | 59.9991 | -61.5509 | -61.702 | -61.7386 | -0.027466 | -0.07782 | 0.036621 | 0.20142 | -0.27924 | -0.25635 | -0.25177 | -0.22888 | -0.073242 | -0.13275 | -0.022889 | 0.013733 | -0.17395 | -0.13733 | -0.10071 | -0.064087 | 0.22888 | 121.6507 | 0.086975 | 121.637 | 121.5363 | 121.5271 | 121.5088 | 121.4539 | -121.6141 | -121.6599 | 121.6232 | 121.5637 | 61.5234 | 61.5326
384.9531 | 121.7606 | -61.5601 | 60.054 | -0.012131 | 0.0031146 | 0.057913 | 0.056646 | 0.0037897 | -0.0036486 | -0.0013138 | -0.0023192 | 0.0030911 | 0.066133 | 0.060131 | -0.0075323 | 0.020119 | 0.0015017 | -0.032043 | 59.9258 | -61.5509 | 60.0906 | -61.3037 | -61.7752 | -61.8027 | 0.022888 | 59.9213 | -61.615 | 60.0494 | -61.5051 | -61.6745 | -61.7203 | 0.009156 | -0.12817 | 0.036621 | 0.25635 | -0.24261 | -0.21515 | -0.25177 | -0.22431 | -0.054931 | -0.13275 | -0.004578 | 0.054932 | -0.16022 | -0.11444 | -0.10529 | -0.05951 | 0.24719 | 121.6415 | 0.10986 | 121.6644 | 121.4767 | 121.5363 | 121.4859 | 121.4813 | -121.6049 | -121.669 | 121.6507 | 121.6095 | 61.528 | 61.5829
386.6406 | 121.7606 | -61.5097 | 60.1135 | -0.012131 | 0.0014056 | 0.056845 | 0.054297 | -0.0015509 | -0.0081348 | 0.0003952 | -0.0084228 | 0.0013821 | 0.067415 | 0.065257 | -0.0098823 | 0.020546 | -0.0021299 | -0.050354 | 59.9945 | -61.5646 | 60.0861 | -61.3174 | -61.7432 | -61.7706 | 0.022888 | 59.9533 | -61.5921 | 60.054 | -61.4777 | -61.6241 | -61.6837 | -0.054931 | -0.11902 | -0.027465 | 0.19226 | -0.26093 | -0.23346 | -0.20599 | -0.17853 | -0.082397 | -0.16022 | -0.059509 | 0.032044 | -0.17395 | -0.11444 | -0.091553 | -0.032044 | 0.24719 | 121.6507 | 0.11444 | 121.6461 | 121.5591 | 121.5454 | 121.5042 | 121.463 | -121.6782 | -121.7056 | 121.5958 | 121.5637 | 61.4594 | 61.5326
388.3438 | 121.7514 | -61.5921 | 60.0266 | -0.012131 | 0.0033282 | 0.057486 | 0.057287 | 0.00015814 | -0.0074938 | -0.0015274 | -0.011475 | 0.0045865 | 0.06592 | 0.059062 | -0.0073187 | 0.020119 | -0.00042085 | -0.11444 | 59.9121 | -61.6379 | 60.0037 | -61.4319 | -61.8851 | -61.8713 | -0.09613 | 59.8801 | -61.6653 | 59.9854 | -61.5829 | -61.7386 | -61.7569 | -0.045776 | -0.11444 | -0.022888 | 0.16022 | -0.27924 | -0.29297 | -0.23346 | -0.24719 | -0.073242 | -0.14648 | -0.041198 | 0.009155 | -0.1648 | -0.14648 | -0.091553 | -0.073242 | 0.20599 | 121.6415 | 0.082397 | 121.6507 | 121.55 | 121.5454 | 121.5042 | 121.4722 | -121.6644 | -121.6919 | 121.5958 | 121.5775 | 61.4777 | 61.496
390.0938 | 121.8567 | -61.5417 | 60.0403 | -0.0045011 | 0.001833 | 0.058127 | 0.051947 | -0.00048286 | -0.005144 | -0.0015274 | -0.005371 | 0.00074128 | 0.066988 | 0.052867 | -0.010737 | 0.021614 | -0.0064023 | -0.091553 | 59.8846 | -61.5555 | 60.1044 | -61.3083 | -61.7386 | -61.7477 | 0.027466 | 59.8663 | -61.6013 | 60.0906 | -61.441 | -61.5692 | -61.6425 | -0.013733 | -0.15564 | 0.064087 | 0.23346 | -0.20599 | -0.19684 | -0.19226 | -0.1831 | -0.059509 | -0.17395 | 0.050354 | 0.10071 | -0.10071 | -0.027466 | -0.041199 | 0.032043 | 0.24719 | 121.6599 | 0.16022 | 121.6919 | 121.4401 | 121.4676 | 121.4264 | 121.4081 | -121.5958 | -121.6415 | 121.6461 | 121.6324 | 61.4502 | 61.5692
391.8438 | 121.7789 | -61.5417 | 60.022 | -0.012131 | 0.0048236 | 0.05834 | 0.057715 | 0.0040033 | -0.0062122 | -0.00345 | -0.0023192 | 0.0020231 | 0.06592 | 0.051586 | -0.0081733 | 0.022255 | -0.0031979 | 0 | 59.935 | -61.5555 | 60.1044 | -61.3129 | -61.7798 | -61.7798 | 0.041199 | 59.9121 | -61.6013 | 60.0449 | -61.496 | -61.6699 | -61.7065 | -0.013733 | -0.086975 | 0.082397 | 0.22888 | -0.23804 | -0.23804 | -0.2243 | -0.2243 | -0.059509 | -0.10986 | 0.022888 | 0.045776 | -0.1648 | -0.12817 | -0.10529 | -0.068665 | 0.24262 | 121.6599 | 0.10528 | 121.6461 | 121.4905 | 121.5134 | 121.4767 | 121.4539 | -121.5775 | -121.6232 | 121.6461 | 121.5866 | 61.5417 | 61.5829
393.6094 | 121.756 | -61.5372 | 60.1227 | -0.0045011 | 0.00076478 | 0.056631 | 0.054724 | 0.0016535 | -0.0072802 | -0.0015274 | -0.005371 | 0.0033047 | 0.066988 | 0.064403 | -0.0094549 | 0.020119 | 0.0023563 | -0.022888 | 60.0174 | -61.5372 | 60.0998 | -61.322 | -61.7477 | -61.7706 | 0.013733 | 59.9579 | -61.5738 | 60.0449 | -61.4822 | -61.6333 | -61.6791 | 0 | -0.10529 | -0.022889 | 0.21515 | -0.23346 | -0.21057 | -0.23346 | -0.21057 | -0.036622 | -0.16479 | -0.07782 | 0.054931 | -0.14191 | -0.096131 | -0.10529 | -0.059509 | 0.21515 | 121.637 | 0.091553 | 121.6187 | 121.5546 | 121.5317 | 121.5546 | 121.4951 | -121.6599 | -121.6965 | 121.637 | 121.582 | 61.5143 | 61.5509
395.3594 | 121.7606 | -61.5784 | 60.0403 | -0.012131 | 0.0039692 | 0.059195 | 0.057287 | 0.0027215 | -0.0045032 | -0.0040908 | -0.005371 | 0.0011685 | 0.06592 | 0.055644 | -0.0088141 | 0.022042 | -0.0029843 | -0.032043 | 59.9533 | -61.5738 | 60.0723 | -61.3358 | -61.8027 | -61.8164 | 0.018311 | 59.8938 | -61.6241 | 60.0082 | -61.5417 | -61.6791 | -61.734 | 0.004577 | -0.086975 | 0.032044 | 0.24262 | -0.23804 | -0.2243 | -0.24261 | -0.22888 | -0.045777 | -0.14648 | -0.032043 | 0.036621 | -0.15564 | -0.10071 | -0.10986 | -0.054931 | 0.23804 | 121.6461 | 0.082398 | 121.6324 | 121.5271 | 121.5179 | 121.5317 | 121.4722 | -121.6141 | -121.6644 | 121.6507 | 121.5866 | 61.5463 | 61.5967
397.0625 | 121.7972 | -61.5692 | 60.0677 | -0.012131 | 0.0039692 | 0.05834 | 0.057074 | 0.00015814 | -0.0066394 | -0.000673 | -0.005371 | 0.0048001 | 0.066774 | 0.05479 | -0.0081733 | 0.022255 | -0.0017027 | -0.004578 | 59.9258 | -61.5509 | 60.1227 | -61.3083 | -61.7615 | -61.7661 | 0.041199 | 59.9213 | -61.5875 | 60.0357 | -61.5051 | -61.6562 | -61.6974 | 0.018311 | -0.14191 | 0.054932 | 0.26093 | -0.19684 | -0.19226 | -0.21515 | -0.21057 | -0.01831 | -0.14648 | -0.032043 | 0.064087 | -0.12817 | -0.086975 | -0.10986 | -0.068665 | 0.24261 | 121.6736 | 0.082397 | 121.6232 | 121.4767 | 121.5088 | 121.4951 | 121.4905 | -121.6187 | -121.6553 | 121.6919 | 121.6049 | 61.5646 | 61.6104
398.8281 | 121.8658 | -61.5555 | 59.9854 | -0.01976 | 0.002901 | 0.059836 | 0.056006 | 0.00037174 | -0.0064258 | -0.0019546 | -0.0023192 | -0.00011332 | 0.065065 | 0.05244 | -0.0083869 | 0.02076 | -0.0021299 | -0.068665 | 59.8709 | -61.6013 | 60.1089 | -61.2762 | -61.7615 | -61.7432 | 0.059509 | 59.816 | -61.6287 | 60.0906 | -61.4456 | -61.5692 | -61.6516 | -0.045776 | -0.11444 | 0.1236 | 0.27924 | -0.18768 | -0.20599 | -0.14191 | -0.16022 | -0.073242 | -0.16937 | 0.10529 | 0.10986 | -0.09613 | -0.013733 | -0.022888 | 0.059509 | 0.32501 | 121.7102 | 0.1831 | 121.7194 | 121.4722 | 121.4447 | 121.4264 | 121.3715 | -121.5866 | -121.6141 | 121.6644 | 121.6461 | 61.4868 | 61.615
400.5156 | 121.788 | -61.5967 | 60.0082 | -0.01976 | 0.0035418 | 0.059622 | 0.055792 | -0.0013373 | -0.0077074 | -0.0021682 | -0.0023192 | 0.0037321 | 0.065706 | 0.060985 | -0.0092413 | 0.021401 | -0.0021299 | -0.10529 | 59.935 | -61.615 | 60.0266 | -61.3907 | -61.8576 | -61.8622 | -0.045776 | 59.8892 | -61.6562 | 60.0174 | -61.5555 | -61.6928 | -61.7249 | -0.01831 | -0.073242 | 0.01831 | 0.20599 | -0.2655 | -0.26093 | -0.24719 | -0.24262 | -0.059509 | -0.11902 | 0.009155 | 0.041199 | -0.12817 | -0.09613 | -0.068665 | -0.036621 | 0.2243 | 121.6415 | 0.10071 | 121.6736 | 121.55 | 121.5454 | 121.5317 | 121.4859 | -121.6232 | -121.6644 | 121.6232 | 121.6141 | 61.4914 | 61.5509
402.2969 | 121.8842 | -61.5692 | 59.9762 | -0.012131 | 0.0054644 | 0.057272 | 0.056433 | -0.0017645 | -0.0055712 | 0.0001816 | -0.005371 | 0.0013821 | 0.066133 | 0.052654 | -0.0092413 | 0.022255 | -0.0017027 | -0.073242 | 59.8755 | -61.6196 | 60.0952 | -61.2991 | -61.7706 | -61.7706 | 0.036621 | 59.8389 | -61.615 | 60.0815 | -61.4548 | -61.5967 | -61.647 | -0.050354 | -0.10071 | 0.11902 | 0.27008 | -0.20142 | -0.20142 | -0.15106 | -0.15106 | -0.045776 | -0.13733 | 0.10529 | 0.11444 | -0.07782 | -0.027466 | -0.032044 | 0.01831 | 0.32044 | 121.7148 | 0.16022 | 121.6965 | 121.4951 | 121.4539 | 121.4447 | 121.4081 | -121.5958 | -121.5912 | 121.6644 | 121.6507 | 61.496 | 61.6058
404.0625 | 121.8338 | -61.5509 | 60.0266 | -0.0045011 | 0.002901 | 0.059622 | 0.053442 | 0.0014397 | -0.0070666 | -0.00345 | -0.005371 | -0.00011332 | 0.066561 | 0.055858 | -0.012232 | 0.021187 | -0.0017027 | -0.086975 | 59.8892 | -61.5692 | 60.0906 | -61.2991 | -61.7706 | -61.7615 | 0.013733 | 59.848 | -61.5967 | 60.054 | -61.4777 | -61.5875 | -61.6791 | -0.018311 | -0.13733 | 0.064087 | 0.25177 | -0.21057 | -0.21973 | -0.19226 | -0.20142 | -0.045777 | -0.17853 | 0.027466 | 0.073242 | -0.12817 | -0.036621 | -0.082397 | 0.009156 | 0.27008 | 121.6599 | 0.11902 | 121.6507 | 121.4584 | 121.4447 | 121.4401 | 121.3989 | -121.5958 | -121.6232 | 121.6415 | 121.6049 | 61.4639 | 61.5646
405.75 | 121.7651 | -61.6104 | 60.0266 | -0.0045011 | 0.00461 | 0.0577 | 0.056646 | 0.0014397 | -0.0062122 | -0.001741 | -0.0023192 | 0.0030911 | 0.06357 | 0.060558 | -0.0075323 | 0.02076 | -0.0076841 | -0.1236 | 59.9304 | -61.6104 | 60.0082 | -61.4182 | -61.8851 | -61.8805 | -0.086975 | 59.8892 | -61.6287 | 59.9854 | -61.5692 | -61.7203 | -61.7615 | 0 | -0.09613 | -0.01831 | 0.19226 | -0.27008 | -0.27466 | -0.27008 | -0.27466 | -0.01831 | -0.13733 | -0.041198 | 0.041199 | -0.15106 | -0.10986 | -0.13275 | -0.091553 | 0.19226 | 121.6187 | 0.059509 | 121.6141 | 121.5408 | 121.5179 | 121.5408 | 121.4996 | -121.637 | -121.6553 | 121.6187 | 121.5958 | 61.4868 | 61.5234
407.4375 | 121.8796 | -61.4822 | 60.0677 | -0.012131 | -0.00051702 | 0.055777 | 0.054724 | 0.00079894 | -0.0072802 | 0.0001816 | -0.0084228 | -0.00011332 | 0.067629 | 0.058422 | -0.010523 | 0.019478 | -0.0023435 | 0.013733 | 59.903 | -61.5234 | 60.2097 | -61.171 | -61.6287 | -61.647 | 0.14648 | 59.8801 | -61.5555 | 60.1456 | -61.3495 | -61.4914 | -61.5875 | -0.041198 | -0.16479 | 0.14191 | 0.31128 | -0.16479 | -0.14648 | -0.1236 | -0.10529 | -0.073242 | -0.18768 | 0.07782 | 0.13275 | -0.10529 | -0.009155 | -0.032043 | 0.064087 | 0.35248 | 121.7331 | 0.20599 | 121.7011 | 121.4264 | 121.4355 | 121.3852 | 121.3623 | -121.5912 | -121.6232 | 121.6919 | 121.6278 | 61.496 | 61.6287
409.2031 | 121.8842 | -61.5601 | 59.9579 | -0.012131 | 0.00461 | 0.058981 | 0.054724 | 0.0033623 | -0.0055712 | -0.0036636 | -0.0023192 | 0.0018095 | 0.063784 | 0.059276 | -0.0071051 | 0.02076 | -0.0046933 | -0.068665 | 59.848 | -61.6013 | 60.1364 | -61.2946 | -61.7661 | -61.7523 | 0.054932 | 59.8206 | -61.6241 | 60.1089 | -61.4502 | -61.6104 | -61.647 | -0.041198 | -0.10986 | 0.17853 | 0.2655 | -0.19226 | -0.20599 | -0.15106 | -0.1648 | -0.064087 | -0.13733 | 0.15106 | 0.10986 | -0.086975 | -0.050354 | -0.022888 | 0.013733 | 0.3067 | 121.7377 | 0.17395 | 121.7331 | 121.4493 | 121.4447 | 121.4081 | 121.3806 | -121.5591 | -121.582 | 121.6965 | 121.669 | 61.4914 | 61.615
410.8906 | 121.7972 | -61.5875 | 59.9945 | -0.012131 | 0.0052508 | 0.0577 | 0.054937 | 0.0016535 | -0.0059986 | -0.000673 | -0.0084228 | 0.0024503 | 0.065065 | 0.061412 | -0.0075323 | 0.021187 | -0.0040525 | -0.11444 | 59.9213 | -61.6058 | 60.0266 | -61.4044 | -61.8576 | -61.853 | -0.045776 | 59.8801 | -61.6608 | 60.0082 | -61.5372 | -61.702 | -61.7249 | -0.018311 | -0.073242 | 0.032043 | 0.18311 | -0.2655 | -0.27008 | -0.24719 | -0.25177 | -0.073243 | -0.11444 | 0.013733 | 0.050354 | -0.13733 | -0.11444 | -0.064087 | -0.041198 | 0.20142 | 121.6324 | 0.1236 | 121.669 | 121.5271 | 121.5408 | 121.5088 | 121.4676 | -121.6003 | -121.6553 | 121.6141 | 121.5958 | 61.4731 | 61.5417
412.6406 | 121.7743 | -61.5967 | 60.0311 | -0.012131 | 0.0033282 | 0.057486 | 0.05686 | -0.00091006 | -0.010485 | -0.002382 | -0.0023192 | 0.0041593 | 0.065065 | 0.05479 | -0.0071051 | 0.022683 | -0.0042661 | -0.11902 | 59.9213 | -61.6196 | 59.9991 | -61.4182 | -61.8713 | -61.8622 | -0.073242 | 59.8846 | -61.6379 | 60.0128 | -61.5555 | -61.7249 | -61.7477 | -0.022888 | -0.10986 | -0.032044 | 0.17853 | -0.2655 | -0.27466 | -0.24262 | -0.25177 | -0.041198 | -0.14648 | -0.018311 | 0.041199 | -0.15106 | -0.12817 | -0.10986 | -0.086976 | 0.20142 | 121.6187 | 0.082397 | 121.6507 | 121.5408 | 121.5225 | 121.5179 | 121.4813 | -121.6507 | -121.669 | 121.5958 | 121.6095 | 61.4777 | 61.5234
414.3906 | 121.8796 | -61.5555 | 59.9854 | -0.01976 | 0.0048236 | 0.060263 | 0.056006 | 0.0022943 | -0.0064258 | -0.001741 | -0.0023192 | 0.00095488 | 0.065065 | 0.059276 | -0.010737 | 0.021187 | -0.00084805 | -0.073242 | 59.8526 | -61.5921 | 60.1181 | -61.2854 | -61.7706 | -61.7432 | 0.073242 | 59.8206 | -61.6196 | 60.1135 | -61.4273 | -61.5875 | -61.6333 | -0.036621 | -0.13275 | 0.13275 | 0.27008 | -0.18768 | -0.21515 | -0.15106 | -0.17853 | -0.064087 | -0.16479 | 0.12817 | 0.12817 | -0.07782 | -0.032043 | -0.013733 | 0.032044 | 0.3067 | 121.7102 | 0.19226 | 121.7331 | 121.4447 | 121.4401 | 121.4081 | 121.376 | -121.5775 | -121.6049 | 121.6736 | 121.669 | 61.4822 | 61.6287
416.1406 | 121.875 | -61.5692 | 59.9899 | -0.012131 | 0.0071734 | 0.059195 | 0.054724 | -5.5462e-05 | -0.006853 | -0.0002456 | -0.005371 | 0.0020231 | 0.067629 | 0.05479 | -0.0090277 | 0.020974 | -0.0023435 | -0.059509 | 59.8526 | -61.6104 | 60.1135 | -61.2946 | -61.7752 | -61.7615 | 0.041199 | 59.8297 | -61.6241 | 60.0998 | -61.4548 | -61.5875 | -61.6379 | -0.041199 | -0.13733 | 0.1236 | 0.27466 | -0.19226 | -0.20599 | -0.15106 | -0.16479 | -0.054932 | -0.16022 | 0.10986 | 0.11444 | -0.068664 | -0.01831 | -0.013732 | 0.036622 | 0.31586 | 121.7239 | 0.16937 | 121.7239 | 121.463 | 121.4539 | 121.4218 | 121.3989 | -121.6003 | -121.6141 | 121.6827 | 121.669 | 61.5097 | 61.6104
417.8906 | 121.788 | -61.5967 | 60.0128 | -0.01976 | 0.0048236 | 0.05834 | 0.05686 | -0.0017645 | -0.006853 | -3.1996e-05 | -0.0023192 | 0.0022367 | 0.066347 | 0.06483 | -0.0075323 | 0.021828 | -0.0036253 | -0.11444 | 59.9121 | -61.6196 | 60.0174 | -61.4182 | -61.8622 | -61.8576 | -0.068665 | 59.8709 | -61.6379 | 60.0128 | -61.5601 | -61.7065 | -61.7523 | -0.022888 | -0.10071 | 0.004578 | 0.17853 | -0.26093 | -0.2655 | -0.23804 | -0.24262 | -0.041198 | -0.14191 | 0 | 0.036621 | -0.15564 | -0.10986 | -0.11444 | -0.068665 | 0.20142 | 121.637 | 0.077819 | 121.6507 | 121.5317 | 121.5088 | 121.5088 | 121.4676 | -121.6324 | -121.6507 | 121.6141 | 121.6095 | 61.4822 | 61.528
419.5781 | 121.875 | -61.5555 | 59.967 | -0.0045011 | 0.0041828 | 0.058127 | 0.053869 | 0.0067803 | -0.006853 | -0.0002456 | -0.005371 | 0.0026639 | 0.063997 | 0.060344 | -0.0092413 | 0.021828 | -0.0029843 | -0.07782 | 59.8755 | -61.6196 | 60.1089 | -61.3083 | -61.7661 | -61.7752 | 0.059509 | 59.8343 | -61.6196 | 60.0861 | -61.4685 | -61.6013 | -61.647 | -0.064087 | -0.091553 | 0.14191 | 0.24719 | -0.21973 | -0.21057 | -0.15564 | -0.14648 | -0.064087 | -0.13275 | 0.11902 | 0.086975 | -0.091553 | -0.045776 | -0.027466 | 0.018311 | 0.31128 | 121.7285 | 0.15106 | 121.7056 | 121.4951 | 121.4539 | 121.431 | 121.3898 | -121.5866 | -121.5866 | 121.6644 | 121.6415 | 61.4777 | 61.615
421.3125 | 121.8796 | -61.5051 | 60.0403 | -0.012131 | 0.00097838 | 0.057272 | 0.054724 | -0.0011237 | -0.0049304 | -0.0032364 | -0.005371 | 0.00074128 | 0.066988 | 0.056713 | -0.010737 | 0.020546 | -0.00084805 | -0.068665 | 59.9167 | -61.5692 | 60.1364 | -61.2717 | -61.7249 | -61.7157 | 0.064087 | 59.8892 | -61.5829 | 60.1227 | -61.3861 | -61.5189 | -61.6104 | -0.064087 | -0.1236 | 0.096131 | 0.23346 | -0.21057 | -0.21973 | -0.14648 | -0.15564 | -0.07782 | -0.15106 | 0.082398 | 0.11902 | -0.10529 | -0.013733 | -0.027466 | 0.064087 | 0.29755 | 121.7056 | 0.19684 | 121.7056 | 121.4859 | 121.4722 | 121.4218 | 121.3943 | -121.6095 | -121.6232 | 121.6415 | 121.6278 | 61.4365 | 61.5692
423.0625 | 121.8063 | -61.528 | 60.0677 | -0.012131 | 0.0039692 | 0.056204 | 0.055151 | 0.0037897 | -0.0057848 | -0.0008866 | -0.005371 | 0.0035183 | 0.065493 | 0.063549 | -0.0077459 | 0.020974 | -0.0061887 | 0.004578 | 59.967 | -61.5967 | 60.1273 | -61.2946 | -61.7477 | -61.7661 | 0.068665 | 59.9304 | -61.5967 | 60.0723 | -61.4639 | -61.6104 | -61.6608 | -0.068665 | -0.10071 | 0.059509 | 0.23346 | -0.23804 | -0.21973 | -0.16937 | -0.15106 | -0.068665 | -0.13733 | 0.004578 | 0.064087 | -0.13275 | -0.082398 | -0.064087 | -0.013733 | 0.30212 | 121.7239 | 0.13275 | 121.669 | 121.5637 | 121.5271 | 121.4951 | 121.4584 | -121.6644 | -121.6644 | 121.6553 | 121.6003 | 61.5326 | 61.5967
424.75 | 121.7468 | -61.5189 | 60.1227 | -0.01976 | 0.00012398 | 0.056845 | 0.055151 | 0.00058534 | -0.0087756 | -0.0019546 | -0.0023192 | 0.0033047 | 0.066988 | 0.060771 | -0.011378 | 0.019265 | -0.0025571 | -0.041199 | 59.9716 | -61.5372 | 60.0998 | -61.3129 | -61.7477 | -61.7477 | 0.027466 | 59.9716 | -61.5646 | 60.0449 | -61.4685 | -61.615 | -61.6928 | -0.01831 | -0.15106 | -0.022889 | 0.20599 | -0.22888 | -0.22888 | -0.21057 | -0.21057 | -0.045776 | -0.15106 | -0.07782 | 0.050354 | -0.17395 | -0.09613 | -0.12817 | -0.050354 | 0.2243 | 121.637 | 0.09613 | 121.6095 | 121.5088 | 121.5363 | 121.4905 | 121.4905 | -121.6599 | -121.6873 | 121.6187 | 121.5637 | 61.4777 | 61.5463
426.5 | 121.8063 | -61.6013 | 59.9899 | -0.0045011 | 0.0050372 | 0.058981 | 0.057074 | -0.00069646 | -0.0047168 | -0.0013138 | -0.005371 | 0.0015957 | 0.066347 | 0.056499 | -0.01031 | 0.019692 | -0.0044797 | -0.12817 | 59.9075 | -61.6241 | 60.0174 | -61.4044 | -61.8622 | -61.8622 | -0.059509 | 59.8709 | -61.647 | 60.022 | -61.528 | -61.702 | -61.7249 | -0.022889 | -0.082397 | 0.027466 | 0.19684 | -0.26093 | -0.26093 | -0.23804 | -0.23804 | -0.045777 | -0.11902 | 0.032044 | 0.073242 | -0.1236 | -0.10071 | -0.07782 | -0.054931 | 0.21973 | 121.6415 | 0.11902 | 121.669 | 121.5317 | 121.5179 | 121.5088 | 121.4722 | -121.6141 | -121.637 | 121.6187 | 121.6232 | 61.4731 | 61.5417
428.2656 | 121.8704 | -61.5601 | 59.9762 | -0.012131 | 0.0037556 | 0.058554 | 0.056006 | -0.0011237 | -0.0059986 | -0.0008866 | -0.005371 | 0.00074128 | 0.066774 | 0.049236 | -0.0092413 | 0.021187 | -0.0053343 | -0.091553 | 59.8846 | -61.6058 | 60.1181 | -61.3358 | -61.7844 | -61.7844 | 0.036621 | 59.8251 | -61.6287 | 60.0952 | -61.4456 | -61.5967 | -61.6287 | -0.045776 | -0.091552 | 0.14191 | 0.22431 | -0.2243 | -0.2243 | -0.17853 | -0.17853 | -0.068664 | -0.15106 | 0.11902 | 0.11444 | -0.068664 | -0.036621 | 0 | 0.032043 | 0.27008 | 121.7239 | 0.1831 | 121.7239 | 121.4905 | 121.4539 | 121.4447 | 121.3852 | -121.582 | -121.6049 | 121.6782 | 121.6553 | 61.4685 | 61.5967
430.0156 | 121.8018 | -61.5372 | 60.0861 | -0.012131 | 0.001192 | 0.056418 | 0.054937 | -0.0021919 | -0.0066394 | -0.000673 | -0.005371 | 0.0039457 | 0.067202 | 0.05714 | -0.0077459 | 0.019905 | -0.0027707 | -0.009155 | 59.9899 | -61.5555 | 60.0998 | -61.3266 | -61.7432 | -61.7752 | 0.027466 | 59.9442 | -61.5646 | 60.0815 | -61.4594 | -61.615 | -61.6562 | -0.018311 | -0.096131 | 0.013732 | 0.21057 | -0.23804 | -0.20599 | -0.21973 | -0.18768 | -0.027466 | -0.14191 | -0.004578 | 0.077819 | -0.11902 | -0.07782 | -0.091553 | -0.050354 | 0.22888 | 121.6553 | 0.10529 | 121.6461 | 121.5454 | 121.5088 | 121.5271 | 121.4813 | -121.6415 | -121.6507 | 121.637 | 121.6187 | 61.528 | 61.5646
431.7031 | 121.8567 | -61.5372 | 60.0311 | -0.012131 | 0.00033758 | 0.057272 | 0.052588 | -0.00026906 | -0.0057848 | -0.0045182 | -0.005371 | 0.00052768 | 0.066774 | 0.055858 | -0.011378 | 0.02076 | -0.0027707 | -0.07782 | 59.8984 | -61.5555 | 60.1044 | -61.3083 | -61.7569 | -61.7432 | 0 | 59.8892 | -61.6241 | 60.0998 | -61.4319 | -61.5646 | -61.6425 | -0.018311 | -0.13275 | 0.073242 | 0.22888 | -0.20599 | -0.21973 | -0.18768 | -0.20142 | -0.086976 | -0.14191 | 0.068664 | 0.10529 | -0.10529 | -0.027466 | -0.01831 | 0.05951 | 0.24719 | 121.6599 | 0.19226 | 121.7239 | 121.4539 | 121.5134 | 121.4355 | 121.4264 | -121.5866 | -121.6553 | 121.6415 | 121.637 | 61.4594 | 61.5372
433.4531 | 121.8109 | -61.5326 | 60.0723 | -0.0045011 | 0.00012398 | 0.057059 | 0.055578 | -0.0021919 | -0.0074938 | -0.0013138 | -0.005371 | 0.0020231 | 0.065279 | 0.063335 | -0.0075323 | 0.022255 | -0.0064023 | -0.022888 | 60.0128 | -61.5646 | 60.0998 | -61.322 | -61.7203 | -61.7661 | 0.032043 | 59.935 | -61.5784 | 60.0723 | -61.4594 | -61.6013 | -61.6699 | -0.032043 | -0.05951 | 0.027465 | 0.21057 | -0.23346 | -0.18768 | -0.20142 | -0.15564 | -0.045776 | -0.13733 | 0 | 0.073242 | -0.13733 | -0.068664 | -0.091553 | -0.022888 | 0.24262 | 121.6644 | 0.11902 | 121.6507 | 121.5775 | 121.5134 | 121.5454 | 121.4676 | -121.637 | -121.6507 | 121.6324 | 121.6049 | 61.5097 | 61.5646
435.2031 | 121.8613 | -61.5051 | 60.0174 | -0.012131 | 0.001192 | 0.057486 | 0.054724 | -0.0021919 | -0.0081348 | -0.0021682 | -0.005371 | 0.00052768 | 0.066561 | 0.055431 | -0.01095 | 0.02311 | 0.0025699 | -0.082397 | 59.8984 | -61.5738 | 60.1044 | -61.2808 | -61.734 | -61.7249 | 0.041199 | 59.8801 | -61.5967 | 60.1089 | -61.409 | -61.5234 | -61.6196 | -0.068665 | -0.11902 | 0.086975 | 0.2243 | -0.21973 | -0.22888 | -0.15106 | -0.16022 | -0.091553 | -0.13733 | 0.091553 | 0.09613 | -0.11444 | -0.01831 | -0.022888 | 0.073243 | 0.29297 | 121.6782 | 0.18768 | 121.7056 | 121.4722 | 121.4767 | 121.4035 | 121.3852 | -121.5912 | -121.6141 | 121.6095 | 121.6141 | 61.4227 | 61.5463
436.8906 | 121.843 | -61.5372 | 60.0174 | -0.012131 | 0.0041828 | 0.060477 | 0.054937 | 0.0025079 | -0.0077074 | -0.00345 | -0.0023192 | 0.0018095 | 0.063784 | 0.057353 | -0.0083869 | 0.020546 | 0.0010745 | -0.10071 | 59.8618 | -61.5738 | 60.0861 | -61.2991 | -61.7569 | -61.7523 | 0.018311 | 59.8755 | -61.6196 | 60.0632 | -61.4685 | -61.6013 | -61.6562 | -0.036622 | -0.15564 | 0.068665 | 0.23804 | -0.21515 | -0.21973 | -0.17853 | -0.18311 | -0.082398 | -0.14191 | 0.045776 | 0.068664 | -0.11902 | -0.064087 | -0.036621 | 0.018311 | 0.27466 | 121.6599 | 0.15106 | 121.6827 | 121.4355 | 121.4951 | 121.3989 | 121.4127 | -121.5912 | -121.637 | 121.6232 | 121.6003 | 61.4365 | 61.5555
438.6406 | 121.8246 | -61.5463 | 60.0174 | -0.0045011 | 0.0026874 | 0.057913 | 0.055365 | -0.0028327 | -0.0064258 | -0.0004592 | -0.0084228 | 0.0020231 | 0.065065 | 0.05714 | -0.0092413 | 0.022683 | -0.0038389 | -0.086975 | 59.8984 | -61.5692 | 60.1089 | -61.3083 | -61.7523 | -61.7523 | -0.004578 | 59.8801 | -61.6058 | 60.0723 | -61.4594 | -61.5875 | -61.6653 | -0.022888 | -0.11902 | 0.091553 | 0.23804 | -0.20599 | -0.20599 | -0.1831 | -0.1831 | -0.059509 | -0.13733 | 0.054932 | 0.086975 | -0.11902 | -0.041198 | -0.059509 | 0.018311 | 0.26093 | 121.6782 | 0.14648 | 121.6782 | 121.4676 | 121.4859 | 121.4447 | 121.4264 | -121.5866 | -121.6232 | 121.6553 | 121.6187 | 61.4594 | 61.5417
440.3906 | 121.756 | -61.5921 | 60.0082 | -0.0045011 | 0.0037556 | 0.057486 | 0.057928 | 0.0025079 | -0.0079212 | -0.0021682 | -0.0023192 | 0.0039457 | 0.06357 | 0.060131 | -0.0079597 | 0.021401 | -0.0044797 | -0.1236 | 59.9396 | -61.6241 | 60.0037 | -61.4365 | -61.8851 | -61.8851 | -0.091553 | 59.8801 | -61.6516 | 59.9716 | -61.5829 | -61.7386 | -61.7523 | -0.032044 | -0.068665 | -0.004578 | 0.15564 | -0.29297 | -0.29297 | -0.26093 | -0.26093 | -0.059509 | -0.12817 | -0.036621 | 0.009155 | -0.16022 | -0.14648 | -0.10071 | -0.086975 | 0.18768 | 121.6278 | 0.068664 | 121.6232 | 121.5637 | 121.5317 | 121.5317 | 121.4722 | -121.6324 | -121.6599 | 121.5958 | 121.5637 | 61.4685 | 61.5005
442.1406 | 121.875 | -61.5692 | 59.9487 | -0.012131 | 0.0054644 | 0.058981 | 0.055365 | 0.00037174 | -0.0066394 | -0.0025956 | -0.005371 | 0.0022367 | 0.065279 | 0.06248 | -0.0088141 | 0.022042 | -0.0044797 | -0.064087 | 59.8709 | -61.5967 | 60.1273 | -61.29 | -61.7706 | -61.7615 | 0.059509 | 59.8114 | -61.6379 | 60.0952 | -61.441 | -61.5921 | -61.647 | -0.027466 | -0.077819 | 0.17853 | 0.27924 | -0.19226 | -0.20142 | -0.16479 | -0.17395 | -0.068664 | -0.13733 | 0.14649 | 0.12817 | -0.07782 | -0.022888 | -0.009156 | 0.045776 | 0.3067 | 121.7239 | 0.19684 | 121.7331 | 121.4676 | 121.4493 | 121.4401 | 121.3806 | -121.5454 | -121.5866 | 121.6965 | 121.6644 | 61.5051 | 61.6287
443.8281 | 121.8704 | -61.4822 | 60.0449 | -0.012131 | -8.9824e-05 | 0.057272 | 0.052801 | -0.0013373 | -0.0077074 | -0.0032364 | -0.005371 | 0.00095488 | 0.066988 | 0.055431 | -0.0092413 | 0.022896 | -0.0027707 | 0.022888 | 59.9213 | -61.5417 | 60.2142 | -61.1893 | -61.6287 | -61.6562 | 0.14648 | 59.935 | -61.5646 | 60.1593 | -61.3586 | -61.496 | -61.5829 | -0.059509 | -0.1236 | 0.16937 | 0.29297 | -0.17395 | -0.14648 | -0.11444 | -0.086975 | -0.082397 | -0.10986 | 0.11444 | 0.1236 | -0.10071 | -0.013733 | -0.018311 | 0.068664 | 0.35248 | 121.756 | 0.20599 | 121.7239 | 121.463 | 121.4996 | 121.4035 | 121.4172 | -121.5866 | -121.6095 | 121.6965 | 121.6415 | 61.5051 | 61.6287
445.5156 | 121.8567 | -61.496 | 60.0494 | -0.0045011 | 0.001192 | 0.0577 | 0.054297 | -0.0026191 | -0.0064258 | -0.0011002 | -0.0023192 | 0.0022367 | 0.063784 | 0.059703 | -0.01095 | 0.019478 | -0.0034117 | 0.022888 | 59.9213 | -61.5326 | 60.2234 | -61.1664 | -61.615 | -61.647 | 0.17395 | 59.9075 | -61.5463 | 60.1501 | -61.3541 | -61.4685 | -61.5875 | -0.036621 | -0.12817 | 0.17395 | 0.32959 | -0.15106 | -0.11902 | -0.11444 | -0.082397 | -0.050354 | -0.14191 | 0.10071 | 0.14191 | -0.091552 | 0.027466 | -0.041198 | 0.07782 | 0.36621 | 121.756 | 0.19226 | 121.6965 | 121.4539 | 121.4539 | 121.4172 | 121.4035 | -121.582 | -121.5958 | 121.7194 | 121.6461 | 61.5189 | 61.6699
447.2656 | 121.788 | -61.5784 | 60.0311 | -0.0045011 | 0.0039692 | 0.057486 | 0.058783 | 0.0078485 | -0.0081348 | -0.0028092 | -0.005371 | 0.0041593 | 0.066988 | 0.058635 | -0.0077459 | 0.019265 | -0.0023435 | -0.11444 | 59.9442 | -61.6241 | 60.0082 | -61.4365 | -61.8896 | -61.8759 | -0.091553 | 59.8938 | -61.6562 | 59.9808 | -61.5784 | -61.734 | -61.7477 | -0.045777 | -0.086975 | -0.022888 | 0.14191 | -0.29755 | -0.31128 | -0.25177 | -0.2655 | -0.07782 | -0.13733 | -0.050354 | 0 | -0.16937 | -0.15564 | -0.091553 | -0.07782 | 0.18768 | 121.6324 | 0.07782 | 121.637 | 121.5683 | 121.55 | 121.5225 | 121.4722 | -121.6553 | -121.6873 | 121.5866 | 121.5591 | 61.4639 | 61.4868
449.0312 | 121.756 | -61.615 | 60.0082 | -0.012131 | 0.00461 | 0.059195 | 0.058996 | 0.0057123 | -0.0062122 | 0.001036 | -0.0084228 | 0.0024503 | 0.066774 | 0.054576 | -0.0083869 | 0.021614 | 0.0021425 | -0.11444 | 59.935 | -61.6287 | 60.0082 | -61.441 | -61.8759 | -61.8896 | -0.091553 | 59.8846 | -61.6425 | 59.9808 | -61.5692 | -61.7203 | -61.7523 | -0.013733 | -0.073242 | 0 | 0.17395 | -0.27466 | -0.26093 | -0.26093 | -0.24719 | -0.027466 | -0.1236 | -0.027466 | 0.045776 | -0.13733 | -0.10529 | -0.10986 | -0.07782 | 0.18768 | 121.637 | 0.073242 | 121.6232 | 121.5637 | 121.5271 | 121.55 | 121.4996 | -121.637 | -121.6507 | 121.6232 | 121.5958 | 61.5005 | 61.5234
450.7969 | 121.7422 | -61.5875 | 60.0357 | -0.012131 | 0.0041828 | 0.058981 | 0.057501 | 0.0020807 | -0.0074938 | -0.000673 | 0.00073235 | 0.0013821 | 0.066347 | 0.063549 | -0.0079597 | 0.021187 | -0.0023435 | -0.068665 | 59.9167 | -61.615 | 60.0311 | -61.409 | -61.853 | -61.8622 | -0.07782 | 59.9075 | -61.647 | 59.9854 | -61.5738 | -61.7157 | -61.7615 | -0.027466 | -0.11902 | -0.004578 | 0.17853 | -0.27466 | -0.2655 | -0.24719 | -0.23804 | -0.05951 | -0.12817 | -0.050354 | 0.013732 | -0.17395 | -0.12817 | -0.11444 | -0.068664 | 0.20599 | 121.6461 | 0.073242 | 121.6324 | 121.5317 | 121.5546 | 121.5042 | 121.4951 | -121.6507 | -121.6827 | 121.6187 | 121.5729 | 61.5189 | 61.5097
452.4844 | 121.8063 | -61.5189 | 60.0723 | -0.01976 | 0.0020466 | 0.059195 | 0.055365 | 0.0027215 | -0.008562 | 0.0008224 | -0.0023192 | 0.0022367 | 0.066774 | 0.06184 | -0.0094549 | 0.020546 | -0.0038389 | -0.013733 | 59.9625 | -61.5463 | 60.1135 | -61.3083 | -61.7432 | -61.7798 | 0.050354 | 59.9442 | -61.5967 | 60.0815 | -61.4548 | -61.6104 | -61.6562 | -0.027466 | -0.10986 | 0.041198 | 0.21057 | -0.26093 | -0.2243 | -0.23346 | -0.19684 | -0.07782 | -0.12817 | 0.009155 | 0.064087 | -0.13733 | -0.091553 | -0.059509 | -0.013733 | 0.23804 | 121.6599 | 0.14191 | 121.6782 | 121.5088 | 121.5408 | 121.4813 | 121.463 | -121.6187 | -121.669 | 121.6324 | 121.6003 | 61.5051 | 61.5692
454.25 | 121.7514 | -61.5738 | 59.9991 | -0.012131 | 0.0035418 | 0.058554 | 0.056006 | 0.0027215 | -0.0070666 | -0.0030228 | -0.0023192 | 0.0030911 | 0.067842 | 0.058849 | -0.0081733 | 0.020119 | -0.0029843 | -0.082397 | 59.9487 | -61.615 | 60.022 | -61.4044 | -61.8622 | -61.8668 | -0.10071 | 59.8938 | -61.6425 | 59.9808 | -61.5875 | -61.7386 | -61.7706 | -0.041198 | -0.050354 | 0.022889 | 0.16937 | -0.29297 | -0.28839 | -0.25177 | -0.24719 | -0.068664 | -0.10529 | -0.01831 | -0.013732 | -0.19684 | -0.16479 | -0.12817 | -0.09613 | 0.21057 | 121.637 | 0.054932 | 121.6232 | 121.5637 | 121.5363 | 121.5225 | 121.4676 | -121.6141 | -121.6415 | 121.5958 | 121.5546 | 61.4914 | 61.4731
455.9375 | 121.7239 | -61.5784 | 60.0311 | -0.012131 | 0.0052508 | 0.058768 | 0.056646 | 0.0018671 | -0.0057848 | -0.0030228 | -0.0084228 | 0.00095488 | 0.068056 | 0.054149 | -0.0077459 | 0.020974 | -0.0010617 | -0.086975 | 59.9533 | -61.6196 | 60.0266 | -61.4273 | -61.8622 | -61.8713 | -0.09613 | 59.9121 | -61.6333 | 59.9716 | -61.5875 | -61.7386 | -61.7706 | -0.041199 | -0.07782 | -0.004578 | 0.15106 | -0.29297 | -0.28381 | -0.25177 | -0.24262 | -0.054932 | -0.11902 | -0.059509 | -0.009155 | -0.19226 | -0.16022 | -0.13733 | -0.10528 | 0.19226 | 121.6461 | 0.045777 | 121.6049 | 121.5729 | 121.5454 | 121.5317 | 121.4905 | -121.6507 | -121.6644 | 121.6049 | 121.55 | 61.4914 | 61.4822
457.6875 | 121.8567 | -61.5417 | 59.9716 | -0.012131 | 0.0031146 | 0.058768 | 0.052801 | -0.0011237 | -0.0059986 | -0.0030228 | -0.0084228 | 0.0020231 | 0.065065 | 0.050945 | -0.0086005 | 0.022255 | 0.0019289 | -0.068665 | 59.8663 | -61.5829 | 60.1089 | -61.2808 | -61.7523 | -61.7477 | 0.050354 | 59.8251 | -61.6333 | 60.0632 | -61.4639 | -61.5829 | -61.6608 | -0.041199 | -0.10529 | 0.13733 | 0.26093 | -0.20599 | -0.21057 | -0.1648 | -0.16937 | -0.091553 | -0.14648 | 0.091552 | 0.07782 | -0.11902 | -0.041199 | -0.027466 | 0.050354 | 0.30212 | 121.6919 | 0.16937 | 121.6965 | 121.4493 | 121.4584 | 121.4081 | 121.3669 | -121.5546 | -121.6049 | 121.6507 | 121.6049 | 61.4731 | 61.5921
459.3906 | 121.8475 | -61.5417 | 59.967 | -0.01976 | 0.0035418 | 0.059195 | 0.056006 | 0.0040033 | -0.0042896 | 0.0008224 | -0.005371 | 0.00010048 | 0.065493 | 0.056285 | -0.01031 | 0.021828 | -0.00063445 | -0.07782 | 59.848 | -61.6058 | 60.1227 | -61.2762 | -61.7477 | -61.7432 | 0.068665 | 59.8068 | -61.6013 | 60.0906 | -61.441 | -61.5829 | -61.6562 | -0.064087 | -0.11902 | 0.15564 | 0.2655 | -0.20142 | -0.20599 | -0.13733 | -0.14191 | -0.059509 | -0.16022 | 0.1236 | 0.10071 | -0.11444 | -0.041199 | -0.054932 | 0.01831 | 0.32959 | 121.7285 | 0.16022 | 121.6919 | 121.4539 | 121.4081 | 121.3898 | 121.3486 | -121.5729 | -121.5683 | 121.6644 | 121.6324 | 61.4639 | 61.6104
461.1406 | 121.8933 | -61.5143 | 60.0311 | -0.012131 | 0.00055118 | 0.056845 | 0.053228 | -0.0047553 | -0.0045032 | -0.0013138 | -0.005371 | -0.00075412 | 0.06592 | 0.059276 | -0.011591 | 0.021187 | -0.00042085 | -0.022888 | 59.9167 | -61.5555 | 60.1639 | -61.2122 | -61.6745 | -61.6837 | 0.12817 | 59.903 | -61.5692 | 60.1547 | -61.3632 | -61.4868 | -61.5875 | -0.041199 | -0.11444 | 0.13275 | 0.30212 | -0.16937 | -0.16022 | -0.12817 | -0.11902 | -0.054932 | -0.12817 | 0.1236 | 0.15106 | -0.073242 | 0.027466 | -0.01831 | 0.082398 | 0.34332 | 121.7194 | 0.20599 | 121.7239 | 121.4722 | 121.4722 | 121.431 | 121.4172 | -121.5866 | -121.6003 | 121.6782 | 121.669 | 61.4914 | 61.6425
462.9062 | 121.8796 | -61.5555 | 59.9762 | -0.012131 | 0.0052508 | 0.056845 | 0.054297 | -0.0017645 | -0.0059986 | -0.0038772 | -0.0084228 | 0.00052768 | 0.065279 | 0.059062 | -0.0096685 | 0.022469 | 0.0032107 | -0.054932 | 59.848 | -61.5829 | 60.1318 | -61.2991 | -61.7569 | -61.7523 | 0.054932 | 59.7931 | -61.6241 | 60.1044 | -61.441 | -61.5829 | -61.6425 | -0.027466 | -0.12817 | 0.15564 | 0.25635 | -0.19684 | -0.20142 | -0.16937 | -0.17395 | -0.068665 | -0.18311 | 0.12817 | 0.11444 | -0.086975 | -0.027466 | -0.01831 | 0.041199 | 0.28381 | 121.7148 | 0.18311 | 121.7285 | 121.431 | 121.4172 | 121.4035 | 121.3486 | -121.5591 | -121.6003 | 121.6873 | 121.6599 | 61.5005 | 61.6104
464.6719 | 121.756 | -61.5051 | 60.1135 | -0.01976 | 0.00076478 | 0.056204 | 0.055365 | -0.0015509 | -0.0049304 | -0.0015274 | -0.011475 | 0.0045865 | 0.069124 | 0.055644 | -0.0092413 | 0.018837 | -0.0014891 | -0.036621 | 59.9945 | -61.5601 | 60.1044 | -61.3083 | -61.7432 | -61.7661 | 0.032043 | 59.9762 | -61.5463 | 60.0403 | -61.4868 | -61.5967 | -61.6791 | -0.054932 | -0.11902 | -0.009155 | 0.19684 | -0.26093 | -0.23804 | -0.20599 | -0.1831 | -0.041199 | -0.13733 | -0.073242 | 0.018311 | -0.17395 | -0.091553 | -0.13275 | -0.050354 | 0.25177 | 121.6644 | 0.05951 | 121.5866 | 121.5546 | 121.5225 | 121.4996 | 121.4813 | -121.6736 | -121.6599 | 121.6095 | 121.5454 | 61.4685 | 61.5372
466.4062 | 121.7926 | -61.5509 | 60.0357 | -0.012131 | 0.0041828 | 0.057272 | 0.057287 | -5.5462e-05 | -0.0083484 | -0.0036636 | -0.0023192 | 0.0045865 | 0.066133 | 0.063549 | -0.010737 | 0.022255 | -0.0021299 | -0.018311 | 59.967 | -61.5784 | 60.1089 | -61.3037 | -61.7569 | -61.7889 | 0.041199 | 59.9075 | -61.6058 | 60.0494 | -61.5005 | -61.6516 | -61.6928 | -0.027466 | -0.068665 | 0.073242 | 0.24719 | -0.23804 | -0.20599 | -0.21057 | -0.17853 | -0.054932 | -0.12817 | 0.013732 | 0.050354 | -0.14191 | -0.10071 | -0.086975 | -0.045776 | 0.27466 | 121.6873 | 0.10529 | 121.6553 | 121.5454 | 121.5134 | 121.5179 | 121.4584 | -121.6141 | -121.6415 | 121.6599 | 121.6003 | 61.5326 | 61.5921
468.0938 | 121.788 | -61.5189 | 60.0677 | -0.0045011 | 0.0016192 | 0.058127 | 0.057074 | -0.00091006 | -0.0070666 | -0.0019546 | -0.005371 | 0.0020231 | 0.06592 | 0.056072 | -0.0068915 | 0.020119 | 0.0012881 | -0.009155 | 59.9762 | -61.5555 | 60.0952 | -61.3174 | -61.7432 | -61.7706 | 0.032043 | 59.9533 | -61.5921 | 60.0723 | -61.4594 | -61.6013 | -61.6562 | -0.036621 | -0.091553 | 0.027466 | 0.20142 | -0.25177 | -0.2243 | -0.21515 | -0.18768 | -0.073242 | -0.11444 | 0.004578 | 0.059509 | -0.13733 | -0.082397 | -0.064087 | -0.009155 | 0.23804 | 121.6507 | 0.13275 | 121.6644 | 121.5317 | 121.5454 | 121.4951 | 121.4722 | -121.6232 | -121.6599 | 121.6141 | 121.5912 | 61.5097 | 61.5509
469.8594 | 121.7514 | -61.528 | 60.0906 | -0.012131 | 0.0016192 | 0.056204 | 0.054724 | -0.0030463 | -0.0062122 | -0.0015274 | -0.005371 | 0.00074128 | 0.065706 | 0.053722 | -0.0090277 | 0.019265 | -0.0059751 | -0.009155 | 59.9854 | -61.5326 | 60.0815 | -61.3083 | -61.7523 | -61.7706 | 0.018311 | 59.9579 | -61.5967 | 60.0449 | -61.4594 | -61.5875 | -61.6699 | -0.004578 | -0.10529 | -0.009155 | 0.21973 | -0.24261 | -0.2243 | -0.23804 | -0.21973 | -0.068665 | -0.13275 | -0.045776 | 0.068664 | -0.14191 | -0.059509 | -0.073242 | 0.009156 | 0.2243 | 121.6141 | 0.13733 | 121.6415 | 121.5179 | 121.5546 | 121.5134 | 121.4859 | -121.6232 | -121.6873 | 121.6095 | 121.5729 | 61.5189 | 61.5463
471.5469 | 121.8704 | -61.4639 | 60.0174 | -0.012131 | -0.00073062 | 0.057272 | 0.053869 | -0.0015509 | -0.0092028 | -0.0015274 | -0.005371 | 0.00031408 | 0.065706 | 0.054149 | -0.012019 | 0.020119 | 0.00086095 | 0.018311 | 59.9258 | -61.528 | 60.228 | -61.1481 | -61.6333 | -61.6562 | 0.16479 | 59.9304 | -61.5555 | 60.1913 | -61.3449 | -61.4685 | -61.5509 | -0.064087 | -0.091553 | 0.21057 | 0.31586 | -0.19226 | -0.16937 | -0.12817 | -0.10529 | -0.091553 | -0.086975 | 0.17395 | 0.11902 | -0.086975 | -0.004578 | 0.004578 | 0.086975 | 0.37994 | 121.756 | 0.21057 | 121.7468 | 121.4539 | 121.4859 | 121.3898 | 121.3943 | -121.5454 | -121.5729 | 121.6919 | 121.6553 | 61.4822 | 61.6287
473.3125 | 121.8384 | -61.5784 | 59.967 | -0.012131 | 0.006319 | 0.058768 | 0.057501 | 0.0022943 | -0.0079212 | -0.0015274 | -0.005371 | 0.0026639 | 0.067415 | 0.057781 | -0.0077459 | 0.020974 | -0.0038389 | -0.1236 | 59.903 | -61.5967 | 60.0357 | -61.3861 | -61.8393 | -61.8439 | -0.027466 | 59.8618 | -61.6287 | 60.0494 | -61.5097 | -61.647 | -61.6791 | -0.018311 | -0.064087 | 0.068665 | 0.19226 | -0.2655 | -0.26093 | -0.24719 | -0.24261 | -0.050354 | -0.10529 | 0.082397 | 0.068664 | -0.10071 | -0.068665 | -0.050354 | -0.018311 | 0.21057 | 121.6324 | 0.11902 | 121.6782 | 121.4996 | 121.4905 | 121.4813 | 121.4401 | -121.5637 | -121.5958 | 121.6141 | 121.6278 | 61.4548 | 61.5509
475 | 121.8475 | -61.5372 | 60.0357 | -0.0045011 | 0.00033758 | 0.059195 | 0.054937 | -0.00069646 | -0.0072802 | -0.002382 | -0.0023192 | 0.00010048 | 0.065706 | 0.052654 | -0.0094549 | 0.021401 | 0.0015017 | -0.07782 | 59.903 | -61.5875 | 60.0998 | -61.3083 | -61.7523 | -61.7386 | 0.013733 | 59.8846 | -61.5921 | 60.0815 | -61.4319 | -61.5601 | -61.6379 | -0.050354 | -0.13275 | 0.064086 | 0.22888 | -0.20142 | -0.21515 | -0.15106 | -0.16479 | -0.054932 | -0.15106 | 0.045776 | 0.10529 | -0.10071 | -0.022889 | -0.045776 | 0.032043 | 0.27923 | 121.6873 | 0.16022 | 121.6736 | 121.4905 | 121.4767 | 121.4401 | 121.4218 | -121.6232 | -121.6278 | 121.637 | 121.6187 | 61.4594 | 61.5509
476.7344 | 121.8155 | -61.5234 | 60.0632 | -0.0045011 | 0.001833 | 0.058768 | 0.057715 | 0.0046441 | -0.0083484 | -0.002382 | -0.0084228 | 0.00095488 | 0.064211 | 0.060131 | -0.0068915 | 0.019265 | -0.0021299 | -0.009155 | 59.935 | -61.5601 | 60.1181 | -61.2946 | -61.7477 | -61.7706 | 0.07782 | 59.9167 | -61.6013 | 60.0861 | -61.4456 | -61.6058 | -61.6653 | -0.036622 | -0.12817 | 0.054932 | 0.22888 | -0.24719 | -0.22431 | -0.21057 | -0.18768 | -0.07782 | -0.14648 | 0.022889 | 0.077819 | -0.14191 | -0.082398 | -0.064087 | -0.004578 | 0.2655 | 121.6782 | 0.15564 | 121.6873 | 121.4951 | 121.5179 | 121.4584 | 121.4401 | -121.6232 | -121.6644 | 121.6415 | 121.6095 | 61.5143 | 61.6013
478.4844 | 121.8521 | -61.5509 | 59.9808 | -0.012131 | 0.0033282 | 0.058981 | 0.054937 | -0.0024055 | -0.0070666 | -0.0043046 | -0.0084228 | 0.00031408 | 0.066347 | 0.05009 | -0.0090277 | 0.020333 | -0.0066159 | -0.082397 | 59.8801 | -61.5829 | 60.1181 | -61.2854 | -61.7752 | -61.7477 | 0.045776 | 59.8389 | -61.615 | 60.0723 | -61.4639 | -61.5921 | -61.6562 | -0.032044 | -0.10071 | 0.13733 | 0.2655 | -0.19684 | -0.22431 | -0.1648 | -0.19226 | -0.064087 | -0.14191 | 0.091553 | 0.086975 | -0.10529 | -0.041199 | -0.041199 | 0.022888 | 0.29755 | 121.701 | 0.15106 | 121.6873 | 121.463 | 121.4539 | 121.431 | 121.3898 | -121.5637 | -121.5958 | 121.669 | 121.6232 | 61.4685 | 61.5967
480.1875 | 121.7514 | -61.5189 | 60.0861 | -0.0045011 | 0.00033758 | 0.056204 | 0.054724 | 0.0016535 | -0.008562 | -0.0025956 | -0.005371 | 0.0033047 | 0.068483 | 0.057994 | -0.011164 | 0.020333 | -0.00020725 | -0.027466 | 59.9899 | -61.5463 | 60.1044 | -61.3083 | -61.7477 | -61.7706 | 0.032043 | 59.967 | -61.5509 | 60.0494 | -61.4639 | -61.6013 | -61.6745 | -0.027466 | -0.096131 | 0.01831 | 0.21057 | -0.25177 | -0.22888 | -0.2243 | -0.20142 | -0.032043 | -0.11902 | -0.036622 | 0.054932 | -0.15564 | -0.082397 | -0.1236 | -0.050354 | 0.23804 | 121.6507 | 0.086975 | 121.6003 | 121.5363 | 121.5179 | 121.5088 | 121.4859 | -121.6324 | -121.637 | 121.6232 | 121.5683 | 61.4914 | 61.5509
481.9375 | 121.8475 | -61.5509 | 59.9808 | -0.012131 | 0.0022602 | 0.056845 | 0.054937 | -0.00026906 | -0.0066394 | -0.0021682 | -0.005371 | 0.00074128 | 0.065493 | 0.057781 | -0.0090277 | 0.020119 | -0.0040525 | -0.07782 | 59.8801 | -61.5967 | 60.1044 | -61.2854 | -61.7569 | -61.7523 | 0.045776 | 59.8434 | -61.6333 | 60.0632 | -61.4594 | -61.5829 | -61.6562 | -0.045777 | -0.10071 | 0.1236 | 0.2655 | -0.20142 | -0.20599 | -0.15564 | -0.16022 | -0.082398 | -0.13733 | 0.082397 | 0.091552 | -0.10529 | -0.032044 | -0.022888 | 0.050354 | 0.31128 | 121.7011 | 0.17395 | 121.6965 | 121.4767 | 121.4767 | 121.431 | 121.3943 | -121.5775 | -121.6141 | 121.6553 | 121.6141 | 61.4731 | 61.5967
483.6875 | 121.7834 | -61.5601 | 60.0357 | -0.012131 | 0.0024738 | 0.0577 | 0.058569 | -0.00048286 | -0.006853 | -0.0032364 | -0.0023192 | 0.0030911 | 0.066133 | 0.061412 | -0.0090277 | 0.019692 | 0.00086095 | -0.027466 | 59.9487 | -61.5692 | 60.1089 | -61.3129 | -61.7661 | -61.7844 | 0.050354 | 59.9258 | -61.6104 | 60.0403 | -61.5143 | -61.6608 | -61.6974 | -0.009155 | -0.086976 | 0.073242 | 0.24719 | -0.2243 | -0.20599 | -0.21515 | -0.19684 | -0.050354 | -0.10986 | 0.004577 | 0.045777 | -0.13733 | -0.10071 | -0.086975 | -0.050354 | 0.25635 | 121.6782 | 0.096131 | 121.6507 | 121.5179 | 121.5363 | 121.5088 | 121.4859 | -121.6049 | -121.6461 | 121.669 | 121.6003 | 61.5326 | 61.6104
485.4375 | 121.7743 | -61.5555 | 60.0403 | -0.012131 | 0.002901 | 0.056845 | 0.058355 | 0.0016535 | -0.0072802 | -0.0004592 | -0.0023192 | 0.0022367 | 0.067202 | 0.054576 | -0.0081733 | 0.019478 | -0.0012753 | -0.009155 | 59.935 | -61.5784 | 60.1044 | -61.3129 | -61.7752 | -61.7844 | 0.054932 | 59.9304 | -61.6013 | 60.0586 | -61.4914 | -61.6608 | -61.6882 | -0.022888 | -0.10529 | 0.064087 | 0.24262 | -0.22888 | -0.21973 | -0.20599 | -0.19684 | -0.045776 | -0.10986 | 0.018311 | 0.064087 | -0.13275 | -0.10529 | -0.086975 | -0.05951 | 0.2655 | 121.6827 | 0.10986 | 121.6599 | 121.5134 | 121.5317 | 121.4905 | 121.4859 | -121.6187 | -121.6415 | 121.6599 | 121.6141 | 61.5463 | 61.6104
487.125 | 121.8063 | -61.5372 | 60.0403 | -0.0045011 | 0.0037556 | 0.058127 | 0.055792 | 0.0018671 | -0.0070666 | -0.0015274 | -0.005371 | 0.0026639 | 0.066133 | 0.062267 | -0.0079597 | 0.020119 | -0.0051205 | 0 | 59.9625 | -61.5509 | 60.1135 | -61.2991 | -61.7294 | -61.7661 | 0.064087 | 59.9075 | -61.5921 | 60.0815 | -61.4594 | -61.6058 | -61.6516 | -0.013733 | -0.07782 | 0.073242 | 0.23804 | -0.22888 | -0.19226 | -0.21515 | -0.17853 | -0.054932 | -0.13275 | 0.041199 | 0.077819 | -0.11444 | -0.068665 | -0.059509 | -0.013733 | 0.25177 | 121.6644 | 0.13275 | 121.6736 | 121.5134 | 121.4996 | 121.4996 | 121.4447 | -121.5912 | -121.6324 | 121.6507 | 121.6187 | 61.5372 | 61.6013
488.875 | 121.7697 | -61.6104 | 59.9899 | -0.012131 | 0.0043964 | 0.059836 | 0.057287 | 0.00037174 | -0.0057848 | -0.0019546 | 0.00073235 | 0.0028775 | 0.065279 | 0.054576 | -0.0064643 | 0.021828 | -0.0029843 | -0.10529 | 59.9167 | -61.6241 | 59.9991 | -61.4365 | -61.8805 | -61.8759 | -0.10529 | 59.8938 | -61.6516 | 59.9716 | -61.5692 | -61.7294 | -61.7569 | -0.013733 | -0.073242 | 0.009155 | 0.17395 | -0.2655 | -0.27008 | -0.25177 | -0.25635 | -0.041198 | -0.09613 | -0.01831 | 0.041199 | -0.14648 | -0.11902 | -0.10529 | -0.07782 | 0.18768 | 121.6232 | 0.082397 | 121.6232 | 121.5408 | 121.5454 | 121.5271 | 121.5042 | -121.6141 | -121.6415 | 121.6095 | 121.582 | 61.5051 | 61.5051
490.625 | 121.7377 | -61.5921 | 60.022 | -0.012131 | 0.0043964 | 0.057486 | 0.057928 | 0.00058534 | -0.0066394 | -0.0004592 | -0.005371 | 0.0043729 | 0.066561 | 0.056926 | -0.0077459 | 0.020546 | -0.0029843 | -0.09613 | 59.9442 | -61.5967 | 60.0174 | -61.441 | -61.8942 | -61.8759 | -0.11902 | 59.8801 | -61.6608 | 59.9854 | -61.5692 | -61.734 | -61.7661 | -0.004578 | -0.07782 | -0.004578 | 0.15106 | -0.28381 | -0.30212 | -0.27924 | -0.29755 | -0.068665 | -0.14191 | -0.036621 | 0.022888 | -0.17395 | -0.14191 | -0.10529 | -0.073242 | 0.15564 | 121.6141 | 0.091553 | 121.6461 | 121.5408 | 121.5408 | 121.5363 | 121.4722 | -121.6187 | -121.6827 | 121.6095 | 121.5775 | 61.496 | 61.4731
492.3906 | 121.8246 | -61.5372 | 60.0082 | -0.0045011 | 0.0020466 | 0.05834 | 0.053869 | -0.0024055 | -0.0030078 | -0.0045182 | -0.0023192 | 0.00074128 | 0.067202 | 0.057353 | -0.0094549 | 0.023964 | 0.00021995 | -0.086975 | 59.8846 | -61.5738 | 60.0861 | -61.2991 | -61.7615 | -61.7432 | 0.022888 | 59.8801 | -61.6104 | 60.0632 | -61.4639 | -61.5829 | -61.6608 | -0.036622 | -0.1236 | 0.07782 | 0.23804 | -0.20599 | -0.2243 | -0.16937 | -0.18768 | -0.073243 | -0.12817 | 0.054931 | 0.073242 | -0.1236 | -0.045777 | -0.050354 | 0.027466 | 0.27466 | 121.6599 | 0.14648 | 121.6736 | 121.4584 | 121.4905 | 121.4218 | 121.4172 | -121.582 | -121.6187 | 121.6232 | 121.6003 | 61.4502 | 61.5601
494.0781 | 121.8246 | -61.5417 | 60.0403 | -0.012131 | -0.00094422 | 0.0577 | 0.053442 | -0.0011237 | -0.0087756 | -0.001741 | -0.011475 | -0.00011332 | 0.065279 | 0.053508 | -0.010523 | 0.020974 | -0.0017027 | -0.082397 | 59.903 | -61.5738 | 60.0998 | -61.3083 | -61.7477 | -61.7569 | 0.018311 | 59.8618 | -61.6241 | 60.0586 | -61.4639 | -61.5829 | -61.6562 | -0.032044 | -0.13733 | 0.059509 | 0.23346 | -0.21515 | -0.20599 | -0.18311 | -0.17395 | -0.082398 | -0.17853 | 0.018311 | 0.07782 | -0.11444 | -0.041199 | -0.032043 | 0.041199 | 0.2655 | 121.6736 | 0.16022 | 121.6827 | 121.4767 | 121.4859 | 121.4447 | 121.4035 | -121.6141 | -121.6644 | 121.6415 | 121.6003 | 61.4594 | 61.5601
495.8281 | 121.8384 | -61.5509 | 60.0082 | -0.01976 | 0.0048236 | 0.056418 | 0.055365 | -0.0017645 | -0.0053576 | -0.0038772 | -0.005371 | 0.0020231 | 0.065065 | 0.053508 | -0.012446 | 0.020333 | -0.0042661 | -0.082397 | 59.8801 | -61.5784 | 60.0998 | -61.29 | -61.7661 | -61.7569 | 0.027466 | 59.8297 | -61.6013 | 60.0494 | -61.4548 | -61.5875 | -61.6608 | -0.027466 | -0.12817 | 0.091552 | 0.26093 | -0.20599 | -0.21515 | -0.17853 | -0.18768 | -0.050354 | -0.17853 | 0.041198 | 0.09613 | -0.10986 | -0.036621 | -0.05951 | 0.013733 | 0.28839 | 121.6782 | 0.14648 | 121.6507 | 121.4584 | 121.431 | 121.431 | 121.3806 | -121.5866 | -121.6095 | 121.6507 | 121.6003 | 61.4685 | 61.5784
497.5156 | 121.7377 | -61.5829 | 60.0357 | -0.0045011 | 0.0050372 | 0.057486 | 0.057074 | 0.0012261 | -0.0066394 | -0.0015274 | -0.0023192 | 0.0028775 | 0.06592 | 0.055004 | -0.0073187 | 0.018837 | -0.0038389 | -0.10071 | 59.9213 | -61.6379 | 60.0037 | -61.4502 | -61.8988 | -61.8942 | -0.07782 | 59.8801 | -61.647 | 59.9808 | -61.5829 | -61.7432 | -61.7523 | -0.054931 | -0.11444 | -0.032044 | 0.13275 | -0.31128 | -0.31586 | -0.25635 | -0.26093 | -0.064087 | -0.15564 | -0.054932 | 0 | -0.16937 | -0.16022 | -0.10529 | -0.09613 | 0.18768 | 121.6415 | 0.064087 | 121.6278 | 121.5591 | 121.5271 | 121.5042 | 121.463 | -121.6736 | -121.6827 | 121.5866 | 121.5637 | 61.4822 | 61.5051
499.2656 | 121.7651 | -61.5189 | 60.1044 | -0.01976 | -8.9824e-05 | 0.056845 | 0.054937 | 0.0046441 | -0.0072802 | -0.0015274 | -0.0084228 | 0.0039457 | 0.064852 | 0.056713 | -0.0098823 | 0.019478 | -0.0014891 | -0.018311 | 59.9762 | -61.5372 | 60.1044 | -61.3129 | -61.7477 | -61.7523 | 0.027466 | 59.9762 | -61.5738 | 60.0357 | -61.4685 | -61.5921 | -61.6745 | -0.01831 | -0.12817 | 0 | 0.20599 | -0.23346 | -0.22888 | -0.21515 | -0.21057 | -0.054932 | -0.12817 | -0.068664 | 0.050354 | -0.15564 | -0.073242 | -0.10071 | -0.01831 | 0.2243 | 121.6415 | 0.10529 | 121.6095 | 121.5134 | 121.55 | 121.4951 | 121.4951 | -121.6415 | -121.6782 | 121.6232 | 121.5546 | 61.5005 | 61.5463
501.0156 | 121.756 | -61.6104 | 59.9991 | -0.012131 | 0.0035418 | 0.060904 | 0.05686 | 0.0042169 | -0.005144 | -0.002382 | -0.005371 | 0.0024503 | 0.063784 | 0.060771 | -0.0081733 | 0.020333 | -0.0038389 | -0.09613 | 59.9304 | -61.6104 | 60.0037 | -61.441 | -61.8896 | -61.8713 | -0.091553 | 59.8846 | -61.6425 | 59.9899 | -61.5829 | -61.7386 | -61.7477 | 0 | -0.068664 | 0.004578 | 0.16937 | -0.26093 | -0.27923 | -0.26093 | -0.27923 | -0.032043 | -0.11444 | -0.009155 | 0.027466 | -0.13733 | -0.12817 | -0.10529 | -0.09613 | 0.16937 | 121.6141 | 0.059509 | 121.6324 | 121.5408 | 121.5271 | 121.5408 | 121.4951 | -121.6095 | -121.6415 | 121.6141 | 121.6003 | 61.5143 | 61.5189
502.7656 | 121.8933 | -61.4914 | 60.0449 | -0.012131 | -8.9824e-05 | 0.056418 | 0.054297 | -0.0039007 | -0.0072802 | 0.0008224 | -0.005371 | -0.00011332 | 0.065706 | 0.054363 | -0.012232 | 0.022469 | 0.00021995 | -0.036621 | 59.9442 | -61.5692 | 60.1547 | -61.2259 | -61.6791 | -61.6699 | 0.10071 | 59.8846 | -61.5646 | 60.141 | -61.3586 | -61.4731 | -61.5738 | -0.07782 | -0.10071 | 0.10986 | 0.2655 | -0.17853 | -0.18768 | -0.10071 | -0.10986 | -0.073242 | -0.16022 | 0.09613 | 0.13275 | -0.082398 | 0.018311 | -0.009156 | 0.091553 | 0.34332 | 121.7239 | 0.20599 | 121.7056 | 121.5134 | 121.4493 | 121.4355 | 121.376 | -121.6141 | -121.6095 | 121.6461 | 121.6324 | 61.4548 | 61.5921
504.4531 | 121.7789 | -61.5326 | 60.0861 | -0.012131 | 0.001192 | 0.059836 | 0.057501 | -0.0036871 | -0.0055712 | -0.000673 | -0.0084228 | 0.0035183 | 0.06827 | 0.05949 | -0.0094549 | 0.019478 | -0.00020725 | -0.013733 | 59.9854 | -61.5463 | 60.0769 | -61.3495 | -61.7798 | -61.7798 | 0.004578 | 59.9533 | -61.5921 | 60.0586 | -61.4456 | -61.6013 | -61.6516 | -0.013733 | -0.10071 | -0.009156 | 0.18311 | -0.24719 | -0.24719 | -0.23346 | -0.23346 | -0.059509 | -0.13275 | -0.027466 | 0.086975 | -0.11902 | -0.068664 | -0.059509 | -0.009155 | 0.19684 | 121.6232 | 0.14648 | 121.6507 | 121.5317 | 121.5454 | 121.5179 | 121.4859 | -121.6324 | -121.6782 | 121.6095 | 121.5912 | 61.5189 | 61.5372
506.1875 | 121.7926 | -61.528 | 60.0494 | 0.0031279 | 0.00055118 | 0.058981 | 0.05451 | 0.0020807 | -0.0079212 | -0.0047318 | -0.005371 | 0.0052273 | 0.067629 | 0.056926 | -0.0094549 | 0.021828 | -0.0031979 | 0 | 59.9716 | -61.5784 | 60.1044 | -61.2991 | -61.7477 | -61.7661 | 0.054932 | 59.9258 | -61.5829 | 60.0723 | -61.4594 | -61.6104 | -61.6562 | -0.050354 | -0.077819 | 0.054932 | 0.22888 | -0.23804 | -0.21973 | -0.18768 | -0.16937 | -0.054932 | -0.1236 | 0.022889 | 0.068664 | -0.12817 | -0.082398 | -0.073242 | -0.027466 | 0.27924 | 121.6827 | 0.1236 | 121.6553 | 121.55 | 121.5088 | 121.4996 | 121.4539 | -121.6278 | -121.6324 | 121.6324 | 121.6003 | 61.528 | 61.5829
507.9375 | 121.7926 | -61.5829 | 60.0174 | -0.012131 | 0.0039692 | 0.057486 | 0.055792 | 0.0022943 | -0.0042896 | -0.00345 | -0.0023192 | 0.0043729 | 0.066774 | 0.05714 | -0.0088141 | 0.022896 | -0.0029843 | -0.11444 | 59.935 | -61.5967 | 60.022 | -61.4044 | -61.8622 | -61.8668 | -0.059509 | 59.8572 | -61.6379 | 59.9945 | -61.5646 | -61.6974 | -61.7249 | -0.013733 | -0.082397 | 0.004578 | 0.17853 | -0.28381 | -0.27924 | -0.27008 | -0.2655 | -0.054931 | -0.16022 | -0.022888 | 0.018311 | -0.14191 | -0.11444 | -0.086976 | -0.05951 | 0.19226 | 121.6187 | 0.073242 | 121.6324 | 121.5317 | 121.4951 | 121.5179 | 121.4401 | -121.6141 | -121.6553 | 121.6049 | 121.5775 | 61.4685 | 61.5234
509.6406 | 121.7331 | -61.5921 | 60.0311 | -0.012131 | 0.0035418 | 0.058981 | 0.056006 | -0.00069646 | -0.0040758 | -0.002382 | -0.005371 | 0.0043729 | 0.067842 | 0.060771 | -0.0068915 | 0.020119 | -0.0066159 | -0.091553 | 59.9396 | -61.6013 | 60.0174 | -61.4136 | -61.8713 | -61.8805 | -0.086975 | 59.9167 | -61.6425 | 59.9808 | -61.5875 | -61.7386 | -61.7615 | -0.009155 | -0.091553 | -0.013733 | 0.17853 | -0.28839 | -0.27924 | -0.27924 | -0.27008 | -0.050354 | -0.11444 | -0.050354 | 0.004578 | -0.16937 | -0.14648 | -0.11902 | -0.09613 | 0.18768 | 121.6187 | 0.054932 | 121.6232 | 121.5408 | 121.5591 | 121.5317 | 121.5088 | -121.6324 | -121.6736 | 121.6095 | 121.5729 | 61.5005 | 61.5051
511.3906 | 121.875 | -61.5646 | 59.9579 | 0.0031279 | 0.0039692 | 0.06069 | 0.055151 | -0.0039007 | -0.006853 | -0.0021682 | -0.0023192 | -0.0011813 | 0.06827 | 0.059917 | -0.0092413 | 0.022255 | -0.0025571 | -0.041199 | 59.8892 | -61.5692 | 60.1181 | -61.2946 | -61.7569 | -61.7523 | 0.050354 | 59.7977 | -61.6241 | 60.0952 | -61.4502 | -61.5875 | -61.6516 | -0.004578 | -0.068665 | 0.16022 | 0.27008 | -0.18768 | -0.19226 | -0.1831 | -0.18768 | -0.05951 | -0.16022 | 0.13733 | 0.11444 | -0.086975 | -0.022888 | -0.027465 | 0.036622 | 0.27466 | 121.6873 | 0.17395 | 121.7194 | 121.4584 | 121.4218 | 121.4539 | 121.3623 | -121.5271 | -121.582 | 121.6827 | 121.6599 | 61.5234 | 61.615
513.1406 | 121.8704 | -61.4914 | 60.0586 | 0.0031279 | -0.0011578 | 0.055777 | 0.052588 | 0.0033623 | -0.008562 | -0.0032364 | -0.005371 | 0.0011685 | 0.066133 | 0.05479 | -0.011378 | 0.021401 | -0.0014891 | 0.027466 | 59.935 | -61.5417 | 60.2051 | -61.1938 | -61.6333 | -61.647 | 0.14648 | 59.9075 | -61.5234 | 60.1501 | -61.3632 | -61.5051 | -61.5738 | -0.050354 | -0.1236 | 0.14648 | 0.29755 | -0.15564 | -0.14191 | -0.10529 | -0.091553 | -0.032043 | -0.15106 | 0.091552 | 0.12817 | -0.082398 | -0.013733 | -0.050355 | 0.01831 | 0.3479 | 121.7468 | 0.16022 | 121.6736 | 121.4767 | 121.431 | 121.4264 | 121.3989 | -121.6003 | -121.582 | 121.6965 | 121.6415 | 61.5189 | 61.6379
514.8281 | 121.7606 | -61.5509 | 60.0403 | -0.012131 | 0.0026874 | 0.058127 | 0.056219 | 0.0018671 | -0.0081348 | 0.0008224 | -0.0023192 | 0.0037321 | 0.064638 | 0.056072 | -0.01031 | 0.020546 | -0.0055479 | -0.022888 | 59.9396 | -61.5829 | 60.0861 | -61.3266 | -61.7935 | -61.8118 | 0.027466 | 59.903 | -61.615 | 60.0266 | -61.528 | -61.6745 | -61.7111 | -0.032044 | -0.10071 | 0.045777 | 0.2243 | -0.26093 | -0.24262 | -0.22888 | -0.21057 | -0.064087 | -0.13733 | -0.013733 | 0.022888 | -0.16022 | -0.1236 | -0.096131 | -0.05951 | 0.25635 | 121.669 | 0.086975 | 121.6415 | 121.5225 | 121.5179 | 121.4905 | 121.4539 | -121.6232 | -121.6553 | 121.637 | 121.5775 | 61.528 | 61.5784
516.5781 | 121.875 | -61.5601 | 59.9533 | 0.0031279 | 0.0043964 | 0.056631 | 0.055365 | 0.00079894 | -0.0049304 | -0.001741 | -0.0023192 | 0.0022367 | 0.064211 | 0.052654 | -0.01031 | 0.023537 | -0.0031979 | -0.050354 | 59.8846 | -61.5875 | 60.1181 | -61.2946 | -61.7706 | -61.7661 | 0.054932 | 59.8343 | -61.6241 | 60.0906 | -61.4548 | -61.5967 | -61.6241 | -0.027465 | -0.068664 | 0.16479 | 0.2655 | -0.20599 | -0.21057 | -0.17853 | -0.18311 | -0.064087 | -0.11902 | 0.13733 | 0.10529 | -0.064087 | -0.036621 | 0 | 0.027466 | 0.29297 | 121.7056 | 0.16937 | 121.7148 | 121.4722 | 121.4584 | 121.4447 | 121.3943 | -121.5408 | -121.5775 | 121.6782 | 121.6507 | 61.5097 | 61.615
518.3281 | 121.7422 | -61.5692 | 60.0082 | -0.01976 | 0.002901 | 0.0577 | 0.056646 | 0.0052851 | -0.0045032 | 0.0003952 | -0.005371 | 0.0024503 | 0.06592 | 0.058422 | -0.0062507 | 0.019265 | -0.0010617 | -0.11902 | 59.9396 | -61.6379 | 59.9945 | -61.441 | -61.8805 | -61.8805 | -0.09613 | 59.9075 | -61.6425 | 59.9854 | -61.5784 | -61.7203 | -61.7477 | -0.068664 | -0.068665 | -0.013733 | 0.12817 | -0.31128 | -0.31128 | -0.24262 | -0.24262 | -0.073242 | -0.10071 | -0.022888 | -0.009155 | -0.17853 | -0.15106 | -0.10529 | -0.07782 | 0.19684 | 121.6324 | 0.064087 | 121.6278 | 121.5775 | 121.55 | 121.5088 | 121.4767 | -121.6461 | -121.6507 | 121.5637 | 121.5546 | 61.4502 | 61.4731
520.0156 | 121.843 | -61.5189 | 60.0174 | -0.01976 | 0.002901 | 0.0577 | 0.05216 | -0.0024055 | -0.0059986 | -0.0049454 | -0.005371 | 0.0011685 | 0.066347 | 0.051586 | -0.0092413 | 0.022042 | -0.0031979 | -0.068665 | 59.9121 | -61.5555 | 60.0906 | -61.2991 | -61.734 | -61.7386 | 0.022888 | 59.8663 | -61.5875 | 60.0906 | -61.441 | -61.5509 | -61.615 | -0.036621 | -0.10529 | 0.073242 | 0.21973 | -0.21973 | -0.21515 | -0.1831 | -0.17853 | -0.068664 | -0.15106 | 0.073242 | 0.07782 | -0.09613 | -0.032043 | -0.027466 | 0.036621 | 0.25635 | 121.6461 | 0.14648 | 121.6782 | 121.4676 | 121.4539 | 121.431 | 121.3852 | -121.5729 | -121.6049 | 121.6095 | 121.6095 | 61.4502 | 61.5417
521.7656 | 121.8475 | -61.5692 | 60.0037 | 0.010757 | 0.0026874 | 0.057913 | 0.054083 | -0.00026906 | -0.0066394 | -0.0025956 | 0.00073235 | 0.0018095 | 0.065279 | 0.050518 | -0.010096 | 0.02076 | 0.0019289 | -0.10529 | 59.8801 | -61.5692 | 60.0861 | -61.29 | -61.7615 | -61.7523 | 0.013733 | 59.8434 | -61.6333 | 60.0632 | -61.4731 | -61.6058 | -61.6516 | 0 | -0.1236 | 0.082398 | 0.27924 | -0.1831 | -0.19226 | -0.1831 | -0.19226 | -0.064087 | -0.16022 | 0.059509 | 0.096131 | -0.082397 | -0.036621 | -0.01831 | 0.027466 | 0.27924 | 121.6553 | 0.16022 | 121.6965 | 121.4493 | 121.4767 | 121.4493 | 121.4127 | -121.5729 | -121.637 | 121.6553 | 121.6324 | 61.4639 | 61.5829
523.4531 | 121.7422 | -61.5189 | 60.1044 | -0.0045011 | 0.001833 | 0.056631 | 0.052801 | -0.0041145 | -0.0089892 | -0.0030228 | -0.005371 | 0.0039457 | 0.066561 | 0.063762 | -0.011164 | 0.021614 | -0.0059751 | -0.027466 | 59.9808 | -61.5417 | 60.0952 | -61.322 | -61.7523 | -61.7523 | 0.036621 | 59.9808 | -61.5601 | 60.0632 | -61.4777 | -61.6013 | -61.6837 | -0.022888 | -0.1236 | -0.009155 | 0.19684 | -0.23346 | -0.23346 | -0.21057 | -0.21057 | -0.041199 | -0.1236 | -0.041199 | 0.041199 | -0.1648 | -0.082397 | -0.1236 | -0.041198 | 0.21973 | 121.637 | 0.082398 | 121.6232 | 121.5225 | 121.5408 | 121.4996 | 121.4996 | -121.6461 | -121.6644 | 121.6141 | 121.582 | 61.4914 | 61.5555
525.2031 | 121.8567 | -61.4914 | 60.0311 | -0.012131 | 0.0016192 | 0.057059 | 0.054724 | -0.0024055 | -0.0074938 | -0.0025956 | -0.005371 | 0.00052768 | 0.06592 | 0.060771 | -0.01031 | 0.020974 | -0.0021299 | -0.07782 | 59.9167 | -61.5921 | 60.1135 | -61.2808 | -61.7294 | -61.7386 | 0.036621 | 59.8618 | -61.5875 | 60.1089 | -61.409 | -61.5326 | -61.5967 | -0.10071 | -0.11444 | 0.082397 | 0.21057 | -0.24719 | -0.23804 | -0.14648 | -0.13733 | -0.09613 | -0.16937 | 0.07782 | 0.082397 | -0.10529 | -0.041199 | -0.009156 | 0.054931 | 0.31128 | 121.7056 | 0.17853 | 121.6965 | 121.5088 | 121.4493 | 121.4081 | 121.3531 | -121.6232 | -121.6187 | 121.6049 | 121.6003 | 61.4136 | 61.528
526.9531 | 121.8475 | -61.5463 | 59.9716 | -0.012131 | 0.00033758 | 0.058127 | 0.054297 | -0.00069646 | -0.0064258 | -0.0002456 | -0.005371 | 0.0018095 | 0.065065 | 0.055858 | -0.010737 | 0.022683 | -0.0070433 | -0.064087 | 59.848 | -61.5784 | 60.1227 | -61.2717 | -61.7569 | -61.7523 | 0.068665 | 59.8297 | -61.6333 | 60.0815 | -61.4685 | -61.5921 | -61.647 | -0.032043 | -0.1236 | 0.15106 | 0.27466 | -0.20599 | -0.21057 | -0.17395 | -0.17853 | -0.086975 | -0.14191 | 0.10986 | 0.07782 | -0.10071 | -0.045776 | -0.013733 | 0.041199 | 0.3067 | 121.7011 | 0.1648 | 121.7148 | 121.4264 | 121.463 | 121.3943 | 121.376 | -121.55 | -121.6049 | 121.669 | 121.6278 | 61.4822 | 61.615
528.6406 | 121.7606 | -61.5646 | 60.022 | -0.01976 | 0.0033282 | 0.056845 | 0.05686 | -0.00069646 | -0.0066394 | -0.0045182 | -0.0023192 | 0.0048001 | 0.066988 | 0.06248 | -0.0096685 | 0.018624 | -0.0072569 | -0.11902 | 59.9167 | -61.6241 | 60.0128 | -61.4273 | -61.8851 | -61.8713 | -0.073242 | 59.8938 | -61.6745 | 59.9945 | -61.5692 | -61.7065 | -61.7477 | -0.05951 | -0.10529 | -0.009156 | 0.13733 | -0.3067 | -0.32044 | -0.24719 | -0.26093 | -0.10986 | -0.12817 | -0.027466 | -0.004578 | -0.18311 | -0.14191 | -0.073242 | -0.032043 | 0.19684 | 121.637 | 0.10529 | 121.669 | 121.5408 | 121.5683 | 121.4813 | 121.4584 | -121.6461 | -121.6965 | 121.5775 | 121.5591 | 61.4456 | 61.4914
530.4062 | 121.788 | -61.528 | 60.0723 | -0.0045011 | 0.001833 | 0.058981 | 0.057074 | -0.0019781 | -0.008562 | -0.0021682 | -0.0023192 | 0.0043729 | 0.064424 | 0.062267 | -0.0073187 | 0.020119 | -0.0038389 | -0.004578 | 59.9991 | -61.5417 | 60.1135 | -61.3083 | -61.7523 | -61.7661 | 0.045776 | 59.9487 | -61.5646 | 60.0723 | -61.4456 | -61.6241 | -61.6562 | -0.013733 | -0.073243 | 0.041198 | 0.21973 | -0.23804 | -0.2243 | -0.2243 | -0.21057 | -0.036621 | -0.1236 | 0 | 0.082397 | -0.12817 | -0.096131 | -0.091553 | -0.05951 | 0.23346 | 121.6553 | 0.11902 | 121.637 | 121.5408 | 121.5134 | 121.5271 | 121.4767 | -121.6141 | -121.637 | 121.6415 | 121.6003 | 61.5234 | 61.5738
532.1562 | 121.7422 | -61.528 | 60.0998 | 0.0031279 | -0.00051702 | 0.057059 | 0.052588 | -0.0024055 | -0.0070666 | -0.000673 | -0.0084228 | 0.0035183 | 0.063784 | 0.05714 | -0.0083869 | 0.020119 | 0.0012881 | -0.022888 | 59.9991 | -61.5372 | 60.0861 | -61.3083 | -61.7523 | -61.7661 | 0.018311 | 59.9762 | -61.5555 | 60.0403 | -61.4685 | -61.6333 | -61.6837 | -0.009155 | -0.10071 | -0.013732 | 0.21973 | -0.23804 | -0.2243 | -0.22888 | -0.21515 | -0.027466 | -0.1236 | -0.059509 | 0.059509 | -0.15564 | -0.10529 | -0.12817 | -0.07782 | 0.22888 | 121.6232 | 0.086975 | 121.5958 | 121.5363 | 121.5317 | 121.5271 | 121.5042 | -121.637 | -121.6553 | 121.6141 | 121.5683 | 61.5051 | 61.5463
533.8438 | 121.8246 | -61.4914 | 60.0586 | -0.012131 | -0.00051702 | 0.056631 | 0.053656 | -0.0028327 | -0.006853 | -0.002382 | -0.0023192 | 0.0022367 | 0.065279 | 0.056072 | -0.0094549 | 0.02311 | -0.00063445 | 0.036621 | 59.9396 | -61.5372 | 60.1822 | -61.2167 | -61.647 | -61.6699 | 0.13275 | 59.8984 | -61.5509 | 60.141 | -61.377 | -61.5097 | -61.5921 | -0.045776 | -0.11902 | 0.1236 | 0.27466 | -0.17853 | -0.15564 | -0.13275 | -0.10986 | -0.059509 | -0.16022 | 0.082397 | 0.11444 | -0.10071 | -0.018311 | -0.041199 | 0.041198 | 0.32043 | 121.7194 | 0.17395 | 121.6919 | 121.4767 | 121.4493 | 121.431 | 121.3898 | -121.5958 | -121.6095 | 121.6736 | 121.6324 | 61.528 | 61.6241
535.5938 | 121.8201 | -61.5417 | 59.9991 | -0.0045011 | 0.0026874 | 0.056204 | 0.054297 | -0.00048286 | -0.0070666 | -0.0025956 | -0.0084228 | -0.00011332 | 0.066133 | 0.053081 | -0.01031 | 0.021614 | -0.00084805 | -0.09613 | 59.9075 | -61.5601 | 60.0815 | -61.3129 | -61.7706 | -61.7569 | 0 | 59.8801 | -61.5921 | 60.0769 | -61.4731 | -61.5967 | -61.6608 | -0.018311 | -0.091552 | 0.082398 | 0.22888 | -0.21515 | -0.22888 | -0.19684 | -0.21057 | -0.050354 | -0.11902 | 0.07782 | 0.068665 | -0.11902 | -0.054932 | -0.068665 | -0.004578 | 0.24719 | 121.6415 | 0.11902 | 121.669 | 121.4676 | 121.4722 | 121.4493 | 121.4218 | -121.5591 | -121.5912 | 121.6232 | 121.6187 | 61.4456 | 61.5417
537.3438 | 121.7422 | -61.5051 | 60.1227 | -0.012131 | 0.00055118 | 0.057272 | 0.054083 | -5.5462e-05 | -0.0072802 | -0.0008866 | -0.005371 | 0.0030911 | 0.063997 | 0.052013 | -0.0092413 | 0.021187 | -0.0055479 | -0.036621 | 59.9854 | -61.5601 | 60.0998 | -61.3083 | -61.7523 | -61.7661 | 0.022888 | 60.0037 | -61.5692 | 60.0449 | -61.4777 | -61.6196 | -61.6791 | -0.054932 | -0.13733 | -0.022889 | 0.19684 | -0.26093 | -0.24719 | -0.20599 | -0.19226 | -0.064087 | -0.11902 | -0.07782 | 0.027466 | -0.17395 | -0.11444 | -0.10986 | -0.050354 | 0.25177 | 121.6599 | 0.091553 | 121.6141 | 121.5454 | 121.5729 | 121.4905 | 121.5088 | -121.6827 | -121.6919 | 121.6049 | 121.55 | 61.4685 | 61.528
539.0312 | 121.8979 | -61.4594 | 60.0311 | -0.0045011 | -0.00073062 | 0.055563 | 0.053228 | -0.0045417 | -0.0074938 | -0.0036636 | -0.0084228 | 0.00095488 | 0.066133 | 0.063976 | -0.012232 | 0.018624 | -0.0061887 | -0.009155 | 59.9075 | -61.5326 | 60.173 | -61.1984 | -61.6516 | -61.6653 | 0.16022 | 59.8938 | -61.5555 | 60.1776 | -61.3403 | -61.4914 | -61.5692 | -0.073242 | -0.1236 | 0.14191 | 0.26093 | -0.20599 | -0.19226 | -0.13275 | -0.11902 | -0.09613 | -0.13733 | 0.14648 | 0.11902 | -0.10986 | -0.032043 | -0.013733 | 0.064087 | 0.33417 | 121.7056 | 0.21515 | 121.7331 | 121.4401 | 121.4493 | 121.3669 | 121.3531 | -121.5637 | -121.5866 | 121.6324 | 121.637 | 61.4502 | 61.6196
540.7969 | 121.8201 | -61.528 | 60.022 | -0.01976 | 0.0022602 | 0.058768 | 0.053228 | -0.0015509 | -0.0040758 | 0.0003952 | -0.0084228 | 0.0013821 | 0.066347 | 0.053935 | -0.011164 | 0.019265 | -0.0010617 | -0.064087 | 59.8846 | -61.5829 | 60.0998 | -61.322 | -61.7523 | -61.7523 | 0.018311 | 59.8663 | -61.6241 | 60.0815 | -61.4456 | -61.5738 | -61.6333 | -0.054932 | -0.13733 | 0.077819 | 0.20599 | -0.2243 | -0.2243 | -0.16937 | -0.16937 | -0.096131 | -0.15564 | 0.059509 | 0.082397 | -0.10529 | -0.045777 | -0.009155 | 0.050354 | 0.26093 | 121.6827 | 0.17853 | 121.7056 | 121.4676 | 121.4905 | 121.4127 | 121.3943 | -121.6049 | -121.6461 | 121.6278 | 121.6095 | 61.4639 | 61.5463
542.5469 | 121.756 | -61.5601 | 60.022 | -0.0045011 | 0.0020466 | 0.056631 | 0.057928 | -0.00069646 | -0.0077074 | -0.002382 | -0.005371 | 0.0039457 | 0.065279 | 0.057567 | -0.0088141 | 0.019265 | -0.0059751 | -0.009155 | 59.9396 | -61.5692 | 60.0998 | -61.322 | -61.7844 | -61.8073 | 0.032043 | 59.9075 | -61.5967 | 60.0357 | -61.5234 | -61.6791 | -61.6974 | -0.009155 | -0.082398 | 0.077819 | 0.23804 | -0.24719 | -0.2243 | -0.23804 | -0.21515 | -0.036621 | -0.11444 | 0.013733 | 0.036622 | -0.13733 | -0.11902 | -0.10071 | -0.082397 | 0.24719 | 121.669 | 0.073243 | 121.6324 | 121.5088 | 121.5042 | 121.4996 | 121.4676 | -121.5912 | -121.6187 | 121.6599 | 121.5958 | 61.5509 | 61.5921
544.2969 | 121.8018 | -61.5326 | 60.0494 | -0.012131 | 0.0026874 | 0.05834 | 0.057501 | 0.0029351 | -0.0066394 | -0.0019546 | -0.0023192 | 0.0037321 | 0.06592 | 0.056499 | -0.0077459 | 0.020974 | -0.0049069 | -0.009155 | 59.9396 | -61.5692 | 60.1135 | -61.2991 | -61.7661 | -61.7615 | 0.082397 | 59.9258 | -61.5921 | 60.0906 | -61.4639 | -61.6104 | -61.6745 | -0.036621 | -0.10986 | 0.064087 | 0.23346 | -0.22888 | -0.23346 | -0.19226 | -0.19684 | -0.059509 | -0.1236 | 0.041199 | 0.068665 | -0.14191 | -0.07782 | -0.082398 | -0.018311 | 0.27008 | 121.6827 | 0.12817 | 121.6827 | 121.5088 | 121.5179 | 121.4722 | 121.4584 | -121.6187 | -121.6415 | 121.6461 | 121.6232 | 61.5234 | 61.615
546.0469 | 121.7377 | -61.5738 | 60.0403 | -0.012131 | 0.0048236 | 0.057059 | 0.056433 | 0.0029351 | -0.0062122 | -0.0028092 | -0.0023192 | 0.0045865 | 0.066561 | 0.057353 | -0.0068915 | 0.022255 | -0.0017027 | -0.045776 | 59.9396 | -61.5738 | 60.054 | -61.3632 | -61.8301 | -61.8164 | -0.018311 | 59.8984 | -61.647 | 60.0174 | -61.5417 | -61.702 | -61.734 | 0 | -0.10071 | 0.013733 | 0.21057 | -0.24261 | -0.25635 | -0.24261 | -0.25635 | -0.073242 | -0.14191 | -0.022888 | 0.032044 | -0.16022 | -0.12817 | -0.086975 | -0.054931 | 0.21057 | 121.6278 | 0.10529 | 121.6644 | 121.5134 | 121.5454 | 121.5134 | 121.4722 | -121.6141 | -121.6873 | 121.6278 | 121.5912 | 61.528 | 61.5555
547.7344 | 121.7926 | -61.5601 | 60.0494 | -0.0045011 | 0.00055118 | 0.057059 | 0.05451 | 0.0052851 | -0.0070666 | 0.0001816 | -0.0084228 | 0.0028775 | 0.066347 | 0.05949 | -0.0066779 | 0.023323 | -0.0010617 | -0.004578 | 59.9808 | -61.5555 | 60.1227 | -61.2946 | -61.7477 | -61.7661 | 0.068665 | 59.9213 | -61.5875 | 60.0861 | -61.4548 | -61.6104 | -61.6653 | 0.004578 | -0.068664 | 0.073243 | 0.2655 | -0.20599 | -0.18768 | -0.21057 | -0.19226 | -0.027465 | -0.12817 | 0.036622 | 0.10529 | -0.10528 | -0.050354 | -0.07782 | -0.022889 | 0.26093 | 121.6782 | 0.13275 | 121.6736 | 121.5363 | 121.5088 | 121.5408 | 121.4813 | -121.6049 | -121.637 | 121.6827 | 121.6461 | 61.5555 | 61.6287
549.4844 | 121.7468 | -61.5326 | 60.1044 | 0.010757 | 0.00055118 | 0.056204 | 0.052588 | 0.0010125 | -0.0066394 | -0.0028092 | -0.005371 | 0.0024503 | 0.066988 | 0.050304 | -0.0098823 | 0.022896 | -0.0017027 | -0.045776 | 59.9808 | -61.5555 | 60.0769 | -61.3129 | -61.7432 | -61.7661 | 0.018311 | 59.9533 | -61.5509 | 60.0357 | -61.4639 | -61.6013 | -61.6745 | -0.022888 | -0.1236 | -0.027466 | 0.21973 | -0.23346 | -0.21057 | -0.21057 | -0.18768 | -0.01831 | -0.15106 | -0.068664 | 0.068665 | -0.14191 | -0.068664 | -0.1236 | -0.050354 | 0.24262 | 121.6324 | 0.086975 | 121.5866 | 121.5363 | 121.5042 | 121.5134 | 121.4859 | -121.6599 | -121.6553 | 121.6095 | 121.5683 | 61.4868 | 61.5509
551.25 | 121.8796 | -61.4777 | 60.0494 | -0.012131 | -0.0017986 | 0.0577 | 0.054297 | 0.0010125 | -0.0083484 | -0.0032364 | -0.005371 | -0.0016085 | 0.066561 | 0.053722 | -0.0096685 | 0.022896 | -0.0027707 | 0 | 59.9258 | -61.528 | 60.1959 | -61.1755 | -61.6379 | -61.6608 | 0.15106 | 59.8709 | -61.5601 | 60.1913 | -61.3358 | -61.4685 | -61.5555 | -0.050354 | -0.1236 | 0.14648 | 0.30212 | -0.18311 | -0.16022 | -0.13275 | -0.10986 | -0.082398 | -0.17853 | 0.14191 | 0.14191 | -0.07782 | 0.009155 | 0.004578 | 0.091553 | 0.35248 | 121.7239 | 0.22431 | 121.7514 | 121.4539 | 121.431 | 121.4035 | 121.3486 | -121.5775 | -121.6095 | 121.6736 | 121.669 | 61.4777 | 61.6287
552.9531 | 121.8292 | -61.5326 | 60.0082 | 0.0031279 | 0.0016192 | 0.057913 | 0.05152 | 0.0014397 | -0.0079212 | -0.0043046 | -0.005371 | 0.0020231 | 0.065493 | 0.050304 | -0.010523 | 0.022042 | -0.0027707 | -0.082397 | 59.8892 | -61.5738 | 60.0906 | -61.2946 | -61.7615 | -61.7569 | 0.013733 | 59.8389 | -61.6104 | 60.0449 | -61.4685 | -61.5692 | -61.6608 | -0.041199 | -0.11902 | 0.082397 | 0.23804 | -0.2243 | -0.22888 | -0.18311 | -0.18768 | -0.07782 | -0.16937 | 0.036621 | 0.064087 | -0.12817 | -0.036621 | -0.050354 | 0.041199 | 0.27924 | 121.6644 | 0.14191 | 121.6553 | 121.463 | 121.4493 | 121.4218 | 121.3715 | -121.582 | -121.6187 | 121.6232 | 121.5775 | 61.4502 | 61.5463
554.7031 | 121.843 | -61.4777 | 60.0952 | -0.0045011 | 0.00012398 | 0.056631 | 0.055578 | 0.00058534 | -0.0077074 | -0.000673 | -0.005371 | 0.00074128 | 0.066988 | 0.053295 | -0.0098823 | 0.019478 | -0.0014891 | 0.013733 | 59.903 | -61.528 | 60.2051 | -61.2076 | -61.6653 | -61.6653 | 0.13275 | 59.9075 | -61.5555 | 60.1364 | -61.3678 | -61.5051 | -61.5875 | -0.050354 | -0.19226 | 0.10986 | 0.27008 | -0.18768 | -0.18768 | -0.13733 | -0.13733 | -0.07782 | -0.18768 | 0.041199 | 0.10986 | -0.10986 | -0.027466 | -0.032043 | 0.050354 | 0.32043 | 121.7331 | 0.18768 | 121.6919 | 121.431 | 121.463 | 121.3806 | 121.3852 | -121.6232 | -121.6507 | 121.6827 | 121.6141 | 61.4914 | 61.6104
556.4688 | 121.8475 | -61.5326 | 59.9991 | -0.0045011 | 0.00012398 | 0.059622 | 0.053869 | 0.0022943 | -0.0079212 | -0.0019546 | -0.011475 | -0.0013949 | 0.066133 | 0.05479 | -0.011805 | 0.021614 | -0.0012753 | -0.082397 | 59.9121 | -61.5784 | 60.0952 | -61.2946 | -61.7523 | -61.7523 | 0.013733 | 59.8846 | -61.6058 | 60.0861 | -61.441 | -61.5692 | -61.6425 | -0.045776 | -0.086975 | 0.096131 | 0.23804 | -0.21973 | -0.21973 | -0.17395 | -0.17395 | -0.073242 | -0.11444 | 0.086976 | 0.091553 | -0.10986 | -0.036621 | -0.036621 | 0.036621 | 0.28381 | 121.6736 | 0.16479 | 121.6919 | 121.4905 | 121.4905 | 121.4447 | 121.4172 | -121.5775 | -121.6049 | 121.6278 | 121.6187 | 61.4502 | 61.5463
558.2188 | 121.7834 | -61.5372 | 60.0815 | -0.0045011 | -0.00030342 | 0.056845 | 0.056006 | 0.0029351 | -0.006853 | -0.0025956 | -0.005371 | 0.0043729 | 0.065279 | 0.062694 | -0.0096685 | 0.021828 | -0.0010617 | -0.018311 | 59.9899 | -61.5463 | 60.0815 | -61.3495 | -61.7661 | -61.7661 | 0.022888 | 59.967 | -61.5646 | 60.0723 | -61.4685 | -61.6104 | -61.6516 | -0.009156 | -0.091553 | 0 | 0.18768 | -0.22888 | -0.22888 | -0.21973 | -0.21973 | -0.027466 | -0.11444 | -0.009155 | 0.068664 | -0.11444 | -0.073243 | -0.086975 | -0.045777 | 0.19684 | 121.6278 | 0.09613 | 121.637 | 121.5363 | 121.5317 | 121.5271 | 121.5042 | -121.6278 | -121.6461 | 121.6187 | 121.6095 | 61.5189 | 61.5601
559.9062 | 121.756 | -61.5601 | 60.0403 | -0.012131 | 0.0043964 | 0.05834 | 0.056006 | -0.00026906 | -0.0059986 | -0.0038772 | -0.0023192 | 0.0018095 | 0.064852 | 0.05949 | -0.0079597 | 0.019905 | -0.0049069 | -0.045776 | 59.967 | -61.5875 | 60.054 | -61.3632 | -61.8256 | -61.8164 | -0.027466 | 59.8984 | -61.6104 | 60.0174 | -61.5555 | -61.6928 | -61.7294 | -0.027465 | -0.073242 | 0.013733 | 0.19684 | -0.25635 | -0.2655 | -0.22888 | -0.23804 | -0.050354 | -0.14191 | -0.022888 | 0.004578 | -0.16937 | -0.13275 | -0.11902 | -0.082397 | 0.2243 | 121.6415 | 0.054932 | 121.6278 | 121.5546 | 121.5088 | 121.5271 | 121.4584 | -121.6278 | -121.6507 | 121.6141 | 121.5775 | 61.5143 | 61.5326
561.6562 | 121.8704 | -61.496 | 60.054 | -0.012131 | -0.00051702 | 0.056418 | 0.053015 | -0.0028327 | -0.0074938 | -0.0030228 | -0.005371 | 0.0011685 | 0.065279 | 0.054363 | -0.0071051 | 0.021614 | -0.0014891 | 0.004578 | 59.8984 | -61.5326 | 60.2234 | -61.1481 | -61.615 | -61.6287 | 0.16479 | 59.8801 | -61.5509 | 60.173 | -61.3403 | -61.4639 | -61.5555 | -0.036621 | -0.15564 | 0.16937 | 0.3479 | -0.13275 | -0.11902 | -0.09613 | -0.082397 | -0.054931 | -0.17395 | 0.11902 | 0.15564 | -0.059509 | 0.032044 | -0.004578 | 0.086975 | 0.38452 | 121.756 | 0.21057 | 121.7239 | 121.431 | 121.431 | 121.3943 | 121.376 | -121.5866 | -121.6049 | 121.7194 | 121.669 | 61.5006 | 61.6608
563.3438 | 121.875 | -61.5601 | 59.9579 | -0.0045011 | 0.0033282 | 0.059195 | 0.055365 | -0.00026906 | -0.0070666 | -0.0032364 | -0.005371 | 0.0018095 | 0.065493 | 0.055004 | -0.0075323 | 0.022042 | -0.0044797 | -0.073242 | 59.8846 | -61.6058 | 60.0952 | -61.2946 | -61.7615 | -61.7798 | 0.032043 | 59.8389 | -61.6013 | 60.0952 | -61.4548 | -61.6013 | -61.6196 | -0.045776 | -0.073242 | 0.13733 | 0.2655 | -0.21973 | -0.20142 | -0.17395 | -0.15564 | -0.041198 | -0.11902 | 0.13733 | 0.10529 | -0.059509 | -0.041198 | -0.018311 | 0 | 0.31128 | 121.7011 | 0.14648 | 121.6965 | 121.4905 | 121.4401 | 121.4447 | 121.3989 | -121.5637 | -121.5591 | 121.6553 | 121.6553 | 61.4868 | 61.5921
565.0938 | 121.7377 | -61.5097 | 60.0998 | -0.0045011 | -0.0013714 | 0.055563 | 0.056006 | 0.0033623 | -0.0087756 | -0.0013138 | -0.0023192 | 0.0018095 | 0.067415 | 0.054363 | -0.0094549 | 0.020546 | -0.0040525 | -0.027466 | 59.9808 | -61.5555 | 60.0861 | -61.3129 | -61.7615 | -61.7569 | 0.009155 | 59.9579 | -61.5646 | 60.054 | -61.4777 | -61.6058 | -61.6745 | -0.045776 | -0.11902 | -0.013732 | 0.19684 | -0.24719 | -0.25177 | -0.20142 | -0.20599 | -0.054931 | -0.14191 | -0.045776 | 0.032044 | -0.1648 | -0.09613 | -0.10986 | -0.041199 | 0.24262 | 121.6415 | 0.086975 | 121.6187 | 121.5363 | 121.5225 | 121.4905 | 121.4676 | -121.6553 | -121.6644 | 121.5958 | 121.5637 | 61.4822 | 61.5189
566.8594 | 121.7972 | -61.5646 | 60.054 | -0.012131 | 0.0026874 | 0.056631 | 0.056433 | -0.00026906 | -0.0079212 | -0.000673 | -0.0084228 | 0.0028775 | 0.065706 | 0.063121 | -0.0056097 | 0.019905 | -0.0010617 | -0.004578 | 59.9945 | -61.5463 | 60.1135 | -61.322 | -61.7432 | -61.7706 | 0.041199 | 59.9396 | -61.5829 | 60.0906 | -61.4685 | -61.6058 | -61.647 | 0.01831 | -0.059509 | 0.059509 | 0.24262 | -0.20599 | -0.17853 | -0.2243 | -0.19684 | -0.018311 | -0.11444 | 0.036621 | 0.09613 | -0.082398 | -0.041199 | -0.064087 | -0.022888 | 0.22431 | 121.6599 | 0.11444 | 121.6736 | 121.5408 | 121.5225 | 121.5591 | 121.5042 | -121.6003 | -121.637 | 121.6782 | 121.6553 | 61.5601 | 61.6058
568.6094 | 121.8658 | -61.528 | 59.9487 | -0.01976 | 0.002901 | 0.059409 | 0.055578 | -0.00026906 | -0.0081348 | -0.0043046 | -0.0023192 | 0.0024503 | 0.064852 | 0.059703 | -0.0077459 | 0.022042 | -0.0017027 | -0.068665 | 59.8389 | -61.6104 | 60.1318 | -61.2762 | -61.7477 | -61.7386 | 0.059509 | 59.8114 | -61.6333 | 60.1044 | -61.4319 | -61.5921 | -61.6333 | -0.082398 | -0.10986 | 0.18311 | 0.25177 | -0.21057 | -0.21973 | -0.12817 | -0.13733 | -0.10529 | -0.13733 | 0.15564 | 0.09613 | -0.10529 | -0.064087 | 0 | 0.041199 | 0.33417 | 121.7422 | 0.20142 | 121.7377 | 121.4493 | 121.4447 | 121.3669 | 121.3394 | -121.5591 | -121.582 | 121.6599 | 121.6324 | 61.4594 | 61.5875
570.3594 | 121.8613 | -61.5326 | 59.9716 | -0.0045011 | 0.0067462 | 0.058981 | 0.055151 | 0.0014397 | -0.0055712 | -0.0045182 | -0.005371 | 0.0013821 | 0.066774 | 0.055004 | -0.0088141 | 0.023323 | -0.0023435 | -0.09613 | 59.9075 | -61.6058 | 60.0769 | -61.3266 | -61.7981 | -61.7706 | 0.018311 | 59.8343 | -61.6196 | 60.1044 | -61.4456 | -61.5829 | -61.6287 | -0.073242 | -0.064087 | 0.10529 | 0.20599 | -0.23804 | -0.2655 | -0.16479 | -0.19226 | -0.086975 | -0.13733 | 0.13275 | 0.086975 | -0.09613 | -0.050354 | -0.009155 | 0.036621 | 0.27924 | 121.6827 | 0.17395 | 121.7239 | 121.5134 | 121.4539 | 121.4401 | 121.3669 | -121.5775 | -121.5912 | 121.6095 | 121.637 | 61.4365 | 61.5509
572.0469 | 121.843 | -61.5646 | 59.9945 | -0.012131 | 0.0016192 | 0.058768 | 0.055151 | -0.0017645 | -0.0042896 | -0.0004592 | -0.0084228 | 0.0015957 | 0.064211 | 0.060558 | -0.0098823 | 0.02076 | -0.0027707 | -0.086975 | 59.8709 | -61.5738 | 60.1089 | -61.2717 | -61.7752 | -61.7569 | 0.036621 | 59.8526 | -61.615 | 60.0769 | -61.4685 | -61.5967 | -61.6653 | -0.009156 | -0.1236 | 0.11444 | 0.29297 | -0.19226 | -0.21057 | -0.18311 | -0.20142 | -0.050354 | -0.14191 | 0.082397 | 0.09613 | -0.10071 | -0.032044 | -0.050354 | 0.01831 | 0.30212 | 121.6827 | 0.14648 | 121.6919 | 121.4447 | 121.4676 | 121.4355 | 121.4172 | -121.5683 | -121.6095 | 121.6736 | 121.6415 | 61.4777 | 61.6013
573.7969 | 121.8155 | -61.5921 | 59.9716 | -0.01976 | 0.0043964 | 0.056418 | 0.056219 | 0.0018671 | -0.0079212 | -0.0025956 | -0.005371 | 0.0033047 | 0.065065 | 0.059062 | -0.0088141 | 0.021614 | -0.00063445 | -0.11444 | 59.9258 | -61.6287 | 60.022 | -61.3953 | -61.8668 | -61.8484 | -0.036621 | 59.8434 | -61.6425 | 60.0494 | -61.5189 | -61.6562 | -61.6928 | -0.036621 | -0.045777 | 0.050354 | 0.19684 | -0.25635 | -0.27466 | -0.21973 | -0.23804 | -0.050354 | -0.12817 | 0.077819 | 0.073242 | -0.10071 | -0.064087 | -0.050354 | -0.013733 | 0.23346 | 121.6507 | 0.1236 | 121.6919 | 121.5546 | 121.4859 | 121.5179 | 121.4355 | -121.6003 | -121.6141 | 121.6141 | 121.6415 | 61.4777 | 61.5555
575.5625 | 121.7743 | -61.5692 | 60.0403 | -0.012131 | 0.0026874 | 0.059195 | 0.057501 | -0.00091006 | -0.0059986 | -0.0025956 | -0.005371 | 0.0018095 | 0.066133 | 0.05949 | -0.0064643 | 0.021614 | -0.0053343 | 0.004578 | 59.9945 | -61.5829 | 60.1089 | -61.29 | -61.7386 | -61.7477 | 0.059509 | 59.9396 | -61.5875 | 60.0906 | -61.4594 | -61.6196 | -61.647 | -0.013733 | -0.045776 | 0.068665 | 0.27924 | -0.17853 | -0.16937 | -0.1648 | -0.15564 | -0.01831 | -0.10071 | 0.050354 | 0.10986 | -0.07782 | -0.050354 | -0.05951 | -0.032044 | 0.29297 | 121.6919 | 0.12817 | 121.6782 | 121.5775 | 121.5271 | 121.5637 | 121.5088 | -121.6232 | -121.6278 | 121.6782 | 121.6599 | 61.5738 | 61.6287
577.3125 | 121.8567 | -61.4822 | 60.0311 | -0.0045011 | 0.001192 | 0.057486 | 0.053442 | -0.0073187 | -0.0062122 | -0.000673 | -0.0023192 | 0.0011685 | 0.064211 | 0.053295 | -0.0096685 | 0.02076 | -0.0027707 | 0.013733 | 59.9167 | -61.5555 | 60.2234 | -61.1664 | -61.6241 | -61.6425 | 0.15564 | 59.8984 | -61.528 | 60.1547 | -61.3541 | -61.4777 | -61.5555 | -0.073242 | -0.11444 | 0.19226 | 0.31586 | -0.16022 | -0.14191 | -0.086975 | -0.068665 | -0.045776 | -0.13275 | 0.1236 | 0.12817 | -0.073242 | 0.004578 | -0.027466 | 0.050354 | 0.3891 | 121.7789 | 0.17395 | 121.6827 | 121.4722 | 121.4264 | 121.3989 | 121.3806 | -121.5866 | -121.5591 | 121.7056 | 121.637 | 61.496 | 61.6379
579 | 121.8246 | -61.5738 | 59.967 | -0.0045011 | 0.0037556 | 0.060904 | 0.05686 | 0.0052851 | -0.003435 | 0.0014634 | -0.0023192 | 0.0041593 | 0.066774 | 0.061412 | -0.0081733 | 0.022255 | -0.0019163 | -0.10529 | 59.935 | -61.6058 | 60.022 | -61.3861 | -61.8622 | -61.8484 | -0.045776 | 59.8526 | -61.6425 | 60.0357 | -61.5189 | -61.6653 | -61.6928 | -0.032043 | -0.032043 | 0.054932 | 0.18768 | -0.27466 | -0.28839 | -0.24262 | -0.25635 | -0.068664 | -0.11444 | 0.068665 | 0.054932 | -0.11902 | -0.091552 | -0.050354 | -0.022888 | 0.21973 | 121.6278 | 0.1236 | 121.6782 | 121.5408 | 121.4951 | 121.5088 | 121.4264 | -121.5729 | -121.6095 | 121.5958 | 121.6095 | 61.4685 | 61.528
580.7812 | 121.7834 | -61.5372 | 60.0403 | -0.01976 | 0.0039692 | 0.059195 | 0.055365 | -0.0013373 | -0.0072802 | -0.00345 | -0.0023192 | 0.0024503 | 0.066133 | 0.060558 | -0.0075323 | 0.020546 | -0.0029843 | 0 | 59.9854 | -61.5601 | 60.1227 | -61.2946 | -61.734 | -61.7706 | 0.059509 | 59.9533 | -61.5784 | 60.0861 | -61.4639 | -61.6241 | -61.6516 | -0.022889 | -0.054931 | 0.082398 | 0.24261 | -0.23346 | -0.19684 | -0.21057 | -0.17395 | -0.041199 | -0.086975 | 0.045777 | 0.073242 | -0.11444 | -0.086976 | -0.073242 | -0.045777 | 0.2655 | 121.6827 | 0.11444 | 121.6644 | 121.5454 | 121.5317 | 121.5225 | 121.4905 | -121.6003 | -121.6187 | 121.6599 | 121.6232 | 61.5372 | 61.5967
582.4844 | 121.8384 | -61.5417 | 59.9899 | -0.012131 | 0.0020466 | 0.058127 | 0.055151 | -0.00069646 | -0.0059986 | -0.0021682 | -0.005371 | -0.00075412 | 0.066988 | 0.06184 | -0.01095 | 0.021401 | 0.0023563 | -0.07782 | 59.8801 | -61.5967 | 60.1089 | -61.2762 | -61.7615 | -61.7523 | 0.059509 | 59.8343 | -61.5967 | 60.0723 | -61.4685 | -61.5829 | -61.6379 | -0.054932 | -0.10986 | 0.11902 | 0.2655 | -0.21057 | -0.21973 | -0.15564 | -0.16479 | -0.054932 | -0.15564 | 0.082398 | 0.073242 | -0.09613 | -0.041199 | -0.041198 | 0.013733 | 0.32043 | 121.7056 | 0.12817 | 121.669 | 121.4767 | 121.431 | 121.4218 | 121.376 | -121.5866 | -121.5866 | 121.6507 | 121.6141 | 61.4639 | 61.6013
584.25 | 121.8796 | -61.5555 | 59.9625 | -0.01976 | 0.0024738 | 0.059409 | 0.054937 | -0.0049689 | -0.0083484 | 0.0025314 | -0.005371 | 0.00074128 | 0.067202 | 0.054576 | -0.0094549 | 0.019478 | 0.0015017 | -0.054932 | 59.8526 | -61.6058 | 60.1044 | -61.2808 | -61.7661 | -61.7523 | 0.054932 | 59.8251 | -61.6104 | 60.1135 | -61.4319 | -61.5784 | -61.6241 | -0.050354 | -0.10986 | 0.14191 | 0.27466 | -0.19684 | -0.21057 | -0.14648 | -0.16022 | -0.054932 | -0.13733 | 0.15106 | 0.1236 | -0.068665 | -0.022888 | -0.013733 | 0.032044 | 0.32501 | 121.7102 | 0.17853 | 121.7239 | 121.4584 | 121.4355 | 121.4081 | 121.3806 | -121.5683 | -121.5729 | 121.6599 | 121.669 | 61.5005 | 61.6104
586.0156 | 121.8018 | -61.5509 | 60.0769 | -0.012131 | 0.0026874 | 0.057486 | 0.057074 | -0.0026191 | -0.0081348 | -0.0019546 | -0.005371 | 0.0030911 | 0.066347 | 0.05479 | -0.0079597 | 0.021828 | -0.00042085 | 0.004578 | 59.9854 | -61.5738 | 60.1227 | -61.2991 | -61.7477 | -61.7752 | 0.073242 | 59.9121 | -61.5875 | 60.0677 | -61.4639 | -61.6013 | -61.647 | -0.022889 | -0.091552 | 0.045777 | 0.25177 | -0.22431 | -0.19684 | -0.20142 | -0.17395 | -0.036621 | -0.16479 | -0.009155 | 0.086975 | -0.096131 | -0.050354 | -0.05951 | -0.013733 | 0.27466 | 121.6965 | 0.1236 | 121.6553 | 121.5591 | 121.4996 | 121.5363 | 121.463 | -121.6507 | -121.6644 | 121.6736 | 121.6187 | 61.5555 | 61.6241
587.7656 | 121.8796 | -61.5692 | 59.9579 | -0.01976 | 0.0031146 | 0.058127 | 0.056433 | 0.0031487 | -0.006853 | -0.001741 | -0.0084228 | -0.00032692 | 0.066561 | 0.061626 | -0.0090277 | 0.02076 | -0.0046933 | -0.068665 | 59.8801 | -61.5784 | 60.1181 | -61.2808 | -61.7523 | -61.7523 | 0.054932 | 59.8114 | -61.615 | 60.0998 | -61.4548 | -61.5875 | -61.6379 | -0.009155 | -0.07782 | 0.16022 | 0.28839 | -0.1831 | -0.1831 | -0.17395 | -0.17395 | -0.045776 | -0.14649 | 0.14191 | 0.11444 | -0.068664 | -0.01831 | -0.022888 | 0.027466 | 0.29755 | 121.6965 | 0.16022 | 121.7148 | 121.4584 | 121.4264 | 121.4493 | 121.3806 | -121.5363 | -121.5729 | 121.6873 | 121.669 | 61.5005 | 61.6241
589.4688 | 121.7926 | -61.5875 | 59.9854 | -0.012131 | 0.0048236 | 0.056845 | 0.055365 | 0.0025079 | -0.0062122 | -0.002382 | -0.005371 | 0.0035183 | 0.067415 | 0.058849 | -0.0088141 | 0.021614 | -0.0053343 | -0.11902 | 59.935 | -61.6333 | 60.0311 | -61.3998 | -61.8622 | -61.8576 | -0.064087 | 59.8846 | -61.6425 | 60.0174 | -61.528 | -61.6837 | -61.6928 | -0.045777 | -0.050354 | 0.045776 | 0.18768 | -0.27008 | -0.27466 | -0.2243 | -0.22888 | -0.054932 | -0.10071 | 0.032043 | 0.059509 | -0.10529 | -0.096131 | -0.050354 | -0.041199 | 0.23346 | 121.6644 | 0.11444 | 121.6599 | 121.5683 | 121.5271 | 121.5225 | 121.4722 | -121.6187 | -121.6278 | 121.6187 | 121.6049 | 61.4685 | 61.5234
591.2188 | 121.7972 | -61.5646 | 60.0494 | -0.0045011 | 0.002901 | 0.055777 | 0.057287 | -5.5462e-05 | -0.006853 | 0.0001816 | -0.0023192 | 0.0033047 | 0.06592 | 0.061626 | -0.0053961 | 0.022042 | 0.0010745 | -0.018311 | 59.9579 | -61.5829 | 60.1044 | -61.2808 | -61.7615 | -61.7706 | 0.07782 | 59.9304 | -61.5738 | 60.0769 | -61.4685 | -61.6287 | -61.647 | -0.018311 | -0.091552 | 0.054932 | 0.28381 | -0.20599 | -0.19684 | -0.18768 | -0.17853 | -0.009156 | -0.11902 | 0.027466 | 0.09613 | -0.082398 | -0.064087 | -0.073242 | -0.054931 | 0.30212 | 121.6873 | 0.10529 | 121.6507 | 121.5408 | 121.5042 | 121.5225 | 121.4951 | -121.6324 | -121.6232 | 121.669 | 121.6415 | 61.5463 | 61.6425
592.9062 | 121.7972 | -61.528 | 60.0494 | -0.0045011 | 0.0031146 | 0.05834 | 0.055365 | -0.0019781 | -0.0094164 | 0.0014634 | -0.005371 | 0.0030911 | 0.064852 | 0.058422 | -0.0062507 | 0.022042 | -0.0042661 | -0.004578 | 59.9487 | -61.5692 | 60.1181 | -61.2854 | -61.7615 | -61.7798 | 0.054932 | 59.9304 | -61.5646 | 60.1044 | -61.4502 | -61.6013 | -61.6653 | -0.041199 | -0.10071 | 0.068665 | 0.24262 | -0.25177 | -0.23346 | -0.21057 | -0.19226 | -0.036621 | -0.11902 | 0.054932 | 0.07782 | -0.13733 | -0.073242 | -0.10071 | -0.036621 | 0.28381 | 121.6873 | 0.11444 | 121.669 | 121.5179 | 121.4951 | 121.4767 | 121.4584 | -121.6187 | -121.6141 | 121.6461 | 121.6324 | 61.5234 | 61.5829
594.6719 | 121.8292 | -61.5601 | 59.9899 | -0.0045011 | 0.0039692 | 0.0577 | 0.054083 | -5.5462e-05 | -0.006853 | -3.1996e-05 | -0.0023192 | 0.00074128 | 0.065706 | 0.05479 | -0.012659 | 0.022683 | -0.0036253 | -0.073242 | 59.8755 | -61.5784 | 60.1135 | -61.2762 | -61.7523 | -61.7432 | 0.050354 | 59.8343 | -61.6425 | 60.0769 | -61.4594 | -61.5875 | -61.6516 | -0.01831 | -0.11444 | 0.1236 | 0.28381 | -0.1831 | -0.19226 | -0.16479 | -0.17395 | -0.082397 | -0.15564 | 0.086975 | 0.10071 | -0.091552 | -0.027465 | -0.009155 | 0.054932 | 0.30212 | 121.6919 | 0.18311 | 121.7194 | 121.4539 | 121.4767 | 121.4355 | 121.3943 | -121.5683 | -121.6324 | 121.6736 | 121.637 | 61.4868 | 61.6104
596.4375 | 121.788 | -61.5784 | 60.0082 | -0.012131 | 0.0048236 | 0.057486 | 0.054937 | 0.00058534 | -0.005144 | 0.0001816 | -0.005371 | 0.0039457 | 0.067202 | 0.057781 | -0.0096685 | 0.021614 | -0.0012753 | -0.11444 | 59.9304 | -61.615 | 60.0174 | -61.409 | -61.853 | -61.8713 | -0.054932 | 59.8801 | -61.6196 | 60.0037 | -61.5646 | -61.6974 | -61.7294 | -0.036621 | -0.07782 | 0.009155 | 0.16937 | -0.29297 | -0.27466 | -0.25635 | -0.23804 | -0.041199 | -0.12817 | -0.004578 | 0.013733 | -0.15106 | -0.11902 | -0.10986 | -0.07782 | 0.20599 | 121.6324 | 0.054932 | 121.6232 | 121.5454 | 121.4996 | 121.5088 | 121.4584 | -121.6232 | -121.6278 | 121.5958 | 121.582 | 61.4639 | 61.5234
598.125 | 121.7606 | -61.5234 | 60.1135 | -0.0045011 | 0.0024738 | 0.054922 | 0.054937 | -5.5462e-05 | -0.010912 | -0.0028092 | -0.011475 | 0.0033047 | 0.066774 | 0.055858 | -0.010523 | 0.021401 | -0.0051205 | -0.036621 | 60.0037 | -61.5509 | 60.0906 | -61.3129 | -61.7432 | -61.7706 | 0.018311 | 59.9808 | -61.5601 | 60.0449 | -61.4731 | -61.615 | -61.6837 | -0.027466 | -0.10986 | -0.022888 | 0.21057 | -0.24719 | -0.21973 | -0.21973 | -0.19226 | -0.036622 | -0.13275 | -0.068664 | 0.050354 | -0.16022 | -0.091553 | -0.1236 | -0.054931 | 0.23804 | 121.6415 | 0.086976 | 121.6049 | 121.5546 | 121.5408 | 121.5271 | 121.5042 | -121.6644 | -121.6736 | 121.6141 | 121.5683 | 61.4868 | 61.5417
599.875 | 121.8475 | -61.5372 | 60.0037 | -0.0045011 | 0.0026874 | 0.058554 | 0.05451 | 0.00015814 | -0.0038622 | 0.001036 | 0.00073235 | -0.00075412 | 0.067842 | 0.056713 | -0.0094549 | 0.022896 | -0.0046933 | -0.07782 | 59.8801 | -61.5921 | 60.1135 | -61.2671 | -61.7661 | -61.7432 | 0.045776 | 59.8297 | -61.6058 | 60.0723 | -61.4594 | -61.5921 | -61.6516 | -0.054932 | -0.1236 | 0.10986 | 0.27008 | -0.20599 | -0.22888 | -0.15106 | -0.17395 | -0.068665 | -0.17395 | 0.068665 | 0.077819 | -0.11444 | -0.054932 | -0.045776 | 0.013733 | 0.32501 | 121.7056 | 0.14648 | 121.6782 | 121.4722 | 121.4355 | 121.4172 | 121.3669 | -121.5958 | -121.6095 | 121.6507 | 121.6095 | 61.4594 | 61.5829
601.625 | 121.7606 | -61.5097 | 60.1273 | 0.010757 | -0.00030342 | 0.055563 | 0.052801 | -0.0019781 | -0.00963 | -0.0025956 | -0.005371 | 0.0033047 | 0.065706 | 0.050731 | -0.011378 | 0.020546 | -0.0017027 | -0.004578 | 59.9899 | -61.5417 | 60.0906 | -61.3129 | -61.7523 | -61.7615 | 0.041199 | 59.9533 | -61.5692 | 60.0494 | -61.4548 | -61.6013 | -61.6699 | -0.032043 | -0.13733 | -0.036621 | 0.19684 | -0.25177 | -0.24261 | -0.21973 | -0.21057 | -0.059509 | -0.17395 | -0.07782 | 0.054932 | -0.16022 | -0.091552 | -0.10071 | -0.032043 | 0.22888 | 121.6324 | 0.11444 | 121.6187 | 121.5317 | 121.5225 | 121.4996 | 121.463 | -121.669 | -121.6965 | 121.6003 | 121.5591 | 61.5051 | 61.5509
603.375 | 121.843 | -61.5692 | 60.0082 | -0.012131 | 0.0031146 | 0.058768 | 0.056433 | 0.0016535 | -0.0049304 | -0.000673 | -0.0023192 | 0.00074128 | 0.065279 | 0.060771 | -0.0096685 | 0.022896 | -0.0036253 | -0.10986 | 59.9075 | -61.615 | 60.0357 | -61.3678 | -61.853 | -61.8256 | -0.018311 | 59.848 | -61.615 | 60.0632 | -61.4822 | -61.6287 | -61.6562 | -0.045776 | -0.10071 | 0.027466 | 0.20142 | -0.25635 | -0.28381 | -0.21057 | -0.23804 | -0.045776 | -0.16022 | 0.054931 | 0.086975 | -0.086975 | -0.059509 | -0.041199 | -0.013733 | 0.24719 | 121.6507 | 0.13275 | 121.6782 | 121.5225 | 121.463 | 121.4767 | 121.4172 | -121.6232 | -121.6232 | 121.6049 | 121.6324 | 61.4594 | 61.5509
605.125 | 121.7468 | -61.5097 | 60.1089 | -0.0045011 | -0.00073062 | 0.055777 | 0.055578 | -0.0017645 | -0.0079212 | -0.0002456 | -0.005371 | 0.0015957 | 0.065065 | 0.059276 | -0.011378 | 0.022255 | -0.00063445 | -0.041199 | 59.9991 | -61.5372 | 60.0861 | -61.3083 | -61.7477 | -61.7661 | 0.022888 | 60.0037 | -61.5601 | 60.0403 | -61.4731 | -61.6196 | -61.6745 | -0.027465 | -0.10986 | -0.022888 | 0.20142 | -0.25635 | -0.23804 | -0.22888 | -0.21057 | -0.050354 | -0.10529 | -0.068665 | 0.036622 | -0.1648 | -0.10986 | -0.11444 | -0.059509 | 0.22888 | 121.6232 | 0.086976 | 121.6003 | 121.5363 | 121.5637 | 121.5088 | 121.5134 | -121.6461 | -121.669 | 121.5958 | 121.55 | 61.4685 | 61.5326
606.8906 | 121.8979 | -61.5005 | 60.0449 | -0.01976 | -0.00030342 | 0.053854 | 0.053442 | 0.00079894 | -0.00963 | -0.002382 | -0.0084228 | 0.0022367 | 0.064211 | 0.060558 | -0.012873 | 0.019478 | -0.0029843 | -0.022888 | 59.8846 | -61.5646 | 60.1547 | -61.2305 | -61.6745 | -61.6791 | 0.10071 | 59.8755 | -61.5555 | 60.141 | -61.3632 | -61.4822 | -61.5738 | -0.064087 | -0.16022 | 0.10986 | 0.27008 | -0.17853 | -0.17395 | -0.11444 | -0.10986 | -0.054932 | -0.16937 | 0.09613 | 0.13733 | -0.073243 | 0.01831 | -0.018311 | 0.073242 | 0.33417 | 121.7194 | 0.19226 | 121.6965 | 121.4493 | 121.431 | 121.3852 | 121.376 | -121.6095 | -121.6003 | 121.6553 | 121.6415 | 61.4777 | 61.6013
608.6406 | 121.7422 | -61.5875 | 59.9991 | -0.0045011 | 0.00076478 | 0.059195 | 0.056219 | -5.5462e-05 | -0.006853 | 0.0008224 | -0.005371 | 0.0035183 | 0.065706 | 0.056499 | -0.0083869 | 0.019051 | -0.0051205 | -0.10529 | 59.9213 | -61.615 | 59.9762 | -61.4594 | -61.8988 | -61.8942 | -0.082397 | 59.8846 | -61.6516 | 59.9762 | -61.5967 | -61.734 | -61.7477 | -0.027466 | -0.077819 | -0.022888 | 0.12817 | -0.3067 | -0.31128 | -0.27924 | -0.28381 | -0.064087 | -0.11444 | -0.022888 | -0.009156 | -0.16022 | -0.14648 | -0.096131 | -0.082398 | 0.15564 | 121.5912 | 0.054931 | 121.6278 | 121.5363 | 121.5363 | 121.5088 | 121.4722 | -121.6141 | -121.6507 | 121.5637 | 121.5637 | 61.4822 | 61.5051
610.3281 | 121.8475 | -61.5326 | 59.9991 | -0.012131 | 0.0033282 | 0.058981 | 0.052588 | 0.00058534 | -0.0036486 | -0.0025956 | 0.00073235 | 0.00095488 | 0.064424 | 0.05714 | -0.010737 | 0.021401 | -0.0019163 | -0.073242 | 59.8709 | -61.5555 | 60.1181 | -61.2717 | -61.7569 | -61.7477 | 0.050354 | 59.8434 | -61.6013 | 60.0769 | -61.4731 | -61.5738 | -61.6425 | -0.022888 | -0.12817 | 0.11902 | 0.26093 | -0.21515 | -0.2243 | -0.19226 | -0.20142 | -0.068664 | -0.15564 | 0.07782 | 0.05951 | -0.10986 | -0.041199 | -0.041199 | 0.027465 | 0.28381 | 121.6736 | 0.12817 | 121.6782 | 121.4264 | 121.4447 | 121.4035 | 121.376 | -121.5546 | -121.6003 | 121.6507 | 121.6095 | 61.4594 | 61.5829
612.0781 | 121.7697 | -61.5829 | 60.0174 | -0.012131 | 0.0037556 | 0.060263 | 0.058355 | 0.0029351 | -0.0081348 | -0.0021682 | 0.00073235 | 0.0035183 | 0.066988 | 0.059062 | -0.0068915 | 0.019051 | -0.0027707 | -0.10529 | 59.9258 | -61.6287 | 59.9945 | -61.4273 | -61.8759 | -61.8668 | -0.073242 | 59.8755 | -61.6241 | 60.0037 | -61.5555 | -61.7111 | -61.7432 | -0.045776 | -0.091553 | -0.022888 | 0.15564 | -0.28381 | -0.29297 | -0.23804 | -0.24719 | -0.041199 | -0.14191 | -0.013733 | 0.027466 | -0.16022 | -0.12817 | -0.11902 | -0.086975 | 0.20142 | 121.6232 | 0.068665 | 121.6278 | 121.5546 | 121.4996 | 121.5088 | 121.4584 | -121.6461 | -121.6415 | 121.5775 | 121.5866 | 61.4777 | 61.5097
613.8281 | 121.7606 | -61.496 | 60.1181 | -0.0045011 | -8.9824e-05 | 0.055777 | 0.05451 | 0.0020807 | -0.0066394 | 0.0025314 | -0.0084228 | 0.0033047 | 0.067842 | 0.049022 | -0.011805 | 0.019905 | -0.0027707 | -0.041199 | 60.0311 | -61.5463 | 60.0952 | -61.3174 | -61.734 | -61.7661 | 0.022888 | 59.9762 | -61.5417 | 60.054 | -61.4731 | -61.6196 | -61.6653 | -0.050354 | -0.086975 | -0.022888 | 0.17853 | -0.27008 | -0.23804 | -0.21973 | -0.18768 | -0.045776 | -0.14191 | -0.064087 | 0.022889 | -0.16937 | -0.1236 | -0.1236 | -0.07782 | 0.22888 | 121.6415 | 0.068665 | 121.5958 | 121.5775 | 121.5179 | 121.5271 | 121.4722 | -121.6644 | -121.6599 | 121.5912 | 121.55 | 61.4548 | 61.5189
615.5781 | 121.7743 | -61.5784 | 60.0128 | -0.01976 | 0.0031146 | 0.057059 | 0.053656 | -0.0034735 | -0.0062122 | -0.002382 | -0.0023192 | 0.0028775 | 0.068911 | 0.056926 | -0.0092413 | 0.018624 | -0.0010617 | -0.11902 | 59.9213 | -61.6196 | 60.0037 | -61.4182 | -61.8713 | -61.8576 | -0.064087 | 59.8846 | -61.6333 | 59.9991 | -61.5692 | -61.7111 | -61.7294 | -0.041199 | -0.091552 | -0.009155 | 0.16022 | -0.27924 | -0.29297 | -0.23804 | -0.25177 | -0.054932 | -0.12817 | -0.013733 | 0.009155 | -0.15106 | -0.13275 | -0.09613 | -0.07782 | 0.20142 | 121.6232 | 0.064087 | 121.6324 | 121.5408 | 121.5179 | 121.4996 | 121.463 | -121.6324 | -121.6461 | 121.582 | 121.5775 | 61.4594 | 61.5143
617.3281 | 121.7972 | -61.5417 | 60.0403 | -0.012131 | 0.0016192 | 0.056631 | 0.058783 | 0.00015814 | -0.0072802 | -0.0011002 | -0.005371 | 0.0026639 | 0.066347 | 0.054363 | -0.01095 | 0.021614 | -0.0044797 | 0 | 59.9625 | -61.5555 | 60.1089 | -61.29 | -61.7477 | -61.7752 | 0.054932 | 59.9258 | -61.5784 | 60.0815 | -61.4639 | -61.6013 | -61.647 | -0.013733 | -0.07782 | 0.068665 | 0.25177 | -0.23346 | -0.20599 | -0.21973 | -0.19226 | -0.036621 | -0.11444 | 0.041199 | 0.07782 | -0.10529 | -0.059509 | -0.068665 | -0.022888 | 0.2655 | 121.6644 | 0.11444 | 121.6599 | 121.5179 | 121.5042 | 121.5042 | 121.4676 | -121.5958 | -121.6187 | 121.6507 | 121.6232 | 61.5417 | 61.5967
619.0156 | 121.7468 | -61.5005 | 60.1044 | -0.012131 | -8.9824e-05 | 0.055991 | 0.053656 | 0.0029351 | -0.00963 | 0.0021042 | -0.0084228 | 0.0037321 | 0.066347 | 0.055644 | -0.0098823 | 0.021187 | -0.00020725 | -0.036621 | 59.9808 | -61.5555 | 60.0815 | -61.3312 | -61.7432 | -61.7661 | 0.022888 | 59.9808 | -61.5784 | 60.0403 | -61.4639 | -61.615 | -61.6791 | -0.054932 | -0.1236 | -0.022888 | 0.16937 | -0.2655 | -0.24262 | -0.21057 | -0.18768 | -0.07782 | -0.1236 | -0.064087 | 0.036621 | -0.17853 | -0.11444 | -0.10071 | -0.036621 | 0.2243 | 121.637 | 0.11444 | 121.6187 | 121.5363 | 121.5591 | 121.4813 | 121.4813 | -121.6599 | -121.6827 | 121.582 | 121.5408 | 61.4639 | 61.5234
620.7656 | 121.7377 | -61.5738 | 60.0311 | -0.012131 | 0.001833 | 0.056845 | 0.057287 | -0.0043281 | -0.0074938 | 0.0001816 | -0.0023192 | 0.0050137 | 0.067202 | 0.061199 | -0.0064643 | 0.019692 | -0.0031979 | -0.068665 | 59.935 | -61.6058 | 60.0266 | -61.3815 | -61.8576 | -61.8576 | -0.059509 | 59.8984 | -61.6013 | 59.9808 | -61.5646 | -61.7157 | -61.734 | -0.032043 | -0.09613 | -0.004578 | 0.19226 | -0.28381 | -0.28381 | -0.25177 | -0.25177 | -0.027465 | -0.13275 | -0.050354 | 0.009156 | -0.16022 | -0.14191 | -0.13275 | -0.11444 | 0.2243 | 121.6324 | 0.036621 | 121.582 | 121.5408 | 121.4996 | 121.5088 | 121.4722 | -121.637 | -121.6324 | 121.6003 | 121.5546 | 61.5051 | 61.5143
622.4688 | 121.8887 | -61.4914 | 60.054 | -0.01976 | 0.00012398 | 0.058127 | 0.053228 | 0.00079894 | -0.0049304 | -0.0028092 | -0.0023192 | 0.00074128 | 0.065279 | 0.050945 | -0.010523 | 0.022255 | -0.0034117 | -0.027466 | 59.9304 | -61.5555 | 60.1776 | -61.2122 | -61.6379 | -61.6653 | 0.14191 | 59.8663 | -61.5646 | 60.1456 | -61.3449 | -61.4868 | -61.5738 | -0.064087 | -0.1236 | 0.1236 | 0.27924 | -0.17395 | -0.14648 | -0.10986 | -0.082397 | -0.073242 | -0.18768 | 0.091553 | 0.14648 | -0.082398 | 0.004578 | -0.009156 | 0.07782 | 0.34332 | 121.7331 | 0.21973 | 121.7102 | 121.4859 | 121.431 | 121.4218 | 121.3577 | -121.6095 | -121.6187 | 121.669 | 121.637 | 61.4639 | 61.6333
624.2031 | 121.7285 | -61.5829 | 60.0357 | 0.0031279 | 0.0050372 | 0.056631 | 0.056006 | 0.0029351 | -0.0079212 | -0.0030228 | -0.0084228 | 0.0037321 | 0.066347 | 0.056072 | -0.0073187 | 0.020974 | -0.0051205 | -0.064087 | 59.9442 | -61.6013 | 60.022 | -61.4044 | -61.8759 | -61.8484 | -0.064087 | 59.9121 | -61.6013 | 59.9808 | -61.5784 | -61.7203 | -61.7294 | -0.01831 | -0.091553 | -0.013733 | 0.17853 | -0.2655 | -0.29297 | -0.24719 | -0.27466 | -0.01831 | -0.1236 | -0.054932 | 0.004578 | -0.14648 | -0.13733 | -0.12817 | -0.11902 | 0.19684 | 121.6232 | 0.022888 | 121.582 | 121.5454 | 121.5134 | 121.5271 | 121.4951 | -121.637 | -121.637 | 121.6049 | 121.5637 | 61.5189 | 61.5189
625.9531 | 121.7834 | -61.5234 | 60.0677 | -0.012131 | 0.0022602 | 0.056631 | 0.05686 | -0.00069646 | -0.006853 | -0.0040908 | -0.0023192 | 0.0018095 | 0.066347 | 0.056285 | -0.0090277 | 0.02076 | -0.0042661 | -0.013733 | 59.9487 | -61.5646 | 60.1135 | -61.3037 | -61.7569 | -61.7706 | 0.059509 | 59.903 | -61.5829 | 60.0586 | -61.4731 | -61.6287 | -61.6791 | -0.041199 | -0.11902 | 0.045776 | 0.21973 | -0.24719 | -0.23346 | -0.20599 | -0.19226 | -0.05951 | -0.16479 | -0.009155 | 0.050354 | -0.15564 | -0.10529 | -0.09613 | -0.045776 | 0.26093 | 121.6782 | 0.10986 | 121.6415 | 121.5134 | 121.4859 | 121.4722 | 121.4264 | -121.6324 | -121.6507 | 121.637 | 121.582 | 61.5097 | 61.5829
627.7031 | 121.7285 | -61.5875 | 60.0266 | -0.012131 | 0.0050372 | 0.05834 | 0.057287 | -0.0013373 | -0.0081348 | -0.0008866 | -0.0023192 | 0.0026639 | 0.067415 | 0.058422 | -0.0088141 | 0.022255 | -0.0014891 | -0.07782 | 59.9442 | -61.5875 | 60.0311 | -61.4182 | -61.8576 | -61.8576 | -0.091553 | 59.8892 | -61.6379 | 59.9579 | -61.5921 | -61.7523 | -61.7615 | 0 | -0.082397 | 0.004578 | 0.16937 | -0.27008 | -0.27008 | -0.27008 | -0.27008 | -0.050354 | -0.13733 | -0.068664 | -0.004578 | -0.17395 | -0.16479 | -0.1236 | -0.11444 | 0.16937 | 121.6187 | 0.045776 | 121.5958 | 121.5317 | 121.5271 | 121.5317 | 121.4767 | -121.6141 | -121.6644 | 121.6187 | 121.5454 | 61.5097 | 61.496
629.4531 | 121.8842 | -61.4731 | 60.0449 | -0.01976 | -0.00073062 | 0.055777 | 0.05451 | -0.0041145 | -0.0066394 | -0.0025956 | -0.005371 | 0.0020231 | 0.066347 | 0.0471 | -0.010523 | 0.022255 | -0.0029843 | 0.009155 | 59.935 | -61.528 | 60.2051 | -61.1664 | -61.6379 | -61.6653 | 0.16479 | 59.8892 | -61.5234 | 60.1593 | -61.3403 | -61.4594 | -61.5692 | -0.054932 | -0.10986 | 0.16022 | 0.3067 | -0.19226 | -0.16479 | -0.13733 | -0.10986 | -0.050354 | -0.15564 | 0.11444 | 0.13275 | -0.096131 | 0.013732 | -0.045777 | 0.064086 | 0.36163 | 121.7331 | 0.18311 | 121.6827 | 121.463 | 121.4127 | 121.4081 | 121.3623 | -121.5729 | -121.5683 | 121.6782 | 121.6324 | 61.4822 | 61.6379
631.1406 | 121.7377 | -61.4914 | 60.0952 | -0.012131 | 0.001192 | 0.056204 | 0.057074 | -0.0013373 | -0.0083484 | -0.000673 | -0.005371 | 0.0018095 | 0.068483 | 0.062053 | -0.010096 | 0.021828 | -0.00084805 | -0.018311 | 60.0082 | -61.5601 | 60.0861 | -61.3403 | -61.7386 | -61.7661 | 0.009155 | 59.967 | -61.5692 | 60.0357 | -61.4822 | -61.6241 | -61.6745 | -0.068665 | -0.086975 | -0.009155 | 0.15106 | -0.27466 | -0.24719 | -0.20599 | -0.17853 | -0.07782 | -0.12817 | -0.059509 | 0.009155 | -0.18311 | -0.13275 | -0.10529 | -0.054932 | 0.21973 | 121.6461 | 0.086975 | 121.6049 | 121.5683 | 121.5363 | 121.4996 | 121.4584 | -121.6553 | -121.6644 | 121.5775 | 121.5271 | 61.4731 | 61.5005
632.8906 | 121.8292 | -61.5601 | 60.0266 | -0.012131 | 0.0016192 | 0.056845 | 0.053228 | 0.0016535 | -0.008562 | -0.0045182 | -0.005371 | 0.00074128 | 0.064211 | 0.062694 | -0.011805 | 0.022255 | -0.0027707 | -0.091553 | 59.8892 | -61.5875 | 60.0861 | -61.3083 | -61.7477 | -61.7523 | 0.009155 | 59.8709 | -61.6058 | 60.0586 | -61.4731 | -61.5921 | -61.6608 | -0.027465 | -0.13733 | 0.05951 | 0.25177 | -0.19226 | -0.18768 | -0.16479 | -0.16022 | -0.045776 | -0.15564 | 0.032044 | 0.086976 | -0.10071 | -0.032043 | -0.054932 | 0.013733 | 0.27923 | 121.6736 | 0.13275 | 121.6644 | 121.4767 | 121.4767 | 121.4493 | 121.431 | -121.6141 | -121.6324 | 121.6461 | 121.6187 | 61.4685 | 61.5692
634.6406 | 121.7514 | -61.5005 | 60.1044 | 0.0031279 | 0.00012398 | 0.055563 | 0.05451 | -0.0030463 | -0.0072802 | -0.002382 | -0.0084228 | 0.0035183 | 0.066774 | 0.057781 | -0.010096 | 0.020546 | -0.0025571 | -0.036621 | 59.9854 | -61.5555 | 60.0769 | -61.3174 | -61.7432 | -61.7477 | 0.018311 | 59.9854 | -61.5555 | 60.0357 | -61.496 | -61.6058 | -61.6653 | -0.054932 | -0.11902 | -0.027466 | 0.1831 | -0.24719 | -0.24262 | -0.19226 | -0.18768 | -0.054932 | -0.11902 | -0.068664 | 0.004577 | -0.16479 | -0.10529 | -0.10986 | -0.050354 | 0.23804 | 121.6324 | 0.059509 | 121.5912 | 121.5408 | 121.5408 | 121.4859 | 121.4859 | -121.6599 | -121.6599 | 121.5775 | 121.5363 | 61.4639 | 61.5189
636.3281 | 121.7468 | -61.5509 | 60.0174 | -0.012131 | 0.0031146 | 0.057059 | 0.056646 | 0.0020807 | -0.0064258 | 0.0003952 | -0.005371 | 0.0052273 | 0.066133 | 0.0471 | -0.0068915 | 0.020974 | -0.0040525 | -0.045776 | 59.935 | -61.5875 | 60.0494 | -61.3678 | -61.8393 | -61.8484 | -0.027466 | 59.8984 | -61.615 | 59.9945 | -61.5692 | -61.7111 | -61.7249 | -0.036621 | -0.082397 | 0.032043 | 0.1831 | -0.29755 | -0.28839 | -0.26093 | -0.25177 | -0.064087 | -0.11902 | -0.022888 | -0.018311 | -0.17395 | -0.16022 | -0.10986 | -0.096131 | 0.21973 | 121.637 | 0.045776 | 121.6095 | 121.5225 | 121.5134 | 121.4859 | 121.4493 | -121.6049 | -121.6324 | 121.6003 | 121.5454 | 61.5051 | 61.5234
638.0781 | 121.8384 | -61.5326 | 59.967 | -0.012131 | 0.0035418 | 0.058768 | 0.053442 | 0.00058534 | -0.0077074 | -0.0025956 | -0.0084228 | 0.0011685 | 0.066988 | 0.055217 | -0.01031 | 0.023323 | -0.0023435 | -0.064087 | 59.8755 | -61.5784 | 60.0815 | -61.2717 | -61.7569 | -61.7569 | 0.041199 | 59.8068 | -61.615 | 60.0677 | -61.4639 | -61.5875 | -61.6425 | -0.045776 | -0.091553 | 0.11444 | 0.26093 | -0.2243 | -0.2243 | -0.17853 | -0.17853 | -0.082397 | -0.16022 | 0.10071 | 0.068665 | -0.10986 | -0.054931 | -0.027466 | 0.027466 | 0.3067 | 121.6599 | 0.15106 | 121.6827 | 121.4539 | 121.4218 | 121.4081 | 121.3394 | -121.5454 | -121.582 | 121.6141 | 121.6003 | 61.4685 | 61.5738
639.8281 | 121.8933 | -61.5051 | 60.0311 | -0.012131 | 0.00033758 | 0.057913 | 0.055578 | 0.00079894 | -0.0074938 | -0.0019546 | -0.0084228 | -0.0013949 | 0.064211 | 0.051372 | -0.012232 | 0.021187 | -0.00084805 | -0.009155 | 59.9213 | -61.5417 | 60.173 | -61.1847 | -61.6425 | -61.6516 | 0.15106 | 59.903 | -61.5601 | 60.141 | -61.3495 | -61.4639 | -61.5509 | -0.036621 | -0.10986 | 0.14191 | 0.32044 | -0.14648 | -0.13733 | -0.10986 | -0.10071 | -0.054932 | -0.12817 | 0.10986 | 0.15564 | -0.045776 | 0.041199 | 0.009156 | 0.096131 | 0.35706 | 121.7148 | 0.21057 | 121.7011 | 121.463 | 121.463 | 121.4264 | 121.4081 | -121.5729 | -121.5912 | 121.6782 | 121.6461 | 61.496 | 61.6562
641.5938 | 121.8658 | -61.4731 | 60.0403 | -0.02739 | -0.00094422 | 0.056631 | 0.052374 | -0.0034735 | -0.0089892 | -0.0011002 | -0.0084228 | 0.00031408 | 0.063356 | 0.057994 | -0.011805 | 0.020333 | 0.00043375 | 0.032043 | 59.9258 | -61.5646 | 60.2188 | -61.1526 | -61.6104 | -61.6425 | 0.16479 | 59.9121 | -61.5417 | 60.1685 | -61.3358 | -61.4594 | -61.5555 | -0.091553 | -0.11444 | 0.17853 | 0.32043 | -0.16937 | -0.13733 | -0.07782 | -0.045777 | -0.068665 | -0.12817 | 0.12817 | 0.13733 | -0.082398 | 0.013732 | -0.013733 | 0.082397 | 0.41199 | 121.7834 | 0.20599 | 121.7102 | 121.4905 | 121.4539 | 121.3989 | 121.3852 | -121.6049 | -121.582 | 121.6919 | 121.6415 | 61.5051 | 61.6379
643.3594 | 121.7514 | -61.528 | 60.0769 | -0.012131 | -0.00094422 | 0.055777 | 0.056219 | -0.0019781 | -0.0066394 | -0.0028092 | -0.005371 | 0.0013821 | 0.066347 | 0.060131 | -0.0090277 | 0.021401 | 0.00021995 | -0.018311 | 60.0082 | -61.5601 | 60.0906 | -61.3312 | -61.7386 | -61.7706 | 0.027466 | 59.9762 | -61.5463 | 60.0494 | -61.496 | -61.6196 | -61.6699 | -0.032044 | -0.068664 | 0.013733 | 0.19684 | -0.24261 | -0.21057 | -0.21057 | -0.17853 | -0.018311 | -0.10071 | -0.027466 | 0.032043 | -0.14191 | -0.091553 | -0.1236 | -0.073242 | 0.22888 | 121.6507 | 0.050354 | 121.5958 | 121.5683 | 121.5225 | 121.5363 | 121.5042 | -121.637 | -121.6232 | 121.6187 | 121.5775 | 61.5097 | 61.5555
645.1094 | 121.8704 | -61.5417 | 59.9487 | -0.012131 | 0.0035418 | 0.05834 | 0.056219 | -0.0034735 | -0.0055712 | 0.0001816 | -0.005371 | 0.0018095 | 0.06592 | 0.053722 | -0.0079597 | 0.022042 | -0.00084805 | -0.068665 | 59.8755 | -61.5967 | 60.1227 | -61.2717 | -61.7615 | -61.7569 | 0.068665 | 59.8434 | -61.6425 | 60.0952 | -61.441 | -61.5784 | -61.615 | -0.054932 | -0.073242 | 0.17395 | 0.27008 | -0.21515 | -0.21973 | -0.16022 | -0.16479 | -0.10071 | -0.10528 | 0.14649 | 0.10071 | -0.073242 | -0.036621 | 0.027466 | 0.064087 | 0.32501 | 121.7194 | 0.20142 | 121.7377 | 121.4722 | 121.4859 | 121.4172 | 121.3852 | -121.5454 | -121.5912 | 121.6644 | 121.637 | 61.4731 | 61.6104
646.8125 | 121.7651 | -61.5189 | 60.0952 | -0.012131 | 0.00033758 | 0.056204 | 0.055578 | 0.0033623 | -0.0094164 | -0.0038772 | -0.0023192 | 0.0045865 | 0.065493 | 0.056499 | -0.010523 | 0.021401 | -0.0051205 | -0.009155 | 59.9854 | -61.5189 | 60.0952 | -61.3174 | -61.7386 | -61.7523 | 0.022888 | 59.9854 | -61.5555 | 60.0494 | -61.4594 | -61.5967 | -61.6562 | 0 | -0.10986 | 0 | 0.20142 | -0.23346 | -0.21973 | -0.23346 | -0.21973 | -0.036621 | -0.10986 | -0.045777 | 0.059509 | -0.13733 | -0.07782 | -0.10071 | -0.041199 | 0.20142 | 121.6141 | 0.09613 | 121.6049 | 121.5042 | 121.5408 | 121.5042 | 121.5042 | -121.6141 | -121.6507 | 121.6141 | 121.5683 | 61.5097 | 61.5417
648.5625 | 121.7377 | -61.5738 | 60.0403 | 0.0031279 | 0.0052508 | 0.058554 | 0.057715 | 0.0022943 | -0.008562 | -0.0015274 | -0.005371 | 0.0020231 | 0.064638 | 0.059917 | -0.0075323 | 0.020333 | -0.0019163 | -0.073242 | 59.9579 | -61.5784 | 60.0449 | -61.3953 | -61.8484 | -61.8484 | -0.054932 | 59.9075 | -61.6287 | 59.9991 | -61.5692 | -61.7249 | -61.7294 | -0.004577 | -0.082397 | 0.004578 | 0.17853 | -0.27466 | -0.27466 | -0.27008 | -0.27008 | -0.054931 | -0.13275 | -0.041199 | 0.004578 | -0.15564 | -0.15106 | -0.10071 | -0.096131 | 0.18311 | 121.6232 | 0.059509 | 121.6278 | 121.5363 | 121.5363 | 121.5317 | 121.4813 | -121.6187 | -121.669 | 121.6187 | 121.5729 | 61.5005 | 61.5189
650.3125 | 121.8842 | -61.496 | 60.0449 | -0.01976 | -0.00051702 | 0.055991 | 0.054083 | -0.0026191 | -0.0089892 | -0.0021682 | -0.005371 | 0.00052768 | 0.067202 | 0.05714 | -0.012019 | 0.020333 | -0.00084805 | 0.032043 | 59.8984 | -61.5143 | 60.1913 | -61.1481 | -61.6287 | -61.647 | 0.15106 | 59.935 | -61.5463 | 60.1547 | -61.3358 | -61.4639 | -61.5555 | -0.01831 | -0.14648 | 0.14648 | 0.3479 | -0.15106 | -0.13275 | -0.13275 | -0.11444 | -0.050354 | -0.10986 | 0.10986 | 0.16022 | -0.059509 | 0.032044 | -0.009155 | 0.082398 | 0.36621 | 121.7056 | 0.21057 | 121.7011 | 121.4127 | 121.4813 | 121.3943 | 121.431 | -121.5591 | -121.5912 | 121.6873 | 121.6507 | 61.528 | 61.647
652.0781 | 121.7926 | -61.5189 | 60.0723 | -0.012131 | 0.0033282 | 0.05834 | 0.054937 | 0.00037174 | -0.0057848 | -0.000673 | -0.0023192 | 0.0043729 | 0.064852 | 0.057994 | -0.0092413 | 0.022469 | -0.0014891 | -0.004578 | 60.0037 | -61.5509 | 60.1089 | -61.322 | -61.7432 | -61.7661 | 0.032043 | 59.9396 | -61.5784 | 60.0677 | -61.4456 | -61.6013 | -61.647 | -0.032043 | -0.068665 | 0.036621 | 0.19684 | -0.24719 | -0.2243 | -0.21515 | -0.19226 | -0.059509 | -0.13275 | -0.004578 | 0.073242 | -0.12817 | -0.082397 | -0.068665 | -0.022888 | 0.22888 | 121.6599 | 0.13275 | 121.6461 | 121.5546 | 121.5179 | 121.5225 | 121.4584 | -121.6232 | -121.6507 | 121.6278 | 121.5866 | 61.5143 | 61.5509
653.8281 | 121.8292 | -61.5646 | 60.022 | -0.012131 | 0.0026874 | 0.056845 | 0.055151 | -0.0017645 | -0.006853 | -0.000673 | -0.005371 | -0.0016085 | 0.066561 | 0.055004 | -0.0096685 | 0.021401 | -0.0021299 | -0.091553 | 59.848 | -61.5829 | 60.0952 | -61.3083 | -61.7798 | -61.7752 | 0.022888 | 59.8526 | -61.615 | 60.0952 | -61.4594 | -61.5921 | -61.647 | -0.018311 | -0.17395 | 0.073242 | 0.25635 | -0.21057 | -0.21515 | -0.19226 | -0.19684 | -0.050354 | -0.16937 | 0.073242 | 0.10529 | -0.082398 | -0.027466 | -0.032044 | 0.022888 | 0.27466 | 121.6782 | 0.15564 | 121.7102 | 121.431 | 121.4676 | 121.4127 | 121.4172 | -121.6049 | -121.637 | 121.6599 | 121.6599 | 61.4731 | 61.5875
655.5156 | 121.8246 | -61.5326 | 60.0266 | -0.012131 | 0.0024738 | 0.058127 | 0.054083 | -0.0017645 | -0.0045032 | -0.0011002 | -0.005371 | 0.0030911 | 0.064638 | 0.058849 | -0.0094549 | 0.022469 | -0.0061887 | -0.10071 | 59.8984 | -61.5875 | 60.0861 | -61.29 | -61.7706 | -61.7477 | 0.013733 | 59.8526 | -61.6196 | 60.0677 | -61.4548 | -61.5829 | -61.6516 | -0.054931 | -0.12817 | 0.05951 | 0.24262 | -0.21515 | -0.23804 | -0.16022 | -0.18311 | -0.086975 | -0.17395 | 0.041199 | 0.07782 | -0.11902 | -0.050354 | -0.032043 | 0.036621 | 0.29755 | 121.6736 | 0.16479 | 121.6873 | 121.4859 | 121.4722 | 121.431 | 121.3852 | -121.6141 | -121.6461 | 121.6187 | 121.6003 | 61.4319 | 61.5463
657.2656 | 121.8384 | -61.5463 | 59.9808 | -0.0045011 | 0.002901 | 0.057913 | 0.053442 | 0.0010125 | -0.0094164 | -0.0045182 | -0.0084228 | 0.00031408 | 0.063997 | 0.061199 | -0.010096 | 0.021614 | -0.0038389 | -0.086975 | 59.8892 | -61.5875 | 60.1135 | -61.29 | -61.7706 | -61.7523 | 0.054932 | 59.8389 | -61.6058 | 60.0723 | -61.4685 | -61.5829 | -61.6608 | -0.041198 | -0.091553 | 0.13275 | 0.25635 | -0.20599 | -0.2243 | -0.16479 | -0.18311 | -0.059509 | -0.14191 | 0.091553 | 0.07782 | -0.11444 | -0.036621 | -0.054932 | 0.022888 | 0.29755 | 121.701 | 0.13733 | 121.6782 | 121.4767 | 121.4447 | 121.4355 | 121.3852 | -121.5683 | -121.5866 | 121.6599 | 121.6187 | 61.4594 | 61.6013
659.0156 | 121.7972 | -61.4868 | 60.0952 | -0.0045011 | 0.00076478 | 0.056845 | 0.054937 | -0.00091006 | -0.0074938 | -0.002382 | -0.005371 | 0.00052768 | 0.065706 | 0.060344 | -0.0092413 | 0.018837 | -0.0019163 | 0.036621 | 59.9167 | -61.5509 | 60.1959 | -61.2076 | -61.6608 | -61.6745 | 0.11902 | 59.9396 | -61.5372 | 60.1135 | -61.4136 | -61.5372 | -61.6058 | -0.064087 | -0.17853 | 0.10071 | 0.27923 | -0.18768 | -0.17395 | -0.1236 | -0.10986 | -0.050354 | -0.15564 | 0.01831 | 0.073242 | -0.11902 | -0.050354 | -0.068665 | 0 | 0.34332 | 121.7468 | 0.1236 | 121.6507 | 121.4676 | 121.4767 | 121.4035 | 121.4264 | -121.6461 | -121.6324 | 121.6827 | 121.6003 | 61.5234 | 61.6058
660.7656 | 121.7239 | -61.5829 | 60.0174 | -0.012131 | 0.0052508 | 0.057913 | 0.05686 | 0.0018671 | -0.0079212 | -0.000673 | -0.0023192 | 0.0020231 | 0.065493 | 0.056499 | -0.0075323 | 0.019692 | -0.00084805 | -0.07782 | 59.9396 | -61.6196 | 60.0266 | -61.409 | -61.8622 | -61.8713 | -0.082397 | 59.9167 | -61.6287 | 59.9716 | -61.5829 | -61.7432 | -61.7477 | -0.036621 | -0.07782 | 0.009155 | 0.17395 | -0.28839 | -0.27924 | -0.25177 | -0.24262 | -0.045776 | -0.10071 | -0.045776 | 0 | -0.1648 | -0.16022 | -0.11902 | -0.11444 | 0.21057 | 121.6461 | 0.045776 | 121.6003 | 121.5591 | 121.5454 | 121.5225 | 121.4996 | -121.637 | -121.6461 | 121.6095 | 121.5546 | 61.5051 | 61.5005
662.4531 | 121.8704 | -61.5234 | 60.022 | -0.0045011 | 0.001833 | 0.060263 | 0.054724 | -0.0039007 | -0.0077074 | 0.0001816 | -0.005371 | 0.0013821 | 0.06592 | 0.055004 | -0.0098823 | 0.023964 | -0.0029843 | -0.064087 | 59.8938 | -61.5875 | 60.1089 | -61.2946 | -61.7294 | -61.7477 | 0.041199 | 59.8526 | -61.5967 | 60.1089 | -61.409 | -61.528 | -61.6058 | -0.064087 | -0.12817 | 0.086975 | 0.22888 | -0.22431 | -0.20599 | -0.16022 | -0.14191 | -0.073243 | -0.16937 | 0.086975 | 0.11444 | -0.082398 | -0.004578 | -0.009155 | 0.068665 | 0.29297 | 121.6965 | 0.18768 | 121.7056 | 121.4813 | 121.4493 | 121.4172 | 121.376 | -121.6095 | -121.6187 | 121.6324 | 121.6324 | 61.4594 | 61.5646
664.2031 | 121.875 | -61.5692 | 59.967 | -0.012131 | 0.0041828 | 0.058554 | 0.055578 | 0.0035761 | -0.0057848 | -0.0008866 | -0.0023192 | 0.00095488 | 0.067415 | 0.059276 | -0.0086005 | 0.020333 | -0.00042085 | -0.073242 | 59.8709 | -61.5738 | 60.1135 | -61.2946 | -61.7661 | -61.7615 | 0.045776 | 59.8022 | -61.6196 | 60.0906 | -61.4365 | -61.5875 | -61.6196 | -0.004578 | -0.09613 | 0.14648 | 0.27466 | -0.19226 | -0.19684 | -0.18768 | -0.19226 | -0.050354 | -0.1648 | 0.1236 | 0.13275 | -0.050354 | -0.01831 | 0 | 0.032044 | 0.27924 | 121.6873 | 0.18311 | 121.7102 | 121.4447 | 121.4218 | 121.4401 | 121.3715 | -121.5408 | -121.5866 | 121.6827 | 121.6599 | 61.496 | 61.615
665.9375 | 121.8979 | -61.496 | 60.0403 | -0.0045011 | -0.0026532 | 0.056418 | 0.053228 | 0.00015814 | -0.0055712 | -0.0047318 | -0.0023192 | 0.00074128 | 0.064638 | 0.056072 | -0.010737 | 0.021828 | -0.0021299 | 0 | 59.935 | -61.5097 | 60.2188 | -61.1572 | -61.615 | -61.6425 | 0.16479 | 59.8938 | -61.528 | 60.1639 | -61.3449 | -61.4685 | -61.5555 | -0.013733 | -0.10529 | 0.17853 | 0.33875 | -0.14648 | -0.11902 | -0.13275 | -0.10529 | -0.032043 | -0.14648 | 0.1236 | 0.15106 | -0.059509 | 0.027466 | -0.027466 | 0.059509 | 0.35248 | 121.7285 | 0.18311 | 121.6919 | 121.4447 | 121.4218 | 121.431 | 121.3898 | -121.55 | -121.5683 | 121.7148 | 121.6599 | 61.496 | 61.6608
667.6406 | 121.7606 | -61.5875 | 60.0311 | -0.01976 | 0.0035418 | 0.057059 | 0.059637 | 0.0037897 | -0.0064258 | -0.0043046 | -0.0084228 | 0.0045865 | 0.064638 | 0.060558 | -0.0062507 | 0.020546 | -0.0051205 | -0.018311 | 59.9579 | -61.5509 | 60.1135 | -61.3174 | -61.7661 | -61.7752 | 0.041199 | 59.9304 | -61.6013 | 60.0494 | -61.4868 | -61.6608 | -61.6745 | 0.036621 | -0.073242 | 0.082397 | 0.27008 | -0.18768 | -0.17853 | -0.22431 | -0.21515 | -0.013733 | -0.10071 | 0.01831 | 0.10071 | -0.086976 | -0.073243 | -0.073243 | -0.05951 | 0.23346 | 121.6644 | 0.11444 | 121.6507 | 121.5088 | 121.5317 | 121.5454 | 121.5179 | -121.582 | -121.6324 | 121.701 | 121.637 | 61.5692 | 61.6287
669.3906 | 121.7789 | -61.4914 | 60.0952 | -0.012131 | 0.001833 | 0.056418 | 0.055792 | -0.0015509 | -0.0079212 | -0.0028092 | -0.005371 | 0.0041593 | 0.066774 | 0.058635 | -0.010096 | 0.020974 | -0.0031979 | -0.027466 | 60.0082 | -61.5601 | 60.0815 | -61.3312 | -61.7615 | -61.7889 | -0.009155 | 59.9762 | -61.5692 | 60.0632 | -61.4777 | -61.5967 | -61.6379 | -0.068665 | -0.086975 | -0.013733 | 0.16022 | -0.29755 | -0.27008 | -0.22888 | -0.20142 | -0.07782 | -0.11902 | -0.032044 | 0.013733 | -0.14648 | -0.10529 | -0.068664 | -0.027466 | 0.22888 | 121.6415 | 0.091553 | 121.6324 | 121.5683 | 121.5454 | 121.4996 | 121.4676 | -121.6553 | -121.6644 | 121.5729 | 121.5546 | 61.4639 | 61.4822
671.0781 | 121.8201 | -61.5143 | 60.022 | -0.012131 | 0.00076478 | 0.0577 | 0.054937 | -0.00026906 | -0.0081348 | -0.001741 | -0.0084228 | 0.0022367 | 0.064424 | 0.053935 | -0.010096 | 0.021401 | -0.0021299 | -0.07782 | 59.9075 | -61.5921 | 60.0998 | -61.3083 | -61.7661 | -61.7615 | 0.009155 | 59.8663 | -61.6013 | 60.0632 | -61.4639 | -61.5784 | -61.6562 | -0.07782 | -0.11444 | 0.077819 | 0.20599 | -0.24719 | -0.25177 | -0.16937 | -0.17395 | -0.086975 | -0.15564 | 0.041198 | 0.050354 | -0.14191 | -0.064087 | -0.054932 | 0.022888 | 0.28381 | 121.6919 | 0.13733 | 121.6644 | 121.4996 | 121.4676 | 121.4218 | 121.3806 | -121.6141 | -121.6232 | 121.6141 | 121.5775 | 61.4365 | 61.5234
672.8438 | 121.756 | -61.5921 | 60.0266 | -0.012131 | 0.0050372 | 0.059409 | 0.055578 | 0.0012261 | -0.005144 | -0.0011002 | -0.005371 | 0.0050137 | 0.066133 | 0.056713 | -0.0062507 | 0.020333 | -0.0055479 | -0.032043 | 59.9716 | -61.5738 | 60.0769 | -61.3358 | -61.7981 | -61.8164 | 0.004578 | 59.8984 | -61.6333 | 60.0174 | -61.5234 | -61.6882 | -61.7065 | 0.01831 | -0.054931 | 0.050354 | 0.25635 | -0.2243 | -0.20599 | -0.24261 | -0.2243 | -0.041199 | -0.12817 | -0.009155 | 0.068665 | -0.11444 | -0.09613 | -0.073242 | -0.054931 | 0.23804 | 121.6507 | 0.10986 | 121.6507 | 121.5454 | 121.5317 | 121.5637 | 121.4905 | -121.6003 | -121.6599 | 121.669 | 121.6095 | 61.5601 | 61.5967
674.5469 | 121.8475 | -61.5463 | 59.9808 | -0.0045011 | 0.0014056 | 0.057272 | 0.056006 | 0.0027215 | -0.0070666 | -0.0015274 | -0.005371 | 0.0026639 | 0.064852 | 0.053722 | -0.0075323 | 0.021828 | 6.346e-06 | -0.09613 | 59.9304 | -61.6333 | 60.0403 | -61.3449 | -61.8073 | -61.7935 | 0.009155 | 59.8663 | -61.615 | 60.0906 | -61.4731 | -61.5967 | -61.6287 | -0.086975 | -0.050354 | 0.059509 | 0.20142 | -0.24719 | -0.26093 | -0.16022 | -0.17395 | -0.068664 | -0.11444 | 0.10986 | 0.073243 | -0.082397 | -0.050354 | -0.013733 | 0.01831 | 0.28839 | 121.6736 | 0.14191 | 121.7056 | 121.5637 | 121.4813 | 121.4767 | 121.4127 | -121.6141 | -121.5958 | 121.5866 | 121.637 | 61.4502 | 61.5555
676.2969 | 121.7834 | -61.5372 | 60.0861 | -0.012131 | 0.001833 | 0.055563 | 0.056433 | 0.0020807 | -0.006853 | -0.0011002 | -0.0023192 | 0.0026639 | 0.066347 | 0.059703 | -0.0077459 | 0.022042 | -0.0051205 | -0.013733 | 59.9762 | -61.5646 | 60.0952 | -61.3037 | -61.7523 | -61.7615 | 0.045776 | 59.9579 | -61.5692 | 60.0815 | -61.4594 | -61.6013 | -61.6562 | -0.027466 | -0.10986 | 0.009155 | 0.23346 | -0.2243 | -0.21515 | -0.19684 | -0.18768 | -0.032044 | -0.12817 | -0.004578 | 0.077819 | -0.11902 | -0.064087 | -0.086975 | -0.032043 | 0.26093 | 121.6599 | 0.10986 | 121.6507 | 121.5408 | 121.5271 | 121.5134 | 121.4951 | -121.6507 | -121.6553 | 121.6324 | 121.6187 | 61.5234 | 61.5829
678.0469 | 121.8063 | -61.5326 | 60.054 | -0.012131 | 0.0024738 | 0.059195 | 0.056219 | -0.0013373 | -0.0092028 | -0.0011002 | -0.0023192 | 0.0028775 | 0.066988 | 0.056072 | -0.0066779 | 0.021187 | -0.0027707 | -0.004578 | 59.9991 | -61.5967 | 60.1044 | -61.2854 | -61.7386 | -61.7706 | 0.059509 | 59.9121 | -61.5829 | 60.0769 | -61.4639 | -61.6058 | -61.6608 | -0.064087 | -0.054932 | 0.050354 | 0.24719 | -0.23804 | -0.20599 | -0.17395 | -0.14191 | -0.050354 | -0.14191 | 0.022888 | 0.068665 | -0.12817 | -0.073242 | -0.07782 | -0.022888 | 0.31128 | 121.7011 | 0.11902 | 121.6599 | 121.5958 | 121.4951 | 121.5317 | 121.4447 | -121.6507 | -121.637 | 121.637 | 121.6095 | 61.528 | 61.5921
679.7344 | 121.8658 | -61.5326 | 59.9762 | -0.0045011 | 0.0033282 | 0.06069 | 0.054083 | -0.00091006 | -0.0079212 | -0.0015274 | -0.005371 | 0.0022367 | 0.064211 | 0.055004 | -0.0086005 | 0.023964 | -0.0014891 | -0.10529 | 59.9258 | -61.6196 | 60.0632 | -61.3358 | -61.8073 | -61.7935 | 0.013733 | 59.8297 | -61.6196 | 60.0769 | -61.4548 | -61.5921 | -61.6287 | -0.086975 | -0.050354 | 0.086975 | 0.19684 | -0.26093 | -0.27466 | -0.17395 | -0.18768 | -0.086975 | -0.14648 | 0.10071 | 0.07782 | -0.09613 | -0.059509 | -0.009155 | 0.027466 | 0.28381 | 121.6827 | 0.16479 | 121.6965 | 121.5454 | 121.4493 | 121.4584 | 121.3623 | -121.5958 | -121.5958 | 121.5958 | 121.6095 | 61.4273 | 61.5463
681.4844 | 121.7972 | -61.5051 | 60.0723 | -0.012131 | 0.0014056 | 0.056204 | 0.054724 | -5.5462e-05 | -0.010485 | -0.0045182 | -0.005371 | 0.0015957 | 0.066133 | 0.056072 | -0.0086005 | 0.020974 | -0.0010617 | -0.022888 | 59.9899 | -61.5509 | 60.0952 | -61.322 | -61.7386 | -61.7523 | 0.018311 | 59.9625 | -61.5555 | 60.0677 | -61.4548 | -61.6013 | -61.647 | -0.045776 | -0.082398 | 0.022888 | 0.18311 | -0.24719 | -0.23346 | -0.20142 | -0.18768 | -0.050354 | -0.10986 | -0.004578 | 0.050354 | -0.14191 | -0.09613 | -0.091553 | -0.045776 | 0.22888 | 121.6461 | 0.10071 | 121.6232 | 121.5408 | 121.5179 | 121.4951 | 121.4676 | -121.6232 | -121.6278 | 121.6003 | 121.5729 | 61.4822 | 61.5234
683.25 | 121.8521 | -61.4731 | 60.1089 | -0.01976 | 0.00055118 | 0.055563 | 0.054937 | 0.0027215 | -0.0089892 | -0.002382 | -0.005371 | 0.00010048 | 0.06592 | 0.055217 | -0.010096 | 0.021828 | -0.0038389 | 0.018311 | 59.9258 | -61.496 | 60.1959 | -61.1893 | -61.6562 | -61.6608 | 0.13275 | 59.903 | -61.5417 | 60.1364 | -61.3541 | -61.4914 | -61.5738 | -0.022889 | -0.18311 | 0.086975 | 0.28381 | -0.18768 | -0.18311 | -0.16479 | -0.16022 | -0.068665 | -0.20599 | 0.027466 | 0.11902 | -0.10071 | -0.018311 | -0.032044 | 0.050354 | 0.3067 | 121.6919 | 0.18768 | 121.6782 | 121.4218 | 121.4447 | 121.3989 | 121.376 | -121.6049 | -121.6507 | 121.669 | 121.6095 | 61.4914 | 61.6058
685.0156 | 121.8521 | -61.5372 | 60.0082 | -0.0045011 | 0.00076478 | 0.056845 | 0.054937 | 0.00037174 | -0.0077074 | -0.0030228 | -0.005371 | 0.0013821 | 0.065493 | 0.051799 | -0.011805 | 0.019905 | -0.0021299 | -0.091553 | 59.8892 | -61.5555 | 60.0861 | -61.2991 | -61.7615 | -61.7386 | 0 | 59.8801 | -61.5738 | 60.0906 | -61.4319 | -61.5646 | -61.6333 | -0.018311 | -0.11902 | 0.07782 | 0.23804 | -0.20142 | -0.2243 | -0.1831 | -0.20599 | -0.036622 | -0.12817 | 0.082397 | 0.10529 | -0.096131 | -0.027466 | -0.059509 | 0.009156 | 0.25635 | 121.6415 | 0.14191 | 121.6644 | 121.4447 | 121.4539 | 121.4264 | 121.4172 | -121.5637 | -121.582 | 121.6232 | 121.6278 | 61.4456 | 61.5372
686.7812 | 121.8567 | -61.5555 | 59.9716 | -0.012131 | 0.0033282 | 0.056845 | 0.053656 | -0.0030463 | -0.0066394 | -0.0025956 | -0.0023192 | 0.00052768 | 0.066774 | 0.0471 | -0.012232 | 0.021614 | -0.0019163 | -0.068665 | 59.8618 | -61.6104 | 60.1181 | -61.2762 | -61.7477 | -61.7432 | 0.045776 | 59.8297 | -61.615 | 60.0815 | -61.4822 | -61.5921 | -61.6425 | -0.054932 | -0.10986 | 0.14648 | 0.27924 | -0.18768 | -0.19226 | -0.13275 | -0.13733 | -0.059509 | -0.14191 | 0.10986 | 0.073242 | -0.086975 | -0.036621 | -0.027466 | 0.022888 | 0.33417 | 121.7285 | 0.13275 | 121.6965 | 121.4722 | 121.4447 | 121.4172 | 121.3852 | -121.582 | -121.5866 | 121.6736 | 121.637 | 61.4868 | 61.6013
688.4844 | 121.875 | -61.5463 | 59.967 | -0.012131 | 0.0041828 | 0.058127 | 0.055578 | 0.0022943 | -0.0064258 | -0.0011002 | -0.005371 | 0.0013821 | 0.063997 | 0.051158 | -0.0094549 | 0.022255 | -0.0068295 | -0.07782 | 59.8526 | -61.6058 | 60.1181 | -61.2762 | -61.7523 | -61.7477 | 0.059509 | 59.8068 | -61.6013 | 60.0952 | -61.4365 | -61.5601 | -61.615 | -0.059509 | -0.11444 | 0.15106 | 0.27008 | -0.20142 | -0.20599 | -0.14191 | -0.14648 | -0.054931 | -0.16022 | 0.12817 | 0.10986 | -0.068664 | -0.013733 | -0.013733 | 0.041198 | 0.32959 | 121.7239 | 0.16479 | 121.6965 | 121.4584 | 121.4081 | 121.3989 | 121.3531 | -121.5729 | -121.5683 | 121.6644 | 121.6415 | 61.4685 | 61.6058
690.2344 | 121.7377 | -61.5143 | 60.1089 | -0.0045011 | 0.00076478 | 0.055777 | 0.055151 | -0.0017645 | -0.0087756 | -0.0011002 | -0.0084228 | 0.0022367 | 0.066347 | 0.055431 | -0.010523 | 0.023323 | -0.0014891 | -0.032043 | 60.0128 | -61.5601 | 60.0815 | -61.3266 | -61.7386 | -61.7661 | 0.004578 | 59.9854 | -61.5509 | 60.0494 | -61.4868 | -61.615 | -61.6745 | -0.045777 | -0.096131 | -0.027466 | 0.18768 | -0.25177 | -0.2243 | -0.20599 | -0.17853 | -0.036621 | -0.1236 | -0.05951 | 0.027466 | -0.16022 | -0.10071 | -0.1236 | -0.064087 | 0.23346 | 121.6415 | 0.064087 | 121.6003 | 121.5729 | 121.5363 | 121.5271 | 121.4996 | -121.669 | -121.6599 | 121.5958 | 121.5637 | 61.4822 | 61.5189
691.9844 | 121.7972 | -61.5143 | 60.0677 | -0.02739 | 0.0048236 | 0.058127 | 0.05686 | 0.0044305 | -0.0077074 | -0.0021682 | -0.0084228 | 0.0011685 | 0.066988 | 0.060131 | -0.0083869 | 0.02076 | -0.0042661 | 0 | 59.9716 | -61.5738 | 60.1135 | -61.2808 | -61.7523 | -61.7752 | 0.068665 | 59.9213 | -61.5875 | 60.0861 | -61.4685 | -61.5829 | -61.6425 | -0.05951 | -0.09613 | 0.045776 | 0.23346 | -0.26093 | -0.23804 | -0.20142 | -0.17853 | -0.073242 | -0.14648 | 0.018311 | 0.045776 | -0.12817 | -0.068665 | -0.054932 | 0.004577 | 0.29297 | 121.6873 | 0.11902 | 121.6736 | 121.5454 | 121.5088 | 121.4859 | 121.4355 | -121.6415 | -121.6553 | 121.6278 | 121.6003 | 61.5143 | 61.5829
693.7344 | 121.8658 | -61.5189 | 60.0449 | -0.012131 | 0.001192 | 0.057272 | 0.053015 | -0.0013373 | -0.0057848 | -0.0032364 | -0.0023192 | 0.00052768 | 0.065065 | 0.051372 | -0.0090277 | 0.021187 | -0.0014891 | -0.091553 | 59.8984 | -61.5692 | 60.0998 | -61.3037 | -61.734 | -61.7386 | 0.009155 | 59.8801 | -61.5921 | 60.1135 | -61.4182 | -61.5463 | -61.6013 | -0.050354 | -0.14648 | 0.054931 | 0.21515 | -0.21973 | -0.21515 | -0.16937 | -0.16479 | -0.073242 | -0.16479 | 0.068664 | 0.10071 | -0.082397 | -0.027466 | -0.009155 | 0.045776 | 0.2655 | 121.669 | 0.17395 | 121.7056 | 121.4676 | 121.4722 | 121.4172 | 121.3989 | -121.6141 | -121.637 | 121.6187 | 121.6324 | 61.4273 | 61.528
695.4219 | 121.8613 | -61.5372 | 59.9808 | -0.012131 | 0.00461 | 0.058127 | 0.054083 | 0.0033623 | -0.0047168 | -0.0038772 | -0.0084228 | -0.0016085 | 0.066133 | 0.055004 | -0.0098823 | 0.021828 | -0.0012753 | -0.073242 | 59.848 | -61.5967 | 60.1273 | -61.2762 | -61.7615 | -61.734 | 0.050354 | 59.8297 | -61.6104 | 60.0998 | -61.4365 | -61.5784 | -61.6241 | -0.05951 | -0.13275 | 0.14648 | 0.26093 | -0.19684 | -0.2243 | -0.13733 | -0.16479 | -0.073243 | -0.15106 | 0.11902 | 0.10071 | -0.086976 | -0.041199 | -0.013733 | 0.032044 | 0.32043 | 121.7239 | 0.17395 | 121.7102 | 121.4447 | 121.4401 | 121.3852 | 121.3669 | -121.5775 | -121.5912 | 121.6644 | 121.637 | 61.4639 | 61.5875
697.1719 | 121.7331 | -61.5738 | 60.0266 | -0.0045011 | 0.00461 | 0.058981 | 0.057715 | -0.0015509 | -0.005144 | -0.0011002 | -0.0023192 | 0.0048001 | 0.064424 | 0.064617 | -0.0094549 | 0.019905 | -0.0029843 | -0.059509 | 59.9533 | -61.6013 | 60.054 | -61.3815 | -61.8393 | -61.8347 | -0.036621 | 59.903 | -61.6058 | 60.0082 | -61.5509 | -61.702 | -61.7249 | -0.027465 | -0.073242 | 0.027466 | 0.19226 | -0.26093 | -0.2655 | -0.23346 | -0.23804 | -0.032043 | -0.1236 | -0.01831 | 0.022889 | -0.15106 | -0.12817 | -0.11902 | -0.09613 | 0.21973 | 121.6553 | 0.054932 | 121.6141 | 121.5546 | 121.5088 | 121.5271 | 121.4767 | -121.6278 | -121.6324 | 121.6278 | 121.582 | 61.5143 | 61.5372
698.9062 | 121.8658 | -61.5555 | 59.9533 | -0.0045011 | 0.0037556 | 0.059622 | 0.056433 | -0.0021919 | -0.0070666 | -0.0043046 | -0.0023192 | 0.00095488 | 0.064638 | 0.056072 | -0.0090277 | 0.019265 | -0.0025571 | -0.045776 | 59.8846 | -61.5646 | 60.1135 | -61.2946 | -61.7615 | -61.7477 | 0.036621 | 59.816 | -61.6241 | 60.0998 | -61.4502 | -61.5829 | -61.6196 | -0.009155 | -0.068664 | 0.16022 | 0.26093 | -0.19226 | -0.20599 | -0.18311 | -0.19684 | -0.068665 | -0.13733 | 0.14648 | 0.10529 | -0.064087 | -0.027466 | 0.004578 | 0.041199 | 0.27008 | 121.6782 | 0.17395 | 121.7239 | 121.4493 | 121.4401 | 121.4401 | 121.3715 | -121.5179 | -121.5775 | 121.669 | 121.6553 | 61.5097 | 61.5921
700.6562 | 121.756 | -61.5509 | 60.0449 | -0.01976 | 0.0048236 | 0.0577 | 0.057074 | 0.0025079 | -0.0053576 | -0.000673 | -0.005371 | 0.0026639 | 0.067415 | 0.060558 | -0.0090277 | 0.019692 | -0.0038389 | -0.018311 | 59.9533 | -61.5967 | 60.0906 | -61.3312 | -61.7981 | -61.8027 | 0.027466 | 59.9167 | -61.6058 | 60.0311 | -61.5189 | -61.6837 | -61.7065 | -0.045777 | -0.091553 | 0.045776 | 0.21973 | -0.25177 | -0.24719 | -0.20599 | -0.20142 | -0.054932 | -0.12817 | -0.013733 | 0.032043 | -0.15564 | -0.13275 | -0.10071 | -0.07782 | 0.2655 | 121.6873 | 0.086975 | 121.637 | 121.55 | 121.5225 | 121.5042 | 121.4676 | -121.6415 | -121.6507 | 121.6415 | 121.582 | 61.5326 | 61.5784
702.3594 | 121.8704 | -61.4868 | 60.0723 | -0.0045011 | 0.0016192 | 0.0577 | 0.054724 | 0.0027215 | -0.006853 | -0.0013138 | -0.005371 | -0.00032692 | 0.066561 | 0.053295 | -0.010096 | 0.021401 | 0.00021995 | 0.027466 | 59.9304 | -61.5326 | 60.2097 | -61.1847 | -61.6241 | -61.647 | 0.14191 | 59.903 | -61.5326 | 60.1547 | -61.3449 | -61.4914 | -61.5509 | -0.045777 | -0.14191 | 0.13733 | 0.30212 | -0.16022 | -0.13733 | -0.11444 | -0.091553 | -0.045777 | -0.16937 | 0.082397 | 0.14191 | -0.064087 | -0.004578 | -0.01831 | 0.041199 | 0.3479 | 121.7422 | 0.18768 | 121.6873 | 121.463 | 121.4355 | 121.4172 | 121.3898 | -121.6049 | -121.6049 | 121.6965 | 121.6415 | 61.5143 | 61.6287
704.1094 | 121.8018 | -61.5509 | 60.0632 | -0.012131 | 0.0014056 | 0.056631 | 0.055792 | 0.0029351 | -0.0074938 | -0.000673 | -0.0084228 | 0.0043729 | 0.066347 | 0.056499 | -0.0094549 | 0.020546 | -0.0053343 | 0.004578 | 59.9716 | -61.5875 | 60.0952 | -61.29 | -61.7615 | -61.7615 | 0.068665 | 59.9304 | -61.6013 | 60.0815 | -61.4548 | -61.6013 | -61.647 | -0.036621 | -0.091552 | 0.032044 | 0.26093 | -0.21057 | -0.21057 | -0.17395 | -0.17395 | -0.050354 | -0.13275 | 0.018311 | 0.09613 | -0.096131 | -0.050354 | -0.045777 | 0 | 0.29755 | 121.6827 | 0.14648 | 121.6827 | 121.5591 | 121.5317 | 121.5225 | 121.4813 | -121.6507 | -121.6644 | 121.6461 | 121.6324 | 61.5555 | 61.6196
705.7969 | 121.7468 | -61.5143 | 60.1089 | -0.0045011 | 0.00055118 | 0.055991 | 0.052801 | -0.0013373 | -0.006853 | -0.0013138 | -0.005371 | 0.0035183 | 0.068483 | 0.055858 | -0.0090277 | 0.021401 | -0.00042085 | -0.041199 | 59.9991 | -61.5829 | 60.0769 | -61.3083 | -61.7523 | -61.7661 | 0.009155 | 59.9854 | -61.5646 | 60.0449 | -61.4685 | -61.6058 | -61.6653 | -0.068665 | -0.10986 | -0.032044 | 0.20599 | -0.25177 | -0.23804 | -0.18311 | -0.16937 | -0.050354 | -0.1236 | -0.064087 | 0.045776 | -0.15106 | -0.091553 | -0.10071 | -0.041199 | 0.27466 | 121.6599 | 0.09613 | 121.6095 | 121.582 | 121.55 | 121.5134 | 121.4996 | -121.6919 | -121.6736 | 121.5912 | 121.5591 | 61.4731 | 61.5234
707.5625 | 121.8292 | -61.5692 | 60.0082 | -0.012131 | 0.0014056 | 0.055136 | 0.055365 | -0.0028327 | -0.005144 | -0.0021682 | -0.005371 | 0.0020231 | 0.066133 | 0.048381 | -0.011164 | 0.02311 | -0.00020725 | -0.086975 | 59.8892 | -61.5646 | 60.0861 | -61.2946 | -61.7615 | -61.734 | 0 | 59.8572 | -61.5967 | 60.0815 | -61.4594 | -61.5784 | -61.6379 | 0.004578 | -0.11902 | 0.07782 | 0.27466 | -0.16479 | -0.19226 | -0.16937 | -0.19684 | -0.027466 | -0.15106 | 0.073242 | 0.10986 | -0.068664 | -0.009155 | -0.041198 | 0.018311 | 0.27008 | 121.6507 | 0.13733 | 121.6782 | 121.4539 | 121.4539 | 121.4584 | 121.4264 | -121.5729 | -121.6049 | 121.6553 | 121.6507 | 61.4822 | 61.5692
709.3125 | 121.7422 | -61.5829 | 60.0174 | -0.0045011 | 0.0056782 | 0.056418 | 0.057287 | 0.0027215 | -0.0070666 | 0.001036 | -0.005371 | 0.0041593 | 0.067202 | 0.059276 | -0.0088141 | 0.020974 | -0.00042085 | -0.09613 | 59.9258 | -61.6196 | 59.9808 | -61.4456 | -61.8942 | -61.8851 | -0.086975 | 59.8892 | -61.6287 | 59.9899 | -61.5692 | -61.7249 | -61.7523 | -0.036621 | -0.091553 | -0.036621 | 0.13733 | -0.30212 | -0.31128 | -0.2655 | -0.27466 | -0.045776 | -0.12817 | -0.027466 | 0.013733 | -0.16937 | -0.14191 | -0.1236 | -0.096131 | 0.17395 | 121.6003 | 0.059509 | 121.6187 | 121.5454 | 121.5179 | 121.5088 | 121.4722 | -121.637 | -121.6461 | 121.5637 | 121.5729 | 61.4868 | 61.496
711.0781 | 121.7422 | -61.5143 | 60.1089 | -0.012131 | 0.0020466 | 0.057272 | 0.054937 | -0.0026191 | -0.0083484 | -0.000673 | -0.005371 | 0.0015957 | 0.066988 | 0.059917 | -0.0094549 | 0.022042 | -0.00042085 | -0.004578 | 59.967 | -61.5417 | 60.1044 | -61.2946 | -61.734 | -61.7294 | 0.027466 | 59.9625 | -61.5417 | 60.0677 | -61.4731 | -61.5784 | -61.6653 | -0.027466 | -0.14191 | -0.004578 | 0.21973 | -0.21515 | -0.21973 | -0.18768 | -0.19226 | -0.027466 | -0.14648 | -0.041199 | 0.041199 | -0.15106 | -0.064087 | -0.1236 | -0.036621 | 0.24719 | 121.6461 | 0.068665 | 121.6095 | 121.5088 | 121.5042 | 121.4813 | 121.4767 | -121.6507 | -121.6507 | 121.6187 | 121.582 | 61.5097 | 61.5417
712.8438 | 121.8201 | -61.5875 | 59.967 | -0.0045011 | 0.0067462 | 0.057913 | 0.055365 | -0.0015509 | -0.0098438 | -0.001741 | -0.0023192 | 0.0013821 | 0.062929 | 0.056926 | -0.0098823 | 0.024819 | -0.0027707 | -0.11902 | 59.935 | -61.615 | 60.0128 | -61.3907 | -61.8576 | -61.8484 | -0.041199 | 59.8663 | -61.6241 | 60.0357 | -61.5051 | -61.6562 | -61.6745 | -0.027466 | -0.032043 | 0.045776 | 0.19684 | -0.26093 | -0.27008 | -0.23346 | -0.24262 | -0.036622 | -0.10071 | 0.068665 | 0.082397 | -0.086976 | -0.068665 | -0.050354 | -0.032043 | 0.2243 | 121.6278 | 0.11902 | 121.6599 | 121.55 | 121.4905 | 121.5225 | 121.4539 | -121.582 | -121.5912 | 121.6003 | 121.6232 | 61.4685 | 61.5463
714.5312 | 121.8201 | -61.4822 | 60.0861 | -0.0045011 | 0.00033758 | 0.057272 | 0.051733 | -0.0015509 | -0.0079212 | -0.0002456 | -0.005371 | -0.00096772 | 0.064424 | 0.057994 | -0.01095 | 0.022042 | 0.0021425 | 0.022888 | 59.9487 | -61.5326 | 60.1776 | -61.2076 | -61.6425 | -61.6653 | 0.10529 | 59.935 | -61.5326 | 60.1089 | -61.3907 | -61.5234 | -61.6058 | -0.050354 | -0.13733 | 0.091552 | 0.27466 | -0.1831 | -0.16022 | -0.13275 | -0.10986 | -0.050354 | -0.15106 | 0.022888 | 0.091553 | -0.1236 | -0.041198 | -0.073242 | 0.009156 | 0.32501 | 121.7102 | 0.14191 | 121.6415 | 121.4813 | 121.4676 | 121.431 | 121.4172 | -121.6187 | -121.6187 | 121.6599 | 121.5912 | 61.5051 | 61.5875
716.2969 | 121.7514 | -61.6058 | 60.0174 | -0.0045011 | 0.0048236 | 0.057486 | 0.056219 | 0.0014397 | -0.0079212 | -0.0013138 | -0.005371 | 0.0024503 | 0.06592 | 0.060558 | -0.0077459 | 0.020119 | 0.0027835 | -0.11902 | 59.9304 | -61.615 | 60.0037 | -61.441 | -61.8805 | -61.8713 | -0.10071 | 59.8938 | -61.6425 | 59.9808 | -61.5738 | -61.734 | -61.734 | -0.009155 | -0.086975 | -0.013733 | 0.16479 | -0.2655 | -0.27466 | -0.25635 | -0.2655 | -0.036621 | -0.1236 | -0.036621 | 0.032043 | -0.12817 | -0.12817 | -0.091553 | -0.091553 | 0.17395 | 121.6187 | 0.068664 | 121.6232 | 121.5454 | 121.5363 | 121.5363 | 121.4996 | -121.6324 | -121.6599 | 121.6095 | 121.5866 | 61.4868 | 61.5051
718 | 121.8567 | -61.5372 | 59.9762 | -0.01976 | 0.0033282 | 0.057913 | 0.055151 | 0.00058534 | -0.006853 | -0.002382 | -0.0023192 | -0.00011332 | 0.068056 | 0.049663 | -0.0088141 | 0.020119 | -0.0029843 | -0.068665 | 59.8526 | -61.6013 | 60.1089 | -61.2671 | -61.7386 | -61.7294 | 0.064087 | 59.8434 | -61.6013 | 60.1089 | -61.441 | -61.5875 | -61.6379 | -0.064087 | -0.1236 | 0.13275 | 0.27008 | -0.19226 | -0.20142 | -0.12817 | -0.13733 | -0.064087 | -0.13275 | 0.13275 | 0.09613 | -0.10071 | -0.050354 | -0.036621 | 0.013733 | 0.33417 | 121.7102 | 0.16022 | 121.7102 | 121.4539 | 121.4447 | 121.3898 | 121.3806 | -121.5775 | -121.5775 | 121.6461 | 121.6461 | 61.4685 | 61.6013
719.75 | 121.7422 | -61.5051 | 60.0861 | -0.012131 | -0.00094422 | 0.055991 | 0.054724 | -0.0043281 | -0.0062122 | -0.0015274 | -0.0023192 | 0.0026639 | 0.068056 | 0.056926 | -0.010737 | 0.022042 | 6.346e-06 | -0.013733 | 59.9716 | -61.5646 | 60.1044 | -61.3174 | -61.7386 | -61.7523 | 0.009155 | 59.967 | -61.5509 | 60.0586 | -61.4502 | -61.5967 | -61.6837 | -0.059509 | -0.11444 | 0.01831 | 0.18768 | -0.24719 | -0.23346 | -0.18768 | -0.17395 | -0.045776 | -0.11902 | -0.027466 | 0.054932 | -0.17853 | -0.091553 | -0.13275 | -0.045777 | 0.24719 | 121.669 | 0.10071 | 121.6095 | 121.5363 | 121.5179 | 121.4767 | 121.4722 | -121.6507 | -121.637 | 121.6095 | 121.5637 | 61.4914 | 61.5143
721.5 | 121.7926 | -61.5463 | 60.022 | -0.01976 | 0.0033282 | 0.056631 | 0.05686 | 0.00037174 | -0.0070666 | -0.0021682 | -0.0023192 | 0.0054409 | 0.066988 | 0.054149 | -0.0083869 | 0.020119 | -0.0055479 | -0.004578 | 59.9762 | -61.5601 | 60.1044 | -61.29 | -61.7477 | -61.7661 | 0.050354 | 59.9442 | -61.5692 | 60.0815 | -61.4548 | -61.6013 | -61.6425 | -0.013733 | -0.045777 | 0.082397 | 0.25635 | -0.21973 | -0.20142 | -0.20599 | -0.18768 | -0.022888 | -0.07782 | 0.059509 | 0.091553 | -0.09613 | -0.054931 | -0.073242 | -0.032043 | 0.27008 | 121.6644 | 0.11444 | 121.6507 | 121.5363 | 121.5134 | 121.5225 | 121.4905 | -121.582 | -121.5912 | 121.6507 | 121.6278 | 61.5417 | 61.5967
723.2656 | 121.8338 | -61.5189 | 60.0082 | -0.012131 | 0.0014056 | 0.057486 | 0.053656 | -0.0043281 | -0.0059986 | -3.1996e-05 | -0.005371 | 0.00031408 | 0.067842 | 0.05479 | -0.010096 | 0.022469 | -0.0027707 | -0.10071 | 59.9121 | -61.5463 | 60.0906 | -61.29 | -61.7661 | -61.734 | -0.004578 | 59.8892 | -61.5967 | 60.0815 | -61.4319 | -61.5509 | -61.6241 | -0.027466 | -0.096131 | 0.082397 | 0.22888 | -0.21515 | -0.24719 | -0.18768 | -0.21973 | -0.07782 | -0.11902 | 0.073242 | 0.086975 | -0.10529 | -0.032043 | -0.027466 | 0.045777 | 0.25635 | 121.637 | 0.16479 | 121.6782 | 121.4584 | 121.4859 | 121.431 | 121.4081 | -121.5546 | -121.6049 | 121.6095 | 121.6003 | 61.4182 | 61.5143
724.9531 | 121.8796 | -61.5692 | 59.9487 | -0.012131 | 0.00461 | 0.057913 | 0.054937 | 0.00015814 | -0.0077074 | -0.0015274 | -0.0023192 | 0.00095488 | 0.064424 | 0.056072 | -0.010737 | 0.020974 | -0.0064023 | -0.059509 | 59.8892 | -61.5829 | 60.1135 | -61.2808 | -61.7706 | -61.7523 | 0.036621 | 59.8251 | -61.6241 | 60.0861 | -61.4502 | -61.5829 | -61.615 | -0.013733 | -0.059509 | 0.1648 | 0.28839 | -0.1831 | -0.20142 | -0.16937 | -0.18768 | -0.054932 | -0.1236 | 0.13733 | 0.11902 | -0.045776 | -0.013733 | 0.009156 | 0.041199 | 0.30212 | 121.6965 | 0.17395 | 121.7102 | 121.4722 | 121.4493 | 121.4584 | 121.3943 | -121.5317 | -121.5729 | 121.6827 | 121.6553 | 61.5097 | 61.6058
726.7031 | 121.7972 | -61.5463 | 60.0632 | 0.0031279 | 0.001192 | 0.057272 | 0.054083 | -0.0013373 | -0.0081348 | -0.0032364 | -0.005371 | 0.0026639 | 0.066774 | 0.058422 | -0.0096685 | 0.020546 | -0.0031979 | -0.009155 | 59.9991 | -61.5555 | 60.1089 | -61.3037 | -61.734 | -61.7706 | 0.036621 | 59.9625 | -61.5463 | 60.0723 | -61.4594 | -61.5967 | -61.6425 | -0.009155 | -0.064087 | 0.045777 | 0.24262 | -0.2243 | -0.18768 | -0.21515 | -0.17853 | 0 | -0.10071 | 0.009156 | 0.086975 | -0.09613 | -0.050354 | -0.09613 | -0.050354 | 0.25177 | 121.6644 | 0.086975 | 121.6187 | 121.5546 | 121.5088 | 121.5454 | 121.5088 | -121.6187 | -121.6095 | 121.6553 | 121.6187 | 61.5372 | 61.5829
728.4531 | 121.8246 | -61.5326 | 59.9945 | -0.01976 | 0.00097838 | 0.056418 | 0.055578 | 0.0022943 | -0.0081348 | -0.00345 | -0.0023192 | -0.00075412 | 0.065279 | 0.059703 | -0.0094549 | 0.022255 | -0.0031979 | -0.09613 | 59.8938 | -61.5875 | 60.0952 | -61.29 | -61.7706 | -61.7523 | 0.009155 | 59.848 | -61.615 | 60.0769 | -61.4685 | -61.5784 | -61.6379 | -0.054931 | -0.10071 | 0.10071 | 0.24262 | -0.21973 | -0.23804 | -0.16479 | -0.18311 | -0.082397 | -0.14648 | 0.082397 | 0.064087 | -0.10529 | -0.045776 | -0.022888 | 0.036621 | 0.29755 | 121.6827 | 0.14648 | 121.6919 | 121.4813 | 121.463 | 121.4264 | 121.3806 | -121.582 | -121.6095 | 121.6278 | 121.6095 | 61.4365 | 61.5417
730.1406 | 121.7743 | -61.5646 | 60.022 | -0.012131 | 0.0041828 | 0.057913 | 0.057501 | 0.0016535 | -0.005144 | -0.0021682 | -0.011475 | 0.0026639 | 0.066133 | 0.056713 | -0.0086005 | 0.021401 | 0.00021995 | -0.1236 | 59.9396 | -61.6104 | 60.0128 | -61.3998 | -61.8713 | -61.8576 | -0.082397 | 59.8938 | -61.6241 | 60.0174 | -61.5555 | -61.7065 | -61.7157 | -0.045777 | -0.082398 | -0.009156 | 0.16479 | -0.29297 | -0.3067 | -0.24719 | -0.26093 | -0.05951 | -0.12817 | -0.004578 | 0.009155 | -0.15106 | -0.14191 | -0.091552 | -0.082397 | 0.21057 | 121.6232 | 0.068665 | 121.6415 | 121.55 | 121.5179 | 121.5042 | 121.4584 | -121.6324 | -121.6461 | 121.5775 | 121.582 | 61.441 | 61.4822
731.8906 | 121.8887 | -61.5005 | 60.0586 | -0.01976 | 0.00012398 | 0.058127 | 0.053442 | -0.0028327 | -0.0089892 | -0.0038772 | -0.011475 | 0.0020231 | 0.065493 | 0.048381 | -0.01031 | 0.02076 | -0.0038389 | -0.050354 | 59.903 | -61.5555 | 60.1547 | -61.235 | -61.6699 | -61.6837 | 0.082397 | 59.903 | -61.5509 | 60.1593 | -61.3541 | -61.4822 | -61.5692 | -0.054932 | -0.15564 | 0.09613 | 0.2655 | -0.18311 | -0.16937 | -0.12817 | -0.11444 | -0.050354 | -0.15564 | 0.10071 | 0.14648 | -0.068665 | 0.01831 | -0.018311 | 0.068664 | 0.32044 | 121.7102 | 0.19684 | 121.7102 | 121.4584 | 121.4539 | 121.4035 | 121.4035 | -121.6141 | -121.6095 | 121.6553 | 121.6599 | 61.4502 | 61.5829
733.6562 | 121.7422 | -61.5326 | 60.1089 | -0.012131 | -8.9824e-05 | 0.055777 | 0.054937 | -0.00069646 | -0.0066394 | -0.002382 | -0.005371 | 0.0020231 | 0.067415 | 0.054576 | -0.01095 | 0.021187 | -0.0038389 | 0.013733 | 59.9899 | -61.5463 | 60.1089 | -61.29 | -61.702 | -61.7249 | 0.013733 | 59.9579 | -61.5509 | 60.0494 | -61.4639 | -61.6058 | -61.6837 | -0.013733 | -0.11902 | 0 | 0.24262 | -0.19226 | -0.16937 | -0.17853 | -0.15564 | -0.01831 | -0.15106 | -0.05951 | 0.068665 | -0.15106 | -0.073242 | -0.13275 | -0.054932 | 0.25635 | 121.6553 | 0.086975 | 121.6003 | 121.5363 | 121.5088 | 121.5225 | 121.4905 | -121.6553 | -121.6599 | 121.6415 | 121.582 | 61.5463 | 61.5463
735.3906 | 121.7422 | -61.5005 | 60.0998 | -0.012131 | 0.0014056 | 0.057272 | 0.053656 | -0.00026906 | -0.0077074 | -0.0015274 | -0.0084228 | 0.0028775 | 0.065706 | 0.06248 | -0.0098823 | 0.019265 | -0.0029843 | 0.009155 | 59.9762 | -61.5143 | 60.1135 | -61.2762 | -61.7386 | -61.7294 | 0.032043 | 59.9304 | -61.5417 | 60.0449 | -61.4502 | -61.5967 | -61.6745 | -0.013733 | -0.1236 | 0.013733 | 0.2243 | -0.22888 | -0.23804 | -0.21515 | -0.2243 | -0.041199 | -0.16937 | -0.054931 | 0.050354 | -0.17395 | -0.096131 | -0.13275 | -0.054932 | 0.23804 | 121.6278 | 0.091553 | 121.5866 | 121.4905 | 121.4722 | 121.4767 | 121.431 | -121.6141 | -121.6415 | 121.6141 | 121.5454 | 61.5097 | 61.5326
737.0781 | 121.9025 | -61.4777 | 60.0494 | -0.0045011 | 0.00033758 | 0.057486 | 0.053228 | -0.0068915 | -0.0059986 | -0.0036636 | 0.00073235 | 0.0024503 | 0.066133 | 0.057567 | -0.011164 | 0.021614 | -0.0042661 | -0.013733 | 59.935 | -61.5234 | 60.1776 | -61.1847 | -61.647 | -61.6608 | 0.14648 | 59.8984 | -61.5463 | 60.1868 | -61.3266 | -61.4822 | -61.5509 | -0.045776 | -0.11444 | 0.12817 | 0.29297 | -0.18311 | -0.16937 | -0.13733 | -0.1236 | -0.068665 | -0.15106 | 0.13733 | 0.15106 | -0.073242 | -0.004578 | -0.004577 | 0.064087 | 0.33875 | 121.701 | 0.21973 | 121.7331 | 121.4584 | 121.4447 | 121.4127 | 121.376 | -121.5729 | -121.5958 | 121.6553 | 121.6644 | 61.4639 | 61.6241
738.8438 | 121.8292 | -61.5601 | 59.9991 | -0.012131 | 0.00097838 | 0.056845 | 0.054297 | 0.00037174 | -0.006853 | -0.0045182 | -0.0084228 | 0.0013821 | 0.066133 | 0.055004 | -0.012019 | 0.021401 | 0.00043375 | -0.082397 | 59.8984 | -61.5784 | 60.0998 | -61.3037 | -61.7569 | -61.7432 | -0.022888 | 59.8709 | -61.5921 | 60.0769 | -61.4548 | -61.5829 | -61.6516 | -0.01831 | -0.10071 | 0.10071 | 0.25635 | -0.1831 | -0.19684 | -0.16479 | -0.17853 | -0.032043 | -0.12817 | 0.07782 | 0.10529 | -0.091552 | -0.022888 | -0.059509 | 0.009155 | 0.27466 | 121.6782 | 0.13733 | 121.669 | 121.4767 | 121.463 | 121.4584 | 121.431 | -121.5775 | -121.5912 | 121.6599 | 121.637 | 61.4777 | 61.5372
740.5938 | 121.7514 | -61.5738 | 60.0357 | -0.012131 | 0.00461 | 0.058768 | 0.057928 | -0.0034735 | -0.0074938 | -0.0008866 | -0.0084228 | 0.0035183 | 0.066988 | 0.061199 | -0.0077459 | 0.023323 | -0.0027707 | -0.018311 | 59.9716 | -61.5784 | 60.1089 | -61.3129 | -61.7889 | -61.8027 | 0.013733 | 59.9258 | -61.5784 | 60.0357 | -61.5234 | -61.6791 | -61.7065 | -0.004577 | -0.064087 | 0.073242 | 0.26093 | -0.22888 | -0.21515 | -0.2243 | -0.21057 | -0.004577 | -0.10986 | 0 | 0.050355 | -0.13275 | -0.10529 | -0.12817 | -0.10071 | 0.2655 | 121.6873 | 0.054932 | 121.6141 | 121.55 | 121.5042 | 121.5454 | 121.4996 | -121.6141 | -121.6141 | 121.6827 | 121.6095 | 61.5555 | 61.5875
742.2812 | 121.7972 | -61.5921 | 59.9945 | -0.012131 | 0.0048236 | 0.057272 | 0.057287 | 0.0020807 | -0.0070666 | -0.0004592 | -0.0023192 | 0.0022367 | 0.068483 | 0.062694 | -0.0073187 | 0.022255 | -0.0014891 | -0.11902 | 59.9396 | -61.615 | 60.0128 | -61.3953 | -61.8622 | -61.8668 | -0.082397 | 59.8755 | -61.6379 | 60.022 | -61.5326 | -61.6928 | -61.7157 | -0.022888 | -0.054932 | 0.01831 | 0.19684 | -0.27466 | -0.27008 | -0.25177 | -0.24719 | -0.045776 | -0.11902 | 0.027466 | 0.059509 | -0.1236 | -0.10071 | -0.07782 | -0.054932 | 0.21973 | 121.6278 | 0.10529 | 121.6599 | 121.5546 | 121.5134 | 121.5317 | 121.4676 | -121.6095 | -121.6324 | 121.6049 | 121.6141 | 61.4731 | 61.5097
744.0312 | 121.756 | -61.5555 | 60.0449 | -0.012131 | 0.0041828 | 0.059409 | 0.056006 | -0.00069646 | -0.0057848 | -0.0015274 | -0.005371 | 0.0030911 | 0.067202 | 0.058208 | -0.0081733 | 0.021614 | -0.0044797 | -0.018311 | 59.9854 | -61.5555 | 60.0906 | -61.3037 | -61.7844 | -61.7981 | 0.022888 | 59.9258 | -61.5784 | 60.0403 | -61.5097 | -61.6745 | -61.6974 | 0 | -0.059509 | 0.045776 | 0.25177 | -0.24262 | -0.22888 | -0.24262 | -0.22888 | -0.022888 | -0.11902 | -0.004578 | 0.045776 | -0.14191 | -0.11902 | -0.11902 | -0.096131 | 0.25177 | 121.6461 | 0.068664 | 121.6187 | 121.5408 | 121.5042 | 121.5408 | 121.4813 | -121.6003 | -121.6232 | 121.6461 | 121.5958 | 61.5372 | 61.5784
745.7812 | 121.8155 | -61.5189 | 60.0082 | -0.0045011 | -0.00051702 | 0.055991 | 0.054297 | -0.0028327 | -0.0066394 | -0.00345 | -0.0023192 | 0.00095488 | 0.064852 | 0.057994 | -0.010096 | 0.022683 | -0.0019163 | -0.10071 | 59.9304 | -61.5921 | 60.0815 | -61.3083 | -61.7523 | -61.734 | -0.022888 | 59.8801 | -61.5967 | 60.0677 | -61.4685 | -61.5967 | -61.6425 | -0.073242 | -0.07782 | 0.073242 | 0.21057 | -0.21515 | -0.23346 | -0.14191 | -0.16022 | -0.07782 | -0.12817 | 0.059509 | 0.050354 | -0.1236 | -0.07782 | -0.045776 | 0 | 0.28381 | 121.6736 | 0.12817 | 121.6644 | 121.5225 | 121.4767 | 121.4493 | 121.3989 | -121.6003 | -121.6049 | 121.6003 | 121.5866 | 61.4182 | 61.496
747.4844 | 121.7422 | -61.5738 | 60.022 | -0.012131 | 0.00461 | 0.058554 | 0.056219 | -0.00091006 | -0.0066394 | -0.0008866 | -0.0023192 | 0.0035183 | 0.06592 | 0.057781 | -0.0086005 | 0.020333 | -0.0053343 | -0.10986 | 59.9304 | -61.6104 | 59.9899 | -61.4365 | -61.8942 | -61.8896 | -0.1236 | 59.8846 | -61.6562 | 59.9945 | -61.5875 | -61.7157 | -61.7294 | -0.036621 | -0.091553 | -0.032044 | 0.13733 | -0.31586 | -0.32043 | -0.27923 | -0.28381 | -0.082397 | -0.13733 | -0.027466 | -0.013732 | -0.15564 | -0.14191 | -0.073242 | -0.059509 | 0.17395 | 121.6003 | 0.068665 | 121.6507 | 121.5408 | 121.5408 | 121.5042 | 121.4584 | -121.6324 | -121.6782 | 121.5637 | 121.5683 | 61.4639 | 61.4502
749.2344 | 121.8704 | -61.4822 | 60.0357 | -0.012131 | 0.00033758 | 0.057059 | 0.053015 | -0.0053961 | -0.0064258 | -0.0013138 | -0.005371 | -0.0022495 | 0.064638 | 0.056926 | -0.01095 | 0.021614 | -0.0014891 | -0.068665 | 59.935 | -61.5921 | 60.1227 | -61.2625 | -61.702 | -61.6974 | 0.045776 | 59.8846 | -61.5738 | 60.1364 | -61.377 | -61.4868 | -61.5784 | -0.10986 | -0.10071 | 0.086975 | 0.21973 | -0.21515 | -0.21973 | -0.10529 | -0.10986 | -0.091553 | -0.15106 | 0.10071 | 0.10529 | -0.09613 | -0.004577 | -0.004577 | 0.086976 | 0.32959 | 121.7148 | 0.19684 | 121.7102 | 121.5271 | 121.4584 | 121.4172 | 121.3669 | -121.6278 | -121.6095 | 121.6049 | 121.6187 | 61.4136 | 61.528
750.9844 | 121.7468 | -61.4914 | 60.1273 | -0.01976 | 0.00097838 | 0.05535 | 0.05451 | -0.0019781 | -0.0079212 | -0.0004592 | -0.0023192 | 0.0033047 | 0.066347 | 0.055217 | -0.0088141 | 0.020119 | -0.0010617 | -0.032043 | 59.9945 | -61.5555 | 60.0815 | -61.2991 | -61.7477 | -61.7569 | -0.009155 | 59.9762 | -61.5509 | 60.0586 | -61.4639 | -61.6058 | -61.6608 | -0.064087 | -0.13275 | -0.045776 | 0.19226 | -0.2655 | -0.25635 | -0.20142 | -0.19226 | -0.059509 | -0.15106 | -0.068664 | 0.027466 | -0.16937 | -0.11444 | -0.10986 | -0.054932 | 0.25635 | 121.637 | 0.086975 | 121.6095 | 121.55 | 121.5271 | 121.4859 | 121.4676 | -121.6827 | -121.6782 | 121.5729 | 121.55 | 61.4594 | 61.4822
752.75 | 121.875 | -61.4914 | 60.054 | -0.012131 | 0.00097838 | 0.05535 | 0.052374 | -0.0011237 | -0.0081348 | -0.00345 | -0.005371 | 0.0015957 | 0.065493 | 0.059917 | -0.010096 | 0.02311 | -0.00020725 | -0.064087 | 59.9304 | -61.5967 | 60.1273 | -61.2671 | -61.7111 | -61.7111 | 0.054932 | 59.8984 | -61.5601 | 60.1181 | -61.377 | -61.5005 | -61.5738 | -0.10529 | -0.1236 | 0.073242 | 0.2243 | -0.21973 | -0.21973 | -0.11444 | -0.11444 | -0.068665 | -0.15564 | 0.064087 | 0.11444 | -0.082398 | -0.009155 | -0.013733 | 0.05951 | 0.32959 | 121.7239 | 0.18311 | 121.6782 | 121.5271 | 121.4584 | 121.4218 | 121.3898 | -121.6507 | -121.6141 | 121.6187 | 121.6095 | 61.4273 | 61.5463
754.5 | 121.8887 | -61.5692 | 59.9442 | -0.012131 | 0.0035418 | 0.058981 | 0.05686 | -0.00048286 | -0.0032214 | 0.0003952 | -0.0023192 | 0.0013821 | 0.065493 | 0.05949 | -0.0096685 | 0.020119 | -0.0025571 | -0.064087 | 59.8846 | -61.5829 | 60.1135 | -61.2808 | -61.7661 | -61.7432 | 0.032043 | 59.816 | -61.6013 | 60.1135 | -61.4365 | -61.5738 | -61.615 | -0.013733 | -0.059509 | 0.16937 | 0.28839 | -0.17395 | -0.19684 | -0.16022 | -0.18311 | -0.032043 | -0.12817 | 0.16937 | 0.13275 | -0.045776 | -0.004578 | -0.013733 | 0.027465 | 0.30212 | 121.6965 | 0.16479 | 121.7148 | 121.4676 | 121.4172 | 121.4539 | 121.3852 | -121.5271 | -121.5454 | 121.6827 | 121.6827 | 61.5051 | 61.6013
756.2656 | 121.8704 | -61.5051 | 60.0586 | -0.0045011 | -0.00051702 | 0.059195 | 0.053656 | -0.0028327 | -0.006853 | -0.001741 | -0.0084228 | 0.0020231 | 0.065065 | 0.053722 | -0.010523 | 0.020974 | -0.0040525 | 0.032043 | 59.9442 | -61.5189 | 60.2142 | -61.1618 | -61.6241 | -61.6562 | 0.1236 | 59.9167 | -61.5189 | 60.141 | -61.3403 | -61.4822 | -61.5555 | -0.013733 | -0.11444 | 0.15564 | 0.34332 | -0.15106 | -0.11902 | -0.13733 | -0.10529 | -0.013733 | -0.14191 | 0.082397 | 0.1648 | -0.050354 | 0.022888 | -0.036621 | 0.036621 | 0.35706 | 121.7331 | 0.17853 | 121.6599 | 121.463 | 121.4355 | 121.4493 | 121.4218 | -121.5775 | -121.5775 | 121.7194 | 121.6461 | 61.5372 | 61.6287
757.9688 | 121.7422 | -61.5921 | 60.0266 | -0.0045011 | 0.002901 | 0.057486 | 0.05686 | 0.0031487 | -0.006853 | -0.0008866 | -0.005371 | 0.0043729 | 0.064852 | 0.061412 | -0.0086005 | 0.020974 | -0.00020725 | -0.10529 | 59.9167 | -61.6287 | 60.0082 | -61.4273 | -61.8759 | -61.8668 | -0.10529 | 59.8709 | -61.6379 | 59.9945 | -61.5784 | -61.7249 | -61.734 | -0.036621 | -0.10986 | -0.01831 | 0.16479 | -0.27466 | -0.28381 | -0.23804 | -0.24719 | -0.045776 | -0.15564 | -0.032043 | 0.013733 | -0.14191 | -0.13275 | -0.096131 | -0.086976 | 0.20142 | 121.637 | 0.059509 | 121.6324 | 121.5454 | 121.5088 | 121.5088 | 121.463 | -121.6553 | -121.6644 | 121.6003 | 121.5866 | 61.4868 | 61.4868
759.7188 | 121.8521 | -61.5097 | 60.022 | -0.01976 | 0.00012398 | 0.057059 | 0.053228 | -0.00026906 | -0.0087756 | -0.0002456 | -0.0023192 | 0.0022367 | 0.063997 | 0.058422 | -0.010096 | 0.020546 | -0.0034117 | -0.07782 | 59.9075 | -61.5784 | 60.1135 | -61.2854 | -61.7111 | -61.7157 | 0.013733 | 59.8801 | -61.5601 | 60.1044 | -61.3953 | -61.5372 | -61.5967 | -0.068664 | -0.11444 | 0.091552 | 0.2243 | -0.20599 | -0.20142 | -0.13733 | -0.13275 | -0.050354 | -0.14191 | 0.082397 | 0.11444 | -0.086975 | -0.027465 | -0.036621 | 0.022889 | 0.29297 | 121.6919 | 0.1648 | 121.6644 | 121.4859 | 121.4401 | 121.4172 | 121.3898 | -121.6003 | -121.582 | 121.6232 | 121.6141 | 61.4319 | 61.5234
761.4688 | 121.8842 | -61.5509 | 59.9487 | -0.012131 | 0.0016192 | 0.056845 | 0.05686 | 0.00058534 | -0.0066394 | -0.0011002 | -0.005371 | 0.0015957 | 0.065706 | 0.053081 | -0.0056097 | 0.019051 | -0.0059751 | -0.045776 | 59.8755 | -61.5921 | 60.1227 | -61.2854 | -61.7523 | -61.7477 | 0.036621 | 59.8297 | -61.615 | 60.0952 | -61.4456 | -61.5784 | -61.6287 | -0.041199 | -0.073242 | 0.17395 | 0.2655 | -0.19684 | -0.20142 | -0.15564 | -0.16022 | -0.064087 | -0.11902 | 0.14649 | 0.10528 | -0.07782 | -0.027466 | -0.013733 | 0.036621 | 0.3067 | 121.7148 | 0.16937 | 121.7102 | 121.4676 | 121.4447 | 121.4264 | 121.3806 | -121.5408 | -121.5637 | 121.6736 | 121.6461 | 61.5051 | 61.5875
763.1719 | 121.7514 | -61.5051 | 60.0952 | -0.012131 | 0.0020466 | 0.055136 | 0.053869 | -0.00048286 | -0.0092028 | -0.0025956 | -0.0084228 | 0.0026639 | 0.064424 | 0.052654 | -0.0092413 | 0.021187 | 0.00043375 | 0.009155 | 59.9716 | -61.5646 | 60.1227 | -61.29 | -61.7065 | -61.7249 | 0.009155 | 59.9762 | -61.5555 | 60.0586 | -61.4594 | -61.5967 | -61.6699 | -0.059509 | -0.1236 | 0.027466 | 0.21515 | -0.21973 | -0.20142 | -0.16022 | -0.14191 | -0.050354 | -0.11902 | -0.036621 | 0.045776 | -0.16479 | -0.091553 | -0.11444 | -0.041199 | 0.27466 | 121.6873 | 0.09613 | 121.6141 | 121.5363 | 121.5317 | 121.4767 | 121.4813 | -121.6599 | -121.6507 | 121.6278 | 121.5637 | 61.5143 | 61.5143
764.9219 | 121.788 | -61.5326 | 60.0494 | -0.0045011 | 0.0014056 | 0.055563 | 0.056433 | -0.00026906 | -0.0049304 | 0.0012496 | -0.0084228 | 0.0033047 | 0.067415 | 0.059276 | -0.0077459 | 0.021401 | -0.0017027 | 0.004578 | 59.9899 | -61.5555 | 60.1044 | -61.3174 | -61.7432 | -61.7661 | 0 | 59.9533 | -61.5509 | 60.0952 | -61.4548 | -61.6058 | -61.6241 | -0.022888 | -0.059509 | 0.054932 | 0.21515 | -0.23346 | -0.21057 | -0.21057 | -0.18768 | -0.01831 | -0.09613 | 0.045777 | 0.07782 | -0.091553 | -0.073242 | -0.073243 | -0.054932 | 0.23804 | 121.6599 | 0.09613 | 121.6461 | 121.5454 | 121.5042 | 121.5225 | 121.4859 | -121.6049 | -121.6003 | 121.637 | 121.6278 | 61.5372 | 61.5326
766.6719 | 121.8246 | -61.5417 | 60.0128 | -0.0045011 | 0.0039692 | 0.059836 | 0.053015 | -0.0011237 | -0.0077074 | -0.00345 | -0.011475 | 0.0024503 | 0.067202 | 0.057567 | -0.0083869 | 0.023323 | 0.00086095 | -0.068665 | 59.8663 | -61.5692 | 60.1089 | -61.2671 | -61.7752 | -61.7615 | 0.022888 | 59.848 | -61.5829 | 60.0723 | -61.4456 | -61.5784 | -61.647 | -0.027466 | -0.14648 | 0.096131 | 0.27466 | -0.21973 | -0.23346 | -0.19226 | -0.20599 | -0.041199 | -0.16479 | 0.05951 | 0.09613 | -0.10529 | -0.036621 | -0.064087 | 0.004578 | 0.30212 | 121.6782 | 0.13733 | 121.6553 | 121.4355 | 121.431 | 121.4081 | 121.3898 | -121.582 | -121.5958 | 121.6507 | 121.6141 | 61.4731 | 61.5646
768.4219 | 121.875 | -61.5509 | 59.9716 | -0.012131 | 0.001833 | 0.059195 | 0.054297 | -0.0015509 | -0.006853 | -0.000673 | -0.005371 | 0.0024503 | 0.063356 | 0.056285 | -0.0098823 | 0.023751 | -0.0019163 | -0.054932 | 59.8846 | -61.5967 | 60.1181 | -61.2854 | -61.7523 | -61.7523 | 0.013733 | 59.8297 | -61.6241 | 60.1181 | -61.4502 | -61.5829 | -61.6196 | -0.045777 | -0.086975 | 0.14648 | 0.2655 | -0.20142 | -0.20142 | -0.15564 | -0.15564 | -0.073243 | -0.14191 | 0.14648 | 0.10071 | -0.068665 | -0.032044 | 0.004578 | 0.041199 | 0.31128 | 121.7148 | 0.17395 | 121.7422 | 121.4813 | 121.4539 | 121.4355 | 121.3806 | -121.5683 | -121.5958 | 121.669 | 121.669 | 61.496 | 61.5646
770.1094 | 121.8338 | -61.5097 | 60.0174 | -0.0045011 | 0.0037556 | 0.057486 | 0.056006 | -5.5462e-05 | -0.0072802 | -0.0030228 | -0.005371 | 0.00074128 | 0.064211 | 0.053081 | -0.0098823 | 0.024391 | -0.0029843 | -0.082397 | 59.8846 | -61.5784 | 60.0906 | -61.2762 | -61.7661 | -61.734 | 0 | 59.8618 | -61.5921 | 60.0861 | -61.4594 | -61.5829 | -61.6333 | -0.068664 | -0.13275 | 0.073242 | 0.23346 | -0.2243 | -0.25635 | -0.15564 | -0.18768 | -0.082397 | -0.15564 | 0.068665 | 0.050354 | -0.1236 | -0.073242 | -0.041199 | 0.009155 | 0.30212 | 121.669 | 0.13275 | 121.6782 | 121.463 | 121.4539 | 121.3943 | 121.3715 | -121.5958 | -121.6095 | 121.6003 | 121.5958 | 61.4273 | 61.5097
771.8594 | 121.8338 | -61.5372 | 60.0266 | -0.02739 | 0.00097838 | 0.057486 | 0.053228 | -0.0032599 | -0.0072802 | -0.0013138 | -0.005371 | 0.0011685 | 0.064638 | 0.063335 | -0.010737 | 0.020546 | -0.0042661 | -0.09613 | 59.9396 | -61.5646 | 60.0952 | -61.3129 | -61.7615 | -61.7477 | -0.036621 | 59.8846 | -61.5967 | 60.0723 | -61.4456 | -61.5692 | -61.6287 | -0.027466 | -0.086975 | 0.068665 | 0.2243 | -0.21057 | -0.2243 | -0.18311 | -0.19684 | -0.05951 | -0.14191 | 0.045777 | 0.091552 | -0.091553 | -0.032044 | -0.032043 | 0.027466 | 0.25177 | 121.6599 | 0.15106 | 121.669 | 121.5042 | 121.4813 | 121.4767 | 121.4218 | -121.5912 | -121.6232 | 121.6324 | 121.6095 | 61.441 | 61.5005
773.5469 | 121.756 | -61.5189 | 60.0952 | -0.0045011 | -0.00073062 | 0.056204 | 0.054083 | 0.0033623 | -0.0070666 | -0.0028092 | -0.0084228 | 0.0033047 | 0.066347 | 0.058422 | -0.0092413 | 0.021187 | -0.0066159 | -0.013733 | 60.0128 | -61.5326 | 60.0952 | -61.3266 | -61.7523 | -61.7706 | -0.022888 | 59.9854 | -61.5646 | 60.0632 | -61.4731 | -61.6104 | -61.6562 | -0.013733 | -0.082398 | 0 | 0.19226 | -0.25177 | -0.23346 | -0.23804 | -0.21973 | -0.045776 | -0.10986 | -0.032044 | 0.045777 | -0.13733 | -0.091553 | -0.091553 | -0.045777 | 0.20599 | 121.6278 | 0.091553 | 121.6278 | 121.5454 | 121.55 | 121.5317 | 121.5042 | -121.6278 | -121.6599 | 121.6141 | 121.582 | 61.5051 | 61.496
775.2969 | 121.875 | -61.5509 | 59.9442 | -0.012131 | 0.0035418 | 0.0577 | 0.053442 | 0.0033623 | -0.0059986 | -0.0008866 | -0.005371 | 0.0018095 | 0.06827 | 0.058208 | -0.0096685 | 0.020333 | -0.0031979 | -0.07782 | 59.8892 | -61.5829 | 60.1135 | -61.2991 | -61.7523 | -61.7477 | 0.009155 | 59.8206 | -61.6058 | 60.1089 | -61.4456 | -61.5921 | -61.6104 | -0.032044 | -0.054932 | 0.16937 | 0.25177 | -0.19684 | -0.20142 | -0.1648 | -0.16937 | -0.054932 | -0.1236 | 0.16479 | 0.10528 | -0.05951 | -0.041199 | -0.004578 | 0.013733 | 0.28381 | 121.6965 | 0.16022 | 121.7148 | 121.4722 | 121.4264 | 121.4401 | 121.3715 | -121.5271 | -121.55 | 121.6644 | 121.6599 | 61.4731 | 61.5601
776.9844 | 121.7377 | -61.6013 | 60.0494 | -0.01976 | 0.0041828 | 0.058554 | 0.057501 | 0.0014397 | -0.0057848 | -0.0028092 | -0.0023192 | 0.0022367 | 0.065706 | 0.055858 | -0.0090277 | 0.019905 | 0.00021995 | -0.086975 | 59.9487 | -61.6104 | 60.022 | -61.4182 | -61.853 | -61.8576 | -0.11444 | 59.9213 | -61.6104 | 59.9899 | -61.5784 | -61.7386 | -61.7432 | -0.009156 | -0.10071 | -0.027465 | 0.1831 | -0.25635 | -0.25177 | -0.24719 | -0.24261 | -0.009156 | -0.12817 | -0.059509 | 0.022888 | -0.14191 | -0.13733 | -0.13275 | -0.12817 | 0.19226 | 121.6324 | 0.032044 | 121.6003 | 121.5591 | 121.5317 | 121.55 | 121.5225 | -121.6599 | -121.6599 | 121.6232 | 121.5912 | 61.5143 | 61.4868
778.7344 | 121.788 | -61.528 | 60.0449 | -0.0045011 | 0.0026874 | 0.056631 | 0.055365 | 0.0025079 | -0.0070666 | -0.001741 | -0.0023192 | 0.0043729 | 0.066561 | 0.062053 | -0.0083869 | 0.020546 | -0.0046933 | -0.027466 | 59.9442 | -61.5738 | 60.1044 | -61.2808 | -61.7432 | -61.7569 | 0.036621 | 59.9167 | -61.5784 | 60.0906 | -61.4639 | -61.6104 | -61.6241 | -0.045777 | -0.10071 | 0.059509 | 0.24719 | -0.22888 | -0.21515 | -0.18311 | -0.16937 | -0.050354 | -0.12817 | 0.045776 | 0.064087 | -0.096131 | -0.082398 | -0.045777 | -0.032044 | 0.29297 | 121.6782 | 0.11444 | 121.669 | 121.5179 | 121.4951 | 121.4722 | 121.4447 | -121.6187 | -121.6232 | 121.6324 | 121.6187 | 61.5005 | 61.5646
780.4844 | 121.7743 | -61.5234 | 60.0998 | -0.0045011 | -0.00030342 | 0.0577 | 0.053869 | 0.0012261 | -0.0077074 | -0.001741 | -0.005371 | 0.00074128 | 0.063784 | 0.057994 | -0.0083869 | 0.022255 | -0.00084805 | -0.009155 | 60.0174 | -61.5326 | 60.0906 | -61.3403 | -61.7569 | -61.7798 | -0.018311 | 59.9625 | -61.5601 | 60.0677 | -61.4365 | -61.5967 | -61.6425 | -0.009156 | -0.082397 | -0.009155 | 0.18311 | -0.25635 | -0.23346 | -0.24719 | -0.2243 | -0.036622 | -0.13733 | -0.032043 | 0.086975 | -0.11902 | -0.073243 | -0.082397 | -0.036621 | 0.19226 | 121.6232 | 0.1236 | 121.6278 | 121.55 | 121.5225 | 121.5408 | 121.4859 | -121.6324 | -121.6599 | 121.6141 | 121.5912 | 61.5143 | 61.5051
782.1719 | 121.8292 | -61.5051 | 60.054 | -0.0045011 | 0.0014056 | 0.055991 | 0.052588 | -0.0013373 | -0.0042896 | -0.0025956 | -0.005371 | 0.00074128 | 0.066133 | 0.049236 | -0.011591 | 0.023751 | -0.0034117 | 0.027466 | 59.935 | -61.5463 | 60.1913 | -61.1938 | -61.6425 | -61.647 | 0.086975 | 59.9121 | -61.528 | 60.1501 | -61.3495 | -61.4822 | -61.5692 | -0.041199 | -0.11902 | 0.13733 | 0.31128 | -0.14191 | -0.13733 | -0.10071 | -0.09613 | -0.022888 | -0.14191 | 0.09613 | 0.15564 | -0.064087 | 0.022888 | -0.041199 | 0.045776 | 0.35248 | 121.7377 | 0.17853 | 121.6782 | 121.4813 | 121.4401 | 121.4401 | 121.4172 | -121.6003 | -121.582 | 121.6965 | 121.6553 | 61.5326 | 61.5921
783.9375 | 121.8338 | -61.5372 | 59.9991 | -0.0045011 | 0.0022602 | 0.057913 | 0.053869 | -5.5462e-05 | -0.0045032 | -0.000673 | -0.005371 | 0.00052768 | 0.065279 | 0.057781 | -0.0098823 | 0.023323 | -0.0027707 | -0.073242 | 59.8434 | -61.5829 | 60.1318 | -61.2625 | -61.7386 | -61.734 | 0.022888 | 59.848 | -61.6058 | 60.0998 | -61.4319 | -61.5738 | -61.6196 | -0.045777 | -0.15564 | 0.13275 | 0.27466 | -0.19684 | -0.20142 | -0.15106 | -0.15564 | -0.068665 | -0.15106 | 0.10071 | 0.10529 | -0.082398 | -0.036622 | -0.013733 | 0.032043 | 0.32043 | 121.7148 | 0.17395 | 121.7056 | 121.4264 | 121.4539 | 121.3806 | 121.3852 | -121.582 | -121.6049 | 121.669 | 121.637 | 61.4639 | 61.5601
785.7031 | 121.7606 | -61.5005 | 60.0815 | -0.0045011 | 0.001192 | 0.055777 | 0.051947 | -5.5462e-05 | -0.0070666 | -0.0019546 | -0.005371 | 0.0022367 | 0.06827 | 0.05949 | -0.010096 | 0.022896 | 6.346e-06 | 0.036621 | 59.9716 | -61.528 | 60.1639 | -61.2259 | -61.6745 | -61.6882 | 0.050354 | 59.9533 | -61.5326 | 60.0861 | -61.441 | -61.5509 | -61.6287 | -0.027466 | -0.10986 | 0.082397 | 0.27466 | -0.18768 | -0.17395 | -0.16022 | -0.14648 | -0.032044 | -0.12817 | 0.004578 | 0.059509 | -0.12817 | -0.050354 | -0.09613 | -0.01831 | 0.30212 | 121.6919 | 0.091553 | 121.6187 | 121.4996 | 121.4859 | 121.4722 | 121.4539 | -121.6095 | -121.6141 | 121.6644 | 121.5866 | 61.5372 | 61.5509
787.4375 | 121.7514 | -61.4914 | 60.0998 | -0.012131 | 0.00033758 | 0.055777 | 0.055365 | 0.0059259 | -0.0053576 | -0.001741 | -0.0084228 | 0.0045865 | 0.068483 | 0.058635 | -0.0094549 | 0.020546 | 0.00021995 | -0.041199 | 60.0082 | -61.5463 | 60.0906 | -61.3174 | -61.7432 | -61.7569 | -0.004578 | 59.9716 | -61.5417 | 60.054 | -61.4548 | -61.5875 | -61.6516 | -0.054932 | -0.091552 | -0.009155 | 0.17395 | -0.2655 | -0.25177 | -0.21057 | -0.19684 | -0.050354 | -0.12817 | -0.045776 | 0.036621 | -0.16022 | -0.09613 | -0.10986 | -0.045776 | 0.22888 | 121.637 | 0.086975 | 121.5958 | 121.5546 | 121.5134 | 121.4996 | 121.463 | -121.6461 | -121.6415 | 121.582 | 121.5454 | 61.4502 | 61.4868
789.125 | 121.8658 | -61.5646 | 59.9945 | -0.012131 | 0.0035418 | 0.057059 | 0.055151 | 0.0018671 | -0.0057848 | -0.0047318 | -0.011475 | 0.0026639 | 0.065493 | 0.055644 | -0.0092413 | 0.022255 | 0.0029971 | -0.068665 | 59.9213 | -61.5829 | 60.1089 | -61.2808 | -61.7477 | -61.7569 | 0.004578 | 59.8434 | -61.6104 | 60.1044 | -61.4365 | -61.5875 | -61.6058 | -0.018311 | -0.073242 | 0.11444 | 0.28381 | -0.19226 | -0.18311 | -0.17395 | -0.1648 | -0.045777 | -0.15106 | 0.10986 | 0.12817 | -0.041199 | -0.022888 | 0.004578 | 0.022889 | 0.30212 | 121.6919 | 0.17395 | 121.7148 | 121.5042 | 121.4539 | 121.4859 | 121.4081 | -121.5775 | -121.6049 | 121.6736 | 121.669 | 61.496 | 61.5692
790.875 | 121.7697 | -61.528 | 60.0677 | -0.0045011 | 0.0016192 | 0.057059 | 0.056006 | 0.0029351 | -0.0070666 | -0.0008866 | -0.0023192 | 0.0033047 | 0.066774 | 0.057567 | -0.0079597 | 0.021614 | -0.0078977 | -0.018311 | 59.9625 | -61.5738 | 60.1135 | -61.2854 | -61.7477 | -61.7661 | 0.022888 | 59.9167 | -61.5829 | 60.0861 | -61.4685 | -61.615 | -61.6379 | -0.045777 | -0.10529 | 0.045776 | 0.24262 | -0.23804 | -0.21973 | -0.19226 | -0.17395 | -0.054932 | -0.15106 | 0.018311 | 0.059509 | -0.10986 | -0.086975 | -0.054931 | -0.032043 | 0.28839 | 121.6873 | 0.11444 | 121.669 | 121.5363 | 121.4996 | 121.4905 | 121.4447 | -121.6415 | -121.6507 | 121.6415 | 121.6141 | 61.5097 | 61.5509
792.5625 | 121.8018 | -61.5005 | 60.0769 | 0.0031279 | 0.0022602 | 0.058554 | 0.055792 | 0.00037174 | -0.0062122 | -0.00345 | -0.005371 | 0.0022367 | 0.065493 | 0.056499 | -0.011164 | 0.023751 | -0.0042661 | -0.004578 | 59.9945 | -61.5509 | 60.1089 | -61.3174 | -61.7294 | -61.7615 | 0 | 59.9808 | -61.5601 | 60.0815 | -61.4365 | -61.5921 | -61.6379 | -0.050354 | -0.082397 | 0.032044 | 0.1831 | -0.26093 | -0.22888 | -0.21057 | -0.17853 | -0.05951 | -0.09613 | 0.004578 | 0.064087 | -0.13733 | -0.091553 | -0.077819 | -0.032043 | 0.23346 | 121.6599 | 0.1236 | 121.6415 | 121.5454 | 121.5408 | 121.4951 | 121.4813 | -121.6278 | -121.637 | 121.6095 | 121.582 | 61.496 | 61.5005
794.3281 | 121.8201 | -61.5326 | 60.0403 | -0.0045011 | 0.0026874 | 0.056204 | 0.05152 | -0.00026906 | -0.0057848 | -0.0045182 | -0.005371 | 0.00095488 | 0.068056 | 0.054149 | -0.01095 | 0.024178 | 0.0012881 | -0.07782 | 59.9304 | -61.5692 | 60.0952 | -61.3083 | -61.7432 | -61.7569 | -0.045776 | 59.8846 | -61.5967 | 60.0723 | -61.441 | -61.5692 | -61.6333 | -0.036621 | -0.10986 | 0.054932 | 0.2243 | -0.2243 | -0.21057 | -0.18768 | -0.17395 | -0.064087 | -0.15564 | 0.032044 | 0.091553 | -0.10071 | -0.036621 | -0.036621 | 0.027466 | 0.26093 | 121.6644 | 0.15564 | 121.669 | 121.4996 | 121.4813 | 121.463 | 121.4172 | -121.6095 | -121.637 | 121.6278 | 121.6049 | 61.4548 | 61.4868
796.0156 | 121.8704 | -61.4868 | 60.0586 | -0.01976 | 0.0022602 | 0.055991 | 0.051306 | -0.0017645 | -0.0089892 | -3.1996e-05 | -0.005371 | 0.0013821 | 0.066133 | 0.056713 | -0.013514 | 0.021187 | 0.00021995 | -0.050354 | 59.9213 | -61.5509 | 60.1364 | -61.2579 | -61.6837 | -61.6928 | 0.041199 | 59.8938 | -61.5601 | 60.141 | -61.3724 | -61.5005 | -61.5646 | -0.064087 | -0.13733 | 0.07782 | 0.22888 | -0.20599 | -0.19684 | -0.14191 | -0.13275 | -0.073243 | -0.16479 | 0.082397 | 0.11444 | -0.07782 | -0.013733 | -0.004577 | 0.05951 | 0.29297 | 121.6873 | 0.18768 | 121.7011 | 121.4722 | 121.4539 | 121.4081 | 121.3806 | -121.6095 | -121.6187 | 121.6232 | 121.6278 | 61.4365 | 61.528
797.7656 | 121.7331 | -61.5097 | 60.1089 | -0.012131 | 0.001833 | 0.053427 | 0.057287 | -0.00091006 | -0.0077074 | -0.0013138 | -0.005371 | 0.0050137 | 0.066561 | 0.059062 | -0.01095 | 0.02076 | -0.0010617 | -0.013733 | 60.0266 | -61.5417 | 60.0906 | -61.322 | -61.7294 | -61.7569 | -0.013733 | 60.0037 | -61.5417 | 60.0586 | -61.4548 | -61.615 | -61.647 | -0.032043 | -0.082398 | -0.018311 | 0.18768 | -0.24719 | -0.21973 | -0.21515 | -0.18768 | -0.032043 | -0.10529 | -0.050354 | 0.054932 | -0.13733 | -0.10529 | -0.10529 | -0.073242 | 0.21973 | 121.6324 | 0.086975 | 121.6003 | 121.5683 | 121.5454 | 121.5363 | 121.5134 | -121.6507 | -121.6507 | 121.6003 | 121.5683 | 61.496 | 61.496
799.5156 | 121.8109 | -61.5372 | 60.0632 | -0.02739 | 0.001833 | 0.058768 | 0.057715 | 0.0040033 | -0.0074938 | -0.001741 | -0.005371 | 0.0035183 | 0.066774 | 0.060771 | -0.010096 | 0.020546 | -0.0059751 | 0.004578 | 59.9487 | -61.5784 | 60.1135 | -61.3083 | -61.7477 | -61.7523 | 0.013733 | 59.967 | -61.5738 | 60.0952 | -61.4548 | -61.5875 | -61.6287 | -0.041199 | -0.11444 | 0.050354 | 0.22888 | -0.21515 | -0.21057 | -0.17395 | -0.16937 | -0.036622 | -0.09613 | 0.032044 | 0.082397 | -0.091553 | -0.050354 | -0.054931 | -0.013732 | 0.27008 | 121.6919 | 0.11902 | 121.669 | 121.5271 | 121.5408 | 121.4859 | 121.5042 | -121.6415 | -121.637 | 121.6507 | 121.6324 | 61.5417 | 61.5509
801.2656 | 121.8292 | -61.4777 | 60.0769 | -0.012131 | 0.001833 | 0.056631 | 0.053228 | -0.0021919 | -0.0081348 | -0.0028092 | -0.005371 | 0.0026639 | 0.066133 | 0.051372 | -0.0079597 | 0.01841 | 0.00021995 | 0.041199 | 59.9579 | -61.5234 | 60.1822 | -61.1847 | -61.6379 | -61.6608 | 0.073242 | 59.9213 | -61.5417 | 60.1318 | -61.3724 | -61.4914 | -61.5784 | -0.045776 | -0.11902 | 0.10529 | 0.29297 | -0.18311 | -0.16022 | -0.13733 | -0.11444 | -0.064087 | -0.15564 | 0.054932 | 0.10529 | -0.10071 | -0.013733 | -0.036621 | 0.050354 | 0.33875 | 121.7056 | 0.16937 | 121.6736 | 121.4813 | 121.463 | 121.4355 | 121.3989 | -121.6003 | -121.6187 | 121.6599 | 121.6095 | 61.5189 | 61.5509
803.0156 | 121.7926 | -61.5189 | 60.0815 | -0.012131 | 0.0024738 | 0.056204 | 0.055792 | -0.0028327 | -0.0077074 | 0.001036 | -0.005371 | 0.0037321 | 0.065493 | 0.06248 | -0.0096685 | 0.021614 | -0.0049069 | 0.013733 | 60.0082 | -61.5784 | 60.1273 | -61.3037 | -61.7386 | -61.7615 | 0.018311 | 59.9167 | -61.5326 | 60.0815 | -61.4502 | -61.6013 | -61.6196 | -0.059509 | -0.073242 | 0.045776 | 0.21515 | -0.24262 | -0.21973 | -0.18311 | -0.16022 | -0.013733 | -0.16479 | 0 | 0.068665 | -0.10071 | -0.082397 | -0.086975 | -0.068664 | 0.27466 | 121.7056 | 0.082398 | 121.6141 | 121.5866 | 121.4493 | 121.5271 | 121.4355 | -121.6599 | -121.6141 | 121.6461 | 121.6003 | 61.5326 | 61.5372
804.7188 | 121.7651 | -61.5738 | 60.0586 | -0.01976 | 0.00461 | 0.055991 | 0.055578 | 0.0020807 | -0.0042896 | -0.000673 | -0.0023192 | 0.0024503 | 0.066133 | 0.056499 | -0.010737 | 0.022255 | -0.0031979 | -0.10071 | 59.9442 | -61.6241 | 59.9991 | -61.441 | -61.8668 | -61.8759 | -0.12817 | 59.8801 | -61.6333 | 59.9945 | -61.5692 | -61.7249 | -61.7249 | -0.050354 | -0.11444 | -0.05951 | 0.13275 | -0.30212 | -0.29297 | -0.25177 | -0.24261 | -0.059509 | -0.17853 | -0.064087 | 0.004578 | -0.15106 | -0.15106 | -0.091553 | -0.091553 | 0.18311 | 121.6232 | 0.064087 | 121.6278 | 121.5683 | 121.5134 | 121.5179 | 121.4539 | -121.6827 | -121.6919 | 121.5729 | 121.5683 | 61.4731 | 61.4456
806.4844 | 121.7285 | -61.5921 | 60.0403 | -0.0045011 | 0.00461 | 0.0577 | 0.056646 | 0.0014397 | -0.005144 | -0.0045182 | -0.005371 | 0.0026639 | 0.065706 | 0.06184 | -0.0081733 | 0.023537 | -0.0046933 | -0.068665 | 59.967 | -61.5829 | 60.022 | -61.409 | -61.8393 | -61.853 | -0.13275 | 59.9167 | -61.6196 | 59.9762 | -61.5738 | -61.7157 | -61.7249 | 0.009155 | -0.073242 | -0.01831 | 0.1831 | -0.26093 | -0.24719 | -0.27008 | -0.25635 | -0.027466 | -0.1236 | -0.064087 | 0.01831 | -0.13275 | -0.1236 | -0.10529 | -0.09613 | 0.17395 | 121.6049 | 0.045776 | 121.5958 | 121.55 | 121.5363 | 121.5591 | 121.5088 | -121.6232 | -121.6599 | 121.6141 | 121.5683 | 61.5234 | 61.4594
808.1719 | 121.788 | -61.5143 | 60.1044 | -0.012131 | 0.001192 | 0.058554 | 0.053442 | -5.5462e-05 | -0.0077074 | 0.001036 | -0.005371 | 0.0035183 | 0.068056 | 0.055858 | -0.0081733 | 0.021187 | -0.0040525 | -0.022888 | 60.022 | -61.5646 | 60.0906 | -61.3266 | -61.7432 | -61.7615 | -0.009155 | 59.9762 | -61.5509 | 60.0769 | -61.4502 | -61.6013 | -61.6241 | -0.050354 | -0.082397 | -0.013733 | 0.18768 | -0.24719 | -0.22888 | -0.19684 | -0.17853 | -0.036621 | -0.12817 | -0.027466 | 0.064087 | -0.10986 | -0.086975 | -0.073243 | -0.050354 | 0.23804 | 121.6553 | 0.10071 | 121.6278 | 121.5866 | 121.5271 | 121.5363 | 121.4905 | -121.669 | -121.6553 | 121.6049 | 121.5912 | 61.4914 | 61.5051
809.9219 | 121.756 | -61.5601 | 60.0082 | -0.012131 | 0.0039692 | 0.058127 | 0.055365 | 0.0020807 | -0.0045032 | -0.0004592 | 0.00073235 | 0.0035183 | 0.064211 | 0.057567 | -0.01095 | 0.021828 | 0.00021995 | -0.041199 | 59.9579 | -61.5967 | 60.0632 | -61.3495 | -61.821 | -61.8164 | -0.050354 | 59.903 | -61.6013 | 60.0266 | -61.5326 | -61.6882 | -61.7111 | -0.036621 | -0.050354 | 0.054931 | 0.21057 | -0.25635 | -0.26093 | -0.21973 | -0.2243 | -0.041198 | -0.10529 | 0.01831 | 0.027466 | -0.15106 | -0.12817 | -0.10986 | -0.086975 | 0.24719 | 121.6599 | 0.068664 | 121.6278 | 121.5546 | 121.5042 | 121.5179 | 121.463 | -121.6049 | -121.6095 | 121.6232 | 121.5866 | 61.5189 | 61.5097
811.6875 | 121.8704 | -61.4777 | 60.0677 | 0.0031279 | 0.0022602 | 0.05535 | 0.052588 | -0.0034735 | -0.0077074 | -0.001741 | -0.0023192 | 0.00010048 | 0.063784 | 0.049022 | -0.0096685 | 0.021614 | -0.00084805 | 0.009155 | 59.9487 | -61.5143 | 60.1913 | -61.1435 | -61.6104 | -61.6196 | 0.11902 | 59.8984 | -61.5189 | 60.1685 | -61.3312 | -61.4685 | -61.5463 | -0.036621 | -0.11902 | 0.1236 | 0.33417 | -0.14191 | -0.13275 | -0.10529 | -0.096131 | -0.041199 | -0.16937 | 0.10071 | 0.14648 | -0.068665 | 0.009155 | -0.027466 | 0.050354 | 0.37079 | 121.7056 | 0.18768 | 121.6873 | 121.463 | 121.4172 | 121.4264 | 121.376 | -121.582 | -121.5866 | 121.669 | 121.6461 | 61.4868 | 61.5967
813.4375 | 121.7743 | -61.5005 | 60.0952 | -0.01976 | 0.00012398 | 0.056204 | 0.053442 | -0.0019781 | -0.0077074 | -0.0021682 | -0.0084228 | 0.0041593 | 0.065706 | 0.058849 | -0.010737 | 0.021828 | -0.0053343 | 0.018311 | 59.9899 | -61.5234 | 60.1135 | -61.2625 | -61.7157 | -61.7203 | 0.004578 | 59.9716 | -61.5555 | 60.0677 | -61.4639 | -61.5784 | -61.6653 | -0.022888 | -0.10529 | 0.01831 | 0.23804 | -0.21973 | -0.21515 | -0.19684 | -0.19226 | -0.054932 | -0.1236 | -0.027466 | 0.036621 | -0.16479 | -0.07782 | -0.10986 | -0.022888 | 0.26093 | 121.637 | 0.091553 | 121.6232 | 121.5134 | 121.5271 | 121.4905 | 121.4722 | -121.6187 | -121.6507 | 121.6141 | 121.5683 | 61.5189 | 61.5051
815.125 | 121.8155 | -61.5234 | 60.0357 | -0.012131 | 0.00012398 | 0.057272 | 0.051947 | -0.0056097 | -0.006853 | -0.001741 | -0.0023192 | -0.00032692 | 0.067629 | 0.058635 | -0.0096685 | 0.019692 | 0.0021425 | -0.09613 | 59.9121 | -61.5829 | 60.0861 | -61.2946 | -61.7432 | -61.7386 | -0.036621 | 59.8709 | -61.5738 | 60.0815 | -61.4639 | -61.5738 | -61.6287 | -0.05951 | -0.1236 | 0.050354 | 0.22888 | -0.21515 | -0.21973 | -0.15564 | -0.16022 | -0.050355 | -0.16479 | 0.045776 | 0.059509 | -0.10529 | -0.050355 | -0.054931 | 0 | 0.28839 | 121.669 | 0.10986 | 121.6553 | 121.4951 | 121.4447 | 121.4355 | 121.3943 | -121.6187 | -121.6095 | 121.6095 | 121.6049 | 61.4273 | 61.4868
816.875 | 121.7926 | -61.5189 | 60.0449 | -0.012131 | 0.0022602 | 0.05535 | 0.054937 | 0.0033623 | -0.008562 | -0.000673 | -0.005371 | 0.0039457 | 0.064852 | 0.05949 | -0.010737 | 0.018624 | -0.0042661 | 0.004578 | 59.9533 | -61.5738 | 60.1135 | -61.3037 | -61.734 | -61.7523 | 0.022888 | 59.9304 | -61.5738 | 60.0861 | -61.441 | -61.5875 | -61.6333 | -0.054932 | -0.091553 | 0.068664 | 0.21515 | -0.23346 | -0.21515 | -0.17853 | -0.16022 | -0.054932 | -0.11444 | 0.041199 | 0.07782 | -0.11444 | -0.068664 | -0.059509 | -0.013732 | 0.27008 | 121.6873 | 0.13275 | 121.6599 | 121.5271 | 121.5042 | 121.4722 | 121.4493 | -121.6187 | -121.6187 | 121.6324 | 121.6049 | 61.5234 | 61.5417
818.625 | 121.7468 | -61.5692 | 60.0586 | -0.0045011 | 0.0050372 | 0.05834 | 0.057715 | 0.0014397 | -0.0064258 | -0.0013138 | -0.005371 | 0.0018095 | 0.067415 | 0.06483 | -0.0090277 | 0.022469 | -0.0021299 | -0.068665 | 59.9579 | -61.5875 | 60.0357 | -61.3907 | -61.8439 | -61.8347 | -0.10529 | 59.9258 | -61.6013 | 59.9945 | -61.5555 | -61.702 | -61.7157 | -0.01831 | -0.10071 | -0.022888 | 0.17853 | -0.2655 | -0.27466 | -0.24719 | -0.25635 | -0.032043 | -0.13275 | -0.064087 | 0.013733 | -0.14648 | -0.13275 | -0.11444 | -0.10071 | 0.19684 | 121.6232 | 0.045776 | 121.5958 | 121.5454 | 121.5271 | 121.5271 | 121.4951 | -121.6461 | -121.6599 | 121.6049 | 121.5637 | 61.5005 | 61.4639
820.375 | 121.7789 | -61.528 | 60.0632 | -0.01976 | 0.0041828 | 0.057059 | 0.058569 | -0.0021919 | -0.0087756 | -0.0019546 | -0.0084228 | 0.0043729 | 0.06592 | 0.058849 | -0.0081733 | 0.022255 | -0.0017027 | -0.004578 | 59.9579 | -61.5784 | 60.1044 | -61.2762 | -61.734 | -61.7569 | 0.027466 | 59.9258 | -61.5738 | 60.0723 | -61.4502 | -61.6241 | -61.6333 | -0.050354 | -0.10528 | 0.041199 | 0.25177 | -0.22888 | -0.20599 | -0.17853 | -0.15564 | -0.045777 | -0.13733 | 0.009156 | 0.07782 | -0.10529 | -0.096131 | -0.059509 | -0.050354 | 0.30212 | 121.6827 | 0.1236 | 121.6461 | 121.5363 | 121.4996 | 121.4859 | 121.4539 | -121.6415 | -121.637 | 121.6324 | 121.6003 | 61.5234 | 61.5555
822.0625 | 121.8887 | -61.5051 | 60.0494 | -0.012131 | -0.00051702 | 0.055991 | 0.054083 | 0.0022943 | -0.0081348 | -0.0015274 | -0.0084228 | 0.0015957 | 0.064852 | 0.052867 | -0.012446 | 0.022042 | -0.0014891 | -0.041199 | 59.9533 | -61.5555 | 60.1547 | -61.2305 | -61.6745 | -61.6699 | 0.050354 | 59.8938 | -61.5601 | 60.1593 | -61.3449 | -61.4822 | -61.5601 | -0.050354 | -0.09613 | 0.10529 | 0.27466 | -0.16479 | -0.16937 | -0.11444 | -0.11902 | -0.054932 | -0.15564 | 0.10986 | 0.16022 | -0.054932 | 0.022888 | 0 | 0.07782 | 0.32501 | 121.7102 | 0.21515 | 121.7194 | 121.5088 | 121.4539 | 121.4584 | 121.3989 | -121.6049 | -121.6095 | 121.6599 | 121.6644 | 61.4639 | 61.5555
823.8438 | 121.7514 | -61.5189 | 60.1089 | -0.012131 | 0.0020466 | 0.056418 | 0.053869 | -0.0015509 | -0.0074938 | -0.002382 | -0.0084228 | 0.0035183 | 0.06592 | 0.052013 | -0.01095 | 0.021614 | -0.0014891 | 0.018311 | 59.9945 | -61.5143 | 60.0998 | -61.2717 | -61.7065 | -61.7477 | -0.009155 | 59.9808 | -61.5234 | 60.054 | -61.4594 | -61.5921 | -61.6516 | 0.004578 | -0.11444 | -0.009156 | 0.24719 | -0.22888 | -0.18768 | -0.23346 | -0.19226 | -0.004577 | -0.12817 | -0.054932 | 0.059509 | -0.13275 | -0.073242 | -0.12817 | -0.068665 | 0.24262 | 121.6141 | 0.064086 | 121.5775 | 121.5088 | 121.5042 | 121.5134 | 121.4996 | -121.6232 | -121.6324 | 121.6187 | 121.5729 | 61.5372 | 61.5097
825.5312 | 121.8658 | -61.496 | 60.0677 | -0.012131 | 0.00033758 | 0.056204 | 0.057074 | 0.00015814 | -0.008562 | -0.0013138 | -0.0084228 | -0.0011813 | 0.065279 | 0.056072 | -0.012019 | 0.022469 | -0.0040525 | -0.054932 | 59.9487 | -61.5234 | 60.1227 | -61.2488 | -61.702 | -61.6882 | 0.045776 | 59.9167 | -61.5555 | 60.1364 | -61.3815 | -61.496 | -61.5738 | -0.027465 | -0.11902 | 0.054932 | 0.24719 | -0.19226 | -0.20599 | -0.16479 | -0.17853 | -0.059509 | -0.15106 | 0.068665 | 0.11444 | -0.07782 | 0 | -0.018311 | 0.059509 | 0.27466 | 121.6461 | 0.17395 | 121.6919 | 121.4722 | 121.4722 | 121.4447 | 121.4127 | -121.5912 | -121.6232 | 121.6187 | 121.6324 | 61.441 | 61.5417
827.2812 | 121.7422 | -61.5189 | 60.1181 | -0.0045011 | 0.0026874 | 0.056845 | 0.054297 | -0.0036871 | -0.0070666 | -3.1996e-05 | 0.00073235 | 0.0037321 | 0.066133 | 0.061199 | -0.0094549 | 0.018624 | 0.0012881 | -0.027466 | 60.0082 | -61.5326 | 60.0769 | -61.3129 | -61.7386 | -61.7523 | -0.036621 | 59.9945 | -61.5372 | 60.0586 | -61.4731 | -61.6058 | -61.6516 | -0.013733 | -0.10986 | -0.041199 | 0.20599 | -0.23346 | -0.21973 | -0.21973 | -0.20599 | -0.01831 | -0.1236 | -0.059509 | 0.045777 | -0.13275 | -0.086975 | -0.11444 | -0.068665 | 0.21973 | 121.6095 | 0.064087 | 121.5958 | 121.5408 | 121.5317 | 121.5271 | 121.5134 | -121.6507 | -121.6553 | 121.5958 | 121.5775 | 61.4914 | 61.4822
829.0469 | 121.7422 | -61.5005 | 60.1089 | -0.01976 | 0.00076478 | 0.055136 | 0.054724 | 0.00058534 | -0.0077074 | -0.0013138 | -0.0084228 | 0.0037321 | 0.068483 | 0.063549 | -0.0075323 | 0.020974 | -0.0025571 | -0.022888 | 60.0357 | -61.5326 | 60.1089 | -61.3083 | -61.7477 | -61.7477 | -0.022888 | 59.9808 | -61.5463 | 60.0403 | -61.4731 | -61.6058 | -61.647 | -0.032044 | -0.073242 | 0 | 0.19226 | -0.24719 | -0.24719 | -0.21515 | -0.21515 | -0.045777 | -0.12817 | -0.068665 | 0.027466 | -0.14648 | -0.10529 | -0.10071 | -0.059509 | 0.2243 | 121.6415 | 0.073243 | 121.5866 | 121.5683 | 121.5271 | 121.5363 | 121.4813 | -121.6415 | -121.6553 | 121.6095 | 121.5408 | 61.4777 | 61.4777
830.8125 | 121.8658 | -61.4868 | 60.0494 | -0.012131 | 0.00097838 | 0.057272 | 0.051733 | 0.0012261 | -0.0094164 | -0.000673 | -0.005371 | 0.00074128 | 0.066133 | 0.055644 | -0.010737 | 0.022469 | -0.0027707 | 0.027466 | 59.9258 | -61.5189 | 60.2051 | -61.171 | -61.6333 | -61.6379 | 0.09613 | 59.9258 | -61.5326 | 60.1547 | -61.3449 | -61.4731 | -61.5509 | -0.032044 | -0.1236 | 0.15564 | 0.31586 | -0.15106 | -0.14649 | -0.11902 | -0.11444 | -0.045777 | -0.1236 | 0.10529 | 0.14191 | -0.064087 | 0.013733 | -0.01831 | 0.05951 | 0.3479 | 121.7239 | 0.18768 | 121.6873 | 121.4447 | 121.4584 | 121.4127 | 121.4127 | -121.5683 | -121.582 | 121.6919 | 121.6415 | 61.5143 | 61.5829
832.5 | 121.8979 | -61.4731 | 60.0311 | -0.012131 | 0.00076478 | 0.057486 | 0.052588 | -5.5462e-05 | -0.005144 | -0.000673 | -0.0084228 | 0.0018095 | 0.065706 | 0.060771 | -0.011378 | 0.020119 | -0.0051205 | -0.027466 | 59.935 | -61.5463 | 60.1547 | -61.2305 | -61.6791 | -61.6745 | 0.050354 | 59.8938 | -61.5417 | 60.1593 | -61.3632 | -61.4868 | -61.5463 | -0.073243 | -0.09613 | 0.1236 | 0.24261 | -0.20142 | -0.20599 | -0.12817 | -0.13275 | -0.068665 | -0.13733 | 0.12817 | 0.10986 | -0.073243 | -0.013733 | -0.004578 | 0.054932 | 0.31586 | 121.7011 | 0.17853 | 121.701 | 121.4813 | 121.4355 | 121.4081 | 121.3669 | -121.5775 | -121.5729 | 121.6278 | 121.6324 | 61.4456 | 61.5234
834.25 | 121.8842 | -61.4822 | 60.0906 | -0.012131 | 0.0020466 | 0.056418 | 0.052801 | -0.00048286 | -0.0064258 | -0.0013138 | -0.0084228 | 0.00031408 | 0.068483 | 0.053935 | -0.0094549 | 0.021187 | 0.0010745 | 0.027466 | 59.9258 | -61.5097 | 60.2097 | -61.1664 | -61.6058 | -61.6379 | 0.12817 | 59.9258 | -61.5417 | 60.1685 | -61.3312 | -61.4365 | -61.5417 | -0.027466 | -0.16479 | 0.11902 | 0.31586 | -0.15564 | -0.1236 | -0.12817 | -0.09613 | -0.059509 | -0.16479 | 0.07782 | 0.15106 | -0.059509 | 0.045777 | 0 | 0.10529 | 0.34332 | 121.7194 | 0.21057 | 121.7102 | 121.4355 | 121.4676 | 121.4081 | 121.4081 | -121.6003 | -121.6324 | 121.6919 | 121.6507 | 61.5097 | 61.6104
835.9375 | 121.907 | -61.4548 | 60.054 | -0.012131 | -0.0013714 | 0.056204 | 0.054724 | 0.00058534 | -0.0079212 | -0.0019546 | -0.0084228 | 0.0026639 | 0.067202 | 0.060344 | -0.011164 | 0.021614 | -0.0055479 | -0.018311 | 59.9533 | -61.5234 | 60.173 | -61.2076 | -61.647 | -61.6516 | 0.11902 | 59.9121 | -61.5326 | 60.1868 | -61.3358 | -61.4594 | -61.5417 | -0.068664 | -0.10071 | 0.11902 | 0.24719 | -0.19684 | -0.19226 | -0.12817 | -0.1236 | -0.07782 | -0.14191 | 0.13275 | 0.11902 | -0.086975 | -0.004578 | -0.009155 | 0.073242 | 0.31586 | 121.6965 | 0.19684 | 121.7194 | 121.4767 | 121.4447 | 121.4081 | 121.3669 | -121.5775 | -121.5866 | 121.6278 | 121.6415 | 61.4365 | 61.5738
837.6875 | 121.8613 | -61.4914 | 60.0494 | -0.0045011 | 0.0016192 | 0.055777 | 0.053656 | 0.00058534 | -0.0072802 | 0.0012496 | -0.0084228 | 0.0015957 | 0.068911 | 0.059276 | -0.011805 | 0.022255 | -0.0040525 | -0.054932 | 59.9487 | -61.5509 | 60.141 | -61.2717 | -61.7111 | -61.6974 | 0.022888 | 59.8938 | -61.5509 | 60.1501 | -61.3678 | -61.5005 | -61.5646 | -0.059509 | -0.10071 | 0.091553 | 0.21973 | -0.20599 | -0.21973 | -0.14648 | -0.16022 | -0.059509 | -0.15564 | 0.10071 | 0.1236 | -0.073242 | -0.009155 | -0.013733 | 0.050354 | 0.27924 | 121.6919 | 0.1831 | 121.701 | 121.4996 | 121.4447 | 121.4401 | 121.3852 | -121.6003 | -121.6003 | 121.6324 | 121.6415 | 61.4365 | 61.5143
839.4375 | 121.8796 | -61.4777 | 60.0357 | -0.0045011 | 0.001833 | 0.056631 | 0.054083 | -0.0028327 | -0.006853 | -0.0025956 | -0.005371 | -0.00054052 | 0.066988 | 0.050731 | -0.011378 | 0.02311 | -0.0038389 | -0.032043 | 59.9258 | -61.5509 | 60.1593 | -61.235 | -61.6653 | -61.6791 | 0.064087 | 59.9121 | -61.5326 | 60.1547 | -61.3586 | -61.4868 | -61.5601 | -0.073242 | -0.10986 | 0.1236 | 0.24262 | -0.20142 | -0.18768 | -0.12817 | -0.11444 | -0.054932 | -0.1236 | 0.11902 | 0.11902 | -0.082398 | -0.009155 | -0.027466 | 0.045777 | 0.31586 | 121.7102 | 0.17395 | 121.6873 | 121.4767 | 121.4447 | 121.4035 | 121.3898 | -121.5866 | -121.5683 | 121.637 | 121.6324 | 61.4456 | 61.5417
841.1875 | 121.8842 | -61.5372 | 59.9716 | -0.0045011 | 0.002901 | 0.05834 | 0.056433 | -0.00026906 | -0.0049304 | -0.0019546 | -0.005371 | 0.0037321 | 0.065065 | 0.055431 | -0.0090277 | 0.022469 | -0.0046933 | -0.041199 | 59.903 | -61.5692 | 60.1318 | -61.2808 | -61.7569 | -61.7569 | 0.009155 | 59.8343 | -61.615 | 60.1044 | -61.4502 | -61.5921 | -61.6196 | -0.032044 | -0.068665 | 0.16022 | 0.25635 | -0.21973 | -0.21973 | -0.18768 | -0.18768 | -0.07782 | -0.13733 | 0.13275 | 0.086975 | -0.082398 | -0.054932 | -0.004578 | 0.022888 | 0.28839 | 121.7011 | 0.16479 | 121.7194 | 121.4722 | 121.4493 | 121.4401 | 121.3715 | -121.5408 | -121.5866 | 121.669 | 121.6415 | 61.496 | 61.5463
842.9375 | 121.7285 | -61.5189 | 60.1181 | -0.0045011 | 0.00012398 | 0.056204 | 0.054297 | -0.0039007 | -0.008562 | -0.0015274 | -0.005371 | 0.0052273 | 0.065279 | 0.060131 | -0.0086005 | 0.022255 | -0.0042661 | -0.036621 | 59.9945 | -61.5509 | 60.1044 | -61.3083 | -61.7386 | -61.7615 | -0.022888 | 59.9716 | -61.5601 | 60.0632 | -61.4594 | -61.5829 | -61.6562 | -0.032043 | -0.1236 | -0.013733 | 0.21057 | -0.24262 | -0.21973 | -0.21057 | -0.18768 | -0.041199 | -0.14648 | -0.054932 | 0.059509 | -0.13733 | -0.064087 | -0.09613 | -0.022888 | 0.24261 | 121.6553 | 0.10071 | 121.6232 | 121.5454 | 121.5317 | 121.5134 | 121.4905 | -121.669 | -121.6782 | 121.6232 | 121.582 | 61.4822 | 61.496
844.6875 | 121.788 | -61.496 | 60.1089 | -0.012131 | 0.00012398 | 0.054495 | 0.053228 | -0.0019781 | -0.00963 | -0.0030228 | -0.005371 | 0.0020231 | 0.064211 | 0.055217 | -0.010737 | 0.021187 | -0.0034117 | 0.036621 | 59.9487 | -61.5326 | 60.173 | -61.2259 | -61.6699 | -61.6837 | 0.032043 | 59.9762 | -61.5601 | 60.0952 | -61.4227 | -61.5784 | -61.6379 | -0.036621 | -0.16022 | 0.064087 | 0.27008 | -0.18768 | -0.17395 | -0.15106 | -0.13733 | -0.064087 | -0.13275 | -0.013733 | 0.073243 | -0.14191 | -0.082397 | -0.077819 | -0.01831 | 0.3067 | 121.7056 | 0.13733 | 121.6553 | 121.4813 | 121.5363 | 121.4447 | 121.4722 | -121.6415 | -121.669 | 121.669 | 121.5912 | 61.5326 | 61.528
846.375 | 121.7468 | -61.5692 | 60.0449 | -0.0045011 | 0.0058918 | 0.059622 | 0.057074 | 0.00058534 | -0.0072802 | 0.0001816 | -0.005371 | 0.0050137 | 0.064852 | 0.060558 | -0.0098823 | 0.022683 | 6.346e-06 | -0.013733 | 59.9762 | -61.5875 | 60.1044 | -61.3174 | -61.7844 | -61.7889 | -0.009155 | 59.903 | -61.6013 | 60.0494 | -61.528 | -61.6837 | -61.6928 | -0.01831 | -0.068665 | 0.059509 | 0.25177 | -0.21973 | -0.21515 | -0.20142 | -0.19684 | -0.032043 | -0.14191 | 0.004577 | 0.041199 | -0.1236 | -0.11444 | -0.091553 | -0.082398 | 0.27008 | 121.6919 | 0.073242 | 121.6507 | 121.5637 | 121.5042 | 121.5454 | 121.4722 | -121.6324 | -121.6461 | 121.6736 | 121.6187 | 61.5555 | 61.5601
848.125 | 121.8613 | -61.5372 | 59.9854 | -0.01976 | 0.0035418 | 0.058554 | 0.054297 | -0.00069646 | -0.0077074 | -0.002382 | -0.0084228 | 0.00052768 | 0.065279 | 0.051586 | -0.0088141 | 0.023323 | -0.0034117 | -0.073242 | 59.8709 | -61.6013 | 60.1318 | -61.2534 | -61.7386 | -61.7294 | 0.022888 | 59.8343 | -61.6104 | 60.1135 | -61.4227 | -61.5738 | -61.6104 | -0.064087 | -0.11444 | 0.14648 | 0.28381 | -0.19226 | -0.20142 | -0.12817 | -0.13733 | -0.073243 | -0.15106 | 0.12817 | 0.11444 | -0.073243 | -0.036622 | 0 | 0.036621 | 0.3479 | 121.7331 | 0.18768 | 121.7239 | 121.4722 | 121.4447 | 121.4081 | 121.3715 | -121.5866 | -121.5958 | 121.669 | 121.6507 | 61.4639 | 61.5601
849.8281 | 121.7422 | -61.5005 | 60.1089 | -0.0045011 | 0.00076478 | 0.055777 | 0.054724 | -0.0017645 | -0.0059986 | 0.0001816 | -0.0023192 | 0.0022367 | 0.065279 | 0.05714 | -0.0098823 | 0.02076 | 0.00021995 | -0.004578 | 59.9991 | -61.5509 | 60.0998 | -61.29 | -61.7386 | -61.7569 | -0.013733 | 59.9625 | -61.5555 | 60.0586 | -61.4548 | -61.6013 | -61.6653 | -0.050354 | -0.10986 | -0.009156 | 0.21057 | -0.25635 | -0.23804 | -0.20599 | -0.18768 | -0.054932 | -0.14648 | -0.050354 | 0.045776 | -0.16479 | -0.10071 | -0.10986 | -0.045776 | 0.26093 | 121.6507 | 0.10071 | 121.6141 | 121.55 | 121.5179 | 121.4996 | 121.463 | -121.6599 | -121.6644 | 121.6003 | 121.5591 | 61.496 | 61.4868
851.5781 | 121.7651 | -61.5051 | 60.0998 | -0.012131 | 0.001833 | 0.056631 | 0.056006 | 0.0012261 | -0.006853 | -0.0013138 | -0.0023192 | 0.0041593 | 0.066988 | 0.057994 | -0.0092413 | 0.020974 | -0.0055479 | -0.013733 | 60.0128 | -61.5509 | 60.0906 | -61.3358 | -61.7432 | -61.7706 | -0.027466 | 59.9762 | -61.5646 | 60.0723 | -61.4594 | -61.6013 | -61.6562 | -0.045776 | -0.086975 | -0.009155 | 0.16937 | -0.2655 | -0.23804 | -0.21973 | -0.19226 | -0.059509 | -0.1236 | -0.027465 | 0.045776 | -0.15106 | -0.09613 | -0.091553 | -0.036621 | 0.21515 | 121.6415 | 0.10529 | 121.637 | 121.5637 | 121.5408 | 121.5179 | 121.4813 | -121.6507 | -121.6644 | 121.5958 | 121.5775 | 61.4914 | 61.4777
853.2656 | 121.875 | -61.4594 | 60.0632 | -0.012131 | -0.0017986 | 0.05535 | 0.053228 | 0.0012261 | -0.0072802 | -0.0025956 | -0.011475 | 0.00095488 | 0.06592 | 0.052013 | -0.010523 | 0.022469 | -0.0078977 | 0.036621 | 59.9487 | -61.5326 | 60.2188 | -61.1664 | -61.6241 | -61.6104 | 0.1236 | 59.9213 | -61.5417 | 60.1776 | -61.3083 | -61.4548 | -61.5417 | -0.073242 | -0.11444 | 0.15564 | 0.29297 | -0.15106 | -0.1648 | -0.07782 | -0.091553 | -0.082397 | -0.14191 | 0.11444 | 0.15106 | -0.082397 | 0.004578 | 0 | 0.086975 | 0.36621 | 121.7514 | 0.23346 | 121.7194 | 121.4813 | 121.463 | 121.4081 | 121.3806 | -121.5958 | -121.6049 | 121.6782 | 121.637 | 61.496 | 61.5829
855.0312 | 121.8155 | -61.5326 | 60.0082 | -0.0045011 | 0.0020466 | 0.056418 | 0.051092 | -0.00048286 | -0.0070666 | -0.0019546 | -0.011475 | 0.00095488 | 0.067202 | 0.054363 | -0.011591 | 0.021187 | -0.0023435 | -0.09613 | 59.8892 | -61.5875 | 60.0815 | -61.2946 | -61.7432 | -61.7386 | -0.041199 | 59.8984 | -61.5784 | 60.0815 | -61.4456 | -61.5646 | -61.6333 | -0.054931 | -0.11902 | 0.073242 | 0.23804 | -0.20599 | -0.21057 | -0.15106 | -0.15564 | -0.045776 | -0.10986 | 0.073242 | 0.086975 | -0.10071 | -0.032043 | -0.054932 | 0.013733 | 0.29297 | 121.669 | 0.13275 | 121.6599 | 121.4767 | 121.4767 | 121.4218 | 121.431 | -121.5958 | -121.5866 | 121.6141 | 121.6141 | 61.4365 | 61.4914
856.7969 | 121.8384 | -61.5143 | 60.0128 | -0.0045011 | 0.001192 | 0.055136 | 0.054083 | -0.0013373 | -0.0055712 | -0.0025956 | -0.005371 | 0.0013821 | 0.06592 | 0.05244 | -0.010096 | 0.021614 | -0.0034117 | -0.086975 | 59.8892 | -61.5784 | 60.0998 | -61.2946 | -61.7615 | -61.7523 | -0.036621 | 59.8938 | -61.5692 | 60.0815 | -61.4273 | -61.5463 | -61.6196 | -0.064087 | -0.1236 | 0.086975 | 0.21973 | -0.23804 | -0.24719 | -0.17395 | -0.18311 | -0.054932 | -0.11902 | 0.068665 | 0.086975 | -0.10529 | -0.032044 | -0.050354 | 0.022888 | 0.28381 | 121.6782 | 0.14191 | 121.6507 | 121.4676 | 121.463 | 121.4035 | 121.4081 | -121.5912 | -121.582 | 121.6141 | 121.5958 | 61.4273 | 61.4777
858.5 | 121.7468 | -61.5646 | 60.0266 | -0.01976 | 0.0058918 | 0.057059 | 0.055578 | 0.0018671 | -0.0062122 | -0.0036636 | -0.0084228 | 0.0052273 | 0.066774 | 0.05949 | -0.0088141 | 0.02311 | -0.0017027 | -0.027466 | 59.9899 | -61.5784 | 60.0906 | -61.3266 | -61.7889 | -61.8118 | -0.032043 | 59.9121 | -61.5875 | 60.0403 | -61.5097 | -61.6699 | -61.6928 | -0.013733 | -0.036621 | 0.064087 | 0.23804 | -0.24719 | -0.2243 | -0.23346 | -0.21057 | -0.022888 | -0.11444 | 0.013733 | 0.054931 | -0.12817 | -0.10529 | -0.10529 | -0.082398 | 0.25177 | 121.669 | 0.077819 | 121.6278 | 121.5683 | 121.4996 | 121.5546 | 121.4767 | -121.6049 | -121.6141 | 121.6553 | 121.6049 | 61.5372 | 61.5326
860.25 | 121.7789 | -61.4731 | 60.1044 | -0.012131 | 0.0022602 | 0.0577 | 0.05152 | -0.0019781 | -0.0062122 | -0.0013138 | -0.0084228 | 0.00052768 | 0.064424 | 0.058208 | -0.011805 | 0.02076 | -0.0012753 | 0.032043 | 59.9762 | -61.5234 | 60.1913 | -61.203 | -61.6608 | -61.6699 | 0.054932 | 59.9533 | -61.5326 | 60.1227 | -61.409 | -61.5463 | -61.6104 | -0.050354 | -0.12817 | 0.086975 | 0.27008 | -0.19684 | -0.18768 | -0.14648 | -0.13733 | -0.05951 | -0.15106 | 0.018311 | 0.064086 | -0.13733 | -0.073243 | -0.07782 | -0.013733 | 0.32043 | 121.7148 | 0.1236 | 121.6553 | 121.4996 | 121.4859 | 121.4493 | 121.4264 | -121.6278 | -121.637 | 121.6644 | 121.5958 | 61.5051 | 61.528
861.9531 | 121.7606 | -61.496 | 60.0815 | -0.012131 | 0.001192 | 0.05535 | 0.053869 | -0.00026906 | -0.0079212 | -0.0015274 | -0.005371 | 0.0022367 | 0.06592 | 0.047954 | -0.0086005 | 0.021187 | -0.0029843 | 0.018311 | 59.9991 | -61.5143 | 60.1273 | -61.2808 | -61.7157 | -61.702 | -0.018311 | 59.9854 | -61.5326 | 60.0723 | -61.4365 | -61.5875 | -61.6516 | -0.01831 | -0.082398 | 0.045776 | 0.21515 | -0.20599 | -0.21973 | -0.18768 | -0.20142 | -0.036621 | -0.09613 | -0.009155 | 0.05951 | -0.15564 | -0.091552 | -0.11902 | -0.054931 | 0.23346 | 121.6415 | 0.096131 | 121.6049 | 121.5134 | 121.5179 | 121.4951 | 121.4813 | -121.5958 | -121.6141 | 121.6232 | 121.5683 | 61.5143 | 61.4777
863.7188 | 121.7148 | -61.5509 | 60.0357 | -0.0045011 | 0.0041828 | 0.057059 | 0.058569 | 0.0010125 | -0.0064258 | -0.000673 | -0.0023192 | 0.0041593 | 0.067629 | 0.062267 | -0.0079597 | 0.021828 | -0.0027707 | -0.086975 | 59.9396 | -61.5784 | 60.0266 | -61.409 | -61.8484 | -61.8576 | -0.1236 | 59.9213 | -61.6104 | 59.9854 | -61.5646 | -61.7111 | -61.7294 | -0.027466 | -0.096131 | -0.009156 | 0.14191 | -0.3067 | -0.29755 | -0.27924 | -0.27008 | -0.05951 | -0.11444 | -0.050354 | -0.013733 | -0.17853 | -0.16022 | -0.11902 | -0.10071 | 0.16937 | 121.6049 | 0.045777 | 121.5958 | 121.5179 | 121.5317 | 121.4905 | 121.4722 | -121.6141 | -121.6461 | 121.5775 | 121.5363 | 61.4639 | 61.4273
865.4688 | 121.7422 | -61.496 | 60.1547 | -0.0045011 | 0.00012398 | 0.054282 | 0.052801 | 0.00058534 | -0.008562 | -0.0032364 | -0.0084228 | 0.0041593 | 0.069338 | 0.052654 | -0.0094549 | 0.023323 | -0.00084805 | -0.027466 | 59.9991 | -61.528 | 60.0861 | -61.2991 | -61.7477 | -61.7569 | -0.022888 | 59.9808 | -61.5463 | 60.0723 | -61.4456 | -61.5875 | -61.6425 | -0.032043 | -0.15564 | -0.068664 | 0.19684 | -0.26093 | -0.25177 | -0.22888 | -0.21973 | -0.050354 | -0.17395 | -0.082397 | 0.050354 | -0.14648 | -0.091552 | -0.09613 | -0.041198 | 0.22888 | 121.6141 | 0.10071 | 121.6187 | 121.5271 | 121.5271 | 121.4951 | 121.4767 | -121.6827 | -121.7011 | 121.582 | 121.5683 | 61.4685 | 61.4731
867.1719 | 121.8292 | -61.4594 | 60.0906 | -0.012131 | -0.0011578 | 0.0577 | 0.053015 | -0.0024055 | -0.0079212 | -0.000673 | -0.0023192 | 0.00052768 | 0.066347 | 0.059703 | -0.01031 | 0.020333 | -0.0029843 | 0.022888 | 59.967 | -61.528 | 60.2051 | -61.1893 | -61.647 | -61.6425 | 0.10071 | 59.9304 | -61.5509 | 60.141 | -61.3495 | -61.496 | -61.5509 | -0.068664 | -0.1236 | 0.11444 | 0.27008 | -0.18311 | -0.18768 | -0.11444 | -0.11902 | -0.091552 | -0.16022 | 0.050354 | 0.10986 | -0.091552 | -0.036621 | 0 | 0.054931 | 0.33875 | 121.7331 | 0.20142 | 121.6919 | 121.4951 | 121.4813 | 121.4264 | 121.3898 | -121.6187 | -121.6415 | 121.6644 | 121.6003 | 61.4822 | 61.5601
868.9375 | 121.788 | -61.5097 | 60.1181 | 0.0031279 | 0.0022602 | 0.057272 | 0.053869 | -0.00048286 | -0.0092028 | -0.002382 | -0.005371 | 0.0045865 | 0.067629 | 0.063762 | -0.010096 | 0.023323 | -0.0036253 | -0.018311 | 60.0128 | -61.5326 | 60.0906 | -61.3266 | -61.7294 | -61.7752 | -0.032043 | 59.9899 | -61.5738 | 60.0769 | -61.4319 | -61.5829 | -61.6287 | -0.022888 | -0.10529 | -0.027466 | 0.18311 | -0.2655 | -0.21973 | -0.24262 | -0.19684 | -0.064087 | -0.12817 | -0.041199 | 0.07782 | -0.11902 | -0.073242 | -0.054931 | -0.009155 | 0.20599 | 121.6232 | 0.14191 | 121.6507 | 121.5454 | 121.5637 | 121.5225 | 121.4996 | -121.6507 | -121.6919 | 121.6003 | 121.5866 | 61.4914 | 61.4777
870.6406 | 121.7422 | -61.5875 | 60.0494 | -0.0045011 | 0.00461 | 0.058981 | 0.056006 | 0.00037174 | -0.005144 | -0.0015274 | -0.0084228 | 0.0048001 | 0.067202 | 0.05714 | -0.0068915 | 0.023537 | 0.00021995 | -0.1236 | 59.9487 | -61.5967 | 59.9991 | -61.4227 | -61.8759 | -61.8759 | -0.12817 | 59.9167 | -61.6287 | 59.9991 | -61.5509 | -61.7111 | -61.7111 | -0.009156 | -0.10071 | -0.050354 | 0.1648 | -0.28839 | -0.28839 | -0.27924 | -0.27924 | -0.041199 | -0.13275 | -0.050354 | 0.036621 | -0.1236 | -0.1236 | -0.082398 | -0.082398 | 0.17395 | 121.5958 | 0.07782 | 121.6278 | 121.5454 | 121.5454 | 121.5363 | 121.5042 | -121.6461 | -121.6782 | 121.5866 | 121.5866 | 61.4639 | 61.4594
872.3906 | 121.8521 | -61.4731 | 60.0815 | -0.0045011 | 0.00033758 | 0.057486 | 0.053869 | -0.00048286 | -0.010057 | 0.0012496 | -0.0023192 | 0.0015957 | 0.066988 | 0.06248 | -0.0090277 | 0.023964 | -0.0046933 | 0.032043 | 59.9396 | -61.528 | 60.1959 | -61.1801 | -61.6379 | -61.6379 | 0.10986 | 59.9533 | -61.5189 | 60.1639 | -61.3495 | -61.4639 | -61.5463 | -0.054932 | -0.14191 | 0.11444 | 0.29297 | -0.16479 | -0.16479 | -0.10986 | -0.10986 | -0.045777 | -0.12817 | 0.082397 | 0.1236 | -0.073243 | 0.009155 | -0.027466 | 0.054932 | 0.3479 | 121.7239 | 0.16937 | 121.6827 | 121.4676 | 121.4722 | 121.4127 | 121.4264 | -121.6095 | -121.6003 | 121.669 | 121.637 | 61.5051 | 61.5829
874.0781 | 121.7422 | -61.5097 | 60.1089 | -0.012131 | 0.0014056 | 0.055136 | 0.056433 | 0.00037174 | -0.0059986 | -0.0019546 | -0.005371 | 0.0026639 | 0.067415 | 0.062908 | -0.01031 | 0.023323 | 0.00021995 | -0.027466 | 60.0128 | -61.5372 | 60.0861 | -61.2991 | -61.7523 | -61.7477 | -0.013733 | 60.0082 | -61.5189 | 60.0677 | -61.4594 | -61.5875 | -61.647 | -0.027465 | -0.096131 | -0.022888 | 0.21057 | -0.23804 | -0.24261 | -0.21057 | -0.21515 | -0.009155 | -0.10071 | -0.041199 | 0.050354 | -0.13733 | -0.077819 | -0.12817 | -0.068664 | 0.23804 | 121.6232 | 0.059509 | 121.5866 | 121.55 | 121.5271 | 121.5225 | 121.5179 | -121.6461 | -121.6278 | 121.5958 | 121.5775 | 61.4822 | 61.496
875.8281 | 121.8658 | -61.5463 | 59.967 | -0.012131 | 0.0014056 | 0.058127 | 0.053656 | 0.0035761 | -0.0079212 | -0.0011002 | -0.005371 | 0.0015957 | 0.067202 | 0.060771 | -0.010523 | 0.021614 | -0.0036253 | -0.059509 | 59.8938 | -61.5784 | 60.1227 | -61.2579 | -61.7386 | -61.7569 | 0 | 59.8297 | -61.5967 | 60.1044 | -61.409 | -61.5646 | -61.5921 | -0.032043 | -0.073242 | 0.15564 | 0.28839 | -0.21057 | -0.19226 | -0.17853 | -0.16022 | -0.050354 | -0.13733 | 0.13733 | 0.13733 | -0.045776 | -0.01831 | 0.004578 | 0.032044 | 0.32043 | 121.7011 | 0.18768 | 121.7011 | 121.4722 | 121.4264 | 121.4401 | 121.376 | -121.5454 | -121.5637 | 121.669 | 121.6507 | 61.4868 | 61.5463
877.5781 | 121.8796 | -61.4639 | 60.054 | -0.0045011 | -0.00051702 | 0.056204 | 0.053656 | -0.0019781 | -0.0094164 | -0.0013138 | -0.0084228 | 0.0018095 | 0.065493 | 0.054576 | -0.01095 | 0.022255 | 0.0012881 | 0.022888 | 59.935 | -61.528 | 60.228 | -61.1343 | -61.6013 | -61.6013 | 0.11902 | 59.9258 | -61.5234 | 60.173 | -61.3174 | -61.4548 | -61.528 | -0.064087 | -0.11902 | 0.17395 | 0.32959 | -0.13733 | -0.13733 | -0.073242 | -0.073242 | -0.059509 | -0.12817 | 0.11902 | 0.14648 | -0.064087 | 0.009155 | -0.004578 | 0.068664 | 0.39368 | 121.756 | 0.20599 | 121.6965 | 121.463 | 121.4493 | 121.3989 | 121.3898 | -121.582 | -121.5775 | 121.6919 | 121.637 | 61.4868 | 61.5829
879.3281 | 121.7422 | -61.5005 | 60.1181 | -0.0045011 | -0.002226 | 0.056204 | 0.053442 | -0.0021919 | -0.0074938 | -0.0043046 | -0.005371 | 0.0035183 | 0.067629 | 0.055644 | -0.010096 | 0.020974 | -0.00042085 | -0.004578 | 60.0128 | -61.5143 | 60.1135 | -61.2854 | -61.7294 | -61.7477 | -0.022888 | 59.9854 | -61.5097 | 60.0769 | -61.4456 | -61.5829 | -61.6562 | -0.013733 | -0.10529 | -0.004578 | 0.21515 | -0.24719 | -0.22888 | -0.23346 | -0.21515 | -0.009156 | -0.13275 | -0.041199 | 0.054931 | -0.15564 | -0.082398 | -0.14648 | -0.073242 | 0.22888 | 121.6278 | 0.064087 | 121.5866 | 121.5271 | 121.4951 | 121.5134 | 121.4859 | -121.6324 | -121.6278 | 121.6141 | 121.5775 | 61.496 | 61.4777
881.0781 | 121.875 | -61.4777 | 60.054 | -0.01976 | 0.001192 | 0.057059 | 0.053228 | -0.0030463 | -0.0074938 | -0.0055862 | -0.011475 | 0.00095488 | 0.06357 | 0.052013 | -0.0098823 | 0.02311 | -0.0072569 | -0.022888 | 59.9487 | -61.5143 | 60.1776 | -61.203 | -61.6562 | -61.647 | 0.050354 | 59.9121 | -61.5417 | 60.1685 | -61.3266 | -61.4639 | -61.5326 | -0.036621 | -0.10529 | 0.1236 | 0.27466 | -0.16937 | -0.17853 | -0.13275 | -0.14191 | -0.064087 | -0.14191 | 0.11444 | 0.15106 | -0.054932 | 0.013733 | 0.009155 | 0.07782 | 0.31128 | 121.6919 | 0.21515 | 121.7102 | 121.463 | 121.4539 | 121.4264 | 121.3898 | -121.5683 | -121.5958 | 121.6553 | 121.6461 | 61.4548 | 61.528
882.8281 | 121.8338 | -61.4868 | 60.0266 | -0.01976 | 0.0020466 | 0.054922 | 0.053442 | -0.0053961 | -0.0066394 | -0.002382 | -0.0084228 | 0.0022367 | 0.065493 | 0.056072 | -0.0088141 | 0.020974 | -0.00063445 | -0.082397 | 59.9121 | -61.5326 | 60.1044 | -61.3037 | -61.7386 | -61.7386 | -0.045776 | 59.8755 | -61.5692 | 60.0815 | -61.4365 | -61.5692 | -61.615 | -0.045777 | -0.11444 | 0.07782 | 0.1831 | -0.25177 | -0.25177 | -0.20599 | -0.20599 | -0.082398 | -0.15106 | 0.054932 | 0.050354 | -0.12817 | -0.082398 | -0.045776 | 0 | 0.22888 | 121.637 | 0.13275 | 121.6507 | 121.4447 | 121.4447 | 121.3989 | 121.3623 | -121.5591 | -121.5958 | 121.5912 | 121.5683 | 61.4044 | 61.441
884.5156 | 121.756 | -61.5326 | 60.0494 | -0.01976 | 0.002901 | 0.057486 | 0.056433 | 0.00079894 | -0.0089892 | -0.0021682 | -0.005371 | 0.0022367 | 0.062075 | 0.059703 | -0.0068915 | 0.021401 | -0.0051205 | -0.022888 | 59.967 | -61.5555 | 60.1044 | -61.2991 | -61.7706 | -61.7752 | -0.018311 | 59.9213 | -61.5875 | 60.0494 | -61.5051 | -61.6699 | -61.6837 | -0.022888 | -0.082397 | 0.054932 | 0.23346 | -0.24262 | -0.23804 | -0.21973 | -0.21515 | -0.054931 | -0.12817 | 0 | 0.027466 | -0.15106 | -0.13733 | -0.096131 | -0.082398 | 0.25635 | 121.6599 | 0.082397 | 121.637 | 121.5225 | 121.5088 | 121.4996 | 121.4539 | -121.6049 | -121.637 | 121.637 | 121.582 | 61.5097 | 61.5143
886.2656 | 121.7926 | -61.5326 | 60.0586 | -0.0045011 | 0.0033282 | 0.057059 | 0.054937 | -0.0028327 | -0.0070666 | 0.0012496 | -0.011475 | 0.0048001 | 0.065279 | 0.059917 | -0.010096 | 0.021401 | -0.0087521 | -0.004578 | 60.0037 | -61.5417 | 60.1181 | -61.2717 | -61.7386 | -61.7569 | 0.004578 | 59.9487 | -61.5692 | 60.0861 | -61.441 | -61.6058 | -61.6287 | -0.009155 | -0.054932 | 0.059509 | 0.26093 | -0.2243 | -0.20599 | -0.21515 | -0.19684 | -0.036621 | -0.10986 | 0.027466 | 0.091553 | -0.09613 | -0.073242 | -0.059509 | -0.036621 | 0.27008 | 121.6599 | 0.12817 | 121.6553 | 121.5454 | 121.5179 | 121.5363 | 121.4813 | -121.6003 | -121.6278 | 121.6507 | 121.6187 | 61.528 | 61.5372
888.0156 | 121.875 | -61.4868 | 60.0769 | -0.01976 | -0.002226 | 0.05535 | 0.052801 | 0.00015814 | -0.0089892 | -0.0013138 | -0.0084228 | 0.00031408 | 0.066347 | 0.059917 | -0.0090277 | 0.021828 | -0.0027707 | 0.018311 | 59.9625 | -61.5189 | 60.2142 | -61.1435 | -61.6196 | -61.6196 | 0.091553 | 59.9304 | -61.5051 | 60.1776 | -61.3129 | -61.4639 | -61.5326 | -0.032044 | -0.11444 | 0.13733 | 0.34332 | -0.13275 | -0.13275 | -0.10071 | -0.10071 | -0.018311 | -0.14648 | 0.10071 | 0.17395 | -0.045777 | 0.022888 | -0.027466 | 0.041199 | 0.37537 | 121.7331 | 0.19226 | 121.6827 | 121.4813 | 121.4355 | 121.4493 | 121.4172 | -121.5958 | -121.582 | 121.701 | 121.6644 | 61.5051 | 61.5784
889.7812 | 121.7606 | -61.5189 | 60.0632 | -0.0045011 | 0.0037556 | 0.056845 | 0.057287 | 0.0018671 | -0.0066394 | -0.0032364 | -0.0023192 | 0.0060819 | 0.066133 | 0.055858 | -0.0075323 | 0.020974 | -0.0049069 | -0.022888 | 59.9991 | -61.5646 | 60.1135 | -61.2762 | -61.734 | -61.7615 | -0.022888 | 59.9442 | -61.5509 | 60.0906 | -61.4594 | -61.615 | -61.647 | -0.045776 | -0.064087 | 0.050354 | 0.24261 | -0.24262 | -0.21515 | -0.19684 | -0.16937 | -0.032043 | -0.11902 | 0.027466 | 0.059509 | -0.12817 | -0.09613 | -0.096131 | -0.064087 | 0.28839 | 121.6782 | 0.091552 | 121.6415 | 121.5637 | 121.4951 | 121.5179 | 121.463 | -121.6278 | -121.6141 | 121.6324 | 121.6095 | 61.496 | 61.496
891.4688 | 121.7377 | -61.5738 | 60.054 | -0.0045011 | 0.00461 | 0.058981 | 0.055151 | 0.0022943 | -0.0059986 | -0.0019546 | -0.0023192 | 0.0020231 | 0.06827 | 0.057353 | -0.0088141 | 0.022896 | -0.0031979 | -0.073242 | 59.9625 | -61.5921 | 60.054 | -61.3586 | -61.8256 | -61.8256 | -0.15564 | 59.9167 | -61.6013 | 60.0128 | -61.5372 | -61.6837 | -61.6928 | -0.01831 | -0.091553 | 0 | 0.21515 | -0.25177 | -0.25177 | -0.23346 | -0.23346 | -0.027465 | -0.13733 | -0.041199 | 0.036622 | -0.11902 | -0.10986 | -0.091553 | -0.082398 | 0.23346 | 121.6461 | 0.064087 | 121.6141 | 121.5546 | 121.5179 | 121.5363 | 121.4905 | -121.6461 | -121.6553 | 121.6278 | 121.5866 | 61.5005 | 61.4182
893.2188 | 121.7606 | -61.4822 | 60.1181 | -0.01976 | 0.0031146 | 0.057059 | 0.05451 | -0.0013373 | -0.0064258 | -0.0008866 | -0.005371 | 0.0020231 | 0.068697 | 0.060985 | -0.0094549 | 0.021828 | -0.0025571 | -0.013733 | 60.0403 | -61.5463 | 60.0952 | -61.3037 | -61.7432 | -61.7569 | -0.11902 | 59.9808 | -61.5417 | 60.0906 | -61.4365 | -61.5829 | -61.6287 | -0.064087 | -0.07782 | -0.022888 | 0.17853 | -0.27466 | -0.26093 | -0.21057 | -0.19684 | -0.059509 | -0.13733 | -0.027466 | 0.045777 | -0.14648 | -0.10071 | -0.086975 | -0.041199 | 0.24262 | 121.6415 | 0.10529 | 121.6324 | 121.5866 | 121.5225 | 121.5225 | 121.463 | -121.6644 | -121.6599 | 121.5775 | 121.5729 | 61.4685 | 61.3632
894.9062 | 121.7468 | -61.5372 | 60.0677 | 0.0031279 | 0.00461 | 0.057059 | 0.055365 | 0.0022943 | -0.0062122 | -0.0021682 | -0.0023192 | 0.0026639 | 0.063997 | 0.063549 | -0.0083869 | 0.023323 | -0.0027707 | -0.027466 | 59.9991 | -61.5555 | 60.0723 | -61.3358 | -61.7889 | -61.8027 | -0.14648 | 59.9121 | -61.5692 | 60.0403 | -61.5005 | -61.6653 | -61.6882 | -0.018311 | -0.068665 | 0.004578 | 0.20142 | -0.2655 | -0.25177 | -0.24719 | -0.23346 | -0.032044 | -0.15564 | -0.027466 | 0.036621 | -0.15106 | -0.12817 | -0.11902 | -0.09613 | 0.21973 | 121.6278 | 0.068665 | 121.6095 | 121.5546 | 121.4813 | 121.5363 | 121.4493 | -121.6232 | -121.637 | 121.6095 | 121.5775 | 61.5097 | 61.3907
896.6562 | 121.8796 | -61.5417 | 59.9899 | -0.01976 | 0.002901 | 0.058127 | 0.055578 | 0.0042169 | -0.0045032 | -0.0008866 | -0.005371 | 0.0015957 | 0.065706 | 0.054149 | -0.011591 | 0.024391 | -0.00084805 | -0.091553 | 59.9304 | -61.5692 | 60.1044 | -61.2762 | -61.7752 | -61.7432 | -0.13275 | 59.848 | -61.5875 | 60.1044 | -61.4182 | -61.5601 | -61.5921 | -0.027466 | -0.059509 | 0.11444 | 0.2655 | -0.20142 | -0.23346 | -0.17395 | -0.20599 | -0.045776 | -0.14191 | 0.11444 | 0.1236 | -0.050354 | -0.018311 | -0.004578 | 0.027465 | 0.29297 | 121.6736 | 0.16937 | 121.6919 | 121.4996 | 121.4355 | 121.4722 | 121.3898 | -121.5591 | -121.5775 | 121.6461 | 121.6461 | 61.4502 | 61.409
898.4062 | 121.7651 | -61.5051 | 60.1181 | -0.01976 | 0.001192 | 0.056845 | 0.05686 | 0.0010125 | -0.0098438 | -3.1996e-05 | -0.005371 | 0.0028775 | 0.069124 | 0.056285 | -0.0094549 | 0.023964 | -0.0034117 | -0.022888 | 60.0632 | -61.5097 | 60.0861 | -61.29 | -61.7432 | -61.7432 | -0.21057 | 59.9991 | -61.5417 | 60.0769 | -61.441 | -61.5921 | -61.6333 | -0.004578 | -0.054932 | -0.032043 | 0.21515 | -0.23804 | -0.23804 | -0.23346 | -0.23346 | -0.036621 | -0.11902 | -0.041199 | 0.064087 | -0.12817 | -0.086975 | -0.091553 | -0.050354 | 0.21973 | 121.5958 | 0.10071 | 121.6187 | 121.5729 | 121.5408 | 121.5683 | 121.5042 | -121.6278 | -121.6599 | 121.5912 | 121.582 | 61.4822 | 61.2946
900.1719 | 121.7606 | -61.5509 | 60.0494 | -0.0045011 | 0.0037556 | 0.0577 | 0.055151 | -0.00091006 | -0.0066394 | -0.0011002 | -0.0023192 | 0.0011685 | 0.067202 | 0.055431 | -0.0081733 | 0.023323 | -0.0023435 | -0.059509 | 59.9899 | -61.5784 | 60.0677 | -61.3403 | -61.8073 | -61.8073 | -0.29297 | 59.9075 | -61.5692 | 60.0357 | -61.5189 | -61.6745 | -61.6745 | -0.027466 | -0.059509 | 0.018311 | 0.21057 | -0.25635 | -0.25635 | -0.22888 | -0.22888 | -0.018311 | -0.14191 | -0.013732 | 0.032043 | -0.1236 | -0.1236 | -0.10529 | -0.10529 | 0.23804 | 121.6461 | 0.050354 | 121.6049 | 121.5683 | 121.4767 | 121.5408 | 121.4584 | -121.6278 | -121.6187 | 121.6187 | 121.5866 | 61.4914 | 61.2579
901.8594 | 121.7926 | -61.5234 | 60.0677 | -0.0045011 | 0.0039692 | 0.057486 | 0.055365 | -0.0017645 | -0.0062122 | -0.0025956 | -0.005371 | 0.0039457 | 0.068483 | 0.052226 | -0.0094549 | 0.022042 | -0.0038389 | -0.013733 | 59.9899 | -61.5326 | 60.1273 | -61.2488 | -61.7249 | -61.7249 | -0.25177 | 59.935 | -61.5509 | 60.1044 | -61.4227 | -61.5738 | -61.615 | -0.009156 | -0.07782 | 0.059509 | 0.27466 | -0.20142 | -0.20142 | -0.19226 | -0.19226 | -0.027466 | -0.13275 | 0.036621 | 0.10071 | -0.091553 | -0.050355 | -0.064087 | -0.022889 | 0.28381 | 121.6599 | 0.12817 | 121.6553 | 121.5225 | 121.4859 | 121.5134 | 121.4584 | -121.6003 | -121.6187 | 121.6507 | 121.6278 | 61.5097 | 61.2717
903.625 | 121.8887 | -61.4502 | 60.0632 | -0.0045011 | -8.9824e-05 | 0.056204 | 0.054724 | -0.0032599 | -0.0062122 | -0.0015274 | -0.0084228 | 0.00031408 | 0.066133 | 0.056499 | -0.012446 | 0.023964 | 0.00021995 | 0 | 59.967 | -61.5326 | 60.2325 | -61.1252 | -61.6013 | -61.5875 | -0.24719 | 59.935 | -61.528 | 60.1685 | -61.3037 | -61.4182 | -61.5097 | -0.082398 | -0.09613 | 0.16937 | 0.32501 | -0.13733 | -0.15106 | -0.054931 | -0.068664 | -0.07782 | -0.12817 | 0.10529 | 0.14648 | -0.05951 | 0.032043 | 0.01831 | 0.10986 | 0.40741 | 121.7651 | 0.2243 | 121.6965 | 121.4996 | 121.463 | 121.4172 | 121.3852 | -121.5958 | -121.5912 | 121.6827 | 121.6187 | 61.4502 | 61.203
905.3906 | 121.7743 | -61.4594 | 60.1318 | -0.0045011 | 0.001192 | 0.057059 | 0.051306 | -0.0041145 | -0.0094164 | -0.0036636 | -0.005371 | 0.00095488 | 0.066988 | 0.05244 | -0.013941 | 0.021187 | -0.0031979 | 0.022888 | 59.9854 | -61.5097 | 60.1913 | -61.1984 | -61.6562 | -61.647 | -0.39368 | 59.9808 | -61.5005 | 60.1135 | -61.3998 | -61.5326 | -61.6104 | -0.050354 | -0.14648 | 0.059509 | 0.26093 | -0.18768 | -0.19684 | -0.13733 | -0.14648 | -0.041198 | -0.15106 | -0.018311 | 0.05951 | -0.15106 | -0.073242 | -0.10986 | -0.032044 | 0.31128 | 121.701 | 0.10071 | 121.6141 | 121.4951 | 121.4813 | 121.4447 | 121.4401 | -121.6415 | -121.6324 | 121.6507 | 121.5729 | 61.4822 | 61.0657
907.0781 | 121.8338 | -61.4502 | 60.1089 | -0.01976 | -0.00073062 | 0.054709 | 0.052374 | -5.5462e-05 | -0.006853 | -0.000673 | -0.005371 | 0.0033047 | 0.065493 | 0.049663 | -0.012019 | 0.021401 | -0.0038389 | 0.022888 | 59.9945 | -61.5051 | 60.2234 | -61.1755 | -61.6196 | -61.6241 | -0.45319 | 59.967 | -61.4914 | 60.1822 | -61.3083 | -61.4639 | -61.5189 | -0.054932 | -0.11444 | 0.11444 | 0.27466 | -0.17395 | -0.16937 | -0.11902 | -0.11444 | -0.041199 | -0.14191 | 0.073242 | 0.14191 | -0.068665 | -0.013733 | -0.027466 | 0.027466 | 0.32959 | 121.7285 | 0.1831 | 121.6736 | 121.4996 | 121.4584 | 121.4447 | 121.4172 | -121.6141 | -121.6003 | 121.6736 | 121.6324 | 61.4731 | 60.997
908.8594 | 121.8704 | -61.4319 | 60.0952 | -0.012131 | -0.0011578 | 0.056845 | 0.05152 | -0.0049689 | -0.0072802 | -0.002382 | -0.005371 | 0.0033047 | 0.065065 | 0.059703 | -0.012873 | 0.020546 | -0.00084805 | 0.013733 | 59.9625 | -61.4822 | 60.2234 | -61.1389 | -61.5875 | -61.6287 | -0.54016 | 59.9396 | -61.5097 | 60.1822 | -61.2946 | -61.441 | -61.5097 | -0.050354 | -0.13275 | 0.12817 | 0.29297 | -0.19684 | -0.15564 | -0.14648 | -0.10529 | -0.07782 | -0.15564 | 0.086975 | 0.13733 | -0.07782 | -0.009155 | 0 | 0.068665 | 0.34332 | 121.7056 | 0.21515 | 121.6919 | 121.4447 | 121.4493 | 121.3943 | 121.3715 | -121.5775 | -121.6049 | 121.6553 | 121.6141 | 61.4456 | 60.8917
910.5625 | 121.7468 | -61.5326 | 60.0723 | -0.01976 | 0.0050372 | 0.0577 | 0.05686 | 0.0027215 | -0.0059986 | -0.0008866 | -0.0084228 | 0.0052273 | 0.064211 | 0.055858 | -0.010523 | 0.020119 | -0.0029843 | -0.022888 | 60.022 | -61.5555 | 60.1135 | -61.2991 | -61.7706 | -61.7706 | -0.8194 | 59.9579 | -61.5555 | 60.0586 | -61.5005 | -61.6516 | -61.6745 | -0.022888 | -0.050354 | 0.041198 | 0.23346 | -0.23804 | -0.23804 | -0.21515 | -0.21515 | -0.022888 | -0.11444 | -0.013733 | 0.032044 | -0.14191 | -0.11902 | -0.11902 | -0.09613 | 0.25635 | 121.669 | 0.054932 | 121.6141 | 121.5775 | 121.5134 | 121.5546 | 121.4905 | -121.6278 | -121.6278 | 121.6461 | 121.5912 | 61.5097 | 60.7132
912.3281 | 121.7834 | -61.4777 | 60.1044 | -0.012131 | 0.002901 | 0.057486 | 0.056219 | 0.0012261 | -0.0066394 | 0.0001816 | -0.0023192 | 0.0028775 | 0.065065 | 0.057994 | -0.0090277 | 0.021614 | 0.0010745 | 0 | 59.9945 | -61.5326 | 60.1456 | -61.2534 | -61.734 | -61.7203 | -0.90637 | 59.967 | -61.5326 | 60.1135 | -61.3998 | -61.5601 | -61.5921 | -0.054932 | -0.10986 | 0.041199 | 0.2243 | -0.24262 | -0.25635 | -0.18768 | -0.20142 | -0.054932 | -0.13733 | 0.009155 | 0.07782 | -0.11444 | -0.082398 | -0.059509 | -0.027466 | 0.27924 | 121.6782 | 0.13275 | 121.6461 | 121.5271 | 121.4996 | 121.4722 | 121.4447 | -121.637 | -121.637 | 121.6232 | 121.5912 | 61.4777 | 60.5713
914.0781 | 121.8292 | -61.4822 | 60.0723 | -0.012131 | 0.002901 | 0.055991 | 0.053228 | -0.0019781 | -0.0066394 | 0.0001816 | -0.005371 | 0.0018095 | 0.065493 | 0.056285 | -0.0096685 | 0.022469 | 0.0012881 | -0.07782 | 59.9625 | -61.496 | 60.1181 | -61.2671 | -61.7203 | -61.7111 | -1.1444 | 59.9075 | -61.5417 | 60.0952 | -61.4044 | -61.5509 | -61.5967 | -0.013733 | -0.10986 | 0.045776 | 0.21515 | -0.22888 | -0.23804 | -0.21515 | -0.2243 | -0.059509 | -0.16479 | 0.022888 | 0.07782 | -0.11444 | -0.068664 | -0.054932 | -0.009155 | 0.22888 | 121.6141 | 0.13733 | 121.637 | 121.4584 | 121.4493 | 121.4447 | 121.3898 | -121.5683 | -121.6141 | 121.6003 | 121.5775 | 61.4044 | 60.3378
915.7812 | 121.7972 | -61.4777 | 60.0952 | -0.0045011 | 0.0043964 | 0.057486 | 0.058996 | 0.0010125 | -0.006853 | -0.0032364 | -0.011475 | 0.0052273 | 0.066988 | 0.063121 | -0.0096685 | 0.021614 | -0.0053343 | 0 | 60.0403 | -61.5143 | 60.1364 | -61.2488 | -61.7065 | -61.7294 | -1.236 | 59.9808 | -61.5051 | 60.141 | -61.3861 | -61.5692 | -61.5784 | -0.036621 | -0.054932 | 0.041199 | 0.22888 | -0.25177 | -0.22888 | -0.21515 | -0.19226 | -0.027466 | -0.11444 | 0.045776 | 0.091553 | -0.10071 | -0.091553 | -0.073242 | -0.064087 | 0.2655 | 121.6507 | 0.11902 | 121.6461 | 121.5546 | 121.4859 | 121.5179 | 121.4584 | -121.6095 | -121.6003 | 121.6141 | 121.6187 | 61.4777 | 60.2417
917.5312 | 121.7514 | -61.4685 | 60.141 | -0.02739 | 0.00055118 | 0.054922 | 0.054083 | -0.0066779 | -0.0059986 | -0.0032364 | -0.0023192 | 0.0030911 | 0.066133 | 0.062053 | -0.0088141 | 0.023964 | -0.0044797 | -0.022888 | 60.0586 | -61.5051 | 60.1227 | -61.2762 | -61.702 | -61.7294 | -1.5198 | 60.022 | -61.5051 | 60.1044 | -61.3907 | -61.5509 | -61.5875 | -0.036621 | -0.082397 | -0.01831 | 0.19226 | -0.26093 | -0.23346 | -0.2243 | -0.19684 | -0.036621 | -0.11902 | -0.036621 | 0.07782 | -0.11902 | -0.082397 | -0.082397 | -0.045776 | 0.22888 | 121.6278 | 0.11444 | 121.6095 | 121.5637 | 121.5271 | 121.5271 | 121.4905 | -121.6461 | -121.6461 | 121.5912 | 121.5729 | 61.4456 | 59.9487
919.2188 | 121.756 | -61.4456 | 60.1547 | -0.0045011 | -0.0011578 | 0.056204 | 0.050879 | 0.0050713 | -0.0066394 | -0.0030228 | -0.005371 | 0.0028775 | 0.06592 | 0.056072 | -0.011164 | 0.021828 | -0.0044797 | 0.013733 | 60.0357 | -61.4777 | 60.2005 | -61.1938 | -61.615 | -61.6608 | -1.6754 | 60.0174 | -61.4594 | 60.1318 | -61.3678 | -61.5189 | -61.5875 | -0.032043 | -0.11902 | 0.045776 | 0.25177 | -0.21515 | -0.16937 | -0.18311 | -0.13733 | -0.013733 | -0.13733 | -0.022888 | 0.07782 | -0.14191 | -0.073242 | -0.12817 | -0.059509 | 0.28381 | 121.6782 | 0.091553 | 121.5912 | 121.5134 | 121.4767 | 121.4813 | 121.463 | -121.6324 | -121.6141 | 121.6461 | 121.5775 | 61.4594 | 59.7702
920.9688 | 121.7789 | -61.4868 | 60.0952 | -0.01976 | 0.0061054 | 0.057059 | 0.055578 | 0.0035761 | -0.0081348 | -0.0015274 | -0.005371 | 0.0026639 | 0.066561 | 0.056499 | -0.0086005 | 0.022042 | -0.0046933 | 0 | 60.0449 | -61.496 | 60.1593 | -61.2442 | -61.7065 | -61.7065 | -1.8814 | 59.9991 | -61.5326 | 60.1227 | -61.3953 | -61.5967 | -61.6013 | -0.009156 | -0.050354 | 0.064087 | 0.24261 | -0.21973 | -0.21973 | -0.21057 | -0.21057 | -0.045777 | -0.096131 | 0.027466 | 0.091552 | -0.11444 | -0.10986 | -0.068664 | -0.064087 | 0.25177 | 121.6553 | 0.13733 | 121.6553 | 121.5408 | 121.5317 | 121.5317 | 121.4859 | -121.5912 | -121.6278 | 121.6461 | 121.6095 | 61.4868 | 59.6054
922.7188 | 121.8155 | -61.4548 | 60.1273 | 0.0031279 | 0.0022602 | 0.053854 | 0.051733 | -0.0032599 | -0.0053576 | -0.0013138 | -0.005371 | 0.0013821 | 0.067202 | 0.05479 | -0.012446 | 0.022042 | -0.0029843 | -0.091553 | 59.9533 | -61.5097 | 60.1547 | -61.2259 | -61.6791 | -61.6837 | -2.1423 | 59.9579 | -61.5051 | 60.1273 | -61.3449 | -61.5051 | -61.5646 | -0.054932 | -0.17395 | 0.027466 | 0.22888 | -0.22888 | -0.2243 | -0.17395 | -0.16937 | -0.050354 | -0.16937 | 0 | 0.10986 | -0.10986 | -0.050354 | -0.059509 | 0 | 0.28381 | 121.6644 | 0.16022 | 121.6324 | 121.463 | 121.463 | 121.4081 | 121.4127 | -121.637 | -121.6324 | 121.6095 | 121.582 | 61.3632 | 59.3124
924.4062 | 121.875 | -61.4685 | 60.0311 | -0.0045011 | 0.0020466 | 0.056631 | 0.055792 | 0.00015814 | -0.0059986 | -0.0043046 | -0.005371 | 0.0013821 | 0.065706 | 0.06248 | -0.0096685 | 0.022896 | -0.0017027 | -0.050354 | 59.9487 | -61.4868 | 60.1868 | -61.203 | -61.6837 | -61.6745 | -2.2842 | 59.9258 | -61.5372 | 60.1913 | -61.3266 | -61.5143 | -61.528 | -0.01831 | -0.082398 | 0.15564 | 0.2655 | -0.20599 | -0.21515 | -0.18768 | -0.19684 | -0.068664 | -0.10529 | 0.16022 | 0.14191 | -0.059509 | -0.045776 | 0.009155 | 0.022888 | 0.28381 | 121.6736 | 0.21057 | 121.7285 | 121.4355 | 121.463 | 121.4172 | 121.3943 | -121.5179 | -121.5683 | 121.6553 | 121.6599 | 61.4182 | 59.1843
926.1562 | 121.7743 | -61.4639 | 60.141 | -0.0045011 | 0.0033282 | 0.056631 | 0.056219 | 0.0057123 | -0.0089892 | -0.0013138 | -0.005371 | 0.0037321 | 0.06827 | 0.049236 | -0.01031 | 0.021828 | -0.0038389 | -0.018311 | 60.0494 | -61.4914 | 60.1822 | -61.235 | -61.6745 | -61.6928 | -2.5406 | 60.0266 | -61.496 | 60.141 | -61.377 | -61.5692 | -61.5875 | -0.027466 | -0.091553 | 0.041199 | 0.22888 | -0.22888 | -0.21057 | -0.20142 | -0.18311 | -0.032044 | -0.11444 | 0 | 0.086975 | -0.1236 | -0.10529 | -0.091552 | -0.073242 | 0.25635 | 121.6736 | 0.11902 | 121.637 | 121.5408 | 121.5225 | 121.5134 | 121.4905 | -121.6324 | -121.637 | 121.6461 | 121.6049 | 61.4456 | 58.9233
927.9062 | 121.8933 | -61.4227 | 60.1181 | -0.012131 | -0.0017986 | 0.056845 | 0.052588 | -0.00026906 | -0.0074938 | -0.0036636 | -0.005371 | -0.00075412 | 0.06592 | 0.056499 | -0.011591 | 0.021614 | -0.0017027 | -0.027466 | 60.0403 | -61.441 | 60.2554 | -61.1114 | -61.5601 | -61.5784 | -2.6917 | 59.9533 | -61.4685 | 60.2371 | -61.2213 | -61.3678 | -61.4548 | -0.018311 | -0.07782 | 0.13733 | 0.31128 | -0.15564 | -0.13733 | -0.13733 | -0.11902 | -0.045777 | -0.16479 | 0.11902 | 0.20142 | -0.032044 | 0.054931 | 0.013733 | 0.10071 | 0.32959 | 121.6965 | 0.24719 | 121.7056 | 121.4813 | 121.4218 | 121.463 | 121.376 | -121.5591 | -121.5866 | 121.6782 | 121.6599 | 61.3953 | 58.7311
929.6562 | 121.8338 | -61.4273 | 60.141 | -0.012131 | 0.00033758 | 0.055136 | 0.05152 | 0.00015814 | -0.0070666 | -0.0008866 | -0.0084228 | 0.0011685 | 0.065493 | 0.053935 | -0.014155 | 0.022255 | -0.0036253 | -0.091553 | 60.0266 | -61.4914 | 60.1776 | -61.2167 | -61.6608 | -61.6516 | -3.067 | 59.9716 | -61.4777 | 60.173 | -61.3083 | -61.4822 | -61.5189 | -0.064087 | -0.11444 | 0.036621 | 0.21057 | -0.2243 | -0.23346 | -0.16022 | -0.16937 | -0.050354 | -0.16937 | 0.032044 | 0.11902 | -0.091553 | -0.054932 | -0.041199 | -0.004578 | 0.27466 | 121.669 | 0.16937 | 121.6507 | 121.5179 | 121.4493 | 121.4539 | 121.3989 | -121.6324 | -121.6187 | 121.6049 | 121.6003 | 61.3358 | 58.3603
931.3594 | 121.7422 | -61.3953 | 60.2005 | -0.0045011 | 0.001192 | 0.056418 | 0.055151 | -0.0021919 | -0.0070666 | -0.0019546 | -0.005371 | 0.0026639 | 0.066774 | 0.056713 | -0.011805 | 0.020974 | -0.00020725 | -0.027466 | 60.1044 | -61.4594 | 60.1868 | -61.2076 | -61.6333 | -61.6516 | -3.273 | 60.0815 | -61.4594 | 60.1547 | -61.3037 | -61.4914 | -61.5463 | -0.064087 | -0.09613 | -0.013732 | 0.18768 | -0.25635 | -0.23804 | -0.19226 | -0.17395 | -0.064087 | -0.11902 | -0.045776 | 0.091553 | -0.15106 | -0.09613 | -0.086975 | -0.032043 | 0.25177 | 121.6461 | 0.15564 | 121.6141 | 121.5637 | 121.5408 | 121.4996 | 121.4767 | -121.6599 | -121.6599 | 121.582 | 121.55 | 61.3678 | 58.1223
933.1094 | 121.8704 | -61.4548 | 60.0815 | -0.0045011 | 0.0048236 | 0.057913 | 0.054297 | -0.0045417 | -0.0055712 | -0.0021682 | -0.005371 | 0.0022367 | 0.064211 | 0.057353 | -0.011164 | 0.023323 | -0.0036253 | -0.064087 | 60.0037 | -61.4731 | 60.228 | -61.1618 | -61.6333 | -61.6241 | -3.4058 | 59.9442 | -61.4868 | 60.2142 | -61.2579 | -61.4731 | -61.5097 | -0.01831 | -0.07782 | 0.14648 | 0.29297 | -0.16937 | -0.17853 | -0.15106 | -0.16022 | -0.032043 | -0.13733 | 0.13275 | 0.19684 | -0.054932 | -0.01831 | -0.022889 | 0.013733 | 0.31128 | 121.701 | 0.22888 | 121.701 | 121.4767 | 121.431 | 121.4584 | 121.3989 | -121.5546 | -121.5683 | 121.6827 | 121.669 | 61.3907 | 58.049
934.7969 | 121.8658 | -61.3998 | 60.1318 | -0.012131 | -0.00051702 | 0.057486 | 0.055151 | -0.0028327 | -0.0066394 | -0.0025956 | -0.0084228 | 0.00074128 | 0.06592 | 0.055004 | -0.0098823 | 0.021187 | 0.00021995 | -0.064087 | 60.0632 | -61.4456 | 60.2097 | -61.1755 | -61.6333 | -61.6196 | -3.6438 | 60.0037 | -61.4548 | 60.2234 | -61.235 | -61.409 | -61.4777 | -0.045777 | -0.068665 | 0.07782 | 0.2243 | -0.21973 | -0.23346 | -0.17395 | -0.18768 | -0.054932 | -0.12817 | 0.091553 | 0.1648 | -0.07782 | -0.009156 | -0.022888 | 0.045776 | 0.27008 | 121.6553 | 0.21973 | 121.6782 | 121.5088 | 121.4584 | 121.463 | 121.4035 | -121.5775 | -121.5866 | 121.6095 | 121.6232 | 61.3358 | 57.756
936.5625 | 121.7651 | -61.409 | 60.2051 | -0.01976 | -8.9824e-05 | 0.056631 | 0.053656 | -0.0013373 | -0.0081348 | -0.0004592 | -0.0084228 | 0.0013821 | 0.067629 | 0.057994 | -0.010096 | 0.021401 | -0.0010617 | 0.027466 | 60.0815 | -61.4136 | 60.2646 | -61.1206 | -61.5875 | -61.5784 | -3.8086 | 60.0586 | -61.4044 | 60.2097 | -61.2671 | -61.4456 | -61.5234 | -0.004577 | -0.1236 | 0.059509 | 0.28839 | -0.16937 | -0.17853 | -0.1648 | -0.17395 | 0.004578 | -0.14648 | 0.004578 | 0.14191 | -0.11444 | -0.036621 | -0.11902 | -0.041199 | 0.29297 | 121.6782 | 0.13733 | 121.6141 | 121.4951 | 121.463 | 121.4905 | 121.4676 | -121.6187 | -121.6095 | 121.6736 | 121.6187 | 61.4365 | 57.6004
938.3281 | 121.7514 | -61.3953 | 60.2234 | 0.0031279 | 0.0026874 | 0.056204 | 0.057501 | -5.5462e-05 | -0.0081348 | -0.000673 | -0.0084228 | 0.0033047 | 0.06357 | 0.06184 | -0.0096685 | 0.022042 | -0.0012753 | -0.022888 | 60.1639 | -61.4136 | 60.2142 | -61.2076 | -61.6425 | -61.6608 | -4.0054 | 60.1044 | -61.4456 | 60.1685 | -61.2854 | -61.4868 | -61.528 | -0.01831 | -0.05951 | -0.009156 | 0.18768 | -0.2655 | -0.24719 | -0.24719 | -0.22888 | -0.050354 | -0.11902 | -0.054932 | 0.10986 | -0.13275 | -0.091552 | -0.082397 | -0.041198 | 0.20599 | 121.6278 | 0.16022 | 121.6141 | 121.5775 | 121.55 | 121.5591 | 121.4996 | -121.637 | -121.669 | 121.6095 | 121.5637 | 61.3724 | 57.3898
940.0312 | 121.7377 | -61.377 | 60.2051 | -0.012131 | 0.00033758 | 0.056204 | 0.054937 | -0.0017645 | -0.0066394 | -0.0028092 | -0.005371 | 0.0041593 | 0.064424 | 0.056499 | -0.010096 | 0.020974 | -0.0040525 | 0.013733 | 60.0952 | -61.3998 | 60.2509 | -61.1343 | -61.5829 | -61.5921 | -4.0512 | 60.0906 | -61.441 | 60.1685 | -61.2579 | -61.4685 | -61.5326 | -0.022888 | -0.10986 | 0.045776 | 0.24262 | -0.21515 | -0.20599 | -0.19226 | -0.18311 | -0.064087 | -0.11444 | -0.036621 | 0.11902 | -0.15564 | -0.091553 | -0.091553 | -0.027466 | 0.2655 | 121.6507 | 0.1831 | 121.6095 | 121.4951 | 121.5317 | 121.4722 | 121.4676 | -121.6049 | -121.6461 | 121.6278 | 121.5454 | 61.3907 | 57.3257
941.7812 | 121.8567 | -61.377 | 60.1547 | -0.012131 | 0.00033758 | 0.056631 | 0.053442 | -0.00069646 | -0.0066394 | -0.00345 | -0.0023192 | 0.0020231 | 0.065706 | 0.049236 | -0.011378 | 0.02076 | -0.0027707 | -0.068665 | 60.0815 | -61.441 | 60.2554 | -61.1343 | -61.5692 | -61.5646 | -4.129 | 60.0128 | -61.4365 | 60.26 | -61.171 | -61.3632 | -61.4365 | -0.064087 | -0.073242 | 0.10071 | 0.24262 | -0.18768 | -0.19226 | -0.1236 | -0.12817 | -0.059509 | -0.14191 | 0.10529 | 0.20599 | -0.059509 | 0.013733 | 0 | 0.073242 | 0.3067 | 121.6965 | 0.2655 | 121.6965 | 121.5225 | 121.4493 | 121.4584 | 121.3898 | -121.5958 | -121.5912 | 121.6324 | 121.637 | 61.3083 | 57.2479
943.5312 | 121.8109 | -61.4227 | 60.1181 | -0.0045011 | 0.0016192 | 0.055563 | 0.054937 | -0.0019781 | -0.0055712 | -0.0030228 | -0.0084228 | -0.00032692 | 0.067202 | 0.057994 | -0.011164 | 0.023323 | -0.0038389 | -0.086975 | 60.0174 | -61.4502 | 60.228 | -61.1664 | -61.6379 | -61.6196 | -4.3579 | 59.9991 | -61.4502 | 60.2142 | -61.2717 | -61.4502 | -61.4914 | -0.027466 | -0.10071 | 0.10986 | 0.25635 | -0.19684 | -0.21515 | -0.16937 | -0.18768 | -0.027466 | -0.11902 | 0.09613 | 0.15106 | -0.068665 | -0.027466 | -0.041199 | 0 | 0.28381 | 121.6782 | 0.17853 | 121.6644 | 121.4676 | 121.4493 | 121.4401 | 121.4218 | -121.5683 | -121.5683 | 121.6507 | 121.637 | 61.3358 | 57.0648
945.2812 | 121.8338 | -61.3998 | 60.141 | -0.01976 | 0.0026874 | 0.056845 | 0.054083 | -0.0017645 | -0.0089892 | -0.000673 | -0.005371 | 0.00095488 | 0.06592 | 0.058208 | -0.011805 | 0.02076 | -0.0017027 | -0.086975 | 60.0266 | -61.4594 | 60.2142 | -61.171 | -61.6379 | -61.6333 | -4.5868 | 60.0037 | -61.4868 | 60.1959 | -61.2488 | -61.4365 | -61.5189 | -0.05951 | -0.11444 | 0.073242 | 0.22888 | -0.23346 | -0.23804 | -0.17395 | -0.17853 | -0.086975 | -0.13733 | 0.054932 | 0.15106 | -0.11902 | -0.036621 | -0.032044 | 0.050354 | 0.28839 | 121.6736 | 0.23804 | 121.6827 | 121.4859 | 121.4905 | 121.4264 | 121.4035 | -121.6003 | -121.6278 | 121.6141 | 121.5958 | 61.3129 | 56.813
947.0312 | 121.788 | -61.409 | 60.1959 | -0.012131 | 0.0020466 | 0.055991 | 0.057501 | -0.0021919 | -0.0081348 | -0.0013138 | -0.0084228 | 0.0050137 | 0.06592 | 0.063549 | -0.0094549 | 0.021401 | -0.0049069 | -0.009155 | 60.1181 | -61.4456 | 60.2142 | -61.203 | -61.6241 | -61.6425 | -4.6646 | 60.0998 | -61.4273 | 60.2005 | -61.235 | -61.4777 | -61.5097 | -0.036621 | -0.07782 | 0.01831 | 0.20599 | -0.23346 | -0.21515 | -0.19684 | -0.17853 | -0.01831 | -0.096131 | 0.004577 | 0.17395 | -0.10071 | -0.068664 | -0.082398 | -0.050354 | 0.24262 | 121.6599 | 0.19226 | 121.6278 | 121.5637 | 121.5271 | 121.5271 | 121.5088 | -121.6415 | -121.6232 | 121.6232 | 121.6095 | 61.3998 | 56.7444
948.7344 | 121.7789 | -61.409 | 60.173 | -0.012131 | 0.002901 | 0.057486 | 0.056646 | -0.0021919 | -0.0072802 | -0.0013138 | -0.0084228 | 0.0045865 | 0.066988 | 0.065471 | -0.0083869 | 0.021401 | -0.0038389 | -0.004578 | 60.0906 | -61.4594 | 60.2234 | -61.1755 | -61.6379 | -61.6562 | -4.7791 | 60.0357 | -61.4594 | 60.1868 | -61.2534 | -61.496 | -61.5326 | -0.050354 | -0.082398 | 0.050354 | 0.23346 | -0.24719 | -0.22888 | -0.19684 | -0.17853 | -0.050354 | -0.13733 | 0.013733 | 0.15564 | -0.1236 | -0.086975 | -0.073242 | -0.036621 | 0.28381 | 121.6827 | 0.20599 | 121.6461 | 121.55 | 121.4951 | 121.4996 | 121.4447 | -121.6324 | -121.6324 | 121.6324 | 121.5958 | 61.4044 | 56.6299
950.5 | 121.8292 | -61.377 | 60.1501 | -0.012131 | 0.00055118 | 0.057486 | 0.052374 | -0.0036871 | -0.0062122 | -0.000673 | -0.0023192 | 0.0024503 | 0.065279 | 0.057994 | -0.011378 | 0.021401 | -0.0042661 | 0.022888 | 60.0494 | -61.4182 | 60.3058 | -61.0748 | -61.5372 | -61.5463 | -4.8386 | 60.0128 | -61.4365 | 60.2737 | -61.1389 | -61.3678 | -61.4319 | -0.041199 | -0.10071 | 0.15564 | 0.30212 | -0.16937 | -0.16022 | -0.12817 | -0.11902 | -0.059509 | -0.13733 | 0.1236 | 0.23804 | -0.054932 | 0.009155 | 0.004577 | 0.068664 | 0.34332 | 121.7239 | 0.29755 | 121.7102 | 121.4676 | 121.4493 | 121.4264 | 121.3898 | -121.5683 | -121.5866 | 121.6827 | 121.6507 | 61.3998 | 56.5384
952.25 | 121.8521 | -61.4456 | 60.0769 | -0.0045011 | 0.0041828 | 0.057913 | 0.054083 | -0.0015509 | -0.0070666 | -0.0025956 | -0.0023192 | 0.0024503 | 0.064211 | 0.056713 | -0.01031 | 0.023964 | -0.00042085 | -0.064087 | 60.0037 | -61.4594 | 60.2371 | -61.1435 | -61.6379 | -61.6241 | -4.9805 | 59.9533 | -61.4685 | 60.2051 | -61.2442 | -61.4594 | -61.5097 | -0.013733 | -0.073242 | 0.16022 | 0.30212 | -0.17853 | -0.19226 | -0.1648 | -0.17853 | -0.022888 | -0.1236 | 0.12817 | 0.20142 | -0.064087 | -0.013733 | -0.041199 | 0.009155 | 0.31586 | 121.6965 | 0.2243 | 121.6736 | 121.463 | 121.4218 | 121.4493 | 121.3989 | -121.5363 | -121.5454 | 121.6827 | 121.6507 | 61.3815 | 56.4651
953.9375 | 121.8338 | -61.3953 | 60.1456 | -0.0045011 | -8.9824e-05 | 0.056204 | 0.053869 | -0.0013373 | -0.0094164 | -0.0045182 | -0.0023192 | -0.00011332 | 0.062502 | 0.051158 | -0.011378 | 0.02311 | -0.0019163 | -0.09613 | 60.0311 | -61.4548 | 60.2097 | -61.1847 | -61.6516 | -61.6333 | -5.1178 | 59.9991 | -61.4685 | 60.2188 | -61.2167 | -61.441 | -61.4822 | -0.059509 | -0.11444 | 0.064087 | 0.21057 | -0.23804 | -0.25635 | -0.17853 | -0.19684 | -0.073242 | -0.14648 | 0.073242 | 0.17853 | -0.086975 | -0.045776 | -0.013733 | 0.027466 | 0.27008 | 121.6644 | 0.25177 | 121.6873 | 121.4859 | 121.4676 | 121.4264 | 121.3943 | -121.6003 | -121.6141 | 121.6049 | 121.6141 | 61.2991 | 56.2775
955.6875 | 121.7422 | -61.4548 | 60.1181 | -0.01976 | 0.0041828 | 0.058981 | 0.057287 | -0.00091006 | -0.0047168 | -0.0030228 | -0.005371 | 0.0050137 | 0.064852 | 0.05949 | -0.0079597 | 0.019905 | -0.0042661 | -0.10986 | 60.0586 | -61.4868 | 60.1089 | -61.3174 | -61.7615 | -61.7615 | -5.4016 | 59.9991 | -61.5234 | 60.1044 | -61.3586 | -61.5921 | -61.5967 | -0.032043 | -0.059509 | -0.009155 | 0.13733 | -0.3067 | -0.3067 | -0.27466 | -0.27466 | -0.068664 | -0.11902 | -0.013733 | 0.09613 | -0.14191 | -0.13733 | -0.073243 | -0.068665 | 0.16937 | 121.5958 | 0.16479 | 121.6278 | 121.5454 | 121.5225 | 121.5134 | 121.4539 | -121.6049 | -121.6415 | 121.5637 | 121.5591 | 61.3449 | 56.0532
957.4375 | 121.7789 | -61.377 | 60.1822 | -0.0045011 | 0.0020466 | 0.054709 | 0.052374 | -0.0043281 | -0.00963 | -0.0055862 | -0.005371 | 0.0022367 | 0.065065 | 0.054149 | -0.0094549 | 0.022683 | -0.0046933 | 0.018311 | 60.0586 | -61.4319 | 60.2692 | -61.1114 | -61.5829 | -61.5738 | -5.3513 | 60.0632 | -61.4319 | 60.2051 | -61.2167 | -61.441 | -61.5051 | -0.054932 | -0.1236 | 0.086975 | 0.2655 | -0.19684 | -0.20599 | -0.14191 | -0.15106 | -0.054932 | -0.11902 | 0.022888 | 0.16022 | -0.12817 | -0.064087 | -0.073242 | -0.009155 | 0.32044 | 121.7011 | 0.21515 | 121.637 | 121.4905 | 121.4951 | 121.4355 | 121.4401 | -121.6141 | -121.6141 | 121.6461 | 121.582 | 61.3953 | 56.0257
959.1875 | 121.8018 | -61.441 | 60.1639 | -0.012131 | 0.00033758 | 0.056418 | 0.056006 | -0.0021919 | -0.0079212 | -0.0019546 | -0.0084228 | 0.0033047 | 0.065493 | 0.060558 | -0.010096 | 0.020974 | -0.0064023 | -0.013733 | 60.1044 | -61.4685 | 60.1959 | -61.2213 | -61.6516 | -61.6608 | -5.5435 | 60.0449 | -61.4914 | 60.1822 | -61.2396 | -61.496 | -61.5189 | -0.027466 | -0.059509 | 0.032044 | 0.21973 | -0.21973 | -0.21057 | -0.19226 | -0.18311 | -0.050354 | -0.11902 | 0.018311 | 0.20142 | -0.07782 | -0.054932 | -0.027466 | -0.004578 | 0.24719 | 121.6644 | 0.25177 | 121.6736 | 121.5729 | 121.5363 | 121.5454 | 121.4859 | -121.6324 | -121.6553 | 121.637 | 121.6232 | 61.4273 | 55.8975
960.8906 | 121.7468 | -61.5051 | 60.1273 | -0.012131 | 0.0050372 | 0.055136 | 0.055792 | 0.0018671 | -0.0042896 | -0.0008866 | -0.0023192 | 0.0048001 | 0.066561 | 0.060344 | -0.0083869 | 0.021828 | -0.0014891 | -0.10529 | 60.0586 | -61.5097 | 60.0815 | -61.3312 | -61.7889 | -61.7798 | -5.7495 | 59.9762 | -61.5463 | 60.0906 | -61.3724 | -61.6196 | -61.6287 | -0.004578 | -0.068664 | -0.045776 | 0.17395 | -0.27466 | -0.28381 | -0.27008 | -0.27923 | -0.041199 | -0.15106 | -0.036621 | 0.13275 | -0.1236 | -0.11444 | -0.082397 | -0.073242 | 0.17853 | 121.5912 | 0.17395 | 121.637 | 121.5683 | 121.5225 | 121.5637 | 121.4813 | -121.637 | -121.6736 | 121.5866 | 121.5958 | 61.3998 | 55.7556
962.6562 | 121.8201 | -61.4456 | 60.1089 | -0.012131 | 0.0024738 | 0.055563 | 0.052801 | -0.0013373 | -0.006853 | -0.002382 | -0.0023192 | 0.00095488 | 0.06592 | 0.055644 | -0.011378 | 0.02311 | 0.00043375 | -0.09613 | 59.9579 | -61.5189 | 60.1639 | -61.1984 | -61.6791 | -61.6699 | -5.6992 | 59.9625 | -61.5005 | 60.1685 | -61.2762 | -61.4914 | -61.5372 | -0.073242 | -0.15106 | 0.054931 | 0.24719 | -0.2243 | -0.23346 | -0.15106 | -0.16022 | -0.054931 | -0.14648 | 0.059509 | 0.16937 | -0.091552 | -0.045776 | -0.036621 | 0.009155 | 0.32043 | 121.6827 | 0.2243 | 121.669 | 121.4767 | 121.463 | 121.4035 | 121.4081 | -121.6278 | -121.6095 | 121.6095 | 121.6141 | 61.3495 | 55.7465
964.3438 | 121.8246 | -61.441 | 60.0861 | -0.012131 | 0.002901 | 0.05834 | 0.052801 | -0.0017645 | -0.0059986 | -0.0028092 | -0.0023192 | -0.00032692 | 0.067415 | 0.060771 | -0.012232 | 0.022255 | -0.0025571 | -0.068665 | 59.9716 | -61.5051 | 60.1868 | -61.2122 | -61.6791 | -61.6699 | -5.8548 | 59.9167 | -61.5372 | 60.1547 | -61.2625 | -61.5005 | -61.5372 | -0.064087 | -0.11444 | 0.10071 | 0.22888 | -0.22888 | -0.23804 | -0.16479 | -0.17395 | -0.09613 | -0.16937 | 0.068664 | 0.17853 | -0.09613 | -0.059509 | 0 | 0.036621 | 0.29297 | 121.6919 | 0.27466 | 121.6919 | 121.4767 | 121.4539 | 121.4127 | 121.3577 | -121.5912 | -121.6232 | 121.6278 | 121.5958 | 61.3724 | 55.5862
966.0938 | 121.8658 | -61.4639 | 60.054 | -0.01976 | 0.0026874 | 0.059409 | 0.054937 | -0.0019781 | -0.0055712 | -0.0028092 | -0.005371 | 0.0013821 | 0.065493 | 0.065257 | -0.0098823 | 0.022255 | -0.0038389 | -0.064087 | 59.9762 | -61.5143 | 60.1822 | -61.203 | -61.6882 | -61.6791 | -5.9372 | 59.903 | -61.5326 | 60.173 | -61.235 | -61.4822 | -61.5326 | -0.050354 | -0.07782 | 0.12817 | 0.26093 | -0.21515 | -0.2243 | -0.16479 | -0.17395 | -0.068665 | -0.15106 | 0.11902 | 0.22888 | -0.068665 | -0.018311 | 0 | 0.050354 | 0.31128 | 121.6965 | 0.29755 | 121.7056 | 121.4905 | 121.4355 | 121.4401 | 121.3669 | -121.5683 | -121.5866 | 121.6461 | 121.637 | 61.3998 | 55.5267
967.8594 | 121.8292 | -61.409 | 60.1364 | -0.0045011 | 0.0014056 | 0.057272 | 0.05152 | -0.00091006 | -0.0094164 | -0.000673 | -0.0023192 | 0.0011685 | 0.066133 | 0.053508 | -0.010737 | 0.021401 | -0.0014891 | 0.027466 | 59.9899 | -61.4777 | 60.2325 | -61.1389 | -61.5967 | -61.6104 | -5.809 | 59.967 | -61.4594 | 60.1776 | -61.1893 | -61.4365 | -61.5051 | -0.068664 | -0.14649 | 0.09613 | 0.27008 | -0.20142 | -0.18768 | -0.13275 | -0.11902 | -0.050354 | -0.16937 | 0.041198 | 0.21973 | -0.09613 | -0.027465 | -0.045776 | 0.022889 | 0.33874 | 121.7102 | 0.27008 | 121.637 | 121.4676 | 121.4264 | 121.3989 | 121.376 | -121.6141 | -121.5958 | 121.6415 | 121.5866 | 61.4365 | 55.6
969.5625 | 121.756 | -61.5051 | 60.1044 | -0.01976 | -8.9824e-05 | 0.054068 | 0.053015 | 0.00079894 | -0.0074938 | -0.0028092 | -0.0084228 | 0.0026639 | 0.067629 | 0.057353 | -0.011164 | 0.021401 | -0.0019163 | -0.027466 | 60.0174 | -61.5417 | 60.0861 | -61.2946 | -61.7432 | -61.7523 | -6.0654 | 59.9991 | -61.5326 | 60.054 | -61.3449 | -61.5784 | -61.6425 | -0.036621 | -0.086975 | -0.01831 | 0.21057 | -0.24719 | -0.23804 | -0.21057 | -0.20142 | -0.027466 | -0.10529 | -0.050354 | 0.16022 | -0.13733 | -0.073242 | -0.10986 | -0.045776 | 0.24719 | 121.6278 | 0.18768 | 121.5866 | 121.5591 | 121.5317 | 121.5225 | 121.5042 | -121.6461 | -121.637 | 121.5912 | 121.5591 | 61.4777 | 55.4398
971.3281 | 121.7468 | -61.528 | 60.0952 | -0.0045011 | -0.00051702 | 0.056418 | 0.055151 | 0.0050713 | -0.0074938 | -0.0008866 | 0.00073235 | 0.0030911 | 0.068056 | 0.055858 | -0.012019 | 0.022042 | -0.0038389 | -0.027466 | 60.0128 | -61.5509 | 60.054 | -61.3403 | -61.7752 | -61.7981 | -6.2439 | 59.967 | -61.5829 | 60.0266 | -61.3632 | -61.6241 | -61.6562 | -0.022888 | -0.082398 | -0.041199 | 0.18768 | -0.27008 | -0.24719 | -0.24719 | -0.22431 | -0.054932 | -0.12817 | -0.068665 | 0.1648 | -0.12817 | -0.096131 | -0.073242 | -0.041199 | 0.21057 | 121.6049 | 0.21973 | 121.6095 | 121.5637 | 121.55 | 121.5408 | 121.4951 | -121.6461 | -121.6782 | 121.582 | 121.5546 | 61.5005 | 55.2841
973.0938 | 121.8979 | -61.528 | 60.0128 | -0.012131 | 0.00012398 | 0.05535 | 0.051092 | -0.0053961 | -0.008562 | -0.001741 | -0.005371 | 0.0011685 | 0.065493 | 0.055431 | -0.010737 | 0.023323 | -0.0021299 | 0 | 59.9075 | -61.5784 | 60.141 | -61.2213 | -61.6837 | -61.6928 | -6.2302 | 59.8663 | -61.5784 | 60.141 | -61.2259 | -61.4822 | -61.5463 | -0.050354 | -0.10528 | 0.12817 | 0.3067 | -0.16479 | -0.15564 | -0.11444 | -0.10529 | -0.050354 | -0.14648 | 0.12817 | 0.30212 | -0.018311 | 0.045776 | 0.032043 | 0.09613 | 0.35706 | 121.7194 | 0.35248 | 121.7194 | 121.4859 | 121.4447 | 121.4355 | 121.3943 | -121.5912 | -121.5912 | 121.669 | 121.669 | 61.528 | 55.2979
974.8594 | 121.8658 | -61.528 | 60.0082 | -0.012131 | -0.0013714 | 0.054709 | 0.052374 | -0.0021919 | -0.0081348 | -0.0043046 | -0.0084228 | 0.0028775 | 0.063784 | 0.060985 | -0.011805 | 0.02311 | 0.00043375 | 0.022888 | 59.8846 | -61.5738 | 60.1593 | -61.2259 | -61.6837 | -61.6882 | -6.4224 | 59.9075 | -61.5829 | 60.1318 | -61.2579 | -61.5234 | -61.5921 | -0.045777 | -0.1236 | 0.15106 | 0.30212 | -0.16022 | -0.15564 | -0.11444 | -0.10986 | -0.054932 | -0.10071 | 0.1236 | 0.27008 | -0.064087 | 0.004578 | -0.009155 | 0.05951 | 0.3479 | 121.7331 | 0.32501 | 121.7148 | 121.4584 | 121.4905 | 121.4127 | 121.4355 | -121.582 | -121.5912 | 121.6873 | 121.6599 | 61.5509 | 55.1056
976.5625 | 121.875 | -61.7294 | 59.8206 | -0.012131 | 0.00012398 | 0.054922 | 0.052374 | -0.0021919 | -0.0077074 | -0.0008866 | -0.005371 | 0.00095488 | 0.066347 | 0.061412 | -0.012873 | 0.021828 | -0.00042085 | -0.086975 | 59.6924 | -61.7935 | 59.903 | -61.4822 | -61.9217 | -61.9171 | -6.6742 | 59.6786 | -61.7889 | 59.8984 | -61.4777 | -61.7111 | -61.7798 | -0.064087 | -0.12817 | 0.082397 | 0.24719 | -0.18768 | -0.19226 | -0.1236 | -0.12817 | -0.059509 | -0.14191 | 0.077819 | 0.25177 | -0.050354 | 0.01831 | 0.009155 | 0.077819 | 0.31128 | 121.6965 | 0.31128 | 121.6873 | 121.4859 | 121.4676 | 121.4218 | 121.4081 | -121.6141 | -121.6095 | 121.6324 | 121.6278 | 61.6425 | 55.0552
978.3125 | 121.7651 | -61.9171 | 59.7107 | -0.012131 | 0.0043964 | 0.054922 | 0.057074 | 0.0012261 | -0.0079212 | -0.0011002 | -0.005371 | 0.0058683 | 0.065706 | 0.056499 | -0.0086005 | 0.019692 | -0.0023435 | -0.11444 | 59.6329 | -61.9308 | 59.6786 | -61.7386 | -62.1872 | -62.178 | -6.8207 | 59.5734 | -61.9308 | 59.697 | -61.7294 | -62.0087 | -62.0132 | -0.013733 | -0.077819 | -0.032043 | 0.17853 | -0.26093 | -0.27008 | -0.24719 | -0.25635 | -0.013733 | -0.13733 | -0.013733 | 0.18768 | -0.096131 | -0.091553 | -0.082398 | -0.07782 | 0.19226 | 121.6095 | 0.20142 | 121.6278 | 121.5637 | 121.5042 | 121.55 | 121.4905 | -121.6415 | -121.6415 | 121.5958 | 121.6141 | 61.8027 | 55.0964
980 | 121.7834 | -61.6974 | 59.8846 | -0.012131 | 0.002901 | 0.056631 | 0.053869 | -0.00091006 | -0.0083484 | -0.001741 | -0.005371 | 0.0035183 | 0.06592 | 0.061199 | -0.0088141 | 0.023323 | -0.0046933 | 0.013733 | 59.8297 | -61.6928 | 59.9533 | -61.4594 | -61.9034 | -61.9308 | -6.7749 | 59.7748 | -61.7157 | 59.9258 | -61.4639 | -61.7477 | -61.7706 | 0.004578 | -0.054932 | 0.068664 | 0.23804 | -0.23346 | -0.20599 | -0.23804 | -0.21057 | -0.01831 | -0.10986 | 0.041198 | 0.23346 | -0.073242 | -0.050354 | -0.054932 | -0.032044 | 0.23346 | 121.6461 | 0.25177 | 121.6415 | 121.5225 | 121.4905 | 121.5271 | 121.4722 | -121.5775 | -121.6003 | 121.6507 | 121.6232 | 61.7111 | 54.9225
981.7656 | 121.875 | -61.7477 | 59.7656 | -0.0045011 | 0.00012398 | 0.052573 | 0.054083 | 0.0059259 | -0.0077074 | -0.0008866 | -0.0084228 | 0.00095488 | 0.06592 | 0.049022 | -0.011805 | 0.021401 | -0.0053343 | -0.045776 | 59.6466 | -61.8164 | 59.8846 | -61.4777 | -61.9308 | -61.9308 | -6.6971 | 59.6237 | -61.821 | 59.8892 | -61.4777 | -61.734 | -61.7981 | -0.068664 | -0.11902 | 0.11902 | 0.27008 | -0.1831 | -0.1831 | -0.11444 | -0.11444 | -0.073242 | -0.14191 | 0.1236 | 0.27008 | -0.050354 | 0.013733 | 0.022888 | 0.086975 | 0.33875 | 121.7011 | 0.34332 | 121.7102 | 121.463 | 121.4447 | 121.3943 | 121.3715 | -121.582 | -121.5866 | 121.6324 | 121.637 | 61.702 | 55.0507
983.4531 | 121.8521 | -61.7569 | 59.7885 | -0.01976 | 0.001192 | 0.05535 | 0.053228 | 0.0018671 | -0.0081348 | -0.0053726 | -0.0023192 | 0.0018095 | 0.067202 | 0.064403 | -0.0094549 | 0.022469 | -0.0042661 | -0.07782 | 59.7061 | -61.7889 | 59.8663 | -61.5143 | -61.9675 | -61.9492 | -6.9122 | 59.642 | -61.8256 | 59.8846 | -61.4777 | -61.734 | -61.8118 | -0.032043 | -0.082397 | 0.07782 | 0.24262 | -0.19226 | -0.21057 | -0.16022 | -0.17853 | -0.068665 | -0.14648 | 0.096131 | 0.27924 | -0.054932 | 0.022888 | 0.013733 | 0.091553 | 0.27466 | 121.6553 | 0.3479 | 121.7102 | 121.4951 | 121.4676 | 121.463 | 121.3989 | -121.5775 | -121.6141 | 121.6232 | 121.6415 | 61.6791 | 54.8447
985.2031 | 121.7422 | -61.8301 | 59.7702 | -0.02739 | 0.0050372 | 0.056631 | 0.057501 | -0.00069646 | -0.005144 | -0.002382 | -0.0023192 | 0.0050137 | 0.066988 | 0.060558 | -0.0083869 | 0.020546 | -0.0021299 | -0.082397 | 59.7061 | -61.8851 | 59.7565 | -61.6745 | -62.1231 | -62.1185 | -7.3517 | 59.6512 | -61.8851 | 59.7382 | -61.6699 | -61.972 | -61.9675 | -0.054932 | -0.064087 | -0.013733 | 0.15564 | -0.28839 | -0.29297 | -0.23346 | -0.23804 | -0.054932 | -0.11902 | -0.032044 | 0.16022 | -0.13733 | -0.14191 | -0.082397 | -0.086975 | 0.21057 | 121.6415 | 0.21515 | 121.6232 | 121.5912 | 121.5363 | 121.5363 | 121.4813 | -121.6553 | -121.6553 | 121.5866 | 121.5683 | 61.7477 | 54.4785
986.9062 | 121.8155 | -61.8851 | 59.6649 | -0.02739 | 0.001192 | 0.055777 | 0.053869 | -0.00091006 | -0.0055712 | -0.0030228 | -0.0084228 | 0.00031408 | 0.066774 | 0.050731 | -0.01095 | 0.022469 | -0.0036253 | -0.091553 | 59.5779 | -61.9217 | 59.7473 | -61.6516 | -62.0956 | -62.0911 | -7.7316 | 59.5367 | -61.9125 | 59.7336 | -61.6287 | -61.8988 | -61.9583 | -0.036621 | -0.086975 | 0.082397 | 0.23346 | -0.20599 | -0.21057 | -0.16937 | -0.17395 | -0.027466 | -0.12817 | 0.068665 | 0.25635 | -0.073242 | -0.013733 | -0.045776 | 0.013733 | 0.27008 | 121.669 | 0.28381 | 121.6461 | 121.4996 | 121.4493 | 121.463 | 121.4218 | -121.5866 | -121.5775 | 121.6324 | 121.6187 | 61.7935 | 54.1534
988.6562 | 121.8201 | -61.9171 | 59.6191 | 0.0031279 | 0.00076478 | 0.058981 | 0.054083 | 0.0010125 | -0.0087756 | -0.0030228 | -0.005371 | 0.0020231 | 0.066347 | 0.056285 | -0.0092413 | 0.023537 | 6.346e-06 | -0.086975 | 59.5184 | -61.9675 | 59.697 | -61.6745 | -62.1323 | -62.1231 | -8.0704 | 59.4955 | -61.9858 | 59.6924 | -61.6699 | -61.9583 | -61.9949 | -0.050354 | -0.10071 | 0.077819 | 0.24261 | -0.20599 | -0.21515 | -0.15564 | -0.1648 | -0.068665 | -0.1236 | 0.073242 | 0.24719 | -0.07782 | -0.041199 | -0.009155 | 0.027466 | 0.29297 | 121.6644 | 0.31586 | 121.6782 | 121.4859 | 121.4813 | 121.4355 | 121.4127 | -121.5866 | -121.6049 | 121.6141 | 121.6095 | 61.8301 | 53.8467
990.3594 | 121.8292 | -61.972 | 59.5642 | -0.02739 | 0.001192 | 0.056631 | 0.054297 | -0.0024055 | -0.0057848 | -0.0036636 | -0.005371 | 0.0020231 | 0.06592 | 0.053722 | -0.0098823 | 0.02076 | -0.0017027 | -0.086975 | 59.4681 | -62.0224 | 59.6558 | -61.7157 | -62.1964 | -62.1735 | -8.1665 | 59.4635 | -62.0132 | 59.6558 | -61.7111 | -61.9858 | -62.0407 | -0.050354 | -0.09613 | 0.091553 | 0.25635 | -0.20142 | -0.2243 | -0.15106 | -0.17395 | -0.041199 | -0.10071 | 0.091553 | 0.26093 | -0.068664 | -0.013733 | -0.027465 | 0.027466 | 0.3067 | 121.6782 | 0.30212 | 121.669 | 121.4905 | 121.4767 | 121.4401 | 121.4355 | -121.5866 | -121.5775 | 121.6278 | 121.6278 | 61.8851 | 53.8055
992.125 | 121.843 | -61.8668 | 59.6924 | -0.012131 | -0.0020124 | 0.055136 | 0.053228 | -0.00091006 | -0.0070666 | -0.0025956 | -0.0084228 | 0.0022367 | 0.065706 | 0.063762 | -0.01031 | 0.022255 | -0.0051205 | -0.086975 | 59.5688 | -61.9263 | 59.7473 | -61.6425 | -62.0865 | -62.0682 | -8.7524 | 59.5413 | -61.9125 | 59.7702 | -61.5692 | -61.8668 | -61.9125 | -0.05951 | -0.1236 | 0.054931 | 0.2243 | -0.20142 | -0.21973 | -0.14191 | -0.16022 | -0.045777 | -0.15106 | 0.07782 | 0.29755 | -0.045777 | 0 | 0 | 0.045777 | 0.28381 | 121.6736 | 0.34332 | 121.6827 | 121.4951 | 121.4539 | 121.4355 | 121.4081 | -121.6187 | -121.6049 | 121.6141 | 121.637 | 61.7798 | 53.1143
993.8906 | 121.788 | -61.9675 | 59.6008 | -0.01976 | 0.0039692 | 0.056204 | 0.057715 | 0.0042169 | -0.0074938 | -0.00345 | -0.011475 | 0.0041593 | 0.067415 | 0.050945 | -0.01031 | 0.022896 | -0.0068295 | -0.10986 | 59.5642 | -62.0041 | 59.6283 | -61.7798 | -62.2421 | -62.233 | -9.1599 | 59.5184 | -62.0132 | 59.6375 | -61.7432 | -62.0361 | -62.0682 | -0.036621 | -0.036621 | 0.027466 | 0.18768 | -0.2655 | -0.27466 | -0.22888 | -0.23804 | -0.045777 | -0.082397 | 0.036621 | 0.2243 | -0.10071 | -0.068665 | -0.054931 | -0.022888 | 0.2243 | 121.6324 | 0.27008 | 121.6507 | 121.5683 | 121.5317 | 121.5317 | 121.4859 | -121.6049 | -121.6141 | 121.5958 | 121.6049 | 61.8576 | 52.8076
995.5781 | 121.7422 | -61.9675 | 59.6603 | -0.01976 | 0.0043964 | 0.059195 | 0.056646 | -0.00026906 | -0.0057848 | -0.0021682 | -0.0023192 | 0.0024503 | 0.064424 | 0.058635 | -0.0096685 | 0.021187 | -0.0046933 | -0.064087 | 59.5734 | -61.9904 | 59.6237 | -61.7935 | -62.2604 | -62.2421 | -9.494 | 59.523 | -62.0132 | 59.5917 | -61.7569 | -62.1048 | -62.0865 | -0.022888 | -0.086975 | -0.036621 | 0.17395 | -0.27466 | -0.29297 | -0.25177 | -0.27008 | -0.045777 | -0.13733 | -0.068664 | 0.21057 | -0.11902 | -0.13733 | -0.073242 | -0.091552 | 0.19684 | 121.6141 | 0.25635 | 121.6049 | 121.5637 | 121.5363 | 121.5408 | 121.4905 | -121.6507 | -121.6736 | 121.5912 | 121.5591 | 61.9034 | 52.4734
997.3281 | 121.756 | -61.9949 | 59.6146 | -0.012131 | 0.0041828 | 0.056845 | 0.057287 | 0.0020807 | -0.0074938 | -3.1996e-05 | -0.005371 | 0.0039457 | 0.067629 | 0.058635 | -0.0062507 | 0.022469 | -0.0010617 | -0.022888 | 59.5276 | -62.0041 | 59.6237 | -61.7661 | -62.2375 | -62.2467 | -10.0662 | 59.4864 | -61.9995 | 59.6008 | -61.7615 | -62.0865 | -62.0956 | -0.009155 | -0.086975 | 0.009155 | 0.22888 | -0.25177 | -0.24262 | -0.24262 | -0.23346 | -0.004578 | -0.12817 | -0.013733 | 0.23346 | -0.10071 | -0.091553 | -0.09613 | -0.086975 | 0.23804 | 121.6278 | 0.23804 | 121.6003 | 121.5317 | 121.4859 | 121.5225 | 121.4813 | -121.6187 | -121.6141 | 121.6187 | 121.5958 | 61.972 | 51.9287
999.0781 | 121.7789 | -61.9812 | 59.61 | -0.0045011 | -0.00073062 | 0.055777 | 0.053656 | 0.00015814 | -0.0062122 | -0.0025956 | -0.0084228 | 0.00074128 | 0.06592 | 0.062908 | -0.0090277 | 0.02076 | -0.0023435 | 0.027466 | 59.491 | -62.0178 | 59.6558 | -61.6928 | -62.1506 | -62.1826 | -10.3592 | 59.4681 | -62.0453 | 59.61 | -61.702 | -62.0041 | -62.0773 | -0.036621 | -0.11902 | 0.045777 | 0.28839 | -0.20142 | -0.16937 | -0.16479 | -0.13275 | -0.064087 | -0.14191 | 0 | 0.27924 | -0.096131 | -0.022888 | -0.032044 | 0.041199 | 0.32501 | 121.6736 | 0.34332 | 121.6553 | 121.5088 | 121.5134 | 121.4722 | 121.4493 | -121.6278 | -121.6553 | 121.637 | 121.5912 | 62.0087 | 51.622
1000.8281 | 121.8842 | -62.1002 | 59.4269 | -0.012131 | 0.0026874 | 0.058127 | 0.054937 | -5.5462e-05 | -0.0057848 | 0.0008224 | -0.005371 | 0.0028775 | 0.06592 | 0.05244 | -0.0088141 | 0.025246 | -0.0012753 | -0.07782 | 59.3582 | -62.1506 | 59.5642 | -61.8393 | -62.3062 | -62.2879 | -10.8536 | 59.2941 | -62.1414 | 59.5505 | -61.7752 | -62.1048 | -62.1185 | -0.050354 | -0.068665 | 0.13733 | 0.26093 | -0.18768 | -0.20599 | -0.13733 | -0.15564 | -0.041198 | -0.13275 | 0.1236 | 0.32501 | -0.01831 | -0.004577 | 0.022888 | 0.036621 | 0.31128 | 121.7148 | 0.36621 | 121.6919 | 121.5088 | 121.4355 | 121.4584 | 121.3943 | -121.5775 | -121.5683 | 121.6644 | 121.6507 | 62.0224 | 51.2466
1002.5312 | 121.8658 | -61.7615 | 59.7519 | 0.010757 | 0.0014056 | 0.055136 | 0.051733 | -0.0056097 | -0.0066394 | -0.0025956 | -0.0023192 | 0.00074128 | 0.064424 | 0.060131 | -0.0096685 | 0.023323 | -0.0025571 | 0.027466 | 59.6558 | -61.8256 | 59.9213 | -61.4502 | -61.9263 | -61.9171 | -11.0641 | 59.6146 | -61.8301 | 59.8801 | -61.3998 | -61.7157 | -61.7935 | -0.064087 | -0.09613 | 0.16937 | 0.31128 | -0.15564 | -0.1648 | -0.091552 | -0.10071 | -0.068664 | -0.13733 | 0.12817 | 0.36163 | -0.032043 | 0.045777 | 0.036621 | 0.11444 | 0.37537 | 121.7468 | 0.4303 | 121.7102 | 121.4813 | 121.4447 | 121.4172 | 121.376 | -121.5775 | -121.582 | 121.6827 | 121.6415 | 61.7889 | 50.6973
1004.2969 | 121.756 | -62.4573 | 59.1476 | -0.0045011 | -0.00073062 | 0.055563 | 0.054297 | -0.00048286 | -0.008562 | -0.0025956 | -0.005371 | 0.0026639 | 0.06592 | 0.056285 | -0.012659 | 0.02311 | -0.0014891 | -0.091553 | 59.0561 | -62.5076 | 59.1431 | -62.2375 | -62.6907 | -62.709 | -11.9888 | 59.0149 | -62.5122 | 59.0973 | -62.1735 | -62.5168 | -62.5809 | -0.050354 | -0.091553 | -0.004578 | 0.21973 | -0.25177 | -0.23346 | -0.20142 | -0.18311 | -0.054932 | -0.13275 | -0.050354 | 0.28381 | -0.1236 | -0.05951 | -0.068665 | -0.004578 | 0.27008 | 121.6507 | 0.33874 | 121.6095 | 121.5637 | 121.5271 | 121.5134 | 121.4722 | -121.6553 | -121.6599 | 121.6003 | 121.5546 | 62.3657 | 50.4684
1006.0625 | 121.8521 | -62.8967 | 58.6349 | -0.012131 | 0.0020466 | 0.056631 | 0.053442 | 0.0035761 | -0.0077074 | -0.0019546 | -0.0084228 | 0.00052768 | 0.069124 | 0.05949 | -0.011378 | 0.023323 | -0.0064023 | -0.068665 | 58.5159 | -62.9654 | 58.7173 | -62.6678 | -63.1119 | -63.1119 | -12.5656 | 58.5205 | -62.9517 | 58.7448 | -62.5168 | -62.8647 | -62.9196 | -0.068664 | -0.11902 | 0.082397 | 0.22888 | -0.21515 | -0.21515 | -0.14648 | -0.14648 | -0.054931 | -0.11444 | 0.10986 | 0.37994 | -0.022888 | 0.032044 | 0.032043 | 0.086975 | 0.29755 | 121.6827 | 0.43487 | 121.6965 | 121.4813 | 121.4722 | 121.4127 | 121.4172 | -121.6003 | -121.5866 | 121.6141 | 121.6415 | 62.8281 | 50.3311
1007.8281 | 121.8567 | -63.2538 | 58.255 | -0.0045011 | 0.00012398 | 0.055136 | 0.053228 | 0.00037174 | -0.0098438 | -0.0011002 | -0.0084228 | 0.0035183 | 0.06592 | 0.062267 | -0.01031 | 0.019905 | -0.0014891 | -0.086975 | 58.1589 | -63.327 | 58.3237 | -63.0295 | -63.4964 | -63.4735 | -13.2202 | 58.1314 | -63.3453 | 58.3466 | -62.8967 | -63.2538 | -63.3133 | -0.073242 | -0.09613 | 0.068664 | 0.2243 | -0.21973 | -0.24261 | -0.14649 | -0.16937 | -0.091553 | -0.1236 | 0.091553 | 0.35706 | -0.059509 | 0 | 0.032044 | 0.091553 | 0.29755 | 121.6507 | 0.44861 | 121.6919 | 121.4859 | 121.4767 | 121.4127 | 121.3852 | -121.582 | -121.6003 | 121.5775 | 121.6003 | 63.1668 | 50.0336
1009.5156 | 121.8338 | -64.0411 | 57.5134 | 0.0031279 | 0.00097838 | 0.056845 | 0.055151 | 0.0018671 | -0.0087756 | -0.001741 | -0.0084228 | 0.0015957 | 0.066347 | 0.053508 | -0.01031 | 0.020546 | -0.0027707 | -0.091553 | 57.4127 | -64.0686 | 57.5592 | -63.8077 | -64.27 | -64.2517 | -14.0488 | 57.3532 | -64.1144 | 57.5409 | -63.6841 | -64.0549 | -64.0869 | -0.027466 | -0.10071 | 0.045776 | 0.23346 | -0.21057 | -0.22888 | -0.18311 | -0.20142 | -0.073242 | -0.16022 | 0.027466 | 0.35706 | -0.045776 | -0.013733 | 0.027466 | 0.059509 | 0.26093 | 121.6278 | 0.4303 | 121.6553 | 121.4813 | 121.4676 | 121.4539 | 121.3943 | -121.582 | -121.6278 | 121.6003 | 121.582 | 63.9496 | 49.9924
1011.2656 | 121.8063 | -64.4623 | 57.0923 | -0.02739 | 0.001192 | 0.054709 | 0.054083 | -0.00069646 | -0.006853 | 0.0021042 | -0.005371 | 0.0026639 | 0.06592 | 0.058422 | -0.013087 | 0.022683 | -0.0072569 | -0.09613 | 56.9962 | -64.5309 | 57.1518 | -64.2151 | -64.6683 | -64.6591 | -14.6393 | 56.9778 | -64.5035 | 57.1518 | -64.0869 | -64.4531 | -64.5126 | -0.068665 | -0.09613 | 0.059509 | 0.24719 | -0.19684 | -0.20599 | -0.12817 | -0.13733 | -0.041199 | -0.11444 | 0.059509 | 0.37537 | -0.050354 | 0.009155 | -0.009155 | 0.050354 | 0.31586 | 121.6827 | 0.41657 | 121.6553 | 121.5271 | 121.4813 | 121.4584 | 121.4401 | -121.6232 | -121.5958 | 121.6141 | 121.6141 | 64.3662 | 49.823
1013.0156 | 121.7926 | -65.1169 | 56.4972 | -0.0045011 | 0.0022602 | 0.055991 | 0.057074 | -0.00026906 | -0.0079212 | -0.001741 | -0.0023192 | 0.0022367 | 0.067202 | 0.065898 | -0.0088141 | 0.020546 | -0.0019163 | -0.027466 | 56.4011 | -65.1764 | 56.4972 | -64.8972 | -65.3366 | -65.3412 | -15.4495 | 56.3599 | -65.1672 | 56.5063 | -64.6957 | -65.1398 | -65.1627 | -0.05951 | -0.09613 | 0 | 0.21973 | -0.22431 | -0.21973 | -0.16479 | -0.16022 | -0.050354 | -0.13733 | 0.009156 | 0.42114 | -0.045777 | -0.022889 | 0.004577 | 0.027465 | 0.27924 | 121.6736 | 0.4715 | 121.6736 | 121.5775 | 121.5271 | 121.5179 | 121.4767 | -121.6736 | -121.6644 | 121.6141 | 121.6232 | 65.0894 | 49.6674
1014.7344 | 121.8979 | -71.0449 | 50.4639 | -0.0045011 | -0.00051702 | 0.055563 | 0.054297 | -5.5462e-05 | -0.0079212 | 0.0001816 | -0.005371 | 0.0013821 | 0.064638 | 0.059703 | -0.010096 | 0.023751 | -0.0017027 | -0.16022 | 50.2945 | -71.1731 | 50.6378 | -70.6833 | -71.1777 | -71.1914 | -18.306 | 50.3632 | -71.109 | 50.5646 | -70.5734 | -70.9946 | -71.0678 | -0.12817 | -0.16937 | 0.17395 | 0.36163 | -0.14648 | -0.13275 | -0.01831 | -0.004577 | -0.064087 | -0.10071 | 0.10071 | 0.4715 | -0.022888 | 0.050354 | 0.041199 | 0.11444 | 0.48981 | 121.8109 | 0.53558 | 121.6736 | 121.4676 | 121.4722 | 121.3394 | 121.4081 | -121.637 | -121.5729 | 121.6827 | 121.6095 | 70.8847 | 52.739
1016.5156 | 121.8979 | -73.2559 | 48.2346 | -0.012131 | -0.00073062 | 0.056845 | 0.053015 | -0.0039007 | -0.0077074 | -0.0030228 | -0.0023192 | -0.00054052 | 0.065706 | 0.053295 | -0.011378 | 0.021401 | -0.0053343 | -0.07782 | 48.1018 | -73.3749 | 48.4039 | -72.8714 | -73.3887 | -73.407 | -20.1233 | 48.1064 | -73.3566 | 48.3765 | -72.7066 | -73.1873 | -73.2605 | -0.11902 | -0.13275 | 0.16937 | 0.38452 | -0.15106 | -0.13275 | -0.032043 | -0.013733 | -0.10071 | -0.12817 | 0.14191 | 0.54932 | -0.004578 | 0.068664 | 0.09613 | 0.16937 | 0.50354 | 121.7789 | 0.65002 | 121.7331 | 121.4767 | 121.463 | 121.3577 | 121.3623 | -121.6095 | -121.5912 | 121.6599 | 121.6324 | 73.1781 | 53.1326
1018.2031 | 121.907 | -74.1486 | 47.3694 | -0.012131 | -0.00030342 | 0.057913 | 0.052801 | -0.0017645 | -0.006853 | -0.0015274 | -0.005371 | 0.00052768 | 0.069124 | 0.063549 | -0.0092413 | 0.021401 | -0.0036253 | -0.041199 | 47.2687 | -74.2035 | 47.5067 | -73.7778 | -74.2722 | -74.2767 | -21.1578 | 47.2504 | -74.2264 | 47.5479 | -73.526 | -74.0158 | -74.1119 | -0.054931 | -0.10071 | 0.13733 | 0.37079 | -0.12817 | -0.1236 | -0.073242 | -0.068665 | -0.077819 | -0.11902 | 0.17853 | 0.62256 | 0.036622 | 0.13275 | 0.11444 | 0.21057 | 0.42572 | 121.7102 | 0.70038 | 121.7743 | 121.4722 | 121.4767 | 121.4172 | 121.3989 | -121.5729 | -121.5958 | 121.6553 | 121.6965 | 74.1074 | 52.9907
1019.9531 | 121.7697 | -76.3733 | 45.2087 | -0.012131 | 0.0052508 | 0.057913 | 0.058142 | -0.0017645 | -0.0057848 | -0.0013138 | -0.005371 | 0.0058683 | 0.065706 | 0.065685 | -0.0062507 | 0.02311 | -0.0017027 | -0.059509 | 45.1401 | -76.4145 | 45.2499 | -76.0574 | -76.6068 | -76.593 | -22.9614 | 45.1218 | -76.4328 | 45.2408 | -75.8423 | -76.4053 | -76.4236 | -0.041199 | -0.068664 | 0.041199 | 0.31586 | -0.21973 | -0.23346 | -0.17853 | -0.19226 | -0.059509 | -0.086975 | 0.032044 | 0.53101 | -0.050354 | -0.032043 | 0.009155 | 0.027466 | 0.35706 | 121.6644 | 0.59051 | 121.6736 | 121.5546 | 121.5546 | 121.5134 | 121.4951 | -121.6232 | -121.6415 | 121.6232 | 121.6141 | 76.3138 | 53.4119
1021.7344 | 121.8155 | -76.3733 | 45.1996 | -0.01976 | 0.0022602 | 0.059195 | 0.055792 | 0.0031487 | -0.006853 | -0.0002456 | -0.005371 | 0.0033047 | 0.065706 | 0.063976 | -0.0081733 | 0.023323 | -0.0051205 | 0.073242 | 45.1447 | -76.4008 | 45.2728 | -76.0162 | -76.5472 | -76.561 | -23.822 | 45.0897 | -76.4374 | 45.2637 | -75.7645 | -76.3412 | -76.387 | -0.027466 | -0.054932 | 0.073242 | 0.35706 | -0.18768 | -0.17395 | -0.16022 | -0.14648 | -0.064087 | -0.10986 | 0.064087 | 0.60883 | -0.013733 | 0.032043 | 0.050354 | 0.09613 | 0.38452 | 121.6736 | 0.67291 | 121.701 | 121.5454 | 121.5271 | 121.5179 | 121.463 | -121.6003 | -121.637 | 121.6461 | 121.637 | 76.4465 | 52.5513
1023.4844 | 121.9208 | -78.2684 | 43.222 | -0.0045011 | -0.0028668 | 0.053641 | 0.052588 | -0.0043281 | -0.0074938 | -0.0021682 | -0.005371 | -0.00011332 | 0.067629 | 0.060985 | -0.011378 | 0.021614 | -0.0061887 | -0.045776 | 43.0801 | -78.3829 | 43.3365 | -77.8793 | -78.4149 | -78.4241 | -25.5066 | 43.103 | -78.392 | 43.3914 | -77.5818 | -78.1403 | -78.2272 | -0.11444 | -0.14191 | 0.11444 | 0.3891 | -0.15564 | -0.14648 | -0.041198 | -0.032043 | -0.1236 | -0.11902 | 0.16937 | 0.68665 | 0.041199 | 0.12817 | 0.16479 | 0.25177 | 0.50354 | 121.7194 | 0.81024 | 121.7834 | 121.463 | 121.4951 | 121.3486 | 121.3715 | -121.6049 | -121.6141 | 121.6049 | 121.6599 | 78.2227 | 52.7618
1025.2344 | 121.8933 | -79.747 | 41.7618 | -0.0045011 | -0.002226 | 0.055777 | 0.052588 | -0.0019781 | -0.0049304 | -0.0013138 | -0.005371 | 0.00074128 | 0.063997 | 0.054576 | -0.0094549 | 0.02311 | -0.0021299 | -0.073242 | 41.6565 | -79.7928 | 41.9266 | -79.3213 | -79.8386 | -79.8431 | -26.8707 | 41.6794 | -79.8065 | 41.9678 | -78.9963 | -79.6234 | -79.7058 | -0.045777 | -0.10529 | 0.16479 | 0.42572 | -0.096131 | -0.091553 | -0.050354 | -0.045776 | -0.05951 | -0.082398 | 0.20599 | 0.75073 | 0.041198 | 0.1236 | 0.10071 | 0.18311 | 0.4715 | 121.7194 | 0.81024 | 121.7743 | 121.4493 | 121.4859 | 121.4035 | 121.4264 | -121.5546 | -121.5683 | 121.6736 | 121.7148 | 79.6738 | 52.8763
1026.9375 | 121.8155 | -83.6609 | 37.8891 | -0.0045011 | 0.001192 | 0.058768 | 0.058142 | 0.00015814 | -0.0083484 | 0.0001816 | -0.0023192 | 0.0037321 | 0.067629 | 0.060558 | -0.0098823 | 0.021614 | 0.00086095 | -0.09613 | 37.7151 | -83.8303 | 37.706 | -83.5236 | -84.0729 | -84.0958 | -29.6173 | 37.6694 | -83.8348 | 37.9349 | -82.9422 | -83.5968 | -83.6426 | -0.16937 | -0.17395 | -0.18311 | 0.13733 | -0.43488 | -0.41199 | -0.2655 | -0.24262 | -0.17395 | -0.21973 | 0.045776 | 0.71869 | 0.018311 | 0.064087 | 0.19226 | 0.23804 | 0.3067 | 121.5363 | 0.89264 | 121.7697 | 121.5454 | 121.5042 | 121.376 | 121.3303 | -121.7194 | -121.7239 | 121.3669 | 121.5958 | 83.5648 | 54.0436
1028.6875 | 121.8933 | -72.2992 | 49.2599 | -0.012131 | -0.001585 | 0.055777 | 0.053228 | 0.00037174 | -0.006853 | -0.0043046 | -0.0084228 | 0.00095488 | 0.065065 | 0.057353 | -0.011591 | 0.022896 | -0.0029843 | -0.032043 | 49.1547 | -72.3084 | 49.3973 | -71.8872 | -72.3999 | -72.4045 | -24.5132 | 49.118 | -72.3404 | 49.4156 | -71.5576 | -72.1252 | -72.1985 | -0.009156 | -0.10529 | 0.13733 | 0.41199 | -0.10529 | -0.10071 | -0.09613 | -0.091552 | -0.041199 | -0.14191 | 0.15564 | 0.74158 | 0.10071 | 0.17395 | 0.14191 | 0.21515 | 0.42114 | 121.7056 | 0.78278 | 121.756 | 121.463 | 121.4584 | 121.4539 | 121.4172 | -121.5683 | -121.6003 | 121.6965 | 121.7148 | 72.2672 | 47.7859
1030.4375 | 121.8475 | -97.5037 | 23.9868 | -0.012131 | 0.0026874 | 0.054922 | 0.055792 | -0.00048286 | -0.0064258 | -0.0055862 | 0.00073235 | 0.0028775 | 0.069338 | 0.053508 | -0.0064643 | 0.022255 | -0.00084805 | -0.10986 | 23.9502 | -97.5861 | 24.0875 | -97.0505 | -97.6593 | -97.6959 | -37.4908 | 23.9502 | -97.6456 | 24.0967 | -96.6385 | -97.435 | -97.4808 | -0.082398 | -0.036621 | 0.10071 | 0.45319 | -0.19226 | -0.15564 | -0.10986 | -0.073242 | -0.14191 | -0.036621 | 0.10986 | 0.86517 | 0.022888 | 0.068664 | 0.16479 | 0.21057 | 0.53558 | 121.6736 | 1.0071 | 121.7422 | 121.5363 | 121.5958 | 121.4539 | 121.4539 | -121.5729 | -121.6324 | 121.5912 | 121.6003 | 97.3938 | 60.0128
1032.2188 | 119.7647 | -108.1421 | 13.3347 | -0.012131 | 0.0016192 | 0.057913 | 0.055151 | 0.0018671 | -0.0089892 | -0.002382 | -0.0084228 | 0.0013821 | 0.067629 | 0.055858 | -0.011378 | 0.025673 | -0.0089659 | -0.19226 | 13.2568 | -108.2474 | 13.4079 | -107.5974 | -108.2474 | -108.2794 | -43.6798 | 13.2797 | -108.3298 | 13.4583 | -107.1121 | -107.9636 | -108.0276 | -0.10529 | -0.07782 | 0.073242 | 0.54474 | -0.13733 | -0.10529 | -0.032044 | 0 | -0.18768 | -0.054932 | 0.1236 | 1.03 | 0.11444 | 0.17853 | 0.30212 | 0.36621 | 0.65002 | 121.6553 | 1.2177 | 121.788 | 121.5042 | 121.6095 | 121.3989 | 121.4218 | -121.582 | -121.6644 | 121.55 | 121.6003 | 107.9498 | 64.4623
1033.9844 | 121.9208 | -110.6461 | 10.8307 | -0.0045011 | 0.0022602 | 0.057272 | 0.054937 | -0.00069646 | -0.006853 | 0.0003952 | -0.0084228 | 0.0033047 | 0.067415 | 0.054149 | -0.0081733 | 0.024178 | -0.00020725 | -0.13275 | 10.7803 | -110.7056 | 10.9268 | -110.051 | -110.733 | -110.7651 | -45.7626 | 10.762 | -110.82 | 10.9863 | -109.552 | -110.4858 | -110.495 | -0.059509 | -0.050354 | 0.096131 | 0.59509 | -0.11902 | -0.086975 | -0.05951 | -0.027466 | -0.17395 | -0.068664 | 0.15564 | 1.0941 | 0.15106 | 0.16022 | 0.32501 | 0.33417 | 0.6546 | 121.6324 | 1.268 | 121.8063 | 121.4859 | 121.582 | 121.4264 | 121.4081 | -121.5363 | -121.6507 | 121.5729 | 121.6324 | 110.5133 | 64.8834
1035.6875 | 121.8338 | -111.7676 | 9.7961 | -0.012131 | 0.0016192 | 0.055563 | 0.057715 | -0.00026906 | -0.0089892 | -0.0021682 | -0.0084228 | 0.0052273 | 0.069124 | 0.055217 | -0.010523 | 0.023537 | -0.0010617 | -0.059509 | 9.7366 | -111.8134 | 9.8053 | -111.1725 | -111.85 | -111.9095 | -47.0032 | 9.7366 | -111.8866 | 9.8282 | -110.6323 | -111.6074 | -111.644 | -0.045776 | -0.05951 | 0.009155 | 0.59509 | -0.14191 | -0.082398 | -0.096131 | -0.036622 | -0.11902 | -0.05951 | 0.032043 | 1.1353 | 0.1236 | 0.16022 | 0.24262 | 0.27924 | 0.64087 | 121.6187 | 1.2543 | 121.7148 | 121.55 | 121.6232 | 121.5042 | 121.5042 | -121.6095 | -121.6827 | 121.5729 | 121.5958 | 111.7081 | 64.7644
1037.4375 | 121.8338 | -111.731 | 9.8053 | -0.0045011 | 0.001833 | 0.057272 | 0.053442 | -5.5462e-05 | -0.0062122 | -0.0002456 | -0.005371 | -0.00032692 | 0.065065 | 0.045391 | -0.010523 | 0.023323 | 0.00043375 | -0.17395 | 9.7183 | -111.7676 | 9.8236 | -111.1176 | -111.8088 | -111.8454 | -47.7219 | 9.7321 | -111.8637 | 9.8648 | -110.5774 | -111.5341 | -111.5936 | -0.036621 | -0.086975 | 0.01831 | 0.6134 | -0.11444 | -0.07782 | -0.07782 | -0.041199 | -0.13275 | -0.073242 | 0.059509 | 1.1536 | 0.13733 | 0.19684 | 0.27008 | 0.32959 | 0.65002 | 121.5912 | 1.2863 | 121.7285 | 121.4859 | 121.5958 | 121.4493 | 121.463 | -121.5729 | -121.669 | 121.5546 | 121.5958 | 111.557 | 64.0091
1039.125 | 121.843 | -111.3922 | 10.1852 | -0.012131 | 0.00033758 | 0.056631 | 0.053228 | -0.0028327 | -0.006853 | 0.0001816 | -0.0084228 | 0.00095488 | 0.066774 | 0.051799 | -0.011378 | 0.023537 | -0.0031979 | -0.16022 | 10.0937 | -111.3831 | 10.1898 | -110.7697 | -111.4288 | -111.4655 | -48.1293 | 10.1257 | -111.4517 | 10.231 | -110.1791 | -111.1542 | -111.1816 | 0.009155 | -0.091553 | 0.004577 | 0.62256 | -0.073242 | -0.036621 | -0.082397 | -0.045776 | -0.059509 | -0.05951 | 0.045776 | 1.2131 | 0.21057 | 0.23804 | 0.27008 | 0.29755 | 0.6134 | 121.5729 | 1.2726 | 121.6827 | 121.4767 | 121.5775 | 121.4859 | 121.5179 | -121.5683 | -121.637 | 121.582 | 121.6232 | 111.232 | 63.2629
1040.875 | 121.7743 | -112.1475 | 9.4482 | -0.0045011 | 0.00033758 | 0.057272 | 0.057074 | -0.00048286 | -0.008562 | -0.0002456 | -0.0084228 | 0.0028775 | 0.066561 | 0.060558 | -0.0098823 | 0.020974 | -0.0021299 | -0.10071 | 9.3613 | -112.207 | 9.3567 | -111.6074 | -112.2528 | -112.3077 | -49.1089 | 9.3933 | -112.2391 | 9.407 | -110.9528 | -111.9965 | -111.9919 | -0.059509 | -0.086975 | -0.091553 | 0.54016 | -0.16022 | -0.10529 | -0.10071 | -0.045777 | -0.091553 | -0.054931 | -0.041199 | 1.1948 | 0.15564 | 0.15106 | 0.24719 | 0.24262 | 0.59967 | 121.5637 | 1.2863 | 121.6461 | 121.5683 | 121.6324 | 121.5088 | 121.5408 | -121.6553 | -121.6873 | 121.5042 | 121.5546 | 112.0468 | 63.0386
1042.6406 | 121.7651 | -112.6053 | 8.9722 | -0.012131 | 0.001833 | 0.056204 | 0.051733 | 0.00037174 | -0.0077074 | -0.0013138 | -0.0084228 | 0.0020231 | 0.065706 | 0.053295 | -0.01031 | 0.020974 | -0.0029843 | -0.064087 | 8.8623 | -112.6007 | 9.0042 | -111.9232 | -112.587 | -112.6465 | -49.8734 | 8.9447 | -112.6923 | 8.9951 | -111.3144 | -112.3535 | -112.3901 | 0.004578 | -0.10986 | 0.032043 | 0.68207 | -0.041198 | 0.018311 | -0.045776 | 0.013733 | -0.086975 | -0.027466 | 0.022888 | 1.2909 | 0.21515 | 0.25177 | 0.30212 | 0.33875 | 0.67749 | 121.6049 | 1.3779 | 121.6873 | 121.463 | 121.637 | 121.4676 | 121.55 | -121.5729 | -121.6644 | 121.6095 | 121.6003 | 112.5412 | 62.7319
1044.3906 | 121.843 | -112.8754 | 8.6609 | -0.02739 | 0.0035418 | 0.057059 | 0.055792 | -0.00048286 | -0.006853 | -0.000673 | -0.005371 | -0.00011332 | 0.067415 | 0.056072 | -0.0083869 | 0.024178 | -0.0023435 | -0.13275 | 8.5831 | -112.8891 | 8.6838 | -112.2482 | -112.944 | -112.9715 | -50.6332 | 8.5922 | -112.9623 | 8.7479 | -111.5479 | -112.619 | -112.6144 | -0.013733 | -0.07782 | 0.022888 | 0.62714 | -0.096131 | -0.068665 | -0.082398 | -0.054932 | -0.086975 | -0.068665 | 0.086975 | 1.3275 | 0.26093 | 0.25635 | 0.3479 | 0.34332 | 0.64087 | 121.5729 | 1.4145 | 121.7102 | 121.4722 | 121.5546 | 121.4584 | 121.4676 | -121.55 | -121.6232 | 121.5591 | 121.6232 | 112.7426 | 62.2421
1046.1406 | 121.7285 | -113.1683 | 8.4412 | -0.01976 | 0.0026874 | 0.055563 | 0.057287 | -0.0026191 | -0.0077074 | -0.0060134 | -0.0023192 | 0.0050137 | 0.067415 | 0.050945 | -0.0090277 | 0.023964 | -0.0029843 | -0.13275 | 8.3405 | -113.1912 | 8.3176 | -112.6236 | -113.3011 | -113.324 | -51.4618 | 8.3862 | -113.2553 | 8.3862 | -111.8912 | -112.9944 | -112.9669 | -0.022888 | -0.10071 | -0.1236 | 0.54474 | -0.15564 | -0.13275 | -0.13275 | -0.10986 | -0.086975 | -0.054932 | -0.054932 | 1.2772 | 0.20142 | 0.17395 | 0.28839 | 0.26093 | 0.56763 | 121.5088 | 1.3641 | 121.6415 | 121.5317 | 121.6415 | 121.5088 | 121.5546 | -121.6324 | -121.6965 | 121.4859 | 121.5546 | 113.0356 | 61.7065
1047.8906 | 121.7468 | -113.3743 | 8.2306 | -0.012131 | 0.002901 | 0.054068 | 0.055792 | 0.00058534 | -0.0081348 | -0.0011002 | -0.0023192 | 0.0030911 | 0.067202 | 0.051799 | -0.0081733 | 0.022255 | -0.0019163 | -0.091553 | 8.1345 | -113.4064 | 8.139 | -112.793 | -113.4567 | -113.4979 | -52.0386 | 8.1573 | -113.4659 | 8.1573 | -111.9965 | -113.1317 | -113.1409 | -0.032043 | -0.096131 | -0.091553 | 0.58136 | -0.1236 | -0.082397 | -0.091553 | -0.050354 | -0.091552 | -0.073242 | -0.073242 | 1.3779 | 0.23346 | 0.24262 | 0.32501 | 0.33417 | 0.6134 | 121.5454 | 1.4694 | 121.6232 | 121.5408 | 121.6232 | 121.5088 | 121.5317 | -121.637 | -121.6965 | 121.5134 | 121.5317 | 113.2828 | 61.3358
1049.6406 | 121.8292 | -113.4476 | 8.0429 | -0.012131 | 0.00076478 | 0.056631 | 0.053869 | -0.0021919 | -0.0074938 | -0.0013138 | -0.0084228 | 0.0013821 | 0.063143 | 0.062694 | -0.010096 | 0.026314 | -0.00020725 | -0.09613 | 7.9376 | -113.5162 | 8.075 | -112.825 | -113.5391 | -113.5529 | -52.4277 | 7.9697 | -113.5986 | 8.1345 | -112.001 | -113.1866 | -113.1729 | -0.068664 | -0.10529 | 0.032043 | 0.62256 | -0.10529 | -0.091553 | -0.036621 | -0.022889 | -0.15106 | -0.073242 | 0.091552 | 1.4465 | 0.27466 | 0.26093 | 0.42572 | 0.41199 | 0.69122 | 121.5912 | 1.5976 | 121.7331 | 121.4539 | 121.5683 | 121.3852 | 121.4172 | -121.5591 | -121.6415 | 121.5225 | 121.582 | 113.3514 | 61.0199
1051.3281 | 121.8201 | -113.6078 | 7.9239 | -0.01976 | 0.0033282 | 0.056845 | 0.054724 | -0.0015509 | -0.0059986 | -0.0019546 | -0.0023192 | 0.00052768 | 0.067202 | 0.062267 | -0.0075323 | 0.024391 | -0.0014891 | -0.1236 | 7.7911 | -113.6307 | 7.9559 | -112.9395 | -113.6444 | -113.6719 | -52.7573 | 7.8415 | -113.7131 | 7.9788 | -112.1155 | -113.3102 | -113.3011 | -0.022888 | -0.13275 | 0.032044 | 0.66833 | -0.064087 | -0.036621 | -0.041199 | -0.013733 | -0.10529 | -0.082397 | 0.054932 | 1.4923 | 0.3067 | 0.29755 | 0.41199 | 0.40283 | 0.69122 | 121.5866 | 1.5976 | 121.6919 | 121.4218 | 121.5546 | 121.3989 | 121.4493 | -121.5546 | -121.637 | 121.5637 | 121.5866 | 113.4842 | 60.8505
1053.0781 | 121.788 | -113.6948 | 7.8827 | -0.01976 | 0.002901 | 0.056204 | 0.05216 | 0.00058534 | -0.0083484 | -0.0025956 | -0.0084228 | -0.00075412 | 0.067415 | 0.055217 | -0.0094549 | 0.02546 | 0.0015017 | -0.15564 | 7.7408 | -113.6993 | 7.8506 | -113.0219 | -113.736 | -113.7588 | -53.0869 | 7.782 | -113.7588 | 7.8598 | -112.175 | -113.3835 | -113.3743 | -0.004578 | -0.14191 | -0.032043 | 0.67291 | -0.064087 | -0.041199 | -0.059509 | -0.036621 | -0.064087 | -0.10071 | -0.022888 | 1.5198 | 0.32043 | 0.31128 | 0.38452 | 0.37537 | 0.67749 | 121.55 | 1.5839 | 121.6187 | 121.4401 | 121.5408 | 121.4355 | 121.4767 | -121.582 | -121.6415 | 121.5454 | 121.5546 | 113.5391 | 60.6079
1054.7656 | 121.7743 | -113.7543 | 7.8049 | -0.0045011 | 0.00097838 | 0.057486 | 0.053656 | -0.0011237 | -0.0077074 | -0.002382 | -0.005371 | 0.0020231 | 0.067202 | 0.06184 | -0.011164 | 0.024819 | -0.00063445 | -0.15564 | 7.695 | -113.7955 | 7.7454 | -113.1226 | -113.8092 | -113.855 | -53.4714 | 7.7133 | -113.855 | 7.7728 | -112.207 | -113.4567 | -113.4659 | -0.041199 | -0.10986 | -0.05951 | 0.63171 | -0.10071 | -0.054932 | -0.059509 | -0.013733 | -0.10071 | -0.091553 | -0.032044 | 1.5472 | 0.28839 | 0.29755 | 0.3891 | 0.39825 | 0.67291 | 121.5408 | 1.6479 | 121.6278 | 121.4905 | 121.5683 | 121.4493 | 121.4676 | -121.6003 | -121.6599 | 121.4996 | 121.5271 | 113.5986 | 60.2829
1056.5156 | 121.6965 | -113.9786 | 7.5897 | -0.01976 | 0.0031146 | 0.059409 | 0.055151 | 0.0018671 | -0.0077074 | -0.001741 | -0.0084228 | 0.0037321 | 0.065493 | 0.062694 | -0.0088141 | 0.022469 | 0.00086095 | -0.14191 | 7.5348 | -114.0106 | 7.4661 | -113.4384 | -114.1296 | -114.1663 | -54.071 | 7.5348 | -114.0747 | 7.5165 | -112.4451 | -113.7543 | -113.7085 | -0.032043 | -0.054932 | -0.1236 | 0.54016 | -0.18768 | -0.15106 | -0.15564 | -0.11902 | -0.09613 | -0.054932 | -0.073243 | 1.5335 | 0.27008 | 0.22431 | 0.36621 | 0.32044 | 0.5722 | 121.4767 | 1.6296 | 121.5912 | 121.5454 | 121.6095 | 121.5134 | 121.5134 | -121.6003 | -121.6644 | 121.4447 | 121.4951 | 113.8367 | 59.9075
1058.2812 | 121.7377 | -113.942 | 7.6035 | -0.012131 | 0.0035418 | 0.056631 | 0.054937 | 0.0016535 | -0.005144 | -0.0025956 | -0.011475 | 0.0052273 | 0.06827 | 0.059276 | -0.0096685 | 0.02311 | -0.0025571 | -0.15106 | 7.5302 | -113.9832 | 7.5027 | -113.3789 | -114.0839 | -114.1068 | -54.4052 | 7.5302 | -114.0381 | 7.576 | -112.3077 | -113.6993 | -113.6215 | -0.041198 | -0.073243 | -0.10071 | 0.56305 | -0.16479 | -0.14191 | -0.1236 | -0.10071 | -0.09613 | -0.073243 | -0.027466 | 1.6342 | 0.32044 | 0.24262 | 0.41657 | 0.33875 | 0.60425 | 121.4859 | 1.7303 | 121.6141 | 121.5134 | 121.5683 | 121.4722 | 121.4722 | -121.5866 | -121.6415 | 121.4447 | 121.5179 | 113.7909 | 59.5367
1060.0469 | 121.7194 | -114.0793 | 7.5073 | -0.012131 | 0.00055118 | 0.056418 | 0.055578 | 0.00015814 | -0.0089892 | -0.0030228 | -0.005371 | 0.0052273 | 0.067415 | 0.062908 | -0.0077459 | 0.02311 | 0.00021995 | -0.07782 | 7.4112 | -114.1708 | 7.37 | -113.5254 | -114.1983 | -114.2395 | -55.2109 | 7.3975 | -114.2029 | 7.3929 | -112.3581 | -113.7817 | -113.736 | -0.091552 | -0.09613 | -0.13733 | 0.55389 | -0.16022 | -0.11902 | -0.068665 | -0.027466 | -0.1236 | -0.10986 | -0.11444 | 1.7212 | 0.34332 | 0.29755 | 0.46692 | 0.42114 | 0.64545 | 121.5408 | 1.8448 | 121.5958 | 121.582 | 121.6003 | 121.4905 | 121.4767 | -121.6782 | -121.7102 | 121.4493 | 121.4722 | 114.0015 | 58.8684
1061.7344 | 121.7148 | -114.1983 | 7.3608 | -0.012131 | 0.00055118 | 0.056204 | 0.056006 | -0.0028327 | -0.010485 | -0.002382 | -0.011475 | 0.0030911 | 0.067842 | 0.058635 | -0.010523 | 0.023537 | -0.0017027 | -0.086975 | 7.2693 | -114.267 | 7.251 | -113.6398 | -114.299 | -114.3494 | -55.9158 | 7.3013 | -114.3265 | 7.2693 | -112.4222 | -113.8916 | -113.8504 | -0.068665 | -0.091553 | -0.10986 | 0.55847 | -0.15106 | -0.10071 | -0.082397 | -0.032043 | -0.12817 | -0.059509 | -0.091553 | 1.7761 | 0.3479 | 0.3067 | 0.47607 | 0.43487 | 0.62714 | 121.5179 | 1.9043 | 121.5958 | 121.5363 | 121.6278 | 121.4676 | 121.4996 | -121.6278 | -121.6873 | 121.4493 | 121.4676 | 114.1113 | 58.2825
1063.4844 | 121.7377 | -114.3585 | 7.1548 | -0.012131 | 0.0024738 | 0.057059 | 0.055365 | -0.00048286 | -0.0062122 | -0.001741 | -0.011475 | 0.0033047 | 0.071474 | 0.060131 | -0.0086005 | 0.024605 | -0.0014891 | -0.10071 | 7.0724 | -114.4135 | 7.132 | -113.7543 | -114.4547 | -114.5004 | -56.3965 | 7.0999 | -114.4775 | 7.1503 | -112.4908 | -114.0381 | -113.9969 | -0.054931 | -0.082397 | -0.022888 | 0.60425 | -0.14191 | -0.09613 | -0.086975 | -0.041199 | -0.11902 | -0.054931 | -0.004577 | 1.8677 | 0.36163 | 0.32043 | 0.48065 | 0.43945 | 0.65918 | 121.5454 | 1.9867 | 121.6278 | 121.4859 | 121.5775 | 121.431 | 121.4584 | -121.5683 | -121.6324 | 121.4905 | 121.5088 | 114.2578 | 57.962
1065.1719 | 121.6919 | -114.299 | 7.2968 | -0.0045011 | -0.00094422 | 0.055777 | 0.054083 | 0.00079894 | -0.0089892 | -0.0015274 | -0.0084228 | 0.0011685 | 0.069551 | 0.056926 | -0.01031 | 0.025887 | 0.00064735 | -0.10986 | 7.1915 | -114.3356 | 7.1548 | -113.7085 | -114.3814 | -114.4363 | -56.6803 | 7.2281 | -114.3951 | 7.1777 | -112.3718 | -113.9603 | -113.9099 | -0.036621 | -0.10529 | -0.14191 | 0.59051 | -0.13733 | -0.082398 | -0.10071 | -0.045777 | -0.096131 | -0.068665 | -0.11902 | 1.9272 | 0.3891 | 0.33874 | 0.48523 | 0.43488 | 0.62714 | 121.4905 | 2.0233 | 121.5729 | 121.5271 | 121.6232 | 121.4905 | 121.5271 | -121.6324 | -121.6919 | 121.4539 | 121.4767 | 114.1891 | 57.6187
1066.9062 | 121.7102 | -114.2899 | 7.2922 | -0.01976 | 0.0048236 | 0.057913 | 0.053656 | 0.00037174 | -0.0074938 | -0.0025956 | -0.0084228 | 0.0020231 | 0.069338 | 0.049022 | -0.0071051 | 0.02546 | 0.0015017 | -0.13733 | 7.1915 | -114.3173 | 7.1686 | -113.7268 | -114.3997 | -114.4501 | -56.7947 | 7.196 | -114.3677 | 7.2144 | -112.2574 | -113.9328 | -113.855 | -0.027466 | -0.10071 | -0.1236 | 0.56305 | -0.16022 | -0.10986 | -0.13275 | -0.082397 | -0.07782 | -0.09613 | -0.07782 | 2.0325 | 0.43488 | 0.35706 | 0.5127 | 0.43488 | 0.59052 | 121.4859 | 2.1103 | 121.582 | 121.5088 | 121.5637 | 121.4813 | 121.4859 | -121.6095 | -121.6599 | 121.4584 | 121.5042 | 114.1525 | 57.4951
1068.6719 | 121.7514 | -114.2807 | 7.2098 | -0.012131 | 0.001833 | 0.056418 | 0.052588 | 0.0033623 | -0.0062122 | 0.0021042 | -0.0084228 | 0.0011685 | 0.06827 | 0.058208 | -0.011164 | 0.023751 | -0.0017027 | -0.059509 | 7.1136 | -114.3402 | 7.2556 | -113.6169 | -114.3036 | -114.3311 | -57.0007 | 7.1457 | -114.4089 | 7.2327 | -112.1292 | -113.8367 | -113.8184 | -0.059509 | -0.096131 | 0.045776 | 0.66376 | -0.050354 | -0.022888 | 0.009155 | 0.036621 | -0.12817 | -0.064087 | 0.022888 | 2.1515 | 0.46234 | 0.44403 | 0.59052 | 0.5722 | 0.72327 | 121.5958 | 2.2797 | 121.6415 | 121.4539 | 121.5546 | 121.3943 | 121.4264 | -121.55 | -121.6187 | 121.5363 | 121.5134 | 114.2212 | 57.28
1070.4062 | 121.701 | -114.2578 | 7.2784 | -0.012131 | 0.0022602 | 0.056204 | 0.055578 | 0.0040033 | -0.0062122 | -0.0011002 | -0.005371 | 0.0035183 | 0.069124 | 0.06184 | -0.010096 | 0.022469 | -0.00042085 | -0.059509 | 7.1732 | -114.2944 | 7.2281 | -113.6261 | -114.3265 | -114.3814 | -57.1518 | 7.2098 | -114.3723 | 7.251 | -112.0651 | -113.8641 | -113.7772 | -0.036622 | -0.10529 | -0.050354 | 0.63171 | -0.1236 | -0.068665 | -0.086975 | -0.032043 | -0.11444 | -0.068664 | -0.027465 | 2.1927 | 0.48065 | 0.39368 | 0.59509 | 0.50812 | 0.66833 | 121.5225 | 2.3071 | 121.6232 | 121.4676 | 121.582 | 121.431 | 121.4676 | -121.5729 | -121.6507 | 121.4859 | 121.5088 | 114.1983 | 57.106
1072.1562 | 121.6736 | -114.4455 | 7.1503 | 0.0031279 | -0.00051702 | 0.05535 | 0.053015 | -0.0015509 | -0.0077074 | -0.0021682 | -0.005371 | 0.0018095 | 0.06827 | 0.056499 | -0.010096 | 0.026314 | 0.0027835 | -0.1236 | 7.0633 | -114.4592 | 7.0358 | -113.8229 | -114.4821 | -114.537 | -57.4219 | 7.0908 | -114.505 | 7.0496 | -112.1017 | -113.9877 | -113.9328 | -0.013733 | -0.086976 | -0.11444 | 0.62256 | -0.091552 | -0.036621 | -0.077819 | -0.022888 | -0.059509 | -0.05951 | -0.10071 | 2.3438 | 0.5127 | 0.45776 | 0.5722 | 0.51727 | 0.63629 | 121.4951 | 2.4033 | 121.5546 | 121.5225 | 121.5958 | 121.5088 | 121.5363 | -121.6095 | -121.6553 | 121.4813 | 121.4951 | 114.3219 | 57.0236
1073.9219 | 121.7194 | -114.3906 | 7.1457 | -0.012131 | 0.0020466 | 0.0577 | 0.054937 | -0.00048286 | -0.0059986 | -0.0040908 | -0.0084228 | 0.0045865 | 0.068911 | 0.061412 | -0.0090277 | 0.02845 | 0.00043375 | -0.15106 | 7.0633 | -114.4363 | 7.0587 | -113.8275 | -114.5187 | -114.5554 | -57.5638 | 7.077 | -114.5096 | 7.0908 | -112.0102 | -113.9603 | -113.8275 | -0.045776 | -0.082398 | -0.086975 | 0.56305 | -0.16479 | -0.12817 | -0.11902 | -0.082398 | -0.11902 | -0.068665 | -0.054932 | 2.3804 | 0.56305 | 0.4303 | 0.68207 | 0.54932 | 0.60882 | 121.4951 | 2.4994 | 121.6003 | 121.4996 | 121.5866 | 121.4539 | 121.4676 | -121.582 | -121.6553 | 121.4493 | 121.4813 | 114.2395 | 56.8268
1075.6719 | 121.6873 | -114.4684 | 7.077 | -0.012131 | 0.00055118 | 0.056845 | 0.05451 | -0.00091006 | -0.0098438 | -0.002382 | -0.0084228 | 0.0043729 | 0.069979 | 0.055858 | -0.0071051 | 0.025246 | -0.00063445 | -0.10529 | 6.9717 | -114.5554 | 6.9351 | -113.9236 | -114.5782 | -114.6286 | -57.5409 | 7.0129 | -114.6011 | 6.9717 | -111.9461 | -114.0335 | -113.8275 | -0.086975 | -0.10529 | -0.14191 | 0.54474 | -0.16022 | -0.10986 | -0.073242 | -0.022888 | -0.13275 | -0.064087 | -0.10529 | 2.5223 | 0.64087 | 0.43488 | 0.77362 | 0.56763 | 0.63171 | 121.4905 | 2.655 | 121.5729 | 121.5271 | 121.6141 | 121.4401 | 121.4813 | -121.6324 | -121.6782 | 121.4035 | 121.4401 | 114.3631 | 56.9275
1077.3594 | 121.6644 | -114.3814 | 7.2006 | -0.02739 | 0.0048236 | 0.058768 | 0.053442 | 0.00058534 | -0.0089892 | -0.0019546 | -0.0084228 | 0.0037321 | 0.067842 | 0.059062 | -0.0075323 | 0.0261 | 0.0055605 | -0.12817 | 7.077 | -114.3997 | 7.0541 | -113.8412 | -114.5142 | -114.5599 | -57.3029 | 7.1136 | -114.4684 | 7.0908 | -111.763 | -113.9374 | -113.681 | -0.01831 | -0.1236 | -0.14649 | 0.54016 | -0.17853 | -0.13275 | -0.16022 | -0.11444 | -0.086975 | -0.086976 | -0.10986 | 2.6184 | 0.70038 | 0.44403 | 0.78735 | 0.53101 | 0.55847 | 121.4539 | 2.7054 | 121.5591 | 121.4767 | 121.582 | 121.4584 | 121.4951 | -121.6003 | -121.669 | 121.4355 | 121.4722 | 114.2532 | 57.0786
1079.125 | 121.7972 | -114.3127 | 7.1365 | -0.0045011 | 0.0033282 | 0.058127 | 0.051947 | -0.00026906 | -0.0062122 | -0.0021682 | -0.005371 | 0.0015957 | 0.069979 | 0.054149 | -0.010737 | 0.027382 | 0.0038515 | -0.091553 | 7.0404 | -114.3768 | 7.1823 | -113.6856 | -114.3814 | -114.4226 | -57.5409 | 7.0312 | -114.4592 | 7.2098 | -111.4792 | -113.3377 | -113.5117 | -0.064087 | -0.096131 | 0.045776 | 0.62714 | -0.10986 | -0.068665 | -0.045776 | -0.004578 | -0.14648 | -0.10529 | 0.073242 | 2.8336 | 0.80109 | 0.97504 | 0.94757 | 1.1215 | 0.69122 | 121.5591 | 2.98 | 121.669 | 121.4172 | 121.4905 | 121.3531 | 121.344 | -121.5134 | -121.5958 | 121.4951 | 121.5225 | 114.2212 | 56.7718
1080.8906 | 121.7834 | -114.2441 | 7.2235 | -0.012131 | 0.0035418 | 0.059836 | 0.055365 | -0.00026906 | -0.0053576 | -0.0019546 | -0.005371 | 0.0030911 | 0.069979 | 0.056285 | -0.011378 | 0.029518 | 0.0025699 | -0.09613 | 7.1182 | -114.2807 | 7.2739 | -113.5666 | -114.2944 | -114.3356 | -68.161 | 7.1411 | -114.3402 | 7.2876 | -111.4609 | -113.1729 | -113.3743 | -0.036621 | -0.10529 | 0.050354 | 0.67749 | -0.091552 | -0.050354 | -0.054931 | -0.013733 | -0.09613 | -0.082398 | 0.064087 | 2.7832 | 0.86975 | 1.0712 | 0.96588 | 1.1673 | 0.71411 | 121.5546 | 2.8793 | 121.6278 | 121.3989 | 121.4813 | 121.3623 | 121.3852 | -121.5042 | -121.5637 | 121.5179 | 121.5317 | 114.1479 | 46.0831
1082.6406 | 121.6507 | -114.386 | 7.1365 | 0.0031279 | 0.002901 | 0.056204 | 0.05451 | 0.0020807 | -0.0070666 | -0.0015274 | -0.005371 | 0.0030911 | 0.070406 | 0.060771 | -0.01031 | 0.026955 | 0.0047061 | -0.091553 | 7.0312 | -114.4409 | 7.0633 | -113.8046 | -114.505 | -114.5508 | -57.1335 | 7.077 | -114.5004 | 7.0541 | -111.3373 | -113.9328 | -113.562 | -0.054932 | -0.10529 | -0.073243 | 0.58136 | -0.16479 | -0.11902 | -0.10986 | -0.064087 | -0.11444 | -0.05951 | -0.082398 | 3.0487 | 0.82397 | 0.45319 | 0.93842 | 0.56763 | 0.63629 | 121.5042 | 3.1631 | 121.5546 | 121.4722 | 121.5775 | 121.4172 | 121.463 | -121.5775 | -121.637 | 121.4493 | 121.4401 | 114.2944 | 57.2525
1084.3281 | 121.7422 | -113.9969 | 7.457 | -0.012131 | 0.0033282 | 0.058981 | 0.05451 | 0.0016535 | -0.0057848 | -0.0019546 | -0.005371 | 0.0018095 | 0.068483 | 0.058208 | -0.012019 | 0.029518 | 0.0038515 | -0.11444 | 7.3334 | -114.0381 | 7.4982 | -113.3331 | -114.0427 | -114.0701 | -68.541 | 7.3654 | -114.1251 | 7.5073 | -110.8246 | -112.8387 | -113.0997 | -0.041199 | -0.1236 | 0.041199 | 0.66376 | -0.073242 | -0.045777 | -0.032043 | -0.004578 | -0.12817 | -0.091553 | 0.050354 | 3.1723 | 0.89722 | 1.1581 | 1.0254 | 1.2863 | 0.70496 | 121.5363 | 3.3005 | 121.6324 | 121.3715 | 121.4905 | 121.3303 | 121.3623 | -121.4951 | -121.582 | 121.4951 | 121.5042 | 113.8824 | 45.4559
1086.0781 | 121.6644 | -113.7588 | 7.7957 | -0.0045011 | 0.0043964 | 0.0577 | 0.054083 | 0.0016535 | -0.0062122 | -0.0040908 | -0.005371 | 0.0048001 | 0.069765 | 0.059276 | -0.01095 | 0.031868 | 0.0042789 | -0.14191 | 7.6813 | -113.7863 | 7.6767 | -113.1821 | -113.8779 | -113.9099 | -69.104 | 7.7133 | -113.8641 | 7.6996 | -110.4904 | -112.587 | -112.8433 | -0.027466 | -0.11444 | -0.11902 | 0.57678 | -0.15106 | -0.11902 | -0.1236 | -0.091553 | -0.10529 | -0.082397 | -0.09613 | 3.2684 | 0.91553 | 1.1719 | 1.0208 | 1.2772 | 0.60425 | 121.463 | 3.3737 | 121.5637 | 121.4676 | 121.5775 | 121.4401 | 121.4722 | -121.582 | -121.6599 | 121.4355 | 121.4584 | 113.6169 | 44.6548
1087.7656 | 121.7331 | -113.7222 | 7.7911 | -0.012131 | 0.001192 | 0.057059 | 0.05152 | -0.0034735 | -0.0064258 | -0.0028092 | -0.0084228 | 0.0022367 | 0.066347 | 0.056926 | -0.012019 | 0.031868 | 0.0079105 | -0.13275 | 7.6675 | -113.7909 | 7.7362 | -113.0951 | -113.7909 | -113.8321 | -69.3146 | 7.6767 | -113.8367 | 7.7545 | -110.2753 | -112.3993 | -112.674 | -0.068665 | -0.1236 | -0.054932 | 0.62714 | -0.10986 | -0.068665 | -0.041198 | 0 | -0.11444 | -0.11444 | -0.036621 | 3.447 | 1.0483 | 1.3229 | 1.1627 | 1.4374 | 0.6958 | 121.5271 | 3.5614 | 121.5912 | 121.4584 | 121.5134 | 121.3898 | 121.3989 | -121.582 | -121.6278 | 121.4584 | 121.4767 | 113.5895 | 44.4077
1089.5156 | 121.7285 | -113.7314 | 7.7728 | -0.02739 | 0.00033758 | 0.056204 | 0.053015 | -0.00048286 | -0.0074938 | -0.0053726 | -0.0084228 | 0.0024503 | 0.068697 | 0.060344 | -0.011164 | 0.032509 | 0.0083377 | -0.16022 | 7.6675 | -113.7497 | 7.7637 | -113.0997 | -113.7726 | -113.8229 | -69.2825 | 7.7133 | -113.8184 | 7.7683 | -109.8907 | -112.1109 | -112.7335 | -0.018311 | -0.10529 | -0.009155 | 0.63171 | -0.091553 | -0.041199 | -0.073242 | -0.022888 | -0.086975 | -0.059509 | -0.004577 | 3.8406 | 0.99793 | 1.6205 | 1.0849 | 1.7075 | 0.65002 | 121.5134 | 3.9276 | 121.5866 | 121.4172 | 121.5317 | 121.3989 | 121.4447 | -121.5225 | -121.5912 | 121.4951 | 121.4996 | 113.5712 | 44.4489
1091.2656 | 121.7743 | -113.7131 | 7.7179 | -0.01976 | 0.0037556 | 0.0577 | 0.054083 | -0.00048286 | -0.0064258 | -0.0011002 | -0.0084228 | 0.0020231 | 0.069338 | 0.065898 | -0.011378 | 0.032509 | 0.0062015 | -0.09613 | 7.6309 | -113.768 | 7.7957 | -113.0585 | -113.7726 | -113.8092 | -69.2551 | 7.6309 | -113.8138 | 7.7316 | -109.9274 | -111.7172 | -112.3032 | -0.054931 | -0.086976 | 0.077819 | 0.6546 | -0.09613 | -0.059509 | -0.041199 | -0.004578 | -0.10071 | -0.086976 | 0.013732 | 3.7857 | 1.4099 | 1.9959 | 1.5106 | 2.0966 | 0.70953 | 121.5637 | 3.8864 | 121.5454 | 121.3989 | 121.4447 | 121.344 | 121.344 | -121.4859 | -121.5317 | 121.5088 | 121.4447 | 113.6169 | 44.458
1093.0156 | 121.7468 | -113.4888 | 7.9971 | -0.012131 | 0.00097838 | 0.059195 | 0.053869 | -0.0024055 | -0.0049304 | -0.0030228 | -0.0084228 | 0.0028775 | 0.069338 | 0.070384 | -0.0098823 | 0.032082 | 0.0072695 | -0.15564 | 7.8552 | -113.5757 | 7.9926 | -112.8571 | -113.5162 | -113.562 | -70.3995 | 7.9239 | -113.5757 | 8.0338 | -109.6664 | -111.319 | -112.088 | -0.086975 | -0.14191 | -0.004577 | 0.63171 | -0.073242 | -0.027465 | 0.013733 | 0.05951 | -0.086975 | -0.073242 | 0.036621 | 3.8223 | 1.4008 | 2.1698 | 1.4877 | 2.2568 | 0.71869 | 121.5683 | 3.9093 | 121.6095 | 121.431 | 121.4996 | 121.344 | 121.4127 | -121.5729 | -121.5729 | 121.4813 | 121.5225 | 113.3331 | 43.0893
1094.7031 | 121.6736 | -81.7062 | 39.6561 | -0.012131 | 0.00076478 | 0.056418 | 0.052588 | 0.00058534 | -0.0059986 | -0.0019546 | -0.005371 | 0.0039457 | 0.066774 | 0.063762 | -0.012873 | 0.027169 | 0.01026 | -1.3092 | 36.3968 | -85.025 | 36.7264 | -84.2194 | -84.9976 | -85.5469 | -36.5799 | 35.5316 | -85.3683 | 40.7318 | -78.0075 | -81.0883 | -80.7449 | -3.3188 | -3.2593 | -2.9297 | -2.5131 | -3.8406 | -3.2913 | -0.52185 | 0.027465 | -3.6621 | -4.1245 | 1.0757 | 3.6987 | 0.9613 | 0.61798 | 4.6234 | 4.2801 | 0.80566 | 121.7514 | 7.3608 | 126.1002 | 121.4218 | 120.9 | 118.103 | 117.2379 | -124.6811 | -125.0244 | 118.4326 | 122.4381 | 80.397 | 45.1263
1096.4531 | 121.4493 | -72.5876 | 48.7656 | -0.012131 | 0.0024738 | 0.056204 | 0.053869 | 0.00058534 | -0.0070666 | -0.0032364 | -0.0084228 | 0.0052273 | 0.069765 | 0.08427 | -0.0096685 | 0.035286 | 0.0081241 | 0.6134 | 48.6923 | -72.5967 | 48.6832 | -72.3404 | -72.8256 | -72.7615 | -40.3336 | 48.7152 | -72.5647 | 48.761 | -70.0653 | -70.4407 | -71.022 | -0.009156 | -0.073242 | -0.082397 | 0.24719 | -0.17395 | -0.23804 | -0.1648 | -0.22888 | 0.022888 | -0.050354 | -0.004578 | 2.5223 | 1.5656 | 2.1469 | 1.5427 | 2.124 | 0.25635 | 121.2799 | 2.4994 | 121.3257 | 121.2891 | 121.2799 | 121.2799 | 121.3028 | -121.3623 | -121.3303 | 121.2708 | 121.3486 | 73.201 | 32.254
1098.2188 | 121.5546 | -77.9251 | 43.1168 | -0.02739 | 0.0041828 | 0.057913 | 0.055365 | 0.0010125 | -0.005144 | -0.000673 | -0.005371 | 0.0067227 | 0.069551 | 0.079143 | -0.0092413 | 0.0355 | 0.0098331 | 0.14191 | 43.7347 | -77.6962 | 42.897 | -77.5955 | -78.0167 | -78.2547 | -45.2087 | 43.5699 | -77.6321 | 43.1259 | -75.2792 | -75.3067 | -75.4578 | 0.22888 | 0.61798 | -0.21973 | 0.32959 | -0.32959 | -0.091553 | -0.55847 | -0.32043 | 0.29297 | 0.45319 | 0.009156 | 2.6459 | 2.4673 | 2.6184 | 2.1744 | 2.3254 | 0.10071 | 120.5933 | 2.3529 | 120.7581 | 121.431 | 121.2021 | 121.6599 | 121.4951 | -120.813 | -120.7489 | 120.8221 | 121.051 | 78.067 | 32.7164
1099.9062 | 121.431 | -83.67 | 37.5183 | -0.01976 | 0.0041828 | 0.055136 | 0.05451 | 0.00015814 | -0.0089892 | -0.0025956 | -0.0084228 | 0.0052273 | 0.070833 | 0.072521 | -0.0073187 | 0.036141 | 0.0072695 | -0.29297 | 37.2803 | -83.8531 | 37.7747 | -83.0109 | -83.7662 | -83.7021 | -49.1867 | 37.5687 | -83.6151 | 37.3306 | -80.7495 | -81.1523 | -81.7291 | -0.1831 | -0.23804 | 0.25635 | 0.65918 | -0.032043 | -0.09613 | 0.15106 | 0.086975 | 0.054932 | 0.050354 | -0.18768 | 2.9205 | 1.9409 | 2.5177 | 1.886 | 2.4628 | 0.84229 | 121.6278 | 2.8656 | 120.9457 | 121.1334 | 121.1838 | 120.9503 | 121.2387 | -121.3715 | -121.1334 | 121.4447 | 121.0007 | 83.3771 | 34.4833
1101.6562 | 121.2799 | -52.652 | 68.3899 | -0.0045011 | 0.0048236 | 0.056631 | 0.052374 | 0.0027215 | -0.0059986 | -0.0030228 | -0.005371 | 0.0052273 | 0.069979 | 0.073162 | -0.0090277 | 0.029305 | 0.012183 | 0.46234 | 68.1793 | -52.8214 | 68.2892 | -52.7069 | -53.0319 | -53.4073 | -7.2189 | 68.0008 | -52.8854 | 68.9484 | -49.9191 | -52.1439 | -50.8575 | -0.16937 | -0.21057 | -0.10071 | -0.054931 | -0.75531 | -0.37994 | -0.58594 | -0.21057 | -0.23346 | -0.3891 | 0.55847 | 2.7328 | 1.7944 | 0.50812 | 2.0279 | 0.74158 | 0.11444 | 121.1105 | 2.9663 | 121.8338 | 121.0007 | 120.8862 | 120.8313 | 120.6528 | -121.2112 | -121.2753 | 120.9412 | 121.6003 | 53.1143 | 45.433
1103.4062 | 121.1472 | -55.6183 | 65.5746 | -0.012131 | -0.00073062 | 0.053 | 0.052588 | -0.0041145 | -0.0064258 | -0.0032364 | -0.005371 | 0.0052273 | 0.071688 | 0.074016 | -0.0088141 | 0.029091 | 0.016242 | -1.0254 | 65.7761 | -55.2155 | 66.4261 | -54.5837 | -54.9179 | -54.6066 | -9.613 | 65.7532 | -55.4352 | 65.6662 | -52.6382 | -54.8538 | -53.0502 | 0.40283 | 0.20142 | 0.85144 | 1.0345 | 1.0117 | 0.70038 | 0.60883 | 0.29755 | 0.1831 | 0.17853 | 0.091553 | 2.98 | 2.5681 | 0.76446 | 2.3849 | 0.58136 | 0.63171 | 121.6415 | 2.7969 | 121.1014 | 120.9915 | 121.1884 | 121.3943 | 121.3715 | -120.7901 | -121.0098 | 122.0444 | 121.2845 | 54.5929 | 46.0052
1105.1562 | 121.3074 | -55.2612 | 65.799 | -0.01976 | 0.00076478 | 0.058127 | 0.051306 | 0.00037174 | -0.0042896 | -0.0045182 | -0.0023192 | 0.0022367 | 0.068911 | 0.083629 | -0.010737 | 0.033364 | 0.019873 | -1.6159 | 64.119 | -56.7444 | 65.6342 | -54.895 | -55.925 | -55.5679 | -16.0904 | 65.387 | -55.5954 | 65.5884 | -52.7847 | -53.8376 | -51.8097 | -1.4832 | -1.68 | -0.16479 | 0.36621 | -0.3067 | -0.66376 | 1.1765 | 0.8194 | -0.33417 | -0.41199 | -0.21057 | 2.4765 | 3.4515 | 1.4236 | 3.7857 | 1.7578 | 1.8494 | 122.3785 | 2.8107 | 121.1838 | 120.8633 | 120.9824 | 119.3802 | 120.6482 | -122.5433 | -121.3943 | 120.8954 | 120.8496 | 53.6453 | 39.1708
1106.9219 | 120.9366 | -49.0814 | 71.8506 | -0.01976 | 0.0054644 | 0.056418 | 0.054297 | -5.5462e-05 | -0.0040758 | -0.0053726 | -0.005371 | 0.0080045 | 0.070406 | 0.081706 | -0.0094549 | 0.036141 | 0.017096 | 0.032043 | 71.4432 | -49.4385 | 71.9879 | -48.6465 | -49.0631 | -49.0814 | -14.566 | 71.5439 | -49.292 | 71.3516 | -46.7056 | -47.1222 | -46.5958 | -0.35706 | -0.40741 | 0.13733 | 0.43488 | 0 | 0.018311 | 0.35706 | 0.37537 | -0.21057 | -0.3067 | -0.49896 | 2.3758 | 2.4857 | 1.9592 | 2.6962 | 2.1698 | 0.79193 | 121.4264 | 2.5864 | 120.6436 | 120.8817 | 120.8359 | 120.5246 | 120.6253 | -121.2891 | -121.1426 | 121.0693 | 120.433 | 49.1135 | 34.5154
1108.6875 | 120.6024 | -50.3128 | 70.1477 | -0.0045011 | 0.006319 | 0.056418 | 0.054297 | 0.00079894 | -0.0064258 | -0.000673 | -0.005371 | 0.0069363 | 0.071047 | 0.09666 | -0.0096685 | 0.036782 | 0.022223 | 1.1124 | 68.0923 | -52.1713 | 70.5917 | -49.6078 | -50.1663 | -50.0519 | -11.7325 | 70.6375 | -49.6307 | 70.491 | -47.7127 | -48.1796 | -47.0718 | -1.8585 | -2.0554 | 0.44403 | 0.70496 | 0.26093 | 0.14648 | 2.1194 | 2.005 | 0.68207 | 0.48981 | 0.34332 | 2.6001 | 3.241 | 2.1332 | 2.5589 | 1.4511 | 2.5635 | 122.7631 | 1.918 | 120.1218 | 120.2637 | 120.2682 | 118.4052 | 120.9503 | -122.319 | -119.7784 | 120.9045 | 120.8038 | 51.4252 | 38.5803
1110.3906 | 121.1792 | -0.19684 | 121.0739 | -0.012131 | 0.0058918 | 0.055563 | 0.053869 | 0.0016535 | -0.0066394 | -0.0028092 | 0.00073235 | 0.0054409 | 0.067629 | 0.097301 | -0.0096685 | 0.034432 | 0.015387 | 0.14191 | 120.9183 | -0.21057 | 120.8633 | -0.10529 | -0.23346 | -0.21057 | 24.5041 | 120.8267 | -0.21515 | 120.845 | 1.6571 | 1.7212 | 3.2455 | -0.013733 | -0.15564 | -0.21057 | 0.091552 | -0.013733 | -0.036621 | 0 | -0.022888 | -0.018311 | -0.24719 | -0.22888 | 1.8539 | 3.4424 | 1.918 | 3.4607 | 1.9363 | 0.10529 | 121.0739 | 1.8723 | 121.0602 | 121.1288 | 121.0419 | 121.1151 | 121.0236 | -121.2845 | -121.2891 | 121.0602 | 121.0419 | 0.33875 | 24.7009
1112.1406 | 121.344 | -0.2243 | 121.1014 | -0.012131 | -0.00073062 | 0.056418 | 0.052801 | -0.00069646 | -0.0049304 | -0.0032364 | -0.005371 | 0.0035183 | 0.06827 | 0.10435 | -0.011378 | 0.035286 | 0.02735 | 0.054932 | 120.9824 | -0.24719 | 121.0007 | -0.064087 | -0.19226 | -0.16022 | 24.4308 | 120.8908 | -0.22888 | 120.9366 | 1.7029 | 1.8219 | 3.9459 | -0.022888 | -0.11902 | -0.10071 | 0.16022 | 0.064087 | 0.032043 | 0.086975 | 0.054931 | -0.004578 | -0.21057 | -0.16479 | 1.9272 | 4.1702 | 2.0462 | 4.1748 | 2.0508 | 0.1831 | 121.2479 | 1.9318 | 121.1655 | 121.2296 | 121.1197 | 121.2067 | 121.1151 | -121.3486 | -121.3303 | 121.225 | 121.1609 | 0.27924 | 24.6552
1113.8594 | 121.4447 | -0.23804 | 121.1151 | -0.01976 | 0.0054644 | 0.057486 | 0.053442 | 0.00015814 | -0.0070666 | -0.00345 | -0.0084228 | 0.0065091 | 0.068911 | 0.11375 | -0.011164 | 0.034859 | 0.029059 | 0.11444 | 121.0052 | -0.24719 | 121.0785 | -0.041199 | -0.17395 | -0.15106 | 24.0463 | 120.9 | -0.2243 | 121.0236 | 1.8356 | 1.6983 | 5.1498 | -0.009155 | -0.10986 | -0.036621 | 0.19684 | 0.086975 | 0.064087 | 0.09613 | 0.073242 | 0.013733 | -0.21515 | -0.091552 | 2.0737 | 5.3879 | 1.9363 | 5.3741 | 1.9226 | 0.20599 | 121.3257 | 2.0599 | 121.2479 | 121.2524 | 121.1243 | 121.2433 | 121.138 | -121.3623 | -121.3394 | 121.3165 | 121.2616 | 0.35248 | 24.2844
1115.6094 | 121.4493 | -0.35706 | 120.9869 | -0.012131 | 0.0014056 | 0.054922 | 0.050024 | 0.00015814 | -0.0092028 | -0.0038772 | -0.0084228 | 0.0052273 | 0.07062 | 0.68071 | -0.013514 | 0.036782 | 0.58362 | 0.082397 | 120.8588 | -0.37994 | 120.9641 | -0.10529 | -0.23804 | -0.21973 | 25.8224 | 120.7306 | -0.3067 | 120.8176 | 7.2784 | 2.5452 | 86.8835 | -0.022888 | -0.12817 | -0.022888 | 0.25177 | 0.13733 | 0.11902 | 0.16022 | 0.14191 | 0.050354 | -0.25635 | -0.16937 | 7.6355 | 87.2406 | 2.9022 | 87.1902 | 2.8519 | 0.27466 | 121.344 | 7.5851 | 121.1243 | 121.2387 | 121.0373 | 121.2158 | 121.0876 | -121.3669 | -121.2936 | 121.3211 | 121.1746 | 0.43945 | 26.1795
1117.3125 | 121.4081 | -0.38452 | 120.9732 | -0.012131 | 0.00076478 | 0.054922 | 0.053656 | -0.00026906 | -0.0055712 | -0.002382 | -0.005371 | 0.0065091 | 0.076387 | 0.84028 | -0.013514 | 0.035286 | 0.74384 | 0.032043 | 120.8267 | -0.3891 | 120.8725 | -0.2243 | -0.35248 | -0.31586 | 24.5361 | 120.7031 | -0.32501 | 120.6802 | 16.7313 | 2.7466 | 111.264 | -0.004578 | -0.14648 | -0.10071 | 0.16022 | 0.068664 | 0.032043 | 0.073242 | 0.036621 | 0.059509 | -0.27008 | -0.29297 | 17.1158 | 111.6486 | 3.1311 | 111.5891 | 3.0716 | 0.16479 | 121.2616 | 17.0563 | 121.0052 | 121.2158 | 121.0281 | 121.2112 | 121.0876 | -121.3623 | -121.2982 | 121.257 | 121.0648 | 0.41656 | 24.9207
1119.0781 | 121.4584 | -0.37537 | 120.9457 | -0.01976 | 0.001833 | 0.05535 | 0.054297 | -5.5462e-05 | -0.0098438 | -0.0015274 | -0.005371 | 0.0058683 | 0.076815 | 0.86036 | -0.013728 | 0.039345 | 0.74961 | 0.09613 | 120.813 | -0.3891 | 120.9366 | -0.1236 | -0.2655 | -0.24719 | 23.9319 | 120.6848 | -0.32959 | 120.7306 | 18.1778 | 2.8839 | 113.3972 | -0.013733 | -0.13275 | -0.009156 | 0.25177 | 0.12817 | 0.10986 | 0.14191 | 0.1236 | 0.045776 | -0.26093 | -0.21515 | 18.5532 | 113.7726 | 3.2593 | 113.7268 | 3.2135 | 0.2655 | 121.3257 | 18.5074 | 121.0602 | 121.2021 | 121.0144 | 121.1884 | 121.0602 | -121.3348 | -121.2753 | 121.3119 | 121.106 | 0.4715 | 24.3073
1120.7812 | 121.4722 | -0.39825 | 120.9 | -0.012131 | 0.00097838 | 0.054709 | 0.053228 | -0.0036871 | -0.0074938 | -0.0049454 | -0.005371 | 0.0043729 | 0.076174 | 0.85908 | -0.014155 | 0.039772 | 0.75239 | 0.07782 | 120.7947 | -0.40741 | 120.9183 | -0.15106 | -0.30212 | -0.28381 | 23.2956 | 120.6665 | -0.34332 | 120.7306 | 19.9448 | 4.0741 | 114.0106 | -0.009156 | -0.10528 | 0.018311 | 0.24719 | 0.11444 | 0.09613 | 0.1236 | 0.10529 | 0.054931 | -0.23346 | -0.16937 | 20.343 | 114.4089 | 4.4724 | 114.3539 | 4.4174 | 0.25635 | 121.3257 | 20.2881 | 121.0739 | 121.2021 | 121.0098 | 121.1929 | 121.0648 | -121.3074 | -121.2433 | 121.3165 | 121.1288 | 0.47607 | 23.6938
1122.5312 | 121.4172 | -0.44861 | 120.8679 | -0.01976 | 0.0048236 | 0.055991 | 0.051306 | -0.0032599 | -0.0074938 | -0.0030228 | -0.0023192 | 0.0082181 | 0.078951 | 0.86314 | -0.012659 | 0.039131 | 0.74876 | 0.004578 | 120.7855 | -0.46692 | 120.8084 | -0.27924 | -0.42114 | -0.39368 | 22.879 | 120.6299 | -0.40741 | 120.6253 | 22.4854 | 2.8793 | 114.4089 | -0.018311 | -0.082398 | -0.059509 | 0.16937 | 0.054931 | 0.027465 | 0.073242 | 0.045776 | 0.041198 | -0.23804 | -0.24262 | 22.934 | 114.8575 | 3.3279 | 114.8163 | 3.2867 | 0.18768 | 121.2753 | 22.8928 | 121.0327 | 121.2524 | 121.0373 | 121.2341 | 121.0785 | -121.3348 | -121.2753 | 121.257 | 121.0739 | 0.45319 | 23.3276
1124.2969 | 121.4218 | -0.47607 | 120.8908 | 0.010757 | 0.00033758 | 0.053854 | 0.054083 | -0.00069646 | -0.0089892 | -0.00345 | -0.005371 | 0.0054409 | 0.080019 | 0.86335 | -0.012446 | 0.041481 | 0.74555 | 0.11902 | 120.7397 | -0.47607 | 120.845 | -0.25177 | -0.38452 | -0.37537 | 21.7987 | 120.6116 | -0.41199 | 120.6207 | 24.8566 | 3.2364 | 114.7385 | 0 | -0.15106 | -0.045776 | 0.2243 | 0.10071 | 0.091553 | 0.10071 | 0.091553 | 0.064087 | -0.27924 | -0.27008 | 25.3326 | 115.2145 | 3.7125 | 115.1505 | 3.6484 | 0.2243 | 121.3211 | 25.2686 | 121.0327 | 121.2158 | 121.0236 | 121.2158 | 121.0876 | -121.3669 | -121.3028 | 121.3211 | 121.0968 | 0.59509 | 22.2748
1126.0469 | 121.3898 | -0.48523 | 120.8633 | -0.01976 | 0.0050372 | 0.056845 | 0.053656 | -0.0030463 | -0.0057848 | -0.0049454 | -0.0023192 | 0.0077909 | 0.080019 | 0.86378 | -0.01031 | 0.044686 | 0.74085 | 0.022888 | 120.7397 | -0.48065 | 120.7993 | -0.30212 | -0.44861 | -0.41199 | 21.0938 | 120.5978 | -0.42114 | 120.5841 | 26.9669 | 3.3966 | 114.9353 | 0.004577 | -0.1236 | -0.064087 | 0.18311 | 0.073242 | 0.036621 | 0.068665 | 0.032044 | 0.064086 | -0.2655 | -0.27924 | 27.4521 | 115.4205 | 3.8818 | 115.3564 | 3.8177 | 0.17853 | 121.2799 | 27.388 | 121.0052 | 121.2204 | 121.019 | 121.225 | 121.0831 | -121.344 | -121.2845 | 121.2845 | 121.0693 | 0.50812 | 21.579
1127.7344 | 121.4264 | -0.47607 | 120.8542 | -0.0045011 | 0.0031146 | 0.053854 | 0.054083 | -0.0015509 | -0.0079212 | -0.0036636 | -0.005371 | 0.0082181 | 0.081301 | 0.86293 | -0.012659 | 0.044045 | 0.74 | 0 | 120.7626 | -0.48065 | 120.7718 | -0.3067 | -0.44403 | -0.41657 | 19.4595 | 120.6162 | -0.41199 | 120.5841 | 26.8295 | 3.5614 | 115.0864 | -0.004578 | -0.091553 | -0.082397 | 0.16937 | 0.059509 | 0.032043 | 0.064087 | 0.036621 | 0.064087 | -0.23804 | -0.27008 | 27.3056 | 115.5624 | 4.0375 | 115.4984 | 3.9734 | 0.17395 | 121.2524 | 27.2415 | 120.9961 | 121.2433 | 121.0281 | 121.2387 | 121.0922 | -121.3348 | -121.2662 | 121.2479 | 121.0602 | 0.47607 | 19.9356
1129.4844 | 121.3303 | -0.54016 | 120.8725 | -0.012131 | 0.0039692 | 0.055991 | 0.057074 | -0.00048286 | -0.0083484 | -0.0008866 | -0.0023192 | 0.0080045 | 0.081301 | 0.86421 | -0.0092413 | 0.046608 | 0.73487 | 0.018311 | 120.7718 | -0.54016 | 120.6757 | -0.44403 | -0.56305 | -0.52185 | 19.2764 | 120.639 | -0.48523 | 120.5292 | 26.2436 | 3.5202 | 115.1779 | 0 | -0.10071 | -0.19684 | 0.09613 | 0.01831 | -0.022888 | 0.01831 | -0.022888 | 0.054932 | -0.23346 | -0.34332 | 26.7838 | 115.7181 | 4.0604 | 115.6631 | 4.0054 | 0.09613 | 121.2158 | 26.7288 | 121.0144 | 121.312 | 121.1243 | 121.312 | 121.1792 | -121.4127 | -121.3577 | 121.2158 | 121.0693 | 0.55847 | 19.8166
1131.1875 | 121.376 | -0.51727 | 120.8725 | -0.012131 | 0.0043964 | 0.054282 | 0.056219 | 0.0052851 | -0.0081348 | -0.0008866 | -0.0084228 | 0.012063 | 0.084078 | 0.86058 | -0.0086005 | 0.04554 | 0.72996 | 0.11444 | 120.7581 | -0.52643 | 120.7718 | -0.3479 | -0.48523 | -0.46234 | 17.1295 | 120.6345 | -0.43945 | 120.575 | 29.6036 | 3.447 | 115.3473 | -0.009155 | -0.11444 | -0.10071 | 0.16937 | 0.054932 | 0.032044 | 0.064087 | 0.041199 | 0.07782 | -0.23804 | -0.29755 | 30.1209 | 115.8646 | 3.9642 | 115.7867 | 3.8864 | 0.17853 | 121.2982 | 30.043 | 121.0144 | 121.2845 | 121.0739 | 121.2753 | 121.1517 | -121.3989 | -121.312 | 121.2891 | 121.0922 | 0.63171 | 17.6468
1132.9375 | 121.3531 | -0.53558 | 120.845 | -0.0045011 | 0.001833 | 0.055777 | 0.050879 | -0.0017645 | -0.0081348 | 0.0006088 | -0.005371 | 0.0082181 | 0.088991 | 0.861 | -0.012446 | 0.044899 | 0.73167 | 0.091553 | 120.7306 | -0.5127 | 120.7672 | -0.31128 | -0.42572 | -0.41657 | 18.4937 | 120.5841 | -0.45319 | 120.5292 | 39.5279 | 3.5248 | 115.2191 | 0.022888 | -0.11444 | -0.07782 | 0.2243 | 0.11902 | 0.10986 | 0.09613 | 0.086975 | 0.082397 | -0.26093 | -0.31586 | 40.0635 | 115.7547 | 4.0604 | 115.6723 | 3.978 | 0.20142 | 121.2799 | 39.9811 | 120.9824 | 121.2433 | 121.0373 | 121.2662 | 121.1197 | -121.3577 | -121.2982 | 121.3028 | 121.0648 | 0.62714 | 19.0292
1134.6875 | 121.4493 | -0.55389 | 120.7489 | -0.0045011 | 0.00097838 | 0.054709 | 0.052588 | 0.00037174 | -0.0081348 | -0.0043046 | -0.0023192 | 0.0058683 | 0.088991 | 1.2652 | -0.011591 | 0.44886 | 0.70539 | 0.091553 | 120.6802 | -0.56763 | 120.7581 | -0.30212 | -0.43488 | -0.42572 | 43.2678 | 120.4559 | -0.45319 | 120.3735 | 41.4185 | 70.1752 | 114.4135 | -0.013733 | -0.068664 | 0.009156 | 0.25177 | 0.12817 | 0.11902 | 0.14191 | 0.13275 | 0.10071 | -0.29297 | -0.37537 | 41.9724 | 114.9673 | 70.7291 | 114.8666 | 70.6284 | 0.2655 | 121.3257 | 41.8716 | 120.8267 | 121.2479 | 120.9091 | 121.2341 | 121.0098 | -121.3165 | -121.2021 | 121.312 | 120.9274 | 0.64545 | 43.8217
1136.4375 | 121.4539 | -0.60883 | 120.6894 | -0.0045011 | 0.00076478 | 0.053214 | 0.053442 | 0.00079894 | -0.0079212 | -0.0036636 | -0.011475 | 0.0056547 | 0.099672 | 1.435 | -0.014582 | 0.6189 | 0.68937 | 0.10986 | 120.575 | -0.63171 | 120.6985 | -0.37537 | -0.5127 | -0.49896 | 78.4058 | 120.3781 | -0.50812 | 120.2225 | 52.9083 | 109.314 | 113.6627 | -0.022888 | -0.11444 | 0.009155 | 0.23346 | 0.10986 | 0.096131 | 0.13275 | 0.11902 | 0.10071 | -0.31128 | -0.46692 | 53.5172 | 114.2715 | 109.9228 | 114.1708 | 109.8221 | 0.25635 | 121.3303 | 53.4164 | 120.7306 | 121.2067 | 120.8862 | 121.1838 | 120.9869 | -121.3211 | -121.1975 | 121.3074 | 120.8313 | 0.71869 | 79.0146
1138.125 | 121.4172 | -0.64087 | 120.7306 | -0.012131 | 0.001833 | 0.056204 | 0.055151 | 0.0029351 | -0.0062122 | -0.0038772 | -0.005371 | 0.0041593 | 0.093904 | 0.20924 | -0.0066779 | 0.078011 | 0.027137 | 0.19684 | 120.7626 | -0.55847 | 120.7031 | -0.43945 | -0.19226 | -0.2655 | 85.5789 | 120.6207 | -0.58136 | 120.163 | 45.5887 | 118.7439 | 83.0933 | 0.082397 | 0.032043 | -0.027466 | 0.20142 | 0.37537 | 0.44861 | 0.29297 | 0.36621 | 0.059509 | -0.10986 | -0.56763 | 46.2296 | 83.7341 | 119.3848 | 83.6746 | 119.3253 | 0.11902 | 121.2616 | 46.17 | 120.7443 | 121.3211 | 121.2021 | 121.4035 | 121.2616 | -121.2891 | -121.312 | 121.344 | 120.8038 | 0.83771 | 86.2198
1139.875 | 121.5179 | -0.42114 | 120.9045 | -0.0045011 | 0.0058918 | 0.055991 | 0.054083 | 0.0022943 | -0.0062122 | -0.0030228 | -0.005371 | 0.0028775 | 0.071901 | -0.0084423 | 0.10526 | 0.046822 | -0.0019163 | 0.16022 | 120.8313 | -0.44403 | 120.9 | -0.23346 | -0.4303 | -0.36621 | 8.9767 | 120.726 | -0.43945 | 1.268 | 121.1517 | 1.3412 | 80.5527 | -0.022888 | -0.073242 | -0.004578 | 0.18768 | 0.054932 | -0.009155 | 0.07782 | 0.013733 | -0.01831 | -0.17853 | -119.6365 | 121.5729 | 80.9738 | 1.7624 | 80.9921 | 1.7807 | 0.21057 | 121.344 | 121.5912 | 1.7075 | 121.2753 | 121.1655 | 121.2524 | 121.1472 | -121.3486 | -121.344 | 121.3211 | 1.6891 | 0.58136 | 9.3979
1141.6406 | 121.5179 | -0.49896 | 120.8817 | -0.01976 | 0.0033282 | 0.053854 | 0.054937 | -0.0015509 | -0.0057848 | -0.001741 | -0.0023192 | 0.0043729 | 0.081728 | -0.011647 | 0.11594 | 0.039772 | -0.0042661 | 0.19226 | 120.7993 | -0.50354 | 120.845 | -0.29755 | -0.42572 | -0.40283 | 13.2156 | 120.7031 | -0.4715 | 14.2639 | 121.1197 | 15.3076 | 79.9942 | -0.004578 | -0.082398 | -0.036621 | 0.20142 | 0.09613 | 0.073242 | 0.10071 | 0.07782 | 0.027465 | -0.17853 | -106.6177 | 121.6187 | 80.4932 | 15.8066 | 80.4657 | 15.7791 | 0.20599 | 121.3486 | 121.5912 | 14.7354 | 121.3028 | 121.1746 | 121.2982 | 121.2021 | -121.3852 | -121.3531 | 121.344 | 14.7629 | 0.69122 | 13.7146
1143.3438 | 121.4127 | -0.36163 | 121.0281 | -0.012131 | 0.0067462 | 0.054495 | 0.056433 | 0.00058534 | -0.0070666 | -0.005159 | -0.005371 | 0.011636 | 0.024263 | 0.99025 | -0.01031 | 0.50932 | 0.46934 | -0.16022 | 120.8725 | -0.44861 | 120.8405 | -0.29755 | -0.42572 | -0.39368 | 16.3925 | 120.7718 | -0.31128 | 19.7983 | 8.757 | 13.0783 | 13.0142 | -0.086975 | -0.15564 | -0.18768 | 0.064087 | -0.032044 | -0.064087 | 0.054931 | 0.022888 | 0.050354 | -0.25635 | -101.2299 | 9.1187 | 13.3759 | 13.4399 | 13.3255 | 13.3896 | 0.15106 | 121.2891 | 9.0683 | 20.1096 | 121.3211 | 121.0831 | 121.2341 | 121.1334 | -121.4767 | -121.3394 | 121.2021 | 20.1599 | 0.20142 | 16.7542
1145.0938 | 121.3715 | -4.5868 | 116.803 | -0.012131 | 0.006319 | 0.057486 | 0.05451 | -5.5462e-05 | -0.0072802 | -0.0019546 | -0.0023192 | 0.0039457 | 0.12915 | -0.0054517 | 0.78843 | 0.10215 | -0.00084805 | 0.022888 | 116.9861 | -4.3167 | 116.7847 | -4.3442 | -4.4998 | -4.4998 | 57.2479 | 116.6885 | -4.4907 | 90.6143 | 116.835 | 88.9114 | 101.7563 | 0.27008 | 0.18311 | -0.018311 | 0.24261 | 0.086975 | 0.086975 | -0.18311 | -0.18311 | 0.09613 | -0.11444 | -26.1887 | 121.4218 | 106.3431 | 93.4982 | 106.2469 | 93.4021 | -0.027466 | 121.1014 | 121.3257 | 95.105 | 121.3028 | 121.1792 | 121.5729 | 121.2753 | -121.1197 | -121.2936 | 121.3715 | 95.2011 | 4.6097 | 61.8347
1146.8594 | 121.4355 | -5.5984 | 115.7455 | -0.0045011 | 0.0037556 | 0.056418 | 0.055365 | -0.00048286 | -0.0059986 | -0.0008866 | -0.005371 | 0.0013821 | 0.13663 | -0.0090833 | 0.99158 | 0.10813 | -0.0012753 | 0.027466 | 115.7089 | -5.5664 | 115.654 | -5.4428 | -5.5756 | -5.5756 | 53.0182 | 115.5396 | -5.5344 | 97.9752 | 115.6815 | 95.874 | 107.0618 | 0.032044 | -0.036621 | -0.091552 | 0.15564 | 0.022888 | 0.022888 | -0.009156 | -0.009156 | 0.064087 | -0.20599 | -17.7704 | 121.2799 | 112.6602 | 101.4725 | 112.5961 | 101.4084 | 0.1236 | 121.2204 | 121.2158 | 103.5095 | 121.2753 | 121.0739 | 121.3074 | 121.138 | -121.3119 | -121.2799 | 121.2524 | 103.5736 | 5.6259 | 58.6166
1148.5625 | 121.3028 | -4.9896 | 116.3589 | 0.0031279 | 0.0041828 | 0.055777 | 0.056219 | 0.0033623 | -0.0072802 | -0.001741 | -0.0023192 | 0.0015957 | 0.12894 | -0.0073743 | 1.1304 | 0.095528 | -0.0029843 | 0.23346 | 116.4368 | -4.747 | 116.1026 | -4.8843 | -4.9576 | -4.953 | 47.3785 | 116.0568 | -4.953 | 82.2098 | 116.3361 | 80.0903 | 84.4299 | 0.24261 | 0.07782 | -0.25635 | 0.10529 | 0.036621 | 0.032043 | -0.20599 | -0.21057 | 0.036621 | -0.30212 | -34.1492 | 121.3257 | 89.4196 | 85.08 | 89.3829 | 85.0433 | -0.13733 | 120.8496 | 121.2891 | 87.1628 | 121.1838 | 121.0098 | 121.4264 | 121.0464 | -121.106 | -121.312 | 121.0922 | 87.1994 | 5.2231 | 52.3682
1150.3125 | 121.3577 | -5.1132 | 116.0477 | -0.012131 | 0.0020466 | 0.05834 | 0.05216 | 0.0035761 | -0.0062122 | -0.001741 | -0.0084228 | 0.00074128 | 0.12979 | -0.0054517 | 1.4423 | 0.097664 | 0.0038515 | -0.25635 | 116.1255 | -4.9026 | 116.2354 | -4.7791 | -5.0537 | -5.0125 | 46.0373 | 115.8737 | -4.9942 | 85.4965 | 116.1438 | 83.4915 | 88.6505 | 0.21057 | 0.07782 | 0.18768 | 0.33417 | 0.10071 | 0.059509 | -0.10986 | -0.15106 | 0.11902 | -0.17395 | -30.5511 | 121.257 | 93.7637 | 88.6047 | 93.6447 | 88.4857 | 0.1236 | 121.138 | 121.138 | 90.4907 | 121.0281 | 120.8679 | 121.2387 | 120.9869 | -120.9503 | -121.0419 | 121.3486 | 90.6097 | 4.8569 | 51.1505
1152.0625 | 121.2341 | -5.2139 | 116.0248 | 0.0031279 | 0.00055118 | 0.054068 | 0.052801 | -0.0030463 | -0.0081348 | 0.001036 | -0.005371 | 0.0022367 | 0.1315 | -0.0013927 | 1.3853 | 0.095101 | 0.0042789 | -0.068665 | 115.9103 | -5.2505 | 115.8691 | -5.1041 | -5.3558 | -5.1682 | 47.8821 | 115.7135 | -5.2094 | 82.0816 | 116.0568 | 79.9438 | 85.1486 | -0.036621 | -0.11444 | -0.15564 | 0.10986 | 0.045776 | -0.14191 | 0.082397 | -0.10529 | 0.004577 | -0.31128 | -33.9432 | 121.2708 | 90.3625 | 85.1578 | 90.358 | 85.1532 | 0.14648 | 121.1197 | 121.2662 | 87.291 | 121.1609 | 120.9229 | 121.1243 | 120.9274 | -121.2753 | -121.2341 | 121.0831 | 87.2955 | 5.1453 | 53.096
1153.8281 | 121.2708 | -0.10986 | 121.0144 | 0.0031279 | -8.9824e-05 | 0.057913 | 0.054724 | -0.0017645 | -0.0066394 | -3.1996e-05 | -0.005371 | 0.0086453 | 0.00097835 | 0.01527 | 0.0037897 | 0.035073 | -0.0014891 | 0.27924 | 120.9824 | -0.13275 | 120.9961 | 0.07782 | -0.068665 | -0.027466 | 1.6205 | 120.8496 | -0.13275 | -0.2243 | 1.9913 | -0.52185 | 0.84228 | -0.022888 | -0.032043 | -0.01831 | 0.18768 | 0.082397 | 0.041198 | 0.10529 | 0.064086 | -0.022888 | -0.16479 | -121.2387 | 2.1011 | 0.95215 | -0.41199 | 0.97504 | -0.3891 | 0.21057 | 121.1288 | 2.124 | -0.091553 | 121.1151 | 120.9824 | 121.0922 | 120.9595 | -121.1472 | -121.1472 | 121.106 | -0.11444 | 0.3891 | 1.7303
1155.5156 | 121.106 | -7.8964 | 113.2004 | -0.0045011 | 0.0031146 | 0.054922 | 0.05451 | 0.00015814 | -0.0045032 | -0.0028092 | -0.0023192 | 2.9857 | 0.15628 | 0.01826 | 0.38788 | 0.095528 | -0.0029843 | -0.4303 | 112.8113 | -8.02 | 113.2416 | -7.5302 | -8.0063 | -7.9788 | 51.3748 | 112.8616 | -7.5989 | 112.2162 | 113.7726 | 78.1494 | 77.9709 | -0.1236 | -0.3891 | 0.041199 | 0.36621 | -0.082398 | -0.10986 | 0.041199 | 0.013733 | 0.29755 | -0.33875 | -0.98419 | 121.669 | 85.8673 | 86.0458 | 85.5698 | 85.7483 | 0.48981 | 121.2616 | 121.3715 | 119.8151 | 120.8313 | 120.4605 | 120.7077 | 120.7581 | -121.2204 | -120.7993 | 121.138 | 120.1126 | 7.4661 | 59.2712
1157.25 | 121.1929 | -3.0533 | 117.8833 | -0.0045011 | 0.001192 | 0.055136 | 0.05451 | -0.0026191 | -0.0064258 | -0.0028092 | -0.005371 | 1.9082 | 0.15372 | 0.0035205 | 0.086462 | 0.10642 | -0.0038389 | -0.073242 | 117.8925 | -3.0258 | 117.9337 | -2.9022 | -2.9388 | -2.948 | 63.4735 | 117.5308 | -3.0029 | 117.2241 | 117.952 | 92.6376 | 94.0063 | 0.027466 | 0.009155 | 0.050354 | 0.15106 | 0.10529 | 0.11444 | 0.07782 | 0.086975 | 0.050354 | -0.35248 | -0.65918 | 121.0052 | 97.0596 | 95.6909 | 97.0093 | 95.6406 | 0.1236 | 120.9595 | 120.9549 | 120.2271 | 120.9183 | 120.5338 | 120.9457 | 120.5841 | -120.9091 | -120.8862 | 120.9869 | 120.2774 | 2.98 | 66.5268
1159.0156 | 120.7352 | -13.5727 | 107.0389 | -0.012131 | -0.00073062 | 0.056631 | 0.053656 | 0.0035761 | -0.0072802 | -0.0002456 | -0.005371 | 7.0266 | 0.16013 | 0.010356 | 1.1174 | 0.0998 | -0.0010617 | -0.050354 | 106.929 | -13.6551 | 106.9199 | -13.7054 | -13.884 | -13.797 | 49.8322 | 106.1417 | -13.5956 | 104.8599 | 106.6177 | 77.71 | 93.7317 | -0.082397 | -0.10986 | -0.11902 | -0.13275 | -0.2243 | -0.31128 | -0.14191 | -0.22888 | -0.022888 | -0.89722 | -2.179 | 120.1904 | 107.3044 | 91.2827 | 107.3273 | 91.3055 | -0.050354 | 120.575 | 120.2133 | 118.4555 | 120.5841 | 119.7372 | 120.5017 | 119.7144 | -120.694 | -120.6345 | 120.4926 | 118.4326 | 13.5223 | 63.4048
1160.7812 | 120.845 | -9.1736 | 111.3373 | -0.012131 | 0.0020466 | 0.055991 | 0.054937 | 0.0012261 | -0.0089892 | -0.0011002 | -0.005371 | 5.6199 | 0.1644 | 0.014415 | 1.1095 | 0.1139 | -0.00042085 | 0.027466 | 111.1725 | -9.2972 | 111.2228 | -9.0866 | -9.1507 | -9.2743 | 67.6529 | 110.6094 | -9.1919 | 109.7122 | 111.4517 | 97.7097 | 103.2394 | -0.1236 | -0.1648 | -0.11444 | 0.086975 | -0.10071 | 0.022888 | 0.022888 | 0.14648 | -0.018311 | -0.72784 | -1.6251 | 120.6253 | 112.413 | 106.8832 | 112.4313 | 106.9016 | 0.21057 | 120.52 | 120.6436 | 118.9041 | 120.4697 | 119.8013 | 120.3461 | 119.783 | -120.6345 | -120.5292 | 120.3964 | 118.8858 | 9.2011 | 76.8265
1162.4688 | 120.5521 | -13.4949 | 106.8054 | -0.01976 | 0.00461 | 0.057272 | 0.053442 | -0.0028327 | -0.0079212 | -0.0008866 | -0.0023192 | 7.0266 | 0.16525 | 0.016979 | 0.16038 | 0.10429 | -0.0023435 | -0.091553 | 106.7001 | -13.6505 | 106.8375 | -13.6047 | -13.6322 | -13.6047 | 59.7244 | 105.6839 | -13.5498 | 103.6377 | 106.4346 | 83.3313 | 103.9078 | -0.15564 | -0.10529 | 0.032043 | -0.10986 | -0.10986 | -0.13733 | 0.045777 | 0.018311 | -0.054932 | -1.1215 | -3.1677 | 119.9295 | 117.4026 | 96.8262 | 117.4576 | 96.8811 | 0.045777 | 120.488 | 119.9844 | 117.1875 | 120.3506 | 119.2337 | 120.195 | 119.1788 | -120.4559 | -120.3552 | 120.3323 | 117.1326 | 13.4033 | 73.2193
1164.2188 | 121.0648 | -116.3818 | 4.6234 | -0.012131 | 0.002901 | 0.055991 | 0.057715 | 0.00037174 | -0.008562 | 0.0001816 | -0.0084228 | 0.2714 | 0.20029 | 0.015911 | 0.08988 | 0.11839 | 0.00064735 | -0.32501 | 4.5914 | -116.3635 | 4.4952 | -115.7135 | -116.4185 | -116.4505 | -23.8586 | 4.5776 | -116.4505 | 4.4586 | 4.5593 | -2.0325 | 4.5456 | 0.018311 | -0.032043 | -0.12817 | 0.66834 | -0.068664 | -0.036621 | -0.086975 | -0.054932 | -0.068664 | -0.045776 | -0.16479 | 120.9412 | 120.9274 | 114.3494 | 120.9961 | 114.418 | 0.65002 | 120.8588 | 121.0098 | 120.9091 | 120.9549 | 121.0281 | 120.9732 | 120.9595 | -120.9869 | -121.0739 | 120.8771 | 120.8405 | 116.0568 | 92.5232
1165.9688 | 121.2296 | -116.629 | 4.3991 | -0.0045011 | -0.0020124 | 0.055777 | 0.055365 | -0.0011237 | -0.0081348 | -0.000673 | -0.0084228 | 0.27268 | 0.20798 | 0.010356 | 0.087957 | 0.11774 | -0.00020725 | -0.19226 | 4.2892 | -116.6107 | 4.4128 | -115.8508 | -116.5649 | -116.6153 | -23.6481 | 4.3167 | -116.7023 | 4.3259 | 4.4815 | -2.9846 | 4.39 | 0.01831 | -0.10986 | 0.013733 | 0.7782 | 0.013733 | 0.064087 | -0.004577 | 0.045777 | -0.073243 | -0.082398 | -0.073242 | 121.1105 | 121.019 | 113.6444 | 121.0922 | 113.7177 | 0.75989 | 121.0236 | 121.1838 | 121.0281 | 120.9 | 121.019 | 120.9183 | 120.9457 | -121.0098 | -121.1014 | 121.0419 | 120.9549 | 116.4368 | 92.981
1167.6562 | 121.3074 | -116.5558 | 4.4495 | -0.012131 | 0.001192 | 0.056204 | 0.052801 | -0.0028327 | -0.0079212 | -0.00345 | -0.005371 | 0.27952 | 0.21097 | 0.010784 | 0.087743 | 0.11796 | 0.00064735 | -0.19226 | 4.3808 | -116.5558 | 4.454 | -115.8325 | -116.51 | -116.5695 | -21.9223 | 4.3808 | -116.6519 | 4.4495 | 4.6051 | -4.0009 | 4.5181 | 0 | -0.068665 | 0.004578 | 0.72327 | -0.013733 | 0.045776 | -0.013733 | 0.045776 | -0.096131 | -0.068665 | 0 | 121.1609 | 121.0739 | 112.5549 | 121.17 | 112.6511 | 0.72327 | 121.0098 | 121.257 | 121.1014 | 120.9366 | 121.0327 | 120.9366 | 120.9366 | -121.0052 | -121.1014 | 121.0098 | 121.0052 | 116.3635 | 94.6335
1169.4062 | 121.3165 | -116.1758 | 4.8386 | -0.012131 | 0.0016192 | 0.056631 | 0.055365 | -5.5462e-05 | -0.0079212 | 0.0018906 | -0.005371 | 0.29276 | 0.22678 | 0.0097157 | 0.090521 | 0.11774 | 0.00021995 | -0.17395 | 4.7836 | -116.153 | 4.8981 | -115.4572 | -116.1987 | -116.2125 | -20.929 | 4.7974 | -116.2628 | 4.8431 | 4.9713 | -4.5181 | 4.8981 | 0.022888 | -0.054932 | 0.059509 | 0.71869 | -0.036621 | -0.022888 | -0.059509 | -0.045776 | -0.086975 | -0.041199 | 0.004578 | 121.1472 | 121.0739 | 111.6577 | 121.1609 | 111.7447 | 0.6958 | 121.051 | 121.2341 | 121.106 | 120.9366 | 121.0602 | 120.9595 | 120.9732 | -120.9915 | -121.1014 | 121.0739 | 121.019 | 116.0019 | 95.2469
1171.1562 | 121.3531 | -116.4505 | 4.6097 | -0.012131 | 0.0022602 | 0.058768 | 0.058142 | -0.0034735 | -0.0047168 | -0.002382 | -0.005371 | 0.27162 | 0.2396 | 0.01057 | 0.12577 | 0.11668 | -0.0029843 | -0.16937 | 4.5319 | -116.4734 | 4.6188 | -115.7639 | -116.4642 | -116.4963 | -20.2927 | 4.5319 | -116.5466 | 4.5868 | 4.7058 | -5.2826 | 4.6463 | -0.022889 | -0.07782 | 0.009155 | 0.68664 | -0.045777 | -0.013733 | -0.022888 | 0.009156 | -0.096131 | -0.07782 | -0.022888 | 121.1563 | 121.0968 | 111.1679 | 121.1929 | 111.264 | 0.70953 | 121.0922 | 121.2524 | 121.1334 | 121.0052 | 121.0785 | 120.9824 | 120.9824 | -121.0831 | -121.1563 | 121.0693 | 121.0373 | 116.2811 | 96.1578
1172.9062 | 121.257 | -116.5375 | 4.5822 | -0.012131 | 0.0031146 | 0.057059 | 0.055578 | 0.0025079 | -0.0057848 | -0.0013138 | -0.005371 | 0.28977 | 0.24451 | 0.0077929 | 0.10676 | 0.11454 | -0.0040525 | -0.31128 | 4.4815 | -116.5192 | 4.5181 | -115.7684 | -116.5924 | -116.6382 | -8.0566 | 4.5364 | -116.597 | 4.4449 | 4.5822 | -6.134 | 4.509 | 0.018311 | -0.10071 | -0.064087 | 0.76904 | -0.10071 | -0.054931 | -0.11902 | -0.073242 | -0.059509 | -0.045776 | -0.13733 | 121.1197 | 121.0464 | 110.4034 | 121.106 | 110.463 | 0.75073 | 121.0373 | 121.1792 | 121.0419 | 121.0007 | 121.1334 | 121.019 | 121.0739 | -121.1014 | -121.1792 | 121.0556 | 120.9824 | 116.2262 | 108.4808
1174.6094 | 121.3165 | -107.0847 | 13.9938 | -0.0045011 | -0.0013714 | 0.054709 | 0.052374 | -0.0015509 | -0.0079212 | -0.0025956 | -0.005371 | 0.76594 | 0.82108 | 0.0073657 | 0.15268 | 0.081002 | -0.0031979 | 0.72327 | 14.2181 | -106.5948 | 14.8773 | -105.6976 | -106.4529 | -106.6544 | -40.892 | 14.2502 | -106.7734 | 14.0121 | 14.328 | -41.6245 | 13.9206 | 0.48981 | 0.2243 | 0.88348 | 1.387 | 0.4303 | 0.63171 | -0.059509 | 0.14191 | 0.31128 | 0.25635 | 0.018311 | 121.4127 | 121.0052 | 65.4602 | 120.694 | 65.1489 | 0.89722 | 121.4722 | 121.1014 | 120.7855 | 120.813 | 121.0236 | 121.3028 | 121.3348 | -120.5887 | -120.7672 | 121.962 | 121.0968 | 107.8079 | 66.1926
1176.375 | 121.1975 | -1.3733 | 119.9707 | -0.0045011 | 0.0020466 | 0.053854 | 0.050238 | -0.0032599 | -0.011125 | -0.0002456 | -0.0023192 | 0.028726 | 0.033449 | 0.0054431 | 0.013189 | 0.029518 | 0.0044925 | 0.20599 | 119.8013 | -1.3779 | 119.7464 | -1.236 | -1.3458 | -1.3367 | -0.72327 | -0.42114 | -1.3184 | -0.55389 | -1.2177 | -0.67291 | -0.46234 | -0.004578 | -0.16937 | -0.2243 | 0.13733 | 0.036621 | 0.027466 | 0.041199 | 0.032044 | 0.054932 | -120.3918 | -120.5246 | 0.15564 | 0.91095 | 0.70038 | 0.85602 | 0.64545 | 0.14191 | 121.1243 | 0.10071 | 0.76447 | 121.1792 | 0.89722 | 121.1746 | 0.95215 | -121.3486 | -121.2891 | 121.1197 | 0.8194 | 1.5793 | 0.65002
1178.0625 | 121.2433 | -1.1856 | 120.1263 | -0.012131 | 0.0020466 | 0.055991 | 0.053442 | -0.0021919 | -0.0057848 | -0.0025956 | -0.005371 | 0.030862 | 0.041353 | 0.010143 | 0.017889 | 0.028878 | 0.0012881 | 0.19226 | 120.0302 | -1.1856 | 119.9799 | -1.0345 | -1.181 | -1.1673 | -0.6546 | -0.48065 | -1.1444 | -0.55847 | -1.062 | -0.63629 | -0.46234 | 0 | -0.096131 | -0.14649 | 0.15106 | 0.018311 | 0.004578 | 0.018311 | 0.004578 | 0.041199 | -120.607 | -120.6848 | 0.1236 | 0.72327 | 0.54932 | 0.68207 | 0.50812 | 0.15106 | 121.1655 | 0.082397 | 0.58594 | 121.2158 | 0.66376 | 121.2158 | 0.70496 | -121.312 | -121.2708 | 121.1655 | 0.62714 | 1.3779 | 0.53101
1179.8125 | 121.2982 | -0.9201 | 120.4147 | -0.012131 | 0.0041828 | 0.056631 | 0.053228 | 0.0022943 | -0.0074938 | -0.0030228 | -0.0084228 | 0.027444 | 0.039003 | 0.010143 | 0.017248 | 0.026741 | -0.0017027 | 0.16937 | 120.3003 | -0.92468 | 120.282 | -0.74616 | -0.88806 | -0.8606 | -0.44403 | -0.44403 | -0.87433 | -0.48065 | -0.74158 | -0.43488 | -0.38452 | -0.004578 | -0.11444 | -0.13275 | 0.17395 | 0.059509 | 0.032043 | 0.064087 | 0.036621 | 0.045776 | -120.8588 | -120.8954 | 0.17853 | 0.53558 | 0.48523 | 0.48981 | 0.43945 | 0.17853 | 121.2067 | 0.13275 | 0.39368 | 121.225 | 0.4303 | 121.2204 | 0.47607 | -121.3394 | -121.2891 | 121.2021 | 0.43945 | 1.0895 | 0.47607
1181.5625 | 121.3806 | -1.03 | 120.2591 | 0.0031279 | 0.001192 | 0.054495 | 0.050024 | -0.0026191 | -0.0066394 | -0.002382 | -0.0023192 | 0.025735 | 0.038576 | 0.0097157 | 0.017034 | 0.028237 | 0.0012881 | 0.12817 | 120.1492 | -1.0437 | 120.2316 | -0.80109 | -0.92468 | -0.91095 | -0.45776 | -0.52185 | -0.99792 | -0.48065 | -0.79193 | -0.38452 | -0.40741 | -0.013733 | -0.10986 | -0.027466 | 0.22888 | 0.11902 | 0.10528 | 0.13275 | 0.11902 | 0.032043 | -120.7809 | -120.7397 | 0.23804 | 0.62256 | 0.64545 | 0.59051 | 0.6134 | 0.24262 | 121.2753 | 0.20599 | 0.51727 | 121.1929 | 0.47607 | 121.1792 | 0.50812 | -121.3028 | -121.257 | 121.2616 | 0.54932 | 1.1581 | 0.5722
1183.3125 | 121.3303 | -2.2156 | 119.0735 | -0.012131 | 0.0056782 | 0.056204 | 0.053015 | -0.0024055 | -0.006853 | -0.0021682 | -0.005371 | 0.02958 | 0.031954 | 0.01057 | 0.015752 | 0.031441 | 0.0023563 | 0.009155 | 119.0094 | -2.243 | 118.9224 | -2.124 | -2.2568 | -2.243 | -1.3641 | -1.2726 | -2.1744 | -1.3504 | -2.0874 | -1.3138 | -1.2497 | -0.027466 | -0.064087 | -0.15106 | 0.091553 | -0.027466 | -0.041199 | 0 | -0.013733 | 0.041199 | -120.3461 | -120.4239 | 0.12817 | 0.96588 | 0.90179 | 0.92468 | 0.86059 | 0.11902 | 121.1655 | 0.086975 | 0.82397 | 121.2524 | 0.90179 | 121.225 | 0.94299 | -121.3165 | -121.2479 | 121.138 | 0.86517 | 2.2247 | 0.85144
1185.0938 | 121.3394 | -1.2955 | 120.0394 | 0.0031279 | 0.0039692 | 0.057272 | 0.053442 | -0.0011237 | -0.0074938 | -0.0047318 | -0.0023192 | 0.030862 | 0.040285 | 0.012279 | 0.020025 | 0.025887 | -0.00084805 | 0.10529 | 119.9478 | -1.3184 | 119.9295 | -1.149 | -1.2589 | -1.2497 | -1.0712 | -1.0483 | -1.2543 | -1.0986 | -1.1307 | -1.0162 | -0.98877 | -0.022888 | -0.091553 | -0.10986 | 0.14648 | 0.045776 | 0.036621 | 0.068664 | 0.059509 | 0.041199 | -121.0876 | -121.138 | 0.1648 | 0.3067 | 0.27924 | 0.2655 | 0.23804 | 0.16937 | 121.2479 | 0.1236 | 0.15564 | 121.2662 | 0.20599 | 121.2433 | 0.24719 | -121.3577 | -121.2936 | 121.225 | 0.19684 | 1.4008 | 0.2243
1186.8438 | 121.3394 | -1.1398 | 120.2454 | -0.012131 | 0.0061054 | 0.0577 | 0.055578 | 0.0025079 | -0.0064258 | -0.0011002 | -0.005371 | 0.028726 | 0.046694 | 0.0065113 | 0.017248 | 0.025246 | 0.00021995 | 0.013733 | 120.1721 | -1.1261 | 120.0806 | -1.0117 | -1.1581 | -1.1215 | -1.0117 | -0.93384 | -1.0849 | -1.0117 | -0.98877 | -0.93842 | -0.90179 | 0.013733 | -0.073242 | -0.16479 | 0.12817 | 0.018311 | -0.01831 | 0.004578 | -0.032043 | 0.054932 | -121.1792 | -121.257 | 0.15106 | 0.23804 | 0.20142 | 0.18311 | 0.14648 | 0.11444 | 121.2067 | 0.09613 | 0.073242 | 121.2982 | 0.15106 | 121.312 | 0.20599 | -121.3715 | -121.3303 | 121.2204 | 0.12817 | 1.1536 | 0.12817
1188.5312 | 121.3028 | -1.0345 | 120.3964 | -0.012131 | 0.0048236 | 0.054495 | 0.055578 | 0.00079894 | -0.008562 | -0.0038772 | -0.0023192 | 0.029153 | 0.043917 | 0.0069385 | 0.016821 | 0.022896 | -0.0019163 | 0.050354 | 120.2866 | -0.99792 | 120.1813 | -0.92468 | -1.0666 | -1.0254 | -1.0117 | -0.85602 | -0.96588 | -0.98877 | -0.93842 | -0.94757 | -0.87891 | 0.036621 | -0.10986 | -0.21515 | 0.10986 | 0.009155 | -0.032043 | -0.027466 | -0.068664 | 0.068665 | -121.2524 | -121.3852 | 0.09613 | 0.15564 | 0.086975 | 0.086975 | 0.01831 | 0.073242 | 121.1792 | 0.027465 | -0.022889 | 121.2845 | 0.10986 | 121.3211 | 0.17853 | -121.3943 | -121.3623 | 121.2158 | 0.045776 | 1.0849 | 0.022888
1190.2969 | 121.344 | -0.97961 | 120.4376 | 0.010757 | 0.00461 | 0.056845 | 0.056006 | 0.0018671 | -0.006853 | -0.0011002 | 0.00073235 | 0.030008 | 0.045839 | 0.016124 | 0.016393 | 0.025887 | 0.00064735 | 0.009155 | 120.3506 | -0.97961 | 120.2362 | -0.88348 | -1.0117 | -0.98877 | -0.94299 | -0.81482 | -0.92926 | -0.93384 | -0.87433 | -0.87433 | -0.82855 | 0 | -0.086975 | -0.20142 | 0.09613 | -0.009156 | -0.032044 | -0.009156 | -0.032044 | 0.050354 | -121.2524 | -121.3715 | 0.10528 | 0.15106 | 0.10528 | 0.10071 | 0.054931 | 0.09613 | 121.2158 | 0.054931 | -0.004578 | 121.3303 | 0.11444 | 121.3303 | 0.1648 | -121.4172 | -121.3669 | 121.2158 | 0.045776 | 0.98877 | 0.036621
1192.0625 | 121.4905 | -0.92926 | 120.4102 | -0.012131 | 0.0052508 | 0.05535 | 0.055578 | 0.0035761 | -0.0079212 | -0.0032364 | -0.0023192 | 0.026803 | 0.044344 | 0.013774 | 0.018316 | 0.026314 | -0.0027707 | 0.050354 | 120.314 | -0.95215 | 120.369 | -0.73242 | -0.88806 | -0.84686 | -0.78735 | -0.8606 | -0.90179 | -0.80566 | -0.72327 | -0.74158 | -0.71411 | -0.022888 | -0.09613 | -0.041198 | 0.19684 | 0.082397 | 0.041198 | 0.10528 | 0.064086 | 0.027466 | -121.2708 | -121.2158 | 0.20599 | 0.21515 | 0.18768 | 0.18768 | 0.16022 | 0.21973 | 121.3211 | 0.17853 | 0.09613 | 121.2662 | 0.041198 | 121.2433 | 0.068664 | -121.3623 | -121.3119 | 121.2982 | 0.1236 | 0.97961 | 0.14191
1193.8438 | 121.431 | -0.97046 | 120.4285 | -0.012131 | 0.00097838 | 0.054495 | 0.05152 | -0.00069646 | -0.0059986 | -0.0053726 | -0.005371 | 0.027871 | 0.043062 | 0.0071521 | 0.016821 | 0.0261 | -0.0042661 | -0.004578 | 120.3186 | -0.96588 | 120.3003 | -0.79651 | -0.93384 | -0.89722 | -0.89264 | -0.87433 | -0.91095 | -0.89264 | -0.80566 | -0.79651 | -0.78735 | 0.004578 | -0.10986 | -0.12817 | 0.17395 | 0.073242 | 0.036621 | 0.068664 | 0.032043 | 0.059509 | -121.3028 | -121.3211 | 0.16479 | 0.1831 | 0.17395 | 0.1236 | 0.11444 | 0.16937 | 121.2662 | 0.10529 | 0.018311 | 121.2845 | 0.036621 | 121.2891 | 0.09613 | -121.3943 | -121.3394 | 121.2708 | 0.07782 | 0.96588 | 0.07782
1195.5312 | 121.4081 | -1.0117 | 120.4147 | -0.012131 | 0.0014056 | 0.057272 | 0.055792 | -0.00026906 | -0.008562 | -0.0038772 | -0.0023192 | 0.030008 | 0.044558 | 0.018047 | 0.017675 | 0.024819 | -0.0051205 | 0.10071 | 120.3323 | -1.0117 | 120.2774 | -0.85144 | -0.97046 | -0.95215 | -0.90637 | -0.88348 | -0.93842 | -0.93384 | -0.83771 | -0.8606 | -0.83771 | 0 | -0.082398 | -0.13733 | 0.16022 | 0.05951 | 0.041199 | 0.05951 | 0.041199 | 0.073242 | -121.2982 | -121.3486 | 0.17395 | 0.17395 | 0.15106 | 0.10071 | 0.07782 | 0.16022 | 121.2891 | 0.10071 | 0.004578 | 121.344 | 0.054932 | 121.344 | 0.12817 | -121.4264 | -121.3531 | 121.2891 | 0.07782 | 1.1124 | 0.10529
1197.2656 | 121.4081 | -1.0117 | 120.4102 | -0.0045011 | 0.0054644 | 0.057486 | 0.055151 | -0.0024055 | -0.0064258 | -0.0013138 | -0.005371 | 0.031503 | 0.043917 | 0.011424 | 0.018102 | 0.024605 | -0.0017027 | 0.004578 | 120.3506 | -1.0071 | 120.2454 | -0.89264 | -1.03 | -0.98877 | -0.93842 | -0.87891 | -0.94757 | -0.93384 | -0.87433 | -0.87433 | -0.83771 | 0.004578 | -0.059509 | -0.16479 | 0.11902 | 0.022888 | -0.01831 | 0.01831 | -0.022888 | 0.064087 | -121.2891 | -121.344 | 0.13733 | 0.17395 | 0.13733 | 0.10986 | 0.073242 | 0.11444 | 121.2524 | 0.073242 | 0.013733 | 121.3577 | 0.068665 | 121.3623 | 0.13275 | -121.4172 | -121.3577 | 121.257 | 0.07782 | 1.0162 | 0.073242
1198.9531 | 121.3943 | -1.0391 | 120.3964 | -0.01976 | 0.0022602 | 0.053214 | 0.052374 | 0.00037174 | -0.0066394 | 0.0006088 | -0.0084228 | 0.029367 | 0.043703 | 0.0073657 | 0.017461 | 0.023751 | -0.0010617 | 0.086975 | 120.3049 | -1.0208 | 120.2362 | -0.88806 | -0.99792 | -0.99335 | -0.97961 | -0.91553 | -0.98419 | -1.0162 | -0.90179 | -0.91553 | -0.90637 | 0.018311 | -0.091552 | -0.16022 | 0.15106 | 0.045777 | 0.041199 | 0.027466 | 0.022888 | 0.054932 | -121.3119 | -121.4127 | 0.13733 | 0.13275 | 0.1236 | 0.07782 | 0.068665 | 0.13275 | 121.257 | 0.082398 | -0.032043 | 121.3257 | 0.068665 | 121.344 | 0.1236 | -121.4172 | -121.3806 | 121.2753 | 0.022889 | 1.1261 | 0.05951
1200.7031 | 121.4767 | -1.0483 | 120.3461 | 0.0031279 | 0.001192 | 0.054495 | 0.053442 | -0.00069646 | -0.0062122 | -0.0038772 | -0.0023192 | 0.02958 | 0.045198 | 0.0084339 | 0.017461 | 0.026528 | -0.0021299 | -0.022888 | 120.282 | -1.0483 | 120.2545 | -0.86975 | -0.99335 | -0.96588 | -0.95673 | -0.9613 | -1.0071 | -0.97961 | -0.87891 | -0.86975 | -0.87433 | 0 | -0.064087 | -0.091552 | 0.17853 | 0.082398 | 0.054932 | 0.082398 | 0.054932 | 0.041199 | -121.3074 | -121.3257 | 0.16937 | 0.17395 | 0.17853 | 0.13275 | 0.13733 | 0.17853 | 121.3028 | 0.12817 | 0.027466 | 121.3303 | 0.045776 | 121.3303 | 0.086975 | -121.3943 | -121.3531 | 121.3028 | 0.068665 | 1.0254 | 0.091553
1202.4688 | 121.5454 | -1.2451 | 120.1263 | -0.012131 | -0.00051702 | 0.054282 | 0.053442 | 0.0022943 | -0.0066394 | -0.0011002 | -0.005371 | 0.02958 | 0.043489 | 0.012706 | 0.016607 | 0.024819 | -0.0034117 | 0.073242 | 120.0211 | -1.2497 | 120.1309 | -0.98419 | -1.1307 | -1.1307 | -1.0712 | -1.1948 | -1.1719 | -1.1444 | -1.0117 | -1.0162 | -1.0483 | -0.004578 | -0.10529 | 0.004577 | 0.26093 | 0.11444 | 0.11444 | 0.11902 | 0.11902 | 0.073242 | -121.3211 | -121.2708 | 0.23346 | 0.19684 | 0.22888 | 0.1236 | 0.15564 | 0.2655 | 121.3806 | 0.16022 | 0.027466 | 121.2708 | -0.022888 | 121.2662 | 0.050354 | -121.376 | -121.2982 | 121.376 | 0.10071 | 1.3184 | 0.17395
1204.1719 | 121.4493 | -1.6251 | 119.7968 | -0.0045011 | 0.006319 | 0.055563 | 0.055578 | 0.0018671 | -0.00963 | -0.0019546 | -0.005371 | 0.033639 | 0.042421 | 0.0099293 | 0.016821 | 0.023964 | -0.0038389 | 0.073242 | 119.7281 | -1.6342 | 119.6732 | -1.5015 | -1.5884 | -1.5884 | -1.5518 | -1.4832 | -1.5701 | -1.5564 | -1.4694 | -1.474 | -1.4465 | -0.009155 | -0.068665 | -0.1236 | 0.1236 | 0.036621 | 0.036621 | 0.045776 | 0.045776 | 0.054932 | -121.2799 | -121.3531 | 0.15564 | 0.17853 | 0.15106 | 0.1236 | 0.09613 | 0.13275 | 121.3074 | 0.10071 | 0.013733 | 121.3623 | 0.086975 | 121.3531 | 0.14191 | -121.431 | -121.3669 | 121.2982 | 0.068665 | 1.6983 | 0.073242
1205.9375 | 121.4905 | -1.7258 | 119.6365 | 0.0031279 | -8.9824e-05 | 0.055991 | 0.05451 | -0.00069646 | -0.0066394 | -0.0015274 | -0.005371 | 0.031503 | 0.042208 | -0.0016065 | 0.017248 | 0.026314 | -0.0031979 | -0.018311 | 119.5953 | -1.7029 | 119.577 | -1.5656 | -1.6983 | -1.6617 | -1.6663 | -1.6525 | -1.6983 | -1.6708 | -1.5793 | -1.5701 | -1.5701 | 0.022888 | -0.041199 | -0.05951 | 0.16022 | 0.064087 | 0.027466 | 0.041199 | 0.004578 | 0.027466 | -121.2891 | -121.3074 | 0.14648 | 0.15564 | 0.15564 | 0.12817 | 0.12817 | 0.13733 | 121.2799 | 0.11902 | 0.027466 | 121.2982 | 0.045776 | 121.3211 | 0.073242 | -121.3394 | -121.3348 | 121.3028 | 0.054932 | 1.7075 | 0.059509
1207.6406 | 121.5042 | -2.2385 | 119.1605 | -0.012131 | -8.9824e-05 | 0.054922 | 0.053228 | 0.0031487 | -0.0098438 | -0.0030228 | -0.0023192 | 0.033853 | 0.044558 | -0.00011113 | 0.013616 | 0.024391 | -0.0010617 | 0.07782 | 119.046 | -2.2202 | 119.1376 | -2.0142 | -2.1423 | -2.1332 | -2.0966 | -2.1698 | -2.1973 | -2.1469 | -2.0187 | -2.0325 | -2.0416 | 0.01831 | -0.11444 | -0.022888 | 0.2243 | 0.10528 | 0.09613 | 0.086975 | 0.07782 | 0.041198 | -121.3303 | -121.3074 | 0.21973 | 0.19684 | 0.20599 | 0.15564 | 0.16479 | 0.20599 | 121.3577 | 0.17853 | 0.050354 | 121.2662 | 0.027466 | 121.2845 | 0.068664 | -121.3806 | -121.3577 | 121.376 | 0.091552 | 2.3163 | 0.14191
1209.3906 | 121.4813 | -2.4216 | 119.0094 | -0.012131 | -8.9824e-05 | 0.053854 | 0.053228 | -0.0030463 | -0.0083484 | -0.0015274 | -0.005371 | 0.035348 | 0.044558 | -0.00096553 | 0.014684 | 0.024178 | -0.0034117 | 0.004578 | 118.8995 | -2.4033 | 118.9133 | -2.2522 | -2.3941 | -2.3392 | -2.3483 | -2.3071 | -2.3575 | -2.3621 | -2.2659 | -2.2842 | -2.2522 | 0.018311 | -0.10986 | -0.09613 | 0.16937 | 0.082398 | 0.027466 | 0.064087 | 0.009155 | 0.064087 | -121.3165 | -121.3715 | 0.15564 | 0.16937 | 0.13733 | 0.10529 | 0.073242 | 0.15106 | 121.3165 | 0.091553 | -0.004578 | 121.3028 | 0.050354 | 121.3211 | 0.11444 | -121.4127 | -121.3669 | 121.3348 | 0.059509 | 2.4261 | 0.073242
1211.1562 | 121.5637 | -2.6184 | 118.7851 | -0.0045011 | 0.00097838 | 0.054709 | 0.051306 | -0.0039007 | -0.011553 | -0.0015274 | -0.0084228 | 0.037271 | 0.043062 | 0.0090747 | 0.015539 | 0.022469 | -0.0049069 | 0.041199 | 118.6844 | -2.6001 | 118.7668 | -2.3849 | -2.5085 | -2.4857 | -2.4445 | -2.5223 | -2.5635 | -2.4902 | -2.3849 | -2.3895 | -2.4078 | 0.01831 | -0.10071 | -0.01831 | 0.23346 | 0.13275 | 0.10986 | 0.11444 | 0.091553 | 0.054931 | -121.3074 | -121.2753 | 0.23346 | 0.21057 | 0.22888 | 0.15564 | 0.17395 | 0.21515 | 121.3669 | 0.17853 | 0.073243 | 121.2845 | 0.041199 | 121.3028 | 0.09613 | -121.3852 | -121.3486 | 121.3852 | 0.12817 | 2.6596 | 0.17395
1212.9062 | 121.5179 | -2.6276 | 118.7759 | -0.0045011 | 0.002901 | 0.055991 | 0.053656 | -0.0034735 | -0.0070666 | 0.001036 | -0.005371 | 0.037698 | 0.041353 | 0.01057 | 0.016821 | 0.024391 | -0.0017027 | -0.027466 | 118.7302 | -2.6184 | 118.6798 | -2.4719 | -2.6047 | -2.5681 | -2.5589 | -2.5452 | -2.5726 | -2.5726 | -2.4719 | -2.4719 | -2.4673 | 0.009155 | -0.045776 | -0.09613 | 0.15564 | 0.059509 | 0.022888 | 0.050354 | 0.013733 | 0.054931 | -121.3211 | -121.3486 | 0.15564 | 0.16022 | 0.15564 | 0.10529 | 0.10071 | 0.14648 | 121.2982 | 0.10071 | 0 | 121.3486 | 0.027466 | 121.3577 | 0.082397 | -121.3943 | -121.3486 | 121.3074 | 0.054931 | 2.6001 | 0.068664
1214.6562 | 121.5088 | -2.6184 | 118.7851 | -0.012131 | 0.00055118 | 0.056418 | 0.054297 | -0.0021919 | -0.0092028 | -0.001741 | -0.005371 | 0.035348 | 0.042421 | 0.0054431 | 0.01853 | 0.022683 | -0.0014891 | -0.022888 | 118.6798 | -2.623 | 118.6935 | -2.4628 | -2.6047 | -2.5726 | -2.5589 | -2.5314 | -2.5909 | -2.5681 | -2.4582 | -2.4673 | -2.4673 | -0.004578 | -0.10528 | -0.091553 | 0.15564 | 0.045776 | 0.013733 | 0.050354 | 0.018311 | 0.027466 | -121.3165 | -121.3531 | 0.16022 | 0.15106 | 0.15106 | 0.1236 | 0.1236 | 0.16022 | 121.3165 | 0.13275 | 0.022888 | 121.3028 | 0.059509 | 121.2982 | 0.086975 | -121.4081 | -121.376 | 121.3119 | 0.050354 | 2.5955 | 0.059509
1216.3438 | 121.5591 | -2.6825 | 118.7302 | -0.012131 | 0.0014056 | 0.05535 | 0.054083 | -0.0026191 | -0.010698 | -0.0004592 | -0.0023192 | 0.037057 | 0.043062 | 0.00031607 | 0.014898 | 0.024178 | -0.0017027 | 0.032043 | 118.6386 | -2.6688 | 118.689 | -2.4765 | -2.6047 | -2.5955 | -2.5497 | -2.6138 | -2.6367 | -2.5909 | -2.4765 | -2.4582 | -2.4948 | 0.013733 | -0.091553 | -0.041199 | 0.20599 | 0.086975 | 0.07782 | 0.073242 | 0.064087 | 0.045776 | -121.344 | -121.3211 | 0.20599 | 0.18768 | 0.2243 | 0.14191 | 0.17853 | 0.19226 | 121.3577 | 0.16022 | 0.045777 | 121.3074 | 0.022888 | 121.3211 | 0.068664 | -121.3989 | -121.3669 | 121.3715 | 0.091553 | 2.7145 | 0.13275
1218.0938 | 121.4539 | -2.6733 | 118.7897 | -0.0045011 | 0.0054644 | 0.0577 | 0.055365 | 0.0012261 | -0.0077074 | -0.0045182 | -0.0084228 | 0.03898 | 0.04413 | 0.0077929 | 0.013403 | 0.022469 | -0.0053343 | 0.091553 | 118.7347 | -2.6505 | 118.7119 | -2.4857 | -2.6321 | -2.6184 | -2.5726 | -2.536 | -2.6001 | -2.5955 | -2.5131 | -2.5497 | -2.5223 | 0.022888 | -0.054932 | -0.07782 | 0.18768 | 0.054932 | 0.041199 | 0.032044 | 0.018311 | 0.073242 | -121.3257 | -121.3852 | 0.16022 | 0.15106 | 0.1236 | 0.07782 | 0.050354 | 0.1648 | 121.3623 | 0.086975 | 0.004578 | 121.3852 | 0.064087 | 121.4081 | 0.13733 | -121.4401 | -121.3898 | 121.3852 | 0.07782 | 2.7649 | 0.10071
1219.8594 | 121.4447 | -2.6413 | 118.8309 | -0.012131 | 0.001833 | 0.053854 | 0.054083 | -0.0019781 | -0.0083484 | -0.0015274 | -0.005371 | 0.038339 | 0.044771 | 0.0050159 | 0.01618 | 0.024819 | -0.0044797 | 0.07782 | 118.7347 | -2.6184 | 118.7164 | -2.4582 | -2.5864 | -2.5772 | -2.5772 | -2.4902 | -2.5864 | -2.6047 | -2.5177 | -2.5177 | -2.5269 | 0.022888 | -0.096131 | -0.11444 | 0.18311 | 0.064087 | 0.054931 | 0.041199 | 0.032043 | 0.054931 | -121.3211 | -121.4355 | 0.1236 | 0.11444 | 0.1236 | 0.05951 | 0.068665 | 0.16022 | 121.3348 | 0.068665 | -0.01831 | 121.3531 | 0.096131 | 121.376 | 0.15106 | -121.4493 | -121.4172 | 121.3577 | 0.036621 | 2.7191 | 0.064087
1221.5625 | 121.431 | -2.742 | 118.7485 | -0.012131 | 0.0056782 | 0.057913 | 0.05686 | -0.00048286 | -0.0064258 | -0.0043046 | -0.005371 | 0.035989 | 0.042421 | 0.011638 | 0.020666 | 0.02546 | -0.0055479 | 0.009155 | 118.7302 | -2.71 | 118.5745 | -2.6413 | -2.7695 | -2.7237 | -2.71 | -2.5589 | -2.6825 | -2.6962 | -2.6459 | -2.6413 | -2.5909 | 0.032043 | -0.01831 | -0.17395 | 0.10071 | 0.01831 | -0.027466 | -0.013733 | -0.059509 | 0.059509 | -121.3074 | -121.4447 | 0.09613 | 0.15106 | 0.10071 | 0.091553 | 0.041199 | 0.068665 | 121.2845 | 0.036621 | -0.013733 | 121.4401 | 0.1236 | 121.4722 | 0.18311 | -121.4584 | -121.431 | 121.3165 | 0.045776 | 2.7512 | 0.032043
1223.3281 | 121.4813 | -2.7969 | 118.7027 | -0.012131 | 0.00055118 | 0.056204 | 0.054083 | 0.0033623 | -0.0087756 | -0.0021682 | -0.005371 | 0.035134 | 0.042208 | 0.013774 | 0.021093 | 0.023964 | -0.0038389 | 0.045776 | 118.6386 | -2.8061 | 118.5287 | -2.6733 | -2.7924 | -2.7832 | -2.7786 | -2.6413 | -2.7466 | -2.7557 | -2.6459 | -2.6642 | -2.6459 | -0.009155 | -0.064087 | -0.17395 | 0.1236 | 0.013733 | 0.004578 | 0.022888 | 0.013733 | 0.050354 | -121.344 | -121.4584 | 0.15106 | 0.15106 | 0.13275 | 0.10071 | 0.082397 | 0.13275 | 121.3348 | 0.10071 | -0.009155 | 121.4447 | 0.10529 | 121.4355 | 0.15564 | -121.5088 | -121.4493 | 121.3257 | 0.041199 | 2.8427 | 0.018311
1225.0938 | 121.5775 | -3.2455 | 118.1992 | -0.012131 | 0.0048236 | 0.055563 | 0.05451 | 0.0016535 | -0.005144 | -0.0019546 | -0.0023192 | 0.025949 | 0.042635 | 0.01826 | 0.01917 | 0.026955 | -0.0064023 | 0.009155 | 118.158 | -3.2455 | 118.1122 | -3.0762 | -3.2181 | -3.1952 | -3.1265 | -3.1586 | -3.1998 | -3.1265 | -3.035 | -3.0624 | -3.035 | 0 | -0.041199 | -0.086975 | 0.16937 | 0.050354 | 0.027465 | 0.050354 | 0.027465 | 0.045776 | -121.3577 | -121.3257 | 0.21057 | 0.21057 | 0.18311 | 0.1648 | 0.13733 | 0.16937 | 121.3577 | 0.1648 | 0.073242 | 121.4035 | 0.041199 | 121.4035 | 0.086975 | -121.4447 | -121.3989 | 121.3577 | 0.11902 | 3.2547 | 0.11902
1226.8438 | 121.4859 | -3.6987 | 117.8192 | 0.0031279 | 0.00076478 | 0.054495 | 0.054724 | -0.0056097 | -0.008562 | -0.0015274 | -0.005371 | 0.025308 | 0.046053 | 0.015697 | 0.017889 | 0.026314 | -0.0068295 | 0.018311 | 117.7734 | -3.6987 | 117.6315 | -3.5522 | -3.6942 | -3.6713 | -3.6758 | -3.5248 | -3.6255 | -3.685 | -3.5568 | -3.5751 | -3.5477 | 0 | -0.045777 | -0.18768 | 0.14648 | 0.027465 | 0.004577 | 0.027465 | 0.004577 | 0.073242 | -121.344 | -121.5042 | 0.14191 | 0.15106 | 0.1236 | 0.07782 | 0.050354 | 0.14648 | 121.3303 | 0.068664 | -0.05951 | 121.4722 | 0.10071 | 121.4722 | 0.17395 | -121.5179 | -121.4447 | 121.3303 | 0.013732 | 3.717 | 0.022888
1228.5469 | 121.4813 | -3.6713 | 117.8284 | -0.012131 | 0.0016192 | 0.054709 | 0.053228 | -0.0015509 | -0.0092028 | 0.0008224 | -0.005371 | 0.023599 | 0.043062 | 0.013561 | 0.01853 | 0.026314 | -0.00084805 | 0.032043 | 117.7734 | -3.6575 | 117.6682 | -3.5522 | -3.6575 | -3.6575 | -3.6621 | -3.4836 | -3.6209 | -3.6346 | -3.511 | -3.5522 | -3.5202 | 0.013733 | -0.054932 | -0.16022 | 0.11902 | 0.013733 | 0.013733 | 0 | 0 | 0.050354 | -121.312 | -121.463 | 0.16022 | 0.15106 | 0.11902 | 0.10071 | 0.068665 | 0.10529 | 121.3257 | 0.10986 | -0.013733 | 121.431 | 0.13733 | 121.4447 | 0.18768 | -121.4859 | -121.4493 | 121.3394 | 0.036621 | 3.7033 | 0.009156
1230.3125 | 121.5225 | -3.6987 | 117.8192 | -0.0045011 | 0.0033282 | 0.05535 | 0.056219 | 0.0040033 | -0.008562 | -0.0013138 | -0.0084228 | 0.020181 | 0.044344 | 0.016124 | 0.017248 | 0.025032 | -0.0070433 | 0.091553 | 117.7185 | -3.6758 | 117.6773 | -3.5385 | -3.6758 | -3.6621 | -3.6163 | -3.5477 | -3.6575 | -3.6392 | -3.5065 | -3.5614 | -3.5294 | 0.022888 | -0.10071 | -0.14191 | 0.16022 | 0.036621 | 0.022888 | 0.013733 | 0 | 0.041198 | -121.3669 | -121.4584 | 0.19226 | 0.16937 | 0.13733 | 0.12817 | 0.096131 | 0.13733 | 121.3531 | 0.15106 | 0.018311 | 121.3943 | 0.10986 | 121.4172 | 0.15106 | -121.4951 | -121.4767 | 121.376 | 0.059509 | 3.7903 | 0.082397
1232.0781 | 121.5134 | -3.6804 | 117.8238 | -0.01976 | 0.0043964 | 0.055563 | 0.054937 | -0.0026191 | -0.005144 | -0.00345 | -0.005371 | 0.022958 | 0.043276 | 0.018474 | 0.018743 | 0.027382 | -0.0036253 | 0.068665 | 117.746 | -3.6804 | 117.691 | -3.5477 | -3.6621 | -3.6667 | -3.6392 | -3.4836 | -3.6118 | -3.6392 | -3.4927 | -3.5385 | -3.5019 | 0 | -0.07782 | -0.13275 | 0.13275 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | 0.068665 | -121.3074 | -121.463 | 0.18768 | 0.17853 | 0.14191 | 0.10986 | 0.073242 | 0.13275 | 121.3715 | 0.11902 | -0.027466 | 121.4264 | 0.12817 | 121.4264 | 0.19684 | -121.5042 | -121.4355 | 121.3715 | 0.041199 | 3.7491 | 0.041199
1233.8438 | 121.5546 | -3.0487 | 118.3731 | -0.0045011 | 0.0033282 | 0.055991 | 0.053656 | 0.0027215 | -0.0074938 | -0.0021682 | -0.005371 | 0.019326 | 0.044771 | 0.01826 | 0.016393 | 0.026528 | 6.346e-06 | 0 | 118.2999 | -3.035 | 118.3319 | -2.8244 | -3.0121 | -2.9663 | -2.9526 | -2.9617 | -2.9984 | -2.9709 | -2.8702 | -2.8839 | -2.8793 | 0.013733 | -0.073242 | -0.041199 | 0.2243 | 0.082397 | 0.036621 | 0.068664 | 0.022888 | 0.050354 | -121.3348 | -121.344 | 0.17853 | 0.16937 | 0.1648 | 0.11902 | 0.11444 | 0.21057 | 121.3669 | 0.12817 | 0.027466 | 121.3348 | 0.036621 | 121.3486 | 0.086975 | -121.4081 | -121.3715 | 121.3806 | 0.07782 | 3.0487 | 0.09613
1235.5312 | 121.4676 | -2.9572 | 118.5471 | -0.01976 | 0.0022602 | 0.055991 | 0.051733 | 0.0018671 | -0.008562 | -0.0021682 | -0.0023192 | 0.021249 | 0.043917 | 0.013774 | 0.017248 | 0.023537 | 0.0010745 | 0.036621 | 118.4647 | -2.9434 | 118.3868 | -2.8198 | -2.9388 | -2.9388 | -2.9251 | -2.7969 | -2.9022 | -2.948 | -2.8152 | -2.8427 | -2.8244 | 0.013733 | -0.082397 | -0.16022 | 0.13733 | 0.01831 | 0.01831 | 0.004577 | 0.004577 | 0.054931 | -121.344 | -121.4951 | 0.14191 | 0.13275 | 0.11444 | 0.07782 | 0.05951 | 0.1236 | 121.3303 | 0.086975 | -0.045776 | 121.4081 | 0.10529 | 121.4218 | 0.16022 | -121.4905 | -121.4493 | 121.344 | 0.009155 | 2.9938 | 0.032043
1237.2812 | 121.6049 | -2.9617 | 118.4601 | -0.0045011 | 0.0052508 | 0.057272 | 0.053869 | 0.0052851 | -0.0064258 | -0.0030228 | -0.0023192 | 0.02189 | 0.043703 | 0.01292 | 0.017675 | 0.026314 | -0.0023435 | 0.050354 | 118.3868 | -2.9526 | 118.4555 | -2.742 | -2.9205 | -2.8748 | -2.829 | -2.8885 | -2.9388 | -2.8519 | -2.7603 | -2.7649 | -2.7603 | 0.009155 | -0.073242 | -0.004578 | 0.21973 | 0.086975 | 0.041199 | 0.07782 | 0.032044 | 0.022888 | -121.3486 | -121.312 | 0.20142 | 0.20142 | 0.19684 | 0.17853 | 0.17395 | 0.21057 | 121.4081 | 0.17853 | 0.086975 | 121.3394 | 0.050354 | 121.3486 | 0.073242 | -121.4127 | -121.3989 | 121.4172 | 0.10986 | 3.0121 | 0.13275
1239.0312 | 121.4859 | -3.2547 | 118.2816 | -0.0045011 | 0.0016192 | 0.053854 | 0.053656 | 0.00058534 | -0.0094164 | 0.0003952 | -0.0084228 | 0.019113 | 0.043062 | 0.021251 | 0.01618 | 0.023964 | -0.0012753 | 0.022888 | 118.19 | -3.2272 | 118.0939 | -3.1403 | -3.2455 | -3.2272 | -3.2227 | -3.0853 | -3.1952 | -3.2501 | -3.1219 | -3.1357 | -3.1219 | 0.027466 | -0.091553 | -0.18768 | 0.11444 | 0.027466 | 0.009156 | 0 | -0.01831 | 0.05951 | -121.3669 | -121.5317 | 0.13275 | 0.13275 | 0.11902 | 0.073242 | 0.059509 | 0.086975 | 121.3211 | 0.073242 | -0.054932 | 121.4172 | 0.10986 | 121.4447 | 0.16937 | -121.5088 | -121.4767 | 121.3486 | 0.004578 | 3.2776 | 0.032044
1240.7344 | 121.5454 | -3.3417 | 118.1717 | -0.0045011 | 0.00012398 | 0.056631 | 0.051947 | -0.0026191 | -0.010698 | -0.001741 | -0.005371 | 0.021463 | 0.041567 | 0.020397 | 0.015539 | 0.024178 | -0.0012753 | 0.086975 | 118.0527 | -3.3051 | 118.0984 | -3.1036 | -3.241 | -3.2227 | -3.2272 | -3.2043 | -3.2684 | -3.2639 | -3.1403 | -3.1586 | -3.154 | 0.036621 | -0.11902 | -0.073242 | 0.23804 | 0.11902 | 0.10071 | 0.082398 | 0.064087 | 0.073242 | -121.376 | -121.4355 | 0.20142 | 0.18768 | 0.18311 | 0.11444 | 0.10986 | 0.20142 | 121.4035 | 0.12817 | 0.004578 | 121.3577 | 0.064087 | 121.3943 | 0.13733 | -121.4767 | -121.4401 | 121.4401 | 0.07782 | 3.4286 | 0.11444
1242.4844 | 121.637 | -3.0487 | 118.3777 | -0.0045011 | 0.001833 | 0.054068 | 0.054297 | -0.0021919 | -0.0055712 | -0.0013138 | -0.0084228 | 0.021463 | 0.042208 | 0.020824 | 0.014898 | 0.025246 | -0.0019163 | 0.041199 | 118.2861 | -3.067 | 118.3502 | -2.8473 | -2.9938 | -2.9755 | -2.9068 | -2.9709 | -3.035 | -2.9297 | -2.7969 | -2.8107 | -2.829 | -0.018311 | -0.091553 | -0.027466 | 0.20142 | 0.073242 | 0.054932 | 0.091553 | 0.073243 | 0.013733 | -121.3486 | -121.3074 | 0.25177 | 0.21973 | 0.23804 | 0.20599 | 0.2243 | 0.21973 | 121.4172 | 0.23804 | 0.10529 | 121.3531 | 0.064087 | 121.3348 | 0.07782 | -121.4447 | -121.4127 | 121.3989 | 0.11902 | 3.0899 | 0.14191
1244.25 | 121.6049 | -2.9068 | 118.5562 | -0.0045011 | 0.0039692 | 0.055991 | 0.057074 | -0.00069646 | -0.0083484 | -0.0008866 | -0.005371 | 0.023172 | 0.042208 | 0.026805 | 0.017889 | 0.026741 | -0.0046933 | -0.004578 | 118.5379 | -2.9434 | 118.4601 | -2.7832 | -2.9205 | -2.8976 | -2.7878 | -2.7786 | -2.8839 | -2.7695 | -2.6779 | -2.7054 | -2.6596 | -0.036621 | -0.01831 | -0.09613 | 0.1236 | 0.009155 | -0.013733 | 0.045776 | 0.022888 | 0.022888 | -121.3348 | -121.3257 | 0.22888 | 0.24719 | 0.20142 | 0.2243 | 0.17853 | 0.16022 | 121.4035 | 0.20599 | 0.11444 | 121.4813 | 0.10529 | 121.4447 | 0.12817 | -121.4996 | -121.4401 | 121.3669 | 0.13733 | 2.9022 | 0.11902
1246.0156 | 121.6095 | -2.9572 | 118.4875 | -0.012131 | -0.0020124 | 0.056631 | 0.050238 | -5.5462e-05 | -0.0094164 | -0.0002456 | -0.005371 | 0.021035 | 0.041994 | 0.014842 | 0.017461 | 0.024819 | -0.0036253 | 0.064087 | 118.4189 | -2.9526 | 118.4967 | -2.7237 | -2.8519 | -2.8564 | -2.7603 | -2.8244 | -2.916 | -2.7924 | -2.6596 | -2.6733 | -2.6871 | 0.004577 | -0.068665 | 0.009155 | 0.23346 | 0.10071 | 0.10528 | 0.096131 | 0.10071 | 0.041198 | -121.312 | -121.2799 | 0.29755 | 0.27008 | 0.28381 | 0.22888 | 0.24261 | 0.22888 | 121.4493 | 0.25635 | 0.1236 | 121.3715 | 0.091553 | 121.376 | 0.13275 | -121.4401 | -121.4035 | 121.4539 | 0.16479 | 3.0212 | 0.19684
1247.7031 | 121.5134 | -3.0853 | 118.4372 | -0.01976 | 0.0020466 | 0.054709 | 0.054937 | -0.0028327 | -0.008562 | -0.0013138 | -0.0084228 | 0.023599 | 0.04178 | 0.024883 | 0.018102 | 0.023323 | -0.0017027 | 0.045776 | 118.364 | -3.0762 | 118.2724 | -2.9846 | -3.0945 | -3.0899 | -3.0167 | -2.8473 | -3.0533 | -2.9709 | -2.8519 | -2.8885 | -2.8427 | 0.009155 | -0.073242 | -0.16479 | 0.10071 | -0.004578 | -0.009155 | -0.013733 | -0.01831 | 0.032043 | -121.2845 | -121.4081 | 0.23346 | 0.24261 | 0.19684 | 0.21057 | 0.1648 | 0.091553 | 121.3486 | 0.20142 | 0.082398 | 121.4401 | 0.20599 | 121.4493 | 0.23804 | -121.5134 | -121.4905 | 121.3577 | 0.11444 | 3.1311 | 0.068664
1249.4531 | 121.4996 | -3.241 | 118.3044 | -0.012131 | 0.00461 | 0.057486 | 0.056433 | -0.00026906 | -0.0055712 | -0.0002456 | 0.00073235 | 0.023385 | 0.039858 | 0.019969 | 0.020452 | 0.028023 | -0.0027707 | -0.004578 | 118.2587 | -3.2227 | 118.0847 | -3.154 | -3.2822 | -3.2501 | -2.9892 | -2.7695 | -3.186 | -2.8885 | -2.8198 | -2.8381 | -2.7832 | 0.018311 | -0.045776 | -0.21973 | 0.086975 | -0.009155 | -0.041199 | -0.027466 | -0.05951 | 0.054932 | -121.0739 | -121.1929 | 0.42114 | 0.45776 | 0.40283 | 0.40283 | 0.3479 | 0.068664 | 121.3074 | 0.36621 | 0.29755 | 121.4813 | 0.41656 | 121.4996 | 0.4715 | -121.5271 | -121.4905 | 121.3257 | 0.35248 | 3.2364 | 0.25177
1251.2344 | 121.5546 | -3.4058 | 118.1259 | -0.01976 | 0.0050372 | 0.056845 | 0.053442 | 0.0025079 | -0.0062122 | -0.0013138 | 0.00073235 | 0.027017 | 0.034945 | 0.012279 | 0.017889 | 0.027596 | 0.00043375 | 0.082397 | 118.0573 | -3.4058 | 118.0023 | -3.2364 | -3.392 | -3.3783 | -2.774 | -2.7008 | -3.36 | -2.7603 | -2.6871 | -2.71 | -2.6733 | 0 | -0.068665 | -0.1236 | 0.16937 | 0.027466 | 0.013733 | 0.027466 | 0.013733 | 0.045777 | -120.8267 | -120.8862 | 0.71869 | 0.73242 | 0.6958 | 0.68664 | 0.65002 | 0.16937 | 121.4081 | 0.67291 | 0.59967 | 121.463 | 0.65918 | 121.463 | 0.70496 | -121.5317 | -121.4859 | 121.4081 | 0.64545 | 3.4882 | 0.63171
1252.9844 | 121.637 | -3.3508 | 118.1213 | -0.01976 | 0.00461 | 0.056845 | 0.053869 | 0.00037174 | -0.0047168 | -0.0008866 | -0.005371 | 0.032357 | 0.039003 | 0.0052295 | 0.020025 | 0.026955 | 0.00021995 | 0.022888 | 118.0756 | -3.3463 | 118.0756 | -3.1769 | -3.3096 | -3.2822 | -2.9755 | -2.98 | -3.2959 | -2.9617 | -2.8748 | -2.8748 | -2.8564 | 0.004578 | -0.045776 | -0.045776 | 0.17395 | 0.068664 | 0.041199 | 0.064086 | 0.036621 | 0.054932 | -121.1014 | -121.0831 | 0.47607 | 0.49439 | 0.47607 | 0.43945 | 0.42114 | 0.16937 | 121.4218 | 0.42114 | 0.33417 | 121.4218 | 0.31586 | 121.4264 | 0.37079 | -121.4676 | -121.4172 | 121.4264 | 0.3891 | 3.3737 | 0.37537
1254.6875 | 121.6415 | -3.2135 | 118.277 | -0.012131 | 0.0033282 | 0.056845 | 0.053656 | -0.0019781 | -0.0062122 | 0.0008224 | -0.0023192 | 0.034921 | 0.043489 | 0.0067249 | 0.017889 | 0.027809 | 0.00043375 | 0.009155 | 118.2175 | -3.2318 | 118.1671 | -3.0624 | -3.2135 | -3.186 | -2.9114 | -2.9205 | -3.186 | -2.916 | -2.8152 | -2.8244 | -2.8152 | -0.018311 | -0.05951 | -0.10986 | 0.15106 | 0.027466 | 0 | 0.045777 | 0.018311 | 0.027466 | -121.1975 | -121.1929 | 0.39825 | 0.39825 | 0.3891 | 0.37079 | 0.36163 | 0.16937 | 121.3989 | 0.37079 | 0.27008 | 121.4493 | 0.2655 | 121.431 | 0.29297 | -121.5088 | -121.463 | 121.3806 | 0.29755 | 3.2227 | 0.30212
1256.4531 | 121.5408 | -3.0121 | 118.5471 | -0.01976 | 0.0039692 | 0.056845 | 0.054083 | 0.0016535 | -0.0062122 | -0.0004592 | -0.005371 | 0.038552 | 0.04114 | 0.0018115 | 0.01917 | 0.023323 | -0.00063445 | -0.013733 | 118.5013 | -2.98 | 118.3777 | -2.8885 | -3.0258 | -3.0075 | -2.8381 | -2.7466 | -2.9343 | -2.8336 | -2.7512 | -2.774 | -2.7374 | 0.032043 | -0.045776 | -0.16937 | 0.1236 | 0.004578 | -0.013733 | -0.027465 | -0.045776 | 0.07782 | -121.2936 | -121.3806 | 0.26092 | 0.27466 | 0.23804 | 0.19684 | 0.16022 | 0.091553 | 121.3577 | 0.1831 | 0.10071 | 121.4813 | 0.18768 | 121.5134 | 0.2655 | -121.5271 | -121.4813 | 121.3898 | 0.17853 | 2.9984 | 0.17395
1258.2031 | 121.55 | -2.9022 | 118.6752 | -0.012131 | 0.00055118 | 0.054068 | 0.05451 | -0.00091006 | -0.0094164 | -0.0025956 | -0.005371 | 0.040902 | 0.044558 | -0.00011113 | 0.018743 | 0.02546 | -0.0057615 | 0.045776 | 118.5654 | -2.8885 | 118.4601 | -2.8015 | -2.9114 | -2.9068 | -2.8473 | -2.7283 | -2.8519 | -2.8656 | -2.7374 | -2.742 | -2.7512 | 0.013733 | -0.10986 | -0.21515 | 0.10071 | -0.004577 | -0.009155 | -0.01831 | -0.022888 | 0.050354 | -121.4035 | -121.5408 | 0.1648 | 0.15106 | 0.16022 | 0.10071 | 0.10986 | 0.086975 | 121.3486 | 0.11444 | -0.013733 | 121.4539 | 0.1236 | 121.4676 | 0.17395 | -121.5637 | -121.5271 | 121.3623 | 0.036621 | 2.948 | 0.054932
1259.9531 | 121.5088 | -2.8519 | 118.7393 | -0.012131 | 0.006319 | 0.057913 | 0.056006 | 0.00058534 | -0.0057848 | -0.0038772 | -0.0084228 | 0.042825 | 0.042635 | -0.0024609 | 0.017889 | 0.024391 | -0.0053343 | 0.036621 | 118.6707 | -2.8519 | 118.5242 | -2.7512 | -2.8793 | -2.8748 | -2.8244 | -2.71 | -2.7924 | -2.8519 | -2.774 | -2.7695 | -2.7283 | 0 | -0.068665 | -0.21515 | 0.10071 | -0.022888 | -0.027465 | -0.022888 | -0.027465 | 0.05951 | -121.4493 | -121.5912 | 0.07782 | 0.1236 | 0.082398 | 0.064087 | 0.022888 | 0.10071 | 121.376 | 0.01831 | -0.05951 | 121.5225 | 0.082397 | 121.5225 | 0.14191 | -121.5912 | -121.5317 | 121.376 | 0 | 2.8885 | 0.027466
1261.6562 | 121.5775 | -2.7374 | 118.8126 | -0.0045011 | 0.0022602 | 0.054922 | 0.053442 | 0.0025079 | -0.0077074 | -0.002382 | -0.0023192 | 0.042184 | 0.043917 | 0.0011707 | 0.019384 | 0.027169 | -0.0010617 | 0.064087 | 118.7668 | -2.7191 | 118.6249 | -2.6321 | -2.7145 | -2.7145 | -2.6733 | -2.6184 | -2.7054 | -2.7008 | -2.5818 | -2.5818 | -2.5772 | 0.018311 | -0.045776 | -0.18768 | 0.10529 | 0.022888 | 0.022888 | 0.004577 | 0.004577 | 0.032044 | -121.431 | -121.5134 | 0.15564 | 0.16022 | 0.15564 | 0.12817 | 0.1236 | 0.086975 | 121.344 | 0.1236 | 0.004577 | 121.4859 | 0.086975 | 121.5042 | 0.11902 | -121.5317 | -121.5179 | 121.3623 | 0.036621 | 2.8015 | 0.064087
1263.3906 | 121.6461 | -2.7008 | 118.8034 | -0.012131 | 0.0041828 | 0.055563 | 0.051947 | 0.0033623 | -0.005144 | -0.0008866 | -0.0084228 | 0.038766 | 0.04413 | -0.0045971 | 0.01917 | 0.025673 | -0.0040525 | 0.032043 | 118.7576 | -2.6917 | 118.7347 | -2.5131 | -2.6596 | -2.623 | -2.5452 | -2.6459 | -2.6596 | -2.6138 | -2.504 | -2.4994 | -2.5085 | 0.009156 | -0.045777 | -0.068665 | 0.18768 | 0.07782 | 0.041199 | 0.068664 | 0.032043 | 0.041199 | -121.4493 | -121.4172 | 0.19684 | 0.19226 | 0.20142 | 0.15106 | 0.16022 | 0.17853 | 121.4264 | 0.15564 | 0.045776 | 121.4493 | 0.013733 | 121.4584 | 0.054932 | -121.4951 | -121.463 | 121.4355 | 0.086975 | 2.7328 | 0.15564
1265.1562 | 121.6003 | -2.6001 | 118.9407 | -0.0045011 | 0.0026874 | 0.054068 | 0.050879 | -0.0015509 | -0.0066394 | -0.0019546 | -0.005371 | 0.038125 | 0.042849 | -0.0052381 | 0.015539 | 0.025246 | -0.0012753 | -0.009155 | 118.8538 | -2.5909 | 118.8217 | -2.4261 | -2.5589 | -2.5314 | -2.4811 | -2.4994 | -2.5452 | -2.5543 | -2.4399 | -2.4124 | -2.4307 | 0.009156 | -0.086975 | -0.11902 | 0.17395 | 0.068665 | 0.041199 | 0.059509 | 0.032043 | 0.054932 | -121.4401 | -121.4951 | 0.16022 | 0.16937 | 0.18768 | 0.11444 | 0.13275 | 0.1648 | 121.4127 | 0.10529 | -0.009155 | 121.4447 | 0.045776 | 121.4539 | 0.10071 | -121.5317 | -121.4859 | 121.4218 | 0.045777 | 2.5909 | 0.11902
1266.9219 | 121.6782 | -2.449 | 119.014 | -0.012131 | 0.002901 | 0.057486 | 0.054083 | 0.0012261 | -0.0049304 | -0.002382 | -0.005371 | 0.041757 | 0.042849 | -0.0026745 | 0.017889 | 0.026741 | -0.0031979 | 0.041199 | 118.9911 | -2.4628 | 118.9911 | -2.2751 | -2.4124 | -2.3804 | -2.298 | -2.4078 | -2.4078 | -2.3575 | -2.2797 | -2.2522 | -2.2614 | -0.013733 | -0.022888 | -0.022888 | 0.17395 | 0.068665 | 0.036621 | 0.082398 | 0.050354 | 0.041199 | -121.4218 | -121.3715 | 0.16937 | 0.18768 | 0.19684 | 0.14648 | 0.15564 | 0.18768 | 121.4539 | 0.12817 | 0.050354 | 121.4539 | 0 | 121.4401 | 0.041199 | -121.4767 | -121.4218 | 121.4401 | 0.091553 | 2.4902 | 0.15106
1268.625 | 121.6324 | -2.623 | 118.9041 | -0.01976 | 0.0031146 | 0.057272 | 0.05152 | -0.0013373 | -0.0062122 | -0.0013138 | -0.0084228 | 0.03898 | 0.043062 | -0.0022473 | 0.017034 | 0.025032 | -0.0019163 | 0.013733 | 118.808 | -2.6093 | 118.8263 | -2.4033 | -2.5772 | -2.5314 | -2.4399 | -2.5772 | -2.5772 | -2.5589 | -2.4673 | -2.4353 | -2.4673 | 0.013733 | -0.096131 | -0.07782 | 0.21973 | 0.091553 | 0.045777 | 0.07782 | 0.032044 | 0.045777 | -121.4813 | -121.463 | 0.15564 | 0.15564 | 0.18768 | 0.10986 | 0.14191 | 0.20599 | 121.4355 | 0.10986 | 0.01831 | 121.4172 | 0 | 121.431 | 0.045777 | -121.5134 | -121.4813 | 121.4493 | 0.064087 | 2.6367 | 0.18311
1270.3906 | 121.637 | -2.504 | 119.014 | -0.0045011 | -8.9824e-05 | 0.056204 | 0.052801 | 0.0035761 | -0.0066394 | -0.0038772 | -0.0084228 | 0.039621 | 0.041567 | 0.0030933 | 0.016607 | 0.024819 | -0.0072569 | -0.013733 | 118.9178 | -2.4948 | 118.9224 | -2.33 | -2.4673 | -2.4445 | -2.3849 | -2.4261 | -2.4536 | -2.4536 | -2.3346 | -2.2797 | -2.3254 | 0.009155 | -0.09613 | -0.091553 | 0.17395 | 0.059509 | 0.036621 | 0.050354 | 0.027466 | 0.050354 | -121.4401 | -121.4676 | 0.16937 | 0.17853 | 0.2243 | 0.12817 | 0.17395 | 0.1648 | 121.4172 | 0.11902 | 0 | 121.4127 | 0.027466 | 121.4218 | 0.07782 | -121.5088 | -121.4676 | 121.4264 | 0.050354 | 2.4902 | 0.11902
1272.1562 | 121.6415 | -2.179 | 119.3344 | -0.012131 | 0.00033758 | 0.054068 | 0.053442 | 0.0020807 | -0.0092028 | -0.0008866 | -0.0084228 | 0.037698 | 0.04413 | 0.0024525 | 0.015752 | 0.023964 | -0.0034117 | 0.004578 | 119.2429 | -2.179 | 119.2383 | -2.0187 | -2.1469 | -2.1378 | -2.0874 | -2.1332 | -2.1515 | -2.1286 | -2.0004 | -1.9867 | -2.0187 | 0 | -0.091553 | -0.096131 | 0.16022 | 0.041199 | 0.032043 | 0.041199 | 0.032043 | 0.027466 | -121.4676 | -121.463 | 0.17853 | 0.16022 | 0.19226 | 0.13275 | 0.1648 | 0.16022 | 121.4172 | 0.15106 | 0.022888 | 121.4218 | 0.01831 | 121.4218 | 0.045776 | -121.5134 | -121.4859 | 121.4172 | 0.050354 | 2.1835 | 0.091553
1273.9219 | 121.5729 | -2.2339 | 119.3802 | -0.0045011 | 0.0016192 | 0.055136 | 0.054297 | -0.00026906 | -0.0070666 | -0.0011002 | -0.0023192 | 0.037912 | 0.044558 | 0.0084339 | 0.017248 | 0.02311 | -0.0059751 | 0.054932 | 119.3115 | -2.211 | 119.1925 | -2.1103 | -2.211 | -2.1927 | -2.1698 | -2.0828 | -2.179 | -2.1973 | -2.0782 | -2.0645 | -2.0599 | 0.022888 | -0.068665 | -0.18768 | 0.1236 | 0.041199 | 0.022888 | 0.018311 | 0 | 0.054932 | -121.463 | -121.5775 | 0.15564 | 0.17395 | 0.16937 | 0.11902 | 0.11444 | 0.10071 | 121.4035 | 0.10071 | -0.018311 | 121.5225 | 0.09613 | 121.5454 | 0.15106 | -121.5912 | -121.5591 | 121.4264 | 0.036621 | 2.2888 | 0.064087
1275.6094 | 121.6461 | -1.8494 | 119.6732 | -0.012131 | 0.0031146 | 0.057486 | 0.053228 | -0.0017645 | -0.0079212 | -0.0025956 | -0.0023192 | 0.038766 | 0.041994 | -0.0050243 | 0.018316 | 0.024178 | -0.0010617 | 0.018311 | 119.6045 | -1.8448 | 119.6365 | -1.6434 | -1.8173 | -1.767 | -1.7029 | -1.799 | -1.7899 | -1.767 | -1.6891 | -1.6617 | -1.68 | 0.004577 | -0.068665 | -0.036621 | 0.20599 | 0.082397 | 0.032043 | 0.07782 | 0.027466 | 0.059509 | -121.4722 | -121.4401 | 0.16022 | 0.16937 | 0.18768 | 0.10986 | 0.12817 | 0.20142 | 121.4813 | 0.10071 | 0.022888 | 121.4493 | -0.009155 | 121.4539 | 0.050354 | -121.5179 | -121.463 | 121.4859 | 0.082397 | 1.8677 | 0.14648
1277.3594 | 121.6782 | -2.0737 | 119.4168 | -0.0045011 | -0.00051702 | 0.054922 | 0.052374 | 0.00015814 | -0.0079212 | -0.0002456 | -0.0023192 | 0.03663 | 0.041353 | 0.0033069 | 0.015112 | 0.024391 | -0.0074705 | 0.064087 | 119.3436 | -2.0782 | 119.4077 | -1.8219 | -1.973 | -1.9501 | -1.9043 | -2.037 | -2.037 | -1.9913 | -1.8631 | -1.8356 | -1.8768 | -0.004578 | -0.073242 | -0.009155 | 0.25177 | 0.1236 | 0.10071 | 0.12817 | 0.10529 | 0.036621 | -121.4539 | -121.4081 | 0.21057 | 0.19684 | 0.23804 | 0.16022 | 0.20142 | 0.25635 | 121.4859 | 0.17395 | 0.045776 | 121.4218 | 0 | 121.4172 | 0.036621 | -121.4951 | -121.4539 | 121.4813 | 0.082397 | 2.1378 | 0.16937
1279.125 | 121.6827 | -2.3071 | 119.2062 | -0.012131 | 0.00012398 | 0.054709 | 0.053015 | -0.00026906 | -0.0079212 | 0.0006088 | -0.005371 | 0.034707 | 0.042421 | 0.0060841 | 0.01618 | 0.025673 | 0.0023563 | 0.068665 | 119.1376 | -2.2888 | 119.1971 | -2.0554 | -2.1881 | -2.179 | -2.1515 | -2.2705 | -2.2568 | -2.2202 | -2.0782 | -2.0737 | -2.1194 | 0.018311 | -0.068665 | -0.009155 | 0.25177 | 0.12817 | 0.11902 | 0.10986 | 0.10071 | 0.050354 | -121.4767 | -121.4264 | 0.22888 | 0.18768 | 0.23346 | 0.13733 | 0.18311 | 0.23346 | 121.4859 | 0.17853 | 0.036621 | 121.4264 | -0.013733 | 121.4447 | 0.036621 | -121.4951 | -121.463 | 121.5042 | 0.086975 | 2.3758 | 0.15564
1280.8906 | 121.6049 | -2.1057 | 119.4763 | -0.012131 | 0.0035418 | 0.057486 | 0.055578 | -0.00069646 | -0.0072802 | -0.0025956 | -0.005371 | 0.03663 | 0.04413 | 0.015911 | 0.018316 | 0.023537 | 0.0021425 | 0.10071 | 119.4168 | -2.0782 | 119.3573 | -1.9318 | -2.0782 | -2.0416 | -2.0096 | -1.9913 | -2.0508 | -2.0233 | -1.9226 | -1.9455 | -1.9455 | 0.027466 | -0.059509 | -0.11902 | 0.17395 | 0.064087 | 0.027466 | 0.036621 | 0 | 0.054932 | -121.4676 | -121.4996 | 0.18311 | 0.16022 | 0.16022 | 0.10529 | 0.10529 | 0.14648 | 121.4355 | 0.12817 | 0.027466 | 121.4951 | 0.059509 | 121.5225 | 0.11444 | -121.5546 | -121.5271 | 121.463 | 0.082398 | 2.2064 | 0.09613
1282.5781 | 121.5408 | -1.9684 | 119.632 | -0.012131 | 0.0048236 | 0.05535 | 0.055792 | 0.0031487 | -0.0089892 | -0.0025956 | -0.0023192 | 0.035775 | 0.043489 | 0.0071521 | 0.019811 | 0.024178 | -0.0029843 | 0.018311 | 119.6182 | -1.9363 | 119.4397 | -1.886 | -2.0142 | -1.9867 | -1.9821 | -1.8402 | -1.918 | -1.9592 | -1.8585 | -1.8814 | -1.8448 | 0.032044 | -0.013733 | -0.19226 | 0.082398 | -0.01831 | -0.045776 | -0.050354 | -0.07782 | 0.050354 | -121.4722 | -121.5912 | 0.10986 | 0.1236 | 0.086975 | 0.073242 | 0.036621 | 0.050354 | 121.376 | 0.059509 | -0.041199 | 121.5546 | 0.07782 | 121.5866 | 0.12817 | -121.5683 | -121.55 | 121.4081 | 0.009155 | 1.9867 | -0.013733
1284.3281 | 121.6827 | -1.9043 | 119.6182 | -0.0045011 | 0.0050372 | 0.058127 | 0.053228 | -0.0028327 | -0.0094164 | -0.0032364 | -0.011475 | 0.032998 | 0.041353 | 0.0039477 | 0.018316 | 0.024178 | -0.0042661 | 0.045776 | 119.5541 | -1.886 | 119.5862 | -1.6937 | -1.8631 | -1.8127 | -1.7532 | -1.886 | -1.8768 | -1.7899 | -1.6983 | -1.712 | -1.7166 | 0.018311 | -0.064087 | -0.032043 | 0.21057 | 0.091553 | 0.041199 | 0.073242 | 0.022888 | 0.027466 | -121.5042 | -121.4081 | 0.20599 | 0.18768 | 0.19226 | 0.16022 | 0.1648 | 0.19226 | 121.4722 | 0.17853 | 0.086975 | 121.4401 | -0.009155 | 121.4584 | 0.018311 | -121.5042 | -121.4951 | 121.4905 | 0.11444 | 1.9501 | 0.15106
1286.0938 | 121.6965 | -1.7899 | 119.7464 | -0.0045011 | 0.0016192 | 0.05535 | 0.051733 | -0.0032599 | -0.0081348 | -0.0011002 | -0.005371 | 0.033426 | 0.042849 | -0.0050243 | 0.018102 | 0.024819 | -0.0025571 | 0.059509 | 119.6365 | -1.7807 | 119.7144 | -1.5472 | -1.6937 | -1.6663 | -1.6296 | -1.7578 | -1.7578 | -1.7166 | -1.5656 | -1.561 | -1.6251 | 0.009155 | -0.10986 | -0.032044 | 0.24261 | 0.1236 | 0.09613 | 0.11444 | 0.086975 | 0.032044 | -121.5042 | -121.463 | 0.2243 | 0.16479 | 0.22888 | 0.13275 | 0.19684 | 0.23346 | 121.4951 | 0.19226 | 0.041198 | 121.4172 | 0 | 121.4264 | 0.032044 | -121.5271 | -121.5042 | 121.5042 | 0.073242 | 1.8494 | 0.16022
1287.8438 | 121.7102 | -1.5793 | 119.9432 | -0.012131 | 0.0056782 | 0.058127 | 0.055151 | 0.00058534 | -0.0055712 | -0.002382 | -0.005371 | 0.037057 | 0.042849 | -0.00075193 | 0.019384 | 0.025887 | -0.0038389 | 0.045776 | 119.9066 | -1.5701 | 119.8975 | -1.3916 | -1.5427 | -1.5015 | -1.442 | -1.5472 | -1.5518 | -1.4832 | -1.3824 | -1.3962 | -1.3916 | 0.009156 | -0.036621 | -0.045776 | 0.18768 | 0.07782 | 0.036621 | 0.068664 | 0.027465 | 0.027466 | -121.4905 | -121.4264 | 0.19684 | 0.18768 | 0.18311 | 0.16022 | 0.15564 | 0.17853 | 121.4676 | 0.16937 | 0.068665 | 121.4767 | 0.004578 | 121.4859 | 0.032044 | -121.5134 | -121.4951 | 121.4767 | 0.096131 | 1.6251 | 0.13733
1289.5312 | 121.6965 | -1.3779 | 120.1813 | -0.0045011 | 0.001833 | 0.054495 | 0.053656 | -0.0013373 | -0.00963 | -0.0004592 | -0.005371 | 0.03898 | 0.042208 | -0.00032473 | 0.015325 | 0.024178 | -0.0059751 | 0.073242 | 120.0851 | -1.355 | 120.1584 | -1.1261 | -1.2543 | -1.2497 | -1.2085 | -1.3046 | -1.3138 | -1.268 | -1.1398 | -1.1353 | -1.1993 | 0.022889 | -0.09613 | -0.022888 | 0.25177 | 0.12817 | 0.1236 | 0.10529 | 0.10071 | 0.064087 | -121.4859 | -121.4493 | 0.23804 | 0.17853 | 0.24262 | 0.11444 | 0.17853 | 0.22888 | 121.5134 | 0.17395 | 0.045777 | 121.4401 | 0.009156 | 121.463 | 0.073243 | -121.5363 | -121.4951 | 121.5363 | 0.10986 | 1.4511 | 0.16937
1291.2812 | 121.669 | -1.4145 | 120.1721 | -0.0045011 | 0.0031146 | 0.05535 | 0.053015 | -0.00048286 | -0.0083484 | -0.0011002 | -0.0023192 | 0.038339 | 0.04413 | 0.00095707 | 0.014684 | 0.024178 | -0.0029843 | 0 | 120.076 | -1.4191 | 120.0439 | -1.2497 | -1.3687 | -1.3458 | -1.3321 | -1.3412 | -1.3733 | -1.3321 | -1.2222 | -1.2085 | -1.2405 | -0.004577 | -0.09613 | -0.12817 | 0.1648 | 0.068665 | 0.045777 | 0.073242 | 0.050354 | 0.041199 | -121.5134 | -121.5042 | 0.19226 | 0.17395 | 0.20599 | 0.13275 | 0.1648 | 0.16937 | 121.463 | 0.15106 | 0.041199 | 121.4951 | 0.032043 | 121.4905 | 0.073242 | -121.5912 | -121.5454 | 121.4584 | 0.082398 | 1.4145 | 0.082398
1293.0312 | 121.6415 | -1.3962 | 120.1447 | -0.0045011 | 0.0016192 | 0.055563 | 0.053656 | -0.0034735 | -0.0089892 | -0.0040908 | -0.0084228 | 0.035775 | 0.042635 | -0.011433 | 0.018957 | 0.025032 | 0.00021995 | -0.009155 | 120.0897 | -1.3962 | 120.0623 | -1.2543 | -1.387 | -1.355 | -1.3275 | -1.3596 | -1.3687 | -1.3504 | -1.2451 | -1.2177 | -1.2543 | 0 | -0.054931 | -0.082397 | 0.14191 | 0.041199 | 0.009155 | 0.041199 | 0.009155 | 0.027466 | -121.5042 | -121.4951 | 0.15106 | 0.14191 | 0.17853 | 0.11444 | 0.15106 | 0.14191 | 121.4584 | 0.1236 | 0.01831 | 121.4859 | 0.009155 | 121.4859 | 0.036621 | -121.5408 | -121.5134 | 121.4584 | 0.045776 | 1.387 | 0.068664
1294.7188 | 121.701 | -1.4923 | 120.0485 | -0.012131 | 0.001833 | 0.05535 | 0.051947 | -0.0051825 | -0.010698 | -0.0013138 | -0.005371 | 0.037698 | 0.041994 | 0.0022389 | 0.01383 | 0.024605 | -0.0053343 | 0.10071 | 119.9661 | -1.4923 | 120.0348 | -1.2589 | -1.3962 | -1.3779 | -1.3367 | -1.442 | -1.442 | -1.387 | -1.2726 | -1.2497 | -1.3046 | 0 | -0.082398 | -0.013733 | 0.23346 | 0.11444 | 0.096131 | 0.11444 | 0.096131 | 0.050354 | -121.4905 | -121.4355 | 0.21973 | 0.18768 | 0.24262 | 0.13733 | 0.19226 | 0.23346 | 121.5271 | 0.16937 | 0.054932 | 121.4584 | 0 | 121.4584 | 0.050354 | -121.5408 | -121.4905 | 121.5271 | 0.10529 | 1.593 | 0.15564
1296.4844 | 121.6507 | -1.4557 | 120.1263 | -0.0045011 | 0.0033282 | 0.055563 | 0.056433 | -0.0017645 | -0.0089892 | 0.001677 | -0.0023192 | 0.040475 | 0.044344 | 0.0054431 | 0.019811 | 0.023323 | -0.0042661 | 0.10529 | 120.1355 | -1.4557 | 120.0439 | -1.2955 | -1.4282 | -1.4099 | -1.3367 | -1.3504 | -1.4053 | -1.3733 | -1.2955 | -1.2863 | -1.2863 | 0 | 0.009155 | -0.082398 | 0.16022 | 0.045776 | 0.027465 | 0.045776 | 0.027465 | 0.050354 | -121.4767 | -121.4996 | 0.16022 | 0.16937 | 0.16937 | 0.11902 | 0.11902 | 0.16022 | 121.4996 | 0.10986 | 0.032043 | 121.5912 | 0.054931 | 121.5912 | 0.10529 | -121.582 | -121.5317 | 121.4996 | 0.082397 | 1.561 | 0.11902
1298.25 | 121.5866 | -1.4328 | 120.1904 | -0.0045011 | 0.00012398 | 0.056845 | 0.054083 | -0.0021919 | -0.00963 | -0.0002456 | -0.0084228 | 0.039834 | 0.043917 | -0.0050243 | 0.018102 | 0.023964 | -0.0055479 | 0.032043 | 120.1309 | -1.4145 | 120.0302 | -1.2909 | -1.4145 | -1.4008 | -1.3916 | -1.2955 | -1.3779 | -1.4008 | -1.2909 | -1.2817 | -1.3 | 0.01831 | -0.05951 | -0.16022 | 0.14191 | 0.032043 | 0.01831 | 0.013733 | 0 | 0.054931 | -121.4859 | -121.5912 | 0.14191 | 0.13275 | 0.15106 | 0.07782 | 0.096131 | 0.1236 | 121.4447 | 0.086975 | -0.022888 | 121.5454 | 0.082398 | 121.5637 | 0.13733 | -121.6049 | -121.5683 | 121.463 | 0.032043 | 1.4648 | 0.041198
1300.0156 | 121.701 | -1.3321 | 120.2042 | -0.012131 | -0.00051702 | 0.05535 | 0.05216 | 0.00058534 | -0.0077074 | -0.0025956 | -0.0023192 | 0.037271 | 0.042421 | -0.00011113 | 0.018102 | 0.026528 | -0.0034117 | 0.07782 | 120.1492 | -1.3275 | 120.2133 | -1.0895 | -1.2131 | -1.1948 | -1.1856 | -1.2772 | -1.2726 | -1.2177 | -1.1032 | -1.0757 | -1.1536 | 0.004577 | -0.054932 | 0.009155 | 0.24261 | 0.13733 | 0.11902 | 0.13275 | 0.11444 | 0.059509 | -121.4813 | -121.4218 | 0.22888 | 0.17853 | 0.25635 | 0.11902 | 0.19684 | 0.23804 | 121.5408 | 0.16937 | 0.054932 | 121.4767 | -0.004578 | 121.4813 | 0.054931 | -121.5317 | -121.4767 | 121.5454 | 0.11444 | 1.4099 | 0.14648
1301.7188 | 121.7194 | -1.2955 | 120.282 | -0.0045011 | 0.0058918 | 0.057272 | 0.054297 | -0.0017645 | -0.0057848 | -0.0028092 | -0.0023192 | 0.037271 | 0.040499 | -0.00053833 | 0.018102 | 0.025032 | -0.0014891 | 0.050354 | 120.2179 | -1.2817 | 120.2362 | -1.0712 | -1.2314 | -1.2085 | -1.1307 | -1.236 | -1.2314 | -1.1627 | -1.0757 | -1.0757 | -1.0803 | 0.013733 | -0.064086 | -0.045776 | 0.2243 | 0.086975 | 0.064087 | 0.073242 | 0.050354 | 0.064087 | -121.5179 | -121.4447 | 0.21973 | 0.21515 | 0.21973 | 0.15106 | 0.15564 | 0.21057 | 121.5179 | 0.15564 | 0.068664 | 121.4996 | -0.004578 | 121.5134 | 0.059509 | -121.5637 | -121.5134 | 121.5317 | 0.13275 | 1.3458 | 0.1648
1303.4688 | 121.7331 | -1.2405 | 120.3049 | -0.012131 | -0.00030342 | 0.056204 | 0.053228 | 0.0010125 | -0.0083484 | 0.0012496 | -0.0084228 | 0.038766 | 0.043703 | 0.0039477 | 0.015539 | 0.023964 | -0.0040525 | 0.073242 | 120.2682 | -1.2497 | 120.3094 | -0.97046 | -1.1169 | -1.0986 | -1.0666 | -1.2039 | -1.1902 | -1.1169 | -0.99335 | -0.98877 | -1.0391 | -0.009155 | -0.036621 | 0.004577 | 0.27008 | 0.14191 | 0.1236 | 0.15106 | 0.13275 | 0.050354 | -121.5088 | -121.4218 | 0.24719 | 0.20142 | 0.25177 | 0.15106 | 0.20142 | 0.27924 | 121.5591 | 0.19684 | 0.073243 | 121.5179 | -0.013732 | 121.5088 | 0.036622 | -121.5546 | -121.4951 | 121.55 | 0.1236 | 1.3138 | 0.17395
1305.2344 | 121.6003 | -1.2909 | 120.3461 | -0.012131 | 0.0048236 | 0.056631 | 0.05451 | 0.00037174 | -0.0066394 | -0.0045182 | -0.0023192 | 0.04197 | 0.043703 | -0.0020337 | 0.019598 | 0.025032 | -0.0057615 | 0.086975 | 120.2866 | -1.2909 | 120.1996 | -1.1444 | -1.2772 | -1.2634 | -1.1993 | -1.1856 | -1.2222 | -1.2314 | -1.1719 | -1.1627 | -1.149 | 0 | -0.059509 | -0.14648 | 0.14648 | 0.027466 | 0.013733 | 0.027466 | 0.013733 | 0.068665 | -121.5317 | -121.5775 | 0.11902 | 0.14191 | 0.12817 | 0.073242 | 0.059509 | 0.14648 | 121.4905 | 0.050354 | -0.009155 | 121.5775 | 0.036621 | 121.5775 | 0.10529 | -121.637 | -121.5683 | 121.4905 | 0.05951 | 1.3779 | 0.091553
1307 | 121.6919 | -1.3138 | 120.2866 | -0.0045011 | 0.0033282 | 0.054709 | 0.05152 | -0.0049689 | -0.0072802 | 0.0006088 | -0.005371 | 0.037271 | 0.042849 | -0.00032473 | 0.01853 | 0.026314 | -0.0051205 | -0.018311 | 120.2362 | -1.3 | 120.1813 | -1.1398 | -1.2817 | -1.2314 | -1.2131 | -1.2497 | -1.2497 | -1.236 | -1.1444 | -1.1169 | -1.1581 | 0.013733 | -0.050354 | -0.10529 | 0.17395 | 0.082398 | 0.032044 | 0.068665 | 0.018311 | 0.064087 | -121.5363 | -121.5225 | 0.16937 | 0.15564 | 0.19684 | 0.091553 | 0.13275 | 0.16022 | 121.4813 | 0.10529 | 0.013733 | 121.5363 | 0 | 121.55 | 0.064087 | -121.5866 | -121.5363 | 121.4951 | 0.07782 | 1.2955 | 0.10071
1308.6875 | 121.7331 | -1.268 | 120.3094 | -0.01976 | 0.00076478 | 0.054068 | 0.051306 | -0.0028327 | -0.0062122 | -0.0015274 | -0.0084228 | 0.039621 | 0.043489 | 0.00031607 | 0.014684 | 0.024819 | -0.0042661 | 0.022888 | 120.2362 | -1.2451 | 120.2545 | -1.0483 | -1.181 | -1.1627 | -1.1078 | -1.2085 | -1.2177 | -1.1536 | -1.0208 | -1.03 | -1.0574 | 0.022888 | -0.073242 | -0.054931 | 0.21973 | 0.10529 | 0.086975 | 0.082397 | 0.064087 | 0.050354 | -121.5179 | -121.463 | 0.24719 | 0.21057 | 0.23804 | 0.16022 | 0.18768 | 0.19684 | 121.4996 | 0.19684 | 0.064087 | 121.4813 | 0.009155 | 121.5042 | 0.059509 | -121.5546 | -121.5271 | 121.5225 | 0.11444 | 1.2909 | 0.16022
1310.4375 | 121.7102 | -1.2039 | 120.369 | -0.012131 | 0.0050372 | 0.054282 | 0.055151 | 0.0016535 | -0.0066394 | -0.0036636 | -0.0023192 | 0.037271 | 0.040712 | 0.0073657 | 0.01853 | 0.02546 | -0.0010617 | 0.059509 | 120.2957 | -1.2039 | 120.3415 | -0.98419 | -1.149 | -1.1124 | -1.0254 | -1.1581 | -1.1581 | -1.0712 | -0.98419 | -1.0025 | -1.0071 | 0 | -0.073243 | -0.027466 | 0.21973 | 0.091552 | 0.054931 | 0.091552 | 0.054931 | 0.045776 | -121.5271 | -121.4401 | 0.21973 | 0.19684 | 0.20142 | 0.15106 | 0.15564 | 0.21973 | 121.5454 | 0.17395 | 0.086975 | 121.4996 | 0 | 121.4996 | 0.045776 | -121.5729 | -121.5271 | 121.5454 | 0.13275 | 1.2634 | 0.17853
1312.2031 | 121.6919 | -1.1902 | 120.3873 | -0.012131 | 0.002901 | 0.055991 | 0.052801 | 0.0035761 | -0.0079212 | -0.0013138 | -0.0084228 | 0.035775 | 0.04413 | 0.00095707 | 0.015966 | 0.024605 | -0.0036253 | -0.013733 | 120.3644 | -1.1765 | 120.2957 | -1.0483 | -1.1536 | -1.1124 | -1.1078 | -1.1124 | -1.1307 | -1.1215 | -1.0162 | -1.0117 | -1.0208 | 0.013733 | -0.022888 | -0.091553 | 0.14191 | 0.07782 | 0.036622 | 0.064087 | 0.022889 | 0.05951 | -121.4996 | -121.5088 | 0.17395 | 0.16937 | 0.17853 | 0.10986 | 0.11902 | 0.12817 | 121.4722 | 0.11444 | 0.009155 | 121.5408 | 0.01831 | 121.5546 | 0.07782 | -121.5637 | -121.5179 | 121.4859 | 0.068665 | 1.1765 | 0.082398
1313.9688 | 121.5958 | -1.2177 | 120.4514 | -0.012131 | 0.0061054 | 0.055777 | 0.056433 | -0.0032599 | -0.0070666 | -0.0049454 | -0.0084228 | 0.03428 | 0.044344 | 0.013561 | 0.01853 | 0.024605 | -0.0038389 | 0.022888 | 120.3827 | -1.2222 | 120.2271 | -1.1261 | -1.2634 | -1.2177 | -1.1719 | -1.0895 | -1.1673 | -1.181 | -1.1169 | -1.1215 | -1.0849 | -0.004578 | -0.068665 | -0.2243 | 0.091552 | 0 | -0.045777 | 0.004578 | -0.041199 | 0.050354 | -121.5408 | -121.6324 | 0.10071 | 0.13275 | 0.09613 | 0.082397 | 0.045776 | 0.09613 | 121.4493 | 0.050354 | -0.013733 | 121.6049 | 0.077819 | 121.6003 | 0.12817 | -121.6736 | -121.6187 | 121.4447 | 0.036621 | 1.2405 | 0.045776
1315.6562 | 121.5912 | -1.1719 | 120.5246 | -0.01976 | 0.0039692 | 0.056631 | 0.055151 | -0.00069646 | -0.00963 | -0.0015274 | -0.0023192 | 0.032571 | 0.045626 | 0.010356 | 0.019384 | 0.023964 | -0.0029843 | 0.027466 | 120.4285 | -1.1673 | 120.2911 | -1.0849 | -1.2131 | -1.1902 | -1.1581 | -1.0391 | -1.1261 | -1.1398 | -1.0803 | -1.0849 | -1.0483 | 0.004578 | -0.09613 | -0.23346 | 0.086975 | -0.018311 | -0.041199 | -0.022889 | -0.045777 | 0.045776 | -121.5637 | -121.6644 | 0.091553 | 0.1236 | 0.086975 | 0.07782 | 0.041199 | 0.082397 | 121.4584 | 0.045777 | -0.013733 | 121.5958 | 0.086975 | 121.6003 | 0.13275 | -121.6919 | -121.6507 | 121.463 | 0.032043 | 1.1993 | 0.013733
1317.4219 | 121.7331 | -1.0712 | 120.52 | -0.01976 | 0.002901 | 0.054922 | 0.051092 | 0.00079894 | -0.006853 | -0.0019546 | -0.0023192 | 0.030435 | 0.041994 | 0.0071521 | 0.016393 | 0.025032 | -0.0023435 | 0.054932 | 120.4147 | -1.0803 | 120.4742 | -0.81482 | -0.94757 | -0.93384 | -0.90179 | -1.0391 | -1.0162 | -0.9613 | -0.82398 | -0.81482 | -0.86517 | -0.009155 | -0.10529 | -0.045777 | 0.25635 | 0.13733 | 0.1236 | 0.14648 | 0.13275 | 0.054932 | -121.5591 | -121.4813 | 0.24719 | 0.20599 | 0.25635 | 0.15106 | 0.20142 | 0.2655 | 121.5546 | 0.19226 | 0.054931 | 121.4951 | -0.022889 | 121.4859 | 0.032043 | -121.6003 | -121.5363 | 121.5454 | 0.10986 | 1.1261 | 0.16937
1319.1719 | 121.6461 | -1.1032 | 120.575 | -0.0045011 | 0.0033282 | 0.052573 | 0.053656 | 0.0016535 | -0.0066394 | -3.1996e-05 | -0.005371 | 0.032998 | 0.044771 | 0.010784 | 0.017675 | 0.024605 | -0.0044797 | 0.064087 | 120.4926 | -1.0712 | 120.3964 | -0.96588 | -1.0803 | -1.062 | -1.0208 | -0.95673 | -1.0345 | -1.0162 | -0.92468 | -0.9201 | -0.90637 | 0.032043 | -0.082397 | -0.17853 | 0.13733 | 0.041198 | 0.022888 | 0.009155 | -0.009155 | 0.068664 | -121.5317 | -121.5912 | 0.17853 | 0.19684 | 0.18311 | 0.12817 | 0.11444 | 0.10529 | 121.4676 | 0.10986 | 0.018311 | 121.5637 | 0.07782 | 121.5958 | 0.14648 | -121.6461 | -121.6095 | 121.4996 | 0.086975 | 1.1673 | 0.082397
1320.9375 | 121.6278 | -1.0483 | 120.5704 | -0.01976 | 0.0052508 | 0.055991 | 0.055792 | 0.00079894 | -0.0053576 | -0.0008866 | -0.0084228 | 0.032357 | 0.047121 | 0.014415 | 0.016821 | 0.024391 | -0.0036253 | 0.086975 | 120.5338 | -1.0391 | 120.4514 | -0.90179 | -1.0529 | -1.0345 | -0.97504 | -0.97504 | -1.0117 | -1.0025 | -0.9201 | -0.92468 | -0.9201 | 0.009155 | -0.036622 | -0.11902 | 0.14648 | 0.013733 | -0.004577 | 0.004578 | -0.013732 | 0.036621 | -121.5454 | -121.5729 | 0.12817 | 0.12817 | 0.1236 | 0.091553 | 0.086975 | 0.13733 | 121.4905 | 0.091553 | 0.009156 | 121.5729 | 0.036621 | 121.582 | 0.073242 | -121.6095 | -121.582 | 121.4996 | 0.045777 | 1.1353 | 0.073242
1322.6406 | 121.6415 | -1.0941 | 120.5978 | 0.0031279 | 0.0033282 | 0.057272 | 0.053869 | -0.0039007 | -0.0072802 | -0.0008866 | 0.00073235 | 0.030648 | 0.042849 | 0.0095019 | 0.018102 | 0.026314 | -0.00084805 | 0 | 120.52 | -1.0757 | 120.3873 | -0.96588 | -1.1124 | -1.0757 | -1.0208 | -0.95673 | -1.0208 | -1.0254 | -0.93842 | -0.94299 | -0.92468 | 0.01831 | -0.077819 | -0.21057 | 0.12817 | 0.01831 | -0.018311 | 0 | -0.036621 | 0.073242 | -121.5546 | -121.6232 | 0.15564 | 0.16937 | 0.15106 | 0.09613 | 0.07782 | 0.10986 | 121.463 | 0.082397 | -0.004578 | 121.5958 | 0.064087 | 121.6141 | 0.13733 | -121.6736 | -121.6187 | 121.4813 | 0.068664 | 1.0941 | 0.073242
1324.4062 | 121.6141 | -1.0895 | 120.6116 | -0.0045011 | 0.0035418 | 0.056845 | 0.054937 | 0.0014397 | -0.0081348 | -0.005159 | -0.0023192 | 0.031503 | 0.046267 | 0.0092883 | 0.020666 | 0.025887 | -0.00084805 | 0.009155 | 120.575 | -1.0483 | 120.3964 | -0.97046 | -1.1032 | -1.0529 | -1.0345 | -0.92468 | -0.98877 | -1.0162 | -0.94757 | -0.94757 | -0.91553 | 0.041199 | -0.036621 | -0.21515 | 0.11902 | 0.036622 | -0.013732 | -0.004577 | -0.054931 | 0.10071 | -121.5363 | -121.6278 | 0.14191 | 0.17395 | 0.14191 | 0.073243 | 0.041199 | 0.07782 | 121.4447 | 0.041199 | -0.027465 | 121.6232 | 0.064087 | 121.6644 | 0.16479 | -121.6599 | -121.6003 | 121.4859 | 0.073243 | 1.0986 | 0.054932
1326.1719 | 121.7743 | -1.0162 | 120.5566 | -0.012131 | 0.00033758 | 0.055777 | 0.051092 | 0.0035761 | -0.0087756 | -0.0025956 | -0.0084228 | 0.028939 | 0.043703 | 0.0058703 | 0.016607 | 0.023751 | 0.0027835 | 0.050354 | 120.4971 | -1.0071 | 120.5338 | -0.76904 | -0.91095 | -0.88806 | -0.82398 | -0.9613 | -0.97504 | -0.89722 | -0.76904 | -0.77362 | -0.8194 | 0.009155 | -0.05951 | -0.022889 | 0.24719 | 0.12817 | 0.10528 | 0.11902 | 0.09613 | 0.041198 | -121.5179 | -121.4539 | 0.24719 | 0.19684 | 0.24261 | 0.15564 | 0.20142 | 0.23804 | 121.5408 | 0.20599 | 0.07782 | 121.5042 | 0.013733 | 121.5134 | 0.054931 | -121.5637 | -121.5317 | 121.55 | 0.11902 | 1.0666 | 0.19226
1327.9219 | 121.6095 | -1.0803 | 120.6162 | -0.0045011 | 0.00076478 | 0.055777 | 0.05216 | -0.0036871 | -0.010057 | -0.0025956 | -0.005371 | 0.028726 | 0.043489 | 0.012065 | 0.014471 | 0.0261 | 0.00043375 | 0.050354 | 120.52 | -1.0391 | 120.4285 | -0.9201 | -1.0391 | -1.03 | -1.0071 | -0.93384 | -0.99792 | -1.0483 | -0.90637 | -0.92468 | -0.9201 | 0.041198 | -0.09613 | -0.18768 | 0.16022 | 0.050354 | 0.041198 | 0.009156 | 0 | 0.082397 | -121.55 | -121.6644 | 0.17395 | 0.16022 | 0.15564 | 0.07782 | 0.073242 | 0.11902 | 121.4676 | 0.091553 | -0.050354 | 121.5591 | 0.064087 | 121.6003 | 0.14648 | -121.6553 | -121.6141 | 121.5088 | 0.032043 | 1.1307 | 0.073242
1329.6094 | 121.6324 | -1.062 | 120.6253 | -0.012131 | 0.0041828 | 0.05834 | 0.053442 | 0.00079894 | -0.0057848 | -0.0011002 | -0.0023192 | 0.033426 | 0.044985 | 0.015911 | 0.016607 | 0.022896 | -0.0012753 | 0.082397 | 120.5429 | -1.03 | 120.4422 | -0.90637 | -1.0483 | -1.0117 | -0.98877 | -0.93384 | -1.0071 | -1.0162 | -0.92468 | -0.94757 | -0.91553 | 0.032044 | -0.082397 | -0.1831 | 0.15564 | 0.050354 | 0.013733 | 0.01831 | -0.018311 | 0.054932 | -121.5591 | -121.6415 | 0.13733 | 0.14648 | 0.11444 | 0.091553 | 0.059509 | 0.1236 | 121.4722 | 0.082397 | -0.009155 | 121.5729 | 0.073242 | 121.6049 | 0.12817 | -121.6553 | -121.6324 | 121.5042 | 0.045777 | 1.1444 | 0.073242
1331.375 | 121.7194 | -1.0254 | 120.575 | -0.01976 | 0.0026874 | 0.053641 | 0.054297 | -0.0036871 | -0.0055712 | -0.002382 | -0.0023192 | 0.028512 | 0.044344 | 0.010143 | 0.01383 | 0.024819 | -0.0019163 | 0 | 120.52 | -0.99792 | 120.5063 | -0.82855 | -0.98877 | -0.93842 | -0.88806 | -0.97046 | -0.96588 | -0.95673 | -0.8606 | -0.84686 | -0.85144 | 0.027466 | -0.054931 | -0.068664 | 0.19684 | 0.086975 | 0.036621 | 0.059509 | 0.009155 | 0.05951 | -121.5454 | -121.5317 | 0.16479 | 0.17395 | 0.17853 | 0.11444 | 0.11902 | 0.16937 | 121.5042 | 0.10528 | 0.009155 | 121.5179 | -0.004578 | 121.5454 | 0.054932 | -121.5729 | -121.5408 | 121.5317 | 0.068665 | 1.0254 | 0.13733
1333.1406 | 121.7148 | -1.062 | 120.5338 | -0.012131 | 0.0024738 | 0.055563 | 0.053228 | 0.0018671 | -0.0098438 | -0.0008866 | -0.0023192 | 0.030008 | 0.042635 | 0.0092883 | 0.014684 | 0.026741 | -0.0055479 | 0.086975 | 120.4742 | -1.0345 | 120.4971 | -0.83313 | -0.96588 | -0.94757 | -0.91095 | -1.0071 | -1.0071 | -0.98419 | -0.85144 | -0.85602 | -0.89264 | 0.027466 | -0.059509 | -0.036621 | 0.22888 | 0.11444 | 0.096131 | 0.086975 | 0.068665 | 0.054932 | -121.5408 | -121.5179 | 0.21057 | 0.16937 | 0.20599 | 0.11444 | 0.15106 | 0.20142 | 121.5317 | 0.15564 | 0.022888 | 121.5088 | 0 | 121.5363 | 0.054932 | -121.5683 | -121.5408 | 121.5591 | 0.07782 | 1.149 | 0.15106
1334.9062 | 121.7468 | -1.1627 | 120.4834 | -0.0045011 | 0.00033758 | 0.056631 | 0.05216 | -0.0011237 | -0.0087756 | -0.0013138 | -0.005371 | 0.027871 | 0.042635 | 0.011211 | 0.015752 | 0.025032 | -0.0038389 | 0.086975 | 120.3552 | -1.1261 | 120.4422 | -0.89722 | -1.0254 | -1.0071 | -0.96588 | -1.1032 | -1.0803 | -1.0345 | -0.90179 | -0.91553 | -0.94299 | 0.036621 | -0.12817 | -0.041198 | 0.2655 | 0.15564 | 0.13733 | 0.11902 | 0.10071 | 0.082398 | -121.5866 | -121.5179 | 0.26093 | 0.21973 | 0.24719 | 0.13733 | 0.1648 | 0.22888 | 121.5683 | 0.17853 | 0.045776 | 121.4813 | -0.022888 | 121.5179 | 0.05951 | -121.6095 | -121.5637 | 121.6049 | 0.12817 | 1.2497 | 0.19684
1336.6719 | 121.6782 | -1.2726 | 120.4102 | -0.012131 | 0.0026874 | 0.0577 | 0.055578 | 0.00058534 | -0.0074938 | -0.0004592 | -0.005371 | 0.030221 | 0.045198 | 0.018474 | 0.016821 | 0.023537 | -0.0059751 | 0.082397 | 120.3781 | -1.2497 | 120.2225 | -1.1398 | -1.2451 | -1.2405 | -1.2222 | -1.1261 | -1.2222 | -1.2085 | -1.0986 | -1.1307 | -1.1032 | 0.022888 | -0.032043 | -0.18768 | 0.13275 | 0.032043 | 0.027466 | 0.009155 | 0.004578 | 0.050354 | -121.5363 | -121.6187 | 0.17395 | 0.16937 | 0.14191 | 0.11902 | 0.091553 | 0.10986 | 121.4722 | 0.1236 | 0.013733 | 121.6278 | 0.09613 | 121.6507 | 0.14648 | -121.6599 | -121.6324 | 121.4951 | 0.064087 | 1.355 | 0.050354
1338.3594 | 121.6095 | -1.3504 | 120.3415 | 0.0031279 | 0.0048236 | 0.055563 | 0.053869 | -0.0015509 | -0.0089892 | -0.0019546 | -0.005371 | 0.031289 | 0.044771 | 0.012279 | 0.019384 | 0.022469 | -0.0053343 | 0.027466 | 120.3003 | -1.3275 | 120.1492 | -1.2405 | -1.3641 | -1.3321 | -1.3412 | -1.2131 | -1.2817 | -1.3138 | -1.2497 | -1.2726 | -1.2085 | 0.022888 | -0.041199 | -0.19226 | 0.10986 | 0.018311 | -0.013733 | -0.004577 | -0.036621 | 0.068665 | -121.5546 | -121.6553 | 0.10071 | 0.14191 | 0.07782 | 0.073242 | 0.009155 | 0.086975 | 121.4767 | 0.032043 | -0.032044 | 121.6278 | 0.068664 | 121.6507 | 0.13733 | -121.669 | -121.6232 | 121.4996 | 0.036621 | 1.3779 | 0.009155
1340.1094 | 121.6187 | -1.3687 | 120.3415 | -0.012131 | 0.0052508 | 0.057913 | 0.05451 | 0.0014397 | -0.006853 | 0.0001816 | -0.0084228 | 0.030435 | 0.044771 | 0.011852 | 0.016393 | 0.023751 | -0.0042661 | -0.009155 | 120.3003 | -1.3367 | 120.1126 | -1.2634 | -1.387 | -1.3733 | -1.3229 | -1.2222 | -1.3092 | -1.3184 | -1.2634 | -1.2772 | -1.2085 | 0.032043 | -0.041199 | -0.22888 | 0.10529 | -0.004578 | -0.018311 | -0.036621 | -0.050354 | 0.059509 | -121.5637 | -121.6599 | 0.10529 | 0.16022 | 0.091552 | 0.10071 | 0.032043 | 0.073242 | 121.4493 | 0.045776 | -0.009155 | 121.637 | 0.086975 | 121.669 | 0.14648 | -121.6782 | -121.6507 | 121.4813 | 0.050354 | 1.3596 | 0.045776
1341.875 | 121.7697 | -1.3321 | 120.2866 | -0.012131 | 0.0020466 | 0.054922 | 0.050879 | -0.0032599 | -0.0081348 | -0.0013138 | -0.0084228 | 0.028299 | 0.04413 | 0.012279 | 0.015539 | 0.023751 | 0.00086095 | 0.059509 | 120.2133 | -1.3092 | 120.2774 | -1.062 | -1.1993 | -1.181 | -1.149 | -1.268 | -1.2772 | -1.2131 | -1.0757 | -1.0849 | -1.1124 | 0.022888 | -0.073242 | -0.009155 | 0.27008 | 0.15106 | 0.13275 | 0.12817 | 0.10986 | 0.054931 | -121.5546 | -121.4996 | 0.25635 | 0.21973 | 0.24719 | 0.1648 | 0.19226 | 0.24719 | 121.5866 | 0.20142 | 0.064087 | 121.5225 | 0.009156 | 121.5454 | 0.064087 | -121.5958 | -121.5637 | 121.6095 | 0.11902 | 1.3916 | 0.18311
1343.5938 | 121.7194 | -1.442 | 120.2271 | -0.0045011 | 0.00033758 | 0.054922 | 0.050451 | -0.0041145 | -0.0092028 | -0.0032364 | -0.0023192 | 0.028939 | 0.04178 | 0.01527 | 0.017889 | 0.026314 | -0.0046933 | 0.082397 | 120.1309 | -1.4191 | 120.1309 | -1.2177 | -1.3275 | -1.3275 | -1.3138 | -1.3824 | -1.387 | -1.3687 | -1.2451 | -1.268 | -1.2726 | 0.022889 | -0.096131 | -0.096131 | 0.2243 | 0.11444 | 0.11444 | 0.091552 | 0.091552 | 0.054932 | -121.6095 | -121.5958 | 0.19684 | 0.16937 | 0.17395 | 0.11444 | 0.11902 | 0.20142 | 121.55 | 0.14191 | 0.018311 | 121.55 | 0.004578 | 121.5729 | 0.05951 | -121.6461 | -121.6141 | 121.5729 | 0.073243 | 1.5244 | 0.12817
1345.3281 | 121.7743 | -1.5106 | 120.1309 | -0.012131 | 0.0056782 | 0.054922 | 0.053015 | -0.0015509 | -0.0066394 | -0.0045182 | -0.005371 | 0.029794 | 0.044771 | 0.015697 | 0.017675 | 0.0261 | 0.00043375 | 0.059509 | 120.0577 | -1.474 | 120.0531 | -1.3092 | -1.4648 | -1.4282 | -1.3641 | -1.4648 | -1.4465 | -1.387 | -1.3138 | -1.3138 | -1.3 | 0.036621 | -0.073242 | -0.077819 | 0.20142 | 0.082397 | 0.045776 | 0.045776 | 0.009155 | 0.064087 | -121.5958 | -121.5179 | 0.19684 | 0.21057 | 0.19684 | 0.14648 | 0.13275 | 0.1648 | 121.5271 | 0.13275 | 0.059509 | 121.5317 | -0.018311 | 121.5683 | 0.045776 | -121.6049 | -121.5775 | 121.5637 | 0.1236 | 1.5701 | 0.14648
1347.0938 | 121.7285 | -1.6205 | 120.0027 | -0.012131 | 0.00097838 | 0.055563 | 0.051306 | -0.0032599 | -0.008562 | -0.000673 | -0.0023192 | 0.027871 | 0.043276 | 0.013133 | 0.016393 | 0.025673 | -0.0055479 | -0.018311 | 119.9341 | -1.593 | 119.9295 | -1.4328 | -1.5701 | -1.5335 | -1.5106 | -1.5518 | -1.5701 | -1.5472 | -1.4648 | -1.4511 | -1.4557 | 0.027465 | -0.068665 | -0.073243 | 0.18768 | 0.086975 | 0.050354 | 0.05951 | 0.022889 | 0.050354 | -121.5546 | -121.55 | 0.15564 | 0.16479 | 0.16937 | 0.11444 | 0.11902 | 0.16022 | 121.5225 | 0.10529 | 0.022888 | 121.5271 | 0.01831 | 121.5546 | 0.068664 | -121.5958 | -121.5729 | 121.55 | 0.073242 | 1.6022 | 0.10986
1348.8594 | 121.6461 | -1.7166 | 119.9661 | -0.012131 | 0.0043964 | 0.055991 | 0.056646 | 0.0012261 | -0.0072802 | -0.0019546 | -0.005371 | 0.031503 | 0.044985 | 0.016979 | 0.017675 | 0.024819 | -0.0014891 | 0.027466 | 119.9203 | -1.7166 | 119.7647 | -1.6525 | -1.7578 | -1.7212 | -1.6937 | -1.5884 | -1.6663 | -1.6846 | -1.6434 | -1.6479 | -1.5793 | 0 | -0.045776 | -0.20142 | 0.064087 | -0.004577 | -0.041198 | -0.004577 | -0.041198 | 0.050354 | -121.5546 | -121.6507 | 0.073242 | 0.13733 | 0.068665 | 0.086975 | 0.018311 | 0.064087 | 121.4813 | 0.022888 | -0.01831 | 121.637 | 0.07782 | 121.637 | 0.12817 | -121.6827 | -121.6324 | 121.4813 | 0.032044 | 1.7441 | 0.022888
1350.5469 | 121.7056 | -1.6708 | 119.9661 | -0.012131 | 0.0014056 | 0.055777 | 0.05686 | 0.0016535 | -0.0066394 | -0.0038772 | -0.005371 | 0.027871 | 0.043703 | 0.016124 | 0.01853 | 0.023537 | -0.0038389 | -0.009155 | 119.9387 | -1.68 | 119.8242 | -1.561 | -1.7075 | -1.6708 | -1.6022 | -1.5793 | -1.6205 | -1.593 | -1.5335 | -1.5427 | -1.5106 | -0.009156 | -0.027465 | -0.14191 | 0.10986 | 0 | -0.036621 | 0.009156 | -0.027465 | 0.050354 | -121.5454 | -121.5591 | 0.13733 | 0.16022 | 0.12817 | 0.10986 | 0.077819 | 0.11902 | 121.5042 | 0.086975 | 0.027465 | 121.6187 | 0.041198 | 121.6095 | 0.091552 | -121.6461 | -121.5866 | 121.4951 | 0.077819 | 1.6617 | 0.068664
1352.3125 | 121.788 | -1.6205 | 120.0165 | -0.012131 | 0.00097838 | 0.053641 | 0.052374 | 0.00015814 | -0.010057 | -0.0004592 | -0.0084228 | 0.027871 | 0.043276 | 0.0062977 | 0.016607 | 0.026955 | -0.0042661 | 0.073242 | 119.9112 | -1.5976 | 119.989 | -1.3779 | -1.5015 | -1.5152 | -1.4511 | -1.5656 | -1.5747 | -1.5106 | -1.3916 | -1.3962 | -1.4328 | 0.022888 | -0.10529 | -0.027465 | 0.24261 | 0.10528 | 0.11902 | 0.082397 | 0.09613 | 0.045776 | -121.582 | -121.5271 | 0.22888 | 0.18768 | 0.2243 | 0.14191 | 0.17853 | 0.21973 | 121.5866 | 0.18311 | 0.064087 | 121.5088 | 0.009155 | 121.5317 | 0.054931 | -121.6141 | -121.5912 | 121.6095 | 0.10986 | 1.6937 | 0.16937
1354.0156 | 121.6919 | -1.6022 | 120.0806 | -0.01976 | 0.0037556 | 0.055777 | 0.056219 | 0.0020807 | -0.006853 | 0.0008224 | -0.005371 | 0.031503 | 0.043703 | 0.012706 | 0.017889 | 0.024178 | -0.0055479 | 0.10529 | 120.0165 | -1.6022 | 119.9203 | -1.4694 | -1.5884 | -1.5656 | -1.5289 | -1.5106 | -1.5656 | -1.5656 | -1.4374 | -1.474 | -1.442 | 0 | -0.064087 | -0.16022 | 0.13275 | 0.036621 | 0.013733 | 0.036621 | 0.013733 | 0.036621 | -121.5912 | -121.6461 | 0.1648 | 0.16022 | 0.12817 | 0.1236 | 0.091553 | 0.13275 | 121.5225 | 0.12817 | 0 | 121.6187 | 0.054932 | 121.6187 | 0.091553 | -121.6827 | -121.6461 | 121.5225 | 0.036621 | 1.7075 | 0.073242
1355.7812 | 121.7926 | -1.5472 | 120.0806 | -0.012131 | 0.00076478 | 0.054495 | 0.051306 | -5.5462e-05 | -0.0092028 | -0.002382 | -0.005371 | 0.02723 | 0.04178 | 0.0058703 | 0.015966 | 0.023964 | -0.0023435 | 0.07782 | 120.0027 | -1.5381 | 120.0439 | -1.2817 | -1.4236 | -1.4374 | -1.3824 | -1.5106 | -1.4877 | -1.4557 | -1.3138 | -1.3229 | -1.3596 | 0.009155 | -0.077819 | -0.036621 | 0.2655 | 0.10986 | 0.1236 | 0.10071 | 0.11444 | 0.059509 | -121.5912 | -121.5363 | 0.23346 | 0.18768 | 0.2243 | 0.12817 | 0.1648 | 0.25635 | 121.582 | 0.17395 | 0.032044 | 121.5408 | -0.022888 | 121.55 | 0.036621 | -121.6187 | -121.5683 | 121.5912 | 0.091553 | 1.6251 | 0.1648
1357.5469 | 121.788 | -1.5289 | 120.1172 | -0.0045011 | 0.001192 | 0.054068 | 0.053015 | -0.0017645 | -0.0077074 | -0.0008866 | -0.005371 | 0.027871 | 0.044771 | 0.0077929 | 0.014684 | 0.025673 | -0.0029843 | 0.022888 | 120.0165 | -1.5198 | 120.0348 | -1.3229 | -1.4511 | -1.4145 | -1.3916 | -1.4786 | -1.4877 | -1.4145 | -1.3092 | -1.3046 | -1.3321 | 0.009156 | -0.10071 | -0.082397 | 0.20599 | 0.11444 | 0.07782 | 0.10529 | 0.068664 | 0.041199 | -121.5958 | -121.5317 | 0.21973 | 0.19684 | 0.2243 | 0.15564 | 0.18311 | 0.19684 | 121.5546 | 0.17853 | 0.073242 | 121.5363 | 0.009155 | 121.5454 | 0.050354 | -121.637 | -121.6049 | 121.5637 | 0.11444 | 1.5518 | 0.13733
1359.3281 | 121.7651 | -1.5152 | 120.1172 | -0.012131 | 0.0014056 | 0.054495 | 0.050879 | -0.0013373 | -0.0081348 | -0.0025956 | 0.00073235 | 0.027017 | 0.042635 | 0.0097157 | 0.016393 | 0.024178 | -0.0055479 | -0.018311 | 120.0211 | -1.5106 | 120.0394 | -1.3321 | -1.4603 | -1.4328 | -1.4282 | -1.442 | -1.4603 | -1.4328 | -1.3184 | -1.3275 | -1.3092 | 0.004578 | -0.09613 | -0.077819 | 0.18311 | 0.082398 | 0.054932 | 0.07782 | 0.050354 | 0.054932 | -121.5591 | -121.55 | 0.19684 | 0.20599 | 0.18768 | 0.15106 | 0.13275 | 0.17853 | 121.55 | 0.14191 | 0.027466 | 121.5317 | 0.01831 | 121.5363 | 0.073242 | -121.6278 | -121.5775 | 121.5546 | 0.082398 | 1.4969 | 0.086975
1361.0938 | 121.7422 | -1.506 | 120.1218 | -0.0045011 | 0.0022602 | 0.056845 | 0.053656 | 0.00015814 | -0.0062122 | -0.0013138 | -0.0023192 | 0.029367 | 0.04413 | 0.0033069 | 0.016821 | 0.024819 | -0.0055479 | -0.004578 | 120.0439 | -1.4877 | 120.0348 | -1.3687 | -1.4694 | -1.4328 | -1.4145 | -1.4465 | -1.4603 | -1.4511 | -1.3321 | -1.3504 | -1.3412 | 0.01831 | -0.07782 | -0.086975 | 0.13733 | 0.073242 | 0.036621 | 0.054932 | 0.018311 | 0.045776 | -121.5683 | -121.5729 | 0.17395 | 0.16479 | 0.15564 | 0.11902 | 0.10986 | 0.11902 | 121.5225 | 0.12817 | 0.009155 | 121.5317 | 0.013733 | 121.55 | 0.059509 | -121.6095 | -121.582 | 121.5408 | 0.054931 | 1.5015 | 0.091552
1362.8594 | 121.6187 | -1.4923 | 120.2133 | -0.0045011 | 0.0048236 | 0.056204 | 0.05451 | 0.0042169 | -0.0083484 | -0.0015274 | -0.0023192 | 0.029367 | 0.043703 | 0.011638 | 0.020666 | 0.023537 | -0.0012753 | 0.036621 | 120.1355 | -1.474 | 119.9982 | -1.4099 | -1.5472 | -1.5152 | -1.4786 | -1.3779 | -1.4374 | -1.4969 | -1.4236 | -1.4374 | -1.387 | 0.018311 | -0.07782 | -0.21515 | 0.082398 | -0.022888 | -0.054931 | -0.041199 | -0.073242 | 0.054932 | -121.5912 | -121.7102 | 0.068665 | 0.10529 | 0.054932 | 0.050354 | 0 | 0.064087 | 121.4722 | 0.013733 | -0.059509 | 121.6095 | 0.059509 | 121.6278 | 0.11444 | -121.6873 | -121.6507 | 121.4905 | -0.004577 | 1.5289 | 0.013733
1364.5469 | 121.7926 | -1.4603 | 120.1721 | -0.0045011 | 0.0037556 | 0.054068 | 0.055151 | 0.0029351 | -0.0066394 | -0.0019546 | 0.00073235 | 0.029794 | 0.04413 | 0.0099293 | 0.017461 | 0.02546 | -0.0040525 | 0.050354 | 120.0943 | -1.442 | 120.1401 | -1.2589 | -1.3962 | -1.3687 | -1.3046 | -1.3962 | -1.387 | -1.3184 | -1.2543 | -1.268 | -1.2497 | 0.01831 | -0.07782 | -0.032043 | 0.20142 | 0.091553 | 0.064087 | 0.073243 | 0.045777 | 0.073242 | -121.5683 | -121.4905 | 0.20599 | 0.21057 | 0.19226 | 0.13733 | 0.11902 | 0.18311 | 121.582 | 0.13275 | 0.068665 | 121.5363 | -0.009155 | 121.5546 | 0.064087 | -121.6141 | -121.5591 | 121.6003 | 0.14191 | 1.5106 | 0.15564
1366.2969 | 121.701 | -1.474 | 120.2087 | -0.0045011 | 0.0048236 | 0.057913 | 0.055151 | 0.0050713 | -0.0066394 | -0.0019546 | -0.005371 | 0.027658 | 0.042849 | 0.015911 | 0.016607 | 0.023751 | -0.0027707 | 0.013733 | 120.1721 | -1.4603 | 120.0394 | -1.3596 | -1.4923 | -1.4694 | -1.3962 | -1.3641 | -1.4191 | -1.387 | -1.3184 | -1.3321 | -1.3 | 0.013733 | -0.036621 | -0.16937 | 0.11444 | 0.004578 | -0.018311 | -0.009155 | -0.032044 | 0.054932 | -121.5729 | -121.5958 | 0.15564 | 0.17395 | 0.14191 | 0.11902 | 0.086975 | 0.10071 | 121.4996 | 0.10071 | 0.032043 | 121.6324 | 0.054931 | 121.6461 | 0.10986 | -121.669 | -121.6278 | 121.5134 | 0.086975 | 1.4877 | 0.07782
1368.0469 | 121.7377 | -1.4374 | 120.2408 | -0.01976 | 0.001192 | 0.056418 | 0.052588 | -0.0013373 | -0.0062122 | -0.0008866 | -0.0023192 | 0.028726 | 0.043703 | 0.013774 | 0.017034 | 0.028664 | -0.0031979 | -0.013733 | 120.1401 | -1.4099 | 120.1172 | -1.268 | -1.4099 | -1.3687 | -1.3412 | -1.3412 | -1.3733 | -1.3458 | -1.268 | -1.2497 | -1.2451 | 0.027466 | -0.10071 | -0.1236 | 0.16937 | 0.068665 | 0.027466 | 0.041199 | 0 | 0.064087 | -121.582 | -121.5866 | 0.16937 | 0.19226 | 0.18768 | 0.12817 | 0.1236 | 0.14191 | 121.5271 | 0.10529 | 0.027466 | 121.55 | 0.032043 | 121.5775 | 0.09613 | -121.6507 | -121.6141 | 121.5546 | 0.091553 | 1.4236 | 0.09613
1369.75 | 121.6827 | -1.4603 | 120.2637 | -0.012131 | 0.0016192 | 0.056845 | 0.053228 | -0.0024055 | -0.0072802 | -0.0040908 | -0.005371 | 0.027658 | 0.042421 | 0.013774 | 0.017034 | 0.025246 | -0.0010617 | 0.086975 | 120.1675 | -1.4236 | 120.1172 | -1.268 | -1.4008 | -1.387 | -1.3367 | -1.3184 | -1.4008 | -1.387 | -1.3184 | -1.2955 | -1.3 | 0.036621 | -0.09613 | -0.14648 | 0.19226 | 0.073242 | 0.059509 | 0.036621 | 0.022888 | 0.059509 | -121.582 | -121.6507 | 0.14191 | 0.16022 | 0.1648 | 0.10071 | 0.10529 | 0.15564 | 121.5408 | 0.082398 | 0.013733 | 121.5912 | 0.082398 | 121.6278 | 0.14191 | -121.6873 | -121.6644 | 121.5775 | 0.073242 | 1.5472 | 0.1236
1371.5 | 121.8155 | -1.4511 | 120.2225 | -0.012131 | 0.0026874 | 0.054922 | 0.051733 | 0.0014397 | -0.0079212 | -0.0043046 | -0.0084228 | 0.028512 | 0.042849 | 0.012493 | 0.018316 | 0.024178 | -0.0027707 | 0.054932 | 120.1401 | -1.4282 | 120.1584 | -1.1948 | -1.3321 | -1.3092 | -1.1627 | -1.3229 | -1.3687 | -1.2405 | -1.1765 | -1.1307 | -1.1581 | 0.022888 | -0.082397 | -0.064087 | 0.25635 | 0.14191 | 0.11902 | 0.11902 | 0.096131 | 0.082398 | -121.5454 | -121.463 | 0.27466 | 0.29297 | 0.32044 | 0.21057 | 0.23804 | 0.23346 | 121.5866 | 0.19226 | 0.12817 | 121.5683 | 0.045776 | 121.5912 | 0.12817 | -121.6507 | -121.5912 | 121.6095 | 0.21057 | 1.506 | 0.28839
1373.2656 | 121.7102 | -1.474 | 120.2408 | -0.0045011 | 0.0041828 | 0.057486 | 0.055578 | 0.0037897 | -0.0066394 | -0.0038772 | -0.005371 | 0.03193 | 0.04114 | 0.017406 | 0.018316 | 0.022469 | -0.0044797 | 0.11902 | 120.1904 | -1.4648 | 120.0943 | -1.3138 | -1.4328 | -1.4282 | -1.2451 | -1.2497 | -1.4008 | -1.2772 | -1.2817 | -1.2131 | -1.1993 | 0.009155 | -0.050354 | -0.14648 | 0.16022 | 0.045776 | 0.041199 | 0.036621 | 0.032044 | 0.073242 | -121.4905 | -121.5179 | 0.19226 | 0.27466 | 0.26093 | 0.20142 | 0.18768 | 0.15106 | 121.5591 | 0.11902 | 0.1236 | 121.6553 | 0.15106 | 121.6644 | 0.2243 | -121.7056 | -121.6415 | 121.5683 | 0.19684 | 1.593 | 0.22888
1375.0312 | 121.6644 | -1.5015 | 120.2362 | -0.0045011 | 0.0037556 | 0.056845 | 0.054724 | 0.0010125 | -0.0066394 | -0.0025956 | -0.0084228 | 0.031717 | 0.044344 | 0.016338 | 0.019384 | 0.0261 | -0.0031979 | 0.009155 | 120.1813 | -1.4694 | 120.0302 | -1.4099 | -1.5198 | -1.4877 | -1.3092 | -1.2131 | -1.4328 | -1.3092 | -1.3687 | -1.2451 | -1.2177 | 0.032044 | -0.054932 | -0.20599 | 0.091553 | 0.013733 | -0.01831 | -0.018311 | -0.050354 | 0.068665 | -121.4493 | -121.5454 | 0.13275 | 0.28381 | 0.25635 | 0.21515 | 0.18768 | 0.059509 | 121.4996 | 0.064087 | 0.1236 | 121.6507 | 0.21973 | 121.6827 | 0.28839 | -121.7056 | -121.669 | 121.5317 | 0.19226 | 1.5106 | 0.19226
1376.7344 | 121.6873 | -1.4603 | 120.2774 | -0.012131 | 0.0052508 | 0.056418 | 0.056219 | 0.00015814 | -0.0047168 | -0.0019546 | -0.0084228 | 0.030221 | 0.04178 | 0.012279 | 0.019598 | 0.026741 | -0.0031979 | 0.10071 | 120.195 | -1.4282 | 120.1172 | -1.2817 | -1.4282 | -1.4053 | -1.2131 | -1.2222 | -1.3916 | -1.2543 | -1.2726 | -1.1765 | -1.1627 | 0.032043 | -0.082398 | -0.16022 | 0.17853 | 0.054932 | 0.032043 | 0.022889 | 0 | 0.068664 | -121.4996 | -121.5317 | 0.18768 | 0.29755 | 0.28381 | 0.22888 | 0.21515 | 0.14648 | 121.5454 | 0.11902 | 0.13733 | 121.6232 | 0.16937 | 121.6553 | 0.23804 | -121.7056 | -121.669 | 121.5775 | 0.20599 | 1.561 | 0.24719
1378.4844 | 121.8018 | -1.387 | 120.2545 | -0.012131 | 0.001833 | 0.05535 | 0.051733 | -0.0028327 | -0.0083484 | -0.0013138 | -0.0023192 | 0.026376 | 0.042849 | -0.0011791 | 0.017034 | 0.026528 | -0.00042085 | 0.022888 | 120.1675 | -1.3916 | 120.163 | -1.2085 | -1.3321 | -1.3138 | -1.1353 | -1.2222 | -1.3504 | -1.1673 | -1.1581 | -1.062 | -1.0849 | -0.004578 | -0.086975 | -0.091553 | 0.17853 | 0.073242 | 0.054932 | 0.07782 | 0.05951 | 0.036621 | -121.4767 | -121.4218 | 0.22888 | 0.30212 | 0.32501 | 0.2655 | 0.28839 | 0.18311 | 121.5546 | 0.19226 | 0.18311 | 121.5591 | 0.12817 | 121.5546 | 0.1648 | -121.6461 | -121.6049 | 121.55 | 0.21973 | 1.4099 | 0.25177
1380.2344 | 121.8063 | -1.4008 | 120.2454 | -0.0045011 | 0.0039692 | 0.059622 | 0.052801 | 0.0016535 | -0.0077074 | -0.0040908 | -0.0023192 | 0.029794 | 0.043276 | 0.0095019 | 0.018102 | 0.027596 | 0.00086095 | 0.054932 | 120.2087 | -1.4008 | 120.195 | -1.1993 | -1.3321 | -1.3046 | -1.1078 | -1.2405 | -1.3367 | -1.1627 | -1.1673 | -1.0757 | -1.0712 | 0 | -0.036621 | -0.050354 | 0.20142 | 0.096131 | 0.068665 | 0.096131 | 0.068665 | 0.064087 | -121.4859 | -121.4081 | 0.23346 | 0.32959 | 0.32501 | 0.2655 | 0.26093 | 0.20142 | 121.5958 | 0.16937 | 0.17395 | 121.6095 | 0.09613 | 121.6095 | 0.16022 | -121.6461 | -121.582 | 121.5958 | 0.23804 | 1.4557 | 0.29297
1381.9844 | 121.8338 | -1.3916 | 120.282 | -0.012131 | -0.001585 | 0.054709 | 0.051092 | -0.00048286 | -0.0064258 | -0.0028092 | -0.005371 | 0.028512 | 0.040712 | 0.017406 | 0.017461 | 0.027596 | -0.0049069 | 0.059509 | 120.195 | -1.3733 | 120.2316 | -1.1261 | -1.2634 | -1.2405 | -1.0895 | -1.2268 | -1.3458 | -1.1398 | -1.1078 | -1.0391 | -1.0574 | 0.018311 | -0.086975 | -0.050354 | 0.2655 | 0.15106 | 0.12817 | 0.13275 | 0.10986 | 0.045777 | -121.5088 | -121.4218 | 0.28381 | 0.33417 | 0.35248 | 0.28839 | 0.3067 | 0.24719 | 121.6049 | 0.23804 | 0.20599 | 121.5683 | 0.11902 | 121.5866 | 0.1648 | -121.6553 | -121.6278 | 121.6232 | 0.25177 | 1.4511 | 0.30212
1383.6719 | 121.6827 | -1.4236 | 120.3323 | -0.012131 | -0.00030342 | 0.055991 | 0.053015 | 0.0033623 | -0.006853 | -0.0028092 | 0.00073235 | 0.029794 | 0.040285 | 0.0062977 | 0.014684 | 0.024819 | -0.0025571 | 0.036621 | 120.2225 | -1.3916 | 120.1355 | -1.2817 | -1.3962 | -1.3596 | -1.236 | -1.1627 | -1.3641 | -1.2634 | -1.2543 | -1.1581 | -1.1627 | 0.032043 | -0.10986 | -0.19684 | 0.14191 | 0.064087 | 0.027466 | 0.032044 | -0.004577 | 0.059509 | -121.4951 | -121.5958 | 0.16937 | 0.26093 | 0.2655 | 0.20142 | 0.20599 | 0.10986 | 121.5271 | 0.10986 | 0.10071 | 121.6141 | 0.20142 | 121.6461 | 0.26093 | -121.7239 | -121.6965 | 121.5591 | 0.16022 | 1.4603 | 0.18768
1385.4219 | 121.7697 | -1.355 | 120.3278 | -0.012131 | 0.0041828 | 0.053214 | 0.052588 | 0.0010125 | -0.006853 | -0.005159 | -0.005371 | 0.028085 | 0.04413 | 0.0099293 | 0.017034 | 0.026314 | -0.0021299 | 0.041199 | 120.2408 | -1.3184 | 120.2682 | -1.1032 | -1.3 | -1.2451 | -1.0529 | -1.1856 | -1.2817 | -1.1398 | -1.1398 | -1.0483 | -1.0483 | 0.036621 | -0.086975 | -0.059509 | 0.25177 | 0.10986 | 0.054931 | 0.073242 | 0.01831 | 0.073242 | -121.5134 | -121.4676 | 0.21515 | 0.3067 | 0.3067 | 0.23346 | 0.23346 | 0.21515 | 121.5866 | 0.14191 | 0.14191 | 121.5591 | 0.09613 | 121.5958 | 0.16937 | -121.6461 | -121.6095 | 121.6232 | 0.21515 | 1.3962 | 0.30212
1387.1875 | 121.7377 | -1.3275 | 120.3735 | -0.0045011 | 0.00461 | 0.056204 | 0.055151 | -0.00048286 | -0.006853 | -0.0025956 | -0.0084228 | 0.031717 | 0.043703 | 0.013988 | 0.017034 | 0.023537 | -0.0029843 | 0.082397 | 120.3278 | -1.3184 | 120.2316 | -1.1948 | -1.2909 | -1.2772 | -1.1398 | -1.1078 | -1.2772 | -1.1536 | -1.1627 | -1.0803 | -1.0483 | 0.009156 | -0.045776 | -0.14191 | 0.13275 | 0.050354 | 0.036621 | 0.041198 | 0.027465 | 0.050354 | -121.4813 | -121.5271 | 0.1648 | 0.27924 | 0.24719 | 0.22888 | 0.19684 | 0.1236 | 121.55 | 0.11444 | 0.1236 | 121.6461 | 0.16937 | 121.6553 | 0.21973 | -121.6919 | -121.6507 | 121.5591 | 0.17395 | 1.4099 | 0.18768
1388.9531 | 121.7834 | -1.2955 | 120.3644 | -0.012131 | 0.0048236 | 0.054709 | 0.053656 | 0.0014397 | -0.0055712 | -0.000673 | -0.0023192 | 0.028512 | 0.042208 | 0.0090747 | 0.017034 | 0.025246 | -0.0029843 | 0.041199 | 120.314 | -1.268 | 120.314 | -1.062 | -1.2405 | -1.1948 | -1.0345 | -1.1581 | -1.2268 | -1.0757 | -1.0803 | -1.0025 | -0.99335 | 0.027466 | -0.050354 | -0.050354 | 0.23346 | 0.10071 | 0.054931 | 0.073242 | 0.027465 | 0.068664 | -121.5225 | -121.4401 | 0.21515 | 0.30212 | 0.29297 | 0.23346 | 0.2243 | 0.20599 | 121.582 | 0.14648 | 0.15106 | 121.582 | 0.068665 | 121.6095 | 0.13733 | -121.6324 | -121.5912 | 121.6095 | 0.21973 | 1.3367 | 0.26093
1390.6406 | 121.8018 | -1.2955 | 120.3964 | 0.0031279 | 0.0024738 | 0.054922 | 0.05216 | -0.0011237 | -0.0070666 | -0.0021682 | -0.0023192 | 0.028085 | 0.040712 | 0.0095019 | 0.014257 | 0.025887 | 0.0012881 | -0.004578 | 120.3506 | -1.2726 | 120.2866 | -1.1169 | -1.2405 | -1.1902 | -1.0666 | -1.1307 | -1.2314 | -1.0941 | -1.0712 | -0.98419 | -0.98419 | 0.022888 | -0.045776 | -0.10986 | 0.17853 | 0.10529 | 0.054931 | 0.082397 | 0.032043 | 0.064087 | -121.5271 | -121.4905 | 0.2243 | 0.31128 | 0.31128 | 0.24719 | 0.24719 | 0.15564 | 121.5591 | 0.16022 | 0.13733 | 121.6232 | 0.10071 | 121.6461 | 0.1648 | -121.669 | -121.6278 | 121.582 | 0.20142 | 1.2909 | 0.22888
1392.3906 | 121.7972 | -1.2451 | 120.4239 | 0.0031279 | 0.00076478 | 0.054068 | 0.051306 | 0.00079894 | -0.0092028 | -0.0013138 | -0.005371 | 0.028299 | 0.043062 | 0.012706 | 0.015752 | 0.026314 | -0.0042661 | 0.082397 | 120.3278 | -1.2405 | 120.3644 | -1.0208 | -1.149 | -1.1307 | -0.98419 | -1.1078 | -1.1948 | -1.0483 | -1.0162 | -0.94299 | -0.96588 | 0.004577 | -0.09613 | -0.059509 | 0.2243 | 0.11444 | 0.09613 | 0.10986 | 0.091553 | 0.050354 | -121.5317 | -121.4722 | 0.22888 | 0.27924 | 0.30212 | 0.22888 | 0.25177 | 0.21973 | 121.6049 | 0.17853 | 0.14648 | 121.5683 | 0.086975 | 121.5729 | 0.13733 | -121.6644 | -121.6187 | 121.6095 | 0.19684 | 1.3275 | 0.26093
1394.1562 | 121.6782 | -1.2772 | 120.4697 | -0.01976 | 0.0054644 | 0.056418 | 0.057287 | -0.0030463 | -0.0057848 | -0.0025956 | -0.005371 | 0.031503 | 0.042849 | 0.010997 | 0.017034 | 0.0261 | -0.0023435 | 0.059509 | 120.4147 | -1.2543 | 120.2682 | -1.1627 | -1.2955 | -1.2772 | -1.1261 | -1.0574 | -1.2085 | -1.149 | -1.1627 | -1.0986 | -1.0529 | 0.022889 | -0.054932 | -0.20142 | 0.11444 | 0 | -0.01831 | -0.022889 | -0.041199 | 0.068665 | -121.5271 | -121.6187 | 0.11444 | 0.2243 | 0.17853 | 0.15564 | 0.10986 | 0.091552 | 121.5225 | 0.045776 | 0.059509 | 121.669 | 0.15106 | 121.6919 | 0.21973 | -121.7239 | -121.6782 | 121.5454 | 0.12817 | 1.3367 | 0.15106
1395.9219 | 121.7102 | -1.2589 | 120.4834 | -0.0045011 | 0.0024738 | 0.054709 | 0.056006 | 0.0010125 | -0.010271 | -0.0021682 | -0.0023192 | 0.030648 | 0.041353 | 0.015056 | 0.017461 | 0.025246 | 0.00086095 | 0.054932 | 120.4193 | -1.2634 | 120.2957 | -1.149 | -1.2543 | -1.2268 | -1.1169 | -1.0437 | -1.2085 | -1.1124 | -1.1078 | -1.0254 | -1.0025 | -0.004578 | -0.064086 | -0.18768 | 0.10986 | 0.032043 | 0.004578 | 0.036621 | 0.009156 | 0.050354 | -121.5271 | -121.5958 | 0.15106 | 0.25635 | 0.23346 | 0.20599 | 0.18311 | 0.11444 | 121.5591 | 0.10071 | 0.09613 | 121.6827 | 0.1648 | 121.6782 | 0.21515 | -121.7468 | -121.6919 | 121.5546 | 0.14648 | 1.3138 | 0.14191
1397.625 | 121.8063 | -1.1856 | 120.4834 | -0.012131 | 0.0014056 | 0.055777 | 0.050665 | -0.0034735 | -0.0087756 | -0.0043046 | -0.011475 | 0.028085 | 0.042421 | 0.0097157 | 0.017248 | 0.025673 | -0.0053343 | 0 | 120.4056 | -1.1627 | 120.3918 | -1.0208 | -1.1398 | -1.1124 | -0.98419 | -1.0391 | -1.1307 | -0.98419 | -0.96588 | -0.87433 | -0.89264 | 0.022888 | -0.077819 | -0.091552 | 0.1648 | 0.073242 | 0.045776 | 0.050354 | 0.022888 | 0.054932 | -121.5225 | -121.4676 | 0.21973 | 0.29297 | 0.31128 | 0.23804 | 0.25635 | 0.14191 | 121.5546 | 0.1648 | 0.14648 | 121.5683 | 0.091552 | 121.5912 | 0.14648 | -121.6461 | -121.6141 | 121.5775 | 0.20142 | 1.1856 | 0.20142
1399.375 | 121.7194 | -1.2177 | 120.5475 | -0.012131 | 0.0039692 | 0.054068 | 0.053656 | -0.0053961 | -0.0081348 | -0.002382 | -0.005371 | 0.033639 | 0.043062 | 0.0075793 | 0.018316 | 0.025673 | -0.0014891 | 0.018311 | 120.4926 | -1.1719 | 120.3278 | -1.1124 | -1.2405 | -1.1993 | -1.0849 | -0.97504 | -1.1353 | -1.0574 | -1.0803 | -1.0162 | -0.97046 | 0.045776 | -0.054931 | -0.21973 | 0.10529 | 0.01831 | -0.022889 | -0.027466 | -0.068665 | 0.082397 | -121.5225 | -121.6049 | 0.13733 | 0.24719 | 0.20142 | 0.1648 | 0.11902 | 0.059509 | 121.4996 | 0.054932 | 0.07782 | 121.6644 | 0.16022 | 121.7102 | 0.24261 | -121.7194 | -121.6827 | 121.5454 | 0.16022 | 1.236 | 0.13275
1401.1406 | 121.8063 | -1.149 | 120.5292 | -0.012131 | 0.0026874 | 0.056845 | 0.052374 | 0.0018671 | -0.0062122 | -3.1996e-05 | 0.00073235 | 0.029794 | 0.042421 | 0.0080067 | 0.017675 | 0.027809 | -0.0031979 | 0.036621 | 120.4697 | -1.1307 | 120.4697 | -0.92926 | -1.0712 | -1.0391 | -0.88806 | -1.0071 | -1.1032 | -0.93842 | -0.93842 | -0.86975 | -0.86975 | 0.018311 | -0.059509 | -0.059509 | 0.21973 | 0.10986 | 0.07782 | 0.091552 | 0.059509 | 0.045777 | -121.5363 | -121.4676 | 0.21057 | 0.27924 | 0.27924 | 0.23346 | 0.23346 | 0.20142 | 121.6003 | 0.16479 | 0.16479 | 121.6003 | 0.09613 | 121.6187 | 0.14191 | -121.6599 | -121.6324 | 121.6187 | 0.21057 | 1.1856 | 0.26092
1402.8906 | 121.8109 | -1.1261 | 120.5521 | -0.01976 | 0.002901 | 0.056631 | 0.053228 | -0.0045417 | -0.0066394 | -0.002382 | -0.0023192 | 0.02958 | 0.043062 | 0.010143 | 0.018743 | 0.025887 | -0.00084805 | 0.050354 | 120.4651 | -1.1032 | 120.5063 | -0.89722 | -1.0529 | -1.03 | -0.85602 | -1.0071 | -1.0941 | -0.91095 | -0.90179 | -0.85144 | -0.84228 | 0.022889 | -0.086975 | -0.045776 | 0.22888 | 0.096131 | 0.073243 | 0.073242 | 0.050354 | 0.032044 | -121.5591 | -121.463 | 0.2243 | 0.28381 | 0.27466 | 0.25177 | 0.24262 | 0.20599 | 121.6095 | 0.19226 | 0.1831 | 121.5683 | 0.086975 | 121.5912 | 0.11902 | -121.6553 | -121.6461 | 121.6324 | 0.21515 | 1.1765 | 0.27008
1404.5781 | 121.7148 | -1.1673 | 120.5658 | -0.012131 | 0.0043964 | 0.055563 | 0.052588 | 0.00015814 | -0.0087756 | -0.0013138 | -0.005371 | 0.031076 | 0.042421 | 0.010143 | 0.015752 | 0.025032 | -0.0036253 | -0.004578 | 120.5154 | -1.1581 | 120.3827 | -1.0757 | -1.2085 | -1.1719 | -1.0391 | -0.96588 | -1.1261 | -1.0254 | -1.0345 | -0.97046 | -0.92468 | 0.009155 | -0.050354 | -0.18311 | 0.091552 | -0.004578 | -0.041199 | -0.013733 | -0.050354 | 0.041198 | -121.5317 | -121.5912 | 0.13275 | 0.24261 | 0.19684 | 0.20142 | 0.15564 | 0.082397 | 121.5408 | 0.091553 | 0.10071 | 121.6736 | 0.16022 | 121.6827 | 0.20142 | -121.7239 | -121.6919 | 121.55 | 0.14191 | 1.1627 | 0.12817
1406.3438 | 121.7972 | -1.1536 | 120.5612 | -0.012131 | 0.0020466 | 0.055563 | 0.05216 | 0.0052851 | -0.0062122 | -0.002382 | -0.005371 | 0.028939 | 0.044771 | 0.0060841 | 0.016821 | 0.0261 | 6.346e-06 | 0 | 120.4834 | -1.1444 | 120.4376 | -0.98877 | -1.1078 | -1.0757 | -0.95673 | -0.97961 | -1.0895 | -0.97504 | -0.94299 | -0.84228 | -0.87433 | 0.009155 | -0.07782 | -0.1236 | 0.16479 | 0.077819 | 0.045776 | 0.068664 | 0.036621 | 0.064086 | -121.5408 | -121.5363 | 0.21057 | 0.27924 | 0.31128 | 0.21515 | 0.24719 | 0.15564 | 121.582 | 0.14648 | 0.11444 | 121.6278 | 0.10986 | 121.637 | 0.17395 | -121.7056 | -121.6507 | 121.5912 | 0.17853 | 1.1536 | 0.19684
1408.0938 | 121.7194 | -1.1673 | 120.6162 | -0.012131 | 0.002901 | 0.055136 | 0.056433 | -0.0030463 | -0.0087756 | -0.002382 | -0.005371 | 0.032785 | 0.045626 | 0.010997 | 0.017461 | 0.024605 | -0.0040525 | 0.045776 | 120.5246 | -1.1444 | 120.3873 | -1.0574 | -1.149 | -1.1398 | -1.03 | -0.93842 | -1.1169 | -1.0254 | -0.99335 | -0.94299 | -0.90637 | 0.022888 | -0.091553 | -0.22888 | 0.10986 | 0.027465 | 0.01831 | 0.004577 | -0.004578 | 0.050354 | -121.5546 | -121.6415 | 0.17395 | 0.26093 | 0.2243 | 0.21057 | 0.17395 | 0.086975 | 121.5317 | 0.1236 | 0.091552 | 121.669 | 0.17853 | 121.6919 | 0.22888 | -121.7606 | -121.7331 | 121.5546 | 0.14191 | 1.2131 | 0.13733
1409.8438 | 121.7148 | -1.1856 | 120.6024 | -0.012131 | 0.00033758 | 0.054922 | 0.053656 | 0.0035761 | -0.0077074 | -0.00345 | -0.005371 | 0.030862 | 0.044985 | 0.0077929 | 0.01853 | 0.025032 | -0.0017027 | 0.050354 | 120.5109 | -1.1536 | 120.3964 | -1.0391 | -1.149 | -1.1169 | -1.0117 | -0.95215 | -1.1032 | -1.0483 | -1.0162 | -0.94299 | -0.94757 | 0.032044 | -0.091553 | -0.20599 | 0.14648 | 0.068665 | 0.036621 | 0.036621 | 0.004577 | 0.082398 | -121.5546 | -121.6507 | 0.16937 | 0.23804 | 0.24262 | 0.15564 | 0.16022 | 0.11444 | 121.55 | 0.086975 | 0.054931 | 121.6644 | 0.15106 | 121.6965 | 0.23346 | -121.756 | -121.7056 | 121.582 | 0.13733 | 1.236 | 0.17395
1411.5312 | 121.6873 | -1.1993 | 120.5933 | -0.0045011 | 0.0061054 | 0.055777 | 0.057074 | 0.0033623 | -0.0074938 | -0.0030228 | -0.005371 | 0.032571 | 0.043703 | 0.0039477 | 0.018743 | 0.023537 | -0.0029843 | 0.054932 | 120.5383 | -1.1536 | 120.369 | -1.0895 | -1.2268 | -1.1719 | -1.0529 | -0.94299 | -1.1307 | -1.0391 | -1.062 | -1.0025 | -0.95215 | 0.045777 | -0.054932 | -0.2243 | 0.10986 | 0.027466 | -0.027466 | -0.018311 | -0.073243 | 0.068665 | -121.5363 | -121.6324 | 0.13733 | 0.24719 | 0.19684 | 0.17853 | 0.12817 | 0.064086 | 121.5225 | 0.068664 | 0.091552 | 121.6919 | 0.18768 | 121.7377 | 0.25635 | -121.7468 | -121.7239 | 121.5683 | 0.16022 | 1.2543 | 0.14648
1413.2969 | 121.7514 | -1.1307 | 120.6207 | -0.0045011 | 0.0035418 | 0.055777 | 0.055365 | 0.0025079 | -0.006853 | -0.0015274 | -0.011475 | 0.032998 | 0.04178 | 0.015697 | 0.017248 | 0.025673 | -0.0029843 | 0.009155 | 120.5795 | -1.1215 | 120.4102 | -1.03 | -1.1627 | -1.1353 | -0.97046 | -0.93842 | -1.0757 | -0.97504 | -0.95673 | -0.90179 | -0.86975 | 0.009155 | -0.041199 | -0.21057 | 0.10071 | -0.004578 | -0.032044 | -0.013733 | -0.041199 | 0.054931 | -121.5591 | -121.5958 | 0.17395 | 0.26092 | 0.22888 | 0.20599 | 0.17395 | 0.091553 | 121.5317 | 0.11902 | 0.10071 | 121.701 | 0.13733 | 121.7102 | 0.19226 | -121.7422 | -121.6965 | 121.5408 | 0.15564 | 1.1398 | 0.16022
1415.0625 | 121.7331 | -1.0986 | 120.6665 | -0.01976 | 0.0039692 | 0.055991 | 0.055365 | -0.0019781 | -0.0042896 | -0.005159 | -0.005371 | 0.032785 | 0.041994 | 0.0099293 | 0.01853 | 0.029091 | 6.346e-06 | 0.004578 | 120.5887 | -1.1078 | 120.4422 | -0.98877 | -1.1353 | -1.0941 | -0.95215 | -0.91095 | -1.0529 | -0.95215 | -0.94299 | -0.89722 | -0.85144 | -0.009155 | -0.07782 | -0.2243 | 0.10986 | 0.004578 | -0.036621 | 0.013733 | -0.027466 | 0.045777 | -121.5775 | -121.6187 | 0.15564 | 0.24719 | 0.20142 | 0.20142 | 0.15564 | 0.11902 | 121.55 | 0.10986 | 0.10071 | 121.6965 | 0.14191 | 121.6873 | 0.18768 | -121.7743 | -121.7194 | 121.5408 | 0.14648 | 1.1032 | 0.14648
1416.8281 | 121.7422 | -1.0941 | 120.6619 | -0.012131 | 0.0035418 | 0.055991 | 0.053656 | 0.00079894 | -0.0077074 | -0.0036636 | -0.005371 | 0.034707 | 0.04114 | 0.0067249 | 0.01853 | 0.025673 | -0.00020725 | 0.086975 | 120.5841 | -1.0712 | 120.5063 | -0.92468 | -1.0666 | -1.0391 | -0.87433 | -0.90637 | -1.03 | -0.93384 | -0.89264 | -0.86517 | -0.83313 | 0.022888 | -0.07782 | -0.15564 | 0.16937 | 0.054931 | 0.027466 | 0.032043 | 0.004578 | 0.064087 | -121.5683 | -121.5958 | 0.20142 | 0.26092 | 0.22888 | 0.19684 | 0.1648 | 0.14648 | 121.5775 | 0.13733 | 0.09613 | 121.6553 | 0.1236 | 121.6782 | 0.18768 | -121.7331 | -121.6919 | 121.6003 | 0.16022 | 1.181 | 0.21973
1418.5312 | 121.8246 | -1.062 | 120.6436 | 0.0031279 | 0.00076478 | 0.054922 | 0.050024 | 0.0010125 | -0.0081348 | -0.0032364 | -0.0023192 | 0.031717 | 0.041567 | -0.0013927 | 0.016821 | 0.025887 | -0.0051205 | 0.091553 | 120.5658 | -1.03 | 120.5933 | -0.82855 | -0.95215 | -0.92926 | -0.82398 | -0.9201 | -0.99792 | -0.86517 | -0.79193 | -0.75531 | -0.79193 | 0.032044 | -0.07782 | -0.050354 | 0.23346 | 0.13275 | 0.10986 | 0.10071 | 0.07782 | 0.064087 | -121.5637 | -121.5088 | 0.27008 | 0.27008 | 0.3067 | 0.20599 | 0.24261 | 0.20142 | 121.6232 | 0.20599 | 0.13275 | 121.5958 | 0.07782 | 121.6278 | 0.14191 | -121.6736 | -121.6415 | 121.6553 | 0.19684 | 1.1536 | 0.23804
1420.2812 | 121.8384 | -1.0437 | 120.6528 | -0.012131 | 0.00461 | 0.056845 | 0.053656 | 0.0018671 | -0.0053576 | -0.0032364 | -0.005371 | 0.030862 | 0.043062 | 0.0045887 | 0.018102 | 0.028237 | -0.0046933 | 0.054932 | 120.6024 | -1.03 | 120.5978 | -0.8194 | -0.98419 | -0.94757 | -0.79193 | -0.91095 | -0.99335 | -0.8194 | -0.77362 | -0.74158 | -0.74616 | 0.013733 | -0.050354 | -0.054932 | 0.2243 | 0.09613 | 0.059509 | 0.082397 | 0.045776 | 0.050354 | -121.5637 | -121.4722 | 0.27008 | 0.29755 | 0.30212 | 0.24719 | 0.25177 | 0.21057 | 121.6278 | 0.21973 | 0.17395 | 121.6324 | 0.082397 | 121.6461 | 0.13275 | -121.6827 | -121.6461 | 121.6415 | 0.2243 | 1.0986 | 0.25177
1422.0469 | 121.7239 | -1.0666 | 120.6894 | -0.012131 | 0.0031146 | 0.057486 | 0.053869 | 0.0012261 | -0.0066394 | -0.0045182 | 0.00073235 | 0.034066 | 0.042635 | 0.011424 | 0.016821 | 0.024605 | -0.0046933 | 0.013733 | 120.6528 | -1.0437 | 120.4834 | -0.9613 | -1.1032 | -1.0483 | -0.91095 | -0.8606 | -1.0071 | -0.91095 | -0.90179 | -0.84686 | -0.81482 | 0.022888 | -0.036621 | -0.20599 | 0.10528 | 0.01831 | -0.036621 | -0.004578 | -0.059509 | 0.059509 | -121.55 | -121.6003 | 0.1648 | 0.25177 | 0.21973 | 0.19226 | 0.16022 | 0.082397 | 121.5271 | 0.10529 | 0.09613 | 121.6965 | 0.14648 | 121.7194 | 0.20599 | -121.7331 | -121.6965 | 121.55 | 0.15564 | 1.0803 | 0.15564
1423.8281 | 121.7148 | -1.1124 | 120.7169 | -0.0045011 | 0.0022602 | 0.05535 | 0.054083 | 0.0012261 | -0.01198 | -0.0047318 | -0.005371 | 0.032571 | 0.042849 | 0.0060841 | 0.015539 | 0.0261 | 0.00043375 | 0.050354 | 120.6253 | -1.0849 | 120.4742 | -0.97046 | -1.0712 | -1.0529 | -0.94299 | -0.84228 | -1.0162 | -0.95215 | -0.89264 | -0.84686 | -0.83771 | 0.027466 | -0.091553 | -0.24262 | 0.14191 | 0.05951 | 0.041199 | 0.032044 | 0.013733 | 0.096131 | -121.5591 | -121.669 | 0.21973 | 0.27466 | 0.2655 | 0.17853 | 0.16937 | 0.11444 | 121.5591 | 0.1236 | 0.064087 | 121.7102 | 0.17395 | 121.7377 | 0.27008 | -121.8018 | -121.7331 | 121.5866 | 0.16022 | 1.1627 | 0.16937
1425.5156 | 121.7285 | -1.0574 | 120.7306 | -0.012131 | 0.0016192 | 0.056204 | 0.052374 | -0.0015509 | -0.0094164 | -0.00345 | 0.0037842 | 0.032998 | 0.043062 | 0.011424 | 0.016821 | 0.025032 | -0.0038389 | 0.041199 | 120.6528 | -1.0162 | 120.52 | -0.92468 | -1.0437 | -1.0391 | -0.88806 | -0.82398 | -0.98877 | -0.94299 | -0.8606 | -0.82855 | -0.81482 | 0.041199 | -0.07782 | -0.21057 | 0.13275 | 0.01831 | 0.013733 | -0.022889 | -0.027466 | 0.068664 | -121.5546 | -121.6736 | 0.19684 | 0.24262 | 0.22888 | 0.17395 | 0.16022 | 0.091552 | 121.5363 | 0.12817 | 0.045777 | 121.669 | 0.1648 | 121.7102 | 0.23346 | -121.7468 | -121.7194 | 121.5775 | 0.11444 | 1.0986 | 0.16937
1427.2656 | 121.7285 | -1.03 | 120.7489 | -0.01976 | 0.0033282 | 0.054709 | 0.056006 | -5.5462e-05 | -0.0081348 | -0.0053726 | -0.0023192 | 0.034921 | 0.041353 | 0.0099293 | 0.017248 | 0.02546 | -0.0027707 | 0.009155 | 120.6757 | -0.99792 | 120.5292 | -0.93842 | -1.0529 | -1.0208 | -0.88806 | -0.80109 | -0.98419 | -0.87891 | -0.84228 | -0.8194 | -0.78278 | 0.032043 | -0.073242 | -0.21973 | 0.091552 | 0.009155 | -0.022888 | -0.022888 | -0.054931 | 0.045776 | -121.55 | -121.6278 | 0.18768 | 0.24719 | 0.21057 | 0.20142 | 0.16479 | 0.059509 | 121.5271 | 0.14191 | 0.10529 | 121.6736 | 0.18311 | 121.7056 | 0.22888 | -121.7468 | -121.7331 | 121.5591 | 0.15106 | 1.0391 | 0.14191
1429.0312 | 121.756 | -1.0162 | 120.7306 | -0.0045011 | 0.001833 | 0.055136 | 0.053442 | 0.0018671 | -0.0079212 | 0.001036 | -0.005371 | 0.032571 | 0.040499 | 0.012279 | 0.017889 | 0.023537 | -0.0027707 | 0.082397 | 120.694 | -1.0071 | 120.5704 | -0.86517 | -0.98877 | -0.97046 | -0.82855 | -0.79651 | -0.96588 | -0.83313 | -0.76904 | -0.75531 | -0.73242 | 0.009155 | -0.036621 | -0.16022 | 0.15106 | 0.045776 | 0.027465 | 0.036621 | 0.01831 | 0.050354 | -121.5271 | -121.5637 | 0.24719 | 0.28381 | 0.26092 | 0.23346 | 0.21057 | 0.14191 | 121.5775 | 0.19684 | 0.13275 | 121.701 | 0.16937 | 121.7102 | 0.21973 | -121.7377 | -121.6965 | 121.5866 | 0.1831 | 1.0986 | 0.18768
1430.7188 | 121.7056 | -1.0025 | 120.7535 | -0.012131 | 0.00461 | 0.056204 | 0.052588 | 0.0020807 | -0.0077074 | -0.0021682 | -0.005371 | 0.032785 | 0.042849 | 0.012493 | 0.016607 | 0.025673 | -0.00063445 | 0.022888 | 120.7077 | -1.0117 | 120.5338 | -0.95673 | -1.0529 | -1.0254 | -0.91095 | -0.79651 | -0.9613 | -0.86975 | -0.8194 | -0.81024 | -0.76446 | -0.009156 | -0.045776 | -0.21973 | 0.045776 | -0.022889 | -0.050354 | -0.013733 | -0.041198 | 0.041198 | -121.55 | -121.6232 | 0.1831 | 0.23804 | 0.19226 | 0.19684 | 0.15106 | 0.054932 | 121.5454 | 0.14191 | 0.091553 | 121.7194 | 0.1648 | 121.7102 | 0.20599 | -121.7651 | -121.7148 | 121.5363 | 0.13275 | 1.0254 | 0.091552
1432.4688 | 121.7056 | -1.0345 | 120.7352 | -0.01976 | 0.0041828 | 0.055991 | 0.056219 | 0.00079894 | -0.0081348 | -0.0032364 | 0.00073235 | 0.032144 | 0.042849 | 0.0062977 | 0.020239 | 0.025246 | -0.00063445 | 0.018311 | 120.7123 | -0.98419 | 120.5429 | -0.92468 | -1.0529 | -1.0254 | -0.86517 | -0.75989 | -0.97046 | -0.83771 | -0.80566 | -0.78278 | -0.737 | 0.050354 | -0.022888 | -0.19226 | 0.10986 | 0.009155 | -0.01831 | -0.041199 | -0.068664 | 0.064087 | -121.4951 | -121.5729 | 0.22888 | 0.29755 | 0.25177 | 0.23346 | 0.18768 | 0.059509 | 121.5271 | 0.16479 | 0.13275 | 121.6965 | 0.21057 | 121.7468 | 0.27466 | -121.7194 | -121.7056 | 121.5775 | 0.19684 | 1.0529 | 0.16937
1434.2188 | 121.7697 | -1.0208 | 120.7489 | -0.0045011 | 0.0054644 | 0.056204 | 0.054937 | 0.0057123 | -0.006853 | -0.0002456 | -0.0023192 | 0.03193 | 0.04413 | 0.0056567 | 0.019598 | 0.025673 | 0.00043375 | 0.10529 | 120.6711 | -1.0025 | 120.5933 | -0.85144 | -0.98877 | -0.96588 | -0.76904 | -0.75531 | -0.95215 | -0.7782 | -0.67291 | -0.69122 | -0.67291 | 0.018311 | -0.077819 | -0.15564 | 0.16937 | 0.054932 | 0.032043 | 0.036621 | 0.013732 | 0.068665 | -121.5042 | -121.5271 | 0.3479 | 0.3479 | 0.32959 | 0.27924 | 0.26092 | 0.15106 | 121.5958 | 0.27924 | 0.17395 | 121.6736 | 0.19684 | 121.6919 | 0.2655 | -121.7514 | -121.701 | 121.6141 | 0.24262 | 1.1261 | 0.25177
1435.9688 | 121.8796 | -0.98877 | 120.7306 | 0.0031279 | -0.00051702 | 0.053427 | 0.05152 | -0.0011237 | -0.0057848 | -0.002382 | -0.005371 | 0.028939 | 0.042208 | 0.0060841 | 0.01618 | 0.028664 | -0.0034117 | 0.032043 | 120.6436 | -0.95215 | 120.6528 | -0.75073 | -0.86975 | -0.85144 | -0.65918 | -0.7782 | -0.93384 | -0.68665 | -0.59052 | -0.56305 | -0.59052 | 0.036622 | -0.086975 | -0.07782 | 0.23804 | 0.13733 | 0.11902 | 0.10071 | 0.082397 | 0.054932 | -121.5088 | -121.4172 | 0.39826 | 0.39826 | 0.42572 | 0.34332 | 0.37079 | 0.20142 | 121.6049 | 0.34332 | 0.24719 | 121.5958 | 0.15564 | 121.6324 | 0.21057 | -121.6827 | -121.6644 | 121.6415 | 0.30212 | 1.0208 | 0.32959
1437.6719 | 121.7422 | -1.03 | 120.7672 | 0.0031279 | 0.0014056 | 0.056631 | 0.051733 | -0.0011237 | -0.0077074 | -0.0002456 | -0.0023192 | 0.031717 | 0.040071 | 0.0073657 | 0.014898 | 0.024819 | -0.00084805 | 0.068665 | 120.6345 | -1.0025 | 120.5978 | -0.84228 | -0.9613 | -0.93384 | -0.78278 | -0.70953 | -0.94757 | -0.79193 | -0.69122 | -0.69122 | -0.68665 | 0.027466 | -0.13275 | -0.16937 | 0.18768 | 0.09613 | 0.068664 | 0.068664 | 0.041198 | 0.082397 | -121.4767 | -121.5591 | 0.33874 | 0.34332 | 0.33874 | 0.26093 | 0.25635 | 0.16022 | 121.6003 | 0.25635 | 0.15564 | 121.637 | 0.23804 | 121.6644 | 0.32043 | -121.7697 | -121.7148 | 121.6278 | 0.23804 | 1.0986 | 0.24719
1439.4219 | 121.7972 | -0.97046 | 120.7626 | -0.01976 | 0.0022602 | 0.055991 | 0.051947 | -0.0011237 | -0.0066394 | -0.0025956 | -0.005371 | 0.029794 | 0.04114 | 0.010784 | 0.015539 | 0.026741 | -0.0019163 | 0.022888 | 120.6528 | -0.95673 | 120.6665 | -0.75531 | -0.92926 | -0.88806 | -0.61798 | -0.74158 | -0.9201 | -0.67291 | -0.6134 | -0.60883 | -0.60883 | 0.013733 | -0.10986 | -0.09613 | 0.21515 | 0.082397 | 0.041199 | 0.068664 | 0.027466 | 0.050354 | -121.5042 | -121.4355 | 0.35706 | 0.36163 | 0.36163 | 0.31128 | 0.31128 | 0.20142 | 121.6232 | 0.3067 | 0.24719 | 121.6095 | 0.17853 | 121.6232 | 0.22888 | -121.7194 | -121.6827 | 121.637 | 0.29755 | 0.99335 | 0.35248
1441.125 | 121.8521 | -0.98877 | 120.7489 | -0.01976 | 0.00076478 | 0.051718 | 0.054724 | -0.00048286 | -0.0072802 | -0.0021682 | -0.005371 | 0.030648 | 0.040285 | 0.0033069 | 0.01618 | 0.025887 | 0.0012881 | 0.032043 | 120.6528 | -0.98419 | 120.639 | -0.80109 | -0.91553 | -0.8606 | -0.64087 | -0.70953 | -0.93384 | -0.68207 | -0.55847 | -0.54016 | -0.55847 | 0.004578 | -0.09613 | -0.10986 | 0.18768 | 0.12817 | 0.073243 | 0.1236 | 0.068665 | 0.054932 | -121.4584 | -121.431 | 0.4303 | 0.4303 | 0.44861 | 0.37537 | 0.39368 | 0.18311 | 121.6232 | 0.37537 | 0.25177 | 121.637 | 0.2243 | 121.6415 | 0.27924 | -121.7331 | -121.6827 | 121.6278 | 0.3067 | 1.0208 | 0.3479
1442.8906 | 121.7239 | -1.0208 | 120.7443 | -0.012131 | 0.0037556 | 0.055563 | 0.055151 | 0.00058534 | -0.0070666 | -0.0004592 | -0.0084228 | 0.033212 | 0.040712 | 0.0065113 | 0.017248 | 0.023964 | -0.0036253 | 0.041199 | 120.726 | -0.97504 | 120.5704 | -0.91095 | -1.0483 | -1.0208 | -0.77362 | -0.67291 | -0.9613 | -0.76446 | -0.70953 | -0.70496 | -0.64545 | 0.045776 | -0.018311 | -0.17395 | 0.10986 | 0 | -0.027466 | -0.045776 | -0.073242 | 0.059509 | -121.4172 | -121.5088 | 0.31128 | 0.37537 | 0.31586 | 0.31586 | 0.25635 | 0.064087 | 121.5454 | 0.25177 | 0.19684 | 121.701 | 0.28839 | 121.7468 | 0.3479 | -121.7194 | -121.7056 | 121.5912 | 0.25635 | 1.062 | 0.24719
1444.6094 | 121.7422 | -1.0254 | 120.7443 | -0.01976 | 0.0033282 | 0.054068 | 0.054297 | 0.0027215 | -0.0081348 | -0.0021682 | -0.005371 | 0.033212 | 0.039217 | 0.0071521 | 0.017889 | 0.026314 | 0.00021995 | 0.11902 | 120.6757 | -0.98877 | 120.5978 | -0.84686 | -0.99335 | -0.97046 | -0.66376 | -0.65002 | -0.94757 | -0.70038 | -0.63629 | -0.63171 | -0.59967 | 0.036621 | -0.068665 | -0.14649 | 0.17853 | 0.054932 | 0.032044 | 0.018311 | -0.004577 | 0.07782 | -121.3943 | -121.4447 | 0.3891 | 0.42572 | 0.39368 | 0.3479 | 0.31586 | 0.14191 | 121.5866 | 0.31128 | 0.24719 | 121.6644 | 0.29755 | 121.701 | 0.37537 | -121.7331 | -121.6919 | 121.6232 | 0.32501 | 1.1444 | 0.36163
1446.3438 | 121.8658 | -0.99792 | 120.7077 | -0.0045011 | 0.00055118 | 0.055563 | 0.05216 | -0.0060371 | -0.0092028 | -0.0021682 | -0.0023192 | 0.031717 | 0.040499 | 0.00052987 | 0.013403 | 0.027382 | 0.0015017 | 0.009155 | 120.6619 | -0.97961 | 120.607 | -0.81482 | -0.92926 | -0.90637 | -0.58594 | -0.65918 | -0.95673 | -0.6134 | -0.53558 | -0.50812 | -0.51727 | 0.018311 | -0.045777 | -0.10071 | 0.18311 | 0.091553 | 0.068665 | 0.073242 | 0.050354 | 0.041199 | -121.3669 | -121.3211 | 0.46234 | 0.48065 | 0.48981 | 0.43945 | 0.44861 | 0.1648 | 121.5866 | 0.42114 | 0.34332 | 121.6415 | 0.29755 | 121.6599 | 0.33874 | -121.6873 | -121.6644 | 121.6049 | 0.38452 | 1.0071 | 0.41199
1448.0938 | 121.8842 | -1.0437 | 120.6985 | -0.01976 | 0.0020466 | 0.055136 | 0.050238 | -0.0028327 | -0.0079212 | -0.0013138 | -0.005371 | 0.030862 | 0.03879 | 0.0022389 | 0.014898 | 0.027382 | -0.0025571 | 0.045776 | 120.6436 | -1.0117 | 120.639 | -0.78735 | -0.91553 | -0.88348 | -0.50812 | -0.64545 | -0.95673 | -0.5722 | -0.50812 | -0.44861 | -0.48065 | 0.032043 | -0.054931 | -0.059509 | 0.25635 | 0.16022 | 0.12817 | 0.12817 | 0.096131 | 0.086975 | -121.344 | -121.2708 | 0.53558 | 0.56305 | 0.59509 | 0.47607 | 0.50812 | 0.2243 | 121.6507 | 0.44861 | 0.38452 | 121.6553 | 0.31128 | 121.6873 | 0.39825 | -121.7102 | -121.6553 | 121.6827 | 0.4715 | 1.0895 | 0.53558
1449.8438 | 121.8521 | -0.99792 | 120.7169 | -0.0045011 | 0.00055118 | 0.054068 | 0.051092 | -0.0011237 | -0.0081348 | -0.0030228 | -0.005371 | 0.030008 | 0.040071 | 0.01057 | 0.014043 | 0.024819 | 0.0027835 | 0.082397 | 120.6528 | -0.97504 | 120.6848 | -0.76446 | -0.87891 | -0.8606 | -0.49896 | -0.63171 | -0.93842 | -0.57678 | -0.46692 | -0.45319 | -0.48981 | 0.022888 | -0.064087 | -0.032044 | 0.23346 | 0.13733 | 0.11902 | 0.11444 | 0.096131 | 0.059509 | -121.3486 | -121.2936 | 0.53101 | 0.50812 | 0.54474 | 0.44861 | 0.48523 | 0.21057 | 121.6599 | 0.4715 | 0.36163 | 121.6278 | 0.3067 | 121.6507 | 0.36621 | -121.6919 | -121.6553 | 121.6827 | 0.42114 | 1.0803 | 0.49896
1451.5312 | 121.7697 | -1.0483 | 120.7581 | -0.01976 | -8.9824e-05 | 0.054922 | 0.053442 | -0.0015509 | -0.0087756 | -0.0021682 | -0.0084228 | 0.032998 | 0.039644 | 0.021465 | 0.017675 | 0.025246 | -0.0019163 | 0.10071 | 120.6848 | -1.0117 | 120.5933 | -0.90179 | -0.98877 | -0.97961 | -0.60425 | -0.60425 | -0.97046 | -0.62714 | -0.59052 | -0.55389 | -0.54016 | 0.036621 | -0.073243 | -0.16479 | 0.14648 | 0.068665 | 0.059509 | 0.032044 | 0.022888 | 0.07782 | -121.3623 | -121.3852 | 0.45776 | 0.50812 | 0.49438 | 0.4303 | 0.41656 | 0.10986 | 121.6049 | 0.37994 | 0.34332 | 121.6965 | 0.36621 | 121.7331 | 0.44403 | -121.7697 | -121.7285 | 121.6415 | 0.42114 | 1.149 | 0.44403
1453.2812 | 121.7422 | -1.0666 | 120.7626 | -0.0045011 | 0.00033758 | 0.054495 | 0.053442 | 0.0012261 | -0.0081348 | -0.0021682 | -0.0023192 | 0.032144 | 0.04178 | 0.0043751 | 0.015539 | 0.0261 | -0.00063445 | 0.054932 | 120.6894 | -1.03 | 120.5383 | -0.94299 | -1.0483 | -1.03 | -0.65918 | -0.59052 | -0.99792 | -0.68207 | -0.61798 | -0.59052 | -0.55389 | 0.036621 | -0.073242 | -0.2243 | 0.1236 | 0.036621 | 0.01831 | 0 | -0.018311 | 0.068664 | -121.3531 | -121.4447 | 0.44861 | 0.5127 | 0.47607 | 0.44403 | 0.40741 | 0.086975 | 121.5683 | 0.37994 | 0.31586 | 121.7194 | 0.40741 | 121.756 | 0.47607 | -121.7926 | -121.7606 | 121.6049 | 0.38452 | 1.1215 | 0.40741
1455.0312 | 121.7789 | -1.03 | 120.7672 | -0.0045011 | 0.0014056 | 0.054495 | 0.052801 | 0.0037897 | -0.00963 | -0.002382 | -0.0023192 | 0.032144 | 0.039644 | 0.0039477 | 0.016821 | 0.028237 | -0.0017027 | 0.10529 | 120.694 | -1.0071 | 120.5978 | -0.8606 | -0.98877 | -0.96588 | -0.55847 | -0.58136 | -0.95673 | -0.59967 | -0.53101 | -0.5127 | -0.49439 | 0.022888 | -0.073242 | -0.16937 | 0.16937 | 0.064087 | 0.041198 | 0.041199 | 0.01831 | 0.073242 | -121.3486 | -121.3669 | 0.49896 | 0.53558 | 0.51727 | 0.46234 | 0.44403 | 0.14648 | 121.6049 | 0.42572 | 0.35706 | 121.701 | 0.37537 | 121.7239 | 0.44861 | -121.7743 | -121.7239 | 121.6278 | 0.4303 | 1.1353 | 0.4715
1456.7344 | 121.8613 | -1.0025 | 120.726 | -0.012131 | 0.0033282 | 0.056845 | 0.054724 | 0.0044305 | -0.0062122 | -0.0015274 | -0.011475 | 0.029794 | 0.037508 | 0.0069385 | 0.018316 | 0.028023 | 0.00064735 | 0.059509 | 120.6528 | -0.99792 | 120.6573 | -0.8194 | -0.95673 | -0.91553 | -0.49439 | -0.60425 | -0.94299 | -0.50812 | -0.47607 | -0.44403 | -0.43488 | 0.004577 | -0.073242 | -0.068664 | 0.1831 | 0.086975 | 0.045776 | 0.082398 | 0.041199 | 0.059509 | -121.3303 | -121.2341 | 0.52643 | 0.56763 | 0.55847 | 0.50812 | 0.49896 | 0.17853 | 121.6553 | 0.46692 | 0.43488 | 121.6507 | 0.33874 | 121.6553 | 0.39825 | -121.7239 | -121.669 | 121.6599 | 0.49438 | 1.062 | 0.50812
1458.5 | 121.7194 | -1.0849 | 120.7214 | -0.0045011 | 0.0061054 | 0.05535 | 0.054937 | 0.0014397 | -0.0070666 | -0.0013138 | -0.005371 | 0.032144 | 0.03879 | 0.013774 | 0.019384 | 0.027169 | 0.0027835 | 0.041199 | 120.6848 | -1.03 | 120.5063 | -0.99335 | -1.1169 | -1.062 | -0.65918 | -0.55389 | -0.99792 | -0.62714 | -0.62256 | -0.57678 | -0.54016 | 0.054932 | -0.036622 | -0.21515 | 0.091553 | 0.022888 | -0.032043 | -0.032044 | -0.086975 | 0.086975 | -121.2753 | -121.3486 | 0.46234 | 0.54474 | 0.50812 | 0.45776 | 0.42114 | 0.036621 | 121.5363 | 0.37537 | 0.37079 | 121.7148 | 0.44403 | 121.7697 | 0.53101 | -121.7514 | -121.7194 | 121.5912 | 0.45776 | 1.1261 | 0.42572
1460.2656 | 121.8201 | -1.0254 | 120.7123 | -0.0045011 | 0.0020466 | 0.055563 | 0.051733 | 0.0012261 | -0.0079212 | -0.0021682 | -0.005371 | 0.027658 | 0.039858 | 0.0043751 | 0.01383 | 0.028023 | 0.00086095 | 0.022888 | 120.6253 | -0.99335 | 120.6116 | -0.82398 | -0.97046 | -0.93842 | -0.48523 | -0.5722 | -0.96588 | -0.54016 | -0.50354 | -0.46234 | -0.45319 | 0.032044 | -0.086975 | -0.10071 | 0.20142 | 0.086975 | 0.054932 | 0.054931 | 0.022888 | 0.05951 | -121.2845 | -121.2524 | 0.52185 | 0.5722 | 0.56305 | 0.5127 | 0.50354 | 0.16937 | 121.6049 | 0.46234 | 0.42572 | 121.6187 | 0.39368 | 121.6507 | 0.45319 | -121.7056 | -121.6782 | 121.637 | 0.48523 | 1.0483 | 0.54016
1461.9688 | 121.8521 | -1.03 | 120.6985 | -0.012131 | 0.00055118 | 0.055136 | 0.053015 | -0.0011237 | -0.0083484 | -0.00345 | -0.005371 | 0.031076 | 0.035372 | 0.0022389 | 0.013616 | 0.028023 | -0.00063445 | 0 | 120.6207 | -1.0162 | 120.5933 | -0.86975 | -1.0117 | -0.9613 | -0.52185 | -0.55847 | -0.98419 | -0.51727 | -0.53101 | -0.41199 | -0.43488 | 0.013733 | -0.077819 | -0.10529 | 0.16022 | 0.068664 | 0.01831 | 0.054931 | 0.004577 | 0.045776 | -121.257 | -121.2158 | 0.49896 | 0.59509 | 0.61798 | 0.54932 | 0.5722 | 0.14648 | 121.6095 | 0.45319 | 0.46692 | 121.637 | 0.42572 | 121.6507 | 0.4715 | -121.7148 | -121.6827 | 121.6232 | 0.5127 | 1.03 | 0.50812
1463.7344 | 121.788 | -1.0437 | 120.7443 | -0.0045011 | 0.00012398 | 0.054068 | 0.052588 | -0.0075323 | -0.0083484 | -0.0053726 | -0.005371 | 0.032357 | 0.035799 | 0.0060841 | 0.014471 | 0.025887 | 6.346e-06 | 0.10529 | 120.6573 | -1.0071 | 120.6162 | -0.84228 | -0.95215 | -0.93842 | -0.46692 | -0.49896 | -0.99335 | -0.53558 | -0.56305 | -0.43488 | -0.45319 | 0.036621 | -0.086975 | -0.12817 | 0.20142 | 0.10528 | 0.091553 | 0.068664 | 0.054932 | 0.050354 | -121.2433 | -121.2799 | 0.48065 | 0.59052 | 0.60883 | 0.54016 | 0.55847 | 0.1648 | 121.6232 | 0.4303 | 0.45776 | 121.6644 | 0.49438 | 121.701 | 0.54474 | -121.7514 | -121.7377 | 121.6599 | 0.50812 | 1.149 | 0.57678
1465.4844 | 121.7697 | -1.0757 | 120.726 | -0.01976 | 0.0039692 | 0.055777 | 0.055151 | 0.0059259 | -0.0079212 | -0.0021682 | -0.0023192 | 0.03193 | 0.037508 | 0.01292 | 0.017248 | 0.028237 | -0.00084805 | 0.009155 | 120.7077 | -1.0391 | 120.5292 | -0.95215 | -1.0895 | -1.0483 | -0.54932 | -0.48523 | -1.0025 | -0.54474 | -0.59052 | -0.49439 | -0.45319 | 0.036621 | -0.01831 | -0.19684 | 0.1236 | 0.027466 | -0.013733 | -0.009155 | -0.050354 | 0.073243 | -121.2112 | -121.2708 | 0.48523 | 0.62256 | 0.58136 | 0.54932 | 0.50812 | 0.086976 | 121.5683 | 0.41199 | 0.45776 | 121.7468 | 0.51727 | 121.7834 | 0.59052 | -121.7651 | -121.7285 | 121.6049 | 0.53101 | 1.0849 | 0.52643
1467.1875 | 121.8521 | -1.0712 | 120.6528 | -0.01976 | 0.0048236 | 0.055991 | 0.053656 | 0.0016535 | -0.006853 | -0.0045182 | -0.005371 | 0.030862 | 0.037935 | 0.013988 | 0.018316 | 0.025887 | 6.346e-06 | 0.050354 | 120.575 | -1.0437 | 120.5978 | -0.84686 | -1.0254 | -0.97961 | -0.38452 | -0.52185 | -1.0117 | -0.40741 | -0.44861 | -0.35706 | -0.35706 | 0.027466 | -0.07782 | -0.054932 | 0.2243 | 0.091553 | 0.045776 | 0.064087 | 0.01831 | 0.059509 | -121.1746 | -121.0602 | 0.62256 | 0.71411 | 0.71411 | 0.6546 | 0.6546 | 0.19684 | 121.6415 | 0.56305 | 0.60425 | 121.6187 | 0.48981 | 121.6461 | 0.54932 | -121.6965 | -121.6644 | 121.669 | 0.66376 | 1.1215 | 0.68665
1468.9531 | 121.8155 | -1.1078 | 120.6528 | -0.0045011 | 0.001192 | 0.054922 | 0.051092 | -0.0058233 | -0.0077074 | -0.000673 | -0.0084228 | 0.028726 | 0.036013 | 0.0052295 | 0.017034 | 0.028664 | 0.00064735 | -0.009155 | 120.575 | -1.1078 | 120.5292 | -0.95215 | -1.0666 | -1.0391 | -0.48065 | -0.50354 | -1.0574 | -0.48523 | -0.51727 | -0.39368 | -0.39825 | 0 | -0.07782 | -0.1236 | 0.15564 | 0.068664 | 0.041199 | 0.068664 | 0.041199 | 0.050354 | -121.1563 | -121.138 | 0.59052 | 0.70953 | 0.71411 | 0.65918 | 0.66376 | 0.15564 | 121.637 | 0.54016 | 0.5722 | 121.6827 | 0.55389 | 121.6827 | 0.60425 | -121.7606 | -121.7102 | 121.637 | 0.62256 | 1.0986 | 0.62714
1470.7188 | 121.8338 | -1.0574 | 120.6802 | -0.012131 | 0.0033282 | 0.05535 | 0.053015 | 0.0027215 | -0.0077074 | -0.0049454 | 0.00073235 | 0.030435 | 0.036653 | -0.0018201 | 0.01618 | 0.029732 | 0.00021995 | 0.036621 | 120.607 | -1.0254 | 120.5795 | -0.8606 | -1.0162 | -0.97504 | -0.42114 | -0.51727 | -1.0071 | -0.47607 | -0.49439 | -0.38452 | -0.40283 | 0.032043 | -0.073242 | -0.10071 | 0.19684 | 0.082397 | 0.041199 | 0.050354 | 0.009156 | 0.050354 | -121.1975 | -121.1563 | 0.56305 | 0.6546 | 0.67291 | 0.60425 | 0.62256 | 0.16479 | 121.6049 | 0.51269 | 0.53101 | 121.6324 | 0.48981 | 121.6644 | 0.54016 | -121.7056 | -121.6873 | 121.637 | 0.58136 | 1.0941 | 0.63629
1472.4219 | 121.8567 | -1.0941 | 120.639 | 0.0031279 | 0.0022602 | 0.054068 | 0.05216 | 0.00015814 | -0.010057 | -0.0019546 | 0.00073235 | 0.032144 | 0.03644 | 0.0082203 | 0.01618 | 0.027809 | 0.0027835 | 0.009155 | 120.5933 | -1.062 | 120.5521 | -0.90637 | -1.0162 | -0.99335 | -0.46234 | -0.52185 | -1.03 | -0.48065 | -0.45776 | -0.3479 | -0.37537 | 0.032043 | -0.045776 | -0.086975 | 0.18768 | 0.10071 | 0.07782 | 0.068665 | 0.045777 | 0.064087 | -121.1609 | -121.1197 | 0.63629 | 0.71869 | 0.74616 | 0.6546 | 0.68207 | 0.15564 | 121.6141 | 0.5722 | 0.54932 | 121.6553 | 0.50812 | 121.6873 | 0.5722 | -121.701 | -121.669 | 121.6461 | 0.6134 | 1.1032 | 0.63171
1474.1875 | 121.756 | -1.1765 | 120.6345 | -0.012131 | 0.0037556 | 0.056418 | 0.055578 | 0.0046441 | -0.0064258 | -0.001741 | -0.0023192 | 0.032998 | 0.036653 | 0.011638 | 0.018743 | 0.026314 | -0.0031979 | 0.027466 | 120.5978 | -1.1444 | 120.4193 | -1.0986 | -1.2177 | -1.181 | -0.64545 | -0.49896 | -1.1261 | -0.58136 | -0.62256 | -0.55389 | -0.50354 | 0.032044 | -0.036621 | -0.21515 | 0.07782 | -0.004577 | -0.041198 | -0.036621 | -0.073242 | 0.050354 | -121.1334 | -121.2158 | 0.55389 | 0.67291 | 0.62256 | 0.62256 | 0.5722 | 0.045776 | 121.5637 | 0.50354 | 0.54474 | 121.7422 | 0.62714 | 121.7743 | 0.67749 | -121.7789 | -121.7606 | 121.5958 | 0.59509 | 1.2039 | 0.53101
1475.9375 | 121.8063 | -1.1536 | 120.6207 | -0.012131 | 0.0039692 | 0.055563 | 0.054083 | 0.0020807 | -0.0077074 | -0.0019546 | -0.005371 | 0.032357 | 0.035585 | 0.0043751 | 0.017034 | 0.027809 | 0.0012881 | 0.10529 | 120.5612 | -1.1444 | 120.4697 | -0.99792 | -1.1307 | -1.1032 | -0.53101 | -0.50354 | -1.1078 | -0.52643 | -0.5127 | -0.43945 | -0.44861 | 0.009155 | -0.05951 | -0.15106 | 0.15564 | 0.050354 | 0.022888 | 0.041199 | 0.013733 | 0.045776 | -121.1243 | -121.1472 | 0.64087 | 0.70496 | 0.71411 | 0.65918 | 0.66834 | 0.14648 | 121.6141 | 0.59509 | 0.58136 | 121.7056 | 0.60425 | 121.7148 | 0.65002 | -121.7651 | -121.7285 | 121.6232 | 0.62714 | 1.2589 | 0.62256
1477.625 | 121.7651 | -1.1581 | 120.6299 | -0.02739 | 0.00461 | 0.054922 | 0.053869 | -0.00048286 | -0.0077074 | -0.0032364 | -0.0023192 | 0.032998 | 0.038576 | 0.013133 | 0.017034 | 0.028878 | 0.0042789 | 0.013733 | 120.5933 | -1.1536 | 120.4102 | -1.0803 | -1.2039 | -1.1673 | -0.60883 | -0.50812 | -1.1215 | -0.58594 | -0.58594 | -0.5127 | -0.48523 | 0.004578 | -0.036621 | -0.21973 | 0.07782 | -0.009155 | -0.045776 | -0.013733 | -0.050354 | 0.036621 | -121.138 | -121.2158 | 0.5722 | 0.67291 | 0.64545 | 0.63629 | 0.60883 | 0.073242 | 121.5637 | 0.53558 | 0.53558 | 121.7468 | 0.6134 | 121.7514 | 0.65002 | -121.7834 | -121.7514 | 121.5683 | 0.5722 | 1.1719 | 0.54932
1479.3906 | 121.8338 | -1.1673 | 120.5933 | -0.012131 | 0.00076478 | 0.055777 | 0.05216 | 0.00058534 | -0.0092028 | 0.001677 | -0.005371 | 0.028939 | 0.037294 | 0.0013843 | 0.015112 | 0.0308 | -0.00020725 | 0.004578 | 120.5154 | -1.1581 | 120.4468 | -0.99792 | -1.1124 | -1.1078 | -0.51727 | -0.53101 | -1.1032 | -0.50354 | -0.46234 | -0.39368 | -0.42114 | 0.009155 | -0.07782 | -0.14648 | 0.16937 | 0.059509 | 0.054931 | 0.050354 | 0.045776 | 0.064087 | -121.1243 | -121.0968 | 0.70496 | 0.74615 | 0.77362 | 0.68207 | 0.70953 | 0.16022 | 121.6049 | 0.64087 | 0.59967 | 121.6736 | 0.5722 | 121.6827 | 0.63629 | -121.7514 | -121.6965 | 121.6141 | 0.66376 | 1.1719 | 0.65002
1481.0938 | 121.8063 | -1.1581 | 120.607 | -0.02739 | 0.00097838 | 0.053854 | 0.051947 | 0.00058534 | -0.0087756 | -0.0038772 | 0.00073235 | 0.030221 | 0.034945 | 0.0095019 | 0.015325 | 0.029518 | -0.00063445 | 0.10529 | 120.5246 | -1.1261 | 120.5246 | -0.95673 | -1.0666 | -1.0483 | -0.44403 | -0.47607 | -1.1032 | -0.48981 | -0.41657 | -0.36621 | -0.38452 | 0.032043 | -0.082398 | -0.082398 | 0.20142 | 0.10986 | 0.091553 | 0.07782 | 0.05951 | 0.054932 | -121.0831 | -121.0968 | 0.74158 | 0.77362 | 0.79193 | 0.71869 | 0.737 | 0.16937 | 121.6507 | 0.68664 | 0.6134 | 121.6507 | 0.62714 | 121.6827 | 0.68207 | -121.7331 | -121.7102 | 121.6827 | 0.66834 | 1.2634 | 0.71411
1482.8594 | 121.8246 | -1.2634 | 120.4971 | -0.01976 | 0.00097838 | 0.05535 | 0.053228 | -0.00069646 | -0.010271 | -0.0021682 | -0.0084228 | 0.031289 | 0.033876 | 0.0095019 | 0.016607 | 0.030587 | 6.346e-06 | 0.10071 | 120.4285 | -1.2222 | 120.4239 | -1.0345 | -1.149 | -1.1444 | -0.42114 | -0.45319 | -1.1902 | -0.42572 | -0.32044 | -0.32044 | -0.33875 | 0.041199 | -0.068664 | -0.073242 | 0.22888 | 0.11902 | 0.11444 | 0.07782 | 0.073242 | 0.073242 | -120.9503 | -120.9229 | 0.94299 | 0.92468 | 0.94299 | 0.85144 | 0.86975 | 0.18768 | 121.6461 | 0.86975 | 0.76447 | 121.6507 | 0.737 | 121.6919 | 0.81024 | -121.7194 | -121.6873 | 121.6873 | 0.83771 | 1.3641 | 0.84228
1484.625 | 121.8018 | -1.2817 | 120.5246 | -0.012131 | 0.001833 | 0.053427 | 0.053442 | 0.0012261 | -0.0081348 | -0.0030228 | -0.0084228 | 0.030008 | 0.033876 | 0.013988 | 0.017034 | 0.028878 | 0.0010745 | 0.10529 | 120.4834 | -1.2772 | 120.3735 | -1.1215 | -1.2222 | -1.2268 | -0.44861 | -0.42114 | -1.2039 | -0.42572 | -0.32044 | -0.35706 | -0.34332 | 0.004577 | -0.041199 | -0.15106 | 0.16022 | 0.054931 | 0.059509 | 0.050354 | 0.054932 | 0.07782 | -120.9457 | -120.9503 | 0.9613 | 0.93841 | 0.92468 | 0.86059 | 0.84686 | 0.15564 | 121.6507 | 0.88348 | 0.7782 | 121.7606 | 0.78277 | 121.7651 | 0.86059 | -121.8018 | -121.7285 | 121.6553 | 0.85602 | 1.387 | 0.83313
1486.3281 | 121.8933 | -1.2634 | 120.4834 | -0.0045011 | 0.0026874 | 0.052786 | 0.051733 | 0.00037174 | -0.0077074 | -0.0049454 | 0.00073235 | 0.030008 | 0.032808 | 0.0062977 | 0.015752 | 0.029732 | 0.0025699 | 0.041199 | 120.4102 | -1.2451 | 120.3964 | -1.0803 | -1.181 | -1.149 | -0.3479 | -0.43945 | -1.2131 | -0.35706 | -0.23346 | -0.24261 | -0.27466 | 0.018311 | -0.073242 | -0.086975 | 0.18311 | 0.11444 | 0.082398 | 0.09613 | 0.064087 | 0.050354 | -120.9229 | -120.8405 | 1.03 | 0.98877 | 1.0208 | 0.93842 | 0.97046 | 0.1648 | 121.6415 | 0.97962 | 0.85602 | 121.6553 | 0.77362 | 121.6736 | 0.82398 | -121.7285 | -121.6965 | 121.6599 | 0.90637 | 1.3046 | 0.91553
1488.0781 | 121.875 | -1.2863 | 120.4742 | -0.012131 | 0.0054644 | 0.054922 | 0.053656 | -0.00026906 | -0.0072802 | -0.0047318 | -0.005371 | 0.030862 | 0.033236 | 0.012065 | 0.019384 | 0.029732 | 0.0036379 | 0.027466 | 120.4193 | -1.2863 | 120.3552 | -1.1398 | -1.268 | -1.2314 | -0.39368 | -0.43945 | -1.2451 | -0.36163 | -0.27466 | -0.28839 | -0.27008 | 0 | -0.054931 | -0.11902 | 0.14648 | 0.054932 | 0.018311 | 0.054932 | 0.018311 | 0.041199 | -120.9137 | -120.8359 | 1.0117 | 1.0162 | 0.99792 | 0.97504 | 0.95673 | 0.14648 | 121.6415 | 0.97046 | 0.88348 | 121.7056 | 0.80566 | 121.7056 | 0.84686 | -121.7606 | -121.7194 | 121.6415 | 0.92468 | 1.3138 | 0.89264
1489.8438 | 121.9025 | -1.268 | 120.4788 | -0.012131 | -0.0013714 | 0.052786 | 0.048742 | -0.00048286 | -0.0092028 | -0.00345 | 0.00073235 | 0.030435 | 0.032595 | 0.0084339 | 0.015325 | 0.031227 | -0.00063445 | 0.073242 | 120.3644 | -1.268 | 120.401 | -1.03 | -1.181 | -1.1444 | -0.3479 | -0.49439 | -1.2222 | -0.39825 | -0.26093 | -0.27924 | -0.32044 | 0 | -0.11444 | -0.07782 | 0.23804 | 0.1236 | 0.086975 | 0.1236 | 0.086975 | 0.045776 | -120.9732 | -120.8771 | 1.0071 | 0.94757 | 0.98877 | 0.90179 | 0.94299 | 0.23804 | 121.669 | 0.9613 | 0.82398 | 121.6324 | 0.72784 | 121.6324 | 0.77362 | -121.7468 | -121.701 | 121.669 | 0.86975 | 1.3412 | 0.92011
1491.5469 | 121.8155 | -1.3321 | 120.4834 | -0.0045011 | 0.0050372 | 0.05535 | 0.056219 | 0.0037897 | -0.0092028 | -0.0036636 | -0.0023192 | 0.034707 | 0.033449 | 0.012493 | 0.017461 | 0.029946 | 0.00086095 | 0.10986 | 120.4239 | -1.3229 | 120.314 | -1.1673 | -1.2909 | -1.2817 | -0.44861 | -0.43945 | -1.2634 | -0.46692 | -0.35248 | -0.37537 | -0.37079 | 0.009155 | -0.059509 | -0.16937 | 0.1648 | 0.050354 | 0.041198 | 0.041199 | 0.032043 | 0.068664 | -120.9229 | -120.9503 | 0.97961 | 0.9613 | 0.95673 | 0.89264 | 0.88806 | 0.15564 | 121.637 | 0.91095 | 0.79651 | 121.7468 | 0.82398 | 121.756 | 0.89264 | -121.8063 | -121.7468 | 121.6461 | 0.86517 | 1.442 | 0.88348
1493.3125 | 121.7651 | -1.3824 | 120.4468 | -0.012131 | 0.00033758 | 0.05535 | 0.054724 | -0.0028327 | -0.0077074 | -0.0053726 | -0.005371 | 0.033426 | 0.034731 | 0.0075793 | 0.017461 | 0.028878 | -0.00084805 | 0.032043 | 120.4239 | -1.3458 | 120.2408 | -1.2451 | -1.3458 | -1.3412 | -0.52185 | -0.41199 | -1.2863 | -0.51727 | -0.39825 | -0.41199 | -0.41657 | 0.036621 | -0.022888 | -0.20599 | 0.13733 | 0.041198 | 0.036621 | 0.004577 | 0 | 0.09613 | -120.8588 | -120.9641 | 0.98419 | 0.96588 | 0.97046 | 0.86975 | 0.87433 | 0.10071 | 121.5866 | 0.88806 | 0.76904 | 121.7697 | 0.87433 | 121.8063 | 0.97046 | -121.7926 | -121.7331 | 121.6232 | 0.86517 | 1.4145 | 0.8606
1495.0781 | 121.756 | -1.3687 | 120.4651 | -0.0045011 | 0.00033758 | 0.055563 | 0.052801 | -0.0060371 | -0.0074938 | -0.0025956 | -0.0084228 | 0.032785 | 0.029604 | 0.012279 | 0.015966 | 0.0308 | 0.0021425 | 0.050354 | 120.401 | -1.3504 | 120.2362 | -1.2451 | -1.3596 | -1.3412 | -0.52185 | -0.39368 | -1.2817 | -0.50354 | -0.35248 | -0.40283 | -0.39825 | 0.01831 | -0.064087 | -0.22888 | 0.1236 | 0.027465 | 0.009155 | 0.009155 | -0.009155 | 0.086975 | -120.8588 | -120.9686 | 1.0162 | 0.97046 | 0.96588 | 0.88348 | 0.87891 | 0.10529 | 121.5866 | 0.92926 | 0.7782 | 121.7514 | 0.88806 | 121.7697 | 0.97504 | -121.8155 | -121.7468 | 121.6049 | 0.86517 | 1.4191 | 0.84686
1496.7812 | 121.8155 | -1.355 | 120.4605 | -0.012131 | 0.0033282 | 0.056631 | 0.054937 | 0.0010125 | -0.0081348 | -0.0030228 | -0.0023192 | 0.031717 | 0.031099 | 0.0028797 | 0.020666 | 0.030159 | 0.0012881 | 0.10529 | 120.401 | -1.3184 | 120.3049 | -1.1948 | -1.3138 | -1.2955 | -0.44861 | -0.41199 | -1.2589 | -0.43945 | -0.33417 | -0.35706 | -0.3479 | 0.036621 | -0.059509 | -0.15564 | 0.16022 | 0.059509 | 0.041198 | 0.022888 | 0.004577 | 0.09613 | -120.8725 | -120.9 | 1.0208 | 1.0071 | 0.99792 | 0.91095 | 0.90179 | 0.1236 | 121.6232 | 0.92468 | 0.8194 | 121.7194 | 0.84686 | 121.756 | 0.94299 | -121.7789 | -121.7194 | 121.6599 | 0.91553 | 1.4603 | 0.90637
1498.5469 | 121.8887 | -1.3046 | 120.433 | -0.01976 | 0.0026874 | 0.053641 | 0.053442 | 0.00079894 | -0.0072802 | -0.0013138 | -0.005371 | 0.029794 | 0.032595 | 0.0048023 | 0.01917 | 0.031655 | 0.0017153 | 0.054932 | 120.3918 | -1.3138 | 120.3552 | -1.1398 | -1.2772 | -1.2497 | -0.3479 | -0.45776 | -1.2726 | -0.36163 | -0.27008 | -0.28839 | -0.26093 | -0.009156 | -0.041198 | -0.077819 | 0.16479 | 0.054931 | 0.027465 | 0.064087 | 0.036621 | 0.032043 | -120.8908 | -120.7947 | 1.0345 | 1.0437 | 1.0162 | 1.0117 | 0.98419 | 0.17395 | 121.669 | 1.0025 | 0.91095 | 121.7056 | 0.81482 | 121.6965 | 0.84686 | -121.7468 | -121.7056 | 121.6599 | 0.94299 | 1.3596 | 0.95673
1500.2344 | 121.8796 | -1.2451 | 120.52 | -0.01976 | 0.0041828 | 0.058127 | 0.054083 | 0.0012261 | -0.0087756 | -0.0013138 | -0.005371 | 0.032357 | 0.035158 | 0.0099293 | 0.016393 | 0.029946 | 6.346e-06 | 0.018311 | 120.4697 | -1.2451 | 120.3873 | -1.0803 | -1.2222 | -1.2177 | -0.38452 | -0.44403 | -1.1993 | -0.36163 | -0.27466 | -0.29755 | -0.28839 | 0 | -0.050354 | -0.13275 | 0.1648 | 0.027466 | 0.022888 | 0.027466 | 0.022888 | 0.045776 | -120.9641 | -120.8817 | 0.97046 | 0.95673 | 0.94757 | 0.91095 | 0.9018 | 0.1648 | 121.6324 | 0.92468 | 0.83771 | 121.7148 | 0.75531 | 121.7148 | 0.80109 | -121.7651 | -121.7194 | 121.6324 | 0.88348 | 1.2634 | 0.8606
1502 | 121.7697 | -1.3275 | 120.5109 | -0.0045011 | 0.0061054 | 0.056845 | 0.053869 | 0.0027215 | -0.0072802 | -0.002382 | -0.0023192 | 0.033853 | 0.032808 | 0.0048023 | 0.018957 | 0.0308 | 6.346e-06 | 0.009155 | 120.4697 | -1.2817 | 120.2545 | -1.236 | -1.355 | -1.3229 | -0.50354 | -0.39825 | -1.2589 | -0.4715 | -0.39368 | -0.41657 | -0.37079 | 0.045777 | -0.041198 | -0.25635 | 0.091553 | 0.004578 | -0.027465 | -0.041199 | -0.073242 | 0.068665 | -120.9091 | -120.9824 | 0.93384 | 0.95673 | 0.91095 | 0.88806 | 0.84228 | 0.045776 | 121.5363 | 0.86517 | 0.78735 | 121.7514 | 0.8606 | 121.7972 | 0.92926 | -121.7926 | -121.7697 | 121.582 | 0.85602 | 1.3367 | 0.82398
1503.7812 | 121.756 | -1.3458 | 120.4834 | -0.012131 | 0.0069598 | 0.053854 | 0.053869 | 0.0018671 | -0.0070666 | -0.0011002 | -0.0023192 | 0.031076 | 0.032595 | 0.010356 | 0.020025 | 0.029946 | 0.0047061 | 0.050354 | 120.433 | -1.3184 | 120.2591 | -1.2634 | -1.3779 | -1.3596 | -0.50812 | -0.3891 | -1.2817 | -0.48523 | -0.40283 | -0.4303 | -0.39368 | 0.027466 | -0.050354 | -0.2243 | 0.082397 | -0.013733 | -0.032044 | -0.041199 | -0.05951 | 0.064087 | -120.8725 | -120.9686 | 0.94299 | 0.95215 | 0.91553 | 0.88806 | 0.85144 | 0.054931 | 121.5775 | 0.87891 | 0.79651 | 121.7514 | 0.89264 | 121.7789 | 0.95673 | -121.8018 | -121.7651 | 121.6049 | 0.8606 | 1.3962 | 0.83771
1505.4844 | 121.7834 | -1.3412 | 120.4742 | -0.012131 | 0.0043964 | 0.05535 | 0.055151 | 0.00058534 | -0.0083484 | -0.002382 | -0.0084228 | 0.032144 | 0.033876 | 0.0062977 | 0.018743 | 0.029518 | 0.0032107 | 0.091553 | 120.4285 | -1.3275 | 120.314 | -1.1673 | -1.3229 | -1.2909 | -0.40741 | -0.37994 | -1.2634 | -0.41657 | -0.31586 | -0.36621 | -0.35248 | 0.013733 | -0.045776 | -0.16022 | 0.17395 | 0.050354 | 0.018311 | 0.036621 | 0.004578 | 0.07782 | -120.8542 | -120.8908 | 1.0254 | 0.98877 | 0.97504 | 0.91095 | 0.89722 | 0.16022 | 121.6415 | 0.94757 | 0.84686 | 121.756 | 0.88348 | 121.7697 | 0.9613 | -121.8018 | -121.7377 | 121.6553 | 0.92468 | 1.4328 | 0.93384
1507.25 | 121.7789 | -1.3641 | 120.4605 | -0.012131 | 0.0043964 | 0.054068 | 0.052801 | 0.0010125 | -0.006853 | -0.0011002 | -0.0023192 | 0.032357 | 0.036226 | 0.0050159 | 0.016821 | 0.032296 | 0.0038515 | 0.041199 | 120.433 | -1.3184 | 120.2362 | -1.236 | -1.3596 | -1.3367 | -0.49439 | -0.37994 | -1.3092 | -0.46692 | -0.35248 | -0.38452 | -0.36163 | 0.045777 | -0.027466 | -0.2243 | 0.12817 | 0.027466 | 0.004578 | -0.018311 | -0.041199 | 0.054932 | -120.8405 | -120.9274 | 1.0117 | 1.0025 | 0.97962 | 0.94757 | 0.92468 | 0.082397 | 121.5546 | 0.95673 | 0.84229 | 121.7514 | 0.92926 | 121.7972 | 0.98419 | -121.7789 | -121.7697 | 121.6003 | 0.89722 | 1.4053 | 0.86975
1509.0156 | 121.8658 | -1.3092 | 120.4559 | -0.012131 | 0.0037556 | 0.053427 | 0.051306 | 0.0033623 | -0.0089892 | -0.0028092 | -0.0023192 | 0.031503 | 0.031099 | 0.0026661 | 0.014684 | 0.031227 | -0.00020725 | 0.004578 | 120.4102 | -1.268 | 120.3552 | -1.1078 | -1.2726 | -1.2268 | -0.37079 | -0.41199 | -1.2451 | -0.37994 | -0.27008 | -0.30212 | -0.29755 | 0.041199 | -0.045777 | -0.10071 | 0.20142 | 0.082397 | 0.036621 | 0.041198 | -0.004578 | 0.064087 | -120.8679 | -120.8359 | 1.0391 | 1.0117 | 1.0071 | 0.94757 | 0.94299 | 0.16022 | 121.6232 | 0.97504 | 0.86517 | 121.6782 | 0.83313 | 121.7194 | 0.89722 | -121.7239 | -121.701 | 121.6644 | 0.92926 | 1.3138 | 0.93841
1510.7031 | 121.8521 | -1.3092 | 120.4788 | -0.02739 | 0.0031146 | 0.055136 | 0.052801 | -0.00069646 | -0.010271 | -0.0043046 | -0.005371 | 0.028726 | 0.030672 | 0.0045887 | 0.014257 | 0.032509 | 0.00064735 | 0 | 120.4056 | -1.2772 | 120.3323 | -1.1444 | -1.2543 | -1.236 | -0.38452 | -0.42114 | -1.2405 | -0.39825 | -0.27466 | -0.30212 | -0.29755 | 0.032043 | -0.073242 | -0.14648 | 0.1648 | 0.073242 | 0.054932 | 0.041199 | 0.022889 | 0.068664 | -120.9 | -120.8771 | 1.0345 | 1.0117 | 1.0071 | 0.94299 | 0.93842 | 0.13275 | 121.6095 | 0.96588 | 0.84229 | 121.6827 | 0.8194 | 121.7148 | 0.88806 | -121.756 | -121.7194 | 121.6415 | 0.91095 | 1.3092 | 0.92468
1512.4688 | 121.7606 | -1.3046 | 120.5612 | -0.0045011 | 0.0061054 | 0.057059 | 0.055365 | -0.0015509 | -0.0053576 | -0.001741 | -0.005371 | 0.033426 | 0.033663 | 0.0043751 | 0.019384 | 0.029946 | 0.0012881 | 0.050354 | 120.4788 | -1.2955 | 120.3049 | -1.2268 | -1.3458 | -1.3046 | -0.50354 | -0.40283 | -1.2543 | -0.48981 | -0.28839 | -0.40283 | -0.3891 | 0.009155 | -0.082397 | -0.25635 | 0.077819 | 0 | -0.041199 | -0.009155 | -0.050354 | 0.050354 | -120.9641 | -121.051 | 1.0162 | 0.91553 | 0.90179 | 0.86517 | 0.85144 | 0.068664 | 121.6003 | 0.96588 | 0.76447 | 121.7743 | 0.85144 | 121.7834 | 0.90179 | -121.8567 | -121.8155 | 121.6095 | 0.81482 | 1.355 | 0.80109
1514.2344 | 121.875 | -1.181 | 120.5795 | -0.0045011 | 0.00012398 | 0.054709 | 0.054083 | -0.0017645 | -0.0089892 | -0.0030228 | 0.00073235 | 0.030862 | 0.032808 | 0.0080067 | 0.014684 | 0.029946 | 0.0023563 | 0.13733 | 120.5017 | -1.1673 | 120.5109 | -0.95673 | -1.0757 | -1.062 | -0.32959 | -0.42572 | -1.1353 | -0.37994 | -0.15564 | -0.23346 | -0.28839 | 0.013733 | -0.07782 | -0.068665 | 0.2243 | 0.11902 | 0.10529 | 0.10529 | 0.091552 | 0.045776 | -121.0052 | -120.9595 | 1.0254 | 0.89264 | 0.94757 | 0.84686 | 0.9018 | 0.21057 | 121.6782 | 0.97961 | 0.75531 | 121.669 | 0.70953 | 121.6827 | 0.75531 | -121.7468 | -121.7148 | 121.6919 | 0.80109 | 1.3184 | 0.85144
1515.9844 | 121.8155 | -1.268 | 120.5429 | -0.0045011 | 0.0033282 | 0.054495 | 0.05451 | 0.0018671 | -0.006853 | -0.0021682 | -0.005371 | 0.032571 | 0.033449 | 0.0075793 | 0.019598 | 0.029946 | 0.00064735 | 0.082397 | 120.4926 | -1.2543 | 120.369 | -1.1765 | -1.268 | -1.2589 | -0.45319 | -0.38452 | -1.2177 | -0.4303 | -0.18768 | -0.32044 | -0.31128 | 0.013733 | -0.050354 | -0.17395 | 0.091552 | 0.009155 | 0 | -0.004578 | -0.013733 | 0.050354 | -120.9274 | -120.9732 | 1.0803 | 0.95673 | 0.94757 | 0.90637 | 0.89722 | 0.077819 | 121.6232 | 1.03 | 0.78735 | 121.7468 | 0.83313 | 121.7606 | 0.88348 | -121.7972 | -121.7606 | 121.637 | 0.83771 | 1.3504 | 0.81482
1517.6719 | 121.8246 | -1.2863 | 120.5521 | -0.0045011 | 0.0026874 | 0.055563 | 0.054083 | 0.0033623 | -0.0092028 | -0.0030228 | -0.0023192 | 0.034066 | 0.034304 | 0.0075793 | 0.015539 | 0.027809 | 0.00064735 | 0.10071 | 120.5109 | -1.2451 | 120.401 | -1.1261 | -1.2131 | -1.2222 | -0.41199 | -0.38452 | -1.1902 | -0.40741 | -0.2243 | -0.30212 | -0.31128 | 0.041199 | -0.041199 | -0.15106 | 0.16022 | 0.064087 | 0.073242 | 0.022888 | 0.032043 | 0.09613 | -120.9366 | -120.9595 | 1.062 | 0.97504 | 0.98419 | 0.87891 | 0.88806 | 0.11902 | 121.6461 | 0.96588 | 0.78278 | 121.756 | 0.80566 | 121.7972 | 0.9018 | -121.7972 | -121.7422 | 121.6873 | 0.87891 | 1.387 | 0.87433
1519.4375 | 121.8063 | -1.2543 | 120.6116 | -0.0045011 | 0.0024738 | 0.053854 | 0.053442 | -0.00069646 | -0.0077074 | -0.0028092 | -0.005371 | 0.031503 | 0.033449 | 0.0048023 | 0.017461 | 0.031655 | 0.0017153 | 0.09613 | 120.4971 | -1.2314 | 120.3918 | -1.1169 | -1.2085 | -1.2177 | -0.40741 | -0.35706 | -1.1993 | -0.39825 | -0.17395 | -0.29297 | -0.31128 | 0.022888 | -0.11444 | -0.21973 | 0.13733 | 0.036621 | 0.045776 | 0.013733 | 0.022888 | 0.054931 | -120.9686 | -121.0098 | 1.0803 | 0.94299 | 0.9613 | 0.88806 | 0.90637 | 0.11444 | 121.6232 | 1.0254 | 0.80109 | 121.7285 | 0.84228 | 121.7514 | 0.89722 | -121.843 | -121.8109 | 121.6461 | 0.85602 | 1.3504 | 0.84686
1521.2031 | 121.8246 | -1.236 | 120.5795 | -0.0045011 | 0.0043964 | 0.055563 | 0.055151 | 0.0044305 | -0.0083484 | -0.002382 | -0.005371 | 0.032785 | 0.032595 | 0.0092883 | 0.017675 | 0.028664 | 0.00021995 | 0.10529 | 120.5521 | -1.1993 | 120.4285 | -1.062 | -1.1902 | -1.1719 | -0.3891 | -0.3891 | -1.181 | -0.3891 | -0.14648 | -0.29755 | -0.31128 | 0.036621 | -0.027466 | -0.15106 | 0.17395 | 0.064087 | 0.045776 | 0.027466 | 0.009155 | 0.054932 | -120.9686 | -120.9686 | 1.0895 | 0.92468 | 0.93842 | 0.86975 | 0.88348 | 0.13733 | 121.6278 | 1.0345 | 0.79193 | 121.7514 | 0.79193 | 121.788 | 0.84686 | -121.7789 | -121.7606 | 121.6644 | 0.84686 | 1.3412 | 0.84686
1522.8906 | 121.7972 | -1.0895 | 120.7764 | -0.01976 | 0.00461 | 0.055777 | 0.053228 | 0.0018671 | -0.0089892 | -0.001741 | -0.005371 | 0.03193 | 0.034945 | 0.0022389 | 0.01917 | 0.029305 | 0.00021995 | 0.10529 | 120.694 | -1.0345 | 120.575 | -0.9201 | -1.062 | -1.0483 | -0.39368 | -0.36163 | -1.0208 | -0.40283 | -0.54474 | -0.32044 | -0.31586 | 0.054932 | -0.082397 | -0.20142 | 0.16937 | 0.041199 | 0.027466 | -0.013733 | -0.027466 | 0.068665 | -121.138 | -121.1792 | 0.54474 | 0.77362 | 0.76904 | 0.70496 | 0.70038 | 0.11444 | 121.6095 | 0.47607 | 0.61798 | 121.7285 | 0.65918 | 121.7834 | 0.72784 | -121.8109 | -121.7972 | 121.6644 | 0.68665 | 1.1948 | 0.6958
1524.6562 | 121.8979 | -1.0483 | 120.7123 | -0.01976 | 0.0041828 | 0.057059 | 0.054937 | 0.00015814 | -0.0072802 | -0.002382 | 0.00073235 | 0.030648 | 0.035372 | 0.012493 | 0.015112 | 0.030587 | -0.0012753 | 0.050354 | 120.7031 | -1.0437 | 120.6436 | -0.84686 | -1.0025 | -0.95215 | -0.28839 | -0.38452 | -0.99792 | -0.28839 | -0.42114 | -0.19226 | -0.20142 | 0.004578 | -0.009155 | -0.068664 | 0.20142 | 0.096131 | 0.045777 | 0.091553 | 0.041199 | 0.050354 | -121.0968 | -121.0007 | 0.62714 | 0.84686 | 0.85602 | 0.79651 | 0.80566 | 0.19684 | 121.6873 | 0.57678 | 0.70953 | 121.7468 | 0.6134 | 121.7514 | 0.66376 | -121.756 | -121.7102 | 121.6919 | 0.75989 | 1.0986 | 0.75989
1526.3594 | 121.8658 | -1.0483 | 120.7535 | -0.0045011 | 0.0024738 | 0.057486 | 0.053656 | -0.0030463 | -0.0098438 | -0.0013138 | -0.0023192 | 0.031503 | 0.033236 | 0.0033069 | 0.015966 | 0.029518 | 0.00043375 | -0.013733 | 120.6528 | -1.0162 | 120.607 | -0.86517 | -1.0025 | -0.97046 | -0.32501 | -0.36163 | -0.97504 | -0.33875 | -0.52185 | -0.22888 | -0.23804 | 0.032044 | -0.10071 | -0.14648 | 0.18311 | 0.07782 | 0.045777 | 0.045776 | 0.013733 | 0.073242 | -121.1151 | -121.0922 | 0.52643 | 0.81024 | 0.8194 | 0.737 | 0.74616 | 0.15106 | 121.6232 | 0.45319 | 0.63629 | 121.669 | 0.6134 | 121.701 | 0.68665 | -121.7697 | -121.7285 | 121.6553 | 0.70953 | 1.0345 | 0.72327
1528.1094 | 121.7697 | -1.0254 | 120.8221 | -0.012131 | 0.0054644 | 0.054068 | 0.055578 | 0.00058534 | -0.006853 | -0.0030228 | -0.0084228 | 0.034707 | 0.03644 | 0.0035205 | 0.017675 | 0.028237 | -0.0023435 | 0.045776 | 120.7626 | -1.0208 | 120.5978 | -0.94757 | -1.0529 | -1.0391 | -0.43945 | -0.31128 | -0.95215 | -0.41657 | -0.61798 | -0.35248 | -0.3067 | 0.004578 | -0.05951 | -0.22431 | 0.07782 | -0.013733 | -0.027465 | -0.018311 | -0.032043 | 0.073243 | -121.1334 | -121.2387 | 0.40741 | 0.71869 | 0.67291 | 0.64545 | 0.59967 | 0.073242 | 121.6187 | 0.33417 | 0.53558 | 121.7834 | 0.64087 | 121.788 | 0.71411 | -121.843 | -121.7743 | 121.6232 | 0.60883 | 1.0712 | 0.58594
1529.8125 | 121.8338 | -1.0391 | 120.7535 | 0.0031279 | 0.0020466 | 0.054282 | 0.049811 | 0.0014397 | -0.0087756 | -0.0015274 | -0.0023192 | 0.030862 | 0.035158 | 0.0039477 | 0.014898 | 0.029518 | -0.0021299 | 0.11444 | 120.694 | -1.0025 | 120.6528 | -0.82855 | -0.95215 | -0.9201 | -0.32044 | -0.35706 | -0.97504 | -0.37079 | -0.42572 | -0.23804 | -0.27466 | 0.036622 | -0.059509 | -0.10071 | 0.21057 | 0.11902 | 0.086976 | 0.082397 | 0.050354 | 0.064087 | -121.1105 | -121.1243 | 0.6134 | 0.76447 | 0.80109 | 0.70038 | 0.737 | 0.17395 | 121.6553 | 0.54932 | 0.60425 | 121.6965 | 0.61798 | 121.7331 | 0.68207 | -121.756 | -121.7285 | 121.6919 | 0.66833 | 1.1536 | 0.71869
1531.5781 | 121.8842 | -1.0162 | 120.7718 | -0.012131 | 0.0041828 | 0.057913 | 0.052801 | 0.0025079 | -0.0055712 | -0.0013138 | -0.005371 | 0.031717 | 0.036013 | 0.0028797 | 0.015539 | 0.028023 | -0.0031979 | 0.036621 | 120.7169 | -0.99792 | 120.6894 | -0.80109 | -0.97046 | -0.91095 | -0.24719 | -0.3479 | -0.9613 | -0.28381 | -0.39368 | -0.19226 | -0.20599 | 0.01831 | -0.054932 | -0.082398 | 0.21515 | 0.10528 | 0.045776 | 0.086975 | 0.027466 | 0.054931 | -121.1197 | -121.0556 | 0.62256 | 0.81024 | 0.82397 | 0.75531 | 0.76904 | 0.19684 | 121.6873 | 0.56763 | 0.67749 | 121.7148 | 0.6134 | 121.7331 | 0.66834 | -121.7697 | -121.7331 | 121.7056 | 0.73242 | 1.0529 | 0.76904
1533.2656 | 121.875 | -1.0849 | 120.7077 | -0.012131 | 0.0033282 | 0.056204 | 0.052801 | -0.0019781 | -0.0089892 | -0.0045182 | -0.0023192 | 0.03193 | 0.035799 | 0.0056567 | 0.014898 | 0.028878 | 0.0051333 | 0.018311 | 120.6573 | -1.0437 | 120.607 | -0.88348 | -1.0254 | -0.97961 | -0.29755 | -0.35248 | -1.0025 | -0.31586 | -0.42114 | -0.22888 | -0.22888 | 0.041199 | -0.050354 | -0.10071 | 0.20142 | 0.10529 | 0.059509 | 0.064087 | 0.01831 | 0.082398 | -121.0602 | -121.0236 | 0.66376 | 0.85602 | 0.85602 | 0.77362 | 0.77362 | 0.16022 | 121.6507 | 0.58136 | 0.68664 | 121.701 | 0.65002 | 121.7422 | 0.73242 | -121.7514 | -121.7102 | 121.6919 | 0.76904 | 1.1032 | 0.78735
1535.0156 | 121.9299 | -1.0757 | 120.7169 | -0.01976 | 0.0014056 | 0.054709 | 0.050451 | 0.00079894 | -0.0055712 | -0.0053726 | -0.0084228 | 0.02958 | 0.036013 | 0.0092883 | 0.014684 | 0.028878 | -0.00063445 | 0.041199 | 120.6802 | -1.0437 | 120.6345 | -0.86975 | -0.99792 | -0.97504 | -0.25635 | -0.34332 | -1.0162 | -0.28381 | -0.34332 | -0.15106 | -0.18768 | 0.032044 | -0.036621 | -0.082398 | 0.20599 | 0.10071 | 0.07782 | 0.068664 | 0.045776 | 0.05951 | -121.0602 | -121.0007 | 0.73242 | 0.88806 | 0.92468 | 0.82855 | 0.86517 | 0.17395 | 121.6782 | 0.67291 | 0.73242 | 121.7239 | 0.67291 | 121.756 | 0.73242 | -121.7606 | -121.7331 | 121.7102 | 0.79193 | 1.1169 | 0.8194
1536.7031 | 121.8292 | -1.0895 | 120.7581 | -0.012131 | 0.0022602 | 0.054282 | 0.053869 | -0.0019781 | -0.0077074 | -0.000673 | -0.005371 | 0.034921 | 0.033663 | 0.0069385 | 0.017248 | 0.028664 | 0.0025699 | 0.07782 | 120.694 | -1.0895 | 120.5521 | -0.98877 | -1.0803 | -1.0666 | -0.39825 | -0.29755 | -1.0254 | -0.37079 | -0.4715 | -0.27008 | -0.2655 | 0 | -0.064087 | -0.20599 | 0.10071 | 0.022889 | 0.009156 | 0.022889 | 0.009156 | 0.064087 | -121.0556 | -121.1288 | 0.61798 | 0.82397 | 0.8194 | 0.75989 | 0.75531 | 0.10071 | 121.6415 | 0.55389 | 0.6546 | 121.7834 | 0.72784 | 121.7834 | 0.79193 | -121.8475 | -121.7834 | 121.6415 | 0.71869 | 1.1673 | 0.69122
1538.4688 | 121.7789 | -1.0666 | 120.7718 | 0.0031279 | 0.001833 | 0.053854 | 0.053869 | -0.00091006 | -0.0062122 | -0.0013138 | -0.005371 | 0.032571 | 0.033876 | 0.0041615 | 0.014257 | 0.027596 | -0.0014891 | 0.036621 | 120.7214 | -1.0529 | 120.5658 | -0.95673 | -1.0483 | -1.03 | -0.41199 | -0.26093 | -0.99792 | -0.36163 | -0.55847 | -0.27008 | -0.27466 | 0.013733 | -0.050354 | -0.20599 | 0.10986 | 0.036621 | 0.01831 | 0.022888 | 0.004577 | 0.068664 | -121.0327 | -121.1334 | 0.50812 | 0.79193 | 0.79651 | 0.72327 | 0.72784 | 0.09613 | 121.6187 | 0.43945 | 0.63629 | 121.7743 | 0.737 | 121.788 | 0.80566 | -121.8246 | -121.7697 | 121.6324 | 0.70496 | 1.1032 | 0.6546
1540.2344 | 121.8292 | -1.0208 | 120.813 | -0.01976 | 0.0031146 | 0.055136 | 0.052801 | -0.0021919 | -0.010271 | -0.0021682 | -0.005371 | 0.031289 | 0.033663 | 0.010997 | 0.01618 | 0.028237 | 0.00043375 | 0.10529 | 120.7169 | -0.97046 | 120.6894 | -0.81482 | -0.93384 | -0.90637 | -0.27924 | -0.28839 | -0.93384 | -0.31586 | -0.55389 | -0.21515 | -0.22888 | 0.050354 | -0.09613 | -0.1236 | 0.20599 | 0.11444 | 0.086975 | 0.064087 | 0.036621 | 0.086975 | -121.1014 | -121.1288 | 0.46692 | 0.79193 | 0.80566 | 0.70496 | 0.71869 | 0.15564 | 121.6599 | 0.37994 | 0.61798 | 121.6873 | 0.64545 | 121.7377 | 0.73242 | -121.7834 | -121.7468 | 121.7102 | 0.70496 | 1.1261 | 0.74158
1541.9219 | 121.9116 | -0.97961 | 120.8359 | -0.012131 | -8.9824e-05 | 0.054282 | 0.051092 | 0.0033623 | -0.0072802 | -0.0038772 | -0.005371 | 0.02958 | 0.037294 | 0.0086475 | 0.015752 | 0.028023 | 6.346e-06 | 0.10986 | 120.7535 | -0.94299 | 120.7397 | -0.74158 | -0.85602 | -0.85602 | -0.20599 | -0.30212 | -0.90179 | -0.24261 | -0.47607 | -0.12817 | -0.15564 | 0.036621 | -0.082397 | -0.09613 | 0.23804 | 0.1236 | 0.1236 | 0.086975 | 0.086975 | 0.07782 | -121.138 | -121.0785 | 0.50354 | 0.82397 | 0.85144 | 0.74615 | 0.77362 | 0.20142 | 121.6827 | 0.42572 | 0.65918 | 121.6965 | 0.59967 | 121.7331 | 0.67749 | -121.7789 | -121.7377 | 121.7194 | 0.737 | 1.0895 | 0.77362
1543.6719 | 121.907 | -0.9201 | 120.8725 | -0.012131 | 0.0033282 | 0.057272 | 0.054937 | -0.00069646 | -0.0064258 | -0.0045182 | -0.005371 | 0.03193 | 0.03409 | 0.0073657 | 0.017675 | 0.029732 | -0.0012753 | 0.022888 | 120.8313 | -0.92926 | 120.7352 | -0.78278 | -0.9201 | -0.88806 | -0.23804 | -0.30212 | -0.87433 | -0.23346 | -0.50812 | -0.15564 | -0.15564 | -0.009155 | -0.041199 | -0.13733 | 0.13733 | 0.032043 | 0 | 0.041198 | 0.009155 | 0.045776 | -121.1746 | -121.106 | 0.41199 | 0.76446 | 0.76446 | 0.71869 | 0.71869 | 0.14648 | 121.6644 | 0.36621 | 0.64087 | 121.7606 | 0.57221 | 121.7514 | 0.61798 | -121.8018 | -121.7468 | 121.6553 | 0.68665 | 0.94299 | 0.68207
1545.375 | 121.8018 | -0.98419 | 120.8633 | -0.012131 | 0.0050372 | 0.053 | 0.054937 | 0.00079894 | -0.0070666 | 0.0012496 | -0.0023192 | 0.034066 | 0.034304 | 0.010784 | 0.01853 | 0.02845 | -0.0046933 | 0.10071 | 120.813 | -0.94757 | 120.6985 | -0.81482 | -0.95673 | -0.93842 | -0.30212 | -0.25635 | -0.91095 | -0.31586 | -0.59052 | -0.26093 | -0.23804 | 0.036621 | -0.050354 | -0.16479 | 0.16937 | 0.045776 | 0.027466 | 0.009155 | -0.009155 | 0.073242 | -121.1197 | -121.1792 | 0.39368 | 0.74615 | 0.72327 | 0.67291 | 0.65003 | 0.13275 | 121.6461 | 0.32044 | 0.59509 | 121.7606 | 0.6546 | 121.7972 | 0.72784 | -121.8109 | -121.7743 | 121.6827 | 0.66833 | 1.0849 | 0.68207
1547.125 | 121.8475 | -0.94299 | 120.8954 | -0.012131 | 0.0033282 | 0.056204 | 0.053656 | -5.5462e-05 | -0.008562 | -0.001741 | -0.0023192 | 0.032357 | 0.035158 | 0.012493 | 0.017461 | 0.029732 | -0.0031979 | 0.10986 | 120.845 | -0.93384 | 120.7397 | -0.78735 | -0.90179 | -0.89264 | -0.32959 | -0.25177 | -0.88806 | -0.26093 | -0.53558 | -0.20599 | -0.17853 | 0.009155 | -0.050354 | -0.15564 | 0.15564 | 0.050354 | 0.041199 | 0.041199 | 0.032044 | 0.054931 | -121.1472 | -121.1563 | 0.40741 | 0.76446 | 0.737 | 0.70953 | 0.68207 | 0.14648 | 121.6736 | 0.35248 | 0.62714 | 121.7789 | 0.63629 | 121.788 | 0.69122 | -121.8292 | -121.7834 | 121.6827 | 0.68207 | 1.0529 | 0.6134
1548.8125 | 121.875 | -0.90179 | 120.8908 | -0.0045011 | 0.0033282 | 0.057486 | 0.052374 | -5.5462e-05 | -0.0062122 | -0.001741 | -0.0084228 | 0.030221 | 0.034517 | 0.0062977 | 0.01618 | 0.028878 | 0.0017153 | -0.004578 | 120.8405 | -0.85144 | 120.7718 | -0.70953 | -0.88348 | -0.82398 | -0.24719 | -0.28381 | -0.85602 | -0.26093 | -0.53101 | -0.15106 | -0.17395 | 0.050354 | -0.050354 | -0.11902 | 0.19226 | 0.077819 | 0.01831 | 0.027465 | -0.032044 | 0.045776 | -121.1746 | -121.1517 | 0.37079 | 0.72784 | 0.75073 | 0.68207 | 0.70496 | 0.14191 | 121.6232 | 0.32501 | 0.59509 | 121.6919 | 0.5722 | 121.7422 | 0.61798 | -121.7422 | -121.7468 | 121.6736 | 0.64087 | 0.89722 | 0.6546
1550.5781 | 121.8384 | -0.87891 | 120.9869 | -0.01976 | 0.002901 | 0.055777 | 0.053228 | 0.0029351 | -0.0087756 | -0.0025956 | -0.011475 | 0.034066 | 0.037935 | 0.0067249 | 0.01618 | 0.027596 | -0.0025571 | 0.10986 | 120.8908 | -0.84686 | 120.8267 | -0.68665 | -0.81482 | -0.81024 | -0.25177 | -0.3067 | -0.79651 | -0.31586 | -0.45319 | -0.21973 | -0.23804 | 0.032043 | -0.09613 | -0.16022 | 0.19226 | 0.068664 | 0.064087 | 0.036621 | 0.032044 | 0.082397 | -121.2936 | -121.3028 | 0.42572 | 0.64087 | 0.65918 | 0.55847 | 0.57678 | 0.16022 | 121.6736 | 0.34332 | 0.48065 | 121.7377 | 0.48981 | 121.7697 | 0.5722 | -121.8338 | -121.7834 | 121.7056 | 0.56305 | 0.98877 | 0.62714
1552.2656 | 121.7926 | -0.83771 | 121.0281 | -0.012131 | 0.00033758 | 0.054068 | 0.051306 | -5.5462e-05 | -0.0087756 | -0.0015274 | -0.0084228 | 0.033212 | 0.037722 | 0.0050159 | 0.017461 | 0.027382 | -0.0019163 | 0.054932 | 120.9366 | -0.82855 | 120.7901 | -0.70496 | -0.84228 | -0.79651 | -0.32959 | -0.31586 | -0.78735 | -0.40741 | -0.44861 | -0.25635 | -0.3067 | 0.009156 | -0.091553 | -0.23804 | 0.13275 | 0.041199 | -0.004577 | 0.032043 | -0.013733 | 0.050354 | -121.344 | -121.4355 | 0.3891 | 0.53101 | 0.58136 | 0.48065 | 0.53101 | 0.1236 | 121.6187 | 0.33875 | 0.37994 | 121.7651 | 0.4715 | 121.7743 | 0.52185 | -121.8567 | -121.8155 | 121.6278 | 0.4303 | 0.89264 | 0.50812
1554.0312 | 121.9254 | -0.77362 | 121.0373 | 0.0031279 | -8.9824e-05 | 0.051932 | 0.050879 | 0.00058534 | -0.0087756 | -0.0004592 | -0.005371 | 0.03193 | 0.037722 | 0.0026661 | 0.013189 | 0.02845 | 0.0025699 | 0.022888 | 120.9457 | -0.74158 | 120.932 | -0.58136 | -0.68665 | -0.6546 | -0.22888 | -0.3479 | -0.71411 | -0.29297 | -0.24719 | -0.1236 | -0.20142 | 0.032044 | -0.091552 | -0.10528 | 0.19226 | 0.11902 | 0.086975 | 0.086975 | 0.054931 | 0.05951 | -121.3852 | -121.3303 | 0.52643 | 0.5722 | 0.65002 | 0.5127 | 0.59052 | 0.16022 | 121.6736 | 0.46692 | 0.42114 | 121.6873 | 0.36621 | 121.7194 | 0.42572 | -121.7789 | -121.7514 | 121.7056 | 0.48065 | 0.79651 | 0.54474
1555.7812 | 121.8842 | -0.76446 | 121.0648 | -0.01976 | 0.0020466 | 0.054068 | 0.05216 | 0.00058534 | -0.0074938 | -0.0028092 | -0.005371 | 0.032357 | 0.039431 | 0.0015979 | 0.014471 | 0.02845 | -0.0010617 | 0.027466 | 120.9549 | -0.73242 | 120.932 | -0.55847 | -0.71411 | -0.66834 | -0.21973 | -0.33875 | -0.70496 | -0.29297 | -0.31128 | -0.17395 | -0.19684 | 0.032043 | -0.10986 | -0.13275 | 0.20599 | 0.09613 | 0.050354 | 0.064087 | 0.018311 | 0.059509 | -121.4035 | -121.3577 | 0.45319 | 0.56763 | 0.59051 | 0.50812 | 0.53101 | 0.17395 | 121.6644 | 0.39368 | 0.41199 | 121.6873 | 0.36621 | 121.7194 | 0.42572 | -121.7972 | -121.7697 | 121.6965 | 0.4715 | 0.79193 | 0.54474
1557.5312 | 121.9254 | -0.70953 | 121.0831 | -0.01976 | 0.0043964 | 0.057059 | 0.053015 | 0.0022943 | -0.0059986 | -0.0043046 | -0.005371 | 0.035562 | 0.038362 | 0.013988 | 0.016393 | 0.02845 | -0.00084805 | 0.036621 | 121.0373 | -0.70496 | 120.9824 | -0.51727 | -0.70038 | -0.64545 | -0.19684 | -0.36163 | -0.67291 | -0.25177 | -0.25635 | -0.14648 | -0.17395 | 0.004578 | -0.045777 | -0.10071 | 0.19226 | 0.064087 | 0.009156 | 0.059509 | 0.004578 | 0.036621 | -121.4447 | -121.3348 | 0.45319 | 0.53558 | 0.56305 | 0.49896 | 0.52643 | 0.18768 | 121.6873 | 0.41656 | 0.42114 | 121.7422 | 0.31128 | 121.7468 | 0.3479 | -121.788 | -121.756 | 121.6919 | 0.45776 | 0.74616 | 0.5127
1559.2969 | 121.9345 | -0.72784 | 121.0648 | -0.012131 | -0.0013714 | 0.056418 | 0.049811 | -0.0021919 | -0.011339 | -0.0011002 | -0.0084228 | 0.034066 | 0.03879 | 0.0024525 | 0.01618 | 0.029305 | -0.0017027 | 0.050354 | 120.9686 | -0.72327 | 120.9824 | -0.53558 | -0.6546 | -0.62714 | -0.17853 | -0.32959 | -0.67291 | -0.2655 | -0.25177 | -0.11444 | -0.17853 | 0.004577 | -0.09613 | -0.082397 | 0.19226 | 0.10071 | 0.073242 | 0.096131 | 0.068665 | 0.054931 | -121.3943 | -121.3303 | 0.47607 | 0.54932 | 0.6134 | 0.49438 | 0.55847 | 0.18768 | 121.7056 | 0.42114 | 0.40741 | 121.6919 | 0.34332 | 121.6965 | 0.39825 | -121.788 | -121.7377 | 121.7102 | 0.46234 | 0.7782 | 0.54932
1561.0625 | 121.8979 | -0.73242 | 121.0693 | -0.0045011 | 0.00033758 | 0.055563 | 0.050238 | -0.0013373 | -0.0087756 | -0.0013138 | -0.005371 | 0.032571 | 0.035585 | 0.0056567 | 0.017248 | 0.027169 | 6.346e-06 | 0.10986 | 121.0007 | -0.70953 | 121.0007 | -0.52643 | -0.64087 | -0.61798 | -0.21057 | -0.29755 | -0.67749 | -0.26093 | -0.29755 | -0.14648 | -0.1831 | 0.022888 | -0.068665 | -0.068665 | 0.20599 | 0.11444 | 0.091553 | 0.091553 | 0.068665 | 0.054932 | -121.3669 | -121.3303 | 0.43488 | 0.54932 | 0.58594 | 0.49439 | 0.53101 | 0.18311 | 121.7102 | 0.37994 | 0.41657 | 121.7102 | 0.37994 | 121.7331 | 0.43488 | -121.7789 | -121.7468 | 121.7331 | 0.4715 | 0.84229 | 0.52185
1562.8438 | 121.9299 | -0.81482 | 120.9778 | -0.012131 | 0.0052508 | 0.055563 | 0.055151 | 0.0027215 | -0.0083484 | -0.0030228 | -0.005371 | 0.032998 | 0.037508 | 0.0052295 | 0.017248 | 0.029305 | 0.0021425 | 0.068665 | 120.9412 | -0.77362 | 120.9274 | -0.59509 | -0.74616 | -0.71411 | -0.1831 | -0.27924 | -0.75073 | -0.16479 | -0.3067 | -0.10071 | -0.10529 | 0.041198 | -0.036621 | -0.050354 | 0.21973 | 0.10071 | 0.068664 | 0.05951 | 0.027466 | 0.064087 | -121.257 | -121.1426 | 0.50812 | 0.70953 | 0.71411 | 0.64545 | 0.65002 | 0.17853 | 121.7011 | 0.44403 | 0.58594 | 121.7148 | 0.4715 | 121.756 | 0.53558 | -121.7514 | -121.7285 | 121.7422 | 0.65002 | 0.88348 | 0.63171
1564.5469 | 121.7972 | -0.86975 | 120.9869 | -0.012131 | 0.0037556 | 0.057272 | 0.054083 | 0.0033623 | -0.0055712 | -0.0025956 | -0.005371 | 0.034494 | 0.036867 | 0.0056567 | 0.016821 | 0.027382 | -0.00063445 | 0.10529 | 120.9503 | -0.8606 | 120.7993 | -0.72784 | -0.87891 | -0.85602 | -0.25635 | -0.2243 | -0.8194 | -0.28381 | -0.43488 | -0.24261 | -0.21515 | 0.009155 | -0.036621 | -0.18768 | 0.14191 | 0.013733 | -0.009155 | 0.004578 | -0.01831 | 0.050354 | -121.2112 | -121.2708 | 0.43488 | 0.6546 | 0.62714 | 0.60425 | 0.57678 | 0.13275 | 121.6599 | 0.38452 | 0.53558 | 121.8109 | 0.59509 | 121.8201 | 0.64545 | -121.8475 | -121.8063 | 121.669 | 0.58594 | 0.97504 | 0.6134
1566.2969 | 121.7926 | -1.1261 | 120.7535 | -0.012131 | 0.0037556 | 0.056418 | 0.057074 | 0.00079894 | -0.0079212 | -0.0047318 | -0.0084228 | 0.03428 | 0.03409 | 0.012065 | 0.020239 | 0.029091 | -0.00084805 | 0.054932 | 120.7169 | -1.0941 | 120.5338 | -1.0208 | -1.149 | -1.1261 | -0.37537 | -0.25635 | -1.062 | -0.31128 | -0.25635 | -0.28839 | -0.23804 | 0.032044 | -0.036621 | -0.21973 | 0.10529 | 0 | -0.022888 | -0.032044 | -0.054932 | 0.064087 | -121.0098 | -121.0648 | 0.86975 | 0.88806 | 0.83771 | 0.82397 | 0.77362 | 0.073242 | 121.6278 | 0.80566 | 0.75073 | 121.8109 | 0.80566 | 121.843 | 0.86975 | -121.8475 | -121.8155 | 121.6599 | 0.81482 | 1.181 | 0.75073
1568.0469 | 121.8475 | -0.99335 | 120.8633 | -0.012131 | 0.0020466 | 0.054709 | 0.056006 | 0.0031487 | -0.0066394 | -0.0030228 | -0.0023192 | 0.032785 | 0.035158 | 0.0050159 | 0.016821 | 0.0308 | -0.0010617 | 0.004578 | 120.8405 | -0.94757 | 120.6573 | -0.8606 | -1.0071 | -0.97504 | -0.33875 | -0.25177 | -0.93384 | -0.27466 | -0.24719 | -0.21973 | -0.19684 | 0.045776 | -0.022888 | -0.20599 | 0.13275 | 0.01831 | -0.013733 | -0.027466 | -0.059509 | 0.059509 | -121.1151 | -121.138 | 0.74616 | 0.79651 | 0.77362 | 0.737 | 0.71411 | 0.086975 | 121.6049 | 0.68665 | 0.65918 | 121.788 | 0.68207 | 121.8338 | 0.74158 | -121.8109 | -121.7972 | 121.6507 | 0.71869 | 0.99792 | 0.6546
1569.8125 | 121.8201 | -0.99792 | 120.8725 | 0.0031279 | 0.0039692 | 0.055991 | 0.054083 | 0.0027215 | -0.008562 | -0.002382 | -0.005371 | 0.03193 | 0.038362 | 0.0039477 | 0.019598 | 0.031227 | 6.346e-06 | 0.10529 | 120.7718 | -0.97046 | 120.6848 | -0.83313 | -0.98877 | -0.97046 | -0.26093 | -0.21973 | -0.9201 | -0.26093 | -0.27924 | -0.2243 | -0.17853 | 0.027466 | -0.10071 | -0.18768 | 0.16479 | 0.027466 | 0.009155 | 0 | -0.018311 | 0.07782 | -121.0922 | -121.1334 | 0.71869 | 0.8194 | 0.77362 | 0.74158 | 0.6958 | 0.13733 | 121.6553 | 0.64087 | 0.65918 | 121.7422 | 0.70038 | 121.7697 | 0.7782 | -121.843 | -121.7926 | 121.6827 | 0.737 | 1.1032 | 0.737
1571.5 | 121.9299 | -0.93384 | 120.8588 | -0.012131 | 0.002901 | 0.05535 | 0.050024 | 0.0035761 | -0.0072802 | -0.00345 | -0.0023192 | 0.029367 | 0.035372 | 0.0030933 | 0.015752 | 0.031014 | 0.0042789 | 0.018311 | 120.8313 | -0.91095 | 120.7535 | -0.75073 | -0.85602 | -0.85602 | -0.19684 | -0.26093 | -0.89722 | -0.17853 | -0.21515 | -0.073242 | -0.086975 | 0.022888 | -0.027466 | -0.10529 | 0.18311 | 0.07782 | 0.07782 | 0.054932 | 0.054932 | 0.036621 | -121.1197 | -121.0373 | 0.71869 | 0.84686 | 0.8606 | 0.81024 | 0.82398 | 0.16022 | 121.6644 | 0.68207 | 0.71869 | 121.7422 | 0.63629 | 121.7651 | 0.67291 | -121.7697 | -121.756 | 121.6873 | 0.75531 | 0.95215 | 0.737
1573.25 | 121.8704 | -0.93384 | 120.9229 | -0.02739 | -0.00073062 | 0.055563 | 0.051092 | -0.0036871 | -0.0087756 | -0.0004592 | -0.0023192 | 0.030862 | 0.036013 | 0.0035205 | 0.014898 | 0.02845 | 0.00064735 | 0.09613 | 120.8084 | -0.90637 | 120.8084 | -0.71411 | -0.84228 | -0.82398 | -0.17395 | -0.24261 | -0.86975 | -0.21973 | -0.22888 | -0.1236 | -0.1236 | 0.027466 | -0.11444 | -0.11444 | 0.21973 | 0.10986 | 0.091553 | 0.082397 | 0.064087 | 0.064087 | -121.1655 | -121.1426 | 0.70496 | 0.81024 | 0.81024 | 0.74616 | 0.74616 | 0.19226 | 121.7148 | 0.64087 | 0.65002 | 121.7148 | 0.62714 | 121.7422 | 0.69122 | -121.8292 | -121.7926 | 121.7422 | 0.71411 | 1.03 | 0.75989
1575.0156 | 121.8018 | -0.97504 | 120.9137 | -0.012131 | 0.0014056 | 0.05535 | 0.053015 | 0.00037174 | -0.0094164 | -0.0036636 | -0.005371 | 0.030648 | 0.037935 | 0.0088611 | 0.017034 | 0.027169 | 0.0010745 | 0.068665 | 120.8496 | -0.93384 | 120.7123 | -0.81482 | -0.92468 | -0.91095 | -0.27466 | -0.17853 | -0.89722 | -0.29755 | -0.32959 | -0.19226 | -0.18768 | 0.041199 | -0.064087 | -0.20142 | 0.16022 | 0.064087 | 0.050354 | 0.022888 | 0.009155 | 0.07782 | -121.0922 | -121.2112 | 0.64545 | 0.78735 | 0.78278 | 0.70953 | 0.70496 | 0.11902 | 121.6461 | 0.56763 | 0.59967 | 121.7834 | 0.71869 | 121.8246 | 0.79651 | -121.8475 | -121.8109 | 121.6873 | 0.67749 | 1.0437 | 0.70038
1576.7812 | 121.9299 | -0.93842 | 120.8908 | -0.012131 | 0.00055118 | 0.054709 | 0.050879 | -0.0013373 | -0.0089892 | -0.0047318 | -0.0084228 | 0.030862 | 0.034517 | 0.0026661 | 0.014684 | 0.02845 | 0.0040651 | 0.018311 | 120.7993 | -0.90179 | 120.7672 | -0.73242 | -0.84686 | -0.83771 | -0.16022 | -0.22888 | -0.86975 | -0.17395 | -0.16937 | -0.059509 | -0.086975 | 0.036622 | -0.091553 | -0.1236 | 0.20599 | 0.10071 | 0.091553 | 0.064086 | 0.054931 | 0.068665 | -121.1197 | -121.0648 | 0.76904 | 0.85144 | 0.87891 | 0.78278 | 0.81024 | 0.16937 | 121.669 | 0.70038 | 0.6958 | 121.701 | 0.64087 | 121.7377 | 0.70953 | -121.7926 | -121.7606 | 121.7056 | 0.76447 | 0.95673 | 0.7782
1578.4844 | 121.8155 | -0.85602 | 121.0327 | -0.01976 | -0.00051702 | 0.054282 | 0.053656 | -0.00048286 | -0.0072802 | -0.0008866 | -0.005371 | 0.032998 | 0.036867 | 0.0069385 | 0.016821 | 0.027809 | -0.0014891 | 0.050354 | 120.9778 | -0.83313 | 120.7947 | -0.737 | -0.84228 | -0.83771 | -0.2655 | -0.19226 | -0.78735 | -0.25635 | -0.36163 | -0.1831 | -0.16937 | 0.022888 | -0.054932 | -0.23804 | 0.11902 | 0.01831 | 0.013733 | -0.004578 | -0.009155 | 0.068664 | -121.225 | -121.2891 | 0.49438 | 0.68664 | 0.67291 | 0.61798 | 0.60425 | 0.09613 | 121.6278 | 0.42572 | 0.53101 | 121.8109 | 0.59509 | 121.8338 | 0.66376 | -121.8658 | -121.8201 | 121.6507 | 0.59967 | 0.90637 | 0.59051
1580.25 | 121.7972 | -0.88806 | 121.0236 | -0.012131 | 0.00033758 | 0.055563 | 0.051733 | -0.0043281 | -0.010271 | -0.0043046 | -0.005371 | 0.032571 | 0.036867 | 0.0086475 | 0.015752 | 0.028664 | 0.0034243 | 0.054932 | 120.932 | -0.84686 | 120.7764 | -0.75531 | -0.85144 | -0.82855 | -0.24719 | -0.17395 | -0.81024 | -0.2655 | -0.3479 | -0.16937 | -0.16937 | 0.041199 | -0.091553 | -0.24719 | 0.13275 | 0.05951 | 0.036622 | 0.018311 | -0.004577 | 0.07782 | -121.1975 | -121.2891 | 0.54016 | 0.71869 | 0.71869 | 0.64087 | 0.64087 | 0.091553 | 121.6232 | 0.46234 | 0.54474 | 121.7789 | 0.63629 | 121.8201 | 0.71411 | -121.8704 | -121.8338 | 121.6644 | 0.62256 | 0.94299 | 0.64087
1582 | 121.9666 | -0.89722 | 120.9 | -0.012131 | 0.00076478 | 0.05535 | 0.050879 | -5.5462e-05 | -0.010271 | -0.00345 | -0.005371 | 0.031717 | 0.033663 | 0.018047 | 0.014043 | 0.029946 | 0.0019289 | 0.073242 | 120.8084 | -0.87891 | 120.8542 | -0.64545 | -0.7782 | -0.76446 | -0.068665 | -0.21973 | -0.83771 | -0.12817 | -0.14191 | -0.032043 | -0.064087 | 0.018311 | -0.091552 | -0.045776 | 0.25177 | 0.13275 | 0.11902 | 0.11444 | 0.10071 | 0.059509 | -121.1197 | -121.0281 | 0.75531 | 0.83313 | 0.86517 | 0.77362 | 0.80566 | 0.23346 | 121.7331 | 0.6958 | 0.70953 | 121.6873 | 0.61798 | 121.7056 | 0.67749 | -121.7789 | -121.7377 | 121.7514 | 0.76904 | 0.97046 | 0.82855
1583.7656 | 121.8567 | -0.84686 | 121.0281 | -0.01976 | 0.0043964 | 0.057272 | 0.055578 | -0.0030463 | -0.0040758 | -0.0013138 | -0.0023192 | 0.034066 | 0.035372 | 0.010784 | 0.016393 | 0.029305 | -0.0059751 | 0.11902 | 120.9778 | -0.81024 | 120.8542 | -0.6958 | -0.79193 | -0.79193 | -0.16479 | -0.16937 | -0.76446 | -0.20142 | -0.32501 | -0.1236 | -0.091553 | 0.036621 | -0.050354 | -0.17395 | 0.15106 | 0.054932 | 0.054932 | 0.018311 | 0.018311 | 0.082398 | -121.1975 | -121.2296 | 0.52185 | 0.75531 | 0.72327 | 0.67291 | 0.64087 | 0.11444 | 121.6644 | 0.43945 | 0.56305 | 121.788 | 0.59509 | 121.8246 | 0.67749 | -121.8384 | -121.7926 | 121.701 | 0.64545 | 0.96588 | 0.68207
1585.4688 | 121.8979 | -0.86517 | 120.9824 | 0.0031279 | 0.0020466 | 0.056845 | 0.052588 | 0.0014397 | -0.00963 | -0.0021682 | -0.005371 | 0.032144 | 0.03644 | 0.0090747 | 0.017248 | 0.028878 | -0.0044797 | 0.004578 | 120.8908 | -0.86517 | 120.8038 | -0.70953 | -0.84686 | -0.81024 | -0.16479 | -0.19226 | -0.83313 | -0.17853 | -0.19226 | -0.10986 | -0.09613 | 0 | -0.091553 | -0.17853 | 0.15564 | 0.054931 | 0.01831 | 0.054931 | 0.01831 | 0.032043 | -121.1746 | -121.1609 | 0.67291 | 0.76904 | 0.75531 | 0.737 | 0.72327 | 0.15564 | 121.669 | 0.64087 | 0.6546 | 121.756 | 0.64087 | 121.756 | 0.67291 | -121.8475 | -121.8155 | 121.669 | 0.68664 | 0.86975 | 0.70038
1587.2188 | 121.8567 | -0.88806 | 121.0052 | 0.0031279 | 0.0043964 | 0.056845 | 0.055365 | -0.0019781 | -0.0081348 | -0.0013138 | -0.005371 | 0.03428 | 0.034945 | 0.010143 | 0.018957 | 0.028878 | 0.0012881 | 0.12817 | 120.9274 | -0.85602 | 120.845 | -0.71411 | -0.82855 | -0.8194 | -0.15106 | -0.18768 | -0.80566 | -0.16937 | -0.19226 | -0.1236 | -0.11444 | 0.032044 | -0.07782 | -0.16022 | 0.17395 | 0.068665 | 0.05951 | 0.036621 | 0.027466 | 0.082398 | -121.1929 | -121.1746 | 0.6958 | 0.77362 | 0.76447 | 0.69122 | 0.68207 | 0.14191 | 121.7011 | 0.6134 | 0.63629 | 121.7834 | 0.61798 | 121.8155 | 0.70038 | -121.8613 | -121.8109 | 121.7331 | 0.71869 | 1.0162 | 0.737
1588.9688 | 121.9482 | -0.70953 | 121.0648 | -0.012131 | 0.00097838 | 0.054709 | 0.048742 | -0.0013373 | -0.00963 | -0.0021682 | -0.0023192 | 0.029794 | 0.038576 | 0.0062977 | 0.014257 | 0.026314 | -0.0021299 | 0.086975 | 121.0144 | -0.6958 | 121.0281 | -0.46234 | -0.60425 | -0.58136 | -0.054932 | -0.21057 | -0.67749 | -0.13275 | -0.19684 | -0.013733 | -0.036621 | 0.013733 | -0.050354 | -0.036621 | 0.24719 | 0.12817 | 0.10529 | 0.11444 | 0.091553 | 0.032044 | -121.2753 | -121.1975 | 0.5127 | 0.67291 | 0.6958 | 0.64087 | 0.66376 | 0.23346 | 121.7239 | 0.48065 | 0.54474 | 121.7102 | 0.46692 | 121.7239 | 0.49896 | -121.7606 | -121.7422 | 121.7377 | 0.57678 | 0.79651 | 0.6546
1590.7344 | 121.8246 | -0.85602 | 121.019 | -0.0045011 | 0.00033758 | 0.054282 | 0.053656 | -0.00091006 | -0.0089892 | -0.001741 | -0.0084228 | 0.032144 | 0.036653 | 0.0037341 | 0.015325 | 0.029091 | -0.0023435 | 0.045776 | 120.9641 | -0.83313 | 120.8038 | -0.737 | -0.85144 | -0.82855 | -0.24719 | -0.17395 | -0.77362 | -0.26093 | -0.27466 | -0.16479 | -0.17395 | 0.022888 | -0.054932 | -0.21515 | 0.11902 | 0.027466 | 0.004578 | 0.004578 | -0.01831 | 0.082397 | -121.1929 | -121.2799 | 0.58136 | 0.68207 | 0.69122 | 0.59967 | 0.60883 | 0.09613 | 121.637 | 0.49896 | 0.5127 | 121.7972 | 0.59967 | 121.8201 | 0.68207 | -121.8521 | -121.7926 | 121.6599 | 0.59509 | 0.90179 | 0.60883
1592.5 | 121.9528 | -0.76446 | 121.0464 | -0.012131 | 0.0054644 | 0.0577 | 0.053869 | 0.0035761 | -0.0053576 | -0.0015274 | -0.005371 | 0.031076 | 0.036867 | 0.015056 | 0.017461 | 0.028237 | -0.0053343 | 0.086975 | 121.0052 | -0.737 | 120.9778 | -0.55389 | -0.70038 | -0.6546 | -0.045776 | -0.19226 | -0.68665 | -0.07782 | -0.24719 | -0.013733 | -0.022888 | 0.027465 | -0.041199 | -0.068665 | 0.21057 | 0.10986 | 0.064087 | 0.082398 | 0.036622 | 0.077819 | -121.2387 | -121.1243 | 0.51727 | 0.74158 | 0.75073 | 0.66376 | 0.67291 | 0.18311 | 121.7148 | 0.43945 | 0.60883 | 121.7422 | 0.49438 | 121.7697 | 0.5722 | -121.7834 | -121.7331 | 121.7422 | 0.68664 | 0.85144 | 0.71869
1594.1875 | 121.8201 | -0.78278 | 121.1105 | -0.01976 | 0.0014056 | 0.057272 | 0.052374 | -0.0051825 | -0.0083484 | -0.0019546 | -0.005371 | 0.030435 | 0.037508 | 0.0030933 | 0.018316 | 0.027809 | 0.0021425 | 0.086975 | 121.0098 | -0.737 | 120.9137 | -0.59967 | -0.737 | -0.70953 | -0.16022 | -0.13275 | -0.70038 | -0.21057 | -0.39368 | -0.11902 | -0.1236 | 0.045776 | -0.10071 | -0.19684 | 0.18311 | 0.073242 | 0.045776 | 0.027466 | 0 | 0.082398 | -121.2433 | -121.3211 | 0.3891 | 0.65918 | 0.66376 | 0.57678 | 0.58136 | 0.13733 | 121.6507 | 0.3067 | 0.48981 | 121.7468 | 0.56763 | 121.7926 | 0.65003 | -121.8475 | -121.8109 | 121.6965 | 0.57221 | 0.86975 | 0.62256
1595.9375 | 121.9574 | -0.72784 | 121.0648 | -0.012131 | -0.0011578 | 0.054068 | 0.051092 | -0.0028327 | -0.011553 | -0.0057998 | -0.005371 | 0.028512 | 0.03879 | 0.010997 | 0.015112 | 0.030587 | -0.00020725 | 0.036621 | 121.0098 | -0.71411 | 120.9869 | -0.53101 | -0.63629 | -0.61798 | -0.059509 | -0.16937 | -0.68207 | -0.07782 | -0.2243 | 0.027466 | -0.022888 | 0.013733 | -0.054931 | -0.07782 | 0.19684 | 0.10986 | 0.091552 | 0.09613 | 0.077819 | 0.045776 | -121.2341 | -121.1426 | 0.50354 | 0.70496 | 0.75531 | 0.65918 | 0.70953 | 0.18311 | 121.701 | 0.45776 | 0.60425 | 121.7239 | 0.5127 | 121.7377 | 0.55847 | -121.7789 | -121.7468 | 121.7148 | 0.65002 | 0.76447 | 0.66834
1597.6875 | 121.9711 | -0.70953 | 121.106 | -0.012131 | 0.00055118 | 0.055991 | 0.04917 | 0.00037174 | -0.0083484 | -0.0030228 | -0.005371 | 0.030435 | 0.036867 | 0.0011707 | 0.015325 | 0.030373 | 0.0017153 | 0.091553 | 121.0052 | -0.71411 | 121.0327 | -0.46234 | -0.60883 | -0.58594 | -0.004578 | -0.1831 | -0.66376 | -0.082397 | -0.21515 | 0.027466 | -0.018311 | -0.004577 | -0.10071 | -0.073242 | 0.24719 | 0.1236 | 0.10071 | 0.12817 | 0.10529 | 0.045777 | -121.2891 | -121.1884 | 0.49438 | 0.69122 | 0.737 | 0.64545 | 0.69122 | 0.25177 | 121.7468 | 0.44861 | 0.58136 | 121.7194 | 0.48065 | 121.7148 | 0.52643 | -121.8201 | -121.7697 | 121.7422 | 0.62714 | 0.80109 | 0.70496
1599.375 | 121.8567 | -0.74158 | 121.1288 | -0.0045011 | 0.0024738 | 0.055563 | 0.053869 | -0.00048286 | -0.0098438 | -0.002382 | -0.0023192 | 0.031717 | 0.035799 | 0.010997 | 0.017461 | 0.027809 | -0.0023435 | 0.082397 | 121.0831 | -0.72784 | 120.9412 | -0.63171 | -0.71869 | -0.71411 | -0.16479 | -0.12817 | -0.68207 | -0.16479 | -0.3479 | -0.086975 | -0.086975 | 0.013733 | -0.045776 | -0.18768 | 0.10986 | 0.027466 | 0.022888 | 0.013733 | 0.009155 | 0.059509 | -121.257 | -121.2936 | 0.39368 | 0.6546 | 0.6546 | 0.59509 | 0.59509 | 0.09613 | 121.669 | 0.33417 | 0.51727 | 121.8109 | 0.55389 | 121.8246 | 0.6134 | -121.8567 | -121.8109 | 121.6827 | 0.57678 | 0.82397 | 0.57678
1601.125 | 121.9345 | -0.71411 | 121.1197 | 0.0031279 | 0.0039692 | 0.056418 | 0.054724 | -5.5462e-05 | -0.0072802 | -0.0015274 | -0.0023192 | 0.030862 | 0.039217 | 0.0082203 | 0.014684 | 0.026955 | 0.0012881 | 0.018311 | 121.0831 | -0.70953 | 120.9686 | -0.58136 | -0.70953 | -0.67291 | -0.10529 | -0.16479 | -0.63629 | -0.09613 | -0.21515 | -0.045776 | -0.054932 | 0.004577 | -0.036621 | -0.15106 | 0.13275 | 0.041198 | 0.004577 | 0.036621 | 0 | 0.077819 | -121.2845 | -121.2158 | 0.49896 | 0.65918 | 0.66834 | 0.58136 | 0.59052 | 0.12817 | 121.6782 | 0.42114 | 0.54016 | 121.7926 | 0.4715 | 121.7972 | 0.54932 | -121.8292 | -121.756 | 121.6827 | 0.61798 | 0.73242 | 0.60883
1602.8906 | 121.9528 | -0.74158 | 121.0785 | -0.012131 | 0.0050372 | 0.056418 | 0.053228 | 0.0018671 | -0.0081348 | 0.0008224 | -0.0023192 | 0.030435 | 0.035372 | 0.0030933 | 0.01853 | 0.029091 | -0.0014891 | 0.009155 | 121.0693 | -0.72327 | 120.9641 | -0.58136 | -0.71411 | -0.69122 | -0.086975 | -0.16479 | -0.66834 | -0.086975 | -0.22888 | -0.027466 | -0.027466 | 0.01831 | -0.009155 | -0.11444 | 0.16022 | 0.050354 | 0.027466 | 0.032044 | 0.009156 | 0.073242 | -121.2433 | -121.1655 | 0.5127 | 0.71411 | 0.71411 | 0.64087 | 0.64087 | 0.14191 | 121.6873 | 0.43945 | 0.58136 | 121.7926 | 0.50354 | 121.8109 | 0.57678 | -121.8018 | -121.7468 | 121.7056 | 0.6546 | 0.75073 | 0.6546
1604.5938 | 121.8567 | -0.77362 | 121.1334 | -0.012131 | 0.0048236 | 0.054709 | 0.055151 | -0.00026906 | -0.0064258 | -0.001741 | -0.0084228 | 0.031503 | 0.037508 | 0.0011707 | 0.017889 | 0.029732 | -0.00063445 | 0.018311 | 121.051 | -0.75531 | 120.8817 | -0.67749 | -0.79193 | -0.75989 | -0.19226 | -0.13275 | -0.70953 | -0.1831 | -0.33417 | -0.1236 | -0.09613 | 0.018311 | -0.082398 | -0.25177 | 0.096131 | 0.013733 | -0.01831 | -0.004578 | -0.036621 | 0.064087 | -121.2662 | -121.3165 | 0.43945 | 0.67749 | 0.65002 | 0.6134 | 0.58594 | 0.07782 | 121.637 | 0.37537 | 0.52643 | 121.8063 | 0.57678 | 121.8246 | 0.64087 | -121.8887 | -121.843 | 121.6553 | 0.59052 | 0.79193 | 0.58136
1606.3594 | 121.843 | -0.84228 | 121.051 | -0.0045011 | 0.0020466 | 0.053427 | 0.054297 | 0.00037174 | -0.0077074 | -0.0011002 | -0.0023192 | 0.030435 | 0.036226 | 0.0048023 | 0.016821 | 0.031227 | -0.00063445 | 0.050354 | 121.0052 | -0.81024 | 120.8313 | -0.71411 | -0.81482 | -0.81024 | -0.20599 | -0.13275 | -0.78735 | -0.21973 | -0.28381 | -0.13733 | -0.11444 | 0.032043 | -0.045776 | -0.21973 | 0.12817 | 0.032043 | 0.027466 | 0 | -0.004577 | 0.054931 | -121.1838 | -121.2708 | 0.55847 | 0.72784 | 0.70496 | 0.67291 | 0.65002 | 0.096131 | 121.6415 | 0.50354 | 0.56763 | 121.8155 | 0.6546 | 121.8475 | 0.70953 | -121.8613 | -121.8384 | 121.6736 | 0.62256 | 0.89264 | 0.63629
1608.0469 | 121.8704 | -0.90179 | 120.9824 | -0.0045011 | 0.0035418 | 0.054709 | 0.052801 | -0.0013373 | -0.0094164 | -0.0002456 | -0.005371 | 0.03193 | 0.035372 | 0.0039477 | 0.017461 | 0.028023 | 0.0010745 | 0.082397 | 120.9595 | -0.88348 | 120.7855 | -0.79193 | -0.87891 | -0.87891 | -0.20142 | -0.15106 | -0.86517 | -0.19226 | -0.21515 | -0.10529 | -0.09613 | 0.01831 | -0.022888 | -0.19684 | 0.10986 | 0.022888 | 0.022888 | 0.004578 | 0.004578 | 0.036621 | -121.1334 | -121.1746 | 0.68664 | 0.80566 | 0.79651 | 0.76904 | 0.75989 | 0.091553 | 121.669 | 0.65002 | 0.67291 | 121.843 | 0.71411 | 121.8613 | 0.75073 | -121.8658 | -121.8475 | 121.6873 | 0.70953 | 0.98419 | 0.70038
1609.8125 | 121.9666 | -0.85602 | 120.9961 | -0.012131 | 0.00055118 | 0.054709 | 0.050451 | -0.0039007 | -0.0081348 | -0.0015274 | -0.0023192 | 0.031503 | 0.034731 | 0.0041615 | 0.015752 | 0.029518 | 0.00064735 | 0.068665 | 120.9091 | -0.8194 | 120.9137 | -0.58594 | -0.74158 | -0.71869 | -0.022888 | -0.20142 | -0.79193 | -0.10986 | -0.11902 | 0.004578 | -0.027466 | 0.036621 | -0.086975 | -0.082398 | 0.27008 | 0.13733 | 0.11444 | 0.10071 | 0.07782 | 0.064087 | -121.1975 | -121.106 | 0.737 | 0.82855 | 0.8606 | 0.76447 | 0.79651 | 0.23346 | 121.7331 | 0.67291 | 0.68207 | 121.7285 | 0.59052 | 121.7651 | 0.6546 | -121.8155 | -121.788 | 121.7697 | 0.74615 | 0.92468 | 0.83313
1611.5781 | 121.9299 | -1.0254 | 120.8038 | -0.0045011 | 0.0052508 | 0.057913 | 0.054724 | 0.00015814 | -0.0077074 | -0.0032364 | -0.0023192 | 0.031503 | 0.03409 | 0.012279 | 0.018316 | 0.032936 | -0.00084805 | 0.036621 | 120.7764 | -1.0254 | 120.6802 | -0.87433 | -0.98877 | -0.9613 | -0.10529 | -0.20142 | -0.9613 | -0.12817 | -0.036621 | -0.07782 | -0.073242 | 0 | -0.027466 | -0.1236 | 0.15106 | 0.064087 | 0.036621 | 0.064087 | 0.036621 | 0.064087 | -121.0052 | -120.932 | 0.98877 | 0.95215 | 0.94757 | 0.88806 | 0.88348 | 0.15106 | 121.7056 | 0.92468 | 0.83313 | 121.8018 | 0.75989 | 121.8018 | 0.82397 | -121.8292 | -121.7651 | 121.7056 | 0.89722 | 1.062 | 0.9201
1613.3281 | 121.8567 | -1.0345 | 120.8771 | -0.012131 | 0.0039692 | 0.056631 | 0.053656 | 0.0033623 | -0.0070666 | -0.0030228 | -0.0023192 | 0.033212 | 0.035372 | 0.00031607 | 0.017034 | 0.028023 | 0.0036379 | 0.018311 | 120.813 | -1.0254 | 120.639 | -0.90637 | -1.0483 | -1.0391 | -0.21515 | -0.1831 | -0.95215 | -0.21973 | -0.16479 | -0.16937 | -0.15106 | 0.009155 | -0.064087 | -0.23804 | 0.12817 | -0.004578 | -0.013733 | -0.013733 | -0.022888 | 0.082398 | -121.0602 | -121.0968 | 0.86975 | 0.88348 | 0.86517 | 0.80109 | 0.78277 | 0.11902 | 121.6644 | 0.78735 | 0.73242 | 121.8384 | 0.76904 | 121.8475 | 0.85144 | -121.9025 | -121.8292 | 121.6736 | 0.81482 | 1.0529 | 0.8194
1615.0156 | 121.9345 | -0.88806 | 120.9549 | -0.0045011 | 0.0014056 | 0.0577 | 0.052801 | -0.0019781 | -0.0074938 | -3.1996e-05 | -0.0084228 | 0.028512 | 0.035372 | -0.0011791 | 0.017034 | 0.031227 | 0.0029971 | 0.073242 | 120.8862 | -0.88348 | 120.8267 | -0.68207 | -0.83313 | -0.79193 | -0.091553 | -0.21057 | -0.84686 | -0.16937 | -0.11444 | -0.068665 | -0.09613 | 0.004578 | -0.068665 | -0.12817 | 0.20599 | 0.096131 | 0.054932 | 0.091553 | 0.050354 | 0.041199 | -121.1655 | -121.1243 | 0.77362 | 0.79193 | 0.8194 | 0.75073 | 0.7782 | 0.20142 | 121.7102 | 0.73242 | 0.67749 | 121.7697 | 0.63629 | 121.7743 | 0.67749 | -121.8384 | -121.8018 | 121.7148 | 0.71869 | 0.9613 | 0.79651
1616.7656 | 121.9299 | -1.0254 | 120.8084 | -0.02739 | 0.0026874 | 0.056418 | 0.052374 | -0.0019781 | -0.0074938 | -0.0049454 | 0.00073235 | 0.031076 | 0.033236 | 0.0073657 | 0.01618 | 0.029732 | 0.0025699 | 0.013733 | 120.7535 | -1.0025 | 120.6802 | -0.84686 | -0.98877 | -0.94299 | -0.15564 | -0.19684 | -0.9613 | -0.17395 | -0.054932 | -0.073242 | -0.091553 | 0.022889 | -0.054932 | -0.12817 | 0.17853 | 0.082398 | 0.036621 | 0.059509 | 0.013732 | 0.064087 | -121.0052 | -120.9824 | 0.97046 | 0.93384 | 0.95215 | 0.86975 | 0.88806 | 0.15564 | 121.6827 | 0.90637 | 0.78735 | 121.756 | 0.76447 | 121.7789 | 0.82855 | -121.8109 | -121.7697 | 121.7056 | 0.85144 | 1.0391 | 0.86975
1618.4531 | 121.962 | -1.03 | 120.8038 | -0.01976 | 0.001192 | 0.055136 | 0.050665 | -0.00026906 | -0.0092028 | -0.0028092 | -0.0023192 | 0.028939 | 0.033876 | 0.016765 | 0.016821 | 0.029732 | -0.00084805 | 0.10071 | 120.7397 | -0.99335 | 120.7581 | -0.77362 | -0.91553 | -0.89264 | -0.054932 | -0.21057 | -0.94299 | -0.14648 | 0.018311 | -0.022888 | -0.050354 | 0.036621 | -0.064087 | -0.045776 | 0.25635 | 0.13733 | 0.11444 | 0.10071 | 0.07782 | 0.086975 | -121.0144 | -120.9503 | 1.0483 | 0.97961 | 1.0071 | 0.89264 | 0.9201 | 0.21973 | 121.7514 | 0.9613 | 0.79651 | 121.7331 | 0.73242 | 121.7697 | 0.8194 | -121.7972 | -121.7468 | 121.788 | 0.88348 | 1.1307 | 0.97504
1620.2031 | 121.9025 | -0.99335 | 120.8954 | -0.012131 | 0.0039692 | 0.056631 | 0.053656 | 0.00015814 | -0.0072802 | 0.0001816 | -0.0023192 | 0.033426 | 0.035585 | 0.0048023 | 0.01917 | 0.029305 | -0.00084805 | 0.1236 | 120.8633 | -0.96588 | 120.7306 | -0.83313 | -0.95673 | -0.94757 | -0.15564 | -0.16479 | -0.92468 | -0.17853 | -0.12817 | -0.10529 | -0.10986 | 0.027466 | -0.032044 | -0.16479 | 0.16022 | 0.045776 | 0.036621 | 0.01831 | 0.009155 | 0.068664 | -121.0602 | -121.0739 | 0.86517 | 0.88348 | 0.88806 | 0.81482 | 0.8194 | 0.13275 | 121.6965 | 0.79651 | 0.74616 | 121.8292 | 0.75989 | 121.8567 | 0.82855 | -121.8613 | -121.8201 | 121.7239 | 0.81482 | 1.1169 | 0.83771
1621.9531 | 121.9757 | -0.91095 | 120.9091 | -0.012131 | 0.00012398 | 0.054282 | 0.053656 | -0.0034735 | -0.008562 | -0.0040908 | -0.005371 | 0.031076 | 0.036653 | 0.0048023 | 0.015752 | 0.028023 | -0.0019163 | 0.086975 | 120.8267 | -0.90637 | 120.8496 | -0.65918 | -0.81024 | -0.79651 | -0.091553 | -0.24261 | -0.87433 | -0.16479 | 0.11444 | -0.036621 | -0.059509 | 0.004578 | -0.082398 | -0.05951 | 0.25177 | 0.11444 | 0.10071 | 0.10986 | 0.09613 | 0.036621 | -121.1517 | -121.0739 | 1.0254 | 0.85144 | 0.87433 | 0.81482 | 0.83771 | 0.24719 | 121.756 | 0.98877 | 0.70953 | 121.7331 | 0.63171 | 121.7377 | 0.66834 | -121.8155 | -121.7834 | 121.7606 | 0.74616 | 0.99793 | 0.8194
1623.7031 | 121.9666 | -1.1124 | 120.7352 | -0.01976 | 0.0033282 | 0.055991 | 0.051947 | 0.0027215 | -0.008562 | -0.0028092 | -0.0023192 | 0.029794 | 0.032381 | 0.0065113 | 0.015966 | 0.030373 | 0.0034243 | 0.027466 | 120.6757 | -1.0666 | 120.6253 | -0.90637 | -1.03 | -0.98419 | -0.13733 | -0.23804 | -1.0345 | -0.16479 | 0.073242 | -0.068665 | -0.068665 | 0.045777 | -0.059509 | -0.10986 | 0.20599 | 0.12817 | 0.082398 | 0.082397 | 0.036621 | 0.07782 | -120.9732 | -120.9 | 1.1856 | 1.0437 | 1.0437 | 0.96588 | 0.96588 | 0.16022 | 121.6919 | 1.1078 | 0.86975 | 121.7422 | 0.79651 | 121.788 | 0.87433 | -121.8018 | -121.7697 | 121.7377 | 0.94757 | 1.1398 | 0.97504
1625.3906 | 121.8109 | -0.65002 | 121.2479 | -0.012131 | 0.0054644 | 0.055563 | 0.056006 | 0.0016535 | -0.0079212 | -0.001741 | -0.0023192 | 0.035989 | 0.040071 | 0.0028797 | 0.017461 | 0.025246 | -0.0012753 | 0.059509 | 121.2112 | -0.63629 | 120.9961 | -0.58136 | -0.69122 | -0.67749 | -0.37537 | -0.28839 | -0.60425 | -0.39368 | -0.073242 | -0.32959 | -0.1236 | 0.013732 | -0.036621 | -0.25177 | 0.068664 | -0.027466 | -0.041199 | -0.041198 | -0.054931 | 0.045776 | -121.5363 | -121.6415 | 0.57678 | 0.52643 | 0.32043 | 0.48065 | 0.27466 | 0.054932 | 121.6324 | 0.53101 | 0.21057 | 121.8475 | 0.31586 | 121.8613 | 0.36163 | -121.8842 | -121.8521 | 121.6461 | 0.25635 | 0.70953 | 0.27466
1627.1406 | 121.8658 | -0.59967 | 121.3348 | -0.012131 | 0.0014056 | 0.054068 | 0.054083 | 0.00079894 | -0.0089892 | -0.005159 | -0.011475 | 0.037698 | 0.040071 | 0.0054431 | 0.015752 | 0.025246 | -0.0023435 | 0.091553 | 121.2341 | -0.5722 | 121.1151 | -0.4715 | -0.56305 | -0.55847 | -0.33875 | -0.28839 | -0.50812 | -0.33875 | -0.022888 | -0.25635 | -0.091553 | 0.027465 | -0.10071 | -0.21973 | 0.12817 | 0.041198 | 0.036621 | 0.013733 | 0.009156 | 0.091552 | -121.6232 | -121.6736 | 0.57678 | 0.50812 | 0.34332 | 0.41656 | 0.25177 | 0.10071 | 121.6873 | 0.48523 | 0.16937 | 121.8063 | 0.21973 | 121.8338 | 0.31128 | -121.907 | -121.843 | 121.7148 | 0.26093 | 0.69122 | 0.26093
1628.8281 | 121.9299 | -0.49896 | 121.376 | -0.0045011 | 0.00097838 | 0.055136 | 0.053228 | -0.00069646 | -0.008562 | -0.0004592 | -0.005371 | 0.037057 | 0.041353 | 0.0039477 | 0.01618 | 0.027809 | -0.0012753 | 0.11444 | 121.2662 | -0.44861 | 121.2616 | -0.27466 | -0.3891 | -0.37079 | -0.19684 | -0.32044 | -0.4303 | -0.2655 | 0.022888 | -0.15106 | -0.11444 | 0.050354 | -0.10986 | -0.11444 | 0.2243 | 0.12817 | 0.10986 | 0.077819 | 0.059509 | 0.068664 | -121.6965 | -121.6415 | 0.52185 | 0.38452 | 0.3479 | 0.31586 | 0.27924 | 0.17395 | 121.7102 | 0.45319 | 0.1648 | 121.7148 | 0.10986 | 121.7651 | 0.17853 | -121.8246 | -121.8063 | 121.7606 | 0.23346 | 0.6134 | 0.30212
1630.6094 | 121.9849 | -0.44403 | 121.3989 | -0.012131 | 0.00012398 | 0.054068 | 0.051306 | -0.0030463 | -0.010271 | -0.0028092 | -0.0084228 | 0.041116 | 0.038149 | -0.0069469 | 0.018743 | 0.026955 | 0.0021425 | 0.064087 | 121.3074 | -0.42572 | 121.312 | -0.21973 | -0.33875 | -0.31128 | -0.15564 | -0.29755 | -0.37994 | -0.20599 | 0.059509 | -0.086975 | -0.09613 | 0.018311 | -0.091553 | -0.086975 | 0.2243 | 0.13275 | 0.10529 | 0.11444 | 0.086975 | 0.064087 | -121.6965 | -121.6049 | 0.50354 | 0.3479 | 0.35706 | 0.28381 | 0.29297 | 0.20599 | 121.7377 | 0.43945 | 0.17395 | 121.7331 | 0.082398 | 121.7514 | 0.14649 | -121.8246 | -121.7789 | 121.756 | 0.23804 | 0.50812 | 0.28839
1632.375 | 121.9254 | -0.40283 | 121.4539 | -0.012131 | 0.0026874 | 0.055563 | 0.051733 | 0.0037897 | -0.0072802 | -0.0025956 | -0.0023192 | 0.041543 | 0.040926 | -0.0011791 | 0.015752 | 0.026741 | -0.0012753 | 0.045776 | 121.3806 | -0.36621 | 121.3348 | -0.17853 | -0.32959 | -0.30212 | -0.1831 | -0.28839 | -0.31128 | -0.23804 | -0.013733 | -0.15564 | -0.14648 | 0.036621 | -0.073242 | -0.11902 | 0.2243 | 0.10071 | 0.073242 | 0.064087 | 0.036621 | 0.091553 | -121.7422 | -121.6919 | 0.3891 | 0.25635 | 0.24719 | 0.16479 | 0.15564 | 0.18768 | 121.7011 | 0.29755 | 0.073242 | 121.7468 | 0.022888 | 121.7834 | 0.11444 | -121.8201 | -121.7651 | 121.7377 | 0.1648 | 0.44861 | 0.21973
1634.0781 | 121.8292 | -0.41199 | 121.5271 | -0.0045011 | -0.00051702 | 0.054068 | 0.052588 | 0.0018671 | -0.008562 | -0.0013138 | -0.0023192 | 0.047097 | 0.043489 | -0.0086559 | 0.016607 | 0.022896 | -0.0014891 | 0.054932 | 121.4264 | -0.37537 | 121.2799 | -0.2655 | -0.3891 | -0.37079 | -0.29755 | -0.24261 | -0.32044 | -0.32501 | -0.10071 | -0.23804 | -0.21973 | 0.036621 | -0.10071 | -0.24719 | 0.14648 | 0.041198 | 0.022888 | 0.004577 | -0.013733 | 0.091552 | -121.7697 | -121.8521 | 0.31128 | 0.19226 | 0.17395 | 0.10071 | 0.082398 | 0.10986 | 121.6553 | 0.21973 | -0.004577 | 121.8018 | 0.07782 | 121.8384 | 0.16937 | -121.9025 | -121.8475 | 121.6919 | 0.086975 | 0.46692 | 0.11444
1635.8438 | 121.9711 | -0.34332 | 121.4905 | -0.012131 | -0.002226 | 0.054068 | 0.052374 | 0.0025079 | -0.0094164 | -0.0013138 | -0.005371 | 0.044107 | 0.040499 | -0.0035291 | 0.016607 | 0.025246 | -0.0025571 | 0.10986 | 121.3852 | -0.32959 | 121.4355 | -0.11902 | -0.22888 | -0.23346 | -0.15106 | -0.27466 | -0.27924 | -0.21515 | 0.041199 | -0.09613 | -0.091553 | 0.013733 | -0.10529 | -0.054932 | 0.2243 | 0.10986 | 0.11444 | 0.096131 | 0.10071 | 0.064087 | -121.7651 | -121.7056 | 0.38452 | 0.25177 | 0.24719 | 0.18768 | 0.18311 | 0.21057 | 121.7651 | 0.32043 | 0.064087 | 121.7148 | 0.004578 | 121.7285 | 0.068665 | -121.8201 | -121.7697 | 121.7789 | 0.12817 | 0.45319 | 0.19226
1637.6094 | 121.8796 | -0.37994 | 121.4996 | -0.012131 | 0.0016192 | 0.054709 | 0.053869 | 0.0033623 | -0.0081348 | -0.0019546 | -0.005371 | 0.048166 | 0.043917 | -0.010365 | 0.017248 | 0.023751 | -0.0010617 | 0.10071 | 121.4493 | -0.37079 | 121.3303 | -0.23346 | -0.34332 | -0.33417 | -0.23346 | -0.24719 | -0.32959 | -0.24719 | -0.059509 | -0.19226 | -0.15564 | 0.009155 | -0.050354 | -0.16937 | 0.14649 | 0.045777 | 0.036621 | 0.036622 | 0.027466 | 0.050354 | -121.7468 | -121.7468 | 0.32044 | 0.2243 | 0.18768 | 0.17395 | 0.13733 | 0.13733 | 121.701 | 0.27008 | 0.082398 | 121.8201 | 0.082398 | 121.8292 | 0.13275 | -121.8704 | -121.8292 | 121.7102 | 0.13275 | 0.48065 | 0.14649
1639.3594 | 121.843 | -0.41657 | 121.5408 | -0.0045011 | -8.9824e-05 | 0.054709 | 0.052588 | -0.0058233 | -0.010698 | -0.0053726 | -0.011475 | 0.047097 | 0.042421 | -0.0020337 | 0.017461 | 0.023537 | -0.0023435 | 0.064087 | 121.4722 | -0.38452 | 121.2753 | -0.28381 | -0.37994 | -0.3891 | -0.28381 | -0.24261 | -0.3479 | -0.32959 | -0.13733 | -0.23346 | -0.17853 | 0.032044 | -0.068665 | -0.2655 | 0.13275 | 0.027466 | 0.036621 | -0.004578 | 0.004577 | 0.068665 | -121.7834 | -121.8704 | 0.27924 | 0.23804 | 0.18311 | 0.16937 | 0.11444 | 0.10071 | 121.6599 | 0.21057 | 0.01831 | 121.8567 | 0.10528 | 121.8887 | 0.17395 | -121.9254 | -121.8887 | 121.6919 | 0.086975 | 0.48065 | 0.13275
1641.125 | 121.9528 | -0.34332 | 121.4722 | -0.01976 | 0.0054644 | 0.055777 | 0.053869 | 0.0010125 | -0.006853 | -0.0013138 | -0.0023192 | 0.043252 | 0.042421 | -0.0028881 | 0.017675 | 0.024605 | -0.0012753 | 0.082397 | 121.4127 | -0.31586 | 121.4172 | -0.13733 | -0.28839 | -0.24261 | -0.11902 | -0.27008 | -0.28839 | -0.17395 | -0.050354 | -0.10986 | -0.045776 | 0.027466 | -0.059509 | -0.054932 | 0.20599 | 0.10071 | 0.054932 | 0.073242 | 0.027466 | 0.054932 | -121.7422 | -121.6461 | 0.29297 | 0.29755 | 0.23346 | 0.24262 | 0.17853 | 0.17853 | 121.7331 | 0.23804 | 0.11444 | 121.7285 | 0.01831 | 121.756 | 0.073242 | -121.788 | -121.7606 | 121.7606 | 0.16937 | 0.42572 | 0.2243
1642.8906 | 121.8521 | -0.39368 | 121.5225 | -0.0045011 | 0.006319 | 0.05535 | 0.057074 | 0.0029351 | -0.0064258 | -0.0021682 | -0.0084228 | 0.042184 | 0.043489 | -0.0013927 | 0.018743 | 0.025032 | -0.00020725 | 0.059509 | 121.4722 | -0.3891 | 121.2662 | -0.31586 | -0.43488 | -0.41199 | -0.28839 | -0.24261 | -0.32959 | -0.31128 | -0.20142 | -0.25177 | -0.10986 | 0.004578 | -0.050354 | -0.25635 | 0.07782 | -0.01831 | -0.041198 | -0.022888 | -0.045776 | 0.064087 | -121.7651 | -121.8338 | 0.19226 | 0.28381 | 0.14191 | 0.21973 | 0.07782 | 0.073242 | 121.6553 | 0.12817 | 0.018311 | 121.8613 | 0.086975 | 121.8658 | 0.15106 | -121.9116 | -121.8521 | 121.6599 | 0.082398 | 0.45319 | 0.10529
1644.5938 | 121.8292 | -0.41657 | 121.5179 | 0.0031279 | 0.00055118 | 0.05535 | 0.053442 | -0.0017645 | -0.0083484 | -0.0011002 | -0.0084228 | 0.042184 | 0.043703 | -0.0056653 | 0.018316 | 0.025887 | -0.0017027 | 0.045776 | 121.4584 | -0.38452 | 121.2891 | -0.27924 | -0.37994 | -0.37079 | -0.30212 | -0.24261 | -0.35706 | -0.33875 | -0.17395 | -0.2243 | -0.10986 | 0.032044 | -0.059509 | -0.22888 | 0.13733 | 0.045776 | 0.036621 | 0.013732 | 0.004577 | 0.059509 | -121.7606 | -121.8567 | 0.24262 | 0.3067 | 0.19226 | 0.24719 | 0.13275 | 0.10529 | 121.6736 | 0.18311 | 0.018311 | 121.843 | 0.11444 | 121.875 | 0.17395 | -121.9025 | -121.875 | 121.7056 | 0.07782 | 0.46234 | 0.11444
1646.3594 | 121.8613 | -0.37079 | 121.5363 | -0.01976 | 0.00097838 | 0.056418 | 0.05152 | -0.00069646 | -0.0094164 | -0.0011002 | -0.005371 | 0.041757 | 0.044558 | -0.0073743 | 0.017889 | 0.025032 | -0.0019163 | 0.10986 | 121.431 | -0.32044 | 121.3806 | -0.16937 | -0.29297 | -0.2655 | -0.21973 | -0.23804 | -0.29755 | -0.27924 | -0.12817 | -0.19684 | -0.086975 | 0.050354 | -0.10529 | -0.15564 | 0.20142 | 0.10529 | 0.07782 | 0.054932 | 0.027466 | 0.073243 | -121.7743 | -121.8155 | 0.24261 | 0.28381 | 0.17395 | 0.21057 | 0.10071 | 0.15106 | 121.7011 | 0.16937 | 0.01831 | 121.7514 | 0.059509 | 121.8018 | 0.13275 | -121.8567 | -121.8338 | 121.7514 | 0.091553 | 0.48065 | 0.15106
1648.1094 | 121.8338 | -0.36163 | 121.55 | 0.010757 | 0.0037556 | 0.056631 | 0.055151 | 0.0018671 | -0.0098438 | -0.0002456 | -0.0084228 | 0.044534 | 0.043917 | -0.0037427 | 0.01917 | 0.024605 | -0.0023435 | 0.09613 | 121.4905 | -0.35706 | 121.3531 | -0.22888 | -0.37994 | -0.35248 | -0.28381 | -0.24261 | -0.29297 | -0.30212 | -0.1831 | -0.25635 | -0.10529 | 0.004577 | -0.059509 | -0.19684 | 0.13275 | 0.009155 | -0.018311 | 0.004578 | -0.022888 | 0.068664 | -121.7926 | -121.8521 | 0.17853 | 0.25635 | 0.10528 | 0.18768 | 0.036621 | 0.12817 | 121.7102 | 0.10986 | -0.009155 | 121.8475 | 0.050354 | 121.8521 | 0.11902 | -121.907 | -121.843 | 121.7148 | 0.059509 | 0.45776 | 0.07782
1649.7969 | 121.9711 | -0.29755 | 121.5271 | -0.012131 | 0.0037556 | 0.057059 | 0.053442 | -0.0030463 | -0.0077074 | 0.0023178 | 0.00073235 | 0.042398 | 0.045626 | -0.0031017 | 0.018743 | 0.024391 | -0.0017027 | 0.036621 | 121.5225 | -0.32959 | 121.4081 | -0.16937 | -0.29297 | -0.26093 | -0.1831 | -0.24719 | -0.27924 | -0.1831 | -0.054932 | -0.1236 | 0 | -0.032044 | -0.004578 | -0.11902 | 0.12817 | 0.036621 | 0.004577 | 0.068665 | 0.036621 | 0.01831 | -121.7743 | -121.7102 | 0.24261 | 0.29755 | 0.17395 | 0.27924 | 0.15564 | 0.16022 | 121.7377 | 0.2243 | 0.096131 | 121.8521 | 0.032044 | 121.8201 | 0.050354 | -121.8567 | -121.8063 | 121.7056 | 0.11444 | 0.33417 | 0.11444
1651.5625 | 121.875 | -0.35248 | 121.5729 | -0.01976 | -0.00030342 | 0.054922 | 0.053015 | -0.0041145 | -0.0062122 | -0.0011002 | -0.005371 | 0.043252 | 0.04114 | -0.0060925 | 0.016393 | 0.024819 | -0.0031979 | 0.082397 | 121.4996 | -0.33417 | 121.3348 | -0.23804 | -0.32959 | -0.32044 | -0.27466 | -0.23804 | -0.27008 | -0.30212 | -0.13733 | -0.18768 | -0.086975 | 0.018311 | -0.073242 | -0.23804 | 0.11444 | 0.032043 | 0.022888 | 0.013732 | 0.004577 | 0.082397 | -121.8109 | -121.875 | 0.21515 | 0.2655 | 0.1648 | 0.18311 | 0.082398 | 0.09613 | 121.669 | 0.13275 | -0.032043 | 121.8338 | 0.032044 | 121.8521 | 0.11444 | -121.907 | -121.843 | 121.6873 | 0.050354 | 0.43488 | 0.07782
1653.25 | 121.8475 | -0.35706 | 121.55 | -0.0045011 | 0.00012398 | 0.054282 | 0.053442 | -0.0015509 | -0.0083484 | -0.002382 | -0.0084228 | 0.043039 | 0.043276 | -0.0035291 | 0.014898 | 0.02546 | -0.00084805 | 0.059509 | 121.4951 | -0.32501 | 121.3303 | -0.22888 | -0.34332 | -0.31128 | -0.26093 | -0.2243 | -0.30212 | -0.31128 | -0.15564 | -0.21515 | -0.11444 | 0.032044 | -0.054932 | -0.21973 | 0.12817 | 0.045777 | 0.013733 | 0.013733 | -0.018311 | 0.054932 | -121.7743 | -121.8613 | 0.20142 | 0.24261 | 0.14191 | 0.18768 | 0.086975 | 0.09613 | 121.6553 | 0.14648 | -0.009155 | 121.8201 | 0.07782 | 121.8521 | 0.13275 | -121.875 | -121.8521 | 121.6873 | 0.045777 | 0.41656 | 0.096131
1655.0156 | 121.9208 | -0.33417 | 121.5546 | -0.0045011 | 0.001833 | 0.054922 | 0.052588 | -0.00026906 | -0.008562 | -0.0019546 | -0.005371 | 0.037912 | 0.041567 | -0.00011113 | 0.014684 | 0.025887 | -0.00042085 | -0.004578 | 121.4767 | -0.30212 | 121.3943 | -0.15564 | -0.27008 | -0.23346 | -0.18768 | -0.27466 | -0.27008 | -0.23804 | -0.10986 | -0.14648 | -0.050354 | 0.032043 | -0.077819 | -0.16022 | 0.17853 | 0.10071 | 0.064086 | 0.068665 | 0.032043 | 0.064086 | -121.8292 | -121.7926 | 0.2243 | 0.28381 | 0.18768 | 0.21973 | 0.1236 | 0.14648 | 121.6965 | 0.16022 | 0.032044 | 121.7789 | -0.004577 | 121.8109 | 0.059509 | -121.8567 | -121.8246 | 121.7285 | 0.09613 | 0.32959 | 0.14648
1656.7812 | 121.9894 | -0.3067 | 121.5225 | -0.01976 | 0.002901 | 0.056204 | 0.053656 | -0.00048286 | -0.0064258 | -0.00345 | -0.005371 | 0.039193 | 0.042421 | -0.0069469 | 0.016393 | 0.0261 | -0.0027707 | 0.073242 | 121.4859 | -0.28839 | 121.4493 | -0.10986 | -0.25635 | -0.21973 | -0.10529 | -0.27466 | -0.25177 | -0.17395 | -0.07782 | -0.073242 | -0.013733 | 0.018311 | -0.036621 | -0.073242 | 0.19684 | 0.086975 | 0.050354 | 0.068664 | 0.032043 | 0.054932 | -121.7972 | -121.6965 | 0.22888 | 0.29297 | 0.23346 | 0.23804 | 0.17853 | 0.17853 | 121.7377 | 0.17395 | 0.07782 | 121.7743 | -0.022888 | 121.7926 | 0.032044 | -121.8109 | -121.7743 | 121.756 | 0.13275 | 0.37994 | 0.20142
1658.4688 | 121.9482 | -0.30212 | 121.5637 | -0.012131 | 0.001192 | 0.056418 | 0.054724 | -0.0024055 | -0.0074938 | -0.002382 | -0.005371 | 0.03663 | 0.041353 | 0.00052987 | 0.017461 | 0.023323 | -0.0031979 | 0.064087 | 121.5134 | -0.27008 | 121.4584 | -0.086975 | -0.24261 | -0.19684 | -0.091553 | -0.25635 | -0.2655 | -0.16937 | -0.064087 | -0.086975 | -0.027466 | 0.032043 | -0.050354 | -0.10529 | 0.21515 | 0.10529 | 0.059509 | 0.073243 | 0.027466 | 0.036621 | -121.8201 | -121.7331 | 0.23804 | 0.27466 | 0.21515 | 0.23804 | 0.17853 | 0.18311 | 121.7285 | 0.20142 | 0.09613 | 121.7834 | 0.009155 | 121.8155 | 0.045776 | -121.8338 | -121.8292 | 121.7606 | 0.13275 | 0.36621 | 0.21057
1660.2188 | 121.8521 | -0.34332 | 121.5866 | -0.0045011 | 0.006319 | 0.055563 | 0.053656 | 0.00037174 | -0.0062122 | -0.0040908 | -0.0023192 | 0.040475 | 0.042635 | -0.0028881 | 0.017675 | 0.025246 | -0.0025571 | 0.045776 | 121.55 | -0.31128 | 121.3348 | -0.27008 | -0.3891 | -0.3479 | -0.2655 | -0.21057 | -0.29297 | -0.31128 | -0.1831 | -0.20599 | -0.10986 | 0.032044 | -0.036621 | -0.25177 | 0.073242 | -0.004577 | -0.045776 | -0.036621 | -0.07782 | 0.050354 | -121.7972 | -121.8979 | 0.16022 | 0.23346 | 0.13733 | 0.18311 | 0.086975 | 0.041198 | 121.6461 | 0.10986 | -0.01831 | 121.8613 | 0.082398 | 121.8933 | 0.13275 | -121.8979 | -121.8796 | 121.6782 | 0.032044 | 0.3891 | 0.07782
1661.9688 | 121.8979 | -0.34332 | 121.582 | -0.0045011 | 0.0035418 | 0.056418 | 0.05451 | 0.0018671 | -0.0092028 | 0.0023178 | -0.005371 | 0.03898 | 0.044344 | -0.00096553 | 0.019384 | 0.026741 | -0.0019163 | 0.11902 | 121.5134 | -0.30212 | 121.4081 | -0.16479 | -0.29755 | -0.27924 | -0.16937 | -0.23346 | -0.27466 | -0.22888 | -0.11444 | -0.13275 | -0.054932 | 0.041199 | -0.068664 | -0.17395 | 0.17853 | 0.064087 | 0.045777 | 0.022888 | 0.004578 | 0.068665 | -121.8155 | -121.8109 | 0.22888 | 0.28839 | 0.21057 | 0.21973 | 0.14191 | 0.13733 | 121.7102 | 0.16022 | 0.045776 | 121.8155 | 0.041199 | 121.8567 | 0.10986 | -121.8842 | -121.8567 | 121.7514 | 0.11444 | 0.46234 | 0.17395
1663.7344 | 121.843 | -0.3479 | 121.5775 | -0.012131 | 0.0050372 | 0.05535 | 0.053869 | 0.0018671 | -0.006853 | -0.0057998 | -0.0023192 | 0.039407 | 0.040926 | -0.0018201 | 0.016821 | 0.025673 | 0.00064735 | 0.032043 | 121.5591 | -0.33417 | 121.3074 | -0.25635 | -0.3891 | -0.3479 | -0.27924 | -0.2243 | -0.27466 | -0.29297 | -0.19684 | -0.20599 | -0.10529 | 0.013733 | -0.018311 | -0.27008 | 0.091552 | 0 | -0.041199 | -0.013733 | -0.054932 | 0.073242 | -121.8018 | -121.8704 | 0.15106 | 0.24261 | 0.14191 | 0.16937 | 0.068664 | 0.077819 | 121.6415 | 0.07782 | -0.018311 | 121.8933 | 0.050354 | 121.907 | 0.1236 | -121.9116 | -121.8521 | 121.6553 | 0.054931 | 0.37994 | 0.068664
1665.4219 | 121.9666 | -0.31586 | 121.5866 | 0.010757 | 0.00012398 | 0.055991 | 0.050238 | -0.0015509 | -0.0066394 | -0.0043046 | -0.005371 | 0.037057 | 0.040712 | -0.0022473 | 0.015966 | 0.027169 | -0.0027707 | 0.013733 | 121.4905 | -0.29297 | 121.4035 | -0.14191 | -0.27466 | -0.23346 | -0.15564 | -0.25635 | -0.24719 | -0.21973 | -0.054932 | -0.059509 | -0.041199 | 0.022888 | -0.09613 | -0.18311 | 0.17395 | 0.082398 | 0.041199 | 0.05951 | 0.018311 | 0.068665 | -121.843 | -121.8063 | 0.26093 | 0.27466 | 0.25635 | 0.20599 | 0.18768 | 0.15106 | 121.6965 | 0.19226 | 0.027465 | 121.7834 | -0.009156 | 121.8063 | 0.059509 | -121.8796 | -121.8338 | 121.7194 | 0.09613 | 0.32959 | 0.16022
1667.1875 | 121.9482 | -0.29297 | 121.5591 | -0.0045011 | 0.00076478 | 0.056204 | 0.049383 | -0.0032599 | -0.006853 | -0.0030228 | -0.005371 | 0.036203 | 0.042421 | 0.0033069 | 0.012334 | 0.026314 | -0.0027707 | 0.11444 | 121.4722 | -0.2655 | 121.4722 | -0.09613 | -0.20142 | -0.19226 | -0.086975 | -0.2655 | -0.25177 | -0.21973 | -0.041199 | -0.045776 | -0.041199 | 0.027466 | -0.086975 | -0.086975 | 0.19684 | 0.10071 | 0.091553 | 0.073242 | 0.064087 | 0.041199 | -121.8246 | -121.7789 | 0.25177 | 0.25177 | 0.24719 | 0.21057 | 0.20599 | 0.16937 | 121.7377 | 0.21057 | 0.032043 | 121.7377 | -0.013733 | 121.7651 | 0.027466 | -121.8246 | -121.8109 | 121.7651 | 0.073242 | 0.40741 | 0.20599
1668.9375 | 121.8704 | -0.33417 | 121.6049 | -0.0045011 | 0.0022602 | 0.053427 | 0.05216 | -0.0011237 | -0.008562 | -0.0038772 | -0.0084228 | 0.040048 | 0.041994 | -0.0080151 | 0.016393 | 0.025673 | -0.0023435 | 0.11444 | 121.4905 | -0.28381 | 121.4172 | -0.15106 | -0.27008 | -0.24719 | -0.14648 | -0.22888 | -0.25177 | -0.28839 | -0.14191 | -0.13275 | -0.11902 | 0.050354 | -0.11444 | -0.18768 | 0.1831 | 0.086975 | 0.064086 | 0.036621 | 0.013732 | 0.082397 | -121.8338 | -121.8933 | 0.19226 | 0.21515 | 0.20142 | 0.13275 | 0.11902 | 0.13275 | 121.701 | 0.10986 | -0.036621 | 121.7743 | 0.022888 | 121.8246 | 0.10528 | -121.8887 | -121.8567 | 121.7514 | 0.045776 | 0.44861 | 0.18768
1670.7031 | 121.8842 | -0.32959 | 121.5958 | -0.012131 | 0.001833 | 0.055136 | 0.054724 | -0.0017645 | -0.0077074 | -0.0038772 | -0.005371 | 0.039834 | 0.043489 | 0.0058703 | 0.017675 | 0.023537 | -0.0040525 | 0.091553 | 121.5271 | -0.32501 | 121.3577 | -0.23346 | -0.32044 | -0.31128 | -0.21515 | -0.21973 | -0.27924 | -0.28839 | -0.14648 | -0.12817 | -0.07782 | 0.004578 | -0.068664 | -0.23804 | 0.096131 | 0.018311 | 0.009155 | 0.013733 | 0.004577 | 0.050354 | -121.8155 | -121.8842 | 0.18311 | 0.25177 | 0.20142 | 0.20142 | 0.15106 | 0.091553 | 121.6827 | 0.13275 | -0.009155 | 121.8521 | 0.059509 | 121.8567 | 0.10986 | -121.9208 | -121.875 | 121.6873 | 0.041199 | 0.42114 | 0.11444
1672.4062 | 121.9482 | -0.31586 | 121.5591 | -0.012131 | 0.002901 | 0.054922 | 0.052374 | 0.0035761 | -0.0077074 | -0.001741 | -0.0023192 | 0.037271 | 0.041994 | -0.012929 | 0.01383 | 0.025887 | -0.00063445 | 0.009155 | 121.4951 | -0.29297 | 121.4172 | -0.13733 | -0.26093 | -0.22888 | -0.1236 | -0.24261 | -0.27466 | -0.21057 | -0.059509 | -0.045776 | -0.022888 | 0.022888 | -0.064087 | -0.14191 | 0.17853 | 0.086975 | 0.054932 | 0.064087 | 0.032044 | 0.041199 | -121.8018 | -121.7697 | 0.25635 | 0.29297 | 0.27008 | 0.25177 | 0.22888 | 0.15564 | 121.7102 | 0.21515 | 0.064087 | 121.788 | 0.032043 | 121.8109 | 0.073242 | -121.8521 | -121.8338 | 121.7331 | 0.10529 | 0.32501 | 0.19226
1674.1562 | 121.875 | -0.3479 | 121.5637 | -0.01976 | 0.0022602 | 0.057059 | 0.055365 | 0.00037174 | -0.0087756 | -0.0019546 | -0.0023192 | 0.041543 | 0.043917 | -0.0011791 | 0.015752 | 0.023964 | -0.0029843 | 0.032043 | 121.5454 | -0.31128 | 121.3486 | -0.25177 | -0.37079 | -0.33417 | -0.20142 | -0.20599 | -0.27466 | -0.27924 | -0.16937 | -0.16022 | -0.09613 | 0.036621 | -0.018311 | -0.21515 | 0.09613 | 0.013733 | -0.022889 | -0.022888 | -0.05951 | 0.073242 | -121.7697 | -121.843 | 0.17853 | 0.25177 | 0.18768 | 0.17853 | 0.11444 | 0.059509 | 121.6599 | 0.10529 | -0.004578 | 121.8567 | 0.068664 | 121.8933 | 0.14191 | -121.875 | -121.8384 | 121.6965 | 0.068664 | 0.37994 | 0.14648
1675.9062 | 121.8658 | -0.32959 | 121.5866 | -0.01976 | 0.00055118 | 0.056204 | 0.052588 | -0.00048286 | -0.008562 | -0.0013138 | -0.005371 | 0.038766 | 0.043917 | -0.00011113 | 0.015966 | 0.024819 | -0.00020725 | 0.086975 | 121.5225 | -0.28381 | 121.376 | -0.17395 | -0.30212 | -0.29755 | -0.19684 | -0.2243 | -0.2655 | -0.29297 | -0.15106 | -0.12817 | -0.1236 | 0.045777 | -0.064087 | -0.21057 | 0.15564 | 0.032044 | 0.027466 | -0.013733 | -0.018311 | 0.064087 | -121.8109 | -121.8796 | 0.17853 | 0.20599 | 0.20142 | 0.14191 | 0.13733 | 0.10986 | 121.6599 | 0.11444 | -0.027466 | 121.8063 | 0.041199 | 121.8521 | 0.10529 | -121.8704 | -121.8521 | 121.7056 | 0.036621 | 0.41656 | 0.13275
1677.6719 | 121.843 | -0.31586 | 121.6187 | -0.012131 | 0.0052508 | 0.055136 | 0.055792 | 0.0012261 | -0.0066394 | -0.0036636 | -0.0023192 | 0.039407 | 0.045839 | -0.0022473 | 0.017675 | 0.025032 | -0.0031979 | 0.082397 | 121.5683 | -0.29755 | 121.3623 | -0.2243 | -0.36163 | -0.32044 | -0.24261 | -0.20599 | -0.2655 | -0.29755 | -0.1831 | -0.1831 | -0.13275 | 0.018311 | -0.050354 | -0.25635 | 0.091553 | -0.004578 | -0.045776 | -0.022889 | -0.064087 | 0.050354 | -121.8246 | -121.9162 | 0.13275 | 0.18311 | 0.13275 | 0.13275 | 0.082398 | 0.073242 | 121.6599 | 0.082398 | -0.032043 | 121.8658 | 0.059509 | 121.8842 | 0.10986 | -121.9162 | -121.8842 | 121.6782 | 0.018311 | 0.39825 | 0.073242
1679.4375 | 121.8521 | -0.33875 | 121.6049 | -0.012131 | 0.0052508 | 0.056631 | 0.056646 | 0.00079894 | -0.0059986 | -0.001741 | -0.0084228 | 0.038552 | 0.046694 | -0.0022473 | 0.016607 | 0.025032 | -0.0029843 | 0.10071 | 121.55 | -0.29297 | 121.4081 | -0.17395 | -0.32044 | -0.28839 | -0.17395 | -0.20142 | -0.27008 | -0.25177 | -0.14648 | -0.15564 | -0.1236 | 0.045776 | -0.054931 | -0.19684 | 0.1648 | 0.050354 | 0.01831 | 0.004578 | -0.027466 | 0.068664 | -121.8063 | -121.8567 | 0.19226 | 0.21515 | 0.18311 | 0.14649 | 0.11444 | 0.11902 | 121.701 | 0.1236 | 0.018311 | 121.843 | 0.068665 | 121.8887 | 0.13733 | -121.8979 | -121.875 | 121.7468 | 0.086975 | 0.43945 | 0.1648
1681.2188 | 121.8887 | -0.31586 | 121.6141 | -0.012131 | 0.00461 | 0.056631 | 0.054724 | 0.00079894 | -0.0049304 | -0.001741 | -0.005371 | 0.040902 | 0.04413 | -0.0054517 | 0.015966 | 0.026741 | -0.0049069 | 0.13275 | 121.5454 | -0.27924 | 121.431 | -0.15564 | -0.28839 | -0.27008 | -0.13733 | -0.19684 | -0.24261 | -0.23346 | -0.1236 | -0.12817 | -0.10071 | 0.036621 | -0.068665 | -0.18311 | 0.16022 | 0.045776 | 0.027466 | 0.009155 | -0.009155 | 0.073242 | -121.8109 | -121.8475 | 0.19226 | 0.21515 | 0.18768 | 0.14191 | 0.11444 | 0.1236 | 121.7102 | 0.11902 | 0.009156 | 121.8246 | 0.045777 | 121.8613 | 0.11902 | -121.8933 | -121.8567 | 121.7468 | 0.082398 | 0.44861 | 0.17853
1682.9219 | 121.9025 | -0.33875 | 121.5958 | -0.01976 | 0.0069598 | 0.054709 | 0.05451 | -0.00069646 | -0.0059986 | -0.002382 | -0.0023192 | 0.038766 | 0.043703 | -0.0028881 | 0.01853 | 0.02845 | -0.0010617 | 0.018311 | 121.5866 | -0.3067 | 121.3669 | -0.21973 | -0.34332 | -0.3067 | -0.16479 | -0.18768 | -0.24719 | -0.21973 | -0.14648 | -0.11444 | -0.10071 | 0.032043 | -0.009155 | -0.22888 | 0.11902 | 0.032043 | -0.004578 | 0 | -0.036621 | 0.091553 | -121.7834 | -121.8155 | 0.19226 | 0.23804 | 0.2243 | 0.14648 | 0.13275 | 0.086975 | 121.6736 | 0.10071 | 0.027465 | 121.8933 | 0.059509 | 121.9254 | 0.15106 | -121.9025 | -121.843 | 121.7056 | 0.11902 | 0.35706 | 0.17395
1684.6875 | 121.9208 | -0.32959 | 121.5958 | -0.012131 | 0.0043964 | 0.054922 | 0.055151 | 0.0022943 | -0.0072802 | -0.001741 | -0.0084228 | 0.036843 | 0.042849 | 0.0026661 | 0.018316 | 0.026314 | -0.0029843 | 0.018311 | 121.5866 | -0.30212 | 121.376 | -0.19684 | -0.34332 | -0.3067 | -0.13733 | -0.19684 | -0.2655 | -0.21515 | -0.11902 | -0.086975 | -0.091553 | 0.027466 | -0.009155 | -0.21973 | 0.13275 | 0.022888 | -0.013733 | -0.004578 | -0.041199 | 0.064087 | -121.7926 | -121.8109 | 0.21057 | 0.23804 | 0.24261 | 0.17395 | 0.17853 | 0.10529 | 121.6782 | 0.14648 | 0.050354 | 121.8887 | 0.068665 | 121.9162 | 0.13275 | -121.8979 | -121.8613 | 121.7056 | 0.11444 | 0.3479 | 0.19226
1686.4531 | 121.8521 | -0.38452 | 121.5912 | -0.012131 | 0.0058918 | 0.055777 | 0.055578 | 0.00037174 | -0.0083484 | -0.0019546 | -0.0023192 | 0.038339 | 0.043276 | -0.0011791 | 0.015752 | 0.025673 | 0.00043375 | 0.050354 | 121.5546 | -0.33875 | 121.3257 | -0.26093 | -0.41199 | -0.36163 | -0.21515 | -0.16479 | -0.28381 | -0.26093 | -0.1831 | -0.14648 | -0.13733 | 0.045776 | -0.036622 | -0.2655 | 0.1236 | 0.022888 | -0.027466 | -0.022888 | -0.073242 | 0.10071 | -121.756 | -121.8521 | 0.20142 | 0.24719 | 0.23804 | 0.14648 | 0.13733 | 0.07782 | 121.6644 | 0.10071 | 0.022888 | 121.8933 | 0.11902 | 121.9391 | 0.21973 | -121.9299 | -121.875 | 121.7102 | 0.1236 | 0.43488 | 0.16937
1688.1562 | 121.9025 | -0.41657 | 121.5042 | -0.01976 | 0.0033282 | 0.057272 | 0.053015 | -0.00069646 | -0.0062122 | -0.0036636 | -0.0023192 | 0.036843 | 0.042421 | 0.0077929 | 0.017461 | 0.026741 | 0.0029971 | 0.12817 | 121.4813 | -0.40283 | 121.3211 | -0.24719 | -0.37079 | -0.34332 | -0.1236 | -0.15106 | -0.35706 | -0.16022 | -0.10071 | -0.068665 | -0.068665 | 0.013733 | -0.022888 | -0.1831 | 0.16937 | 0.073242 | 0.045776 | 0.059509 | 0.032043 | 0.059509 | -121.6553 | -121.6644 | 0.31586 | 0.3479 | 0.3479 | 0.28839 | 0.28839 | 0.15564 | 121.7239 | 0.25635 | 0.19684 | 121.8842 | 0.20599 | 121.8979 | 0.2655 | -121.907 | -121.8613 | 121.7377 | 0.25635 | 0.54474 | 0.29297
1689.9219 | 121.9666 | -0.40283 | 121.463 | -0.012131 | -8.9824e-05 | 0.054282 | 0.049383 | 0.0016535 | -0.0083484 | -0.0011002 | -0.011475 | 0.033426 | 0.041567 | -0.00032473 | 0.015539 | 0.027809 | -0.00063445 | 0.10529 | 121.3852 | -0.37079 | 121.3852 | -0.16479 | -0.29755 | -0.27924 | -0.027466 | -0.17853 | -0.32959 | -0.11902 | -0.045776 | 0.022888 | -0.022888 | 0.032043 | -0.07782 | -0.07782 | 0.23804 | 0.1236 | 0.10529 | 0.091553 | 0.073243 | 0.073242 | -121.6415 | -121.582 | 0.35706 | 0.37994 | 0.42572 | 0.3067 | 0.35248 | 0.20599 | 121.756 | 0.28381 | 0.21057 | 121.756 | 0.15106 | 121.788 | 0.2243 | -121.8338 | -121.7926 | 121.788 | 0.28381 | 0.50812 | 0.37537
1691.625 | 121.8704 | -0.4303 | 121.4996 | -0.0045011 | 0.0048236 | 0.053641 | 0.053442 | -0.00069646 | -0.0070666 | -0.0040908 | 0.00073235 | 0.035989 | 0.041353 | 0.0095019 | 0.015966 | 0.028023 | -0.0019163 | 0.068665 | 121.4539 | -0.42114 | 121.2524 | -0.31586 | -0.42572 | -0.40741 | -0.21515 | -0.13733 | -0.36621 | -0.21515 | -0.16022 | -0.10986 | -0.10986 | 0.009155 | -0.045777 | -0.24719 | 0.11444 | 0.022888 | 0.004578 | 0.013733 | -0.004577 | 0.064087 | -121.637 | -121.7148 | 0.27008 | 0.32044 | 0.32044 | 0.25635 | 0.25635 | 0.10529 | 121.6736 | 0.20599 | 0.15106 | 121.875 | 0.22888 | 121.8842 | 0.29297 | -121.9208 | -121.8658 | 121.6827 | 0.21515 | 0.49896 | 0.21515
1693.375 | 121.962 | -0.40283 | 121.4584 | -0.012131 | 0.0033282 | 0.056418 | 0.051947 | 0.0022943 | -0.006853 | -0.0036636 | -0.005371 | 0.034066 | 0.041567 | -0.0022473 | 0.014471 | 0.027809 | -0.0010617 | 0.041199 | 121.4127 | -0.36621 | 121.3623 | -0.1831 | -0.34332 | -0.3067 | 0 | -0.19684 | -0.32959 | -0.10071 | -0.068665 | -0.004578 | -0.022888 | 0.036621 | -0.045776 | -0.09613 | 0.21973 | 0.09613 | 0.059509 | 0.059509 | 0.022888 | 0.073242 | -121.6553 | -121.5591 | 0.33417 | 0.37994 | 0.39825 | 0.3067 | 0.32501 | 0.18311 | 121.7285 | 0.26092 | 0.22888 | 121.7789 | 0.13275 | 121.8155 | 0.20599 | -121.8246 | -121.788 | 121.7651 | 0.30212 | 0.44403 | 0.40283
1695.0781 | 121.994 | -0.41199 | 121.4493 | -0.0045011 | -0.00030342 | 0.054495 | 0.050451 | -0.0030463 | -0.008562 | -0.001741 | -0.0023192 | 0.032357 | 0.038576 | 0.0045887 | 0.01383 | 0.027809 | 0.0019289 | 0.018311 | 121.3898 | -0.39825 | 121.3165 | -0.23804 | -0.33875 | -0.31128 | -0.059509 | -0.17853 | -0.35248 | -0.11902 | -0.059509 | 0.018311 | -0.032043 | 0.013733 | -0.059509 | -0.13275 | 0.17395 | 0.10071 | 0.073242 | 0.086975 | 0.059509 | 0.059509 | -121.6278 | -121.5683 | 0.35248 | 0.37994 | 0.4303 | 0.32044 | 0.37079 | 0.16022 | 121.7148 | 0.29297 | 0.23346 | 121.788 | 0.17395 | 121.8018 | 0.23346 | -121.8475 | -121.8018 | 121.7285 | 0.29297 | 0.4303 | 0.35248
1696.8438 | 121.8842 | -0.44403 | 121.4813 | -0.02739 | 0.0043964 | 0.056418 | 0.056646 | 0.0027215 | -0.0092028 | -0.0049454 | -0.0084228 | 0.035775 | 0.04114 | 0.0056567 | 0.015539 | 0.025032 | -0.0029843 | 0.032043 | 121.4813 | -0.42114 | 121.2387 | -0.35706 | -0.48981 | -0.43945 | -0.15106 | -0.12817 | -0.38452 | -0.19226 | -0.19684 | -0.10986 | -0.10071 | 0.022888 | 0 | -0.24262 | 0.086975 | 0.004578 | -0.045776 | -0.01831 | -0.068664 | 0.05951 | -121.6095 | -121.6736 | 0.24719 | 0.34332 | 0.33417 | 0.28381 | 0.27466 | 0.064087 | 121.6599 | 0.18768 | 0.19226 | 121.9025 | 0.25635 | 121.9254 | 0.31586 | -121.9025 | -121.8658 | 121.6827 | 0.25177 | 0.47607 | 0.29297
1698.5312 | 121.962 | -0.40741 | 121.4493 | -0.01976 | 0.0043964 | 0.0577 | 0.05451 | -0.0039007 | -0.0057848 | 0.0001816 | -0.005371 | 0.032998 | 0.040499 | 0.0090747 | 0.015112 | 0.025887 | -0.0029843 | 0.054932 | 121.4035 | -0.37537 | 121.3715 | -0.20142 | -0.33417 | -0.31128 | 0 | -0.17853 | -0.32501 | -0.10529 | -0.082397 | -0.018311 | -0.050354 | 0.032044 | -0.045777 | -0.07782 | 0.20599 | 0.096131 | 0.073243 | 0.064087 | 0.041199 | 0.082398 | -121.6278 | -121.5546 | 0.32501 | 0.35706 | 0.3891 | 0.27466 | 0.3067 | 0.17395 | 121.7468 | 0.24262 | 0.21973 | 121.7789 | 0.14648 | 121.8109 | 0.22888 | -121.8246 | -121.7743 | 121.7789 | 0.30212 | 0.46234 | 0.40741
1700.2812 | 121.9666 | -0.40283 | 121.4676 | -0.012131 | 0.0033282 | 0.055991 | 0.053656 | -5.5462e-05 | -0.0074938 | -0.0013138 | -0.005371 | 0.033426 | 0.039644 | -0.0013927 | 0.016393 | 0.025246 | -0.0025571 | 0.032043 | 121.431 | -0.4303 | 121.2982 | -0.28381 | -0.42572 | -0.37994 | -0.068665 | -0.14648 | -0.36621 | -0.068665 | -0.086975 | 0.009155 | -0.004578 | -0.027466 | -0.036621 | -0.16937 | 0.11902 | 0.022888 | -0.022888 | 0.050354 | 0.004578 | 0.036621 | -121.6141 | -121.5363 | 0.31586 | 0.39825 | 0.41199 | 0.36163 | 0.37537 | 0.14649 | 121.7285 | 0.27924 | 0.29755 | 121.8613 | 0.21973 | 121.8338 | 0.25635 | -121.8979 | -121.8338 | 121.7011 | 0.33417 | 0.43488 | 0.33417
1701.9844 | 121.9116 | -0.44403 | 121.4813 | -0.012131 | 0.0037556 | 0.054068 | 0.054297 | 0.0061395 | -0.0083484 | -0.0011002 | -0.0023192 | 0.033639 | 0.040499 | 0.0067249 | 0.017675 | 0.025246 | -0.00063445 | 0.1236 | 121.4493 | -0.41199 | 121.312 | -0.2655 | -0.39825 | -0.3891 | -0.082397 | -0.15106 | -0.37994 | -0.16022 | -0.11444 | -0.059509 | -0.064087 | 0.032044 | -0.032043 | -0.16937 | 0.17853 | 0.054932 | 0.045777 | 0.022888 | 0.013733 | 0.064087 | -121.6324 | -121.6415 | 0.32959 | 0.37994 | 0.38452 | 0.31586 | 0.32044 | 0.14648 | 121.7239 | 0.2655 | 0.21973 | 121.8613 | 0.22888 | 121.8933 | 0.29297 | -121.8933 | -121.8613 | 121.756 | 0.28381 | 0.56763 | 0.36163
1703.75 | 121.8292 | -0.45319 | 121.4996 | -0.012131 | 0.0065326 | 0.054495 | 0.054297 | 0.0035761 | -0.0055712 | -0.0030228 | -0.005371 | 0.034921 | 0.040926 | 0.0054431 | 0.018316 | 0.0261 | -0.0025571 | 0.050354 | 121.4539 | -0.43488 | 121.2341 | -0.36621 | -0.49896 | -0.45319 | -0.19226 | -0.10986 | -0.39368 | -0.21973 | -0.19684 | -0.1236 | -0.082397 | 0.018311 | -0.045777 | -0.2655 | 0.086975 | 0 | -0.045776 | -0.018311 | -0.064087 | 0.059509 | -121.6095 | -121.7194 | 0.25635 | 0.37079 | 0.32959 | 0.31128 | 0.27008 | 0.068664 | 121.669 | 0.19684 | 0.17395 | 121.8887 | 0.28381 | 121.907 | 0.34332 | -121.9345 | -121.8933 | 121.6873 | 0.23346 | 0.50354 | 0.26092
1705.4375 | 121.843 | -0.44861 | 121.5179 | -0.012131 | 0.0033282 | 0.056631 | 0.055151 | 0.0035761 | -0.0079212 | -0.0011002 | -0.0084228 | 0.033639 | 0.040712 | 0.0058703 | 0.018316 | 0.027169 | 0.0017153 | 0.07782 | 121.4584 | -0.43488 | 121.2479 | -0.3479 | -0.49439 | -0.45319 | -0.18768 | -0.10986 | -0.37537 | -0.20142 | -0.17853 | -0.12817 | -0.091553 | 0.013733 | -0.059509 | -0.27008 | 0.10071 | -0.004578 | -0.045777 | -0.018311 | -0.05951 | 0.073242 | -121.6278 | -121.7194 | 0.27008 | 0.35706 | 0.32043 | 0.28381 | 0.24719 | 0.086975 | 121.6827 | 0.19684 | 0.17395 | 121.8933 | 0.2655 | 121.907 | 0.33875 | -121.9528 | -121.8933 | 121.6965 | 0.24719 | 0.52643 | 0.26093
1707.2031 | 121.9025 | -0.44403 | 121.4905 | -0.0045011 | 0.0052508 | 0.057272 | 0.052801 | 0.00037174 | -0.0092028 | -0.0015274 | 0.00073235 | 0.03428 | 0.04114 | 0.0069385 | 0.017034 | 0.027809 | -0.0031979 | 0.1236 | 121.4172 | -0.42572 | 121.2936 | -0.29297 | -0.4303 | -0.40283 | -0.086975 | -0.13733 | -0.37537 | -0.14191 | -0.11902 | -0.07782 | -0.059509 | 0.018311 | -0.073243 | -0.19684 | 0.15106 | 0.041199 | 0.013733 | 0.022888 | -0.004578 | 0.068665 | -121.6278 | -121.6324 | 0.32501 | 0.38452 | 0.36621 | 0.31586 | 0.29755 | 0.13275 | 121.7194 | 0.25635 | 0.23346 | 121.843 | 0.23804 | 121.8613 | 0.3067 | -121.9162 | -121.8658 | 121.7377 | 0.30212 | 0.56763 | 0.35706
1708.9531 | 121.8658 | -0.48065 | 121.4722 | -0.012131 | 0.00097838 | 0.05535 | 0.051947 | 0.0027215 | -0.0081348 | -0.0032364 | -0.005371 | 0.033639 | 0.042208 | 0.015697 | 0.017034 | 0.027596 | -0.0027707 | 0.059509 | 121.431 | -0.44403 | 121.2341 | -0.35706 | -0.44861 | -0.4303 | -0.17853 | -0.10529 | -0.41657 | -0.20142 | -0.14648 | -0.082397 | -0.09613 | 0.036621 | -0.041199 | -0.23804 | 0.1236 | 0.050354 | 0.032044 | 0.013733 | -0.004577 | 0.064087 | -121.5775 | -121.6736 | 0.33417 | 0.38452 | 0.39826 | 0.32044 | 0.33417 | 0.086975 | 121.6782 | 0.27008 | 0.21515 | 121.875 | 0.31128 | 121.9116 | 0.37537 | -121.9162 | -121.8887 | 121.7148 | 0.27924 | 0.54016 | 0.30212
1710.7188 | 121.8658 | -0.47607 | 121.4951 | -0.01976 | -0.0011578 | 0.055777 | 0.053656 | -0.0028327 | -0.0074938 | -0.0025956 | -0.0023192 | 0.034066 | 0.039003 | 0.0048023 | 0.017461 | 0.026528 | -0.0012753 | 0.068665 | 121.4172 | -0.45776 | 121.2341 | -0.33875 | -0.44861 | -0.43945 | -0.16937 | -0.10529 | -0.39825 | -0.20599 | -0.14191 | -0.082397 | -0.086975 | 0.01831 | -0.07782 | -0.26093 | 0.13733 | 0.036621 | 0.027466 | 0.018311 | 0.009156 | 0.07782 | -121.6003 | -121.7011 | 0.33417 | 0.3891 | 0.39368 | 0.31128 | 0.31586 | 0.11902 | 121.6919 | 0.25635 | 0.19226 | 121.875 | 0.29297 | 121.8933 | 0.37079 | -121.9528 | -121.8933 | 121.7102 | 0.27008 | 0.54474 | 0.3067
1712.4219 | 121.8842 | -0.47607 | 121.4767 | -0.012131 | 0.0065326 | 0.056631 | 0.055365 | 0.00058534 | -0.008562 | -0.0036636 | -0.0084228 | 0.034707 | 0.040712 | 0.0075793 | 0.018316 | 0.026955 | -0.00084805 | 0.054932 | 121.431 | -0.44861 | 121.2204 | -0.37079 | -0.50812 | -0.46234 | -0.16937 | -0.10529 | -0.40741 | -0.16937 | -0.15564 | -0.11902 | -0.064087 | 0.027466 | -0.045777 | -0.25635 | 0.10529 | 0.013733 | -0.032044 | -0.013733 | -0.05951 | 0.068664 | -121.582 | -121.6461 | 0.32043 | 0.41199 | 0.35706 | 0.34332 | 0.28839 | 0.077819 | 121.669 | 0.25177 | 0.23804 | 121.8796 | 0.30212 | 121.907 | 0.37079 | -121.9254 | -121.8842 | 121.6965 | 0.3067 | 0.53101 | 0.3067
1714.1719 | 121.8887 | -0.4715 | 121.4676 | -0.012131 | 0.0026874 | 0.054709 | 0.05216 | 0.0014397 | -0.0092028 | -0.0025956 | -0.0023192 | 0.030435 | 0.039431 | 0.010143 | 0.016821 | 0.02845 | -0.00063445 | 0.068665 | 121.4401 | -0.44403 | 121.225 | -0.36621 | -0.46692 | -0.45319 | -0.16937 | -0.10529 | -0.41657 | -0.17853 | -0.1236 | -0.086975 | -0.068665 | 0.027466 | -0.027465 | -0.24261 | 0.10529 | 0.018311 | 0.004578 | -0.009155 | -0.022888 | 0.054932 | -121.5729 | -121.6461 | 0.3479 | 0.40283 | 0.38452 | 0.3479 | 0.32959 | 0.07782 | 121.669 | 0.29297 | 0.23804 | 121.8842 | 0.31128 | 121.9116 | 0.36621 | -121.9116 | -121.8842 | 121.6965 | 0.29297 | 0.54016 | 0.30212
1715.9219 | 121.907 | -0.50812 | 121.4264 | -0.012131 | 0.00033758 | 0.054282 | 0.052801 | 0.0012261 | -0.0081348 | -0.0032364 | -0.005371 | 0.030221 | 0.040712 | 0.0018115 | 0.015966 | 0.026955 | 0.0019289 | 0.11902 | 121.3303 | -0.44861 | 121.2708 | -0.28839 | -0.41199 | -0.37537 | -0.068665 | -0.11444 | -0.45319 | -0.12817 | -0.064087 | -0.018311 | -0.036621 | 0.05951 | -0.096131 | -0.15564 | 0.21973 | 0.13275 | 0.096131 | 0.073242 | 0.036621 | 0.054932 | -121.5408 | -121.5546 | 0.44403 | 0.4715 | 0.48981 | 0.41656 | 0.43487 | 0.16022 | 121.7194 | 0.3891 | 0.32501 | 121.7789 | 0.33874 | 121.8384 | 0.39368 | -121.875 | -121.8796 | 121.7789 | 0.37994 | 0.62714 | 0.43945
1717.625 | 121.8658 | -0.52643 | 121.463 | -0.0045011 | 0.0020466 | 0.056418 | 0.052374 | -0.0015509 | -0.0070666 | -0.001741 | -0.005371 | 0.031289 | 0.039858 | 0.0024525 | 0.016607 | 0.028237 | -0.0023435 | 0.054932 | 121.3577 | -0.49439 | 121.2067 | -0.37079 | -0.48981 | -0.48065 | -0.15106 | -0.082397 | -0.45776 | -0.1831 | -0.10986 | -0.073242 | -0.073242 | 0.032043 | -0.10529 | -0.25635 | 0.15564 | 0.045776 | 0.036621 | 0.013733 | 0.004578 | 0.068664 | -121.5454 | -121.6461 | 0.41657 | 0.45319 | 0.45319 | 0.38452 | 0.38452 | 0.1236 | 121.701 | 0.3479 | 0.27466 | 121.8521 | 0.37537 | 121.8842 | 0.44403 | -121.9574 | -121.9208 | 121.7331 | 0.34332 | 0.58136 | 0.37537
1719.375 | 121.9528 | -0.46692 | 121.3943 | -0.012131 | 0.0022602 | 0.054495 | 0.052588 | 0.00079894 | -0.006853 | -0.0030228 | -0.0023192 | 0.030008 | 0.038362 | 0.0033069 | 0.014043 | 0.026528 | 0.00043375 | 0.009155 | 121.3577 | -0.44403 | 121.2708 | -0.31586 | -0.44403 | -0.40283 | -0.054932 | -0.14191 | -0.4303 | -0.10071 | -0.059509 | -0.018311 | -0.013733 | 0.022888 | -0.036621 | -0.1236 | 0.15106 | 0.064087 | 0.022888 | 0.041199 | 0 | 0.036621 | -121.5363 | -121.4951 | 0.40741 | 0.45319 | 0.44861 | 0.41657 | 0.41199 | 0.12817 | 121.7148 | 0.37079 | 0.32959 | 121.8018 | 0.28839 | 121.8246 | 0.32501 | -121.8384 | -121.8246 | 121.7377 | 0.36621 | 0.47607 | 0.41199
1721.125 | 121.8521 | -0.50812 | 121.463 | -0.012131 | 0.0035418 | 0.055563 | 0.053228 | 0.0010125 | -0.006853 | -0.0019546 | -0.005371 | 0.033212 | 0.039858 | 0.0048023 | 0.018102 | 0.027169 | -0.0014891 | 0.073242 | 121.3898 | -0.47607 | 121.2112 | -0.40741 | -0.52643 | -0.49896 | -0.17395 | -0.091553 | -0.4303 | -0.16022 | -0.16022 | -0.11444 | -0.059509 | 0.032044 | -0.073242 | -0.25177 | 0.10071 | 0.009156 | -0.01831 | -0.022888 | -0.050354 | 0.07782 | -121.5546 | -121.6232 | 0.3479 | 0.44861 | 0.39368 | 0.37079 | 0.31586 | 0.068664 | 121.6873 | 0.27008 | 0.27008 | 121.8658 | 0.33875 | 121.8979 | 0.41656 | -121.9391 | -121.8933 | 121.7194 | 0.3479 | 0.58136 | 0.33417
1722.8281 | 122.0123 | -0.44861 | 121.431 | -0.012131 | 0.001192 | 0.053641 | 0.05152 | -0.0013373 | -0.0077074 | -0.0036636 | -0.011475 | 0.031289 | 0.03879 | 0.00095707 | 0.017034 | 0.028023 | -0.0029843 | 0.068665 | 121.3348 | -0.43945 | 121.312 | -0.23804 | -0.35706 | -0.33417 | 0.032043 | -0.11444 | -0.37994 | -0.027466 | 0.032043 | 0.073242 | 0.059509 | 0.009155 | -0.09613 | -0.11902 | 0.21057 | 0.11444 | 0.091552 | 0.10529 | 0.082397 | 0.068664 | -121.5454 | -121.4584 | 0.48065 | 0.50812 | 0.52185 | 0.43945 | 0.45319 | 0.20142 | 121.7514 | 0.41199 | 0.35248 | 121.7743 | 0.2655 | 121.7834 | 0.33417 | -121.8704 | -121.8109 | 121.7606 | 0.42114 | 0.51727 | 0.48065
1724.5938 | 122.0032 | -0.37994 | 121.5225 | -0.012131 | 0.00097838 | 0.055777 | 0.052374 | 0.0033623 | -0.006853 | -0.0021682 | -0.005371 | 0.028299 | 0.042208 | 0.0082203 | 0.014471 | 0.025246 | 0.0012881 | 0.10529 | 121.4127 | -0.34332 | 121.4355 | -0.15106 | -0.27924 | -0.24719 | -0.027466 | -0.11444 | -0.32501 | -0.036621 | 0.018311 | 0.009155 | 0.045776 | 0.036621 | -0.10986 | -0.086975 | 0.22888 | 0.13275 | 0.10071 | 0.096131 | 0.064087 | 0.054932 | -121.637 | -121.5591 | 0.39826 | 0.42572 | 0.3891 | 0.37079 | 0.33417 | 0.19226 | 121.7789 | 0.34332 | 0.28839 | 121.756 | 0.21057 | 121.7926 | 0.2655 | -121.8658 | -121.8475 | 121.8155 | 0.34332 | 0.48523 | 0.35248
1726.3594 | 121.9254 | -0.32959 | 121.6003 | -0.0045011 | 0.0031146 | 0.057059 | 0.054083 | -0.0030463 | -0.0072802 | -0.0040908 | 0.00073235 | 0.030648 | 0.043062 | 0.013133 | 0.021093 | 0.026528 | -0.0029843 | 0.13733 | 121.5225 | -0.31128 | 121.4172 | -0.16937 | -0.31128 | -0.27008 | -0.15564 | -0.082397 | -0.27466 | -0.091553 | -0.036621 | -0.11444 | -0.004578 | 0.018311 | -0.07782 | -0.18311 | 0.16022 | 0.059509 | 0.018311 | 0.041198 | 0 | 0.054932 | -121.6827 | -121.6919 | 0.29297 | 0.32501 | 0.21515 | 0.27008 | 0.16022 | 0.14191 | 121.7285 | 0.23804 | 0.18311 | 121.8338 | 0.19226 | 121.8521 | 0.24719 | -121.9116 | -121.875 | 121.7468 | 0.23804 | 0.46692 | 0.17395
1728.0625 | 121.9894 | -0.29755 | 121.6095 | -0.012131 | -0.0011578 | 0.055777 | 0.052374 | 0.0012261 | -0.0083484 | -0.002382 | -0.0023192 | 0.026803 | 0.041994 | -0.0018201 | 0.016393 | 0.023964 | -0.0025571 | 0.013733 | 121.5271 | -0.28839 | 121.4493 | -0.13275 | -0.23346 | -0.20142 | -0.16479 | -0.10986 | -0.22888 | -0.073242 | 0.022888 | -0.082397 | 0.018311 | 0.009155 | -0.082397 | -0.16022 | 0.16479 | 0.09613 | 0.064087 | 0.086975 | 0.054932 | 0.068664 | -121.7194 | -121.6827 | 0.32043 | 0.31586 | 0.21515 | 0.24719 | 0.14649 | 0.15564 | 121.7377 | 0.25177 | 0.15564 | 121.8155 | 0.11902 | 121.8246 | 0.18768 | -121.8979 | -121.8384 | 121.7468 | 0.2243 | 0.31128 | 0.13275
1729.8281 | 121.9254 | -0.32044 | 121.6415 | -0.01976 | 0.0048236 | 0.05834 | 0.053228 | 0.0012261 | -0.010057 | -0.0030228 | -0.005371 | 0.029153 | 0.044344 | 0.013561 | 0.018316 | 0.023964 | -0.00020725 | 0.13275 | 121.5912 | -0.28381 | 121.4539 | -0.14191 | -0.2655 | -0.24719 | -0.17853 | -0.07782 | -0.24261 | -0.091553 | -0.009155 | -0.1236 | -0.004578 | 0.036622 | -0.050354 | -0.18768 | 0.17853 | 0.073243 | 0.054932 | 0.036621 | 0.01831 | 0.07782 | -121.7194 | -121.7331 | 0.31128 | 0.31586 | 0.19684 | 0.23804 | 0.11902 | 0.14191 | 121.7377 | 0.23346 | 0.15106 | 121.875 | 0.16479 | 121.9116 | 0.24262 | -121.9254 | -121.8842 | 121.7743 | 0.22888 | 0.45319 | 0.14191
1731.5156 | 121.9894 | -0.27924 | 121.6141 | -0.01976 | 0.0039692 | 0.053427 | 0.052374 | 0.0029351 | -0.010057 | -0.0030228 | -0.005371 | 0.027658 | 0.041353 | 0.015483 | 0.017248 | 0.02311 | -0.0029843 | 0.027466 | 121.582 | -0.27466 | 121.4493 | -0.15106 | -0.28839 | -0.24719 | -0.16022 | -0.10529 | -0.23804 | -0.050354 | 0.022888 | -0.068665 | 0.027466 | 0.004578 | -0.032044 | -0.16479 | 0.12817 | 0.032044 | -0.009155 | 0.027466 | -0.013733 | 0.041199 | -121.7194 | -121.6644 | 0.30212 | 0.3067 | 0.21057 | 0.2655 | 0.16937 | 0.1236 | 121.7239 | 0.26093 | 0.18768 | 121.8567 | 0.13275 | 121.8613 | 0.17395 | -121.8887 | -121.8521 | 121.7285 | 0.22888 | 0.3067 | 0.11902
1733.2656 | 121.9528 | -0.27008 | 121.6507 | -0.0045011 | 0.0039692 | 0.054282 | 0.053442 | 0.0025079 | -0.0070666 | -0.002382 | -0.005371 | 0.027444 | 0.04114 | 0.0090747 | 0.015539 | 0.02546 | -0.00020725 | 0.018311 | 121.5775 | -0.25635 | 121.4676 | -0.10986 | -0.26093 | -0.19684 | -0.14648 | -0.13733 | -0.21515 | -0.086975 | 0.004578 | -0.086975 | 0.004578 | 0.013733 | -0.073242 | -0.18311 | 0.16022 | 0.073243 | 0.009156 | 0.05951 | -0.004577 | 0.054932 | -121.788 | -121.7377 | 0.27466 | 0.27466 | 0.18311 | 0.21973 | 0.12817 | 0.14649 | 121.7239 | 0.21973 | 0.12817 | 121.8338 | 0.07782 | 121.8475 | 0.13275 | -121.907 | -121.8658 | 121.7377 | 0.18311 | 0.28839 | 0.1236
1734.9531 | 121.9666 | -0.27466 | 121.6232 | -0.0045011 | 0.001192 | 0.056204 | 0.053442 | -0.0024055 | -0.0074938 | -0.0015274 | -0.0023192 | 0.02659 | 0.043489 | 0.016765 | 0.015752 | 0.024178 | -0.0042661 | 0.041199 | 121.5683 | -0.25177 | 121.4996 | -0.064087 | -0.21973 | -0.16022 | -0.082397 | -0.11444 | -0.21515 | -0.064087 | 0.022888 | -0.068665 | 0.022888 | 0.022888 | -0.054932 | -0.1236 | 0.21057 | 0.11444 | 0.054931 | 0.091553 | 0.032043 | 0.059509 | -121.7377 | -121.6873 | 0.29755 | 0.29755 | 0.20599 | 0.23804 | 0.14648 | 0.18768 | 121.7514 | 0.23804 | 0.15106 | 121.8201 | 0.10071 | 121.843 | 0.16022 | -121.875 | -121.8384 | 121.7743 | 0.21057 | 0.31586 | 0.19226
1736.7188 | 121.9116 | -0.3067 | 121.6461 | -0.012131 | 0.0056782 | 0.056845 | 0.05451 | 0.0027215 | -0.0081348 | -0.0045182 | -0.005371 | 0.031289 | 0.041567 | 0.014842 | 0.016393 | 0.024819 | -0.0021299 | 0.11902 | 121.5912 | -0.27924 | 121.4584 | -0.12817 | -0.27008 | -0.24261 | -0.13275 | -0.10986 | -0.23346 | -0.10529 | -0.022888 | -0.10529 | -0.009155 | 0.027466 | -0.054931 | -0.18768 | 0.17853 | 0.064087 | 0.036621 | 0.036621 | 0.009155 | 0.073243 | -121.756 | -121.7514 | 0.28381 | 0.29755 | 0.20142 | 0.2243 | 0.12817 | 0.15106 | 121.7377 | 0.21057 | 0.12817 | 121.8704 | 0.1236 | 121.8979 | 0.19684 | -121.9254 | -121.8796 | 121.7651 | 0.20142 | 0.42572 | 0.17395
1738.4844 | 122.0123 | -0.27924 | 121.6049 | -0.0045011 | 0.00076478 | 0.056204 | 0.049811 | 0.00058534 | -0.0083484 | -0.0040908 | -0.0023192 | 0.026162 | 0.040071 | 0.0065113 | 0.015325 | 0.024391 | 6.346e-06 | 0.091553 | 121.5454 | -0.27008 | 121.5271 | -0.022888 | -0.1831 | -0.13733 | -0.022888 | -0.13275 | -0.22888 | -0.045776 | 0.091553 | 0.027466 | 0.059509 | 0.009155 | -0.059509 | -0.077819 | 0.25635 | 0.14191 | 0.096131 | 0.13275 | 0.086976 | 0.050354 | -121.7377 | -121.6507 | 0.37079 | 0.33874 | 0.3067 | 0.28839 | 0.25635 | 0.24719 | 121.7972 | 0.32044 | 0.18311 | 121.8155 | 0.096131 | 121.8246 | 0.14648 | -121.875 | -121.8338 | 121.8063 | 0.23346 | 0.37079 | 0.25635
1740.2344 | 122.0123 | -0.29755 | 121.5866 | -0.012131 | 0.00055118 | 0.055777 | 0.05152 | 0.0033623 | -0.0074938 | -0.0008866 | -0.005371 | 0.027444 | 0.041994 | 0.0062977 | 0.013616 | 0.024178 | -0.0064023 | 0.10986 | 121.4951 | -0.28839 | 121.5271 | -0.059509 | -0.19684 | -0.19226 | -0.018311 | -0.10071 | -0.23804 | -0.032043 | 0.09613 | 0.045776 | 0.032043 | 0.009155 | -0.091553 | -0.059509 | 0.23804 | 0.10528 | 0.10071 | 0.09613 | 0.091553 | 0.059509 | -121.6873 | -121.6187 | 0.39368 | 0.32959 | 0.34332 | 0.27008 | 0.28381 | 0.22888 | 121.8155 | 0.33417 | 0.20599 | 121.7834 | 0.13733 | 121.7926 | 0.19684 | -121.875 | -121.8246 | 121.8246 | 0.2655 | 0.40741 | 0.27923
1741.9844 | 121.9528 | -0.3067 | 121.6095 | -0.0045011 | 0.00076478 | 0.053854 | 0.053015 | -0.00026906 | -0.010485 | -0.0025956 | -0.0084228 | 0.028939 | 0.043062 | 0.01292 | 0.015112 | 0.02546 | -0.0036253 | 0.11444 | 121.5271 | -0.27466 | 121.5088 | -0.07782 | -0.20599 | -0.17395 | -0.064087 | -0.10986 | -0.22888 | -0.07782 | 0.013733 | -0.013733 | 0.018311 | 0.032044 | -0.082397 | -0.10071 | 0.22888 | 0.13275 | 0.10071 | 0.10071 | 0.068664 | 0.07782 | -121.7194 | -121.6873 | 0.32043 | 0.32501 | 0.29297 | 0.24719 | 0.21515 | 0.19684 | 121.7834 | 0.24261 | 0.15106 | 121.8018 | 0.11902 | 121.8338 | 0.19684 | -121.8842 | -121.8384 | 121.8155 | 0.22888 | 0.42114 | 0.24261
1743.6875 | 121.9666 | -0.28381 | 121.6003 | -0.0045011 | 0.0035418 | 0.056418 | 0.052588 | 0.0012261 | -0.0070666 | -0.002382 | -0.005371 | 0.027444 | 0.042421 | 0.010997 | 0.015112 | 0.025246 | -0.0046933 | 0.050354 | 121.5546 | -0.24261 | 121.5179 | -0.068665 | -0.22888 | -0.16937 | -0.013733 | -0.12817 | -0.21515 | -0.036621 | 0 | 0 | 0.036621 | 0.041198 | -0.045777 | -0.082398 | 0.21515 | 0.11444 | 0.054931 | 0.073242 | 0.013733 | 0.068664 | -121.7285 | -121.637 | 0.28381 | 0.32043 | 0.28381 | 0.25177 | 0.21515 | 0.17395 | 121.7606 | 0.21515 | 0.17853 | 121.7972 | 0.086975 | 121.8384 | 0.15564 | -121.843 | -121.8155 | 121.8018 | 0.24719 | 0.33417 | 0.27008
1745.4531 | 121.8796 | -0.32501 | 121.637 | -0.01976 | 0.0043964 | 0.057059 | 0.055151 | 0.0029351 | -0.006853 | -0.0013138 | -0.011475 | 0.031717 | 0.041994 | 0.0092883 | 0.018957 | 0.026955 | -0.0051205 | 0.07782 | 121.6003 | -0.27008 | 121.3852 | -0.23804 | -0.36621 | -0.32501 | -0.19684 | -0.07782 | -0.26093 | -0.14648 | -0.13733 | -0.12817 | -0.045776 | 0.054931 | -0.036621 | -0.25177 | 0.086975 | 0 | -0.041199 | -0.054931 | -0.09613 | 0.064087 | -121.7148 | -121.7834 | 0.18768 | 0.27924 | 0.19684 | 0.21515 | 0.13275 | 0.032044 | 121.6553 | 0.1236 | 0.11444 | 121.8704 | 0.18311 | 121.9254 | 0.24719 | -121.907 | -121.8979 | 121.7102 | 0.17853 | 0.40283 | 0.12817
1747.2344 | 122.0123 | -0.25635 | 121.6232 | -0.012131 | 0.00076478 | 0.054282 | 0.05152 | 0.00015814 | -0.010057 | -0.0008866 | -0.0084228 | 0.026803 | 0.039858 | 0.0067249 | 0.015325 | 0.024391 | -0.0034117 | 0.10529 | 121.5363 | -0.24719 | 121.5408 | -0.027466 | -0.15564 | -0.13733 | 0.045776 | -0.10071 | -0.21515 | -0.022888 | 0.050354 | 0.064087 | 0.050354 | 0.009156 | -0.086975 | -0.082397 | 0.22888 | 0.11902 | 0.10071 | 0.10986 | 0.091552 | 0.041199 | -121.7239 | -121.6461 | 0.3067 | 0.3067 | 0.32044 | 0.2655 | 0.27924 | 0.21973 | 121.788 | 0.2655 | 0.19226 | 121.7834 | 0.11444 | 121.7926 | 0.15564 | -121.8704 | -121.8384 | 121.7972 | 0.23346 | 0.36163 | 0.30212
1748.9844 | 121.9528 | -0.31586 | 121.5912 | -0.012131 | 0.0024738 | 0.054709 | 0.051733 | -0.0015509 | -0.0081348 | -0.001741 | -0.0084228 | 0.028085 | 0.042635 | 0.0090747 | 0.017248 | 0.025887 | -0.0034117 | 0.009155 | 121.55 | -0.27924 | 121.4401 | -0.15564 | -0.27466 | -0.23346 | -0.059509 | -0.091553 | -0.27008 | -0.064087 | -0.050354 | -0.009155 | 0.004578 | 0.036621 | -0.041199 | -0.15106 | 0.16022 | 0.082398 | 0.041199 | 0.045777 | 0.004578 | 0.045776 | -121.6827 | -121.6553 | 0.2655 | 0.32044 | 0.3067 | 0.27466 | 0.26093 | 0.1236 | 121.7194 | 0.21973 | 0.20599 | 121.8292 | 0.17853 | 121.8658 | 0.2243 | -121.8704 | -121.8613 | 121.756 | 0.25177 | 0.32501 | 0.25635
1750.7031 | 121.9986 | -0.32501 | 121.5775 | -0.012131 | 0.00055118 | 0.053854 | 0.050451 | -0.0015509 | -0.0081348 | -0.002382 | -0.005371 | 0.028085 | 0.04178 | 0.0080067 | 0.014257 | 0.026314 | -0.0027707 | 0.032043 | 121.5134 | -0.27924 | 121.463 | -0.12817 | -0.25635 | -0.20142 | -0.018311 | -0.10071 | -0.27008 | -0.041199 | 0 | 0.054932 | 0.050354 | 0.045776 | -0.064087 | -0.11444 | 0.19684 | 0.1236 | 0.068664 | 0.07782 | 0.022888 | 0.054931 | -121.6782 | -121.6187 | 0.32501 | 0.37537 | 0.37994 | 0.32044 | 0.32501 | 0.15106 | 121.7422 | 0.27008 | 0.22888 | 121.7926 | 0.16937 | 121.8384 | 0.2243 | -121.8567 | -121.8475 | 121.788 | 0.28381 | 0.35706 | 0.3067
1752.4688 | 121.907 | -0.35706 | 121.5775 | -0.0045011 | 0.0048236 | 0.054922 | 0.056646 | -0.00048286 | -0.0072802 | -0.0019546 | -0.0084228 | 0.030435 | 0.040285 | 0.01292 | 0.019384 | 0.023964 | -0.0017027 | 0.036621 | 121.5454 | -0.32959 | 121.376 | -0.23346 | -0.37994 | -0.34332 | -0.09613 | -0.07782 | -0.28839 | -0.10071 | -0.10529 | -0.045776 | -0.018311 | 0.027466 | -0.032044 | -0.20142 | 0.1236 | 0.013733 | -0.022888 | -0.013733 | -0.050354 | 0.068665 | -121.6553 | -121.6782 | 0.25177 | 0.33874 | 0.31128 | 0.27008 | 0.24262 | 0.096131 | 121.7056 | 0.18311 | 0.18768 | 121.875 | 0.21057 | 121.9025 | 0.27924 | -121.907 | -121.8658 | 121.7331 | 0.25635 | 0.39368 | 0.26093
1754.2188 | 121.907 | -0.35706 | 121.5912 | -0.0045011 | 0.0043964 | 0.056631 | 0.056433 | -0.0015509 | -0.008562 | -0.001741 | -0.005371 | 0.032357 | 0.040926 | 0.013774 | 0.018316 | 0.0261 | -0.0014891 | 0.11902 | 121.55 | -0.32959 | 121.4264 | -0.1831 | -0.33417 | -0.31128 | -0.045776 | -0.082397 | -0.28839 | -0.10071 | -0.068665 | -0.032043 | -0.013733 | 0.027466 | -0.041199 | -0.16479 | 0.17395 | 0.045777 | 0.022889 | 0.018311 | -0.004577 | 0.068665 | -121.6736 | -121.6919 | 0.28839 | 0.34332 | 0.32501 | 0.27466 | 0.25635 | 0.14649 | 121.756 | 0.21973 | 0.18768 | 121.8796 | 0.20599 | 121.907 | 0.27466 | -121.9208 | -121.8796 | 121.7834 | 0.25635 | 0.47607 | 0.31128
1755.9844 | 121.8842 | -0.46234 | 121.5271 | -0.0045011 | 0.00055118 | 0.054282 | 0.050879 | -0.0021919 | -0.0079212 | -0.0038772 | -0.005371 | 0.030008 | 0.040285 | -0.0022473 | 0.017034 | 0.0261 | -0.0025571 | 0.068665 | 121.4401 | -0.43945 | 121.2524 | -0.33875 | -0.45776 | -0.43488 | -0.14191 | -0.045776 | -0.42572 | -0.13733 | -0.027466 | -0.068665 | -0.018311 | 0.022888 | -0.086975 | -0.27466 | 0.1236 | 0.027466 | 0.004577 | 0.004578 | -0.018311 | 0.036621 | -121.5729 | -121.6644 | 0.43488 | 0.44403 | 0.39368 | 0.40741 | 0.35706 | 0.10071 | 121.6919 | 0.39825 | 0.28839 | 121.8796 | 0.37994 | 121.9025 | 0.41657 | -121.9666 | -121.9528 | 121.7148 | 0.32501 | 0.53101 | 0.32043
1757.6875 | 122.0352 | -0.39368 | 121.4722 | -0.012131 | -0.00030342 | 0.056204 | 0.050238 | -0.0013373 | -0.0077074 | -0.0011002 | -0.005371 | 0.028085 | 0.04178 | 0.0033069 | 0.017034 | 0.026314 | -0.00020725 | 0.07782 | 121.4127 | -0.3891 | 121.4035 | -0.15106 | -0.29755 | -0.27466 | 0.036621 | -0.086975 | -0.37079 | 0.009155 | 0.11902 | 0.10071 | 0.086975 | 0.004578 | -0.059509 | -0.068665 | 0.24261 | 0.11902 | 0.096131 | 0.11444 | 0.091553 | 0.022888 | -121.5591 | -121.463 | 0.5127 | 0.48065 | 0.49439 | 0.45776 | 0.4715 | 0.23804 | 121.7926 | 0.48981 | 0.37994 | 121.8018 | 0.28381 | 121.8063 | 0.3067 | -121.8613 | -121.843 | 121.7972 | 0.40283 | 0.4715 | 0.4303
1759.4531 | 122.0306 | -0.43488 | 121.431 | -0.0045011 | -0.00073062 | 0.05535 | 0.051092 | -0.0017645 | -0.0087756 | -0.0025956 | -0.005371 | 0.02723 | 0.041567 | 0.010997 | 0.01618 | 0.028237 | -0.0023435 | 0.086975 | 121.3852 | -0.40283 | 121.3852 | -0.17395 | -0.31128 | -0.29755 | 0.064087 | -0.086975 | -0.36621 | 0.009155 | 0.13275 | 0.11902 | 0.10529 | 0.032043 | -0.045776 | -0.045776 | 0.26093 | 0.13733 | 0.1236 | 0.10529 | 0.091553 | 0.068664 | -121.5179 | -121.4218 | 0.56763 | 0.54016 | 0.55389 | 0.4715 | 0.48523 | 0.22888 | 121.788 | 0.49896 | 0.37537 | 121.788 | 0.27924 | 121.8201 | 0.3479 | -121.8338 | -121.7972 | 121.8201 | 0.44403 | 0.52185 | 0.49896
1761.2188 | 122.0123 | -0.42572 | 121.4447 | -0.0045011 | 0.0031146 | 0.055136 | 0.052801 | 0.0050713 | -0.0049304 | -0.005159 | -0.005371 | 0.027017 | 0.03879 | 0.011852 | 0.016821 | 0.026741 | -0.0014891 | 0.082397 | 121.3898 | -0.38452 | 121.3806 | -0.21973 | -0.37079 | -0.32501 | 0.022888 | -0.10986 | -0.36163 | 0.013733 | 0.086975 | 0.059509 | 0.10071 | 0.041199 | -0.054931 | -0.064087 | 0.20599 | 0.10071 | 0.054931 | 0.059509 | 0.013732 | 0.064087 | -121.5546 | -121.431 | 0.5127 | 0.52643 | 0.48523 | 0.46234 | 0.42114 | 0.16479 | 121.7651 | 0.44861 | 0.37537 | 121.7743 | 0.25177 | 121.8155 | 0.31586 | -121.8292 | -121.8063 | 121.8063 | 0.43945 | 0.50812 | 0.44861
1762.9844 | 122.0032 | -0.42114 | 121.4905 | -0.01976 | 0.0048236 | 0.055777 | 0.053228 | -0.0011237 | -0.0059986 | -0.00345 | -0.0084228 | 0.028299 | 0.040926 | 0.016124 | 0.017034 | 0.026955 | -0.0019163 | 0.073242 | 121.4081 | -0.3891 | 121.3898 | -0.21057 | -0.35248 | -0.31128 | 0.045776 | -0.09613 | -0.36621 | 0.004578 | 0.09613 | 0.059509 | 0.073242 | 0.032044 | -0.082398 | -0.10071 | 0.21057 | 0.10986 | 0.068665 | 0.07782 | 0.036621 | 0.054932 | -121.5866 | -121.4859 | 0.51727 | 0.49438 | 0.48065 | 0.43945 | 0.42572 | 0.17853 | 121.7789 | 0.46234 | 0.37079 | 121.7972 | 0.27008 | 121.8292 | 0.32501 | -121.8796 | -121.8567 | 121.8109 | 0.42572 | 0.49438 | 0.46692
1764.6875 | 121.9757 | -0.41657 | 121.4996 | -0.02739 | 0.0016192 | 0.05535 | 0.052588 | -0.0015509 | -0.01198 | -0.0053726 | -0.0023192 | 0.027871 | 0.038149 | 0.012706 | 0.016393 | 0.027596 | 0.00064735 | 0.018311 | 121.4264 | -0.42114 | 121.3211 | -0.27008 | -0.40741 | -0.36621 | -0.032043 | -0.07782 | -0.36621 | -0.045776 | 0.050354 | 0.032043 | 0.041199 | -0.004578 | -0.073242 | -0.17853 | 0.14648 | 0.050354 | 0.009155 | 0.054932 | 0.013733 | 0.050354 | -121.5775 | -121.5454 | 0.46692 | 0.45776 | 0.44861 | 0.40741 | 0.39825 | 0.15106 | 121.7422 | 0.41657 | 0.32044 | 121.8475 | 0.28839 | 121.843 | 0.33875 | -121.9208 | -121.8658 | 121.7377 | 0.37079 | 0.43488 | 0.38452
1766.4531 | 121.9025 | -0.46234 | 121.4996 | -0.012131 | 0.0054644 | 0.056845 | 0.056006 | 0.0027215 | -0.0074938 | -0.0030228 | -0.011475 | 0.030008 | 0.04114 | 0.015056 | 0.017248 | 0.025673 | -0.0029843 | 0.045776 | 121.4813 | -0.43488 | 121.2616 | -0.35248 | -0.48981 | -0.45776 | -0.10986 | -0.059509 | -0.37537 | -0.10986 | -0.027466 | -0.054932 | -0.018311 | 0.027466 | -0.018311 | -0.23804 | 0.10986 | 0.004577 | -0.027466 | -0.022889 | -0.054932 | 0.086975 | -121.5591 | -121.6095 | 0.43488 | 0.44403 | 0.40741 | 0.35705 | 0.32043 | 0.082397 | 121.6965 | 0.3479 | 0.2655 | 121.9162 | 0.31586 | 121.9437 | 0.40283 | -121.9345 | -121.875 | 121.7239 | 0.35248 | 0.50812 | 0.35248
1768.2188 | 121.994 | -0.40283 | 121.4813 | -0.012131 | 0.0024738 | 0.056845 | 0.050879 | 0.0010125 | -0.0070666 | -0.0008866 | -0.0023192 | 0.027871 | 0.040712 | 0.011424 | 0.018316 | 0.026528 | -0.00063445 | 0.082397 | 121.4218 | -0.37994 | 121.3943 | -0.17395 | -0.33417 | -0.29755 | 0.068665 | -0.086975 | -0.33875 | 0.004578 | 0.09613 | 0.068665 | 0.059509 | 0.022888 | -0.059509 | -0.086975 | 0.22888 | 0.10529 | 0.068665 | 0.082398 | 0.045777 | 0.064087 | -121.5683 | -121.4767 | 0.49896 | 0.46234 | 0.4715 | 0.39825 | 0.40741 | 0.20599 | 121.7743 | 0.43488 | 0.34332 | 121.8018 | 0.25177 | 121.8246 | 0.31586 | -121.8613 | -121.8201 | 121.7972 | 0.40741 | 0.48523 | 0.4715
1769.9688 | 121.8933 | -0.44861 | 121.5363 | -0.0045011 | 0.00012398 | 0.053854 | 0.053656 | -0.0032599 | -0.010271 | -0.0032364 | -0.005371 | 0.030435 | 0.040499 | 0.014842 | 0.017889 | 0.026955 | -0.0038389 | 0.086975 | 121.4355 | -0.41657 | 121.3028 | -0.29755 | -0.41199 | -0.3891 | -0.11444 | -0.045776 | -0.40283 | -0.12817 | -0.022888 | -0.050354 | -0.036621 | 0.032043 | -0.10071 | -0.23346 | 0.15106 | 0.059509 | 0.036621 | 0.027466 | 0.004578 | 0.045776 | -121.582 | -121.6644 | 0.42572 | 0.41199 | 0.39825 | 0.36621 | 0.35248 | 0.11902 | 121.7194 | 0.37994 | 0.27466 | 121.8521 | 0.35706 | 121.8842 | 0.40283 | -121.9528 | -121.9391 | 121.7514 | 0.32043 | 0.53558 | 0.33417
1771.6562 | 121.9116 | -0.36621 | 121.5729 | -0.012131 | 0.0039692 | 0.055563 | 0.055578 | 0.0063531 | -0.011766 | -0.002382 | -0.0084228 | 0.031289 | 0.03879 | 0.01292 | 0.019384 | 0.025673 | -0.0031979 | 0.13733 | 121.5317 | -0.32959 | 121.4081 | -0.19684 | -0.3479 | -0.31586 | -0.054932 | -0.07782 | -0.29755 | -0.091553 | -0.022888 | -0.036621 | -0.022888 | 0.036621 | -0.041199 | -0.16479 | 0.16937 | 0.050354 | 0.018311 | 0.013733 | -0.01831 | 0.068665 | -121.6507 | -121.6644 | 0.34332 | 0.34332 | 0.32959 | 0.27466 | 0.26092 | 0.13275 | 121.7377 | 0.27466 | 0.20599 | 121.8613 | 0.21973 | 121.8979 | 0.28839 | -121.9025 | -121.8704 | 121.7743 | 0.27466 | 0.50354 | 0.31128
1773.4219 | 122.0306 | -0.28839 | 121.5775 | -0.02739 | 0.0033282 | 0.055991 | 0.055151 | -0.0011237 | -0.0081348 | -0.0036636 | -0.005371 | 0.031289 | 0.043276 | 0.011852 | 0.017461 | 0.028023 | 0.00064735 | 0.041199 | 121.5591 | -0.31128 | 121.4584 | -0.15106 | -0.27466 | -0.24261 | 0.018311 | -0.10986 | -0.25635 | -0.009155 | 0.059509 | 0.059509 | 0.07782 | -0.022888 | -0.018311 | -0.11902 | 0.13733 | 0.045776 | 0.013733 | 0.068664 | 0.036621 | 0.032043 | -121.6873 | -121.5866 | 0.3479 | 0.36621 | 0.3479 | 0.33417 | 0.31586 | 0.16022 | 121.7697 | 0.31586 | 0.24719 | 121.8704 | 0.14649 | 121.8475 | 0.17853 | -121.8887 | -121.8338 | 121.7468 | 0.27924 | 0.32959 | 0.3067
1775.1875 | 122.0078 | -0.36621 | 121.5225 | -0.0045011 | 0.0039692 | 0.056631 | 0.054297 | 0.00015814 | -0.008562 | -0.0028092 | 0.00073235 | 0.03193 | 0.040285 | 0.0060841 | 0.015966 | 0.028023 | -0.0046933 | 0.041199 | 121.5042 | -0.35706 | 121.3806 | -0.21057 | -0.35706 | -0.32501 | 0.018311 | -0.073242 | -0.3067 | -0.004578 | 0.082397 | 0.068665 | 0.082397 | 0.009155 | -0.018311 | -0.14191 | 0.15564 | 0.041199 | 0.009155 | 0.032044 | 0 | 0.059509 | -121.5958 | -121.5271 | 0.44861 | 0.44861 | 0.43488 | 0.3891 | 0.37537 | 0.14648 | 121.7377 | 0.3891 | 0.30212 | 121.8613 | 0.23346 | 121.8704 | 0.29297 | -121.8796 | -121.8292 | 121.7468 | 0.36163 | 0.40741 | 0.38452
1776.9375 | 121.9025 | -0.45319 | 121.5271 | -0.012131 | 0.006319 | 0.056845 | 0.054724 | 0.0016535 | -0.0081348 | -0.0032364 | -0.0023192 | 0.029794 | 0.043489 | 0.0022389 | 0.01917 | 0.028023 | 0.00086095 | 0.050354 | 121.5088 | -0.40741 | 121.2799 | -0.34332 | -0.47607 | -0.42114 | -0.10071 | -0.036621 | -0.3891 | -0.10071 | -0.018311 | -0.064087 | -0.004578 | 0.045776 | -0.018311 | -0.24719 | 0.10986 | 0.032043 | -0.022888 | -0.013733 | -0.068664 | 0.064087 | -121.5637 | -121.6278 | 0.43487 | 0.44861 | 0.3891 | 0.38452 | 0.32501 | 0.064087 | 121.6873 | 0.37079 | 0.28839 | 121.9162 | 0.35248 | 121.962 | 0.41656 | -121.9345 | -121.9162 | 121.7331 | 0.35248 | 0.50354 | 0.35248
1778.6562 | 122.0352 | -0.3891 | 121.4951 | 0.0031279 | 0.0039692 | 0.055136 | 0.05216 | 0.0016535 | -0.0066394 | -0.005159 | -0.0084228 | 0.029794 | 0.039003 | 0.0026661 | 0.016821 | 0.027169 | -0.0019163 | 0.091553 | 121.4539 | -0.36621 | 121.3898 | -0.18768 | -0.32959 | -0.31128 | 0.050354 | -0.082397 | -0.32959 | 0.036621 | 0.10529 | 0.064087 | 0.091553 | 0.022888 | -0.041199 | -0.10529 | 0.20142 | 0.07782 | 0.059509 | 0.054932 | 0.036621 | 0.059509 | -121.5775 | -121.4584 | 0.49438 | 0.48065 | 0.45319 | 0.42114 | 0.39368 | 0.17853 | 121.756 | 0.43488 | 0.36621 | 121.8201 | 0.24719 | 121.843 | 0.3067 | -121.8613 | -121.8246 | 121.7789 | 0.42572 | 0.48065 | 0.43945
1780.4062 | 121.9254 | -0.4303 | 121.5179 | -0.012131 | 0.0058918 | 0.056418 | 0.054083 | 0.0018671 | -0.0057848 | -0.0049454 | -0.005371 | 0.02958 | 0.040926 | 0.016124 | 0.015112 | 0.028023 | 0.00043375 | 0.032043 | 121.5454 | -0.41657 | 121.3074 | -0.31586 | -0.45776 | -0.41657 | -0.073242 | -0.036621 | -0.36621 | -0.07782 | -0.013733 | -0.022888 | 0.022888 | 0.013733 | 0.027466 | -0.21057 | 0.11444 | 0.013733 | -0.027466 | 0 | -0.041199 | 0.064087 | -121.5546 | -121.5958 | 0.41657 | 0.45319 | 0.40741 | 0.3891 | 0.34332 | 0.10071 | 121.7239 | 0.35248 | 0.28839 | 121.962 | 0.32959 | 121.9757 | 0.39368 | -121.9345 | -121.8842 | 121.7377 | 0.35248 | 0.46234 | 0.35706
1782.1562 | 121.8704 | -0.4303 | 121.582 | -0.01976 | 0.0061054 | 0.056418 | 0.055365 | -0.0017645 | -0.0079212 | -0.002382 | -0.0023192 | 0.029367 | 0.040285 | 0.0086475 | 0.01618 | 0.027169 | -0.0031979 | 0.064087 | 121.5134 | -0.40741 | 121.2891 | -0.35248 | -0.48065 | -0.45319 | -0.13733 | -0.022888 | -0.36163 | -0.091553 | -0.050354 | -0.068665 | -0.013733 | 0.022888 | -0.068664 | -0.29297 | 0.07782 | -0.022888 | -0.050354 | -0.045776 | -0.073242 | 0.068665 | -121.6049 | -121.6736 | 0.37994 | 0.41657 | 0.36163 | 0.3479 | 0.29297 | 0.054932 | 121.6965 | 0.31128 | 0.27008 | 121.9208 | 0.33874 | 121.9437 | 0.40741 | -121.9894 | -121.9437 | 121.7194 | 0.33875 | 0.49439 | 0.29297
1783.9219 | 121.9757 | -0.40283 | 121.5408 | -0.0045011 | 0.0043964 | 0.055991 | 0.054083 | -0.00069646 | -0.0062122 | -0.000673 | -0.005371 | 0.028299 | 0.043062 | 0.015483 | 0.015539 | 0.028237 | -0.0017027 | 0.027466 | 121.5363 | -0.3891 | 121.3348 | -0.2655 | -0.41657 | -0.37994 | -0.036621 | -0.050354 | -0.33417 | -0.036621 | 0.022888 | 0.022888 | 0.050354 | 0.013733 | -0.004578 | -0.20599 | 0.13733 | 0.022888 | -0.013733 | 0.009155 | -0.027466 | 0.068665 | -121.5912 | -121.5775 | 0.42572 | 0.45319 | 0.42572 | 0.38452 | 0.35706 | 0.1236 | 121.7239 | 0.35706 | 0.29755 | 121.9254 | 0.28381 | 121.9391 | 0.35248 | -121.9299 | -121.875 | 121.7377 | 0.36621 | 0.4303 | 0.36621
1785.625 | 122.0123 | -0.36621 | 121.5363 | -0.012131 | 0.006319 | 0.057486 | 0.053228 | 0.00058534 | -0.0074938 | -0.0055862 | -0.0023192 | 0.026803 | 0.040499 | 0.0041615 | 0.015966 | 0.02845 | -0.0023435 | 0.091553 | 121.4676 | -0.34332 | 121.4493 | -0.15106 | -0.32044 | -0.27466 | 0.068665 | -0.082397 | -0.31586 | 0.036621 | 0.10986 | 0.091553 | 0.09613 | 0.022888 | -0.068665 | -0.086975 | 0.21515 | 0.091553 | 0.045776 | 0.068665 | 0.022888 | 0.050354 | -121.6187 | -121.4996 | 0.47607 | 0.46234 | 0.45776 | 0.41199 | 0.40741 | 0.19226 | 121.7926 | 0.42572 | 0.35248 | 121.8109 | 0.23346 | 121.8338 | 0.28381 | -121.8796 | -121.8521 | 121.8155 | 0.40283 | 0.45776 | 0.43488
1787.375 | 121.9254 | -0.39368 | 121.5591 | -0.0045011 | 0.002901 | 0.054282 | 0.053656 | 0.00015814 | -0.0081348 | -0.0015274 | -0.0023192 | 0.02958 | 0.04114 | 0.0095019 | 0.018316 | 0.025673 | -0.0064023 | 0.13733 | 121.4951 | -0.37994 | 121.3669 | -0.21973 | -0.36621 | -0.33875 | -0.013733 | -0.036621 | -0.33875 | -0.059509 | 0.013733 | 0.004578 | 0.022888 | 0.013733 | -0.064087 | -0.19226 | 0.17395 | 0.054932 | 0.027466 | 0.041199 | 0.013733 | 0.054932 | -121.5958 | -121.6187 | 0.40741 | 0.41657 | 0.39826 | 0.36163 | 0.34332 | 0.16022 | 121.7468 | 0.35248 | 0.27924 | 121.875 | 0.30212 | 121.8887 | 0.35706 | -121.9391 | -121.8979 | 121.7606 | 0.33417 | 0.53101 | 0.37994
1789.125 | 121.9528 | -0.38452 | 121.5317 | -0.012131 | 0.0039692 | 0.055991 | 0.053869 | -0.00048286 | -0.0066394 | -0.002382 | -0.0084228 | 0.029794 | 0.040499 | 0.0056567 | 0.017034 | 0.026955 | -0.0010617 | 0.036621 | 121.5363 | -0.39368 | 121.3348 | -0.2655 | -0.42114 | -0.38452 | -0.059509 | -0.054932 | -0.33875 | -0.041199 | 0.032043 | 0.013733 | 0.045776 | -0.009156 | 0.004578 | -0.19684 | 0.11902 | 0 | -0.036622 | 0.009156 | -0.027466 | 0.045776 | -121.5866 | -121.5729 | 0.41656 | 0.4303 | 0.39825 | 0.38452 | 0.35248 | 0.12817 | 121.7285 | 0.37079 | 0.29755 | 121.9299 | 0.28381 | 121.9208 | 0.32959 | -121.9254 | -121.8704 | 121.7194 | 0.34332 | 0.42114 | 0.32501
1790.8125 | 122.0306 | -0.37079 | 121.5637 | -0.0045011 | 0.00076478 | 0.055563 | 0.051733 | 0.00079894 | -0.0081348 | -3.1996e-05 | -0.0084228 | 0.026803 | 0.039217 | 0.0069385 | 0.015325 | 0.026528 | -0.0029843 | 0.032043 | 121.4767 | -0.36163 | 121.4172 | -0.19684 | -0.29755 | -0.27924 | 0.013733 | -0.073242 | -0.3067 | -0.013733 | 0.10529 | 0.09613 | 0.07782 | 0.009156 | -0.086975 | -0.14648 | 0.17395 | 0.091553 | 0.073243 | 0.082397 | 0.064087 | 0.064087 | -121.637 | -121.5775 | 0.47607 | 0.44861 | 0.46692 | 0.38452 | 0.40283 | 0.16479 | 121.7789 | 0.41199 | 0.29297 | 121.8384 | 0.23346 | 121.8475 | 0.29755 | -121.9254 | -121.8704 | 121.788 | 0.35706 | 0.40283 | 0.38452
1792.5 | 122.0123 | -0.36621 | 121.5591 | -0.0045011 | -0.00030342 | 0.056204 | 0.051306 | -0.00091006 | -0.0059986 | -0.0053726 | -0.011475 | 0.029153 | 0.040285 | 0.0048023 | 0.015539 | 0.027809 | -0.0025571 | 0.12817 | 121.4813 | -0.34332 | 121.4447 | -0.11444 | -0.24719 | -0.23804 | 0.054932 | -0.068665 | -0.31128 | -0.009155 | 0.10986 | 0.10529 | 0.073242 | 0.022888 | -0.07782 | -0.11444 | 0.25177 | 0.12817 | 0.11902 | 0.10529 | 0.096131 | 0.054932 | -121.6278 | -121.5683 | 0.47607 | 0.43945 | 0.4715 | 0.38452 | 0.41656 | 0.22888 | 121.788 | 0.42114 | 0.30212 | 121.8246 | 0.24261 | 121.8475 | 0.29755 | -121.9025 | -121.8704 | 121.8109 | 0.35706 | 0.49439 | 0.42114
1794.2656 | 121.8887 | -0.42114 | 121.5683 | -0.0045011 | 0.0026874 | 0.051718 | 0.054297 | -0.00091006 | -0.0089892 | -0.001741 | -0.005371 | 0.031717 | 0.040071 | 0.013347 | 0.015539 | 0.025673 | -0.00084805 | 0.050354 | 121.5271 | -0.38452 | 121.3211 | -0.27466 | -0.39368 | -0.37537 | -0.086975 | -0.032043 | -0.33417 | -0.14191 | -0.004578 | -0.022888 | -0.009155 | 0.036622 | -0.041198 | -0.24719 | 0.14648 | 0.045777 | 0.027466 | 0.009155 | -0.009156 | 0.086976 | -121.6003 | -121.7102 | 0.41656 | 0.41199 | 0.39825 | 0.32501 | 0.31128 | 0.10986 | 121.7056 | 0.32959 | 0.19226 | 121.9116 | 0.30212 | 121.9482 | 0.3891 | -121.9528 | -121.9025 | 121.7422 | 0.27924 | 0.4715 | 0.33417
1796.0156 | 121.8933 | -0.40741 | 121.5958 | 0.0031279 | 0.0024738 | 0.053641 | 0.05152 | 0.0014397 | -0.010271 | -0.0019546 | -0.0023192 | 0.030648 | 0.040499 | 0.0067249 | 0.016393 | 0.027596 | -0.0010617 | 0.068665 | 121.5408 | -0.38452 | 121.3348 | -0.27008 | -0.37537 | -0.36163 | -0.10071 | -0.041199 | -0.3479 | -0.11902 | -0.018311 | -0.032043 | -0.027466 | 0.022889 | -0.054931 | -0.26093 | 0.13733 | 0.045777 | 0.032044 | 0.022888 | 0.009155 | 0.05951 | -121.637 | -121.7148 | 0.3891 | 0.37994 | 0.37537 | 0.32043 | 0.31586 | 0.11444 | 121.7194 | 0.32959 | 0.22888 | 121.9254 | 0.3067 | 121.9482 | 0.36621 | -121.9803 | -121.9437 | 121.7422 | 0.28839 | 0.47608 | 0.3067
1797.7188 | 122.0169 | -0.36621 | 121.5637 | -0.012131 | 0.0054644 | 0.055991 | 0.054297 | -0.0041145 | -0.0066394 | -0.0028092 | -0.005371 | 0.030648 | 0.040712 | 0.0067249 | 0.017675 | 0.026741 | -0.0017027 | 0.054932 | 121.5591 | -0.35706 | 121.3943 | -0.19226 | -0.33417 | -0.28839 | 0.022888 | -0.07782 | -0.28839 | 0.009155 | 0.09613 | 0.07782 | 0.10071 | 0.009155 | -0.004578 | -0.16937 | 0.17395 | 0.07782 | 0.032044 | 0.068665 | 0.022889 | 0.07782 | -121.6415 | -121.5546 | 0.46234 | 0.46692 | 0.44403 | 0.3891 | 0.36621 | 0.16479 | 121.7514 | 0.38452 | 0.29755 | 121.9162 | 0.21057 | 121.9254 | 0.28839 | -121.9208 | -121.8521 | 121.7606 | 0.37537 | 0.42114 | 0.3891
1799.4844 | 121.9208 | -0.36621 | 121.5958 | -0.01976 | 0.0052508 | 0.056631 | 0.055365 | 0.0033623 | -0.0072802 | -0.00345 | -0.0084228 | 0.033212 | 0.040499 | 0.0077929 | 0.017889 | 0.026528 | 0.00086095 | 0.13275 | 121.5546 | -0.33417 | 121.4035 | -0.19226 | -0.32959 | -0.32044 | -0.027466 | -0.041199 | -0.3067 | -0.059509 | 0.013733 | -0.004578 | 0.009155 | 0.032044 | -0.041199 | -0.19226 | 0.17395 | 0.045776 | 0.036621 | 0.013732 | 0.004577 | 0.059509 | -121.637 | -121.6553 | 0.37994 | 0.37537 | 0.36163 | 0.31586 | 0.30212 | 0.14191 | 121.7377 | 0.32043 | 0.24719 | 121.8887 | 0.2655 | 121.9208 | 0.32501 | -121.9299 | -121.9025 | 121.7697 | 0.3067 | 0.49896 | 0.33875
1801.25 | 121.9345 | -0.37994 | 121.6049 | 0.0031279 | 0.0069598 | 0.056631 | 0.053869 | 0.0052851 | -0.0098438 | -0.0025956 | -0.005371 | 0.032998 | 0.040499 | 0.0065113 | 0.015966 | 0.024819 | -0.0010617 | 0.13733 | 121.5317 | -0.37079 | 121.4035 | -0.20599 | -0.35248 | -0.32501 | -0.022888 | -0.041199 | -0.31128 | -0.073242 | 0.027466 | -0.013733 | 0.004578 | 0.009155 | -0.073242 | -0.20142 | 0.17395 | 0.054932 | 0.027466 | 0.045777 | 0.018311 | 0.068665 | -121.6461 | -121.6782 | 0.40741 | 0.38452 | 0.36621 | 0.31586 | 0.29755 | 0.16479 | 121.7743 | 0.33874 | 0.23804 | 121.9025 | 0.27008 | 121.9116 | 0.33875 | -121.9757 | -121.9162 | 121.7834 | 0.3067 | 0.51727 | 0.35706
1802.9688 | 121.907 | -0.3891 | 121.6003 | -0.012131 | 0.0022602 | 0.054709 | 0.051306 | 0.0029351 | -0.00963 | -0.0015274 | 0.00073235 | 0.031503 | 0.042849 | 0.0037341 | 0.015752 | 0.029091 | -0.00084805 | 0.082397 | 121.5683 | -0.37079 | 121.344 | -0.27008 | -0.35248 | -0.3479 | -0.10986 | -0.041199 | -0.32044 | -0.11902 | -0.009155 | -0.022888 | -0.018311 | 0.01831 | -0.032044 | -0.25635 | 0.11902 | 0.041199 | 0.036621 | 0.022889 | 0.018311 | 0.068664 | -121.6415 | -121.7194 | 0.37994 | 0.37079 | 0.36621 | 0.30212 | 0.29755 | 0.10071 | 121.7148 | 0.31128 | 0.20142 | 121.9391 | 0.27924 | 121.9574 | 0.3479 | -121.9711 | -121.9208 | 121.7331 | 0.27008 | 0.4715 | 0.27924
1804.7188 | 121.907 | -0.40283 | 121.6095 | -0.012131 | -0.00094422 | 0.053641 | 0.050238 | -0.0015509 | -0.0083484 | -0.0013138 | -0.0023192 | 0.031289 | 0.040499 | 0.0073657 | 0.016393 | 0.028878 | 0.0019289 | 0.054932 | 121.5591 | -0.35248 | 121.3394 | -0.23804 | -0.36621 | -0.33875 | -0.10529 | -0.045776 | -0.31128 | -0.11444 | 0 | -0.018311 | -0.022888 | 0.050354 | -0.050354 | -0.27008 | 0.1648 | 0.064087 | 0.036621 | 0.013733 | -0.013733 | 0.091553 | -121.6553 | -121.7239 | 0.40283 | 0.37994 | 0.38452 | 0.28839 | 0.29297 | 0.11444 | 121.6919 | 0.31128 | 0.19684 | 121.9116 | 0.2655 | 121.962 | 0.35706 | -121.962 | -121.9208 | 121.7422 | 0.28839 | 0.45776 | 0.29755
1806.4062 | 121.9025 | -0.37079 | 121.6003 | -0.0045011 | 0.0037556 | 0.054282 | 0.055578 | -0.0011237 | -0.006853 | 0.0001816 | -0.005371 | 0.031076 | 0.041567 | 0.012493 | 0.01853 | 0.0261 | -0.0036253 | 0.09613 | 121.5729 | -0.34332 | 121.3715 | -0.23346 | -0.3891 | -0.35248 | -0.091553 | -0.009155 | -0.30212 | -0.10529 | -0.013733 | -0.032043 | -0.009155 | 0.027466 | -0.027466 | -0.22888 | 0.13733 | 0.018311 | -0.01831 | -0.009155 | -0.045776 | 0.068665 | -121.6095 | -121.7056 | 0.35706 | 0.36163 | 0.33875 | 0.29297 | 0.27008 | 0.10986 | 121.7148 | 0.28839 | 0.19684 | 121.9162 | 0.29297 | 121.9437 | 0.36163 | -121.9437 | -121.9025 | 121.7422 | 0.2655 | 0.46692 | 0.27924
1808.1562 | 121.8979 | -0.37079 | 121.5912 | -0.012131 | 0.0048236 | 0.055136 | 0.053442 | 0.0012261 | -0.006853 | -0.0030228 | -0.0084228 | 0.031717 | 0.044985 | 0.0048023 | 0.015752 | 0.029091 | 0.0027835 | 0.054932 | 121.582 | -0.35248 | 121.344 | -0.3067 | -0.42114 | -0.3891 | -0.1236 | -0.036621 | -0.29297 | -0.09613 | -0.022888 | -0.050354 | 0.009155 | 0.018311 | -0.009156 | -0.24719 | 0.064087 | -0.01831 | -0.050354 | -0.036621 | -0.068665 | 0.07782 | -121.6278 | -121.6873 | 0.3479 | 0.37994 | 0.32043 | 0.30212 | 0.24261 | 0.045776 | 121.6965 | 0.27008 | 0.19684 | 121.9345 | 0.25635 | 121.9528 | 0.33417 | -121.9437 | -121.8842 | 121.7148 | 0.27466 | 0.42572 | 0.24719
1809.9062 | 121.9025 | -0.37994 | 121.6278 | -0.012131 | 0.001192 | 0.053854 | 0.05216 | 0.0010125 | -0.011125 | -0.0030228 | -0.0084228 | 0.031076 | 0.041353 | 0.0030933 | 0.016821 | 0.026955 | -0.0012753 | 0.064087 | 121.5775 | -0.33875 | 121.344 | -0.24261 | -0.33875 | -0.33875 | -0.10071 | -0.022888 | -0.31128 | -0.12817 | -0.004578 | -0.013733 | -0.004578 | 0.041199 | -0.050354 | -0.28381 | 0.13733 | 0.041199 | 0.041199 | 0 | 0 | 0.068665 | -121.6507 | -121.756 | 0.37537 | 0.37537 | 0.36621 | 0.3067 | 0.29755 | 0.09613 | 121.6827 | 0.3067 | 0.1831 | 121.9162 | 0.28839 | 121.9574 | 0.35706 | -121.9666 | -121.9391 | 121.7239 | 0.25177 | 0.44403 | 0.27924
1811.6719 | 121.9711 | -0.35706 | 121.6095 | -0.0045011 | 0.0022602 | 0.054282 | 0.055365 | 0.00058534 | -0.0055712 | -0.0021682 | -0.0023192 | 0.03193 | 0.040499 | 0.010143 | 0.017248 | 0.02546 | -0.0023435 | 0.14648 | 121.5683 | -0.33417 | 121.4172 | -0.16937 | -0.31586 | -0.29297 | -0.013733 | -0.032043 | -0.29297 | -0.041199 | 0.068665 | 0.018311 | 0.050354 | 0.022889 | -0.041199 | -0.19226 | 0.18768 | 0.064087 | 0.041199 | 0.041198 | 0.01831 | 0.064087 | -121.6415 | -121.6507 | 0.42572 | 0.40741 | 0.37537 | 0.34332 | 0.31128 | 0.16479 | 121.7514 | 0.36163 | 0.25177 | 121.9025 | 0.26093 | 121.9254 | 0.32501 | -121.9437 | -121.9025 | 121.7743 | 0.31586 | 0.50354 | 0.34332
1813.4219 | 122.0352 | -0.3067 | 121.6095 | -0.012131 | 0.0041828 | 0.0577 | 0.054083 | 0.0016535 | -0.0081348 | -0.002382 | -0.0023192 | 0.028512 | 0.043062 | 0.00052987 | 0.017248 | 0.027169 | -0.0031979 | 0.064087 | 121.5591 | -0.30212 | 121.463 | -0.16022 | -0.28381 | -0.24261 | 0.032043 | -0.059509 | -0.25635 | 0.013733 | 0.1236 | 0.10071 | 0.10529 | 0.004578 | -0.050354 | -0.14648 | 0.14648 | 0.064087 | 0.022889 | 0.059509 | 0.018311 | 0.050354 | -121.669 | -121.5958 | 0.4303 | 0.41199 | 0.40741 | 0.36163 | 0.35706 | 0.14191 | 121.7651 | 0.37994 | 0.27008 | 121.8613 | 0.19684 | 121.8658 | 0.24719 | -121.9116 | -121.8658 | 121.7697 | 0.32043 | 0.37079 | 0.33874
1815.1875 | 121.9849 | -0.32044 | 121.6095 | -0.012131 | 0.0037556 | 0.055777 | 0.05216 | -0.0024055 | -0.0072802 | -0.0038772 | -0.0023192 | 0.030862 | 0.042208 | 0.0024525 | 0.015325 | 0.02546 | -0.00084805 | 0.064087 | 121.5591 | -0.26093 | 121.463 | -0.10529 | -0.25177 | -0.21973 | 0.054932 | -0.073242 | -0.23804 | -0.018311 | 0.07782 | 0.068665 | 0.064087 | 0.05951 | -0.050354 | -0.14648 | 0.21515 | 0.10071 | 0.068665 | 0.041198 | 0.009155 | 0.082398 | -121.6827 | -121.6278 | 0.39826 | 0.38452 | 0.3891 | 0.30212 | 0.3067 | 0.15564 | 121.7239 | 0.31586 | 0.21973 | 121.8201 | 0.16479 | 121.8796 | 0.24719 | -121.8704 | -121.8475 | 121.7834 | 0.30212 | 0.38452 | 0.37537
1816.8906 | 121.9894 | -0.29297 | 121.6141 | -0.01976 | 0.0020466 | 0.056418 | 0.05216 | -0.0051825 | -0.010698 | -0.0030228 | -0.005371 | 0.030862 | 0.039217 | 0.010997 | 0.015325 | 0.02546 | 0.0010745 | 0.050354 | 121.5775 | -0.24719 | 121.4996 | -0.082397 | -0.24719 | -0.21057 | 0.054932 | -0.073242 | -0.23804 | -0.027466 | 0.082397 | 0.059509 | 0.073242 | 0.045777 | -0.036621 | -0.11444 | 0.21057 | 0.082398 | 0.045777 | 0.036621 | 0 | 0.054932 | -121.6873 | -121.6415 | 0.37537 | 0.36621 | 0.35248 | 0.31128 | 0.29755 | 0.16479 | 121.7468 | 0.32043 | 0.21057 | 121.8246 | 0.16479 | 121.8704 | 0.21973 | -121.8613 | -121.8521 | 121.7926 | 0.2655 | 0.34332 | 0.3479
1818.6719 | 121.962 | -0.31128 | 121.6461 | 0.0031279 | 0.0020466 | 0.057059 | 0.053656 | -0.0028327 | -0.010057 | -0.0025956 | -0.005371 | 0.033426 | 0.043489 | 0.013561 | 0.01618 | 0.024391 | -0.0031979 | 0.15106 | 121.6553 | -0.31128 | 121.4584 | -0.14191 | -0.27466 | -0.26093 | -0.004578 | -0.045776 | -0.25177 | -0.041199 | 0.059509 | 0.013733 | 0.045776 | 0 | 0.009155 | -0.18768 | 0.16937 | 0.050354 | 0.036621 | 0.050354 | 0.036621 | 0.059509 | -121.6919 | -121.6873 | 0.37079 | 0.35705 | 0.32501 | 0.29755 | 0.2655 | 0.16937 | 121.7697 | 0.31128 | 0.21057 | 121.9666 | 0.20599 | 121.9666 | 0.2655 | -121.9574 | -121.8979 | 121.7697 | 0.27008 | 0.46234 | 0.3067
1820.4219 | 121.9254 | -0.32501 | 121.6553 | -0.012131 | 0.0069598 | 0.055136 | 0.053869 | 0.0057123 | -0.00963 | -0.0032364 | -0.0084228 | 0.032144 | 0.042208 | 0.012706 | 0.016607 | 0.0261 | -0.0034117 | 0.041199 | 121.6141 | -0.30212 | 121.4081 | -0.21973 | -0.35248 | -0.31128 | -0.064087 | -0.032043 | -0.25635 | -0.091553 | -0.004578 | -0.032043 | 0.027466 | 0.022888 | -0.041198 | -0.24719 | 0.10529 | 0.013733 | -0.027466 | -0.009155 | -0.050354 | 0.068664 | -121.6873 | -121.7468 | 0.32043 | 0.35248 | 0.29297 | 0.28381 | 0.22431 | 0.082397 | 121.7102 | 0.25177 | 0.1648 | 121.9162 | 0.22431 | 121.9391 | 0.29297 | -121.9574 | -121.9116 | 121.7331 | 0.23346 | 0.36621 | 0.26093
1822.125 | 121.9894 | -0.27924 | 121.669 | -0.012131 | 0.00097838 | 0.055777 | 0.05152 | -0.0032599 | -0.0074938 | -0.0036636 | -0.005371 | 0.030862 | 0.04114 | 0.0026661 | 0.013403 | 0.025246 | 0.00086095 | 0.022888 | 121.582 | -0.25177 | 121.4722 | -0.11902 | -0.24261 | -0.20599 | -0.027466 | -0.064087 | -0.23804 | -0.054932 | 0.07782 | 0.050354 | 0.082397 | 0.027466 | -0.086975 | -0.19684 | 0.16022 | 0.073242 | 0.036621 | 0.045776 | 0.009155 | 0.041199 | -121.7331 | -121.7239 | 0.35706 | 0.36163 | 0.32959 | 0.32043 | 0.28839 | 0.13275 | 121.7239 | 0.31586 | 0.1831 | 121.8338 | 0.17395 | 121.8613 | 0.21515 | -121.9208 | -121.907 | 121.7514 | 0.2243 | 0.30212 | 0.25177
1823.8906 | 121.8933 | -0.29297 | 121.6919 | -0.012131 | 0.0037556 | 0.0577 | 0.055151 | 0.0035761 | -0.0066394 | -0.00345 | -0.0084228 | 0.033212 | 0.042849 | 0.011852 | 0.018743 | 0.024391 | 0.0017153 | 0.10529 | 121.6461 | -0.25635 | 121.463 | -0.1831 | -0.32501 | -0.29755 | -0.07782 | -0.032043 | -0.24261 | -0.10529 | -0.013733 | -0.054932 | -0.004578 | 0.036621 | -0.045777 | -0.22888 | 0.10986 | -0.004577 | -0.032043 | -0.041198 | -0.068664 | 0.050354 | -121.7239 | -121.7972 | 0.27924 | 0.28839 | 0.23804 | 0.23804 | 0.18768 | 0.073243 | 121.7194 | 0.22888 | 0.13733 | 121.9025 | 0.21057 | 121.9391 | 0.26093 | -121.9482 | -121.9345 | 121.756 | 0.18768 | 0.39825 | 0.21515
1825.6406 | 121.9299 | -0.3067 | 121.6919 | -0.012131 | 0.0014056 | 0.057059 | 0.053228 | 0.0046441 | -0.008562 | -0.0047318 | -0.0084228 | 0.032571 | 0.043062 | 0.0069385 | 0.01618 | 0.02546 | -0.0029843 | 0.032043 | 121.6461 | -0.27008 | 121.4081 | -0.20142 | -0.33875 | -0.29297 | -0.091553 | -0.036621 | -0.2243 | -0.10071 | 0.004578 | -0.041199 | 0.004578 | 0.036621 | -0.045777 | -0.28381 | 0.10529 | 0.013733 | -0.032043 | -0.022888 | -0.068664 | 0.082398 | -121.7285 | -121.7926 | 0.31128 | 0.31128 | 0.2655 | 0.22888 | 0.18311 | 0.068665 | 121.6782 | 0.22888 | 0.1236 | 121.9162 | 0.18768 | 121.9528 | 0.27008 | -121.962 | -121.9162 | 121.7148 | 0.20599 | 0.33874 | 0.21515
1827.3281 | 122.0444 | -0.27008 | 121.6553 | -0.012131 | 0.00012398 | 0.053641 | 0.050451 | -0.0011237 | -0.0081348 | -0.0004592 | -0.0023192 | 0.031289 | 0.041567 | -0.00075193 | 0.014898 | 0.025032 | -0.0010617 | 0.07782 | 121.6232 | -0.24261 | 121.5271 | -0.059509 | -0.18768 | -0.13275 | 0.032043 | -0.068665 | -0.18768 | 0.013733 | 0.14191 | 0.10529 | 0.11444 | 0.027466 | -0.032043 | -0.12817 | 0.21057 | 0.13733 | 0.082398 | 0.10986 | 0.054932 | 0.082398 | -121.7239 | -121.6415 | 0.41199 | 0.38452 | 0.37537 | 0.30212 | 0.29297 | 0.18311 | 121.7697 | 0.32959 | 0.20142 | 121.8658 | 0.11902 | 121.8933 | 0.20142 | -121.8979 | -121.843 | 121.7972 | 0.28381 | 0.3479 | 0.30212
1829.0938 | 121.9391 | -0.29297 | 121.6965 | -0.012131 | -8.9824e-05 | 0.055777 | 0.054297 | 0.0040033 | -0.0087756 | 0.0001816 | -0.0023192 | 0.032571 | 0.040071 | 0.0048023 | 0.017248 | 0.026528 | -0.0010617 | 0.10071 | 121.669 | -0.27466 | 121.4447 | -0.17853 | -0.27924 | -0.27466 | -0.09613 | -0.036621 | -0.24261 | -0.11444 | 0.027466 | -0.018311 | 0.022888 | 0.018311 | -0.027466 | -0.25177 | 0.11444 | 0.018311 | 0.013733 | 0 | -0.004578 | 0.050354 | -121.7331 | -121.8109 | 0.32043 | 0.31586 | 0.27466 | 0.2655 | 0.2243 | 0.09613 | 121.7194 | 0.27008 | 0.12817 | 121.9437 | 0.20599 | 121.962 | 0.25635 | -121.9711 | -121.9391 | 121.7377 | 0.17853 | 0.39368 | 0.19684
1830.8438 | 122.0581 | -0.23346 | 121.669 | -0.012131 | -0.00051702 | 0.054922 | 0.050238 | 0.00079894 | -0.0098438 | -0.0045182 | -0.005371 | 0.030221 | 0.04114 | 0.0052295 | 0.016607 | 0.025673 | -0.0044797 | 0.11444 | 121.6095 | -0.21515 | 121.6003 | -0.004578 | -0.1236 | -0.11444 | 0.10986 | -0.068665 | -0.19684 | 0 | 0.15564 | 0.10986 | 0.086975 | 0.01831 | -0.059509 | -0.068664 | 0.22888 | 0.11902 | 0.10986 | 0.10071 | 0.091553 | 0.036621 | -121.7377 | -121.669 | 0.3891 | 0.32043 | 0.34332 | 0.28381 | 0.3067 | 0.21057 | 121.8155 | 0.35248 | 0.19684 | 121.8246 | 0.12817 | 121.843 | 0.16479 | -121.8842 | -121.8658 | 121.8338 | 0.23346 | 0.3479 | 0.34332
1832.5938 | 121.994 | -0.24719 | 121.6965 | -0.0045011 | 0.002901 | 0.056845 | 0.05451 | 0.0014397 | -0.0087756 | -0.0032364 | -0.005371 | 0.033853 | 0.043062 | 0.0011707 | 0.017675 | 0.024605 | -0.0012753 | 0.036621 | 121.6827 | -0.23804 | 121.5134 | -0.13733 | -0.25177 | -0.20599 | -0.009155 | -0.059509 | -0.19684 | -0.013733 | 0.086975 | 0.045776 | 0.086975 | 0.009155 | -0.013733 | -0.1831 | 0.10986 | 0.041198 | -0.004578 | 0.032043 | -0.013733 | 0.050354 | -121.756 | -121.7102 | 0.33417 | 0.33417 | 0.29297 | 0.28381 | 0.24261 | 0.10071 | 121.7514 | 0.28381 | 0.18311 | 121.9208 | 0.13733 | 121.9299 | 0.18768 | -121.9345 | -121.8933 | 121.7606 | 0.23346 | 0.28381 | 0.23804
1834.3594 | 121.9208 | -0.28839 | 121.7468 | -0.012131 | 0.00033758 | 0.053854 | 0.054724 | -0.0015509 | -0.010057 | -0.000673 | -0.0084228 | 0.032785 | 0.043489 | 0.010997 | 0.016393 | 0.026314 | -0.0042661 | 0.086975 | 121.6827 | -0.23804 | 121.4767 | -0.15564 | -0.24261 | -0.23804 | -0.10529 | -0.027466 | -0.20599 | -0.10529 | 0.013733 | -0.032043 | 0.004578 | 0.050354 | -0.064087 | -0.27008 | 0.13275 | 0.050354 | 0.045776 | 0 | -0.004578 | 0.082397 | -121.7743 | -121.8521 | 0.30212 | 0.29297 | 0.25635 | 0.21057 | 0.17395 | 0.082397 | 121.7148 | 0.21973 | 0.10071 | 121.9208 | 0.17853 | 121.9711 | 0.26093 | -121.9849 | -121.9528 | 121.7651 | 0.18311 | 0.37537 | 0.18311
1836.125 | 121.9391 | -0.23346 | 121.7285 | -0.01976 | 0.0037556 | 0.054495 | 0.05152 | -0.0015509 | -0.010485 | -0.0011002 | -0.005371 | 0.032998 | 0.042849 | 0.01057 | 0.018102 | 0.025246 | -0.0038389 | 0.12817 | 121.7102 | -0.22888 | 121.5225 | -0.12817 | -0.21515 | -0.21057 | -0.082397 | -0.036621 | -0.18768 | -0.073242 | 0.041199 | 0.004578 | 0.050354 | 0.004577 | -0.018311 | -0.20599 | 0.10528 | 0.022888 | 0.01831 | 0.018311 | 0.013733 | 0.045776 | -121.7651 | -121.8018 | 0.27466 | 0.28381 | 0.23804 | 0.23804 | 0.19226 | 0.10071 | 121.7514 | 0.22888 | 0.11444 | 121.9391 | 0.15106 | 121.9437 | 0.19684 | -121.9574 | -121.9162 | 121.756 | 0.16022 | 0.36163 | 0.15106
1837.8906 | 122.0398 | -0.2243 | 121.6873 | -0.012131 | -0.00073062 | 0.055777 | 0.051092 | -0.0026191 | -0.0089892 | -0.000673 | -0.0023192 | 0.031076 | 0.043062 | 0.0067249 | 0.016393 | 0.025246 | -0.0055479 | 0.11902 | 121.6644 | -0.1831 | 121.6278 | 0.027466 | -0.10986 | -0.07782 | 0.054932 | -0.059509 | -0.16022 | 0.018311 | 0.14191 | 0.13275 | 0.10071 | 0.041199 | -0.022888 | -0.059509 | 0.25177 | 0.14648 | 0.11444 | 0.10528 | 0.073242 | 0.064087 | -121.7468 | -121.669 | 0.36621 | 0.32501 | 0.35706 | 0.26093 | 0.29297 | 0.21057 | 121.8109 | 0.30212 | 0.17853 | 121.8475 | 0.10071 | 121.8887 | 0.16479 | -121.8704 | -121.8475 | 121.8521 | 0.24261 | 0.34332 | 0.27924
1839.5938 | 122.0032 | -0.18768 | 121.7468 | -0.012131 | 0.0033282 | 0.056204 | 0.053015 | -0.0019781 | -0.008562 | -0.0002456 | -0.005371 | 0.03663 | 0.042208 | 0.0013843 | 0.018316 | 0.028023 | -0.0044797 | 0.036621 | 121.7422 | -0.1831 | 121.5637 | -0.059509 | -0.19226 | -0.16479 | -0.032043 | -0.07782 | -0.13733 | -0.013733 | 0.10529 | 0.064087 | 0.09613 | 0.004578 | -0.004577 | -0.1831 | 0.12817 | 0.022888 | -0.004578 | 0.01831 | -0.009156 | 0.050354 | -121.8246 | -121.7606 | 0.29297 | 0.28381 | 0.25177 | 0.23346 | 0.20142 | 0.1236 | 121.7468 | 0.24262 | 0.1236 | 121.9254 | 0.059509 | 121.9299 | 0.10986 | -121.9299 | -121.8842 | 121.7514 | 0.17395 | 0.2243 | 0.15564
1841.3438 | 122.0444 | -0.15106 | 121.7468 | 0.0031279 | 0.0052508 | 0.056418 | 0.053015 | 0.00015814 | -0.006853 | -0.0019546 | -0.0084228 | 0.034707 | 0.04178 | 0.00095707 | 0.01853 | 0.025887 | -0.0042661 | 0.09613 | 121.7331 | -0.12817 | 121.6644 | 0.041199 | -0.10071 | -0.064087 | 0.045776 | -0.09613 | -0.086975 | 0.009155 | 0.13733 | 0.064087 | 0.11444 | 0.022888 | -0.013733 | -0.082397 | 0.19226 | 0.086975 | 0.050354 | 0.064087 | 0.027466 | 0.064087 | -121.843 | -121.7377 | 0.28839 | 0.2655 | 0.21515 | 0.20142 | 0.15106 | 0.16937 | 121.7926 | 0.2243 | 0.09613 | 121.8613 | -0.009155 | 121.8842 | 0.054932 | -121.875 | -121.8338 | 121.8155 | 0.16022 | 0.24719 | 0.19684
1843.0312 | 122.0032 | -0.16022 | 121.8018 | -0.012131 | 0.001833 | 0.05535 | 0.05216 | 0.0046441 | -0.010057 | -0.0036636 | -0.0084228 | 0.03663 | 0.042849 | 0.0013843 | 0.013189 | 0.02546 | -0.00020725 | 0.032043 | 121.756 | -0.14191 | 121.6095 | -0.004578 | -0.11902 | -0.086975 | -0.036621 | -0.068665 | -0.091553 | -0.054932 | 0.09613 | 0.032043 | 0.068665 | 0.01831 | -0.045777 | -0.19226 | 0.15564 | 0.073242 | 0.041198 | 0.054932 | 0.022888 | 0.068664 | -121.8704 | -121.8567 | 0.25635 | 0.22888 | 0.19226 | 0.16022 | 0.1236 | 0.13733 | 121.7514 | 0.18768 | 0.036621 | 121.8979 | 0.022888 | 121.9162 | 0.091552 | -121.9437 | -121.8933 | 121.7697 | 0.10528 | 0.19226 | 0.1236
1844.7812 | 121.9254 | -0.19684 | 121.8109 | -0.0045011 | 0.0014056 | 0.055136 | 0.051947 | -0.0032599 | -0.0094164 | -0.001741 | -0.005371 | 0.037271 | 0.04413 | 0.0060841 | 0.016821 | 0.0261 | -0.0012753 | 0.09613 | 121.7651 | -0.16937 | 121.5637 | -0.082397 | -0.1831 | -0.16022 | -0.11902 | -0.064087 | -0.11902 | -0.13275 | 0.009155 | -0.032043 | 0.004578 | 0.027465 | -0.045776 | -0.24719 | 0.11444 | 0.036621 | 0.013733 | 0.009156 | -0.013732 | 0.077819 | -121.875 | -121.9437 | 0.20599 | 0.20142 | 0.1648 | 0.1236 | 0.086976 | 0.086976 | 121.7331 | 0.12817 | -0.013732 | 121.9345 | 0.054932 | 121.962 | 0.13275 | -121.9803 | -121.9299 | 121.7606 | 0.064087 | 0.29297 | 0.077819
1846.5469 | 121.9391 | -0.16937 | 121.7834 | -0.0045011 | 0.0043964 | 0.055777 | 0.054724 | 0.0035761 | -0.0066394 | -0.0004592 | -0.0084228 | 0.037057 | 0.042849 | -0.0033153 | 0.01853 | 0.02311 | -0.0061887 | 0.14191 | 121.7789 | -0.14191 | 121.6049 | -0.022888 | -0.16479 | -0.11902 | -0.045776 | -0.068665 | -0.09613 | -0.10071 | 0.027466 | -0.041199 | 0.009155 | 0.027466 | -0.004577 | -0.17853 | 0.14649 | 0.050354 | 0.004578 | 0.022888 | -0.022888 | 0.073243 | -121.8521 | -121.8842 | 0.19684 | 0.17853 | 0.12817 | 0.10528 | 0.054931 | 0.11902 | 121.7468 | 0.1236 | -0.004578 | 121.9208 | 0.027465 | 121.9482 | 0.10071 | -121.9254 | -121.8796 | 121.7743 | 0.068665 | 0.31128 | 0.1236
1848.2656 | 121.9162 | -0.1831 | 121.8018 | 0.0031279 | 0.0039692 | 0.05535 | 0.052588 | 0.0025079 | -0.0092028 | -0.0019546 | -0.0023192 | 0.03663 | 0.042635 | 0.0058703 | 0.018316 | 0.022896 | -0.0051205 | 0.13733 | 121.7926 | -0.1236 | 121.6095 | -0.018311 | -0.16022 | -0.13733 | -0.054932 | -0.059509 | -0.10071 | -0.11444 | 0.036621 | -0.045776 | 0.018311 | 0.059509 | -0.009155 | -0.19226 | 0.16479 | 0.045776 | 0.022888 | -0.013733 | -0.036621 | 0.082397 | -121.8613 | -121.9162 | 0.21973 | 0.20142 | 0.13733 | 0.11902 | 0.054932 | 0.10528 | 121.7331 | 0.13733 | -0.013733 | 121.9162 | 0.041199 | 121.9757 | 0.1236 | -121.9254 | -121.9025 | 121.7926 | 0.068664 | 0.32043 | 0.12817
1850.0312 | 122.0398 | -0.12817 | 121.7789 | -0.012131 | 0.0043964 | 0.056845 | 0.054083 | 0.0022943 | -0.0057848 | -0.0008866 | -0.005371 | 0.035348 | 0.043489 | 0.0033069 | 0.018957 | 0.026741 | -0.0012753 | 0.09613 | 121.7606 | -0.12817 | 121.6736 | 0.054932 | -0.073242 | -0.036621 | 0.041199 | -0.086975 | -0.068665 | 0.013733 | 0.13733 | 0.068665 | 0.10986 | 0 | -0.018311 | -0.10529 | 0.18311 | 0.091553 | 0.054932 | 0.091553 | 0.054932 | 0.059509 | -121.8658 | -121.7651 | 0.2655 | 0.23804 | 0.19684 | 0.17853 | 0.13733 | 0.18311 | 121.8018 | 0.20599 | 0.082398 | 121.8887 | -0.01831 | 121.8887 | 0.041199 | -121.907 | -121.8475 | 121.8018 | 0.14191 | 0.2243 | 0.16937
1851.7969 | 121.9894 | -0.15564 | 121.8063 | -0.01976 | 0.002901 | 0.055563 | 0.05216 | -0.0019781 | -0.006853 | -0.0025956 | -0.005371 | 0.037057 | 0.045626 | 0.0011707 | 0.016393 | 0.027382 | -0.0029843 | 0.032043 | 121.7514 | -0.12817 | 121.637 | 0.018311 | -0.09613 | -0.064087 | -0.036621 | -0.09613 | -0.082397 | -0.064087 | 0.07782 | 0.036621 | 0.050354 | 0.027466 | -0.054931 | -0.16937 | 0.17395 | 0.091553 | 0.05951 | 0.064087 | 0.032044 | 0.073243 | -121.9025 | -121.8704 | 0.23346 | 0.20599 | 0.19226 | 0.13275 | 0.11902 | 0.14649 | 121.7651 | 0.16022 | 0.01831 | 121.8796 | -0.013733 | 121.907 | 0.05951 | -121.9345 | -121.8887 | 121.7926 | 0.091553 | 0.18768 | 0.11902
1853.4844 | 121.9528 | -0.16937 | 121.8292 | -0.01976 | 0.0022602 | 0.054495 | 0.052801 | 0.0040033 | -0.010485 | -0.0030228 | 0.00073235 | 0.03898 | 0.043703 | -0.00075193 | 0.018743 | 0.025246 | 0.0010745 | 0.1236 | 121.7972 | -0.16022 | 121.6003 | -0.054932 | -0.12817 | -0.14191 | -0.10529 | -0.041199 | -0.086975 | -0.10986 | 0.059509 | 0.004578 | 0.041199 | 0.009156 | -0.032044 | -0.22888 | 0.11444 | 0.027466 | 0.041199 | 0.01831 | 0.032043 | 0.082398 | -121.8704 | -121.9391 | 0.22888 | 0.21057 | 0.17395 | 0.12817 | 0.091553 | 0.10528 | 121.7606 | 0.14648 | -0.022888 | 121.9574 | 0.045776 | 121.9666 | 0.12817 | -121.9894 | -121.9162 | 121.7697 | 0.05951 | 0.29297 | 0.064087
1855.25 | 122.0398 | -0.13275 | 121.8018 | -0.02739 | 0.0022602 | 0.058127 | 0.055151 | 0.0027215 | -0.008562 | -0.0045182 | -0.0023192 | 0.038125 | 0.04413 | 0.0048023 | 0.016393 | 0.025673 | -0.0049069 | 0.045776 | 121.7972 | -0.13733 | 121.637 | 0.013733 | -0.13275 | -0.10529 | 0 | -0.082397 | -0.07782 | -0.013733 | 0.11444 | 0.064087 | 0.11444 | -0.004578 | -0.004578 | -0.1648 | 0.14648 | 0.027465 | 0 | 0.032043 | 0.004578 | 0.054931 | -121.8842 | -121.8155 | 0.24719 | 0.24719 | 0.19684 | 0.19226 | 0.14191 | 0.15106 | 121.7743 | 0.19226 | 0.064087 | 121.9345 | -0.004577 | 121.9299 | 0.050354 | -121.9391 | -121.8796 | 121.7697 | 0.11902 | 0.17853 | 0.13275
1857.0156 | 121.9437 | -0.17853 | 121.8292 | -0.0045011 | 0.0039692 | 0.054495 | 0.054083 | -0.00069646 | -0.0077074 | -0.0032364 | -0.0084228 | 0.034494 | 0.04413 | 0.00031607 | 0.016821 | 0.0261 | -0.0014891 | 0.059509 | 121.8109 | -0.14191 | 121.5729 | -0.054932 | -0.19226 | -0.15564 | -0.09613 | -0.054932 | -0.10071 | -0.091553 | 0.022888 | -0.032043 | 0.013733 | 0.036621 | -0.018311 | -0.25635 | 0.1236 | 0.022888 | -0.013733 | -0.013733 | -0.050354 | 0.07782 | -121.8842 | -121.9208 | 0.20142 | 0.19226 | 0.14648 | 0.11444 | 0.068665 | 0.086975 | 121.7148 | 0.1236 | 0.009155 | 121.9528 | 0.045776 | 121.9894 | 0.1236 | -121.9711 | -121.9299 | 121.7514 | 0.086975 | 0.23804 | 0.082398
1858.7812 | 121.9803 | -0.14648 | 121.8063 | -0.012131 | 0.002901 | 0.056418 | 0.050238 | -0.0036871 | -0.00963 | -0.0008866 | -0.005371 | 0.035989 | 0.043276 | -0.0052381 | 0.015112 | 0.025887 | -0.0042661 | 0.13733 | 121.788 | -0.09613 | 121.7056 | 0.082397 | -0.050354 | -0.018311 | 0.018311 | -0.082397 | -0.091553 | -0.050354 | 0.11444 | 0.068665 | 0.068665 | 0.050354 | -0.01831 | -0.10071 | 0.22888 | 0.12817 | 0.09613 | 0.077819 | 0.045776 | 0.054931 | -121.8887 | -121.8567 | 0.26093 | 0.21515 | 0.21515 | 0.16022 | 0.16022 | 0.17853 | 121.8018 | 0.20599 | 0.041199 | 121.8842 | 0.009156 | 121.9345 | 0.064087 | -121.9025 | -121.8979 | 121.8521 | 0.09613 | 0.28381 | 0.16479
1860.4844 | 122.0032 | -0.15106 | 121.8201 | -0.012131 | 0.0041828 | 0.055777 | 0.05451 | 0.0010125 | -0.0072802 | -0.0040908 | 0.00073235 | 0.03898 | 0.044344 | -0.0060925 | 0.018316 | 0.025246 | -0.0059751 | 0.045776 | 121.8246 | -0.14648 | 121.6095 | -0.036621 | -0.15106 | -0.13275 | -0.050354 | -0.059509 | -0.086975 | -0.036621 | 0.082397 | 0.022888 | 0.10071 | 0.004578 | 0.004578 | -0.21057 | 0.11444 | 0.018311 | 0 | 0.013733 | -0.004578 | 0.064087 | -121.8796 | -121.8567 | 0.23346 | 0.25177 | 0.17395 | 0.18768 | 0.10986 | 0.10986 | 121.756 | 0.16937 | 0.050354 | 121.9711 | 0.027466 | 121.9757 | 0.091553 | -121.9666 | -121.907 | 121.7606 | 0.11444 | 0.19684 | 0.10071
1862.25 | 121.8979 | -0.17853 | 121.8384 | -0.0045011 | 0.0043964 | 0.056845 | 0.052801 | 0.00079894 | -0.0079212 | -0.0057998 | -0.005371 | 0.037912 | 0.044985 | 0.0071521 | 0.016821 | 0.026528 | -0.0021299 | 0.082397 | 121.8246 | -0.15106 | 121.5775 | -0.082397 | -0.21057 | -0.17395 | -0.13275 | -0.050354 | -0.09613 | -0.1236 | -0.022888 | -0.054932 | 0.004578 | 0.027466 | -0.013733 | -0.26093 | 0.096131 | 0.004578 | -0.032043 | -0.022888 | -0.059509 | 0.082398 | -121.8887 | -121.962 | 0.15564 | 0.18311 | 0.1236 | 0.10071 | 0.041198 | 0.068665 | 121.7285 | 0.073242 | -0.027466 | 121.9757 | 0.045776 | 122.0032 | 0.12817 | -121.9894 | -121.9345 | 121.756 | 0.054932 | 0.26092 | 0.045777
1863.9531 | 121.9254 | -0.1831 | 121.8475 | 0.0031279 | 0.0016192 | 0.054922 | 0.053442 | 0.0035761 | -0.00963 | -0.0032364 | -0.005371 | 0.038339 | 0.043703 | -0.00075193 | 0.016821 | 0.025032 | -0.0031979 | 0.086975 | 121.7834 | -0.15564 | 121.5729 | -0.054932 | -0.16022 | -0.14648 | -0.11444 | -0.036621 | -0.11902 | -0.11902 | 0.009155 | -0.032043 | 0.013733 | 0.027465 | -0.064087 | -0.27466 | 0.12817 | 0.036621 | 0.022888 | 0.009156 | -0.004577 | 0.064086 | -121.8842 | -121.9666 | 0.19226 | 0.19684 | 0.15106 | 0.13275 | 0.086976 | 0.10071 | 121.7285 | 0.12817 | 0 | 121.9391 | 0.082398 | 121.9666 | 0.14648 | -122.0032 | -121.9666 | 121.756 | 0.064086 | 0.27008 | 0.068664
1865.7188 | 122.0123 | -0.11902 | 121.8063 | -0.0045011 | 0.00055118 | 0.056631 | 0.051733 | -0.0058233 | -0.010271 | -0.0038772 | -0.0023192 | 0.036843 | 0.04413 | -0.00053833 | 0.015325 | 0.023537 | -0.0021299 | 0.032043 | 121.7697 | -0.10986 | 121.6415 | 0.027466 | -0.10529 | -0.050354 | -0.045776 | -0.086975 | -0.09613 | -0.045776 | 0.082397 | 0.064087 | 0.091553 | 0.009156 | -0.036621 | -0.16479 | 0.14649 | 0.068665 | 0.013733 | 0.059509 | 0.004577 | 0.022889 | -121.8933 | -121.8521 | 0.20142 | 0.21057 | 0.18311 | 0.18768 | 0.16022 | 0.13733 | 121.7514 | 0.17853 | 0.050354 | 121.8796 | 0.009155 | 121.8887 | 0.032044 | -121.9162 | -121.9025 | 121.7606 | 0.073243 | 0.15106 | 0.073243
1867.4844 | 121.907 | -0.15564 | 121.8521 | -0.012131 | 0.006319 | 0.056418 | 0.054083 | 0.0040033 | -0.006853 | -0.0004592 | -0.0023192 | 0.038552 | 0.043062 | 0.0065113 | 0.01917 | 0.023323 | -0.0034117 | 0.10529 | 121.8201 | -0.13275 | 121.5958 | -0.050354 | -0.16479 | -0.14191 | -0.091553 | -0.059509 | -0.086975 | -0.13275 | -0.013733 | -0.050354 | 0.004578 | 0.022889 | -0.032044 | -0.25635 | 0.10529 | 0.013733 | -0.009155 | -0.009156 | -0.032044 | 0.068665 | -121.9116 | -121.9849 | 0.14191 | 0.16022 | 0.10529 | 0.091553 | 0.036621 | 0.082397 | 121.7285 | 0.073242 | -0.045776 | 121.9528 | 0.027466 | 121.9757 | 0.096131 | -121.9849 | -121.9391 | 121.7514 | 0.022889 | 0.26093 | 0.064087
1869.25 | 121.9299 | -0.18768 | 121.875 | -0.0045011 | 0.00012398 | 0.054282 | 0.051947 | -0.0015509 | -0.010698 | 0.0003952 | -0.005371 | 0.038125 | 0.043489 | -0.00096553 | 0.014898 | 0.024819 | -0.0017027 | 0.12817 | 121.7651 | -0.1236 | 121.6141 | -0.018311 | -0.11902 | -0.10529 | -0.073242 | -0.050354 | -0.10529 | -0.13275 | 0 | 0 | -0.004578 | 0.064087 | -0.10986 | -0.26093 | 0.16937 | 0.082397 | 0.068664 | 0.01831 | 0.004577 | 0.082397 | -121.9254 | -122.0078 | 0.18768 | 0.1831 | 0.18768 | 0.10071 | 0.10529 | 0.10528 | 121.7377 | 0.10529 | -0.027465 | 121.8887 | 0.054932 | 121.9528 | 0.13733 | -121.9986 | -121.9803 | 121.8018 | 0.054932 | 0.31586 | 0.11444
1871 | 122.0535 | -0.12817 | 121.8109 | -0.012131 | 0.0020466 | 0.055777 | 0.050665 | -0.00091006 | -0.0087756 | -0.0030228 | -0.005371 | 0.037271 | 0.04178 | 0.0058703 | 0.01383 | 0.025032 | -0.0066159 | 0.059509 | 121.7651 | -0.10071 | 121.6827 | 0.073242 | -0.032043 | -0.027466 | 0.050354 | -0.082397 | -0.082397 | -0.004578 | 0.12817 | 0.1236 | 0.1236 | 0.027466 | -0.045776 | -0.12817 | 0.20142 | 0.10071 | 0.096131 | 0.073242 | 0.068665 | 0.045777 | -121.8933 | -121.8155 | 0.25635 | 0.25177 | 0.25177 | 0.20599 | 0.20599 | 0.17395 | 121.7834 | 0.21057 | 0.077819 | 121.8658 | 0 | 121.8933 | 0.045777 | -121.9116 | -121.8933 | 121.8109 | 0.1236 | 0.18768 | 0.17853
1872.6875 | 121.9528 | -0.14648 | 121.8704 | -0.012131 | 0.0014056 | 0.055136 | 0.05152 | 0.0010125 | -0.0074938 | -0.000673 | -0.0084228 | 0.037698 | 0.046907 | -0.00096553 | 0.018102 | 0.02311 | -0.0031979 | 0.10986 | 121.8063 | -0.13733 | 121.6003 | -0.059509 | -0.13733 | -0.1236 | -0.09613 | -0.045776 | -0.11444 | -0.10529 | 0 | 0.004578 | 0.018311 | 0.009155 | -0.064087 | -0.27008 | 0.086975 | 0.022888 | 0.009155 | 0.013733 | 0 | 0.032043 | -121.9162 | -121.9757 | 0.14648 | 0.16479 | 0.15106 | 0.13275 | 0.11902 | 0.07782 | 121.7377 | 0.11444 | 0.009155 | 121.9437 | 0.068665 | 121.9528 | 0.10071 | -122.0078 | -121.9849 | 121.7468 | 0.041198 | 0.25635 | 0.050354
1874.4531 | 121.9299 | -0.16022 | 121.8063 | -0.012131 | 0.0061054 | 0.057913 | 0.053869 | -0.0013373 | -0.0083484 | -0.000673 | -0.005371 | 0.037057 | 0.043917 | 0.011852 | 0.016393 | 0.0261 | -0.0051205 | 0.054932 | 121.8384 | -0.13275 | 121.5912 | -0.054932 | -0.19684 | -0.14648 | -0.10529 | -0.013733 | -0.09613 | -0.091553 | -0.041199 | -0.027466 | 0.022888 | 0.027466 | 0.032044 | -0.21515 | 0.10528 | 0.013733 | -0.036621 | -0.013733 | -0.064087 | 0.064087 | -121.8201 | -121.8979 | 0.11902 | 0.1831 | 0.13275 | 0.11902 | 0.068664 | 0.077819 | 121.7239 | 0.054931 | 0.004577 | 121.9711 | 0.082397 | 121.9986 | 0.14648 | -121.9391 | -121.9025 | 121.7514 | 0.068664 | 0.21515 | 0.054931
1876.2031 | 121.9574 | -0.15564 | 121.8658 | -0.012131 | 0.0026874 | 0.055991 | 0.053442 | -0.0019781 | -0.0098438 | -0.0021682 | -0.005371 | 0.036843 | 0.042208 | 0.0024525 | 0.016393 | 0.024178 | -0.0085385 | 0.10986 | 121.8063 | -0.13733 | 121.6187 | -0.036621 | -0.12817 | -0.13275 | -0.07782 | -0.041199 | -0.086975 | -0.082397 | 0.018311 | 0.009155 | 0.041199 | 0.018311 | -0.05951 | -0.24719 | 0.11902 | 0.022889 | 0.027466 | 0.004578 | 0.009155 | 0.068665 | -121.907 | -121.9482 | 0.17395 | 0.19684 | 0.16479 | 0.12817 | 0.09613 | 0.10071 | 121.756 | 0.10529 | 0.004578 | 121.9437 | 0.045776 | 121.962 | 0.11444 | -122.0032 | -121.9528 | 121.7743 | 0.073243 | 0.2655 | 0.07782
1877.9688 | 121.9666 | -0.16022 | 121.8475 | -0.012131 | 0.0050372 | 0.054709 | 0.054083 | 0.0016535 | -0.0089892 | -0.0015274 | -0.005371 | 0.034921 | 0.043703 | 0.0011707 | 0.017889 | 0.025246 | -0.0046933 | 0.15106 | 121.8338 | -0.10529 | 121.6599 | 0.041199 | -0.10071 | -0.091553 | -0.027466 | -0.032043 | -0.086975 | -0.059509 | 0.045776 | 0.018311 | 0.059509 | 0.054931 | -0.013733 | -0.18768 | 0.20142 | 0.068664 | 0.059509 | 0.013733 | 0.004578 | 0.073242 | -121.8796 | -121.907 | 0.20599 | 0.21973 | 0.17853 | 0.14648 | 0.10529 | 0.14649 | 121.7651 | 0.13275 | 0.027466 | 121.9391 | 0.054932 | 121.994 | 0.12817 | -121.9528 | -121.9345 | 121.8201 | 0.10071 | 0.31128 | 0.13275
1879.6719 | 121.9986 | -0.14648 | 121.8292 | -0.01976 | 0.00097838 | 0.057059 | 0.051306 | 0.0031487 | -0.0079212 | -0.0032364 | -0.0084228 | 0.03428 | 0.043062 | -0.0024609 | 0.015539 | 0.027169 | -0.0014891 | 0.022888 | 121.7926 | -0.10071 | 121.6553 | 0.032043 | -0.086975 | -0.050354 | -0.013733 | -0.07782 | -0.059509 | -0.041199 | 0.050354 | 0.054932 | 0.050354 | 0.045776 | -0.036621 | -0.17395 | 0.17853 | 0.09613 | 0.059509 | 0.050354 | 0.013733 | 0.086975 | -121.907 | -121.8704 | 0.19684 | 0.19684 | 0.20142 | 0.10986 | 0.11444 | 0.13275 | 121.756 | 0.10986 | 0.01831 | 121.8933 | -0.018311 | 121.9391 | 0.068664 | -121.9299 | -121.8887 | 121.8018 | 0.10529 | 0.16937 | 0.13275
1881.4375 | 122.0535 | -0.11902 | 121.8201 | -0.01976 | 0.0048236 | 0.057272 | 0.054937 | 0.0022943 | -0.005144 | -0.0043046 | -0.0084228 | 0.036416 | 0.042635 | 0.0082203 | 0.016607 | 0.025673 | -0.0040525 | 0.068665 | 121.8338 | -0.10986 | 121.6919 | 0.059509 | -0.091553 | -0.036621 | 0.059509 | -0.073242 | -0.054932 | 0.022888 | 0.091553 | 0.086975 | 0.1236 | 0.009156 | 0.013733 | -0.12817 | 0.17853 | 0.082398 | 0.027466 | 0.073242 | 0.01831 | 0.064087 | -121.8933 | -121.7972 | 0.21057 | 0.24261 | 0.20599 | 0.17853 | 0.14191 | 0.16937 | 121.8018 | 0.14649 | 0.07782 | 121.9437 | -0.01831 | 121.9528 | 0.045777 | -121.9299 | -121.875 | 121.8109 | 0.14191 | 0.18768 | 0.17853
1883.2031 | 122.0215 | -0.11444 | 121.8338 | -0.01976 | 0.0037556 | 0.055563 | 0.051306 | -0.0043281 | -0.0049304 | -0.0013138 | -0.0084228 | 0.035348 | 0.04413 | 0.0030933 | 0.01618 | 0.024819 | 0.00086095 | 0.068665 | 121.7926 | -0.073242 | 121.7148 | 0.1236 | -0.068665 | -0.013733 | 0.059509 | -0.068665 | -0.036621 | -0.027466 | 0.082397 | 0.07782 | 0.086975 | 0.041199 | -0.041198 | -0.11902 | 0.23804 | 0.10071 | 0.045776 | 0.059509 | 0.004577 | 0.07782 | -121.9025 | -121.8613 | 0.19684 | 0.20142 | 0.19226 | 0.1236 | 0.11444 | 0.19684 | 121.788 | 0.11902 | 0.009155 | 121.8658 | -0.032044 | 121.907 | 0.045776 | -121.907 | -121.8704 | 121.8292 | 0.086975 | 0.18311 | 0.17395
1884.9844 | 121.9528 | -0.15106 | 121.8658 | -0.012131 | 0.001192 | 0.053854 | 0.053442 | 0.0016535 | -0.0072802 | -0.0015274 | -0.0084228 | 0.036416 | 0.043703 | 0.00010247 | 0.015966 | 0.024605 | -0.0038389 | 0.10986 | 121.7926 | -0.1236 | 121.6003 | -0.041199 | -0.14648 | -0.11902 | -0.091553 | -0.041199 | -0.09613 | -0.11444 | -0.004578 | -0.009155 | 0.004578 | 0.027466 | -0.073242 | -0.2655 | 0.10986 | 0.032043 | 0.004578 | 0.004577 | -0.022888 | 0.054932 | -121.907 | -121.9803 | 0.14648 | 0.15564 | 0.14191 | 0.10071 | 0.086975 | 0.082397 | 121.7239 | 0.091552 | -0.018311 | 121.9162 | 0.054931 | 121.9437 | 0.10986 | -121.9894 | -121.962 | 121.7514 | 0.036621 | 0.26093 | 0.059509
1886.6875 | 121.9299 | -0.15564 | 121.8842 | -0.012131 | 0.0052508 | 0.055777 | 0.055151 | 0.00058534 | -0.0059986 | -0.000673 | -0.0023192 | 0.036843 | 0.042208 | 0.0050159 | 0.018957 | 0.023537 | -0.0031979 | 0.10986 | 121.8475 | -0.11902 | 121.6187 | -0.036621 | -0.16479 | -0.12817 | -0.082397 | -0.022888 | -0.068665 | -0.11444 | -0.032043 | -0.045776 | 0.004578 | 0.036621 | -0.036621 | -0.2655 | 0.11902 | 0.027466 | -0.009155 | -0.009155 | -0.045776 | 0.086975 | -121.907 | -121.9986 | 0.1236 | 0.16022 | 0.10986 | 0.073243 | 0.022889 | 0.082398 | 121.7377 | 0.036622 | -0.045776 | 121.9666 | 0.045777 | 122.0032 | 0.13275 | -122.0032 | -121.9528 | 121.7743 | 0.041199 | 0.2655 | 0.073243
1888.4375 | 121.9711 | -0.15564 | 121.8475 | -0.02739 | 0.0043964 | 0.054709 | 0.053869 | -0.0026191 | -0.00963 | -0.0019546 | -0.005371 | 0.037271 | 0.045412 | 0.010143 | 0.015966 | 0.02311 | -0.0012753 | 0.16022 | 121.8338 | -0.10529 | 121.6553 | 0.018311 | -0.10071 | -0.091553 | -0.022888 | -0.032043 | -0.064087 | -0.073242 | 0.045776 | 0.027466 | 0.036621 | 0.050354 | -0.013733 | -0.19226 | 0.17395 | 0.064087 | 0.054932 | 0.013733 | 0.004578 | 0.091553 | -121.8796 | -121.9208 | 0.20142 | 0.19226 | 0.18311 | 0.10071 | 0.091553 | 0.1236 | 121.7606 | 0.10986 | -0.009155 | 121.9391 | 0.032044 | 121.9894 | 0.1236 | -121.9528 | -121.9116 | 121.8109 | 0.082398 | 0.31586 | 0.13275
1890.1406 | 122.0123 | -0.11444 | 121.843 | -0.0045011 | 0.002901 | 0.054709 | 0.052374 | -0.0015509 | -0.010057 | -0.0013138 | -0.005371 | 0.03428 | 0.044558 | -0.0067333 | 0.017248 | 0.02546 | -0.0034117 | 0.045776 | 121.7926 | -0.09613 | 121.6599 | 0.050354 | -0.07782 | -0.036621 | -0.004578 | -0.073242 | -0.050354 | -0.045776 | 0.064087 | 0.054932 | 0.054932 | 0.018311 | -0.050354 | -0.18311 | 0.16479 | 0.07782 | 0.036621 | 0.059509 | 0.01831 | 0.064087 | -121.9162 | -121.8887 | 0.17853 | 0.16937 | 0.16937 | 0.10529 | 0.10529 | 0.14648 | 121.756 | 0.11444 | 0.004578 | 121.8887 | -0.022888 | 121.907 | 0.041199 | -121.9391 | -121.8933 | 121.7743 | 0.068665 | 0.16022 | 0.10986
1891.9062 | 121.9208 | -0.17853 | 121.8704 | -0.01976 | 0.00097838 | 0.052786 | 0.052588 | -0.00091006 | -0.0094164 | 0.0012496 | -0.005371 | 0.034921 | 0.044344 | 0.01057 | 0.015966 | 0.023751 | -0.0027707 | 0.10529 | 121.7972 | -0.13733 | 121.6049 | -0.032043 | -0.14191 | -0.1236 | -0.07782 | -0.018311 | -0.086975 | -0.10986 | -0.013733 | -0.009155 | -0.013733 | 0.041199 | -0.073242 | -0.2655 | 0.14648 | 0.054932 | 0.036621 | 0.013733 | -0.004578 | 0.091553 | -121.8887 | -121.9803 | 0.16479 | 0.16479 | 0.16937 | 0.073242 | 0.07782 | 0.10529 | 121.7422 | 0.073242 | -0.022888 | 121.9345 | 0.068664 | 121.9757 | 0.16022 | -122.0078 | -121.9574 | 121.7834 | 0.068665 | 0.28381 | 0.10071
1893.6094 | 122.0306 | -0.14191 | 121.7972 | -0.012131 | -0.0011578 | 0.054709 | 0.050024 | -0.0011237 | -0.0074938 | -0.0047318 | -0.0023192 | 0.032998 | 0.040712 | 0.013347 | 0.014257 | 0.024178 | -0.0036253 | 0.12817 | 121.7514 | -0.11444 | 121.6919 | 0.07782 | -0.041199 | -0.032043 | 0.054932 | -0.036621 | -0.082397 | 0.004578 | 0.14191 | 0.1236 | 0.10071 | 0.027466 | -0.045776 | -0.10528 | 0.21973 | 0.10986 | 0.10071 | 0.082398 | 0.073242 | 0.05951 | -121.8338 | -121.7926 | 0.28381 | 0.24262 | 0.2655 | 0.18311 | 0.20599 | 0.19226 | 121.8063 | 0.2243 | 0.086975 | 121.8658 | 0.045776 | 121.8933 | 0.10529 | -121.9116 | -121.8796 | 121.8338 | 0.14649 | 0.27008 | 0.19684
1895.3906 | 122.0169 | -0.17853 | 121.788 | -0.012131 | 0.00097838 | 0.054922 | 0.053869 | -0.00026906 | -0.0092028 | -0.0015274 | -0.005371 | 0.028726 | 0.040499 | 0.0045887 | 0.014257 | 0.025246 | -0.00084805 | 0.054932 | 121.7056 | -0.13733 | 121.6461 | 0.032043 | -0.11444 | -0.091553 | 0.032043 | -0.050354 | -0.10071 | 0.009155 | 0.07782 | 0.082397 | 0.073242 | 0.041199 | -0.082398 | -0.14191 | 0.21057 | 0.086975 | 0.064087 | 0.045776 | 0.022888 | 0.07782 | -121.8384 | -121.7789 | 0.25635 | 0.25177 | 0.26092 | 0.17395 | 0.18311 | 0.16937 | 121.7834 | 0.17853 | 0.10986 | 121.843 | 0.050354 | 121.8842 | 0.12817 | -121.9254 | -121.8887 | 121.8246 | 0.18768 | 0.23346 | 0.21057
1897.1406 | 121.9711 | -0.19226 | 121.7834 | -0.012131 | 0.006319 | 0.055991 | 0.055365 | 0.00015814 | -0.006853 | -0.0013138 | -0.0084228 | 0.03193 | 0.040712 | 0.016124 | 0.017461 | 0.024605 | -0.0036253 | 0.054932 | 121.7834 | -0.1831 | 121.5637 | -0.086975 | -0.22888 | -0.17853 | -0.045776 | -0.027466 | -0.13275 | -0.018311 | 0.045776 | 0.027466 | 0.059509 | 0.009156 | 0 | -0.21973 | 0.10529 | 0.013733 | -0.036621 | 0.004577 | -0.045777 | 0.05951 | -121.8109 | -121.8018 | 0.23804 | 0.25177 | 0.21973 | 0.19226 | 0.16022 | 0.09613 | 121.7468 | 0.17853 | 0.11444 | 121.9666 | 0.10529 | 121.9757 | 0.16479 | -121.9666 | -121.9162 | 121.756 | 0.17395 | 0.24719 | 0.14648
1898.9062 | 122.0581 | -0.16022 | 121.7743 | -0.012131 | 0.0039692 | 0.0577 | 0.05451 | 0.00015814 | -0.010485 | -0.0038772 | -0.0023192 | 0.02723 | 0.042208 | 0.016551 | 0.018102 | 0.024819 | -0.0051205 | 0.09613 | 121.7606 | -0.15564 | 121.6461 | 0.018311 | -0.11902 | -0.086975 | 0.064087 | -0.064087 | -0.10529 | 0.036621 | 0.11444 | 0.10529 | 0.1236 | 0.004577 | -0.013733 | -0.12817 | 0.17853 | 0.073242 | 0.041198 | 0.068665 | 0.036621 | 0.054931 | -121.8384 | -121.7377 | 0.27466 | 0.28381 | 0.2655 | 0.22888 | 0.21057 | 0.17395 | 121.8018 | 0.21973 | 0.14191 | 121.9162 | 0.041199 | 121.9208 | 0.09613 | -121.9299 | -121.8796 | 121.8063 | 0.19684 | 0.25635 | 0.2243
1900.6094 | 121.9803 | -0.20142 | 121.7926 | -0.01976 | 0.0039692 | 0.05535 | 0.054297 | -0.0024055 | -0.0083484 | -0.002382 | -0.005371 | 0.031289 | 0.042635 | 0.013561 | 0.019598 | 0.025246 | -0.0055479 | 0.059509 | 121.7743 | -0.19226 | 121.55 | -0.10071 | -0.23346 | -0.18768 | -0.054932 | -0.009155 | -0.14191 | -0.054932 | 0.032043 | 0 | 0.045776 | 0.009155 | -0.018311 | -0.24262 | 0.10071 | 0.013733 | -0.032043 | 0.004578 | -0.041198 | 0.059509 | -121.8018 | -121.8475 | 0.23346 | 0.24719 | 0.20142 | 0.18768 | 0.14191 | 0.091553 | 121.7422 | 0.17395 | 0.086975 | 121.9666 | 0.13275 | 121.9757 | 0.19226 | -121.9849 | -121.9345 | 121.7514 | 0.14648 | 0.26093 | 0.14648
1902.3594 | 122.0398 | -0.19226 | 121.7789 | -0.0045011 | 0.0037556 | 0.056845 | 0.051092 | -0.0013373 | -0.0070666 | -0.0047318 | -0.005371 | 0.029794 | 0.043917 | 0.0084339 | 0.017675 | 0.0261 | -0.00063445 | 0.073242 | 121.7285 | -0.14648 | 121.6644 | 0.059509 | -0.10529 | -0.064087 | 0.086975 | -0.059509 | -0.10986 | 0.027466 | 0.11902 | 0.10071 | 0.10071 | 0.045777 | -0.050354 | -0.11444 | 0.25177 | 0.12817 | 0.086975 | 0.082397 | 0.041198 | 0.082398 | -121.8384 | -121.7514 | 0.31128 | 0.29297 | 0.29297 | 0.21057 | 0.21057 | 0.20599 | 121.8109 | 0.22888 | 0.13733 | 121.875 | 0.050354 | 121.9208 | 0.13275 | -121.9254 | -121.8887 | 121.8567 | 0.21973 | 0.2655 | 0.27924
1904.0469 | 122.081 | -0.16937 | 121.7834 | -0.01976 | -0.0011578 | 0.053 | 0.050451 | -0.0017645 | -0.0092028 | -0.0030228 | -0.0084228 | 0.029153 | 0.042208 | 0.0095019 | 0.01618 | 0.027382 | -0.0074705 | 0.14648 | 121.701 | -0.13275 | 121.7056 | 0.073242 | -0.064087 | -0.032043 | 0.10529 | -0.050354 | -0.10986 | 0.032043 | 0.17395 | 0.16022 | 0.10986 | 0.036622 | -0.082397 | -0.07782 | 0.24261 | 0.13733 | 0.10529 | 0.10071 | 0.068664 | 0.05951 | -121.8338 | -121.7514 | 0.34332 | 0.27924 | 0.32959 | 0.21973 | 0.27008 | 0.20599 | 121.8384 | 0.28381 | 0.14191 | 121.8338 | 0.059509 | 121.8704 | 0.11902 | -121.9162 | -121.8933 | 121.875 | 0.20142 | 0.31586 | 0.27466
1905.8125 | 122.0215 | -0.16022 | 121.7834 | -0.0045011 | 0.0035418 | 0.056631 | 0.052801 | 0.0050713 | -0.0053576 | -0.001741 | -0.0023192 | 0.029153 | 0.041994 | 0.010997 | 0.016607 | 0.023323 | -0.0044797 | 0.059509 | 121.7834 | -0.16937 | 121.5912 | -0.059509 | -0.18768 | -0.15106 | 0.004578 | -0.018311 | -0.1236 | 0.022888 | 0.10529 | 0.068665 | 0.091553 | -0.009156 | 0 | -0.19226 | 0.10071 | 0.009155 | -0.027466 | 0.018311 | -0.01831 | 0.036621 | -121.8018 | -121.7606 | 0.2655 | 0.25177 | 0.22888 | 0.21515 | 0.19226 | 0.10986 | 121.7606 | 0.22888 | 0.14648 | 121.9528 | 0.10528 | 121.9437 | 0.14191 | -121.9528 | -121.907 | 121.7514 | 0.1831 | 0.21973 | 0.16479
1907.5625 | 122.049 | -0.16937 | 121.7834 | -0.012131 | 0.0022602 | 0.0577 | 0.051947 | 0.0014397 | -0.0087756 | -0.0008866 | -0.0023192 | 0.029367 | 0.04178 | 0.0082203 | 0.014684 | 0.0261 | -0.0023435 | 0.091553 | 121.7285 | -0.13275 | 121.6873 | 0.050354 | -0.10986 | -0.050354 | 0.091553 | -0.041199 | -0.086975 | 0.045776 | 0.12817 | 0.11902 | 0.11902 | 0.036622 | -0.054931 | -0.09613 | 0.21973 | 0.11902 | 0.05951 | 0.082397 | 0.022888 | 0.082398 | -121.8246 | -121.7377 | 0.29755 | 0.28839 | 0.28839 | 0.20599 | 0.20599 | 0.18311 | 121.8201 | 0.21515 | 0.13275 | 121.8613 | 0.045776 | 121.8979 | 0.12817 | -121.9162 | -121.8704 | 121.8567 | 0.21515 | 0.26093 | 0.26093
1909.25 | 122.0718 | -0.16937 | 121.7789 | -0.01976 | -0.00030342 | 0.054282 | 0.050238 | -0.0019781 | -0.008562 | -0.001741 | -0.0084228 | 0.02723 | 0.042849 | 0.01057 | 0.014257 | 0.027809 | -0.0066159 | 0.13733 | 121.7148 | -0.13275 | 121.7102 | 0.10529 | -0.032043 | -0.027466 | 0.09613 | -0.041199 | -0.09613 | 0.027466 | 0.16479 | 0.14191 | 0.11902 | 0.036622 | -0.064087 | -0.068665 | 0.27466 | 0.14191 | 0.13733 | 0.10529 | 0.10071 | 0.073243 | -121.8201 | -121.7514 | 0.33417 | 0.28839 | 0.31128 | 0.21515 | 0.23804 | 0.23804 | 121.843 | 0.26092 | 0.1236 | 121.8475 | 0.054931 | 121.8842 | 0.12817 | -121.9116 | -121.875 | 121.8796 | 0.19684 | 0.3067 | 0.2655
1911.0156 | 121.994 | -0.18768 | 121.8018 | -0.0045011 | 0.0020466 | 0.056631 | 0.053228 | 0.0035761 | -0.0079212 | -0.0036636 | -0.0084228 | 0.031717 | 0.042208 | 0.0071521 | 0.01618 | 0.024605 | -0.0017027 | 0.15564 | 121.7697 | -0.1831 | 121.6003 | -0.045776 | -0.16479 | -0.14648 | -0.004578 | -0.022888 | -0.11902 | -0.013733 | 0.073242 | 0.045776 | 0.073242 | 0.004578 | -0.032044 | -0.20142 | 0.14191 | 0.041199 | 0.022888 | 0.036621 | 0.01831 | 0.068664 | -121.8246 | -121.8155 | 0.26092 | 0.26092 | 0.23346 | 0.19226 | 0.16479 | 0.13733 | 121.7834 | 0.19226 | 0.10529 | 121.9528 | 0.096131 | 121.9574 | 0.16479 | -121.9849 | -121.9208 | 121.788 | 0.17395 | 0.34332 | 0.1831
1912.7188 | 121.9574 | -0.19684 | 121.7972 | -0.0045011 | 0.0056782 | 0.055777 | 0.053228 | 0.00037174 | -0.0074938 | -0.0038772 | -0.0084228 | 0.029794 | 0.042635 | 0.0035205 | 0.015966 | 0.024178 | 0.00064735 | 0.073242 | 121.8018 | -0.16937 | 121.5637 | -0.1236 | -0.24719 | -0.19684 | -0.086975 | -0.013733 | -0.14648 | -0.073242 | 0 | -0.022888 | 0.013733 | 0.027465 | 0.004578 | -0.23346 | 0.073242 | 0 | -0.050354 | -0.027465 | -0.077819 | 0.050354 | -121.8109 | -121.8704 | 0.19684 | 0.21057 | 0.17395 | 0.16022 | 0.1236 | 0.045777 | 121.7331 | 0.14648 | 0.073242 | 121.9711 | 0.13275 | 121.9986 | 0.18311 | -121.9666 | -121.9437 | 121.7606 | 0.1236 | 0.27008 | 0.10986
1914.4844 | 122.0078 | -0.16937 | 121.8018 | -0.01976 | 0.0037556 | 0.057486 | 0.053656 | 0.0018671 | -0.008562 | -0.0028092 | -0.014526 | 0.028726 | 0.044558 | 0.0090747 | 0.015539 | 0.024819 | 0.00064735 | 0.054932 | 121.8018 | -0.17853 | 121.5591 | -0.073242 | -0.20142 | -0.17395 | -0.027466 | -0.022888 | -0.12817 | -0.004578 | 0.059509 | 0.036621 | 0.073242 | -0.009155 | 0 | -0.24262 | 0.096131 | -0.004577 | -0.032043 | 0.004578 | -0.022888 | 0.041199 | -121.8246 | -121.8063 | 0.22888 | 0.24261 | 0.20599 | 0.20142 | 0.1648 | 0.10529 | 121.7377 | 0.18768 | 0.1236 | 121.9803 | 0.10529 | 121.9711 | 0.14649 | -121.9803 | -121.9299 | 121.7285 | 0.16479 | 0.22431 | 0.14191
1916.2656 | 121.9757 | -0.20599 | 121.7926 | -0.0045011 | 0.0033282 | 0.056418 | 0.054937 | 0.0078485 | -0.0083484 | -0.0049454 | -0.0084228 | 0.028726 | 0.040926 | 0.014629 | 0.014471 | 0.025246 | -0.0044797 | 0.15564 | 121.7606 | -0.17853 | 121.6095 | -0.022888 | -0.15564 | -0.14648 | -0.027466 | -0.022888 | -0.13275 | -0.018311 | 0.068665 | 0.050354 | 0.059509 | 0.027466 | -0.032044 | -0.18311 | 0.18311 | 0.05951 | 0.050354 | 0.032044 | 0.022888 | 0.073243 | -121.8155 | -121.8109 | 0.27466 | 0.2655 | 0.25635 | 0.19226 | 0.18311 | 0.15564 | 121.788 | 0.20142 | 0.11444 | 121.9391 | 0.10986 | 121.9666 | 0.18311 | -121.9711 | -121.9254 | 121.8155 | 0.18768 | 0.36163 | 0.17853
1918.0312 | 121.9345 | -0.21973 | 121.8246 | -0.0045011 | 0.00076478 | 0.05535 | 0.052588 | -0.00069646 | -0.00963 | -0.0019546 | 0.00073235 | 0.029794 | 0.042635 | 0.0039477 | 0.014471 | 0.025887 | 0.00086095 | 0.082397 | 121.7743 | -0.17853 | 121.5408 | -0.082397 | -0.18768 | -0.16479 | -0.091553 | -0.027466 | -0.15106 | -0.10529 | -0.004578 | 0.004578 | 0.022888 | 0.041199 | -0.050354 | -0.28381 | 0.13733 | 0.054932 | 0.032044 | 0.013733 | -0.009155 | 0.068665 | -121.8521 | -121.9299 | 0.21515 | 0.24261 | 0.22431 | 0.17395 | 0.15564 | 0.096131 | 121.7194 | 0.14648 | 0.045776 | 121.9528 | 0.1236 | 121.994 | 0.19226 | -122.0032 | -121.9757 | 121.7606 | 0.11444 | 0.30212 | 0.12817
1919.7344 | 121.9757 | -0.20142 | 121.788 | -0.02739 | 0.0039692 | 0.057486 | 0.05451 | 0.00037174 | -0.0083484 | -0.0025956 | -0.0084228 | 0.029367 | 0.041567 | 0.011852 | 0.015752 | 0.027809 | -0.0014891 | 0.059509 | 121.8155 | -0.17395 | 121.55 | -0.082397 | -0.21057 | -0.18768 | -0.050354 | -0.018311 | -0.13733 | -0.032043 | 0.022888 | 0 | 0.045776 | 0.027466 | 0.027466 | -0.23804 | 0.11902 | 0.013733 | -0.009155 | -0.013733 | -0.036621 | 0.064087 | -121.8063 | -121.8201 | 0.2243 | 0.24719 | 0.20142 | 0.18311 | 0.13733 | 0.091553 | 121.7239 | 0.16022 | 0.10529 | 121.9894 | 0.11902 | 122.0169 | 0.18311 | -121.962 | -121.9254 | 121.7514 | 0.16937 | 0.26093 | 0.15106
1921.5 | 121.9437 | -0.21057 | 121.7972 | -0.0045011 | -0.00073062 | 0.055777 | 0.050665 | -0.0034735 | -0.0077074 | -3.1996e-05 | -0.005371 | 0.027444 | 0.043062 | 0.0071521 | 0.01618 | 0.027596 | -0.00042085 | 0.11444 | 121.7651 | -0.15564 | 121.5683 | -0.045776 | -0.16022 | -0.14191 | -0.068665 | -0.013733 | -0.14191 | -0.082397 | 0.022888 | 0.027466 | 0.013733 | 0.054931 | -0.032043 | -0.22888 | 0.1648 | 0.068664 | 0.050354 | 0.013733 | -0.004577 | 0.068664 | -121.8109 | -121.8796 | 0.23346 | 0.2243 | 0.23804 | 0.15564 | 0.16937 | 0.10986 | 121.7239 | 0.16479 | 0.05951 | 121.9208 | 0.12817 | 121.9757 | 0.19684 | -121.9528 | -121.9391 | 121.7789 | 0.12817 | 0.32501 | 0.14191
1923.2656 | 122.0535 | -0.15564 | 121.756 | -0.01976 | 0.00097838 | 0.054709 | 0.048956 | -5.5462e-05 | -0.008562 | 0.0006088 | -0.005371 | 0.029153 | 0.043276 | 0.010784 | 0.012548 | 0.027169 | -0.0031979 | 0.07782 | 121.7422 | -0.13733 | 121.6599 | 0.041199 | -0.059509 | -0.041199 | 0.054932 | -0.050354 | -0.10071 | 0.041199 | 0.15106 | 0.14191 | 0.13275 | 0.018311 | -0.013732 | -0.09613 | 0.19684 | 0.11444 | 0.096131 | 0.09613 | 0.07782 | 0.054932 | -121.8063 | -121.7148 | 0.3067 | 0.28839 | 0.29755 | 0.23346 | 0.24262 | 0.17853 | 121.7972 | 0.25177 | 0.14191 | 121.8796 | 0.050354 | 121.8979 | 0.10529 | -121.8933 | -121.8567 | 121.8155 | 0.19684 | 0.23346 | 0.21057
1924.9688 | 121.9711 | -0.20142 | 121.8201 | -0.01976 | 0.0041828 | 0.054068 | 0.053869 | -0.00048286 | -0.006853 | -0.0032364 | -0.0023192 | 0.030862 | 0.044771 | 0.012493 | 0.016393 | 0.024819 | -0.00020725 | 0.16479 | 121.8109 | -0.15106 | 121.637 | -0.009155 | -0.16479 | -0.11902 | -0.004578 | -0.009155 | -0.11444 | -0.041199 | 0.036621 | 0.018311 | 0.045776 | 0.050354 | -0.009155 | -0.18311 | 0.19226 | 0.082397 | 0.036621 | 0.032043 | -0.013733 | 0.086975 | -121.8292 | -121.8613 | 0.23804 | 0.24719 | 0.21973 | 0.16022 | 0.13275 | 0.14191 | 121.788 | 0.15106 | 0.073242 | 121.962 | 0.10529 | 122.0123 | 0.19226 | -121.9711 | -121.9345 | 121.8384 | 0.16022 | 0.36621 | 0.19684
1926.7344 | 121.9757 | -0.17395 | 121.8292 | -0.012131 | 0.0039692 | 0.055777 | 0.052588 | 0.00058534 | -0.0070666 | 0.0008224 | -0.005371 | 0.031289 | 0.043062 | 0.011211 | 0.017461 | 0.024819 | -0.0017027 | 0.16022 | 121.8018 | -0.15106 | 121.6141 | -0.032043 | -0.13733 | -0.1236 | -0.013733 | -0.009155 | -0.1236 | -0.032043 | 0.068665 | 0.027466 | 0.050354 | 0.022888 | -0.027466 | -0.21515 | 0.14191 | 0.050354 | 0.036621 | 0.027466 | 0.013733 | 0.050354 | -121.8384 | -121.8613 | 0.24261 | 0.2243 | 0.20142 | 0.17395 | 0.15106 | 0.11902 | 121.7651 | 0.19226 | 0.091553 | 121.9528 | 0.11444 | 121.9757 | 0.16479 | -121.9803 | -121.9528 | 121.788 | 0.14191 | 0.33417 | 0.16022
1928.4844 | 121.9391 | -0.20142 | 121.8384 | -0.0045011 | 0.0031146 | 0.056418 | 0.053442 | -0.0011237 | -0.011553 | -0.002382 | -0.005371 | 0.030435 | 0.043276 | 0.012706 | 0.016821 | 0.026314 | 0.00086095 | 0.10529 | 121.8109 | -0.14648 | 121.5683 | -0.036621 | -0.15106 | -0.15564 | -0.064087 | -0.018311 | -0.10986 | -0.068665 | 0.036621 | 0.013733 | 0 | 0.054932 | -0.027466 | -0.27008 | 0.1648 | 0.045776 | 0.050354 | -0.009156 | -0.004578 | 0.091553 | -121.8567 | -121.907 | 0.23804 | 0.20142 | 0.21515 | 0.10986 | 0.1236 | 0.10986 | 121.7148 | 0.14648 | 0.041198 | 121.9574 | 0.091552 | 122.0123 | 0.18311 | -121.9849 | -121.9482 | 121.7697 | 0.13275 | 0.3067 | 0.13733
1930.1875 | 121.9116 | -0.1831 | 121.8475 | -0.0045011 | 0.0052508 | 0.057486 | 0.053015 | 0.0010125 | -0.0070666 | -0.0015274 | -0.005371 | 0.02958 | 0.043062 | 0.0054431 | 0.01618 | 0.025673 | -0.0021299 | 0.082397 | 121.8018 | -0.16022 | 121.5683 | -0.09613 | -0.21973 | -0.1831 | -0.10071 | -0.009155 | -0.09613 | -0.10071 | -0.022888 | -0.045776 | 0.013733 | 0.022888 | -0.045776 | -0.27924 | 0.086975 | 0 | -0.036622 | -0.022888 | -0.05951 | 0.086975 | -121.8567 | -121.9482 | 0.16022 | 0.19684 | 0.13733 | 0.10986 | 0.050354 | 0.064087 | 121.7285 | 0.073242 | -0.004578 | 121.962 | 0.086975 | 121.9849 | 0.17395 | -122.0078 | -121.9437 | 121.7514 | 0.082397 | 0.2655 | 0.082397
1931.9531 | 121.9711 | -0.1831 | 121.8338 | -0.012131 | 0.00461 | 0.058127 | 0.053869 | 0.00079894 | -0.0070666 | -0.002382 | -0.0084228 | 0.02958 | 0.04413 | 0.010143 | 0.017889 | 0.024819 | -0.0040525 | 0.15106 | 121.8201 | -0.15564 | 121.6461 | -0.018311 | -0.14191 | -0.1236 | -0.009155 | -0.027466 | -0.12817 | -0.032043 | 0.059509 | 0.004578 | 0.041199 | 0.027465 | -0.013733 | -0.18768 | 0.16479 | 0.059509 | 0.041198 | 0.032044 | 0.013733 | 0.054931 | -121.8613 | -121.8658 | 0.24261 | 0.2243 | 0.18768 | 0.16937 | 0.13275 | 0.13733 | 121.8018 | 0.18768 | 0.096131 | 121.9757 | 0.10071 | 122.0032 | 0.15564 | -121.9894 | -121.962 | 121.8292 | 0.15106 | 0.33417 | 0.17395
1933.6719 | 121.9391 | -0.19226 | 121.8384 | -0.0045011 | -0.0011578 | 0.054709 | 0.050879 | -0.0028327 | -0.008562 | -0.002382 | 0.00073235 | 0.028939 | 0.042849 | 0.0095019 | 0.015325 | 0.025673 | -0.0029843 | 0.11444 | 121.7972 | -0.13733 | 121.6095 | -0.022888 | -0.13275 | -0.11902 | -0.054932 | -0.018311 | -0.10529 | -0.091553 | 0.027466 | 0.004578 | 0.004578 | 0.054932 | -0.041199 | -0.22888 | 0.16937 | 0.073242 | 0.05951 | 0.01831 | 0.004578 | 0.086975 | -121.8567 | -121.9299 | 0.21973 | 0.19684 | 0.19684 | 0.10986 | 0.10986 | 0.11444 | 121.7468 | 0.13275 | 0.013733 | 121.9345 | 0.086975 | 121.9894 | 0.17395 | -121.9757 | -121.9437 | 121.8018 | 0.10071 | 0.3067 | 0.13733
1935.4375 | 121.9391 | -0.17395 | 121.8292 | -0.012131 | 0.002901 | 0.054495 | 0.054937 | 0.0014397 | -0.0092028 | -3.1996e-05 | -0.005371 | 0.030008 | 0.044985 | 0.011211 | 0.019384 | 0.024605 | -0.00063445 | 0.13733 | 121.8246 | -0.14191 | 121.6095 | -0.022888 | -0.16479 | -0.13275 | -0.027466 | -0.018311 | -0.086975 | -0.073242 | 0.022888 | -0.013733 | 0.032043 | 0.032043 | -0.004578 | -0.21973 | 0.15106 | 0.041199 | 0.009155 | 0.009156 | -0.022888 | 0.086975 | -121.8475 | -121.9025 | 0.19684 | 0.20599 | 0.16022 | 0.11902 | 0.073242 | 0.11902 | 121.7514 | 0.10986 | 0.013733 | 121.9666 | 0.068664 | 121.9986 | 0.15564 | -121.9711 | -121.9162 | 121.7834 | 0.10071 | 0.31128 | 0.14648
1937.2031 | 121.9894 | -0.16479 | 121.8292 | -0.01976 | 0.0037556 | 0.055777 | 0.052588 | 0.0020807 | -0.0092028 | -0.0025956 | -0.005371 | 0.030648 | 0.043703 | 0.015056 | 0.017034 | 0.026955 | -0.0038389 | 0.064087 | 121.8292 | -0.14648 | 121.5958 | -0.050354 | -0.17853 | -0.15106 | -0.022888 | -0.027466 | -0.10529 | -0.050354 | 0.045776 | 0.032043 | 0.059509 | 0.018311 | 0 | -0.23346 | 0.11444 | 0.013733 | -0.013733 | -0.004578 | -0.032044 | 0.059509 | -121.8567 | -121.8796 | 0.21057 | 0.2243 | 0.19684 | 0.16479 | 0.13733 | 0.09613 | 121.7422 | 0.15106 | 0.054932 | 121.9757 | 0.07782 | 121.994 | 0.13733 | -121.9757 | -121.9345 | 121.7606 | 0.11444 | 0.22888 | 0.14191
1938.9062 | 122.049 | -0.13733 | 121.8201 | -0.012131 | 0.0033282 | 0.056631 | 0.049383 | -5.5462e-05 | -0.0081348 | -0.0045182 | -0.005371 | 0.028299 | 0.044344 | -0.00032473 | 0.01618 | 0.028237 | -0.0049069 | 0.050354 | 121.7697 | -0.10986 | 121.6415 | 0.027466 | -0.10071 | -0.059509 | 0.004578 | -0.054932 | -0.091553 | -0.013733 | 0.09613 | 0.10529 | 0.09613 | 0.027466 | -0.050354 | -0.17853 | 0.16479 | 0.07782 | 0.036621 | 0.050354 | 0.009155 | 0.045776 | -121.875 | -121.8338 | 0.23346 | 0.23346 | 0.24262 | 0.18768 | 0.19684 | 0.13733 | 121.7514 | 0.18768 | 0.07782 | 121.8796 | 0.036621 | 121.907 | 0.082397 | -121.9299 | -121.9116 | 121.7789 | 0.1236 | 0.18768 | 0.14191
1940.6719 | 121.9528 | -0.16937 | 121.8704 | -0.0045011 | 0.0061054 | 0.057272 | 0.054083 | 0.0018671 | -0.0064258 | -0.0008866 | -0.0023192 | 0.030648 | 0.042635 | 0.0050159 | 0.015325 | 0.025887 | -0.0038389 | 0.07782 | 121.8201 | -0.16022 | 121.582 | -0.09613 | -0.21057 | -0.17395 | -0.059509 | -0.013733 | -0.11444 | -0.091553 | 0.004578 | -0.027466 | 0.018311 | 0.009156 | -0.050354 | -0.28839 | 0.073243 | -0.004577 | -0.041198 | -0.013733 | -0.050354 | 0.054932 | -121.8842 | -121.962 | 0.17395 | 0.18768 | 0.14191 | 0.13275 | 0.086975 | 0.064087 | 121.7422 | 0.11902 | 0.022888 | 121.9803 | 0.10071 | 121.9894 | 0.15564 | -122.0306 | -121.9849 | 121.7514 | 0.07782 | 0.24719 | 0.10986
1942.375 | 121.994 | -0.16022 | 121.8384 | -0.0045011 | 0.00033758 | 0.054495 | 0.05216 | 0.0022943 | -0.0087756 | -0.0021682 | -0.0023192 | 0.026376 | 0.044558 | 0.0045887 | 0.014684 | 0.025032 | -0.0014891 | 0.14191 | 121.7606 | -0.11902 | 121.6873 | 0.064087 | -0.068665 | -0.027466 | 0.032043 | -0.032043 | -0.086975 | -0.032043 | 0.10071 | 0.082397 | 0.059509 | 0.041198 | -0.07782 | -0.15106 | 0.2243 | 0.13275 | 0.091552 | 0.091553 | 0.050354 | 0.073242 | -121.8704 | -121.8704 | 0.26093 | 0.21973 | 0.24261 | 0.14648 | 0.16937 | 0.18311 | 121.8063 | 0.18768 | 0.054932 | 121.8796 | 0.054932 | 121.9208 | 0.12817 | -121.9574 | -121.9254 | 121.8475 | 0.12817 | 0.30212 | 0.19226
1944.125 | 121.9437 | -0.18768 | 121.8658 | -0.01976 | 0.00033758 | 0.053641 | 0.054297 | 0.00015814 | -0.010057 | -0.0047318 | 0.0037842 | 0.030221 | 0.044771 | 0.0092883 | 0.015752 | 0.024178 | -0.0010617 | 0.086975 | 121.7972 | -0.13733 | 121.5866 | -0.050354 | -0.15564 | -0.14648 | -0.07782 | -0.004578 | -0.10986 | -0.09613 | 0.009155 | 0.004578 | -0.004578 | 0.050354 | -0.068665 | -0.27924 | 0.13733 | 0.041199 | 0.032043 | -0.009155 | -0.018311 | 0.07782 | -121.8704 | -121.962 | 0.19684 | 0.1831 | 0.19226 | 0.10529 | 0.11444 | 0.086975 | 121.7239 | 0.11902 | 0.013733 | 121.9345 | 0.10529 | 121.9849 | 0.1831 | -122.0032 | -121.9757 | 121.7743 | 0.091553 | 0.27466 | 0.10986
1945.9062 | 122.0078 | -0.16479 | 121.8475 | -0.01976 | 0.001833 | 0.055563 | 0.05152 | -0.0015509 | -0.0081348 | -0.0043046 | -0.0023192 | 0.028939 | 0.042635 | 0.0045887 | 0.014684 | 0.025032 | -0.00084805 | 0.050354 | 121.788 | -0.11902 | 121.6553 | 0.022888 | -0.10986 | -0.07782 | -0.013733 | -0.032043 | -0.091553 | -0.027466 | 0.064087 | 0.064087 | 0.073242 | 0.045776 | -0.059509 | -0.19226 | 0.18768 | 0.086975 | 0.054932 | 0.041199 | 0.009156 | 0.073242 | -121.8796 | -121.875 | 0.22888 | 0.23804 | 0.22888 | 0.16479 | 0.15564 | 0.14191 | 121.7743 | 0.15564 | 0.064087 | 121.907 | 0.05951 | 121.9528 | 0.13275 | -121.9666 | -121.9391 | 121.8201 | 0.13733 | 0.21515 | 0.15106
1947.5938 | 121.9528 | -0.16937 | 121.8704 | -0.0045011 | 0.00076478 | 0.054495 | 0.053015 | -0.0028327 | -0.00963 | -0.0032364 | -0.005371 | 0.02958 | 0.043062 | 0.0090747 | 0.016607 | 0.025032 | -0.0021299 | 0.11444 | 121.8384 | -0.15106 | 121.6003 | -0.059509 | -0.16937 | -0.13275 | -0.086975 | 0 | -0.10986 | -0.091553 | 0.004578 | -0.004578 | 0.022888 | 0.018311 | -0.032043 | -0.27008 | 0.10986 | 0.036622 | 0 | 0.018311 | -0.018311 | 0.05951 | -121.8704 | -121.962 | 0.17395 | 0.19226 | 0.16479 | 0.13275 | 0.10529 | 0.091553 | 121.7514 | 0.11444 | 0.01831 | 121.9894 | 0.10986 | 122.0078 | 0.16937 | -122.0215 | -121.9803 | 121.7697 | 0.07782 | 0.28381 | 0.082398
1949.3438 | 122.0352 | -0.14648 | 121.7972 | -0.012131 | 0.0022602 | 0.053854 | 0.052588 | -0.0026191 | -0.0077074 | -0.0015274 | -0.0023192 | 0.028085 | 0.044558 | 0.0054431 | 0.014898 | 0.025246 | -0.0040525 | 0.045776 | 121.788 | -0.10986 | 121.6461 | 0.004578 | -0.10986 | -0.068665 | -0.009155 | -0.041199 | -0.064087 | -0.027466 | 0.091553 | 0.07782 | 0.068665 | 0.036621 | -0.009155 | -0.15106 | 0.15106 | 0.077819 | 0.036621 | 0.041198 | 0 | 0.082397 | -121.8384 | -121.8246 | 0.23804 | 0.21515 | 0.2243 | 0.13275 | 0.14191 | 0.11444 | 121.756 | 0.15564 | 0.036621 | 121.8979 | 0.022888 | 121.9345 | 0.10529 | -121.907 | -121.8613 | 121.7926 | 0.11902 | 0.19226 | 0.13733
1951.1094 | 122.0352 | -0.13733 | 121.8384 | -0.012131 | -0.0011578 | 0.057486 | 0.051092 | -0.00026906 | -0.0089892 | -0.0032364 | -0.0023192 | 0.027444 | 0.042421 | 0.013561 | 0.014043 | 0.026314 | -0.0040525 | 0.14648 | 121.7697 | -0.091553 | 121.7148 | 0.086975 | -0.036621 | -0.018311 | 0.050354 | -0.036621 | -0.073242 | -0.013733 | 0.11902 | 0.09613 | 0.086975 | 0.045776 | -0.068665 | -0.1236 | 0.2243 | 0.11902 | 0.10071 | 0.073242 | 0.054932 | 0.064087 | -121.875 | -121.8521 | 0.25635 | 0.2243 | 0.23346 | 0.16022 | 0.16937 | 0.17853 | 121.8063 | 0.19226 | 0.059509 | 121.8613 | 0.036621 | 121.907 | 0.10071 | -121.9299 | -121.9116 | 121.8521 | 0.1236 | 0.28381 | 0.18768
1952.7969 | 121.962 | -0.14648 | 121.843 | -0.01976 | 0.0039692 | 0.055991 | 0.053869 | -0.00069646 | -0.0077074 | -0.0028092 | -0.005371 | 0.03193 | 0.042849 | 0.0086475 | 0.017889 | 0.0261 | -0.0017027 | 0.16022 | 121.8155 | -0.13275 | 121.6461 | -0.004578 | -0.13733 | -0.10986 | -0.004578 | -0.022888 | -0.064087 | -0.041199 | 0.036621 | 0.013733 | 0.027466 | 0.013733 | -0.027466 | -0.19684 | 0.14191 | 0.036621 | 0.009155 | 0.022888 | -0.004578 | 0.082397 | -121.8658 | -121.8842 | 0.18311 | 0.17395 | 0.16022 | 0.091553 | 0.07782 | 0.12817 | 121.7789 | 0.10071 | 0.022888 | 121.9482 | 0.041199 | 121.962 | 0.1236 | -121.9757 | -121.907 | 121.7926 | 0.10529 | 0.3067 | 0.14191
1954.5469 | 122.0032 | -0.11902 | 121.843 | -0.012131 | 0.0016192 | 0.055777 | 0.050451 | 0.00015814 | -0.0089892 | 0.0006088 | -0.005371 | 0.027658 | 0.042208 | 0.0043751 | 0.016607 | 0.026314 | -0.0019163 | 0.15106 | 121.7972 | -0.082397 | 121.7285 | 0.09613 | -0.009155 | 0.013733 | 0.036621 | -0.054932 | -0.041199 | -0.027466 | 0.11444 | 0.073242 | 0.07782 | 0.036622 | -0.045777 | -0.11444 | 0.21515 | 0.13275 | 0.10986 | 0.09613 | 0.073242 | 0.07782 | -121.8979 | -121.8704 | 0.23346 | 0.19684 | 0.19226 | 0.11902 | 0.11444 | 0.17853 | 121.8109 | 0.15564 | 0.013733 | 121.8796 | -0.013733 | 121.9162 | 0.064087 | -121.9254 | -121.8842 | 121.8475 | 0.091553 | 0.27008 | 0.15564
1956.3281 | 121.9391 | -0.15564 | 121.8567 | -0.01976 | 0.00076478 | 0.053854 | 0.051092 | -0.0017645 | -0.00963 | -0.0004592 | -0.005371 | 0.028512 | 0.044344 | 0.0041615 | 0.01618 | 0.02311 | -0.0078977 | 0.10986 | 121.8292 | -0.10071 | 121.6507 | 0.004578 | -0.09613 | -0.091553 | -0.082397 | -0.009155 | -0.054932 | -0.10986 | 0.018311 | -0.022888 | -0.013733 | 0.054932 | -0.027465 | -0.20599 | 0.16022 | 0.064087 | 0.05951 | 0.009155 | 0.004578 | 0.10071 | -121.8658 | -121.9666 | 0.17395 | 0.14191 | 0.13275 | 0.041199 | 0.032044 | 0.10529 | 121.7514 | 0.073243 | -0.054931 | 121.9299 | 0.045777 | 121.9849 | 0.14649 | -121.9574 | -121.9116 | 121.8063 | 0.045777 | 0.2655 | 0.073243
1958.0781 | 121.9711 | -0.14191 | 121.8842 | -0.0045011 | 0.00012398 | 0.054068 | 0.052801 | 0.0018671 | -0.0089892 | -0.0036636 | -0.0084228 | 0.030008 | 0.046053 | 0.0024525 | 0.014257 | 0.024391 | -0.0061887 | 0.11902 | 121.875 | -0.11444 | 121.637 | -0.027466 | -0.13733 | -0.09613 | -0.091553 | -0.027466 | -0.082397 | -0.09613 | 0.032043 | -0.004578 | 0.022888 | 0.027466 | -0.009155 | -0.24719 | 0.11444 | 0.045777 | 0.004578 | 0.018311 | -0.022888 | 0.05951 | -121.9116 | -121.9803 | 0.17395 | 0.16479 | 0.13733 | 0.10528 | 0.077819 | 0.086975 | 121.7514 | 0.11444 | -0.013733 | 121.9894 | 0.054931 | 122.0169 | 0.11444 | -121.9986 | -121.9666 | 121.7789 | 0.045777 | 0.26093 | 0.050354
1959.7656 | 122.0673 | -0.07782 | 121.8475 | -0.02739 | 0.0052508 | 0.057059 | 0.052801 | -0.0017645 | -0.0070666 | -0.0036636 | -0.0084228 | 0.02958 | 0.042849 | 0.0080067 | 0.01618 | 0.025032 | -0.0029843 | 0.11902 | 121.8201 | -0.059509 | 121.7514 | 0.11444 | -0.027466 | -0.004578 | 0.07782 | -0.068665 | -0.013733 | 0.045776 | 0.15106 | 0.11902 | 0.11444 | 0.018311 | -0.027466 | -0.09613 | 0.19226 | 0.073242 | 0.050354 | 0.054931 | 0.032043 | 0.064087 | -121.9162 | -121.8018 | 0.22888 | 0.19226 | 0.19684 | 0.12817 | 0.13275 | 0.17395 | 121.8109 | 0.16479 | 0.059509 | 121.8796 | -0.054932 | 121.8979 | 0.009155 | -121.907 | -121.8613 | 121.8292 | 0.1236 | 0.19684 | 0.15564
1961.5156 | 122.0215 | -0.11902 | 121.8521 | -0.012131 | 0.002901 | 0.055777 | 0.055151 | -5.5462e-05 | -0.0064258 | -0.0028092 | -0.0084228 | 0.030008 | 0.044558 | 0.012279 | 0.014898 | 0.02546 | -0.0029843 | 0.054932 | 121.8567 | -0.091553 | 121.6507 | -0.013733 | -0.13733 | -0.10071 | -0.045776 | -0.022888 | -0.045776 | -0.018311 | 0.059509 | 0.018311 | 0.064087 | 0.027466 | 0.004577 | -0.20142 | 0.10529 | 0.018311 | -0.01831 | -0.009155 | -0.045776 | 0.073243 | -121.875 | -121.8704 | 0.17853 | 0.18311 | 0.13733 | 0.10986 | 0.064087 | 0.07782 | 121.7422 | 0.10528 | 0.027465 | 121.9482 | 0.022888 | 121.9757 | 0.096131 | -121.9437 | -121.8979 | 121.7697 | 0.10071 | 0.17395 | 0.073243
1963.2656 | 122.0764 | -0.07782 | 121.875 | -0.012131 | 0.0061054 | 0.056631 | 0.052588 | 0.0016535 | -0.0064258 | 0.0003952 | -0.0084228 | 0.028939 | 0.043917 | 0.00052987 | 0.016393 | 0.025887 | -0.0038389 | 0.1236 | 121.843 | -0.050354 | 121.7514 | 0.11444 | -0.041199 | 0.009155 | 0.086975 | -0.050354 | -0.018311 | 0.032043 | 0.15106 | 0.10529 | 0.11902 | 0.027466 | -0.032043 | -0.1236 | 0.19226 | 0.086975 | 0.036621 | 0.059509 | 0.009155 | 0.059509 | -121.9254 | -121.843 | 0.22888 | 0.19684 | 0.18311 | 0.13733 | 0.1236 | 0.16479 | 121.8018 | 0.16937 | 0.050354 | 121.8933 | -0.032043 | 121.9208 | 0.027466 | -121.9254 | -121.8933 | 121.8292 | 0.10986 | 0.20142 | 0.16479
1964.9688 | 121.962 | -0.14648 | 121.9162 | -0.0045011 | 0.0033282 | 0.05535 | 0.051947 | -0.00069646 | -0.010271 | -0.0021682 | -0.0023192 | 0.031503 | 0.045626 | 0.0028797 | 0.015325 | 0.026314 | -0.0036253 | 0.1236 | 121.8338 | -0.09613 | 121.6644 | 0 | -0.10529 | -0.073242 | -0.064087 | -0.022888 | -0.054932 | -0.10529 | 0.027466 | -0.013733 | -0.004578 | 0.050354 | -0.082398 | -0.25177 | 0.14648 | 0.073242 | 0.041198 | 0.022888 | -0.009156 | 0.091552 | -121.9391 | -122.0215 | 0.17395 | 0.14191 | 0.13275 | 0.050354 | 0.041199 | 0.09613 | 121.7606 | 0.082398 | -0.050354 | 121.9299 | 0.032044 | 121.9803 | 0.1236 | -122.0123 | -121.9711 | 121.8109 | 0.041198 | 0.27008 | 0.082397
1966.7344 | 122.0169 | -0.10986 | 121.8475 | -0.012131 | 0.001192 | 0.054068 | 0.052801 | 0.0012261 | -0.0087756 | -0.002382 | -0.0084228 | 0.031289 | 0.041994 | 0.010143 | 0.012975 | 0.025246 | -0.0049069 | 0.059509 | 121.8613 | -0.073242 | 121.701 | 0.050354 | -0.059509 | -0.036621 | 0.013733 | -0.036621 | -0.054932 | -0.045776 | 0.07782 | 0.059509 | 0.064087 | 0.036621 | 0.013733 | -0.14648 | 0.16022 | 0.073242 | 0.050354 | 0.036621 | 0.013733 | 0.054931 | -121.8842 | -121.8933 | 0.18768 | 0.17395 | 0.16937 | 0.11902 | 0.11444 | 0.1236 | 121.7743 | 0.13275 | 0.009156 | 121.9345 | 0.018311 | 121.9711 | 0.073242 | -121.9208 | -121.9025 | 121.8109 | 0.064087 | 0.16937 | 0.1236
1968.4375 | 122.0673 | -0.082397 | 121.843 | -0.012131 | 0.0052508 | 0.054709 | 0.055151 | -0.0019781 | -0.0087756 | -0.0004592 | -0.0023192 | 0.032144 | 0.043276 | 0.0097157 | 0.015966 | 0.025246 | -0.0014891 | 0.11902 | 121.8338 | -0.054932 | 121.7697 | 0.1236 | -0.041199 | 0.018311 | 0.091553 | -0.059509 | -0.022888 | 0.045776 | 0.13733 | 0.11444 | 0.11444 | 0.027465 | -0.009156 | -0.073243 | 0.20599 | 0.10071 | 0.041198 | 0.073243 | 0.013733 | 0.059509 | -121.9025 | -121.7972 | 0.21973 | 0.19684 | 0.19684 | 0.13733 | 0.13733 | 0.17853 | 121.8246 | 0.16022 | 0.068664 | 121.8887 | -0.036621 | 121.9162 | 0.022888 | -121.8979 | -121.8658 | 121.8521 | 0.12817 | 0.20142 | 0.17395
1970.1875 | 122.0581 | -0.10986 | 121.8613 | -0.01976 | 0.0026874 | 0.055777 | 0.053228 | -0.0015509 | -0.0057848 | -0.000673 | -0.0023192 | 0.03193 | 0.044558 | 0.0026661 | 0.016393 | 0.025246 | -0.0044797 | 0.10529 | 121.8475 | -0.050354 | 121.7606 | 0.13275 | -0.013733 | -0.004578 | 0.086975 | -0.064087 | -0.027466 | 0.050354 | 0.13733 | 0.09613 | 0.10529 | 0.059509 | -0.013733 | -0.10071 | 0.24261 | 0.10529 | 0.09613 | 0.045776 | 0.036621 | 0.082397 | -121.9254 | -121.8109 | 0.24719 | 0.21515 | 0.20599 | 0.13275 | 0.1236 | 0.18311 | 121.8109 | 0.16479 | 0.07782 | 121.8979 | -0.036621 | 121.9574 | 0.045776 | -121.9116 | -121.8887 | 121.8704 | 0.16022 | 0.21515 | 0.19684
1971.9531 | 121.9482 | -0.13733 | 121.907 | 0.0031279 | 0.00055118 | 0.052359 | 0.050024 | -0.00069646 | -0.010698 | -0.002382 | -0.005371 | 0.031076 | 0.04413 | 0.0067249 | 0.015325 | 0.024391 | -0.0021299 | 0.13275 | 121.8475 | -0.091553 | 121.6599 | 0.018311 | -0.09613 | -0.064087 | -0.045776 | -0.027466 | -0.064087 | -0.10529 | 0.018311 | 0.013733 | 0.013733 | 0.045776 | -0.059509 | -0.24719 | 0.15564 | 0.073242 | 0.041199 | 0.027466 | -0.004577 | 0.073242 | -121.9345 | -122.0123 | 0.15564 | 0.15106 | 0.15106 | 0.07782 | 0.07782 | 0.10986 | 121.7514 | 0.082398 | -0.041199 | 121.9391 | 0.036621 | 121.9849 | 0.10986 | -121.9986 | -121.9711 | 121.7972 | 0.032043 | 0.27008 | 0.091553
1973.6562 | 122.0673 | -0.10529 | 121.875 | -0.012131 | 0.0014056 | 0.055136 | 0.052374 | 0.0022943 | -0.006853 | -0.002382 | -0.005371 | 0.031289 | 0.04114 | 0.0026661 | 0.01383 | 0.024819 | -0.0019163 | 0.068665 | 121.8338 | -0.082397 | 121.7285 | 0.07782 | -0.018311 | 0.018311 | 0.064087 | -0.041199 | -0.045776 | 0.022888 | 0.14648 | 0.13275 | 0.11902 | 0.022889 | -0.041199 | -0.14648 | 0.18311 | 0.1236 | 0.086975 | 0.10071 | 0.064086 | 0.05951 | -121.9162 | -121.8521 | 0.25177 | 0.22431 | 0.23804 | 0.16479 | 0.17853 | 0.16022 | 121.8109 | 0.19226 | 0.068664 | 121.9162 | 0.004577 | 121.9391 | 0.064087 | -121.9574 | -121.9208 | 121.8338 | 0.12817 | 0.17395 | 0.16937
1975.4062 | 122.0673 | -0.086975 | 121.8521 | -0.012131 | 0.0035418 | 0.054709 | 0.052588 | 0.0027215 | -0.008562 | -0.00345 | -0.0084228 | 0.032785 | 0.042635 | -0.00032473 | 0.014043 | 0.023537 | -0.0021299 | 0.11444 | 121.843 | -0.073242 | 121.7697 | 0.11444 | -0.022888 | 0.013733 | 0.086975 | -0.064087 | -0.036621 | 0.032043 | 0.13275 | 0.10071 | 0.11902 | 0.013733 | -0.009155 | -0.082398 | 0.20142 | 0.10071 | 0.064087 | 0.086975 | 0.050354 | 0.050354 | -121.9162 | -121.8201 | 0.21973 | 0.20599 | 0.18768 | 0.15564 | 0.13733 | 0.18768 | 121.843 | 0.16937 | 0.068664 | 121.9162 | -0.027466 | 121.9299 | 0.022888 | -121.9254 | -121.8887 | 121.8567 | 0.11902 | 0.20142 | 0.17395
1977.0938 | 121.9345 | -0.13733 | 121.8887 | -0.0045011 | 0.00097838 | 0.054709 | 0.051947 | 0.00037174 | -0.0077074 | -0.0021682 | -0.0084228 | 0.032998 | 0.043703 | 0.0082203 | 0.016607 | 0.022683 | -0.0014891 | 0.11902 | 121.8613 | -0.082397 | 121.6736 | 0.027466 | -0.09613 | -0.07782 | -0.059509 | -0.018311 | -0.054932 | -0.10529 | 0.004578 | 0.009155 | 0 | 0.054932 | -0.027466 | -0.21515 | 0.16479 | 0.059509 | 0.041199 | 0.004577 | -0.013733 | 0.082397 | -121.907 | -121.994 | 0.14191 | 0.13733 | 0.14648 | 0.054932 | 0.064087 | 0.10986 | 121.756 | 0.05951 | -0.050354 | 121.9437 | 0.036621 | 121.9986 | 0.11902 | -121.9711 | -121.9437 | 121.8109 | 0.032043 | 0.25635 | 0.07782
1978.8438 | 122.0535 | -0.086975 | 121.8704 | -0.012131 | 0.00097838 | 0.053 | 0.050665 | -0.0017645 | -0.010698 | -0.0011002 | -0.0023192 | 0.030648 | 0.042635 | 0.0045887 | 0.017461 | 0.024391 | -0.0029843 | 0.15106 | 121.8063 | -0.054932 | 121.7697 | 0.1236 | 0.004578 | 0.041199 | 0.064087 | -0.059509 | -0.036621 | 0.018311 | 0.14648 | 0.12817 | 0.11444 | 0.032043 | -0.064087 | -0.10071 | 0.21057 | 0.12817 | 0.091553 | 0.096131 | 0.05951 | 0.050354 | -121.9299 | -121.8521 | 0.23346 | 0.20142 | 0.21515 | 0.15106 | 0.1648 | 0.17853 | 121.8246 | 0.18311 | 0.054932 | 121.8613 | -0.022888 | 121.8933 | 0.027466 | -121.9254 | -121.907 | 121.8567 | 0.10529 | 0.23804 | 0.15106
1980.5938 | 121.9528 | -0.13733 | 121.9208 | -0.0045011 | 0.0022602 | 0.053427 | 0.053869 | 0.00079894 | -0.010912 | -0.0030228 | -0.005371 | 0.033639 | 0.045198 | 0.012065 | 0.016607 | 0.02546 | -0.00063445 | 0.14191 | 121.8338 | -0.10071 | 121.6873 | 0.018311 | -0.091553 | -0.082397 | -0.041199 | -0.027466 | -0.054932 | -0.09613 | 0.032043 | 0 | 0.018311 | 0.036621 | -0.086975 | -0.23346 | 0.15564 | 0.054932 | 0.045776 | 0.018311 | 0.009155 | 0.082397 | -121.9482 | -122.0169 | 0.16937 | 0.15564 | 0.13733 | 0.073243 | 0.054932 | 0.11902 | 121.788 | 0.086975 | -0.041198 | 121.9345 | 0.027466 | 121.9711 | 0.10986 | -122.0215 | -121.9757 | 121.8246 | 0.041199 | 0.27924 | 0.09613
1982.3594 | 121.962 | -0.1236 | 121.907 | -0.0045011 | 0.0050372 | 0.054922 | 0.055365 | 0.0010125 | -0.0074938 | -0.0015274 | -0.0023192 | 0.034066 | 0.043489 | 0.012493 | 0.015112 | 0.025032 | -0.0040525 | 0.073242 | 121.8887 | -0.10071 | 121.6278 | -0.045776 | -0.16022 | -0.11902 | -0.082397 | -0.013733 | -0.059509 | -0.059509 | -0.004578 | -0.027466 | 0.022888 | 0.022888 | -0.01831 | -0.27923 | 0.07782 | 0.004577 | -0.036621 | -0.018311 | -0.059509 | 0.064087 | -121.9208 | -121.9666 | 0.11902 | 0.14648 | 0.09613 | 0.082397 | 0.032043 | 0.054932 | 121.7285 | 0.054931 | 0 | 121.9894 | 0.045776 | 122.0123 | 0.10986 | -122.0078 | -121.9666 | 121.7514 | 0.064087 | 0.19684 | 0.041199
1984.125 | 121.9574 | -0.11902 | 121.9116 | -0.012131 | 0.00461 | 0.056418 | 0.056006 | -0.0045417 | -0.0083484 | -0.0038772 | -0.0084228 | 0.03428 | 0.043703 | 0.010143 | 0.017461 | 0.027596 | 0.00021995 | 0.10071 | 121.9116 | -0.10986 | 121.637 | -0.045776 | -0.16479 | -0.12817 | -0.07782 | -0.013733 | -0.064087 | -0.082397 | -0.013733 | -0.032043 | 0.018311 | 0.009156 | 0 | -0.27466 | 0.073243 | -0.009155 | -0.045776 | -0.018311 | -0.054932 | 0.054932 | -121.9254 | -121.994 | 0.10529 | 0.13733 | 0.086976 | 0.082398 | 0.032044 | 0.064087 | 121.7468 | 0.050354 | -0.01831 | 122.0215 | 0.050354 | 122.0306 | 0.10529 | -122.0215 | -121.9757 | 121.756 | 0.036622 | 0.21973 | 0.041199
1985.9062 | 121.962 | -0.1236 | 121.9437 | -0.0045011 | 0.0022602 | 0.054495 | 0.054083 | -0.00091006 | -0.0083484 | -0.0015274 | -0.005371 | 0.032785 | 0.046267 | 0.0026661 | 0.015325 | 0.025673 | -0.0029843 | 0.10529 | 121.8613 | -0.10071 | 121.6507 | -0.018311 | -0.11444 | -0.10529 | -0.09613 | -0.009155 | -0.07782 | -0.086975 | 0.009155 | 0.004578 | 0.022888 | 0.022888 | -0.082398 | -0.29297 | 0.10528 | 0.01831 | 0.009155 | -0.004578 | -0.013733 | 0.045776 | -121.9528 | -122.0306 | 0.13275 | 0.14648 | 0.12817 | 0.10071 | 0.082398 | 0.082397 | 121.7514 | 0.086975 | -0.009155 | 121.962 | 0.068665 | 121.9849 | 0.11444 | -122.0444 | -122.0215 | 121.7743 | 0.036621 | 0.22888 | 0.027466
1987.6094 | 121.9391 | -0.11902 | 121.8887 | -0.012131 | 0.0065326 | 0.056418 | 0.053442 | 0.0016535 | -0.0094164 | -0.0043046 | -0.0023192 | 0.032571 | 0.043276 | 0.0065113 | 0.017675 | 0.025032 | -0.0044797 | 0.14191 | 121.8933 | -0.10529 | 121.6736 | 0.009155 | -0.13275 | -0.11902 | -0.050354 | -0.032043 | -0.045776 | -0.059509 | 0.022888 | -0.036621 | 0.009155 | 0.013733 | 0.004578 | -0.21515 | 0.12817 | 0 | -0.013732 | -0.013733 | -0.027465 | 0.073243 | -121.9208 | -121.9482 | 0.14191 | 0.12817 | 0.082398 | 0.054931 | 0.009155 | 0.11444 | 121.7789 | 0.068664 | -0.013733 | 121.9986 | 0.013733 | 122.0123 | 0.086976 | -121.994 | -121.9345 | 121.7926 | 0.05951 | 0.26093 | 0.068665
1989.3594 | 122.0901 | -0.09613 | 121.8704 | -0.01976 | 0.001833 | 0.054495 | 0.05152 | 0.00015814 | -0.0083484 | -0.0025956 | -0.0023192 | 0.02958 | 0.042849 | 0.0056567 | 0.017248 | 0.02546 | -0.0029843 | 0.14648 | 121.8201 | -0.073242 | 121.7651 | 0.15564 | 0.027466 | 0.032043 | 0.086975 | -0.059509 | -0.022888 | 0.022888 | 0.15564 | 0.14648 | 0.1236 | 0.022888 | -0.050354 | -0.10529 | 0.25177 | 0.12817 | 0.1236 | 0.10529 | 0.10071 | 0.073242 | -121.9299 | -121.8475 | 0.25177 | 0.21973 | 0.24261 | 0.14648 | 0.16937 | 0.22888 | 121.8384 | 0.17853 | 0.045776 | 121.8933 | -0.036621 | 121.9162 | 0.036621 | -121.9437 | -121.8933 | 121.8613 | 0.11902 | 0.24261 | 0.1831
1991.0625 | 122.0673 | -0.07782 | 121.8475 | -0.012131 | 0.0035418 | 0.056845 | 0.053015 | -0.00048286 | -0.0079212 | -0.0049454 | -0.0023192 | 0.031289 | 0.045839 | 0.0058703 | 0.016607 | 0.026528 | -0.0036253 | 0.10986 | 121.8567 | -0.050354 | 121.7789 | 0.13733 | -0.022888 | 0.032043 | 0.091553 | -0.054932 | -0.022888 | 0.045776 | 0.14648 | 0.11444 | 0.1236 | 0.027466 | 0.009155 | -0.068664 | 0.21515 | 0.10986 | 0.054932 | 0.082397 | 0.027466 | 0.054932 | -121.9025 | -121.8018 | 0.2243 | 0.20142 | 0.19226 | 0.14648 | 0.13733 | 0.18768 | 121.8292 | 0.16937 | 0.068664 | 121.907 | -0.032044 | 121.9345 | 0.022888 | -121.8979 | -121.8704 | 121.8567 | 0.1236 | 0.18768 | 0.16937
1992.8281 | 121.9757 | -0.13275 | 121.8933 | -0.012131 | 0.0048236 | 0.056418 | 0.055578 | 0.0040033 | -0.0098438 | -0.001741 | -0.005371 | 0.033212 | 0.047548 | 0.0022389 | 0.018316 | 0.025887 | -0.0021299 | 0.073242 | 121.9162 | -0.09613 | 121.6415 | -0.009155 | -0.14191 | -0.11444 | -0.054932 | -0.004578 | -0.059509 | -0.045776 | 0.027466 | 0.018311 | 0.045776 | 0.036621 | 0.022888 | -0.25177 | 0.1236 | 0.01831 | -0.009156 | -0.018311 | -0.045777 | 0.073242 | -121.8979 | -121.9391 | 0.16022 | 0.17853 | 0.15106 | 0.10528 | 0.07782 | 0.086975 | 121.7377 | 0.086975 | 0.013733 | 122.0123 | 0.054931 | 122.049 | 0.12817 | -121.9894 | -121.9528 | 121.7743 | 0.086975 | 0.20599 | 0.077819
1994.5938 | 121.9574 | -0.13275 | 121.9254 | -0.012131 | 0.0048236 | 0.055991 | 0.053442 | 0.0040033 | -0.0081348 | -0.0032364 | -0.0023192 | 0.034921 | 0.046694 | 0.0075793 | 0.017034 | 0.027169 | -0.0038389 | 0.086975 | 121.9116 | -0.11444 | 121.6324 | -0.059509 | -0.15564 | -0.12817 | -0.073242 | -0.018311 | -0.068665 | -0.07782 | -0.018311 | -0.041199 | 0.022888 | 0.01831 | -0.013733 | -0.29297 | 0.073242 | 0.004577 | -0.022889 | -0.013733 | -0.041199 | 0.064086 | -121.9437 | -122.0032 | 0.11444 | 0.15564 | 0.091552 | 0.091553 | 0.027466 | 0.054932 | 121.7468 | 0.050354 | -0.009155 | 122.0261 | 0.050354 | 122.0444 | 0.11444 | -122.0398 | -121.994 | 121.7651 | 0.054931 | 0.21973 | 0.059509
1996.3125 | 122.0032 | -0.11902 | 121.8933 | -0.012131 | 0.0035418 | 0.05535 | 0.053869 | 0.00037174 | -0.0066394 | -0.0011002 | -0.005371 | 0.032571 | 0.047335 | 0.0060841 | 0.017034 | 0.024819 | -0.0031979 | 0.16479 | 121.875 | -0.10986 | 121.7056 | 0.041199 | -0.07782 | -0.059509 | 0.018311 | -0.013733 | -0.041199 | -0.027466 | 0.068665 | 0.045776 | 0.073242 | 0.009156 | -0.018311 | -0.18768 | 0.16022 | 0.05951 | 0.041199 | 0.050354 | 0.032043 | 0.07782 | -121.907 | -121.9208 | 0.18768 | 0.19226 | 0.16479 | 0.11444 | 0.086975 | 0.15106 | 121.8155 | 0.10986 | 0.013733 | 121.9849 | 0.027466 | 121.994 | 0.10529 | -122.0032 | -121.9345 | 121.8246 | 0.091553 | 0.28381 | 0.13733
1998.0625 | 122.0581 | -0.091553 | 121.9025 | -0.012131 | 0.002901 | 0.052786 | 0.048529 | -0.00091006 | -0.011125 | -0.00345 | -0.0084228 | 0.029794 | 0.043489 | 0.0035205 | 0.016393 | 0.025673 | -0.0038389 | 0.13733 | 121.8246 | -0.050354 | 121.7743 | 0.14648 | 0.022888 | 0.041199 | 0.086975 | -0.054932 | -0.027466 | 0.018311 | 0.14648 | 0.13275 | 0.12817 | 0.041199 | -0.07782 | -0.12817 | 0.23804 | 0.13275 | 0.11444 | 0.091553 | 0.073242 | 0.064087 | -121.9574 | -121.8842 | 0.23804 | 0.21973 | 0.2243 | 0.15564 | 0.16022 | 0.19684 | 121.8246 | 0.17395 | 0.045777 | 121.875 | -0.027466 | 121.9162 | 0.036621 | -121.9528 | -121.9299 | 121.8658 | 0.10986 | 0.22888 | 0.17853
1999.8125 | 122.0535 | -0.10071 | 121.8796 | -0.012131 | -0.00030342 | 0.054709 | 0.050238 | -0.00026906 | -0.0064258 | -3.1996e-05 | -0.005371 | 0.03193 | 0.045198 | 0.0035205 | 0.015325 | 0.024391 | -0.0031979 | 0.059509 | 121.8475 | -0.07782 | 121.7056 | 0.059509 | -0.050354 | -0.018311 | 0.013733 | -0.054932 | -0.045776 | -0.013733 | 0.10529 | 0.10071 | 0.091553 | 0.022888 | -0.032044 | -0.17395 | 0.16022 | 0.082397 | 0.050354 | 0.059509 | 0.027466 | 0.054932 | -121.9345 | -121.8933 | 0.20599 | 0.19226 | 0.20142 | 0.13733 | 0.14648 | 0.13733 | 121.7834 | 0.15106 | 0.032043 | 121.9254 | -0.009156 | 121.9482 | 0.045776 | -121.9574 | -121.9254 | 121.8063 | 0.086975 | 0.16022 | 0.11444
2001.5625 | 122.0215 | -0.1236 | 121.8887 | -0.0045011 | 0.0020466 | 0.054068 | 0.052801 | -0.00069646 | -0.0083484 | -0.001741 | -0.0023192 | 0.03193 | 0.040712 | 0.00052987 | 0.015752 | 0.025032 | -0.0061887 | 0.14191 | 121.843 | -0.073242 | 121.756 | 0.1236 | 0.004578 | 0.013733 | 0.027466 | -0.027466 | -0.027466 | -0.027466 | 0.091553 | 0.07782 | 0.068665 | 0.050354 | -0.045776 | -0.13275 | 0.24719 | 0.13733 | 0.12817 | 0.086975 | 0.07782 | 0.09613 | -121.9162 | -121.9162 | 0.21515 | 0.19226 | 0.20142 | 0.096131 | 0.10529 | 0.19684 | 121.8292 | 0.11902 | 0 | 121.9162 | 0 | 121.9666 | 0.09613 | -121.962 | -121.9162 | 121.8796 | 0.09613 | 0.2655 | 0.15106
2003.3281 | 121.9482 | -0.13275 | 121.9025 | -0.012131 | 0.002901 | 0.054922 | 0.052801 | 0.00058534 | -0.0098438 | -0.0002456 | -0.0023192 | 0.033212 | 0.045626 | 0.0062977 | 0.015539 | 0.0261 | -0.0034117 | 0.11444 | 121.9025 | -0.10986 | 121.6553 | -0.013733 | -0.10986 | -0.09613 | -0.091553 | -0.004578 | -0.068665 | -0.10986 | -0.009155 | -0.013733 | 0.009155 | 0.022888 | 0 | -0.24719 | 0.11902 | 0.036621 | 0.022888 | 0.013733 | 0 | 0.064086 | -121.907 | -122.0123 | 0.1236 | 0.14191 | 0.11902 | 0.07782 | 0.054932 | 0.09613 | 121.7651 | 0.05951 | -0.041198 | 122.0123 | 0.064087 | 122.0352 | 0.12817 | -122.0123 | -121.9711 | 121.788 | 0.022888 | 0.24719 | 0.041198
2005.0938 | 121.9803 | -0.13275 | 121.8887 | 0.0031279 | -0.00073062 | 0.055991 | 0.049811 | -0.0013373 | -0.012194 | -0.0013138 | -0.0023192 | 0.03193 | 0.044558 | 0.012279 | 0.018316 | 0.026741 | -0.0044797 | 0.15106 | 121.8384 | -0.068665 | 121.7285 | 0.082397 | -0.027466 | -0.009155 | 0 | -0.036621 | -0.041199 | -0.068665 | 0.064087 | 0.027466 | 0.045776 | 0.064086 | -0.050354 | -0.16022 | 0.21515 | 0.1236 | 0.10529 | 0.05951 | 0.041199 | 0.091552 | -121.9254 | -121.9574 | 0.19684 | 0.17853 | 0.16022 | 0.086975 | 0.068665 | 0.15106 | 121.7972 | 0.10529 | -0.027466 | 121.907 | 0.004578 | 121.9711 | 0.09613 | -121.9574 | -121.9299 | 121.8613 | 0.064086 | 0.28381 | 0.13275
2006.7969 | 121.9803 | -0.11444 | 121.9162 | -0.012131 | 0.00012398 | 0.054709 | 0.051947 | -0.00069646 | -0.0098438 | -0.0004592 | -0.005371 | 0.033426 | 0.043062 | -0.00053833 | 0.01618 | 0.024391 | -0.0040525 | 0.14191 | 121.8384 | -0.07782 | 121.6919 | 0.050354 | -0.064087 | -0.045776 | -0.032043 | -0.018311 | -0.059509 | -0.091553 | 0.013733 | 0.022888 | 0.013733 | 0.036621 | -0.07782 | -0.2243 | 0.16479 | 0.068665 | 0.050354 | 0.032044 | 0.013733 | 0.054932 | -121.9345 | -122.0078 | 0.12817 | 0.12817 | 0.13733 | 0.073242 | 0.082397 | 0.12817 | 121.7697 | 0.073242 | -0.032044 | 121.9162 | 0.041198 | 121.9528 | 0.09613 | -121.994 | -121.9757 | 121.8063 | 0.022888 | 0.25635 | 0.082398
2008.5469 | 122.0535 | -0.09613 | 121.8704 | 0.0031279 | 0.0026874 | 0.056204 | 0.053015 | -0.0026191 | -0.010485 | -0.0038772 | -0.0084228 | 0.033426 | 0.042208 | 0.00074347 | 0.017034 | 0.025032 | -0.0012753 | 0.064087 | 121.8521 | -0.059509 | 121.7331 | 0.07782 | -0.027466 | -0.004578 | 0.032043 | -0.045776 | -0.022888 | 0.009155 | 0.1236 | 0.1236 | 0.10986 | 0.036621 | -0.01831 | -0.13733 | 0.17395 | 0.091552 | 0.068664 | 0.054931 | 0.032043 | 0.073242 | -121.9162 | -121.8613 | 0.21973 | 0.20599 | 0.21973 | 0.13275 | 0.14648 | 0.13733 | 121.7926 | 0.14648 | 0.032043 | 121.9116 | -0.022888 | 121.9482 | 0.050354 | -121.9299 | -121.8933 | 121.8292 | 0.10528 | 0.16022 | 0.12817
2010.3125 | 121.9803 | -0.1236 | 121.9025 | -0.012131 | 0.0016192 | 0.052786 | 0.053442 | 0.00058534 | -0.0094164 | -0.0040908 | -0.005371 | 0.036416 | 0.043062 | 0.0054431 | 0.016821 | 0.025246 | -0.0053343 | 0.13275 | 121.8933 | -0.11444 | 121.6553 | -0.022888 | -0.11444 | -0.10071 | -0.073242 | -0.009155 | -0.064087 | -0.086975 | 0.032043 | 0.022888 | 0.041199 | 0.009155 | -0.009155 | -0.24719 | 0.10071 | 0.022888 | 0.009155 | 0.013733 | 0 | 0.059509 | -121.9116 | -121.9894 | 0.15564 | 0.16479 | 0.14648 | 0.10529 | 0.086975 | 0.091553 | 121.7697 | 0.09613 | -0.022888 | 122.0078 | 0.054932 | 122.0169 | 0.11444 | -122.0169 | -121.9666 | 121.7789 | 0.036621 | 0.25635 | 0.050354
2012.0156 | 122.0306 | -0.10529 | 121.8658 | -0.0045011 | 0.0022602 | 0.053854 | 0.052588 | 0.0016535 | -0.0083484 | -0.001741 | -0.005371 | 0.035348 | 0.042849 | -0.00011113 | 0.014043 | 0.026741 | -0.0066159 | 0.054932 | 121.8475 | -0.068665 | 121.7148 | 0.064087 | -0.068665 | -0.018311 | -0.004578 | -0.050354 | -0.027466 | -0.018311 | 0.068665 | 0.07782 | 0.07782 | 0.036621 | -0.018311 | -0.15106 | 0.16937 | 0.086975 | 0.036621 | 0.050354 | 0 | 0.07782 | -121.9162 | -121.8842 | 0.17395 | 0.18311 | 0.18311 | 0.10529 | 0.10529 | 0.13275 | 121.7834 | 0.096131 | 0.009155 | 121.9162 | -0.022888 | 121.9528 | 0.054932 | -121.9345 | -121.8933 | 121.8201 | 0.086975 | 0.16022 | 0.10071
2013.7656 | 121.9574 | -0.13733 | 121.907 | 0.0031279 | -0.00030342 | 0.053427 | 0.054083 | 0.0052851 | -0.00963 | -3.1996e-05 | -0.005371 | 0.033853 | 0.042208 | 0.0028797 | 0.015325 | 0.024178 | -0.0066159 | 0.11444 | 121.8567 | -0.09613 | 121.6507 | 0.004578 | -0.11444 | -0.086975 | -0.059509 | -0.004578 | -0.073242 | -0.09613 | 0.027466 | 0.009155 | 0.009155 | 0.041199 | -0.050354 | -0.25635 | 0.14191 | 0.050354 | 0.022888 | 0.009155 | -0.018311 | 0.064087 | -121.9116 | -122.0032 | 0.16479 | 0.14648 | 0.14648 | 0.082397 | 0.082397 | 0.10071 | 121.7468 | 0.10071 | -0.022888 | 121.9528 | 0.068664 | 121.994 | 0.13275 | -122.0032 | -121.9803 | 121.788 | 0.041199 | 0.25177 | 0.07782
2015.4688 | 121.9437 | -0.15106 | 121.8842 | -0.012131 | 0.0058918 | 0.056204 | 0.055151 | 0.00037174 | -0.0089892 | -0.0028092 | -0.005371 | 0.034494 | 0.044985 | 0.0062977 | 0.017461 | 0.024178 | -0.0055479 | 0.11444 | 121.9025 | -0.10529 | 121.6461 | -0.064087 | -0.17395 | -0.12817 | -0.10071 | -0.004578 | -0.054932 | -0.073242 | -0.013733 | -0.022888 | 0.022888 | 0.045776 | 0.018311 | -0.23804 | 0.086975 | 0.022888 | -0.022888 | -0.022888 | -0.068664 | 0.09613 | -121.8887 | -121.9574 | 0.13733 | 0.17395 | 0.12817 | 0.07782 | 0.032044 | 0.041199 | 121.7514 | 0.041199 | -0.01831 | 122.0078 | 0.050354 | 122.0535 | 0.14648 | -121.9894 | -121.9391 | 121.7972 | 0.07782 | 0.2655 | 0.050354
2017.2344 | 121.962 | -0.14648 | 121.8933 | -0.012131 | 0.0048236 | 0.05535 | 0.054083 | -0.00048286 | -0.0083484 | -0.0030228 | -0.005371 | 0.034066 | 0.043062 | 0.011424 | 0.020025 | 0.023323 | -0.0040525 | 0.07782 | 121.9025 | -0.086975 | 121.6553 | -0.032043 | -0.15106 | -0.12817 | -0.073242 | -0.009155 | -0.064087 | -0.073242 | -0.013733 | -0.018311 | 0.004578 | 0.059509 | 0.009155 | -0.23804 | 0.11444 | 0.01831 | -0.004578 | -0.041199 | -0.064087 | 0.082397 | -121.9025 | -121.9666 | 0.13275 | 0.15106 | 0.12817 | 0.068665 | 0.045776 | 0.054932 | 121.7422 | 0.050354 | -0.009155 | 121.9894 | 0.054932 | 122.049 | 0.13733 | -121.9803 | -121.9574 | 121.8018 | 0.073242 | 0.2243 | 0.073242
2019 | 121.994 | -0.12817 | 121.9116 | -0.0045011 | 0.00461 | 0.056204 | 0.055151 | 0.0014397 | -0.0062122 | -0.005159 | -0.005371 | 0.032357 | 0.046267 | 0.0030933 | 0.016821 | 0.024178 | -0.0029843 | 0.068665 | 121.907 | -0.10071 | 121.6507 | -0.009155 | -0.14648 | -0.10529 | -0.045776 | -0.022888 | -0.064087 | -0.045776 | 0.022888 | -0.004578 | 0.022888 | 0.027466 | -0.004578 | -0.26093 | 0.11902 | 0.022888 | -0.01831 | -0.004578 | -0.045776 | 0.064087 | -121.9345 | -121.9574 | 0.15106 | 0.15106 | 0.1236 | 0.086975 | 0.059509 | 0.091553 | 121.7514 | 0.086975 | 0.018311 | 122.0078 | 0.041199 | 122.0352 | 0.10529 | -122.0123 | -121.9757 | 121.7789 | 0.082398 | 0.19684 | 0.082398
2020.7031 | 121.9711 | -0.14191 | 121.9345 | 0.0031279 | 0.00076478 | 0.054068 | 0.050024 | -0.0034735 | -0.0083484 | -0.002382 | -0.0084228 | 0.034494 | 0.04413 | 0.00010247 | 0.014471 | 0.027382 | -0.0010617 | 0.15564 | 121.8613 | -0.07782 | 121.7148 | 0.068665 | -0.050354 | -0.036621 | -0.018311 | -0.036621 | -0.054932 | -0.073242 | 0.045776 | 0.027466 | 0.018311 | 0.064087 | -0.073242 | -0.21973 | 0.21057 | 0.10529 | 0.091553 | 0.041199 | 0.027466 | 0.086975 | -121.9711 | -122.0078 | 0.18768 | 0.16022 | 0.16937 | 0.073243 | 0.082398 | 0.14649 | 121.7926 | 0.10071 | -0.01831 | 121.9391 | 0.018311 | 122.0032 | 0.10529 | -122.0123 | -121.9894 | 121.8567 | 0.068665 | 0.29755 | 0.1236
2022.4531 | 121.9757 | -0.13275 | 121.8979 | -0.012131 | 0.0039692 | 0.055563 | 0.052588 | 0.00079894 | -0.0074938 | -0.0025956 | -0.0084228 | 0.034707 | 0.043703 | 0.0062977 | 0.017461 | 0.02546 | -0.0025571 | 0.17395 | 121.8704 | -0.10071 | 121.7056 | 0.050354 | -0.091553 | -0.054932 | 0.013733 | 0 | -0.054932 | -0.036621 | 0.054932 | 0.018311 | 0.041199 | 0.032043 | -0.027466 | -0.19226 | 0.18311 | 0.077819 | 0.041198 | 0.045776 | 0.009155 | 0.077819 | -121.8979 | -121.9345 | 0.18768 | 0.17395 | 0.15106 | 0.096131 | 0.073243 | 0.15106 | 121.8063 | 0.10986 | 0.018311 | 121.9711 | 0.054932 | 122.0032 | 0.13275 | -121.9986 | -121.9528 | 121.8384 | 0.09613 | 0.3067 | 0.14648
2024.2031 | 121.962 | -0.12817 | 121.8933 | -0.012131 | 0.001192 | 0.053854 | 0.051947 | -0.00091006 | -0.0074938 | -0.0019546 | -0.005371 | 0.032571 | 0.041353 | 0.0045887 | 0.016607 | 0.025673 | -0.0034117 | 0.14191 | 121.875 | -0.086975 | 121.7102 | 0.050354 | -0.050354 | -0.032043 | -0.041199 | -0.013733 | -0.064087 | -0.086975 | 0.045776 | 0.013733 | 0.018311 | 0.041199 | -0.018311 | -0.18311 | 0.17853 | 0.096131 | 0.07782 | 0.054932 | 0.036621 | 0.064087 | -121.907 | -121.9803 | 0.17395 | 0.14649 | 0.14191 | 0.082398 | 0.07782 | 0.13733 | 121.7972 | 0.10986 | -0.022888 | 121.962 | 0.050354 | 122.0032 | 0.11444 | -121.9803 | -121.9574 | 121.8384 | 0.041199 | 0.27008 | 0.086975
2025.9219 | 121.9391 | -0.13733 | 121.9345 | -0.012131 | 0.006319 | 0.055991 | 0.052374 | -0.0013373 | -0.008562 | 0.0001816 | -0.005371 | 0.033426 | 0.043703 | 0.0024525 | 0.017675 | 0.02546 | -0.0031979 | 0.09613 | 121.9025 | -0.10529 | 121.6553 | -0.045776 | -0.16937 | -0.13733 | -0.091553 | -0.009155 | -0.064087 | -0.091553 | -0.027466 | -0.036621 | 0.009155 | 0.032043 | -0.032043 | -0.27924 | 0.091553 | 0 | -0.032044 | -0.032043 | -0.064087 | 0.073242 | -121.9437 | -122.0261 | 0.10986 | 0.14648 | 0.10071 | 0.073242 | 0.027466 | 0.05951 | 121.7606 | 0.036621 | -0.027466 | 122.0078 | 0.054932 | 122.0398 | 0.12817 | -122.0398 | -121.9986 | 121.7926 | 0.045776 | 0.23346 | 0.045776
2027.6875 | 122.0856 | -0.086975 | 121.8567 | -0.012131 | 0.0039692 | 0.057486 | 0.053228 | 0.0050713 | -0.0055712 | -0.0021682 | -0.005371 | 0.031717 | 0.043489 | 0.0026661 | 0.016607 | 0.027809 | -0.0023435 | 0.11902 | 121.8521 | -0.07782 | 121.7514 | 0.13275 | -0.018311 | 0.013733 | 0.091553 | -0.050354 | -0.009155 | 0.050354 | 0.14648 | 0.1236 | 0.11902 | 0.009155 | -0.004577 | -0.10529 | 0.21973 | 0.10071 | 0.068664 | 0.091553 | 0.059509 | 0.07782 | -121.907 | -121.8063 | 0.23346 | 0.20599 | 0.21057 | 0.12817 | 0.13275 | 0.21057 | 121.8292 | 0.15564 | 0.059509 | 121.9299 | -0.041199 | 121.9391 | 0.036621 | -121.9345 | -121.8658 | 121.8384 | 0.13733 | 0.20599 | 0.17853
2029.4375 | 122.0673 | -0.11444 | 121.8658 | -0.01976 | 0.00033758 | 0.055991 | 0.050879 | -0.0032599 | -0.010271 | -0.0013138 | -0.0023192 | 0.030008 | 0.043703 | 0.0033069 | 0.013189 | 0.025887 | -0.0049069 | 0.16022 | 121.843 | -0.091553 | 121.7697 | 0.11902 | 0.009155 | 0.022888 | 0.073242 | -0.045776 | -0.050354 | 0.004578 | 0.13275 | 0.11902 | 0.086975 | 0.022888 | -0.022888 | -0.096131 | 0.23346 | 0.13733 | 0.1236 | 0.11444 | 0.10071 | 0.064087 | -121.9116 | -121.8613 | 0.24719 | 0.20142 | 0.23346 | 0.13733 | 0.16937 | 0.21057 | 121.8613 | 0.18311 | 0.054932 | 121.9345 | 0.004578 | 121.9574 | 0.068665 | -121.9574 | -121.9162 | 121.8842 | 0.11902 | 0.27466 | 0.18768
2031.125 | 121.9757 | -0.14191 | 121.8704 | -0.012131 | 0.0026874 | 0.056418 | 0.054724 | 0.00058534 | -0.0074938 | -0.002382 | -0.0023192 | 0.032998 | 0.042849 | 0.0065113 | 0.01618 | 0.02546 | -0.0025571 | 0.064087 | 121.8658 | -0.13275 | 121.6324 | -0.041199 | -0.15564 | -0.12817 | -0.045776 | -0.009155 | -0.073242 | -0.068665 | 0.004578 | 0.004578 | 0.032043 | 0.009156 | -0.004577 | -0.23804 | 0.10071 | 0.013733 | -0.013733 | 0.004577 | -0.022889 | 0.068665 | -121.8796 | -121.9391 | 0.14649 | 0.17395 | 0.14649 | 0.10529 | 0.07782 | 0.091552 | 121.7651 | 0.07782 | 0.004577 | 121.9986 | 0.064087 | 122.0078 | 0.13275 | -122.0032 | -121.9437 | 121.7743 | 0.073242 | 0.20599 | 0.096131
2032.8906 | 122.0581 | -0.10986 | 121.8979 | 0.010757 | -0.0020124 | 0.055563 | 0.051092 | -0.0017645 | -0.010698 | -0.001741 | -0.0023192 | 0.02958 | 0.042208 | 0.0056567 | 0.015539 | 0.025246 | -0.0049069 | 0.16479 | 121.8201 | -0.07782 | 121.756 | 0.13733 | -0.004578 | 0.004578 | 0.073242 | -0.036621 | -0.050354 | 0.022888 | 0.13733 | 0.13275 | 0.10071 | 0.032043 | -0.07782 | -0.14191 | 0.24719 | 0.11444 | 0.10529 | 0.082398 | 0.073242 | 0.059509 | -121.9345 | -121.875 | 0.24719 | 0.21057 | 0.24261 | 0.15106 | 0.18311 | 0.21515 | 121.8338 | 0.18768 | 0.073242 | 121.8979 | 0.013733 | 121.9299 | 0.073242 | -121.9757 | -121.9482 | 121.8658 | 0.13275 | 0.27466 | 0.18311
2034.6406 | 122.1085 | -0.086975 | 121.8613 | -0.0045011 | 0.006319 | 0.053214 | 0.054083 | -0.0011237 | -0.008562 | -0.001741 | -0.005371 | 0.029153 | 0.044985 | 0.0041615 | 0.016607 | 0.028237 | -0.0023435 | 0.1236 | 121.8704 | -0.073242 | 121.756 | 0.091553 | -0.036621 | 0.013733 | 0.10986 | -0.050354 | -0.041199 | 0.064087 | 0.14648 | 0.13275 | 0.12817 | 0.013733 | 0.009155 | -0.10529 | 0.17853 | 0.10071 | 0.050354 | 0.086975 | 0.036621 | 0.045776 | -121.9116 | -121.7972 | 0.23346 | 0.21515 | 0.21973 | 0.16937 | 0.17395 | 0.16479 | 121.8292 | 0.18768 | 0.10529 | 121.9437 | -0.009155 | 121.9574 | 0.036621 | -121.9345 | -121.9025 | 121.843 | 0.15106 | 0.21057 | 0.19684
2036.4062 | 121.9666 | -0.14648 | 121.9025 | -0.012131 | 0.0050372 | 0.054709 | 0.054937 | 0.0027215 | -0.010698 | -0.0008866 | -0.0023192 | 0.033853 | 0.044344 | 0.0045887 | 0.017675 | 0.023323 | -0.0053343 | 0.16022 | 121.8842 | -0.11444 | 121.6599 | 0.004578 | -0.14191 | -0.11444 | -0.032043 | -0.009155 | -0.073242 | -0.073242 | -0.009155 | -0.018311 | 0.009155 | 0.032043 | -0.018311 | -0.24262 | 0.15106 | 0.032043 | 0.004577 | 0 | -0.027466 | 0.073242 | -121.9116 | -121.9757 | 0.13733 | 0.15564 | 0.12817 | 0.082397 | 0.054931 | 0.11902 | 121.7743 | 0.064087 | 0 | 121.9986 | 0.064087 | 122.0306 | 0.13733 | -122.0169 | -121.9757 | 121.8063 | 0.073242 | 0.3067 | 0.11444
2038.1094 | 121.9574 | -0.15564 | 121.9116 | -0.012131 | 0.0020466 | 0.054709 | 0.053228 | -0.0011237 | -0.0072802 | -0.001741 | -0.005371 | 0.032998 | 0.04413 | 0.0033069 | 0.014684 | 0.023323 | -0.0036253 | 0.10986 | 121.8887 | -0.11902 | 121.6461 | -0.022888 | -0.13733 | -0.10071 | -0.045776 | -0.032043 | -0.082397 | -0.10071 | 0.013733 | 0.018311 | 0.018311 | 0.036621 | -0.022888 | -0.2655 | 0.13275 | 0.054932 | 0.018311 | 0.018311 | -0.01831 | 0.073243 | -121.9437 | -122.0123 | 0.16937 | 0.17395 | 0.17395 | 0.10071 | 0.10071 | 0.096131 | 121.7651 | 0.09613 | -0.018311 | 122.0078 | 0.050354 | 122.0444 | 0.1236 | -122.0306 | -121.994 | 121.8018 | 0.054932 | 0.2655 | 0.10986
2039.8594 | 121.9986 | -0.13275 | 121.8933 | -0.0045011 | 0.0054644 | 0.055563 | 0.053228 | 0.0042169 | -0.0079212 | -0.0032364 | -0.005371 | 0.03428 | 0.043703 | 0.0090747 | 0.016607 | 0.024391 | -0.0038389 | 0.16937 | 121.875 | -0.09613 | 121.6965 | 0.032043 | -0.091553 | -0.073242 | 0.027466 | -0.018311 | -0.050354 | -0.036621 | 0.045776 | 0.036621 | 0.054932 | 0.036621 | -0.018311 | -0.19684 | 0.16479 | 0.059509 | 0.041198 | 0.022888 | 0.004577 | 0.082397 | -121.9116 | -121.9299 | 0.17853 | 0.18768 | 0.16937 | 0.10529 | 0.086975 | 0.12817 | 121.7926 | 0.09613 | 0.013733 | 121.9711 | 0.032043 | 122.0078 | 0.11444 | -121.9894 | -121.9437 | 121.8292 | 0.09613 | 0.30212 | 0.16022
2041.5625 | 122.0947 | -0.10529 | 121.8796 | -0.012131 | 0.0037556 | 0.057272 | 0.050451 | 0.00058534 | -0.0077074 | -0.005159 | -0.0023192 | 0.031076 | 0.043062 | 0.0065113 | 0.016393 | 0.023537 | -0.0038389 | 0.11902 | 121.843 | -0.068665 | 121.7514 | 0.10986 | -0.032043 | 0.013733 | 0.10071 | -0.050354 | -0.045776 | 0.050354 | 0.15106 | 0.11902 | 0.12817 | 0.036621 | -0.036621 | -0.12817 | 0.21515 | 0.11902 | 0.073243 | 0.082398 | 0.036622 | 0.05951 | -121.9299 | -121.8292 | 0.25635 | 0.23346 | 0.22431 | 0.17395 | 0.16479 | 0.17853 | 121.8201 | 0.19684 | 0.09613 | 121.9116 | -0.004578 | 121.9482 | 0.054932 | -121.9482 | -121.9254 | 121.8567 | 0.15564 | 0.22431 | 0.20599
2043.3281 | 122.1085 | -0.091553 | 121.8292 | -0.012131 | -8.9824e-05 | 0.055563 | 0.051733 | 0.00058534 | -0.0077074 | -0.0025956 | -0.0023192 | 0.030008 | 0.04413 | 0.0054431 | 0.015112 | 0.026955 | -0.00042085 | 0.11444 | 121.8292 | -0.10071 | 121.7514 | 0.11902 | -0.004578 | 0.022888 | 0.11902 | -0.027466 | -0.050354 | 0.054932 | 0.17395 | 0.16937 | 0.14191 | -0.009155 | 0 | -0.07782 | 0.21057 | 0.11444 | 0.086975 | 0.1236 | 0.09613 | 0.041199 | -121.8567 | -121.7743 | 0.2655 | 0.23346 | 0.26093 | 0.19226 | 0.21973 | 0.21973 | 121.8521 | 0.2243 | 0.10529 | 121.9299 | 0.022888 | 121.9208 | 0.064087 | -121.9299 | -121.8796 | 121.843 | 0.14649 | 0.20599 | 0.21057
2045.0938 | 122.0764 | -0.10071 | 121.8796 | -0.012131 | 0.0043964 | 0.056631 | 0.054297 | 0.00037174 | -0.008562 | -0.002382 | -0.005371 | 0.028726 | 0.042421 | 0.0048023 | 0.014471 | 0.025032 | -0.0042661 | 0.11902 | 121.8521 | -0.068665 | 121.7606 | 0.11902 | -0.027466 | 0 | 0.10071 | -0.036621 | -0.032043 | 0.045776 | 0.15106 | 0.11902 | 0.10986 | 0.032043 | -0.027466 | -0.11902 | 0.21973 | 0.10071 | 0.073242 | 0.068665 | 0.041199 | 0.068665 | -121.9162 | -121.8338 | 0.25177 | 0.21057 | 0.21973 | 0.14191 | 0.15106 | 0.18768 | 121.8292 | 0.18311 | 0.077819 | 121.9208 | -0.004578 | 121.9528 | 0.064087 | -121.9482 | -121.9116 | 121.8613 | 0.14648 | 0.21973 | 0.20142
2046.7969 | 121.9437 | -0.1236 | 121.8979 | -0.0045011 | 0.0052508 | 0.056204 | 0.052801 | 0.00058534 | -0.0070666 | -0.000673 | -0.005371 | 0.033212 | 0.042421 | 0.016765 | 0.018102 | 0.02311 | -0.0055479 | 0.1236 | 121.8887 | -0.11444 | 121.6461 | -0.041199 | -0.17395 | -0.11444 | -0.068665 | 0 | -0.073242 | -0.086975 | -0.013733 | -0.022888 | 0.013733 | 0.009155 | -0.009155 | -0.25177 | 0.082397 | 0.009155 | -0.050354 | 0 | -0.059509 | 0.050354 | -121.8979 | -121.9849 | 0.10986 | 0.13733 | 0.10071 | 0.086975 | 0.050354 | 0.073242 | 121.7606 | 0.059509 | -0.013733 | 122.0032 | 0.073242 | 122.0123 | 0.1236 | -122.0123 | -121.9711 | 121.7697 | 0.036621 | 0.24719 | 0.054931
2048.5469 | 121.9391 | -0.16022 | 121.8796 | -0.012131 | 0.0041828 | 0.054068 | 0.055792 | 0.0012261 | -0.0098438 | 0.0001816 | -0.005371 | 0.036843 | 0.045198 | 0.012065 | 0.017248 | 0.024819 | 0.0015017 | 0.14648 | 121.8796 | -0.10986 | 121.6599 | -0.004578 | -0.14648 | -0.10986 | -0.054932 | -0.004578 | -0.068665 | -0.073242 | -0.004578 | -0.018311 | 0.032043 | 0.050354 | 0 | -0.21973 | 0.15564 | 0.050354 | 0.013733 | 0 | -0.036621 | 0.091552 | -121.8842 | -121.9528 | 0.15564 | 0.19226 | 0.14191 | 0.10071 | 0.050354 | 0.10529 | 121.7697 | 0.064087 | -0.004577 | 121.9894 | 0.064087 | 122.0398 | 0.15564 | -121.9894 | -121.9482 | 121.8201 | 0.086975 | 0.3067 | 0.10528
2050.2969 | 121.9666 | -0.13275 | 121.875 | -0.012131 | 0.0022602 | 0.054709 | 0.053015 | -0.0028327 | -0.0074938 | -0.0030228 | -0.011475 | 0.034494 | 0.045198 | 0.0095019 | 0.017248 | 0.027169 | -0.0059751 | 0.15564 | 121.9116 | -0.10986 | 121.6827 | 0.032043 | -0.11444 | -0.10986 | -0.018311 | -0.022888 | -0.059509 | -0.054932 | 0.032043 | -0.004578 | 0.041199 | 0.022888 | 0.036621 | -0.19226 | 0.16479 | 0.022888 | 0.01831 | 0 | -0.004578 | 0.073242 | -121.8979 | -121.9299 | 0.16479 | 0.17395 | 0.12817 | 0.10071 | 0.054931 | 0.14191 | 121.7926 | 0.091552 | 0.004577 | 122.0215 | 0.036621 | 122.0444 | 0.10986 | -121.9849 | -121.9345 | 121.8155 | 0.077819 | 0.28839 | 0.11444
2052 | 122.0856 | -0.10529 | 121.8521 | -0.0045011 | 0.00012398 | 0.052359 | 0.051306 | -0.00026906 | -0.0089892 | -0.0025956 | -0.0084228 | 0.030221 | 0.042208 | 0.0069385 | 0.015325 | 0.026314 | -0.0059751 | 0.13733 | 121.8246 | -0.10529 | 121.7789 | 0.16479 | 0.027466 | 0.045776 | 0.11902 | -0.045776 | -0.041199 | 0.041199 | 0.16937 | 0.16022 | 0.14191 | 0 | -0.027466 | -0.073242 | 0.27008 | 0.15106 | 0.13275 | 0.15106 | 0.13275 | 0.064087 | -121.8979 | -121.8109 | 0.27466 | 0.24719 | 0.2655 | 0.18311 | 0.20142 | 0.27008 | 121.8842 | 0.21057 | 0.082398 | 121.9299 | -0.004577 | 121.9299 | 0.05951 | -121.9574 | -121.8933 | 121.8842 | 0.14649 | 0.24262 | 0.22431
2053.75 | 122.0764 | -0.13733 | 121.8796 | -0.012131 | 0.0035418 | 0.055777 | 0.051733 | -0.00026906 | -0.006853 | 0.0003952 | -0.0023192 | 0.028512 | 0.04114 | -0.0026745 | 0.015112 | 0.027382 | -0.0036253 | 0.07782 | 121.8475 | -0.086975 | 121.701 | 0.068665 | -0.050354 | -0.022888 | 0.018311 | -0.032043 | -0.045776 | 0 | 0.13275 | 0.11902 | 0.11902 | 0.050354 | -0.032044 | -0.17853 | 0.20599 | 0.11444 | 0.086975 | 0.064087 | 0.036621 | 0.091553 | -121.9116 | -121.8796 | 0.27008 | 0.25635 | 0.25635 | 0.16479 | 0.16479 | 0.15564 | 121.788 | 0.17853 | 0.045776 | 121.9345 | 0.013733 | 121.9849 | 0.10529 | -121.9666 | -121.9254 | 121.8384 | 0.13733 | 0.21515 | 0.15564
2055.5 | 122.0856 | -0.10529 | 121.8842 | -0.01976 | 0.0020466 | 0.053641 | 0.049383 | -0.0024055 | -0.0074938 | -0.0055862 | -0.0023192 | 0.030862 | 0.041567 | 0.0048023 | 0.013403 | 0.022469 | 6.346e-06 | 0.10986 | 121.8613 | -0.07782 | 121.756 | 0.10071 | -0.018311 | 0.013733 | 0.073242 | -0.045776 | -0.059509 | 0.041199 | 0.15106 | 0.15106 | 0.12817 | 0.027466 | -0.022888 | -0.12817 | 0.20599 | 0.11902 | 0.086975 | 0.091553 | 0.059509 | 0.045777 | -121.9299 | -121.843 | 0.25635 | 0.23346 | 0.25635 | 0.18768 | 0.21057 | 0.17853 | 121.8338 | 0.21057 | 0.10071 | 121.9391 | 0.013733 | 121.9666 | 0.05951 | -121.962 | -121.9437 | 121.8613 | 0.14649 | 0.21515 | 0.17853
2057.2812 | 122.0627 | -0.11444 | 121.8704 | -0.01976 | -0.0020124 | 0.052359 | 0.051092 | -0.0017645 | -0.0092028 | -0.0036636 | -0.0084228 | 0.032571 | 0.042208 | 0.0037341 | 0.014257 | 0.026741 | -0.0057615 | 0.068665 | 121.8475 | -0.091553 | 121.7056 | 0.050354 | -0.064087 | -0.027466 | 0.004578 | -0.032043 | -0.054932 | -0.009155 | 0.10986 | 0.10986 | 0.10071 | 0.022888 | -0.022888 | -0.16479 | 0.16479 | 0.086975 | 0.050354 | 0.064087 | 0.027466 | 0.059509 | -121.9025 | -121.8796 | 0.2243 | 0.21515 | 0.2243 | 0.15564 | 0.16479 | 0.14191 | 121.7972 | 0.16479 | 0.045777 | 121.9391 | 0.022889 | 121.962 | 0.082398 | -121.962 | -121.9254 | 121.8201 | 0.10529 | 0.18311 | 0.11902
2059.0469 | 122.0352 | -0.11444 | 121.8613 | 0.0031279 | 0.00055118 | 0.054709 | 0.051092 | -0.0026191 | -0.008562 | -0.0019546 | -0.005371 | 0.031289 | 0.043062 | 0.0075793 | 0.015325 | 0.026314 | 0.00064735 | 0.059509 | 121.8155 | -0.09613 | 121.7102 | 0.045776 | -0.082397 | -0.027466 | 0.009155 | -0.027466 | -0.054932 | -0.018311 | 0.082397 | 0.068665 | 0.086975 | 0.018311 | -0.045776 | -0.15106 | 0.16022 | 0.086975 | 0.032044 | 0.068664 | 0.013733 | 0.059509 | -121.8887 | -121.8796 | 0.19684 | 0.20142 | 0.18311 | 0.14191 | 0.1236 | 0.14191 | 121.8063 | 0.13733 | 0.036621 | 121.9116 | 0.027466 | 121.9299 | 0.086975 | -121.9574 | -121.9162 | 121.8246 | 0.09613 | 0.17395 | 0.1236
2060.8125 | 122.0535 | -0.09613 | 121.8796 | -0.012131 | -0.0011578 | 0.053 | 0.051092 | 0.0027215 | -0.0098438 | -0.002382 | -0.0023192 | 0.031076 | 0.044558 | 0.0018115 | 0.015752 | 0.022683 | -0.0023435 | 0.15564 | 121.8201 | -0.068665 | 121.7606 | 0.10986 | -0.009155 | 0.027466 | 0.073242 | -0.027466 | -0.041199 | 0.027466 | 0.13275 | 0.13275 | 0.11444 | 0.027465 | -0.05951 | -0.11902 | 0.20599 | 0.1236 | 0.086975 | 0.096131 | 0.05951 | 0.054931 | -121.907 | -121.8521 | 0.22888 | 0.21057 | 0.22888 | 0.15564 | 0.17395 | 0.17853 | 121.8292 | 0.17395 | 0.068665 | 121.8887 | 0.013733 | 121.9162 | 0.068664 | -121.9482 | -121.9208 | 121.8567 | 0.1236 | 0.25177 | 0.16937
2062.5156 | 122.0352 | -0.1236 | 121.8658 | -0.012131 | 0.0024738 | 0.055991 | 0.052588 | 0.00015814 | -0.008562 | -0.0038772 | -0.0023192 | 0.031717 | 0.041567 | 0.0018115 | 0.014043 | 0.0261 | 6.346e-06 | 0.073242 | 121.8521 | -0.073242 | 121.7194 | 0.059509 | -0.086975 | -0.018311 | 0.018311 | -0.041199 | -0.054932 | -0.004578 | 0.091553 | 0.082397 | 0.09613 | 0.050354 | -0.013733 | -0.14648 | 0.1831 | 0.10528 | 0.036621 | 0.054931 | -0.013733 | 0.068664 | -121.907 | -121.8704 | 0.21515 | 0.21973 | 0.20599 | 0.15106 | 0.13733 | 0.13275 | 121.7926 | 0.14649 | 0.050354 | 121.9254 | 0.013733 | 121.9757 | 0.082397 | -121.9391 | -121.9208 | 121.843 | 0.11902 | 0.19684 | 0.14191
2064.2812 | 122.0901 | -0.10986 | 121.8567 | -0.012131 | -0.00030342 | 0.053854 | 0.05152 | -0.0032599 | -0.008562 | -0.0032364 | -0.005371 | 0.031076 | 0.04114 | 0.0015979 | 0.015112 | 0.024178 | -0.0085385 | 0.10071 | 121.8613 | -0.073242 | 121.7422 | 0.086975 | -0.027466 | 0.009155 | 0.068665 | -0.036621 | -0.036621 | 0.027466 | 0.14648 | 0.15106 | 0.12817 | 0.036621 | 0.004578 | -0.11444 | 0.19684 | 0.11902 | 0.082397 | 0.082397 | 0.045776 | 0.073242 | -121.8933 | -121.8292 | 0.25635 | 0.23804 | 0.26093 | 0.1648 | 0.18768 | 0.16022 | 121.8155 | 0.18311 | 0.064087 | 121.9345 | 0 | 121.9711 | 0.073242 | -121.9299 | -121.8933 | 121.8521 | 0.13733 | 0.21057 | 0.17853
2066.0469 | 122.0078 | -0.1236 | 121.8796 | 0.0031279 | 0.0039692 | 0.054495 | 0.056646 | 0.0014397 | -0.0074938 | -0.001741 | -0.0084228 | 0.034494 | 0.042635 | 0.01527 | 0.017889 | 0.024605 | -0.0012753 | 0.17853 | 121.875 | -0.09613 | 121.701 | 0.032043 | -0.091553 | -0.073242 | 0 | -0.013733 | -0.041199 | -0.018311 | 0.054932 | 0.018311 | 0.045776 | 0.027466 | -0.004578 | -0.17853 | 0.15564 | 0.050354 | 0.032043 | 0.022888 | 0.004577 | 0.082397 | -121.8933 | -121.8979 | 0.17853 | 0.16937 | 0.14191 | 0.086975 | 0.05951 | 0.12817 | 121.7972 | 0.096131 | 0.022888 | 121.9711 | 0.027466 | 121.9986 | 0.10986 | -121.9757 | -121.9208 | 121.8246 | 0.10528 | 0.30212 | 0.1236
2067.75 | 121.962 | -0.15106 | 121.907 | -0.0045011 | 0.00033758 | 0.054495 | 0.053869 | 0.00037174 | -0.011553 | -0.0002456 | -0.0084228 | 0.034066 | 0.042208 | -0.00032473 | 0.015966 | 0.024391 | -0.0046933 | 0.13733 | 121.9162 | -0.10529 | 121.6415 | -0.022888 | -0.1236 | -0.10986 | -0.064087 | 0 | -0.07782 | -0.07782 | 0.022888 | 0.009155 | 0.036621 | 0.045776 | 0.009156 | -0.2655 | 0.12817 | 0.041199 | 0.027466 | -0.004577 | -0.01831 | 0.073242 | -121.907 | -121.9849 | 0.17395 | 0.18768 | 0.16022 | 0.11444 | 0.086975 | 0.082398 | 121.7468 | 0.10071 | 0 | 122.0215 | 0.07782 | 122.0673 | 0.15106 | -122.0123 | -121.9849 | 121.7926 | 0.073242 | 0.28839 | 0.086975
2069.5156 | 121.994 | -0.1236 | 121.907 | -0.012131 | 0.0020466 | 0.055136 | 0.051733 | -0.0034735 | -0.010271 | -0.0011002 | -0.0084228 | 0.030862 | 0.042635 | 0.0037341 | 0.015539 | 0.025246 | -0.0070433 | 0.1831 | 121.8292 | -0.07782 | 121.756 | 0.086975 | -0.032043 | -0.013733 | 0.041199 | -0.018311 | -0.050354 | -0.032043 | 0.09613 | 0.091553 | 0.050354 | 0.045776 | -0.077819 | -0.15106 | 0.21057 | 0.10986 | 0.091553 | 0.064087 | 0.045777 | 0.073242 | -121.9254 | -121.9391 | 0.21973 | 0.17395 | 0.21515 | 0.10071 | 0.14191 | 0.16479 | 121.8338 | 0.14648 | 0.018311 | 121.907 | 0.032043 | 121.9528 | 0.10528 | -121.9849 | -121.9574 | 121.8796 | 0.091553 | 0.3067 | 0.16479
2071.2188 | 122.0627 | -0.10529 | 121.8887 | -0.012131 | 0.00033758 | 0.055777 | 0.049597 | -0.0011237 | -0.010485 | -0.0008866 | -0.005371 | 0.028512 | 0.042635 | 0.0035205 | 0.015539 | 0.023751 | -0.00020725 | 0.17395 | 121.8338 | -0.082397 | 121.7606 | 0.11444 | -0.013733 | 0.013733 | 0.064087 | -0.045776 | -0.032043 | 0 | 0.11444 | 0.11444 | 0.091553 | 0.022889 | -0.054932 | -0.12817 | 0.21973 | 0.11902 | 0.091553 | 0.09613 | 0.068664 | 0.073243 | -121.9345 | -121.8887 | 0.21973 | 0.19684 | 0.21973 | 0.1236 | 0.14648 | 0.19684 | 121.843 | 0.14648 | 0.032043 | 121.9162 | -0.013733 | 121.9391 | 0.05951 | -121.9711 | -121.9208 | 121.8658 | 0.10529 | 0.27924 | 0.16937
2072.9844 | 122.0352 | -0.10071 | 121.8933 | -0.0045011 | 0.0043964 | 0.054282 | 0.052588 | 0.0022943 | -0.0070666 | -0.005159 | -0.0084228 | 0.030862 | 0.044558 | 0.0092883 | 0.01618 | 0.024605 | -0.0034117 | 0.073242 | 121.8658 | -0.07782 | 121.7102 | 0.059509 | -0.054932 | -0.036621 | 0.013733 | -0.041199 | -0.032043 | -0.018311 | 0.09613 | 0.068665 | 0.086975 | 0.022888 | -0.027466 | -0.18311 | 0.16022 | 0.064087 | 0.045776 | 0.041199 | 0.022888 | 0.068665 | -121.9345 | -121.9116 | 0.19684 | 0.18768 | 0.16937 | 0.11902 | 0.10071 | 0.13733 | 121.788 | 0.12817 | 0.013732 | 121.9437 | -0.009156 | 121.9666 | 0.059509 | -121.9711 | -121.9254 | 121.8109 | 0.082397 | 0.17395 | 0.11444
2074.7344 | 122.0581 | -0.10986 | 121.8796 | -0.012131 | 0.0014056 | 0.053854 | 0.048742 | -0.0013373 | -0.0064258 | -0.0032364 | -0.005371 | 0.028939 | 0.045198 | 0.0052295 | 0.015112 | 0.0261 | -0.0046933 | 0.068665 | 121.8475 | -0.082397 | 121.7102 | 0.050354 | -0.068665 | -0.036621 | 0.022888 | -0.022888 | -0.036621 | -0.004578 | 0.11444 | 0.09613 | 0.091553 | 0.027466 | -0.032044 | -0.16937 | 0.16022 | 0.073242 | 0.041198 | 0.045776 | 0.013732 | 0.073242 | -121.9025 | -121.8842 | 0.2243 | 0.20142 | 0.20599 | 0.12817 | 0.13275 | 0.13275 | 121.7926 | 0.15106 | 0.032043 | 121.9299 | 0.013733 | 121.9574 | 0.086975 | -121.962 | -121.9162 | 121.8201 | 0.10529 | 0.17853 | 0.13275
2076.4375 | 122.0032 | -0.13275 | 121.907 | -0.0045011 | 0.00055118 | 0.053214 | 0.054297 | 0.00079894 | -0.0089892 | -0.0038772 | -0.0084228 | 0.032998 | 0.044985 | 0.0075793 | 0.017889 | 0.025246 | 0.00043375 | 0.16022 | 121.8842 | -0.11444 | 121.6873 | -0.004578 | -0.10071 | -0.09613 | -0.041199 | -0.004578 | -0.054932 | -0.036621 | 0.059509 | 0.050354 | 0.059509 | 0.01831 | -0.022888 | -0.21973 | 0.12817 | 0.036621 | 0.032043 | 0.018311 | 0.013733 | 0.077819 | -121.9116 | -121.9437 | 0.19226 | 0.19226 | 0.18311 | 0.11444 | 0.10529 | 0.10986 | 121.8018 | 0.11444 | 0.018311 | 121.9986 | 0.050354 | 122.0169 | 0.12817 | -122.0215 | -121.962 | 121.8201 | 0.09613 | 0.29297 | 0.091552
2078.2031 | 122.0856 | -0.068665 | 121.843 | -0.0045011 | 0.0043964 | 0.055136 | 0.051947 | -0.0019781 | -0.0079212 | -0.0028092 | -0.005371 | 0.029794 | 0.04413 | 0.0039477 | 0.019384 | 0.02546 | -0.00084805 | 0.15106 | 121.8704 | -0.059509 | 121.7697 | 0.11902 | -0.032043 | -0.013733 | 0.082397 | -0.032043 | -0.022888 | 0.054932 | 0.15106 | 0.1236 | 0.13733 | 0.009156 | 0.027465 | -0.073243 | 0.18768 | 0.054932 | 0.036622 | 0.045776 | 0.027466 | 0.045777 | -121.875 | -121.788 | 0.21973 | 0.20599 | 0.19226 | 0.16022 | 0.14648 | 0.17853 | 121.8292 | 0.17395 | 0.07782 | 121.9299 | -0.009155 | 121.9391 | 0.036622 | -121.9025 | -121.8658 | 121.8384 | 0.1236 | 0.21973 | 0.15106
2079.9531 | 122.0352 | -0.09613 | 121.8842 | -0.01976 | 0.006319 | 0.057486 | 0.054083 | -0.00091006 | -0.0077074 | -3.1996e-05 | -0.005371 | 0.030862 | 0.042208 | 0.0090747 | 0.014471 | 0.024819 | -0.00042085 | 0.10071 | 121.8338 | -0.045776 | 121.7514 | 0.13275 | -0.027466 | 0 | 0.068665 | -0.036621 | -0.032043 | 0.032043 | 0.13275 | 0.10071 | 0.10071 | 0.050354 | -0.050354 | -0.13275 | 0.22888 | 0.09613 | 0.068664 | 0.045776 | 0.01831 | 0.064087 | -121.9208 | -121.8521 | 0.22888 | 0.19684 | 0.19684 | 0.13275 | 0.13275 | 0.17853 | 121.7972 | 0.16479 | 0.064086 | 121.8796 | -0.004578 | 121.9299 | 0.059509 | -121.9299 | -121.9162 | 121.8475 | 0.12817 | 0.19684 | 0.16479
2081.7031 | 122.0398 | -0.10529 | 121.8933 | -0.01976 | 0.0024738 | 0.05535 | 0.05216 | 0.0072077 | -0.0089892 | -0.00345 | -0.0084228 | 0.031076 | 0.04413 | 0.0099293 | 0.018102 | 0.024178 | -0.0049069 | 0.086975 | 121.8521 | -0.064087 | 121.7422 | 0.09613 | -0.050354 | -0.018311 | 0.064087 | -0.050354 | -0.050354 | 0.009155 | 0.09613 | 0.09613 | 0.086975 | 0.041199 | -0.041199 | -0.15106 | 0.20142 | 0.086975 | 0.054932 | 0.045776 | 0.013733 | 0.054932 | -121.9437 | -121.8842 | 0.20142 | 0.19226 | 0.20142 | 0.13733 | 0.14648 | 0.16022 | 121.8063 | 0.14648 | 0.059509 | 121.9162 | 0 | 121.9574 | 0.054932 | -121.9574 | -121.9437 | 121.8475 | 0.11444 | 0.19226 | 0.16937
2083.4062 | 121.9482 | -0.12817 | 121.9208 | -0.0045011 | 0.0052508 | 0.054282 | 0.056006 | 0.0012261 | -0.008562 | -0.0028092 | -0.005371 | 0.033853 | 0.042635 | 0.019969 | 0.017461 | 0.026314 | -0.0034117 | 0.1236 | 121.9254 | -0.11444 | 121.6644 | -0.032043 | -0.15106 | -0.13733 | -0.082397 | 0.009155 | -0.059509 | -0.10071 | -0.022888 | -0.032043 | 0.022888 | 0.013733 | 0.004578 | -0.25635 | 0.096131 | -0.009155 | -0.022888 | -0.022888 | -0.036621 | 0.068665 | -121.9116 | -122.0215 | 0.10529 | 0.15106 | 0.096131 | 0.082397 | 0.027466 | 0.082398 | 121.7789 | 0.036621 | -0.041199 | 122.0398 | 0.068664 | 122.0535 | 0.13733 | -122.0352 | -121.9803 | 121.7926 | 0.027466 | 0.25177 | 0.045777
2085.1719 | 121.9574 | -0.1236 | 121.9254 | -0.0045011 | 0.0056782 | 0.055563 | 0.054937 | -0.0019781 | -0.0070666 | -0.0002456 | -0.0084228 | 0.033212 | 0.044771 | 0.014202 | 0.018743 | 0.024819 | -0.0064023 | 0.13275 | 121.8979 | -0.09613 | 121.669 | -0.022888 | -0.15564 | -0.11902 | -0.091553 | -0.004578 | -0.054932 | -0.07782 | -0.004578 | -0.032043 | 0.022888 | 0.027466 | -0.027466 | -0.25635 | 0.10071 | 0.004577 | -0.032044 | -0.022889 | -0.05951 | 0.068664 | -121.9299 | -122.0032 | 0.11902 | 0.14648 | 0.091553 | 0.07782 | 0.022889 | 0.073242 | 121.7651 | 0.050354 | -0.022888 | 121.994 | 0.050354 | 122.0215 | 0.11902 | -122.0215 | -121.9803 | 121.7926 | 0.045776 | 0.25635 | 0.032043
2086.9375 | 122.0352 | -0.10986 | 121.9208 | -0.01976 | 0.0024738 | 0.053214 | 0.050879 | -0.0019781 | -0.0066394 | -0.002382 | -0.005371 | 0.030435 | 0.044771 | 0.0026661 | 0.014684 | 0.026314 | -0.0042661 | 0.059509 | 121.8613 | -0.064087 | 121.7194 | 0.059509 | -0.050354 | -0.036621 | 0.004578 | -0.036621 | -0.027466 | -0.009155 | 0.091553 | 0.082397 | 0.086975 | 0.045776 | -0.059509 | -0.20142 | 0.16937 | 0.073242 | 0.059509 | 0.027466 | 0.013733 | 0.082397 | -121.9574 | -121.9299 | 0.20142 | 0.19684 | 0.19226 | 0.11444 | 0.10986 | 0.1236 | 121.7834 | 0.11902 | 0.018311 | 121.9254 | -0.009155 | 121.9711 | 0.073242 | -121.9849 | -121.9482 | 121.8292 | 0.10071 | 0.16937 | 0.11444
2088.7031 | 122.049 | -0.082397 | 121.907 | -0.0045011 | 0.0043964 | 0.054495 | 0.05216 | -0.0021919 | -0.0094164 | -0.0004592 | -0.0023192 | 0.030221 | 0.04413 | 0.0037341 | 0.015966 | 0.027596 | -0.0021299 | 0.082397 | 121.8613 | -0.07782 | 121.7285 | 0.068665 | -0.054932 | -0.013733 | 0.018311 | -0.013733 | -0.032043 | 0 | 0.10071 | 0.091553 | 0.086975 | 0.004577 | -0.045776 | -0.17853 | 0.15106 | 0.068664 | 0.027465 | 0.064087 | 0.022888 | 0.050354 | -121.9208 | -121.907 | 0.18311 | 0.16937 | 0.17395 | 0.11902 | 0.1236 | 0.14649 | 121.8063 | 0.13275 | 0.032043 | 121.9391 | 0.01831 | 121.9437 | 0.068664 | -121.9849 | -121.9391 | 121.8109 | 0.082397 | 0.16479 | 0.10071
2090.3906 | 122.0078 | -0.12817 | 121.9025 | -0.01976 | 0.0035418 | 0.056204 | 0.054297 | 0.0012261 | -0.0081348 | -0.0038772 | -0.005371 | 0.032357 | 0.042849 | 0.0020251 | 0.018316 | 0.024178 | -0.0072569 | 0.1831 | 121.907 | -0.091553 | 121.7056 | 0.045776 | -0.07782 | -0.07782 | 0.009155 | -0.013733 | -0.050354 | -0.022888 | 0.068665 | 0.050354 | 0.073242 | 0.036621 | 0.004577 | -0.19684 | 0.17395 | 0.050354 | 0.050354 | 0.013733 | 0.013733 | 0.07782 | -121.9162 | -121.9254 | 0.19684 | 0.20142 | 0.17853 | 0.1236 | 0.10071 | 0.13733 | 121.7972 | 0.11902 | 0.027466 | 121.9986 | 0.036621 | 122.0352 | 0.11444 | -121.994 | -121.9528 | 121.8338 | 0.10529 | 0.31128 | 0.13733
2092.1406 | 122.1039 | -0.086975 | 121.8979 | -0.012131 | -0.00094422 | 0.052359 | 0.051306 | -0.0013373 | -0.011339 | -0.0038772 | -0.005371 | 0.030008 | 0.044344 | 0.0095019 | 0.013403 | 0.02546 | -0.0053343 | 0.1831 | 121.8658 | -0.068665 | 121.8155 | 0.16022 | 0.022888 | 0.041199 | 0.09613 | -0.045776 | -0.018311 | 0.036621 | 0.17853 | 0.17395 | 0.1236 | 0.01831 | -0.032043 | -0.082397 | 0.24719 | 0.12817 | 0.10986 | 0.10986 | 0.091553 | 0.068664 | -121.9437 | -121.8613 | 0.2655 | 0.21057 | 0.26092 | 0.14191 | 0.19226 | 0.22888 | 121.8842 | 0.19684 | 0.054932 | 121.9345 | -0.027465 | 121.9528 | 0.041199 | -121.9666 | -121.9162 | 121.9025 | 0.1236 | 0.27008 | 0.1831
2093.9062 | 121.9849 | -0.1236 | 121.907 | 0.0031279 | 0.0033282 | 0.058127 | 0.053228 | -5.5462e-05 | -0.0094164 | -0.0013138 | -0.0023192 | 0.033853 | 0.044558 | 0.0080067 | 0.017248 | 0.02546 | -0.0070433 | 0.1831 | 121.8979 | -0.091553 | 121.7148 | 0.027466 | -0.10986 | -0.091553 | -0.018311 | -0.004578 | -0.054932 | -0.054932 | 0.022888 | 0.009155 | 0.032043 | 0.032043 | -0.009155 | -0.19226 | 0.15106 | 0.032043 | 0.013733 | 0 | -0.01831 | 0.068664 | -121.9116 | -121.962 | 0.14648 | 0.15564 | 0.13275 | 0.086975 | 0.064087 | 0.11902 | 121.8063 | 0.07782 | 0 | 121.9894 | 0.050354 | 122.0215 | 0.11902 | -121.9986 | -121.962 | 121.8384 | 0.068664 | 0.3067 | 0.10528
2095.6719 | 122.0764 | -0.09613 | 121.8979 | -0.012131 | 0.0043964 | 0.053854 | 0.053015 | 0.0040033 | -0.0064258 | -0.0028092 | -0.005371 | 0.032571 | 0.04648 | 0.0080067 | 0.015752 | 0.025887 | -0.0049069 | 0.082397 | 121.8979 | -0.09613 | 121.6965 | 0.036621 | -0.10071 | -0.073242 | 0.009155 | -0.022888 | -0.041199 | 0.036621 | 0.11902 | 0.10071 | 0.10986 | 0 | 0 | -0.20142 | 0.13275 | 0.022888 | -0.004578 | 0.022888 | -0.004578 | 0.054931 | -121.9208 | -121.8613 | 0.21515 | 0.20599 | 0.19684 | 0.15106 | 0.14191 | 0.13275 | 121.7926 | 0.16022 | 0.07782 | 121.994 | 0.018311 | 121.994 | 0.073242 | -121.994 | -121.9391 | 121.7926 | 0.13275 | 0.17853 | 0.10528
2097.3594 | 121.994 | -0.11902 | 121.9025 | -0.012131 | 0.0052508 | 0.054068 | 0.051092 | 0.00037174 | -0.0066394 | -0.0062272 | -0.005371 | 0.033212 | 0.045412 | 0.0071521 | 0.017675 | 0.025887 | -0.0057615 | 0.086975 | 121.9025 | -0.11902 | 121.669 | -0.009155 | -0.13733 | -0.11902 | -0.041199 | 0.004578 | -0.064087 | -0.050354 | 0.045776 | 0.022888 | 0.045776 | 0 | 0 | -0.23346 | 0.10986 | 0 | -0.01831 | 0 | -0.01831 | 0.054932 | -121.8979 | -121.9528 | 0.16479 | 0.16479 | 0.14191 | 0.10986 | 0.086975 | 0.10986 | 121.788 | 0.10986 | 0.013733 | 122.0215 | 0.068665 | 122.0215 | 0.1236 | -122.0215 | -121.9666 | 121.788 | 0.068665 | 0.20599 | 0.07782
2099.125 | 122.0535 | -0.10529 | 121.9025 | -0.012131 | 0.0016192 | 0.053641 | 0.053015 | 0.0022943 | -0.010698 | -0.0030228 | -0.0023192 | 0.02958 | 0.043917 | 0.0024525 | 0.013403 | 0.026741 | -0.0010617 | 0.068665 | 121.8613 | -0.07782 | 121.7331 | 0.07782 | -0.059509 | -0.013733 | 0.013733 | -0.050354 | -0.032043 | -0.004578 | 0.086975 | 0.07782 | 0.086975 | 0.027466 | -0.041199 | -0.16937 | 0.18311 | 0.091553 | 0.045777 | 0.064087 | 0.018311 | 0.073243 | -121.9528 | -121.907 | 0.19226 | 0.19226 | 0.18311 | 0.11902 | 0.10986 | 0.15564 | 121.8109 | 0.11902 | 0.027465 | 121.9391 | -0.018311 | 121.9666 | 0.054932 | -121.9803 | -121.9345 | 121.8384 | 0.10071 | 0.17395 | 0.11902
2100.875 | 122.0901 | -0.07782 | 121.9025 | -0.0045011 | 0.00012398 | 0.053854 | 0.051092 | -0.00026906 | -0.008562 | -0.002382 | -0.005371 | 0.031076 | 0.043489 | 0.010356 | 0.01618 | 0.024819 | -0.0061887 | 0.15564 | 121.8796 | -0.059509 | 121.8018 | 0.17395 | 0.022888 | 0.041199 | 0.11444 | -0.050354 | -0.018311 | 0.036621 | 0.16022 | 0.16022 | 0.1236 | 0.018311 | -0.022888 | -0.10071 | 0.25177 | 0.11902 | 0.10071 | 0.10071 | 0.082397 | 0.059509 | -121.9528 | -121.8658 | 0.23804 | 0.20142 | 0.23804 | 0.14191 | 0.17853 | 0.23346 | 121.8613 | 0.17853 | 0.054932 | 121.9391 | -0.032043 | 121.9574 | 0.027466 | -121.962 | -121.9208 | 121.8796 | 0.11444 | 0.23346 | 0.19226
2102.5781 | 122.0398 | -0.11444 | 121.8979 | -0.01976 | 0.0033282 | 0.056845 | 0.055365 | -0.00069646 | -0.0083484 | -0.00345 | -0.005371 | 0.031289 | 0.044985 | 0.0082203 | 0.015539 | 0.0261 | -0.0034117 | 0.082397 | 121.9254 | -0.086975 | 121.6736 | 0.004578 | -0.14191 | -0.11444 | -0.027466 | -0.022888 | -0.050354 | -0.004578 | 0.059509 | 0.068665 | 0.068665 | 0.027466 | 0.027466 | -0.2243 | 0.11902 | 0 | -0.027466 | -0.027466 | -0.054932 | 0.064087 | -121.9208 | -121.9025 | 0.17395 | 0.18311 | 0.18311 | 0.11902 | 0.11902 | 0.091553 | 121.7606 | 0.10986 | 0.045776 | 122.0123 | 0.027466 | 122.0398 | 0.091553 | -121.9849 | -121.9482 | 121.788 | 0.10986 | 0.19684 | 0.086975
2104.3594 | 122.0901 | -0.082397 | 121.8933 | 0.0031279 | 0.0020466 | 0.054922 | 0.052374 | 0.00079894 | -0.0072802 | -0.0021682 | -0.0084228 | 0.029153 | 0.043703 | 0.0062977 | 0.015112 | 0.026528 | -0.0019163 | 0.10529 | 121.8658 | -0.07782 | 121.7743 | 0.10986 | -0.013733 | 0.022888 | 0.082397 | -0.041199 | -0.054932 | 0.045776 | 0.14648 | 0.14648 | 0.12817 | 0.004577 | -0.027466 | -0.11902 | 0.19226 | 0.10528 | 0.068664 | 0.10071 | 0.064087 | 0.027465 | -121.9345 | -121.8475 | 0.22888 | 0.21057 | 0.22888 | 0.18311 | 0.20142 | 0.18768 | 121.8521 | 0.20142 | 0.10071 | 121.9437 | 0.013733 | 121.9482 | 0.041198 | -121.9711 | -121.9482 | 121.8567 | 0.12817 | 0.18768 | 0.16479
2106.0625 | 122.081 | -0.10071 | 121.907 | -0.012131 | 0.002901 | 0.055136 | 0.051306 | 0.0012261 | -0.0059986 | -0.000673 | -0.0084228 | 0.030008 | 0.03879 | 0.0035205 | 0.013616 | 0.024178 | -0.0010617 | 0.086975 | 121.8704 | -0.07782 | 121.7194 | 0.059509 | -0.032043 | -0.018311 | 0.027466 | -0.032043 | -0.032043 | 0.004578 | 0.12817 | 0.10986 | 0.10071 | 0.022888 | -0.036621 | -0.18768 | 0.16022 | 0.082397 | 0.068665 | 0.059509 | 0.045777 | 0.068665 | -121.9391 | -121.9025 | 0.22888 | 0.20142 | 0.21057 | 0.13275 | 0.14191 | 0.13733 | 121.7972 | 0.16022 | 0.036621 | 121.9482 | 0 | 121.9711 | 0.068665 | -121.9849 | -121.9391 | 121.8201 | 0.10529 | 0.18768 | 0.12817
2107.8125 | 122.0169 | -0.1236 | 121.9345 | -0.012131 | 0.00076478 | 0.052573 | 0.053656 | 0.0025079 | -0.00963 | -0.0008866 | -0.005371 | 0.035348 | 0.043276 | 0.0082203 | 0.01618 | 0.024605 | -0.0051205 | 0.20142 | 121.907 | -0.10529 | 121.7148 | 0.004578 | -0.082397 | -0.059509 | -0.013733 | -0.004578 | -0.045776 | -0.032043 | 0.068665 | 0.045776 | 0.068665 | 0.01831 | -0.027466 | -0.21973 | 0.12817 | 0.064087 | 0.041199 | 0.045777 | 0.022889 | 0.07782 | -121.9391 | -121.9666 | 0.19226 | 0.19226 | 0.16937 | 0.11444 | 0.091552 | 0.10986 | 121.8201 | 0.11444 | 0.013733 | 122.0123 | 0.041198 | 122.0306 | 0.11902 | -122.0398 | -121.9803 | 121.8384 | 0.091553 | 0.32501 | 0.10986
2109.5 | 121.9894 | -0.12817 | 121.9437 | -0.0045011 | 0.00055118 | 0.055777 | 0.052374 | 0.0025079 | -0.0081348 | -0.001741 | -0.005371 | 0.033639 | 0.042635 | 0.0080067 | 0.015966 | 0.024605 | -0.0036253 | 0.086975 | 121.907 | -0.10986 | 121.6599 | -0.032043 | -0.16479 | -0.10986 | -0.086975 | 0 | -0.059509 | -0.064087 | 0.018311 | -0.009155 | 0.041199 | 0.018311 | -0.036622 | -0.28381 | 0.096131 | 0.018311 | -0.036621 | 0 | -0.054932 | 0.068665 | -121.9437 | -122.0078 | 0.14649 | 0.16937 | 0.11902 | 0.10071 | 0.050354 | 0.07782 | 121.7697 | 0.07782 | -0.004578 | 122.0169 | 0.059509 | 122.0352 | 0.12817 | -122.0535 | -122.0032 | 121.788 | 0.064087 | 0.21515 | 0.041199
2111.25 | 122.0901 | -0.082397 | 121.8933 | -0.012131 | 0.0014056 | 0.054068 | 0.050879 | -0.0036871 | -0.0087756 | -0.0019546 | 0.00073235 | 0.030435 | 0.044558 | 0.0015979 | 0.015325 | 0.024178 | -0.0066159 | 0.15564 | 121.8384 | -0.059509 | 121.7926 | 0.16022 | 0.036621 | 0.045776 | 0.10529 | -0.050354 | -0.018311 | 0.041199 | 0.17853 | 0.15564 | 0.10986 | 0.022888 | -0.054932 | -0.10071 | 0.24261 | 0.12817 | 0.11902 | 0.10528 | 0.09613 | 0.064086 | -121.9437 | -121.8521 | 0.26092 | 0.19226 | 0.23804 | 0.12817 | 0.17395 | 0.21973 | 121.8521 | 0.19684 | 0.05951 | 121.8979 | -0.032043 | 121.9208 | 0.032043 | -121.9528 | -121.9116 | 121.875 | 0.1236 | 0.23804 | 0.18768
2113 | 121.9986 | -0.1236 | 121.9116 | -0.012131 | 0.001192 | 0.054495 | 0.051306 | -0.0015509 | -0.0098438 | -0.0021682 | -0.011475 | 0.031076 | 0.044344 | 0.0035205 | 0.016393 | 0.026314 | 0.0010745 | 0.17395 | 121.8704 | -0.068665 | 121.7651 | 0.086975 | -0.013733 | -0.013733 | 0.018311 | -0.027466 | -0.045776 | -0.041199 | 0.07782 | 0.045776 | 0.041199 | 0.054931 | -0.041199 | -0.14648 | 0.21057 | 0.10986 | 0.10986 | 0.054932 | 0.054932 | 0.07782 | -121.9391 | -121.9528 | 0.20142 | 0.16479 | 0.16937 | 0.086975 | 0.091552 | 0.15564 | 121.8338 | 0.1236 | 0.004577 | 121.9391 | 0.01831 | 121.994 | 0.09613 | -121.9803 | -121.9574 | 121.8887 | 0.082397 | 0.29755 | 0.14191
2114.6875 | 122.0444 | -0.091553 | 121.8842 | -0.01976 | 0.0048236 | 0.054282 | 0.054937 | -0.0015509 | -0.006853 | -0.0060134 | -0.0023192 | 0.034066 | 0.044344 | 0.012493 | 0.016607 | 0.024391 | -0.00042085 | 0.086975 | 121.9345 | -0.10529 | 121.6919 | 0.009155 | -0.14648 | -0.091553 | -0.027466 | -0.009155 | -0.041199 | -0.004578 | 0.059509 | 0.041199 | 0.073242 | -0.013733 | 0.050354 | -0.19226 | 0.10071 | 0 | -0.054931 | 0.013733 | -0.041198 | 0.050354 | -121.8933 | -121.8887 | 0.15106 | 0.16479 | 0.13275 | 0.11444 | 0.082398 | 0.11444 | 121.7972 | 0.10071 | 0.036621 | 122.0398 | 0.032044 | 122.0261 | 0.082398 | -121.9894 | -121.9254 | 121.7834 | 0.086975 | 0.17853 | 0.064087
2116.4375 | 122.0078 | -0.11444 | 121.9162 | -0.01976 | 0.0043964 | 0.054709 | 0.05451 | -0.0013373 | -0.0087756 | -0.0008866 | -0.0023192 | 0.032571 | 0.043276 | 0.0092883 | 0.017461 | 0.026314 | -0.0029843 | 0.10071 | 121.9299 | -0.10529 | 121.6553 | -0.013733 | -0.13733 | -0.10986 | -0.054932 | -0.013733 | -0.050354 | -0.054932 | 0.009155 | 0 | 0.041199 | 0.009155 | 0.013733 | -0.26093 | 0.10071 | 0.004578 | -0.022888 | -0.004577 | -0.032043 | 0.064087 | -121.9299 | -121.9711 | 0.1236 | 0.15564 | 0.11444 | 0.091553 | 0.050354 | 0.091553 | 121.7606 | 0.059509 | -0.004578 | 122.0352 | 0.036621 | 122.0444 | 0.10071 | -122.0215 | -121.9666 | 121.7697 | 0.059509 | 0.21515 | 0.059509
2118.2031 | 122.0261 | -0.09613 | 121.9254 | -0.01976 | 0.0033282 | 0.057059 | 0.053015 | 0.0025079 | -0.008562 | -0.0043046 | -0.005371 | 0.034066 | 0.045626 | 0.0048023 | 0.01917 | 0.025032 | -0.0044797 | 0.1831 | 121.9208 | -0.07782 | 121.7148 | 0.045776 | -0.064087 | -0.059509 | 0.004578 | -0.013733 | -0.041199 | -0.027466 | 0.073242 | 0.064087 | 0.073242 | 0.01831 | -0.004578 | -0.21057 | 0.14191 | 0.036621 | 0.032043 | 0.018311 | 0.013733 | 0.054931 | -121.9391 | -121.9528 | 0.16937 | 0.16937 | 0.16022 | 0.11444 | 0.10529 | 0.1236 | 121.7926 | 0.11444 | 0.013733 | 121.9986 | 0.027466 | 122.0169 | 0.082397 | -122.0032 | -121.9666 | 121.8109 | 0.068664 | 0.27924 | 0.10071
2119.9531 | 122.0123 | -0.1236 | 121.9437 | -0.012131 | 0.002901 | 0.05535 | 0.05216 | 0.0054987 | -0.0059986 | -0.0019546 | -0.0084228 | 0.03428 | 0.043062 | 0.012493 | 0.020452 | 0.024391 | 0.00021995 | 0.15564 | 121.9162 | -0.1236 | 121.701 | 0 | -0.07782 | -0.073242 | -0.045776 | -0.018311 | -0.050354 | -0.050354 | 0.068665 | 0.050354 | 0.059509 | 0 | -0.027466 | -0.24262 | 0.1236 | 0.050354 | 0.045776 | 0.050354 | 0.045776 | 0.073242 | -121.962 | -121.994 | 0.19226 | 0.1831 | 0.17395 | 0.10986 | 0.10071 | 0.1236 | 121.8246 | 0.11902 | 0 | 122.0398 | 0.032043 | 122.0398 | 0.10528 | -122.0673 | -121.994 | 121.8246 | 0.073242 | 0.27924 | 0.07782
2121.7031 | 121.9894 | -0.13275 | 121.9162 | -0.0045011 | 0.0022602 | 0.055136 | 0.053869 | -0.0041145 | -0.0079212 | -0.0028092 | -0.005371 | 0.033639 | 0.044344 | 0.0088611 | 0.016393 | 0.027596 | -0.0038389 | 0.16479 | 121.9025 | -0.10071 | 121.6736 | 0.004578 | -0.09613 | -0.09613 | -0.091553 | 0 | -0.068665 | -0.068665 | 0.045776 | 0.013733 | 0.050354 | 0.032043 | -0.013733 | -0.24262 | 0.13733 | 0.036621 | 0.036621 | 0.004578 | 0.004578 | 0.064086 | -121.9162 | -121.9849 | 0.17853 | 0.18311 | 0.14648 | 0.11902 | 0.082398 | 0.10529 | 121.7743 | 0.11444 | 0 | 122.0032 | 0.068665 | 122.0352 | 0.13275 | -122.0169 | -121.9849 | 121.8063 | 0.064086 | 0.29755 | 0.041198
2123.4062 | 122.0535 | -0.086975 | 121.9116 | -0.01976 | 0.00076478 | 0.055136 | 0.048529 | 0.0025079 | -0.0087756 | -0.000673 | -0.005371 | 0.032571 | 0.04413 | 0.0026661 | 0.014043 | 0.025246 | -0.00042085 | 0.064087 | 121.8658 | -0.07782 | 121.7331 | 0.07782 | -0.050354 | -0.027466 | -0.018311 | -0.027466 | -0.027466 | -0.018311 | 0.10071 | 0.086975 | 0.068665 | 0.009155 | -0.045776 | -0.17853 | 0.16479 | 0.059509 | 0.036621 | 0.050354 | 0.027466 | 0.059509 | -121.9391 | -121.9299 | 0.18768 | 0.15564 | 0.17395 | 0.096131 | 0.11444 | 0.15564 | 121.8109 | 0.12817 | 0.009155 | 121.9437 | 0 | 121.9528 | 0.059509 | -121.9894 | -121.9391 | 121.8201 | 0.068664 | 0.15106 | 0.068664
2125.1562 | 122.0901 | -0.082397 | 121.9025 | -0.02739 | 0.0048236 | 0.056631 | 0.05451 | -0.0034735 | -0.0057848 | -0.0011002 | -0.005371 | 0.03193 | 0.045412 | 0.0026661 | 0.016821 | 0.026955 | -0.0021299 | 0.11444 | 121.9025 | -0.073242 | 121.756 | 0.086975 | -0.054932 | -0.013733 | 0.054932 | -0.041199 | -0.009155 | 0.036621 | 0.12817 | 0.10986 | 0.13275 | 0.009155 | 0 | -0.14648 | 0.16937 | 0.068664 | 0.027465 | 0.059509 | 0.01831 | 0.073242 | -121.9437 | -121.8658 | 0.21057 | 0.21515 | 0.19226 | 0.14191 | 0.11902 | 0.16022 | 121.8292 | 0.13733 | 0.045776 | 121.9757 | -0.032044 | 121.9849 | 0.041198 | -121.9757 | -121.9116 | 121.8384 | 0.11902 | 0.19684 | 0.13733
2126.9062 | 121.9803 | -0.13733 | 121.9391 | -0.012131 | 0.0043964 | 0.055777 | 0.053656 | 0.0029351 | -0.0089892 | -0.0030228 | -0.005371 | 0.035348 | 0.045198 | 0.0088611 | 0.017248 | 0.02546 | -0.0025571 | 0.10071 | 121.9345 | -0.091553 | 121.6553 | -0.036621 | -0.15564 | -0.11444 | -0.091553 | 0 | -0.045776 | -0.064087 | -0.004578 | -0.032043 | 0.036621 | 0.045776 | -0.004578 | -0.28381 | 0.10071 | 0.022888 | -0.018311 | -0.022888 | -0.064087 | 0.091553 | -121.9391 | -122.0032 | 0.13275 | 0.17395 | 0.10529 | 0.082397 | 0.013733 | 0.054932 | 121.7468 | 0.041198 | -0.018311 | 122.0261 | 0.045776 | 122.0718 | 0.13733 | -122.0306 | -121.9849 | 121.7926 | 0.073242 | 0.23804 | 0.045776
2128.6719 | 122.0078 | -0.12817 | 121.9391 | -0.01976 | -0.00051702 | 0.055991 | 0.050024 | -0.0013373 | -0.0079212 | -0.0025956 | -0.005371 | 0.030862 | 0.04413 | 0.0080067 | 0.015539 | 0.025887 | -0.0017027 | 0.16479 | 121.8887 | -0.064087 | 121.7422 | 0.073242 | -0.041199 | -0.018311 | -0.013733 | -0.009155 | -0.041199 | -0.064087 | 0.041199 | 0.045776 | 0.032043 | 0.064087 | -0.050354 | -0.19684 | 0.20142 | 0.10986 | 0.086975 | 0.045776 | 0.022888 | 0.086975 | -121.9482 | -122.0032 | 0.16937 | 0.16022 | 0.17395 | 0.073242 | 0.086975 | 0.13733 | 121.8063 | 0.082398 | -0.022888 | 121.9528 | 0.032044 | 122.0169 | 0.11902 | -122.0032 | -121.9803 | 121.8704 | 0.064087 | 0.29297 | 0.11444
2130.4375 | 121.9666 | -0.1236 | 121.9666 | -0.0045011 | -0.00094422 | 0.054068 | 0.052801 | -0.0047553 | -0.0098438 | -0.0021682 | -0.011475 | 0.034066 | 0.04114 | 0.0037341 | 0.015966 | 0.0261 | -0.0031979 | 0.12817 | 121.9254 | -0.09613 | 121.6782 | 0.009155 | -0.10071 | -0.07782 | -0.07782 | -0.004578 | -0.064087 | -0.10071 | 0.018311 | 0.004578 | 0.013733 | 0.027466 | -0.041199 | -0.28839 | 0.13275 | 0.045776 | 0.022888 | 0.01831 | -0.004578 | 0.059509 | -121.9711 | -122.0673 | 0.14191 | 0.13733 | 0.12817 | 0.07782 | 0.068665 | 0.10528 | 121.7743 | 0.082398 | -0.036621 | 122.0215 | 0.059509 | 122.049 | 0.11902 | -122.0627 | -122.0306 | 121.8018 | 0.022888 | 0.25177 | 0.045776
2132.1875 | 122.0627 | -0.086975 | 121.9254 | -0.01976 | 0.0037556 | 0.05535 | 0.050238 | 0.0012261 | -0.0092028 | -0.0013138 | -0.0023192 | 0.033212 | 0.043276 | 0.0030933 | 0.015325 | 0.026314 | -0.0036253 | 0.1831 | 121.8658 | -0.050354 | 121.8018 | 0.14648 | 0.013733 | 0.045776 | 0.059509 | -0.041199 | -0.018311 | 0.009155 | 0.14191 | 0.1236 | 0.10529 | 0.036621 | -0.059509 | -0.1236 | 0.23346 | 0.13275 | 0.10071 | 0.09613 | 0.064087 | 0.068664 | -121.9666 | -121.9162 | 0.22888 | 0.19226 | 0.21057 | 0.1236 | 0.14191 | 0.19684 | 121.8521 | 0.16022 | 0.027466 | 121.9162 | -0.022888 | 121.9528 | 0.045776 | -121.9757 | -121.9437 | 121.8887 | 0.09613 | 0.27008 | 0.14648
2133.9062 | 122.0627 | -0.091553 | 121.9208 | -0.02739 | -0.00073062 | 0.055563 | 0.051947 | -0.0049689 | -0.008562 | -0.0047318 | -0.0084228 | 0.032785 | 0.043489 | -0.00032473 | 0.014684 | 0.023964 | -0.0027707 | 0.082397 | 121.8521 | -0.059509 | 121.7377 | 0.059509 | -0.054932 | -0.018311 | 0.009155 | -0.022888 | -0.032043 | -0.022888 | 0.068665 | 0.07782 | 0.09613 | 0.032044 | -0.068664 | -0.1831 | 0.15106 | 0.073242 | 0.036621 | 0.041198 | 0.004577 | 0.05951 | -121.9437 | -121.9437 | 0.16022 | 0.18768 | 0.16937 | 0.12817 | 0.10986 | 0.11902 | 121.7972 | 0.10071 | 0.009155 | 121.9116 | 0.009155 | 121.9437 | 0.068665 | -121.9803 | -121.9528 | 121.8292 | 0.068665 | 0.17395 | 0.10071
2135.6719 | 122.0947 | -0.073242 | 121.8933 | 0.010757 | -0.0017986 | 0.057272 | 0.05152 | -0.00048286 | -0.0079212 | -0.0021682 | -0.0084228 | 0.032998 | 0.040499 | 0.0028797 | 0.01618 | 0.024178 | -0.0025571 | 0.086975 | 121.8475 | -0.07782 | 121.756 | 0.091553 | -0.027466 | 0.009155 | 0.045776 | -0.041199 | -0.018311 | 0.027466 | 0.14191 | 0.14648 | 0.12817 | -0.004578 | -0.045777 | -0.13733 | 0.16479 | 0.082397 | 0.045776 | 0.086975 | 0.050354 | 0.054931 | -121.9345 | -121.8658 | 0.21515 | 0.20142 | 0.21973 | 0.14649 | 0.16479 | 0.16937 | 121.8338 | 0.16022 | 0.045777 | 121.9254 | -0.022888 | 121.9208 | 0.032043 | -121.9711 | -121.9116 | 121.8292 | 0.10071 | 0.16022 | 0.11902
2137.4219 | 121.9803 | -0.11444 | 121.9528 | -0.012131 | 0.0041828 | 0.054922 | 0.053228 | -0.0013373 | -0.0087756 | 0.0003952 | -0.005371 | 0.038125 | 0.042208 | 0.0050159 | 0.018957 | 0.023964 | -0.0068295 | 0.19226 | 121.9025 | -0.073242 | 121.7194 | 0.018311 | -0.12817 | -0.082397 | -0.027466 | 0.004578 | -0.050354 | -0.07782 | 0.018311 | -0.022888 | 0.027466 | 0.041199 | -0.050354 | -0.23346 | 0.13275 | 0.032044 | -0.013733 | -0.009155 | -0.054932 | 0.064087 | -121.9482 | -122.0306 | 0.13275 | 0.14191 | 0.091553 | 0.07782 | 0.027466 | 0.091553 | 121.7926 | 0.068665 | -0.027466 | 121.9757 | 0.054932 | 122.0169 | 0.11902 | -122.0261 | -122.0032 | 121.8338 | 0.036621 | 0.3067 | 0.086975
2139.125 | 121.9757 | -0.11444 | 121.9299 | -0.01976 | 0.0024738 | 0.054282 | 0.052374 | 0.00058534 | -0.00963 | -0.0011002 | -0.0023192 | 0.035348 | 0.045626 | 0.0092883 | 0.017889 | 0.024819 | -0.0029843 | 0.13733 | 121.9116 | -0.10529 | 121.6736 | -0.018311 | -0.10071 | -0.10529 | -0.07782 | -0.009155 | -0.059509 | -0.10071 | 0.009155 | 0 | 0.013733 | 0.009155 | -0.018311 | -0.25635 | 0.09613 | 0.009155 | 0.013733 | 0 | 0.004578 | 0.054932 | -121.9391 | -122.0306 | 0.1236 | 0.12817 | 0.11444 | 0.073242 | 0.059509 | 0.086975 | 121.7789 | 0.068664 | -0.041199 | 122.0169 | 0.050354 | 122.0261 | 0.10529 | -122.0352 | -121.9894 | 121.788 | 0.013733 | 0.25177 | 0.036621
2140.8906 | 122.1039 | -0.073242 | 121.9025 | -0.012131 | 0.00461 | 0.055991 | 0.051947 | 0.0022943 | -0.0064258 | -0.0019546 | -0.005371 | 0.032357 | 0.043062 | 0.0050159 | 0.017034 | 0.024819 | -0.0036253 | 0.14191 | 121.8842 | -0.054932 | 121.788 | 0.11444 | -0.022888 | 0.013733 | 0.073242 | -0.041199 | -0.004578 | 0.050354 | 0.15106 | 0.10986 | 0.13733 | 0.01831 | -0.018311 | -0.11444 | 0.18768 | 0.086975 | 0.050354 | 0.068665 | 0.032044 | 0.068664 | -121.9437 | -121.8521 | 0.2243 | 0.21057 | 0.18311 | 0.14191 | 0.11444 | 0.16937 | 121.843 | 0.15564 | 0.054932 | 121.9391 | -0.036621 | 121.9574 | 0.032043 | -121.9574 | -121.907 | 121.8613 | 0.1236 | 0.21515 | 0.14648
2142.5781 | 122.0627 | -0.082397 | 121.9299 | -0.0045011 | 0.002901 | 0.055136 | 0.053015 | -0.00048286 | -0.0081348 | -0.0047318 | -0.0084228 | 0.03193 | 0.042635 | -0.0024609 | 0.016821 | 0.027382 | -0.0023435 | 0.091553 | 121.8979 | -0.054932 | 121.7285 | 0.064087 | -0.059509 | -0.013733 | 0.018311 | -0.027466 | -0.041199 | 0 | 0.09613 | 0.086975 | 0.086975 | 0.027465 | -0.032044 | -0.20142 | 0.14648 | 0.068664 | 0.022888 | 0.041199 | -0.004577 | 0.041198 | -121.9574 | -121.9299 | 0.17853 | 0.16937 | 0.16937 | 0.12817 | 0.12817 | 0.11902 | 121.7834 | 0.13733 | 0.041199 | 121.9528 | 0.013733 | 121.9803 | 0.054931 | -121.9849 | -121.9711 | 121.8109 | 0.082397 | 0.17395 | 0.10071
2144.3281 | 121.9757 | -0.13733 | 121.9528 | -0.012131 | -0.00094422 | 0.052786 | 0.053015 | -0.0019781 | -0.0087756 | -0.0032364 | -0.0084228 | 0.037057 | 0.044558 | 0.0039477 | 0.017034 | 0.024178 | -0.0029843 | 0.13733 | 121.9116 | -0.07782 | 121.6873 | 0.027466 | -0.09613 | -0.073242 | -0.059509 | 0.004578 | -0.054932 | -0.086975 | 0.018311 | 0.013733 | 0.027466 | 0.059509 | -0.041199 | -0.2655 | 0.16479 | 0.064087 | 0.041199 | 0.004578 | -0.01831 | 0.082397 | -121.9482 | -122.0398 | 0.15564 | 0.16479 | 0.15106 | 0.082398 | 0.068665 | 0.10529 | 121.7651 | 0.073243 | -0.032043 | 121.9894 | 0.05951 | 122.0489 | 0.14191 | -122.0306 | -122.0078 | 121.8246 | 0.050354 | 0.27466 | 0.07782
2146.1094 | 121.9986 | -0.10529 | 121.9528 | -0.01976 | 0.0014056 | 0.05535 | 0.05216 | -0.0030463 | -0.0070666 | -0.001741 | -0.005371 | 0.034066 | 0.043917 | 0.0041615 | 0.015966 | 0.024819 | -0.0010617 | 0.19226 | 121.8704 | -0.068665 | 121.7468 | 0.07782 | -0.022888 | -0.013733 | -0.004578 | -0.018311 | -0.050354 | -0.07782 | 0.054932 | 0.045776 | 0.032043 | 0.036621 | -0.082398 | -0.20599 | 0.18311 | 0.091553 | 0.082398 | 0.054932 | 0.045777 | 0.054932 | -121.9711 | -122.0306 | 0.16022 | 0.13733 | 0.15106 | 0.082397 | 0.09613 | 0.14649 | 121.8155 | 0.10529 | -0.027466 | 121.9391 | 0.032043 | 121.9757 | 0.086975 | -122.0215 | -122.0032 | 121.8521 | 0.027466 | 0.29755 | 0.10071
2147.8125 | 121.9849 | -0.10529 | 121.9299 | -0.01976 | 0.0048236 | 0.053854 | 0.054083 | 0.0020807 | -0.0081348 | -0.0019546 | -0.0084228 | 0.035134 | 0.045626 | 0.0058703 | 0.018102 | 0.02311 | -0.0061887 | 0.19684 | 121.8979 | -0.082397 | 121.7377 | 0.045776 | -0.082397 | -0.064087 | 0 | -0.009155 | -0.036621 | -0.045776 | 0.050354 | 0.027466 | 0.045776 | 0.022889 | -0.032044 | -0.19226 | 0.15106 | 0.041199 | 0.022889 | 0.01831 | 0 | 0.068665 | -121.9391 | -121.9757 | 0.15564 | 0.15106 | 0.13275 | 0.082397 | 0.064087 | 0.12817 | 121.8201 | 0.086975 | -0.009155 | 121.9803 | 0.027466 | 122.0032 | 0.096131 | -122.0123 | -121.9666 | 121.843 | 0.05951 | 0.30212 | 0.10529
2149.5781 | 122.1405 | -0.073242 | 121.8887 | -0.012131 | -8.9824e-05 | 0.054709 | 0.051092 | 0.00079894 | -0.0094164 | -0.0028092 | -0.011475 | 0.032144 | 0.043062 | 0.00052987 | 0.014898 | 0.025887 | -0.0044797 | 0.16022 | 121.8933 | -0.036621 | 121.8109 | 0.17853 | 0.032043 | 0.054932 | 0.1236 | -0.045776 | -0.009155 | 0.036621 | 0.17853 | 0.15564 | 0.11444 | 0.036621 | 0.004578 | -0.07782 | 0.25177 | 0.12817 | 0.10529 | 0.091553 | 0.068664 | 0.064087 | -121.9345 | -121.8521 | 0.25177 | 0.18768 | 0.22888 | 0.1236 | 0.16479 | 0.21515 | 121.8475 | 0.18768 | 0.045776 | 121.9299 | -0.036621 | 121.9666 | 0.027466 | -121.9254 | -121.8979 | 121.8842 | 0.10986 | 0.23346 | 0.19684
2151.3281 | 122.1268 | -0.068665 | 121.9162 | -0.0045011 | 0.00033758 | 0.053427 | 0.049811 | -0.0017645 | -0.0079212 | -0.0011002 | -0.0023192 | 0.03193 | 0.043489 | 0.0065113 | 0.015112 | 0.024819 | -0.0081113 | 0.14191 | 121.875 | -0.054932 | 121.7972 | 0.15106 | 0.027466 | 0.045776 | 0.11444 | -0.036621 | -0.022888 | 0.068665 | 0.18768 | 0.16479 | 0.13733 | 0.013733 | -0.041199 | -0.11902 | 0.21973 | 0.11444 | 0.096131 | 0.10071 | 0.082398 | 0.045777 | -121.9528 | -121.8475 | 0.25635 | 0.20599 | 0.23346 | 0.16022 | 0.18768 | 0.20599 | 121.8521 | 0.21057 | 0.091553 | 121.9299 | -0.013733 | 121.9437 | 0.032044 | -121.9711 | -121.9391 | 121.8658 | 0.13733 | 0.21057 | 0.18311
2153.0781 | 122.0673 | -0.07782 | 121.9025 | -0.0045011 | 0.00076478 | 0.053427 | 0.050879 | -0.00048286 | -0.010057 | -0.000673 | -0.005371 | 0.032357 | 0.042421 | 0.0095019 | 0.014684 | 0.023323 | -0.0040525 | 0.19226 | 121.8567 | -0.068665 | 121.7926 | 0.12817 | 0.022888 | 0.018311 | 0.054932 | -0.018311 | -0.027466 | 0.004578 | 0.13733 | 0.10986 | 0.09613 | 0.009155 | -0.045777 | -0.10986 | 0.20599 | 0.096131 | 0.10071 | 0.086976 | 0.091553 | 0.050354 | -121.9208 | -121.8979 | 0.21515 | 0.17395 | 0.18768 | 0.1236 | 0.13733 | 0.19684 | 121.8613 | 0.16479 | 0.032044 | 121.9254 | 0.009155 | 121.9345 | 0.059509 | -121.9711 | -121.9299 | 121.8704 | 0.082398 | 0.27008 | 0.13275
2154.8438 | 122.0627 | -0.082397 | 121.9116 | -0.01976 | 0.0016192 | 0.054068 | 0.052801 | 0.00015814 | -0.0062122 | -0.0004592 | -0.0023192 | 0.032144 | 0.043917 | 0.00010247 | 0.016393 | 0.024178 | -0.0042661 | 0.11444 | 121.8658 | -0.054932 | 121.7468 | 0.068665 | -0.059509 | -0.018311 | 0.027466 | -0.032043 | -0.032043 | -0.013733 | 0.09613 | 0.07782 | 0.07782 | 0.027465 | -0.045776 | -0.16479 | 0.15106 | 0.064086 | 0.022888 | 0.036621 | -0.004577 | 0.050354 | -121.9437 | -121.9254 | 0.17853 | 0.16022 | 0.16022 | 0.10986 | 0.10986 | 0.1236 | 121.8018 | 0.12817 | 0.01831 | 121.9208 | 0 | 121.9482 | 0.050354 | -121.9666 | -121.9437 | 121.8292 | 0.068664 | 0.19684 | 0.10986
2156.5312 | 122.0169 | -0.1236 | 121.9391 | -0.012131 | 0.0035418 | 0.055563 | 0.05451 | -0.00048286 | -0.0089892 | -0.0004592 | -0.0023192 | 0.035562 | 0.043276 | 0.010997 | 0.017889 | 0.025673 | -0.0036253 | 0.19226 | 121.9299 | -0.086975 | 121.7194 | 0.032043 | -0.086975 | -0.059509 | -0.004578 | -0.013733 | -0.045776 | -0.027466 | 0.068665 | 0.045776 | 0.073242 | 0.036621 | -0.009155 | -0.21973 | 0.15564 | 0.064087 | 0.036621 | 0.027466 | 0 | 0.07782 | -121.9528 | -121.9666 | 0.19226 | 0.19684 | 0.16937 | 0.11902 | 0.091552 | 0.11902 | 121.8063 | 0.11444 | 0.01831 | 122.0169 | 0.032043 | 122.0535 | 0.10986 | -122.0261 | -121.9849 | 121.843 | 0.09613 | 0.31586 | 0.11902
2158.2812 | 122.0947 | -0.073242 | 121.9208 | -0.01976 | 0.0035418 | 0.055777 | 0.049811 | -5.5462e-05 | -0.006853 | -0.0013138 | -0.0023192 | 0.030008 | 0.042635 | 0.0020251 | 0.01618 | 0.024178 | -0.0036253 | 0.1831 | 121.8658 | -0.050354 | 121.8063 | 0.16022 | 0.018311 | 0.041199 | 0.086975 | -0.045776 | 0.004578 | 0.045776 | 0.17395 | 0.13275 | 0.11444 | 0.022888 | -0.054931 | -0.11444 | 0.23346 | 0.11444 | 0.091553 | 0.091553 | 0.068665 | 0.07782 | -121.9666 | -121.875 | 0.24719 | 0.18768 | 0.20599 | 0.10986 | 0.12817 | 0.21057 | 121.8567 | 0.16937 | 0.041198 | 121.9162 | -0.050354 | 121.9391 | 0.027466 | -121.9711 | -121.9162 | 121.8796 | 0.11902 | 0.25635 | 0.16022
2160.0312 | 121.994 | -0.1236 | 121.9482 | 0.0031279 | 0.001833 | 0.052145 | 0.05152 | 0.0010125 | -0.0092028 | -0.0008866 | -0.0023192 | 0.034066 | 0.043276 | 0.0069385 | 0.014898 | 0.022255 | -0.0055479 | 0.15564 | 121.9116 | -0.10529 | 121.6736 | -0.009155 | -0.11444 | -0.09613 | -0.07782 | 0.004578 | -0.045776 | -0.068665 | 0.027466 | 0.004578 | 0.022888 | 0.01831 | -0.036621 | -0.27466 | 0.11444 | 0.027466 | 0.009155 | 0.009156 | -0.009155 | 0.07782 | -121.9437 | -122.0169 | 0.15106 | 0.14648 | 0.12817 | 0.068664 | 0.050354 | 0.096131 | 121.7789 | 0.073242 | -0.022889 | 122.0169 | 0.050354 | 122.0352 | 0.12817 | -122.0535 | -121.994 | 121.7972 | 0.054931 | 0.27924 | 0.045776
2161.7969 | 122.0261 | -0.11444 | 121.907 | -0.012131 | 0.0031146 | 0.055136 | 0.054083 | 0.0018671 | -0.0094164 | -0.0015274 | -0.0023192 | 0.032144 | 0.042421 | 0.0060841 | 0.01917 | 0.023323 | -0.0038389 | 0.09613 | 121.9208 | -0.091553 | 121.6919 | -0.004578 | -0.13275 | -0.091553 | -0.027466 | -0.004578 | -0.045776 | -0.027466 | 0.027466 | 0.018311 | 0.064087 | 0.022888 | 0.013733 | -0.21515 | 0.10986 | 0.022888 | -0.01831 | 0 | -0.041198 | 0.068665 | -121.9116 | -121.9345 | 0.14191 | 0.17853 | 0.13275 | 0.10986 | 0.064087 | 0.086975 | 121.7834 | 0.073242 | 0.01831 | 122.0123 | 0.041198 | 122.0352 | 0.10986 | -121.9986 | -121.9528 | 121.8063 | 0.086975 | 0.21057 | 0.086975
2163.5 | 122.1039 | -0.054932 | 121.8933 | -0.0045011 | 0.0020466 | 0.055563 | 0.053228 | 0.0040033 | -0.005144 | -0.000673 | -0.005371 | 0.033212 | 0.045198 | 0.0067249 | 0.018102 | 0.02546 | -0.0023435 | 0.10071 | 121.8979 | -0.073242 | 121.7422 | 0.064087 | -0.054932 | -0.054932 | 0.050354 | -0.032043 | -0.018311 | 0.041199 | 0.13275 | 0.091553 | 0.13275 | -0.01831 | 0.004577 | -0.15106 | 0.11902 | 0 | 0 | 0.01831 | 0.01831 | 0.036621 | -121.9254 | -121.8521 | 0.18768 | 0.18768 | 0.14649 | 0.15106 | 0.10986 | 0.13733 | 121.8155 | 0.15106 | 0.05951 | 121.9711 | -0.013732 | 121.9528 | 0.022889 | -121.9666 | -121.9116 | 121.7972 | 0.096131 | 0.15564 | 0.10529
2165.25 | 121.9757 | -0.12817 | 121.9482 | -0.012131 | 0.0041828 | 0.054709 | 0.053442 | 0.0012261 | -0.0072802 | -0.0019546 | -0.0084228 | 0.034494 | 0.042208 | 0.0067249 | 0.017461 | 0.025246 | -0.0031979 | 0.17853 | 121.9391 | -0.068665 | 121.701 | 0.009155 | -0.10529 | -0.09613 | -0.050354 | -0.004578 | -0.041199 | -0.068665 | 0.032043 | -0.013733 | 0.013733 | 0.059509 | -0.009155 | -0.24719 | 0.13733 | 0.032044 | 0.022888 | -0.027465 | -0.036621 | 0.086975 | -121.9528 | -122.0169 | 0.16022 | 0.14191 | 0.11444 | 0.054932 | 0.027466 | 0.07782 | 121.7697 | 0.073242 | -0.027466 | 122.0078 | 0.036621 | 122.0673 | 0.1236 | -122.0169 | -121.9894 | 121.8292 | 0.059509 | 0.3067 | 0.07782
2166.9531 | 122.049 | -0.082397 | 121.9254 | 0.0031279 | 0.0024738 | 0.054495 | 0.050879 | 0.00079894 | -0.00963 | 0.0001816 | -0.005371 | 0.032785 | 0.042208 | -0.0078015 | 0.01618 | 0.024819 | 6.346e-06 | 0.10986 | 121.8887 | -0.045776 | 121.7697 | 0.11902 | -0.041199 | -0.009155 | 0.064087 | -0.054932 | -0.013733 | 0.004578 | 0.10071 | 0.082397 | 0.086975 | 0.036621 | -0.036621 | -0.15564 | 0.20142 | 0.073242 | 0.041198 | 0.036621 | 0.004577 | 0.068664 | -121.9803 | -121.9208 | 0.18311 | 0.16937 | 0.16479 | 0.10071 | 0.09613 | 0.16479 | 121.8155 | 0.11444 | 0.018311 | 121.9345 | -0.041199 | 121.9711 | 0.027465 | -121.9711 | -121.9391 | 121.8521 | 0.086975 | 0.19226 | 0.14648
2168.7188 | 121.994 | -0.1236 | 121.9254 | -0.012131 | 0.0043964 | 0.057272 | 0.056219 | 0.0027215 | -0.0081348 | -0.001741 | -0.0084228 | 0.035775 | 0.044558 | -0.0016065 | 0.017889 | 0.025673 | -0.0027707 | 0.10986 | 121.9345 | -0.10071 | 121.6827 | -0.009155 | -0.14191 | -0.11444 | -0.045776 | -0.004578 | -0.045776 | -0.064087 | 0.018311 | 0 | 0.027466 | 0.022888 | 0.009155 | -0.24262 | 0.11444 | 0.009155 | -0.018311 | -0.013733 | -0.041199 | 0.07782 | -121.9299 | -121.9894 | 0.14191 | 0.15106 | 0.1236 | 0.073242 | 0.045776 | 0.091553 | 121.7834 | 0.064087 | -0.018311 | 122.0352 | 0.041198 | 122.0581 | 0.11902 | -122.0261 | -121.9711 | 121.8063 | 0.059509 | 0.23346 | 0.07782
2170.4688 | 121.9849 | -0.10986 | 121.9391 | -0.0045011 | 0.0022602 | 0.055777 | 0.051947 | 0.0022943 | -0.0074938 | -0.0036636 | -0.0023192 | 0.03428 | 0.044558 | 0.0056567 | 0.018316 | 0.026314 | -0.0014891 | 0.10986 | 121.9208 | -0.11444 | 121.669 | -0.032043 | -0.14191 | -0.09613 | -0.064087 | -0.032043 | -0.054932 | -0.054932 | 0.018311 | 0 | 0.041199 | -0.004578 | -0.018311 | -0.27008 | 0.07782 | 0.013733 | -0.032044 | 0.018311 | -0.027466 | 0.054931 | -121.9711 | -121.994 | 0.12817 | 0.15106 | 0.10986 | 0.096131 | 0.054932 | 0.082398 | 121.7834 | 0.073243 | 0 | 122.0352 | 0.022889 | 122.0306 | 0.07782 | -122.0535 | -121.994 | 121.7789 | 0.054931 | 0.21973 | 0.045776
2172.1562 | 122.1039 | -0.064087 | 121.9208 | -0.02739 | 0.0022602 | 0.056631 | 0.05216 | -5.5462e-05 | -0.0094164 | -0.0030228 | -0.0023192 | 0.031717 | 0.043489 | 0.0026661 | 0.01618 | 0.024178 | -0.0089659 | 0.16022 | 121.8796 | -0.036621 | 121.8063 | 0.13733 | 0.004578 | 0.045776 | 0.10529 | -0.041199 | -0.013733 | 0.050354 | 0.15106 | 0.1236 | 0.14191 | 0.027466 | -0.041198 | -0.11444 | 0.20142 | 0.10986 | 0.068665 | 0.082397 | 0.041199 | 0.050354 | -121.962 | -121.8704 | 0.21515 | 0.20599 | 0.18768 | 0.15564 | 0.13733 | 0.17395 | 121.843 | 0.16479 | 0.064087 | 121.9162 | -0.027466 | 121.9437 | 0.022888 | -121.9574 | -121.9345 | 121.8704 | 0.11444 | 0.2243 | 0.16937
2173.9219 | 122.0535 | -0.09613 | 121.9254 | -0.012131 | 0.00033758 | 0.055563 | 0.05152 | -0.0013373 | -0.0094164 | -0.0047318 | -0.005371 | 0.032571 | 0.043703 | -0.0037427 | 0.015752 | 0.026314 | -0.0036253 | 0.082397 | 121.8933 | -0.068665 | 121.7377 | 0.073242 | -0.041199 | -0.009155 | 0.004578 | -0.050354 | -0.027466 | -0.013733 | 0.091553 | 0.082397 | 0.07782 | 0.027465 | -0.032043 | -0.18768 | 0.16937 | 0.086975 | 0.054931 | 0.05951 | 0.027466 | 0.068664 | -121.9757 | -121.9391 | 0.18768 | 0.17395 | 0.17853 | 0.10529 | 0.10986 | 0.14191 | 121.8063 | 0.11902 | 0.013733 | 121.962 | -0.022888 | 121.9894 | 0.045776 | -121.994 | -121.9528 | 121.8338 | 0.082397 | 0.17853 | 0.10071
2175.6875 | 121.9803 | -0.12817 | 121.9711 | -0.0045011 | 0.001192 | 0.053641 | 0.052801 | 0.00079894 | -0.0098438 | -0.0028092 | -0.0023192 | 0.032785 | 0.04413 | 0.00095707 | 0.015539 | 0.024819 | -0.0038389 | 0.13733 | 121.9254 | -0.09613 | 121.7056 | 0.013733 | -0.09613 | -0.086975 | -0.064087 | 0.013733 | -0.032043 | -0.086975 | 0.027466 | 0.009155 | 0.018311 | 0.032044 | -0.045776 | -0.2655 | 0.14191 | 0.041199 | 0.032044 | 0.009155 | 0 | 0.096131 | -121.9574 | -122.0581 | 0.15564 | 0.14649 | 0.13733 | 0.050354 | 0.041198 | 0.10986 | 121.8018 | 0.059509 | -0.054932 | 122.0215 | 0.045776 | 122.0535 | 0.14191 | -122.0673 | -122.0032 | 121.8338 | 0.041199 | 0.2655 | 0.064087
2177.3906 | 122.0215 | -0.11902 | 121.9437 | -0.01976 | 0.001192 | 0.056418 | 0.053228 | -0.00069646 | -0.011339 | -0.002382 | -0.0023192 | 0.032571 | 0.044771 | 0.0099293 | 0.017889 | 0.02546 | -0.00063445 | 0.20142 | 121.9254 | -0.09613 | 121.7148 | 0.032043 | -0.064087 | -0.068665 | -0.022888 | 0.004578 | -0.050354 | -0.027466 | 0.082397 | 0.041199 | 0.073242 | 0.022889 | -0.018311 | -0.22888 | 0.15106 | 0.050354 | 0.054932 | 0.027465 | 0.032043 | 0.068665 | -121.9391 | -121.9711 | 0.20142 | 0.19226 | 0.16022 | 0.1236 | 0.091553 | 0.12817 | 121.8109 | 0.13275 | 0.022888 | 122.0215 | 0.054932 | 122.0444 | 0.1236 | -122.0398 | -121.994 | 121.8338 | 0.091553 | 0.32044 | 0.096131
2179.1719 | 121.9711 | -0.11444 | 121.9757 | -0.012131 | 0.0020466 | 0.055563 | 0.05216 | -0.0043281 | -0.0087756 | -0.0036636 | 0.00073235 | 0.034494 | 0.041353 | -0.0024609 | 0.017248 | 0.024178 | -0.0023435 | 0.14191 | 121.907 | -0.09613 | 121.6782 | 0 | -0.10529 | -0.09613 | -0.07782 | 0.004578 | -0.059509 | -0.086975 | 0.027466 | 0.004578 | 0.027466 | 0.018311 | -0.068665 | -0.29755 | 0.11444 | 0.018311 | 0.009155 | 0 | -0.009156 | 0.054932 | -121.9711 | -122.0627 | 0.14191 | 0.14191 | 0.11902 | 0.086975 | 0.064087 | 0.09613 | 121.7743 | 0.086975 | -0.027466 | 122.0032 | 0.064087 | 122.0215 | 0.11902 | -122.0718 | -122.0352 | 121.7926 | 0.027466 | 0.25635 | 0.036621
2180.9375 | 122.0032 | -0.10071 | 121.9711 | 0.0031279 | 0.002901 | 0.054495 | 0.054724 | 0.0031487 | -0.010057 | -0.0021682 | -0.0023192 | 0.033426 | 0.043062 | 0.0043751 | 0.016821 | 0.02546 | -0.0025571 | 0.20142 | 121.9162 | -0.07782 | 121.7285 | 0.059509 | -0.064087 | -0.050354 | -0.004578 | -0.004578 | -0.032043 | -0.032043 | 0.059509 | 0.041199 | 0.059509 | 0.022888 | -0.054931 | -0.24261 | 0.16022 | 0.050354 | 0.036621 | 0.027466 | 0.013733 | 0.068665 | -121.9757 | -122.0032 | 0.16022 | 0.16022 | 0.14191 | 0.091552 | 0.073242 | 0.13733 | 121.8063 | 0.091552 | 0 | 121.994 | 0.027465 | 122.0169 | 0.09613 | -122.049 | -122.0032 | 121.8292 | 0.068665 | 0.30212 | 0.09613
2182.625 | 122.0627 | -0.073242 | 121.9162 | -0.0045011 | 0.0043964 | 0.055777 | 0.05152 | 0.0025079 | -0.0079212 | -0.0036636 | -0.0023192 | 0.029794 | 0.042635 | 0.0060841 | 0.014257 | 0.023964 | -0.0051205 | 0.1236 | 121.8842 | -0.032043 | 121.7606 | 0.10071 | -0.032043 | 0.009155 | 0.045776 | -0.050354 | -0.022888 | 0 | 0.09613 | 0.10071 | 0.10071 | 0.041199 | -0.032044 | -0.15564 | 0.17395 | 0.082397 | 0.041199 | 0.041198 | 0 | 0.050354 | -121.9666 | -121.9162 | 0.16937 | 0.17395 | 0.17395 | 0.1236 | 0.1236 | 0.13275 | 121.7926 | 0.11902 | 0.022888 | 121.9162 | -0.027466 | 121.9574 | 0.022888 | -121.9482 | -121.9391 | 121.8338 | 0.073242 | 0.19684 | 0.11902
2184.375 | 121.9803 | -0.11444 | 121.9666 | -0.012131 | 0.0014056 | 0.055563 | 0.050451 | -0.0026191 | -0.0094164 | -0.0025956 | -0.005371 | 0.032144 | 0.043062 | 0.0092883 | 0.015325 | 0.022896 | -0.0031979 | 0.16022 | 121.8979 | -0.07782 | 121.701 | 0.041199 | -0.086975 | -0.068665 | -0.036621 | -0.009155 | -0.041199 | -0.082397 | 0.032043 | 0.013733 | 0.022888 | 0.036621 | -0.068665 | -0.2655 | 0.15564 | 0.045776 | 0.027466 | 0.009155 | -0.009155 | 0.073242 | -121.9757 | -122.049 | 0.14648 | 0.13733 | 0.12817 | 0.064087 | 0.054932 | 0.11902 | 121.7789 | 0.073242 | -0.041198 | 121.9757 | 0.032044 | 122.0123 | 0.10529 | -122.0444 | -122.0078 | 121.8155 | 0.032044 | 0.27466 | 0.07782
2186.0781 | 122.0993 | -0.091553 | 121.9116 | -0.012131 | -0.0013714 | 0.054495 | 0.051733 | -0.0013373 | -0.0083484 | -0.0030228 | -0.0084228 | 0.030648 | 0.045198 | 0.0056567 | 0.015752 | 0.026528 | -0.0036253 | 0.09613 | 121.8842 | -0.054932 | 121.7514 | 0.082397 | -0.036621 | 0 | 0.027466 | -0.036621 | -0.041199 | 0 | 0.12817 | 0.1236 | 0.11444 | 0.036621 | -0.027466 | -0.16022 | 0.17395 | 0.091553 | 0.054932 | 0.054932 | 0.018311 | 0.050354 | -121.9482 | -121.9116 | 0.21973 | 0.20599 | 0.21515 | 0.15564 | 0.16479 | 0.13733 | 121.8063 | 0.16937 | 0.041199 | 121.9391 | 0.004578 | 121.9757 | 0.054932 | -121.9666 | -121.9528 | 121.843 | 0.091553 | 0.18768 | 0.11902
2187.8281 | 121.994 | -0.10529 | 121.9574 | -0.012131 | 0.0043964 | 0.05535 | 0.05451 | 0.0016535 | -0.0081348 | -0.0028092 | -0.005371 | 0.033212 | 0.041994 | 0.0071521 | 0.016821 | 0.025673 | -0.0014891 | 0.11902 | 121.9345 | -0.10071 | 121.6782 | -0.018311 | -0.11902 | -0.11444 | -0.050354 | -0.004578 | -0.041199 | -0.045776 | 0.018311 | -0.004578 | 0.054932 | 0.004578 | -0.022888 | -0.27923 | 0.086975 | -0.009155 | -0.013733 | -0.013733 | -0.018311 | 0.064087 | -121.962 | -122.0032 | 0.1236 | 0.16022 | 0.10071 | 0.096131 | 0.036621 | 0.082397 | 121.7789 | 0.05951 | -0.004577 | 122.0352 | 0.036621 | 122.0398 | 0.10071 | -122.0581 | -121.9986 | 121.7834 | 0.05951 | 0.22431 | 0.054932
2189.6094 | 122.0032 | -0.11902 | 121.9528 | -0.0045011 | 0.00076478 | 0.054922 | 0.051733 | -0.0011237 | -0.0092028 | -0.002382 | -0.005371 | 0.033426 | 0.043703 | 0.0071521 | 0.017461 | 0.024178 | -0.0027707 | 0.16937 | 121.9208 | -0.091553 | 121.6736 | 0.009155 | -0.10986 | -0.10071 | -0.068665 | 0.009155 | -0.059509 | -0.082397 | 0.027466 | 0.018311 | 0.045776 | 0.027466 | -0.032044 | -0.27924 | 0.12817 | 0.018311 | 0.009156 | -0.009155 | -0.01831 | 0.05951 | -121.9437 | -122.0352 | 0.14649 | 0.16479 | 0.13733 | 0.10528 | 0.07782 | 0.10071 | 121.7651 | 0.086975 | -0.022888 | 122.0123 | 0.068664 | 122.0398 | 0.12817 | -122.0444 | -122.0123 | 121.7926 | 0.036622 | 0.28839 | 0.050354
2191.2969 | 122.049 | -0.10529 | 121.9162 | -0.012131 | 0.00033758 | 0.053427 | 0.049597 | 0.0018671 | -0.010912 | -0.0002456 | -0.0084228 | 0.032998 | 0.043276 | 0.00095707 | 0.014471 | 0.026314 | -0.0021299 | 0.20142 | 121.8658 | -0.064087 | 121.8063 | 0.13733 | 0.018311 | 0.032043 | 0.050354 | -0.032043 | -0.022888 | -0.009155 | 0.11902 | 0.10529 | 0.07782 | 0.041199 | -0.050354 | -0.10986 | 0.24262 | 0.13733 | 0.1236 | 0.09613 | 0.082398 | 0.082398 | -121.9482 | -121.9254 | 0.22431 | 0.18311 | 0.21057 | 0.10071 | 0.12817 | 0.20142 | 121.8704 | 0.14191 | 0.013733 | 121.9299 | -0.009155 | 121.9711 | 0.073243 | -121.9803 | -121.9391 | 121.9116 | 0.096131 | 0.3067 | 0.15564
2193.0469 | 122.0673 | -0.086975 | 121.9391 | -0.0045011 | 0.001833 | 0.054495 | 0.05152 | 0.0012261 | -0.0094164 | -0.002382 | -0.005371 | 0.029794 | 0.043276 | 0.0062977 | 0.015966 | 0.025673 | -0.0042661 | 0.10529 | 121.9025 | -0.064087 | 121.7422 | 0.064087 | -0.041199 | -0.013733 | 0.018311 | -0.036621 | -0.018311 | -0.018311 | 0.10071 | 0.091553 | 0.082397 | 0.022888 | -0.036621 | -0.19684 | 0.15106 | 0.073242 | 0.045776 | 0.050354 | 0.022888 | 0.068664 | -121.9757 | -121.9574 | 0.18768 | 0.16937 | 0.17853 | 0.10071 | 0.10986 | 0.12817 | 121.8063 | 0.11902 | 0 | 121.9666 | -0.01831 | 121.9894 | 0.050354 | -122.0032 | -121.9574 | 121.8292 | 0.068664 | 0.19226 | 0.10529
2194.8281 | 121.9894 | -0.13275 | 121.962 | -0.01976 | 0.00461 | 0.054922 | 0.055365 | 0.0014397 | -0.0066394 | -0.0015274 | -0.0084228 | 0.033426 | 0.04648 | 0.0024525 | 0.017461 | 0.023537 | -0.0040525 | 0.11444 | 121.9391 | -0.073242 | 121.6553 | -0.027466 | -0.15564 | -0.11444 | -0.054932 | 0.013733 | -0.050354 | -0.068665 | 0 | -0.009155 | 0.018311 | 0.059509 | -0.022888 | -0.3067 | 0.10529 | 0.01831 | -0.022889 | -0.041199 | -0.082398 | 0.082397 | -121.9482 | -122.0306 | 0.13275 | 0.15106 | 0.1236 | 0.068665 | 0.041199 | 0.045776 | 121.7285 | 0.050354 | -0.018311 | 122.0123 | 0.064087 | 122.0718 | 0.14648 | -122.0352 | -122.0123 | 121.788 | 0.064086 | 0.24719 | 0.077819
2196.5312 | 122.113 | -0.07782 | 121.907 | -0.012131 | 0.0041828 | 0.056845 | 0.051947 | -5.5462e-05 | -0.0079212 | -0.0019546 | -0.005371 | 0.03193 | 0.045198 | 0.0067249 | 0.015966 | 0.026528 | -0.0038389 | 0.1831 | 121.8979 | -0.041199 | 121.8063 | 0.14648 | -0.013733 | 0.018311 | 0.10986 | -0.059509 | -0.009155 | 0.059509 | 0.14191 | 0.13733 | 0.1236 | 0.036621 | -0.009155 | -0.10071 | 0.2243 | 0.096131 | 0.064087 | 0.05951 | 0.027466 | 0.068665 | -121.9666 | -121.8475 | 0.21973 | 0.20142 | 0.21515 | 0.13275 | 0.14648 | 0.18768 | 121.8475 | 0.15106 | 0.068664 | 121.9391 | -0.050354 | 121.9757 | 0.018311 | -121.9482 | -121.9162 | 121.8842 | 0.13733 | 0.26092 | 0.18768
2198.2812 | 122.0352 | -0.12817 | 121.9482 | -0.01976 | 0.0058918 | 0.055991 | 0.053442 | -0.0015509 | -0.0072802 | -0.0047318 | -0.005371 | 0.033853 | 0.043062 | 0.0035205 | 0.017461 | 0.026314 | -0.0040525 | 0.1236 | 121.9482 | -0.086975 | 121.6827 | 0.013733 | -0.12817 | -0.07782 | -0.050354 | -0.004578 | -0.041199 | -0.032043 | 0.050354 | 0.013733 | 0.050354 | 0.041199 | 0 | -0.2655 | 0.14191 | 0.050354 | 0 | 0.009155 | -0.041199 | 0.086975 | -121.9528 | -121.9803 | 0.17853 | 0.17853 | 0.14191 | 0.091553 | 0.054932 | 0.10071 | 121.7697 | 0.091553 | 0.009156 | 122.0352 | 0.036621 | 122.0764 | 0.1236 | -122.0352 | -121.9894 | 121.8109 | 0.096131 | 0.25177 | 0.07782
2200.0469 | 122.0764 | -0.10071 | 121.9299 | -0.012131 | 0.0014056 | 0.054495 | 0.051947 | -0.0051825 | -0.0094164 | -0.0011002 | -0.011475 | 0.031717 | 0.045198 | 0.0045887 | 0.015112 | 0.024391 | -0.0021299 | 0.10071 | 121.8842 | -0.07782 | 121.7468 | 0.07782 | -0.064087 | -0.022888 | 0.027466 | -0.050354 | -0.022888 | -0.009155 | 0.1236 | 0.11902 | 0.091553 | 0.022888 | -0.045777 | -0.18311 | 0.17853 | 0.07782 | 0.036621 | 0.054932 | 0.013733 | 0.07782 | -121.9803 | -121.9391 | 0.2243 | 0.19226 | 0.21973 | 0.11444 | 0.14191 | 0.15564 | 121.8246 | 0.14648 | 0.013733 | 121.962 | -0.027466 | 121.9849 | 0.050354 | -122.0078 | -121.9528 | 121.8475 | 0.091553 | 0.20142 | 0.12817
2201.8125 | 122.0398 | -0.10986 | 121.9391 | -0.012131 | 0.002901 | 0.057272 | 0.054297 | 0.0012261 | -0.0087756 | -0.0021682 | -0.0023192 | 0.035562 | 0.044558 | 0.0024525 | 0.01917 | 0.025246 | -0.0038389 | 0.21057 | 121.9162 | -0.086975 | 121.7468 | 0.064087 | -0.059509 | -0.036621 | 0.022888 | -0.009155 | -0.041199 | -0.009155 | 0.07782 | 0.050354 | 0.064087 | 0.022888 | -0.022888 | -0.19226 | 0.17395 | 0.073242 | 0.050354 | 0.050354 | 0.027466 | 0.068664 | -121.9482 | -121.9482 | 0.18768 | 0.17395 | 0.16022 | 0.10529 | 0.091553 | 0.15106 | 121.8338 | 0.11902 | 0.032044 | 122.0032 | 0.032044 | 122.0261 | 0.10071 | -122.0261 | -121.9803 | 121.8567 | 0.10071 | 0.32043 | 0.13275
2203.5156 | 121.9894 | -0.1236 | 121.9666 | -0.0045011 | 0.0037556 | 0.055136 | 0.052374 | 0.0020807 | -0.0094164 | -0.0030228 | -0.0023192 | 0.034494 | 0.045198 | 0.0035205 | 0.015539 | 0.025246 | -0.0070433 | 0.16022 | 121.9574 | -0.091553 | 121.6736 | -0.009155 | -0.09613 | -0.09613 | -0.07782 | -0.018311 | -0.045776 | -0.073242 | 0.013733 | 0.009155 | 0.027466 | 0.032043 | -0.009156 | -0.29297 | 0.11444 | 0.027466 | 0.027466 | -0.004577 | -0.004577 | 0.07782 | -121.9849 | -122.0398 | 0.13733 | 0.15106 | 0.13275 | 0.073242 | 0.054931 | 0.082398 | 121.7651 | 0.059509 | -0.027466 | 122.049 | 0.027465 | 122.081 | 0.10528 | -122.0581 | -122.0123 | 121.7972 | 0.050354 | 0.28381 | 0.045776
2205.2656 | 122.0306 | -0.1236 | 121.9391 | 0.0031279 | 0.0022602 | 0.057486 | 0.052374 | -0.0013373 | -0.0077074 | -0.0028092 | -0.0023192 | 0.034494 | 0.043276 | 0.0099293 | 0.017461 | 0.025673 | -0.00020725 | 0.22888 | 121.9208 | -0.091553 | 121.7331 | 0.045776 | -0.059509 | -0.032043 | 0.013733 | -0.009155 | -0.027466 | -0.013733 | 0.064087 | 0.045776 | 0.068665 | 0.032043 | -0.018311 | -0.20599 | 0.16937 | 0.091553 | 0.064087 | 0.05951 | 0.032044 | 0.09613 | -121.9482 | -121.9528 | 0.18768 | 0.19226 | 0.16937 | 0.096131 | 0.073242 | 0.13733 | 121.8246 | 0.091553 | 0.013733 | 122.0123 | 0.018311 | 122.0444 | 0.11444 | -122.0306 | -121.9666 | 121.8567 | 0.10986 | 0.35248 | 0.13733
2207.0312 | 122.0535 | -0.09613 | 121.9116 | -0.0045011 | 0.0039692 | 0.056418 | 0.049811 | -0.00048286 | -0.0070666 | -0.0021682 | -0.005371 | 0.030435 | 0.042849 | -0.00053833 | 0.015752 | 0.024819 | -0.0036253 | 0.11444 | 121.8933 | -0.050354 | 121.7606 | 0.10071 | -0.045776 | -0.009155 | 0.054932 | -0.032043 | -0.036621 | -0.004578 | 0.09613 | 0.10071 | 0.086975 | 0.045776 | -0.01831 | -0.15106 | 0.19684 | 0.086975 | 0.050354 | 0.041199 | 0.004578 | 0.059509 | -121.9437 | -121.9162 | 0.19226 | 0.1831 | 0.19684 | 0.1236 | 0.13733 | 0.15106 | 121.8109 | 0.13275 | 0.032043 | 121.9437 | 0.004578 | 121.9894 | 0.064087 | -121.962 | -121.9482 | 121.8567 | 0.091552 | 0.21057 | 0.15106
2208.7969 | 122.0764 | -0.068665 | 121.9528 | -0.012131 | -8.9824e-05 | 0.054068 | 0.051092 | 0.0012261 | -0.0087756 | -0.0008866 | -0.005371 | 0.02958 | 0.04178 | 0.0033069 | 0.015325 | 0.02546 | 6.346e-06 | 0.20599 | 121.8796 | -0.050354 | 121.8018 | 0.14191 | 0.027466 | 0.050354 | 0.086975 | -0.041199 | -0.027466 | 0.022888 | 0.13733 | 0.12817 | 0.10986 | 0.018311 | -0.073242 | -0.15106 | 0.21057 | 0.11902 | 0.096131 | 0.10071 | 0.07782 | 0.041199 | -121.994 | -121.9299 | 0.20599 | 0.17853 | 0.19684 | 0.13733 | 0.15564 | 0.19226 | 121.8521 | 0.16479 | 0.050354 | 121.9299 | -0.013733 | 121.9482 | 0.027466 | -122.0032 | -121.9803 | 121.8704 | 0.091553 | 0.27466 | 0.15564
2210.5 | 122.0901 | -0.086975 | 121.9299 | -0.012131 | 0.0024738 | 0.054068 | 0.049811 | -0.0024055 | -0.0094164 | -0.001741 | -0.005371 | 0.030221 | 0.041994 | -0.00096553 | 0.01618 | 0.025246 | 0.00021995 | 0.1236 | 121.8979 | -0.068665 | 121.7422 | 0.068665 | -0.041199 | -0.013733 | 0.022888 | -0.018311 | -0.032043 | 0 | 0.1236 | 0.10529 | 0.10071 | 0.01831 | -0.032044 | -0.18768 | 0.15564 | 0.073242 | 0.045776 | 0.054932 | 0.027466 | 0.054932 | -121.9482 | -121.9299 | 0.21057 | 0.18768 | 0.19226 | 0.13275 | 0.13733 | 0.13733 | 121.8109 | 0.15564 | 0.032043 | 121.9666 | 0.013732 | 121.9849 | 0.068664 | -121.9986 | -121.962 | 121.8292 | 0.086975 | 0.21057 | 0.10986
2212.2656 | 122.0627 | -0.10071 | 121.9528 | -0.01976 | 0.001833 | 0.054282 | 0.052588 | 0.0014397 | -0.0066394 | -0.0025956 | -0.0084228 | 0.030862 | 0.044558 | 0.0033069 | 0.015112 | 0.02311 | -0.0046933 | 0.11444 | 121.8933 | -0.050354 | 121.7468 | 0.068665 | -0.054932 | -0.013733 | 0.018311 | -0.032043 | -0.027466 | -0.013733 | 0.09613 | 0.07782 | 0.086975 | 0.050354 | -0.059509 | -0.20599 | 0.16937 | 0.086975 | 0.045776 | 0.036621 | -0.004578 | 0.073242 | -121.9849 | -121.9666 | 0.19684 | 0.18768 | 0.17853 | 0.11444 | 0.10529 | 0.11902 | 121.7972 | 0.1236 | 0.013733 | 121.9437 | -0.004577 | 121.994 | 0.068665 | -122.0032 | -121.9803 | 121.8475 | 0.086975 | 0.21515 | 0.11902
2214.0312 | 122.1085 | -0.059509 | 121.9299 | -0.035019 | 0.002901 | 0.055136 | 0.053656 | -0.00048286 | -0.0083484 | -0.0028092 | -0.005371 | 0.032357 | 0.045839 | 0.0099293 | 0.014257 | 0.02546 | -0.0055479 | 0.16479 | 121.8933 | -0.032043 | 121.8246 | 0.13733 | -0.009155 | 0.022888 | 0.13733 | -0.050354 | -0.004578 | 0.045776 | 0.15106 | 0.1236 | 0.1236 | 0.027466 | -0.036621 | -0.10529 | 0.19684 | 0.082397 | 0.050354 | 0.054931 | 0.022888 | 0.054931 | -121.9803 | -121.8842 | 0.21057 | 0.1831 | 0.1831 | 0.12817 | 0.12817 | 0.16937 | 121.8567 | 0.15564 | 0.050354 | 121.9254 | -0.045776 | 121.9528 | 0.009155 | -121.962 | -121.9345 | 121.8842 | 0.10528 | 0.2243 | 0.19684
2215.75 | 122.0673 | -0.064087 | 121.9025 | -0.012131 | 0.0026874 | 0.056418 | 0.053656 | -0.00048286 | -0.0077074 | -0.0004592 | -0.005371 | 0.032571 | 0.044771 | 0.012279 | 0.015752 | 0.024391 | -0.0027707 | 0.14648 | 121.875 | -0.050354 | 121.7926 | 0.12817 | -0.032043 | 0.032043 | 0.091553 | -0.041199 | -0.013733 | 0.022888 | 0.10986 | 0.091553 | 0.10071 | 0.013733 | -0.027466 | -0.10986 | 0.19226 | 0.09613 | 0.032044 | 0.082397 | 0.018311 | 0.050354 | -121.9437 | -121.8796 | 0.17395 | 0.1648 | 0.15564 | 0.11444 | 0.10529 | 0.17853 | 121.843 | 0.1236 | 0.036621 | 121.9254 | -0.027466 | 121.9391 | 0.022888 | -121.9528 | -121.9162 | 121.8567 | 0.086975 | 0.21057 | 0.15564
2217.5 | 122.1085 | -0.064087 | 121.9208 | -0.01976 | 0.0024738 | 0.056845 | 0.053015 | -0.0045417 | -0.005144 | -0.0008866 | -0.005371 | 0.032785 | 0.043489 | 0.00095707 | 0.01618 | 0.025887 | -0.0023435 | 0.16022 | 121.8933 | -0.064087 | 121.8109 | 0.12817 | -0.009155 | 0.018311 | 0.091553 | -0.041199 | 0 | 0.064087 | 0.13733 | 0.1236 | 0.13733 | 0 | -0.027465 | -0.10986 | 0.19226 | 0.082398 | 0.054932 | 0.082398 | 0.054932 | 0.064087 | -121.962 | -121.8567 | 0.20142 | 0.20142 | 0.18768 | 0.13733 | 0.1236 | 0.19226 | 121.875 | 0.13733 | 0.064087 | 121.9574 | -0.041199 | 121.9574 | 0.022888 | -121.9849 | -121.9208 | 121.875 | 0.12817 | 0.2243 | 0.15564
2219.2656 | 122.0947 | -0.10071 | 121.9299 | -0.012131 | 0.00076478 | 0.054282 | 0.050238 | 0.00037174 | -0.010698 | -0.0019546 | -0.0023192 | 0.031289 | 0.04413 | 0.0045887 | 0.015539 | 0.025246 | -0.0031979 | 0.13275 | 121.8933 | -0.059509 | 121.7606 | 0.07782 | -0.036621 | 0.004578 | 0.041199 | -0.027466 | -0.036621 | 0 | 0.13275 | 0.1236 | 0.10986 | 0.041199 | -0.036621 | -0.16937 | 0.17853 | 0.10529 | 0.064087 | 0.064087 | 0.022888 | 0.064087 | -121.9574 | -121.9299 | 0.23346 | 0.21057 | 0.2243 | 0.14648 | 0.16022 | 0.13733 | 121.8201 | 0.16937 | 0.036621 | 121.9528 | 0.009155 | 121.994 | 0.073242 | -121.9894 | -121.9666 | 121.8613 | 0.10071 | 0.23346 | 0.14191
2220.9844 | 122.0993 | -0.073242 | 121.8933 | -0.012131 | 0.002901 | 0.053641 | 0.052801 | -0.0034735 | -0.0092028 | -0.00345 | -0.005371 | 0.033212 | 0.043276 | 0.014415 | 0.017675 | 0.025032 | -0.0034117 | 0.17395 | 121.8796 | -0.059509 | 121.8109 | 0.1236 | -0.004578 | 0.032043 | 0.11444 | -0.022888 | -0.004578 | 0.059509 | 0.15564 | 0.13275 | 0.11902 | 0.013733 | -0.013733 | -0.082398 | 0.19684 | 0.10529 | 0.068664 | 0.091552 | 0.054931 | 0.068664 | -121.9162 | -121.8338 | 0.22888 | 0.19226 | 0.20599 | 0.1236 | 0.13733 | 0.1831 | 121.8704 | 0.16022 | 0.064087 | 121.9391 | -0.01831 | 121.9528 | 0.050354 | -121.9528 | -121.8979 | 121.8842 | 0.13275 | 0.24719 | 0.18768
2222.75 | 122.0856 | -0.086975 | 121.9437 | -0.01976 | -0.00030342 | 0.054068 | 0.05216 | 0.0012261 | -0.010698 | -0.0032364 | 0.00073235 | 0.032571 | 0.043062 | 0.011638 | 0.015966 | 0.025887 | -0.0017027 | 0.10986 | 121.8842 | -0.054932 | 121.7468 | 0.050354 | -0.054932 | -0.009155 | 0.018311 | -0.022888 | -0.027466 | 0 | 0.10529 | 0.091553 | 0.082397 | 0.032043 | -0.05951 | -0.19684 | 0.13733 | 0.07782 | 0.032043 | 0.045777 | 0 | 0.059509 | -121.9666 | -121.9437 | 0.19226 | 0.16937 | 0.17853 | 0.10986 | 0.11902 | 0.10529 | 121.8018 | 0.13275 | 0.027466 | 121.9391 | 0.004578 | 121.9711 | 0.064087 | -121.9986 | -121.9711 | 121.8338 | 0.086975 | 0.19684 | 0.10529
2224.5156 | 121.994 | -0.14191 | 121.9482 | -0.012131 | 0.00033758 | 0.053427 | 0.052588 | -0.0011237 | -0.00963 | -0.001741 | -0.0023192 | 0.036416 | 0.043703 | 0.01292 | 0.01618 | 0.02546 | -0.0036253 | 0.16479 | 121.9116 | -0.10529 | 121.6873 | 0 | -0.10071 | -0.10529 | -0.050354 | 0 | -0.059509 | -0.082397 | 0 | 0.004578 | 0.027466 | 0.036621 | -0.036621 | -0.26093 | 0.14191 | 0.036621 | 0.041199 | 0 | 0.004578 | 0.082398 | -121.9482 | -122.0306 | 0.14191 | 0.16937 | 0.14649 | 0.086975 | 0.064087 | 0.10529 | 121.7926 | 0.059509 | -0.022888 | 122.0169 | 0.059509 | 122.0535 | 0.14191 | -122.0535 | -122.0078 | 121.8292 | 0.05951 | 0.3067 | 0.091553
2226.2188 | 122.0901 | -0.082397 | 121.9025 | 0.0031279 | 0.001833 | 0.053854 | 0.05152 | -0.0015509 | -0.00963 | -0.0015274 | -0.005371 | 0.030435 | 0.042635 | 0.011638 | 0.014471 | 0.024391 | -0.0027707 | 0.11444 | 121.9025 | -0.059509 | 121.7514 | 0.086975 | -0.041199 | -0.009155 | 0.032043 | -0.032043 | -0.041199 | 0.009155 | 0.11902 | 0.10986 | 0.10529 | 0.022888 | 0 | -0.15106 | 0.16937 | 0.073242 | 0.041198 | 0.050354 | 0.01831 | 0.041198 | -121.9345 | -121.8933 | 0.20142 | 0.18768 | 0.19226 | 0.14649 | 0.15106 | 0.14648 | 121.8109 | 0.16022 | 0.050354 | 121.962 | 0.009156 | 121.9849 | 0.050354 | -121.962 | -121.9437 | 121.8338 | 0.091552 | 0.19684 | 0.11444
2227.9844 | 122.0718 | -0.09613 | 121.9482 | -0.012131 | 0.001192 | 0.056631 | 0.052374 | -0.0019781 | -0.011766 | -0.0028092 | -0.005371 | 0.032785 | 0.042635 | 0.0041615 | 0.016607 | 0.024391 | -0.0034117 | 0.11902 | 121.8979 | -0.064087 | 121.7606 | 0.068665 | -0.050354 | -0.009155 | 0.027466 | -0.027466 | -0.013733 | 0.004578 | 0.09613 | 0.082397 | 0.086975 | 0.032043 | -0.050354 | -0.18768 | 0.16479 | 0.086975 | 0.045776 | 0.054932 | 0.013733 | 0.082397 | -121.9757 | -121.9437 | 0.19226 | 0.1831 | 0.17853 | 0.10071 | 0.09613 | 0.13275 | 121.8246 | 0.10986 | 0.018311 | 121.962 | -0.013733 | 121.994 | 0.068664 | -122.0123 | -121.962 | 121.8567 | 0.10071 | 0.21515 | 0.1236
2229.7031 | 122.0764 | -0.091553 | 121.9345 | -0.012131 | -0.0017986 | 0.052786 | 0.05216 | -0.00091006 | -0.0087756 | -0.0025956 | -0.0084228 | 0.030862 | 0.043703 | -0.00053833 | 0.015752 | 0.023751 | -0.0042661 | 0.11444 | 121.875 | -0.073242 | 121.7422 | 0.054932 | -0.045776 | -0.027466 | 0.032043 | -0.041199 | -0.027466 | 0 | 0.10986 | 0.10071 | 0.10986 | 0.018311 | -0.059509 | -0.19226 | 0.14649 | 0.064087 | 0.045777 | 0.045776 | 0.027466 | 0.064087 | -121.9757 | -121.9345 | 0.20142 | 0.20142 | 0.19226 | 0.13733 | 0.12817 | 0.12817 | 121.8155 | 0.13733 | 0.027466 | 121.9482 | -0.013733 | 121.9666 | 0.050354 | -122.0078 | -121.962 | 121.8338 | 0.091553 | 0.20599 | 0.1236
2231.4688 | 122.0856 | -0.07782 | 121.9254 | -0.012131 | 0.0022602 | 0.05535 | 0.052801 | 0.0010125 | -0.00963 | -0.0040908 | -0.0023192 | 0.031289 | 0.042421 | 0.0065113 | 0.016393 | 0.026741 | -0.0044797 | 0.16479 | 121.8979 | -0.045776 | 121.8063 | 0.13275 | -0.013733 | 0.027466 | 0.1236 | -0.036621 | -0.018311 | 0.050354 | 0.11444 | 0.10071 | 0.10529 | 0.032044 | -0.027466 | -0.11902 | 0.21057 | 0.10529 | 0.064087 | 0.073242 | 0.032043 | 0.059509 | -121.962 | -121.875 | 0.19226 | 0.18311 | 0.17853 | 0.1236 | 0.11902 | 0.17853 | 121.8521 | 0.13275 | 0.068665 | 121.9437 | -0.01831 | 121.9757 | 0.041199 | -121.9711 | -121.9437 | 121.8842 | 0.12817 | 0.24261 | 0.20142
2233.1719 | 121.9803 | -0.11902 | 121.9666 | -0.0045011 | 0.0026874 | 0.053427 | 0.056006 | 0.0025079 | -0.0083484 | -0.00345 | -0.005371 | 0.035134 | 0.045626 | 0.0097157 | 0.01618 | 0.023537 | -0.0023435 | 0.16479 | 121.9437 | -0.10071 | 121.6919 | 0 | -0.11444 | -0.091553 | -0.054932 | 0.009155 | -0.054932 | -0.07782 | 0.027466 | 0.009155 | 0.032043 | 0.018311 | -0.022888 | -0.27466 | 0.11902 | 0.027466 | 0.004578 | 0.009155 | -0.013733 | 0.064087 | -121.9574 | -122.0444 | 0.14649 | 0.15106 | 0.12817 | 0.086975 | 0.064087 | 0.10071 | 121.7926 | 0.082398 | -0.022888 | 122.0444 | 0.064087 | 122.0627 | 0.12817 | -122.0673 | -122.0215 | 121.8109 | 0.041199 | 0.28381 | 0.064087
2234.9375 | 122.0947 | -0.082397 | 121.9025 | -0.012131 | 0.0048236 | 0.057059 | 0.054083 | -5.5462e-05 | -0.0077074 | -0.0049454 | -0.0084228 | 0.032357 | 0.044771 | 0.0039477 | 0.015966 | 0.025246 | -0.0042661 | 0.13275 | 121.9437 | -0.09613 | 121.7422 | 0.027466 | -0.10986 | -0.07782 | 0.032043 | -0.018311 | -0.022888 | 0.018311 | 0.09613 | 0.082397 | 0.09613 | -0.013733 | 0.041199 | -0.16022 | 0.10986 | 0.004577 | -0.027466 | 0.01831 | -0.013733 | 0.059509 | -121.9208 | -121.8842 | 0.17853 | 0.17853 | 0.16479 | 0.11902 | 0.10528 | 0.1236 | 121.8384 | 0.11902 | 0.041199 | 122.0398 | 0.004577 | 122.0261 | 0.064086 | -121.9986 | -121.9254 | 121.8246 | 0.10071 | 0.21515 | 0.11444
2236.6406 | 122.0947 | -0.07782 | 121.9528 | -0.0045011 | -0.0013714 | 0.054282 | 0.05152 | -0.00069646 | -0.0077074 | -0.0013138 | -0.0023192 | 0.031717 | 0.040926 | 0.0082203 | 0.014471 | 0.026955 | -0.0068295 | 0.11902 | 121.8979 | -0.068665 | 121.7377 | 0.073242 | -0.041199 | -0.004578 | 0.013733 | -0.027466 | -0.036621 | 0.027466 | 0.12817 | 0.11444 | 0.086975 | 0.009155 | -0.054932 | -0.21515 | 0.15106 | 0.073242 | 0.036621 | 0.064087 | 0.027466 | 0.041199 | -121.9803 | -121.9254 | 0.20599 | 0.16479 | 0.19226 | 0.1236 | 0.15106 | 0.14191 | 121.8063 | 0.1648 | 0.064087 | 121.9666 | 0.009155 | 121.9757 | 0.050354 | -122.0215 | -121.9894 | 121.8155 | 0.10529 | 0.19684 | 0.091553
2238.3906 | 122.1313 | -0.086975 | 121.8979 | -0.012131 | -0.00073062 | 0.054709 | 0.05216 | -0.0021919 | -0.0089892 | -0.0038772 | -0.005371 | 0.032571 | 0.044558 | 0.0062977 | 0.016393 | 0.024605 | -0.0061887 | 0.16937 | 121.8887 | -0.050354 | 121.7926 | 0.1236 | 0 | 0.032043 | 0.09613 | -0.027466 | -0.013733 | 0.050354 | 0.16479 | 0.15564 | 0.14191 | 0.036621 | -0.009155 | -0.10528 | 0.21057 | 0.11902 | 0.086975 | 0.082397 | 0.050354 | 0.073242 | -121.9254 | -121.8475 | 0.25177 | 0.22888 | 0.24261 | 0.15564 | 0.16937 | 0.17395 | 121.843 | 0.17853 | 0.064087 | 121.9391 | -0.013733 | 121.9757 | 0.059509 | -121.9482 | -121.9116 | 121.8796 | 0.13733 | 0.25635 | 0.1831
2240.1562 | 122.1268 | -0.068665 | 121.9299 | -0.0045011 | 0.0022602 | 0.053854 | 0.050665 | -0.0036871 | -0.0092028 | -0.0045182 | -0.005371 | 0.031076 | 0.043489 | 0.0050159 | 0.014898 | 0.022896 | 0.00064735 | 0.21515 | 121.8658 | -0.050354 | 121.8521 | 0.17853 | 0.036621 | 0.036621 | 0.1236 | -0.059509 | -0.009155 | 0.054932 | 0.18768 | 0.17853 | 0.13275 | 0.018311 | -0.064087 | -0.07782 | 0.24719 | 0.10529 | 0.10529 | 0.086975 | 0.086975 | 0.05951 | -121.9894 | -121.875 | 0.25635 | 0.20142 | 0.24719 | 0.14191 | 0.18768 | 0.22888 | 121.9025 | 0.19684 | 0.064087 | 121.9162 | -0.050354 | 121.9345 | 0.009156 | -121.9803 | -121.9391 | 121.9208 | 0.1236 | 0.28381 | 0.19226
2241.8594 | 121.9711 | -0.13275 | 121.9391 | 0.0031279 | 0.0071734 | 0.056845 | 0.056433 | 0.0037897 | -0.0074938 | -0.0025956 | -0.0084228 | 0.034921 | 0.042421 | 0.0041615 | 0.017248 | 0.021187 | -0.0029843 | 0.16937 | 121.9666 | -0.091553 | 121.6873 | -0.041199 | -0.16479 | -0.13275 | -0.091553 | 0 | -0.064087 | -0.059509 | -0.018311 | -0.027466 | 0.018311 | 0.041198 | 0.027466 | -0.25177 | 0.091552 | 0 | -0.032044 | -0.041198 | -0.073242 | 0.068664 | -121.9391 | -121.9986 | 0.11444 | 0.15106 | 0.10529 | 0.082398 | 0.036621 | 0.050354 | 121.7789 | 0.045776 | 0.004578 | 122.0581 | 0.064087 | 122.0993 | 0.13275 | -122.0306 | -122.0032 | 121.8201 | 0.073242 | 0.30212 | 0.041198
2243.625 | 122.0123 | -0.12817 | 121.9803 | 0.0031279 | 0.0024738 | 0.053854 | 0.051733 | -0.00091006 | -0.0092028 | 0.0021042 | -0.005371 | 0.032998 | 0.04648 | 0.0071521 | 0.018102 | 0.0261 | -0.0036253 | 0.16937 | 121.9299 | -0.091553 | 121.6919 | -0.009155 | -0.10529 | -0.091553 | -0.064087 | 0.009155 | -0.050354 | -0.064087 | 0.022888 | 0.022888 | 0.027466 | 0.036621 | -0.050354 | -0.28839 | 0.11902 | 0.036621 | 0.022888 | 0 | -0.013733 | 0.07782 | -121.9711 | -122.0444 | 0.15106 | 0.15564 | 0.15106 | 0.07782 | 0.073242 | 0.082398 | 121.7834 | 0.073242 | -0.013733 | 122.0215 | 0.059509 | 122.0581 | 0.13733 | -122.0718 | -122.0306 | 121.8201 | 0.064087 | 0.29755 | 0.064087
2245.3281 | 122.0993 | -0.068665 | 121.9254 | -0.01976 | -8.9824e-05 | 0.052786 | 0.05152 | -0.0045417 | -0.0081348 | 0.001036 | -0.0023192 | 0.030648 | 0.041353 | 0.0026661 | 0.015539 | 0.025246 | -0.0023435 | 0.1236 | 121.8933 | -0.041199 | 121.7697 | 0.09613 | -0.022888 | 0.009155 | 0.036621 | -0.027466 | -0.036621 | 0.027466 | 0.13733 | 0.13733 | 0.10986 | 0.027466 | -0.032043 | -0.15564 | 0.16479 | 0.07782 | 0.045777 | 0.050354 | 0.018311 | 0.032044 | -121.9528 | -121.8979 | 0.20599 | 0.17853 | 0.20599 | 0.14648 | 0.17395 | 0.13733 | 121.8109 | 0.17395 | 0.064087 | 121.9345 | 0.009155 | 121.962 | 0.041199 | -121.9666 | -121.962 | 121.8384 | 0.096131 | 0.19226 | 0.10529
2247.0781 | 122.049 | -0.09613 | 121.9254 | 0.0031279 | -0.00051702 | 0.054282 | 0.050238 | -0.0015509 | -0.010912 | -0.0021682 | -0.0023192 | 0.031289 | 0.04178 | 0.0090747 | 0.017889 | 0.024605 | -0.0053343 | 0.2243 | 121.8796 | -0.050354 | 121.8063 | 0.13275 | -0.004578 | 0.022888 | 0.054932 | -0.018311 | -0.032043 | -0.018311 | 0.1236 | 0.10986 | 0.073242 | 0.045776 | -0.045776 | -0.11902 | 0.22888 | 0.11902 | 0.091552 | 0.073242 | 0.045776 | 0.064087 | -121.9437 | -121.9437 | 0.21973 | 0.16937 | 0.20599 | 0.10529 | 0.14191 | 0.18311 | 121.8567 | 0.15564 | 0.013732 | 121.9299 | 0.013732 | 121.9757 | 0.077819 | -121.9757 | -121.9574 | 121.9025 | 0.077819 | 0.32043 | 0.15106
2248.8281 | 122.113 | -0.091553 | 121.907 | -0.0045011 | -8.9824e-05 | 0.053641 | 0.050024 | -0.0024055 | -0.0070666 | -0.0004592 | -0.005371 | 0.033212 | 0.042635 | 0.0069385 | 0.017034 | 0.025032 | -0.0025571 | 0.20599 | 121.8613 | -0.050354 | 121.8246 | 0.16479 | 0.027466 | 0.050354 | 0.091553 | -0.036621 | -0.018311 | 0.059509 | 0.16937 | 0.17395 | 0.12817 | 0.041199 | -0.045776 | -0.082397 | 0.25635 | 0.14191 | 0.11902 | 0.10071 | 0.07782 | 0.073242 | -121.9437 | -121.8475 | 0.26093 | 0.21973 | 0.2655 | 0.14649 | 0.19226 | 0.21515 | 121.875 | 0.18768 | 0.07782 | 121.9116 | -0.01831 | 121.9528 | 0.054932 | -121.9574 | -121.9254 | 121.9162 | 0.15106 | 0.29755 | 0.18311
2250.5312 | 122.081 | -0.09613 | 121.9162 | -0.01976 | 0.0022602 | 0.054068 | 0.051733 | -0.0056097 | -0.0079212 | -0.0047318 | -0.005371 | 0.03193 | 0.04413 | 0.0039477 | 0.016393 | 0.026528 | -0.0040525 | 0.13733 | 121.9116 | -0.064087 | 121.7468 | 0.068665 | -0.045776 | -0.009155 | 0.013733 | -0.036621 | -0.013733 | 0 | 0.10529 | 0.091553 | 0.082397 | 0.032043 | -0.004578 | -0.16937 | 0.16479 | 0.086975 | 0.050354 | 0.054932 | 0.018311 | 0.082397 | -121.9528 | -121.9162 | 0.20142 | 0.17853 | 0.18768 | 0.09613 | 0.10529 | 0.13275 | 121.8109 | 0.11902 | 0.013733 | 121.9757 | -0.022888 | 122.0078 | 0.059509 | -121.9803 | -121.9299 | 121.843 | 0.09613 | 0.23346 | 0.10986
2252.3125 | 121.994 | -0.10986 | 121.9482 | -0.0045011 | 0.0043964 | 0.056418 | 0.057501 | 0.00015814 | -0.008562 | -0.0025956 | -0.0023192 | 0.032785 | 0.043917 | 0.01057 | 0.018957 | 0.024605 | -0.0014891 | 0.20599 | 121.9391 | -0.086975 | 121.7285 | 0.027466 | -0.1236 | -0.091553 | -0.027466 | 0.009155 | -0.041199 | -0.054932 | 0.013733 | -0.013733 | 0.022888 | 0.022888 | -0.009155 | -0.21973 | 0.13733 | 0.01831 | -0.013733 | -0.004578 | -0.036621 | 0.068664 | -121.9391 | -122.0032 | 0.1236 | 0.13275 | 0.09613 | 0.064087 | 0.027466 | 0.11444 | 121.8155 | 0.054932 | -0.013733 | 122.0261 | 0.050354 | 122.049 | 0.11902 | -122.0352 | -121.9894 | 121.8384 | 0.054931 | 0.31586 | 0.082397
2254.0156 | 122.1085 | -0.091553 | 121.9254 | -0.01976 | 0.00033758 | 0.05535 | 0.052588 | -0.0011237 | -0.010698 | -0.0047318 | -0.005371 | 0.031503 | 0.043917 | 0.0037341 | 0.015752 | 0.026528 | -0.0017027 | 0.12817 | 121.8842 | -0.068665 | 121.7743 | 0.09613 | -0.018311 | 0.004578 | 0.054932 | -0.018311 | -0.032043 | 0.032043 | 0.15106 | 0.14648 | 0.11902 | 0.022888 | -0.041199 | -0.15106 | 0.18768 | 0.096131 | 0.073242 | 0.073243 | 0.050354 | 0.05951 | -121.9437 | -121.8933 | 0.24261 | 0.21057 | 0.23804 | 0.15106 | 0.17853 | 0.16479 | 121.843 | 0.18311 | 0.064086 | 121.9528 | 0.013732 | 121.9757 | 0.073242 | -121.994 | -121.9574 | 121.8658 | 0.1236 | 0.21973 | 0.14649
2255.7812 | 121.9894 | -0.11444 | 121.9528 | -0.012131 | 0.0048236 | 0.054709 | 0.053015 | 0.0027215 | -0.0081348 | -0.00345 | -0.0084228 | 0.034494 | 0.043703 | 0.010356 | 0.015752 | 0.02311 | -0.0021299 | 0.16022 | 121.9757 | -0.09613 | 121.6919 | -0.027466 | -0.15564 | -0.11902 | -0.059509 | 0.009155 | -0.054932 | -0.064087 | 0.013733 | -0.009155 | 0.022888 | 0.018311 | 0.022888 | -0.26093 | 0.086975 | -0.004578 | -0.041199 | -0.022889 | -0.05951 | 0.059509 | -121.9437 | -122.0169 | 0.12817 | 0.13733 | 0.10529 | 0.07782 | 0.045777 | 0.068664 | 121.788 | 0.068665 | -0.009155 | 122.0718 | 0.064087 | 122.0901 | 0.1236 | -122.049 | -122.0078 | 121.8063 | 0.050354 | 0.27466 | 0.054932
2257.5312 | 121.9803 | -0.09613 | 121.9482 | -0.012131 | 0.0022602 | 0.056631 | 0.052588 | 0.0016535 | -0.0087756 | -0.0021682 | -0.0023192 | 0.032571 | 0.044344 | 0.012279 | 0.016821 | 0.0261 | -0.0046933 | 0.16022 | 121.9711 | -0.086975 | 121.6827 | -0.036621 | -0.15564 | -0.1236 | -0.073242 | 0.009155 | -0.059509 | -0.059509 | -0.004578 | -0.009155 | 0.032043 | 0.009155 | 0.022888 | -0.2655 | 0.059509 | -0.027466 | -0.05951 | -0.036621 | -0.068665 | 0.036621 | -121.9391 | -122.0078 | 0.091552 | 0.12817 | 0.086975 | 0.091552 | 0.050354 | 0.050354 | 121.7697 | 0.054931 | 0 | 122.0581 | 0.068664 | 122.0673 | 0.10528 | -122.0352 | -122.0078 | 121.7789 | 0.036621 | 0.25635 | 0.022888
2259.2969 | 121.9986 | -0.1236 | 121.9574 | -0.012131 | 0.0037556 | 0.055777 | 0.054724 | -0.0015509 | -0.0083484 | -0.0045182 | -0.005371 | 0.032998 | 0.045412 | 0.011424 | 0.016821 | 0.024819 | -0.0019163 | 0.13733 | 121.9574 | -0.091553 | 121.6782 | -0.013733 | -0.14191 | -0.09613 | -0.036621 | -0.018311 | -0.041199 | -0.054932 | 0.009155 | -0.004578 | 0.032043 | 0.032043 | 0 | -0.27923 | 0.10986 | 0.027466 | -0.018311 | -0.004577 | -0.050354 | 0.082397 | -121.9757 | -122.0123 | 0.13275 | 0.15564 | 0.11902 | 0.073242 | 0.036621 | 0.07782 | 121.7697 | 0.050354 | -0.013733 | 122.049 | 0.022888 | 122.081 | 0.10528 | -122.049 | -121.9986 | 121.8018 | 0.068664 | 0.26093 | 0.086975
2261 | 122.1176 | -0.064087 | 121.9254 | -0.012131 | 0.0054644 | 0.055991 | 0.051306 | 0.00079894 | -0.0059986 | -0.00345 | -0.0023192 | 0.03193 | 0.045626 | 0.0099293 | 0.017889 | 0.0261 | -0.0027707 | 0.20599 | 121.9116 | -0.054932 | 121.8018 | 0.14191 | -0.013733 | 0.013733 | 0.09613 | -0.045776 | -0.013733 | 0.064087 | 0.14191 | 0.11902 | 0.15564 | 0.009155 | -0.013733 | -0.1236 | 0.20599 | 0.07782 | 0.050354 | 0.068665 | 0.041199 | 0.050354 | -121.9711 | -121.8613 | 0.20599 | 0.21973 | 0.18311 | 0.16937 | 0.13275 | 0.19684 | 121.8567 | 0.15564 | 0.07782 | 121.9666 | -0.032043 | 121.9757 | 0.018311 | -121.9803 | -121.9391 | 121.8658 | 0.12817 | 0.27008 | 0.16022
2262.7656 | 122.1085 | -0.07782 | 121.9025 | -0.012131 | 0.0020466 | 0.052786 | 0.051306 | -0.0011237 | -0.010271 | -0.0032364 | -0.0084228 | 0.030648 | 0.041994 | 0.0071521 | 0.014257 | 0.028023 | -0.0012753 | 0.21057 | 121.8933 | -0.059509 | 121.8201 | 0.16479 | 0.027466 | 0.041199 | 0.09613 | -0.041199 | -0.009155 | 0.041199 | 0.17395 | 0.16022 | 0.12817 | 0.018311 | -0.009155 | -0.082398 | 0.24261 | 0.11902 | 0.10529 | 0.10071 | 0.086975 | 0.068665 | -121.9437 | -121.8613 | 0.25177 | 0.20599 | 0.23804 | 0.13733 | 0.16937 | 0.2243 | 121.8796 | 0.1831 | 0.050354 | 121.9528 | -0.032044 | 121.9711 | 0.036621 | -121.962 | -121.9116 | 121.8979 | 0.11902 | 0.28839 | 0.17395
2264.5312 | 122.0398 | -0.10529 | 121.9528 | -0.0045011 | 0.001833 | 0.05535 | 0.053442 | 0.0044305 | -0.0087756 | -0.0021682 | -0.0084228 | 0.032998 | 0.046694 | 0.0041615 | 0.017461 | 0.026528 | -0.0023435 | 0.20142 | 121.9345 | -0.082397 | 121.7285 | 0.036621 | -0.07782 | -0.064087 | -0.018311 | -0.004578 | -0.041199 | -0.032043 | 0.073242 | 0.054932 | 0.064087 | 0.022889 | -0.018311 | -0.2243 | 0.14191 | 0.041199 | 0.027466 | 0.01831 | 0.004577 | 0.064087 | -121.9574 | -121.9849 | 0.17853 | 0.16937 | 0.16022 | 0.10529 | 0.096131 | 0.11902 | 121.8109 | 0.11444 | 0.009156 | 122.0169 | 0.036621 | 122.0398 | 0.10071 | -122.0352 | -121.994 | 121.8338 | 0.073243 | 0.3067 | 0.086975
2266.25 | 122.113 | -0.086975 | 121.9482 | -0.012131 | 0.001833 | 0.055777 | 0.050024 | -0.00091006 | -0.00963 | -0.00345 | -0.011475 | 0.031717 | 0.042421 | 0.00010247 | 0.014043 | 0.026741 | -0.0019163 | 0.13275 | 121.8979 | -0.054932 | 121.7651 | 0.082397 | -0.022888 | 0 | 0.027466 | -0.032043 | -0.027466 | 0.018311 | 0.11444 | 0.10986 | 0.10986 | 0.032043 | -0.050354 | -0.1831 | 0.16937 | 0.086975 | 0.064087 | 0.054932 | 0.032044 | 0.059509 | -121.9803 | -121.9299 | 0.20142 | 0.19684 | 0.19684 | 0.13733 | 0.13733 | 0.13733 | 121.8201 | 0.14191 | 0.045777 | 121.9528 | -0.004577 | 121.9849 | 0.054932 | -122.0032 | -121.9757 | 121.8521 | 0.10529 | 0.21973 | 0.11444
2268 | 122.1222 | -0.07782 | 121.9254 | -0.01976 | 0.0035418 | 0.055563 | 0.051947 | -0.0013373 | -0.006853 | -0.0049454 | -0.005371 | 0.030008 | 0.044344 | 0.0035205 | 0.016821 | 0.026955 | 0.0036379 | 0.19226 | 121.9162 | -0.064087 | 121.8018 | 0.1236 | -0.022888 | 0.009155 | 0.091553 | -0.036621 | -0.009155 | 0.059509 | 0.14648 | 0.12817 | 0.14648 | 0.013733 | -0.009155 | -0.1236 | 0.20142 | 0.086975 | 0.054932 | 0.073242 | 0.041199 | 0.068665 | -121.962 | -121.8658 | 0.2243 | 0.2243 | 0.20599 | 0.15564 | 0.13733 | 0.18768 | 121.8658 | 0.15564 | 0.068664 | 121.9803 | -0.027466 | 121.994 | 0.041199 | -121.9894 | -121.9345 | 121.8796 | 0.13733 | 0.27008 | 0.16937
2269.7656 | 122.0718 | -0.07782 | 121.9299 | -0.012131 | 0.00012398 | 0.053641 | 0.048956 | 0.00015814 | -0.00963 | -0.0030228 | -0.011475 | 0.030008 | 0.044344 | 0.0084339 | 0.014898 | 0.02546 | -0.0031979 | 0.12817 | 121.907 | -0.050354 | 121.7422 | 0.073242 | -0.041199 | -0.022888 | 0.009155 | -0.022888 | -0.032043 | 0 | 0.11444 | 0.091553 | 0.091553 | 0.027466 | -0.022889 | -0.18768 | 0.15106 | 0.054932 | 0.036621 | 0.027466 | 0.009155 | 0.045777 | -121.9528 | -121.9299 | 0.19226 | 0.16937 | 0.16937 | 0.1236 | 0.1236 | 0.1236 | 121.7926 | 0.14648 | 0.032043 | 121.9574 | 0.009155 | 121.9849 | 0.054932 | -121.9803 | -121.962 | 121.8201 | 0.07782 | 0.20599 | 0.086975
2271.4688 | 122.0306 | -0.10986 | 121.9757 | -0.01976 | 0.0039692 | 0.055136 | 0.055151 | -0.0028327 | -0.0083484 | -0.0038772 | 0.00073235 | 0.032998 | 0.042635 | 0.0045887 | 0.017889 | 0.022469 | -0.0053343 | 0.21057 | 121.9299 | -0.11902 | 121.7194 | -0.004578 | -0.082397 | -0.07782 | -0.041199 | 0 | -0.050354 | -0.022888 | 0.068665 | 0.050354 | 0.059509 | -0.009156 | -0.045776 | -0.25635 | 0.10529 | 0.032043 | 0.027466 | 0.041199 | 0.036622 | 0.059509 | -121.9757 | -121.9986 | 0.17853 | 0.16937 | 0.16022 | 0.10986 | 0.10071 | 0.11444 | 121.8384 | 0.11902 | 0.027466 | 122.049 | 0.050354 | 122.0398 | 0.10986 | -122.0947 | -122.0261 | 121.8292 | 0.086975 | 0.32043 | 0.068664
2273.2344 | 121.9986 | -0.10986 | 121.9437 | -0.012131 | 0.0050372 | 0.054922 | 0.052374 | 0.0044305 | -0.0081348 | -0.0025956 | -0.0084228 | 0.032144 | 0.043489 | 0.013133 | 0.016607 | 0.02546 | -0.0036253 | 0.15564 | 121.9482 | -0.09613 | 121.669 | -0.036621 | -0.14648 | -0.11902 | -0.068665 | 0.009155 | -0.050354 | -0.059509 | -0.009155 | -0.022888 | 0.032043 | 0.013733 | 0.004577 | -0.27466 | 0.073242 | -0.009156 | -0.036621 | -0.022889 | -0.050354 | 0.059509 | -121.9345 | -122.0032 | 0.10071 | 0.14191 | 0.086975 | 0.082397 | 0.027466 | 0.059509 | 121.7651 | 0.041199 | -0.009155 | 122.0444 | 0.059509 | 122.0581 | 0.11902 | -122.0398 | -121.994 | 121.7789 | 0.050354 | 0.2655 | 0.041198
2274.9844 | 122.0123 | -0.1236 | 121.9437 | -0.012131 | 0.0043964 | 0.053214 | 0.054297 | 0.0010125 | -0.0074938 | -3.1996e-05 | -0.005371 | 0.031717 | 0.043703 | 0.0054431 | 0.017889 | 0.024819 | -0.00020725 | 0.15564 | 121.9528 | -0.086975 | 121.6873 | 0 | -0.14191 | -0.10529 | -0.045776 | -0.013733 | -0.050354 | -0.027466 | 0.032043 | -0.004578 | 0.041199 | 0.036621 | 0.009155 | -0.25635 | 0.1236 | 0.01831 | -0.018311 | -0.018311 | -0.054932 | 0.073242 | -121.9574 | -121.9711 | 0.15564 | 0.16479 | 0.11902 | 0.091553 | 0.045776 | 0.086975 | 121.7743 | 0.082397 | 0.022888 | 122.0398 | 0.036621 | 122.0764 | 0.10986 | -122.0306 | -121.994 | 121.8109 | 0.09613 | 0.27924 | 0.07782
2276.75 | 122.1313 | -0.082397 | 121.9299 | -0.012131 | -8.9824e-05 | 0.055563 | 0.050879 | -0.0019781 | -0.00963 | -0.0028092 | -0.0023192 | 0.03193 | 0.04178 | 0.0035205 | 0.015966 | 0.024605 | -0.0036253 | 0.20599 | 121.8933 | -0.050354 | 121.8338 | 0.1831 | 0.045776 | 0.07782 | 0.10529 | -0.027466 | -0.022888 | 0.041199 | 0.19684 | 0.16022 | 0.13733 | 0.032043 | -0.036621 | -0.096131 | 0.2655 | 0.16022 | 0.12817 | 0.12817 | 0.09613 | 0.059509 | -121.9574 | -121.8887 | 0.27924 | 0.21973 | 0.24261 | 0.16022 | 0.1831 | 0.23346 | 121.8842 | 0.21973 | 0.064087 | 121.9437 | -0.004578 | 121.9757 | 0.054931 | -121.9803 | -121.9528 | 121.9162 | 0.1236 | 0.28839 | 0.18768
2278.4531 | 122.1313 | -0.068665 | 121.9116 | -0.012131 | 0.00461 | 0.056418 | 0.05152 | 0.0016535 | -0.0087756 | 0.0001816 | -0.005371 | 0.031289 | 0.043062 | 0.0067249 | 0.015966 | 0.027596 | -0.0070433 | 0.19684 | 121.907 | -0.045776 | 121.8155 | 0.13275 | -0.009155 | 0.018311 | 0.10071 | -0.032043 | -0.013733 | 0.059509 | 0.15564 | 0.15106 | 0.13733 | 0.022889 | -0.004578 | -0.09613 | 0.20142 | 0.086976 | 0.05951 | 0.064087 | 0.036621 | 0.054932 | -121.9437 | -121.8521 | 0.22431 | 0.20599 | 0.21973 | 0.15106 | 0.16479 | 0.17853 | 121.8613 | 0.16937 | 0.073242 | 121.9528 | -0.01831 | 121.9757 | 0.036622 | -121.9574 | -121.9254 | 121.8842 | 0.12817 | 0.2655 | 0.16937
2280.2031 | 122.1085 | -0.068665 | 121.9162 | -0.01976 | 0.0041828 | 0.059195 | 0.053656 | 0.0010125 | -0.0064258 | -0.0013138 | -0.005371 | 0.031717 | 0.041567 | 0.0041615 | 0.017461 | 0.026528 | -0.0042661 | 0.16479 | 121.9299 | -0.068665 | 121.7514 | 0.07782 | -0.059509 | -0.018311 | 0.068665 | -0.041199 | -0.022888 | 0.054932 | 0.13275 | 0.11444 | 0.14648 | 0 | 0.013733 | -0.1648 | 0.14649 | 0.050354 | 0.009156 | 0.050354 | 0.009156 | 0.045777 | -121.9574 | -121.8613 | 0.20142 | 0.21515 | 0.18311 | 0.16937 | 0.13733 | 0.14649 | 121.8201 | 0.15564 | 0.07782 | 121.9986 | -0.018311 | 121.9986 | 0.027466 | -121.9849 | -121.9391 | 121.8201 | 0.1236 | 0.23346 | 0.13733
2281.9531 | 122.0718 | -0.073242 | 121.9116 | -0.012131 | 0.00097838 | 0.05535 | 0.051733 | -0.0017645 | -0.0077074 | -0.0036636 | -0.0084228 | 0.02958 | 0.043276 | 0.0058703 | 0.015325 | 0.0261 | -0.0042661 | 0.13275 | 121.875 | -0.059509 | 121.756 | 0.086975 | -0.041199 | -0.018311 | 0.013733 | -0.041199 | -0.045776 | 0.018311 | 0.10071 | 0.09613 | 0.091553 | 0.013733 | -0.036621 | -0.15564 | 0.16022 | 0.054931 | 0.032043 | 0.041198 | 0.01831 | 0.027466 | -121.9528 | -121.8933 | 0.17395 | 0.16479 | 0.16937 | 0.13733 | 0.14191 | 0.14648 | 121.8155 | 0.14648 | 0.064087 | 121.9345 | 0.004577 | 121.9482 | 0.032043 | -121.9711 | -121.9574 | 121.8292 | 0.091553 | 0.20599 | 0.086975
2283.7188 | 122.0947 | -0.091553 | 121.9391 | -0.012131 | 0.00033758 | 0.053854 | 0.051092 | -0.0024055 | -0.0077074 | -0.000673 | -0.0023192 | 0.03193 | 0.043917 | 0.011638 | 0.013403 | 0.022255 | -0.0038389 | 0.23804 | 121.9025 | -0.054932 | 121.8063 | 0.14191 | 0.009155 | 0.032043 | 0.082397 | -0.045776 | -0.018311 | 0.036621 | 0.14191 | 0.12817 | 0.10986 | 0.036621 | -0.036621 | -0.13275 | 0.23346 | 0.1236 | 0.10071 | 0.086975 | 0.064087 | 0.073242 | -121.9849 | -121.9025 | 0.23346 | 0.20142 | 0.21973 | 0.12817 | 0.14649 | 0.19684 | 121.8613 | 0.16022 | 0.054932 | 121.9574 | -0.027465 | 121.994 | 0.045777 | -121.994 | -121.9574 | 121.8979 | 0.12817 | 0.32959 | 0.17395
2285.4219 | 122.0673 | -0.086975 | 121.9208 | -0.02739 | 0.0037556 | 0.055563 | 0.050451 | 0.0027215 | -0.0089892 | -0.00345 | -0.0023192 | 0.030435 | 0.042635 | 0.0067249 | 0.015539 | 0.023751 | -0.0023435 | 0.16479 | 121.9025 | -0.045776 | 121.7789 | 0.14191 | -0.032043 | 0.027466 | 0.064087 | -0.032043 | -0.013733 | 0.018311 | 0.11444 | 0.10071 | 0.10529 | 0.041199 | -0.01831 | -0.14191 | 0.22888 | 0.11444 | 0.054932 | 0.073242 | 0.013733 | 0.073242 | -121.9528 | -121.9025 | 0.20142 | 0.19226 | 0.18768 | 0.11902 | 0.11444 | 0.18768 | 121.8246 | 0.12817 | 0.032044 | 121.9482 | -0.01831 | 121.9894 | 0.054932 | -121.9666 | -121.9345 | 121.8658 | 0.10529 | 0.25177 | 0.15106
2287.1719 | 122.0993 | -0.086975 | 121.9254 | -0.012131 | 0.0024738 | 0.055991 | 0.050665 | 0.0012261 | -0.0081348 | -0.0013138 | -0.005371 | 0.030648 | 0.043062 | 0.0080067 | 0.015325 | 0.025673 | -0.0038389 | 0.14648 | 121.8979 | -0.068665 | 121.7651 | 0.07782 | -0.041199 | 0.004578 | 0.041199 | -0.041199 | -0.022888 | 0.022888 | 0.13275 | 0.11902 | 0.10071 | 0.01831 | -0.027466 | -0.16022 | 0.16479 | 0.091553 | 0.045776 | 0.073243 | 0.027466 | 0.064087 | -121.9666 | -121.9025 | 0.21973 | 0.18768 | 0.20599 | 0.1236 | 0.14191 | 0.14649 | 121.8338 | 0.15564 | 0.045776 | 121.9666 | -0.018311 | 121.9849 | 0.045776 | -121.994 | -121.9482 | 121.8521 | 0.10986 | 0.23346 | 0.12817
2288.9219 | 122.1405 | -0.068665 | 121.907 | -0.0045011 | 0.00097838 | 0.055563 | 0.054724 | -0.0019781 | -0.010485 | -0.0008866 | -0.005371 | 0.030862 | 0.04413 | 0.0088611 | 0.014471 | 0.022896 | -0.0044797 | 0.20599 | 121.9025 | -0.068665 | 121.8155 | 0.14648 | 0.032043 | 0.064087 | 0.13275 | -0.050354 | -0.009155 | 0.054932 | 0.17395 | 0.17853 | 0.14191 | 0 | -0.004577 | -0.091552 | 0.21515 | 0.13275 | 0.10071 | 0.13275 | 0.10071 | 0.05951 | -121.9574 | -121.8521 | 0.24261 | 0.21057 | 0.24719 | 0.15106 | 0.18768 | 0.21515 | 121.8842 | 0.1831 | 0.064087 | 121.9711 | -0.041199 | 121.9711 | 0.018311 | -121.9757 | -121.9162 | 121.8842 | 0.1236 | 0.27466 | 0.20142
2290.625 | 122.1176 | -0.091553 | 121.9391 | -0.012131 | 0.0014056 | 0.057059 | 0.051306 | -0.0011237 | -0.0081348 | -0.0028092 | -0.0084228 | 0.030435 | 0.043489 | 0.0073657 | 0.015325 | 0.024819 | -0.0093931 | 0.21973 | 121.8933 | -0.045776 | 121.8384 | 0.16479 | 0.027466 | 0.050354 | 0.10071 | -0.027466 | -0.018311 | 0.045776 | 0.17395 | 0.14648 | 0.13733 | 0.045777 | -0.045776 | -0.10071 | 0.25635 | 0.14191 | 0.11902 | 0.09613 | 0.073242 | 0.073242 | -121.9666 | -121.8933 | 0.2655 | 0.22888 | 0.23804 | 0.15564 | 0.16479 | 0.21057 | 121.8842 | 0.19226 | 0.064087 | 121.9391 | -0.009155 | 121.9849 | 0.064087 | -121.9849 | -121.9574 | 121.9299 | 0.13733 | 0.31128 | 0.19226
2292.375 | 122.0901 | -0.091553 | 121.9528 | -0.0045011 | 0.0031146 | 0.055136 | 0.053228 | -0.00048286 | -0.0077074 | -0.00345 | -0.0023192 | 0.030648 | 0.044771 | 0.013988 | 0.01618 | 0.022896 | -0.0017027 | 0.17853 | 121.9254 | -0.054932 | 121.8155 | 0.13733 | -0.013733 | 0.018311 | 0.09613 | -0.036621 | 0.004578 | 0.054932 | 0.13733 | 0.10071 | 0.11444 | 0.036621 | -0.027466 | -0.13733 | 0.22888 | 0.10986 | 0.07782 | 0.073243 | 0.041199 | 0.096131 | -121.9894 | -121.8979 | 0.22888 | 0.20599 | 0.19226 | 0.10986 | 0.09613 | 0.19226 | 121.8704 | 0.13275 | 0.050354 | 121.9803 | -0.041199 | 122.0169 | 0.054932 | -122.0078 | -121.9482 | 121.907 | 0.14649 | 0.27008 | 0.18768
2294.1406 | 122.0352 | -0.10071 | 121.9391 | -0.0045011 | 0.0035418 | 0.056418 | 0.055151 | 0.0016535 | -0.011553 | -0.0025956 | -0.005371 | 0.033639 | 0.045839 | 0.012493 | 0.017889 | 0.02311 | -0.0059751 | 0.26093 | 121.9437 | -0.086975 | 121.7651 | 0.068665 | -0.054932 | -0.041199 | 0.041199 | 0.004578 | -0.045776 | 0 | 0.07782 | 0.045776 | 0.073242 | 0.013733 | 0.004578 | -0.17395 | 0.16937 | 0.059509 | 0.045776 | 0.045776 | 0.032043 | 0.054932 | -121.9345 | -121.9391 | 0.17853 | 0.17395 | 0.14648 | 0.11902 | 0.091552 | 0.15564 | 121.8521 | 0.1236 | 0.045776 | 122.0306 | 0.050354 | 122.0444 | 0.10529 | -122.0261 | -121.9849 | 121.8658 | 0.10071 | 0.36163 | 0.14191
2295.9219 | 121.9803 | -0.10986 | 121.9757 | -0.0045011 | 0.006319 | 0.055136 | 0.053015 | 0.0037897 | -0.0079212 | -0.002382 | -0.0023192 | 0.033853 | 0.044771 | 0.01057 | 0.018957 | 0.025246 | -0.0019163 | 0.1831 | 121.9803 | -0.086975 | 121.6873 | -0.036621 | -0.14648 | -0.1236 | -0.086975 | -0.004578 | -0.041199 | -0.082397 | 0.018311 | -0.018311 | 0.027466 | 0.022888 | 0.004578 | -0.28839 | 0.073242 | -0.013733 | -0.036621 | -0.036621 | -0.059509 | 0.068664 | -121.9803 | -122.0581 | 0.12817 | 0.13733 | 0.091552 | 0.068665 | 0.022888 | 0.050354 | 121.7743 | 0.05951 | -0.041198 | 122.0673 | 0.036621 | 122.0901 | 0.10529 | -122.0627 | -122.0169 | 121.7972 | 0.027466 | 0.29297 | 0.022888
2297.6875 | 122.1222 | -0.068665 | 121.907 | -0.012131 | 0.0048236 | 0.055136 | 0.052374 | -0.0036871 | -0.0053576 | -0.001741 | -0.0084228 | 0.031503 | 0.043489 | 0.0075793 | 0.01917 | 0.02546 | -0.0034117 | 0.20599 | 121.9208 | -0.041199 | 121.8155 | 0.14191 | 0 | 0.027466 | 0.11444 | -0.050354 | -0.004578 | 0.068665 | 0.16937 | 0.1236 | 0.13733 | 0.027466 | 0.013733 | -0.091552 | 0.21057 | 0.096131 | 0.068665 | 0.068665 | 0.041199 | 0.064087 | -121.9574 | -121.8384 | 0.23804 | 0.20599 | 0.19226 | 0.14191 | 0.12817 | 0.18311 | 121.8567 | 0.17395 | 0.073243 | 121.962 | -0.045776 | 121.9894 | 0.018311 | -121.9482 | -121.9116 | 121.8842 | 0.13733 | 0.27466 | 0.18311
2299.3906 | 122.0764 | -0.10071 | 121.9574 | -0.012131 | 0.001833 | 0.053427 | 0.050451 | -0.00048286 | -0.0092028 | -0.0013138 | -0.0084228 | 0.03193 | 0.044558 | 0.0080067 | 0.01618 | 0.025673 | -0.0036253 | 0.13733 | 121.907 | -0.064087 | 121.7743 | 0.091553 | -0.041199 | -0.013733 | 0.032043 | -0.041199 | -0.027466 | 0.009155 | 0.091553 | 0.082397 | 0.086975 | 0.036621 | -0.050354 | -0.1831 | 0.19226 | 0.086975 | 0.059509 | 0.050354 | 0.022888 | 0.073242 | -121.9986 | -121.9482 | 0.19226 | 0.18768 | 0.18311 | 0.11444 | 0.10986 | 0.15564 | 121.8384 | 0.11902 | 0.036621 | 121.9711 | -0.013733 | 122.0078 | 0.059509 | -122.0215 | -121.9849 | 121.875 | 0.10986 | 0.23804 | 0.13275
2301.1719 | 122.0627 | -0.073242 | 121.9299 | -0.012131 | 0.0037556 | 0.057486 | 0.051092 | 0.0012261 | -0.0087756 | -0.001741 | -0.005371 | 0.031717 | 0.042849 | 0.0058703 | 0.018743 | 0.02546 | -0.0014891 | 0.1831 | 121.8933 | -0.041199 | 121.8109 | 0.14648 | -0.013733 | 0.027466 | 0.10986 | -0.050354 | -0.004578 | 0.054932 | 0.14191 | 0.11444 | 0.11444 | 0.032043 | -0.036621 | -0.11902 | 0.21973 | 0.10071 | 0.059509 | 0.068665 | 0.027466 | 0.068664 | -121.9803 | -121.875 | 0.21515 | 0.18768 | 0.18768 | 0.11902 | 0.11902 | 0.18768 | 121.8521 | 0.14649 | 0.05951 | 121.9345 | -0.045776 | 121.9666 | 0.022888 | -121.9711 | -121.9345 | 121.8842 | 0.12817 | 0.25635 | 0.18311
2302.9375 | 122.0627 | -0.082397 | 121.9528 | -0.012131 | 0.0052508 | 0.056204 | 0.054083 | 0.0020807 | -0.0074938 | -0.0025956 | -0.005371 | 0.032785 | 0.041994 | 0.0073657 | 0.016821 | 0.026314 | -0.00084805 | 0.15564 | 121.9666 | -0.086975 | 121.7285 | 0.004578 | -0.1236 | -0.09613 | -0.009155 | -0.009155 | -0.050354 | -0.009155 | 0.082397 | 0.050354 | 0.07782 | -0.004578 | 0.013733 | -0.2243 | 0.086975 | -0.013733 | -0.041199 | -0.009155 | -0.036621 | 0.032043 | -121.962 | -121.962 | 0.16479 | 0.16022 | 0.13275 | 0.12817 | 0.10071 | 0.091553 | 121.8155 | 0.13275 | 0.041199 | 122.0535 | 0.041199 | 122.049 | 0.073242 | -122.0398 | -122.0032 | 121.8109 | 0.073242 | 0.23804 | 0.073242
2304.7031 | 122.0123 | -0.09613 | 121.9574 | -0.012131 | 0.0041828 | 0.052786 | 0.052588 | 0.0010125 | -0.0072802 | -0.0025956 | -0.005371 | 0.034066 | 0.043062 | 0.0090747 | 0.015966 | 0.0261 | -0.0042661 | 0.16479 | 121.962 | -0.091553 | 121.6919 | -0.022888 | -0.15564 | -0.10986 | -0.045776 | 0.013733 | -0.050354 | -0.050354 | 0.009155 | 0.004578 | 0.036621 | 0.004577 | 0.004578 | -0.2655 | 0.073242 | -0.013733 | -0.05951 | -0.01831 | -0.064087 | 0.045776 | -121.9437 | -122.0078 | 0.10528 | 0.13275 | 0.10071 | 0.086975 | 0.054932 | 0.068665 | 121.7834 | 0.059509 | 0 | 122.0535 | 0.064087 | 122.0581 | 0.10986 | -122.049 | -122.0078 | 121.788 | 0.045776 | 0.26092 | 0.050354
2306.4844 | 122.0032 | -0.11444 | 121.9574 | -0.0045011 | 0.0065326 | 0.05535 | 0.055792 | -0.0019781 | -0.0087756 | -0.0032364 | -0.005371 | 0.033639 | 0.043276 | 0.0097157 | 0.017461 | 0.024605 | -0.0031979 | 0.25635 | 121.9574 | -0.07782 | 121.7606 | 0.068665 | -0.091553 | -0.073242 | 0.004578 | 0.013733 | -0.050354 | -0.036621 | 0.064087 | 0.022888 | 0.045776 | 0.036621 | 0 | -0.19684 | 0.18311 | 0.041199 | 0.022888 | 0.004578 | -0.013733 | 0.064087 | -121.9437 | -121.994 | 0.17853 | 0.16022 | 0.13733 | 0.09613 | 0.073242 | 0.14649 | 121.8384 | 0.11444 | 0.013733 | 122.0352 | 0.064087 | 122.0718 | 0.12817 | -122.0352 | -122.0078 | 121.875 | 0.07782 | 0.37079 | 0.11902
2308.25 | 122.081 | -0.086975 | 121.9254 | -0.012131 | 0.00097838 | 0.054922 | 0.050879 | -0.0013373 | -0.0059986 | -0.002382 | -0.0084228 | 0.030221 | 0.044344 | 0.00052987 | 0.014684 | 0.026314 | -0.00084805 | 0.13733 | 121.8887 | -0.064087 | 121.756 | 0.073242 | -0.041199 | -0.009155 | 0.013733 | -0.036621 | -0.032043 | 0.009155 | 0.10986 | 0.11444 | 0.086975 | 0.022888 | -0.036621 | -0.16937 | 0.16022 | 0.07782 | 0.045776 | 0.054932 | 0.022888 | 0.054932 | -121.962 | -121.9162 | 0.19684 | 0.17395 | 0.20142 | 0.11902 | 0.14648 | 0.13733 | 121.8201 | 0.14191 | 0.041198 | 121.9528 | -0.004578 | 121.9757 | 0.050354 | -121.9894 | -121.9574 | 121.843 | 0.09613 | 0.2243 | 0.10071
2310 | 122.0306 | -0.10071 | 121.9757 | -0.0045011 | -8.9824e-05 | 0.055563 | 0.05216 | -0.0043281 | -0.0089892 | -0.0021682 | -0.0084228 | 0.031503 | 0.041994 | 0.0071521 | 0.01618 | 0.024605 | -0.00084805 | 0.24261 | 121.8704 | -0.050354 | 121.7834 | 0.10986 | 0 | 0.004578 | 0.032043 | -0.018311 | -0.036621 | -0.032043 | 0.091553 | 0.050354 | 0.041199 | 0.050354 | -0.10529 | -0.19226 | 0.21057 | 0.10529 | 0.10071 | 0.054932 | 0.050354 | 0.064087 | -121.994 | -122.0078 | 0.19226 | 0.14191 | 0.15106 | 0.07782 | 0.086975 | 0.16022 | 121.8338 | 0.12817 | 0.004578 | 121.9208 | 0.01831 | 121.9711 | 0.082397 | -122.0261 | -122.0123 | 121.8842 | 0.068665 | 0.34332 | 0.13275
2311.7031 | 122.1497 | -0.064087 | 121.9391 | -0.012131 | 0.001192 | 0.052359 | 0.049811 | -0.00048286 | -0.010057 | -0.0021682 | -0.0023192 | 0.030435 | 0.043703 | 0.0022389 | 0.016821 | 0.025246 | -0.00020725 | 0.21515 | 121.8979 | -0.064087 | 121.8155 | 0.15564 | 0.036621 | 0.059509 | 0.13275 | -0.032043 | -0.013733 | 0.064087 | 0.1831 | 0.1831 | 0.14191 | 0 | -0.041199 | -0.1236 | 0.21973 | 0.1236 | 0.10071 | 0.1236 | 0.10071 | 0.050354 | -121.9711 | -121.875 | 0.24719 | 0.20599 | 0.24719 | 0.15564 | 0.19684 | 0.21973 | 121.8796 | 0.19684 | 0.07782 | 121.962 | -0.01831 | 121.962 | 0.032044 | -122.0032 | -121.9528 | 121.8796 | 0.12817 | 0.27924 | 0.19684
2313.4531 | 122.1313 | -0.064087 | 121.9666 | -0.012131 | -0.00073062 | 0.054068 | 0.047247 | -0.0015509 | -0.0079212 | -0.0030228 | -0.0023192 | 0.030862 | 0.042635 | 0.0058703 | 0.015752 | 0.024391 | -0.0034117 | 0.23346 | 121.8933 | -0.045776 | 121.843 | 0.16937 | 0.027466 | 0.045776 | 0.11902 | -0.041199 | -0.018311 | 0.045776 | 0.19226 | 0.16022 | 0.12817 | 0.018311 | -0.073242 | -0.1236 | 0.23346 | 0.10986 | 0.091553 | 0.091552 | 0.073242 | 0.045776 | -122.0078 | -121.9208 | 0.25635 | 0.19226 | 0.2243 | 0.14649 | 0.17853 | 0.21515 | 121.8887 | 0.21057 | 0.064087 | 121.9391 | -0.022888 | 121.9574 | 0.022888 | -122.0123 | -121.9849 | 121.907 | 0.10986 | 0.29755 | 0.18311
2315.1406 | 121.9849 | -0.10529 | 121.9711 | -0.012131 | 0.0058918 | 0.055563 | 0.053869 | 0.0010125 | -0.0064258 | -0.0045182 | -0.0084228 | 0.034921 | 0.046053 | 0.013347 | 0.015112 | 0.025032 | -0.0031979 | 0.19226 | 121.9437 | -0.07782 | 121.6736 | -0.032043 | -0.15106 | -0.11444 | -0.059509 | -0.013733 | -0.045776 | -0.073242 | -0.009155 | -0.013733 | 0.018311 | 0.027466 | -0.027465 | -0.29755 | 0.073243 | -0.009155 | -0.045776 | -0.036621 | -0.073242 | 0.05951 | -121.9849 | -122.0444 | 0.096131 | 0.1236 | 0.091553 | 0.064087 | 0.032043 | 0.045777 | 121.7514 | 0.036621 | -0.027466 | 122.0215 | 0.032043 | 122.049 | 0.091553 | -122.049 | -122.0169 | 121.7789 | 0.032044 | 0.29755 | 0.045777
2316.9062 | 122.0078 | -0.11444 | 121.9666 | -0.012131 | 0.00012398 | 0.052786 | 0.052588 | 0.0027215 | -0.008562 | -0.0036636 | -0.0084228 | 0.034494 | 0.045198 | 0.0035205 | 0.013403 | 0.022896 | -0.0085385 | 0.20142 | 121.9528 | -0.10529 | 121.6919 | 0 | -0.10529 | -0.082397 | -0.07782 | -0.004578 | -0.036621 | -0.082397 | 0.018311 | 0.009155 | 0.022888 | 0.009155 | -0.013733 | -0.27466 | 0.11444 | 0.032044 | 0.009155 | 0.022889 | 0 | 0.07782 | -121.9711 | -122.049 | 0.13275 | 0.13733 | 0.1236 | 0.059509 | 0.045776 | 0.10529 | 121.7972 | 0.054932 | -0.045776 | 122.0581 | 0.032043 | 122.0673 | 0.10986 | -122.0718 | -122.0032 | 121.8063 | 0.032044 | 0.31586 | 0.036621
2318.6719 | 122.0398 | -0.09613 | 121.9528 | -0.0045011 | 0.0033282 | 0.054282 | 0.052801 | 0.0022943 | -0.011125 | -0.0019546 | -0.005371 | 0.033426 | 0.045839 | 0.0090747 | 0.017675 | 0.026528 | -0.0021299 | 0.26093 | 121.9437 | -0.073242 | 121.7514 | 0.050354 | -0.059509 | -0.059509 | 0.022888 | -0.009155 | -0.027466 | -0.018311 | 0.086975 | 0.064087 | 0.073242 | 0.022888 | -0.009155 | -0.20142 | 0.14648 | 0.036621 | 0.036621 | 0.013733 | 0.013733 | 0.068664 | -121.962 | -121.9711 | 0.1831 | 0.16937 | 0.16022 | 0.10071 | 0.091553 | 0.1236 | 121.8246 | 0.11444 | 0.009155 | 122.0169 | 0.018311 | 122.0398 | 0.086975 | -122.0261 | -121.9803 | 121.8475 | 0.077819 | 0.35706 | 0.11902
2320.3594 | 121.9849 | -0.11444 | 121.9803 | -0.0045011 | 0.0052508 | 0.055991 | 0.05216 | 0.0042169 | -0.0087756 | -0.0013138 | -0.0084228 | 0.033212 | 0.043917 | 0.012279 | 0.018102 | 0.024178 | -0.0066159 | 0.21973 | 121.9299 | -0.082397 | 121.7102 | 0.004578 | -0.13733 | -0.10986 | -0.050354 | 0.009155 | -0.059509 | -0.068665 | 0.018311 | -0.018311 | 0.018311 | 0.032044 | -0.050354 | -0.27008 | 0.11902 | 0.004578 | -0.022888 | -0.027466 | -0.054932 | 0.054932 | -121.9711 | -122.049 | 0.13275 | 0.13275 | 0.09613 | 0.07782 | 0.041198 | 0.086975 | 121.7926 | 0.07782 | -0.009156 | 122.0123 | 0.068664 | 122.0444 | 0.1236 | -122.0627 | -122.0398 | 121.8246 | 0.045776 | 0.33417 | 0.064087
2322.1094 | 122.0856 | -0.091553 | 121.9116 | -0.01976 | 0.0033282 | 0.053854 | 0.053656 | 0.00037174 | -0.0055712 | -0.0047318 | -0.005371 | 0.032144 | 0.046694 | 0.0082203 | 0.017034 | 0.025887 | -0.0014891 | 0.16022 | 121.9299 | -0.086975 | 121.7285 | 0.032043 | -0.11444 | -0.059509 | 0.013733 | -0.013733 | -0.045776 | 0.018311 | 0.09613 | 0.07782 | 0.10986 | 0.004578 | 0.018311 | -0.1831 | 0.1236 | 0.032044 | -0.022888 | 0.027466 | -0.027466 | 0.045777 | -121.9254 | -121.8933 | 0.18768 | 0.20142 | 0.16937 | 0.15564 | 0.1236 | 0.11902 | 121.8155 | 0.14191 | 0.064087 | 122.0169 | 0.032043 | 122.0215 | 0.07782 | -121.9986 | -121.9574 | 121.8201 | 0.10986 | 0.25177 | 0.10529
2323.7969 | 122.0947 | -0.054932 | 121.9116 | -0.0045011 | 0.0056782 | 0.054495 | 0.052588 | -0.00048286 | -0.0064258 | -0.0032364 | -0.0023192 | 0.030648 | 0.042208 | 0.0086475 | 0.01618 | 0.027596 | 0.00021995 | 0.20142 | 121.9208 | -0.054932 | 121.7972 | 0.14648 | -0.009155 | 0.045776 | 0.10986 | -0.032043 | -0.018311 | 0.054932 | 0.14191 | 0.11902 | 0.11902 | 0 | 0.009155 | -0.11444 | 0.20142 | 0.10071 | 0.045777 | 0.10071 | 0.045777 | 0.036621 | -121.9437 | -121.8567 | 0.19684 | 0.17395 | 0.17395 | 0.13733 | 0.13733 | 0.20142 | 121.8521 | 0.16022 | 0.073243 | 121.9757 | -0.013732 | 121.9757 | 0.022889 | -121.9666 | -121.9299 | 121.8521 | 0.10986 | 0.25635 | 0.16479
2325.5625 | 122.1222 | -0.07782 | 121.9208 | 0.0031279 | 0.00055118 | 0.05535 | 0.050879 | -0.0019781 | -0.0083484 | -0.0021682 | -0.005371 | 0.030862 | 0.043062 | 0.0088611 | 0.016607 | 0.025887 | -0.0019163 | 0.2243 | 121.8887 | -0.036621 | 121.8338 | 0.15564 | 0.041199 | 0.054932 | 0.10529 | -0.018311 | -0.018311 | 0.059509 | 0.18768 | 0.16937 | 0.11902 | 0.041199 | -0.032043 | -0.086975 | 0.23346 | 0.13275 | 0.11902 | 0.091553 | 0.07782 | 0.059509 | -121.9391 | -121.8613 | 0.2655 | 0.19684 | 0.24719 | 0.13733 | 0.18768 | 0.19226 | 121.8704 | 0.20599 | 0.07782 | 121.9254 | 0 | 121.9666 | 0.059509 | -121.9574 | -121.9391 | 121.9116 | 0.13733 | 0.30212 | 0.18311
2327.3281 | 122.0169 | -0.12817 | 121.9482 | -0.012131 | 0.0050372 | 0.055563 | 0.054083 | -0.00091006 | -0.008562 | -0.0055862 | -0.005371 | 0.033426 | 0.043703 | 0.0092883 | 0.017461 | 0.024605 | -0.0034117 | 0.17853 | 121.9803 | -0.091553 | 121.6919 | -0.032043 | -0.15106 | -0.10071 | -0.064087 | 0.004578 | -0.050354 | -0.050354 | 0.009155 | -0.009155 | 0.032043 | 0.036621 | 0.032044 | -0.25635 | 0.096131 | 0.027466 | -0.022888 | -0.009155 | -0.059509 | 0.07782 | -121.9437 | -121.9986 | 0.13733 | 0.16022 | 0.11902 | 0.082397 | 0.041199 | 0.05951 | 121.7834 | 0.059509 | 0 | 122.0718 | 0.054932 | 122.1085 | 0.13275 | -122.0398 | -121.9986 | 121.8201 | 0.07782 | 0.3067 | 0.064087
2329.0938 | 122.0901 | -0.086975 | 121.9345 | -0.012131 | -0.0011578 | 0.055563 | 0.050238 | -5.5462e-05 | -0.0089892 | -0.002382 | -0.005371 | 0.031717 | 0.044558 | 0.0056567 | 0.014684 | 0.024819 | -0.00084805 | 0.15106 | 121.907 | -0.059509 | 121.7606 | 0.059509 | -0.045776 | -0.004578 | 0.036621 | -0.032043 | -0.032043 | -0.004578 | 0.091553 | 0.082397 | 0.10071 | 0.027466 | -0.027466 | -0.17395 | 0.14648 | 0.082397 | 0.041199 | 0.054931 | 0.013733 | 0.054932 | -121.9666 | -121.9391 | 0.17853 | 0.18768 | 0.16937 | 0.13275 | 0.11444 | 0.11902 | 121.8201 | 0.1236 | 0.027465 | 121.9666 | 0 | 121.994 | 0.054932 | -121.994 | -121.9666 | 121.8475 | 0.082397 | 0.23804 | 0.1236
2330.7969 | 122.0306 | -0.13275 | 121.9437 | -0.012131 | 0.0035418 | 0.052573 | 0.054297 | 0.00058534 | -0.0079212 | -0.0038772 | -0.005371 | 0.032144 | 0.045626 | 0.0060841 | 0.014898 | 0.024605 | 0.0025699 | 0.17395 | 121.9528 | -0.10071 | 121.701 | -0.009155 | -0.13275 | -0.10529 | -0.036621 | -0.032043 | -0.059509 | -0.050354 | 0.018311 | 0.018311 | 0.045776 | 0.032043 | 0.009155 | -0.24262 | 0.1236 | 0.027465 | 0 | -0.004578 | -0.032043 | 0.073242 | -121.9757 | -121.994 | 0.15106 | 0.17853 | 0.15106 | 0.10528 | 0.07782 | 0.091553 | 121.8018 | 0.07782 | 0.009155 | 122.0535 | 0.027466 | 122.0856 | 0.10071 | -122.0444 | -122.0032 | 121.8338 | 0.082397 | 0.3067 | 0.09613
2332.5625 | 122.1497 | -0.073242 | 121.9299 | -0.0045011 | -0.002226 | 0.054495 | 0.050451 | -0.0032599 | -0.0092028 | -0.0008866 | -0.005371 | 0.030862 | 0.040926 | 0.0041615 | 0.014257 | 0.0261 | -0.0072569 | 0.20599 | 121.875 | -0.045776 | 121.8201 | 0.16022 | 0.022888 | 0.054932 | 0.10986 | -0.018311 | -0.009155 | 0.068665 | 0.18768 | 0.16937 | 0.15106 | 0.027466 | -0.054932 | -0.10986 | 0.23346 | 0.12817 | 0.09613 | 0.10071 | 0.068664 | 0.064087 | -121.9482 | -121.8613 | 0.26092 | 0.2243 | 0.24261 | 0.16022 | 0.17853 | 0.20599 | 121.8658 | 0.19684 | 0.07782 | 121.9208 | -0.009156 | 121.9482 | 0.054931 | -121.9757 | -121.9391 | 121.8933 | 0.14191 | 0.27924 | 0.18311
2334.2656 | 122.0398 | -0.10071 | 121.9299 | -0.0045011 | 0.002901 | 0.054495 | 0.053015 | -5.5462e-05 | -0.0081348 | -0.0015274 | 0.00073235 | 0.032144 | 0.044771 | 0.015911 | 0.017248 | 0.024605 | -0.0049069 | 0.2655 | 121.9482 | -0.082397 | 121.7468 | 0.045776 | -0.059509 | -0.073242 | 0.013733 | 0.009155 | -0.041199 | -0.022888 | 0.07782 | 0.050354 | 0.082397 | 0.018311 | 0.01831 | -0.18311 | 0.14648 | 0.027466 | 0.041199 | 0.009155 | 0.022888 | 0.059509 | -121.9208 | -121.9528 | 0.17853 | 0.18311 | 0.15106 | 0.1236 | 0.091553 | 0.12817 | 121.8292 | 0.11902 | 0.018311 | 122.0306 | 0.050354 | 122.0489 | 0.10986 | -122.0123 | -121.9711 | 121.8475 | 0.07782 | 0.36621 | 0.11444
2336.0469 | 121.994 | -0.12817 | 121.9803 | -0.0045011 | -0.00094422 | 0.055777 | 0.050665 | -5.5462e-05 | -0.0072802 | -0.0021682 | -0.0023192 | 0.031076 | 0.044985 | 0.01292 | 0.016821 | 0.024819 | -0.0034117 | 0.19226 | 121.9528 | -0.091553 | 121.6965 | 0 | -0.086975 | -0.10071 | -0.073242 | -0.004578 | -0.054932 | -0.082397 | 0.027466 | 0.004578 | 0.032043 | 0.036621 | -0.027466 | -0.28381 | 0.12817 | 0.027466 | 0.041199 | -0.009155 | 0.004578 | 0.073242 | -121.9849 | -122.0627 | 0.15564 | 0.16022 | 0.13275 | 0.086975 | 0.05951 | 0.091553 | 121.788 | 0.082398 | -0.027465 | 122.0444 | 0.050354 | 122.081 | 0.1236 | -122.0718 | -122.0352 | 121.8246 | 0.045777 | 0.32044 | 0.054932
2337.8125 | 122.0032 | -0.1236 | 121.9528 | -0.01976 | 0.00461 | 0.054709 | 0.055151 | -0.0011237 | -0.0077074 | -0.0043046 | -0.0023192 | 0.032571 | 0.046267 | 0.010784 | 0.016821 | 0.025032 | -0.0038389 | 0.19684 | 121.9666 | -0.091553 | 121.6827 | -0.027466 | -0.16022 | -0.1236 | -0.064087 | 0 | -0.059509 | -0.068665 | -0.004578 | -0.013733 | 0.022888 | 0.032043 | 0.013733 | -0.27008 | 0.09613 | 0 | -0.036621 | -0.032043 | -0.068664 | 0.064087 | -121.9528 | -122.0215 | 0.11902 | 0.14648 | 0.10986 | 0.082397 | 0.045776 | 0.064087 | 121.7743 | 0.054931 | -0.009156 | 122.0581 | 0.059509 | 122.0901 | 0.1236 | -122.0444 | -122.0123 | 121.8063 | 0.054931 | 0.32043 | 0.059509
2339.5 | 122.1222 | -0.068665 | 121.9574 | -0.012131 | 0.00055118 | 0.055777 | 0.050665 | -0.0039007 | -0.0083484 | -0.0019546 | -0.0084228 | 0.027017 | 0.043276 | 0.0020251 | 0.014471 | 0.024391 | -0.0046933 | 0.25635 | 121.9208 | -0.045776 | 121.8521 | 0.17395 | 0.054932 | 0.045776 | 0.10529 | -0.045776 | -0.009155 | 0.054932 | 0.17395 | 0.16937 | 0.12817 | 0.022889 | -0.036621 | -0.10528 | 0.24261 | 0.11444 | 0.1236 | 0.091552 | 0.10071 | 0.05951 | -122.0032 | -121.9025 | 0.24261 | 0.19684 | 0.23804 | 0.13733 | 0.17853 | 0.21973 | 121.8979 | 0.1831 | 0.064087 | 121.9666 | -0.036621 | 121.9894 | 0.022889 | -122.0032 | -121.9666 | 121.9208 | 0.1236 | 0.32501 | 0.17395
2341.2812 | 122.0169 | -0.1236 | 121.9711 | 0.0031279 | 0.001192 | 0.052786 | 0.051947 | 0.00079894 | -0.0087756 | -0.0057998 | -0.005371 | 0.032144 | 0.043703 | 0.0090747 | 0.017461 | 0.023751 | -0.0017027 | 0.21057 | 121.9482 | -0.10529 | 121.701 | -0.004578 | -0.10071 | -0.091553 | -0.059509 | 0.009155 | -0.050354 | -0.07782 | 0.041199 | 0.013733 | 0.022888 | 0.01831 | -0.022888 | -0.27008 | 0.11902 | 0.032043 | 0.022888 | 0.013733 | 0.004578 | 0.073242 | -121.962 | -122.049 | 0.16479 | 0.14648 | 0.13733 | 0.073242 | 0.064087 | 0.10071 | 121.8063 | 0.091553 | -0.027466 | 122.0535 | 0.059509 | 122.0718 | 0.13275 | -122.0764 | -122.0215 | 121.8246 | 0.045776 | 0.33417 | 0.064087
2342.9844 | 122.1176 | -0.073242 | 121.9437 | -0.0045011 | 0.0041828 | 0.054922 | 0.053869 | -0.0028327 | -0.0087756 | -0.0028092 | -0.0084228 | 0.033639 | 0.043062 | 0.0097157 | 0.016607 | 0.026955 | -0.0044797 | 0.21515 | 121.9025 | -0.045776 | 121.8155 | 0.14648 | -0.009155 | 0.027466 | 0.11902 | -0.045776 | -0.009155 | 0.07782 | 0.16022 | 0.15106 | 0.12817 | 0.027466 | -0.041199 | -0.12817 | 0.21973 | 0.10071 | 0.064087 | 0.073242 | 0.036621 | 0.064087 | -121.9894 | -121.8658 | 0.23346 | 0.20142 | 0.2243 | 0.13733 | 0.16022 | 0.19226 | 121.8613 | 0.16937 | 0.086975 | 121.9482 | -0.036621 | 121.9757 | 0.027466 | -121.9894 | -121.9528 | 121.8887 | 0.15106 | 0.28839 | 0.19226
2344.7344 | 122.1176 | -0.07782 | 121.9345 | -0.012131 | -0.00073062 | 0.054282 | 0.049811 | 0.00037174 | -0.010057 | -0.0013138 | -0.0084228 | 0.030221 | 0.042421 | 0.013133 | 0.017034 | 0.024391 | -0.0027707 | 0.25177 | 121.9116 | -0.054932 | 121.8155 | 0.16022 | 0.032043 | 0.050354 | 0.09613 | -0.041199 | -0.027466 | 0.045776 | 0.16022 | 0.15564 | 0.1236 | 0.022888 | -0.022888 | -0.11902 | 0.23804 | 0.12817 | 0.10986 | 0.10529 | 0.086975 | 0.050354 | -121.9757 | -121.8887 | 0.23804 | 0.20142 | 0.23346 | 0.15106 | 0.18311 | 0.21515 | 121.8704 | 0.18768 | 0.073242 | 121.9666 | -0.013733 | 121.9894 | 0.036621 | -121.9894 | -121.962 | 121.8933 | 0.1236 | 0.32959 | 0.17395
2346.5 | 122.1176 | -0.073242 | 121.9299 | -0.01976 | 0.0054644 | 0.055777 | 0.053442 | -0.0015509 | -0.0089892 | -0.0025956 | 0.00073235 | 0.030648 | 0.043489 | 0.0028797 | 0.015966 | 0.023964 | -0.0042661 | 0.19684 | 121.9528 | -0.086975 | 121.7606 | 0.068665 | -0.068665 | -0.036621 | 0.054932 | -0.013733 | -0.036621 | 0.041199 | 0.1236 | 0.10529 | 0.13733 | -0.013733 | 0.022888 | -0.16937 | 0.14191 | 0.036621 | 0.004577 | 0.050354 | 0.01831 | 0.036621 | -121.9437 | -121.8887 | 0.19684 | 0.21057 | 0.17853 | 0.17395 | 0.14191 | 0.15564 | 121.8475 | 0.16022 | 0.07782 | 122.0398 | 0.022888 | 122.0261 | 0.059509 | -122.0169 | -121.9666 | 121.8338 | 0.11444 | 0.27008 | 0.12817
2348.1875 | 122.0032 | -0.10986 | 121.994 | 0.0031279 | 0.001833 | 0.054068 | 0.04917 | -0.0041145 | -0.0083484 | -0.000673 | -0.0023192 | 0.031289 | 0.044344 | 0.0086475 | 0.014898 | 0.022255 | -0.0027707 | 0.24261 | 121.8887 | -0.068665 | 121.756 | 0.073242 | -0.041199 | -0.027466 | -0.013733 | -0.004578 | -0.036621 | -0.068665 | 0.045776 | 0.050354 | 0.032043 | 0.041198 | -0.10529 | -0.23804 | 0.18311 | 0.082397 | 0.068664 | 0.041199 | 0.027466 | 0.073242 | -121.9986 | -122.0627 | 0.15564 | 0.14191 | 0.16022 | 0.068664 | 0.086975 | 0.14191 | 121.8246 | 0.082397 | -0.032044 | 121.9574 | 0.032043 | 121.9986 | 0.10529 | -122.0627 | -122.0306 | 121.8658 | 0.041198 | 0.35248 | 0.09613
2349.9375 | 122.1222 | -0.068665 | 121.962 | -0.012131 | 0.00097838 | 0.054282 | 0.050238 | 0.0035761 | -0.010912 | -3.1996e-05 | 0.00073235 | 0.030648 | 0.043062 | 0.0050159 | 0.014043 | 0.02546 | -0.0042661 | 0.26093 | 121.9116 | -0.045776 | 121.8246 | 0.16022 | 0.032043 | 0.050354 | 0.09613 | -0.032043 | 0.009155 | 0.041199 | 0.16937 | 0.15106 | 0.11444 | 0.022889 | -0.050354 | -0.13733 | 0.22888 | 0.11902 | 0.10071 | 0.09613 | 0.077819 | 0.07782 | -121.994 | -121.9208 | 0.23804 | 0.18311 | 0.21973 | 0.10529 | 0.14191 | 0.20599 | 121.8704 | 0.16022 | 0.032044 | 121.9574 | -0.041198 | 121.9803 | 0.036622 | -122.0078 | -121.9528 | 121.8933 | 0.10986 | 0.32959 | 0.16479
2351.7031 | 121.9986 | -0.10986 | 121.9849 | -0.01976 | 0.0056782 | 0.05535 | 0.054937 | 0.0048577 | -0.0059986 | -0.002382 | -0.0023192 | 0.032998 | 0.045626 | 0.014202 | 0.01853 | 0.026741 | -0.0017027 | 0.23346 | 121.9437 | -0.086975 | 121.6919 | -0.022888 | -0.13275 | -0.10529 | -0.064087 | 0.018311 | -0.036621 | -0.091553 | -0.009155 | -0.018311 | 0.022888 | 0.022888 | -0.041198 | -0.29297 | 0.086975 | 0.004577 | -0.022888 | -0.018311 | -0.045776 | 0.073242 | -121.9666 | -122.0764 | 0.10071 | 0.13275 | 0.091552 | 0.059509 | 0.01831 | 0.064087 | 121.7789 | 0.027466 | -0.054932 | 122.0306 | 0.054932 | 122.0535 | 0.12817 | -122.0718 | -122.0215 | 121.8018 | 0.01831 | 0.34332 | 0.045776
2353.4062 | 122.1313 | -0.054932 | 121.9299 | -0.01976 | 0.0041828 | 0.056845 | 0.051733 | -0.00026906 | -0.0077074 | -0.0019546 | 0.00073235 | 0.030862 | 0.042635 | 0.0077929 | 0.017248 | 0.02546 | -0.0038389 | 0.2243 | 121.9208 | -0.050354 | 121.8201 | 0.13275 | -0.022888 | 0.027466 | 0.09613 | -0.041199 | -0.027466 | 0.086975 | 0.15564 | 0.1236 | 0.14648 | 0.004578 | -0.009156 | -0.10986 | 0.18768 | 0.082398 | 0.032044 | 0.07782 | 0.027466 | 0.027466 | -121.9711 | -121.843 | 0.21057 | 0.20142 | 0.17853 | 0.17395 | 0.15106 | 0.18311 | 121.8704 | 0.18311 | 0.11444 | 121.9711 | -0.013733 | 121.9757 | 0.013733 | -121.9803 | -121.9574 | 121.875 | 0.14191 | 0.27924 | 0.15106
2355.1719 | 122.081 | -0.09613 | 121.9482 | -0.012131 | 0.001833 | 0.055136 | 0.050879 | -0.0015509 | -0.0092028 | -0.0040908 | -0.0084228 | 0.030221 | 0.044985 | 0.010784 | 0.015325 | 0.026314 | 0.00086095 | 0.17395 | 121.9116 | -0.068665 | 121.756 | 0.073242 | -0.036621 | -0.022888 | 0.018311 | -0.041199 | -0.036621 | 0.004578 | 0.12817 | 0.10986 | 0.10986 | 0.027465 | -0.036621 | -0.19226 | 0.16937 | 0.073242 | 0.059509 | 0.045777 | 0.032044 | 0.059509 | -121.9894 | -121.9437 | 0.2243 | 0.20599 | 0.20599 | 0.14648 | 0.14648 | 0.14191 | 121.8246 | 0.1648 | 0.041199 | 121.9803 | -0.004578 | 122.0078 | 0.054931 | -122.0169 | -121.9849 | 121.8521 | 0.10071 | 0.27008 | 0.11444
2356.9375 | 121.9986 | -0.1236 | 121.9666 | -0.0045011 | 0.0020466 | 0.053427 | 0.053015 | 0.0022943 | -0.011339 | -0.0028092 | -0.005371 | 0.030862 | 0.04413 | 0.0067249 | 0.015112 | 0.023323 | -0.0023435 | 0.20599 | 121.9208 | -0.091553 | 121.701 | 0.018311 | -0.10529 | -0.073242 | -0.059509 | -0.004578 | -0.054932 | -0.068665 | 0.027466 | 0 | 0.022888 | 0.032043 | -0.045777 | -0.2655 | 0.14191 | 0.050354 | 0.01831 | 0.018311 | -0.013733 | 0.068664 | -121.9711 | -122.0352 | 0.15106 | 0.14648 | 0.1236 | 0.07782 | 0.054932 | 0.10986 | 121.7926 | 0.082398 | -0.013733 | 122.0123 | 0.050354 | 122.0444 | 0.11902 | -122.0581 | -122.0215 | 121.8246 | 0.054931 | 0.32959 | 0.064087
2358.6406 | 122.0078 | -0.1236 | 121.9711 | -0.01976 | -0.0026532 | 0.054068 | 0.05152 | -0.0024055 | -0.0081348 | -0.0040908 | -0.0084228 | 0.032357 | 0.044558 | 0.011638 | 0.018316 | 0.023537 | -0.0029843 | 0.21515 | 121.9254 | -0.09613 | 121.6919 | -0.027466 | -0.10986 | -0.086975 | -0.064087 | -0.004578 | -0.054932 | -0.064087 | 0.027466 | 0.018311 | 0.032043 | 0.027466 | -0.045776 | -0.27923 | 0.09613 | 0.036621 | 0.013733 | 0.009155 | -0.013733 | 0.068664 | -121.9757 | -122.0352 | 0.15106 | 0.15564 | 0.14191 | 0.086975 | 0.073243 | 0.068664 | 121.788 | 0.082398 | -0.009155 | 122.0215 | 0.050354 | 122.049 | 0.11902 | -122.0673 | -122.0261 | 121.8155 | 0.059509 | 0.33875 | 0.059509
2360.4062 | 122.0215 | -0.11902 | 121.9757 | -0.0045011 | -0.0020124 | 0.053854 | 0.050238 | -0.00069646 | -0.00963 | -0.0049454 | -0.011475 | 0.032357 | 0.043489 | 0.0067249 | 0.014684 | 0.024819 | -0.0049069 | 0.21515 | 121.9345 | -0.086975 | 121.6919 | 0.027466 | -0.09613 | -0.082397 | -0.045776 | 0.013733 | -0.064087 | -0.07782 | 0.045776 | 0.022888 | 0.027466 | 0.032044 | -0.041199 | -0.28381 | 0.14649 | 0.036622 | 0.022889 | 0.004578 | -0.009155 | 0.054932 | -121.962 | -122.0535 | 0.16479 | 0.14649 | 0.14191 | 0.091553 | 0.086975 | 0.11444 | 121.7789 | 0.10986 | -0.013733 | 122.0215 | 0.07782 | 122.0535 | 0.13275 | -122.0627 | -122.0398 | 121.8109 | 0.041199 | 0.33417 | 0.073243
2362.1719 | 122.0444 | -0.12817 | 121.9574 | -0.012131 | 0.0065326 | 0.057272 | 0.054937 | 0.0018671 | -0.010057 | -0.0028092 | -0.0023192 | 0.03193 | 0.043062 | 0.0090747 | 0.017675 | 0.024819 | -0.0031979 | 0.19226 | 121.9666 | -0.10529 | 121.701 | 0.009155 | -0.13275 | -0.10071 | -0.022888 | -0.009155 | -0.045776 | -0.032043 | 0.041199 | 0.009155 | 0.059509 | 0.022888 | 0.009156 | -0.25635 | 0.13733 | 0.027466 | -0.004577 | 0.004578 | -0.027465 | 0.082398 | -121.9666 | -121.9894 | 0.16937 | 0.18768 | 0.13733 | 0.10528 | 0.054931 | 0.11444 | 121.8063 | 0.086975 | 0.013733 | 122.0718 | 0.036621 | 122.0947 | 0.11902 | -122.0627 | -122.0032 | 121.8292 | 0.096131 | 0.32044 | 0.10529
2363.9375 | 121.9894 | -0.10986 | 121.9711 | -0.012131 | 0.0069598 | 0.057272 | 0.054937 | 0.0048577 | -0.0064258 | -0.0040908 | -0.0084228 | 0.033212 | 0.044558 | 0.012493 | 0.017034 | 0.023964 | -0.0051205 | 0.19226 | 121.994 | -0.09613 | 121.6644 | -0.041199 | -0.14648 | -0.11902 | -0.059509 | -0.013733 | -0.064087 | -0.068665 | 0.004578 | -0.027466 | 0.032043 | 0.013733 | 0.022889 | -0.3067 | 0.068664 | -0.009156 | -0.036621 | -0.022889 | -0.050354 | 0.045776 | -121.9849 | -122.0398 | 0.11444 | 0.14191 | 0.082397 | 0.09613 | 0.036621 | 0.054931 | 121.7606 | 0.068665 | -0.004578 | 122.0901 | 0.050354 | 122.1039 | 0.09613 | -122.0673 | -122.0352 | 121.7743 | 0.041198 | 0.30212 | 0.050354
2365.6406 | 122.1542 | -0.068665 | 121.9574 | -0.012131 | 0.00097838 | 0.053214 | 0.050238 | -0.00091006 | -0.0072802 | -0.0015274 | -0.0023192 | 0.030008 | 0.043062 | 0.0013843 | 0.015539 | 0.026741 | -0.0072569 | 0.2655 | 121.9025 | -0.054932 | 121.8567 | 0.16937 | 0.036621 | 0.059509 | 0.11902 | -0.036621 | 0 | 0.036621 | 0.19684 | 0.16937 | 0.11444 | 0.013733 | -0.054931 | -0.10071 | 0.23804 | 0.12817 | 0.10529 | 0.11444 | 0.091553 | 0.068665 | -121.994 | -121.9208 | 0.2655 | 0.18311 | 0.23804 | 0.11444 | 0.16937 | 0.22431 | 121.9116 | 0.19684 | 0.036621 | 121.9574 | -0.036621 | 121.9711 | 0.032044 | -122.0123 | -121.9574 | 121.9254 | 0.10529 | 0.33417 | 0.18768
2367.3906 | 122.1268 | -0.086975 | 121.9299 | -0.012131 | 0.00055118 | 0.055563 | 0.049383 | -0.0021919 | -0.0098438 | -0.0045182 | -0.0084228 | 0.028939 | 0.044985 | 0.0013843 | 0.015112 | 0.026528 | -0.0027707 | 0.24719 | 121.8887 | -0.045776 | 121.8246 | 0.1831 | 0.045776 | 0.07782 | 0.14191 | -0.032043 | -0.009155 | 0.050354 | 0.18768 | 0.16479 | 0.13733 | 0.041199 | -0.041199 | -0.10529 | 0.27008 | 0.16479 | 0.13275 | 0.1236 | 0.091552 | 0.07782 | -121.962 | -121.8796 | 0.27466 | 0.2243 | 0.25177 | 0.14648 | 0.17395 | 0.22888 | 121.8704 | 0.19684 | 0.059509 | 121.9345 | -0.022888 | 121.9757 | 0.054932 | -121.9757 | -121.9391 | 121.9116 | 0.13733 | 0.33417 | 0.22888
2369.1406 | 122.0078 | -0.1236 | 121.9803 | -0.0045011 | 0.00033758 | 0.053214 | 0.052588 | -0.00091006 | -0.00963 | 0.0001816 | -0.0023192 | 0.032785 | 0.042635 | 0.0022389 | 0.01618 | 0.025032 | -0.0029843 | 0.22888 | 121.9437 | -0.086975 | 121.7148 | 0.013733 | -0.09613 | -0.068665 | -0.036621 | 0.009155 | -0.041199 | -0.09613 | 0.032043 | 0.032043 | 0.013733 | 0.036621 | -0.036621 | -0.2655 | 0.13733 | 0.054931 | 0.027466 | 0.01831 | -0.009155 | 0.082397 | -121.9711 | -122.0764 | 0.15564 | 0.13733 | 0.15564 | 0.054932 | 0.073242 | 0.10071 | 121.8018 | 0.073242 | -0.054931 | 122.0306 | 0.050354 | 122.0673 | 0.13275 | -122.0673 | -122.0215 | 121.8384 | 0.027466 | 0.35248 | 0.086975
2370.8438 | 122.1451 | -0.064087 | 121.9254 | -0.01976 | 0.0033282 | 0.054709 | 0.05451 | 0.0042169 | -0.0089892 | -0.0032364 | -0.005371 | 0.030648 | 0.043703 | 0.0024525 | 0.016821 | 0.023751 | -0.0055479 | 0.24261 | 121.8933 | -0.059509 | 121.8155 | 0.12817 | -0.022888 | 0.032043 | 0.09613 | -0.032043 | -0.009155 | 0.068665 | 0.14648 | 0.12817 | 0.14191 | 0.004578 | -0.032043 | -0.10986 | 0.19226 | 0.09613 | 0.041199 | 0.091552 | 0.036621 | 0.054932 | -121.9574 | -121.8567 | 0.21057 | 0.20599 | 0.19226 | 0.15106 | 0.13733 | 0.18768 | 121.875 | 0.15564 | 0.07782 | 121.9528 | -0.022888 | 121.9574 | 0.032044 | -121.9849 | -121.9345 | 121.8796 | 0.13275 | 0.3067 | 0.16022
2372.6094 | 122.1085 | -0.07782 | 121.9116 | 0.0031279 | 0.0031146 | 0.056845 | 0.05216 | -0.00091006 | -0.0089892 | -0.005159 | -0.0023192 | 0.030008 | 0.043489 | 0.0043751 | 0.016607 | 0.027596 | -0.0034117 | 0.21973 | 121.9116 | -0.054932 | 121.8201 | 0.15106 | -0.013733 | 0.027466 | 0.10986 | -0.032043 | -0.013733 | 0.054932 | 0.14648 | 0.11444 | 0.10529 | 0.022888 | 0 | -0.091553 | 0.22888 | 0.10529 | 0.064087 | 0.082398 | 0.041199 | 0.064087 | -121.9437 | -121.8567 | 0.2243 | 0.18311 | 0.19226 | 0.11902 | 0.12817 | 0.20599 | 121.875 | 0.16022 | 0.068665 | 121.9666 | -0.01831 | 121.9894 | 0.045777 | -121.9666 | -121.9254 | 121.8979 | 0.13275 | 0.29755 | 0.18768
2374.3125 | 121.9803 | -0.1236 | 121.9757 | -0.01976 | 0.0043964 | 0.054068 | 0.054724 | 0.0012261 | -0.006853 | -0.005159 | -0.005371 | 0.033212 | 0.042849 | 0.010784 | 0.015752 | 0.023537 | 0.00021995 | 0.20142 | 121.9803 | -0.10529 | 121.6873 | -0.041199 | -0.15564 | -0.10986 | -0.10071 | 0.009155 | -0.068665 | -0.064087 | 0.004578 | -0.018311 | 0.032043 | 0.01831 | 0.004578 | -0.28839 | 0.082397 | 0.013733 | -0.032044 | -0.004577 | -0.050354 | 0.054931 | -121.9666 | -122.0398 | 0.12817 | 0.15564 | 0.10528 | 0.10071 | 0.050354 | 0.064087 | 121.7926 | 0.073243 | 0.004578 | 122.0856 | 0.07782 | 122.1039 | 0.13275 | -122.081 | -122.0444 | 121.8109 | 0.059509 | 0.32501 | 0.022888
2376.0781 | 121.9986 | -0.11902 | 121.9574 | -0.01976 | 0.0065326 | 0.056418 | 0.054724 | 0.0012261 | -0.0066394 | -0.0025956 | -0.0084228 | 0.031289 | 0.044985 | 0.0062977 | 0.017461 | 0.024605 | -0.0061887 | 0.2243 | 121.9666 | -0.086975 | 121.6919 | -0.032043 | -0.15106 | -0.12817 | -0.091553 | 0 | -0.068665 | -0.073242 | 0.004578 | -0.032043 | 0.022888 | 0.032044 | 0.009156 | -0.2655 | 0.086976 | -0.009155 | -0.032043 | -0.041199 | -0.064087 | 0.050354 | -121.9574 | -122.0306 | 0.1236 | 0.14191 | 0.086976 | 0.091553 | 0.036622 | 0.054932 | 121.7789 | 0.073243 | -0.004577 | 122.0535 | 0.068665 | 122.0856 | 0.11902 | -122.0444 | -122.0261 | 121.8109 | 0.045777 | 0.34332 | 0.027466
2377.8438 | 122.0901 | -0.064087 | 121.9574 | -0.012131 | 0.00033758 | 0.055777 | 0.049597 | -0.0032599 | -0.0077074 | -0.0002456 | -0.005371 | 0.028939 | 0.04413 | -0.0054517 | 0.015966 | 0.025246 | -0.0023435 | 0.27008 | 121.9254 | -0.059509 | 121.8109 | 0.14191 | 0.018311 | 0.041199 | 0.07782 | -0.018311 | -0.027466 | 0.027466 | 0.15106 | 0.1236 | 0.10986 | 0.004578 | -0.032043 | -0.14648 | 0.20599 | 0.10529 | 0.082398 | 0.10071 | 0.07782 | 0.036621 | -121.9757 | -121.9299 | 0.21515 | 0.17395 | 0.18768 | 0.13733 | 0.15106 | 0.20142 | 121.8704 | 0.17853 | 0.054932 | 121.9849 | 0.009155 | 121.9894 | 0.045776 | -122.0169 | -121.9849 | 121.875 | 0.091553 | 0.33417 | 0.14191
2379.5312 | 122.0352 | -0.10986 | 121.9437 | -0.01976 | 0.0014056 | 0.055136 | 0.05216 | 0.00015814 | -0.0077074 | -0.000673 | -0.0084228 | 0.032357 | 0.044558 | 0.0088611 | 0.01618 | 0.027169 | -0.0034117 | 0.1831 | 121.9666 | -0.091553 | 121.6919 | -0.004578 | -0.14191 | -0.09613 | -0.027466 | -0.009155 | -0.045776 | -0.027466 | 0.064087 | 0.027466 | 0.059509 | 0.01831 | 0.022888 | -0.25177 | 0.10529 | 0.013733 | -0.032044 | -0.004577 | -0.050354 | 0.064087 | -121.9528 | -121.9711 | 0.17395 | 0.16937 | 0.13733 | 0.10528 | 0.073242 | 0.086975 | 121.7834 | 0.10986 | 0.01831 | 122.0581 | 0.036621 | 122.0764 | 0.10071 | -122.0352 | -121.9894 | 121.8018 | 0.082397 | 0.29297 | 0.082397
2381.2969 | 122.1359 | -0.059509 | 121.9391 | 0.0031279 | 0.0035418 | 0.05535 | 0.050451 | 0.0031487 | -0.0062122 | -0.0030228 | -0.005371 | 0.029367 | 0.043489 | -0.0035291 | 0.014684 | 0.025887 | -0.0068295 | 0.2243 | 121.9162 | -0.041199 | 121.8292 | 0.14648 | -0.004578 | 0.027466 | 0.10986 | -0.032043 | -0.018311 | 0.054932 | 0.16937 | 0.14191 | 0.13275 | 0.01831 | -0.022888 | -0.10986 | 0.20599 | 0.086975 | 0.054931 | 0.068665 | 0.036621 | 0.041198 | -121.9711 | -121.8842 | 0.22888 | 0.19226 | 0.20142 | 0.15106 | 0.16022 | 0.18768 | 121.8704 | 0.18768 | 0.073243 | 121.9574 | -0.013732 | 121.9757 | 0.027466 | -121.9803 | -121.9574 | 121.8887 | 0.11444 | 0.28381 | 0.16937
2383 | 122.0352 | -0.10529 | 121.9482 | -0.0045011 | 0.0037556 | 0.055991 | 0.055151 | -0.0026191 | -0.0081348 | -0.001741 | -0.005371 | 0.030435 | 0.044771 | 0.018901 | 0.017889 | 0.026314 | -0.0029843 | 0.17395 | 121.9849 | -0.10986 | 121.6919 | -0.013733 | -0.13733 | -0.09613 | -0.045776 | 0.009155 | -0.041199 | -0.036621 | 0.027466 | 0.013733 | 0.036621 | -0.004577 | 0.036621 | -0.25635 | 0.091553 | 0.009156 | -0.032043 | 0.013733 | -0.027466 | 0.064087 | -121.9391 | -121.9849 | 0.13275 | 0.14191 | 0.11902 | 0.07782 | 0.054932 | 0.09613 | 121.8018 | 0.068665 | 0.004578 | 122.0947 | 0.050354 | 122.0901 | 0.11444 | -122.0581 | -121.9894 | 121.7972 | 0.068665 | 0.27924 | 0.05951
2384.75 | 122.0947 | -0.073242 | 121.9437 | -0.012131 | 0.0050372 | 0.05834 | 0.050238 | -0.0051825 | -0.0057848 | -0.002382 | -0.0084228 | 0.028085 | 0.044985 | 0.0043751 | 0.016607 | 0.027382 | -0.0055479 | 0.21973 | 121.9208 | -0.059509 | 121.8246 | 0.14648 | -0.004578 | 0.032043 | 0.10529 | -0.027466 | -0.009155 | 0.041199 | 0.15106 | 0.1236 | 0.11902 | 0.013733 | -0.022889 | -0.11902 | 0.21973 | 0.10529 | 0.068664 | 0.091552 | 0.054931 | 0.064087 | -121.9711 | -121.9025 | 0.2243 | 0.19226 | 0.19684 | 0.12817 | 0.13275 | 0.20599 | 121.8842 | 0.16022 | 0.050354 | 121.9803 | -0.018311 | 121.994 | 0.045776 | -122.0032 | -121.9528 | 121.8979 | 0.11444 | 0.29297 | 0.17853
2386.5 | 122.0078 | -0.11902 | 121.9574 | 0.0031279 | 0.0065326 | 0.056418 | 0.053015 | 0.00058534 | -0.0064258 | -0.0008866 | -0.0023192 | 0.031289 | 0.045839 | 0.0097157 | 0.015539 | 0.02311 | -0.0025571 | 0.19684 | 121.9437 | -0.07782 | 121.6919 | -0.027466 | -0.15106 | -0.10529 | -0.045776 | 0.018311 | -0.050354 | -0.073242 | 0 | -0.009155 | 0.045776 | 0.041199 | -0.013732 | -0.2655 | 0.091553 | 0.013733 | -0.032043 | -0.027466 | -0.073242 | 0.068665 | -121.9391 | -122.0306 | 0.11902 | 0.16479 | 0.10986 | 0.09613 | 0.041199 | 0.050354 | 121.7697 | 0.050354 | -0.022888 | 122.0215 | 0.068665 | 122.0627 | 0.13733 | -122.0352 | -122.0078 | 121.8109 | 0.045777 | 0.31586 | 0.073243
2388.2656 | 122.0078 | -0.11444 | 121.994 | -0.012131 | 0.0033282 | 0.054495 | 0.052588 | 0.0025079 | -0.0055712 | -0.0011002 | -0.005371 | 0.030435 | 0.044558 | 0.0045887 | 0.018102 | 0.025673 | -0.0053343 | 0.27924 | 121.9528 | -0.07782 | 121.7331 | 0.041199 | -0.10529 | -0.086975 | -0.018311 | 0.009155 | -0.045776 | -0.045776 | 0.018311 | 0 | 0.027466 | 0.036621 | -0.041199 | -0.26093 | 0.15564 | 0.027466 | 0.009155 | -0.009155 | -0.027466 | 0.068665 | -121.9849 | -122.0398 | 0.13275 | 0.14191 | 0.11444 | 0.073242 | 0.045776 | 0.11902 | 121.8109 | 0.064087 | 0 | 122.0306 | 0.054931 | 122.0673 | 0.1236 | -122.0718 | -122.0398 | 121.8475 | 0.068665 | 0.39368 | 0.09613
2389.9531 | 122.113 | -0.073242 | 121.9711 | -0.0045011 | 0.00076478 | 0.055563 | 0.04917 | -0.0024055 | -0.0077074 | 0.0008224 | -0.005371 | 0.031076 | 0.045626 | 0.0058703 | 0.017461 | 0.026955 | -0.0042661 | 0.27008 | 121.9025 | -0.045776 | 121.8246 | 0.15106 | 0.018311 | 0.045776 | 0.10071 | -0.041199 | -0.027466 | 0.041199 | 0.16479 | 0.14191 | 0.11444 | 0.027466 | -0.068664 | -0.14648 | 0.2243 | 0.11902 | 0.091553 | 0.091552 | 0.064087 | 0.045776 | -122.0123 | -121.9299 | 0.23804 | 0.18768 | 0.21515 | 0.14191 | 0.16937 | 0.19684 | 121.8704 | 0.19226 | 0.068665 | 121.9482 | -0.013733 | 121.9757 | 0.032043 | -122.0169 | -121.9986 | 121.8979 | 0.11444 | 0.34332 | 0.17395
2391.7188 | 122.1451 | -0.09613 | 121.9482 | -0.0045011 | -0.0011578 | 0.052786 | 0.050451 | -0.0021919 | -0.0094164 | -0.0030228 | -0.0023192 | 0.030008 | 0.045839 | 0.0065113 | 0.014471 | 0.025246 | -0.0034117 | 0.21515 | 121.9254 | -0.064087 | 121.7926 | 0.11444 | 0.004578 | 0.036621 | 0.10071 | -0.041199 | -0.013733 | 0.059509 | 0.16022 | 0.1831 | 0.13733 | 0.032043 | -0.022888 | -0.15564 | 0.21057 | 0.13275 | 0.10071 | 0.10071 | 0.068665 | 0.082397 | -121.9894 | -121.8887 | 0.25635 | 0.23346 | 0.27924 | 0.15106 | 0.19684 | 0.17853 | 121.8567 | 0.17395 | 0.073242 | 121.9894 | -0.027466 | 122.0215 | 0.054931 | -122.0123 | -121.962 | 121.8887 | 0.15564 | 0.31128 | 0.19684
2393.4844 | 122.0032 | -0.11444 | 121.9803 | -0.0045011 | 0.0022602 | 0.053641 | 0.053228 | 0.0037897 | -0.0081348 | -0.0021682 | -0.005371 | 0.032144 | 0.044344 | 0.01057 | 0.018102 | 0.02546 | -0.0051205 | 0.27008 | 121.962 | -0.082397 | 121.7285 | 0.022888 | -0.11444 | -0.082397 | -0.022888 | 0.004578 | -0.027466 | -0.054932 | 0.022888 | -0.004578 | 0.027466 | 0.032044 | -0.018311 | -0.25177 | 0.13733 | 0.032044 | 0 | 0 | -0.032044 | 0.086975 | -121.9757 | -122.0352 | 0.13733 | 0.14191 | 0.10986 | 0.054932 | 0.022888 | 0.10528 | 121.8109 | 0.050354 | -0.027466 | 122.0444 | 0.032044 | 122.0764 | 0.11902 | -122.0627 | -122.0078 | 121.843 | 0.059509 | 0.38452 | 0.091553
2395.25 | 122.1039 | -0.07782 | 121.9528 | -0.0045011 | 0.0037556 | 0.054709 | 0.053015 | -0.00026906 | -0.008562 | -0.005159 | -0.005371 | 0.029794 | 0.043276 | 0.0092883 | 0.015112 | 0.026314 | -0.0023435 | 0.19684 | 121.9528 | -0.10071 | 121.7285 | 0.036621 | -0.10986 | -0.073242 | 0.013733 | -0.018311 | -0.036621 | 0.013733 | 0.091553 | 0.082397 | 0.11444 | -0.022888 | 0 | -0.2243 | 0.11444 | 0.004578 | -0.032043 | 0.027466 | -0.009155 | 0.041199 | -121.9711 | -121.9391 | 0.16937 | 0.19226 | 0.16022 | 0.15106 | 0.11902 | 0.13733 | 121.8292 | 0.12817 | 0.050354 | 122.0535 | 0.01831 | 122.0306 | 0.059509 | -122.0535 | -121.9894 | 121.8063 | 0.091553 | 0.27466 | 0.091553
2397.0156 | 122.0032 | -0.10986 | 121.9757 | -0.02739 | 0.0031146 | 0.054495 | 0.055578 | 0.0059259 | -0.00963 | -0.0021682 | -0.0084228 | 0.030008 | 0.045839 | 0.010997 | 0.017248 | 0.026741 | -0.0072569 | 0.2243 | 121.962 | -0.091553 | 121.6782 | -0.054932 | -0.16937 | -0.14648 | -0.073242 | 0 | -0.064087 | -0.050354 | 0 | 0 | 0.041199 | 0.01831 | -0.013733 | -0.29755 | 0.054931 | -0.036621 | -0.05951 | -0.054931 | -0.07782 | 0.045776 | -121.9757 | -122.0261 | 0.10986 | 0.15106 | 0.10986 | 0.10529 | 0.064087 | 0.036621 | 121.7697 | 0.064087 | 0.013733 | 122.0535 | 0.064087 | 122.0718 | 0.10986 | -122.0673 | -122.0398 | 121.788 | 0.059509 | 0.33417 | 0.036621
2398.7031 | 122.1039 | -0.086975 | 121.9391 | -0.012131 | -0.00030342 | 0.053854 | 0.04917 | 0.0016535 | -0.0094164 | 0.0003952 | -0.005371 | 0.029367 | 0.042635 | 0.0026661 | 0.014684 | 0.026741 | -0.0023435 | 0.27924 | 121.8979 | -0.054932 | 121.8246 | 0.14191 | 0.022888 | 0.036621 | 0.091553 | -0.036621 | -0.018311 | 0.027466 | 0.15106 | 0.14191 | 0.11902 | 0.032043 | -0.041199 | -0.11444 | 0.22888 | 0.1236 | 0.10986 | 0.091553 | 0.07782 | 0.068664 | -121.9757 | -121.9116 | 0.23804 | 0.20599 | 0.22888 | 0.13733 | 0.16022 | 0.19684 | 121.8796 | 0.16937 | 0.045777 | 121.9528 | -0.01831 | 121.9849 | 0.050354 | -121.994 | -121.9574 | 121.9116 | 0.11444 | 0.36621 | 0.17853
2400.4688 | 122.0947 | -0.082397 | 121.9803 | -0.0045011 | 0.0022602 | 0.051932 | 0.048102 | -0.00026906 | -0.0083484 | -3.1996e-05 | -0.0084228 | 0.031076 | 0.043917 | 0.0071521 | 0.012548 | 0.024391 | -0.0044797 | 0.27008 | 121.9025 | -0.068665 | 121.8063 | 0.13733 | 0.018311 | 0.045776 | 0.082397 | -0.027466 | -0.013733 | 0.036621 | 0.15106 | 0.14191 | 0.11902 | 0.013732 | -0.07782 | -0.17395 | 0.21973 | 0.12817 | 0.10071 | 0.11444 | 0.086976 | 0.068664 | -122.0078 | -121.9437 | 0.23346 | 0.20142 | 0.2243 | 0.13275 | 0.15564 | 0.20599 | 121.875 | 0.16479 | 0.050354 | 121.9711 | -0.013733 | 121.9849 | 0.054931 | -122.049 | -121.994 | 121.8887 | 0.11902 | 0.35248 | 0.16479
2402.2344 | 122.1359 | -0.07782 | 121.9299 | -0.0045011 | 0.0067462 | 0.053854 | 0.053869 | -0.0011237 | -0.0059986 | -0.0004592 | -0.0023192 | 0.02958 | 0.044344 | 0.013133 | 0.016607 | 0.025032 | -0.0014891 | 0.24261 | 121.9391 | -0.073242 | 121.8109 | 0.10529 | 0.004578 | 0.027466 | 0.086975 | -0.032043 | 0 | 0.054932 | 0.14648 | 0.11902 | 0.16022 | 0.004578 | 0.009155 | -0.11902 | 0.18311 | 0.10529 | 0.082398 | 0.10071 | 0.07782 | 0.07782 | -121.962 | -121.875 | 0.2243 | 0.23804 | 0.19684 | 0.16022 | 0.11902 | 0.17853 | 121.8842 | 0.14648 | 0.054932 | 122.0123 | -0.032043 | 122.0169 | 0.045777 | -122.0032 | -121.9299 | 121.8887 | 0.13275 | 0.32044 | 0.16479
2403.9375 | 121.9986 | -0.13733 | 121.994 | -0.012131 | 0.0016192 | 0.053 | 0.053015 | -0.00048286 | -0.010698 | -0.001741 | -0.005371 | 0.031289 | 0.043917 | 0.0080067 | 0.015752 | 0.023537 | -0.0031979 | 0.22888 | 121.9528 | -0.10071 | 121.7056 | -0.009155 | -0.10986 | -0.086975 | -0.045776 | 0 | -0.064087 | -0.091553 | 0.027466 | 0.018311 | 0.013733 | 0.036621 | -0.041199 | -0.28839 | 0.12817 | 0.050354 | 0.027466 | 0.013733 | -0.009155 | 0.073242 | -121.994 | -122.0856 | 0.16479 | 0.15106 | 0.15564 | 0.07782 | 0.082398 | 0.091553 | 121.8063 | 0.091553 | -0.027466 | 122.0535 | 0.064087 | 122.0901 | 0.13733 | -122.0947 | -122.0581 | 121.843 | 0.045776 | 0.36621 | 0.091553
2405.6875 | 122.1451 | -0.07782 | 121.9345 | -0.01976 | 0.00033758 | 0.052786 | 0.049811 | -0.0021919 | -0.0083484 | -0.0032364 | -0.0023192 | 0.030862 | 0.043489 | 0.0060841 | 0.015112 | 0.026528 | -0.0021299 | 0.27008 | 121.8796 | -0.073242 | 121.8155 | 0.17395 | 0.041199 | 0.050354 | 0.13733 | -0.041199 | -0.013733 | 0.064087 | 0.19226 | 0.17853 | 0.13275 | 0.004578 | -0.054931 | -0.11902 | 0.25177 | 0.12817 | 0.11902 | 0.1236 | 0.11444 | 0.064087 | -121.9757 | -121.8704 | 0.27008 | 0.21057 | 0.25635 | 0.14648 | 0.19226 | 0.24719 | 121.8887 | 0.20599 | 0.07782 | 121.9528 | -0.027466 | 121.9574 | 0.036621 | -122.0078 | -121.9482 | 121.8933 | 0.14191 | 0.3479 | 0.21515
2407.4531 | 122.0032 | -0.10986 | 122.0078 | -0.01976 | 0.00097838 | 0.052145 | 0.051733 | 0.00058534 | -0.0087756 | -0.0030228 | -0.0023192 | 0.030648 | 0.045626 | 0.010997 | 0.01618 | 0.0261 | -0.0031979 | 0.23804 | 121.9437 | -0.07782 | 121.7056 | 0.009155 | -0.10529 | -0.064087 | -0.050354 | -0.018311 | -0.073242 | -0.07782 | 0.036621 | 0.009155 | 0.027466 | 0.032043 | -0.064086 | -0.30212 | 0.11902 | 0.045776 | 0.004577 | 0.013733 | -0.027466 | 0.036621 | -122.0261 | -122.0856 | 0.14648 | 0.13733 | 0.11902 | 0.10071 | 0.082397 | 0.086975 | 121.7834 | 0.10986 | -0.004578 | 122.0215 | 0.054931 | 122.0535 | 0.091552 | -122.0856 | -122.081 | 121.8155 | 0.032043 | 0.3479 | 0.059509
2409.1562 | 122.1222 | -0.073242 | 121.9528 | -0.012131 | 0.0039692 | 0.054709 | 0.052374 | 0.0037897 | -0.0087756 | -0.0025956 | -0.0084228 | 0.029367 | 0.043703 | 0.0088611 | 0.017889 | 0.02311 | -0.0046933 | 0.21973 | 121.9391 | -0.082397 | 121.756 | 0.073242 | -0.073242 | -0.027466 | 0.068665 | -0.036621 | -0.036621 | 0.041199 | 0.13275 | 0.11444 | 0.15106 | -0.009155 | -0.013733 | -0.19684 | 0.14648 | 0.045776 | 0 | 0.054931 | 0.009155 | 0.036621 | -121.9894 | -121.9116 | 0.20599 | 0.2243 | 0.18768 | 0.18768 | 0.15106 | 0.15564 | 121.8384 | 0.16937 | 0.07782 | 122.0215 | 0 | 122.0123 | 0.036621 | -122.0352 | -121.9894 | 121.8292 | 0.11444 | 0.29297 | 0.14191
2410.9219 | 122.1497 | -0.086975 | 121.9528 | -0.012131 | 0.001192 | 0.051932 | 0.051733 | -0.00091006 | -0.011766 | -0.0004592 | -0.005371 | 0.029367 | 0.042635 | -0.00011113 | 0.017675 | 0.023323 | -0.0053343 | 0.24719 | 121.8979 | -0.054932 | 121.8155 | 0.16479 | 0.041199 | 0.059509 | 0.13275 | -0.041199 | -0.022888 | 0.059509 | 0.21057 | 0.1831 | 0.15564 | 0.032043 | -0.054932 | -0.13733 | 0.25177 | 0.14648 | 0.12817 | 0.11444 | 0.096131 | 0.064087 | -121.994 | -121.8933 | 0.29755 | 0.24261 | 0.27008 | 0.17853 | 0.20599 | 0.21973 | 121.8704 | 0.23346 | 0.082397 | 121.9528 | -0.018311 | 121.9849 | 0.045776 | -122.0078 | -121.9757 | 121.9025 | 0.14648 | 0.33417 | 0.21973
2412.6875 | 122.0627 | -0.086975 | 121.9528 | -0.012131 | 0.0039692 | 0.053641 | 0.05451 | 0.0035761 | -0.006853 | -0.005159 | -0.0023192 | 0.031717 | 0.044558 | 0.0075793 | 0.016821 | 0.023964 | -0.0044797 | 0.27466 | 121.9482 | -0.082397 | 121.7285 | 0.009155 | -0.091553 | -0.068665 | -0.032043 | -0.009155 | -0.018311 | -0.036621 | 0.068665 | 0.045776 | 0.068665 | 0.004578 | -0.004578 | -0.2243 | 0.09613 | 0.01831 | -0.004578 | 0.013732 | -0.009156 | 0.068664 | -121.962 | -121.9894 | 0.15564 | 0.15564 | 0.13275 | 0.086976 | 0.064087 | 0.091552 | 121.8109 | 0.086976 | -0.01831 | 122.0306 | 0.009156 | 122.0352 | 0.07782 | -122.0352 | -121.9711 | 121.8155 | 0.050354 | 0.36163 | 0.054932
2414.3906 | 122.1268 | -0.07782 | 121.9482 | -0.01976 | 0.00033758 | 0.055777 | 0.051306 | -0.0047553 | -0.0092028 | -0.0030228 | -0.005371 | 0.02958 | 0.044344 | 0.0056567 | 0.014471 | 0.025246 | -0.0038389 | 0.18768 | 121.8979 | -0.073242 | 121.7651 | 0.07782 | -0.032043 | -0.004578 | 0.045776 | -0.041199 | -0.027466 | 0.022888 | 0.13275 | 0.11444 | 0.11902 | 0.004578 | -0.050354 | -0.1831 | 0.15564 | 0.073242 | 0.045777 | 0.068664 | 0.041199 | 0.050354 | -121.9894 | -121.9254 | 0.21057 | 0.19684 | 0.19226 | 0.14649 | 0.14191 | 0.15106 | 121.8384 | 0.16022 | 0.050354 | 121.9711 | -0.013733 | 121.9757 | 0.036621 | -122.0215 | -121.9757 | 121.843 | 0.10071 | 0.2655 | 0.1236
2416.1406 | 122.1359 | -0.082397 | 121.8979 | -0.01976 | 0.0026874 | 0.054495 | 0.053228 | -0.0030463 | -0.0077074 | -0.001741 | -0.005371 | 0.027658 | 0.044771 | 0.0099293 | 0.014684 | 0.025246 | -0.0029843 | 0.24261 | 121.907 | -0.064087 | 121.8292 | 0.14648 | -0.009155 | 0.032043 | 0.10529 | -0.041199 | -0.009155 | 0.054932 | 0.14648 | 0.13733 | 0.13275 | 0.01831 | 0.009155 | -0.068664 | 0.22888 | 0.11444 | 0.073242 | 0.09613 | 0.054932 | 0.073242 | -121.9391 | -121.843 | 0.22888 | 0.21515 | 0.21973 | 0.14191 | 0.14648 | 0.21057 | 121.8933 | 0.15564 | 0.064087 | 121.9711 | -0.032044 | 121.9894 | 0.041198 | -121.962 | -121.907 | 121.9116 | 0.13733 | 0.32501 | 0.18768
2417.9062 | 122.0947 | -0.09613 | 121.9391 | -0.012131 | 0.0016192 | 0.053641 | 0.051733 | 0.0016535 | -0.0087756 | -0.0021682 | -0.005371 | 0.028939 | 0.04413 | 0.0043751 | 0.014471 | 0.02845 | -0.0017027 | 0.19226 | 121.9162 | -0.064087 | 121.7743 | 0.07782 | -0.036621 | -0.013733 | 0.009155 | -0.036621 | -0.027466 | 0.013733 | 0.1236 | 0.10986 | 0.10986 | 0.032043 | -0.022888 | -0.16479 | 0.17395 | 0.082397 | 0.059509 | 0.050354 | 0.027466 | 0.068664 | -121.9757 | -121.9254 | 0.21973 | 0.20599 | 0.20599 | 0.13733 | 0.13733 | 0.14191 | 121.8384 | 0.15106 | 0.041199 | 121.9803 | -0.009155 | 122.0123 | 0.059509 | -122.0032 | -121.9666 | 121.8704 | 0.10986 | 0.28839 | 0.10528
2419.6562 | 122.1405 | -0.07782 | 121.9437 | -0.012131 | 0.00055118 | 0.053214 | 0.051092 | -0.0021919 | -0.0089892 | -0.0030228 | -0.0023192 | 0.028939 | 0.043276 | 0.0015979 | 0.014898 | 0.025673 | -0.0029843 | 0.27466 | 121.8704 | -0.050354 | 121.8384 | 0.17853 | 0.041199 | 0.068665 | 0.14648 | -0.036621 | -0.018311 | 0.054932 | 0.18768 | 0.15106 | 0.13275 | 0.027466 | -0.073243 | -0.10529 | 0.25635 | 0.14649 | 0.11902 | 0.11902 | 0.091553 | 0.059509 | -121.9803 | -121.8887 | 0.2655 | 0.21057 | 0.22888 | 0.15106 | 0.16937 | 0.22888 | 121.8887 | 0.20599 | 0.073243 | 121.9208 | -0.01831 | 121.9482 | 0.041199 | -121.994 | -121.962 | 121.9162 | 0.13275 | 0.35248 | 0.2243
2421.4219 | 122.0306 | -0.11444 | 121.962 | -0.012131 | 0.0016192 | 0.055563 | 0.053015 | -0.0013373 | -0.0098438 | -0.0025956 | -0.0023192 | 0.029367 | 0.042849 | 0.0048023 | 0.016821 | 0.024178 | -0.0017027 | 0.24719 | 121.9574 | -0.091553 | 121.6965 | -0.004578 | -0.10986 | -0.086975 | -0.068665 | 0.018311 | -0.068665 | -0.059509 | 0.045776 | 0.027466 | 0.032043 | 0.022888 | -0.004578 | -0.2655 | 0.10986 | 0.027466 | 0.004578 | 0.004578 | -0.01831 | 0.045776 | -121.9437 | -122.0215 | 0.16022 | 0.14648 | 0.14191 | 0.10071 | 0.096131 | 0.086975 | 121.788 | 0.11444 | 0.009156 | 122.049 | 0.086976 | 122.0718 | 0.13275 | -122.0535 | -122.0306 | 121.8109 | 0.054932 | 0.36163 | 0.045776
2423.1406 | 122.0261 | -0.1236 | 121.9757 | -0.0045011 | 0.0050372 | 0.052786 | 0.054083 | 0.0027215 | -0.01198 | -0.0040908 | -0.0084228 | 0.03193 | 0.044344 | 0.0086475 | 0.018316 | 0.023751 | -0.0059751 | 0.21515 | 121.9574 | -0.082397 | 121.701 | -0.022888 | -0.15564 | -0.1236 | -0.050354 | 0.013733 | -0.054932 | -0.07782 | 0 | 0.004578 | 0.045776 | 0.041199 | -0.018311 | -0.27466 | 0.10071 | 0 | -0.032044 | -0.041199 | -0.073243 | 0.068664 | -121.962 | -122.0535 | 0.1236 | 0.16937 | 0.12817 | 0.10071 | 0.05951 | 0.059509 | 121.7834 | 0.054932 | -0.022888 | 122.0398 | 0.068665 | 122.081 | 0.13733 | -122.0581 | -122.0306 | 121.8246 | 0.045776 | 0.33875 | 0.073242
2424.9062 | 122.0947 | -0.10071 | 121.962 | -0.01976 | 0.0016192 | 0.053427 | 0.050238 | -0.0013373 | -0.0092028 | -0.0045182 | -0.0084228 | 0.029794 | 0.044558 | 0.010784 | 0.016821 | 0.024819 | -0.00084805 | 0.19226 | 121.9025 | -0.064087 | 121.7606 | 0.064087 | -0.041199 | -0.009155 | 0.041199 | -0.027466 | -0.032043 | 0.004578 | 0.10529 | 0.091553 | 0.09613 | 0.036621 | -0.059509 | -0.20142 | 0.1648 | 0.091553 | 0.059509 | 0.054932 | 0.022888 | 0.068665 | -121.9894 | -121.9574 | 0.20599 | 0.19684 | 0.19226 | 0.12817 | 0.1236 | 0.12817 | 121.8246 | 0.13733 | 0.036621 | 121.9666 | 0.004577 | 122.0032 | 0.073242 | -122.0261 | -121.994 | 121.8613 | 0.10529 | 0.29297 | 0.14191
2426.5938 | 122.0078 | -0.11902 | 121.9666 | -0.0045011 | 0.00461 | 0.054282 | 0.054297 | 0.0067803 | -0.0092028 | -0.0004592 | -0.005371 | 0.036203 | 0.043276 | 0.011638 | 0.021093 | 0.024391 | -0.0040525 | 0.28839 | 121.9299 | -0.068665 | 121.7331 | 0.018311 | -0.12817 | -0.086975 | -0.041199 | 0.009155 | -0.036621 | -0.059509 | 0.027466 | -0.018311 | 0.032043 | 0.050354 | -0.036621 | -0.23346 | 0.13733 | 0.032044 | -0.009155 | -0.01831 | -0.059509 | 0.082398 | -121.9574 | -122.0261 | 0.14649 | 0.15106 | 0.10071 | 0.068664 | 0.01831 | 0.086976 | 121.8018 | 0.064087 | -0.022888 | 121.9986 | 0.045776 | 122.049 | 0.12817 | -122.0352 | -122.0032 | 121.8521 | 0.05951 | 0.40741 | 0.07782
2428.375 | 122.0627 | -0.09613 | 121.9803 | -0.012131 | 0.0058918 | 0.054068 | 0.053656 | -0.0017645 | -0.0081348 | -0.0030228 | -0.0023192 | 0.032357 | 0.046053 | 0.0065113 | 0.018743 | 0.027382 | -0.0034117 | 0.20599 | 121.9437 | -0.07782 | 121.701 | 0.009155 | -0.14191 | -0.10071 | -0.036621 | -0.013733 | -0.032043 | -0.041199 | 0.045776 | 0.022888 | 0.073242 | 0.01831 | -0.036621 | -0.27924 | 0.10528 | -0.004578 | -0.045777 | -0.022888 | -0.064087 | 0.064087 | -121.994 | -122.0215 | 0.14191 | 0.16937 | 0.11902 | 0.10529 | 0.054931 | 0.086975 | 121.7789 | 0.077819 | -0.009156 | 122.0215 | 0.01831 | 122.0398 | 0.082397 | -122.0581 | -122.0123 | 121.7972 | 0.054931 | 0.30212 | 0.059509
2430.0781 | 122.0032 | -0.1236 | 121.9849 | -0.0045011 | -0.00073062 | 0.051932 | 0.052801 | -0.0030463 | -0.0072802 | -0.0030228 | -0.0023192 | 0.030435 | 0.04114 | 0.0041615 | 0.018102 | 0.025246 | -0.00084805 | 0.27466 | 121.9116 | -0.073242 | 121.7194 | 0.050354 | -0.068665 | -0.045776 | -0.027466 | -0.009155 | -0.054932 | -0.073242 | 0.054932 | 0.022888 | 0.022888 | 0.050354 | -0.073242 | -0.2655 | 0.17395 | 0.07782 | 0.054931 | 0.027466 | 0.004577 | 0.068664 | -121.994 | -122.0581 | 0.17853 | 0.14648 | 0.14648 | 0.07782 | 0.07782 | 0.1236 | 121.7926 | 0.10986 | -0.01831 | 121.9849 | 0.045777 | 122.0352 | 0.11444 | -122.0581 | -122.0398 | 121.843 | 0.050354 | 0.39825 | 0.09613
2431.8281 | 122.0947 | -0.082397 | 121.9757 | -0.01976 | 0.001192 | 0.054495 | 0.05216 | -0.0036871 | -0.0092028 | -0.0011002 | -0.011475 | 0.030008 | 0.043276 | 0.0071521 | 0.015325 | 0.024819 | -0.0074705 | 0.1831 | 121.907 | -0.054932 | 121.7651 | 0.07782 | -0.059509 | -0.013733 | 0.027466 | -0.022888 | -0.032043 | -0.004578 | 0.07782 | 0.07782 | 0.086975 | 0.027465 | -0.068665 | -0.21057 | 0.16022 | 0.068664 | 0.022888 | 0.041199 | -0.004577 | 0.050354 | -121.9986 | -121.9803 | 0.16022 | 0.16937 | 0.16022 | 0.11902 | 0.10986 | 0.13275 | 121.8201 | 0.10986 | 0.027465 | 121.962 | 0.009155 | 121.9894 | 0.059509 | -122.0306 | -122.0078 | 121.8475 | 0.077819 | 0.2655 | 0.10986
2433.5938 | 122.0444 | -0.10529 | 121.9666 | -0.012131 | 0.0073872 | 0.054282 | 0.051947 | -0.0028327 | -0.0087756 | -0.001741 | -0.005371 | 0.03193 | 0.044771 | 0.0082203 | 0.017461 | 0.025032 | -0.0027707 | 0.3067 | 121.9482 | -0.073242 | 121.7606 | 0.059509 | -0.059509 | -0.064087 | 0.022888 | -0.004578 | -0.032043 | -0.004578 | 0.064087 | 0.036621 | 0.054932 | 0.032044 | -0.018311 | -0.20599 | 0.16479 | 0.041199 | 0.045777 | 0.009155 | 0.013733 | 0.073243 | -121.9711 | -121.9711 | 0.16937 | 0.16022 | 0.14191 | 0.086975 | 0.068664 | 0.13275 | 121.8338 | 0.09613 | 0.027465 | 122.0215 | 0.027465 | 122.0535 | 0.10071 | -122.0398 | -121.9986 | 121.8658 | 0.10071 | 0.41199 | 0.12817
2435.2969 | 122.1085 | -0.07782 | 121.9208 | -0.01976 | 0.0031146 | 0.05535 | 0.050238 | -0.00091006 | -0.006853 | -0.001741 | -0.005371 | 0.029153 | 0.045198 | 0.0062977 | 0.017675 | 0.026955 | -0.0042661 | 0.24719 | 121.9025 | -0.041199 | 121.8292 | 0.15564 | -0.004578 | 0.036621 | 0.10071 | -0.032043 | -0.013733 | 0.050354 | 0.14191 | 0.11902 | 0.11902 | 0.036621 | -0.01831 | -0.091552 | 0.23346 | 0.11444 | 0.073242 | 0.07782 | 0.036621 | 0.064087 | -121.9528 | -121.8704 | 0.21973 | 0.19684 | 0.19684 | 0.13275 | 0.13275 | 0.19684 | 121.8704 | 0.15564 | 0.064087 | 121.9437 | -0.01831 | 121.9803 | 0.045777 | -121.962 | -121.9345 | 121.907 | 0.12817 | 0.32501 | 0.17853
2437.0625 | 122.0261 | -0.11444 | 121.9894 | -0.01976 | -0.0011578 | 0.053 | 0.050879 | -0.00048286 | -0.0066394 | -0.0025956 | -0.0023192 | 0.032357 | 0.04413 | 0.0026661 | 0.016393 | 0.024819 | -0.0076841 | 0.25635 | 121.962 | -0.091553 | 121.6965 | 0.004578 | -0.09613 | -0.09613 | -0.068665 | 0.009155 | -0.073242 | -0.054932 | 0.036621 | 0 | 0.041199 | 0.022888 | -0.027466 | -0.29297 | 0.11902 | 0.018311 | 0.018311 | -0.004577 | -0.004577 | 0.041199 | -121.9803 | -122.0444 | 0.15106 | 0.15564 | 0.11444 | 0.11444 | 0.073242 | 0.096131 | 121.788 | 0.10986 | 0.01831 | 122.0535 | 0.082397 | 122.0764 | 0.1236 | -122.081 | -122.0627 | 121.8109 | 0.059509 | 0.37079 | 0.045776
2438.8125 | 122.1176 | -0.059509 | 121.9254 | -0.012131 | 0.0048236 | 0.05535 | 0.052801 | 0.0025079 | -0.0062122 | -0.0013138 | -0.0084228 | 0.029367 | 0.046907 | 0.010784 | 0.016821 | 0.025887 | -0.0027707 | 0.27008 | 121.9254 | -0.041199 | 121.8292 | 0.14191 | -0.009155 | 0.027466 | 0.1236 | -0.027466 | -0.027466 | 0.082397 | 0.16022 | 0.13275 | 0.13275 | 0.01831 | 0 | -0.09613 | 0.20142 | 0.086975 | 0.050354 | 0.068665 | 0.032044 | 0.032043 | -121.9528 | -121.843 | 0.21973 | 0.19226 | 0.19226 | 0.16022 | 0.16022 | 0.18311 | 121.8704 | 0.18768 | 0.10986 | 121.9666 | 0 | 121.9849 | 0.032043 | -121.9666 | -121.9528 | 121.8887 | 0.14191 | 0.32959 | 0.1831
2440.5156 | 122.1039 | -0.068665 | 121.9391 | -0.0045011 | 0.00033758 | 0.054495 | 0.049597 | 0.0010125 | -0.0092028 | -0.000673 | -0.011475 | 0.030008 | 0.045412 | 0.0073657 | 0.014471 | 0.024605 | -0.0027707 | 0.29297 | 121.8979 | -0.045776 | 121.8292 | 0.16937 | 0.032043 | 0.050354 | 0.10071 | -0.032043 | -0.013733 | 0.032043 | 0.17395 | 0.14648 | 0.13275 | 0.022889 | -0.041199 | -0.10986 | 0.23804 | 0.11902 | 0.10071 | 0.09613 | 0.077819 | 0.054932 | -121.9711 | -121.907 | 0.24261 | 0.20142 | 0.21515 | 0.14648 | 0.16022 | 0.21515 | 121.875 | 0.18768 | 0.045776 | 121.9437 | -0.01831 | 121.9666 | 0.036622 | -121.9849 | -121.9528 | 121.8979 | 0.10071 | 0.36163 | 0.16937
2442.2812 | 122.0535 | -0.11444 | 121.9711 | -0.012131 | 0.0039692 | 0.053854 | 0.052374 | 0.0012261 | -0.0089892 | 0.0006088 | -0.0023192 | 0.031717 | 0.046053 | 0.014629 | 0.017889 | 0.023751 | -0.0038389 | 0.31586 | 121.9482 | -0.082397 | 121.7697 | 0.068665 | -0.064087 | -0.036621 | 0.022888 | -0.009155 | -0.041199 | -0.004578 | 0.086975 | 0.073242 | 0.068665 | 0.032044 | -0.022888 | -0.20142 | 0.18311 | 0.07782 | 0.050354 | 0.045776 | 0.01831 | 0.073242 | -121.9803 | -121.9757 | 0.20142 | 0.18311 | 0.18768 | 0.10986 | 0.11444 | 0.15106 | 121.8521 | 0.12817 | 0.036621 | 122.0306 | 0.032044 | 122.0627 | 0.10529 | -122.0535 | -122.0123 | 121.8842 | 0.10986 | 0.4303 | 0.13733
2444.0312 | 122.0947 | -0.059509 | 121.9345 | 0.0031279 | 0.001192 | 0.053427 | 0.050238 | 0.0059259 | -0.0079212 | -3.1996e-05 | -0.005371 | 0.028939 | 0.045839 | 0.0073657 | 0.014257 | 0.024819 | -0.0031979 | 0.25177 | 121.9208 | -0.045776 | 121.8109 | 0.14191 | -0.004578 | 0.018311 | 0.10529 | -0.041199 | -0.009155 | 0.045776 | 0.13275 | 0.10071 | 0.10529 | 0.013733 | -0.013733 | -0.1236 | 0.20142 | 0.07782 | 0.054931 | 0.064087 | 0.041198 | 0.050354 | -121.9757 | -121.8887 | 0.19226 | 0.16479 | 0.16022 | 0.11444 | 0.10986 | 0.18768 | 121.8567 | 0.14191 | 0.054931 | 121.9666 | -0.032044 | 121.9803 | 0.01831 | -121.9803 | -121.9437 | 121.8704 | 0.10528 | 0.31128 | 0.16479
2445.9062 | 121.9711 | -0.11444 | 121.9711 | -0.012131 | 0.0052508 | 0.055991 | 0.052801 | 0.00058534 | -0.0089892 | -0.0021682 | -0.005371 | 0.032357 | 0.048189 | 0.010356 | 0.019598 | 0.026528 | -0.0042661 | 0.24719 | 121.9711 | -0.082397 | 121.6873 | -0.036621 | -0.15564 | -0.1236 | -0.086975 | 0 | -0.073242 | -0.064087 | 0 | -0.013733 | 0.045776 | 0.032044 | 0 | -0.28381 | 0.07782 | -0.009155 | -0.041199 | -0.041199 | -0.073243 | 0.041199 | -121.9711 | -122.0352 | 0.11444 | 0.16022 | 0.10071 | 0.11902 | 0.059509 | 0.045776 | 121.7697 | 0.073242 | 0.009155 | 122.0535 | 0.073242 | 122.0856 | 0.11444 | -122.0535 | -122.0444 | 121.8018 | 0.050354 | 0.36163 | 0.027466
2449.4844 | 122.0856 | -0.082397 | 121.9528 | 0.0031279 | 0.0022602 | 0.053 | 0.04917 | 0.0050713 | -0.0077074 | -0.0057998 | -0.005371 | 0.027871 | 0.044558 | 0.0071521 | 0.014043 | 0.026528 | -0.0029843 | 0.23346 | 121.9162 | -0.054932 | 121.788 | 0.12817 | -0.027466 | 0.013733 | 0.082397 | -0.041199 | -0.032043 | 0.022888 | 0.10986 | 0.09613 | 0.09613 | 0.027465 | -0.036621 | -0.16479 | 0.21057 | 0.09613 | 0.054931 | 0.068665 | 0.027466 | 0.050354 | -121.994 | -121.9299 | 0.19226 | 0.17853 | 0.17853 | 0.12817 | 0.12817 | 0.18311 | 121.843 | 0.14191 | 0.054931 | 121.9711 | -0.009156 | 121.9986 | 0.041198 | -122.0078 | -121.9849 | 121.8704 | 0.10528 | 0.31586 | 0.16479
2453.375 | 122.1039 | -0.07782 | 121.9345 | -0.01976 | -0.001585 | 0.053 | 0.05216 | -0.00026906 | -0.0083484 | -0.0025956 | -0.005371 | 0.030221 | 0.044985 | 0.0090747 | 0.014471 | 0.026528 | -0.0025571 | 0.3067 | 121.9116 | -0.041199 | 121.8292 | 0.16022 | 0.009155 | 0.041199 | 0.091553 | -0.009155 | -0.027466 | 0.022888 | 0.15106 | 0.14648 | 0.11902 | 0.036621 | -0.022888 | -0.10529 | 0.23804 | 0.11902 | 0.086975 | 0.082398 | 0.050354 | 0.050354 | -121.9437 | -121.9116 | 0.22888 | 0.19684 | 0.2243 | 0.14649 | 0.17395 | 0.20142 | 121.8704 | 0.17853 | 0.050354 | 121.9528 | 0.018311 | 121.9894 | 0.068665 | -121.9757 | -121.962 | 121.907 | 0.10071 | 0.38452 | 0.16937
2459.2188 | 122.0764 | -0.09613 | 121.9345 | -0.012131 | 0.0031146 | 0.054922 | 0.051947 | 0.0016535 | -0.0079212 | -0.001741 | -0.0023192 | 0.028939 | 0.043917 | 0.0090747 | 0.015752 | 0.025246 | -0.0046933 | 0.2243 | 121.9208 | -0.032043 | 121.7697 | 0.10529 | -0.036621 | 0.009155 | 0.041199 | -0.022888 | -0.004578 | 0.013733 | 0.091553 | 0.10071 | 0.086975 | 0.064087 | -0.013733 | -0.1648 | 0.20142 | 0.10528 | 0.059509 | 0.041198 | -0.004578 | 0.091552 | -121.9574 | -121.9208 | 0.18768 | 0.1831 | 0.19684 | 0.091553 | 0.10529 | 0.13733 | 121.8018 | 0.096131 | 0.018311 | 121.9528 | -0.01831 | 122.0169 | 0.073242 | -121.9666 | -121.9391 | 121.8658 | 0.10986 | 0.32043 | 0.13733
2460.9375 | 122.0856 | -0.10071 | 121.9757 | 0.0031279 | 0.00097838 | 0.056204 | 0.049597 | -0.0041145 | -0.0092028 | 0.0008224 | -0.005371 | 0.029794 | 0.043276 | 0.0030933 | 0.015112 | 0.022896 | -0.0023435 | 0.3067 | 121.8933 | -0.050354 | 121.8063 | 0.11902 | 0.013733 | 0.032043 | 0.064087 | -0.009155 | -0.009155 | 0.004578 | 0.10986 | 0.10986 | 0.09613 | 0.050354 | -0.082397 | -0.16937 | 0.21973 | 0.13275 | 0.11444 | 0.082397 | 0.064087 | 0.091553 | -121.9849 | -121.9711 | 0.21057 | 0.19684 | 0.21057 | 0.10528 | 0.11902 | 0.16937 | 121.8567 | 0.11902 | 0.013733 | 121.9437 | 0 | 121.994 | 0.091553 | -122.0261 | -121.9849 | 121.907 | 0.10529 | 0.40741 | 0.1648
2462.6406 | 121.9803 | -0.11444 | 121.9757 | -0.01976 | 0.0067462 | 0.055136 | 0.056006 | 0.0014397 | -0.0089892 | -3.1996e-05 | -0.0084228 | 0.032357 | 0.043489 | 0.013561 | 0.019384 | 0.025032 | -0.0027707 | 0.25635 | 121.9391 | -0.091553 | 121.7102 | -0.036621 | -0.14191 | -0.11902 | -0.091553 | 0.009155 | -0.045776 | -0.064087 | -0.018311 | -0.041199 | 0.018311 | 0.022888 | -0.036621 | -0.2655 | 0.07782 | -0.004578 | -0.027466 | -0.027466 | -0.050354 | 0.068665 | -121.9666 | -122.0398 | 0.09613 | 0.13275 | 0.073242 | 0.064087 | 0.004577 | 0.054932 | 121.8018 | 0.027465 | -0.018311 | 122.0306 | 0.054931 | 122.0535 | 0.1236 | -122.0673 | -122.0215 | 121.8246 | 0.050354 | 0.37079 | 0.022888
2464.4062 | 122.1268 | -0.09613 | 121.9437 | -0.012131 | -0.0011578 | 0.05535 | 0.050024 | 0.00037174 | -0.0077074 | -0.0015274 | -0.0023192 | 0.029367 | 0.044344 | 0.011211 | 0.016607 | 0.026741 | -0.00084805 | 0.21973 | 121.9162 | -0.059509 | 121.7743 | 0.091553 | -0.004578 | 0.018311 | 0.036621 | -0.027466 | -0.018311 | 0.050354 | 0.14191 | 0.15106 | 0.1236 | 0.036621 | -0.027466 | -0.16937 | 0.18768 | 0.11444 | 0.091552 | 0.07782 | 0.054931 | 0.077819 | -121.9711 | -121.8933 | 0.23804 | 0.21973 | 0.24719 | 0.14191 | 0.16937 | 0.15106 | 121.8338 | 0.16022 | 0.068665 | 121.9757 | -0.009155 | 122.0123 | 0.068664 | -122.0032 | -121.962 | 121.8704 | 0.14648 | 0.31586 | 0.13275
2466.1719 | 122.0535 | -0.10071 | 121.9528 | -0.012131 | 0.0043964 | 0.054495 | 0.052374 | -0.0015509 | -0.0081348 | -0.0047318 | -0.0023192 | 0.032785 | 0.045198 | 0.013347 | 0.017675 | 0.024391 | -0.0025571 | 0.33875 | 121.9711 | -0.091553 | 121.756 | 0.054932 | -0.07782 | -0.059509 | 0.022888 | 0.004578 | -0.041199 | 0 | 0.09613 | 0.050354 | 0.073242 | 0.009155 | 0.01831 | -0.19684 | 0.15564 | 0.041199 | 0.022888 | 0.032044 | 0.013733 | 0.059509 | -121.9482 | -121.9528 | 0.19684 | 0.17395 | 0.15106 | 0.11444 | 0.091553 | 0.14649 | 121.8475 | 0.13733 | 0.041199 | 122.0627 | 0.045777 | 122.0718 | 0.10529 | -122.0444 | -121.994 | 121.8567 | 0.10071 | 0.43945 | 0.1236
2467.9375 | 122.1405 | -0.082397 | 121.9528 | -0.012131 | 0.00076478 | 0.051505 | 0.051306 | -0.00069646 | -0.011125 | -0.0030228 | -0.0023192 | 0.029153 | 0.046267 | 0.0086475 | 0.016607 | 0.0261 | 0.0017153 | 0.24261 | 121.9254 | -0.064087 | 121.8063 | 0.11902 | 0.022888 | 0.022888 | 0.068665 | -0.032043 | -0.018311 | 0.045776 | 0.16937 | 0.15106 | 0.13733 | 0.01831 | -0.027466 | -0.14648 | 0.20142 | 0.10528 | 0.10528 | 0.086975 | 0.086975 | 0.064086 | -121.9849 | -121.907 | 0.25177 | 0.21973 | 0.23346 | 0.15564 | 0.16937 | 0.18311 | 121.8704 | 0.18768 | 0.064087 | 121.9894 | -0.013732 | 122.0078 | 0.050354 | -122.0169 | -121.9711 | 121.8887 | 0.12817 | 0.32501 | 0.15106
2469.7031 | 122.049 | -0.1236 | 121.9528 | 0.0031279 | 0.00097838 | 0.052786 | 0.051733 | -0.0028327 | -0.010912 | -0.00345 | -0.0023192 | 0.030435 | 0.043917 | 0.0048023 | 0.01618 | 0.025246 | -0.0027707 | 0.32501 | 121.9116 | -0.050354 | 121.8018 | 0.1236 | 0.004578 | 0.022888 | 0.050354 | -0.027466 | -0.022888 | -0.018311 | 0.091553 | 0.082397 | 0.064087 | 0.073242 | -0.041199 | -0.15106 | 0.24719 | 0.14648 | 0.12817 | 0.073242 | 0.054932 | 0.10071 | -121.9803 | -121.9711 | 0.21515 | 0.18768 | 0.20599 | 0.086975 | 0.10528 | 0.17395 | 121.8521 | 0.11444 | 0.004577 | 121.962 | -0.004578 | 122.0352 | 0.09613 | -122.0032 | -121.9757 | 121.9254 | 0.10528 | 0.44861 | 0.17395
2471.4062 | 122.0398 | -0.11902 | 121.9574 | -0.0045011 | 0.001833 | 0.054495 | 0.052801 | 0.0025079 | -0.010271 | -0.00345 | -0.005371 | 0.031717 | 0.044985 | 0.010356 | 0.016607 | 0.022896 | 6.346e-06 | 0.29297 | 121.9849 | -0.09613 | 121.7148 | -0.009155 | -0.10529 | -0.07782 | -0.064087 | 0.013733 | -0.036621 | -0.073242 | 0.050354 | 0.018311 | 0.041199 | 0.022889 | 0.027466 | -0.24261 | 0.10986 | 0.041199 | 0.013733 | 0.01831 | -0.009156 | 0.082398 | -121.9437 | -122.0306 | 0.16937 | 0.16022 | 0.13733 | 0.07782 | 0.054932 | 0.086975 | 121.8109 | 0.086975 | -0.036621 | 122.081 | 0.050354 | 122.1039 | 0.13275 | -122.0535 | -121.994 | 121.8338 | 0.045777 | 0.41199 | 0.054932
2473.1094 | 122.1313 | -0.082397 | 121.9482 | -0.0045011 | 0.00033758 | 0.054922 | 0.050238 | -0.0028327 | -0.0077074 | -0.0021682 | -0.005371 | 0.029153 | 0.042635 | 0.0026661 | 0.015112 | 0.024819 | -0.0036253 | 0.20599 | 121.9025 | -0.036621 | 121.7606 | 0.086975 | -0.032043 | -0.004578 | 0.050354 | -0.032043 | -0.027466 | 0.041199 | 0.15564 | 0.13733 | 0.1236 | 0.045776 | -0.045776 | -0.18768 | 0.16937 | 0.077819 | 0.050354 | 0.032043 | 0.004578 | 0.054931 | -121.9803 | -121.907 | 0.23804 | 0.20599 | 0.21973 | 0.15106 | 0.16479 | 0.1236 | 121.7972 | 0.18311 | 0.068665 | 121.9391 | -0.004577 | 121.9849 | 0.050354 | -121.9849 | -121.9757 | 121.843 | 0.1236 | 0.28839 | 0.13275
2474.875 | 122.0901 | -0.068665 | 121.9437 | -0.01976 | 0.0024738 | 0.055563 | 0.052801 | -0.0028327 | -0.0074938 | -0.0030228 | -0.005371 | 0.030435 | 0.046053 | 0.0052295 | 0.015966 | 0.024605 | -0.00063445 | 0.24261 | 121.9208 | -0.045776 | 121.788 | 0.13275 | -0.036621 | 0.013733 | 0.068665 | -0.027466 | -0.041199 | 0.009155 | 0.10529 | 0.09613 | 0.09613 | 0.022889 | -0.022889 | -0.15564 | 0.20142 | 0.082398 | 0.032044 | 0.059509 | 0.009155 | 0.027466 | -121.9711 | -121.9345 | 0.17395 | 0.16479 | 0.16479 | 0.13733 | 0.13733 | 0.17853 | 121.8338 | 0.14649 | 0.050354 | 121.9666 | 0.013733 | 121.9894 | 0.041199 | -121.9894 | -121.9849 | 121.8567 | 0.07782 | 0.31128 | 0.13733
2476.5625 | 122.1313 | -0.068665 | 121.9345 | -0.012131 | 0.0014056 | 0.055991 | 0.04917 | -0.0021919 | -0.008562 | -0.001741 | -0.005371 | 0.029367 | 0.045198 | 0.01292 | 0.014257 | 0.022683 | -0.0040525 | 0.31128 | 121.9116 | -0.036621 | 121.8384 | 0.16022 | 0.036621 | 0.054932 | 0.10986 | -0.045776 | -0.022888 | 0.050354 | 0.17395 | 0.14648 | 0.1236 | 0.032044 | -0.022888 | -0.09613 | 0.22888 | 0.1236 | 0.10529 | 0.091553 | 0.073242 | 0.045777 | -121.9803 | -121.8842 | 0.24261 | 0.19226 | 0.21515 | 0.14648 | 0.16937 | 0.19684 | 121.875 | 0.19684 | 0.073242 | 121.9482 | -0.022888 | 121.9803 | 0.022889 | -121.9711 | -121.9574 | 121.907 | 0.11902 | 0.37994 | 0.17853
2478.3125 | 122.0444 | -0.10529 | 121.994 | -0.01976 | 0.0024738 | 0.052359 | 0.051947 | -0.00091006 | -0.0087756 | -0.0021682 | -0.005371 | 0.031503 | 0.047976 | 0.018047 | 0.016607 | 0.025246 | -0.0042661 | 0.33875 | 121.9299 | -0.09613 | 121.7651 | 0.045776 | -0.073242 | -0.050354 | 0.013733 | -0.009155 | -0.018311 | -0.018311 | 0.073242 | 0.041199 | 0.082397 | 0.009156 | -0.064087 | -0.22888 | 0.15106 | 0.054932 | 0.032044 | 0.045776 | 0.022888 | 0.086975 | -122.0032 | -122.0123 | 0.17853 | 0.18768 | 0.14649 | 0.10071 | 0.05951 | 0.14191 | 121.8613 | 0.091553 | 0 | 122.0261 | 0.009156 | 122.0352 | 0.096131 | -122.0901 | -122.0123 | 121.8704 | 0.086975 | 0.44403 | 0.11902
2480.0781 | 122.1313 | -0.064087 | 121.9391 | -0.01976 | -0.00073062 | 0.053427 | 0.049597 | -0.00048286 | -0.0087756 | -0.0057998 | -0.005371 | 0.029367 | 0.041567 | 0.0092883 | 0.016393 | 0.0261 | -0.00020725 | 0.24719 | 121.9391 | -0.050354 | 121.8063 | 0.13275 | 0.013733 | 0.032043 | 0.091553 | -0.032043 | -0.013733 | 0.045776 | 0.17853 | 0.15564 | 0.13275 | 0.013733 | 0 | -0.13275 | 0.19684 | 0.09613 | 0.07782 | 0.082397 | 0.064087 | 0.050354 | -121.9711 | -121.8933 | 0.24261 | 0.19684 | 0.21973 | 0.14648 | 0.16937 | 0.18311 | 121.8567 | 0.19226 | 0.059509 | 121.9894 | -0.01831 | 122.0032 | 0.032044 | -121.9894 | -121.9528 | 121.8704 | 0.10986 | 0.31128 | 0.15564
2481.8281 | 122.0581 | -0.13275 | 121.962 | -0.0045011 | 0.0016192 | 0.053214 | 0.053442 | 0.00079894 | -0.00963 | -0.0013138 | -0.005371 | 0.03193 | 0.045626 | 0.013988 | 0.018957 | 0.024605 | -0.0038389 | 0.30212 | 121.962 | -0.09613 | 121.7285 | 0.004578 | -0.086975 | -0.082397 | -0.032043 | 0.018311 | -0.054932 | -0.036621 | 0.073242 | 0.059509 | 0.07782 | 0.036621 | 0 | -0.23346 | 0.13733 | 0.050354 | 0.045776 | 0.013733 | 0.009155 | 0.077819 | -121.9437 | -121.9986 | 0.20599 | 0.21057 | 0.19226 | 0.13275 | 0.11444 | 0.10071 | 121.8246 | 0.12817 | 0.018311 | 122.0581 | 0.073243 | 122.0947 | 0.15106 | -122.0581 | -122.0169 | 121.8613 | 0.09613 | 0.43488 | 0.10071
2483.5312 | 122.0261 | -0.10986 | 121.9849 | -0.0045011 | 0.0037556 | 0.055991 | 0.053228 | 0.00015814 | -0.0064258 | -0.0030228 | -0.0084228 | 0.031503 | 0.046907 | 0.0090747 | 0.019598 | 0.025673 | -0.0057615 | 0.23804 | 121.9849 | -0.10986 | 121.6965 | -0.018311 | -0.14191 | -0.10986 | -0.036621 | 0.013733 | -0.064087 | -0.045776 | 0.018311 | -0.004578 | 0.027466 | 0 | 0 | -0.28839 | 0.091552 | 0 | -0.032044 | 0 | -0.032044 | 0.045776 | -121.9711 | -122.0306 | 0.12817 | 0.13733 | 0.10529 | 0.091553 | 0.059509 | 0.091552 | 121.8063 | 0.082398 | 0.018311 | 122.0947 | 0.07782 | 122.0947 | 0.1236 | -122.0947 | -122.049 | 121.8063 | 0.064087 | 0.3479 | 0.073242
2485.2969 | 122.1085 | -0.073242 | 121.962 | -0.0045011 | 0.00097838 | 0.053427 | 0.048315 | -0.0017645 | -0.0081348 | -0.0030228 | -0.005371 | 0.027658 | 0.047121 | 0.011424 | 0.015325 | 0.02546 | -0.0046933 | 0.31128 | 121.875 | -0.068665 | 121.8246 | 0.15106 | 0.022888 | 0.036621 | 0.091553 | -0.022888 | -0.013733 | 0.036621 | 0.15106 | 0.12817 | 0.10986 | 0.004577 | -0.086975 | -0.13733 | 0.2243 | 0.10986 | 0.09613 | 0.10529 | 0.091553 | 0.059509 | -121.9849 | -121.9254 | 0.2243 | 0.18311 | 0.20142 | 0.1236 | 0.14191 | 0.21973 | 121.8933 | 0.16479 | 0.050354 | 121.9437 | -0.009155 | 121.9482 | 0.050354 | -122.0306 | -121.9757 | 121.8979 | 0.10986 | 0.38452 | 0.16479
2487.0469 | 122.0581 | -0.09613 | 121.9574 | -0.0045011 | 0.0043964 | 0.053641 | 0.05152 | 0.00079894 | -0.0083484 | -0.0040908 | -0.0023192 | 0.031717 | 0.044771 | 0.010356 | 0.017248 | 0.023751 | -0.0053343 | 0.34332 | 121.9482 | -0.086975 | 121.7651 | 0.064087 | -0.068665 | -0.045776 | 0.027466 | -0.009155 | -0.022888 | -0.004578 | 0.10071 | 0.059509 | 0.082397 | 0.009155 | -0.009155 | -0.19226 | 0.16022 | 0.050354 | 0.027465 | 0.041199 | 0.01831 | 0.073242 | -121.9666 | -121.962 | 0.19684 | 0.17853 | 0.15564 | 0.10528 | 0.082397 | 0.15106 | 121.8521 | 0.1236 | 0.01831 | 122.0352 | 0.013733 | 122.0444 | 0.086975 | -122.0444 | -121.9803 | 121.8613 | 0.091552 | 0.43945 | 0.1236
2488.75 | 122.0947 | -0.09613 | 121.9574 | -0.01976 | 0.00055118 | 0.054495 | 0.048529 | 0.0022943 | -0.00963 | -0.000673 | -0.005371 | 0.029794 | 0.046694 | 0.0022389 | 0.014471 | 0.025887 | -0.0023435 | 0.22888 | 121.9116 | -0.064087 | 121.7606 | 0.068665 | -0.054932 | -0.027466 | 0.027466 | -0.032043 | -0.022888 | 0.013733 | 0.10986 | 0.10071 | 0.09613 | 0.032043 | -0.045776 | -0.19684 | 0.16479 | 0.068664 | 0.041198 | 0.036621 | 0.009155 | 0.073242 | -121.9894 | -121.9437 | 0.20599 | 0.19226 | 0.19684 | 0.11902 | 0.1236 | 0.13275 | 121.8246 | 0.13275 | 0.036621 | 121.9757 | -0.009155 | 122.0078 | 0.064087 | -122.0215 | -121.9803 | 121.8567 | 0.10986 | 0.32501 | 0.1236
2490.5312 | 122.1313 | -0.054932 | 121.9391 | -0.012131 | 0.00461 | 0.05535 | 0.053442 | 0.0010125 | -0.008562 | -0.0045182 | -0.0023192 | 0.029794 | 0.04648 | 0.0050159 | 0.016393 | 0.024605 | -0.0025571 | 0.27924 | 121.9574 | -0.045776 | 121.8018 | 0.10529 | -0.032043 | 0.027466 | 0.09613 | -0.022888 | -0.018311 | 0.068665 | 0.15106 | 0.11902 | 0.15106 | 0.009156 | 0.01831 | -0.13733 | 0.16022 | 0.082398 | 0.022889 | 0.073242 | 0.013733 | 0.036621 | -121.962 | -121.8704 | 0.20599 | 0.20599 | 0.17395 | 0.16937 | 0.13733 | 0.15106 | 121.8475 | 0.16937 | 0.086976 | 122.0032 | -0.004577 | 122.0123 | 0.032044 | -121.9849 | -121.9574 | 121.8567 | 0.1236 | 0.33417 | 0.15106
2492.2969 | 122.0947 | -0.082397 | 121.9574 | -0.012131 | 0.00012398 | 0.053641 | 0.049597 | -0.00091006 | -0.01198 | -0.0045182 | -0.0023192 | 0.028726 | 0.043062 | 0.0067249 | 0.016821 | 0.026955 | 6.346e-06 | 0.22888 | 121.9254 | -0.054932 | 121.7697 | 0.068665 | -0.050354 | -0.009155 | 0.004578 | -0.009155 | -0.022888 | 0.009155 | 0.10071 | 0.086975 | 0.091553 | 0.027465 | -0.032043 | -0.18768 | 0.15106 | 0.073242 | 0.032043 | 0.045777 | 0.004578 | 0.059509 | -121.9666 | -121.9482 | 0.18311 | 0.17395 | 0.16937 | 0.11444 | 0.10986 | 0.1236 | 121.8246 | 0.1236 | 0.032043 | 121.9803 | 0.013733 | 122.0078 | 0.073242 | -122.0123 | -121.9803 | 121.8521 | 0.091552 | 0.31128 | 0.086975
2494.0625 | 122.1497 | -0.07782 | 121.9666 | -0.012131 | 0.00076478 | 0.051505 | 0.051306 | -0.00069646 | -0.010698 | -0.001741 | -0.0023192 | 0.029153 | 0.045626 | 0.0050159 | 0.014898 | 0.024391 | -0.0053343 | 0.32044 | 121.8979 | -0.032043 | 121.843 | 0.1831 | 0.054932 | 0.07782 | 0.11902 | -0.022888 | -0.009155 | 0.050354 | 0.19684 | 0.17853 | 0.12817 | 0.045777 | -0.068665 | -0.1236 | 0.26092 | 0.15564 | 0.13275 | 0.10986 | 0.086975 | 0.068665 | -121.9894 | -121.9162 | 0.27466 | 0.20599 | 0.25635 | 0.13733 | 0.18768 | 0.21515 | 121.875 | 0.20599 | 0.059509 | 121.9299 | -0.013733 | 121.9757 | 0.054932 | -121.9986 | -121.9757 | 121.9208 | 0.12817 | 0.39826 | 0.19684
2495.8281 | 122.0993 | -0.07782 | 121.9574 | -0.012131 | 0.0052508 | 0.053641 | 0.053656 | 0.00037174 | -0.0083484 | -0.001741 | -0.005371 | 0.031717 | 0.043489 | 0.0095019 | 0.015112 | 0.025673 | -0.0017027 | 0.23346 | 121.962 | -0.068665 | 121.7331 | 0.027466 | -0.10986 | -0.073242 | 0.022888 | -0.022888 | -0.022888 | 0.018311 | 0.10529 | 0.082397 | 0.10986 | 0.009155 | 0.004578 | -0.2243 | 0.10529 | 0.004578 | -0.032043 | -0.004577 | -0.041198 | 0.054932 | -121.9803 | -121.9391 | 0.18311 | 0.18768 | 0.16022 | 0.13275 | 0.10528 | 0.096131 | 121.8018 | 0.12817 | 0.041199 | 122.0306 | 0 | 122.0398 | 0.054932 | -122.0261 | -121.9803 | 121.8109 | 0.096131 | 0.31128 | 0.10071
2497.5312 | 122.1313 | -0.091553 | 121.9574 | -0.012131 | 0.0022602 | 0.054709 | 0.049811 | 0.0010125 | -0.0077074 | -0.0021682 | -0.0084228 | 0.028726 | 0.045839 | 0.017406 | 0.016393 | 0.024605 | -0.0029843 | 0.24261 | 121.9482 | -0.059509 | 121.788 | 0.091553 | -0.036621 | 0.004578 | 0.041199 | -0.027466 | -0.022888 | 0.022888 | 0.13275 | 0.13275 | 0.11902 | 0.032044 | -0.009155 | -0.16937 | 0.18311 | 0.096131 | 0.054932 | 0.064087 | 0.022888 | 0.068665 | -121.9849 | -121.9345 | 0.2243 | 0.21057 | 0.2243 | 0.14191 | 0.15564 | 0.15106 | 121.8475 | 0.15564 | 0.045776 | 122.0078 | -0.004578 | 122.0398 | 0.064087 | -122.0169 | -121.9803 | 121.8796 | 0.11444 | 0.33417 | 0.13275
2499.2969 | 122.1222 | -0.073242 | 121.9482 | -0.012131 | 0.0024738 | 0.054068 | 0.051733 | 0.0014397 | -0.0072802 | -0.0004592 | -0.0023192 | 0.029794 | 0.045839 | 0.0095019 | 0.014684 | 0.024819 | -0.0064023 | 0.28381 | 121.9208 | -0.036621 | 121.8292 | 0.15106 | -0.004578 | 0.041199 | 0.11902 | -0.022888 | -0.009155 | 0.064087 | 0.13275 | 0.13733 | 0.12817 | 0.036621 | -0.027466 | -0.11902 | 0.2243 | 0.11444 | 0.068664 | 0.07782 | 0.032043 | 0.064087 | -121.9711 | -121.8842 | 0.20599 | 0.20142 | 0.21057 | 0.13733 | 0.14648 | 0.18768 | 121.8658 | 0.14191 | 0.073242 | 121.9574 | -0.013733 | 121.994 | 0.050354 | -121.9849 | -121.9574 | 121.9025 | 0.13733 | 0.35706 | 0.19226
2501.0625 | 122.0627 | -0.10071 | 121.9711 | -0.0045011 | 0.0043964 | 0.054068 | 0.052374 | -0.00091006 | -0.0087756 | -0.0032364 | -0.005371 | 0.032571 | 0.044985 | 0.010356 | 0.018316 | 0.024391 | -0.0068295 | 0.36163 | 121.9482 | -0.09613 | 121.7697 | 0.073242 | -0.07782 | -0.045776 | 0.045776 | 0.004578 | -0.036621 | 0 | 0.086975 | 0.073242 | 0.07782 | 0.004578 | -0.022888 | -0.20142 | 0.17395 | 0.054932 | 0.022888 | 0.050354 | 0.01831 | 0.064087 | -121.9666 | -121.9711 | 0.18768 | 0.17853 | 0.17395 | 0.11444 | 0.10986 | 0.16937 | 121.8658 | 0.1236 | 0.036621 | 122.0444 | 0.041199 | 122.0489 | 0.10529 | -122.0673 | -122.0078 | 121.8704 | 0.10071 | 0.46234 | 0.14648
2502.8281 | 122.1039 | -0.073242 | 121.9894 | -0.01976 | 0.0020466 | 0.054068 | 0.051092 | -0.0051825 | -0.0092028 | -0.0047318 | -0.0084228 | 0.031076 | 0.045412 | 0.011211 | 0.015752 | 0.025032 | -0.0025571 | 0.23346 | 121.9116 | -0.054932 | 121.7697 | 0.082397 | -0.036621 | -0.004578 | 0.027466 | -0.018311 | -0.032043 | 0.004578 | 0.10071 | 0.082397 | 0.091553 | 0.01831 | -0.07782 | -0.21973 | 0.15564 | 0.068664 | 0.036621 | 0.050354 | 0.018311 | 0.041199 | -122.0078 | -121.9849 | 0.17395 | 0.16479 | 0.15564 | 0.1236 | 0.11444 | 0.13733 | 121.8246 | 0.13275 | 0.036621 | 121.9666 | 0.013732 | 121.9849 | 0.054931 | -122.0444 | -122.0215 | 121.843 | 0.07782 | 0.3067 | 0.10071
2504.5312 | 122.0032 | -0.11902 | 121.9849 | -0.012131 | 0.0056782 | 0.055563 | 0.054083 | -5.5462e-05 | -0.0089892 | -0.0013138 | -0.005371 | 0.032357 | 0.043703 | 0.01057 | 0.016393 | 0.025246 | -0.00063445 | 0.2655 | 121.9849 | -0.082397 | 121.6965 | -0.022888 | -0.16022 | -0.11444 | -0.050354 | 0.018311 | -0.050354 | -0.064087 | 0 | -0.018311 | 0.027466 | 0.036622 | 0 | -0.28839 | 0.096131 | 0.004578 | -0.041198 | -0.032044 | -0.07782 | 0.068665 | -121.9666 | -122.049 | 0.11902 | 0.14649 | 0.10071 | 0.07782 | 0.032043 | 0.059509 | 121.7789 | 0.050354 | -0.013733 | 122.0673 | 0.068665 | 122.1039 | 0.13733 | -122.0673 | -122.0352 | 121.8155 | 0.054932 | 0.38452 | 0.068665
2506.3125 | 122.1268 | -0.086975 | 121.9299 | -0.012131 | 0.0024738 | 0.052786 | 0.05451 | 0.0040033 | -0.0072802 | -0.0030228 | -0.005371 | 0.030648 | 0.04413 | 0.011852 | 0.017248 | 0.025673 | -0.0055479 | 0.25177 | 121.9757 | -0.07782 | 121.7606 | 0.050354 | -0.10529 | -0.068665 | 0.009155 | -0.009155 | -0.018311 | 0.045776 | 0.10986 | 0.086975 | 0.10529 | 0.009155 | 0.045776 | -0.16937 | 0.13733 | 0.01831 | -0.018311 | 0.009155 | -0.027466 | 0.068664 | -121.9391 | -121.8842 | 0.19684 | 0.19226 | 0.17395 | 0.1236 | 0.10529 | 0.12817 | 121.8384 | 0.12817 | 0.064087 | 122.0535 | 0.009156 | 122.0627 | 0.07782 | -122.0078 | -121.9482 | 121.8475 | 0.13275 | 0.33874 | 0.09613
2508.0781 | 122.0261 | -0.12817 | 122.0032 | -0.01976 | 0.00055118 | 0.055777 | 0.053656 | -0.0011237 | -0.010271 | -0.0002456 | -0.005371 | 0.030435 | 0.045198 | 0.0071521 | 0.018957 | 0.026528 | -0.0036253 | 0.28839 | 121.9757 | -0.11444 | 121.6965 | 0.004578 | -0.10071 | -0.086975 | -0.068665 | 0 | -0.050354 | -0.07782 | 0.036621 | 0.018311 | 0.027466 | 0.013733 | -0.027466 | -0.3067 | 0.13275 | 0.041199 | 0.027466 | 0.027466 | 0.013733 | 0.07782 | -122.0032 | -122.081 | 0.1648 | 0.15564 | 0.14649 | 0.07782 | 0.068665 | 0.11902 | 121.8109 | 0.086975 | -0.027466 | 122.0901 | 0.050354 | 122.1039 | 0.12817 | -122.1176 | -122.0535 | 121.8246 | 0.050354 | 0.41657 | 0.059509
2509.7812 | 122.1268 | -0.054932 | 121.9391 | -0.0045011 | 0.006319 | 0.055777 | 0.050238 | 0.00058534 | -0.0079212 | -0.00345 | -0.005371 | 0.028939 | 0.045626 | 0.010784 | 0.015752 | 0.024819 | -0.0044797 | 0.3067 | 121.9162 | -0.064087 | 121.8246 | 0.14648 | -0.009155 | 0.032043 | 0.09613 | -0.032043 | -0.022888 | 0.073242 | 0.15106 | 0.13733 | 0.15106 | -0.009155 | -0.022888 | -0.11444 | 0.20142 | 0.086975 | 0.045777 | 0.09613 | 0.054932 | 0.032044 | -121.9711 | -121.8658 | 0.20599 | 0.20599 | 0.19226 | 0.17395 | 0.16022 | 0.21057 | 121.8887 | 0.17395 | 0.09613 | 121.9803 | -0.009155 | 121.9711 | 0.022889 | -122.0032 | -121.962 | 121.8796 | 0.12817 | 0.36163 | 0.15106
2511.5469 | 122.0947 | -0.091553 | 121.962 | -0.01976 | 0.001192 | 0.054922 | 0.050665 | -0.00048286 | -0.010057 | -0.0030228 | 0.00073235 | 0.029153 | 0.045626 | 0.0062977 | 0.01618 | 0.026528 | -0.0038389 | 0.3479 | 121.9116 | -0.068665 | 121.8201 | 0.14191 | 0.009155 | 0.059509 | 0.082397 | -0.041199 | -0.018311 | 0.009155 | 0.13733 | 0.1236 | 0.11444 | 0.022888 | -0.050354 | -0.14191 | 0.23346 | 0.15106 | 0.10071 | 0.12817 | 0.07782 | 0.073242 | -122.0032 | -121.9528 | 0.22888 | 0.20599 | 0.21515 | 0.13275 | 0.14191 | 0.21057 | 121.8887 | 0.15564 | 0.027466 | 121.9803 | -0.022888 | 122.0032 | 0.050354 | -122.0306 | -121.9803 | 121.9116 | 0.10071 | 0.43945 | 0.17395
2513.2969 | 122.0215 | -0.1236 | 121.9803 | -0.0045011 | 0.0052508 | 0.05535 | 0.056433 | 0.0014397 | -0.008562 | -0.0013138 | -0.0084228 | 0.030435 | 0.046053 | 0.010997 | 0.016821 | 0.023964 | -0.0034117 | 0.33875 | 121.9482 | -0.082397 | 121.7422 | 0.041199 | -0.10986 | -0.073242 | -0.004578 | 0 | -0.045776 | -0.054932 | 0.032043 | -0.009155 | 0.032043 | 0.041199 | -0.032044 | -0.23804 | 0.16479 | 0.050354 | 0.013733 | 0.009155 | -0.027466 | 0.07782 | -121.9803 | -122.0352 | 0.15564 | 0.15564 | 0.11444 | 0.077819 | 0.036621 | 0.1236 | 121.8246 | 0.077819 | -0.009156 | 122.0306 | 0.045776 | 122.0718 | 0.1236 | -122.0627 | -122.0261 | 121.8658 | 0.068664 | 0.46234 | 0.11902
2515.0625 | 122.049 | -0.10986 | 121.994 | -0.012131 | 0.0031146 | 0.054282 | 0.053442 | 0.0025079 | -0.008562 | -0.0040908 | -0.005371 | 0.032998 | 0.046267 | 0.0092883 | 0.017248 | 0.025032 | -0.0038389 | 0.36163 | 121.9711 | -0.073242 | 121.756 | 0.064087 | -0.064087 | -0.036621 | 0.050354 | -0.004578 | -0.036621 | -0.009155 | 0.07782 | 0.045776 | 0.073242 | 0.036621 | -0.022889 | -0.23804 | 0.17395 | 0.073242 | 0.045776 | 0.036621 | 0.009155 | 0.073242 | -121.9986 | -122.0032 | 0.18768 | 0.18311 | 0.15564 | 0.10986 | 0.082397 | 0.13733 | 121.8292 | 0.11444 | 0.027466 | 122.0444 | 0.032043 | 122.081 | 0.10529 | -122.0673 | -122.0306 | 121.8658 | 0.10071 | 0.4715 | 0.16022
2516.8281 | 122.1451 | -0.064087 | 121.9528 | -0.012131 | 0.002901 | 0.055777 | 0.051947 | -0.0017645 | -0.0055712 | -0.002382 | -0.0023192 | 0.028939 | 0.04648 | 0.0033069 | 0.01618 | 0.0261 | -0.0025571 | 0.32501 | 121.9528 | -0.054932 | 121.8201 | 0.11902 | -0.004578 | 0.022888 | 0.10529 | -0.041199 | -0.009155 | 0.073242 | 0.16937 | 0.12817 | 0.13733 | 0.009155 | 0 | -0.13275 | 0.18311 | 0.086975 | 0.059509 | 0.07782 | 0.050354 | 0.054932 | -121.994 | -121.8796 | 0.23346 | 0.20142 | 0.19226 | 0.14648 | 0.13733 | 0.17395 | 121.875 | 0.17853 | 0.082397 | 122.0078 | -0.032044 | 122.0169 | 0.022888 | -122.0078 | -121.962 | 121.8842 | 0.13733 | 0.3891 | 0.16937
2518.5469 | 122.1222 | -0.086975 | 121.9757 | -0.01976 | 0.0071734 | 0.057059 | 0.054297 | -0.0019781 | -0.0081348 | -0.0040908 | -0.0084228 | 0.031717 | 0.046907 | 0.012493 | 0.015112 | 0.028878 | -0.0034117 | 0.25177 | 121.9528 | -0.091553 | 121.7331 | 0.036621 | -0.10986 | -0.073242 | 0.022888 | 0 | -0.041199 | 0.018311 | 0.11444 | 0.09613 | 0.10071 | -0.004578 | -0.022888 | -0.24262 | 0.1236 | 0.013733 | -0.022888 | 0.018311 | -0.01831 | 0.045776 | -121.9757 | -121.9574 | 0.20142 | 0.18768 | 0.1831 | 0.14191 | 0.13733 | 0.12817 | 121.8246 | 0.15564 | 0.05951 | 122.0444 | 0.041199 | 122.0398 | 0.086975 | -122.0673 | -122.0169 | 121.8201 | 0.10529 | 0.33874 | 0.10986
2520.3281 | 122.0078 | -0.13275 | 122.0032 | -0.012131 | 0.0061054 | 0.054922 | 0.052801 | 0.0037897 | -0.0089892 | -0.0015274 | 0.00073235 | 0.030648 | 0.049471 | 0.0062977 | 0.016607 | 0.026955 | -0.0014891 | 0.32501 | 121.9849 | -0.09613 | 121.7331 | 0.041199 | -0.1236 | -0.07782 | -0.013733 | 0 | -0.050354 | -0.07782 | 0.004578 | -0.004578 | 0.013733 | 0.036621 | -0.018311 | -0.27008 | 0.17395 | 0.054931 | 0.009155 | 0.01831 | -0.027466 | 0.082397 | -122.0032 | -122.081 | 0.13733 | 0.14648 | 0.12817 | 0.064087 | 0.045776 | 0.13733 | 121.8292 | 0.054932 | -0.027466 | 122.081 | 0.050354 | 122.1176 | 0.13275 | -122.0993 | -122.0535 | 121.8658 | 0.054931 | 0.45776 | 0.11902
2522.0312 | 122.0398 | -0.10529 | 121.9803 | -0.012131 | 0.001192 | 0.053214 | 0.049597 | 0.0014397 | -0.00963 | -0.0011002 | -0.005371 | 0.027658 | 0.046267 | 0.0073657 | 0.015539 | 0.028023 | -0.0031979 | 0.34332 | 121.9208 | -0.054932 | 121.7834 | 0.091553 | -0.018311 | -0.009155 | 0 | -0.004578 | -0.032043 | -0.059509 | 0.068665 | 0.064087 | 0.032043 | 0.050354 | -0.05951 | -0.19684 | 0.19684 | 0.096131 | 0.086975 | 0.045777 | 0.036621 | 0.073243 | -121.9849 | -122.0398 | 0.17395 | 0.13733 | 0.16937 | 0.064086 | 0.09613 | 0.14649 | 121.8384 | 0.10071 | -0.027466 | 121.9757 | 0.027465 | 122.0261 | 0.10071 | -122.0352 | -122.0123 | 121.8887 | 0.045777 | 0.44861 | 0.10529
2523.7812 | 122.0856 | -0.10071 | 121.9437 | -0.0045011 | 0.00012398 | 0.052786 | 0.051092 | -0.0032599 | -0.008562 | -0.002382 | -0.0023192 | 0.029794 | 0.047121 | 0.0092883 | 0.014898 | 0.0261 | -0.0038389 | 0.24261 | 121.9162 | -0.064087 | 121.756 | 0.086975 | -0.045776 | -0.009155 | 0.041199 | -0.022888 | -0.022888 | 0.004578 | 0.10071 | 0.086975 | 0.082397 | 0.036621 | -0.027466 | -0.18768 | 0.18768 | 0.091553 | 0.054932 | 0.054932 | 0.018311 | 0.07782 | -121.9666 | -121.9391 | 0.20142 | 0.18311 | 0.18768 | 0.10528 | 0.10986 | 0.15106 | 121.8201 | 0.1236 | 0.027466 | 121.9803 | 0 | 122.0169 | 0.07782 | -122.0078 | -121.9666 | 121.8567 | 0.10529 | 0.34332 | 0.14191
2525.5625 | 122.1039 | -0.07782 | 121.9437 | -0.0045011 | 0.0033282 | 0.051718 | 0.050238 | -0.0021919 | -0.0059986 | -0.0045182 | -0.0023192 | 0.02958 | 0.044985 | -0.00096553 | 0.014898 | 0.026955 | -0.0044797 | 0.27466 | 121.9299 | -0.050354 | 121.8109 | 0.14648 | -0.018311 | 0.022888 | 0.10071 | -0.032043 | -0.004578 | 0.018311 | 0.11444 | 0.10071 | 0.09613 | 0.027466 | -0.013733 | -0.13275 | 0.2243 | 0.10071 | 0.059509 | 0.073242 | 0.032043 | 0.073242 | -121.9757 | -121.9254 | 0.19226 | 0.17395 | 0.17853 | 0.10071 | 0.10529 | 0.19684 | 121.8613 | 0.11902 | 0.022889 | 121.9803 | -0.027465 | 122.0078 | 0.045777 | -121.994 | -121.9482 | 121.8887 | 0.096131 | 0.35248 | 0.17853
2527.2656 | 122.0993 | -0.064087 | 121.962 | -0.01976 | 0.00012398 | 0.052145 | 0.052374 | 0.0010125 | -0.0072802 | -0.0030228 | -0.005371 | 0.028726 | 0.044985 | 0.0050159 | 0.014898 | 0.025673 | -0.0031979 | 0.24261 | 121.9299 | -0.059509 | 121.7651 | 0.073242 | -0.041199 | -0.022888 | 0.022888 | -0.027466 | -0.022888 | 0 | 0.09613 | 0.091553 | 0.09613 | 0.004578 | -0.032043 | -0.19684 | 0.13733 | 0.041199 | 0.022888 | 0.036621 | 0.01831 | 0.041199 | -121.9894 | -121.962 | 0.16022 | 0.16022 | 0.15564 | 0.11902 | 0.11444 | 0.13275 | 121.8246 | 0.11902 | 0.022888 | 121.9894 | -0.004578 | 121.994 | 0.036621 | -122.0215 | -121.9849 | 121.8292 | 0.064087 | 0.3067 | 0.086975
2529.0312 | 122.0306 | -0.10529 | 121.9711 | 0.0031279 | 0.0048236 | 0.055563 | 0.054937 | 0.0018671 | -0.0094164 | -0.0049454 | -0.005371 | 0.030221 | 0.046267 | 0.0062977 | 0.014043 | 0.024819 | -0.0059751 | 0.28381 | 121.9849 | -0.091553 | 121.7148 | -0.013733 | -0.14191 | -0.091553 | -0.032043 | -0.004578 | -0.045776 | -0.045776 | 0.032043 | 0.013733 | 0.045776 | 0.013733 | 0.013733 | -0.25635 | 0.091553 | 0.013733 | -0.036621 | 0 | -0.050354 | 0.05951 | -121.9757 | -122.0169 | 0.13733 | 0.15106 | 0.11902 | 0.091552 | 0.059509 | 0.07782 | 121.8063 | 0.077819 | 0 | 122.0764 | 0.041198 | 122.0901 | 0.10071 | -122.0627 | -122.0169 | 121.8201 | 0.05951 | 0.3891 | 0.073243
2530.7969 | 122.1222 | -0.086975 | 121.9894 | -0.012131 | -8.9824e-05 | 0.054068 | 0.051092 | -0.0015509 | -0.0098438 | -0.0028092 | -0.005371 | 0.029794 | 0.046907 | 0.0033069 | 0.015966 | 0.025246 | -0.0040525 | 0.35706 | 121.9345 | -0.059509 | 121.8292 | 0.13733 | 0.009155 | 0.041199 | 0.068665 | -0.032043 | -0.027466 | 0.013733 | 0.13275 | 0.10986 | 0.091553 | 0.027466 | -0.054932 | -0.16022 | 0.2243 | 0.12817 | 0.09613 | 0.10071 | 0.068664 | 0.059509 | -122.0215 | -121.9757 | 0.21973 | 0.17853 | 0.19684 | 0.11902 | 0.13733 | 0.19684 | 121.8887 | 0.16022 | 0.041199 | 121.994 | -0.004577 | 122.0215 | 0.054932 | -122.049 | -122.0169 | 121.9162 | 0.10071 | 0.44403 | 0.15564
2532.5469 | 122.0444 | -0.10071 | 121.994 | -0.0045011 | -8.9824e-05 | 0.055136 | 0.051306 | -0.00091006 | -0.010698 | -0.0030228 | -0.0023192 | 0.031289 | 0.04648 | 0.01057 | 0.015539 | 0.024605 | 0.00043375 | 0.35706 | 121.9116 | -0.059509 | 121.788 | 0.091553 | -0.018311 | 0 | 0.013733 | -0.018311 | -0.027466 | -0.045776 | 0.064087 | 0.036621 | 0.036621 | 0.041199 | -0.082398 | -0.20599 | 0.19226 | 0.10071 | 0.082397 | 0.059509 | 0.041198 | 0.073242 | -122.0123 | -122.0398 | 0.1648 | 0.13733 | 0.13733 | 0.064087 | 0.064087 | 0.15106 | 121.8475 | 0.091553 | -0.01831 | 121.9711 | 0.009155 | 122.0123 | 0.082397 | -122.0535 | -122.0215 | 121.8887 | 0.054932 | 0.45776 | 0.11444
2534.2969 | 122.0352 | -0.10986 | 121.9757 | -0.012131 | 0.0052508 | 0.054922 | 0.054083 | -0.0019781 | -0.010057 | -0.0011002 | -0.0023192 | 0.032571 | 0.048189 | 0.010143 | 0.017248 | 0.024178 | -0.0068295 | 0.36621 | 121.9391 | -0.09613 | 121.788 | 0.073242 | -0.073242 | -0.041199 | 0.013733 | -0.009155 | -0.022888 | -0.022888 | 0.054932 | 0.036621 | 0.064087 | 0.013733 | -0.036621 | -0.18768 | 0.18311 | 0.068664 | 0.036621 | 0.054931 | 0.022888 | 0.086975 | -121.9849 | -121.9986 | 0.16479 | 0.17395 | 0.14648 | 0.086975 | 0.059509 | 0.16937 | 121.8842 | 0.07782 | 0 | 122.0352 | 0.013733 | 122.049 | 0.10071 | -122.0718 | -121.9986 | 121.8979 | 0.086975 | 0.47607 | 0.1236
2536 | 122.1222 | -0.073242 | 121.9528 | 0.0031279 | -0.0024396 | 0.052786 | 0.048956 | -0.0053961 | -0.0077074 | -0.0004592 | -0.0023192 | 0.028085 | 0.048189 | 0.0071521 | 0.015112 | 0.024819 | 0.0010745 | 0.25635 | 121.9574 | -0.068665 | 121.7743 | 0.09613 | -0.032043 | 0 | 0.022888 | -0.032043 | -0.032043 | 0.022888 | 0.13733 | 0.12817 | 0.11902 | 0.004577 | 0.004577 | -0.17853 | 0.16937 | 0.073242 | 0.041199 | 0.068665 | 0.036622 | 0.041199 | -121.9849 | -121.9299 | 0.21057 | 0.19226 | 0.20142 | 0.15106 | 0.16022 | 0.16479 | 121.843 | 0.16937 | 0.054931 | 122.0261 | 0 | 122.0306 | 0.041199 | -122.0215 | -121.9849 | 121.8475 | 0.09613 | 0.32959 | 0.09613
2537.7656 | 121.994 | -0.11444 | 121.9849 | -0.012131 | 0.0056782 | 0.054922 | 0.053228 | 0.0012261 | -0.0079212 | -0.0015274 | -0.0084228 | 0.031717 | 0.044558 | 0.0077929 | 0.018102 | 0.024391 | -0.0021299 | 0.31586 | 121.962 | -0.10071 | 121.7102 | -0.027466 | -0.14648 | -0.11902 | -0.07782 | -0.004578 | -0.064087 | -0.082397 | -0.018311 | -0.032043 | 0.013733 | 0.013733 | -0.022888 | -0.27466 | 0.086975 | -0.004578 | -0.032043 | -0.018311 | -0.045776 | 0.050354 | -121.9894 | -122.0673 | 0.09613 | 0.12817 | 0.082398 | 0.07782 | 0.032044 | 0.073242 | 121.8109 | 0.045776 | -0.01831 | 122.0627 | 0.059509 | 122.0764 | 0.10986 | -122.0856 | -122.049 | 121.8246 | 0.032044 | 0.4303 | 0.036621
2539.4531 | 122.1451 | -0.050354 | 121.9391 | -0.012131 | 0.0048236 | 0.054922 | 0.050879 | -0.00026906 | -0.0062122 | -0.00345 | -0.005371 | 0.029153 | 0.046907 | 0.0097157 | 0.017461 | 0.027382 | -0.0038389 | 0.32959 | 121.9391 | -0.045776 | 121.8155 | 0.13275 | -0.013733 | 0.027466 | 0.10529 | -0.041199 | -0.018311 | 0.050354 | 0.16022 | 0.1236 | 0.14648 | 0.004578 | 0 | -0.1236 | 0.18311 | 0.07782 | 0.036621 | 0.073242 | 0.032043 | 0.032043 | -121.9803 | -121.8887 | 0.21057 | 0.19684 | 0.17395 | 0.16479 | 0.14191 | 0.17853 | 121.8613 | 0.17853 | 0.068665 | 121.9849 | -0.022888 | 121.9894 | 0.009155 | -121.9849 | -121.9574 | 121.8658 | 0.10071 | 0.37994 | 0.15564
2541.2188 | 122.1359 | -0.064087 | 121.9345 | -0.0045011 | 0.0033282 | 0.054068 | 0.054083 | 0.0014397 | -0.0077074 | -0.0013138 | -0.0023192 | 0.027871 | 0.047976 | 0.0062977 | 0.015966 | 0.025032 | -0.0025571 | 0.3067 | 121.9299 | -0.041199 | 121.843 | 0.15106 | -0.004578 | 0.036621 | 0.10986 | -0.041199 | -0.009155 | 0.050354 | 0.15106 | 0.11444 | 0.12817 | 0.022888 | -0.004577 | -0.091552 | 0.21515 | 0.10071 | 0.059509 | 0.07782 | 0.036621 | 0.054932 | -121.9757 | -121.8842 | 0.21515 | 0.19226 | 0.17853 | 0.13733 | 0.1236 | 0.19226 | 121.8842 | 0.16022 | 0.059509 | 121.9711 | -0.032044 | 121.994 | 0.022888 | -121.9757 | -121.9437 | 121.907 | 0.11444 | 0.37079 | 0.17395
2542.9844 | 122.081 | -0.10071 | 121.9757 | -0.012131 | 0.0020466 | 0.053214 | 0.052588 | 0.00058534 | -0.0074938 | -3.1996e-05 | -0.0084228 | 0.030648 | 0.048189 | 0.014842 | 0.017675 | 0.025887 | -0.0019163 | 0.2655 | 121.9574 | -0.07782 | 121.7239 | -0.009155 | -0.13733 | -0.086975 | 0.009155 | -0.009155 | -0.041199 | 0.009155 | 0.073242 | 0.068665 | 0.082397 | 0.022888 | -0.018311 | -0.25177 | 0.091553 | 0.013733 | -0.036621 | -0.009155 | -0.059509 | 0.059509 | -121.9849 | -121.9666 | 0.17395 | 0.18311 | 0.16937 | 0.1236 | 0.10986 | 0.068665 | 121.8018 | 0.11444 | 0.050354 | 122.0352 | 0.032044 | 122.0581 | 0.091553 | -122.0535 | -122.0169 | 121.8246 | 0.10986 | 0.36621 | 0.10986
2544.6875 | 122.049 | -0.10986 | 121.9849 | 0.0031279 | 0.001833 | 0.053641 | 0.049597 | -0.0047553 | -0.0059986 | -0.0045182 | -0.0023192 | 0.029153 | 0.045626 | 0.0088611 | 0.014684 | 0.02546 | -0.0046933 | 0.36163 | 121.9345 | -0.054932 | 121.7926 | 0.10071 | -0.004578 | 0.004578 | 0.022888 | -0.013733 | -0.022888 | -0.041199 | 0.068665 | 0.050354 | 0.041199 | 0.054931 | -0.050354 | -0.19226 | 0.21057 | 0.11444 | 0.10529 | 0.05951 | 0.050354 | 0.086975 | -121.9986 | -122.0261 | 0.17853 | 0.15106 | 0.16022 | 0.064087 | 0.073242 | 0.15564 | 121.8475 | 0.091553 | -0.018311 | 121.9894 | 0.009155 | 122.0444 | 0.09613 | -122.0398 | -122.0078 | 121.9025 | 0.068664 | 0.4715 | 0.13275
2546.4531 | 122.1176 | -0.07782 | 121.9437 | -0.012131 | 0.0033282 | 0.054922 | 0.052801 | 0.0010125 | -0.0059986 | -0.0047318 | -0.011475 | 0.030648 | 0.04648 | 0.0071521 | 0.015539 | 0.026314 | -0.0034117 | 0.27466 | 121.9528 | -0.073242 | 121.788 | 0.07782 | -0.064087 | -0.036621 | 0.068665 | -0.027466 | -0.032043 | 0.045776 | 0.14648 | 0.11444 | 0.1236 | 0.004578 | 0.009155 | -0.15564 | 0.15564 | 0.041199 | 0.013733 | 0.036621 | 0.009155 | 0.045777 | -121.9711 | -121.8979 | 0.2243 | 0.20142 | 0.19226 | 0.15564 | 0.14648 | 0.15106 | 121.8613 | 0.17853 | 0.077819 | 122.0261 | 0.004577 | 122.0306 | 0.050354 | -122.0169 | -121.9757 | 121.8658 | 0.1236 | 0.35248 | 0.14649
2548.2188 | 122.0901 | -0.082397 | 121.9528 | -0.0045011 | 0.0014056 | 0.055777 | 0.050665 | -0.0024055 | -0.0079212 | -0.0032364 | -0.0023192 | 0.030221 | 0.046694 | 0.0067249 | 0.018102 | 0.026314 | -0.0023435 | 0.2655 | 121.9299 | -0.054932 | 121.7789 | 0.09613 | -0.041199 | 0.004578 | 0.036621 | -0.027466 | -0.013733 | -0.004578 | 0.09613 | 0.09613 | 0.086975 | 0.027465 | -0.022888 | -0.17395 | 0.17853 | 0.086975 | 0.041198 | 0.05951 | 0.013733 | 0.068664 | -121.9803 | -121.9574 | 0.17853 | 0.16937 | 0.17853 | 0.10071 | 0.10986 | 0.15106 | 121.8338 | 0.10986 | 0.009155 | 121.9849 | -0.013733 | 122.0123 | 0.054931 | -122.0078 | -121.9666 | 121.8613 | 0.077819 | 0.3479 | 0.11902
2549.9844 | 122.1497 | -0.059509 | 121.9666 | -0.012131 | 0.00055118 | 0.052786 | 0.050879 | 0.00015814 | -0.010057 | -0.0043046 | -0.0084228 | 0.028512 | 0.045412 | 0.010356 | 0.014471 | 0.025673 | -0.0023435 | 0.35706 | 121.9299 | -0.036621 | 121.8338 | 0.17395 | 0.027466 | 0.059509 | 0.11902 | -0.036621 | -0.004578 | 0.050354 | 0.17853 | 0.16022 | 0.11902 | 0.022888 | -0.036621 | -0.13275 | 0.23346 | 0.11902 | 0.086975 | 0.09613 | 0.064087 | 0.054931 | -122.0032 | -121.9162 | 0.23804 | 0.17853 | 0.21973 | 0.1236 | 0.16479 | 0.21057 | 121.8704 | 0.18311 | 0.054932 | 121.9666 | -0.032043 | 121.9894 | 0.022888 | -122.0032 | -121.9711 | 121.8933 | 0.10986 | 0.41656 | 0.17853
2551.6875 | 122.1451 | -0.07782 | 121.9391 | -0.012131 | 0.0054644 | 0.057059 | 0.05216 | 0.00058534 | -0.0098438 | 0.0003952 | 0.00073235 | 0.02958 | 0.045412 | 0.013133 | 0.015966 | 0.023537 | -0.0051205 | 0.34332 | 121.9254 | -0.036621 | 121.843 | 0.15106 | -0.013733 | 0.036621 | 0.11444 | -0.032043 | -0.018311 | 0.068665 | 0.16479 | 0.14191 | 0.15106 | 0.041199 | -0.013733 | -0.09613 | 0.22888 | 0.11444 | 0.064087 | 0.073242 | 0.022888 | 0.059509 | -121.9711 | -121.8704 | 0.24261 | 0.22888 | 0.21973 | 0.16937 | 0.16022 | 0.18768 | 121.8796 | 0.18311 | 0.086976 | 121.962 | -0.013732 | 122.0032 | 0.045777 | -121.9757 | -121.9574 | 121.9208 | 0.14649 | 0.42114 | 0.19226
2553.4531 | 122.0993 | -0.091553 | 121.9528 | -0.0045011 | 0.0022602 | 0.053854 | 0.050665 | 0.00015814 | -0.0087756 | -0.002382 | -0.011475 | 0.02958 | 0.046053 | 0.0088611 | 0.015325 | 0.025032 | -0.0036253 | 0.2655 | 121.962 | -0.068665 | 121.788 | 0.082397 | -0.041199 | 0.004578 | 0.022888 | -0.022888 | -0.041199 | -0.009155 | 0.10529 | 0.086975 | 0.086975 | 0.022888 | 0.009155 | -0.16479 | 0.17395 | 0.096131 | 0.050354 | 0.073243 | 0.027466 | 0.050354 | -121.9757 | -121.962 | 0.19684 | 0.17853 | 0.17853 | 0.12817 | 0.12817 | 0.15106 | 121.8567 | 0.14649 | 0.032044 | 122.0306 | 0.018311 | 122.0535 | 0.068665 | -122.0215 | -121.994 | 121.8796 | 0.082398 | 0.35706 | 0.11444
2555.1562 | 122.0123 | -0.11444 | 121.9528 | -0.01976 | 0.0037556 | 0.054709 | 0.053869 | 0.00015814 | -0.0062122 | -0.0028092 | -0.005371 | 0.032785 | 0.047335 | 0.0095019 | 0.017889 | 0.02311 | -0.0031979 | 0.32501 | 121.9849 | -0.09613 | 121.6965 | -0.036621 | -0.16022 | -0.10986 | -0.10071 | 0.009155 | -0.054932 | -0.064087 | 0.004578 | -0.027466 | 0.032043 | 0.018311 | 0.032043 | -0.25635 | 0.07782 | 0.004578 | -0.045776 | -0.013733 | -0.064087 | 0.059509 | -121.9437 | -122.0169 | 0.11902 | 0.14648 | 0.086975 | 0.086975 | 0.027466 | 0.059509 | 121.7926 | 0.05951 | -0.009155 | 122.081 | 0.064087 | 122.0993 | 0.1236 | -122.049 | -122.0078 | 121.8109 | 0.050354 | 0.43945 | 0.013733
2556.9219 | 122.0856 | -0.073242 | 121.962 | -0.01976 | 0.001192 | 0.053214 | 0.050879 | -0.0053961 | -0.0079212 | -0.002382 | -0.0084228 | 0.028726 | 0.047976 | 0.0030933 | 0.015539 | 0.022469 | -0.0012753 | 0.27008 | 121.9208 | -0.064087 | 121.7743 | 0.082397 | -0.036621 | -0.022888 | 0.027466 | -0.027466 | -0.041199 | 0 | 0.10071 | 0.073242 | 0.091553 | 0.009155 | -0.041199 | -0.18768 | 0.15564 | 0.050354 | 0.036621 | 0.041199 | 0.027466 | 0.032043 | -121.9894 | -121.962 | 0.17395 | 0.16479 | 0.14648 | 0.13275 | 0.11444 | 0.14648 | 121.8384 | 0.14191 | 0.041199 | 121.9849 | 0.013733 | 121.994 | 0.045776 | -122.0261 | -122.0032 | 121.8475 | 0.073242 | 0.34332 | 0.10071
2558.625 | 122.1268 | -0.064087 | 121.9528 | -0.012131 | 0.0048236 | 0.054282 | 0.051947 | -5.5462e-05 | -0.0074938 | -0.0038772 | 0.00073235 | 0.029153 | 0.046694 | 0.0065113 | 0.015325 | 0.0261 | -0.0040525 | 0.3067 | 121.962 | -0.068665 | 121.7972 | 0.086975 | -0.064087 | 0.013733 | 0.073242 | -0.036621 | -0.022888 | 0.050354 | 0.14648 | 0.1236 | 0.14191 | -0.004578 | 0.009155 | -0.15564 | 0.15106 | 0.07782 | 0 | 0.082398 | 0.004578 | 0.041199 | -121.9894 | -121.9025 | 0.21057 | 0.20599 | 0.18768 | 0.16479 | 0.14648 | 0.15564 | 121.8658 | 0.16937 | 0.073242 | 122.0306 | -0.013733 | 122.0261 | 0.027466 | -122.0215 | -121.9757 | 121.8613 | 0.11444 | 0.37079 | 0.13733
2560.3906 | 122.0352 | -0.086975 | 121.9894 | -0.01976 | -8.9824e-05 | 0.054068 | 0.049811 | -0.00048286 | -0.010271 | -0.0043046 | -0.005371 | 0.028939 | 0.047548 | 0.0048023 | 0.015966 | 0.025246 | -0.0046933 | 0.37994 | 121.9482 | -0.050354 | 121.8018 | 0.10986 | -0.004578 | 0.004578 | 0.036621 | -0.036621 | -0.036621 | -0.036621 | 0.07782 | 0.054932 | 0.050354 | 0.036621 | -0.041199 | -0.18768 | 0.19684 | 0.091553 | 0.082397 | 0.054932 | 0.045776 | 0.050354 | -122.0261 | -122.0261 | 0.16479 | 0.13733 | 0.14191 | 0.086975 | 0.091553 | 0.16022 | 121.8521 | 0.11444 | 0 | 121.9986 | 0 | 122.0352 | 0.050354 | -122.0398 | -122.0261 | 121.8887 | 0.050354 | 0.46692 | 0.1236
2562.0938 | 122.1039 | -0.07782 | 121.9299 | -0.0045011 | 0.0014056 | 0.055136 | 0.049811 | -0.0024055 | -0.008562 | -0.0011002 | -0.0023192 | 0.028939 | 0.045412 | 0.0056567 | 0.013403 | 0.026314 | -0.0017027 | 0.37537 | 121.9116 | -0.050354 | 121.8155 | 0.13733 | 0.009155 | 0.045776 | 0.064087 | -0.041199 | -0.022888 | 0.018311 | 0.14191 | 0.1236 | 0.09613 | 0.027466 | -0.018311 | -0.11444 | 0.21515 | 0.1236 | 0.086975 | 0.09613 | 0.059509 | 0.054932 | -121.9711 | -121.9116 | 0.21973 | 0.17395 | 0.20142 | 0.11902 | 0.14648 | 0.18768 | 121.8658 | 0.16479 | 0.041199 | 121.962 | -0.018311 | 121.9894 | 0.036621 | -121.9803 | -121.9528 | 121.8933 | 0.096131 | 0.45319 | 0.14191
2563.8438 | 122.1542 | -0.050354 | 121.9666 | -0.012131 | -0.00094422 | 0.052786 | 0.049811 | -0.0028327 | -0.0064258 | -0.001741 | -0.005371 | 0.026376 | 0.046907 | 0.0082203 | 0.015752 | 0.024819 | -0.0034117 | 0.33875 | 121.9116 | -0.041199 | 121.8521 | 0.17853 | 0.041199 | 0.073242 | 0.14648 | -0.036621 | -0.009155 | 0.064087 | 0.18768 | 0.16022 | 0.1236 | 0.009155 | -0.054932 | -0.11444 | 0.22888 | 0.1236 | 0.091553 | 0.11444 | 0.082398 | 0.041199 | -122.0032 | -121.9025 | 0.23804 | 0.17395 | 0.21057 | 0.13275 | 0.16937 | 0.21973 | 121.8933 | 0.19684 | 0.073242 | 121.9528 | -0.027466 | 121.962 | 0.013733 | -122.0078 | -121.9757 | 121.9025 | 0.11444 | 0.3891 | 0.19684
2565.625 | 122.0032 | -0.1236 | 121.9894 | -0.01976 | 0.002901 | 0.054709 | 0.054083 | 0.0016535 | -0.0077074 | -0.0015274 | -0.0023192 | 0.033639 | 0.043917 | 0.0073657 | 0.017034 | 0.023537 | -0.0036253 | 0.33875 | 121.9666 | -0.09613 | 121.701 | -0.018311 | -0.14648 | -0.11444 | -0.07782 | 0.013733 | -0.045776 | -0.07782 | 0 | -0.027466 | 0.032043 | 0.027466 | -0.022888 | -0.28839 | 0.10528 | 0.009155 | -0.022888 | -0.018311 | -0.050354 | 0.07782 | -121.9757 | -122.0673 | 0.1236 | 0.15564 | 0.09613 | 0.077819 | 0.01831 | 0.077819 | 121.7972 | 0.045776 | -0.032044 | 122.0627 | 0.059509 | 122.0901 | 0.13733 | -122.0856 | -122.0352 | 121.8246 | 0.045776 | 0.46234 | 0.045776
2567.3125 | 122.0352 | -0.11902 | 121.994 | -0.012131 | 0.0033282 | 0.054709 | 0.05216 | 0.0027215 | -0.00963 | -0.0025956 | -0.0023192 | 0.032357 | 0.047548 | 0.0054431 | 0.017248 | 0.024605 | -0.0014891 | 0.3067 | 121.9849 | -0.091553 | 121.7056 | 0 | -0.15106 | -0.10529 | -0.050354 | 0.004578 | -0.050354 | -0.041199 | 0.036621 | 0 | 0.032043 | 0.027466 | -0.009156 | -0.28839 | 0.11902 | 0.013733 | -0.032043 | -0.013733 | -0.059509 | 0.068665 | -121.9894 | -122.0352 | 0.15564 | 0.15106 | 0.11902 | 0.082397 | 0.050354 | 0.091553 | 121.7972 | 0.086975 | 0.009155 | 122.0764 | 0.054932 | 122.1039 | 0.1236 | -122.0856 | -122.0444 | 121.8246 | 0.07782 | 0.42572 | 0.068665
2569.0781 | 122.0856 | -0.09613 | 121.9391 | -0.0045011 | 0.0016192 | 0.053 | 0.050451 | -0.00026906 | -0.0089892 | -0.0025956 | -0.005371 | 0.027658 | 0.04648 | 0.0069385 | 0.017034 | 0.024605 | -0.0023435 | 0.28839 | 121.9666 | -0.068665 | 121.7743 | 0.082397 | -0.027466 | -0.013733 | 0.027466 | -0.032043 | -0.027466 | 0.009155 | 0.10986 | 0.091553 | 0.082397 | 0.027465 | 0.027466 | -0.16479 | 0.17853 | 0.082397 | 0.068664 | 0.054932 | 0.041199 | 0.068664 | -121.9711 | -121.9299 | 0.20599 | 0.17853 | 0.18768 | 0.10986 | 0.11902 | 0.15106 | 121.843 | 0.13733 | 0.036621 | 122.0352 | -0.004577 | 122.0627 | 0.064087 | -122.0078 | -121.9666 | 121.8704 | 0.10528 | 0.38452 | 0.1236
2570.7812 | 122.0215 | -0.11902 | 121.9757 | -0.012131 | 0.0054644 | 0.055136 | 0.054083 | 0.0022943 | -0.006853 | -0.0025956 | -0.005371 | 0.032357 | 0.046267 | 0.0092883 | 0.014898 | 0.024391 | -0.0031979 | 0.3891 | 121.9986 | -0.068665 | 121.7514 | 0.050354 | -0.086975 | -0.064087 | 0.013733 | -0.009155 | -0.027466 | -0.027466 | 0.050354 | 0 | 0.050354 | 0.050354 | 0.022888 | -0.2243 | 0.16937 | 0.054932 | 0.032044 | 0.004578 | -0.01831 | 0.091553 | -121.9849 | -122.0032 | 0.16937 | 0.16937 | 0.11902 | 0.07782 | 0.027466 | 0.11902 | 121.8201 | 0.07782 | 0 | 122.0673 | 0.018311 | 122.1176 | 0.10986 | -122.0444 | -122.0032 | 121.8704 | 0.091553 | 0.50812 | 0.13275
2572.5469 | 122.1039 | -0.07782 | 121.9528 | -0.0045011 | 0.0043964 | 0.053427 | 0.050238 | 0.0014397 | -0.0079212 | -0.0032364 | -0.005371 | 0.029153 | 0.047121 | 0.0060841 | 0.015752 | 0.025673 | -0.0012753 | 0.32501 | 121.9391 | -0.032043 | 121.843 | 0.14648 | -0.009155 | 0.032043 | 0.11444 | -0.050354 | -0.013733 | 0.050354 | 0.13275 | 0.13275 | 0.10986 | 0.045777 | -0.013733 | -0.10986 | 0.2243 | 0.10986 | 0.068665 | 0.064086 | 0.022888 | 0.064087 | -122.0032 | -121.9025 | 0.21057 | 0.18768 | 0.21057 | 0.1236 | 0.14648 | 0.17853 | 121.875 | 0.14648 | 0.064087 | 121.9711 | -0.036621 | 122.0169 | 0.027466 | -121.9849 | -121.9666 | 121.9208 | 0.12817 | 0.40283 | 0.19226
2574.2969 | 122.0215 | -0.11444 | 121.9803 | -0.0045011 | 0.0020466 | 0.054068 | 0.051092 | -0.0058233 | -0.00963 | 0.001036 | -0.0023192 | 0.031076 | 0.045412 | 0.012279 | 0.015966 | 0.02546 | -0.0019163 | 0.37079 | 121.9711 | -0.07782 | 121.7514 | 0.050354 | -0.054932 | -0.036621 | -0.022888 | 0.004578 | -0.032043 | -0.068665 | 0.059509 | 0.032043 | 0.041199 | 0.036621 | -0.009156 | -0.22888 | 0.16479 | 0.07782 | 0.059509 | 0.041199 | 0.022888 | 0.082398 | -121.9757 | -122.049 | 0.17395 | 0.15564 | 0.14648 | 0.073242 | 0.064086 | 0.12817 | 121.8292 | 0.091552 | -0.036622 | 122.049 | 0.036621 | 122.0856 | 0.11902 | -122.0581 | -122.0123 | 121.8658 | 0.045776 | 0.48523 | 0.091553
2576 | 122.1268 | -0.064087 | 121.9345 | -0.0045011 | 0.00033758 | 0.050223 | 0.05152 | -0.0021919 | -0.0083484 | -0.0021682 | -0.005371 | 0.030008 | 0.045839 | 0.0026661 | 0.014898 | 0.025246 | -0.0027707 | 0.3891 | 121.9025 | -0.054932 | 121.8384 | 0.16937 | 0.027466 | 0.054932 | 0.091553 | -0.032043 | -0.004578 | 0.050354 | 0.1831 | 0.15564 | 0.13275 | 0.009155 | -0.032043 | -0.09613 | 0.23346 | 0.11902 | 0.091553 | 0.10986 | 0.082398 | 0.059509 | -121.9666 | -121.8842 | 0.24719 | 0.19684 | 0.21973 | 0.13733 | 0.16022 | 0.22431 | 121.8933 | 0.18768 | 0.054932 | 121.9574 | -0.027465 | 121.9666 | 0.032044 | -121.9894 | -121.9391 | 121.9025 | 0.11444 | 0.45319 | 0.15564
2577.7656 | 122.1085 | -0.073242 | 121.9437 | -0.01976 | 0.0024738 | 0.053854 | 0.049597 | -0.0021919 | -0.010485 | -0.005159 | -0.0023192 | 0.029794 | 0.045412 | 0.012493 | 0.016607 | 0.026528 | -0.0027707 | 0.29297 | 121.9482 | -0.064087 | 121.7697 | 0.073242 | -0.041199 | -0.027466 | 0.022888 | -0.018311 | -0.041199 | -0.009155 | 0.09613 | 0.082397 | 0.07782 | 0.009155 | 0.004577 | -0.17395 | 0.14648 | 0.045776 | 0.032043 | 0.036621 | 0.022888 | 0.032043 | -121.962 | -121.9528 | 0.16937 | 0.15106 | 0.15564 | 0.11902 | 0.1236 | 0.13733 | 121.8338 | 0.13733 | 0.032044 | 122.0123 | 0.022888 | 122.0215 | 0.054931 | -122.0078 | -121.9849 | 121.843 | 0.064087 | 0.36621 | 0.09613
2579.5156 | 122.0215 | -0.10986 | 122.0078 | -0.0045011 | 0.0033282 | 0.053214 | 0.04917 | 0.0012261 | -0.0094164 | -0.0025956 | -0.0023192 | 0.031076 | 0.047762 | 0.011852 | 0.015325 | 0.023751 | -0.0057615 | 0.39825 | 121.9208 | -0.054932 | 121.7834 | 0.07782 | -0.018311 | -0.009155 | 0.027466 | -0.004578 | -0.054932 | -0.059509 | 0.050354 | 0.027466 | 0.036621 | 0.054931 | -0.086975 | -0.2243 | 0.18768 | 0.10071 | 0.091552 | 0.045777 | 0.036621 | 0.054931 | -122.0123 | -122.0673 | 0.16022 | 0.14648 | 0.13733 | 0.091553 | 0.082398 | 0.13275 | 121.8384 | 0.10529 | -0.004577 | 121.9757 | 0.050354 | 122.0306 | 0.10529 | -122.0627 | -122.0627 | 121.8933 | 0.050354 | 0.50812 | 0.13733
2581.2812 | 122.1588 | -0.07782 | 121.9528 | -0.0045011 | 0.00012398 | 0.053854 | 0.050879 | 0.00079894 | -0.00963 | -0.0011002 | -0.0023192 | 0.029367 | 0.046907 | 0.0058703 | 0.015112 | 0.025246 | 6.346e-06 | 0.36163 | 121.9254 | -0.07782 | 121.8567 | 0.16937 | 0.041199 | 0.073242 | 0.11902 | -0.027466 | -0.004578 | 0.068665 | 0.1831 | 0.16022 | 0.12817 | 0 | -0.027466 | -0.096131 | 0.24719 | 0.15106 | 0.11902 | 0.15106 | 0.11902 | 0.073242 | -121.9803 | -121.8842 | 0.26092 | 0.20599 | 0.23804 | 0.13275 | 0.16479 | 0.24719 | 121.9345 | 0.18768 | 0.073243 | 122.0032 | -0.022888 | 122.0032 | 0.050354 | -122.0306 | -121.9574 | 121.9345 | 0.14649 | 0.43945 | 0.19684
2582.9844 | 122.0169 | -0.1236 | 121.9711 | -0.012131 | 0.0039692 | 0.053427 | 0.053228 | 0.00058534 | -0.0059986 | -0.002382 | -0.005371 | 0.031503 | 0.047335 | 0.0069385 | 0.018743 | 0.023964 | -0.0029843 | 0.31586 | 121.994 | -0.09613 | 121.7056 | -0.018311 | -0.14648 | -0.10986 | -0.050354 | -0.013733 | -0.022888 | -0.050354 | 0.027466 | 0 | 0.027466 | 0.027466 | 0.022889 | -0.2655 | 0.10528 | 0.013733 | -0.022888 | -0.013733 | -0.050354 | 0.10071 | -121.9849 | -122.0215 | 0.15106 | 0.15106 | 0.1236 | 0.050354 | 0.022888 | 0.077819 | 121.8018 | 0.050354 | -0.027466 | 122.0901 | 0.009155 | 122.1176 | 0.10986 | -122.0673 | -121.994 | 121.8292 | 0.073242 | 0.43945 | 0.073242
2584.75 | 122.168 | -0.068665 | 121.9391 | -0.01976 | 0.00033758 | 0.053854 | 0.052588 | -0.0024055 | -0.010271 | -0.0013138 | -0.005371 | 0.028726 | 0.044985 | 0.0095019 | 0.015325 | 0.025887 | -0.0040525 | 0.36621 | 121.907 | -0.054932 | 121.8292 | 0.18768 | 0.041199 | 0.073242 | 0.15106 | -0.045776 | -0.022888 | 0.050354 | 0.19684 | 0.15564 | 0.13275 | 0.013733 | -0.032044 | -0.10986 | 0.25635 | 0.14191 | 0.10986 | 0.12817 | 0.096131 | 0.045777 | -121.9849 | -121.8887 | 0.2655 | 0.20142 | 0.22431 | 0.15564 | 0.17853 | 0.24261 | 121.8842 | 0.21973 | 0.073242 | 121.962 | -0.022888 | 121.9757 | 0.022889 | -121.994 | -121.962 | 121.8979 | 0.11902 | 0.43488 | 0.21973
2586.5 | 122.049 | -0.12817 | 121.9894 | -0.012131 | 0.0039692 | 0.053854 | 0.054937 | -0.0028327 | -0.010271 | -0.000673 | -0.005371 | 0.030221 | 0.048189 | 0.010784 | 0.018102 | 0.024391 | -0.0051205 | 0.36621 | 121.9757 | -0.10071 | 121.7239 | -0.009155 | -0.091553 | -0.082397 | -0.036621 | 0.009155 | -0.041199 | -0.059509 | 0.064087 | 0.041199 | 0.054932 | 0.027466 | -0.013733 | -0.2655 | 0.11902 | 0.045777 | 0.036621 | 0.018311 | 0.009155 | 0.086975 | -121.9803 | -122.049 | 0.19226 | 0.18311 | 0.16937 | 0.096131 | 0.082398 | 0.091553 | 121.8246 | 0.10529 | -0.01831 | 122.0764 | 0.050354 | 122.1039 | 0.13733 | -122.0901 | -122.0306 | 121.8521 | 0.068665 | 0.49439 | 0.091553
2588.2656 | 122.1359 | -0.073242 | 121.9299 | -0.0045011 | 0.0020466 | 0.053 | 0.050024 | -0.00026906 | -0.0074938 | -0.0032364 | -0.0084228 | 0.029794 | 0.04648 | 0.0020251 | 0.014471 | 0.024819 | -0.00084805 | 0.32044 | 121.9345 | -0.050354 | 121.8063 | 0.13733 | 0.004578 | 0.050354 | 0.091553 | -0.041199 | -0.022888 | 0.050354 | 0.16937 | 0.16022 | 0.13733 | 0.022888 | 0.004577 | -0.1236 | 0.21057 | 0.1236 | 0.07782 | 0.10071 | 0.054932 | 0.050354 | -121.9711 | -121.8796 | 0.24261 | 0.21057 | 0.23346 | 0.16022 | 0.1831 | 0.18768 | 121.8567 | 0.19226 | 0.073242 | 121.9849 | -0.018311 | 122.0078 | 0.032043 | -121.9803 | -121.9528 | 121.8796 | 0.1236 | 0.39368 | 0.16479
2589.9688 | 122.0123 | -0.10986 | 121.9849 | -0.012131 | 0.0061054 | 0.055563 | 0.054297 | -0.00069646 | -0.0098438 | -0.000673 | -0.005371 | 0.030008 | 0.047121 | 0.013133 | 0.015539 | 0.023964 | -0.0066159 | 0.37994 | 121.994 | -0.07782 | 121.7331 | 0 | -0.12817 | -0.10986 | -0.054932 | 0.027466 | -0.045776 | -0.073242 | -0.009155 | -0.032043 | 0.018311 | 0.032043 | 0.009156 | -0.25177 | 0.10986 | 0 | -0.018311 | -0.032043 | -0.050354 | 0.064087 | -121.9574 | -122.0581 | 0.10071 | 0.12817 | 0.07782 | 0.064087 | 0.013733 | 0.07782 | 121.8109 | 0.036621 | -0.027466 | 122.0718 | 0.073242 | 122.1039 | 0.13733 | -122.0627 | -122.0306 | 121.843 | 0.036621 | 0.48981 | 0.054931
2591.7344 | 122.0169 | -0.11902 | 121.9757 | -0.01976 | -0.0024396 | 0.054495 | 0.049597 | -0.0026191 | -0.0081348 | -0.0036636 | -0.005371 | 0.030008 | 0.047335 | 0.0073657 | 0.014898 | 0.0261 | -0.00042085 | 0.38452 | 121.9482 | -0.086975 | 121.7468 | 0.050354 | -0.064087 | -0.050354 | -0.013733 | -0.004578 | -0.036621 | -0.064087 | 0.050354 | 0.032043 | 0.022888 | 0.032044 | -0.027466 | -0.22888 | 0.16937 | 0.068665 | 0.054932 | 0.036621 | 0.022888 | 0.082398 | -121.9803 | -122.0398 | 0.16937 | 0.14191 | 0.15106 | 0.059509 | 0.068664 | 0.13733 | 121.8338 | 0.086975 | -0.027466 | 122.0352 | 0.032043 | 122.0673 | 0.11444 | -122.0627 | -122.0123 | 121.8658 | 0.054932 | 0.50354 | 0.10529
2593.4844 | 122.0261 | -0.12817 | 122.0078 | -0.01976 | 0.00033758 | 0.053641 | 0.052374 | -0.0017645 | -0.0074938 | -0.0008866 | -0.011475 | 0.030221 | 0.048189 | 0.0090747 | 0.017889 | 0.025887 | -0.0061887 | 0.36621 | 121.9711 | -0.09613 | 121.6965 | -0.009155 | -0.10529 | -0.091553 | -0.059509 | 0.004578 | -0.036621 | -0.073242 | 0.027466 | 0.022888 | 0.036621 | 0.032044 | -0.036621 | -0.31128 | 0.11902 | 0.036621 | 0.022888 | 0.004577 | -0.009156 | 0.091553 | -122.0032 | -122.081 | 0.15564 | 0.1648 | 0.15106 | 0.073242 | 0.059509 | 0.086975 | 121.7926 | 0.064087 | -0.036621 | 122.0673 | 0.041199 | 122.0993 | 0.13275 | -122.1039 | -122.0444 | 121.8246 | 0.054932 | 0.49439 | 0.068665
2595.1875 | 122.1313 | -0.07782 | 121.9391 | -0.01976 | 0.0035418 | 0.054495 | 0.05152 | -0.00069646 | -0.0066394 | -0.0057998 | -0.005371 | 0.030008 | 0.047121 | 0.0069385 | 0.016393 | 0.025673 | -0.0038389 | 0.35706 | 121.9208 | -0.050354 | 121.8338 | 0.15106 | -0.022888 | 0.022888 | 0.11444 | -0.009155 | 0 | 0.050354 | 0.16479 | 0.13275 | 0.12817 | 0.027466 | -0.018311 | -0.10529 | 0.22888 | 0.10071 | 0.054932 | 0.073242 | 0.027466 | 0.07782 | -121.9482 | -121.8887 | 0.24261 | 0.20599 | 0.21057 | 0.12817 | 0.13275 | 0.20142 | 121.8842 | 0.16479 | 0.050354 | 121.9711 | -0.009155 | 121.9986 | 0.068665 | -121.9894 | -121.9391 | 121.9116 | 0.12817 | 0.43488 | 0.19226
2596.9688 | 122.0535 | -0.10529 | 121.9757 | -0.01976 | 0.002901 | 0.052786 | 0.053442 | 0.0031487 | -0.008562 | -0.005159 | -0.0023192 | 0.031289 | 0.045839 | 0.0097157 | 0.017034 | 0.024605 | -0.0078977 | 0.39825 | 121.9666 | -0.082397 | 121.7697 | 0.068665 | -0.059509 | -0.054932 | 0.013733 | 0 | -0.036621 | -0.022888 | 0.082397 | 0.064087 | 0.082397 | 0.022889 | -0.009155 | -0.20599 | 0.17395 | 0.050354 | 0.045777 | 0.027465 | 0.022888 | 0.068665 | -121.9757 | -121.9986 | 0.18768 | 0.18768 | 0.16937 | 0.11902 | 0.10071 | 0.15106 | 121.8521 | 0.11902 | 0.013733 | 122.049 | 0.036621 | 122.0718 | 0.10529 | -122.0581 | -122.0123 | 121.875 | 0.082398 | 0.50354 | 0.11902
2598.6719 | 122.1359 | -0.073242 | 121.9574 | -0.01976 | 0.0014056 | 0.054068 | 0.048102 | -0.0030463 | -0.0092028 | -0.0040908 | -0.0084228 | 0.026803 | 0.046694 | 0.0088611 | 0.015752 | 0.02546 | -0.0034117 | 0.3891 | 121.9299 | -0.059509 | 121.8475 | 0.16479 | 0.036621 | 0.045776 | 0.10986 | -0.018311 | -0.018311 | 0.059509 | 0.16937 | 0.14648 | 0.11444 | 0.013733 | -0.027465 | -0.10986 | 0.23804 | 0.11902 | 0.10986 | 0.10528 | 0.09613 | 0.054931 | -121.9757 | -121.8979 | 0.24261 | 0.18768 | 0.21973 | 0.13275 | 0.16479 | 0.2243 | 121.907 | 0.18768 | 0.07782 | 121.9894 | 0 | 122.0032 | 0.054931 | -122.0169 | -121.9757 | 121.9208 | 0.13275 | 0.46234 | 0.18311
2600.4219 | 122.0261 | -0.14648 | 122.0078 | -0.012131 | 0.0024738 | 0.051505 | 0.05216 | 0.00079894 | -0.0092028 | -0.00345 | -0.005371 | 0.028512 | 0.048616 | 0.0039477 | 0.015539 | 0.025246 | -0.0081113 | 0.34332 | 121.9574 | -0.091553 | 121.7102 | 0.022888 | -0.10529 | -0.086975 | -0.050354 | 0.018311 | -0.054932 | -0.082397 | 0.036621 | 0.009155 | 0.032043 | 0.054931 | -0.050354 | -0.29755 | 0.16937 | 0.059509 | 0.041198 | 0.004578 | -0.013733 | 0.091552 | -121.9894 | -122.0901 | 0.18311 | 0.17853 | 0.15564 | 0.086975 | 0.064087 | 0.11444 | 121.8018 | 0.091553 | -0.027465 | 122.049 | 0.073243 | 122.1039 | 0.16479 | -122.0993 | -122.0627 | 121.8567 | 0.064087 | 0.48981 | 0.09613
2602.1875 | 122.0169 | -0.10986 | 122.0032 | -0.012131 | 0.0056782 | 0.055777 | 0.053869 | -5.5462e-05 | -0.0070666 | -0.0040908 | -0.005371 | 0.032998 | 0.049685 | 0.0015979 | 0.018102 | 0.026528 | -0.0042661 | 0.3479 | 121.9986 | -0.082397 | 121.6965 | -0.027466 | -0.15564 | -0.10529 | -0.064087 | -0.004578 | -0.054932 | -0.045776 | 0 | -0.013733 | 0.041199 | 0.027466 | -0.004578 | -0.3067 | 0.082397 | 0.004577 | -0.045777 | -0.022889 | -0.073243 | 0.054931 | -122.0078 | -122.049 | 0.10986 | 0.15106 | 0.09613 | 0.096131 | 0.041199 | 0.054931 | 121.7789 | 0.054932 | 0.009156 | 122.081 | 0.050354 | 122.1085 | 0.10529 | -122.0856 | -122.0581 | 121.8063 | 0.064087 | 0.45776 | 0.045776
2603.9531 | 122.0993 | -0.07782 | 121.9574 | -0.012131 | 0.00097838 | 0.055991 | 0.047888 | -0.00048286 | -0.0098438 | -0.0015274 | -0.005371 | 0.028085 | 0.046907 | 0.012279 | 0.012975 | 0.02546 | 0.0027835 | 0.31586 | 121.9482 | -0.064087 | 121.7834 | 0.10986 | -0.032043 | 0.004578 | 0.054932 | -0.036621 | -0.018311 | 0.004578 | 0.10986 | 0.091553 | 0.091553 | 0.013733 | -0.009155 | -0.17395 | 0.18768 | 0.082398 | 0.045777 | 0.068665 | 0.032044 | 0.059509 | -121.994 | -121.9528 | 0.18768 | 0.16937 | 0.16937 | 0.10986 | 0.10986 | 0.17395 | 121.8475 | 0.12817 | 0.022889 | 122.0123 | -0.01831 | 122.0261 | 0.041199 | -122.0215 | -121.9757 | 121.8613 | 0.082398 | 0.39368 | 0.13275
2605.6562 | 122.1542 | -0.059509 | 121.9574 | -0.01976 | 0.0020466 | 0.055777 | 0.052374 | 0.00037174 | -0.0083484 | -0.00345 | -0.005371 | 0.030221 | 0.047762 | 0.011638 | 0.018316 | 0.024178 | -0.0057615 | 0.38452 | 121.9391 | -0.059509 | 121.8246 | 0.14191 | -0.013733 | 0.018311 | 0.10986 | -0.041199 | -0.022888 | 0.07782 | 0.16022 | 0.1236 | 0.14648 | 0 | -0.01831 | -0.13275 | 0.20142 | 0.07782 | 0.045776 | 0.07782 | 0.045776 | 0.036621 | -121.9986 | -121.8796 | 0.21973 | 0.20599 | 0.1831 | 0.16937 | 0.14648 | 0.20142 | 121.8842 | 0.1831 | 0.10071 | 121.9986 | -0.018311 | 121.9986 | 0.01831 | -122.0169 | -121.9803 | 121.8842 | 0.13733 | 0.44403 | 0.16937
2607.3594 | 122.0718 | -0.09613 | 121.994 | -0.01976 | 0.0022602 | 0.053 | 0.052801 | -0.0026191 | -0.0098438 | -0.005159 | -0.005371 | 0.03193 | 0.047548 | 0.010143 | 0.017034 | 0.024819 | -0.0034117 | 0.43488 | 121.9482 | -0.07782 | 121.7743 | 0.073242 | -0.064087 | -0.036621 | 0.036621 | 0.009155 | -0.036621 | -0.009155 | 0.07782 | 0.054932 | 0.064087 | 0.01831 | -0.045777 | -0.21973 | 0.16937 | 0.059509 | 0.032043 | 0.041199 | 0.013733 | 0.059509 | -121.9849 | -122.0032 | 0.17395 | 0.16022 | 0.15106 | 0.10071 | 0.091553 | 0.15106 | 121.8521 | 0.11444 | 0.027466 | 122.0261 | 0.045776 | 122.0444 | 0.10528 | -122.0718 | -122.0306 | 121.8704 | 0.086975 | 0.531 | 0.13275
2609.0469 | 122.1085 | -0.07782 | 121.9528 | -0.012131 | 0.0037556 | 0.05535 | 0.050665 | -0.0049689 | -0.0077074 | -0.0013138 | -0.005371 | 0.028939 | 0.047121 | 0.0041615 | 0.018102 | 0.026528 | -0.0036253 | 0.33875 | 121.9666 | -0.045776 | 121.8246 | 0.13733 | -0.027466 | 0.027466 | 0.10529 | -0.041199 | 0 | 0.032043 | 0.1236 | 0.10986 | 0.11444 | 0.032044 | 0.013733 | -0.12817 | 0.21515 | 0.10529 | 0.050354 | 0.073242 | 0.01831 | 0.07782 | -121.994 | -121.9208 | 0.20142 | 0.19226 | 0.18768 | 0.11444 | 0.10986 | 0.18311 | 121.8704 | 0.1236 | 0.032043 | 122.0123 | -0.041199 | 122.0444 | 0.036621 | -121.9986 | -121.9528 | 121.9025 | 0.10986 | 0.41657 | 0.18311
2610.8125 | 122.1451 | -0.068665 | 121.9574 | -0.012131 | 0.00076478 | 0.055563 | 0.050451 | 0.0014397 | -0.010485 | -0.0036636 | -0.005371 | 0.028085 | 0.046694 | 0.012493 | 0.014898 | 0.027382 | -0.0019163 | 0.39368 | 121.9116 | -0.059509 | 121.8475 | 0.17853 | 0.027466 | 0.045776 | 0.09613 | -0.022888 | -0.022888 | 0.045776 | 0.17395 | 0.15564 | 0.1236 | 0.009156 | -0.045776 | -0.10986 | 0.24719 | 0.11444 | 0.096131 | 0.10528 | 0.086975 | 0.045777 | -121.9803 | -121.9116 | 0.24261 | 0.19226 | 0.22431 | 0.14648 | 0.17853 | 0.23804 | 121.907 | 0.19684 | 0.068664 | 121.9711 | 0 | 121.9803 | 0.045777 | -122.0169 | -121.9803 | 121.9162 | 0.11444 | 0.46234 | 0.16479
2612.5312 | 122.1222 | -0.068665 | 121.9757 | -0.012131 | -0.001585 | 0.052359 | 0.05152 | -0.00026906 | -0.010271 | -0.001741 | -0.0084228 | 0.028512 | 0.046267 | 0.0082203 | 0.015752 | 0.024819 | 0.00064735 | 0.32044 | 121.9208 | -0.068665 | 121.7789 | 0.082397 | -0.018311 | 0.004578 | 0.045776 | -0.004578 | -0.036621 | 0.018311 | 0.1236 | 0.15106 | 0.13275 | 0 | -0.054932 | -0.19684 | 0.15106 | 0.073243 | 0.050354 | 0.073243 | 0.050354 | 0.032044 | -121.9803 | -121.9574 | 0.19226 | 0.20142 | 0.21973 | 0.16937 | 0.18768 | 0.15106 | 121.8475 | 0.16022 | 0.054932 | 121.9894 | 0.032043 | 121.9894 | 0.064087 | -122.0444 | -122.0123 | 121.8475 | 0.086976 | 0.3891 | 0.11444
2614.2969 | 122.1085 | -0.082397 | 121.9849 | -0.012131 | 0.0037556 | 0.054282 | 0.05216 | 0.0018671 | -0.010485 | -0.005159 | -0.0084228 | 0.028085 | 0.045198 | 0.0080067 | 0.015966 | 0.025887 | -0.0055479 | 0.35248 | 121.9208 | -0.041199 | 121.8201 | 0.14648 | -0.022888 | 0.036621 | 0.09613 | -0.032043 | -0.004578 | 0.036621 | 0.1236 | 0.10529 | 0.10071 | 0.041198 | -0.064087 | -0.16479 | 0.22888 | 0.11902 | 0.059509 | 0.07782 | 0.018311 | 0.077819 | -122.0169 | -121.9482 | 0.20599 | 0.18311 | 0.18768 | 0.10529 | 0.10986 | 0.18768 | 121.8613 | 0.12817 | 0.041199 | 121.962 | -0.027465 | 122.0032 | 0.050354 | -122.0261 | -121.9894 | 121.9025 | 0.11902 | 0.43488 | 0.17853
2616 | 122.0352 | -0.1236 | 121.9894 | -0.0045011 | 0.0024738 | 0.053854 | 0.051947 | 0.00015814 | -0.0087756 | -0.001741 | -0.0023192 | 0.030435 | 0.046053 | 0.0062977 | 0.014898 | 0.02311 | -0.0034117 | 0.37537 | 121.9528 | -0.10529 | 121.7056 | 0 | -0.086975 | -0.082397 | -0.050354 | 0.009155 | -0.059509 | -0.082397 | 0.009155 | 0.009155 | 0.036621 | 0.01831 | -0.036621 | -0.28381 | 0.1236 | 0.041199 | 0.036621 | 0.022889 | 0.018311 | 0.064087 | -121.9803 | -122.0718 | 0.13275 | 0.16022 | 0.13275 | 0.09613 | 0.068664 | 0.10529 | 121.8109 | 0.068664 | -0.022888 | 122.0581 | 0.068664 | 122.0764 | 0.13275 | -122.0947 | -122.049 | 121.8292 | 0.041199 | 0.49896 | 0.073242
2617.7812 | 122.0078 | -0.10529 | 121.994 | -0.0045011 | 0.0033282 | 0.055563 | 0.053015 | -0.00069646 | -0.0083484 | 0.001036 | -0.0023192 | 0.032144 | 0.048616 | 0.016979 | 0.017461 | 0.025673 | -0.0023435 | 0.37537 | 121.9711 | -0.10071 | 121.7102 | -0.041199 | -0.16479 | -0.11902 | -0.086975 | 0 | -0.068665 | -0.064087 | 0.009155 | -0.013733 | 0.032043 | 0.004578 | -0.022889 | -0.28381 | 0.064087 | -0.013733 | -0.059509 | -0.018311 | -0.064087 | 0.036621 | -121.994 | -122.0581 | 0.11444 | 0.13733 | 0.091553 | 0.10071 | 0.054932 | 0.059509 | 121.8109 | 0.07782 | 0.004578 | 122.0718 | 0.068665 | 122.0764 | 0.10529 | -122.0947 | -122.0627 | 121.8155 | 0.041199 | 0.48065 | 0.018311
2619.4688 | 122.1542 | -0.068665 | 121.962 | -0.012131 | 0.006319 | 0.055991 | 0.051947 | 0.00015814 | -0.0094164 | -0.0021682 | -0.0023192 | 0.031717 | 0.047548 | 0.0062977 | 0.015539 | 0.025032 | 6.346e-06 | 0.3891 | 121.9666 | -0.036621 | 121.8201 | 0.13275 | -0.018311 | 0.018311 | 0.09613 | -0.027466 | -0.013733 | 0.07782 | 0.15564 | 0.13733 | 0.15564 | 0.032044 | 0.004578 | -0.14191 | 0.20142 | 0.086976 | 0.050354 | 0.054932 | 0.01831 | 0.054932 | -121.9894 | -121.8842 | 0.22431 | 0.22431 | 0.20599 | 0.16937 | 0.15106 | 0.16937 | 121.8567 | 0.16937 | 0.091553 | 122.0032 | -0.013733 | 122.0352 | 0.041199 | -121.9986 | -121.9757 | 121.8887 | 0.14649 | 0.45776 | 0.16479
2621.1562 | 122.1313 | -0.082397 | 121.9803 | -0.012131 | 0.0020466 | 0.053427 | 0.048742 | 0.00015814 | -0.010912 | -0.0002456 | -0.0023192 | 0.027658 | 0.045839 | 0.0088611 | 0.015966 | 0.023964 | -0.0059751 | 0.40283 | 121.9116 | -0.059509 | 121.8475 | 0.1831 | 0.041199 | 0.041199 | 0.10529 | -0.027466 | -0.013733 | 0.050354 | 0.17395 | 0.14648 | 0.1236 | 0.022888 | -0.068665 | -0.13275 | 0.2655 | 0.1236 | 0.1236 | 0.10071 | 0.10071 | 0.068664 | -122.0078 | -121.9299 | 0.25635 | 0.20599 | 0.22888 | 0.13733 | 0.16022 | 0.24261 | 121.907 | 0.18768 | 0.064087 | 121.9711 | -0.013733 | 121.994 | 0.054931 | -122.0398 | -121.994 | 121.9299 | 0.13275 | 0.48523 | 0.18768
2622.9219 | 122.0581 | -0.09613 | 121.9574 | -0.012131 | 0.0043964 | 0.056418 | 0.057074 | 0.0037897 | -0.0079212 | -0.0032364 | -0.0084228 | 0.030862 | 0.047762 | 0.01762 | 0.018743 | 0.024819 | -0.0017027 | 0.33875 | 121.9757 | -0.091553 | 121.7148 | 0.004578 | -0.11902 | -0.091553 | -0.009155 | 0.004578 | -0.041199 | -0.022888 | 0.032043 | 0.027466 | 0.059509 | 0.004577 | 0.018311 | -0.24261 | 0.10071 | 0.004577 | -0.022889 | 0 | -0.027466 | 0.054931 | -121.9528 | -121.9803 | 0.12817 | 0.15564 | 0.1236 | 0.10071 | 0.068665 | 0.096131 | 121.8063 | 0.073242 | 0.018311 | 122.0673 | 0.045777 | 122.0718 | 0.10071 | -122.049 | -121.9986 | 121.8109 | 0.073242 | 0.43488 | 0.086975
2624.6875 | 122.1405 | -0.064087 | 121.9299 | -0.012131 | 0.0050372 | 0.055136 | 0.05216 | 0.0042169 | -0.0062122 | -0.000673 | -0.005371 | 0.028512 | 0.045626 | 0.011852 | 0.018316 | 0.025032 | -0.0057615 | 0.39368 | 121.9208 | -0.050354 | 121.8246 | 0.14191 | -0.018311 | 0.022888 | 0.11444 | -0.027466 | -0.004578 | 0.064087 | 0.15564 | 0.12817 | 0.13733 | 0.013733 | -0.009156 | -0.10529 | 0.20599 | 0.086975 | 0.045776 | 0.073242 | 0.032043 | 0.059509 | -121.9574 | -121.8658 | 0.21973 | 0.20142 | 0.19226 | 0.14191 | 0.13275 | 0.19226 | 121.875 | 0.16022 | 0.068665 | 121.9711 | -0.022888 | 121.9849 | 0.036621 | -121.9803 | -121.9345 | 121.8887 | 0.12817 | 0.45776 | 0.17853
2626.3906 | 122.1634 | -0.082397 | 121.9711 | -0.012131 | 0.00033758 | 0.054709 | 0.050451 | -0.00026906 | -0.0089892 | -0.0004592 | -0.005371 | 0.027017 | 0.046907 | 0.0028797 | 0.01383 | 0.022896 | -0.0019163 | 0.39825 | 121.9299 | -0.054932 | 121.8704 | 0.1831 | 0.045776 | 0.059509 | 0.10986 | -0.009155 | -0.022888 | 0.045776 | 0.1831 | 0.16479 | 0.11902 | 0.027465 | -0.041198 | -0.10071 | 0.2655 | 0.14191 | 0.12817 | 0.11444 | 0.10071 | 0.059509 | -121.9803 | -121.9254 | 0.2655 | 0.20142 | 0.24719 | 0.14191 | 0.18768 | 0.23804 | 121.9254 | 0.20599 | 0.068664 | 121.9849 | 0.013733 | 122.0123 | 0.073242 | -122.0261 | -121.994 | 121.9528 | 0.12817 | 0.48065 | 0.19226
2628.1562 | 122.0535 | -0.086975 | 121.9574 | -0.012131 | 0.0037556 | 0.054709 | 0.052801 | 0.0010125 | -0.0053576 | -0.001741 | -0.0084228 | 0.031076 | 0.047548 | 0.0088611 | 0.017461 | 0.025246 | -0.0031979 | 0.43945 | 121.9574 | -0.086975 | 121.7606 | 0.064087 | -0.059509 | -0.045776 | 0.022888 | -0.009155 | -0.027466 | -0.004578 | 0.091553 | 0.059509 | 0.068665 | 0 | 0 | -0.19684 | 0.15106 | 0.041199 | 0.027466 | 0.041199 | 0.027466 | 0.059509 | -121.9666 | -121.962 | 0.17853 | 0.15564 | 0.14648 | 0.096131 | 0.086975 | 0.15106 | 121.8475 | 0.11902 | 0.022888 | 122.0444 | 0.018311 | 122.0444 | 0.07782 | -122.0444 | -121.9849 | 121.8475 | 0.082397 | 0.52643 | 0.10986
2629.9219 | 121.9757 | -0.10529 | 121.9849 | -0.012131 | 0.0054644 | 0.058127 | 0.054937 | 0.0050713 | -0.0083484 | -3.1996e-05 | -0.005371 | 0.031503 | 0.047762 | 0.011638 | 0.018957 | 0.02546 | -0.0053343 | 0.36621 | 121.9986 | -0.068665 | 121.701 | -0.027466 | -0.16479 | -0.11444 | -0.086975 | -0.004578 | -0.032043 | -0.054932 | 0 | -0.018311 | 0.041199 | 0.036621 | 0.013733 | -0.28381 | 0.07782 | -0.009155 | -0.059509 | -0.045776 | -0.09613 | 0.073243 | -121.9894 | -122.0398 | 0.10529 | 0.14649 | 0.086975 | 0.073242 | 0.013732 | 0.041199 | 121.7697 | 0.032043 | -0.022889 | 122.0673 | 0.027465 | 122.1039 | 0.10071 | -122.0535 | -122.0169 | 121.8063 | 0.050354 | 0.4715 | 0.018311
2631.6406 | 122.0535 | -0.10529 | 121.9528 | -0.0045011 | 0.0031146 | 0.054709 | 0.051947 | 0.0020807 | -0.0083484 | -0.002382 | -0.005371 | 0.03193 | 0.049044 | 0.014415 | 0.017034 | 0.026528 | -0.0021299 | 0.43945 | 121.994 | -0.073242 | 121.7789 | 0.073242 | -0.050354 | -0.041199 | 0.045776 | -0.004578 | -0.045776 | 0.004578 | 0.082397 | 0.064087 | 0.073242 | 0.032044 | 0.041199 | -0.17395 | 0.17853 | 0.064087 | 0.054932 | 0.032043 | 0.022888 | 0.05951 | -121.9574 | -121.9482 | 0.18768 | 0.17853 | 0.16937 | 0.11902 | 0.10986 | 0.14648 | 121.8521 | 0.12817 | 0.050354 | 122.0673 | 0.041198 | 122.0993 | 0.10071 | -122.0261 | -121.9986 | 121.8842 | 0.10986 | 0.54474 | 0.15106
2633.4062 | 122.0444 | -0.11444 | 121.9986 | -0.0045011 | 0.002901 | 0.052786 | 0.050024 | -0.0011237 | -0.0094164 | -0.0030228 | -0.0023192 | 0.031289 | 0.049044 | 0.0020251 | 0.015752 | 0.023537 | -0.0012753 | 0.38452 | 121.9711 | -0.10529 | 121.7056 | -0.004578 | -0.09613 | -0.10986 | -0.059509 | 0.013733 | -0.050354 | -0.054932 | 0.059509 | 0.032043 | 0.036621 | 0.009155 | -0.027466 | -0.29297 | 0.10986 | 0.004578 | 0.018311 | -0.004577 | 0.009156 | 0.064087 | -121.9849 | -122.0535 | 0.17395 | 0.15106 | 0.14648 | 0.086975 | 0.082397 | 0.10071 | 121.8109 | 0.10986 | -0.004578 | 122.0764 | 0.064087 | 122.0856 | 0.12817 | -122.1039 | -122.049 | 121.8201 | 0.059509 | 0.49896 | 0.054932
2635.1719 | 122.0398 | -0.11444 | 122.0078 | -0.01976 | 0.00012398 | 0.054709 | 0.050665 | 0.0010125 | -0.0094164 | -0.0004592 | -0.0023192 | 0.030435 | 0.048403 | 0.0097157 | 0.016821 | 0.0261 | -0.0042661 | 0.40283 | 121.9849 | -0.09613 | 121.7056 | 0 | -0.091553 | -0.07782 | -0.050354 | 0.018311 | -0.054932 | -0.064087 | 0.036621 | 0.027466 | 0.041199 | 0.018311 | -0.022888 | -0.30212 | 0.11444 | 0.036621 | 0.022888 | 0.01831 | 0.004577 | 0.059509 | -121.9894 | -122.0718 | 0.15106 | 0.15564 | 0.14191 | 0.096131 | 0.082398 | 0.09613 | 121.8018 | 0.091553 | -0.009155 | 122.081 | 0.073243 | 122.0993 | 0.13275 | -122.1039 | -122.0627 | 121.8201 | 0.050354 | 0.51727 | 0.064087
2636.9375 | 122.1359 | -0.059509 | 121.9345 | -0.0045011 | 0.0026874 | 0.057272 | 0.052588 | 0.00015814 | -0.0062122 | -0.0025956 | -0.005371 | 0.027871 | 0.047976 | 0.01057 | 0.017675 | 0.026955 | -0.0068295 | 0.39825 | 121.9391 | -0.050354 | 121.8109 | 0.14648 | -0.018311 | 0.027466 | 0.11902 | -0.050354 | -0.013733 | 0.068665 | 0.16022 | 0.14191 | 0.13733 | 0.009155 | 0.004578 | -0.1236 | 0.20599 | 0.086975 | 0.041198 | 0.07782 | 0.032043 | 0.045776 | -121.9849 | -121.8658 | 0.21973 | 0.19684 | 0.20142 | 0.15106 | 0.15564 | 0.19684 | 121.8613 | 0.17395 | 0.082398 | 121.9894 | -0.036621 | 121.9986 | 0.009155 | -121.9849 | -121.9482 | 121.8704 | 0.12817 | 0.45776 | 0.17853
2638.6406 | 121.994 | -0.11444 | 121.994 | -0.012131 | 0.0069598 | 0.054495 | 0.051306 | 0.0046441 | -0.0062122 | 0.0008224 | -0.0084228 | 0.032357 | 0.048403 | 0.0069385 | 0.018957 | 0.025673 | -0.0040525 | 0.38452 | 121.9849 | -0.091553 | 121.7148 | -0.009155 | -0.14648 | -0.10986 | -0.073242 | 0.009155 | -0.045776 | -0.073242 | -0.004578 | -0.018311 | 0.027466 | 0.022888 | -0.009156 | -0.27924 | 0.10529 | 0.004578 | -0.032043 | -0.01831 | -0.054931 | 0.068665 | -121.9849 | -122.0673 | 0.10986 | 0.14191 | 0.09613 | 0.073242 | 0.027465 | 0.082398 | 121.8063 | 0.041198 | -0.027466 | 122.0764 | 0.054931 | 122.0993 | 0.1236 | -122.0856 | -122.0398 | 121.8292 | 0.041199 | 0.49896 | 0.041199
2640.4062 | 122.0032 | -0.11902 | 121.9894 | -0.012131 | 0.0052508 | 0.053427 | 0.053442 | 0.0044305 | -0.0077074 | -0.0015274 | -0.0084228 | 0.030648 | 0.050325 | 0.012065 | 0.016393 | 0.025246 | -0.0010617 | 0.36163 | 122.0123 | -0.09613 | 121.6873 | -0.027466 | -0.16022 | -0.10986 | -0.073242 | 0.004578 | -0.036621 | -0.064087 | 0.004578 | -0.009155 | 0.045776 | 0.022889 | 0.022888 | -0.30212 | 0.091553 | 0.009156 | -0.041198 | -0.013733 | -0.064087 | 0.082398 | -121.9849 | -122.0535 | 0.1236 | 0.16479 | 0.10986 | 0.082397 | 0.027466 | 0.068664 | 121.7834 | 0.041199 | -0.027466 | 122.1085 | 0.041199 | 122.1313 | 0.1236 | -122.0856 | -122.0261 | 121.8063 | 0.054932 | 0.48065 | 0.045777
2642.1719 | 122.113 | -0.050354 | 121.9666 | -0.01976 | 0.0016192 | 0.056204 | 0.050665 | -0.0026191 | -0.0092028 | -0.0025956 | -0.0084228 | 0.02958 | 0.049685 | 0.0088611 | 0.015112 | 0.027382 | -0.0059751 | 0.42572 | 121.9208 | -0.036621 | 121.8246 | 0.16479 | 0.032043 | 0.045776 | 0.091553 | -0.022888 | -0.027466 | 0.041199 | 0.16479 | 0.15106 | 0.1236 | 0.013733 | -0.045777 | -0.14191 | 0.21515 | 0.09613 | 0.082397 | 0.082397 | 0.068664 | 0.022888 | -121.9894 | -121.9254 | 0.21515 | 0.17395 | 0.20142 | 0.15106 | 0.17853 | 0.20142 | 121.8613 | 0.19226 | 0.068665 | 121.9574 | 0.004578 | 121.9711 | 0.027466 | -122.0032 | -121.994 | 121.875 | 0.091553 | 0.47607 | 0.14191
2643.9375 | 122.1268 | -0.10071 | 121.9437 | -0.012131 | 0.00012398 | 0.053427 | 0.049597 | -0.0024055 | -0.010485 | -0.0057998 | -0.005371 | 0.029153 | 0.049471 | 0.00031607 | 0.014898 | 0.026528 | -0.00084805 | 0.4303 | 121.8933 | -0.064087 | 121.8338 | 0.15106 | 0.022888 | 0.041199 | 0.10986 | -0.013733 | -0.027466 | 0.036621 | 0.16479 | 0.14191 | 0.11444 | 0.036621 | -0.050354 | -0.10986 | 0.25177 | 0.14191 | 0.1236 | 0.10529 | 0.086975 | 0.073242 | -121.9574 | -121.907 | 0.2655 | 0.21515 | 0.24262 | 0.14191 | 0.16937 | 0.21515 | 121.8979 | 0.19226 | 0.064087 | 121.9574 | 0.013733 | 121.994 | 0.086975 | -122.0078 | -121.9711 | 121.9345 | 0.13733 | 0.53101 | 0.21057
2645.6406 | 122.1359 | -0.068665 | 121.9528 | -0.01976 | 0.0054644 | 0.054282 | 0.053869 | 0.0012261 | -0.0072802 | -0.0047318 | -0.0023192 | 0.030435 | 0.045198 | 0.0075793 | 0.017889 | 0.026528 | -0.0014891 | 0.37537 | 121.9574 | -0.073242 | 121.7834 | 0.091553 | -0.036621 | -0.018311 | 0.082397 | -0.027466 | -0.013733 | 0.059509 | 0.13733 | 0.11444 | 0.14191 | -0.004577 | 0.004577 | -0.16937 | 0.16022 | 0.050354 | 0.032044 | 0.054931 | 0.036621 | 0.054932 | -121.9803 | -121.8933 | 0.20599 | 0.21057 | 0.18311 | 0.15564 | 0.12817 | 0.16479 | 121.8567 | 0.15106 | 0.073242 | 122.0306 | -0.013733 | 122.0261 | 0.041199 | -122.0261 | -121.9666 | 121.8521 | 0.12817 | 0.44403 | 0.15106
2647.4062 | 122.168 | -0.059509 | 121.9574 | 0.0031279 | 0.001833 | 0.053214 | 0.049597 | -0.00048286 | -0.0098438 | -3.1996e-05 | -0.0084228 | 0.028726 | 0.046694 | 0.0041615 | 0.013616 | 0.024819 | -0.0034117 | 0.41199 | 121.9345 | -0.045776 | 121.8338 | 0.16479 | 0.036621 | 0.054932 | 0.13733 | -0.050354 | -0.004578 | 0.07782 | 0.19226 | 0.16022 | 0.14191 | 0.013733 | -0.022888 | -0.1236 | 0.2243 | 0.11444 | 0.09613 | 0.10071 | 0.082397 | 0.054931 | -122.0078 | -121.8796 | 0.25177 | 0.20142 | 0.21973 | 0.14649 | 0.16479 | 0.21057 | 121.8796 | 0.19684 | 0.082398 | 121.9803 | -0.045776 | 121.994 | 0.009155 | -122.0032 | -121.962 | 121.8933 | 0.13733 | 0.4715 | 0.19684
2649.1719 | 122.0856 | -0.10529 | 121.9666 | -0.0045011 | 0.0039692 | 0.054709 | 0.052588 | 0.0012261 | -0.0098438 | -0.0036636 | -0.005371 | 0.031503 | 0.049898 | 0.0092883 | 0.01618 | 0.025032 | -0.0029843 | 0.44403 | 121.9574 | -0.086975 | 121.7514 | 0.059509 | -0.064087 | -0.032043 | 0.018311 | -0.004578 | -0.032043 | -0.004578 | 0.086975 | 0.059509 | 0.068665 | 0.018311 | -0.009156 | -0.21515 | 0.16479 | 0.073243 | 0.041199 | 0.054932 | 0.022888 | 0.073243 | -121.9711 | -121.9711 | 0.19226 | 0.17395 | 0.16479 | 0.10071 | 0.091552 | 0.14648 | 121.8384 | 0.11902 | 0.027465 | 122.0444 | 0.027465 | 122.0627 | 0.10071 | -122.0535 | -121.9986 | 121.8567 | 0.10071 | 0.54932 | 0.1236
2650.9375 | 122.1085 | -0.09613 | 121.9574 | -0.012131 | 0.0020466 | 0.054282 | 0.050024 | 0.00079894 | -0.0092028 | -0.0036636 | -0.0084228 | 0.028085 | 0.048403 | 0.0050159 | 0.015325 | 0.025032 | 0.0015017 | 0.35706 | 121.9162 | -0.045776 | 121.7926 | 0.10529 | -0.054932 | 0.004578 | 0.054932 | -0.027466 | 0 | 0.018311 | 0.10529 | 0.082397 | 0.086975 | 0.050354 | -0.041198 | -0.16479 | 0.20142 | 0.10071 | 0.041198 | 0.050354 | -0.009156 | 0.09613 | -121.9849 | -121.9391 | 0.20142 | 0.1831 | 0.17853 | 0.086975 | 0.082397 | 0.15106 | 121.8384 | 0.10529 | 0.018311 | 121.962 | -0.027466 | 122.0123 | 0.068664 | -122.0032 | -121.9574 | 121.8887 | 0.11444 | 0.45319 | 0.15106
2652.6562 | 122.0352 | -0.11902 | 121.9803 | -0.012131 | 0.0026874 | 0.053214 | 0.054083 | -0.0024055 | -0.0089892 | -0.000673 | -0.005371 | 0.02958 | 0.049685 | 0.0058703 | 0.016393 | 0.025032 | -0.0053343 | 0.40741 | 121.9849 | -0.091553 | 121.7285 | 0.004578 | -0.091553 | -0.07782 | -0.050354 | 0 | -0.050354 | -0.036621 | 0.064087 | 0.045776 | 0.064087 | 0.027466 | 0.004577 | -0.25177 | 0.1236 | 0.041199 | 0.027466 | 0.013733 | 0 | 0.068665 | -121.9803 | -122.0169 | 0.18311 | 0.18311 | 0.16479 | 0.11444 | 0.09613 | 0.096131 | 121.8201 | 0.11444 | 0.013733 | 122.0764 | 0.050354 | 122.1039 | 0.11902 | -122.0718 | -122.0306 | 121.8475 | 0.082398 | 0.52643 | 0.068665
2654.4219 | 122.1588 | -0.082397 | 121.962 | -0.01976 | -0.00073062 | 0.050864 | 0.049383 | 0.00037174 | -0.0092028 | -0.0038772 | -0.005371 | 0.028512 | 0.047335 | 0.0075793 | 0.014684 | 0.023964 | -0.0064023 | 0.43488 | 121.8979 | -0.045776 | 121.8567 | 0.17395 | 0.032043 | 0.050354 | 0.11444 | -0.032043 | -0.004578 | 0.045776 | 0.1831 | 0.16022 | 0.11902 | 0.036621 | -0.064087 | -0.10529 | 0.25635 | 0.13275 | 0.11444 | 0.09613 | 0.077819 | 0.077819 | -121.994 | -121.9162 | 0.2655 | 0.20142 | 0.24261 | 0.1236 | 0.16479 | 0.21973 | 121.9025 | 0.18768 | 0.050354 | 121.9437 | -0.027465 | 121.9803 | 0.050354 | -122.0078 | -121.9666 | 121.9391 | 0.12817 | 0.51727 | 0.19684
2656.1875 | 122.0306 | -0.11444 | 122.0032 | -0.012131 | 0.001192 | 0.051718 | 0.05216 | -0.00091006 | -0.0098438 | -0.002382 | -0.0023192 | 0.030435 | 0.049257 | 0.01057 | 0.015752 | 0.025887 | -0.00084805 | 0.39368 | 121.9757 | -0.10529 | 121.7056 | -0.009155 | -0.10986 | -0.07782 | -0.073242 | 0.004578 | -0.054932 | -0.086975 | 0.032043 | -0.004578 | 0.022888 | 0.009155 | -0.027466 | -0.29755 | 0.10529 | 0.036621 | 0.004578 | 0.027466 | -0.004577 | 0.059509 | -121.9986 | -122.0901 | 0.14648 | 0.13733 | 0.10986 | 0.07782 | 0.050354 | 0.096131 | 121.8109 | 0.086975 | -0.032043 | 122.081 | 0.05951 | 122.0901 | 0.11902 | -122.1085 | -122.0581 | 121.8201 | 0.027466 | 0.50812 | 0.041199
2657.8906 | 122.0215 | -0.11902 | 122.0078 | 0.0031279 | 0.00012398 | 0.053854 | 0.050451 | 0.00037174 | -0.011125 | -0.0028092 | -0.005371 | 0.029367 | 0.04648 | 0.0071521 | 0.013403 | 0.023323 | -0.0031979 | 0.3891 | 121.9437 | -0.091553 | 121.7194 | 0.022888 | -0.10529 | -0.07782 | -0.064087 | -0.004578 | -0.054932 | -0.082397 | 0.027466 | 0.022888 | 0.013733 | 0.027466 | -0.064086 | -0.28839 | 0.14191 | 0.041199 | 0.013733 | 0.013733 | -0.013733 | 0.064087 | -122.0123 | -122.0901 | 0.14649 | 0.13275 | 0.14191 | 0.068665 | 0.07782 | 0.11444 | 121.8109 | 0.082398 | -0.027465 | 122.0352 | 0.050354 | 122.0627 | 0.11444 | -122.0993 | -122.0627 | 121.8384 | 0.036622 | 0.50812 | 0.054932
2659.6562 | 122.0352 | -0.11444 | 122.0032 | -0.012131 | 0.0024738 | 0.053427 | 0.053442 | 0.0018671 | -0.010698 | -0.0036636 | -0.0084228 | 0.031717 | 0.048403 | 0.0095019 | 0.017461 | 0.024178 | 0.0038515 | 0.42114 | 121.9711 | -0.10071 | 121.701 | 0 | -0.10071 | -0.09613 | -0.068665 | 0.009155 | -0.059509 | -0.068665 | 0.022888 | 0.013733 | 0.036621 | 0.013733 | -0.032044 | -0.30212 | 0.11444 | 0.018311 | 0.013733 | 0.004578 | 0 | 0.054932 | -121.994 | -122.0718 | 0.13733 | 0.15106 | 0.12817 | 0.09613 | 0.073242 | 0.10071 | 121.8018 | 0.082397 | -0.009156 | 122.0718 | 0.068664 | 122.0856 | 0.1236 | -122.1039 | -122.0627 | 121.8155 | 0.045776 | 0.53558 | 0.045776
2661.4062 | 122.0901 | -0.09613 | 121.9666 | -0.0045011 | -0.0011578 | 0.053 | 0.050024 | -0.0015509 | -0.0072802 | -0.0038772 | -0.005371 | 0.028939 | 0.048189 | 0.00095707 | 0.015539 | 0.024605 | -0.0021299 | 0.44403 | 121.9162 | -0.050354 | 121.8155 | 0.14648 | 0.013733 | 0.045776 | 0.068665 | -0.032043 | -0.027466 | 0 | 0.11902 | 0.10529 | 0.091553 | 0.045776 | -0.050354 | -0.15106 | 0.24261 | 0.14191 | 0.10986 | 0.09613 | 0.064087 | 0.068664 | -121.9986 | -121.9666 | 0.21515 | 0.18768 | 0.20142 | 0.11902 | 0.13275 | 0.19684 | 121.8658 | 0.14649 | 0.027466 | 121.9666 | -0.004577 | 122.0123 | 0.064087 | -122.0169 | -121.994 | 121.9116 | 0.09613 | 0.54016 | 0.16479
2663.1094 | 122.0078 | -0.11902 | 122.0032 | -0.01976 | -0.00051702 | 0.051291 | 0.048956 | -0.0064643 | -0.010271 | -0.00345 | -0.0084228 | 0.029367 | 0.04883 | 0.0088611 | 0.015325 | 0.024178 | -0.0051205 | 0.38452 | 121.9803 | -0.091553 | 121.701 | 0.004578 | -0.10529 | -0.07782 | -0.050354 | 0.013733 | -0.054932 | -0.091553 | 0.032043 | 0.018311 | 0.018311 | 0.027466 | -0.022888 | -0.30212 | 0.1236 | 0.041199 | 0.013733 | 0.013733 | -0.013733 | 0.064087 | -121.9894 | -122.0947 | 0.15106 | 0.13733 | 0.13733 | 0.073243 | 0.073243 | 0.096131 | 121.7926 | 0.086975 | -0.036621 | 122.0718 | 0.068665 | 122.0993 | 0.13275 | -122.0947 | -122.0581 | 121.8201 | 0.027466 | 0.50354 | 0.068665
2664.8594 | 122.0718 | -0.10529 | 121.9803 | -0.0045011 | 0.002901 | 0.053854 | 0.053442 | 0.00058534 | -0.010057 | -0.0008866 | -0.0023192 | 0.031289 | 0.04883 | 0.011211 | 0.017889 | 0.024178 | -0.0061887 | 0.43945 | 121.962 | -0.09613 | 121.7331 | 0.009155 | -0.07782 | -0.07782 | -0.032043 | -0.009155 | -0.050354 | -0.032043 | 0.082397 | 0.041199 | 0.064087 | 0.009156 | -0.018311 | -0.24719 | 0.11444 | 0.027466 | 0.027466 | 0.01831 | 0.01831 | 0.054932 | -121.9894 | -122.0123 | 0.18768 | 0.16937 | 0.14649 | 0.11444 | 0.091553 | 0.10528 | 121.8292 | 0.13275 | 0.018311 | 122.0581 | 0.041199 | 122.0673 | 0.096131 | -122.0764 | -122.0306 | 121.8384 | 0.073243 | 0.54474 | 0.073243
2666.5625 | 122.1497 | -0.07782 | 121.9803 | -0.01976 | -0.00051702 | 0.054068 | 0.048315 | -0.00048286 | -0.0079212 | -0.0019546 | -0.005371 | 0.030008 | 0.046907 | 0.0035205 | 0.014684 | 0.02546 | -0.0038389 | 0.44403 | 121.9162 | -0.050354 | 121.8521 | 0.16937 | 0.045776 | 0.045776 | 0.11902 | -0.018311 | -0.004578 | 0.054932 | 0.16479 | 0.17395 | 0.13275 | 0.027466 | -0.064087 | -0.12817 | 0.24719 | 0.1236 | 0.1236 | 0.09613 | 0.09613 | 0.073242 | -121.9986 | -121.9254 | 0.24261 | 0.21057 | 0.25177 | 0.13733 | 0.17853 | 0.21973 | 121.9025 | 0.16937 | 0.05951 | 121.9666 | -0.013733 | 121.994 | 0.059509 | -122.0306 | -121.9849 | 121.9299 | 0.13275 | 0.52185 | 0.19684
2668.3281 | 122.1542 | -0.068665 | 121.9574 | -0.01976 | -0.00030342 | 0.052359 | 0.051092 | -0.0011237 | -0.011339 | -0.0040908 | -0.0084228 | 0.028726 | 0.048189 | 0.0056567 | 0.016821 | 0.026741 | 6.346e-06 | 0.43945 | 121.9025 | -0.050354 | 121.8613 | 0.1831 | 0.050354 | 0.045776 | 0.11444 | -0.036621 | -0.009155 | 0.045776 | 0.1831 | 0.16937 | 0.1236 | 0.018311 | -0.054931 | -0.09613 | 0.25177 | 0.11444 | 0.11902 | 0.09613 | 0.10071 | 0.05951 | -121.994 | -121.9116 | 0.25177 | 0.19226 | 0.23804 | 0.13275 | 0.17853 | 0.23346 | 121.9116 | 0.19226 | 0.054931 | 121.9528 | -0.027466 | 121.9711 | 0.032044 | -122.0078 | -121.9666 | 121.9299 | 0.11444 | 0.50812 | 0.18311
2670.0156 | 122.1268 | -0.059509 | 121.9711 | -0.01976 | 0.0065326 | 0.054282 | 0.053228 | 0.0027215 | -0.00963 | -0.0049454 | -0.0084228 | 0.031289 | 0.050112 | 0.0058703 | 0.015966 | 0.025673 | -0.0051205 | 0.37079 | 121.9757 | -0.064087 | 121.7514 | 0.027466 | -0.086975 | -0.054932 | 0.027466 | -0.004578 | -0.041199 | 0.032043 | 0.1236 | 0.11444 | 0.11902 | -0.004578 | 0.004578 | -0.21973 | 0.086975 | 0.004577 | -0.027466 | 0.009155 | -0.022888 | 0.01831 | -121.9757 | -121.9391 | 0.1831 | 0.17853 | 0.17395 | 0.16022 | 0.15564 | 0.091553 | 121.8155 | 0.16479 | 0.073242 | 122.0398 | 0.036621 | 122.0352 | 0.054931 | -122.0352 | -122.0123 | 121.8109 | 0.091552 | 0.4303 | 0.086975
2671.7656 | 121.994 | -0.11444 | 121.9803 | -0.0045011 | 0.006319 | 0.053427 | 0.055151 | 0.0031487 | -0.0081348 | -0.0047318 | -0.0084228 | 0.032998 | 0.049257 | 0.015911 | 0.019811 | 0.024178 | -0.0070433 | 0.42572 | 121.9711 | -0.082397 | 121.7148 | -0.013733 | -0.13275 | -0.11902 | -0.059509 | 0.022888 | -0.054932 | -0.082397 | 0.009155 | -0.013733 | 0.027466 | 0.032044 | -0.009156 | -0.2655 | 0.10071 | -0.004578 | -0.01831 | -0.036622 | -0.050354 | 0.059509 | -121.9574 | -122.0627 | 0.1236 | 0.14191 | 0.10071 | 0.082398 | 0.041199 | 0.068664 | 121.7972 | 0.064087 | -0.027465 | 122.0535 | 0.07782 | 122.0856 | 0.13733 | -122.0627 | -122.0352 | 121.8292 | 0.032044 | 0.54016 | 0.054932
2673.5312 | 122.0215 | -0.10986 | 121.9803 | 0.0031279 | 0.0031146 | 0.054495 | 0.051306 | -0.0043281 | -0.00963 | -0.0011002 | -0.011475 | 0.028085 | 0.050753 | 0.010356 | 0.015966 | 0.025673 | -0.0031979 | 0.42572 | 121.9437 | -0.068665 | 121.7377 | 0.032043 | -0.09613 | -0.068665 | -0.068665 | 0.009155 | -0.050354 | -0.082397 | 0.045776 | 0.022888 | 0.009155 | 0.041198 | -0.036621 | -0.24262 | 0.14191 | 0.041198 | 0.013733 | 0 | -0.027465 | 0.059509 | -121.9711 | -122.0627 | 0.15564 | 0.11902 | 0.13275 | 0.059509 | 0.073242 | 0.10071 | 121.8063 | 0.09613 | -0.032043 | 122.0123 | 0.059509 | 122.0535 | 0.11902 | -122.049 | -122.0306 | 121.8475 | 0.027466 | 0.53558 | 0.041198
2675.2969 | 122.0581 | -0.10986 | 121.962 | -0.0045011 | 0.0050372 | 0.054922 | 0.053656 | 0.0016535 | -0.0083484 | -0.0028092 | -0.0023192 | 0.030221 | 0.048189 | 0.0092883 | 0.017248 | 0.0261 | -0.0053343 | 0.45319 | 121.9666 | -0.082397 | 121.7285 | 0.032043 | -0.10529 | -0.082397 | -0.032043 | 0.009155 | -0.032043 | -0.07782 | 0.022888 | 0 | 0.032043 | 0.027466 | 0.004578 | -0.23346 | 0.14191 | 0.027466 | 0.004577 | 0 | -0.022889 | 0.07782 | -121.9528 | -122.0398 | 0.13275 | 0.14191 | 0.10986 | 0.064086 | 0.032043 | 0.11444 | 121.8109 | 0.054931 | -0.045777 | 122.049 | 0.041198 | 122.0764 | 0.11902 | -122.0444 | -121.994 | 121.8384 | 0.032043 | 0.56305 | 0.07782
2677.0625 | 122.1451 | -0.064087 | 121.962 | -0.0045011 | 0.0031146 | 0.055136 | 0.051733 | 0.0050713 | -0.0074938 | -0.0019546 | -0.0023192 | 0.02723 | 0.051393 | 0.013774 | 0.016607 | 0.027382 | -0.0064023 | 0.40283 | 121.9437 | -0.050354 | 121.8018 | 0.12817 | -0.027466 | 0.009155 | 0.091553 | -0.027466 | -0.018311 | 0.064087 | 0.15106 | 0.13275 | 0.15106 | 0.013733 | -0.01831 | -0.16022 | 0.19226 | 0.073242 | 0.036621 | 0.059509 | 0.022888 | 0.045776 | -121.9894 | -121.8979 | 0.21515 | 0.21515 | 0.19684 | 0.16937 | 0.15106 | 0.17853 | 121.8521 | 0.16937 | 0.082398 | 121.994 | -0.009155 | 122.0078 | 0.036621 | -122.0123 | -121.9803 | 121.8658 | 0.12817 | 0.46692 | 0.15564
2678.7812 | 122.0581 | -0.091553 | 121.9666 | -0.0045011 | 0.0061054 | 0.056418 | 0.05216 | 0.0014397 | -0.0089892 | -0.00345 | -0.005371 | 0.031503 | 0.049898 | 0.0067249 | 0.018102 | 0.025887 | -0.0040525 | 0.37537 | 122.0078 | -0.09613 | 121.7239 | -0.018311 | -0.12817 | -0.091553 | -0.032043 | 0 | -0.045776 | -0.045776 | 0.041199 | 0.013733 | 0.054932 | -0.004577 | 0.041198 | -0.24262 | 0.073242 | 0 | -0.036621 | 0.004577 | -0.032044 | 0.045777 | -121.9666 | -122.0123 | 0.13275 | 0.14649 | 0.10529 | 0.10071 | 0.059509 | 0.077819 | 121.8201 | 0.086975 | 0 | 122.1039 | 0.045776 | 122.0993 | 0.091553 | -122.0627 | -122.0123 | 121.8155 | 0.045777 | 0.46692 | 0.05951
2680.5469 | 122.1268 | -0.073242 | 121.9666 | -0.0045011 | 0.0065326 | 0.057059 | 0.051092 | 0.0012261 | -0.0083484 | -0.0004592 | -0.0084228 | 0.028512 | 0.050325 | 0.013988 | 0.015966 | 0.0261 | -0.0044797 | 0.41199 | 121.9391 | -0.036621 | 121.8475 | 0.14191 | -0.004578 | 0.032043 | 0.10529 | -0.050354 | -0.009155 | 0.054932 | 0.16022 | 0.1236 | 0.1236 | 0.036621 | -0.027466 | -0.11902 | 0.21515 | 0.10529 | 0.068664 | 0.068664 | 0.032043 | 0.064087 | -122.0169 | -121.9116 | 0.23346 | 0.19684 | 0.19684 | 0.13275 | 0.13275 | 0.17853 | 121.8842 | 0.16937 | 0.064087 | 121.9757 | -0.041199 | 122.0123 | 0.022888 | -122.0032 | -121.9757 | 121.9208 | 0.12817 | 0.48523 | 0.17853
2682.25 | 122.0673 | -0.11444 | 121.994 | -0.0045011 | 0.00033758 | 0.053427 | 0.053656 | 0.0029351 | -0.0087756 | -0.002382 | -0.0084228 | 0.031503 | 0.050112 | 0.012065 | 0.01853 | 0.0261 | -0.0029843 | 0.43488 | 121.9849 | -0.086975 | 121.7239 | 0.009155 | -0.091553 | -0.091553 | -0.041199 | 0 | -0.036621 | -0.054932 | 0.059509 | 0.032043 | 0.054932 | 0.027466 | -0.009156 | -0.27008 | 0.1236 | 0.022888 | 0.022888 | -0.004578 | -0.004578 | 0.07782 | -121.994 | -122.049 | 0.17395 | 0.16937 | 0.14648 | 0.091553 | 0.068664 | 0.09613 | 121.8109 | 0.09613 | -0.018311 | 122.0718 | 0.036621 | 122.0993 | 0.11444 | -122.081 | -122.0306 | 121.8384 | 0.059509 | 0.54932 | 0.073242
2684.0156 | 122.0169 | -0.11444 | 121.994 | -0.01976 | 0.00461 | 0.053214 | 0.051947 | -0.00026906 | -0.0089892 | -0.0030228 | 0.00073235 | 0.031076 | 0.050753 | 0.0082203 | 0.017889 | 0.024819 | -0.0023435 | 0.41657 | 122.0032 | -0.086975 | 121.6965 | -0.036621 | -0.15564 | -0.10986 | -0.07782 | -0.004578 | -0.059509 | -0.059509 | -0.004578 | -0.004578 | 0.032043 | 0.027466 | 0.009155 | -0.29755 | 0.07782 | 0.004578 | -0.041199 | -0.022888 | -0.068665 | 0.054932 | -121.9986 | -122.0535 | 0.10986 | 0.14648 | 0.10986 | 0.091552 | 0.054931 | 0.050354 | 121.7834 | 0.054931 | 0 | 122.0901 | 0.054931 | 122.1176 | 0.10986 | -122.081 | -122.0535 | 121.8109 | 0.054932 | 0.53101 | 0.036621
2685.7812 | 122.049 | -0.086975 | 121.9849 | -0.012131 | 0.0048236 | 0.053214 | 0.052801 | -0.00069646 | -0.0081348 | -0.0019546 | -0.0023192 | 0.031076 | 0.049044 | 0.013774 | 0.016607 | 0.026314 | -0.0023435 | 0.46692 | 121.994 | -0.073242 | 121.7697 | 0.068665 | -0.059509 | -0.050354 | 0.045776 | -0.009155 | -0.036621 | 0 | 0.091553 | 0.059509 | 0.073242 | 0.013733 | 0.009156 | -0.21515 | 0.15564 | 0.036621 | 0.027466 | 0.022888 | 0.013733 | 0.050354 | -121.994 | -121.9849 | 0.17853 | 0.16022 | 0.14648 | 0.10986 | 0.09613 | 0.14191 | 121.843 | 0.12817 | 0.036621 | 122.0673 | 0.027466 | 122.081 | 0.07782 | -122.0581 | -122.0215 | 121.8567 | 0.086975 | 0.55389 | 0.13275
2687.5469 | 121.9986 | -0.10529 | 121.994 | -0.02739 | 0.0054644 | 0.054068 | 0.053442 | 0.0025079 | -0.0081348 | -0.0047318 | -0.0023192 | 0.030648 | 0.05118 | -0.00011113 | 0.016393 | 0.026955 | 0.00043375 | 0.39825 | 122.0123 | -0.091553 | 121.6827 | -0.027466 | -0.16022 | -0.10986 | -0.059509 | 0.004578 | -0.050354 | -0.064087 | 0 | -0.009155 | 0.027466 | 0.013733 | 0.01831 | -0.31128 | 0.07782 | -0.004577 | -0.054931 | -0.01831 | -0.068664 | 0.054932 | -121.9894 | -122.0581 | 0.10529 | 0.13275 | 0.096131 | 0.07782 | 0.041199 | 0.064087 | 121.7743 | 0.050354 | -0.013733 | 122.1039 | 0.054932 | 122.1176 | 0.10986 | -122.0856 | -122.0444 | 121.788 | 0.041199 | 0.50354 | 0.045777
2689.3125 | 122.1313 | -0.059509 | 121.9574 | -0.012131 | 0.00461 | 0.055136 | 0.053015 | 0.0027215 | -0.0098438 | -0.005159 | -0.0084228 | 0.028299 | 0.049257 | 0.0058703 | 0.016821 | 0.026314 | -0.0083249 | 0.40283 | 121.9528 | -0.073242 | 121.7834 | 0.082397 | -0.045776 | 0 | 0.068665 | -0.045776 | -0.022888 | 0.041199 | 0.13275 | 0.12817 | 0.14191 | -0.013733 | -0.004577 | -0.17395 | 0.14191 | 0.059509 | 0.013733 | 0.073242 | 0.027466 | 0.036621 | -122.0032 | -121.9162 | 0.19226 | 0.20142 | 0.18768 | 0.16479 | 0.15106 | 0.15564 | 121.8567 | 0.15564 | 0.064087 | 122.0261 | -0.022888 | 122.0123 | 0.013733 | -122.0306 | -121.9803 | 121.843 | 0.10071 | 0.46234 | 0.12817
2691.0625 | 122.1222 | -0.07782 | 121.9666 | -0.012131 | 0.0016192 | 0.053854 | 0.048315 | 0.0048577 | -0.0092028 | -0.0049454 | -0.005371 | 0.02958 | 0.050966 | 0.012065 | 0.014684 | 0.025673 | -0.0031979 | 0.46692 | 121.9162 | -0.064087 | 121.8201 | 0.13733 | 0.036621 | 0.054932 | 0.09613 | -0.032043 | -0.013733 | 0.022888 | 0.15564 | 0.13733 | 0.11902 | 0.013733 | -0.050354 | -0.14648 | 0.21515 | 0.13275 | 0.11444 | 0.11902 | 0.10071 | 0.064087 | -121.9986 | -121.9437 | 0.23346 | 0.19684 | 0.21515 | 0.13275 | 0.15106 | 0.20142 | 121.8842 | 0.16937 | 0.036621 | 121.9803 | -0.01831 | 121.994 | 0.045777 | -122.0306 | -121.9803 | 121.8979 | 0.10071 | 0.54474 | 0.17395
2692.7656 | 122.1222 | -0.07782 | 121.9345 | -0.012131 | 0.00033758 | 0.053854 | 0.049383 | -0.0030463 | -0.0092028 | -0.002382 | -0.0084228 | 0.029153 | 0.049044 | 0.0024525 | 0.012334 | 0.023964 | -0.0017027 | 0.37994 | 121.9391 | -0.050354 | 121.7651 | 0.073242 | -0.041199 | -0.009155 | 0.032043 | -0.022888 | -0.018311 | 0.009155 | 0.1236 | 0.11444 | 0.10986 | 0.027466 | 0.004578 | -0.16937 | 0.15106 | 0.068665 | 0.036621 | 0.041199 | 0.009155 | 0.059509 | -121.9574 | -121.9254 | 0.20142 | 0.18768 | 0.19226 | 0.12817 | 0.13275 | 0.1236 | 121.8155 | 0.14191 | 0.027466 | 121.9894 | -0.004577 | 122.0169 | 0.054932 | -121.9849 | -121.9528 | 121.843 | 0.086975 | 0.45776 | 0.10986
2694.5312 | 122.0581 | -0.10986 | 122.0078 | -0.0045011 | 0.0026874 | 0.051077 | 0.051947 | 0.0027215 | -0.0094164 | -0.000673 | -0.0084228 | 0.030221 | 0.050325 | 0.01057 | 0.014898 | 0.024178 | -0.0025571 | 0.46692 | 121.9849 | -0.10071 | 121.7377 | 0.013733 | -0.086975 | -0.073242 | -0.036621 | 0.013733 | -0.050354 | -0.036621 | 0.064087 | 0.032043 | 0.068665 | 0.009155 | -0.022888 | -0.27008 | 0.1236 | 0.036621 | 0.022888 | 0.027466 | 0.013733 | 0.059509 | -121.994 | -122.0444 | 0.17395 | 0.17853 | 0.14191 | 0.11902 | 0.082397 | 0.11444 | 121.8384 | 0.11444 | 0.013733 | 122.0856 | 0.064087 | 122.0947 | 0.1236 | -122.1085 | -122.0581 | 121.8475 | 0.073242 | 0.57678 | 0.073242
2696.2969 | 122.1451 | -0.07782 | 121.9391 | -0.012131 | 0.0041828 | 0.055136 | 0.051733 | 0.0027215 | -0.0083484 | -0.0047318 | -0.005371 | 0.027444 | 0.050112 | 0.0030933 | 0.015539 | 0.023751 | 0.00021995 | 0.44861 | 121.9391 | -0.032043 | 121.8292 | 0.14191 | -0.013733 | 0.032043 | 0.10986 | -0.032043 | -0.004578 | 0.073242 | 0.15564 | 0.14191 | 0.14191 | 0.045777 | 0 | -0.10986 | 0.21973 | 0.10986 | 0.064087 | 0.064086 | 0.01831 | 0.073242 | -121.9711 | -121.8658 | 0.23346 | 0.21973 | 0.21973 | 0.14649 | 0.14649 | 0.17395 | 121.8613 | 0.16022 | 0.07782 | 121.9711 | -0.027465 | 122.0169 | 0.045777 | -121.9711 | -121.9437 | 121.907 | 0.15106 | 0.52643 | 0.18768
2698 | 122.0169 | -0.09613 | 122.0169 | -0.02739 | 0.0024738 | 0.055563 | 0.05152 | 0.0025079 | -0.0083484 | -0.0019546 | -0.005371 | 0.030435 | 0.049898 | 0.016124 | 0.016393 | 0.024819 | -0.0029843 | 0.48065 | 121.9711 | -0.07782 | 121.7468 | 0.036621 | -0.10986 | -0.082397 | -0.022888 | -0.004578 | -0.045776 | -0.050354 | 0.027466 | -0.004578 | 0.027466 | 0.01831 | -0.045777 | -0.27008 | 0.13275 | 0.013733 | -0.013733 | -0.004577 | -0.032043 | 0.050354 | -122.0215 | -122.0673 | 0.1236 | 0.1236 | 0.091552 | 0.073242 | 0.041198 | 0.11444 | 121.8246 | 0.073242 | -0.004578 | 122.049 | 0.041198 | 122.0673 | 0.091552 | -122.0947 | -122.0627 | 121.843 | 0.045776 | 0.57678 | 0.073242
2699.7656 | 122.1313 | -0.064087 | 121.9437 | -0.01976 | 0.0041828 | 0.053854 | 0.050238 | 0.0022943 | -0.0066394 | 0.0001816 | -0.0023192 | 0.02958 | 0.04883 | 0.0088611 | 0.014043 | 0.025246 | -0.00020725 | 0.42572 | 121.9391 | -0.041199 | 121.8338 | 0.15106 | 0.004578 | 0.036621 | 0.10529 | -0.041199 | -0.009155 | 0.045776 | 0.13733 | 0.11902 | 0.14648 | 0.022888 | -0.004578 | -0.10986 | 0.21515 | 0.10071 | 0.068665 | 0.07782 | 0.045777 | 0.054932 | -121.9849 | -121.8979 | 0.20142 | 0.21057 | 0.18311 | 0.15564 | 0.12817 | 0.19226 | 121.875 | 0.14648 | 0.054931 | 121.9803 | -0.032044 | 122.0032 | 0.022888 | -121.9849 | -121.9528 | 121.8979 | 0.10986 | 0.48981 | 0.16937
2701.5156 | 122.0352 | -0.10986 | 121.9849 | 0.0031279 | 0.001192 | 0.053854 | 0.049383 | 0.0025079 | -0.0098438 | -0.0025956 | -0.005371 | 0.030221 | 0.051821 | 0.0080067 | 0.017034 | 0.02546 | -0.0021299 | 0.4303 | 121.9986 | -0.09613 | 121.7056 | -0.009155 | -0.11902 | -0.086975 | -0.068665 | 0.009155 | -0.036621 | -0.07782 | 0.022888 | 0.018311 | 0.036621 | 0.013733 | 0.013733 | -0.27924 | 0.10071 | 0.022888 | -0.009156 | 0.009155 | -0.022889 | 0.073242 | -121.9757 | -122.0627 | 0.13275 | 0.14648 | 0.12817 | 0.073242 | 0.054932 | 0.086975 | 121.8018 | 0.059509 | -0.041199 | 122.0947 | 0.045776 | 122.1085 | 0.11902 | -122.081 | -122.0215 | 121.8155 | 0.032043 | 0.54016 | 0.041198
2703.2969 | 122.1039 | -0.07782 | 121.9711 | -0.012131 | 0.00033758 | 0.053641 | 0.049811 | -0.0036871 | -0.0077074 | -0.0036636 | -0.0023192 | 0.02958 | 0.049471 | 0.0035205 | 0.014471 | 0.025673 | -0.00063445 | 0.37079 | 121.9299 | -0.07782 | 121.7789 | 0.073242 | -0.036621 | -0.018311 | 0.013733 | -0.045776 | -0.032043 | -0.022888 | 0.086975 | 0.082397 | 0.073242 | 0 | -0.041198 | -0.19226 | 0.15106 | 0.059509 | 0.041199 | 0.059509 | 0.041199 | 0.045777 | -122.0169 | -121.994 | 0.16479 | 0.15106 | 0.16022 | 0.10529 | 0.11444 | 0.15106 | 121.8567 | 0.11902 | 0.009155 | 122.0078 | -0.013733 | 122.0078 | 0.032044 | -122.049 | -122.0032 | 121.8567 | 0.054932 | 0.44861 | 0.091553
2705.0625 | 122.1313 | -0.086975 | 121.9391 | -0.012131 | 0.00055118 | 0.053427 | 0.049597 | -0.0051825 | -0.011553 | -0.0011002 | -0.005371 | 0.029794 | 0.048616 | 0.0026661 | 0.016607 | 0.026741 | -0.0034117 | 0.45776 | 121.9208 | -0.064087 | 121.8384 | 0.15564 | 0.032043 | 0.050354 | 0.082397 | -0.018311 | -0.013733 | 0.041199 | 0.15564 | 0.13275 | 0.11444 | 0.022888 | -0.018311 | -0.10071 | 0.24261 | 0.13733 | 0.11902 | 0.11444 | 0.09613 | 0.073242 | -121.9574 | -121.8979 | 0.24261 | 0.20142 | 0.21973 | 0.12817 | 0.14648 | 0.21973 | 121.9025 | 0.16937 | 0.054932 | 121.9849 | -0.004578 | 122.0078 | 0.068664 | -122.0032 | -121.9528 | 121.9254 | 0.12817 | 0.54474 | 0.16937
2706.8281 | 122.0123 | -0.11902 | 121.9803 | -0.0045011 | 0.0050372 | 0.056631 | 0.053656 | -0.00026906 | -0.00963 | -0.0019546 | -0.005371 | 0.031717 | 0.050325 | 0.010997 | 0.01618 | 0.023751 | -0.0025571 | 0.4715 | 121.994 | -0.091553 | 121.7331 | 0.018311 | -0.13275 | -0.082397 | -0.032043 | -0.004578 | -0.041199 | -0.054932 | 0.027466 | -0.009155 | 0.027466 | 0.027466 | 0.013733 | -0.24719 | 0.13733 | 0.036622 | -0.013732 | 0.009156 | -0.041198 | 0.07782 | -121.9849 | -122.0352 | 0.14649 | 0.14649 | 0.10986 | 0.068665 | 0.032044 | 0.10986 | 121.8246 | 0.068665 | -0.013733 | 122.0856 | 0.036621 | 122.113 | 0.11444 | -122.0718 | -122.0215 | 121.8521 | 0.064087 | 0.59052 | 0.086976
2708.5469 | 122.1451 | -0.073242 | 121.9528 | -0.012131 | 0.0031146 | 0.056631 | 0.052801 | 0.00037174 | -0.006853 | -0.0028092 | -0.0084228 | 0.029367 | 0.049257 | 0.0030933 | 0.013403 | 0.025246 | -0.0049069 | 0.44403 | 121.9391 | -0.045776 | 121.8384 | 0.15106 | -0.018311 | 0.041199 | 0.10986 | -0.036621 | -0.018311 | 0.059509 | 0.16479 | 0.13275 | 0.13733 | 0.027466 | -0.013733 | -0.11444 | 0.2243 | 0.11444 | 0.054931 | 0.086975 | 0.027465 | 0.054931 | -121.9894 | -121.8933 | 0.23804 | 0.21057 | 0.20599 | 0.15564 | 0.15106 | 0.19684 | 121.8842 | 0.18311 | 0.07782 | 121.9849 | -0.01831 | 122.0123 | 0.036621 | -121.9986 | -121.9711 | 121.9116 | 0.13275 | 0.51727 | 0.18311
2710.3125 | 122.1085 | -0.068665 | 121.9711 | -0.012131 | 0.0039692 | 0.055777 | 0.050238 | 0.0010125 | -0.0083484 | -0.0015274 | 0.00073235 | 0.02958 | 0.050112 | 0.011638 | 0.014471 | 0.024178 | -0.0025571 | 0.41657 | 121.9208 | -0.041199 | 121.8109 | 0.12817 | -0.027466 | 0.032043 | 0.11444 | -0.032043 | -0.009155 | 0.027466 | 0.11902 | 0.10986 | 0.10986 | 0.027466 | -0.050354 | -0.16022 | 0.19684 | 0.10071 | 0.041199 | 0.073242 | 0.013733 | 0.05951 | -122.0032 | -121.9437 | 0.18768 | 0.17853 | 0.17853 | 0.11902 | 0.11902 | 0.16937 | 121.8521 | 0.12817 | 0.036621 | 121.962 | -0.022888 | 121.9894 | 0.036622 | -122.0123 | -121.9803 | 121.8796 | 0.096131 | 0.48523 | 0.18311
2712.0781 | 122.0215 | -0.13275 | 121.9849 | -0.012131 | 0.001192 | 0.052786 | 0.049811 | 0.00037174 | -0.0094164 | -0.0019546 | -0.0023192 | 0.029794 | 0.052889 | 0.0077929 | 0.014471 | 0.023751 | 0.00021995 | 0.45319 | 121.9528 | -0.073242 | 121.7194 | 0.009155 | -0.10071 | -0.073242 | -0.045776 | 0 | -0.045776 | -0.091553 | 0.022888 | 0.018311 | 0.018311 | 0.059509 | -0.032043 | -0.2655 | 0.14191 | 0.059509 | 0.032043 | 0 | -0.027466 | 0.086975 | -121.9849 | -122.0764 | 0.15564 | 0.15106 | 0.15106 | 0.064087 | 0.064087 | 0.082397 | 121.7926 | 0.068664 | -0.045777 | 122.0261 | 0.045776 | 122.0856 | 0.13275 | -122.0581 | -122.0306 | 121.8521 | 0.041198 | 0.58594 | 0.086975
2713.8438 | 121.994 | -0.11902 | 122.0169 | -0.0045011 | 0.0043964 | 0.053854 | 0.052374 | 0.00079894 | -0.00963 | -0.0028092 | -0.005371 | 0.031503 | 0.052462 | 0.0045887 | 0.014898 | 0.026955 | -0.0034117 | 0.4303 | 121.962 | -0.091553 | 121.6873 | -0.032043 | -0.15564 | -0.1236 | -0.064087 | 0 | -0.050354 | -0.059509 | 0.013733 | -0.018311 | 0.022888 | 0.027466 | -0.054932 | -0.32959 | 0.086976 | -0.004577 | -0.036621 | -0.032043 | -0.064087 | 0.068665 | -122.0169 | -122.0764 | 0.13275 | 0.14191 | 0.10071 | 0.073242 | 0.032043 | 0.05951 | 121.7789 | 0.064087 | -0.009155 | 122.0535 | 0.050354 | 122.081 | 0.11902 | -122.1085 | -122.0673 | 121.8063 | 0.05951 | 0.54932 | 0.054932
2715.5469 | 122.1359 | -0.068665 | 121.9345 | -0.0045011 | 0.0031146 | 0.05535 | 0.050451 | -0.0024055 | -0.0098438 | -0.000673 | -0.005371 | 0.028299 | 0.049257 | 0.0058703 | 0.01618 | 0.02546 | -0.0057615 | 0.44403 | 121.9345 | -0.059509 | 121.8201 | 0.16479 | -0.013733 | 0.041199 | 0.10071 | -0.045776 | -0.018311 | 0.054932 | 0.16022 | 0.1236 | 0.11902 | 0.009156 | 0 | -0.11444 | 0.23346 | 0.10986 | 0.054932 | 0.10071 | 0.045776 | 0.050354 | -121.9803 | -121.8796 | 0.22888 | 0.18768 | 0.19226 | 0.13733 | 0.14191 | 0.2243 | 121.8796 | 0.17853 | 0.073243 | 121.994 | -0.027465 | 122.0032 | 0.022889 | -121.994 | -121.9528 | 121.8887 | 0.1236 | 0.5127 | 0.16937
2717.25 | 122.1176 | -0.068665 | 121.9574 | -0.012131 | 0.002901 | 0.053214 | 0.049383 | 0.0010125 | -0.0087756 | -0.0025956 | -0.005371 | 0.028726 | 0.048403 | 0.010356 | 0.014471 | 0.025246 | -0.0057615 | 0.50354 | 121.9208 | -0.059509 | 121.8338 | 0.14191 | 0.018311 | 0.045776 | 0.086975 | -0.032043 | -0.009155 | 0.050354 | 0.15564 | 0.13275 | 0.11444 | 0.009156 | -0.036621 | -0.1236 | 0.21057 | 0.11444 | 0.086976 | 0.10528 | 0.07782 | 0.05951 | -121.9894 | -121.907 | 0.22431 | 0.18311 | 0.20142 | 0.1236 | 0.14191 | 0.20142 | 121.8933 | 0.16479 | 0.059509 | 121.9803 | -0.022888 | 121.9894 | 0.036622 | -122.0169 | -121.9666 | 121.9025 | 0.11902 | 0.5722 | 0.15564
2718.9688 | 122.0398 | -0.11444 | 121.9666 | -0.0045011 | -0.0011578 | 0.053 | 0.04917 | -0.00091006 | -0.011125 | -0.0030228 | -0.011475 | 0.02958 | 0.051821 | 0.0018115 | 0.012762 | 0.025673 | -0.0040525 | 0.49439 | 121.9299 | -0.082397 | 121.788 | 0.09613 | -0.022888 | -0.004578 | -0.004578 | 0 | -0.041199 | -0.041199 | 0.068665 | 0.054932 | 0.050354 | 0.032044 | -0.036621 | -0.17853 | 0.21057 | 0.10986 | 0.091553 | 0.077819 | 0.059509 | 0.073242 | -121.9666 | -122.0078 | 0.18311 | 0.16479 | 0.16937 | 0.091553 | 0.096131 | 0.17853 | 121.8704 | 0.10986 | 0 | 122.0123 | 0.041199 | 122.0444 | 0.11444 | -122.049 | -122.0078 | 121.9025 | 0.073242 | 0.60883 | 0.10986
2720.6719 | 122.0444 | -0.10529 | 121.9574 | -0.01976 | 0.0043964 | 0.05535 | 0.052801 | 0.00015814 | -0.0077074 | -0.001741 | -0.005371 | 0.033212 | 0.052889 | 0.0033069 | 0.017889 | 0.022896 | -0.0010617 | 0.40741 | 122.0032 | -0.064087 | 121.701 | -0.004578 | -0.12817 | -0.10071 | -0.032043 | -0.004578 | -0.041199 | -0.054932 | 0.041199 | 0.013733 | 0.045776 | 0.041199 | 0.045777 | -0.25635 | 0.10071 | 0.004578 | -0.022888 | -0.036621 | -0.064087 | 0.064087 | -121.962 | -122.0123 | 0.14649 | 0.15106 | 0.11902 | 0.086975 | 0.054932 | 0.059509 | 121.7651 | 0.082398 | -0.013733 | 122.0673 | 0.036621 | 122.1085 | 0.10071 | -122.0215 | -121.9986 | 121.8063 | 0.050354 | 0.5127 | 0.073243
2722.375 | 122.1451 | -0.068665 | 121.9528 | -0.0045011 | 0.0039692 | 0.057059 | 0.054297 | 0.0012261 | -0.0059986 | -0.001741 | -0.0023192 | 0.028512 | 0.050753 | 0.011211 | 0.015325 | 0.026528 | -0.0046933 | 0.46234 | 121.9299 | -0.045776 | 121.8155 | 0.12817 | -0.022888 | 0.013733 | 0.091553 | -0.032043 | -0.009155 | 0.073242 | 0.16022 | 0.11902 | 0.14191 | 0.022889 | -0.022888 | -0.13733 | 0.19684 | 0.082398 | 0.045777 | 0.059509 | 0.022888 | 0.05951 | -121.9849 | -121.8796 | 0.22888 | 0.21057 | 0.18768 | 0.15106 | 0.12817 | 0.17395 | 121.8613 | 0.16937 | 0.082397 | 121.9757 | -0.022888 | 121.9986 | 0.036622 | -121.9986 | -121.962 | 121.8842 | 0.14191 | 0.53101 | 0.16022
2724.0938 | 122.0169 | -0.12817 | 121.9894 | -0.012131 | 0.0043964 | 0.054495 | 0.053228 | 0.0022943 | -0.010271 | -0.0043046 | -0.005371 | 0.032571 | 0.052034 | 0.0062977 | 0.017248 | 0.024178 | -0.0019163 | 0.42572 | 122.0032 | -0.10071 | 121.701 | -0.027466 | -0.16022 | -0.10986 | -0.050354 | 0.009155 | -0.050354 | -0.050354 | 0.013733 | -0.009155 | 0.032043 | 0.027466 | 0.013733 | -0.28839 | 0.10071 | 0.018311 | -0.032043 | -0.009155 | -0.059509 | 0.07782 | -121.9803 | -122.0398 | 0.14191 | 0.16022 | 0.11902 | 0.082397 | 0.041199 | 0.073242 | 121.8018 | 0.064087 | 0 | 122.1039 | 0.059509 | 122.1313 | 0.13733 | -122.0901 | -122.0398 | 121.8292 | 0.07782 | 0.55389 | 0.07782
2725.8594 | 122.0215 | -0.10529 | 121.994 | -0.0045011 | 0.001833 | 0.053641 | 0.050238 | -0.0045417 | -0.0081348 | -0.0030228 | -0.005371 | 0.027871 | 0.05353 | 0.0041615 | 0.015325 | 0.02546 | -0.0027707 | 0.44403 | 121.9574 | -0.091553 | 121.701 | 0.004578 | -0.09613 | -0.068665 | -0.050354 | 0.004578 | -0.050354 | -0.086975 | 0.036621 | 0.027466 | 0 | 0.013733 | -0.036622 | -0.29297 | 0.10986 | 0.036621 | 0.009156 | 0.022888 | -0.004577 | 0.054932 | -121.9894 | -122.081 | 0.14191 | 0.10529 | 0.13275 | 0.050354 | 0.07782 | 0.096131 | 121.7926 | 0.086975 | -0.036621 | 122.049 | 0.054932 | 122.0627 | 0.10986 | -122.0856 | -122.0444 | 121.8063 | 0.018311 | 0.54932 | 0.054932
2727.5469 | 122.1588 | -0.068665 | 121.9391 | -0.012131 | 0.0048236 | 0.054495 | 0.051092 | -5.5462e-05 | -0.0083484 | -0.0019546 | -0.0023192 | 0.028939 | 0.050753 | 0.0033069 | 0.016821 | 0.025673 | -0.0053343 | 0.47607 | 121.9528 | -0.064087 | 121.8201 | 0.14191 | -0.013733 | 0.032043 | 0.09613 | -0.036621 | -0.009155 | 0.073242 | 0.17395 | 0.13733 | 0.15564 | 0.004578 | 0.013733 | -0.11902 | 0.21057 | 0.10071 | 0.054932 | 0.09613 | 0.050354 | 0.05951 | -121.9757 | -121.8658 | 0.24261 | 0.22431 | 0.20599 | 0.16479 | 0.14648 | 0.20599 | 121.8842 | 0.1831 | 0.082397 | 122.0169 | -0.027466 | 122.0215 | 0.032044 | -122.0032 | -121.9482 | 121.8887 | 0.14191 | 0.54474 | 0.16479
2729.3125 | 122.168 | -0.068665 | 121.9116 | -0.0045011 | -0.00030342 | 0.051932 | 0.049811 | -0.0028327 | -0.0064258 | -0.0025956 | -0.005371 | 0.02958 | 0.051393 | 0.0026661 | 0.015325 | 0.026314 | -0.0042661 | 0.45776 | 121.9299 | -0.082397 | 121.8338 | 0.16022 | 0.036621 | 0.064087 | 0.12817 | -0.036621 | -0.018311 | 0.064087 | 0.19226 | 0.17395 | 0.13275 | -0.013732 | 0.018311 | -0.07782 | 0.22888 | 0.13275 | 0.10529 | 0.14648 | 0.11902 | 0.050354 | -121.9482 | -121.8475 | 0.26093 | 0.20142 | 0.24261 | 0.15106 | 0.19226 | 0.24261 | 121.9162 | 0.21057 | 0.082398 | 122.0123 | -0.01831 | 121.9986 | 0.032044 | -121.994 | -121.9299 | 121.9025 | 0.13275 | 0.52643 | 0.19684
2731.0781 | 122.0306 | -0.11444 | 121.9803 | -0.0045011 | -0.0011578 | 0.053214 | 0.051947 | 0.0014397 | -0.010271 | -0.0013138 | -0.0084228 | 0.03193 | 0.050112 | 0.0077929 | 0.016821 | 0.023323 | -0.0027707 | 0.4715 | 121.9666 | -0.09613 | 121.701 | -0.013733 | -0.11902 | -0.091553 | -0.068665 | 0.004578 | -0.036621 | -0.064087 | 0.045776 | 0.018311 | 0.041199 | 0.018311 | -0.013733 | -0.27924 | 0.10071 | 0.022888 | -0.004578 | 0.004577 | -0.022889 | 0.07782 | -121.9757 | -122.0444 | 0.16022 | 0.15564 | 0.13275 | 0.07782 | 0.054932 | 0.082397 | 121.7972 | 0.082397 | -0.027466 | 122.0627 | 0.041199 | 122.081 | 0.11902 | -122.0764 | -122.0169 | 121.8155 | 0.050354 | 0.58594 | 0.045776
2732.8438 | 122.081 | -0.09613 | 121.9849 | 0.0031279 | 0.0035418 | 0.054068 | 0.055792 | 0.0022943 | -0.0049304 | -0.001741 | -0.0023192 | 0.02958 | 0.051607 | 0.012706 | 0.016607 | 0.02311 | -0.0046933 | 0.41657 | 122.0032 | -0.086975 | 121.7194 | 0.013733 | -0.11902 | -0.10071 | -0.013733 | -0.009155 | -0.045776 | -0.004578 | 0.064087 | 0.054932 | 0.073242 | 0.009155 | 0.018311 | -0.2655 | 0.10986 | -0.004578 | -0.022889 | -0.013733 | -0.032044 | 0.050354 | -121.994 | -121.9894 | 0.16022 | 0.16937 | 0.15106 | 0.11902 | 0.10071 | 0.10071 | 121.8063 | 0.10986 | 0.041198 | 122.0901 | 0.036621 | 122.0993 | 0.086975 | -122.0718 | -122.0306 | 121.8155 | 0.091552 | 0.5127 | 0.082397
2734.5625 | 122.0718 | -0.091553 | 121.9482 | -0.01976 | 0.002901 | 0.056204 | 0.051092 | 0.0016535 | -0.0072802 | -0.0021682 | -0.005371 | 0.030008 | 0.050966 | 0.0071521 | 0.017461 | 0.024605 | -0.0012753 | 0.41657 | 122.0123 | -0.091553 | 121.7148 | 0.004578 | -0.12817 | -0.09613 | -0.027466 | 0 | -0.050354 | -0.013733 | 0.059509 | 0.045776 | 0.073242 | 0 | 0.064087 | -0.23346 | 0.096131 | -0.004577 | -0.036621 | -0.004577 | -0.036621 | 0.041199 | -121.9482 | -121.962 | 0.15106 | 0.16479 | 0.13733 | 0.1236 | 0.09613 | 0.096131 | 121.8063 | 0.10986 | 0.036621 | 122.1039 | 0.050354 | 122.1039 | 0.091553 | -122.0398 | -121.9986 | 121.8063 | 0.07782 | 0.50812 | 0.064087
2736.3281 | 122.1085 | -0.07782 | 121.962 | -0.012131 | 0.001833 | 0.05535 | 0.049811 | 0.0035761 | -0.0089892 | -0.0032364 | -0.0084228 | 0.029794 | 0.051607 | 0.0041615 | 0.015325 | 0.025032 | -0.0031979 | 0.45319 | 121.907 | -0.054932 | 121.8246 | 0.14191 | -0.013733 | 0.027466 | 0.10071 | -0.022888 | -0.027466 | 0.041199 | 0.13733 | 0.11444 | 0.11444 | 0.022888 | -0.054932 | -0.13733 | 0.21973 | 0.10529 | 0.064087 | 0.082398 | 0.041199 | 0.050354 | -121.9849 | -121.9208 | 0.21515 | 0.19226 | 0.19226 | 0.14191 | 0.14191 | 0.19684 | 121.8796 | 0.16479 | 0.068665 | 121.962 | 0.004578 | 121.9849 | 0.054932 | -122.0169 | -121.9894 | 121.9025 | 0.11902 | 0.53101 | 0.17853
2738.0938 | 122.1497 | -0.07782 | 121.9391 | -0.0045011 | 0.0014056 | 0.052359 | 0.050024 | -0.0045417 | -0.011125 | -0.0066544 | -0.0023192 | 0.028726 | 0.053102 | 0.0039477 | 0.015966 | 0.025246 | -0.0057615 | 0.5127 | 121.9391 | -0.045776 | 121.8658 | 0.16479 | 0.045776 | 0.054932 | 0.14191 | -0.022888 | -0.022888 | 0.045776 | 0.18768 | 0.15564 | 0.12817 | 0.032044 | 0 | -0.073242 | 0.24261 | 0.13275 | 0.1236 | 0.10071 | 0.091552 | 0.054932 | -121.962 | -121.8933 | 0.2655 | 0.20599 | 0.23346 | 0.15106 | 0.17853 | 0.21057 | 121.9116 | 0.21057 | 0.068664 | 121.9849 | 0 | 122.0169 | 0.054932 | -121.9849 | -121.962 | 121.9437 | 0.1236 | 0.59052 | 0.21973
2739.8594 | 122.0215 | -0.11902 | 121.994 | -0.012131 | 0.0065326 | 0.054282 | 0.053442 | -0.00026906 | -0.0072802 | -0.0040908 | 0.00073235 | 0.03193 | 0.053743 | 0.0090747 | 0.015752 | 0.025246 | -0.0027707 | 0.44403 | 121.9849 | -0.091553 | 121.7148 | -0.032043 | -0.14648 | -0.10529 | -0.045776 | 0.004578 | -0.041199 | -0.041199 | 0.004578 | -0.009155 | 0.041199 | 0.027466 | -0.009156 | -0.27924 | 0.086976 | 0.013733 | -0.027465 | -0.013733 | -0.054931 | 0.07782 | -121.9894 | -122.0352 | 0.1236 | 0.16022 | 0.10986 | 0.082398 | 0.032044 | 0.05951 | 121.8063 | 0.045777 | 0 | 122.0764 | 0.045777 | 122.1039 | 0.1236 | -122.0856 | -122.0352 | 121.8338 | 0.07782 | 0.56305 | 0.073243
2741.5625 | 122.081 | -0.10071 | 121.9711 | -0.0045011 | -0.0013714 | 0.054068 | 0.049597 | -0.00048286 | -0.0081348 | -0.0025956 | -0.0023192 | 0.028726 | 0.053957 | 0.0056567 | 0.014684 | 0.025032 | -0.0029843 | 0.51727 | 121.9254 | -0.054932 | 121.8109 | 0.11444 | 0.013733 | 0.018311 | 0.064087 | -0.018311 | -0.032043 | -0.013733 | 0.10071 | 0.086975 | 0.068665 | 0.045776 | -0.045776 | -0.16022 | 0.21515 | 0.11902 | 0.11444 | 0.073243 | 0.068665 | 0.068665 | -121.9894 | -121.9849 | 0.20142 | 0.16937 | 0.18768 | 0.10071 | 0.11902 | 0.16937 | 121.8658 | 0.13275 | 0.01831 | 121.9803 | 0.013732 | 122.0261 | 0.082397 | -122.0261 | -122.0032 | 121.9116 | 0.086975 | 0.61798 | 0.1648
2743.3125 | 122.1085 | -0.086975 | 122.0032 | -0.012131 | 0.00076478 | 0.053427 | 0.050879 | -0.0013373 | -0.0098438 | -0.005159 | -0.011475 | 0.029367 | 0.051821 | 0.00010247 | 0.015539 | 0.023964 | -0.0038389 | 0.41657 | 121.9208 | -0.054932 | 121.7651 | 0.064087 | -0.050354 | -0.032043 | 0.022888 | -0.032043 | -0.032043 | -0.013733 | 0.09613 | 0.082397 | 0.086975 | 0.032043 | -0.082398 | -0.23804 | 0.15106 | 0.054932 | 0.036621 | 0.022889 | 0.004578 | 0.054932 | -122.0352 | -122.0169 | 0.1831 | 0.17395 | 0.16937 | 0.11902 | 0.11444 | 0.11902 | 121.8201 | 0.12817 | 0.01831 | 121.9757 | 0 | 122.0078 | 0.054932 | -122.0581 | -122.0352 | 121.8521 | 0.073242 | 0.50354 | 0.10986
2745.0938 | 122.0673 | -0.11444 | 121.9757 | -0.0045011 | 0.0039692 | 0.052145 | 0.053869 | 0.00079894 | -0.0079212 | -0.0019546 | -0.005371 | 0.032144 | 0.052889 | 0.013774 | 0.017248 | 0.023964 | -0.0064023 | 0.54016 | 121.962 | -0.086975 | 121.7789 | 0.059509 | -0.064087 | -0.041199 | 0.032043 | -0.004578 | -0.027466 | -0.013733 | 0.068665 | 0.041199 | 0.041199 | 0.027466 | -0.013733 | -0.19684 | 0.17395 | 0.073242 | 0.050354 | 0.045776 | 0.022888 | 0.086975 | -121.9803 | -121.9894 | 0.18311 | 0.15564 | 0.15564 | 0.068665 | 0.068665 | 0.14648 | 121.8658 | 0.096131 | 0.013733 | 122.0489 | 0.022888 | 122.0764 | 0.10986 | -122.0627 | -122.0032 | 121.8933 | 0.10071 | 0.6546 | 0.14648
2746.8594 | 122.0306 | -0.1236 | 121.9711 | -0.012131 | 0.0058918 | 0.057059 | 0.05451 | 0.0012261 | -0.0098438 | -0.001741 | -0.005371 | 0.032357 | 0.054171 | 0.012706 | 0.017675 | 0.02546 | -0.0031979 | 0.50354 | 121.994 | -0.086975 | 121.7285 | 0.009155 | -0.12817 | -0.091553 | -0.018311 | 0 | -0.041199 | -0.073242 | 0.013733 | -0.009155 | 0.022888 | 0.036621 | 0.022889 | -0.24261 | 0.13275 | 0.032043 | -0.004578 | -0.004578 | -0.041199 | 0.082397 | -121.9711 | -122.0444 | 0.13733 | 0.14648 | 0.11444 | 0.064087 | 0.032044 | 0.09613 | 121.8155 | 0.054932 | -0.032043 | 122.081 | 0.041199 | 122.1176 | 0.1236 | -122.0581 | -122.0123 | 121.8521 | 0.050354 | 0.62714 | 0.10528
2748.5781 | 122.1451 | -0.086975 | 121.9757 | -0.012131 | 0.00461 | 0.054922 | 0.05216 | 0.0042169 | -0.0081348 | -0.0011002 | -0.0084228 | 0.029153 | 0.053102 | 0.0024525 | 0.014684 | 0.025246 | -0.0051205 | 0.46234 | 121.9666 | -0.082397 | 121.7606 | 0.059509 | -0.073242 | -0.041199 | 0.059509 | -0.022888 | -0.050354 | 0.045776 | 0.14191 | 0.11444 | 0.12817 | 0.004578 | -0.009155 | -0.21515 | 0.14648 | 0.045776 | 0.013733 | 0.041198 | 0.009155 | 0.036621 | -121.9986 | -121.9299 | 0.22888 | 0.21515 | 0.20142 | 0.17853 | 0.16479 | 0.14191 | 121.843 | 0.19226 | 0.09613 | 122.049 | 0.027466 | 122.0535 | 0.064087 | -122.0581 | -122.0261 | 121.8475 | 0.13275 | 0.54932 | 0.14648
2750.3438 | 122.1497 | -0.073242 | 121.9391 | -0.0045011 | 0.0016192 | 0.054709 | 0.047247 | 0.00037174 | -0.010057 | -0.0013138 | -0.005371 | 0.028085 | 0.05118 | 0.011638 | 0.014684 | 0.024819 | -0.0070433 | 0.47607 | 121.9116 | -0.059509 | 121.8109 | 0.14648 | 0.022888 | 0.050354 | 0.1236 | -0.041199 | -0.032043 | 0.068665 | 0.20142 | 0.16937 | 0.13733 | 0.013733 | -0.027466 | -0.12817 | 0.21973 | 0.1236 | 0.09613 | 0.10986 | 0.082397 | 0.041199 | -121.9803 | -121.8704 | 0.27466 | 0.21057 | 0.24261 | 0.16937 | 0.20142 | 0.20599 | 121.8704 | 0.23346 | 0.10071 | 121.9711 | -0.009156 | 121.9849 | 0.032043 | -121.9986 | -121.9711 | 121.8842 | 0.14191 | 0.54932 | 0.19684
2752.0938 | 122.049 | -0.11444 | 121.9574 | -0.012131 | 0.00076478 | 0.053427 | 0.053015 | 0.0052851 | -0.00963 | -0.000673 | -0.005371 | 0.032144 | 0.05353 | 0.0092883 | 0.01853 | 0.0261 | -0.0017027 | 0.52643 | 121.9666 | -0.086975 | 121.7651 | 0.041199 | -0.07782 | -0.054932 | -0.004578 | 0.018311 | -0.050354 | -0.004578 | 0.091553 | 0.050354 | 0.07782 | 0.027466 | 0.009156 | -0.19226 | 0.15564 | 0.059509 | 0.036621 | 0.032043 | 0.009155 | 0.064087 | -121.9391 | -121.962 | 0.20599 | 0.19226 | 0.16479 | 0.12817 | 0.10071 | 0.12817 | 121.8521 | 0.14191 | 0.045776 | 122.0535 | 0.068665 | 122.081 | 0.13275 | -122.0444 | -122.0078 | 121.8796 | 0.10986 | 0.64087 | 0.10986
2753.8594 | 122.0215 | -0.13733 | 121.9894 | -0.012131 | 0.00012398 | 0.053214 | 0.050665 | -0.0024055 | -0.0092028 | -0.00345 | -0.005371 | 0.031076 | 0.052248 | 0.0097157 | 0.016393 | 0.024819 | -0.0036253 | 0.48523 | 121.9803 | -0.09613 | 121.7102 | 0.022888 | -0.10071 | -0.082397 | -0.045776 | 0.004578 | -0.054932 | -0.082397 | 0.036621 | 0.022888 | 0.018311 | 0.041199 | -0.009155 | -0.27924 | 0.16022 | 0.054932 | 0.036621 | 0.013733 | -0.004578 | 0.082397 | -121.9849 | -122.0718 | 0.17395 | 0.15564 | 0.16022 | 0.073243 | 0.07782 | 0.11902 | 121.8063 | 0.091553 | -0.027465 | 122.0764 | 0.05951 | 122.1176 | 0.14191 | -122.0856 | -122.0444 | 121.8475 | 0.054932 | 0.62256 | 0.091553
2755.5625 | 122.1313 | -0.064087 | 121.9666 | -0.012131 | 0.0065326 | 0.056204 | 0.052374 | 0.0016535 | -0.0077074 | -0.0040908 | -0.011475 | 0.031503 | 0.053316 | 0.01292 | 0.018743 | 0.026955 | -0.0025571 | 0.44861 | 121.962 | -0.082397 | 121.7651 | 0.050354 | -0.07782 | -0.041199 | 0.050354 | -0.018311 | -0.018311 | 0.054932 | 0.13733 | 0.10529 | 0.12817 | -0.01831 | -0.004578 | -0.20142 | 0.11444 | 0.022888 | -0.013733 | 0.041198 | 0.004577 | 0.045776 | -121.9849 | -121.9116 | 0.20142 | 0.19226 | 0.16937 | 0.14649 | 0.1236 | 0.13275 | 121.8475 | 0.15564 | 0.073243 | 122.0444 | 0 | 122.0261 | 0.045776 | -122.049 | -121.9849 | 121.8292 | 0.11902 | 0.5127 | 0.11444
2757.3281 | 122.0261 | -0.11444 | 121.9711 | -0.01976 | 0.0035418 | 0.054922 | 0.050451 | 0.0037897 | -0.0077074 | -0.0021682 | -0.0084228 | 0.031076 | 0.052248 | 0.01057 | 0.016607 | 0.025887 | -0.0059751 | 0.45319 | 121.994 | -0.10986 | 121.7056 | -0.013733 | -0.14648 | -0.10986 | -0.050354 | -0.013733 | -0.059509 | -0.059509 | 0.018311 | -0.009155 | 0.050354 | 0.004578 | 0.022889 | -0.2655 | 0.10071 | 0.004578 | -0.032043 | 0 | -0.036621 | 0.054932 | -121.9849 | -122.0306 | 0.13275 | 0.16479 | 0.10529 | 0.10986 | 0.050354 | 0.09613 | 121.8155 | 0.07782 | 0 | 122.1039 | 0.045776 | 122.1085 | 0.10071 | -122.081 | -122.0306 | 121.8201 | 0.054932 | 0.56763 | 0.064087
2759.0312 | 122.0215 | -0.10529 | 121.994 | -0.012131 | 0.0020466 | 0.055563 | 0.05152 | 0.0027215 | -0.0092028 | -0.00345 | -0.0023192 | 0.031503 | 0.054171 | 0.0056567 | 0.017461 | 0.025246 | -0.0061887 | 0.46234 | 121.9849 | -0.10986 | 121.6965 | -0.032043 | -0.16022 | -0.1236 | -0.045776 | 0.004578 | -0.045776 | -0.064087 | 0.009155 | -0.013733 | 0.032043 | -0.004577 | -0.009156 | -0.29755 | 0.073243 | -0.01831 | -0.054931 | -0.013733 | -0.050354 | 0.05951 | -121.9894 | -122.0581 | 0.11444 | 0.13733 | 0.091553 | 0.077819 | 0.032043 | 0.07782 | 121.8063 | 0.054931 | -0.018311 | 122.0947 | 0.050354 | 122.0901 | 0.10986 | -122.1039 | -122.0398 | 121.8018 | 0.041199 | 0.56763 | 0.05951
2760.7969 | 122.0352 | -0.11902 | 121.9711 | -0.012131 | 0.00097838 | 0.053854 | 0.051947 | -0.00069646 | -0.0079212 | -0.0013138 | 0.00073235 | 0.030008 | 0.055239 | 0.0048023 | 0.017675 | 0.024605 | -0.0019163 | 0.48065 | 121.9757 | -0.10986 | 121.6919 | -0.004578 | -0.10986 | -0.091553 | -0.064087 | 0.027466 | -0.050354 | -0.068665 | 0.027466 | 0.018311 | 0.045776 | 0.009156 | 0.004578 | -0.27923 | 0.11444 | 0.027466 | 0.009156 | 0.01831 | 0 | 0.068665 | -121.9437 | -122.0398 | 0.14649 | 0.16479 | 0.13733 | 0.09613 | 0.068665 | 0.10529 | 121.8018 | 0.07782 | -0.018311 | 122.0856 | 0.07782 | 122.0947 | 0.14649 | -122.081 | -122.0215 | 121.8109 | 0.050354 | 0.59967 | 0.054932
2762.5625 | 122.0627 | -0.10071 | 121.9986 | -0.012131 | 0.0022602 | 0.053641 | 0.050238 | 0.0016535 | -0.0094164 | -0.0021682 | -0.005371 | 0.030435 | 0.052248 | 0.013347 | 0.016393 | 0.025673 | -0.00063445 | 0.55389 | 121.9757 | -0.10529 | 121.756 | 0.073242 | -0.082397 | -0.054932 | 0.018311 | 0.009155 | -0.013733 | -0.018311 | 0.086975 | 0.073242 | 0.07782 | -0.004578 | -0.022888 | -0.24262 | 0.17395 | 0.045776 | 0.018311 | 0.050354 | 0.022889 | 0.086975 | -121.9894 | -122.0169 | 0.18768 | 0.17853 | 0.17395 | 0.091553 | 0.086975 | 0.17853 | 121.8613 | 0.10071 | -0.004578 | 122.081 | 0.022888 | 122.0764 | 0.10986 | -122.1039 | -122.0123 | 121.8567 | 0.082397 | 0.6546 | 0.11902
2764.2656 | 122.0352 | -0.1236 | 122.0123 | -0.012131 | 0.0024738 | 0.052573 | 0.051092 | -5.5462e-05 | -0.008562 | -0.0008866 | -0.005371 | 0.030648 | 0.053316 | 0.0095019 | 0.016607 | 0.024178 | -0.0038389 | 0.51727 | 121.9803 | -0.10529 | 121.7056 | -0.004578 | -0.091553 | -0.082397 | -0.068665 | 0.013733 | -0.054932 | -0.068665 | 0.054932 | 0.027466 | 0.064087 | 0.01831 | -0.032043 | -0.3067 | 0.11902 | 0.041199 | 0.032043 | 0.022889 | 0.013733 | 0.068664 | -121.9986 | -122.081 | 0.17853 | 0.18768 | 0.15106 | 0.11902 | 0.082398 | 0.10071 | 121.8109 | 0.10986 | -0.013733 | 122.0856 | 0.068665 | 122.1039 | 0.13733 | -122.1176 | -122.0673 | 121.8292 | 0.054931 | 0.64087 | 0.054931
2765.9531 | 122.1085 | -0.086975 | 121.9574 | -0.01976 | 0.00055118 | 0.054282 | 0.050879 | -0.0039007 | -0.0074938 | -0.0043046 | -0.005371 | 0.029153 | 0.052675 | 0.0088611 | 0.014257 | 0.024605 | -0.0017027 | 0.44861 | 121.9345 | -0.059509 | 121.7697 | 0.10986 | -0.054932 | -0.004578 | 0.032043 | -0.036621 | -0.032043 | 0.009155 | 0.10986 | 0.086975 | 0.10071 | 0.027466 | -0.022888 | -0.18768 | 0.19684 | 0.082397 | 0.032043 | 0.054931 | 0.004577 | 0.054932 | -121.994 | -121.9482 | 0.19684 | 0.18768 | 0.17395 | 0.13275 | 0.11902 | 0.16937 | 121.8292 | 0.14191 | 0.041198 | 121.994 | -0.004578 | 122.0215 | 0.050354 | -122.0169 | -121.9894 | 121.8567 | 0.09613 | 0.53558 | 0.11902
2767.6562 | 122.1085 | -0.059509 | 121.9894 | -0.012131 | -0.00030342 | 0.055563 | 0.050024 | 0.0012261 | -0.012621 | -0.0036636 | -0.0023192 | 0.029153 | 0.05353 | 0.0028797 | 0.012762 | 0.027169 | -0.0031979 | 0.54016 | 121.9254 | -0.045776 | 121.8384 | 0.13733 | 0 | 0.032043 | 0.10071 | -0.036621 | -0.018311 | 0.018311 | 0.14648 | 0.11902 | 0.10529 | 0.013733 | -0.064087 | -0.15106 | 0.19684 | 0.091552 | 0.059509 | 0.077819 | 0.045776 | 0.041198 | -122.0261 | -121.9711 | 0.20599 | 0.16479 | 0.17853 | 0.1236 | 0.13733 | 0.18311 | 121.8842 | 0.16479 | 0.036622 | 121.9711 | -0.01831 | 121.9849 | 0.022888 | -122.0352 | -122.0078 | 121.8979 | 0.07782 | 0.59967 | 0.16022
2769.3594 | 122.1542 | -0.068665 | 121.9482 | -0.012131 | 0.0022602 | 0.054495 | 0.051306 | -0.0039007 | -0.0092028 | -0.001741 | -0.0023192 | 0.028299 | 0.053957 | 0.0056567 | 0.014043 | 0.024605 | -0.0034117 | 0.51727 | 121.9116 | -0.045776 | 121.843 | 0.17853 | 0.036621 | 0.091553 | 0.14191 | -0.036621 | -0.009155 | 0.032043 | 0.18768 | 0.16022 | 0.11902 | 0.022889 | -0.036621 | -0.10528 | 0.24719 | 0.16022 | 0.10529 | 0.13733 | 0.082397 | 0.05951 | -121.9849 | -121.9162 | 0.25635 | 0.18768 | 0.22888 | 0.12817 | 0.16937 | 0.2243 | 121.8887 | 0.19684 | 0.041198 | 121.9574 | -0.027466 | 121.9803 | 0.032044 | -121.994 | -121.9574 | 121.9116 | 0.10071 | 0.58594 | 0.21057
2771.1094 | 122.1497 | -0.10071 | 121.9574 | 0.0031279 | 0.00033758 | 0.052359 | 0.049383 | -5.5462e-05 | -0.0092028 | -0.0040908 | -0.005371 | 0.029794 | 0.052889 | 0.0030933 | 0.013403 | 0.023537 | -0.0040525 | 0.53558 | 121.9482 | -0.064087 | 121.8384 | 0.16479 | 0.027466 | 0.064087 | 0.11902 | -0.041199 | -0.009155 | 0.059509 | 0.17395 | 0.16022 | 0.14191 | 0.036621 | -0.009155 | -0.11902 | 0.2655 | 0.1648 | 0.12817 | 0.12817 | 0.091553 | 0.091553 | -121.9986 | -121.8979 | 0.27466 | 0.24262 | 0.26093 | 0.15106 | 0.16937 | 0.22888 | 121.9025 | 0.1831 | 0.068664 | 122.0123 | -0.032044 | 122.0489 | 0.059509 | -122.0215 | -121.9666 | 121.9391 | 0.16022 | 0.63629 | 0.21973
2772.875 | 122.0261 | -0.11902 | 121.9849 | -0.0045011 | 0.00012398 | 0.052359 | 0.052801 | -0.0034735 | -0.00963 | -0.0028092 | -0.005371 | 0.031289 | 0.05353 | 0.0048023 | 0.015112 | 0.023537 | -0.0012753 | 0.48981 | 121.9482 | -0.09613 | 121.6965 | -0.004578 | -0.10986 | -0.09613 | -0.07782 | 0.018311 | -0.045776 | -0.091553 | 0.027466 | 0.022888 | 0.018311 | 0.022889 | -0.036621 | -0.28839 | 0.11444 | 0.022889 | 0.009156 | 0 | -0.013733 | 0.073243 | -121.9666 | -122.0764 | 0.14649 | 0.13733 | 0.14191 | 0.064087 | 0.068664 | 0.091552 | 121.7926 | 0.073242 | -0.045777 | 122.0444 | 0.064087 | 122.0673 | 0.13733 | -122.081 | -122.0306 | 121.8155 | 0.027466 | 0.60883 | 0.041199
2774.6406 | 122.1268 | -0.059509 | 121.9345 | -0.0045011 | 0.00461 | 0.055777 | 0.05152 | -0.0019781 | -0.0087756 | -0.0049454 | -0.0023192 | 0.028939 | 0.053102 | 0.0060841 | 0.017675 | 0.026955 | -0.0085385 | 0.53558 | 121.9437 | -0.054932 | 121.8292 | 0.13733 | 0 | 0.036621 | 0.10986 | -0.036621 | -0.004578 | 0.054932 | 0.14648 | 0.1236 | 0.14648 | 0.004577 | 0.009156 | -0.10529 | 0.19684 | 0.09613 | 0.059509 | 0.091553 | 0.054932 | 0.054931 | -121.9711 | -121.8796 | 0.20599 | 0.20599 | 0.1831 | 0.15106 | 0.12817 | 0.19226 | 121.8842 | 0.15106 | 0.05951 | 121.9986 | -0.032043 | 122.0032 | 0.022888 | -121.9894 | -121.9391 | 121.8887 | 0.11444 | 0.59509 | 0.16937
2776.4062 | 122.1451 | -0.073242 | 121.9528 | -0.0045011 | 0.0014056 | 0.054282 | 0.04917 | -0.0041145 | -0.0092028 | -0.0030228 | -0.0023192 | 0.02723 | 0.053102 | 0.0080067 | 0.014471 | 0.026528 | -0.0038389 | 0.53558 | 121.9254 | -0.050354 | 121.8384 | 0.17395 | 0.027466 | 0.050354 | 0.12817 | -0.032043 | -0.018311 | 0.041199 | 0.17853 | 0.16022 | 0.13275 | 0.022888 | -0.027466 | -0.11444 | 0.24719 | 0.1236 | 0.10071 | 0.10071 | 0.07782 | 0.054931 | -121.9849 | -121.9116 | 0.25177 | 0.20599 | 0.23346 | 0.15106 | 0.17853 | 0.2243 | 121.8887 | 0.19684 | 0.05951 | 121.9757 | -0.013732 | 121.9986 | 0.041199 | -122.0032 | -121.9711 | 121.9116 | 0.11444 | 0.60883 | 0.20142
2778.1719 | 122.0398 | -0.10986 | 122.0123 | -0.012131 | 0.00055118 | 0.052786 | 0.050024 | 0.0022943 | -0.010698 | -0.0047318 | -0.0023192 | 0.030008 | 0.052248 | 0.0073657 | 0.015539 | 0.02311 | 0.00021995 | 0.53101 | 121.9437 | -0.086975 | 121.7194 | 0.032043 | -0.10071 | -0.054932 | -0.041199 | 0.022888 | -0.041199 | -0.082397 | 0.045776 | 0.018311 | 0.009155 | 0.022888 | -0.068664 | -0.29297 | 0.14191 | 0.054931 | 0.009155 | 0.032043 | -0.013733 | 0.068664 | -121.9894 | -122.0947 | 0.15564 | 0.11902 | 0.12817 | 0.050354 | 0.05951 | 0.11902 | 121.8063 | 0.086975 | -0.041198 | 122.0306 | 0.064087 | 122.0535 | 0.13275 | -122.0993 | -122.0535 | 121.8292 | 0.027466 | 0.64087 | 0.068664
2779.8906 | 122.1451 | -0.07782 | 121.9849 | -0.0045011 | 0.00097838 | 0.051932 | 0.050024 | -5.5462e-05 | -0.011339 | -0.00345 | -0.005371 | 0.028726 | 0.054384 | 0.0082203 | 0.014898 | 0.02546 | -0.0068295 | 0.55847 | 121.9025 | -0.050354 | 121.8292 | 0.17395 | 0.027466 | 0.050354 | 0.1236 | -0.032043 | -0.022888 | 0.045776 | 0.17395 | 0.16022 | 0.12817 | 0.027466 | -0.082397 | -0.15564 | 0.25177 | 0.12817 | 0.10529 | 0.10071 | 0.07782 | 0.054932 | -122.0169 | -121.9391 | 0.25177 | 0.20599 | 0.23804 | 0.15106 | 0.1831 | 0.2243 | 121.8796 | 0.19684 | 0.068664 | 121.9528 | -0.009155 | 121.9803 | 0.045777 | -122.0352 | -122.0078 | 121.907 | 0.1236 | 0.63629 | 0.20142
2781.6719 | 122.0123 | -0.12817 | 122.0032 | -0.012131 | -0.00073062 | 0.05065 | 0.05152 | 0.0040033 | -0.0098438 | -0.00345 | -0.0084228 | 0.031076 | 0.052034 | 0.012065 | 0.014684 | 0.020974 | -0.00042085 | 0.5127 | 121.9757 | -0.10071 | 121.7194 | 0.009155 | -0.10529 | -0.082397 | -0.059509 | 0.018311 | -0.050354 | -0.09613 | 0.022888 | 0.009155 | 0.013733 | 0.027466 | -0.027466 | -0.28381 | 0.13733 | 0.045777 | 0.022888 | 0.018311 | -0.004578 | 0.07782 | -121.9849 | -122.0993 | 0.15106 | 0.14191 | 0.13733 | 0.064087 | 0.059509 | 0.10986 | 121.8201 | 0.073242 | -0.045776 | 122.0764 | 0.068665 | 122.1039 | 0.14649 | -122.1039 | -122.0535 | 121.8475 | 0.032044 | 0.64087 | 0.068665
2783.375 | 122.1039 | -0.09613 | 121.9345 | -0.012131 | 0.0026874 | 0.05535 | 0.05152 | -0.0024055 | -0.0077074 | -0.0032364 | -0.005371 | 0.028299 | 0.053743 | -0.00075193 | 0.017675 | 0.02546 | -0.0042661 | 0.46692 | 121.9299 | -0.054932 | 121.7789 | 0.082397 | -0.050354 | -0.004578 | 0.022888 | -0.018311 | -0.027466 | -0.009155 | 0.10071 | 0.09613 | 0.091553 | 0.041198 | -0.004577 | -0.15564 | 0.17853 | 0.091552 | 0.045776 | 0.050354 | 0.004578 | 0.068664 | -121.9528 | -121.9437 | 0.19684 | 0.18768 | 0.19226 | 0.11902 | 0.1236 | 0.13733 | 121.8338 | 0.12817 | 0.018311 | 121.9849 | 0.009155 | 122.0261 | 0.077819 | -121.9894 | -121.962 | 121.875 | 0.086975 | 0.56305 | 0.11902
2785.1406 | 122.0215 | -0.1236 | 121.9894 | -0.02739 | 0.00076478 | 0.053214 | 0.051092 | 0.0010125 | -0.0094164 | -0.0064408 | -0.005371 | 0.030862 | 0.055452 | 0.0073657 | 0.015112 | 0.024391 | -0.0014891 | 0.50354 | 121.9528 | -0.10529 | 121.7102 | 0.004578 | -0.09613 | -0.086975 | -0.050354 | 0.018311 | -0.059509 | -0.091553 | 0.036621 | 0.018311 | 0.032043 | 0.01831 | -0.036621 | -0.27924 | 0.12817 | 0.036621 | 0.027466 | 0.018311 | 0.009156 | 0.064087 | -121.9711 | -122.081 | 0.16022 | 0.15564 | 0.14191 | 0.091552 | 0.07782 | 0.10986 | 121.8155 | 0.09613 | -0.032044 | 122.0581 | 0.07782 | 122.0764 | 0.14191 | -122.0947 | -122.049 | 121.8338 | 0.032043 | 0.62714 | 0.073242
2786.9062 | 122.0169 | -0.1236 | 121.9757 | -0.01976 | 0.0031146 | 0.053427 | 0.05686 | 0.0029351 | -0.0094164 | -0.0028092 | -0.005371 | 0.032144 | 0.056093 | 0.013774 | 0.017675 | 0.022469 | -0.0072569 | 0.48523 | 121.9986 | -0.091553 | 121.6827 | -0.027466 | -0.16479 | -0.10986 | -0.07782 | 0.004578 | -0.054932 | -0.073242 | 0.009155 | -0.022888 | 0.032043 | 0.032043 | 0.022888 | -0.29297 | 0.09613 | 0.013733 | -0.041199 | -0.01831 | -0.073242 | 0.068664 | -121.9711 | -122.0489 | 0.13275 | 0.15564 | 0.10071 | 0.086975 | 0.032044 | 0.064087 | 121.7743 | 0.064087 | -0.01831 | 122.0901 | 0.05951 | 122.1222 | 0.12817 | -122.0673 | -122.0306 | 121.8063 | 0.050354 | 0.60883 | 0.045776
2788.6094 | 122.0306 | -0.11444 | 121.9711 | -0.012131 | 0.0033282 | 0.053 | 0.053869 | 0.0014397 | -0.008562 | -0.002382 | -0.005371 | 0.031503 | 0.054384 | 0.012279 | 0.017889 | 0.024819 | -0.00020725 | 0.58594 | 121.9711 | -0.068665 | 121.7468 | 0.068665 | -0.09613 | -0.054932 | 0.022888 | -0.009155 | -0.045776 | -0.022888 | 0.068665 | 0.004578 | 0.041199 | 0.045776 | 0 | -0.2243 | 0.18311 | 0.059509 | 0.018311 | 0.013733 | -0.027465 | 0.068665 | -121.9803 | -121.994 | 0.18311 | 0.15564 | 0.11902 | 0.086975 | 0.050354 | 0.13733 | 121.8155 | 0.11444 | 0.022888 | 122.0398 | 0.036621 | 122.0856 | 0.10529 | -122.0398 | -122.0169 | 121.8613 | 0.091553 | 0.70038 | 0.13733
2790.3906 | 122.0352 | -0.11444 | 122.0123 | -0.012131 | 0.001192 | 0.052573 | 0.050238 | -0.0043281 | -0.010485 | -0.0025956 | -0.0084228 | 0.028726 | 0.056307 | 0.0050159 | 0.016393 | 0.027809 | -0.0023435 | 0.56763 | 121.9437 | -0.07782 | 121.7743 | 0.09613 | -0.022888 | -0.013733 | 0.018311 | 0 | -0.059509 | -0.059509 | 0.073242 | 0.036621 | 0.041199 | 0.036621 | -0.068664 | -0.23804 | 0.21057 | 0.10071 | 0.091553 | 0.064087 | 0.054932 | 0.054932 | -122.0123 | -122.0718 | 0.18768 | 0.15564 | 0.15106 | 0.10071 | 0.09613 | 0.17395 | 121.8521 | 0.13275 | 0 | 122.0215 | 0.059509 | 122.0581 | 0.11444 | -122.0901 | -122.0718 | 121.8887 | 0.054932 | 0.68207 | 0.13275
2792.0938 | 122.0947 | -0.07782 | 121.9482 | -0.0045011 | 0.0022602 | 0.053214 | 0.051092 | -0.0051825 | -0.0083484 | -0.0004592 | -0.005371 | 0.029367 | 0.055239 | 0.0024525 | 0.012548 | 0.024819 | -0.0055479 | 0.47607 | 121.9528 | -0.059509 | 121.7606 | 0.073242 | -0.045776 | -0.018311 | 0.018311 | -0.013733 | -0.018311 | -0.013733 | 0.10071 | 0.07782 | 0.082397 | 0.018311 | 0.004578 | -0.18768 | 0.15106 | 0.059509 | 0.032044 | 0.041198 | 0.013733 | 0.059509 | -121.962 | -121.962 | 0.17853 | 0.16022 | 0.15564 | 0.10071 | 0.096131 | 0.13275 | 121.8201 | 0.11902 | 0.004578 | 122.0123 | 0.004578 | 122.0306 | 0.064087 | -122.0078 | -121.9666 | 121.8384 | 0.064087 | 0.55389 | 0.096131
2793.8594 | 122.1268 | -0.07782 | 121.9391 | -0.02739 | -0.00051702 | 0.054068 | 0.050024 | -5.5462e-05 | -0.0083484 | 0.0008224 | -0.0084228 | 0.02723 | 0.054171 | 0.0062977 | 0.013189 | 0.025887 | -0.0014891 | 0.49439 | 121.9025 | -0.068665 | 121.7697 | 0.091553 | -0.022888 | 0.004578 | 0.032043 | -0.018311 | -0.041199 | 0.032043 | 0.13733 | 0.13275 | 0.11902 | 0.009155 | -0.036621 | -0.16937 | 0.16937 | 0.082398 | 0.054932 | 0.073243 | 0.045777 | 0.036621 | -121.9574 | -121.907 | 0.21515 | 0.19684 | 0.21057 | 0.16022 | 0.17395 | 0.16022 | 121.8384 | 0.17853 | 0.073242 | 121.9711 | 0.022888 | 121.9803 | 0.059509 | -122.0078 | -121.9803 | 121.8475 | 0.10986 | 0.57221 | 0.10986
2795.625 | 122.1497 | -0.064087 | 121.9391 | -0.012131 | 0.0054644 | 0.054922 | 0.053015 | 0.0025079 | -0.0070666 | -0.0047318 | -0.0084228 | 0.030008 | 0.053957 | 0.013774 | 0.014684 | 0.028023 | -0.0021299 | 0.54016 | 121.9482 | -0.059509 | 121.8246 | 0.1236 | -0.032043 | 0.027466 | 0.091553 | -0.036621 | -0.004578 | 0.073242 | 0.15564 | 0.14191 | 0.14191 | 0.004578 | 0.009155 | -0.11444 | 0.18768 | 0.091553 | 0.032044 | 0.086975 | 0.027466 | 0.059509 | -121.9757 | -121.8658 | 0.21973 | 0.20599 | 0.20599 | 0.14649 | 0.14649 | 0.1831 | 121.8842 | 0.16022 | 0.07782 | 122.0078 | -0.032043 | 122.0123 | 0.027466 | -121.9986 | -121.9437 | 121.8887 | 0.13733 | 0.60425 | 0.15564
2797.375 | 122.1085 | -0.10071 | 121.9711 | -0.01976 | 0.0020466 | 0.054495 | 0.051092 | -0.0045417 | -0.0079212 | -0.00345 | -0.0084228 | 0.028726 | 0.054811 | -0.0011791 | 0.01383 | 0.024605 | -0.0021299 | 0.48981 | 121.9162 | -0.068665 | 121.7789 | 0.073242 | -0.041199 | -0.022888 | 0.022888 | -0.027466 | -0.018311 | -0.004578 | 0.11444 | 0.09613 | 0.09613 | 0.032043 | -0.054931 | -0.19226 | 0.17395 | 0.07782 | 0.059509 | 0.045777 | 0.027466 | 0.082397 | -121.9986 | -121.9757 | 0.21515 | 0.19684 | 0.19684 | 0.11444 | 0.11444 | 0.14191 | 121.8475 | 0.13275 | 0.013733 | 121.9849 | -0.009155 | 122.0169 | 0.073242 | -122.0398 | -121.9894 | 121.8796 | 0.09613 | 0.59052 | 0.1236
2799.0781 | 122.0627 | -0.10529 | 121.9666 | -0.012131 | 0.0041828 | 0.053214 | 0.055578 | 0.0033623 | -0.0081348 | -0.000673 | -0.0023192 | 0.032144 | 0.058016 | 0.0082203 | 0.015325 | 0.026955 | -0.0034117 | 0.59967 | 121.9803 | -0.082397 | 121.7697 | 0.068665 | -0.068665 | -0.064087 | 0.032043 | 0.004578 | -0.050354 | -0.004578 | 0.091553 | 0.054932 | 0.073242 | 0.022889 | 0.013733 | -0.19684 | 0.17395 | 0.041199 | 0.036621 | 0.01831 | 0.013732 | 0.054932 | -121.962 | -121.9711 | 0.19684 | 0.17853 | 0.16022 | 0.1236 | 0.10529 | 0.15106 | 121.8521 | 0.14191 | 0.045776 | 122.0627 | 0.054932 | 122.0856 | 0.10986 | -122.049 | -122.0169 | 121.875 | 0.10071 | 0.70496 | 0.13733
2800.8438 | 122.1542 | -0.064087 | 121.9391 | -0.0045011 | 0.00076478 | 0.053641 | 0.051306 | 0.00058534 | -0.0077074 | -0.0049454 | -0.005371 | 0.029367 | 0.05652 | 0.0052295 | 0.015325 | 0.022255 | -0.0098203 | 0.55847 | 121.9437 | -0.059509 | 121.8201 | 0.14648 | 0.013733 | 0.050354 | 0.10986 | -0.050354 | -0.022888 | 0.07782 | 0.17853 | 0.17853 | 0.14191 | 0.004578 | 0.004578 | -0.11902 | 0.21057 | 0.11444 | 0.07782 | 0.10986 | 0.073242 | 0.041199 | -121.9894 | -121.8613 | 0.24261 | 0.20599 | 0.24261 | 0.16479 | 0.20142 | 0.20599 | 121.8796 | 0.20142 | 0.10071 | 122.0032 | -0.027466 | 122.0078 | 0.013733 | -121.9986 | -121.962 | 121.8842 | 0.14191 | 0.62256 | 0.17395
2802.6094 | 122.0535 | -0.10986 | 121.9666 | -0.012131 | 0.0043964 | 0.054068 | 0.053442 | 0.0022943 | -0.008562 | -0.0040908 | -0.0084228 | 0.032571 | 0.055025 | 0.013347 | 0.017675 | 0.024819 | -0.0034117 | 0.60425 | 121.9711 | -0.068665 | 121.7789 | 0.082397 | -0.064087 | -0.036621 | 0.027466 | -0.009155 | -0.022888 | -0.004578 | 0.073242 | 0.054932 | 0.073242 | 0.041198 | 0.004577 | -0.18768 | 0.19226 | 0.073242 | 0.045776 | 0.032044 | 0.004578 | 0.086975 | -121.9757 | -121.9711 | 0.18311 | 0.18311 | 0.16479 | 0.09613 | 0.07782 | 0.15106 | 121.8475 | 0.09613 | 0.01831 | 122.0398 | 0.013733 | 122.081 | 0.10071 | -122.0352 | -121.9894 | 121.8887 | 0.10529 | 0.71411 | 0.13733
2804.3125 | 122.0261 | -0.13275 | 121.9894 | -0.01976 | -8.9824e-05 | 0.052573 | 0.050879 | 0.00079894 | -0.0087756 | -0.0028092 | -0.011475 | 0.028939 | 0.05652 | 0.0060841 | 0.015539 | 0.023751 | -0.0044797 | 0.56305 | 121.9345 | -0.09613 | 121.7285 | 0.032043 | -0.10529 | -0.086975 | -0.045776 | -0.009155 | -0.059509 | -0.082397 | 0.045776 | 0.027466 | 0.013733 | 0.036621 | -0.054932 | -0.26093 | 0.16479 | 0.045776 | 0.027465 | 0.009155 | -0.009156 | 0.073242 | -121.9986 | -122.0718 | 0.17853 | 0.14648 | 0.16022 | 0.073242 | 0.086975 | 0.12817 | 121.8246 | 0.10528 | -0.022888 | 122.0306 | 0.050354 | 122.0673 | 0.1236 | -122.0856 | -122.049 | 121.8613 | 0.050354 | 0.6958 | 0.086975
2806.0781 | 122.0078 | -0.12817 | 121.9894 | -0.012131 | 0.00076478 | 0.052786 | 0.051306 | -0.00069646 | -0.0081348 | -0.00345 | -0.005371 | 0.031076 | 0.055239 | 0.013133 | 0.013403 | 0.023751 | -0.00063445 | 0.5722 | 121.9574 | -0.09613 | 121.7056 | -0.009155 | -0.10071 | -0.10071 | -0.059509 | 0 | -0.041199 | -0.07782 | 0.027466 | 0.022888 | 0.027466 | 0.032044 | -0.032044 | -0.28381 | 0.11902 | 0.027466 | 0.027466 | -0.004578 | -0.004578 | 0.086975 | -121.9894 | -122.0673 | 0.15564 | 0.15564 | 0.15106 | 0.068665 | 0.064087 | 0.086975 | 121.8018 | 0.068665 | -0.036621 | 122.0535 | 0.041199 | 122.0856 | 0.12817 | -122.0856 | -122.0306 | 121.8338 | 0.050354 | 0.70038 | 0.068665
2807.8281 | 122.0352 | -0.10071 | 121.9849 | -0.012131 | 0.0016192 | 0.053427 | 0.049811 | -0.0013373 | -0.012194 | -0.0036636 | -0.005371 | 0.02958 | 0.055666 | 0.0075793 | 0.015112 | 0.026528 | -0.0042661 | 0.62256 | 121.9254 | -0.068665 | 121.7743 | 0.09613 | -0.027466 | -0.004578 | 0.027466 | 0 | -0.032043 | -0.054932 | 0.064087 | 0.082397 | 0.050354 | 0.032043 | -0.059509 | -0.21057 | 0.19684 | 0.09613 | 0.073242 | 0.064087 | 0.041199 | 0.068665 | -121.9849 | -122.0398 | 0.1648 | 0.15106 | 0.18311 | 0.082397 | 0.11444 | 0.16479 | 121.843 | 0.09613 | -0.022889 | 121.994 | 0.032043 | 122.0261 | 0.10071 | -122.0535 | -122.0169 | 121.875 | 0.045776 | 0.72327 | 0.12817
2809.5938 | 122.1497 | -0.064087 | 121.9574 | -0.0045011 | 0.0026874 | 0.054495 | 0.051947 | 0.0016535 | -0.0070666 | -0.0038772 | 0.00073235 | 0.029153 | 0.055025 | 0.0086475 | 0.01618 | 0.024178 | -0.0019163 | 0.60883 | 121.9299 | -0.050354 | 121.8201 | 0.12817 | -0.018311 | 0.032043 | 0.11902 | -0.032043 | -0.018311 | 0.07782 | 0.15106 | 0.12817 | 0.15106 | 0.013733 | -0.027465 | -0.13733 | 0.19226 | 0.09613 | 0.045776 | 0.082397 | 0.032043 | 0.045776 | -121.9894 | -121.8796 | 0.21515 | 0.21515 | 0.19226 | 0.16937 | 0.14649 | 0.17853 | 121.8704 | 0.16937 | 0.096131 | 121.9803 | -0.013732 | 121.994 | 0.032044 | -122.0078 | -121.9757 | 121.8842 | 0.14191 | 0.67291 | 0.18311
2811.3438 | 122.1268 | -0.073242 | 121.9574 | -0.012131 | -0.0011578 | 0.053641 | 0.047461 | 0.00058534 | -0.0064258 | -0.0047318 | -0.005371 | 0.02958 | 0.056307 | 0.0052295 | 0.01618 | 0.026528 | 0.0017153 | 0.62256 | 121.9208 | -0.064087 | 121.8567 | 0.17853 | 0.041199 | 0.054932 | 0.1236 | -0.027466 | -0.013733 | 0.041199 | 0.1831 | 0.16937 | 0.13733 | 0.009155 | -0.036621 | -0.10071 | 0.25177 | 0.12817 | 0.11444 | 0.11902 | 0.10529 | 0.059509 | -121.9849 | -121.9162 | 0.25635 | 0.21057 | 0.24261 | 0.15106 | 0.18311 | 0.24261 | 121.9208 | 0.19684 | 0.054932 | 121.9849 | -0.013733 | 121.994 | 0.045776 | -122.0215 | -121.9711 | 121.9299 | 0.11444 | 0.6958 | 0.19684
2813.0469 | 122.0032 | -0.11902 | 121.994 | -0.012131 | 0.0054644 | 0.055136 | 0.051733 | 0.0048577 | -0.0077074 | -0.0030228 | -0.0084228 | 0.032357 | 0.055239 | 0.0082203 | 0.015966 | 0.023751 | -0.0064023 | 0.59509 | 121.9849 | -0.082397 | 121.7148 | -0.032043 | -0.15106 | -0.1236 | -0.07782 | 0.013733 | -0.045776 | -0.064087 | -0.018311 | -0.022888 | 0.018311 | 0.036622 | -0.009156 | -0.27924 | 0.086976 | -0.004577 | -0.032043 | -0.041199 | -0.068665 | 0.073243 | -121.9803 | -122.0581 | 0.10071 | 0.13733 | 0.096131 | 0.064087 | 0.022888 | 0.050354 | 121.7972 | 0.027465 | -0.018311 | 122.0673 | 0.059509 | 122.1039 | 0.13275 | -122.0764 | -122.0398 | 121.8338 | 0.054932 | 0.71411 | 0.041199
2814.8281 | 122.1451 | -0.082397 | 121.9437 | -0.012131 | 0.0024738 | 0.053641 | 0.049597 | -0.0034735 | -0.010057 | -0.0036636 | -0.005371 | 0.028939 | 0.056948 | 0.0084339 | 0.015325 | 0.0261 | -0.0012753 | 0.62256 | 121.907 | -0.050354 | 121.8521 | 0.19226 | 0.054932 | 0.045776 | 0.1236 | -0.018311 | -0.022888 | 0.050354 | 0.19684 | 0.17853 | 0.13275 | 0.032043 | -0.036622 | -0.091553 | 0.27466 | 0.12817 | 0.13733 | 0.09613 | 0.10529 | 0.059509 | -121.962 | -121.8933 | 0.27924 | 0.21515 | 0.26092 | 0.15564 | 0.20142 | 0.24261 | 121.9025 | 0.21973 | 0.073242 | 121.9574 | 0.004577 | 121.9894 | 0.064086 | -121.994 | -121.9666 | 121.9345 | 0.13275 | 0.70496 | 0.20599
2816.5938 | 122.0673 | -0.11444 | 121.9711 | -0.012131 | 0.0050372 | 0.056631 | 0.051947 | 0.0016535 | -0.006853 | -0.0038772 | -0.0084228 | 0.033639 | 0.057802 | 0.0054431 | 0.017248 | 0.0261 | -0.0027707 | 0.56305 | 121.9894 | -0.09613 | 121.7056 | -0.009155 | -0.13733 | -0.10071 | -0.036621 | 0.009155 | -0.041199 | -0.032043 | 0.054932 | 0.013733 | 0.050354 | 0.018311 | 0.018311 | -0.2655 | 0.10529 | 0.013733 | -0.022888 | -0.004578 | -0.041199 | 0.073242 | -121.962 | -122.0032 | 0.16937 | 0.16479 | 0.12817 | 0.091553 | 0.054932 | 0.086975 | 121.8018 | 0.096131 | 0.009156 | 122.0856 | 0.050354 | 122.1039 | 0.1236 | -122.0673 | -122.0123 | 121.8201 | 0.082398 | 0.67749 | 0.07782
2818.3594 | 122.0535 | -0.11444 | 121.9986 | -0.012131 | 0.0016192 | 0.054709 | 0.048529 | -0.0015509 | -0.010271 | -0.001741 | -0.0084228 | 0.028726 | 0.057161 | 0.0033069 | 0.015539 | 0.025887 | -0.0044797 | 0.64545 | 121.9299 | -0.068665 | 121.7972 | 0.10529 | -0.009155 | 0.009155 | 0.041199 | -0.018311 | -0.036621 | -0.036621 | 0.073242 | 0.068665 | 0.059509 | 0.045776 | -0.068664 | -0.20142 | 0.21973 | 0.1236 | 0.10529 | 0.07782 | 0.05951 | 0.07782 | -122.0169 | -122.0352 | 0.18768 | 0.17395 | 0.18311 | 0.09613 | 0.10529 | 0.17395 | 121.8658 | 0.10986 | 0 | 121.9986 | 0.01831 | 122.0444 | 0.09613 | -122.0673 | -122.0352 | 121.9116 | 0.07782 | 0.75989 | 0.15564
2820.0625 | 122.1405 | -0.068665 | 121.962 | -0.0045011 | -0.00030342 | 0.052359 | 0.049597 | -0.0013373 | -0.010057 | -0.0028092 | -0.005371 | 0.030862 | 0.055239 | 0.0099293 | 0.013616 | 0.024391 | -0.0044797 | 0.64087 | 121.8979 | -0.064087 | 121.8475 | 0.16937 | 0.045776 | 0.050354 | 0.10986 | -0.018311 | -0.022888 | 0.045776 | 0.1831 | 0.16022 | 0.13275 | 0.004578 | -0.064087 | -0.11444 | 0.23804 | 0.11902 | 0.11444 | 0.11444 | 0.10986 | 0.045777 | -121.9803 | -121.9162 | 0.25177 | 0.20142 | 0.22888 | 0.15564 | 0.1831 | 0.23346 | 121.9116 | 0.20599 | 0.068664 | 121.962 | 0.004577 | 121.9666 | 0.050354 | -122.0261 | -121.9849 | 121.9162 | 0.11444 | 0.70953 | 0.17853
2821.8281 | 122.1588 | -0.064087 | 121.9345 | -0.012131 | 0.0056782 | 0.055777 | 0.053015 | 0.0016535 | -0.0062122 | -0.0045182 | -0.0084228 | 0.030008 | 0.054811 | 0.0069385 | 0.014898 | 0.027596 | -0.0046933 | 0.60425 | 121.9711 | -0.059509 | 121.7972 | 0.09613 | -0.054932 | 0 | 0.068665 | -0.022888 | -0.022888 | 0.054932 | 0.15106 | 0.1236 | 0.15106 | 0.004578 | 0.036621 | -0.13733 | 0.16022 | 0.064087 | 0.009155 | 0.059509 | 0.004577 | 0.041199 | -121.9574 | -121.8796 | 0.21515 | 0.21515 | 0.18768 | 0.17395 | 0.14648 | 0.15564 | 121.8567 | 0.17395 | 0.07782 | 122.0306 | 0 | 122.0352 | 0.041199 | -121.994 | -121.9574 | 121.8613 | 0.11902 | 0.66834 | 0.13275
2823.5156 | 122.0215 | -0.1236 | 121.9711 | -0.0045011 | 0.002901 | 0.054282 | 0.051947 | 0.0010125 | -0.0089892 | -0.0028092 | -0.005371 | 0.03193 | 0.056734 | 0.010784 | 0.017248 | 0.0261 | -0.0025571 | 0.66376 | 121.9666 | -0.07782 | 121.7331 | 0.018311 | -0.1236 | -0.091553 | -0.013733 | -0.009155 | -0.045776 | -0.059509 | 0.022888 | 0 | 0.041199 | 0.045776 | -0.004577 | -0.23804 | 0.14191 | 0.032043 | 0 | -0.013733 | -0.045776 | 0.07782 | -121.9803 | -122.0306 | 0.14648 | 0.16479 | 0.1236 | 0.086975 | 0.045776 | 0.096131 | 121.8109 | 0.068664 | -0.013733 | 122.0444 | 0.036621 | 122.0901 | 0.11444 | -122.049 | -122.0169 | 121.8567 | 0.064087 | 0.78735 | 0.10986
2825.2812 | 122.0993 | -0.07782 | 121.9391 | -0.0045011 | 0.0020466 | 0.051718 | 0.049597 | -0.00026906 | -0.00963 | -0.0021682 | -0.005371 | 0.029153 | 0.057802 | 0.0095019 | 0.01383 | 0.026314 | -0.0040525 | 0.59052 | 121.9345 | -0.064087 | 121.7606 | 0.064087 | -0.045776 | -0.022888 | 0.022888 | -0.018311 | -0.022888 | -0.004578 | 0.10986 | 0.091553 | 0.10071 | 0.013733 | -0.004578 | -0.17853 | 0.14191 | 0.054932 | 0.032044 | 0.041199 | 0.018311 | 0.054932 | -121.9574 | -121.9437 | 0.18768 | 0.17853 | 0.16937 | 0.1236 | 0.11444 | 0.12817 | 121.8246 | 0.13275 | 0.01831 | 121.9986 | 0.004577 | 122.0123 | 0.059509 | -122.0032 | -121.962 | 121.8384 | 0.073242 | 0.66834 | 0.10071
2826.9844 | 122.0627 | -0.10986 | 121.9528 | -0.012131 | 0.0037556 | 0.055136 | 0.052374 | -0.00091006 | -0.0094164 | -0.0021682 | -0.005371 | 0.029794 | 0.056948 | 0.013133 | 0.014684 | 0.025887 | -0.0076841 | 0.70496 | 121.9711 | -0.086975 | 121.7606 | 0.050354 | -0.082397 | -0.050354 | 0.022888 | 0 | -0.045776 | -0.022888 | 0.09613 | 0.064087 | 0.064087 | 0.022888 | 0.01831 | -0.19226 | 0.16022 | 0.059509 | 0.027466 | 0.036621 | 0.004578 | 0.064087 | -121.9528 | -121.9757 | 0.20599 | 0.17395 | 0.17395 | 0.10986 | 0.10986 | 0.13733 | 121.8475 | 0.14191 | 0.022888 | 122.0581 | 0.045776 | 122.081 | 0.10986 | -122.0398 | -121.9986 | 121.8704 | 0.086975 | 0.81482 | 0.13275
2828.75 | 122.0581 | -0.091553 | 121.9574 | -0.01976 | 0.0031146 | 0.055777 | 0.05152 | -0.0017645 | -0.0098438 | -0.0013138 | -0.0084228 | 0.032144 | 0.058229 | 0.0075793 | 0.017248 | 0.025032 | -0.0044797 | 0.70953 | 121.9711 | -0.09613 | 121.7651 | 0.059509 | -0.068665 | -0.054932 | 0.041199 | 0.004578 | -0.032043 | -0.013733 | 0.068665 | 0.054932 | 0.064087 | -0.004577 | 0.013733 | -0.19226 | 0.15106 | 0.036621 | 0.022888 | 0.041198 | 0.027465 | 0.05951 | -121.9528 | -121.9711 | 0.16022 | 0.15564 | 0.14649 | 0.09613 | 0.086975 | 0.15564 | 121.8613 | 0.10071 | 0.01831 | 122.0673 | 0.036621 | 122.0627 | 0.096131 | -122.0535 | -121.9894 | 121.8567 | 0.07782 | 0.80109 | 0.13275
2830.4531 | 122.0261 | -0.11444 | 121.9803 | -0.0045011 | 0.0024738 | 0.053854 | 0.052588 | -0.0030463 | -0.0064258 | -0.0008866 | -0.005371 | 0.030008 | 0.058657 | 0.0024525 | 0.016393 | 0.025032 | -0.0059751 | 0.70038 | 121.9849 | -0.10071 | 121.7377 | 0.064087 | -0.10071 | -0.073242 | -0.013733 | 0.004578 | -0.045776 | -0.045776 | 0.041199 | 0.009155 | 0.036621 | 0.013733 | 0.004577 | -0.24262 | 0.17853 | 0.041199 | 0.013733 | 0.027466 | 0 | 0.068665 | -121.9757 | -122.0261 | 0.15564 | 0.15106 | 0.1236 | 0.082397 | 0.054931 | 0.1648 | 121.8384 | 0.086975 | 0 | 122.0856 | 0.050354 | 122.0993 | 0.11902 | -122.081 | -122.0261 | 121.8521 | 0.068665 | 0.81482 | 0.10071
2832.2188 | 122.0718 | -0.091553 | 121.9803 | -0.0045011 | 0.0033282 | 0.052786 | 0.051947 | -0.00026906 | -0.0094164 | -0.0045182 | -0.0023192 | 0.031717 | 0.058443 | 0.0037341 | 0.017034 | 0.025673 | 6.346e-06 | 0.62256 | 121.9849 | -0.091553 | 121.7102 | 0 | -0.14191 | -0.07782 | -0.004578 | -0.018311 | -0.059509 | 0.004578 | 0.082397 | 0.045776 | 0.07782 | 0 | 0.004577 | -0.27008 | 0.091553 | 0.013733 | -0.050354 | 0.013733 | -0.050354 | 0.032044 | -121.9986 | -121.9757 | 0.17395 | 0.16937 | 0.13733 | 0.13733 | 0.10528 | 0.091553 | 121.8018 | 0.14191 | 0.064087 | 122.0764 | 0.041198 | 122.0764 | 0.073242 | -122.0718 | -122.0398 | 121.8018 | 0.096131 | 0.71411 | 0.086975
2833.9844 | 122.1497 | -0.068665 | 121.9299 | -0.012131 | 0.0035418 | 0.055136 | 0.052588 | -0.0013373 | -0.008562 | -0.002382 | -0.005371 | 0.030008 | 0.05887 | 0.0069385 | 0.017034 | 0.026955 | -0.0061887 | 0.66376 | 121.9574 | -0.07782 | 121.8018 | 0.1236 | -0.027466 | 0.018311 | 0.086975 | -0.032043 | -0.009155 | 0.064087 | 0.14648 | 0.11902 | 0.15106 | -0.009155 | 0.027465 | -0.12817 | 0.19226 | 0.086976 | 0.041199 | 0.096131 | 0.050354 | 0.05951 | -121.962 | -121.8658 | 0.21515 | 0.21973 | 0.18768 | 0.16022 | 0.12817 | 0.20142 | 121.8796 | 0.15564 | 0.073242 | 122.0352 | -0.022888 | 122.0261 | 0.036622 | -122.0078 | -121.9391 | 121.8704 | 0.13275 | 0.73242 | 0.15564
2835.7031 | 121.9894 | -0.10986 | 121.9849 | -0.012131 | 0.00461 | 0.054709 | 0.053442 | 0.0022943 | -0.0092028 | -0.0038772 | -0.005371 | 0.032144 | 0.058016 | 0.010784 | 0.016393 | 0.023964 | -0.0014891 | 0.68207 | 121.994 | -0.086975 | 121.701 | -0.036621 | -0.15106 | -0.11444 | -0.07782 | 0.018311 | -0.045776 | -0.091553 | -0.018311 | -0.032043 | 0.022888 | 0.022888 | 0.009156 | -0.28381 | 0.073242 | -0.004578 | -0.041199 | -0.027466 | -0.064087 | 0.064087 | -121.9666 | -122.0764 | 0.091552 | 0.13275 | 0.07782 | 0.068664 | 0.013733 | 0.050354 | 121.788 | 0.027465 | -0.045777 | 122.081 | 0.064087 | 122.1039 | 0.12817 | -122.0718 | -122.0306 | 121.8109 | 0.01831 | 0.79193 | 0.032043
2837.4531 | 122.0627 | -0.09613 | 121.9803 | -0.012131 | 0.00076478 | 0.054709 | 0.052374 | -0.00091006 | -0.0087756 | -0.0015274 | -0.005371 | 0.02958 | 0.056948 | 0.012706 | 0.016393 | 0.024819 | -0.0038389 | 0.75073 | 121.9574 | -0.09613 | 121.7514 | 0.054932 | -0.068665 | -0.064087 | 0.041199 | -0.009155 | -0.036621 | -0.018311 | 0.091553 | 0.050354 | 0.082397 | 0 | -0.022889 | -0.22888 | 0.15106 | 0.032043 | 0.027465 | 0.032043 | 0.027465 | 0.059509 | -121.9894 | -121.9986 | 0.18768 | 0.17853 | 0.14648 | 0.11902 | 0.086975 | 0.15106 | 121.8475 | 0.12817 | 0.01831 | 122.0535 | 0.027466 | 122.0535 | 0.086975 | -122.0764 | -122.0169 | 121.8475 | 0.077819 | 0.84686 | 0.13733
2839.1562 | 122.1313 | -0.091553 | 121.9666 | -0.0045011 | -0.00051702 | 0.054922 | 0.050024 | -0.0039007 | -0.0087756 | -0.0036636 | -0.005371 | 0.028512 | 0.057802 | 0.0045887 | 0.014043 | 0.028023 | -0.0017027 | 0.65918 | 121.9208 | -0.064087 | 121.7606 | 0.09613 | -0.027466 | 0.013733 | 0.054932 | -0.009155 | -0.041199 | 0.027466 | 0.15106 | 0.13733 | 0.11902 | 0.027466 | -0.045777 | -0.20599 | 0.18768 | 0.10529 | 0.064087 | 0.07782 | 0.036621 | 0.050354 | -121.9757 | -121.9391 | 0.24261 | 0.21057 | 0.22888 | 0.16022 | 0.17853 | 0.16022 | 121.8246 | 0.19226 | 0.068665 | 121.9849 | 0.032044 | 122.0123 | 0.082398 | -122.0306 | -122.0078 | 121.8521 | 0.11902 | 0.75073 | 0.14649
2840.9219 | 122.0078 | -0.11444 | 121.994 | -0.012131 | -8.9824e-05 | 0.05065 | 0.048742 | -0.0036871 | -0.0066394 | -0.0013138 | -0.005371 | 0.031503 | 0.059938 | 0.0080067 | 0.014043 | 0.024605 | -0.0031979 | 0.72327 | 121.9666 | -0.086975 | 121.6965 | 0.004578 | -0.09613 | -0.086975 | -0.054932 | 0.004578 | -0.068665 | -0.086975 | 0.036621 | 0.022888 | 0.027466 | 0.027466 | -0.027466 | -0.29755 | 0.11902 | 0.027466 | 0.018311 | 0 | -0.009155 | 0.045776 | -121.9894 | -122.081 | 0.15106 | 0.14191 | 0.13733 | 0.096131 | 0.091553 | 0.091553 | 121.7834 | 0.10529 | -0.01831 | 122.0535 | 0.073243 | 122.081 | 0.11902 | -122.081 | -122.0627 | 121.8109 | 0.027466 | 0.83771 | 0.059509
2842.6875 | 122.0261 | -0.1236 | 121.9849 | -0.012131 | 0.0054644 | 0.055136 | 0.052801 | 0.0020807 | -0.008562 | -0.0008866 | -0.0084228 | 0.031717 | 0.059511 | 0.0052295 | 0.018102 | 0.024819 | -0.0012753 | 0.72784 | 122.0078 | -0.11444 | 121.6965 | -0.045776 | -0.16479 | -0.13275 | -0.086975 | 0.004578 | -0.064087 | -0.073242 | -0.009155 | -0.018311 | 0.022888 | 0.009155 | 0.022888 | -0.28839 | 0.07782 | -0.009155 | -0.041199 | -0.01831 | -0.050354 | 0.059509 | -121.9803 | -122.0581 | 0.11444 | 0.14648 | 0.10528 | 0.086975 | 0.045776 | 0.068665 | 121.8109 | 0.054932 | -0.009155 | 122.1222 | 0.068665 | 122.1313 | 0.12817 | -122.0993 | -122.049 | 121.8201 | 0.050354 | 0.85144 | 0.036621
2844.3906 | 122.0215 | -0.12817 | 121.9757 | -0.0045011 | 0.0022602 | 0.052786 | 0.050238 | 0.0012261 | -0.0098438 | -0.0038772 | -0.005371 | 0.030648 | 0.060366 | 0.0062977 | 0.015966 | 0.02546 | -0.0040525 | 0.737 | 121.9482 | -0.10986 | 121.701 | 0.004578 | -0.10529 | -0.082397 | -0.045776 | 0.018311 | -0.054932 | -0.091553 | 0.027466 | 0.004578 | 0.009155 | 0.018311 | -0.027466 | -0.27466 | 0.13275 | 0.045777 | 0.022888 | 0.027466 | 0.004577 | 0.073242 | -121.9574 | -122.0673 | 0.15564 | 0.13733 | 0.13275 | 0.064087 | 0.05951 | 0.11444 | 121.8109 | 0.082398 | -0.036621 | 122.0581 | 0.073243 | 122.0764 | 0.14649 | -122.0856 | -122.0306 | 121.8292 | 0.036621 | 0.86517 | 0.082398
2846.1562 | 122.1588 | -0.091553 | 121.9299 | -0.012131 | 0.00012398 | 0.053641 | 0.048102 | -0.0034735 | -0.0094164 | -0.00345 | -0.005371 | 0.027871 | 0.060793 | 0.0039477 | 0.012334 | 0.025032 | 0.00086095 | 0.76904 | 121.9208 | -0.073242 | 121.8063 | 0.15106 | 0.027466 | 0.050354 | 0.11444 | -0.022888 | -0.018311 | 0.041199 | 0.17853 | 0.17395 | 0.13275 | 0.018311 | -0.009156 | -0.1236 | 0.24261 | 0.14191 | 0.11902 | 0.1236 | 0.10071 | 0.073242 | -121.9528 | -121.8887 | 0.27008 | 0.2243 | 0.2655 | 0.15106 | 0.19226 | 0.2243 | 121.8796 | 0.19684 | 0.05951 | 121.994 | -0.004577 | 122.0123 | 0.068665 | -122.0032 | -121.9482 | 121.8979 | 0.13275 | 0.8606 | 0.20599
2847.9219 | 122.1222 | -0.09613 | 121.9711 | 0.0031279 | 0.00076478 | 0.054709 | 0.050238 | -0.0013373 | -0.0087756 | -0.0002456 | -0.005371 | 0.028299 | 0.057802 | 0.01057 | 0.015966 | 0.025246 | -0.0012753 | 0.83313 | 121.9299 | -0.054932 | 121.8155 | 0.14648 | 0.022888 | 0.045776 | 0.07782 | -0.027466 | -0.036621 | 0.032043 | 0.15106 | 0.13733 | 0.11902 | 0.041198 | -0.041198 | -0.15564 | 0.24261 | 0.14191 | 0.11902 | 0.10071 | 0.07782 | 0.059509 | -121.9986 | -121.9391 | 0.24719 | 0.21515 | 0.23346 | 0.15564 | 0.17395 | 0.20142 | 121.8704 | 0.18768 | 0.068664 | 121.9849 | 0.009155 | 122.0261 | 0.068664 | -122.0261 | -122.0078 | 121.9116 | 0.12817 | 0.92926 | 0.17395
2849.6719 | 121.9986 | -0.14191 | 121.994 | -0.012131 | 0.0039692 | 0.056204 | 0.053015 | 0.0031487 | -0.00963 | -0.0028092 | -0.0084228 | 0.030648 | 0.058443 | 0.011424 | 0.017034 | 0.026528 | -0.0049069 | 0.79193 | 121.9803 | -0.086975 | 121.7056 | -0.032043 | -0.15106 | -0.10986 | -0.073242 | 0.004578 | -0.050354 | -0.07782 | -0.013733 | -0.027466 | 0.018311 | 0.054932 | -0.013733 | -0.28839 | 0.10986 | 0.032044 | -0.009155 | -0.022888 | -0.064087 | 0.091553 | -121.9894 | -122.0718 | 0.12817 | 0.16022 | 0.11444 | 0.068665 | 0.022888 | 0.054932 | 121.7926 | 0.036621 | -0.027466 | 122.0673 | 0.054932 | 122.1222 | 0.14649 | -122.081 | -122.0444 | 121.8475 | 0.064087 | 0.93384 | 0.068665
2851.4375 | 122.0444 | -0.11902 | 121.9757 | -0.0045011 | 0.00076478 | 0.052573 | 0.050238 | -0.0019781 | -0.0094164 | -0.0013138 | -0.0084228 | 0.030862 | 0.058229 | 0.0056567 | 0.017461 | 0.023323 | -0.0046933 | 0.84228 | 121.9666 | -0.1236 | 121.7148 | -0.004578 | -0.091553 | -0.086975 | -0.059509 | 0 | -0.045776 | -0.073242 | 0.054932 | 0.018311 | 0.036621 | -0.004577 | -0.009155 | -0.26093 | 0.11444 | 0.032044 | 0.027466 | 0.036621 | 0.032043 | 0.073243 | -121.9757 | -122.0489 | 0.17395 | 0.15564 | 0.13733 | 0.082397 | 0.064087 | 0.11902 | 121.8384 | 0.10071 | -0.027466 | 122.0901 | 0.045776 | 122.0856 | 0.11902 | -122.0993 | -122.0215 | 121.8338 | 0.045777 | 0.9613 | 0.05951
2853.2031 | 121.994 | -0.10986 | 122.0078 | -0.01976 | 0.0043964 | 0.053 | 0.054083 | 0.0037897 | -0.0070666 | -0.0047318 | 0.0037842 | 0.030862 | 0.060579 | 0.0077929 | 0.014684 | 0.026314 | 0.0019289 | 0.85144 | 121.9757 | -0.091553 | 121.6965 | -0.032043 | -0.16022 | -0.11444 | -0.086975 | 0.022888 | -0.068665 | -0.082397 | 0.013733 | -0.018311 | 0.036621 | 0.01831 | -0.032043 | -0.31128 | 0.07782 | -0.004578 | -0.050354 | -0.022888 | -0.068664 | 0.041198 | -121.9849 | -122.0901 | 0.1236 | 0.14648 | 0.091552 | 0.10529 | 0.050354 | 0.05951 | 121.788 | 0.082398 | -0.013732 | 122.0673 | 0.091553 | 122.0856 | 0.13275 | -122.0993 | -122.0764 | 121.8063 | 0.027466 | 0.9613 | 0.022888
2854.9688 | 122.0261 | -0.10071 | 121.9849 | -0.01976 | 0.0048236 | 0.054922 | 0.052588 | 0.0031487 | -0.0062122 | -0.0062272 | -0.005371 | 0.031076 | 0.060366 | 0.010784 | 0.015966 | 0.024391 | -0.0014891 | 0.83771 | 121.9803 | -0.10071 | 121.6919 | -0.027466 | -0.16479 | -0.11902 | -0.041199 | 0.009155 | -0.059509 | -0.054932 | 0.013733 | -0.004578 | 0.036621 | 0 | -0.004577 | -0.29297 | 0.073242 | -0.018311 | -0.064087 | -0.018311 | -0.064087 | 0.041199 | -121.9757 | -122.0398 | 0.11444 | 0.13733 | 0.09613 | 0.09613 | 0.054931 | 0.073242 | 121.7926 | 0.073242 | 0.004577 | 122.081 | 0.068664 | 122.081 | 0.10986 | -122.0856 | -122.0444 | 121.7926 | 0.045776 | 0.93842 | 0.059509
2856.6875 | 122.0444 | -0.11902 | 121.962 | -0.012131 | 0.0054644 | 0.053427 | 0.053228 | 0.0061395 | -0.010485 | -0.0040908 | -0.005371 | 0.028299 | 0.061647 | 0.0018115 | 0.017034 | 0.02546 | -0.0066159 | 0.87433 | 121.9757 | -0.10529 | 121.6827 | -0.018311 | -0.15564 | -0.11444 | -0.050354 | 0.004578 | -0.054932 | -0.064087 | 0.013733 | -0.013733 | 0.036621 | 0.013733 | 0.013733 | -0.27924 | 0.10071 | 0.004578 | -0.036621 | -0.009155 | -0.050354 | 0.064087 | -121.9574 | -122.0261 | 0.13275 | 0.15564 | 0.10529 | 0.091553 | 0.041199 | 0.086975 | 121.788 | 0.068665 | -0.009155 | 122.081 | 0.05951 | 122.0947 | 0.1236 | -122.0673 | -122.0169 | 121.8018 | 0.054932 | 0.99335 | 0.068665
2858.4531 | 122.1542 | -0.068665 | 121.9391 | -0.0045011 | -8.9824e-05 | 0.053854 | 0.049811 | -0.0034735 | -0.0072802 | -0.0030228 | -0.0023192 | 0.028299 | 0.060366 | 0.0018115 | 0.013616 | 0.026314 | -0.0010617 | 0.89264 | 121.9208 | -0.073242 | 121.8063 | 0.14648 | 0.018311 | 0.045776 | 0.10071 | -0.027466 | -0.032043 | 0.045776 | 0.16937 | 0.16479 | 0.14191 | -0.004577 | -0.018311 | -0.13275 | 0.21515 | 0.11444 | 0.086976 | 0.11902 | 0.091553 | 0.036622 | -121.9666 | -121.8933 | 0.23804 | 0.21057 | 0.23346 | 0.17395 | 0.19684 | 0.21973 | 121.8796 | 0.20142 | 0.077819 | 121.994 | 0.004577 | 121.9894 | 0.041199 | -122.0123 | -121.9711 | 121.875 | 0.11444 | 0.9613 | 0.16937
2860.1562 | 122.1085 | -0.091553 | 121.9574 | -0.0045011 | 0.0026874 | 0.055136 | 0.048315 | 0.0010125 | -0.006853 | -0.0015274 | -0.014526 | 0.028939 | 0.060152 | 0.0013843 | 0.015325 | 0.024178 | -0.0042661 | 0.88348 | 121.9391 | -0.091553 | 121.7651 | 0.068665 | -0.041199 | 0 | 0.018311 | -0.027466 | -0.027466 | 0.009155 | 0.11902 | 0.11444 | 0.11902 | 0 | -0.01831 | -0.19226 | 0.16022 | 0.091553 | 0.050354 | 0.091553 | 0.050354 | 0.064087 | -121.9849 | -121.9482 | 0.21057 | 0.21057 | 0.20599 | 0.14649 | 0.14191 | 0.16022 | 121.8567 | 0.14649 | 0.036621 | 122.0306 | 0 | 122.0306 | 0.064087 | -122.049 | -121.9849 | 121.8567 | 0.10071 | 0.97504 | 0.10986
2861.9219 | 122.0078 | -0.13733 | 121.9894 | -0.0045011 | 0.00055118 | 0.052145 | 0.05152 | 0.0012261 | -0.0074938 | -0.0030228 | 0.00073235 | 0.03193 | 0.062929 | -0.0011791 | 0.016607 | 0.025673 | 0.00064735 | 0.9613 | 121.9574 | -0.10986 | 121.6919 | 0 | -0.10529 | -0.073242 | -0.059509 | 0 | -0.054932 | -0.07782 | 0.022888 | 0.022888 | 0.022888 | 0.027466 | -0.032044 | -0.29755 | 0.13733 | 0.064087 | 0.032043 | 0.036621 | 0.004577 | 0.082397 | -121.9894 | -122.0673 | 0.16022 | 0.16022 | 0.16022 | 0.07782 | 0.07782 | 0.10986 | 121.8018 | 0.07782 | -0.022888 | 122.0673 | 0.054932 | 122.0947 | 0.13733 | -122.0993 | -122.0444 | 121.8292 | 0.059509 | 1.0986 | 0.07782
2863.625 | 122.1222 | -0.086975 | 121.9482 | -0.0045011 | 0.0014056 | 0.050864 | 0.048742 | -0.0013373 | -0.0098438 | -0.0021682 | -0.005371 | 0.027658 | 0.059084 | 0.0020251 | 0.015112 | 0.023751 | -0.0034117 | 1.0345 | 121.8933 | -0.064087 | 121.8338 | 0.14191 | 0.013733 | 0.050354 | 0.07782 | -0.018311 | -0.018311 | 0.013733 | 0.14648 | 0.13275 | 0.11902 | 0.022888 | -0.054931 | -0.11444 | 0.22888 | 0.13733 | 0.10071 | 0.11444 | 0.07782 | 0.068664 | -121.9666 | -121.9345 | 0.23346 | 0.20599 | 0.21973 | 0.13733 | 0.15106 | 0.20599 | 121.8979 | 0.16479 | 0.032044 | 121.9574 | 0 | 121.9803 | 0.068664 | -122.0123 | -121.9666 | 121.9208 | 0.10071 | 1.1215 | 0.16479
2865.3906 | 122.0169 | -0.13733 | 121.994 | -0.0045011 | 0.0058918 | 0.053214 | 0.053015 | 0.0022943 | -0.0077074 | -0.0021682 | -0.005371 | 0.03193 | 0.061861 | 0.0075793 | 0.017034 | 0.0261 | -0.0021299 | 1.0208 | 121.9849 | -0.09613 | 121.7056 | -0.027466 | -0.15564 | -0.10529 | -0.068665 | 0 | -0.045776 | -0.07782 | 0.009155 | -0.009155 | 0.018311 | 0.041199 | -0.009156 | -0.28839 | 0.10986 | 0.032043 | -0.018311 | -0.009156 | -0.05951 | 0.091553 | -121.994 | -122.0718 | 0.14648 | 0.15564 | 0.12817 | 0.064087 | 0.036621 | 0.068664 | 121.8018 | 0.054931 | -0.032044 | 122.081 | 0.045776 | 122.1222 | 0.13733 | -122.0901 | -122.0398 | 121.843 | 0.059509 | 1.1581 | 0.068664
2867.0938 | 122.1359 | -0.073242 | 121.9345 | -0.01976 | 0.0052508 | 0.054495 | 0.05152 | 0.0029351 | -0.0062122 | -0.0055862 | -0.0023192 | 0.028085 | 0.060152 | 0.0099293 | 0.013616 | 0.025246 | -0.0040525 | 1.0803 | 121.9528 | -0.064087 | 121.8201 | 0.13733 | -0.022888 | 0.027466 | 0.11902 | -0.050354 | -0.009155 | 0.073242 | 0.16479 | 0.13733 | 0.13733 | 0.009155 | 0.018311 | -0.11444 | 0.21057 | 0.10071 | 0.050354 | 0.091553 | 0.041199 | 0.064087 | -121.9849 | -121.8613 | 0.23804 | 0.21057 | 0.21057 | 0.14648 | 0.14648 | 0.20142 | 121.8842 | 0.17395 | 0.082397 | 122.0169 | -0.041199 | 122.0261 | 0.022888 | -121.9986 | -121.9437 | 121.8933 | 0.14648 | 1.1536 | 0.19226
2868.875 | 122.1176 | -0.10071 | 121.962 | -0.012131 | 0.0041828 | 0.055777 | 0.051306 | 0.0025079 | -0.0064258 | -0.0030228 | -0.005371 | 0.028939 | 0.058443 | 0.0073657 | 0.015752 | 0.025246 | 0.0010745 | 1.1032 | 121.9208 | -0.068665 | 121.8155 | 0.1236 | -0.036621 | 0.045776 | 0.11902 | -0.022888 | -0.013733 | 0.054932 | 0.14191 | 0.11902 | 0.1236 | 0.032043 | -0.041199 | -0.14648 | 0.2243 | 0.14648 | 0.064087 | 0.11444 | 0.032044 | 0.086975 | -121.9849 | -121.907 | 0.24262 | 0.2243 | 0.21973 | 0.13733 | 0.13275 | 0.19226 | 121.8842 | 0.15564 | 0.068665 | 121.9894 | -0.009155 | 122.0215 | 0.07782 | -122.0306 | -121.9757 | 121.9162 | 0.15564 | 1.2039 | 0.21973
2870.6406 | 122.0581 | -0.12817 | 122.0032 | -0.012131 | 0.00097838 | 0.053214 | 0.051947 | 0.0014397 | -0.011553 | -0.000673 | -0.0084228 | 0.031076 | 0.060793 | 0.01527 | 0.014043 | 0.023323 | -0.0034117 | 1.1536 | 121.9482 | -0.10986 | 121.7056 | -0.013733 | -0.10529 | -0.091553 | -0.054932 | 0.009155 | -0.054932 | -0.064087 | 0.050354 | 0.036621 | 0.082397 | 0.018311 | -0.054932 | -0.29755 | 0.11444 | 0.036621 | 0.022888 | 0.01831 | 0.004577 | 0.073242 | -121.994 | -122.0673 | 0.17853 | 0.21057 | 0.1648 | 0.13733 | 0.091553 | 0.09613 | 121.8155 | 0.10529 | -0.009155 | 122.0581 | 0.064087 | 122.0764 | 0.13733 | -122.113 | -122.0581 | 121.8338 | 0.064087 | 1.2817 | 0.073242
2872.3281 | 122.0901 | -0.086975 | 121.9482 | -0.01976 | 0.0026874 | 0.053214 | 0.048529 | -5.5462e-05 | -0.008562 | -0.00345 | -0.005371 | 0.027658 | 0.061647 | 0.0045887 | 0.01383 | 0.024178 | -0.0036253 | 1.1307 | 121.9482 | -0.059509 | 121.7606 | 0.07782 | -0.050354 | -0.013733 | 0.022888 | -0.036621 | -0.027466 | 0.004578 | 0.09613 | 0.086975 | 0.07782 | 0.027466 | 0 | -0.18768 | 0.16479 | 0.073242 | 0.036621 | 0.045776 | 0.009155 | 0.059509 | -121.9849 | -121.9437 | 0.1831 | 0.16479 | 0.17395 | 0.10529 | 0.11444 | 0.13733 | 121.8201 | 0.1236 | 0.032044 | 122.0078 | -0.009155 | 122.0352 | 0.050354 | -122.0078 | -121.9757 | 121.8475 | 0.091553 | 1.2177 | 0.10986
2874.0938 | 122.0169 | -0.11902 | 121.9894 | -0.012131 | 0.0067462 | 0.054282 | 0.052588 | -0.0019781 | -0.0083484 | -0.0011002 | -0.005371 | 0.031503 | 0.061007 | 0.01057 | 0.018102 | 0.024605 | -0.0014891 | 1.2131 | 121.962 | -0.091553 | 121.6919 | -0.041199 | -0.16022 | -0.11902 | -0.07782 | 0.009155 | -0.059509 | -0.068665 | 0 | -0.032043 | 0.013733 | 0.027466 | -0.027466 | -0.29755 | 0.07782 | 0 | -0.041198 | -0.027466 | -0.068664 | 0.05951 | -121.9803 | -122.0581 | 0.11902 | 0.13275 | 0.086976 | 0.073242 | 0.027466 | 0.050354 | 121.7834 | 0.059509 | -0.009156 | 122.0535 | 0.068664 | 122.081 | 0.12817 | -122.081 | -122.049 | 121.8109 | 0.050354 | 1.3321 | 0.041199
2875.8438 | 122.0947 | -0.086975 | 121.9757 | 0.0031279 | 0.0016192 | 0.052359 | 0.05152 | -0.00091006 | -0.0083484 | -0.005159 | -0.0023192 | 0.029153 | 0.059298 | 0.0035205 | 0.016393 | 0.026955 | -0.0031979 | 1.2131 | 121.9437 | -0.068665 | 121.7651 | 0.07782 | -0.054932 | -0.022888 | 0.018311 | -0.041199 | -0.036621 | -0.004578 | 0.091553 | 0.091553 | 0.086975 | 0.01831 | -0.032043 | -0.21057 | 0.16479 | 0.064087 | 0.032043 | 0.045777 | 0.013733 | 0.050354 | -122.0169 | -121.9803 | 0.17853 | 0.17395 | 0.17853 | 0.1236 | 0.12817 | 0.14649 | 121.8338 | 0.12817 | 0.032043 | 122.0123 | -0.004578 | 122.0306 | 0.045776 | -122.0444 | -122.0123 | 121.8521 | 0.082397 | 1.3 | 0.10529
2877.6094 | 122.0215 | -0.11444 | 121.9711 | -0.012131 | 0.0058918 | 0.053854 | 0.054297 | 0.00015814 | -0.010698 | 0.001677 | -0.0023192 | 0.030862 | 0.060366 | 0.0097157 | 0.017248 | 0.0261 | -0.0051205 | 1.3779 | 121.9482 | -0.086975 | 121.7606 | 0.050354 | -0.073242 | -0.059509 | -0.004578 | -0.013733 | -0.041199 | -0.027466 | 0.059509 | 0.022888 | 0.068665 | 0.027466 | -0.022888 | -0.21057 | 0.16479 | 0.054932 | 0.041199 | 0.027466 | 0.013733 | 0.073242 | -121.9849 | -121.9986 | 0.17395 | 0.18311 | 0.13733 | 0.10986 | 0.064087 | 0.13733 | 121.8475 | 0.10071 | 0.013733 | 122.0352 | 0.027466 | 122.0627 | 0.10071 | -122.0581 | -122.0123 | 121.875 | 0.086975 | 1.4923 | 0.10986
2879.2969 | 122.1176 | -0.09613 | 121.9574 | -0.0045011 | 0.0043964 | 0.054709 | 0.049811 | 0.0012261 | -0.0092028 | -0.0015274 | -0.0023192 | 0.028726 | 0.060579 | 0.0015979 | 0.013616 | 0.026741 | -0.0036253 | 1.3321 | 121.9574 | -0.086975 | 121.7697 | 0.091553 | -0.045776 | -0.009155 | 0.027466 | -0.022888 | -0.036621 | 0.018311 | 0.12817 | 0.11902 | 0.10529 | 0.009155 | 0 | -0.18768 | 0.18768 | 0.086975 | 0.050354 | 0.07782 | 0.041199 | 0.059509 | -121.9803 | -121.9391 | 0.2243 | 0.20142 | 0.21515 | 0.14191 | 0.15564 | 0.17853 | 121.8567 | 0.1648 | 0.054932 | 122.0444 | 0.013733 | 122.0535 | 0.073242 | -122.0444 | -121.994 | 121.8658 | 0.11444 | 1.4282 | 0.1236
2881.0625 | 122.0123 | -0.13275 | 121.9849 | -0.0045011 | 0.0022602 | 0.052573 | 0.052374 | -0.0011237 | -0.010698 | -0.0040908 | -0.011475 | 0.030862 | 0.060152 | 0.0058703 | 0.016821 | 0.024391 | -0.0014891 | 1.3962 | 121.9482 | -0.09613 | 121.6873 | -0.013733 | -0.10986 | -0.09613 | -0.054932 | 0.022888 | -0.068665 | -0.09613 | 0.027466 | 0.018311 | 0.022888 | 0.036621 | -0.036621 | -0.29755 | 0.11902 | 0.036621 | 0.022888 | 0 | -0.013733 | 0.064086 | -121.962 | -122.081 | 0.16022 | 0.15564 | 0.15106 | 0.091553 | 0.086976 | 0.082397 | 121.7834 | 0.096131 | -0.027465 | 122.0444 | 0.091553 | 122.081 | 0.15564 | -122.081 | -122.0535 | 121.8201 | 0.036621 | 1.5289 | 0.077819
2882.8281 | 122.0306 | -0.13275 | 121.9528 | -0.0045011 | 0.0054644 | 0.055563 | 0.052588 | 0.0040033 | -0.0092028 | -0.0032364 | -0.005371 | 0.032357 | 0.062075 | 0.011638 | 0.017248 | 0.023751 | -0.0055479 | 1.4465 | 122.0078 | -0.09613 | 121.6919 | -0.032043 | -0.15106 | -0.10986 | -0.064087 | 0.009155 | -0.050354 | -0.068665 | 0.004578 | -0.009155 | 0.027466 | 0.036621 | 0.054931 | -0.26093 | 0.10071 | 0.022888 | -0.018311 | -0.013733 | -0.054932 | 0.082397 | -121.9437 | -122.0215 | 0.13733 | 0.16022 | 0.1236 | 0.07782 | 0.041199 | 0.064087 | 121.788 | 0.054932 | -0.018311 | 122.1039 | 0.059509 | 122.1405 | 0.14191 | -122.049 | -122.0032 | 121.8246 | 0.064086 | 1.5793 | 0.068664
2884.5312 | 121.9986 | -0.11902 | 121.9849 | -0.01976 | 0.00076478 | 0.053427 | 0.051092 | 0.00058534 | -0.0087756 | -0.0019546 | -0.0084228 | 0.030435 | 0.062716 | 0.0077929 | 0.015966 | 0.026741 | -0.0014891 | 1.5198 | 121.9437 | -0.091553 | 121.6919 | 0.013733 | -0.10529 | -0.082397 | -0.054932 | 0.004578 | -0.059509 | -0.091553 | 0.027466 | 0.009155 | 0.013733 | 0.027466 | -0.041198 | -0.29297 | 0.13275 | 0.036622 | 0.013733 | 0.009156 | -0.013733 | 0.05951 | -121.9803 | -122.0764 | 0.14649 | 0.13275 | 0.12817 | 0.073242 | 0.068664 | 0.10529 | 121.7834 | 0.086975 | -0.032044 | 122.0352 | 0.064087 | 122.0627 | 0.1236 | -122.0764 | -122.0444 | 121.8109 | 0.027466 | 1.6388 | 0.064087
2886.2969 | 122.1176 | -0.082397 | 121.9437 | -0.012131 | 0.0037556 | 0.055991 | 0.049597 | 0.00037174 | -0.0074938 | -0.0002456 | -0.005371 | 0.028512 | 0.063356 | 0.0065113 | 0.014471 | 0.02546 | -0.0036253 | 1.5884 | 121.9254 | -0.050354 | 121.8109 | 0.15106 | -0.022888 | 0.018311 | 0.10986 | -0.032043 | -0.009155 | 0.041199 | 0.12817 | 0.11902 | 0.10071 | 0.032043 | -0.018311 | -0.13275 | 0.23346 | 0.10071 | 0.059509 | 0.068665 | 0.027466 | 0.073242 | -121.9757 | -121.9025 | 0.21057 | 0.18311 | 0.20142 | 0.10986 | 0.12817 | 0.20142 | 121.8613 | 0.13733 | 0.050354 | 121.9757 | -0.022888 | 122.0078 | 0.050354 | -121.994 | -121.9528 | 121.8933 | 0.1236 | 1.6708 | 0.19226
2888.0625 | 122.049 | -0.11444 | 121.9482 | -0.012131 | 0.0026874 | 0.053427 | 0.049383 | 0.0016535 | -0.0089892 | -0.0015274 | -0.0023192 | 0.031076 | 0.062716 | 0.0022389 | 0.014043 | 0.023751 | -0.0031979 | 1.7075 | 121.9208 | -0.068665 | 121.7972 | 0.10529 | -0.018311 | -0.004578 | 0.027466 | -0.027466 | -0.036621 | -0.032043 | 0.091553 | 0.054932 | 0.059509 | 0.045776 | -0.027466 | -0.15106 | 0.21973 | 0.10986 | 0.09613 | 0.064087 | 0.050354 | 0.07782 | -121.9757 | -121.9803 | 0.20599 | 0.17395 | 0.16937 | 0.09613 | 0.091553 | 0.17395 | 121.8658 | 0.12817 | 0.004578 | 121.9894 | 0.009155 | 122.0352 | 0.086975 | -122.0169 | -121.9849 | 121.9116 | 0.082398 | 1.8219 | 0.14191
2889.8281 | 122.0901 | -0.11444 | 121.9391 | -0.012131 | 0.0039692 | 0.054495 | 0.049597 | -5.5462e-05 | -0.0083484 | -0.002382 | -0.005371 | 0.030435 | 0.063143 | 0.0033069 | 0.014471 | 0.026955 | 0.00043375 | 1.6891 | 121.9299 | -0.045776 | 121.7606 | 0.10529 | -0.068665 | -0.018311 | 0.045776 | -0.036621 | -0.041199 | 0 | 0.10071 | 0.09613 | 0.082397 | 0.068665 | -0.009155 | -0.17853 | 0.21973 | 0.09613 | 0.045776 | 0.027465 | -0.022889 | 0.073242 | -121.9757 | -121.9391 | 0.21515 | 0.19684 | 0.21057 | 0.1236 | 0.13733 | 0.15106 | 121.8063 | 0.14191 | 0.041199 | 121.9757 | 0.004578 | 122.0444 | 0.07782 | -121.9849 | -121.9803 | 121.875 | 0.11444 | 1.8036 | 0.16022
2891.5469 | 122.1497 | -0.082397 | 121.9482 | -0.01976 | -0.00094422 | 0.05065 | 0.050451 | -0.00069646 | -0.0077074 | -0.0032364 | -0.0023192 | 0.028726 | 0.062288 | 0.0065113 | 0.014257 | 0.025032 | -0.0070433 | 1.799 | 121.9162 | -0.068665 | 121.8246 | 0.16479 | 0.022888 | 0.050354 | 0.12817 | -0.027466 | -0.022888 | 0.059509 | 0.18768 | 0.18768 | 0.13733 | 0.013732 | -0.032043 | -0.1236 | 0.24719 | 0.13275 | 0.10528 | 0.11902 | 0.091553 | 0.059509 | -121.9757 | -121.8887 | 0.27008 | 0.21973 | 0.27008 | 0.16022 | 0.21057 | 0.23346 | 121.8933 | 0.21057 | 0.082397 | 121.9849 | -0.004578 | 121.9986 | 0.054931 | -122.0169 | -121.9711 | 121.907 | 0.14191 | 1.8814 | 0.21057
2893.3125 | 121.994 | -0.10529 | 121.9711 | 0.0031279 | 0.0033282 | 0.052359 | 0.052588 | 0.0027215 | -0.0077074 | -0.0002456 | -0.005371 | 0.031717 | 0.063784 | 0.0082203 | 0.018316 | 0.022469 | -0.0042661 | 1.8997 | 121.9482 | -0.082397 | 121.7285 | 0.032043 | -0.11902 | -0.07782 | -0.018311 | 0.009155 | -0.045776 | -0.064087 | 0.032043 | 0 | 0.027466 | 0.022889 | -0.022888 | -0.24261 | 0.13733 | 0.027466 | -0.013733 | 0.004577 | -0.036622 | 0.05951 | -121.962 | -122.0352 | 0.13733 | 0.13275 | 0.10529 | 0.073242 | 0.045776 | 0.11444 | 121.8109 | 0.077819 | -0.018311 | 122.0306 | 0.054931 | 122.0535 | 0.11444 | -122.0535 | -122.0169 | 121.8338 | 0.041199 | 2.005 | 0.086975
2895.0625 | 122.1085 | -0.082397 | 121.9528 | -0.01976 | 0.00033758 | 0.052359 | 0.049383 | -0.0032599 | -0.010271 | -0.002382 | -0.005371 | 0.02723 | 0.063143 | 0.0056567 | 0.013403 | 0.024605 | -0.0049069 | 1.9958 | 121.9482 | -0.068665 | 121.8201 | 0.15564 | 0.022888 | 0.036621 | 0.09613 | -0.050354 | -0.027466 | 0.036621 | 0.16479 | 0.14191 | 0.1236 | 0.013732 | -0.004578 | -0.13275 | 0.23804 | 0.11902 | 0.10528 | 0.10529 | 0.091553 | 0.054931 | -122.0032 | -121.9162 | 0.24719 | 0.20599 | 0.2243 | 0.15106 | 0.16937 | 0.22431 | 121.8887 | 0.19226 | 0.064087 | 122.0169 | -0.022888 | 122.0306 | 0.032043 | -122.0215 | -121.9803 | 121.9025 | 0.11902 | 2.0782 | 0.17853
2896.7656 | 122.1222 | -0.082397 | 121.9528 | -0.0045011 | 0.00076478 | 0.052786 | 0.050879 | -0.0041145 | -0.011339 | -0.002382 | -0.0023192 | 0.030435 | 0.063143 | 0.0077929 | 0.014043 | 0.026528 | -0.0025571 | 2.0416 | 121.907 | -0.059509 | 121.8338 | 0.16022 | 0.032043 | 0.036621 | 0.10529 | -0.036621 | -0.027466 | 0.032043 | 0.16479 | 0.14191 | 0.12817 | 0.022888 | -0.045777 | -0.11902 | 0.24261 | 0.11902 | 0.11444 | 0.09613 | 0.091552 | 0.054931 | -121.9894 | -121.9208 | 0.24719 | 0.21057 | 0.2243 | 0.15564 | 0.16937 | 0.21973 | 121.8933 | 0.19226 | 0.059509 | 121.9666 | -0.009155 | 121.9894 | 0.045776 | -122.0123 | -121.9803 | 121.9162 | 0.11444 | 2.124 | 0.18768
2898.5312 | 122.1176 | -0.09613 | 121.9482 | -0.012131 | 0.0056782 | 0.054922 | 0.051947 | -0.0030463 | -0.0066394 | -0.0004592 | -0.0023192 | 0.030435 | 0.064211 | 0.0060841 | 0.017034 | 0.023964 | -0.0027707 | 2.0737 | 121.9574 | -0.086975 | 121.7422 | 0.068665 | -0.10071 | -0.050354 | 0.045776 | -0.027466 | -0.041199 | 0.036621 | 0.1236 | 0.11444 | 0.12817 | 0.009155 | 0.009155 | -0.20599 | 0.16479 | 0.045776 | -0.004578 | 0.036621 | -0.013733 | 0.054931 | -121.9757 | -121.9116 | 0.21973 | 0.2243 | 0.21057 | 0.16937 | 0.15564 | 0.15564 | 121.8292 | 0.16479 | 0.07782 | 122.0444 | 0.013733 | 122.0535 | 0.068664 | -122.0352 | -121.9894 | 121.8384 | 0.13275 | 2.1698 | 0.14191
2900.2969 | 122.1222 | -0.07782 | 121.9345 | -0.012131 | 0.001192 | 0.053 | 0.04917 | -5.5462e-05 | -0.0094164 | -0.000673 | -0.0084228 | 0.030008 | 0.062502 | 0.0099293 | 0.01383 | 0.024391 | -0.0036253 | 2.1469 | 121.9116 | -0.054932 | 121.7926 | 0.10529 | -0.009155 | 0 | 0.068665 | -0.018311 | -0.009155 | 0.045776 | 0.16479 | 0.15106 | 0.10986 | 0.022888 | -0.022888 | -0.14191 | 0.18311 | 0.07782 | 0.068665 | 0.054932 | 0.045777 | 0.068665 | -121.9528 | -121.8887 | 0.24261 | 0.18768 | 0.22888 | 0.11902 | 0.16022 | 0.16022 | 121.8475 | 0.17395 | 0.054931 | 121.9666 | -0.009156 | 121.9894 | 0.059509 | -121.9894 | -121.9437 | 121.8704 | 0.1236 | 2.2247 | 0.14649
2902.0625 | 122.1313 | -0.07782 | 121.9162 | 0.0031279 | 0.0048236 | 0.056418 | 0.05451 | 0.0010125 | -0.0066394 | -0.0077224 | -0.005371 | 0.029794 | 0.065065 | 0.0088611 | 0.018102 | 0.024391 | -0.0029843 | 2.243 | 121.9574 | -0.064087 | 121.7651 | 0.082397 | -0.064087 | -0.032043 | 0.07782 | -0.036621 | -0.036621 | 0.050354 | 0.13275 | 0.10529 | 0.13275 | 0.013733 | 0.041198 | -0.15106 | 0.16022 | 0.045777 | 0.013733 | 0.032044 | 0 | 0.041199 | -121.9528 | -121.8658 | 0.21057 | 0.21057 | 0.18311 | 0.16937 | 0.14191 | 0.14648 | 121.8292 | 0.16937 | 0.086975 | 122.0215 | 0 | 122.0352 | 0.041199 | -121.9803 | -121.9528 | 121.843 | 0.12817 | 2.3209 | 0.15564
2903.8281 | 121.9986 | -0.11902 | 122.0169 | -0.012131 | 0.0043964 | 0.053641 | 0.056646 | 0.0025079 | -0.0077074 | -0.0038772 | -0.005371 | 0.031076 | 0.065065 | 0.010997 | 0.017461 | 0.023751 | -0.0021299 | 2.3575 | 121.9528 | -0.091553 | 121.7056 | -0.013733 | -0.14648 | -0.11902 | -0.068665 | -0.009155 | -0.054932 | -0.064087 | 0 | -0.018311 | 0.018311 | 0.027466 | -0.064087 | -0.31128 | 0.10529 | 0 | -0.027465 | -0.027466 | -0.054931 | 0.064087 | -122.0261 | -122.081 | 0.11902 | 0.13733 | 0.10071 | 0.073243 | 0.036621 | 0.07782 | 121.7972 | 0.054932 | -0.009155 | 122.0444 | 0.045777 | 122.0718 | 0.10986 | -122.1085 | -122.0718 | 121.8246 | 0.054932 | 2.4765 | 0.050354
2905.5156 | 122.1313 | -0.10529 | 121.9437 | -0.012131 | 0.0031146 | 0.054922 | 0.051306 | 0.0040033 | -0.0094164 | -0.001741 | -0.005371 | 0.029153 | 0.066988 | 0.0052295 | 0.017889 | 0.024605 | -0.0017027 | 2.4033 | 121.9528 | -0.068665 | 121.7697 | 0.091553 | -0.022888 | 0.004578 | 0.059509 | -0.036621 | -0.036621 | 0.013733 | 0.14191 | 0.13275 | 0.1236 | 0.036621 | 0.009155 | -0.17395 | 0.19684 | 0.10986 | 0.082398 | 0.073243 | 0.045777 | 0.068665 | -121.9803 | -121.9299 | 0.24719 | 0.22888 | 0.23804 | 0.16022 | 0.16937 | 0.16022 | 121.8384 | 0.17853 | 0.050354 | 122.0215 | 0 | 122.0581 | 0.068665 | -122.0123 | -121.9803 | 121.875 | 0.11902 | 2.5085 | 0.16479
2907.2812 | 122.0306 | -0.1236 | 121.9711 | -0.0045011 | -0.00051702 | 0.051932 | 0.05216 | -0.0013373 | -0.010698 | -0.0013138 | -0.0084228 | 0.033639 | 0.06592 | 0.0092883 | 0.015112 | 0.023751 | -0.0042661 | 2.5177 | 121.9574 | -0.091553 | 121.6965 | -0.004578 | -0.11444 | -0.091553 | -0.064087 | 0.018311 | -0.059509 | -0.064087 | 0.036621 | 0.018311 | 0.045776 | 0.032043 | -0.013733 | -0.27466 | 0.11902 | 0.032043 | 0.009155 | 0 | -0.022888 | 0.064087 | -121.9528 | -122.0352 | 0.16022 | 0.16937 | 0.14191 | 0.10528 | 0.07782 | 0.086975 | 121.788 | 0.09613 | -0.004578 | 122.049 | 0.07782 | 122.081 | 0.14191 | -122.0627 | -122.0306 | 121.8201 | 0.059509 | 2.6413 | 0.059509
2909.0469 | 122.1405 | -0.068665 | 121.9391 | -0.012131 | 0.0037556 | 0.055136 | 0.050665 | 0.00015814 | -0.0081348 | -0.005159 | -0.0084228 | 0.029794 | 0.06122 | 0.011852 | 0.017675 | 0.024819 | -0.0040525 | 2.6505 | 121.9391 | -0.045776 | 121.8201 | 0.15106 | -0.013733 | 0.027466 | 0.11902 | -0.036621 | -0.022888 | 0.073242 | 0.15564 | 0.13733 | 0.12817 | 0.022889 | 0 | -0.11902 | 0.21973 | 0.096131 | 0.054932 | 0.073242 | 0.032043 | 0.045777 | -121.9757 | -121.8658 | 0.22431 | 0.19684 | 0.20599 | 0.15106 | 0.16022 | 0.19684 | 121.8658 | 0.17853 | 0.09613 | 121.9849 | -0.013733 | 122.0078 | 0.032044 | -121.9849 | -121.962 | 121.8887 | 0.14191 | 2.7191 | 0.18768
2910.75 | 122.0123 | -0.1236 | 121.9528 | -0.012131 | 0.0043964 | 0.054709 | 0.052588 | 0.0022943 | -0.012194 | -0.0013138 | -0.0084228 | 0.033639 | 0.065493 | 0.0090747 | 0.018102 | 0.025246 | -0.0023435 | 2.7603 | 121.9574 | -0.068665 | 121.7102 | 0.036621 | -0.13275 | -0.10071 | -0.027466 | 0 | -0.050354 | -0.045776 | 0.027466 | -0.004578 | 0.036621 | 0.054931 | 0.004577 | -0.24262 | 0.16022 | 0.022888 | -0.009155 | -0.032043 | -0.064086 | 0.073242 | -121.9528 | -121.9986 | 0.15106 | 0.16022 | 0.11902 | 0.086975 | 0.045776 | 0.10529 | 121.7789 | 0.07782 | 0.004578 | 122.0261 | 0.050354 | 122.081 | 0.1236 | -122.0215 | -122.0032 | 121.8338 | 0.07782 | 2.8839 | 0.09613
2912.5312 | 122.0444 | -0.13733 | 121.9757 | -0.012131 | -0.00073062 | 0.052145 | 0.04917 | -0.0028327 | -0.0081348 | -0.0025956 | -0.005371 | 0.029367 | 0.063997 | 0.0039477 | 0.015112 | 0.0261 | -0.0010617 | 2.8748 | 121.9254 | -0.054932 | 121.7789 | 0.10529 | -0.027466 | -0.013733 | 0.009155 | -0.004578 | -0.032043 | -0.050354 | 0.059509 | 0.045776 | 0.041199 | 0.082397 | -0.050354 | -0.19684 | 0.24262 | 0.1236 | 0.10986 | 0.041199 | 0.027466 | 0.10529 | -121.9803 | -122.0261 | 0.19684 | 0.17853 | 0.18311 | 0.073242 | 0.077819 | 0.16022 | 121.8338 | 0.091552 | -0.018311 | 121.9803 | 0.027465 | 122.0627 | 0.13275 | -122.0306 | -122.0078 | 121.9162 | 0.086975 | 3.0121 | 0.14648
2914.2969 | 122.0398 | -0.10529 | 121.9437 | -0.01976 | 0.0043964 | 0.054068 | 0.052588 | 0.0022943 | -0.0081348 | -0.0049454 | 0.00073235 | 0.031503 | 0.067415 | 0.01292 | 0.017889 | 0.025887 | -0.0025571 | 3.0029 | 121.962 | -0.073242 | 121.7606 | 0.073242 | -0.082397 | -0.050354 | 0.027466 | 0.004578 | -0.041199 | -0.004578 | 0.068665 | 0.036621 | 0.059509 | 0.032044 | 0.01831 | -0.18311 | 0.17853 | 0.054932 | 0.022889 | 0.022888 | -0.009155 | 0.064087 | -121.9391 | -121.9482 | 0.17395 | 0.16479 | 0.14191 | 0.10071 | 0.07782 | 0.14648 | 121.8338 | 0.10986 | 0.036621 | 122.0352 | 0.045777 | 122.0673 | 0.10986 | -122.0169 | -121.9849 | 121.8658 | 0.10071 | 3.1082 | 0.13275
2916.0156 | 121.994 | -0.11444 | 121.9849 | -0.012131 | 0.0041828 | 0.053427 | 0.05216 | -0.00048286 | -0.0072802 | -0.0030228 | -0.0023192 | 0.032785 | 0.06592 | 0.0060841 | 0.015752 | 0.025673 | -0.0040525 | 3.0304 | 121.9849 | -0.091553 | 121.6965 | -0.027466 | -0.14648 | -0.11444 | -0.073242 | 0.009155 | -0.045776 | -0.091553 | -0.004578 | -0.036621 | 0.009155 | 0.022888 | 0 | -0.28839 | 0.086975 | 0 | -0.032043 | -0.022888 | -0.054931 | 0.068665 | -121.9757 | -122.0764 | 0.10986 | 0.1236 | 0.07782 | 0.054931 | 0.009155 | 0.064087 | 121.788 | 0.041198 | -0.045777 | 122.0764 | 0.054931 | 122.0993 | 0.1236 | -122.0764 | -122.0306 | 121.8109 | 0.022888 | 3.1448 | 0.041199
2917.7188 | 122.0123 | -0.11902 | 121.9894 | -0.0045011 | -0.00030342 | 0.052145 | 0.047674 | -5.5462e-05 | -0.006853 | -0.0036636 | -0.0084228 | 0.028939 | 0.066347 | 0.0075793 | 0.015325 | 0.025887 | -0.0064023 | 3.1815 | 121.9299 | -0.07782 | 121.7468 | 0.091553 | -0.050354 | -0.004578 | -0.013733 | 0.004578 | -0.018311 | -0.054932 | 0.050354 | 0.054932 | 0.022888 | 0.041199 | -0.059509 | -0.24262 | 0.21057 | 0.11444 | 0.068665 | 0.073242 | 0.027466 | 0.10071 | -121.9849 | -122.0444 | 0.16937 | 0.14191 | 0.17395 | 0.041199 | 0.073243 | 0.16937 | 121.8246 | 0.068665 | -0.036621 | 122.0078 | 0.022889 | 122.049 | 0.1236 | -122.0673 | -122.0078 | 121.8658 | 0.064087 | 3.3005 | 0.10529
2919.4219 | 122.1222 | -0.07782 | 121.9391 | -0.0045011 | -0.00094422 | 0.054495 | 0.048956 | -0.0051825 | -0.008562 | -0.002382 | -0.005371 | 0.030862 | 0.06592 | 0.0050159 | 0.014043 | 0.025673 | 0.0029971 | 3.186 | 121.9162 | -0.068665 | 121.7743 | 0.11902 | -0.018311 | 0.004578 | 0.041199 | -0.032043 | -0.032043 | 0.022888 | 0.15106 | 0.13275 | 0.12817 | 0.009155 | -0.022888 | -0.16479 | 0.19684 | 0.082398 | 0.059509 | 0.073243 | 0.050354 | 0.045777 | -121.9711 | -121.9162 | 0.22888 | 0.20599 | 0.21057 | 0.16022 | 0.16479 | 0.18768 | 121.843 | 0.18311 | 0.054931 | 121.9849 | 0 | 121.994 | 0.045777 | -122.0078 | -121.9711 | 121.8521 | 0.10071 | 3.2639 | 0.11902
2921.1875 | 122.0078 | -0.13733 | 121.9894 | -0.012131 | 0.0035418 | 0.05535 | 0.051092 | -0.00026906 | -0.005144 | -0.002382 | -0.005371 | 0.030221 | 0.064424 | 0.0058703 | 0.017889 | 0.022896 | -0.0049069 | 3.3188 | 121.9849 | -0.09613 | 121.6599 | -0.027466 | -0.16022 | -0.12817 | -0.064087 | 0.009155 | -0.045776 | -0.064087 | 0 | -0.009155 | 0.027466 | 0.041199 | -0.004578 | -0.32959 | 0.10986 | 0.009155 | -0.022888 | -0.032044 | -0.064087 | 0.091553 | -121.9803 | -122.0535 | 0.13733 | 0.16479 | 0.12817 | 0.073242 | 0.036621 | 0.068664 | 121.756 | 0.045776 | -0.018311 | 122.081 | 0.054931 | 122.1222 | 0.14648 | -122.0856 | -122.0352 | 121.7972 | 0.073242 | 3.4561 | 0.073242
2922.9531 | 122.1085 | -0.07782 | 121.9299 | -0.012131 | 0.0037556 | 0.051718 | 0.050451 | 0.00037174 | -0.0079212 | -0.0004592 | -0.005371 | 0.029153 | 0.06357 | 0.0052295 | 0.015539 | 0.023964 | -0.0034117 | 3.4241 | 121.9162 | -0.059509 | 121.7743 | 0.12817 | -0.041199 | 0.004578 | 0.068665 | -0.036621 | -0.009155 | 0.009155 | 0.10071 | 0.086975 | 0.09613 | 0.018311 | -0.013733 | -0.15564 | 0.20599 | 0.082398 | 0.036621 | 0.064087 | 0.01831 | 0.068665 | -121.9666 | -121.9208 | 0.17853 | 0.17395 | 0.16479 | 0.10528 | 0.09613 | 0.18768 | 121.8338 | 0.10986 | 0.01831 | 121.9757 | -0.027466 | 121.994 | 0.041199 | -121.9894 | -121.9391 | 121.8521 | 0.086975 | 3.5019 | 0.14649
2924.7188 | 122.0856 | -0.09613 | 121.9666 | -0.012131 | 0.0014056 | 0.052359 | 0.052801 | -0.00069646 | -0.0083484 | -0.0028092 | -0.0084228 | 0.02723 | 0.066133 | 0.010143 | 0.013616 | 0.024391 | -0.0010617 | 3.4973 | 121.9254 | -0.064087 | 121.756 | 0.10071 | -0.064087 | -0.009155 | 0.027466 | -0.032043 | -0.032043 | 0.004578 | 0.086975 | 0.091553 | 0.09613 | 0.032043 | -0.041199 | -0.21057 | 0.19684 | 0.086975 | 0.032043 | 0.054932 | 0 | 0.064087 | -121.9986 | -121.962 | 0.1831 | 0.19226 | 0.18768 | 0.12817 | 0.1236 | 0.1648 | 121.8201 | 0.11902 | 0.036621 | 121.9894 | 0 | 122.0215 | 0.064087 | -122.0306 | -121.9986 | 121.8521 | 0.10071 | 3.5934 | 0.1236
2926.5 | 122.1542 | -0.064087 | 121.9299 | -0.01976 | 0.0022602 | 0.055136 | 0.05216 | 0.0025079 | -0.0070666 | 0.0006088 | -0.0023192 | 0.030435 | 0.06592 | 0.013347 | 0.016607 | 0.024178 | -0.0027707 | 3.6942 | 121.9025 | -0.059509 | 121.8109 | 0.15106 | -0.022888 | 0.013733 | 0.09613 | -0.041199 | -0.027466 | 0.068665 | 0.16479 | 0.11444 | 0.15106 | 0.004578 | -0.027466 | -0.11902 | 0.21515 | 0.07782 | 0.041199 | 0.073242 | 0.036621 | 0.036621 | -121.9711 | -121.8613 | 0.22888 | 0.21515 | 0.17853 | 0.17853 | 0.14191 | 0.21057 | 121.8704 | 0.19226 | 0.096131 | 121.962 | -0.013733 | 121.9666 | 0.022888 | -121.9894 | -121.9574 | 121.875 | 0.13275 | 3.7582 | 0.16022
2928.2656 | 122.0123 | -0.11902 | 121.9803 | -0.0045011 | 0.00097838 | 0.053 | 0.050451 | -0.0028327 | -0.0089892 | -0.0013138 | -0.005371 | 0.029794 | 0.06827 | 0.0048023 | 0.014257 | 0.024178 | -0.00084805 | 3.804 | 121.9299 | -0.10071 | 121.701 | 0.032043 | -0.10071 | -0.082397 | -0.036621 | 0 | -0.050354 | -0.082397 | 0.027466 | 0.022888 | 0.004578 | 0.018311 | -0.050354 | -0.27924 | 0.15106 | 0.036622 | 0.018311 | 0.018311 | 0 | 0.068665 | -121.9803 | -122.0627 | 0.14649 | 0.1236 | 0.14191 | 0.054932 | 0.073242 | 0.13275 | 121.8018 | 0.07782 | -0.032043 | 122.0306 | 0.050354 | 122.049 | 0.11902 | -122.081 | -122.0306 | 121.8201 | 0.036622 | 3.923 | 0.082398
2930.0312 | 122.0444 | -0.10529 | 121.9757 | -0.01976 | 0.0048236 | 0.053 | 0.050879 | 0.0010125 | -0.0089892 | -0.0038772 | -0.005371 | 0.032785 | 0.066347 | 0.014415 | 0.016821 | 0.024819 | -0.0038389 | 3.978 | 121.962 | -0.10071 | 121.7514 | 0.086975 | -0.068665 | -0.032043 | 0.041199 | -0.004578 | -0.027466 | -0.004578 | 0.073242 | 0.054932 | 0.07782 | 0.004578 | -0.013733 | -0.2243 | 0.19226 | 0.073243 | 0.036621 | 0.068665 | 0.032043 | 0.07782 | -121.9803 | -121.9803 | 0.17853 | 0.18311 | 0.16022 | 0.10529 | 0.082398 | 0.18768 | 121.8521 | 0.10071 | 0.022888 | 122.0627 | 0.022888 | 122.0673 | 0.10071 | -122.0764 | -122.0032 | 121.8567 | 0.10071 | 4.0833 | 0.14649
2931.75 | 122.0032 | -0.1236 | 121.9711 | -0.02739 | 0.0054644 | 0.052786 | 0.053015 | 0.0014397 | -0.0081348 | -0.001741 | -0.0084228 | 0.031717 | 0.066988 | 0.010356 | 0.017675 | 0.024819 | -0.0072569 | 4.0558 | 121.9711 | -0.082397 | 121.701 | 0.018311 | -0.13275 | -0.11444 | -0.050354 | -0.009155 | -0.054932 | -0.073242 | 0.009155 | -0.018311 | 0.022888 | 0.041199 | 0 | -0.27008 | 0.14191 | 0.009155 | -0.009155 | -0.032044 | -0.050354 | 0.068664 | -121.9803 | -122.0444 | 0.13275 | 0.14648 | 0.10528 | 0.07782 | 0.036621 | 0.10071 | 121.7834 | 0.064087 | -0.01831 | 122.0535 | 0.045777 | 122.0947 | 0.11444 | -122.0535 | -122.0261 | 121.8246 | 0.050354 | 4.1794 | 0.073242
2933.5156 | 122.1451 | -0.068665 | 121.9208 | -0.01976 | 0.0058918 | 0.054922 | 0.050451 | -0.0013373 | -0.010698 | -0.002382 | -0.0023192 | 0.028299 | 0.065279 | 0.012065 | 0.016607 | 0.0261 | -0.0042661 | 4.1519 | 121.9482 | -0.068665 | 121.7926 | 0.12817 | -0.036621 | 0.004578 | 0.091553 | -0.032043 | 0 | 0.064087 | 0.14648 | 0.1236 | 0.14191 | 0 | 0.027466 | -0.12817 | 0.19684 | 0.073243 | 0.032044 | 0.073243 | 0.032044 | 0.068665 | -121.9528 | -121.8567 | 0.21515 | 0.21057 | 0.19226 | 0.14191 | 0.1236 | 0.19684 | 121.8613 | 0.14648 | 0.064087 | 122.0169 | -0.032043 | 122.0169 | 0.036622 | -121.9894 | -121.9208 | 121.8613 | 0.13275 | 4.2206 | 0.16022
2935.2188 | 122.1451 | -0.073242 | 121.9391 | -0.012131 | -0.002226 | 0.052786 | 0.048315 | -0.00026906 | -0.0089892 | -0.0019546 | -0.0023192 | 0.029794 | 0.067415 | 0.0071521 | 0.015112 | 0.025032 | -0.0042661 | 4.2526 | 121.907 | -0.068665 | 121.788 | 0.15106 | 0.018311 | 0.036621 | 0.10071 | -0.041199 | -0.036621 | 0.059509 | 0.16937 | 0.16479 | 0.14191 | 0.004577 | -0.032044 | -0.15106 | 0.2243 | 0.10986 | 0.091553 | 0.10529 | 0.086976 | 0.036621 | -121.9803 | -121.8796 | 0.24261 | 0.21515 | 0.23804 | 0.17853 | 0.20142 | 0.21973 | 121.8567 | 0.20599 | 0.09613 | 121.9757 | -0.004578 | 121.9803 | 0.032043 | -122.0078 | -121.9757 | 121.8613 | 0.13275 | 4.3259 | 0.17395
2936.9844 | 122.0032 | -0.13275 | 121.994 | -0.01976 | 0.0061054 | 0.053854 | 0.052374 | 0.0040033 | -0.0077074 | -0.0011002 | -0.005371 | 0.032571 | 0.069124 | 0.013774 | 0.016821 | 0.025673 | 0.00021995 | 4.3671 | 121.9482 | -0.10529 | 121.6736 | -0.041199 | -0.16937 | -0.13275 | -0.068665 | 0.004578 | -0.064087 | -0.068665 | 0 | -0.018311 | 0.036621 | 0.027465 | -0.045777 | -0.32043 | 0.091552 | 0 | -0.036622 | -0.027465 | -0.064087 | 0.068664 | -121.9894 | -122.0627 | 0.13275 | 0.16937 | 0.11444 | 0.10071 | 0.045776 | 0.064087 | 121.7789 | 0.064087 | -0.004578 | 122.0535 | 0.068665 | 122.081 | 0.13733 | -122.0993 | -122.0581 | 121.8063 | 0.064086 | 4.4998 | 0.064086
2938.75 | 122.0718 | -0.091553 | 121.9803 | 0.0031279 | 0.0037556 | 0.052786 | 0.052374 | 0.00079894 | -0.010057 | -0.000673 | 0.0037842 | 0.031076 | 0.069124 | 0.012493 | 0.014471 | 0.024819 | -0.0031979 | 4.5731 | 121.9345 | -0.082397 | 121.7422 | 0.068665 | -0.068665 | -0.050354 | 0.050354 | -0.009155 | -0.032043 | 0 | 0.091553 | 0.059509 | 0.082397 | 0.009156 | -0.045777 | -0.23804 | 0.16022 | 0.041199 | 0.022888 | 0.032043 | 0.013732 | 0.05951 | -121.9894 | -121.9803 | 0.18311 | 0.17395 | 0.15106 | 0.11444 | 0.091552 | 0.15106 | 121.8246 | 0.1236 | 0.032043 | 122.0169 | 0.022888 | 122.0261 | 0.082398 | -122.0627 | -122.0123 | 121.8338 | 0.091553 | 4.6646 | 0.14191
2940.5156 | 122.0215 | -0.11902 | 121.9757 | -0.01976 | 0.0039692 | 0.054709 | 0.05152 | 0.0035761 | -0.0081348 | -0.0011002 | -0.005371 | 0.030221 | 0.069765 | 0.0086475 | 0.018102 | 0.023964 | -0.0044797 | 4.6509 | 121.9894 | -0.091553 | 121.7285 | 0.064087 | -0.10986 | -0.091553 | -0.027466 | 0 | -0.045776 | -0.064087 | 0.027466 | -0.009155 | 0.032043 | 0.027466 | 0.013733 | -0.24719 | 0.18311 | 0.027466 | 0.009156 | 0 | -0.01831 | 0.073243 | -121.9757 | -122.0398 | 0.14649 | 0.15106 | 0.10986 | 0.077819 | 0.036621 | 0.15564 | 121.8201 | 0.073242 | -0.018311 | 122.081 | 0.045776 | 122.1085 | 0.11902 | -122.0673 | -122.0215 | 121.8475 | 0.054932 | 4.7699 | 0.091553
2942.2188 | 122.1039 | -0.09613 | 121.9528 | -0.012131 | 0.0043964 | 0.053427 | 0.050879 | 0.0014397 | -0.0087756 | 0.0003952 | -0.0023192 | 0.028512 | 0.068483 | 0.0095019 | 0.017461 | 0.025032 | -0.0053343 | 4.6738 | 121.9757 | -0.086975 | 121.7239 | 0.059509 | -0.10529 | -0.054932 | 0.022888 | -0.022888 | -0.041199 | 0.041199 | 0.12817 | 0.10986 | 0.11902 | 0.009155 | 0.022888 | -0.22888 | 0.15564 | 0.041198 | -0.009156 | 0.032043 | -0.018311 | 0.054931 | -121.9757 | -121.9116 | 0.2243 | 0.21515 | 0.20599 | 0.16022 | 0.15106 | 0.14648 | 121.8109 | 0.16937 | 0.082398 | 122.0627 | 0.018311 | 122.0718 | 0.073242 | -122.0398 | -121.994 | 121.8201 | 0.13733 | 4.7699 | 0.11902
2943.9844 | 122.0581 | -0.11902 | 121.9391 | -0.0045011 | 0.0041828 | 0.054068 | 0.051947 | 0.0010125 | -0.0092028 | -0.002382 | -0.0023192 | 0.031076 | 0.069124 | 0.0088611 | 0.017675 | 0.025032 | -0.0019163 | 4.7882 | 121.9757 | -0.10986 | 121.6827 | 0.027466 | -0.13275 | -0.091553 | -0.027466 | -0.004578 | -0.045776 | -0.018311 | 0.050354 | 0.022888 | 0.068665 | 0.009156 | 0.036621 | -0.25635 | 0.14649 | 0.027466 | -0.013732 | 0.01831 | -0.022888 | 0.073243 | -121.9437 | -121.9574 | 0.16937 | 0.18768 | 0.14191 | 0.11444 | 0.068664 | 0.13733 | 121.7926 | 0.09613 | 0.027465 | 122.0856 | 0.041198 | 122.0947 | 0.11444 | -122.049 | -121.9849 | 121.8018 | 0.10071 | 4.9072 | 0.091553
2945.75 | 122.0261 | -0.12817 | 121.962 | -0.012131 | 0.0050372 | 0.054922 | 0.051092 | 0.0012261 | -0.0064258 | -0.0040908 | -0.0023192 | 0.031289 | 0.070833 | 0.0067249 | 0.016821 | 0.023537 | -0.0036253 | 4.9255 | 121.9894 | -0.09613 | 121.6644 | 0.009155 | -0.15106 | -0.10529 | -0.054932 | -0.009155 | -0.045776 | -0.068665 | 0.027466 | 0 | 0.045776 | 0.032044 | 0.027466 | -0.29755 | 0.13733 | 0.022888 | -0.022888 | -0.009156 | -0.054932 | 0.082398 | -121.9711 | -122.0306 | 0.15564 | 0.17395 | 0.12817 | 0.091552 | 0.045776 | 0.10528 | 121.7606 | 0.073242 | -0.022889 | 122.0856 | 0.036621 | 122.1176 | 0.11902 | -122.0581 | -122.0078 | 121.7926 | 0.059509 | 5.0537 | 0.073242
2947.5156 | 122.049 | -0.11902 | 121.962 | -0.012131 | 0.0037556 | 0.053641 | 0.050451 | 0.0037897 | -0.008562 | -0.0030228 | -0.005371 | 0.03193 | 0.069124 | 0.010997 | 0.017034 | 0.025032 | -0.0040525 | 5.1453 | 121.9345 | -0.091553 | 121.7377 | 0.09613 | -0.073242 | -0.064087 | 0.022888 | 0 | -0.050354 | -0.004578 | 0.082397 | 0.064087 | 0.073242 | 0.027466 | -0.027466 | -0.2243 | 0.21515 | 0.054932 | 0.045777 | 0.027466 | 0.018311 | 0.068665 | -121.962 | -121.9666 | 0.20142 | 0.19226 | 0.18311 | 0.1236 | 0.11444 | 0.18768 | 121.8292 | 0.13275 | 0.045776 | 122.0261 | 0.050354 | 122.0535 | 0.11902 | -122.0535 | -122.0123 | 121.8567 | 0.11444 | 5.2643 | 0.14191
2949.2656 | 121.9894 | -0.13733 | 121.9711 | -0.012131 | 0.0043964 | 0.052145 | 0.052801 | 0.0057123 | -0.006853 | -0.0019546 | -0.0084228 | 0.031076 | 0.071474 | 0.011852 | 0.016607 | 0.026314 | -0.0027707 | 5.159 | 121.9849 | -0.09613 | 121.6507 | -0.009155 | -0.16022 | -0.1236 | -0.086975 | 0.004578 | -0.068665 | -0.07782 | -0.009155 | -0.013733 | 0.022888 | 0.041199 | 0.013733 | -0.32043 | 0.12817 | 0.013733 | -0.022888 | -0.027466 | -0.064087 | 0.068664 | -121.9666 | -122.049 | 0.12817 | 0.16022 | 0.1236 | 0.091553 | 0.054932 | 0.086975 | 121.7468 | 0.05951 | -0.009155 | 122.081 | 0.073243 | 122.1222 | 0.14191 | -122.0673 | -122.0398 | 121.788 | 0.059509 | 5.2963 | 0.050354
2950.9688 | 122.0581 | -0.10529 | 121.9482 | -0.01976 | 0.0022602 | 0.053641 | 0.051306 | -0.0024055 | -0.010485 | -0.0043046 | -0.0023192 | 0.029367 | 0.071901 | 0.01057 | 0.016393 | 0.025887 | -0.0038389 | 5.365 | 121.9574 | -0.091553 | 121.7377 | 0.09613 | -0.082397 | -0.054932 | 0.022888 | 0 | -0.054932 | -0.009155 | 0.082397 | 0.064087 | 0.064087 | 0.013733 | 0.009155 | -0.21057 | 0.20142 | 0.050354 | 0.022889 | 0.036621 | 0.009156 | 0.050354 | -121.9482 | -121.9574 | 0.18768 | 0.16937 | 0.16937 | 0.11902 | 0.11902 | 0.18768 | 121.8292 | 0.13733 | 0.045777 | 122.049 | 0.054932 | 122.0627 | 0.10529 | -122.0398 | -122.0032 | 121.843 | 0.096131 | 5.4703 | 0.12817
2952.7344 | 122.0352 | -0.10529 | 121.9528 | -0.012131 | 0.00461 | 0.052359 | 0.051306 | 0.00058534 | -0.0074938 | -0.0019546 | -0.0023192 | 0.030435 | 0.071047 | 0.0028797 | 0.014684 | 0.025673 | -0.0034117 | 5.4657 | 121.9391 | -0.091553 | 121.7285 | 0.10071 | -0.059509 | -0.045776 | 0.032043 | 0 | -0.054932 | -0.004578 | 0.07782 | 0.064087 | 0.064087 | 0.013733 | -0.013733 | -0.2243 | 0.20599 | 0.05951 | 0.045777 | 0.045777 | 0.032044 | 0.050354 | -121.9528 | -121.9574 | 0.18311 | 0.16937 | 0.16937 | 0.11902 | 0.11902 | 0.19226 | 121.8201 | 0.13275 | 0.050354 | 122.0306 | 0.054932 | 122.0444 | 0.10529 | -122.0444 | -122.0078 | 121.8338 | 0.10071 | 5.571 | 0.13733
2954.4219 | 122.1451 | -0.082397 | 121.9528 | -0.0045011 | 0.00012398 | 0.051718 | 0.04917 | 0.0025079 | -0.0083484 | -0.0030228 | -0.005371 | 0.028512 | 0.070833 | 0.0075793 | 0.014898 | 0.028878 | -0.0040525 | 5.571 | 121.9299 | -0.064087 | 121.8155 | 0.20142 | 0.022888 | 0.032043 | 0.10986 | -0.032043 | -0.027466 | 0.059509 | 0.17853 | 0.17395 | 0.12817 | 0.01831 | -0.022888 | -0.13733 | 0.28381 | 0.11444 | 0.10528 | 0.09613 | 0.086975 | 0.054931 | -121.9849 | -121.8933 | 0.26092 | 0.21057 | 0.25635 | 0.15564 | 0.20142 | 0.2655 | 121.8796 | 0.20599 | 0.086975 | 121.994 | -0.004577 | 122.0123 | 0.050354 | -122.0169 | -121.9803 | 121.8979 | 0.14191 | 5.6534 | 0.19226
2956.1875 | 122.1313 | -0.068665 | 121.9528 | -0.01976 | -8.9824e-05 | 0.054282 | 0.048742 | -0.0021919 | -0.0094164 | -0.0032364 | -0.005371 | 0.028939 | 0.07126 | 0.0045887 | 0.013189 | 0.025673 | -0.0066159 | 5.6442 | 121.9116 | -0.082397 | 121.7651 | 0.13275 | -0.009155 | 0.018311 | 0.064087 | -0.032043 | -0.032043 | 0.018311 | 0.16022 | 0.14191 | 0.12817 | -0.013732 | -0.041199 | -0.18768 | 0.20142 | 0.086976 | 0.05951 | 0.10071 | 0.073242 | 0.036622 | -121.9849 | -121.9345 | 0.22888 | 0.19684 | 0.21057 | 0.16022 | 0.17395 | 0.21515 | 121.8475 | 0.19226 | 0.050354 | 121.994 | 0 | 121.9803 | 0.036622 | -122.0352 | -121.9849 | 121.8338 | 0.086976 | 5.7129 | 0.13275
2957.9531 | 122.0169 | -0.13275 | 121.9711 | -0.012131 | 0.0041828 | 0.055136 | 0.052588 | 0.0035761 | -0.008562 | -0.0015274 | -0.0084228 | 0.031717 | 0.071901 | 0.0071521 | 0.017034 | 0.025887 | -0.0042661 | 5.7678 | 121.9666 | -0.09613 | 121.6782 | -0.004578 | -0.16937 | -0.11902 | -0.068665 | 0.004578 | -0.059509 | -0.068665 | -0.004578 | -0.004578 | 0.032043 | 0.036621 | -0.004577 | -0.29297 | 0.12817 | 0.013732 | -0.036622 | -0.022889 | -0.073243 | 0.073242 | -121.9666 | -122.0398 | 0.12817 | 0.16479 | 0.12817 | 0.091552 | 0.054931 | 0.091552 | 121.7743 | 0.054931 | -0.009156 | 122.0627 | 0.064087 | 122.0993 | 0.13733 | -122.0673 | -122.0306 | 121.8109 | 0.064086 | 5.9006 | 0.064086
2959.7031 | 122.0901 | -0.11444 | 121.9437 | -0.012131 | 0.00012398 | 0.052786 | 0.050879 | 0.00015814 | -0.0070666 | -0.0057998 | -0.0084228 | 0.030648 | 0.071474 | -0.0016065 | 0.012121 | 0.022683 | 0.00021995 | 5.864 | 121.9437 | -0.068665 | 121.7331 | 0.091553 | -0.068665 | -0.018311 | 0.027466 | -0.032043 | -0.032043 | -0.018311 | 0.10071 | 0.082397 | 0.07782 | 0.045776 | 0 | -0.21057 | 0.20599 | 0.09613 | 0.045776 | 0.050354 | 0 | 0.082398 | -121.9757 | -121.962 | 0.21515 | 0.19226 | 0.19684 | 0.10986 | 0.11444 | 0.16022 | 121.8018 | 0.13275 | 0.013732 | 122.0123 | 0 | 122.0581 | 0.082398 | -122.0123 | -121.9757 | 121.8475 | 0.09613 | 5.9784 | 0.14191
2961.4062 | 122.0627 | -0.10529 | 121.9711 | -0.01976 | 0.0043964 | 0.055777 | 0.053015 | -0.00026906 | -0.010271 | -0.0025956 | -0.0023192 | 0.030648 | 0.070192 | 0.010997 | 0.014898 | 0.02546 | -0.00063445 | 6.0745 | 121.9757 | -0.082397 | 121.7285 | 0.064087 | -0.07782 | -0.059509 | 0.018311 | 0 | -0.050354 | -0.027466 | 0.064087 | 0.054932 | 0.059509 | 0.022889 | 0.004578 | -0.24261 | 0.16937 | 0.045777 | 0.027466 | 0.022888 | 0.004577 | 0.054932 | -121.9711 | -121.9986 | 0.16937 | 0.16479 | 0.16022 | 0.10986 | 0.10529 | 0.14648 | 121.8109 | 0.11444 | 0.022888 | 122.0581 | 0.050354 | 122.081 | 0.10529 | -122.0535 | -122.0215 | 121.8338 | 0.07782 | 6.1798 | 0.1236
2963.1719 | 122.0535 | -0.10529 | 121.9162 | -0.012131 | 0.00461 | 0.054709 | 0.051733 | 0.00079894 | -0.0055712 | -0.0025956 | -0.0084228 | 0.031717 | 0.071688 | 0.0065113 | 0.018102 | 0.024391 | -0.0023435 | 6.102 | 121.9849 | -0.09613 | 121.6736 | 0.022888 | -0.14648 | -0.10071 | -0.013733 | -0.018311 | -0.054932 | -0.018311 | 0.054932 | 0.041199 | 0.059509 | 0.009156 | 0.068664 | -0.24262 | 0.12817 | 0.004578 | -0.041198 | -0.004578 | -0.050354 | 0.050354 | -121.9345 | -121.9345 | 0.16022 | 0.16479 | 0.14649 | 0.11444 | 0.096131 | 0.11902 | 121.7697 | 0.10986 | 0.036621 | 122.081 | 0.036621 | 122.0901 | 0.086975 | -122.0123 | -121.9711 | 121.7789 | 0.086975 | 6.2073 | 0.091553
2964.875 | 122.0306 | -0.12817 | 121.9666 | -0.01976 | -0.00094422 | 0.050864 | 0.05216 | 0.0025079 | -0.011766 | -0.0025956 | -0.005371 | 0.029367 | 0.07062 | 0.0028797 | 0.015752 | 0.023751 | -0.0034117 | 6.2485 | 121.9391 | -0.10986 | 121.6736 | 0.013733 | -0.11902 | -0.10071 | -0.07782 | 0 | -0.068665 | -0.064087 | 0.032043 | 0.018311 | 0.041199 | 0.018311 | -0.027466 | -0.29297 | 0.14191 | 0.027466 | 0.009155 | 0.009155 | -0.009156 | 0.059509 | -121.9666 | -122.0306 | 0.16022 | 0.16937 | 0.14649 | 0.10986 | 0.086976 | 0.1236 | 121.7834 | 0.10071 | 0.004578 | 122.049 | 0.068665 | 122.0673 | 0.12817 | -122.0764 | -122.0352 | 121.8018 | 0.064087 | 6.3766 | 0.050354
2966.6406 | 122.0856 | -0.10071 | 121.9574 | -0.012131 | 0.00033758 | 0.054068 | 0.049383 | -0.0013373 | -0.008562 | -0.0013138 | -0.0023192 | 0.031289 | 0.069979 | 0.0024525 | 0.014043 | 0.025887 | -0.0025571 | 6.4133 | 121.8796 | -0.059509 | 121.788 | 0.15106 | -0.004578 | 0.018311 | 0.064087 | -0.013733 | -0.050354 | -0.018311 | 0.09613 | 0.091553 | 0.07782 | 0.041199 | -0.077819 | -0.16937 | 0.25177 | 0.11902 | 0.09613 | 0.07782 | 0.054931 | 0.050354 | -121.9711 | -121.9757 | 0.19684 | 0.17853 | 0.19226 | 0.12817 | 0.14191 | 0.21057 | 121.8475 | 0.14648 | 0.032043 | 121.9391 | 0.036621 | 121.9803 | 0.086975 | -122.0169 | -122.0078 | 121.8887 | 0.082397 | 6.514 | 0.1648
2968.3438 | 122.0169 | -0.13275 | 121.9849 | 0.0031279 | 0.0014056 | 0.053427 | 0.050238 | 0.00015814 | -0.0062122 | -0.0047318 | -0.011475 | 0.030008 | 0.072115 | 0.0097157 | 0.014471 | 0.024178 | -0.0036253 | 6.4407 | 121.9299 | -0.086975 | 121.6782 | 0.036621 | -0.10071 | -0.082397 | -0.050354 | 0.022888 | -0.064087 | -0.086975 | 0.036621 | 0.022888 | 0.018311 | 0.045776 | -0.054931 | -0.3067 | 0.16937 | 0.050354 | 0.032043 | 0.004578 | -0.013733 | 0.068664 | -121.962 | -122.0718 | 0.16937 | 0.15106 | 0.15564 | 0.082398 | 0.086975 | 0.1236 | 121.7651 | 0.10071 | -0.022888 | 122.0169 | 0.086975 | 122.0627 | 0.15564 | -122.0718 | -122.049 | 121.8109 | 0.045776 | 6.5735 | 0.082397
2970.0938 | 122.0261 | -0.13733 | 121.9666 | -0.012131 | 0.0043964 | 0.052359 | 0.053228 | 0.0037897 | -0.0072802 | -0.0032364 | -0.0023192 | 0.031503 | 0.072115 | 0.010143 | 0.017461 | 0.022469 | -0.0044797 | 6.6238 | 121.9437 | -0.10071 | 121.7285 | 0.09613 | -0.091553 | -0.064087 | 0.018311 | -0.009155 | -0.045776 | -0.036621 | 0.041199 | 0.022888 | 0.050354 | 0.036621 | -0.022888 | -0.23804 | 0.23346 | 0.073242 | 0.045776 | 0.036621 | 0.009155 | 0.091553 | -121.9757 | -122.0032 | 0.17853 | 0.18768 | 0.16022 | 0.09613 | 0.068664 | 0.19684 | 121.8292 | 0.086975 | 0.009155 | 122.0444 | 0.036621 | 122.081 | 0.12817 | -122.0673 | -122.0123 | 121.8658 | 0.10071 | 6.7612 | 0.15564
2971.8594 | 122.0901 | -0.07782 | 121.9482 | -0.0045011 | 0.0014056 | 0.053854 | 0.051306 | -0.0034735 | -0.0066394 | -0.00345 | -0.0084228 | 0.030435 | 0.074465 | 0.0018115 | 0.015752 | 0.025887 | -0.0036253 | 6.6605 | 121.9025 | -0.064087 | 121.7468 | 0.15106 | -0.059509 | -0.013733 | 0.064087 | -0.036621 | -0.032043 | 0.009155 | 0.10071 | 0.10071 | 0.10071 | 0.013733 | -0.045776 | -0.20142 | 0.22888 | 0.064087 | 0.018311 | 0.050354 | 0.004578 | 0.045777 | -121.9849 | -121.9391 | 0.17853 | 0.17853 | 0.17853 | 0.13275 | 0.13275 | 0.21515 | 121.8109 | 0.13275 | 0.041198 | 121.9666 | -0.004578 | 121.9803 | 0.041199 | -122.0123 | -121.9803 | 121.8246 | 0.086975 | 6.7383 | 0.14191
2973.5938 | 122.1222 | -0.082397 | 121.9299 | -0.012131 | -0.0020124 | 0.053 | 0.046606 | 0.0010125 | -0.0087756 | -0.0043046 | -0.005371 | 0.02958 | 0.072756 | 0.0062977 | 0.01618 | 0.025032 | -0.0038389 | 6.8436 | 121.8842 | -0.054932 | 121.8109 | 0.19684 | 0.050354 | 0.045776 | 0.10071 | -0.036621 | -0.018311 | 0.045776 | 0.16937 | 0.16022 | 0.1236 | 0.027465 | -0.045777 | -0.11902 | 0.27924 | 0.12817 | 0.13275 | 0.10071 | 0.10529 | 0.064086 | -121.9666 | -121.8842 | 0.25177 | 0.20599 | 0.24261 | 0.14191 | 0.17853 | 0.25177 | 121.8658 | 0.18768 | 0.064087 | 121.9391 | -0.01831 | 121.9666 | 0.045776 | -121.9849 | -121.9482 | 121.8933 | 0.12817 | 6.926 | 0.18311
2975.3281 | 122.0261 | -0.13275 | 121.9574 | -0.012131 | 0.0037556 | 0.053214 | 0.05216 | -0.00091006 | -0.0070666 | -0.0019546 | -0.0023192 | 0.03428 | 0.072115 | 0.0041615 | 0.014257 | 0.024605 | -0.00063445 | 6.871 | 121.9528 | -0.10986 | 121.6827 | 0.013733 | -0.15106 | -0.09613 | -0.050354 | -0.009155 | -0.064087 | -0.036621 | 0.022888 | -0.013733 | 0.050354 | 0.022888 | -0.004577 | -0.27466 | 0.14648 | 0.036621 | -0.018311 | 0.013733 | -0.041199 | 0.068664 | -121.9666 | -121.994 | 0.15564 | 0.18311 | 0.11902 | 0.11444 | 0.050354 | 0.1236 | 121.7926 | 0.086975 | 0.027466 | 122.0627 | 0.054932 | 122.0856 | 0.1236 | -122.0673 | -122.0215 | 121.8155 | 0.09613 | 7.0038 | 0.082397
2977.0938 | 122.0901 | -0.10071 | 121.9025 | -0.012131 | -0.00051702 | 0.05535 | 0.050665 | 0.00037174 | -0.010057 | -0.0049454 | -0.0023192 | 0.028512 | 0.074465 | 0.0090747 | 0.013403 | 0.023964 | -0.00020725 | 6.9809 | 121.907 | -0.050354 | 121.7239 | 0.11902 | -0.050354 | -0.009155 | 0.027466 | -0.036621 | -0.032043 | 0 | 0.091553 | 0.086975 | 0.082397 | 0.050354 | 0.004577 | -0.17853 | 0.21973 | 0.091553 | 0.050354 | 0.041199 | 0 | 0.068665 | -121.9391 | -121.9025 | 0.19226 | 0.18311 | 0.18768 | 0.11444 | 0.11902 | 0.16937 | 121.7743 | 0.1236 | 0.032043 | 121.9574 | -0.004578 | 122.0078 | 0.064087 | -121.9528 | -121.9345 | 121.8246 | 0.10071 | 7.0816 | 0.12817
2978.8594 | 122.0398 | -0.10986 | 121.9666 | -0.01976 | 0.0024738 | 0.052573 | 0.051092 | -0.0045417 | -0.010485 | -0.0045182 | 0.00073235 | 0.033426 | 0.075319 | 0.012706 | 0.016607 | 0.023323 | -0.0046933 | 7.2235 | 121.9391 | -0.10529 | 121.6827 | 0.027466 | -0.12817 | -0.10071 | -0.045776 | 0 | -0.068665 | -0.068665 | 0.050354 | 0.013733 | 0.045776 | 0.004577 | -0.027466 | -0.28381 | 0.13733 | 0.009155 | -0.018311 | 0.004578 | -0.022888 | 0.041198 | -121.9666 | -122.0352 | 0.16022 | 0.15564 | 0.1236 | 0.11444 | 0.082398 | 0.13275 | 121.788 | 0.11902 | 0 | 122.0444 | 0.068665 | 122.049 | 0.10986 | -122.0718 | -122.0352 | 121.7926 | 0.041198 | 7.3334 | 0.064087
2980.6094 | 122.0215 | -0.12817 | 121.9666 | -0.012131 | 0.0050372 | 0.054282 | 0.05216 | 0.00037174 | -0.008562 | -0.0040908 | -0.0023192 | 0.02958 | 0.076601 | 0.012706 | 0.017034 | 0.024819 | -0.0019163 | 7.3288 | 121.9528 | -0.10529 | 121.7194 | 0.082397 | -0.10071 | -0.086975 | 0 | 0 | -0.059509 | -0.041199 | 0.032043 | -0.009155 | 0.032043 | 0.022888 | -0.013733 | -0.24719 | 0.21057 | 0.041199 | 0.027466 | 0.018311 | 0.004578 | 0.068665 | -121.9666 | -122.0078 | 0.16022 | 0.16022 | 0.11902 | 0.091552 | 0.050354 | 0.18768 | 121.8246 | 0.091552 | 0.01831 | 122.0581 | 0.059509 | 122.081 | 0.12817 | -122.0718 | -122.0261 | 121.8475 | 0.086975 | 7.457 | 0.12817
2982.375 | 122.0032 | -0.1236 | 121.9894 | -0.01976 | 0.00076478 | 0.052573 | 0.052374 | 0.0018671 | -0.0072802 | -0.000673 | -0.0023192 | 0.029367 | 0.078737 | 0.0018115 | 0.01618 | 0.023964 | -0.0023435 | 7.3196 | 121.9482 | -0.10986 | 121.6736 | 0.041199 | -0.10986 | -0.10529 | -0.064087 | 0.018311 | -0.041199 | -0.10071 | 0.032043 | 0.022888 | 0.013733 | 0.013733 | -0.041199 | -0.31586 | 0.16479 | 0.01831 | 0.013733 | 0.004577 | 0 | 0.082397 | -121.9711 | -122.0901 | 0.15564 | 0.13733 | 0.14648 | 0.054932 | 0.064087 | 0.15106 | 121.7834 | 0.073242 | -0.059509 | 122.0581 | 0.05951 | 122.0718 | 0.14191 | -122.0993 | -122.0306 | 121.7972 | 0.022888 | 7.4432 | 0.059509
2984.0781 | 122.1497 | -0.07782 | 121.9116 | -0.012131 | 0.00033758 | 0.054495 | 0.048956 | -0.0019781 | -0.010698 | -0.0019546 | -0.0084228 | 0.031076 | 0.077242 | 0.0028797 | 0.013189 | 0.025246 | -0.0044797 | 7.489 | 121.9299 | -0.082397 | 121.7834 | 0.1831 | 0.018311 | 0.036621 | 0.11902 | -0.041199 | -0.022888 | 0.054932 | 0.1831 | 0.16479 | 0.13733 | -0.004577 | 0.018311 | -0.12817 | 0.26092 | 0.11444 | 0.096131 | 0.11902 | 0.10071 | 0.054932 | -121.9528 | -121.8567 | 0.26092 | 0.21515 | 0.24261 | 0.16022 | 0.18768 | 0.2655 | 121.8658 | 0.20599 | 0.07782 | 122.0123 | -0.018311 | 122.0078 | 0.036621 | -121.994 | -121.9345 | 121.8613 | 0.13275 | 7.5668 | 0.19684
2985.8438 | 122.1176 | -0.086975 | 121.9254 | -0.012131 | 0.0056782 | 0.054282 | 0.050238 | -0.00026906 | -0.0083484 | -0.0060134 | -0.0023192 | 0.029794 | 0.075747 | 0.0033069 | 0.014471 | 0.023964 | -0.0029843 | 7.5989 | 121.9116 | -0.050354 | 121.8063 | 0.18768 | -0.009155 | 0.032043 | 0.10986 | -0.032043 | -0.032043 | 0.045776 | 0.15106 | 0.1236 | 0.13275 | 0.036621 | -0.013733 | -0.11902 | 0.27466 | 0.11902 | 0.07782 | 0.082397 | 0.041199 | 0.054932 | -121.9574 | -121.8796 | 0.23804 | 0.21973 | 0.21057 | 0.16479 | 0.15564 | 0.23804 | 121.8567 | 0.18311 | 0.077819 | 121.962 | 0 | 121.9986 | 0.054932 | -121.9757 | -121.9574 | 121.8933 | 0.13275 | 7.6859 | 0.19684
2987.6094 | 122.0581 | -0.13275 | 121.9482 | -0.012131 | 0.0024738 | 0.052145 | 0.053015 | 0.0012261 | -0.0083484 | -0.0021682 | -0.005371 | 0.032144 | 0.081728 | 0.0050159 | 0.015752 | 0.024391 | -0.0027707 | 7.7408 | 121.9254 | -0.09613 | 121.6919 | 0.027466 | -0.10071 | -0.082397 | -0.045776 | 0.013733 | -0.054932 | -0.045776 | 0.073242 | 0.032043 | 0.064087 | 0.036621 | -0.022888 | -0.25635 | 0.16022 | 0.050354 | 0.032043 | 0.013733 | -0.004578 | 0.077819 | -121.9345 | -121.994 | 0.20599 | 0.19684 | 0.16479 | 0.11902 | 0.086975 | 0.1236 | 121.788 | 0.12817 | 0.009156 | 122.0215 | 0.068665 | 122.0581 | 0.14648 | -122.0444 | -122.0032 | 121.8246 | 0.086975 | 7.8735 | 0.086975
2989.3594 | 121.9986 | -0.13733 | 121.9757 | -0.012131 | 0.0043964 | 0.055136 | 0.050238 | -0.0024055 | -0.0098438 | -0.0040908 | -0.005371 | 0.032998 | 0.077669 | 0.0013843 | 0.015325 | 0.026314 | -0.0029843 | 7.8323 | 121.9437 | -0.11444 | 121.6919 | 0.064087 | -0.12817 | -0.10071 | -0.036621 | -0.004578 | -0.036621 | -0.059509 | 0.027466 | -0.027466 | 0.032043 | 0.022888 | -0.032043 | -0.28381 | 0.20142 | 0.036621 | 0.009155 | 0.013733 | -0.013733 | 0.10071 | -121.9803 | -122.0352 | 0.16479 | 0.16937 | 0.10986 | 0.068664 | 0.009155 | 0.17853 | 121.8063 | 0.064087 | -0.022888 | 122.0581 | 0.032043 | 122.081 | 0.13275 | -122.0901 | -122.0123 | 121.8292 | 0.07782 | 7.9697 | 0.10071
2991.0625 | 122.0673 | -0.10071 | 121.9345 | -0.01976 | -0.0013714 | 0.051505 | 0.049811 | 0.0014397 | -0.008562 | 0.0003952 | -0.005371 | 0.028939 | 0.078096 | 0.0037341 | 0.014257 | 0.02311 | -0.0044797 | 7.9468 | 121.9116 | -0.073242 | 121.7926 | 0.16937 | -0.009155 | 0.032043 | 0.068665 | -0.027466 | -0.036621 | 0.004578 | 0.13275 | 0.10986 | 0.086975 | 0.027466 | -0.022888 | -0.14191 | 0.27008 | 0.13275 | 0.091553 | 0.10529 | 0.064087 | 0.064087 | -121.962 | -121.9299 | 0.23346 | 0.18768 | 0.21057 | 0.1236 | 0.14648 | 0.24261 | 121.8658 | 0.16937 | 0.041199 | 121.9849 | 0.009155 | 122.0123 | 0.073242 | -122.0078 | -121.9711 | 121.8933 | 0.10529 | 8.0475 | 0.16937
2992.8438 | 122.113 | -0.10986 | 121.9208 | -0.012131 | -0.00073062 | 0.051718 | 0.04917 | 0.0027215 | -0.0089892 | -0.0013138 | -0.005371 | 0.030008 | 0.078524 | 0.0086475 | 0.013403 | 0.023964 | -0.0010617 | 7.9376 | 121.8887 | -0.086975 | 121.7285 | 0.10986 | -0.064087 | -0.013733 | 0.009155 | -0.022888 | -0.032043 | 0.009155 | 0.10986 | 0.10071 | 0.10071 | 0.022888 | -0.032043 | -0.19226 | 0.21973 | 0.09613 | 0.045776 | 0.073242 | 0.022888 | 0.07782 | -121.9437 | -121.9116 | 0.21973 | 0.21057 | 0.21057 | 0.13275 | 0.13275 | 0.19684 | 121.8155 | 0.14191 | 0.041198 | 121.9757 | 0.009155 | 121.9986 | 0.086975 | -122.0078 | -121.9528 | 121.8384 | 0.11902 | 8.0475 | 0.11902
2994.5469 | 122.0856 | -0.10071 | 121.9391 | -0.02739 | 0.00012398 | 0.053641 | 0.052801 | 0.0037897 | -0.0083484 | -0.0036636 | -0.0023192 | 0.030862 | 0.080019 | 0.0065113 | 0.015112 | 0.023323 | -0.0040525 | 8.075 | 121.9116 | -0.059509 | 121.7789 | 0.17395 | -0.032043 | 0.013733 | 0.10529 | -0.045776 | -0.022888 | 0.027466 | 0.11444 | 0.10071 | 0.091553 | 0.041199 | -0.027466 | -0.16022 | 0.27466 | 0.11444 | 0.068665 | 0.073242 | 0.027466 | 0.07782 | -121.9849 | -121.9116 | 0.21515 | 0.19226 | 0.20142 | 0.11444 | 0.1236 | 0.23346 | 121.8384 | 0.13733 | 0.050354 | 121.9711 | -0.022888 | 122.0123 | 0.054932 | -121.9986 | -121.962 | 121.8796 | 0.12817 | 8.1757 | 0.20599
2996.3125 | 122.0123 | -0.13733 | 121.9666 | -0.01976 | 0.0041828 | 0.054495 | 0.055151 | 0.0029351 | -0.0087756 | -0.00345 | -0.0084228 | 0.033426 | 0.079805 | 0.0075793 | 0.015966 | 0.025032 | -0.0044797 | 8.1253 | 121.9666 | -0.10986 | 121.6553 | 0.009155 | -0.16022 | -0.11902 | -0.059509 | 0.013733 | -0.073242 | -0.07782 | 0.004578 | -0.018311 | 0.022888 | 0.027466 | 0 | -0.31128 | 0.14648 | 0.01831 | -0.022888 | -0.009156 | -0.050354 | 0.064087 | -121.9528 | -122.0444 | 0.14191 | 0.16022 | 0.11902 | 0.09613 | 0.054931 | 0.11902 | 121.7651 | 0.07782 | -0.004578 | 122.0764 | 0.086975 | 122.1039 | 0.15106 | -122.0764 | -122.0398 | 121.7926 | 0.059509 | 8.2626 | 0.07782
2998.0781 | 122.0169 | -0.13733 | 121.9666 | -0.0045011 | 0.001833 | 0.051505 | 0.052801 | -0.0013373 | -0.00963 | -0.0030228 | -0.005371 | 0.033212 | 0.084078 | 0.017833 | 0.016607 | 0.02546 | -0.0044797 | 8.2626 | 121.9482 | -0.10529 | 121.6644 | 0.027466 | -0.1236 | -0.10071 | -0.064087 | -0.004578 | -0.064087 | -0.073242 | 0.041199 | 0.027466 | 0.041199 | 0.032043 | -0.018311 | -0.30212 | 0.16479 | 0.036621 | 0.013733 | 0.004578 | -0.01831 | 0.073242 | -121.9711 | -122.0398 | 0.17853 | 0.17853 | 0.16479 | 0.10529 | 0.091553 | 0.13275 | 121.7697 | 0.10529 | -0.009155 | 122.0535 | 0.059509 | 122.0856 | 0.13275 | -122.0718 | -122.0306 | 121.8018 | 0.064087 | 8.4 | 0.073242
2999.8594 | 122.0856 | -0.10529 | 121.9208 | -0.012131 | 0.0026874 | 0.053 | 0.050238 | 0.0012261 | -0.010057 | -0.0030228 | -0.0023192 | 0.031503 | 0.084291 | 0.0030933 | 0.013189 | 0.026528 | -0.0025571 | 8.3176 | 121.8796 | -0.07782 | 121.7514 | 0.15106 | -0.064087 | -0.013733 | 0.041199 | -0.032043 | -0.022888 | 0.004578 | 0.086975 | 0.091553 | 0.09613 | 0.027466 | -0.041198 | -0.16937 | 0.25635 | 0.091553 | 0.041199 | 0.064087 | 0.013733 | 0.082398 | -121.9528 | -121.9162 | 0.19226 | 0.20142 | 0.19684 | 0.11902 | 0.11444 | 0.22888 | 121.8292 | 0.10986 | 0.027466 | 121.9574 | -0.009155 | 121.9849 | 0.073243 | -121.9986 | -121.9437 | 121.8567 | 0.10986 | 8.4229 | 0.14649
3001.5625 | 122.1039 | -0.09613 | 121.9299 | -0.012131 | 0.0037556 | 0.054709 | 0.051092 | 0.0018671 | -0.0074938 | -0.0021682 | -0.005371 | 0.029367 | 0.086 | 0.0024525 | 0.016393 | 0.024819 | -0.00020725 | 8.4412 | 121.9116 | -0.068665 | 121.788 | 0.1831 | -0.036621 | 0.027466 | 0.10529 | -0.032043 | -0.027466 | 0.054932 | 0.13275 | 0.10986 | 0.11902 | 0.027465 | -0.018311 | -0.14191 | 0.27924 | 0.1236 | 0.059509 | 0.096131 | 0.032044 | 0.068664 | -121.962 | -121.875 | 0.22888 | 0.21515 | 0.20599 | 0.14649 | 0.13733 | 0.25177 | 121.8567 | 0.16022 | 0.082398 | 121.9803 | -0.004577 | 122.0078 | 0.064087 | -121.9986 | -121.9574 | 121.8842 | 0.15106 | 8.5373 | 0.20142
3003.3281 | 122.1085 | -0.09613 | 121.9254 | -0.01976 | 0.00097838 | 0.050436 | 0.050879 | 0.0014397 | -0.0098438 | -0.001741 | 0.00073235 | 0.03193 | 0.087282 | 0.0022389 | 0.014471 | 0.024605 | -0.0057615 | 8.5785 | 121.8887 | -0.073242 | 121.7972 | 0.17395 | 0.013733 | 0.041199 | 0.073242 | -0.032043 | -0.027466 | 0.018311 | 0.14648 | 0.12817 | 0.10986 | 0.022888 | -0.036621 | -0.12817 | 0.27008 | 0.13733 | 0.10986 | 0.11444 | 0.086975 | 0.068664 | -121.9574 | -121.907 | 0.24261 | 0.20599 | 0.2243 | 0.13733 | 0.15564 | 0.24719 | 121.8704 | 0.17395 | 0.045777 | 121.962 | -0.004577 | 121.9849 | 0.064087 | -121.9986 | -121.9528 | 121.8933 | 0.11444 | 8.6746 | 0.16937
3005.0312 | 122.1497 | -0.091553 | 121.9208 | -0.0045011 | -0.00073062 | 0.052786 | 0.048742 | -0.0019781 | -0.010912 | -0.0025956 | -0.005371 | 0.031289 | 0.090273 | 0.00052987 | 0.01383 | 0.023751 | -0.00084805 | 8.6517 | 121.907 | -0.064087 | 121.7743 | 0.1831 | 0.004578 | 0.032043 | 0.11444 | -0.022888 | -0.032043 | 0.064087 | 0.17395 | 0.16937 | 0.13275 | 0.027466 | -0.013733 | -0.14648 | 0.27466 | 0.1236 | 0.096131 | 0.09613 | 0.068665 | 0.05951 | -121.9437 | -121.8567 | 0.2655 | 0.2243 | 0.26093 | 0.16479 | 0.20142 | 0.24719 | 121.8384 | 0.20599 | 0.09613 | 121.9711 | 0.009155 | 121.9986 | 0.068665 | -121.9849 | -121.9528 | 121.8658 | 0.15564 | 8.7433 | 0.20599
3006.7969 | 122.0764 | -0.091553 | 121.9254 | -0.012131 | 0.00097838 | 0.054068 | 0.051306 | -0.0024055 | -0.010698 | 0.0003952 | -0.0084228 | 0.030435 | 0.093904 | 0.0043751 | 0.01383 | 0.025032 | -0.0019163 | 8.7067 | 121.9116 | -0.07782 | 121.7285 | 0.12817 | -0.086975 | -0.018311 | 0.032043 | -0.027466 | -0.050354 | 0.004578 | 0.09613 | 0.091553 | 0.086975 | 0.013733 | -0.013733 | -0.19684 | 0.21973 | 0.073242 | 0.004578 | 0.059509 | -0.009155 | 0.041199 | -121.9528 | -121.9208 | 0.18768 | 0.17853 | 0.18311 | 0.13733 | 0.14191 | 0.20599 | 121.8063 | 0.14648 | 0.054932 | 121.9894 | 0.022888 | 122.0032 | 0.064087 | -122.0032 | -121.9757 | 121.8201 | 0.096131 | 8.7982 | 0.1236
3008.5625 | 122.0947 | -0.10071 | 121.8842 | -0.01976 | 0.0033282 | 0.052359 | 0.051733 | 0.00079894 | -0.0089892 | -0.0013138 | -0.005371 | 0.030008 | 0.09775 | 0.0073657 | 0.014898 | 0.023964 | -0.0031979 | 8.812 | 121.8842 | -0.054932 | 121.7331 | 0.15106 | -0.059509 | 0 | 0.068665 | -0.018311 | -0.045776 | 0.004578 | 0.10986 | 0.07782 | 0.086975 | 0.045776 | 0 | -0.15106 | 0.25177 | 0.10071 | 0.041199 | 0.054932 | -0.004577 | 0.054932 | -121.9025 | -121.8796 | 0.21057 | 0.18768 | 0.17853 | 0.13275 | 0.1236 | 0.20599 | 121.788 | 0.15564 | 0.050354 | 121.9391 | 0.027465 | 121.9849 | 0.082397 | -121.9391 | -121.9299 | 121.8338 | 0.10529 | 8.9127 | 0.16937
3010.3125 | 122.0444 | -0.11444 | 121.9345 | -0.012131 | 0.00055118 | 0.053854 | 0.048529 | -0.00048286 | -0.013475 | -0.0030228 | -0.011475 | 0.030648 | 0.090059 | 0.0026661 | 0.015325 | 0.021828 | -0.0068295 | 8.9722 | 121.8842 | -0.07782 | 121.7651 | 0.15564 | -0.018311 | 0.004578 | 0.041199 | -0.013733 | -0.050354 | -0.022888 | 0.09613 | 0.068665 | 0.073242 | 0.036621 | -0.050354 | -0.16937 | 0.27008 | 0.11902 | 0.09613 | 0.082398 | 0.059509 | 0.064087 | -121.9482 | -121.9574 | 0.21057 | 0.18768 | 0.18311 | 0.1236 | 0.11902 | 0.23346 | 121.843 | 0.14648 | 0.027466 | 121.962 | 0.036621 | 121.9986 | 0.10071 | -122.0123 | -121.9849 | 121.8796 | 0.091553 | 9.0866 | 0.15564
3012.0156 | 122.0901 | -0.10529 | 121.8979 | -0.012131 | 0.001192 | 0.054068 | 0.049383 | -0.0015509 | -0.008562 | -0.0028092 | -0.0023192 | 0.032571 | 0.097963 | 0.0018115 | 0.015966 | 0.024605 | -0.0036253 | 8.9767 | 121.8979 | -0.10529 | 121.7148 | 0.11902 | -0.068665 | -0.036621 | 0.013733 | -0.036621 | -0.054932 | 0.013733 | 0.11444 | 0.082397 | 0.09613 | 0 | 0 | -0.1831 | 0.22431 | 0.068665 | 0.036621 | 0.068665 | 0.036621 | 0.050354 | -121.9345 | -121.8842 | 0.21973 | 0.20142 | 0.18768 | 0.15106 | 0.13733 | 0.22431 | 121.8201 | 0.16937 | 0.068665 | 122.0032 | 0.018311 | 122.0032 | 0.068665 | -122.0032 | -121.9528 | 121.8201 | 0.11902 | 9.082 | 0.11902
3013.7812 | 122.1268 | -0.10986 | 121.907 | -0.012131 | 0.00055118 | 0.053214 | 0.049811 | -0.0043281 | -0.0092028 | -0.0028092 | -0.0084228 | 0.030862 | 0.10651 | 0.0052295 | 0.014898 | 0.024819 | -0.0055479 | 9.0775 | 121.8796 | -0.09613 | 121.7422 | 0.12817 | -0.041199 | -0.013733 | 0.027466 | -0.013733 | -0.045776 | 0.027466 | 0.14648 | 0.1236 | 0.1236 | 0.013733 | -0.027465 | -0.16479 | 0.23804 | 0.09613 | 0.068664 | 0.082397 | 0.054931 | 0.064087 | -121.9208 | -121.8796 | 0.25635 | 0.23346 | 0.23346 | 0.16937 | 0.16937 | 0.2243 | 121.8384 | 0.19226 | 0.073242 | 121.9757 | 0.032043 | 121.9894 | 0.09613 | -122.0032 | -121.9528 | 121.8521 | 0.13733 | 9.1873 | 0.13733
3015.4688 | 122.0261 | -0.15106 | 121.8933 | -0.0045011 | 0.00097838 | 0.054282 | 0.052588 | 0.00037174 | -0.00963 | -0.0019546 | -0.005371 | 0.034707 | 0.12103 | 0.0058703 | 0.014898 | 0.02546 | -0.0036253 | 9.2331 | 121.9025 | -0.13733 | 121.6644 | 0.036621 | -0.14648 | -0.10986 | -0.050354 | -0.004578 | -0.086975 | -0.036621 | 0.059509 | 0.027466 | 0.059509 | 0.013733 | 0.009155 | -0.22888 | 0.18768 | 0.041199 | 0.004578 | 0.027466 | -0.009155 | 0.064087 | -121.8979 | -121.9299 | 0.21057 | 0.21057 | 0.17853 | 0.14648 | 0.11444 | 0.17395 | 121.8018 | 0.14648 | 0.050354 | 122.0398 | 0.082397 | 122.0535 | 0.14648 | -122.0306 | -121.9803 | 121.8155 | 0.11444 | 9.3842 | 0.10071
3017.2188 | 121.9986 | -0.091553 | 121.9528 | -0.012131 | 0.0048236 | 0.054282 | 0.054083 | 0.0012261 | -0.010485 | -0.0025956 | -0.011475 | 0.016763 | 0.033876 | -0.013356 | 0.018957 | 0.022896 | -0.0070433 | 9.343 | 121.9299 | -0.068665 | 121.7148 | 0.13275 | -0.064087 | -0.045776 | 0.004578 | 0.004578 | -0.018311 | -0.018311 | 0.064087 | 0.036621 | 0.059509 | 0.022888 | -0.022888 | -0.23804 | 0.2243 | 0.045777 | 0.027466 | 0.022889 | 0.004578 | 0.073242 | -121.9482 | -121.9711 | 0.15564 | 0.15106 | 0.12817 | 0.07782 | 0.054932 | 0.20142 | 121.7834 | 0.082398 | 0 | 121.9986 | 0.022889 | 122.0215 | 0.096131 | -122.0215 | -121.9711 | 121.8063 | 0.073242 | 9.4345 | 0.096131
3018.9844 | 121.994 | -0.11444 | 121.9437 | -0.01976 | 0.0084552 | 0.054709 | 0.051733 | -0.0013373 | -0.010057 | -0.001741 | -0.0023192 | 0.017617 | 0.048403 | -0.0035291 | 0.017675 | 0.024605 | -0.0027707 | 9.3796 | 121.9482 | -0.091553 | 121.6599 | 0.059509 | -0.15564 | -0.09613 | -0.050354 | 0 | -0.050354 | -0.064087 | 0.018311 | -0.004578 | 0.041199 | 0.022888 | 0.004577 | -0.28381 | 0.17395 | 0.018311 | -0.041199 | -0.004577 | -0.064087 | 0.064087 | -121.9437 | -122.0078 | 0.13275 | 0.15564 | 0.10986 | 0.091553 | 0.045776 | 0.15106 | 121.7514 | 0.068665 | -0.013733 | 122.0398 | 0.050354 | 122.0627 | 0.11444 | -122.0352 | -121.994 | 121.7743 | 0.050354 | 9.494 | 0.064087
3020.6875 | 122.0535 | -0.09613 | 121.9528 | -0.0045011 | 0.00076478 | 0.052359 | 0.050238 | -0.0041145 | -0.011339 | -0.00345 | -0.0023192 | 0.013986 | 0.04883 | -0.012501 | 0.018316 | 0.025673 | 0.00043375 | 9.5444 | 121.875 | -0.064087 | 121.7834 | 0.20599 | 0.018311 | 0.036621 | 0.064087 | -0.018311 | -0.022888 | 0.009155 | 0.10986 | 0.091553 | 0.09613 | 0.032043 | -0.07782 | -0.16937 | 0.30212 | 0.13275 | 0.11444 | 0.10071 | 0.082398 | 0.073242 | -121.9711 | -121.9437 | 0.20599 | 0.19226 | 0.18768 | 0.11902 | 0.11444 | 0.27008 | 121.8475 | 0.13275 | 0.032043 | 121.9391 | 0.004577 | 121.9711 | 0.077819 | -122.0169 | -121.9757 | 121.8796 | 0.10528 | 9.6405 | 0.16022
3022.4531 | 122.0306 | -0.09613 | 121.9482 | -0.012131 | 0.0041828 | 0.053 | 0.051306 | 0.0014397 | -0.0089892 | -0.0038772 | -0.0084228 | 0.015054 | 0.053102 | -0.0037427 | 0.01853 | 0.024605 | -0.00042085 | 9.5535 | 121.9666 | -0.086975 | 121.6736 | 0.064087 | -0.11444 | -0.07782 | -0.027466 | 0.009155 | -0.045776 | -0.027466 | 0.050354 | 0.022888 | 0.059509 | 0.009155 | 0.018311 | -0.27466 | 0.16022 | 0.01831 | -0.018311 | 0.009155 | -0.027466 | 0.050354 | -121.9391 | -121.9757 | 0.14648 | 0.15564 | 0.11902 | 0.10528 | 0.068664 | 0.15106 | 121.7606 | 0.09613 | 0.01831 | 122.0535 | 0.054931 | 122.0627 | 0.10528 | -122.0352 | -121.994 | 121.7697 | 0.068664 | 9.6497 | 0.068664
3024.1562 | 121.9849 | -0.11902 | 121.9391 | -0.0045011 | 0.00461 | 0.052573 | 0.054297 | 0.0067803 | -0.0074938 | -0.0040908 | -0.0084228 | 0.018258 | 0.050966 | -0.0069469 | 0.016607 | 0.025032 | -0.0055479 | 9.6909 | 121.9666 | -0.086975 | 121.701 | 0.091553 | -0.12817 | -0.082397 | -0.054932 | 0.018311 | -0.045776 | -0.059509 | 0.013733 | -0.009155 | 0.036621 | 0.032044 | 0.027466 | -0.23804 | 0.21057 | 0.036622 | -0.009155 | 0.004578 | -0.041199 | 0.073243 | -121.9208 | -121.9986 | 0.13275 | 0.15564 | 0.10986 | 0.082397 | 0.036621 | 0.17853 | 121.788 | 0.059509 | -0.013733 | 122.0535 | 0.064087 | 122.0856 | 0.13733 | -122.0261 | -121.9849 | 121.8201 | 0.05951 | 9.8099 | 0.064087
3025.9062 | 122.0764 | -0.068665 | 121.9299 | -0.01976 | 0.0020466 | 0.053 | 0.05152 | 0.0014397 | -0.0059986 | -0.0025956 | -0.005371 | 0.014199 | 0.050966 | -0.013142 | 0.012975 | 0.0261 | -0.0019163 | 9.7412 | 121.9025 | -0.054932 | 121.7514 | 0.16479 | -0.027466 | 0.009155 | 0.036621 | -0.032043 | -0.022888 | 0.009155 | 0.10071 | 0.091553 | 0.086975 | 0.013733 | -0.027466 | -0.17853 | 0.23346 | 0.07782 | 0.041199 | 0.064087 | 0.027466 | 0.045777 | -121.962 | -121.9208 | 0.16937 | 0.15564 | 0.16022 | 0.10986 | 0.11444 | 0.21973 | 121.8063 | 0.1236 | 0.032043 | 121.9574 | -0.009155 | 121.9711 | 0.036622 | -121.9849 | -121.9528 | 121.8201 | 0.07782 | 9.8099 | 0.10529
3027.6719 | 121.994 | -0.11444 | 121.9803 | 0.0031279 | 0.0026874 | 0.051505 | 0.048956 | -0.00026906 | -0.008562 | -0.0055862 | -0.005371 | 0.015908 | 0.051821 | -0.0060925 | 0.015112 | 0.024605 | -0.0036253 | 9.8099 | 121.9528 | -0.086975 | 121.6919 | 0.086975 | -0.091553 | -0.059509 | -0.054932 | 0.009155 | -0.050354 | -0.064087 | 0.041199 | 0.041199 | 0.027466 | 0.027466 | -0.027466 | -0.28839 | 0.20142 | 0.054932 | 0.022888 | 0.027466 | -0.004578 | 0.064087 | -121.9711 | -122.0444 | 0.15564 | 0.14191 | 0.15564 | 0.07782 | 0.091553 | 0.17395 | 121.7789 | 0.091553 | -0.013733 | 122.0398 | 0.059509 | 122.0673 | 0.1236 | -122.0673 | -122.0306 | 121.8063 | 0.050354 | 9.9243 | 0.059509
3029.375 | 122.113 | -0.064087 | 121.9299 | -0.012131 | 0.00055118 | 0.053214 | 0.048742 | 0.0016535 | -0.0098438 | -0.0062272 | -0.0023192 | 0.014627 | 0.048616 | -0.011433 | 0.013189 | 0.024605 | -0.0038389 | 9.9152 | 121.9208 | -0.054932 | 121.7606 | 0.16937 | -0.022888 | 0.018311 | 0.045776 | -0.036621 | -0.032043 | 0.022888 | 0.14648 | 0.12817 | 0.11444 | 0.009155 | -0.009156 | -0.16937 | 0.23346 | 0.082398 | 0.041199 | 0.073243 | 0.032044 | 0.032044 | -121.9666 | -121.907 | 0.21057 | 0.17853 | 0.19226 | 0.14648 | 0.16022 | 0.22431 | 121.8155 | 0.17853 | 0.054931 | 121.9757 | -0.004578 | 121.9849 | 0.027466 | -121.9849 | -121.962 | 121.8246 | 0.086975 | 9.9792 | 0.10986
3031.1406 | 122.1405 | -0.082397 | 121.9437 | -0.012131 | 0.00055118 | 0.051932 | 0.049383 | 0.0010125 | -0.0079212 | -0.0021682 | -0.005371 | 0.012918 | 0.049898 | -0.011647 | 0.014257 | 0.024819 | -0.0034117 | 10.0708 | 121.8933 | -0.054932 | 121.8155 | 0.24719 | 0.036621 | 0.059509 | 0.10986 | -0.036621 | -0.018311 | 0.050354 | 0.1831 | 0.15564 | 0.1236 | 0.027465 | -0.050354 | -0.12817 | 0.32959 | 0.14191 | 0.11902 | 0.11444 | 0.091553 | 0.064086 | -121.9803 | -121.8933 | 0.2655 | 0.20599 | 0.23804 | 0.14191 | 0.17395 | 0.30212 | 121.8704 | 0.20142 | 0.068665 | 121.9482 | -0.01831 | 121.9757 | 0.045776 | -121.9986 | -121.962 | 121.8979 | 0.13275 | 10.1532 | 0.19226
3032.9062 | 122.0993 | -0.073242 | 121.8979 | -0.012131 | 0.0033282 | 0.052359 | 0.049597 | 0.00037174 | -0.00963 | -0.0036636 | 0.00073235 | 0.015054 | 0.04883 | -0.0048107 | 0.01618 | 0.025246 | -0.0029843 | 10.1212 | 121.9208 | -0.059509 | 121.788 | 0.2243 | -0.009155 | 0.041199 | 0.11902 | -0.027466 | -0.009155 | 0.054932 | 0.14191 | 0.11902 | 0.11902 | 0.013733 | 0.022888 | -0.10986 | 0.29755 | 0.11444 | 0.064087 | 0.10071 | 0.050354 | 0.064087 | -121.9254 | -121.843 | 0.21515 | 0.19226 | 0.19226 | 0.12817 | 0.12817 | 0.28381 | 121.8475 | 0.15106 | 0.064087 | 121.9803 | -0.018311 | 121.994 | 0.045776 | -121.9574 | -121.907 | 121.8613 | 0.12817 | 10.1944 | 0.19226
3034.6719 | 121.9849 | -0.1236 | 121.962 | -0.012131 | 0.0052508 | 0.053 | 0.053442 | 0.0025079 | -0.00963 | -0.000673 | -0.005371 | 0.015054 | 0.052889 | -0.0054517 | 0.017461 | 0.023537 | -0.0051205 | 10.2036 | 121.9803 | -0.086975 | 121.7102 | 0.082397 | -0.11902 | -0.07782 | -0.050354 | 0.022888 | -0.041199 | -0.059509 | 0.022888 | -0.013733 | 0.027466 | 0.036621 | 0.018311 | -0.25177 | 0.20599 | 0.045776 | 0.004577 | 0.009155 | -0.032044 | 0.082397 | -121.9391 | -122.0215 | 0.14648 | 0.15106 | 0.10986 | 0.068665 | 0.027466 | 0.16937 | 121.7972 | 0.064087 | -0.01831 | 122.0673 | 0.064087 | 122.1039 | 0.14648 | -122.0489 | -122.0032 | 121.8338 | 0.064087 | 10.3271 | 0.073242
3036.375 | 121.9986 | -0.12817 | 121.9849 | -0.012131 | 0.00055118 | 0.051932 | 0.052588 | 0.0059259 | -0.010271 | -0.0028092 | -0.005371 | 0.018686 | 0.050966 | -0.0071607 | 0.016393 | 0.027169 | -0.0089659 | 10.2631 | 121.9482 | -0.10529 | 121.6736 | 0.064087 | -0.11444 | -0.082397 | -0.064087 | 0.009155 | -0.054932 | -0.07782 | 0.036621 | 0.018311 | 0.045776 | 0.022888 | -0.036621 | -0.31128 | 0.19226 | 0.045777 | 0.013733 | 0.022889 | -0.009155 | 0.073242 | -121.9757 | -122.0627 | 0.1648 | 0.17395 | 0.14649 | 0.10071 | 0.073243 | 0.16937 | 121.7789 | 0.091553 | -0.022888 | 122.0535 | 0.064087 | 122.0764 | 0.13733 | -122.0901 | -122.0398 | 121.8018 | 0.050354 | 10.3912 | 0.064087
3038.1406 | 122.1039 | -0.068665 | 121.9574 | -0.0045011 | 0.0048236 | 0.053427 | 0.054724 | 0.0033623 | -0.0092028 | -0.0015274 | -0.0084228 | 0.014413 | 0.052034 | -0.0065197 | 0.017675 | 0.024178 | -0.0031979 | 10.3226 | 121.9803 | -0.068665 | 121.7239 | 0.11902 | -0.091553 | -0.041199 | 0.045776 | -0.009155 | -0.018311 | 0.036621 | 0.12817 | 0.073242 | 0.11902 | 0 | 0.022889 | -0.23346 | 0.18768 | 0.027466 | -0.022888 | 0.027466 | -0.022888 | 0.050354 | -121.9666 | -121.9208 | 0.19684 | 0.18768 | 0.14191 | 0.13733 | 0.091553 | 0.18768 | 121.7926 | 0.14649 | 0.054932 | 122.049 | 0.009156 | 122.049 | 0.05951 | -122.0261 | -121.9757 | 121.7926 | 0.10529 | 10.3912 | 0.11444
3039.8438 | 122.0444 | -0.086975 | 121.994 | -0.012131 | 0.00461 | 0.053641 | 0.049383 | 0.0048577 | -0.0087756 | -0.0008866 | -0.0023192 | 0.01484 | 0.05118 | -0.0050243 | 0.017034 | 0.025673 | -0.0025571 | 10.5148 | 121.962 | -0.086975 | 121.7422 | 0.13275 | -0.054932 | -0.045776 | 0.027466 | 0.004578 | -0.027466 | 0 | 0.086975 | 0.054932 | 0.082397 | 0 | -0.032044 | -0.25177 | 0.21973 | 0.041199 | 0.032043 | 0.041199 | 0.032043 | 0.059509 | -121.9894 | -121.994 | 0.17395 | 0.16937 | 0.14191 | 0.10986 | 0.082398 | 0.21973 | 121.8292 | 0.11444 | 0.027466 | 122.0489 | 0.032044 | 122.0489 | 0.091553 | -122.081 | -122.0215 | 121.8292 | 0.086975 | 10.6018 | 0.11444
3041.625 | 122.0261 | -0.10071 | 122.0078 | -0.0045011 | 0.0041828 | 0.053214 | 0.051947 | -5.5462e-05 | -0.0079212 | -0.0030228 | -0.0084228 | 0.018258 | 0.053102 | 0.0018115 | 0.016607 | 0.027169 | -0.0014891 | 10.6018 | 121.9437 | -0.082397 | 121.7377 | 0.13733 | -0.082397 | -0.036621 | 0.022888 | 0.004578 | -0.036621 | -0.022888 | 0.054932 | 0.022888 | 0.041199 | 0.018311 | -0.064086 | -0.27008 | 0.23804 | 0.064087 | 0.018311 | 0.045776 | 0 | 0.064087 | -122.0032 | -122.0306 | 0.15564 | 0.14191 | 0.1236 | 0.07782 | 0.059509 | 0.21973 | 121.8201 | 0.091553 | 0.013733 | 122.0261 | 0.041199 | 122.0444 | 0.10529 | -122.0901 | -122.0444 | 121.8384 | 0.07782 | 10.7025 | 0.1236
3043.3906 | 122.1497 | -0.068665 | 121.9299 | -0.01976 | 0.00055118 | 0.051932 | 0.048742 | -0.00091006 | -0.0079212 | -0.0036636 | -0.005371 | 0.013345 | 0.054384 | -0.0065197 | 0.014043 | 0.027809 | -0.0040525 | 10.6888 | 121.9025 | -0.054932 | 121.8109 | 0.2655 | 0.054932 | 0.082397 | 0.14191 | -0.041199 | -0.009155 | 0.045776 | 0.19684 | 0.16937 | 0.13275 | 0.013733 | -0.027466 | -0.11902 | 0.33417 | 0.15106 | 0.1236 | 0.13733 | 0.10986 | 0.05951 | -121.9711 | -121.8842 | 0.2655 | 0.20142 | 0.23804 | 0.14191 | 0.17853 | 0.32043 | 121.8658 | 0.20599 | 0.054931 | 121.9574 | -0.032044 | 121.9711 | 0.027466 | -121.9849 | -121.9391 | 121.8796 | 0.11444 | 10.7574 | 0.21057
3045.0938 | 122.113 | -0.054932 | 121.907 | -0.012131 | 0.0037556 | 0.054922 | 0.051092 | 0.0035761 | -0.0055712 | -0.0025956 | 0.00073235 | 0.013772 | 0.050966 | -0.0048107 | 0.016607 | 0.025032 | -0.0021299 | 10.7437 | 121.9482 | -0.045776 | 121.8018 | 0.2243 | -0.013733 | 0.041199 | 0.11444 | -0.036621 | -0.004578 | 0.059509 | 0.16022 | 0.11902 | 0.13275 | 0.009156 | 0.041199 | -0.10528 | 0.27924 | 0.096131 | 0.041199 | 0.086975 | 0.032043 | 0.050354 | -121.9437 | -121.8475 | 0.21515 | 0.18768 | 0.17395 | 0.13733 | 0.1236 | 0.27008 | 121.8475 | 0.16479 | 0.064087 | 121.994 | -0.032043 | 122.0032 | 0.018311 | -121.9528 | -121.9116 | 121.8567 | 0.11444 | 10.7986 | 0.16937
3046.8594 | 121.9803 | -0.10529 | 121.9757 | 0.010757 | 0.0061054 | 0.054495 | 0.052801 | 0.0016535 | -0.00963 | 0.0008224 | -0.005371 | 0.015054 | 0.050325 | -0.0050243 | 0.018316 | 0.025032 | -0.0021299 | 10.7941 | 121.994 | -0.086975 | 121.7102 | 0.082397 | -0.1236 | -0.082397 | -0.059509 | 0.013733 | -0.041199 | -0.054932 | -0.004578 | -0.018311 | 0.018311 | 0.018311 | 0.018311 | -0.2655 | 0.18768 | 0.022889 | -0.01831 | 0.004578 | -0.036621 | 0.064087 | -121.962 | -122.0306 | 0.10071 | 0.1236 | 0.086975 | 0.05951 | 0.022888 | 0.16937 | 121.7972 | 0.036621 | -0.013733 | 122.081 | 0.054932 | 122.0993 | 0.11902 | -122.0627 | -122.0169 | 121.8155 | 0.050354 | 10.8994 | 0.045777
3048.5781 | 122.0581 | -0.086975 | 121.9757 | -0.0045011 | 0.0037556 | 0.053 | 0.050879 | 0.00015814 | -0.0094164 | -0.0038772 | -0.011475 | 0.01719 | 0.050966 | -0.0056653 | 0.015752 | 0.024391 | 0.0012881 | 10.9314 | 121.9757 | -0.10071 | 121.7422 | 0.15106 | -0.068665 | -0.041199 | 0.022888 | -0.009155 | -0.009155 | -0.009155 | 0.091553 | 0.068665 | 0.086975 | -0.013733 | 0 | -0.23346 | 0.23804 | 0.045776 | 0.01831 | 0.059509 | 0.032043 | 0.07782 | -121.9849 | -121.9849 | 0.17853 | 0.17395 | 0.15564 | 0.09613 | 0.07782 | 0.25177 | 121.843 | 0.10071 | 0 | 122.0764 | 0 | 122.0627 | 0.07782 | -122.0764 | -121.9849 | 121.8292 | 0.07782 | 11.0184 | 0.10986
3050.3438 | 122.0901 | -0.068665 | 121.9528 | -0.012131 | 0.00055118 | 0.054922 | 0.048956 | 0.0012261 | -0.011553 | -0.0028092 | -0.0084228 | 0.014627 | 0.054384 | -0.010579 | 0.014043 | 0.02546 | -0.0049069 | 10.9497 | 121.9254 | -0.068665 | 121.7514 | 0.15106 | -0.050354 | -0.013733 | 0.022888 | -0.045776 | -0.022888 | -0.009155 | 0.10529 | 0.082397 | 0.10986 | 0 | -0.027466 | -0.20142 | 0.21973 | 0.054932 | 0.018311 | 0.054932 | 0.018311 | 0.045777 | -121.9986 | -121.962 | 0.17395 | 0.17853 | 0.15106 | 0.13275 | 0.10528 | 0.21973 | 121.8201 | 0.12817 | 0.013733 | 121.994 | -0.022888 | 121.994 | 0.022889 | -122.0215 | -121.9757 | 121.8201 | 0.05951 | 11.0184 | 0.091553
3052.0938 | 122.1176 | -0.07782 | 121.9711 | -0.012131 | 0.0016192 | 0.052359 | 0.048529 | -0.0021919 | -0.010485 | -0.0032364 | -0.0023192 | 0.016122 | 0.050325 | -0.0088695 | 0.014257 | 0.026528 | -0.0029843 | 11.087 | 121.8933 | -0.041199 | 121.8109 | 0.21973 | 0.027466 | 0.045776 | 0.073242 | -0.022888 | -0.027466 | 0.027466 | 0.14191 | 0.1236 | 0.10529 | 0.036621 | -0.077819 | -0.16022 | 0.29755 | 0.1236 | 0.10529 | 0.086975 | 0.068665 | 0.050354 | -121.994 | -121.9437 | 0.21973 | 0.18311 | 0.20142 | 0.13275 | 0.15106 | 0.26093 | 121.8521 | 0.16937 | 0.054932 | 121.9345 | 0.004578 | 121.9711 | 0.054932 | -122.0123 | -121.9986 | 121.8887 | 0.10529 | 11.1649 | 0.15106
3053.8125 | 121.9986 | -0.10529 | 121.9666 | -0.012131 | 0.0052508 | 0.055136 | 0.053442 | 0.0022943 | -0.008562 | -0.0049454 | -0.0084228 | 0.016549 | 0.053743 | 0.00010247 | 0.017034 | 0.025246 | -0.0046933 | 11.1145 | 122.0078 | -0.10986 | 121.6782 | 0.050354 | -0.16022 | -0.11902 | -0.09613 | 0.004578 | -0.050354 | -0.073242 | 0 | -0.013733 | 0.027466 | -0.004577 | 0.041198 | -0.28839 | 0.15564 | -0.013733 | -0.054931 | -0.009156 | -0.050354 | 0.054932 | -121.962 | -122.0398 | 0.10529 | 0.13275 | 0.091553 | 0.07782 | 0.036621 | 0.16022 | 121.788 | 0.050354 | -0.022888 | 122.1176 | 0.054932 | 122.113 | 0.10986 | -122.0764 | -122.0169 | 121.7834 | 0.032044 | 11.2198 | 0.009156
3055.5781 | 122.081 | -0.07782 | 121.9482 | -0.012131 | 0.0022602 | 0.053214 | 0.050024 | -0.00048286 | -0.0074938 | -0.002382 | -0.0023192 | 0.014199 | 0.05353 | -0.013783 | 0.014898 | 0.022683 | -0.0044797 | 11.1969 | 121.9254 | -0.050354 | 121.7697 | 0.23346 | -0.018311 | 0.036621 | 0.082397 | -0.022888 | -0.018311 | 0.027466 | 0.11902 | 0.10986 | 0.10529 | 0.027466 | -0.022888 | -0.17853 | 0.31128 | 0.11444 | 0.059509 | 0.086975 | 0.032043 | 0.059509 | -121.9711 | -121.9208 | 0.19684 | 0.18311 | 0.18768 | 0.1236 | 0.12817 | 0.28381 | 121.8201 | 0.13733 | 0.045777 | 121.9757 | -0.004577 | 122.0032 | 0.054932 | -121.9986 | -121.9666 | 121.8475 | 0.10529 | 11.2747 | 0.16022
3057.3438 | 122.0306 | -0.11444 | 121.9528 | -0.012131 | 0.00055118 | 0.051077 | 0.051947 | 0.00037174 | -0.010912 | -0.0015274 | -0.0084228 | 0.015695 | 0.049898 | -0.0048107 | 0.01618 | 0.024605 | -0.0034117 | 11.3434 | 121.9437 | -0.054932 | 121.7697 | 0.17395 | -0.022888 | 0 | 0.004578 | 0 | -0.041199 | -0.041199 | 0.068665 | 0.041199 | 0.050354 | 0.059509 | -0.009155 | -0.18311 | 0.28839 | 0.11444 | 0.091553 | 0.054932 | 0.032044 | 0.073242 | -121.9528 | -121.994 | 0.18311 | 0.16479 | 0.15564 | 0.091553 | 0.082398 | 0.22888 | 121.8246 | 0.10986 | 0 | 121.9986 | 0.041199 | 122.0581 | 0.11444 | -122.0078 | -121.994 | 121.8842 | 0.073242 | 11.4578 | 0.11902
3059.1406 | 122.1542 | -0.068665 | 121.9345 | -0.012131 | 0.00012398 | 0.051077 | 0.048315 | -0.00069646 | -0.011125 | -0.0011002 | -0.005371 | 0.014627 | 0.053957 | -0.0071607 | 0.013616 | 0.024178 | -0.0066159 | 11.3892 | 121.9116 | -0.068665 | 121.8018 | 0.25177 | 0.027466 | 0.059509 | 0.13275 | -0.027466 | 0 | 0.054932 | 0.19226 | 0.16479 | 0.14648 | 0 | -0.022888 | -0.13275 | 0.32044 | 0.12817 | 0.096131 | 0.12817 | 0.096131 | 0.068665 | -121.962 | -121.8796 | 0.26093 | 0.21515 | 0.23346 | 0.14648 | 0.16479 | 0.32044 | 121.8704 | 0.19226 | 0.054932 | 121.9803 | -0.027466 | 121.9803 | 0.041199 | -122.0032 | -121.9345 | 121.8704 | 0.1236 | 11.4578 | 0.20142
3060.8438 | 122.0901 | -0.073242 | 121.9391 | -0.01976 | 0.0026874 | 0.053214 | 0.048529 | 0.00015814 | -0.0064258 | -0.0021682 | -0.0084228 | 0.016122 | 0.05353 | -0.010365 | 0.01383 | 0.02546 | -0.0034117 | 11.4807 | 121.9345 | -0.050354 | 121.7743 | 0.17853 | -0.045776 | 0.009155 | 0.036621 | -0.022888 | -0.013733 | 0.004578 | 0.10071 | 0.082397 | 0.068665 | 0.022888 | -0.004578 | -0.16479 | 0.25177 | 0.082397 | 0.027466 | 0.059509 | 0.004578 | 0.059509 | -121.962 | -121.9345 | 0.17395 | 0.14191 | 0.15564 | 0.082398 | 0.09613 | 0.22888 | 121.8246 | 0.11444 | 0.018311 | 121.9849 | -0.009155 | 122.0078 | 0.050354 | -121.9894 | -121.9528 | 121.8475 | 0.07782 | 11.554 | 0.10986
3062.5938 | 122.0901 | -0.09613 | 121.9391 | -0.01976 | -0.00030342 | 0.052145 | 0.047247 | -0.0011237 | -0.0092028 | -0.0021682 | -0.0023192 | 0.01484 | 0.051821 | -0.0078015 | 0.013616 | 0.024391 | -0.0044797 | 11.6455 | 121.9254 | -0.054932 | 121.7972 | 0.22888 | 0.036621 | 0.068665 | 0.059509 | -0.009155 | -0.032043 | 0.004578 | 0.1236 | 0.10071 | 0.086975 | 0.041198 | -0.013733 | -0.14191 | 0.32501 | 0.16479 | 0.13275 | 0.1236 | 0.091553 | 0.064087 | -121.9482 | -121.9345 | 0.21973 | 0.1831 | 0.19684 | 0.11902 | 0.13275 | 0.28381 | 121.8521 | 0.15564 | 0.036621 | 121.9803 | 0.022888 | 122.0215 | 0.086975 | -121.994 | -121.9711 | 121.8933 | 0.10071 | 11.7416 | 0.15564
3064.2969 | 122.1405 | -0.068665 | 121.9482 | -0.012131 | 0.00076478 | 0.053641 | 0.049383 | 0.0018671 | -0.0089892 | -0.002382 | 0.00073235 | 0.015695 | 0.053316 | -0.0090833 | 0.014043 | 0.023751 | -0.00063445 | 11.6821 | 121.9391 | -0.050354 | 121.7972 | 0.2243 | 0.009155 | 0.054932 | 0.086975 | -0.041199 | -0.027466 | 0.045776 | 0.17853 | 0.15564 | 0.14191 | 0.018311 | -0.009155 | -0.15106 | 0.29297 | 0.1236 | 0.07782 | 0.10529 | 0.059509 | 0.041199 | -121.9894 | -121.9025 | 0.24719 | 0.21057 | 0.22431 | 0.16937 | 0.18311 | 0.27466 | 121.8475 | 0.20599 | 0.073242 | 121.9894 | -0.013733 | 122.0078 | 0.027466 | -121.9986 | -121.9757 | 121.8658 | 0.11444 | 11.7508 | 0.15564
3066.0469 | 122.081 | -0.10071 | 121.9849 | -0.012131 | -0.0020124 | 0.054068 | 0.049597 | -0.00091006 | -0.008562 | -0.002382 | -0.0084228 | 0.01484 | 0.034731 | -0.0071607 | 0.013616 | 0.022469 | -0.0012753 | 11.8195 | 121.9391 | -0.041199 | 121.8018 | 0.22888 | 0.013733 | 0.036621 | 0.054932 | -0.018311 | -0.022888 | -0.018311 | 0.091553 | 0.09613 | 0.07782 | 0.059509 | -0.045776 | -0.1831 | 0.32959 | 0.13733 | 0.11444 | 0.07782 | 0.054932 | 0.07782 | -122.0032 | -122.0032 | 0.19226 | 0.17853 | 0.19684 | 0.10071 | 0.11902 | 0.27008 | 121.843 | 0.11444 | 0.004577 | 121.9803 | 0.004577 | 122.0398 | 0.082397 | -122.0261 | -122.0078 | 121.9025 | 0.082397 | 11.9202 | 0.15564
3067.8125 | 122.1085 | -0.073242 | 121.9162 | -0.0045011 | 0.0065326 | 0.054922 | 0.049597 | -0.0015509 | -0.0087756 | -0.0060134 | -0.005371 | 0.015481 | 0.050112 | -0.0011791 | 0.015325 | 0.023537 | -0.0066159 | 11.8286 | 121.9391 | -0.041199 | 121.8246 | 0.24261 | -0.004578 | 0.050354 | 0.10529 | -0.032043 | -0.004578 | 0.045776 | 0.14648 | 0.13275 | 0.11444 | 0.032043 | 0.022888 | -0.091553 | 0.31586 | 0.1236 | 0.068664 | 0.091553 | 0.036621 | 0.068664 | -121.9482 | -121.8704 | 0.21973 | 0.18768 | 0.20599 | 0.11902 | 0.13733 | 0.28381 | 121.8658 | 0.15106 | 0.050354 | 121.9803 | -0.027465 | 122.0123 | 0.041199 | -121.9574 | -121.9208 | 121.8979 | 0.11902 | 11.9019 | 0.17853
3069.5156 | 121.9986 | -0.1236 | 121.9849 | -0.01976 | 0.001833 | 0.052359 | 0.050024 | 0.0010125 | -0.0083484 | -0.0013138 | -0.005371 | 0.016122 | 0.053316 | -0.0099377 | 0.016821 | 0.024605 | -0.0040525 | 11.911 | 121.9711 | -0.086975 | 121.7239 | 0.14191 | -0.082397 | -0.059509 | -0.041199 | 0.009155 | -0.054932 | -0.07782 | 0.027466 | 0.022888 | 0.009155 | 0.036621 | -0.013733 | -0.26093 | 0.2655 | 0.064087 | 0.041199 | 0.027466 | 0.004578 | 0.068664 | -121.9757 | -122.0627 | 0.15106 | 0.13275 | 0.14648 | 0.064087 | 0.07782 | 0.22888 | 121.8109 | 0.082398 | -0.022888 | 122.0581 | 0.064087 | 122.0947 | 0.13275 | -122.0718 | -122.0398 | 121.8475 | 0.045776 | 12.0346 | 0.082397
3071.2656 | 122.0261 | -0.10071 | 121.9482 | -0.02739 | 0.00461 | 0.055777 | 0.052801 | 0.0020807 | -0.0089892 | -0.001741 | -0.005371 | 0.016549 | 0.045626 | -0.0084423 | 0.017248 | 0.025246 | -0.0051205 | 12.0163 | 121.9528 | -0.09613 | 121.7697 | 0.17853 | -0.050354 | -0.027466 | 0.041199 | -0.004578 | -0.036621 | -0.013733 | 0.073242 | 0.045776 | 0.059509 | 0.004578 | 0.004578 | -0.17853 | 0.27924 | 0.073242 | 0.050354 | 0.068664 | 0.045776 | 0.064087 | -121.9528 | -121.962 | 0.17395 | 0.16022 | 0.14648 | 0.09613 | 0.082397 | 0.27466 | 121.8658 | 0.10986 | 0.022888 | 122.049 | 0.032043 | 122.0535 | 0.09613 | -122.0444 | -121.9849 | 121.8704 | 0.086975 | 12.117 | 0.14191
3072.9688 | 122.1588 | -0.068665 | 121.9757 | -0.0045011 | 0.00033758 | 0.051932 | 0.050451 | -0.0019781 | -0.0081348 | -0.0030228 | -0.005371 | 0.014413 | 0.04648 | -0.0041699 | 0.01618 | 0.027382 | -0.0066159 | 12.0987 | 121.9391 | -0.045776 | 121.8109 | 0.27466 | 0.041199 | 0.082397 | 0.13275 | -0.032043 | -0.013733 | 0.073242 | 0.20142 | 0.17395 | 0.14648 | 0.022889 | -0.036621 | -0.16479 | 0.34332 | 0.15106 | 0.10986 | 0.12817 | 0.086975 | 0.054932 | -122.0078 | -121.9025 | 0.27008 | 0.21515 | 0.24261 | 0.16022 | 0.18768 | 0.32043 | 121.8567 | 0.21515 | 0.086975 | 121.9849 | -0.01831 | 122.0078 | 0.036622 | -122.0215 | -121.9894 | 121.8796 | 0.14191 | 12.1674 | 0.20142
3074.75 | 122.0261 | -0.10986 | 121.9803 | -0.012131 | -0.00051702 | 0.053 | 0.051306 | -0.00069646 | -0.012194 | -0.002382 | -0.0084228 | 0.018045 | 0.049898 | -0.0045971 | 0.018102 | 0.026314 | -0.0031979 | 12.1582 | 121.962 | -0.091553 | 121.701 | 0.09613 | -0.091553 | -0.073242 | -0.073242 | 0 | -0.054932 | -0.045776 | 0.041199 | 0.027466 | 0.032043 | 0.01831 | -0.018311 | -0.27924 | 0.20599 | 0.036621 | 0.01831 | 0.018311 | 0 | 0.054931 | -121.9803 | -122.0261 | 0.15106 | 0.14191 | 0.13733 | 0.086975 | 0.082398 | 0.18768 | 121.7926 | 0.096131 | 0.009156 | 122.0535 | 0.054932 | 122.0718 | 0.10986 | -122.0718 | -122.0352 | 121.8109 | 0.064087 | 12.2681 | 0.036621
3076.5156 | 122.1451 | -0.054932 | 121.9437 | -0.0045011 | 0.00097838 | 0.053214 | 0.048956 | -0.00048286 | -0.0094164 | -0.001741 | 0.00073235 | 0.01484 | 0.047335 | -0.0075879 | 0.016821 | 0.025673 | -0.0017027 | 12.2543 | 121.9208 | -0.059509 | 121.8063 | 0.23346 | 0.018311 | 0.050354 | 0.082397 | -0.022888 | -0.018311 | 0.045776 | 0.17395 | 0.16022 | 0.13275 | -0.004577 | -0.022889 | -0.13733 | 0.28839 | 0.10529 | 0.073243 | 0.10986 | 0.07782 | 0.036621 | -121.9666 | -121.8979 | 0.22888 | 0.18768 | 0.21515 | 0.15106 | 0.17853 | 0.29297 | 121.8658 | 0.19226 | 0.064087 | 121.9803 | -0.004577 | 121.9757 | 0.032044 | -122.0032 | -121.962 | 121.8613 | 0.10071 | 12.3093 | 0.13733
3078.2656 | 122.0673 | -0.10071 | 121.9666 | -0.0045011 | 0.0022602 | 0.053214 | 0.053228 | 0.0025079 | -0.0079212 | -0.0025956 | -0.005371 | 0.016763 | 0.049685 | -0.0031017 | 0.015966 | 0.024391 | -0.0012753 | 12.355 | 121.9208 | -0.068665 | 121.7514 | 0.17853 | -0.059509 | -0.027466 | 0.022888 | 0 | -0.032043 | -0.004578 | 0.091553 | 0.059509 | 0.07782 | 0.032043 | -0.045777 | -0.21515 | 0.27924 | 0.073242 | 0.041199 | 0.041199 | 0.009156 | 0.068665 | -121.9666 | -121.9711 | 0.19226 | 0.17853 | 0.16022 | 0.10986 | 0.091552 | 0.24719 | 121.8201 | 0.1236 | 0.027465 | 121.9894 | 0.032043 | 122.0215 | 0.10071 | -122.0352 | -121.9986 | 121.8521 | 0.09613 | 12.4557 | 0.1236
3079.9688 | 122.049 | -0.10986 | 121.9757 | -0.0045011 | 0.0024738 | 0.053854 | 0.051947 | 0.00037174 | -0.010057 | -0.0032364 | -0.005371 | 0.018258 | 0.050325 | -0.0069469 | 0.015752 | 0.022683 | -0.0023435 | 12.4512 | 121.9711 | -0.091553 | 121.7514 | 0.17853 | -0.064087 | -0.045776 | 0.041199 | 0.004578 | -0.032043 | -0.004578 | 0.091553 | 0.068665 | 0.082397 | 0.01831 | -0.004578 | -0.2243 | 0.28839 | 0.064087 | 0.045776 | 0.045777 | 0.027466 | 0.07782 | -121.9711 | -121.9803 | 0.20142 | 0.19226 | 0.17853 | 0.11444 | 0.10071 | 0.27008 | 121.843 | 0.1236 | 0.027465 | 122.0627 | 0.036621 | 122.081 | 0.11444 | -122.0673 | -122.0078 | 121.8613 | 0.10529 | 12.561 | 0.15106
3081.6719 | 122.0444 | -0.10529 | 121.9803 | -0.01976 | 0.0050372 | 0.057272 | 0.05216 | -0.00026906 | -0.0070666 | -0.0021682 | -0.0084228 | 0.016336 | 0.044771 | -0.0060925 | 0.017248 | 0.026314 | -0.0012753 | 12.4146 | 121.9803 | -0.082397 | 121.6919 | 0.11444 | -0.1236 | -0.073242 | -0.032043 | 0 | -0.045776 | -0.032043 | 0.054932 | 0.009155 | 0.050354 | 0.022889 | 0 | -0.28839 | 0.21973 | 0.032044 | -0.01831 | 0.009155 | -0.041199 | 0.05951 | -121.9803 | -122.0123 | 0.16022 | 0.15564 | 0.11444 | 0.09613 | 0.054931 | 0.19684 | 121.7743 | 0.10071 | 0.013733 | 122.0627 | 0.045776 | 122.0856 | 0.10529 | -122.0627 | -122.0261 | 121.7972 | 0.073243 | 12.5198 | 0.073243
3083.4219 | 122.0032 | -0.11444 | 121.9757 | 0.0031279 | 0.0037556 | 0.053854 | 0.053015 | -0.00026906 | -0.0072802 | -0.00345 | -0.0084228 | 0.016336 | 0.044344 | -0.0063061 | 0.016821 | 0.024605 | -0.0061887 | 12.5793 | 122.0032 | -0.086975 | 121.7194 | 0.13275 | -0.10071 | -0.086975 | -0.041199 | 0.013733 | -0.041199 | -0.064087 | 0.022888 | -0.009155 | 0.032043 | 0.027466 | 0.027466 | -0.25635 | 0.24719 | 0.027466 | 0.013733 | 0 | -0.013733 | 0.073242 | -121.962 | -122.0398 | 0.13733 | 0.14648 | 0.10529 | 0.073242 | 0.032044 | 0.21973 | 121.8063 | 0.064087 | -0.022888 | 122.0901 | 0.054932 | 122.1176 | 0.12817 | -122.0627 | -122.0169 | 121.8338 | 0.050354 | 12.6938 | 0.073242
3085.1875 | 122.0032 | -0.10529 | 121.9757 | -0.01976 | 0.0037556 | 0.053214 | 0.050238 | 0.0016535 | -0.0087756 | -0.0021682 | -0.005371 | 0.017404 | 0.042849 | -0.0069469 | 0.016607 | 0.026528 | -0.0072569 | 12.6572 | 121.9803 | -0.091553 | 121.7606 | 0.19226 | -0.064087 | -0.032043 | 0.013733 | -0.013733 | -0.045776 | -0.032043 | 0.068665 | 0.027466 | 0.054932 | 0.013733 | 0.004578 | -0.21515 | 0.29755 | 0.073243 | 0.041199 | 0.05951 | 0.027466 | 0.05951 | -121.9894 | -122.0078 | 0.17395 | 0.16022 | 0.13275 | 0.10071 | 0.073242 | 0.28381 | 121.8521 | 0.11444 | 0.013733 | 122.0718 | 0.032043 | 122.0856 | 0.091553 | -122.0673 | -122.0215 | 121.8658 | 0.073243 | 12.7625 | 0.11902
3086.9531 | 122.1313 | -0.068665 | 121.9574 | -0.012131 | 0.0048236 | 0.05535 | 0.049383 | -0.0032599 | -0.0066394 | -0.0049454 | -0.005371 | 0.012063 | 0.040926 | -0.01186 | 0.016821 | 0.024605 | -0.00042085 | 12.7396 | 121.9208 | -0.059509 | 121.8201 | 0.27466 | 0.018311 | 0.045776 | 0.10986 | -0.036621 | -0.004578 | 0.068665 | 0.15564 | 0.13733 | 0.13275 | 0.009156 | -0.036621 | -0.13733 | 0.34332 | 0.11444 | 0.086976 | 0.10528 | 0.07782 | 0.064087 | -121.994 | -121.8887 | 0.22431 | 0.20142 | 0.20599 | 0.13733 | 0.14191 | 0.33417 | 121.8796 | 0.16022 | 0.073243 | 121.9803 | -0.032043 | 121.9894 | 0.032044 | -122.0169 | -121.962 | 121.8887 | 0.13733 | 12.8082 | 0.17853
3088.6562 | 122.0169 | -0.10529 | 121.9711 | -0.01976 | 0.00461 | 0.053427 | 0.052374 | 0.0033623 | -0.0064258 | -0.0049454 | -0.0023192 | 0.017404 | 0.04114 | -0.0035291 | 0.016393 | 0.02546 | -0.0027707 | 12.7625 | 121.9803 | -0.091553 | 121.6873 | 0.10986 | -0.12817 | -0.073242 | -0.059509 | 0.013733 | -0.045776 | -0.054932 | 0.027466 | 0 | 0.045776 | 0.013733 | 0.009156 | -0.28381 | 0.21515 | 0.032044 | -0.022888 | 0.018311 | -0.036621 | 0.05951 | -121.9574 | -122.0261 | 0.13275 | 0.15106 | 0.10529 | 0.091552 | 0.045776 | 0.20142 | 121.7789 | 0.073242 | -0.009156 | 122.0718 | 0.059509 | 122.0856 | 0.11902 | -122.0627 | -122.0169 | 121.7926 | 0.050354 | 12.8677 | 0.045777
3090.4219 | 122.0901 | -0.082397 | 121.9666 | -0.0045011 | 0.00097838 | 0.052786 | 0.04917 | -0.0047553 | -0.0087756 | -0.000673 | -0.0023192 | 0.01249 | 0.03879 | -0.01186 | 0.016393 | 0.02311 | -0.00084805 | 12.8311 | 121.9528 | -0.045776 | 121.7514 | 0.18768 | -0.036621 | 0.022888 | 0.009155 | -0.022888 | -0.018311 | -0.009155 | 0.10986 | 0.091553 | 0.091553 | 0.036621 | -0.013733 | -0.21515 | 0.27008 | 0.10528 | 0.045776 | 0.068664 | 0.009155 | 0.064086 | -121.9894 | -121.9757 | 0.19226 | 0.17395 | 0.17395 | 0.10986 | 0.10986 | 0.23346 | 121.7972 | 0.12817 | 0.009156 | 121.9986 | -0.004577 | 122.0352 | 0.059509 | -122.0123 | -121.9849 | 121.8338 | 0.073242 | 12.9135 | 0.091552
3092.125 | 122.0215 | -0.10986 | 121.994 | -0.0045011 | 0.0041828 | 0.052786 | 0.050879 | 0.0027215 | -0.0094164 | -0.0021682 | -0.0023192 | 0.016549 | 0.04648 | -0.0052381 | 0.014898 | 0.025032 | -0.0036253 | 12.9547 | 121.9757 | -0.073242 | 121.6919 | 0.10986 | -0.11902 | -0.086975 | -0.059509 | 0.009155 | -0.032043 | -0.07782 | 0 | -0.032043 | 0.013733 | 0.036621 | -0.018311 | -0.30212 | 0.21973 | 0.022888 | -0.009156 | -0.013733 | -0.045777 | 0.07782 | -121.9849 | -122.0718 | 0.10986 | 0.1236 | 0.07782 | 0.045776 | 0 | 0.18311 | 121.7651 | 0.032043 | -0.045777 | 122.0489 | 0.041198 | 122.0856 | 0.11902 | -122.0673 | -122.0261 | 121.8018 | 0.032043 | 13.0646 | 0.050354
3093.9062 | 122.0993 | -0.07782 | 121.962 | -0.0045011 | 0.0022602 | 0.052145 | 0.049811 | 0.0057123 | -0.010485 | -0.0043046 | -0.005371 | 0.013772 | 0.049257 | -0.0045971 | 0.014471 | 0.023964 | -0.0049069 | 13.0692 | 121.907 | -0.054932 | 121.8063 | 0.26093 | 0.027466 | 0.050354 | 0.07782 | -0.018311 | -0.018311 | 0.009155 | 0.13275 | 0.11902 | 0.10529 | 0.022888 | -0.054932 | -0.15564 | 0.33875 | 0.12817 | 0.10529 | 0.10529 | 0.082398 | 0.059509 | -121.9803 | -121.9528 | 0.21057 | 0.18311 | 0.19684 | 0.1236 | 0.13733 | 0.31586 | 121.8613 | 0.15106 | 0.027466 | 121.962 | 0 | 121.9849 | 0.059509 | -122.0169 | -121.9803 | 121.8842 | 0.086975 | 13.147 | 0.15564
3095.6719 | 121.994 | -0.11444 | 121.9894 | -0.0045011 | 0.0048236 | 0.053 | 0.052588 | -0.0024055 | -0.006853 | -0.001741 | -0.005371 | 0.016977 | 0.050539 | -0.0052381 | 0.016821 | 0.023751 | -0.0044797 | 13.0646 | 121.9849 | -0.10071 | 121.669 | 0.082397 | -0.15106 | -0.091553 | -0.082397 | 0.009155 | -0.050354 | -0.054932 | 0.004578 | -0.027466 | 0.045776 | 0.013733 | -0.004578 | -0.32044 | 0.19684 | 0.022888 | -0.036621 | 0.009155 | -0.050354 | 0.064087 | -121.9803 | -122.0444 | 0.11902 | 0.16022 | 0.086975 | 0.09613 | 0.022888 | 0.18311 | 121.7697 | 0.054932 | -0.004578 | 122.0856 | 0.059509 | 122.0993 | 0.1236 | -122.0901 | -122.0398 | 121.7834 | 0.059509 | 13.179 | 0.032044
3097.4219 | 122.0627 | -0.10529 | 121.994 | -0.012131 | 0.0037556 | 0.054709 | 0.052588 | 0.0033623 | -0.0089892 | -0.0015274 | -0.0023192 | 0.016336 | 0.047976 | -0.0092969 | 0.015966 | 0.025246 | -0.0031979 | 13.2339 | 121.9666 | -0.07782 | 121.7651 | 0.19226 | -0.036621 | -0.054932 | 0.027466 | -0.009155 | -0.036621 | -0.009155 | 0.10529 | 0.064087 | 0.068665 | 0.027466 | -0.027466 | -0.22888 | 0.29755 | 0.050354 | 0.068665 | 0.022888 | 0.041199 | 0.068665 | -122.0032 | -122.0032 | 0.21057 | 0.17395 | 0.16937 | 0.10529 | 0.10071 | 0.27008 | 121.843 | 0.14191 | 0.027466 | 122.0444 | 0.027466 | 122.0718 | 0.096131 | -122.0718 | -122.0306 | 121.8704 | 0.096131 | 13.3392 | 0.13275
3099.2031 | 122.0993 | -0.07782 | 121.9711 | -0.012131 | 0.0043964 | 0.050436 | 0.048529 | 0.0037897 | -0.005144 | -0.0015274 | -0.005371 | 0.013559 | 0.046267 | -0.01186 | 0.016393 | 0.024391 | -0.0021299 | 13.2568 | 121.9528 | -0.041199 | 121.7606 | 0.25635 | -0.018311 | 0.036621 | 0.059509 | -0.018311 | -0.022888 | 0 | 0.11444 | 0.086975 | 0.10071 | 0.036621 | -0.01831 | -0.21057 | 0.33417 | 0.11444 | 0.059509 | 0.07782 | 0.022888 | 0.054932 | -121.9894 | -121.9711 | 0.19226 | 0.17853 | 0.16479 | 0.1236 | 0.10986 | 0.29755 | 121.8018 | 0.13733 | 0.022888 | 121.994 | 0.004577 | 122.0306 | 0.059509 | -122.0123 | -121.994 | 121.8384 | 0.07782 | 13.3347 | 0.13733
3100.9688 | 122.0123 | -0.11444 | 121.9666 | -0.0045011 | 0.00097838 | 0.052145 | 0.050451 | -5.5462e-05 | -0.0092028 | -0.002382 | -0.0084228 | 0.015908 | 0.048403 | -0.013142 | 0.013403 | 0.025032 | -0.0042661 | 13.3163 | 121.9437 | -0.07782 | 121.7056 | 0.15106 | -0.086975 | -0.064087 | -0.045776 | 0.013733 | -0.041199 | -0.086975 | 0.041199 | 0.013733 | 0.022888 | 0.036621 | -0.022888 | -0.26093 | 0.2655 | 0.050354 | 0.027466 | 0.013733 | -0.009155 | 0.073242 | -121.9528 | -122.0535 | 0.15564 | 0.13733 | 0.12817 | 0.064087 | 0.054932 | 0.22888 | 121.7834 | 0.082398 | -0.045776 | 122.0215 | 0.054932 | 122.0581 | 0.12817 | -122.0444 | -122.0078 | 121.8201 | 0.027466 | 13.4308 | 0.068665
3102.6719 | 122.1451 | -0.073242 | 121.9345 | -0.01976 | -0.00073062 | 0.053 | 0.049811 | 0.0025079 | -0.0062122 | -0.0036636 | -0.005371 | 0.015054 | 0.044985 | -0.0069469 | 0.015112 | 0.0261 | -0.0036253 | 13.4491 | 121.9482 | -0.045776 | 121.8155 | 0.30212 | 0.064087 | 0.068665 | 0.13275 | -0.027466 | -0.004578 | 0.064087 | 0.1831 | 0.16479 | 0.13733 | 0.027466 | 0.013733 | -0.11902 | 0.37537 | 0.14191 | 0.13733 | 0.11444 | 0.10986 | 0.068664 | -121.962 | -121.8704 | 0.25635 | 0.21057 | 0.23804 | 0.14191 | 0.16937 | 0.3479 | 121.8613 | 0.18768 | 0.068665 | 121.994 | -0.022888 | 122.0215 | 0.045776 | -121.9803 | -121.9391 | 121.8887 | 0.13733 | 13.5223 | 0.20599
3104.4375 | 122.0306 | -0.10529 | 122.0169 | -0.0045011 | 0.0026874 | 0.052145 | 0.051306 | -0.0030463 | -0.0079212 | -0.002382 | -0.005371 | 0.018899 | 0.047335 | 0.00031607 | 0.016821 | 0.023323 | -0.0023435 | 13.4903 | 121.9482 | -0.10529 | 121.6919 | 0.14191 | -0.10071 | -0.068665 | -0.068665 | 0.013733 | -0.054932 | -0.054932 | 0.045776 | 0.027466 | 0.032043 | 0 | -0.068665 | -0.32501 | 0.24719 | 0.036621 | 0.004578 | 0.036621 | 0.004578 | 0.050354 | -122.0032 | -122.0718 | 0.15106 | 0.13733 | 0.13275 | 0.086975 | 0.082398 | 0.24719 | 121.7972 | 0.10071 | 0 | 122.0535 | 0.068665 | 122.0535 | 0.11902 | -122.1222 | -122.0718 | 121.7972 | 0.050354 | 13.5956 | 0.036621
3106.1562 | 122.0032 | -0.10986 | 121.9803 | -0.01976 | 0.0020466 | 0.054068 | 0.053869 | 0.00037174 | -0.008562 | -0.00345 | 0.00073235 | 0.016977 | 0.047121 | -0.0026745 | 0.015325 | 0.025032 | -0.0040525 | 13.6139 | 121.9711 | -0.07782 | 121.7285 | 0.15564 | -0.10986 | -0.068665 | -0.027466 | 0 | -0.032043 | -0.045776 | 0.036621 | -0.009155 | 0.032043 | 0.032043 | -0.009156 | -0.25177 | 0.2655 | 0.041198 | 0 | 0.009155 | -0.032043 | 0.07782 | -121.9803 | -122.0261 | 0.14648 | 0.14191 | 0.10071 | 0.064086 | 0.022888 | 0.23346 | 121.8063 | 0.068664 | -0.013733 | 122.049 | 0.032043 | 122.081 | 0.10986 | -122.0581 | -122.0123 | 121.8384 | 0.064087 | 13.7238 | 0.082397
3107.9219 | 122.0261 | -0.10071 | 121.9437 | -0.012131 | 0.0031146 | 0.053641 | 0.051733 | 0.00037174 | -0.0077074 | -0.0002456 | -0.005371 | 0.018045 | 0.045839 | -0.0099377 | 0.015112 | 0.025246 | -0.0042661 | 13.678 | 122.0032 | -0.064087 | 121.756 | 0.21057 | -0.054932 | -0.041199 | 0.022888 | 0.013733 | -0.027466 | -0.013733 | 0.086975 | 0.045776 | 0.064087 | 0.036621 | 0.059509 | -0.18768 | 0.31128 | 0.059509 | 0.045776 | 0.022888 | 0.009155 | 0.073242 | -121.9299 | -121.9574 | 0.18768 | 0.1648 | 0.14648 | 0.091553 | 0.073242 | 0.27466 | 121.8201 | 0.11444 | 0.013733 | 122.0673 | 0.041199 | 122.1039 | 0.11444 | -122.0078 | -121.9711 | 121.8567 | 0.086975 | 13.7787 | 0.1236
3109.7031 | 122.1405 | -0.073242 | 121.9482 | -0.012131 | -0.001585 | 0.051505 | 0.04917 | -5.5462e-05 | -0.008562 | -0.000673 | -0.005371 | 0.015268 | 0.047762 | -0.0065197 | 0.014471 | 0.0261 | -0.0055479 | 13.765 | 121.9162 | -0.041199 | 121.8246 | 0.32044 | 0.045776 | 0.086975 | 0.14648 | -0.036621 | -0.013733 | 0.059509 | 0.17853 | 0.16479 | 0.13733 | 0.032043 | -0.032043 | -0.1236 | 0.39368 | 0.16022 | 0.11902 | 0.12817 | 0.086975 | 0.059509 | -121.9849 | -121.8887 | 0.25177 | 0.21057 | 0.23804 | 0.15106 | 0.17853 | 0.36163 | 121.8658 | 0.19226 | 0.073242 | 121.9574 | -0.022888 | 121.9894 | 0.036621 | -121.9894 | -121.962 | 121.8979 | 0.13275 | 13.8382 | 0.21973
3111.4062 | 122.1542 | -0.032043 | 121.9482 | -0.0045011 | 0.002901 | 0.053214 | 0.050879 | 0.0016535 | -0.0074938 | -0.0002456 | -0.0084228 | 0.014627 | 0.044558 | -0.0033153 | 0.015325 | 0.025887 | -0.0023435 | 13.8153 | 121.9437 | -0.045776 | 121.7972 | 0.2655 | -0.009155 | 0.045776 | 0.10986 | -0.036621 | -0.004578 | 0.07782 | 0.16479 | 0.13275 | 0.14191 | -0.013733 | -0.004577 | -0.15106 | 0.29755 | 0.077819 | 0.022888 | 0.091552 | 0.036621 | 0.027465 | -121.9849 | -121.8704 | 0.19684 | 0.17395 | 0.16479 | 0.14649 | 0.13733 | 0.31128 | 121.843 | 0.16937 | 0.082398 | 121.9894 | -0.032043 | 121.9757 | -0.004578 | -121.994 | -121.9528 | 121.8292 | 0.10986 | 13.8474 | 0.14191
3113.1562 | 122.081 | -0.07782 | 121.962 | -0.01976 | 0.0033282 | 0.055136 | 0.04917 | -0.0024055 | -0.0074938 | -0.0019546 | -0.005371 | 0.014627 | 0.047121 | -0.0071607 | 0.013616 | 0.024391 | -0.0010617 | 13.8474 | 121.9482 | -0.059509 | 121.7606 | 0.24719 | -0.013733 | 0.027466 | 0.054932 | -0.036621 | -0.018311 | 0.009155 | 0.10529 | 0.09613 | 0.082397 | 0.018311 | -0.013733 | -0.20142 | 0.32501 | 0.10529 | 0.064087 | 0.086975 | 0.045776 | 0.059509 | -121.9986 | -121.9528 | 0.18311 | 0.16022 | 0.17395 | 0.10071 | 0.11444 | 0.3067 | 121.8201 | 0.1236 | 0.027466 | 122.0078 | -0.01831 | 122.0261 | 0.041199 | -122.0215 | -121.9803 | 121.8384 | 0.086975 | 13.9252 | 0.13275
3114.9219 | 122.0444 | -0.11444 | 121.9666 | -0.012131 | 0.0050372 | 0.053214 | 0.053228 | -0.0032599 | -0.00963 | -3.1996e-05 | -0.0023192 | 0.015481 | 0.049044 | -0.0099377 | 0.016821 | 0.024391 | 0.00021995 | 13.8931 | 122.0032 | -0.068665 | 121.6919 | 0.14648 | -0.12817 | -0.07782 | -0.041199 | -0.013733 | -0.036621 | -0.050354 | 0.018311 | 0.004578 | 0.050354 | 0.045776 | 0.036621 | -0.27466 | 0.26093 | 0.036621 | -0.013733 | -0.009155 | -0.059509 | 0.07782 | -121.9803 | -122.0169 | 0.13275 | 0.16479 | 0.11902 | 0.086975 | 0.041199 | 0.21515 | 121.7606 | 0.054932 | -0.013733 | 122.0718 | 0.022888 | 122.1176 | 0.10071 | -122.0352 | -122.0032 | 121.8063 | 0.064087 | 14.0076 | 0.073242
3116.6875 | 122.0535 | -0.10529 | 121.9757 | -0.02739 | 0.0033282 | 0.052359 | 0.05216 | 0.0052851 | -0.0089892 | -0.0015274 | -0.005371 | 0.01484 | 0.052248 | -0.0020337 | 0.016821 | 0.024819 | -0.0023435 | 14.0259 | 121.9711 | -0.09613 | 121.7285 | 0.17395 | -0.050354 | -0.050354 | -0.004578 | 0.018311 | -0.041199 | -0.018311 | 0.07782 | 0.054932 | 0.064087 | 0.009156 | -0.004578 | -0.24719 | 0.27924 | 0.054932 | 0.054932 | 0.045776 | 0.045776 | 0.064087 | -121.9574 | -121.994 | 0.18311 | 0.16937 | 0.16022 | 0.10529 | 0.096131 | 0.27008 | 121.8246 | 0.11902 | 0.022888 | 122.0673 | 0.05951 | 122.0764 | 0.1236 | -122.0718 | -122.0169 | 121.8338 | 0.086975 | 14.1312 | 0.10071
3118.3906 | 122.0947 | -0.064087 | 121.9437 | -0.012131 | 0.00097838 | 0.052573 | 0.048102 | 0.0014397 | -0.010271 | -0.002382 | -0.005371 | 0.013559 | 0.050325 | -0.017842 | 0.014684 | 0.025887 | -0.0042661 | 14.0488 | 121.9299 | -0.054932 | 121.756 | 0.21973 | -0.041199 | 0.004578 | 0.013733 | -0.032043 | -0.018311 | -0.009155 | 0.09613 | 0.09613 | 0.07782 | 0.009155 | -0.013733 | -0.18768 | 0.28381 | 0.068665 | 0.022888 | 0.05951 | 0.013733 | 0.045776 | -121.9757 | -121.9528 | 0.16022 | 0.14191 | 0.16022 | 0.096131 | 0.11444 | 0.27466 | 121.8109 | 0.11444 | 0.009156 | 121.9849 | -0.013732 | 121.994 | 0.032044 | -121.9986 | -121.962 | 121.8201 | 0.054932 | 14.1129 | 0.07782
3120.1562 | 122.1313 | -0.059509 | 121.962 | -0.012131 | 0.0031146 | 0.054282 | 0.050238 | 0.0025079 | -0.0066394 | -0.0045182 | -0.0084228 | 0.015908 | 0.052675 | -0.010151 | 0.015966 | 0.02311 | -0.0012753 | 14.1449 | 121.9299 | -0.045776 | 121.8018 | 0.29297 | 0.009155 | 0.050354 | 0.11902 | -0.036621 | -0.018311 | 0.07782 | 0.16022 | 0.11902 | 0.12817 | 0.013733 | -0.032043 | -0.16022 | 0.35248 | 0.10986 | 0.068664 | 0.09613 | 0.054931 | 0.041198 | -121.9986 | -121.8842 | 0.21973 | 0.18768 | 0.17853 | 0.14649 | 0.13733 | 0.33874 | 121.8475 | 0.17853 | 0.096131 | 121.9757 | -0.01831 | 121.9894 | 0.022888 | -122.0078 | -121.9803 | 121.8613 | 0.13733 | 14.2044 | 0.17853
3121.9062 | 122.1497 | -0.082397 | 121.9437 | -0.012131 | 0.0024738 | 0.052145 | 0.048956 | -0.0045417 | -0.0083484 | -0.000673 | -0.0084228 | 0.012918 | 0.050325 | -0.0071607 | 0.013189 | 0.022896 | -0.00084805 | 14.209 | 121.9162 | -0.064087 | 121.788 | 0.26093 | 0.009155 | 0.041199 | 0.068665 | -0.027466 | -0.032043 | 0.050354 | 0.16937 | 0.16479 | 0.1236 | 0.01831 | -0.027466 | -0.15564 | 0.34332 | 0.1236 | 0.091552 | 0.10529 | 0.073242 | 0.050354 | -121.9711 | -121.8933 | 0.25177 | 0.20599 | 0.24719 | 0.15564 | 0.19684 | 0.32501 | 121.8521 | 0.20142 | 0.082397 | 121.9803 | 0.004577 | 121.9986 | 0.054931 | -122.0078 | -121.9757 | 121.8704 | 0.13275 | 14.2914 | 0.15106
3123.6562 | 122.0261 | -0.086975 | 121.9803 | -0.012131 | 0.0020466 | 0.052145 | 0.047674 | -0.00026906 | -0.0092028 | -0.0013138 | -0.0023192 | 0.017831 | 0.054598 | -0.013356 | 0.016393 | 0.022683 | -0.0017027 | 14.328 | 121.9208 | -0.068665 | 121.7743 | 0.25635 | 0 | 0.018311 | 0.036621 | -0.004578 | -0.036621 | -0.041199 | 0.068665 | 0.050354 | 0.054932 | 0.01831 | -0.05951 | -0.20599 | 0.34332 | 0.10529 | 0.086975 | 0.086976 | 0.068665 | 0.050354 | -121.9849 | -122.0215 | 0.15564 | 0.14191 | 0.13733 | 0.091553 | 0.086975 | 0.32501 | 121.843 | 0.10529 | -0.004578 | 121.9894 | 0.032043 | 122.0078 | 0.082397 | -122.049 | -122.0169 | 121.8613 | 0.045776 | 14.415 | 0.1236
3125.3594 | 122.1313 | -0.082397 | 121.9482 | -0.012131 | 0.0026874 | 0.053 | 0.050451 | -0.0034735 | -0.0087756 | -0.002382 | -0.005371 | 0.016549 | 0.056948 | -0.015492 | 0.012762 | 0.025887 | -0.00063445 | 14.36 | 121.9391 | -0.07782 | 121.7789 | 0.25177 | -0.004578 | 0.045776 | 0.073242 | -0.027466 | -0.022888 | 0.036621 | 0.16022 | 0.14191 | 0.11902 | 0.004577 | -0.009155 | -0.16937 | 0.33417 | 0.12817 | 0.077819 | 0.1236 | 0.073242 | 0.059509 | -121.9757 | -121.9116 | 0.24261 | 0.20142 | 0.2243 | 0.14191 | 0.16479 | 0.32959 | 121.8567 | 0.1831 | 0.059509 | 122.0169 | -0.004578 | 122.0215 | 0.054931 | -122.0261 | -121.9711 | 121.8613 | 0.11902 | 14.4424 | 0.15564
3127.125 | 122.0581 | -0.10071 | 121.9711 | -0.012131 | 0.0033282 | 0.052786 | 0.052374 | -0.00026906 | -0.0077074 | -0.0025956 | -0.005371 | 0.017617 | 0.053102 | -0.0054517 | 0.017248 | 0.022255 | -0.0036253 | 14.4791 | 121.9299 | -0.073242 | 121.7468 | 0.22888 | -0.050354 | -0.027466 | 0.041199 | 0.004578 | -0.041199 | 0 | 0.09613 | 0.054932 | 0.07782 | 0.027466 | -0.041198 | -0.2243 | 0.32959 | 0.073242 | 0.050354 | 0.045776 | 0.022888 | 0.059509 | -121.9666 | -121.9711 | 0.19684 | 0.17853 | 0.15564 | 0.11902 | 0.096131 | 0.30212 | 121.8201 | 0.13733 | 0.041199 | 122.0032 | 0.045777 | 122.0306 | 0.10529 | -122.0444 | -122.0123 | 121.8475 | 0.10071 | 14.5798 | 0.14191
3128.9062 | 121.994 | -0.12817 | 121.994 | -0.0045011 | -0.00094422 | 0.052145 | 0.050665 | -0.00048286 | -0.008562 | -0.0004592 | -0.0084228 | 0.017831 | 0.05353 | -0.0071607 | 0.01853 | 0.025032 | -0.0010617 | 14.4928 | 121.9574 | -0.10071 | 121.6965 | 0.14191 | -0.086975 | -0.068665 | -0.059509 | 0.009155 | -0.050354 | -0.082397 | 0.022888 | 0.013733 | 0.036621 | 0.027466 | -0.036622 | -0.29755 | 0.27008 | 0.059509 | 0.041199 | 0.032043 | 0.013733 | 0.07782 | -121.9849 | -122.0764 | 0.15106 | 0.1648 | 0.14191 | 0.086975 | 0.064087 | 0.24262 | 121.7972 | 0.073242 | -0.032043 | 122.0581 | 0.059509 | 122.0856 | 0.13733 | -122.0947 | -122.0444 | 121.8246 | 0.045777 | 14.621 | 0.068665
3130.6719 | 122.1085 | -0.064087 | 121.9528 | -0.01976 | 0.0033282 | 0.054068 | 0.051092 | -0.0015509 | -0.0094164 | -0.0032364 | -0.0084228 | 0.016549 | 0.056093 | -0.011647 | 0.014471 | 0.025887 | -0.0036253 | 14.5981 | 121.9345 | -0.054932 | 121.8063 | 0.29755 | -0.013733 | 0.041199 | 0.10071 | -0.036621 | -0.032043 | 0.054932 | 0.15564 | 0.1236 | 0.1236 | 0.009155 | -0.018311 | -0.14648 | 0.36163 | 0.10529 | 0.050354 | 0.096131 | 0.041199 | 0.032044 | -121.9894 | -121.8979 | 0.21973 | 0.18768 | 0.18768 | 0.15564 | 0.15564 | 0.35248 | 121.8613 | 0.18768 | 0.086975 | 121.9894 | -0.004578 | 121.9986 | 0.027466 | -122.0078 | -121.9849 | 121.8704 | 0.11902 | 14.6622 | 0.1648
3132.3594 | 122.049 | -0.10529 | 121.994 | -0.0045011 | 0.001833 | 0.053 | 0.050879 | 0.0033623 | -0.010698 | -0.0028092 | -0.005371 | 0.019113 | 0.055452 | -0.0045971 | 0.017889 | 0.025673 | -0.0012753 | 14.6484 | 121.9437 | -0.07782 | 121.756 | 0.22888 | -0.054932 | -0.022888 | 0.041199 | -0.004578 | -0.041199 | 0 | 0.091553 | 0.059509 | 0.082397 | 0.027466 | -0.050354 | -0.23804 | 0.33417 | 0.082398 | 0.050354 | 0.054932 | 0.022888 | 0.064087 | -121.9986 | -121.994 | 0.19684 | 0.18768 | 0.16479 | 0.1236 | 0.10071 | 0.3067 | 121.8338 | 0.13275 | 0.041199 | 122.0215 | 0.036621 | 122.049 | 0.10071 | -122.0718 | -122.0352 | 121.8613 | 0.10529 | 14.7537 | 0.14649
3134.125 | 122.0947 | -0.091553 | 121.9528 | -0.0045011 | 0.00012398 | 0.053214 | 0.048956 | 0.0014397 | -0.010912 | -0.0015274 | -0.005371 | 0.014199 | 0.053316 | -0.017201 | 0.016607 | 0.025246 | -0.0038389 | 14.7903 | 121.9299 | -0.059509 | 121.8018 | 0.3067 | 0.022888 | 0.064087 | 0.068665 | -0.018311 | -0.004578 | 0.027466 | 0.15106 | 0.12817 | 0.10071 | 0.032044 | -0.022888 | -0.15106 | 0.39825 | 0.15564 | 0.11444 | 0.1236 | 0.082397 | 0.086975 | -121.9711 | -121.9254 | 0.24261 | 0.19226 | 0.21973 | 0.10529 | 0.13275 | 0.36621 | 121.8613 | 0.15564 | 0.032044 | 121.9894 | -0.013733 | 122.0215 | 0.073242 | -122.0123 | -121.9574 | 121.8933 | 0.11902 | 14.8819 | 0.16022
3135.8906 | 122.081 | -0.09613 | 121.9711 | -0.012131 | 0.00097838 | 0.052786 | 0.048315 | 0.00058534 | -0.011553 | -0.0030228 | -0.0023192 | 0.015481 | 0.05118 | -0.012501 | 0.015325 | 0.023964 | -0.00084805 | 14.8682 | 121.9254 | -0.054932 | 121.7926 | 0.30212 | 0.036621 | 0.050354 | 0.073242 | -0.032043 | -0.032043 | 0.009155 | 0.14191 | 0.10986 | 0.082397 | 0.041198 | -0.045776 | -0.17853 | 0.39825 | 0.14648 | 0.13275 | 0.10529 | 0.091553 | 0.064087 | -122.0032 | -121.962 | 0.23804 | 0.17853 | 0.20599 | 0.11444 | 0.14191 | 0.35706 | 121.8475 | 0.17395 | 0.041198 | 121.9803 | 0 | 122.0215 | 0.064087 | -122.0261 | -122.0032 | 121.8887 | 0.10528 | 14.9643 | 0.16937
3137.5938 | 122.0993 | -0.086975 | 121.9528 | -0.02739 | 0.006319 | 0.052786 | 0.05152 | 0.0018671 | -0.0072802 | -0.0038772 | -0.0084228 | 0.016763 | 0.04178 | -0.0078015 | 0.017034 | 0.025673 | -0.0042661 | 14.8315 | 121.9803 | -0.086975 | 121.7285 | 0.20599 | -0.09613 | -0.027466 | 0.027466 | -0.013733 | -0.045776 | 0.032043 | 0.11444 | 0.082397 | 0.1236 | 0 | 0.027466 | -0.2243 | 0.29297 | 0.059509 | -0.009155 | 0.059509 | -0.009155 | 0.041199 | -121.9666 | -121.9208 | 0.20142 | 0.21057 | 0.16937 | 0.16937 | 0.12817 | 0.29297 | 121.8155 | 0.16022 | 0.077819 | 122.0673 | 0.032043 | 122.0673 | 0.073242 | -122.0398 | -121.9986 | 121.8155 | 0.11902 | 14.9185 | 0.11444
3139.3594 | 122.0993 | -0.068665 | 121.962 | -0.012131 | -0.00094422 | 0.053854 | 0.048529 | 0.0020807 | -0.010698 | -0.0030228 | -0.0084228 | 0.014199 | 0.042208 | -0.010792 | 0.013403 | 0.0261 | -0.0023435 | 14.9689 | 121.9116 | -0.054932 | 121.8109 | 0.31128 | 0.022888 | 0.064087 | 0.068665 | -0.009155 | -0.009155 | 0.027466 | 0.15106 | 0.14648 | 0.10529 | 0.013733 | -0.050354 | -0.15106 | 0.37994 | 0.13275 | 0.091553 | 0.11902 | 0.07782 | 0.05951 | -121.9711 | -121.9345 | 0.21973 | 0.17395 | 0.21515 | 0.11444 | 0.15564 | 0.36621 | 121.8658 | 0.16022 | 0.036621 | 121.9666 | 0 | 121.9803 | 0.05951 | -122.0169 | -121.9711 | 121.8796 | 0.096131 | 15.0375 | 0.13733
3141.125 | 122.1313 | -0.054932 | 121.9437 | -0.012131 | 0.00097838 | 0.05065 | 0.050451 | -0.0021919 | -0.012194 | -0.002382 | -0.005371 | 0.016549 | 0.052462 | -0.0097241 | 0.013403 | 0.023537 | -0.0025571 | 15.0055 | 121.9116 | -0.050354 | 121.8018 | 0.29755 | 0.018311 | 0.068665 | 0.11902 | -0.036621 | -0.009155 | 0.064087 | 0.17853 | 0.16937 | 0.15564 | 0.004578 | -0.032044 | -0.14191 | 0.35248 | 0.1236 | 0.073243 | 0.11902 | 0.068665 | 0.045777 | -121.9803 | -121.8796 | 0.23346 | 0.21057 | 0.22431 | 0.16479 | 0.17853 | 0.3479 | 121.8521 | 0.18768 | 0.073242 | 121.962 | -0.027466 | 121.9666 | 0.018311 | -121.994 | -121.9528 | 121.8567 | 0.11902 | 15.0604 | 0.17395
3142.8125 | 122.0032 | -0.10986 | 121.9894 | -0.0045011 | 0.0031146 | 0.054709 | 0.055578 | 0.0031487 | -0.0094164 | -0.0030228 | -0.0023192 | 0.018045 | 0.057161 | 0.0011707 | 0.016821 | 0.023323 | -0.0029843 | 15.0146 | 121.9894 | -0.091553 | 121.6736 | 0.12817 | -0.13733 | -0.10986 | -0.073242 | 0.004578 | -0.054932 | -0.064087 | -0.009155 | -0.018311 | 0.041199 | 0.01831 | 0 | -0.31586 | 0.23804 | 0 | -0.027466 | -0.01831 | -0.045776 | 0.054931 | -121.9849 | -122.0535 | 0.10071 | 0.15106 | 0.091552 | 0.096131 | 0.036621 | 0.21973 | 121.7651 | 0.045777 | -0.009155 | 122.081 | 0.05951 | 122.0993 | 0.11444 | -122.081 | -122.0444 | 121.7834 | 0.045776 | 15.1245 | 0.036621
3144.5781 | 122.081 | -0.082397 | 121.9528 | -0.01976 | 0.0024738 | 0.052573 | 0.049383 | -0.00026906 | -0.010912 | -0.0038772 | -0.0084228 | 0.016549 | 0.057802 | -0.010151 | 0.01383 | 0.023751 | -0.0027707 | 15.0742 | 121.9254 | -0.059509 | 121.756 | 0.23346 | -0.045776 | 0.004578 | 0 | -0.022888 | -0.032043 | -0.009155 | 0.10986 | 0.091553 | 0.09613 | 0.022888 | -0.027466 | -0.19684 | 0.31586 | 0.086975 | 0.036621 | 0.064087 | 0.013733 | 0.050354 | -121.9757 | -121.962 | 0.19226 | 0.17853 | 0.17395 | 0.12817 | 0.1236 | 0.29297 | 121.8155 | 0.14191 | 0.022888 | 121.9849 | 0.009155 | 122.0078 | 0.059509 | -122.0123 | -121.9849 | 121.8384 | 0.073242 | 15.1566 | 0.082397
3146.3438 | 122.0261 | -0.11444 | 121.9666 | -0.012131 | 0.0050372 | 0.053214 | 0.049811 | -0.0019781 | -0.00963 | -0.0038772 | -0.005371 | 0.017617 | 0.048403 | -0.0020337 | 0.016607 | 0.024391 | -0.0014891 | 15.2206 | 121.9437 | -0.082397 | 121.7743 | 0.23804 | -0.036621 | -0.022888 | 0.036621 | 0.013733 | -0.032043 | -0.004578 | 0.082397 | 0.054932 | 0.054932 | 0.032044 | -0.022888 | -0.19226 | 0.35248 | 0.091553 | 0.07782 | 0.059509 | 0.045776 | 0.082398 | -121.9528 | -121.9711 | 0.19684 | 0.16937 | 0.16937 | 0.086975 | 0.086975 | 0.32043 | 121.8567 | 0.11444 | 0.027465 | 122.0261 | 0.045776 | 122.0581 | 0.12817 | -122.049 | -121.9986 | 121.8887 | 0.10986 | 15.3351 | 0.15106
3148.1094 | 122.1176 | -0.068665 | 121.9299 | 0.0031279 | 0.0058918 | 0.053854 | 0.052374 | 0.0018671 | -0.0066394 | -0.001741 | -0.005371 | 0.013345 | 0.043917 | -0.011433 | 0.016393 | 0.024178 | -0.0021299 | 15.2435 | 121.9574 | -0.045776 | 121.8155 | 0.32501 | 0.004578 | 0.064087 | 0.11444 | -0.036621 | -0.018311 | 0.054932 | 0.15106 | 0.11902 | 0.11444 | 0.022889 | 0.027465 | -0.11444 | 0.39368 | 0.13275 | 0.073243 | 0.10986 | 0.050354 | 0.050354 | -121.9666 | -121.875 | 0.21973 | 0.18311 | 0.18768 | 0.13275 | 0.13733 | 0.37079 | 121.8613 | 0.16937 | 0.073243 | 122.0032 | -0.01831 | 122.0261 | 0.032044 | -121.9757 | -121.9482 | 121.8842 | 0.1236 | 15.3122 | 0.18311
3149.8281 | 122.1451 | -0.064087 | 121.9391 | -0.0045011 | 0.0037556 | 0.054709 | 0.049811 | -0.0021919 | -0.0047168 | -0.0021682 | -0.0084228 | 0.013986 | 0.040071 | -0.0041699 | 0.015966 | 0.02546 | -0.0057615 | 15.3214 | 121.9299 | -0.050354 | 121.8155 | 0.32959 | 0 | 0.041199 | 0.086975 | -0.032043 | -0.004578 | 0.07782 | 0.15106 | 0.13275 | 0.14648 | 0.013733 | -0.009155 | -0.1236 | 0.39368 | 0.10529 | 0.064087 | 0.091553 | 0.050354 | 0.059509 | -121.9711 | -121.8613 | 0.21515 | 0.21057 | 0.19684 | 0.15106 | 0.13733 | 0.37994 | 121.8658 | 0.15564 | 0.082398 | 121.9803 | -0.027465 | 121.994 | 0.032044 | -121.9894 | -121.9437 | 121.8796 | 0.14191 | 15.3854 | 0.15106
3151.5938 | 122.0581 | -0.10529 | 122.0123 | -0.0045011 | 0.0016192 | 0.054495 | 0.053015 | 0.0035761 | -0.010057 | -0.005159 | -0.005371 | 0.014627 | 0.039431 | 0.0043751 | 0.016393 | 0.026528 | -0.0057615 | 15.3946 | 121.9666 | -0.09613 | 121.7422 | 0.23804 | -0.045776 | -0.022888 | 0.032043 | 0 | -0.032043 | -0.022888 | 0.086975 | 0.054932 | 0.07782 | 0.009156 | -0.045776 | -0.27008 | 0.34332 | 0.082398 | 0.05951 | 0.073242 | 0.050354 | 0.073243 | -122.0123 | -122.0352 | 0.19226 | 0.18311 | 0.16022 | 0.10986 | 0.086975 | 0.33417 | 121.8384 | 0.11902 | 0.009155 | 122.0627 | 0.032043 | 122.0718 | 0.10529 | -122.1085 | -122.0444 | 121.8475 | 0.082398 | 15.4999 | 0.13733
3153.3594 | 122.1313 | -0.064087 | 121.9391 | -0.01976 | 0.0037556 | 0.054282 | 0.051306 | -0.00091006 | -0.0089892 | -0.0011002 | -0.005371 | 0.014199 | 0.03879 | -0.0078015 | 0.016393 | 0.028237 | -0.0029843 | 15.4816 | 121.9345 | -0.050354 | 121.8018 | 0.32044 | -0.004578 | 0.054932 | 0.11444 | -0.027466 | 0.009155 | 0.086975 | 0.16479 | 0.1236 | 0.13733 | 0.013733 | -0.004578 | -0.13733 | 0.38452 | 0.11902 | 0.059509 | 0.10529 | 0.045776 | 0.073242 | -121.9666 | -121.8521 | 0.22888 | 0.20142 | 0.18768 | 0.12817 | 0.11444 | 0.37079 | 121.8521 | 0.15564 | 0.07782 | 121.9849 | -0.036621 | 121.9986 | 0.036621 | -121.9894 | -121.9299 | 121.8658 | 0.15106 | 15.5457 | 0.17853
3155.1406 | 122.0444 | -0.091553 | 121.9849 | -0.012131 | 0.0033282 | 0.051077 | 0.051092 | -0.00048286 | -0.010698 | -0.0043046 | -0.005371 | 0.019326 | 0.039431 | -0.0024609 | 0.016393 | 0.02546 | -0.0040525 | 15.4724 | 121.9894 | -0.073242 | 121.7194 | 0.21973 | -0.041199 | -0.045776 | -0.009155 | 0.022888 | -0.027466 | -0.022888 | 0.082397 | 0.059509 | 0.073242 | 0.018311 | 0.004578 | -0.2655 | 0.31128 | 0.045777 | 0.050354 | 0.027466 | 0.032043 | 0.064087 | -121.962 | -122.0078 | 0.17395 | 0.16479 | 0.15106 | 0.10071 | 0.086975 | 0.29297 | 121.7926 | 0.10986 | 0.004578 | 122.0627 | 0.050354 | 122.081 | 0.11444 | -122.0581 | -122.0123 | 121.8109 | 0.068665 | 15.564 | 0.082398
3156.9062 | 122.1039 | -0.07782 | 121.9528 | -0.012131 | 0.00461 | 0.053854 | 0.050024 | -0.00026906 | -0.008562 | -0.0032364 | -0.0023192 | 0.013772 | 0.040499 | -0.0041699 | 0.014684 | 0.024819 | -0.0010617 | 15.5411 | 121.9574 | -0.045776 | 121.8063 | 0.33417 | 0.013733 | 0.045776 | 0.10071 | -0.041199 | -0.009155 | 0.036621 | 0.14648 | 0.11444 | 0.10986 | 0.032044 | 0.004577 | -0.14648 | 0.41199 | 0.1236 | 0.091553 | 0.091552 | 0.059509 | 0.068665 | -121.994 | -121.9162 | 0.2243 | 0.18768 | 0.19226 | 0.11902 | 0.1236 | 0.37994 | 121.8521 | 0.15564 | 0.045776 | 122.0032 | -0.032044 | 122.0352 | 0.036621 | -121.9986 | -121.962 | 121.8842 | 0.11444 | 15.6189 | 0.17853
3158.6562 | 122.0261 | -0.12817 | 121.9803 | -0.012131 | 0.0035418 | 0.053 | 0.053442 | -0.00069646 | -0.0098438 | -0.00345 | -0.0084228 | 0.016977 | 0.038362 | -0.0031017 | 0.016607 | 0.025246 | -0.0046933 | 15.5777 | 121.9894 | -0.07782 | 121.701 | 0.19226 | -0.086975 | -0.07782 | -0.059509 | 0.009155 | -0.059509 | -0.073242 | 0.045776 | 0.018311 | 0.041199 | 0.050354 | 0.009155 | -0.27924 | 0.32044 | 0.050354 | 0.041199 | 0 | -0.009155 | 0.068665 | -121.9711 | -122.0535 | 0.17395 | 0.16937 | 0.14649 | 0.10071 | 0.07782 | 0.27008 | 121.7789 | 0.10528 | -0.013733 | 122.0673 | 0.068664 | 122.1176 | 0.13733 | -122.0581 | -122.0398 | 121.8292 | 0.054932 | 15.7059 | 0.068665
3160.3594 | 122.0581 | -0.086975 | 121.9666 | -0.012131 | 0.001833 | 0.054068 | 0.053228 | -0.0032599 | -0.0083484 | -0.0021682 | -0.011475 | 0.016763 | 0.042849 | 0.0028797 | 0.012975 | 0.023537 | -0.0010617 | 15.715 | 121.9666 | -0.091553 | 121.7514 | 0.2655 | -0.050354 | -0.013733 | 0.036621 | -0.009155 | -0.013733 | 0.009155 | 0.09613 | 0.07782 | 0.086975 | -0.004578 | 0 | -0.21515 | 0.35248 | 0.073242 | 0.036621 | 0.07782 | 0.041199 | 0.073242 | -121.9757 | -121.9574 | 0.1831 | 0.17395 | 0.16479 | 0.10071 | 0.091553 | 0.35706 | 121.843 | 0.10986 | 0.022888 | 122.0581 | 0.004578 | 122.0535 | 0.07782 | -122.0581 | -121.9803 | 121.8384 | 0.09613 | 15.802 | 0.1236
3162.125 | 122.0398 | -0.09613 | 121.9986 | -0.0045011 | 0.0050372 | 0.052359 | 0.05216 | 0.0020807 | -0.010698 | -0.0047318 | -0.005371 | 0.016336 | 0.043703 | -0.0011791 | 0.017248 | 0.025246 | -0.0031979 | 15.7608 | 121.9711 | -0.073242 | 121.7422 | 0.27008 | -0.022888 | -0.009155 | 0.032043 | 0.004578 | -0.036621 | -0.009155 | 0.07782 | 0.045776 | 0.064087 | 0.022888 | -0.027466 | -0.25635 | 0.36621 | 0.086975 | 0.073242 | 0.064087 | 0.050354 | 0.059509 | -121.994 | -122.0078 | 0.17395 | 0.16022 | 0.14191 | 0.10071 | 0.082397 | 0.34332 | 121.8155 | 0.11444 | 0.027466 | 122.0444 | 0.041199 | 122.0673 | 0.10071 | -122.0718 | -122.0352 | 121.8384 | 0.086975 | 15.8569 | 0.12817
3163.9062 | 121.9986 | -0.11444 | 121.9894 | -0.012131 | 0.006319 | 0.053854 | 0.052588 | -0.0021919 | -0.006853 | -0.001741 | -0.005371 | 0.01719 | 0.050753 | -0.0013927 | 0.017889 | 0.025246 | -0.0044797 | 15.7608 | 121.9894 | -0.091553 | 121.7285 | 0.24719 | -0.07782 | -0.045776 | -0.009155 | 0.013733 | -0.050354 | -0.059509 | 0.041199 | -0.004578 | 0.032043 | 0.022888 | 0 | -0.26093 | 0.36163 | 0.068665 | 0.036621 | 0.045777 | 0.013733 | 0.064087 | -121.9757 | -122.049 | 0.15564 | 0.14648 | 0.10986 | 0.082397 | 0.045776 | 0.33874 | 121.8201 | 0.091553 | -0.009155 | 122.081 | 0.064087 | 122.1039 | 0.12817 | -122.081 | -122.0398 | 121.843 | 0.054932 | 15.8752 | 0.10529
3165.625 | 122.1313 | -0.064087 | 121.9482 | -0.01976 | 0.0035418 | 0.054282 | 0.050451 | 0.0025079 | -0.0094164 | -0.0036636 | -0.0084228 | 0.015268 | 0.059725 | -0.0043835 | 0.016393 | 0.026955 | -0.0014891 | 15.8249 | 121.9345 | -0.054932 | 121.8063 | 0.33417 | 0.009155 | 0.059509 | 0.11444 | -0.018311 | -0.022888 | 0.059509 | 0.17853 | 0.13733 | 0.14191 | 0.009155 | -0.013733 | -0.14191 | 0.39825 | 0.1236 | 0.073242 | 0.11444 | 0.064087 | 0.041199 | -121.9666 | -121.8887 | 0.24261 | 0.20599 | 0.20142 | 0.16479 | 0.16022 | 0.3891 | 121.8613 | 0.20142 | 0.082397 | 121.9894 | 0.004577 | 121.9986 | 0.045776 | -122.0032 | -121.9711 | 121.8704 | 0.1236 | 15.889 | 0.17853
3167.3906 | 122.0352 | -0.1236 | 121.9803 | -0.012131 | -0.00030342 | 0.052359 | 0.050879 | -0.00069646 | -0.0094164 | -0.0047318 | -0.005371 | 0.016763 | 0.060579 | -0.012501 | 0.015539 | 0.025673 | 0.00043375 | 15.8844 | 121.9299 | -0.082397 | 121.7422 | 0.28381 | -0.009155 | 0.004578 | 0.013733 | -0.004578 | -0.041199 | -0.054932 | 0.068665 | 0.036621 | 0.036621 | 0.041199 | -0.050354 | -0.23804 | 0.40741 | 0.12817 | 0.11444 | 0.086975 | 0.073242 | 0.082397 | -121.9849 | -122.0352 | 0.19226 | 0.16022 | 0.16022 | 0.07782 | 0.07782 | 0.36621 | 121.8246 | 0.10986 | -0.013733 | 122.0123 | 0.036621 | 122.0535 | 0.11902 | -122.0627 | -122.0215 | 121.8658 | 0.068664 | 16.008 | 0.13733
3169.0938 | 122.0535 | -0.11902 | 121.9711 | -0.012131 | 0.0022602 | 0.051718 | 0.052374 | -5.5462e-05 | -0.0077074 | -0.0043046 | -0.0084228 | 0.016763 | 0.062502 | -0.0071607 | 0.014684 | 0.026314 | -0.0031979 | 15.9668 | 121.962 | -0.10986 | 121.7194 | 0.23804 | -0.050354 | -0.027466 | 0.013733 | 0 | -0.018311 | -0.013733 | 0.082397 | 0.050354 | 0.082397 | 0.009156 | -0.009155 | -0.25177 | 0.35706 | 0.091553 | 0.068665 | 0.082397 | 0.059509 | 0.10071 | -121.9711 | -121.9849 | 0.20142 | 0.20142 | 0.16937 | 0.10071 | 0.068665 | 0.3479 | 121.8292 | 0.10071 | 0.004578 | 122.0718 | 0.018311 | 122.081 | 0.11902 | -122.081 | -121.9894 | 121.8384 | 0.10529 | 16.0858 | 0.13275
3170.8594 | 122.0673 | -0.10529 | 121.9574 | -0.012131 | 0.0033282 | 0.053854 | 0.051947 | -0.0032599 | -0.011553 | -0.0002456 | -0.0023192 | 0.018258 | 0.06122 | -0.00075193 | 0.015752 | 0.024391 | -0.0031979 | 15.9851 | 121.9116 | -0.10529 | 121.7422 | 0.27008 | -0.059509 | -0.027466 | 0.018311 | -0.018311 | -0.050354 | -0.004578 | 0.091553 | 0.064087 | 0.07782 | 0 | -0.045776 | -0.21515 | 0.37537 | 0.07782 | 0.045777 | 0.07782 | 0.045777 | 0.054932 | -121.9757 | -121.962 | 0.19684 | 0.18311 | 0.16937 | 0.12817 | 0.11444 | 0.37537 | 121.8475 | 0.14191 | 0.045776 | 122.0169 | 0.032043 | 122.0169 | 0.086975 | -122.0627 | -122.0078 | 121.8475 | 0.10071 | 16.0904 | 0.1236
3172.5625 | 122.1313 | -0.073242 | 121.9345 | -0.012131 | 0.0014056 | 0.053641 | 0.045752 | -0.0056097 | -0.0079212 | -0.0055862 | -0.005371 | 0.013131 | 0.060793 | -0.0080151 | 0.013616 | 0.026314 | -0.0023435 | 15.9714 | 121.8979 | -0.073242 | 121.7651 | 0.35706 | 0.022888 | 0.059509 | 0.10529 | -0.018311 | -0.032043 | 0.041199 | 0.17395 | 0.16022 | 0.13733 | 0 | -0.036621 | -0.16937 | 0.4303 | 0.13275 | 0.09613 | 0.13275 | 0.09613 | 0.041199 | -121.9528 | -121.8933 | 0.24719 | 0.21057 | 0.23346 | 0.16937 | 0.19226 | 0.4303 | 121.8384 | 0.20599 | 0.073242 | 121.9711 | 0.013732 | 121.9711 | 0.054931 | -122.0078 | -121.9666 | 121.8384 | 0.11444 | 16.0446 | 0.17853
3174.3281 | 122.0444 | -0.11444 | 121.9757 | -0.01976 | 0.0014056 | 0.051291 | 0.053228 | -0.0041145 | -0.0098438 | -0.000673 | 0.00073235 | 0.015908 | 0.065065 | -0.0082287 | 0.017461 | 0.024605 | -0.0023435 | 16.008 | 121.962 | -0.10529 | 121.6782 | 0.21515 | -0.07782 | -0.064087 | -0.059509 | 0.004578 | -0.050354 | -0.045776 | 0.050354 | 0.036621 | 0.059509 | 0.009155 | -0.013733 | -0.29755 | 0.32959 | 0.050354 | 0.036621 | 0.041199 | 0.027466 | 0.064087 | -121.9711 | -122.0215 | 0.16479 | 0.17395 | 0.15106 | 0.10986 | 0.086975 | 0.32044 | 121.7834 | 0.10071 | 0.004578 | 122.0673 | 0.054932 | 122.0764 | 0.11902 | -122.081 | -122.0261 | 121.7926 | 0.068665 | 16.1224 | 0.054932
3176.0938 | 122.1268 | -0.091553 | 121.907 | -0.012131 | -8.9824e-05 | 0.052573 | 0.047033 | -0.0015509 | -0.0083484 | -0.0011002 | -0.0084228 | 0.014199 | 0.062929 | -0.012288 | 0.013189 | 0.025032 | -0.00084805 | 16.0675 | 121.907 | -0.091553 | 121.7514 | 0.32044 | 0.022888 | 0.054932 | 0.091553 | -0.041199 | -0.041199 | 0.045776 | 0.17395 | 0.14648 | 0.1236 | 0 | 0 | -0.15564 | 0.41199 | 0.14649 | 0.11444 | 0.14649 | 0.11444 | 0.050354 | -121.9482 | -121.8613 | 0.2655 | 0.21515 | 0.23804 | 0.16479 | 0.18768 | 0.41199 | 121.843 | 0.21515 | 0.086975 | 121.9986 | 0 | 121.9986 | 0.050354 | -121.9986 | -121.9482 | 121.843 | 0.13733 | 16.1591 | 0.18311
3177.8594 | 122.0947 | -0.10529 | 121.9482 | -0.012131 | 0.00097838 | 0.053854 | 0.050665 | -0.0056097 | -0.0087756 | -0.0040908 | -0.0023192 | 0.013131 | 0.063784 | -0.0065197 | 0.011907 | 0.026314 | -0.00042085 | 16.1179 | 121.9162 | -0.068665 | 121.7285 | 0.27466 | -0.036621 | 0.018311 | 0.022888 | -0.027466 | -0.041199 | 0.009155 | 0.10529 | 0.11902 | 0.10071 | 0.036621 | -0.032043 | -0.21973 | 0.37994 | 0.1236 | 0.068665 | 0.086976 | 0.032044 | 0.064087 | -121.9757 | -121.9391 | 0.21057 | 0.20599 | 0.22431 | 0.14191 | 0.16022 | 0.34332 | 121.7972 | 0.14649 | 0.050354 | 121.9849 | 0.013733 | 122.0215 | 0.07782 | -122.0169 | -121.9894 | 121.8338 | 0.11444 | 16.2231 | 0.12817
3179.6406 | 122.0123 | -0.10529 | 121.9666 | -0.01976 | 0.0033282 | 0.054495 | 0.05152 | 0.0020807 | -0.0074938 | -0.001741 | -0.005371 | 0.017831 | 0.065706 | -0.0037427 | 0.014684 | 0.023751 | -0.0014891 | 16.1728 | 121.9757 | -0.09613 | 121.6599 | 0.20142 | -0.13275 | -0.082397 | -0.045776 | 0 | -0.054932 | -0.036621 | 0.018311 | 0.004578 | 0.027466 | 0.009156 | 0.009155 | -0.3067 | 0.3067 | 0.022889 | -0.027465 | 0.013733 | -0.036621 | 0.050354 | -121.9666 | -122.0032 | 0.1236 | 0.13275 | 0.10986 | 0.082398 | 0.05951 | 0.29755 | 121.756 | 0.073243 | 0.018311 | 122.0718 | 0.054932 | 122.081 | 0.10529 | -122.0627 | -122.0215 | 121.7651 | 0.068665 | 16.2781 | 0.05951
3181.4062 | 122.0123 | -0.10986 | 121.962 | -0.0045011 | 0.00012398 | 0.053 | 0.048102 | -0.0041145 | -0.00963 | 0.0012496 | -0.0084228 | 0.015054 | 0.063784 | -0.0097241 | 0.015539 | 0.02311 | -0.0014891 | 16.2415 | 121.9299 | -0.082397 | 121.6873 | 0.23346 | -0.07782 | -0.059509 | -0.036621 | -0.004578 | -0.054932 | -0.082397 | 0.045776 | 0.027466 | 0.018311 | 0.027466 | -0.032043 | -0.27466 | 0.34332 | 0.050354 | 0.032043 | 0.022888 | 0.004577 | 0.054931 | -121.9666 | -122.0444 | 0.15564 | 0.12817 | 0.13733 | 0.073243 | 0.082398 | 0.31586 | 121.7697 | 0.10071 | -0.027465 | 122.0123 | 0.050354 | 122.0398 | 0.10529 | -122.0444 | -122.0169 | 121.7972 | 0.027466 | 16.3513 | 0.073242
3183.1094 | 122.0901 | -0.10071 | 121.9666 | -0.0045011 | 0.00012398 | 0.052359 | 0.04917 | -0.0017645 | -0.0083484 | -0.0013138 | -0.005371 | 0.013345 | 0.061647 | -0.010151 | 0.014257 | 0.025887 | -0.0034117 | 16.2781 | 121.8979 | -0.07782 | 121.7285 | 0.2655 | -0.045776 | 0.009155 | 0.004578 | -0.022888 | -0.009155 | -0.013733 | 0.10529 | 0.086975 | 0.086975 | 0.022888 | -0.068665 | -0.23804 | 0.36621 | 0.10986 | 0.054932 | 0.086975 | 0.032044 | 0.091553 | -121.9894 | -121.9803 | 0.20599 | 0.18768 | 0.18768 | 0.09613 | 0.09613 | 0.34332 | 121.8063 | 0.11444 | -0.004578 | 121.9757 | -0.013733 | 121.9986 | 0.07782 | -122.0444 | -121.9757 | 121.8292 | 0.086975 | 16.3788 | 0.10529
3184.875 | 122.0169 | -0.13733 | 121.9437 | -0.02739 | 0.0014056 | 0.052145 | 0.050024 | 0.0027215 | -0.0081348 | -0.0049454 | -0.0084228 | 0.017617 | 0.066561 | -0.013356 | 0.015325 | 0.022042 | -0.0059751 | 16.3559 | 121.9299 | -0.09613 | 121.6873 | 0.23346 | -0.091553 | -0.045776 | -0.041199 | 0.004578 | -0.050354 | -0.091553 | 0.036621 | 0.009155 | 0.013733 | 0.041199 | -0.013733 | -0.25635 | 0.37079 | 0.091553 | 0.045776 | 0.050354 | 0.004577 | 0.086975 | -121.9391 | -122.0352 | 0.17395 | 0.15106 | 0.14648 | 0.064087 | 0.059509 | 0.32959 | 121.7834 | 0.086975 | -0.041199 | 122.0261 | 0.054932 | 122.0673 | 0.14191 | -122.0398 | -121.994 | 121.8246 | 0.045776 | 16.4932 | 0.09613
3186.5781 | 121.9849 | -0.1236 | 121.9666 | -0.012131 | 0.0054644 | 0.053214 | 0.055151 | 0.00079894 | -0.0064258 | -0.0030228 | -0.0084228 | 0.018045 | 0.066561 | -0.0033153 | 0.015539 | 0.023964 | -0.0010617 | 16.3788 | 121.962 | -0.091553 | 121.6461 | 0.16022 | -0.14648 | -0.09613 | -0.073242 | 0.004578 | -0.059509 | -0.07782 | 0 | -0.022888 | 0.027466 | 0.032043 | -0.004578 | -0.32044 | 0.28381 | 0.027466 | -0.022888 | -0.004577 | -0.054931 | 0.064087 | -121.962 | -122.0444 | 0.1236 | 0.15106 | 0.10071 | 0.086975 | 0.036621 | 0.25177 | 121.7377 | 0.059509 | -0.018311 | 122.0535 | 0.064087 | 122.0856 | 0.12817 | -122.0581 | -122.0261 | 121.7697 | 0.045776 | 16.5024 | 0.050354
3188.3438 | 122.0901 | -0.086975 | 121.9254 | -0.012131 | 0.0014056 | 0.053427 | 0.049811 | -5.5462e-05 | -0.0074938 | 0.0006088 | -0.005371 | 0.013559 | 0.065493 | -0.0092969 | 0.012548 | 0.0261 | -0.00084805 | 16.4658 | 121.8979 | -0.073242 | 121.7331 | 0.29297 | -0.045776 | 0.027466 | 0.022888 | -0.009155 | -0.036621 | -0.009155 | 0.11902 | 0.09613 | 0.091553 | 0.013733 | -0.027466 | -0.19226 | 0.37994 | 0.11444 | 0.041199 | 0.10071 | 0.027466 | 0.050354 | -121.9345 | -121.9345 | 0.20599 | 0.17853 | 0.1831 | 0.12817 | 0.13275 | 0.36621 | 121.8063 | 0.15564 | 0.027466 | 121.9711 | 0.027466 | 121.9849 | 0.07782 | -121.9986 | -121.962 | 121.8201 | 0.07782 | 16.5527 | 0.10986
3190.0469 | 122.0261 | -0.11444 | 121.9345 | -0.0045011 | 0.0033282 | 0.055991 | 0.052801 | 0.00015814 | -0.0083484 | -0.00345 | -0.005371 | 0.016122 | 0.068056 | 0.0020251 | 0.013616 | 0.022683 | -0.0040525 | 16.5115 | 121.9391 | -0.1236 | 121.669 | 0.2243 | -0.13275 | -0.091553 | -0.032043 | -0.004578 | -0.050354 | -0.036621 | 0.032043 | -0.004578 | 0.041199 | -0.009155 | 0.004578 | -0.2655 | 0.33875 | 0.022888 | -0.01831 | 0.032043 | -0.009155 | 0.064087 | -121.9391 | -121.9711 | 0.14648 | 0.15564 | 0.10986 | 0.091553 | 0.045776 | 0.3479 | 121.7926 | 0.082397 | 0.013733 | 122.0627 | 0.045776 | 122.0535 | 0.10986 | -122.0581 | -121.9849 | 121.7834 | 0.07782 | 16.626 | 0.082398
3191.8125 | 121.994 | -0.11902 | 121.9528 | -0.012131 | 0.00461 | 0.055136 | 0.055151 | 0.0042169 | -0.0081348 | -0.0055862 | -0.005371 | 0.016977 | 0.065065 | -0.0022473 | 0.018743 | 0.02546 | -0.0074705 | 16.5848 | 121.9574 | -0.10071 | 121.637 | 0.19226 | -0.15564 | -0.07782 | -0.064087 | 0 | -0.059509 | -0.059509 | -0.009155 | -0.036621 | 0.018311 | 0.018311 | 0.004577 | -0.31586 | 0.31128 | 0.041199 | -0.036621 | 0.022888 | -0.054932 | 0.05951 | -121.9528 | -122.0123 | 0.10986 | 0.13733 | 0.082398 | 0.07782 | 0.022888 | 0.29297 | 121.7377 | 0.050354 | 0 | 122.0581 | 0.059509 | 122.0764 | 0.11902 | -122.0535 | -122.0123 | 121.756 | 0.05951 | 16.7038 | 0.054932
3193.5781 | 122.1176 | -0.064087 | 121.9254 | -0.02739 | -0.00094422 | 0.054068 | 0.048742 | -0.0019781 | -0.010698 | -3.1996e-05 | -0.0084228 | 0.013345 | 0.065706 | -0.0075879 | 0.015112 | 0.025673 | -0.0046933 | 16.7038 | 121.8796 | -0.064087 | 121.8063 | 0.40741 | 0.045776 | 0.068665 | 0.1236 | -0.041199 | -0.013733 | 0.041199 | 0.17395 | 0.16479 | 0.13275 | 0 | -0.045776 | -0.11902 | 0.4715 | 0.13275 | 0.10986 | 0.13275 | 0.10986 | 0.050354 | -121.9666 | -121.8842 | 0.23804 | 0.19684 | 0.22888 | 0.14648 | 0.17853 | 0.4715 | 121.8704 | 0.18768 | 0.054932 | 121.9437 | -0.027466 | 121.9437 | 0.022888 | -121.9894 | -121.9391 | 121.8704 | 0.10529 | 16.7679 | 0.18768
3195.2812 | 121.994 | -0.12817 | 121.9666 | -0.02739 | 0.0050372 | 0.054068 | 0.056219 | 0.0035761 | -0.0072802 | -0.0011002 | -0.005371 | 0.018258 | 0.065279 | -0.0058789 | 0.017675 | 0.024819 | -0.0027707 | 16.7038 | 121.9482 | -0.11902 | 121.637 | 0.18768 | -0.15106 | -0.10071 | -0.068665 | 0 | -0.054932 | -0.059509 | 0.009155 | -0.041199 | 0.013733 | 0.009155 | -0.018311 | -0.32959 | 0.31586 | 0.027466 | -0.022888 | 0.018311 | -0.032043 | 0.073242 | -121.9666 | -122.0261 | 0.13733 | 0.14191 | 0.086975 | 0.068665 | 0.013733 | 0.3067 | 121.756 | 0.064087 | -0.004577 | 122.0673 | 0.054932 | 122.0764 | 0.12817 | -122.0856 | -122.0215 | 121.7651 | 0.068665 | 16.832 | 0.059509
3197.0469 | 122.1176 | -0.073242 | 121.9116 | -0.0045011 | 0.001192 | 0.052573 | 0.049383 | 0.00058534 | -0.0087756 | -0.00345 | -0.0023192 | 0.014413 | 0.068483 | -0.0056653 | 0.014043 | 0.024391 | -0.0038389 | 16.777 | 121.8842 | -0.064087 | 121.756 | 0.37537 | 0.032043 | 0.068665 | 0.11444 | -0.045776 | -0.009155 | 0.059509 | 0.17853 | 0.16479 | 0.13733 | 0.009155 | -0.027466 | -0.15564 | 0.44861 | 0.14191 | 0.10529 | 0.13275 | 0.09613 | 0.064087 | -121.9574 | -121.8521 | 0.25177 | 0.21057 | 0.23804 | 0.14648 | 0.17395 | 0.43945 | 121.8201 | 0.18768 | 0.068664 | 121.9482 | -0.036621 | 121.9574 | 0.027466 | -121.9757 | -121.9208 | 121.8292 | 0.13275 | 16.8503 | 0.18768
3198.8125 | 122.0673 | -0.091553 | 121.9299 | -0.01976 | 0.0039692 | 0.053854 | 0.052801 | -0.00026906 | -0.010912 | -0.0030228 | -0.005371 | 0.016549 | 0.081728 | -0.0099377 | 0.013403 | 0.024605 | -0.0010617 | 16.8274 | 121.8979 | -0.07782 | 121.7377 | 0.3479 | -0.032043 | 0.032043 | 0.050354 | -0.032043 | -0.027466 | 0 | 0.10986 | 0.091553 | 0.09613 | 0.013733 | -0.032044 | -0.19226 | 0.43945 | 0.1236 | 0.05951 | 0.10986 | 0.045777 | 0.064087 | -121.962 | -121.9299 | 0.20142 | 0.18768 | 0.18311 | 0.1236 | 0.11902 | 0.42572 | 121.8155 | 0.13733 | 0.027466 | 121.9757 | -0.004577 | 121.9894 | 0.05951 | -122.0078 | -121.9574 | 121.8292 | 0.091553 | 16.9189 | 0.14191
3200.5156 | 121.843 | -1.6983 | 119.9615 | -0.01976 | 0.0022602 | 0.054068 | 0.049383 | 0.0016535 | -0.0064258 | -0.0032364 | -0.011475 | 0.099008 | 3.2897 | -0.090687 | 0.014257 | 0.030373 | 0.0017153 | 16.008 | 120.0027 | -1.6663 | 119.8746 | -1.2177 | -1.6296 | -1.5656 | -0.35248 | -0.48065 | -1.3824 | -0.38452 | -0.31128 | -0.23804 | -0.22888 | 0.032043 | 0.041199 | -0.086975 | 0.48065 | 0.13275 | 0.068664 | 0.10071 | 0.036621 | 0.31586 | -120.4422 | -120.3461 | 1.387 | 1.4694 | 1.4603 | 1.1536 | 1.1444 | 0.44861 | 121.5408 | 1.0712 | 0.99793 | 121.669 | 0.90179 | 121.701 | 1.2177 | -121.6278 | -121.344 | 121.5729 | 1.3138 | 17.7063 | 1.3458
3202.2812 | 122.0352 | -0.041199 | 121.8246 | -0.0045011 | 0.0016192 | 0.052786 | 0.052374 | -0.0015509 | -0.0072802 | -0.0030228 | -0.005371 | 0.019754 | 0.040712 | -0.016987 | 0.013403 | 0.023964 | -0.0066159 | 17.038 | 121.7834 | -0.045776 | 121.701 | 0.43945 | 0.073242 | 0.10986 | 0.14648 | -0.041199 | 0.004578 | 0.082397 | 0.20142 | 0.16937 | 0.13275 | -0.004577 | -0.041199 | -0.1236 | 0.48065 | 0.15106 | 0.11444 | 0.15564 | 0.11902 | 0.045777 | -121.8658 | -121.7422 | 0.24262 | 0.17395 | 0.21057 | 0.12817 | 0.16479 | 0.48523 | 121.7468 | 0.19684 | 0.077819 | 121.8292 | -0.045777 | 121.8246 | 0 | -121.8704 | -121.8201 | 121.7422 | 0.1236 | 17.0792 | 0.18768
3203.9844 | 122.0581 | -0.050354 | 121.8475 | -0.0045011 | -0.00030342 | 0.051505 | 0.049597 | 0.00058534 | -0.0098438 | -0.0019546 | -0.0084228 | 0.018686 | 0.039644 | -0.018696 | 0.01383 | 0.022896 | -0.0021299 | 17.1158 | 121.8201 | -0.054932 | 121.7194 | 0.45319 | 0.068665 | 0.10529 | 0.12817 | -0.022888 | -0.004578 | 0.068665 | 0.21057 | 0.16937 | 0.13733 | -0.004578 | -0.027466 | -0.12817 | 0.50354 | 0.15564 | 0.11902 | 0.16022 | 0.1236 | 0.045776 | -121.8704 | -121.7789 | 0.26093 | 0.18768 | 0.21973 | 0.14191 | 0.17395 | 0.50812 | 121.7743 | 0.21515 | 0.073243 | 121.875 | -0.01831 | 121.8704 | 0.027466 | -121.9025 | -121.8521 | 121.7697 | 0.11902 | 17.1661 | 0.17853
3205.75 | 121.9208 | -0.10986 | 121.9162 | -0.01976 | 0.006319 | 0.056631 | 0.051092 | 0.0040033 | -0.0077074 | -0.0015274 | -0.0084228 | 0.022958 | 0.040926 | -0.018055 | 0.01618 | 0.02076 | -0.0021299 | 17.1066 | 121.9254 | -0.082397 | 121.6095 | 0.24719 | -0.13275 | -0.068665 | -0.045776 | 0.018311 | -0.041199 | -0.032043 | 0.027466 | -0.013733 | 0.036621 | 0.027466 | 0.009155 | -0.3067 | 0.35706 | 0.041198 | -0.022888 | 0.013732 | -0.050354 | 0.068664 | -121.8979 | -121.9482 | 0.13733 | 0.14648 | 0.09613 | 0.07782 | 0.027466 | 0.32959 | 121.6919 | 0.068665 | 0.009156 | 122.0078 | 0.05951 | 122.0352 | 0.12817 | -121.9986 | -121.9574 | 121.7194 | 0.07782 | 17.2165 | 0.064087
3207.5156 | 122.0444 | -0.059509 | 121.8704 | -0.0045011 | 0.0033282 | 0.053641 | 0.049597 | 0.0022943 | -0.0077074 | -0.0036636 | -0.005371 | 0.019754 | 0.043703 | -0.012074 | 0.014471 | 0.024605 | -0.0031979 | 17.2073 | 121.8796 | -0.050354 | 121.6873 | 0.3479 | -0.004578 | 0.041199 | 0.036621 | -0.022888 | -0.022888 | 0.018311 | 0.13733 | 0.12817 | 0.10529 | 0.009155 | 0.009156 | -0.18311 | 0.40741 | 0.10071 | 0.054931 | 0.091553 | 0.045776 | 0.036621 | -121.8933 | -121.8521 | 0.19684 | 0.16479 | 0.18768 | 0.12817 | 0.15106 | 0.39825 | 121.7377 | 0.16022 | 0.041199 | 121.9299 | 0 | 121.9391 | 0.036621 | -121.9208 | -121.8933 | 121.7468 | 0.07782 | 17.2668 | 0.09613
3209.2969 | 122.0673 | -0.054932 | 121.8842 | -0.012131 | 0.0039692 | 0.053854 | 0.05216 | 0.00037174 | -0.0074938 | -0.0013138 | -0.011475 | 0.022744 | 0.04413 | -0.0073743 | 0.017034 | 0.025887 | -0.0042661 | 17.2897 | 121.907 | -0.050354 | 121.7285 | 0.37994 | 0.009155 | 0.050354 | 0.09613 | -0.018311 | -0.009155 | 0.082397 | 0.15564 | 0.1236 | 0.14648 | 0.004578 | 0.022888 | -0.15564 | 0.43488 | 0.10529 | 0.064087 | 0.10071 | 0.059509 | 0.045777 | -121.9025 | -121.8018 | 0.21057 | 0.20142 | 0.17853 | 0.15564 | 0.13275 | 0.4303 | 121.7789 | 0.16479 | 0.091552 | 121.9574 | -0.009156 | 121.962 | 0.036621 | -121.9345 | -121.8933 | 121.7834 | 0.13733 | 17.3447 | 0.15106
3211 | 122.0581 | -0.064087 | 121.8842 | -0.0045011 | 0.0039692 | 0.051932 | 0.048315 | -0.00048286 | -0.0064258 | -0.0040908 | -0.005371 | 0.022958 | 0.045198 | -0.021473 | 0.015752 | 0.024819 | -0.0038389 | 17.4088 | 121.8384 | -0.045776 | 121.788 | 0.46234 | 0.068665 | 0.10071 | 0.13275 | -0.041199 | 0.004578 | 0.054932 | 0.19226 | 0.16479 | 0.14191 | 0.018311 | -0.045776 | -0.09613 | 0.52643 | 0.1648 | 0.13275 | 0.14648 | 0.11444 | 0.068665 | -121.9254 | -121.8292 | 0.25635 | 0.20599 | 0.22888 | 0.13733 | 0.16022 | 0.50812 | 121.8338 | 0.18768 | 0.050354 | 121.8842 | -0.045777 | 121.9025 | 0.022888 | -121.9299 | -121.8796 | 121.8521 | 0.11902 | 17.4728 | 0.19684
3212.7656 | 121.9711 | -0.09613 | 121.8979 | -0.012131 | 0.0048236 | 0.053214 | 0.052801 | 0.0029351 | -0.0098438 | -0.0021682 | -0.0023192 | 0.022744 | 0.050112 | -0.01186 | 0.018957 | 0.024819 | -0.0044797 | 17.5049 | 121.9345 | -0.073242 | 121.6965 | 0.35248 | -0.045776 | -0.013733 | 0.022888 | -0.004578 | -0.013733 | -0.013733 | 0.073242 | 0.022888 | 0.054932 | 0.022888 | 0.036621 | -0.20142 | 0.44861 | 0.082397 | 0.050354 | 0.059509 | 0.027466 | 0.082397 | -121.9025 | -121.9116 | 0.16937 | 0.15106 | 0.11902 | 0.068665 | 0.036621 | 0.42572 | 121.7697 | 0.086975 | 0 | 122.0078 | 0.009155 | 122.0306 | 0.091552 | -121.9711 | -121.9116 | 121.7926 | 0.082397 | 17.601 | 0.11902
3214.5312 | 121.9803 | -0.10529 | 121.9254 | -0.012131 | 0.0022602 | 0.052573 | 0.048529 | 0.0012261 | -0.01198 | -0.0032364 | -0.0023192 | 0.019967 | 0.046694 | -0.01656 | 0.015752 | 0.025032 | -0.0038389 | 17.6056 | 121.875 | -0.059509 | 121.7239 | 0.37537 | 0 | 0.045776 | 0.013733 | 0 | -0.022888 | -0.032043 | 0.091553 | 0.050354 | 0.036621 | 0.045777 | -0.050354 | -0.20142 | 0.48065 | 0.15106 | 0.10529 | 0.10528 | 0.059509 | 0.082398 | -121.9254 | -121.9574 | 0.19684 | 0.14191 | 0.15564 | 0.059509 | 0.073242 | 0.43487 | 121.7834 | 0.11444 | -0.009155 | 121.9345 | 0.022888 | 121.9803 | 0.10529 | -121.9849 | -121.9482 | 121.8292 | 0.073243 | 17.7109 | 0.11902
3216.25 | 122.0718 | -0.054932 | 121.9025 | -0.01976 | 0.0048236 | 0.054282 | 0.052801 | -0.0028327 | -0.0098438 | -0.0038772 | -0.005371 | 0.021463 | 0.046267 | -0.0095105 | 0.014898 | 0.02546 | -0.0023435 | 17.6147 | 121.9116 | -0.068665 | 121.6965 | 0.33875 | -0.050354 | 0.013733 | 0.041199 | -0.018311 | -0.018311 | 0.054932 | 0.13733 | 0.1236 | 0.12817 | -0.013733 | 0.009155 | -0.20599 | 0.39368 | 0.068665 | 0.004578 | 0.082398 | 0.018311 | 0.036621 | -121.9208 | -121.8475 | 0.19226 | 0.18311 | 0.17853 | 0.14649 | 0.14191 | 0.40741 | 121.7651 | 0.15564 | 0.073243 | 121.9803 | 0 | 121.9666 | 0.036621 | -121.9711 | -121.9208 | 121.7514 | 0.10986 | 17.6697 | 0.096131
3218.0156 | 122.081 | -0.054932 | 121.8842 | -0.012131 | 0.0016192 | 0.051291 | 0.04917 | -0.0060371 | -0.0079212 | -0.00345 | -0.0084228 | 0.019326 | 0.044771 | -0.019551 | 0.014898 | 0.027382 | -0.0034117 | 17.7795 | 121.875 | -0.041199 | 121.788 | 0.45776 | 0.073242 | 0.10529 | 0.10071 | -0.041199 | -0.018311 | 0.059509 | 0.1831 | 0.15106 | 0.1236 | 0.013733 | -0.009155 | -0.09613 | 0.5127 | 0.16022 | 0.12817 | 0.14649 | 0.11444 | 0.036621 | -121.9254 | -121.8246 | 0.23804 | 0.17853 | 0.20599 | 0.14191 | 0.16937 | 0.49896 | 121.8292 | 0.20142 | 0.07782 | 121.9162 | -0.022888 | 121.9299 | 0.013733 | -121.9254 | -121.9025 | 121.843 | 0.11444 | 17.8345 | 0.15564
3219.7812 | 122.0627 | -0.07782 | 121.9025 | -0.0045011 | 0.001833 | 0.054282 | 0.04917 | -0.0011237 | -0.0094164 | -0.0019546 | -0.005371 | 0.019754 | 0.046267 | -0.015492 | 0.014257 | 0.0261 | -0.0068295 | 17.7704 | 121.8887 | -0.073242 | 121.7102 | 0.37537 | -0.018311 | 0.036621 | 0.032043 | -0.018311 | -0.032043 | 0.009155 | 0.13275 | 0.11444 | 0.10529 | 0.004578 | -0.013733 | -0.19226 | 0.45319 | 0.11444 | 0.059509 | 0.10986 | 0.054931 | 0.045777 | -121.9208 | -121.8933 | 0.21057 | 0.18311 | 0.19226 | 0.13733 | 0.14648 | 0.44861 | 121.7834 | 0.16479 | 0.041198 | 121.962 | 0.013732 | 121.9666 | 0.059509 | -121.9757 | -121.9345 | 121.788 | 0.086975 | 17.8482 | 0.10986
3221.4844 | 122.0261 | -0.068665 | 121.8796 | -0.01976 | 0.0020466 | 0.054068 | 0.048956 | 0.0029351 | -0.010057 | -0.00345 | -0.0023192 | 0.019326 | 0.045626 | -0.016133 | 0.01383 | 0.024391 | -0.0017027 | 17.8024 | 121.8933 | -0.064087 | 121.7194 | 0.37537 | -0.004578 | 0.036621 | 0.013733 | -0.022888 | -0.027466 | -0.004578 | 0.10529 | 0.082397 | 0.086975 | 0.004578 | 0.013733 | -0.16022 | 0.44403 | 0.10529 | 0.064087 | 0.10071 | 0.059509 | 0.041199 | -121.9025 | -121.8842 | 0.17395 | 0.15564 | 0.15106 | 0.11444 | 0.10986 | 0.43945 | 121.7834 | 0.13275 | 0.022888 | 121.9574 | 0.004578 | 121.962 | 0.045777 | -121.9437 | -121.907 | 121.788 | 0.064087 | 17.8711 | 0.082398
3223.25 | 122.0169 | -0.11444 | 121.9528 | -0.012131 | 0.001833 | 0.053 | 0.051306 | 0.0025079 | -0.0098438 | -0.0032364 | -0.0084228 | 0.025308 | 0.048403 | -0.010579 | 0.01618 | 0.02311 | -0.0049069 | 17.9031 | 121.907 | -0.10071 | 121.6553 | 0.31586 | -0.064087 | -0.036621 | -0.045776 | 0.022888 | -0.041199 | -0.041199 | 0.054932 | 0.041199 | 0.059509 | 0.013733 | -0.045777 | -0.29755 | 0.4303 | 0.07782 | 0.050354 | 0.064087 | 0.036621 | 0.073242 | -121.9299 | -121.994 | 0.16937 | 0.17395 | 0.15564 | 0.10071 | 0.082398 | 0.41657 | 121.756 | 0.096131 | 0 | 122.0078 | 0.064087 | 122.0215 | 0.13733 | -122.0535 | -121.994 | 121.7697 | 0.073242 | 18.0176 | 0.068665
3225.0156 | 121.9574 | -0.11444 | 121.9574 | -0.0045011 | 0.0054644 | 0.056204 | 0.053869 | 0.0029351 | -0.0081348 | -0.002382 | -0.005371 | 0.023385 | 0.048616 | -0.0092969 | 0.016393 | 0.023964 | -0.0014891 | 17.9764 | 121.9803 | -0.07782 | 121.6324 | 0.26093 | -0.10986 | -0.059509 | -0.068665 | 0.009155 | -0.032043 | -0.054932 | 0.009155 | -0.027466 | 0.027466 | 0.036621 | 0.022889 | -0.32501 | 0.37537 | 0.054932 | 0.004578 | 0.018311 | -0.032043 | 0.082398 | -121.9482 | -122.0123 | 0.1236 | 0.14191 | 0.086975 | 0.059509 | 0.004577 | 0.33875 | 121.7102 | 0.041198 | -0.022889 | 122.0581 | 0.041198 | 122.0947 | 0.1236 | -122.0352 | -121.9894 | 121.7468 | 0.059509 | 18.0908 | 0.045776
3226.7344 | 122.1268 | -0.050354 | 121.9116 | -0.012131 | -0.00030342 | 0.053854 | 0.050451 | -0.00069646 | -0.0098438 | -3.1996e-05 | -0.0084228 | 0.020822 | 0.047121 | -0.019551 | 0.014471 | 0.023323 | -0.0038389 | 18.1091 | 121.9025 | -0.064087 | 121.788 | 0.48523 | 0.068665 | 0.12817 | 0.13275 | -0.032043 | 0 | 0.082397 | 0.21973 | 0.16937 | 0.15564 | -0.013733 | -0.009155 | -0.1236 | 0.53558 | 0.17853 | 0.11902 | 0.19226 | 0.13275 | 0.050354 | -121.9437 | -121.8292 | 0.27008 | 0.20599 | 0.21973 | 0.15564 | 0.16937 | 0.54932 | 121.8521 | 0.21973 | 0.082397 | 121.9666 | -0.032043 | 121.9528 | 0.018311 | -121.9757 | -121.9116 | 121.8384 | 0.13275 | 18.1595 | 0.18311
3228.4844 | 122.0078 | -0.10071 | 121.9574 | -0.012131 | 0.0024738 | 0.050009 | 0.050451 | -0.0017645 | -0.00963 | -0.0013138 | -0.0023192 | 0.022958 | 0.049685 | -0.01421 | 0.015752 | 0.026955 | -0.0027707 | 18.132 | 121.9437 | -0.068665 | 121.6736 | 0.31586 | -0.059509 | -0.027466 | -0.041199 | 0 | -0.036621 | -0.022888 | 0.07782 | 0.045776 | 0.068665 | 0.032043 | -0.013732 | -0.28381 | 0.41657 | 0.073242 | 0.041199 | 0.041199 | 0.009156 | 0.064087 | -121.9574 | -121.9803 | 0.17853 | 0.16937 | 0.14648 | 0.10529 | 0.082397 | 0.38452 | 121.7422 | 0.11444 | 0.013733 | 122.0123 | 0.036621 | 122.0444 | 0.10071 | -122.0261 | -121.994 | 121.7743 | 0.07782 | 18.2327 | 0.059509
3230.25 | 121.9574 | -0.086975 | 121.9437 | -0.012131 | 0.0058918 | 0.052573 | 0.053015 | -0.0011237 | -0.0081348 | -0.0013138 | -0.005371 | 0.02189 | 0.051607 | -0.024464 | 0.01618 | 0.025887 | -0.0027707 | 18.187 | 121.9574 | -0.07782 | 121.6782 | 0.33875 | -0.09613 | -0.045776 | -0.041199 | 0.027466 | -0.032043 | -0.059509 | 0.009155 | -0.018311 | 0.027466 | 0.009155 | 0.013732 | -0.2655 | 0.42572 | 0.041199 | -0.009155 | 0.032044 | -0.01831 | 0.054932 | -121.9162 | -122.0032 | 0.09613 | 0.11444 | 0.068664 | 0.059509 | 0.013732 | 0.41657 | 121.756 | 0.041198 | -0.027466 | 122.0352 | 0.059509 | 122.0444 | 0.11444 | -122.0215 | -121.9757 | 121.7651 | 0.027466 | 18.2739 | 0.045776
3231.9531 | 121.9757 | -0.10986 | 121.9757 | -0.0045011 | 0.0086688 | 0.055136 | 0.05216 | 0.0029351 | -0.0059986 | -0.0015274 | -0.005371 | 0.022958 | 0.051607 | -0.015706 | 0.016607 | 0.02546 | -0.0051205 | 18.2556 | 121.9757 | -0.073242 | 121.6873 | 0.35706 | -0.07782 | -0.041199 | -0.004578 | 0.004578 | -0.027466 | -0.050354 | 0.036621 | -0.009155 | 0.018311 | 0.036621 | 0 | -0.28839 | 0.46692 | 0.068664 | 0.032043 | 0.032043 | -0.004578 | 0.082397 | -121.9711 | -122.0261 | 0.14648 | 0.12817 | 0.10071 | 0.045777 | 0.018311 | 0.4303 | 121.7606 | 0.064087 | -0.022888 | 122.0489 | 0.032044 | 122.0856 | 0.11444 | -122.0489 | -122.0032 | 121.7972 | 0.059509 | 18.3655 | 0.10529
3233.7188 | 122.0718 | -0.064087 | 121.9162 | -0.012131 | 0.0026874 | 0.054495 | 0.051092 | 0.0016535 | -0.0089892 | -0.0019546 | -0.0084228 | 0.02189 | 0.05353 | -0.019337 | 0.015539 | 0.026741 | -0.00020725 | 18.3472 | 121.9116 | -0.045776 | 121.7834 | 0.48523 | 0.032043 | 0.082397 | 0.11444 | -0.041199 | -0.004578 | 0.059509 | 0.16479 | 0.1236 | 0.1236 | 0.018311 | -0.004578 | -0.13275 | 0.54932 | 0.14648 | 0.09613 | 0.12817 | 0.077819 | 0.059509 | -121.9574 | -121.8567 | 0.22888 | 0.18768 | 0.18768 | 0.12817 | 0.12817 | 0.53101 | 121.8292 | 0.16937 | 0.064087 | 121.9574 | -0.036621 | 121.9757 | 0.022888 | -121.962 | -121.9208 | 121.8475 | 0.1236 | 18.4113 | 0.17853
3235.4219 | 122.113 | -0.064087 | 121.9528 | -0.0045011 | -8.9824e-05 | 0.051718 | 0.048742 | -0.0011237 | -0.0092028 | -0.0011002 | -0.0084228 | 0.021035 | 0.052248 | -0.018055 | 0.012334 | 0.025246 | 0.00021995 | 18.4433 | 121.8933 | -0.036621 | 121.8109 | 0.50354 | 0.086975 | 0.10986 | 0.1236 | -0.022888 | -0.004578 | 0.045776 | 0.18768 | 0.1831 | 0.13733 | 0.027466 | -0.059509 | -0.14191 | 0.56763 | 0.17395 | 0.15106 | 0.14648 | 0.1236 | 0.059509 | -121.9757 | -121.907 | 0.25177 | 0.20142 | 0.24719 | 0.14191 | 0.18768 | 0.54016 | 121.8475 | 0.19226 | 0.050354 | 121.9299 | -0.01831 | 121.9574 | 0.041199 | -121.9894 | -121.9574 | 121.875 | 0.10986 | 18.5074 | 0.18768
3237.2031 | 122.0673 | -0.082397 | 121.9437 | -0.0045011 | 0.0016192 | 0.052145 | 0.049597 | 0.0012261 | -0.010271 | -0.0049454 | -0.005371 | 0.021249 | 0.051821 | -0.022114 | 0.012762 | 0.025032 | -0.0049069 | 18.5028 | 121.9162 | -0.054932 | 121.7743 | 0.47607 | 0.050354 | 0.09613 | 0.073242 | -0.036621 | -0.032043 | 0.027466 | 0.15106 | 0.14191 | 0.11902 | 0.027465 | -0.027466 | -0.16937 | 0.55847 | 0.17853 | 0.13275 | 0.15106 | 0.10529 | 0.050354 | -121.9803 | -121.9162 | 0.23346 | 0.20142 | 0.2243 | 0.15106 | 0.17395 | 0.53101 | 121.8292 | 0.18311 | 0.059509 | 121.9711 | -0.004578 | 121.9986 | 0.045776 | -121.9986 | -121.9757 | 121.8567 | 0.10986 | 18.5852 | 0.15564
3238.9531 | 122.0215 | -0.091553 | 121.9482 | -0.012131 | 0.0022602 | 0.054282 | 0.053869 | -0.00091006 | -0.008562 | 0.0006088 | -0.0084228 | 0.024667 | 0.051821 | -0.010579 | 0.017675 | 0.023537 | 0.0015017 | 18.5486 | 121.9437 | -0.082397 | 121.7102 | 0.35706 | -0.036621 | -0.018311 | -0.009155 | -0.004578 | -0.041199 | -0.013733 | 0.082397 | 0.054932 | 0.07782 | 0.009156 | -0.004577 | -0.23804 | 0.44861 | 0.073242 | 0.054932 | 0.064086 | 0.045776 | 0.050354 | -121.9528 | -121.962 | 0.17395 | 0.16937 | 0.14649 | 0.11902 | 0.096131 | 0.43945 | 121.7926 | 0.1236 | 0.027466 | 122.0261 | 0.036621 | 122.0352 | 0.086975 | -122.0306 | -121.9894 | 121.8018 | 0.07782 | 18.6401 | 0.082398
3240.7188 | 122.1176 | -0.045776 | 121.9162 | -0.012131 | 0.0035418 | 0.051718 | 0.050879 | 0.0027215 | -0.0070666 | -0.0013138 | 0.00073235 | 0.020395 | 0.052462 | -0.013142 | 0.014898 | 0.026528 | -0.00020725 | 18.631 | 121.9116 | -0.045776 | 121.8155 | 0.49896 | 0.036621 | 0.082397 | 0.11444 | -0.018311 | -0.009155 | 0.068665 | 0.17395 | 0.14191 | 0.14191 | 0 | -0.004578 | -0.10071 | 0.54474 | 0.12817 | 0.082397 | 0.12817 | 0.082397 | 0.036621 | -121.9345 | -121.8475 | 0.21973 | 0.18768 | 0.18768 | 0.15106 | 0.15106 | 0.54474 | 121.8613 | 0.1831 | 0.07782 | 121.9574 | -0.009156 | 121.9574 | 0.027465 | -121.962 | -121.9254 | 121.8613 | 0.11444 | 18.6768 | 0.16022
3242.4375 | 122.1085 | -0.059509 | 121.9437 | -0.01976 | 0.0041828 | 0.055136 | 0.051092 | 0.0033623 | -0.010057 | -0.0028092 | -0.005371 | 0.021463 | 0.050966 | -0.02126 | 0.015966 | 0.025887 | -0.0076841 | 18.6996 | 121.9025 | -0.041199 | 121.8063 | 0.49439 | 0.045776 | 0.091553 | 0.1236 | -0.041199 | 0.004578 | 0.07782 | 0.16937 | 0.14191 | 0.13275 | 0.01831 | -0.041199 | -0.13733 | 0.55389 | 0.15106 | 0.10528 | 0.13275 | 0.086975 | 0.064087 | -121.9849 | -121.8658 | 0.22888 | 0.19226 | 0.20142 | 0.12817 | 0.13733 | 0.53558 | 121.8475 | 0.16479 | 0.073242 | 121.9437 | -0.045777 | 121.962 | 0.01831 | -121.9849 | -121.9391 | 121.8658 | 0.13733 | 18.7592 | 0.1831
3244.2031 | 121.9894 | -0.10529 | 121.9482 | -0.0045011 | 0.00055118 | 0.053214 | 0.050024 | 0.0016535 | -0.008562 | -0.001741 | -0.005371 | 0.023172 | 0.051607 | -0.0099377 | 0.014898 | 0.022896 | -0.0040525 | 18.6859 | 121.9574 | -0.091553 | 121.669 | 0.37079 | -0.064087 | -0.018311 | -0.064087 | 0.004578 | -0.050354 | -0.068665 | 0.045776 | 0.009155 | 0.027466 | 0.013733 | 0.009155 | -0.27924 | 0.47607 | 0.086975 | 0.041199 | 0.073242 | 0.027466 | 0.054932 | -121.9437 | -122.0169 | 0.15106 | 0.13275 | 0.11444 | 0.07782 | 0.059509 | 0.46234 | 121.7606 | 0.09613 | -0.018311 | 122.049 | 0.054932 | 122.0627 | 0.10986 | -122.0398 | -121.9986 | 121.7743 | 0.036621 | 18.7912 | 0.041199
3245.9688 | 122.0535 | -0.091553 | 121.9208 | -0.0045011 | 0.0048236 | 0.05535 | 0.053015 | 0.0010125 | -0.008562 | 0.0003952 | -0.005371 | 0.023599 | 0.051607 | -0.0099377 | 0.014898 | 0.023323 | -0.0023435 | 18.7546 | 121.9711 | -0.07782 | 121.6965 | 0.37079 | -0.068665 | -0.022888 | 0.004578 | 0.022888 | -0.036621 | 0.004578 | 0.086975 | 0.054932 | 0.091553 | 0.013733 | 0.050354 | -0.2243 | 0.46234 | 0.068665 | 0.022888 | 0.054932 | 0.009155 | 0.054932 | -121.8979 | -121.9162 | 0.17853 | 0.18311 | 0.14649 | 0.12817 | 0.091553 | 0.44861 | 121.7743 | 0.1236 | 0.041199 | 122.049 | 0.059509 | 122.0627 | 0.11444 | -121.9986 | -121.9574 | 121.788 | 0.096131 | 18.8461 | 0.096131
3247.75 | 122.0078 | -0.10071 | 121.9437 | -0.012131 | 0.00461 | 0.054068 | 0.051306 | -0.0024055 | -0.006853 | 0.0012496 | -0.0023192 | 0.023599 | 0.052248 | -0.022969 | 0.017461 | 0.021401 | 0.0010745 | 18.8278 | 121.9986 | -0.082397 | 121.6736 | 0.34332 | -0.09613 | -0.041199 | -0.050354 | 0 | -0.036621 | -0.036621 | 0.013733 | 0.009155 | 0.045776 | 0.018311 | 0.054931 | -0.27008 | 0.44403 | 0.059509 | 0.004578 | 0.041198 | -0.013733 | 0.064087 | -121.9437 | -121.9803 | 0.11444 | 0.14648 | 0.10986 | 0.082397 | 0.045776 | 0.42572 | 121.756 | 0.050354 | 0 | 122.081 | 0.036621 | 122.0993 | 0.10071 | -122.0261 | -121.9803 | 121.7743 | 0.064087 | 18.9285 | 0.050354
3249.4531 | 122.0947 | -0.07782 | 121.962 | 0.0031279 | 0.002901 | 0.053641 | 0.048956 | -0.0021919 | -0.010485 | -0.0011002 | -0.011475 | 0.021035 | 0.050325 | -0.016987 | 0.015112 | 0.027382 | -0.0068295 | 18.9926 | 121.8933 | -0.041199 | 121.8018 | 0.52643 | 0.054932 | 0.10071 | 0.10071 | -0.036621 | -0.022888 | 0.018311 | 0.15106 | 0.13275 | 0.10986 | 0.036621 | -0.068664 | -0.16022 | 0.60425 | 0.17853 | 0.13275 | 0.14191 | 0.096131 | 0.054932 | -121.9986 | -121.9437 | 0.22888 | 0.18768 | 0.21057 | 0.13275 | 0.15564 | 0.56763 | 121.843 | 0.17395 | 0.041199 | 121.9345 | -0.013733 | 121.9711 | 0.041199 | -122.0032 | -121.9849 | 121.8796 | 0.096131 | 19.0704 | 0.17853
3251.2188 | 122.0215 | -0.10529 | 121.9208 | -0.01976 | 0.0037556 | 0.054282 | 0.055151 | 0.0029351 | -0.0087756 | -0.0040908 | -0.0084228 | 0.022317 | 0.050753 | -0.018055 | 0.015112 | 0.023964 | -0.0031979 | 18.9468 | 121.9711 | -0.086975 | 121.669 | 0.36163 | -0.09613 | -0.041199 | -0.036621 | 0.009155 | -0.041199 | -0.036621 | 0.041199 | 0 | 0.050354 | 0.018311 | 0.050354 | -0.25177 | 0.46692 | 0.064087 | 0.009156 | 0.045776 | -0.009155 | 0.064087 | -121.9116 | -121.9574 | 0.14649 | 0.15564 | 0.10529 | 0.091553 | 0.041199 | 0.44861 | 121.756 | 0.082398 | 0.004578 | 122.0581 | 0.050354 | 122.0764 | 0.11444 | -122.0078 | -121.962 | 121.7743 | 0.068665 | 19.0521 | 0.068665
3253 | 122.0032 | -0.12817 | 121.9574 | -0.01976 | 0.0035418 | 0.053641 | 0.053015 | -0.00026906 | -0.0053576 | -0.00345 | -0.005371 | 0.021249 | 0.051821 | -0.014638 | 0.016821 | 0.025246 | -0.0029843 | 19.0109 | 121.9757 | -0.07782 | 121.6644 | 0.36163 | -0.10071 | -0.050354 | -0.054932 | 0.009155 | -0.050354 | -0.054932 | 0.013733 | 0.004578 | 0.041199 | 0.050354 | 0.018311 | -0.29297 | 0.48981 | 0.07782 | 0.027466 | 0.027466 | -0.022888 | 0.07782 | -121.9482 | -122.0123 | 0.14191 | 0.16937 | 0.13275 | 0.091553 | 0.054932 | 0.43945 | 121.7422 | 0.064087 | -0.004578 | 122.0535 | 0.059509 | 122.1039 | 0.13733 | -122.0352 | -122.0078 | 121.7926 | 0.073242 | 19.1391 | 0.073242
3254.7031 | 121.9757 | -0.11902 | 121.9711 | -0.012131 | 0.0054644 | 0.052786 | 0.050879 | 0.00058534 | -0.0083484 | -0.0015274 | -0.011475 | 0.025094 | 0.050539 | -0.011647 | 0.016821 | 0.025032 | -0.0034117 | 19.0338 | 121.9757 | -0.091553 | 121.6782 | 0.36621 | -0.082397 | -0.054932 | -0.091553 | 0.013733 | -0.036621 | -0.07782 | -0.009155 | -0.032043 | 0.018311 | 0.027466 | 0.004578 | -0.29297 | 0.48523 | 0.064087 | 0.036622 | 0.036621 | 0.009156 | 0.082398 | -121.9574 | -122.049 | 0.10986 | 0.13733 | 0.086976 | 0.054932 | 0.004578 | 0.45776 | 121.7697 | 0.027466 | -0.041199 | 122.0673 | 0.050354 | 122.0947 | 0.13275 | -122.0627 | -122.0078 | 121.7972 | 0.041199 | 19.1528 | 0.027466
3256.4219 | 122.049 | -0.086975 | 121.9711 | -0.02739 | 0.00076478 | 0.054495 | 0.047674 | -0.0051825 | -0.0092028 | 0.0003952 | -0.0023192 | 0.021249 | 0.05118 | -0.015492 | 0.016607 | 0.025673 | -0.0034117 | 19.1849 | 121.9437 | -0.059509 | 121.7834 | 0.52185 | 0.059509 | 0.091553 | 0.064087 | -0.022888 | -0.032043 | -0.004578 | 0.1236 | 0.10071 | 0.09613 | 0.027466 | -0.027465 | -0.18768 | 0.60883 | 0.17853 | 0.14648 | 0.15106 | 0.11902 | 0.054932 | -121.994 | -121.9757 | 0.21057 | 0.1831 | 0.18768 | 0.12817 | 0.13275 | 0.58136 | 121.843 | 0.15564 | 0.027465 | 122.0032 | 0.009155 | 122.0306 | 0.064087 | -122.0306 | -122.0032 | 121.8704 | 0.082397 | 19.2719 | 0.15106
3258.1875 | 122.0718 | -0.073242 | 121.9528 | -0.01976 | 0.001192 | 0.053214 | 0.048742 | -0.0058233 | -0.0081348 | -0.0030228 | -0.0084228 | 0.020822 | 0.052034 | -0.018483 | 0.012762 | 0.026314 | -0.00020725 | 19.1849 | 121.9025 | -0.064087 | 121.7377 | 0.46234 | -0.009155 | 0.050354 | 0.022888 | -0.018311 | -0.004578 | 0.004578 | 0.1236 | 0.091553 | 0.09613 | 0.009155 | -0.050354 | -0.21515 | 0.53558 | 0.1236 | 0.064087 | 0.11444 | 0.054932 | 0.068664 | -121.9711 | -121.9482 | 0.19684 | 0.16937 | 0.16479 | 0.10071 | 0.096131 | 0.52643 | 121.8018 | 0.12817 | 0.009156 | 121.9666 | -0.013733 | 121.9757 | 0.054931 | -122.0169 | -121.9574 | 121.8109 | 0.07782 | 19.2581 | 0.09613
3259.9531 | 121.9757 | -0.11444 | 121.9849 | -0.0045011 | 0.0052508 | 0.054282 | 0.052801 | 0.0010125 | -0.0077074 | -0.0019546 | -0.0084228 | 0.022744 | 0.050112 | -0.015065 | 0.017248 | 0.023537 | -0.0031979 | 19.2123 | 121.962 | -0.068665 | 121.6827 | 0.37079 | -0.09613 | -0.064087 | -0.082397 | 0.018311 | -0.041199 | -0.073242 | -0.009155 | -0.032043 | 0.018311 | 0.045776 | -0.022888 | -0.30212 | 0.48523 | 0.050354 | 0.018311 | 0.004578 | -0.027465 | 0.073242 | -121.9666 | -122.0581 | 0.10529 | 0.13275 | 0.082398 | 0.05951 | 0.009156 | 0.43945 | 121.7514 | 0.032044 | -0.032043 | 122.0306 | 0.05951 | 122.0764 | 0.13275 | -122.0535 | -122.0261 | 121.7972 | 0.041199 | 19.3268 | 0.032044
3261.6562 | 122.1085 | -0.068665 | 121.9208 | -0.012131 | 0.0035418 | 0.053427 | 0.050238 | -0.0036871 | -0.0077074 | -0.0004592 | -0.005371 | 0.01954 | 0.052675 | -0.01891 | 0.01383 | 0.024819 | -0.0055479 | 19.3176 | 121.9162 | -0.041199 | 121.8018 | 0.54474 | 0.041199 | 0.086975 | 0.11902 | -0.027466 | -0.022888 | 0.050354 | 0.17395 | 0.12817 | 0.14191 | 0.027466 | -0.004577 | -0.11902 | 0.6134 | 0.15564 | 0.10986 | 0.12817 | 0.082398 | 0.045777 | -121.9482 | -121.8704 | 0.24261 | 0.21057 | 0.19684 | 0.16479 | 0.15106 | 0.58594 | 121.843 | 0.19684 | 0.073242 | 121.9574 | -0.004578 | 121.9849 | 0.041199 | -121.962 | -121.9437 | 121.8704 | 0.11902 | 19.3863 | 0.18768
3263.4219 | 122.081 | -0.073242 | 121.9299 | -0.0045011 | 0.001833 | 0.052359 | 0.050024 | 0.0014397 | -0.0081348 | -0.00345 | -0.0023192 | 0.019967 | 0.052034 | -0.01656 | 0.014471 | 0.024819 | -0.0019163 | 19.3542 | 121.9208 | -0.064087 | 121.7377 | 0.47607 | 0.009155 | 0.027466 | 0.022888 | -0.022888 | -0.022888 | -0.004578 | 0.10071 | 0.086975 | 0.09613 | 0.009155 | -0.009156 | -0.19226 | 0.54932 | 0.10071 | 0.082397 | 0.091553 | 0.073242 | 0.050354 | -121.9528 | -121.9345 | 0.17395 | 0.16937 | 0.16022 | 0.11902 | 0.10986 | 0.54016 | 121.8018 | 0.1236 | 0.01831 | 121.9849 | 0 | 121.994 | 0.050354 | -121.994 | -121.9528 | 121.8109 | 0.068664 | 19.4275 | 0.09613
3265.125 | 122.0718 | -0.068665 | 121.9254 | -0.012131 | 0.0061054 | 0.054068 | 0.054297 | 0.00058534 | -0.0098438 | -0.0055862 | -0.005371 | 0.025094 | 0.05118 | -0.0099377 | 0.015966 | 0.025032 | -0.0051205 | 19.3954 | 122.0032 | -0.086975 | 121.7056 | 0.44861 | -0.064087 | -0.027466 | 0.018311 | -0.009155 | -0.018311 | 0.022888 | 0.10071 | 0.073242 | 0.11902 | -0.01831 | 0.07782 | -0.21973 | 0.51727 | 0.041199 | 0.004578 | 0.059509 | 0.022888 | 0.050354 | -121.9345 | -121.9025 | 0.16937 | 0.18768 | 0.14191 | 0.13733 | 0.091553 | 0.53558 | 121.7926 | 0.11902 | 0.041199 | 122.0901 | 0.009156 | 122.0718 | 0.05951 | -122.0123 | -121.9437 | 121.7743 | 0.091553 | 19.4641 | 0.086976
3266.8906 | 121.9986 | -0.11902 | 121.994 | -0.0045011 | 0.001833 | 0.053854 | 0.051092 | -0.00091006 | -0.011125 | -0.0013138 | -0.005371 | 0.020181 | 0.053743 | -0.013997 | 0.014684 | 0.023537 | -0.0061887 | 19.4916 | 121.9666 | -0.086975 | 121.6873 | 0.43488 | -0.045776 | -0.013733 | -0.041199 | -0.004578 | -0.045776 | -0.064087 | 0.045776 | 0.027466 | 0.022888 | 0.032044 | -0.027466 | -0.3067 | 0.55389 | 0.10529 | 0.073243 | 0.073242 | 0.041199 | 0.073243 | -121.9986 | -122.0581 | 0.16479 | 0.14191 | 0.14649 | 0.068664 | 0.073242 | 0.52185 | 121.7743 | 0.091552 | -0.018311 | 122.0535 | 0.041198 | 122.0856 | 0.11444 | -122.081 | -122.0398 | 121.8063 | 0.054932 | 19.6106 | 0.07782
3268.5938 | 122.081 | -0.07782 | 121.9345 | -0.012131 | 0.00461 | 0.054922 | 0.052374 | 0.0018671 | -0.0066394 | -0.0025956 | -0.0023192 | 0.020395 | 0.050966 | -0.019124 | 0.015112 | 0.02546 | -0.0059751 | 19.5786 | 121.9437 | -0.032043 | 121.756 | 0.53558 | 0.009155 | 0.073242 | 0.059509 | -0.018311 | -0.013733 | 0.004578 | 0.11444 | 0.091553 | 0.10529 | 0.045777 | 0.009156 | -0.17853 | 0.6134 | 0.15106 | 0.086975 | 0.10529 | 0.041198 | 0.064087 | -121.9528 | -121.9299 | 0.19226 | 0.18311 | 0.16937 | 0.11902 | 0.10529 | 0.56763 | 121.788 | 0.12817 | 0.018311 | 121.9757 | -0.004578 | 122.0215 | 0.059509 | -121.9666 | -121.9482 | 121.8338 | 0.082398 | 19.6564 | 0.13733
3270.3594 | 122.0581 | -0.073242 | 121.9803 | -0.0045011 | 0.0048236 | 0.052359 | 0.053015 | -0.00091006 | -0.00963 | -0.0025956 | -0.005371 | 0.02424 | 0.050753 | -0.021046 | 0.016393 | 0.023537 | -0.0010617 | 19.6838 | 121.9528 | -0.091553 | 121.7285 | 0.48523 | -0.027466 | 0.018311 | 0.036621 | 0.009155 | -0.018311 | 0.009155 | 0.086975 | 0.050354 | 0.082397 | -0.018311 | -0.027466 | -0.25177 | 0.55847 | 0.091553 | 0.045776 | 0.10986 | 0.064087 | 0.054931 | -121.9711 | -121.9711 | 0.16022 | 0.15564 | 0.1236 | 0.10071 | 0.068665 | 0.57678 | 121.8201 | 0.10529 | 0.027466 | 122.0444 | 0.027466 | 122.0261 | 0.082397 | -122.0718 | -121.9986 | 121.8018 | 0.082397 | 19.7571 | 0.10986
3272.1406 | 121.9711 | -0.10529 | 121.9666 | -0.012131 | 0.001192 | 0.051505 | 0.047888 | -0.0015509 | -0.013689 | -0.0043046 | -0.0084228 | 0.022103 | 0.05353 | -0.017415 | 0.01383 | 0.023537 | -0.0012753 | 19.7159 | 121.9711 | -0.082397 | 121.6782 | 0.43945 | -0.054932 | -0.018311 | -0.054932 | 0.013733 | -0.041199 | -0.073242 | 0.018311 | 0.009155 | 0.032043 | 0.022889 | 0.004577 | -0.28839 | 0.54474 | 0.086975 | 0.050354 | 0.064086 | 0.027465 | 0.064087 | -121.9528 | -122.0398 | 0.1236 | 0.13733 | 0.11444 | 0.073242 | 0.050354 | 0.52185 | 121.7606 | 0.05951 | -0.032043 | 122.0535 | 0.054932 | 122.0764 | 0.11902 | -122.049 | -122.0078 | 121.7834 | 0.032044 | 19.8212 | 0.050354
3273.8594 | 121.994 | -0.11444 | 121.9849 | -0.0045011 | 0.0020466 | 0.053641 | 0.049811 | -0.0030463 | -0.0079212 | -0.0019546 | -0.0084228 | 0.021463 | 0.050966 | -0.018269 | 0.015325 | 0.025887 | -0.00063445 | 19.7708 | 121.9528 | -0.068665 | 121.6965 | 0.46692 | -0.041199 | -0.009155 | -0.050354 | 0.009155 | -0.032043 | -0.07782 | 0.054932 | 0.022888 | 0.022888 | 0.045776 | -0.032043 | -0.28839 | 0.58136 | 0.10529 | 0.073242 | 0.05951 | 0.027466 | 0.082398 | -121.9757 | -122.0627 | 0.16937 | 0.13733 | 0.13733 | 0.054931 | 0.054931 | 0.53558 | 121.7651 | 0.086975 | -0.045777 | 122.0215 | 0.041198 | 122.0673 | 0.1236 | -122.0535 | -122.0169 | 121.8109 | 0.036621 | 19.8853 | 0.064087
3275.625 | 122.0993 | -0.059509 | 121.9482 | -0.012131 | 0.0061054 | 0.053214 | 0.051306 | 0.0044305 | -0.0092028 | -0.0055862 | -0.0084228 | 0.02189 | 0.050112 | -0.017628 | 0.014257 | 0.025246 | -0.0074705 | 19.8532 | 121.9391 | -0.073242 | 121.7514 | 0.52185 | 0 | 0.041199 | 0.064087 | -0.013733 | -0.009155 | 0.050354 | 0.11902 | 0.10529 | 0.13733 | -0.013733 | -0.009155 | -0.19684 | 0.58136 | 0.10071 | 0.059509 | 0.11444 | 0.073242 | 0.050354 | -121.962 | -121.8979 | 0.17853 | 0.19684 | 0.16479 | 0.14648 | 0.11444 | 0.59509 | 121.8246 | 0.12817 | 0.059509 | 122.0123 | -0.004578 | 121.9986 | 0.045776 | -122.0215 | -121.9574 | 121.8109 | 0.10986 | 19.9127 | 0.1236
3277.3906 | 121.9803 | -0.11444 | 121.9894 | -0.012131 | 0.0050372 | 0.054495 | 0.051733 | 0.00037174 | -0.008562 | -0.0028092 | -0.011475 | 0.022317 | 0.051393 | -0.014424 | 0.016393 | 0.025246 | -0.00042085 | 19.9448 | 121.9757 | -0.10071 | 121.6782 | 0.42114 | -0.086975 | -0.054932 | -0.10529 | 0.009155 | -0.054932 | -0.07782 | 0.009155 | -0.022888 | 0.018311 | 0.013733 | -0.013733 | -0.31128 | 0.53558 | 0.059509 | 0.027466 | 0.045776 | 0.013733 | 0.059509 | -121.9803 | -122.0673 | 0.1236 | 0.13275 | 0.091553 | 0.073243 | 0.032044 | 0.52185 | 121.7789 | 0.064087 | -0.022888 | 122.0764 | 0.064087 | 122.0901 | 0.1236 | -122.0901 | -122.0444 | 121.7926 | 0.036621 | 20.0592 | 0.009155
3279.1562 | 121.9894 | -0.10071 | 121.9849 | -0.012131 | 0.0037556 | 0.053427 | 0.052801 | 0.0046441 | -0.0098438 | -0.00345 | -0.005371 | 0.024026 | 0.049471 | -0.011433 | 0.015112 | 0.02546 | -0.0023435 | 20.0592 | 121.9849 | -0.073242 | 121.701 | 0.47607 | -0.073242 | -0.009155 | -0.022888 | 0.004578 | -0.036621 | -0.045776 | 0.045776 | -0.004578 | 0.022888 | 0.027466 | 0 | -0.28381 | 0.57678 | 0.091553 | 0.027466 | 0.064087 | 0 | 0.064087 | -121.9803 | -122.0306 | 0.14648 | 0.1236 | 0.09613 | 0.059509 | 0.032043 | 0.54932 | 121.7743 | 0.082397 | -0.009155 | 122.0581 | 0.041199 | 122.0856 | 0.10529 | -122.0581 | -122.0215 | 121.8018 | 0.054932 | 20.1599 | 0.07782
3280.8594 | 121.994 | -0.11444 | 121.994 | -0.012131 | 0.0024738 | 0.05065 | 0.050024 | 0.0029351 | -0.0083484 | -0.0043046 | -0.0023192 | 0.022744 | 0.051393 | -0.013997 | 0.015752 | 0.026528 | -0.0027707 | 20.0821 | 121.9574 | -0.10071 | 121.6782 | 0.4715 | -0.041199 | -0.009155 | -0.073242 | 0.022888 | -0.059509 | -0.073242 | 0.032043 | 0.018311 | 0.032043 | 0.013733 | -0.036622 | -0.31586 | 0.58594 | 0.10529 | 0.073242 | 0.091553 | 0.059509 | 0.054932 | -121.9711 | -122.0673 | 0.14648 | 0.14648 | 0.13275 | 0.091552 | 0.07782 | 0.5722 | 121.7789 | 0.091552 | -0.013733 | 122.0581 | 0.082397 | 122.0718 | 0.13733 | -122.0947 | -122.0535 | 121.7926 | 0.041199 | 20.1965 | 0.041199
3282.625 | 122.1176 | -0.082397 | 121.9574 | -0.0045011 | 0.0014056 | 0.051718 | 0.04917 | 0.0022943 | -0.0070666 | -0.0030228 | -0.005371 | 0.019754 | 0.050539 | -0.017628 | 0.015112 | 0.024819 | -0.0044797 | 20.2606 | 121.9162 | -0.045776 | 121.8063 | 0.6134 | 0.086975 | 0.1236 | 0.091553 | -0.022888 | -0.009155 | 0.041199 | 0.17853 | 0.15106 | 0.11902 | 0.036621 | -0.041198 | -0.15106 | 0.6958 | 0.20599 | 0.16937 | 0.16937 | 0.13275 | 0.073242 | -121.9803 | -121.9162 | 0.26092 | 0.20142 | 0.23346 | 0.12817 | 0.16022 | 0.65918 | 121.8521 | 0.18768 | 0.050354 | 121.962 | -0.013733 | 121.9986 | 0.059509 | -122.0032 | -121.9666 | 121.8887 | 0.1236 | 20.343 | 0.17395
3284.4062 | 122.1176 | -0.054932 | 121.9482 | -0.012131 | 0.00097838 | 0.052573 | 0.050451 | -0.00048286 | -0.008562 | -0.0021682 | -0.0084228 | 0.02189 | 0.050753 | -0.022969 | 0.014898 | 0.025032 | -0.0070433 | 20.311 | 121.9116 | -0.050354 | 121.8155 | 0.63171 | 0.10071 | 0.1236 | 0.10529 | -0.027466 | -0.004578 | 0.045776 | 0.1831 | 0.16937 | 0.1236 | 0.004578 | -0.036621 | -0.13275 | 0.68665 | 0.17853 | 0.15564 | 0.17395 | 0.15106 | 0.050354 | -121.9757 | -121.9025 | 0.23804 | 0.17853 | 0.22431 | 0.12817 | 0.17395 | 0.68207 | 121.8658 | 0.18768 | 0.050354 | 121.962 | -0.022888 | 121.9666 | 0.027466 | -121.9986 | -121.9528 | 121.8704 | 0.10071 | 20.3659 | 0.16022
3286.125 | 122.0581 | -0.09613 | 121.9482 | -0.0045011 | 0.0050372 | 0.053854 | 0.050451 | 0.0044305 | -0.0081348 | -0.0028092 | -0.005371 | 0.024026 | 0.052034 | -0.0060925 | 0.01917 | 0.0261 | -0.0012753 | 20.3613 | 121.962 | -0.068665 | 121.7194 | 0.50354 | -0.022888 | 0.027466 | -0.009155 | 0.018311 | -0.027466 | -0.032043 | 0.07782 | 0.059509 | 0.073242 | 0.027465 | 0.013733 | -0.22888 | 0.59967 | 0.1236 | 0.073242 | 0.096131 | 0.045777 | 0.068664 | -121.9299 | -121.9803 | 0.17395 | 0.16937 | 0.15564 | 0.10071 | 0.086975 | 0.5722 | 121.788 | 0.10529 | -0.004577 | 122.0306 | 0.045777 | 122.0581 | 0.11444 | -122.0169 | -121.9757 | 121.8155 | 0.064087 | 20.4575 | 0.086975
3287.8906 | 122.081 | -0.068665 | 121.9391 | -0.02739 | 0.0020466 | 0.051291 | 0.048315 | -0.0028327 | -0.011339 | -0.0028092 | -0.0084228 | 0.01954 | 0.050753 | -0.017415 | 0.015112 | 0.026528 | -0.00020725 | 20.4163 | 121.9437 | -0.068665 | 121.7422 | 0.55847 | 0.022888 | 0.073242 | 0.032043 | -0.013733 | -0.036621 | 0.009155 | 0.1236 | 0.10071 | 0.10529 | 0 | 0.004578 | -0.19684 | 0.62714 | 0.14191 | 0.091553 | 0.14191 | 0.091553 | 0.032044 | -121.9528 | -121.9299 | 0.19226 | 0.17395 | 0.16937 | 0.14191 | 0.13733 | 0.62714 | 121.8109 | 0.16022 | 0.045776 | 122.0123 | 0.022888 | 122.0123 | 0.054932 | -122.0078 | -121.9757 | 121.8109 | 0.07782 | 20.4849 | 0.10071
3289.5938 | 122.0718 | -0.064087 | 121.9254 | -0.0045011 | 0.0054644 | 0.054709 | 0.051092 | -0.0017645 | -0.0094164 | -0.00345 | 0.00073235 | 0.019326 | 0.049471 | -0.012501 | 0.015966 | 0.024819 | -0.0059751 | 20.5215 | 121.9162 | -0.041199 | 121.788 | 0.64087 | 0.018311 | 0.091553 | 0.10071 | -0.032043 | -0.013733 | 0.032043 | 0.11444 | 0.10529 | 0.10529 | 0.022888 | -0.009155 | -0.13733 | 0.70496 | 0.15564 | 0.082398 | 0.13275 | 0.05951 | 0.050354 | -121.9574 | -121.8933 | 0.17853 | 0.16937 | 0.16937 | 0.11902 | 0.11902 | 0.68207 | 121.8292 | 0.12817 | 0.045776 | 121.9574 | -0.01831 | 121.9803 | 0.032044 | -121.9666 | -121.9391 | 121.8521 | 0.09613 | 20.5856 | 0.1648
3291.3594 | 122.0215 | -0.10529 | 121.9849 | -0.012131 | 0.0065326 | 0.053214 | 0.052801 | 0.0027215 | -0.0089892 | -0.000673 | -0.0084228 | 0.024026 | 0.049898 | -0.0092969 | 0.015966 | 0.022683 | -0.0036253 | 20.5948 | 121.9528 | -0.054932 | 121.7651 | 0.55847 | -0.009155 | 0.018311 | 0.032043 | 0.013733 | -0.041199 | -0.027466 | 0.050354 | 0.032043 | 0.050354 | 0.050354 | -0.032043 | -0.21973 | 0.66376 | 0.1236 | 0.096131 | 0.073243 | 0.045777 | 0.064087 | -121.9711 | -122.0123 | 0.15564 | 0.15564 | 0.13733 | 0.091553 | 0.073242 | 0.6134 | 121.8201 | 0.091553 | 0.013733 | 122.0078 | 0.054932 | 122.0581 | 0.11902 | -122.0398 | -122.0261 | 121.8704 | 0.07782 | 20.7001 | 0.13733
3293.1406 | 122.0032 | -0.1236 | 121.994 | -0.01976 | 0.00012398 | 0.054068 | 0.049383 | -0.0026191 | -0.010698 | -0.0030228 | -0.005371 | 0.019967 | 0.047976 | -0.018055 | 0.017461 | 0.023964 | -0.00063445 | 20.6589 | 121.9345 | -0.054932 | 121.7331 | 0.55847 | 0.013733 | 0.027466 | -0.022888 | 0 | -0.054932 | -0.068665 | 0.064087 | 0.036621 | 0.032043 | 0.068664 | -0.05951 | -0.26093 | 0.68207 | 0.15106 | 0.13733 | 0.082398 | 0.068665 | 0.068664 | -121.994 | -122.0627 | 0.18768 | 0.15564 | 0.16022 | 0.086975 | 0.091553 | 0.6134 | 121.788 | 0.11902 | -0.013733 | 121.9894 | 0.054932 | 122.0581 | 0.1236 | -122.049 | -122.049 | 121.8567 | 0.054931 | 20.7825 | 0.10071
3294.9062 | 122.1313 | -0.054932 | 121.9437 | -0.01976 | 0.0052508 | 0.054922 | 0.05152 | 0.0040033 | -0.0098438 | -0.0021682 | -0.005371 | 0.021463 | 0.047976 | -0.017415 | 0.013403 | 0.023537 | -0.0057615 | 20.7367 | 121.9482 | -0.036621 | 121.8018 | 0.64545 | 0.041199 | 0.082397 | 0.11444 | -0.045776 | -0.018311 | 0.07782 | 0.15564 | 0.13733 | 0.14648 | 0.018311 | 0.004577 | -0.14191 | 0.70038 | 0.13733 | 0.096131 | 0.11902 | 0.07782 | 0.036621 | -121.9894 | -121.8658 | 0.21057 | 0.20142 | 0.19226 | 0.16479 | 0.15564 | 0.68207 | 121.8384 | 0.17395 | 0.096131 | 121.9849 | -0.027465 | 122.0032 | 0.009156 | -121.9803 | -121.962 | 121.8567 | 0.13275 | 20.7916 | 0.16937
3296.6094 | 122.113 | -0.082397 | 121.9345 | -0.0045011 | 0.00461 | 0.051291 | 0.050665 | 0.0022943 | -0.0098438 | -0.0040908 | -0.0084228 | 0.020395 | 0.048189 | -0.016347 | 0.012762 | 0.0261 | -0.0055479 | 20.7642 | 121.9254 | -0.045776 | 121.7743 | 0.61798 | 0.045776 | 0.10529 | 0.059509 | -0.027466 | -0.018311 | 0.036621 | 0.15564 | 0.14648 | 0.13275 | 0.036621 | -0.009155 | -0.16022 | 0.70038 | 0.18768 | 0.12817 | 0.15106 | 0.091552 | 0.064086 | -121.962 | -121.8979 | 0.23804 | 0.21515 | 0.22888 | 0.15106 | 0.16479 | 0.66376 | 121.8201 | 0.17395 | 0.054932 | 121.9711 | -0.009155 | 122.0078 | 0.054931 | -121.9803 | -121.9528 | 121.8567 | 0.11902 | 20.8466 | 0.14191
3298.375 | 122.0947 | -0.082397 | 121.9528 | -0.01976 | 0.0037556 | 0.054709 | 0.05216 | 0.00079894 | -0.0087756 | -0.0040908 | -0.005371 | 0.019326 | 0.048403 | -0.015919 | 0.012975 | 0.025032 | -0.0040525 | 20.8511 | 121.9299 | -0.045776 | 121.7834 | 0.6546 | 0.013733 | 0.10529 | 0.086975 | -0.027466 | -0.022888 | 0.018311 | 0.11444 | 0.091553 | 0.10071 | 0.036621 | -0.022888 | -0.16937 | 0.737 | 0.18768 | 0.09613 | 0.15106 | 0.059509 | 0.059509 | -121.9803 | -121.9345 | 0.19684 | 0.18311 | 0.17395 | 0.1236 | 0.11444 | 0.70038 | 121.8292 | 0.13733 | 0.041199 | 121.9757 | -0.004578 | 122.0123 | 0.054931 | -121.9986 | -121.9757 | 121.8658 | 0.10071 | 20.9335 | 0.16937
3300.0781 | 122.1039 | -0.059509 | 121.9391 | -0.0045011 | 0.0037556 | 0.053641 | 0.051733 | 0.0014397 | -0.0072802 | -0.0013138 | -0.0084228 | 0.020395 | 0.047976 | -0.012929 | 0.015752 | 0.023751 | -0.0012753 | 20.9152 | 121.9345 | -0.041199 | 121.8063 | 0.66376 | 0.045776 | 0.10986 | 0.10529 | -0.022888 | 0.013733 | 0.064087 | 0.12817 | 0.11902 | 0.11444 | 0.01831 | -0.004578 | -0.13275 | 0.72327 | 0.16937 | 0.10528 | 0.15106 | 0.086975 | 0.073242 | -121.962 | -121.875 | 0.18768 | 0.17395 | 0.17853 | 0.10071 | 0.10529 | 0.70496 | 121.8475 | 0.11444 | 0.050354 | 121.9757 | -0.036621 | 121.994 | 0.036621 | -121.9803 | -121.9254 | 121.8658 | 0.1236 | 20.9747 | 0.16479
3301.8438 | 122.0261 | -0.10529 | 121.9528 | -0.012131 | -0.00073062 | 0.052786 | 0.050024 | 0.0012261 | -0.0070666 | -0.0025956 | -0.0084228 | 0.022103 | 0.046907 | -0.015492 | 0.015112 | 0.022469 | -0.0025571 | 21.0251 | 121.9162 | -0.045776 | 121.7651 | 0.64087 | 0.054932 | 0.091553 | 0.027466 | -0.004578 | -0.027466 | -0.041199 | 0.082397 | 0.050354 | 0.032043 | 0.05951 | -0.036621 | -0.18768 | 0.74616 | 0.19684 | 0.16022 | 0.13733 | 0.10071 | 0.07782 | -121.9574 | -121.994 | 0.18768 | 0.13733 | 0.15564 | 0.059509 | 0.07782 | 0.68665 | 121.8109 | 0.10986 | -0.013733 | 121.962 | 0.022888 | 122.0215 | 0.10071 | -121.9986 | -121.9803 | 121.8704 | 0.064087 | 21.1304 | 0.13275
3303.6094 | 122.1405 | -0.050354 | 121.9437 | -0.0045011 | -0.00030342 | 0.052359 | 0.050238 | 0.0025079 | -0.00963 | -0.00345 | -0.005371 | 0.020181 | 0.047121 | -0.018696 | 0.015539 | 0.023751 | -0.0038389 | 21.0663 | 121.9254 | -0.050354 | 121.7972 | 0.69122 | 0.10071 | 0.12817 | 0.10986 | -0.041199 | -0.009155 | 0.064087 | 0.17395 | 0.16479 | 0.15106 | 0 | -0.018311 | -0.14648 | 0.74158 | 0.17853 | 0.15106 | 0.17853 | 0.15106 | 0.041199 | -121.9849 | -121.8796 | 0.2243 | 0.20142 | 0.21515 | 0.16022 | 0.17395 | 0.74158 | 121.8475 | 0.1831 | 0.073242 | 121.9757 | -0.032044 | 121.9757 | 0.009155 | -121.994 | -121.9528 | 121.8475 | 0.11444 | 21.1166 | 0.16022
3305.3594 | 121.9986 | -0.13275 | 122.0032 | -0.01976 | 0.0031146 | 0.052359 | 0.05152 | -0.0043281 | -0.010057 | -0.0036636 | -0.0084228 | 0.023172 | 0.04648 | -0.014638 | 0.017034 | 0.022042 | -0.0014891 | 21.0892 | 121.9666 | -0.091553 | 121.6919 | 0.55389 | -0.027466 | -0.018311 | -0.068665 | 0.018311 | -0.054932 | -0.07782 | 0.036621 | 0.013733 | 0.013733 | 0.041198 | -0.036621 | -0.31128 | 0.68664 | 0.11444 | 0.10529 | 0.073242 | 0.064087 | 0.077819 | -121.9849 | -122.081 | 0.16937 | 0.14648 | 0.14648 | 0.068665 | 0.068665 | 0.64545 | 121.7834 | 0.091553 | -0.022888 | 122.0581 | 0.073243 | 122.0993 | 0.15106 | -122.0947 | -122.0581 | 121.8246 | 0.054931 | 21.2219 | 0.064086
3307.0625 | 122.0856 | -0.073242 | 121.962 | -0.012131 | 0.0016192 | 0.053854 | 0.051733 | 0.0025079 | -0.0092028 | 0.0021042 | -0.0084228 | 0.020608 | 0.046053 | -0.018055 | 0.014471 | 0.023323 | -0.0014891 | 21.1624 | 121.907 | -0.036621 | 121.7789 | 0.65918 | 0.018311 | 0.07782 | 0.059509 | -0.036621 | -0.009155 | 0.018311 | 0.10071 | 0.091553 | 0.091553 | 0.036621 | -0.054932 | -0.1831 | 0.73242 | 0.15106 | 0.091553 | 0.11444 | 0.054932 | 0.064087 | -121.9986 | -121.9437 | 0.17395 | 0.16479 | 0.16479 | 0.10071 | 0.10071 | 0.6958 | 121.8155 | 0.10986 | 0.027466 | 121.9437 | -0.027466 | 121.9803 | 0.036621 | -121.9986 | -121.9711 | 121.8521 | 0.091553 | 21.2357 | 0.13275
3308.8438 | 122.1176 | -0.064087 | 121.9437 | -0.01976 | 0.001192 | 0.053427 | 0.050665 | -0.0021919 | -0.0094164 | -0.0021682 | -0.0023192 | 0.021463 | 0.04648 | -0.015278 | 0.015966 | 0.025673 | -0.0057615 | 21.2769 | 121.9208 | -0.045776 | 121.8246 | 0.73242 | 0.09613 | 0.1236 | 0.10986 | -0.027466 | 0 | 0.041199 | 0.16937 | 0.13733 | 0.13733 | 0.018311 | -0.022889 | -0.11902 | 0.79651 | 0.18768 | 0.16022 | 0.16937 | 0.14191 | 0.064087 | -121.9711 | -121.9025 | 0.23346 | 0.20142 | 0.20142 | 0.13733 | 0.13733 | 0.7782 | 121.8704 | 0.16937 | 0.041199 | 121.9666 | -0.027466 | 121.9849 | 0.036621 | -121.9894 | -121.9437 | 121.8887 | 0.10529 | 21.3409 | 0.17395
3310.5312 | 122.1359 | -0.045776 | 121.9345 | -0.01976 | 0.0054644 | 0.053854 | 0.052801 | 0.0018671 | -0.0074938 | -0.001741 | -0.005371 | 0.021463 | 0.045412 | -0.011006 | 0.017675 | 0.025887 | -0.0029843 | 21.3547 | 121.9391 | -0.045776 | 121.8109 | 0.70496 | 0.064087 | 0.12817 | 0.11444 | -0.036621 | -0.009155 | 0.073242 | 0.16022 | 0.14648 | 0.15106 | 0 | 0.004578 | -0.1236 | 0.75073 | 0.17395 | 0.10986 | 0.17395 | 0.10986 | 0.036621 | -121.9711 | -121.8613 | 0.20599 | 0.19684 | 0.19226 | 0.16022 | 0.15564 | 0.75073 | 121.8567 | 0.16937 | 0.082397 | 121.9849 | -0.027466 | 121.9849 | 0.009155 | -121.9803 | -121.9437 | 121.8567 | 0.11902 | 21.4005 | 0.16022
3312.2969 | 122.0306 | -0.086975 | 121.9391 | -0.012131 | 0.0041828 | 0.054282 | 0.052588 | 0.0031487 | -0.010271 | -0.001741 | -0.005371 | 0.024881 | 0.04883 | -0.013783 | 0.015752 | 0.023964 | -0.0031979 | 21.3776 | 121.962 | -0.082397 | 121.7514 | 0.63629 | -0.004578 | 0.032043 | 0.004578 | 0.004578 | -0.032043 | -0.013733 | 0.064087 | 0.022888 | 0.054932 | 0.004578 | 0.022888 | -0.18768 | 0.72327 | 0.11902 | 0.082397 | 0.11444 | 0.077819 | 0.054932 | -121.9345 | -121.9528 | 0.15106 | 0.14191 | 0.10986 | 0.086975 | 0.054931 | 0.71869 | 121.8338 | 0.09613 | 0.01831 | 122.0444 | 0.036621 | 122.0489 | 0.091553 | -122.0215 | -121.9711 | 121.8384 | 0.073242 | 21.4645 | 0.091553
3314 | 122.0627 | -0.073242 | 121.9666 | -0.012131 | 0.0050372 | 0.052573 | 0.050451 | 0.00079894 | -0.0092028 | -0.0028092 | -0.0084228 | 0.020822 | 0.047548 | -0.019124 | 0.015325 | 0.0261 | -0.0064023 | 21.4096 | 121.9482 | -0.045776 | 121.7468 | 0.68207 | 0.022888 | 0.10071 | 0.032043 | -0.036621 | -0.022888 | 0.009155 | 0.11902 | 0.082397 | 0.09613 | 0.027466 | -0.018311 | -0.21973 | 0.75531 | 0.17395 | 0.09613 | 0.14648 | 0.068664 | 0.050354 | -122.0032 | -121.9574 | 0.19226 | 0.16937 | 0.15564 | 0.11902 | 0.10528 | 0.72784 | 121.7926 | 0.14191 | 0.032043 | 121.994 | -0.013733 | 122.0215 | 0.036621 | -122.0123 | -121.9894 | 121.8201 | 0.082397 | 21.4828 | 0.10529
3315.7656 | 122.1313 | -0.041199 | 121.9345 | -0.012131 | 0.0043964 | 0.056845 | 0.051947 | -0.0028327 | -0.0079212 | 0.0012496 | -0.005371 | 0.021676 | 0.04648 | -0.014851 | 0.016393 | 0.023964 | -0.0044797 | 21.5286 | 121.9437 | -0.045776 | 121.8018 | 0.72327 | 0.07782 | 0.10986 | 0.10986 | -0.032043 | -0.004578 | 0.082397 | 0.17395 | 0.12817 | 0.14648 | -0.004577 | 0.009156 | -0.13275 | 0.76447 | 0.15106 | 0.11902 | 0.15564 | 0.1236 | 0.036621 | -121.9666 | -121.8521 | 0.21515 | 0.18768 | 0.16937 | 0.15106 | 0.13275 | 0.76904 | 121.8475 | 0.17853 | 0.086975 | 121.9894 | -0.027465 | 121.9849 | 0.009156 | -121.9803 | -121.9391 | 121.843 | 0.1236 | 21.5698 | 0.15106
3317.4844 | 121.9894 | -0.091553 | 121.9757 | -0.0045011 | 0.0048236 | 0.054068 | 0.052374 | 0.00015814 | -0.0089892 | -0.002382 | -0.0084228 | 0.022744 | 0.044985 | -0.012074 | 0.017675 | 0.023537 | -0.0057615 | 21.5103 | 121.9574 | -0.07782 | 121.6965 | 0.58594 | -0.073242 | -0.018311 | -0.082397 | 0 | -0.036621 | -0.059509 | -0.009155 | -0.022888 | 0.013733 | 0.013733 | -0.018311 | -0.27924 | 0.67749 | 0.073242 | 0.018311 | 0.059509 | 0.004578 | 0.054932 | -121.9757 | -122.0352 | 0.082398 | 0.10529 | 0.068665 | 0.050354 | 0.013733 | 0.66376 | 121.7743 | 0.027466 | -0.022888 | 122.0352 | 0.036621 | 122.049 | 0.091553 | -122.0535 | -122.0123 | 121.788 | 0.032044 | 21.6019 | 0.009156
3319.25 | 122.1085 | -0.082397 | 121.9437 | -0.01976 | 0.00076478 | 0.052786 | 0.051092 | -0.0047553 | -0.0081348 | -0.0036636 | -0.0023192 | 0.020822 | 0.047335 | -0.01421 | 0.012975 | 0.024391 | -0.0019163 | 21.5698 | 121.9345 | -0.082397 | 121.756 | 0.68207 | 0.032043 | 0.09613 | 0.032043 | -0.022888 | -0.022888 | 0.022888 | 0.12817 | 0.11902 | 0.10529 | 0 | -0.009156 | -0.18768 | 0.76446 | 0.17853 | 0.11444 | 0.17853 | 0.11444 | 0.059509 | -121.9666 | -121.9208 | 0.21057 | 0.18768 | 0.20142 | 0.12817 | 0.14191 | 0.76446 | 121.8384 | 0.15106 | 0.045776 | 122.0169 | 0 | 122.0169 | 0.059509 | -122.0261 | -121.9666 | 121.8384 | 0.10528 | 21.6522 | 0.11444
3320.9531 | 122.0718 | -0.10071 | 121.9482 | 0.0031279 | 0.0052508 | 0.053 | 0.053015 | 0.0029351 | -0.006853 | -0.0008866 | -0.0084228 | 0.023172 | 0.049685 | -0.019337 | 0.014898 | 0.027809 | -0.0055479 | 21.5881 | 121.9666 | -0.086975 | 121.6919 | 0.61798 | -0.050354 | -0.013733 | -0.013733 | -0.004578 | -0.045776 | 0.004578 | 0.068665 | 0.041199 | 0.07782 | 0.013733 | 0.018311 | -0.25635 | 0.71869 | 0.086975 | 0.050354 | 0.073242 | 0.036621 | 0.054932 | -121.9528 | -121.9437 | 0.16937 | 0.17853 | 0.14191 | 0.1236 | 0.086975 | 0.70496 | 121.7789 | 0.11444 | 0.050354 | 122.0535 | 0.041198 | 122.0673 | 0.09613 | -122.0352 | -121.994 | 121.7926 | 0.10529 | 21.6888 | 0.086975
3322.7188 | 122.081 | -0.073242 | 121.9437 | -0.012131 | 0.00076478 | 0.053641 | 0.049811 | -0.0019781 | -0.0074938 | -0.0025956 | -0.0023192 | 0.020608 | 0.045626 | -0.012929 | 0.01618 | 0.026314 | -0.0066159 | 21.6568 | 121.9162 | -0.032043 | 121.8109 | 0.75531 | 0.091553 | 0.12817 | 0.068665 | -0.018311 | -0.022888 | 0.013733 | 0.13733 | 0.11902 | 0.10071 | 0.041199 | -0.027466 | -0.13275 | 0.82855 | 0.20142 | 0.16479 | 0.16022 | 0.1236 | 0.050354 | -121.962 | -121.9299 | 0.21057 | 0.17395 | 0.19226 | 0.1236 | 0.14191 | 0.78735 | 121.843 | 0.16022 | 0.036621 | 121.9482 | 0.004577 | 121.9894 | 0.054931 | -121.9757 | -121.9666 | 121.8842 | 0.086975 | 21.73 | 0.14191
3324.4844 | 122.0947 | -0.07782 | 121.9391 | -0.0045011 | 0.0052508 | 0.056845 | 0.051733 | 0.00015814 | -0.0070666 | -0.000673 | -0.005371 | 0.020608 | 0.049471 | -0.013783 | 0.016821 | 0.024178 | -0.0012753 | 21.6568 | 121.9803 | -0.073242 | 121.7285 | 0.67291 | -0.009155 | 0.032043 | 0.032043 | -0.013733 | -0.032043 | 0.045776 | 0.1236 | 0.091553 | 0.13275 | 0.004578 | 0.041199 | -0.21057 | 0.75073 | 0.10986 | 0.068665 | 0.10529 | 0.064087 | 0.045777 | -121.9528 | -121.8933 | 0.20142 | 0.21057 | 0.16937 | 0.16479 | 0.1236 | 0.74616 | 121.8018 | 0.15564 | 0.077819 | 122.0535 | 0.01831 | 122.0581 | 0.064087 | -122.0123 | -121.9711 | 121.8063 | 0.1236 | 21.7346 | 0.10986
3326.1875 | 122.0123 | -0.086975 | 121.9757 | 0.0031279 | 0.006319 | 0.054495 | 0.053015 | -0.00048286 | -0.006853 | -0.0004592 | -0.005371 | 0.025308 | 0.047335 | -0.012288 | 0.016607 | 0.024391 | -0.0070433 | 21.7712 | 121.9666 | -0.073242 | 121.7422 | 0.69122 | 0.013733 | 0.041199 | 0.027466 | -0.004578 | -0.032043 | -0.018311 | 0.073242 | 0.041199 | 0.073242 | 0.013733 | -0.009155 | -0.23346 | 0.7782 | 0.12817 | 0.10071 | 0.11444 | 0.086975 | 0.054932 | -121.9803 | -121.994 | 0.16022 | 0.16022 | 0.12817 | 0.10529 | 0.073242 | 0.76447 | 121.8155 | 0.10529 | 0.013732 | 122.0398 | 0.027465 | 122.0535 | 0.082397 | -122.0489 | -122.0078 | 121.8292 | 0.068664 | 21.8582 | 0.11444
3327.9688 | 121.9986 | -0.11902 | 121.9894 | -0.012131 | 0.0016192 | 0.05065 | 0.049597 | 0.00037174 | -0.008562 | -0.0028092 | -0.005371 | 0.022317 | 0.047548 | -0.0065197 | 0.014257 | 0.024819 | -0.0025571 | 21.7804 | 121.9482 | -0.091553 | 121.6873 | 0.63629 | -0.013733 | 0.004578 | -0.068665 | 0.013733 | -0.041199 | -0.068665 | 0.045776 | 0.022888 | 0.032043 | 0.027466 | -0.041199 | -0.30212 | 0.75531 | 0.1236 | 0.10529 | 0.096131 | 0.07782 | 0.07782 | -121.9757 | -122.0581 | 0.16479 | 0.15106 | 0.14191 | 0.073242 | 0.064087 | 0.72784 | 121.7789 | 0.086975 | -0.027466 | 122.0398 | 0.054932 | 122.0673 | 0.13275 | -122.081 | -122.0306 | 121.8063 | 0.050354 | 21.8994 | 0.050354
3329.7344 | 122.0123 | -0.10529 | 121.9757 | -0.0045011 | 0.0050372 | 0.053641 | 0.052588 | -0.0026191 | -0.0062122 | 0.0001816 | -0.005371 | 0.022958 | 0.049044 | -0.012074 | 0.016393 | 0.024178 | -0.0027707 | 21.8719 | 122.0032 | -0.091553 | 121.669 | 0.62714 | -0.064087 | -0.018311 | -0.050354 | 0.009155 | -0.022888 | -0.054932 | 0.013733 | 0.004578 | 0.036621 | 0.013733 | 0.027466 | -0.3067 | 0.73242 | 0.086975 | 0.041199 | 0.073242 | 0.027466 | 0.082398 | -121.9666 | -122.0306 | 0.11902 | 0.14191 | 0.10986 | 0.059509 | 0.027466 | 0.71869 | 121.7606 | 0.036621 | -0.032044 | 122.0947 | 0.032043 | 122.1085 | 0.11444 | -122.0673 | -121.9986 | 121.7743 | 0.050354 | 21.9772 | 0.054932
3331.4375 | 121.9986 | -0.10071 | 121.9803 | -0.012131 | 0.0069598 | 0.053854 | 0.052374 | -0.00069646 | -0.0066394 | -0.0011002 | -0.0023192 | 0.022103 | 0.048403 | -0.015065 | 0.01618 | 0.023537 | -0.0053343 | 21.9452 | 121.9803 | -0.091553 | 121.6965 | 0.69122 | -0.032043 | 0.004578 | -0.022888 | 0.004578 | -0.022888 | -0.036621 | 0.032043 | -0.013733 | 0.041199 | 0.009155 | 0 | -0.28381 | 0.79193 | 0.10529 | 0.068665 | 0.096131 | 0.05951 | 0.07782 | -121.9757 | -122.0169 | 0.13275 | 0.14191 | 0.086975 | 0.064087 | 0.009155 | 0.78278 | 121.788 | 0.054931 | -0.013733 | 122.0718 | 0.027466 | 122.081 | 0.10529 | -122.0718 | -122.0032 | 121.7972 | 0.064087 | 22.0459 | 0.07782
3333.2031 | 122.0718 | -0.082397 | 121.9574 | -0.01976 | 0.0016192 | 0.054282 | 0.050665 | 0.0014397 | -0.010271 | -0.00345 | -0.0023192 | 0.019754 | 0.047762 | -0.01122 | 0.016393 | 0.024819 | -0.0061887 | 22.0093 | 121.9254 | -0.045776 | 121.7926 | 0.80566 | 0.091553 | 0.13733 | 0.064087 | -0.013733 | -0.013733 | -0.004578 | 0.1236 | 0.10986 | 0.091553 | 0.036621 | -0.032043 | -0.16479 | 0.88806 | 0.21973 | 0.17395 | 0.18311 | 0.13733 | 0.068664 | -121.9711 | -121.962 | 0.20599 | 0.17395 | 0.19226 | 0.10529 | 0.1236 | 0.85144 | 121.8384 | 0.13733 | 0.009155 | 121.9711 | 0 | 122.0078 | 0.068664 | -122.0032 | -121.9711 | 121.875 | 0.077819 | 22.0917 | 0.14648
3334.9688 | 121.9986 | -0.1236 | 121.9986 | -0.012131 | 0.001833 | 0.050223 | 0.051092 | -0.0011237 | -0.0070666 | -0.0013138 | -0.005371 | 0.023599 | 0.049257 | -0.01891 | 0.014684 | 0.02546 | -0.0014891 | 21.9955 | 121.9849 | -0.07782 | 121.7056 | 0.67749 | -0.027466 | 0.032043 | -0.041199 | 0.013733 | -0.050354 | -0.086975 | 0.059509 | 0.022888 | 0.022888 | 0.045776 | -0.013733 | -0.29297 | 0.80109 | 0.15564 | 0.09613 | 0.10986 | 0.050354 | 0.073242 | -121.9849 | -122.0856 | 0.1831 | 0.14648 | 0.14648 | 0.073242 | 0.073242 | 0.75531 | 121.7834 | 0.10986 | -0.036621 | 122.0627 | 0.064087 | 122.1085 | 0.13733 | -122.0764 | -122.049 | 121.8292 | 0.036621 | 22.1191 | 0.082397
3336.75 | 122.113 | -0.082397 | 121.9528 | -0.0045011 | 0.0014056 | 0.050436 | 0.049597 | -0.0041145 | -0.0098438 | -0.0043046 | -0.005371 | 0.018472 | 0.046694 | -0.020192 | 0.014898 | 0.025246 | -0.0019163 | 22.1146 | 121.9299 | -0.045776 | 121.8018 | 0.8194 | 0.11902 | 0.13733 | 0.073242 | -0.022888 | -0.009155 | 0.027466 | 0.14648 | 0.12817 | 0.10986 | 0.036621 | -0.022888 | -0.15106 | 0.90179 | 0.21973 | 0.20142 | 0.18311 | 0.16479 | 0.073242 | -121.9757 | -121.9254 | 0.22888 | 0.19226 | 0.21057 | 0.11902 | 0.13733 | 0.86517 | 121.8475 | 0.15564 | 0.036621 | 121.9757 | -0.013733 | 122.0123 | 0.059509 | -121.9986 | -121.962 | 121.8842 | 0.10986 | 22.197 | 0.15564
3338.4688 | 122.049 | -0.09613 | 121.9528 | -0.012131 | 0.0031146 | 0.052359 | 0.051092 | 0.0040033 | -0.0092028 | -0.002382 | -0.0084228 | 0.022103 | 0.047976 | -0.0086559 | 0.015539 | 0.023323 | -0.0046933 | 22.1191 | 121.9711 | -0.091553 | 121.7422 | 0.73242 | 0.027466 | 0.045776 | 0.013733 | 0 | -0.022888 | -0.009155 | 0.086975 | 0.064087 | 0.086975 | 0.004577 | 0.01831 | -0.21057 | 0.82855 | 0.14191 | 0.1236 | 0.13733 | 0.11902 | 0.073242 | -121.9528 | -121.962 | 0.1831 | 0.1831 | 0.16022 | 0.10986 | 0.086975 | 0.82398 | 121.8338 | 0.10986 | 0.013733 | 122.0627 | 0.022888 | 122.0673 | 0.09613 | -122.0444 | -121.9757 | 121.8384 | 0.086975 | 22.2153 | 0.10986
3340.2344 | 122.1222 | -0.045776 | 121.9254 | -0.01976 | 0.0035418 | 0.056845 | 0.049597 | 0.0031487 | -0.0072802 | -0.002382 | -0.0023192 | 0.022531 | 0.046267 | -0.012929 | 0.015966 | 0.026528 | -0.0087521 | 22.1741 | 121.9391 | -0.050354 | 121.7972 | 0.83313 | 0.073242 | 0.12817 | 0.086975 | -0.022888 | -0.009155 | 0.068665 | 0.16022 | 0.11902 | 0.16479 | -0.004578 | 0.013733 | -0.12817 | 0.87891 | 0.17395 | 0.11902 | 0.17853 | 0.1236 | 0.036621 | -121.9482 | -121.8567 | 0.20599 | 0.21057 | 0.16479 | 0.17395 | 0.12817 | 0.88348 | 121.8475 | 0.16937 | 0.07782 | 121.9894 | -0.013733 | 121.9849 | 0.022888 | -121.9757 | -121.9345 | 121.843 | 0.11444 | 22.2198 | 0.13275
3341.9844 | 122.0993 | -0.064087 | 121.9574 | -0.012131 | 0.0020466 | 0.053 | 0.048529 | -0.0041145 | -0.0079212 | -0.0019546 | -0.005371 | 0.021463 | 0.048189 | -0.021687 | 0.014471 | 0.024391 | 0.0021425 | 22.1512 | 121.9574 | -0.054932 | 121.7514 | 0.7782 | 0.050354 | 0.10071 | 0.022888 | -0.022888 | -0.018311 | 0.027466 | 0.11902 | 0.11902 | 0.11444 | 0.009155 | 0 | -0.20599 | 0.84228 | 0.1648 | 0.11444 | 0.15564 | 0.10529 | 0.045776 | -121.9803 | -121.9299 | 0.18311 | 0.17853 | 0.18311 | 0.13275 | 0.13733 | 0.83313 | 121.8063 | 0.13733 | 0.045777 | 122.0123 | -0.004577 | 122.0215 | 0.041199 | -122.0123 | -121.9757 | 121.8155 | 0.091553 | 22.2153 | 0.086975
3343.75 | 121.962 | -0.11902 | 121.9986 | -0.0045011 | 0.0043964 | 0.054495 | 0.05451 | -5.5462e-05 | -0.0083484 | -0.0015274 | -0.0084228 | 0.022103 | 0.049257 | -0.016347 | 0.01618 | 0.024605 | -0.0072569 | 22.1741 | 121.9894 | -0.091553 | 121.6736 | 0.66834 | -0.073242 | -0.013733 | -0.082397 | 0.009155 | -0.059509 | -0.064087 | 0.013733 | -0.013733 | 0.041199 | 0.027466 | -0.009155 | -0.32501 | 0.78735 | 0.10529 | 0.045777 | 0.07782 | 0.018311 | 0.05951 | -121.9894 | -122.0627 | 0.13275 | 0.16022 | 0.10529 | 0.10071 | 0.045776 | 0.75989 | 121.7651 | 0.073242 | -0.004578 | 122.081 | 0.068664 | 122.1085 | 0.12817 | -122.0901 | -122.0581 | 121.7926 | 0.054932 | 22.2931 | 0.036622
3345.5 | 122.0673 | -0.068665 | 121.9666 | -0.012131 | 0.0043964 | 0.052786 | 0.048956 | 0.0016535 | -0.0055712 | -0.0025956 | -0.005371 | 0.020181 | 0.047548 | -0.016133 | 0.012121 | 0.023751 | -0.0010617 | 22.229 | 121.9482 | -0.054932 | 121.7514 | 0.78735 | 0.036621 | 0.10071 | 0.009155 | -0.013733 | -0.018311 | -0.013733 | 0.091553 | 0.07782 | 0.086975 | 0.013733 | -0.018311 | -0.21515 | 0.85602 | 0.16937 | 0.10529 | 0.15564 | 0.091553 | 0.050354 | -121.9803 | -121.9803 | 0.16022 | 0.15564 | 0.14649 | 0.10529 | 0.096131 | 0.84229 | 121.8063 | 0.10986 | 0.004578 | 122.0032 | 0.004578 | 122.0169 | 0.054932 | -122.0215 | -121.9849 | 121.8201 | 0.054932 | 22.2977 | 0.07782
3347.2656 | 121.9894 | -0.10986 | 121.9757 | -0.012131 | 0.0067462 | 0.054709 | 0.053228 | 0.0063531 | -0.0083484 | 0.0006088 | -0.005371 | 0.021249 | 0.04648 | -0.013142 | 0.016393 | 0.024391 | -0.0025571 | 22.2519 | 121.9666 | -0.086975 | 121.6873 | 0.6546 | -0.064087 | -0.013733 | -0.10529 | 0.013733 | -0.054932 | -0.059509 | -0.004578 | -0.018311 | 0.027466 | 0.022888 | -0.009155 | -0.28839 | 0.76447 | 0.09613 | 0.045776 | 0.073242 | 0.022888 | 0.054931 | -121.962 | -122.0352 | 0.10529 | 0.13733 | 0.091552 | 0.082398 | 0.036621 | 0.74158 | 121.7743 | 0.050354 | -0.004577 | 122.0535 | 0.068665 | 122.0764 | 0.1236 | -122.0627 | -122.0306 | 121.7972 | 0.050354 | 22.3618 | 0.004577
3349.0312 | 121.994 | -0.10986 | 121.9803 | -0.012131 | 0.0050372 | 0.053641 | 0.054083 | 0.0020807 | -0.008562 | 0.0003952 | -0.005371 | 0.022531 | 0.046267 | -0.014638 | 0.017034 | 0.024819 | -0.0025571 | 22.2931 | 121.9986 | -0.082397 | 121.6644 | 0.68207 | -0.07782 | -0.013733 | -0.086975 | 0 | -0.050354 | -0.054932 | 0.004578 | -0.036621 | 0.045776 | 0.027466 | 0.01831 | -0.31586 | 0.79193 | 0.09613 | 0.032043 | 0.068664 | 0.004577 | 0.059509 | -121.9803 | -122.0352 | 0.11444 | 0.15564 | 0.073242 | 0.09613 | 0.013733 | 0.76446 | 121.7468 | 0.054932 | -0.004578 | 122.081 | 0.050354 | 122.1085 | 0.10986 | -122.0627 | -122.0306 | 121.7743 | 0.054931 | 22.403 | 0.022888
3350.7344 | 122.0078 | -0.09613 | 121.994 | -0.012131 | 0.001192 | 0.051932 | 0.051092 | -0.0028327 | -0.0089892 | -0.000673 | -0.0084228 | 0.024026 | 0.047762 | -0.012929 | 0.017248 | 0.026314 | -0.0064023 | 22.3251 | 121.9849 | -0.091553 | 121.6827 | 0.74158 | -0.004578 | 0.009155 | -0.082397 | 0.009155 | -0.054932 | -0.068665 | 0.032043 | 0.013733 | 0.027466 | 0.004577 | -0.009156 | -0.31128 | 0.83771 | 0.10528 | 0.091552 | 0.10071 | 0.086975 | 0.041198 | -121.9849 | -122.0627 | 0.12817 | 0.1236 | 0.10986 | 0.082398 | 0.068665 | 0.83313 | 121.7743 | 0.086975 | -0.013733 | 122.0764 | 0.064087 | 122.081 | 0.10528 | -122.0856 | -122.049 | 121.7789 | 0.027465 | 22.4213 | 0.013733
3352.5 | 122.0398 | -0.10071 | 121.9666 | -0.012131 | 0.0052508 | 0.054068 | 0.050238 | 0.00037174 | -0.0066394 | -0.0015274 | -0.0023192 | 0.022958 | 0.047121 | -0.012715 | 0.015752 | 0.02546 | -0.0027707 | 22.4396 | 121.9666 | -0.07782 | 121.7331 | 0.79193 | 0.032043 | 0.07782 | 0.022888 | 0.022888 | -0.027466 | 0 | 0.10071 | 0.07782 | 0.082397 | 0.022888 | 0 | -0.23346 | 0.89264 | 0.17853 | 0.13275 | 0.15564 | 0.10986 | 0.073242 | -121.9437 | -121.9666 | 0.20142 | 0.18311 | 0.17853 | 0.10986 | 0.10529 | 0.86975 | 121.8109 | 0.12817 | 0.027466 | 122.0444 | 0.050354 | 122.0673 | 0.1236 | -122.0444 | -121.994 | 121.8338 | 0.10071 | 22.5403 | 0.1236
3354.2812 | 122.0123 | -0.1236 | 122.0261 | -0.0045011 | 0.0022602 | 0.050009 | 0.052588 | -0.0021919 | -0.0089892 | -0.0028092 | -0.005371 | 0.022103 | 0.047762 | -0.016774 | 0.01618 | 0.023964 | -0.0034117 | 22.4167 | 121.9803 | -0.10071 | 121.6599 | 0.75531 | -0.009155 | 0.022888 | -0.059509 | 0.013733 | -0.045776 | -0.073242 | 0.022888 | 0.013733 | 0.018311 | 0.022888 | -0.045776 | -0.36621 | 0.87891 | 0.14648 | 0.11444 | 0.1236 | 0.091553 | 0.07782 | -122.0123 | -122.0993 | 0.14648 | 0.14191 | 0.13733 | 0.064087 | 0.059509 | 0.85602 | 121.7606 | 0.068664 | -0.027466 | 122.081 | 0.059509 | 122.1039 | 0.13733 | -122.1268 | -122.0718 | 121.7834 | 0.050354 | 22.5403 | 0.064087
3356.0469 | 121.994 | -0.10986 | 121.9849 | -0.012131 | 0.0050372 | 0.053641 | 0.052801 | 0.0033623 | -0.0062122 | -0.0019546 | -0.011475 | 0.02189 | 0.048616 | -0.019337 | 0.015966 | 0.025673 | -0.0029843 | 22.4213 | 121.9894 | -0.086975 | 121.6644 | 0.71869 | -0.045776 | -0.009155 | -0.073242 | 0.018311 | -0.032043 | -0.059509 | 0.018311 | -0.022888 | 0.032043 | 0.022888 | 0.004578 | -0.32043 | 0.82855 | 0.10071 | 0.064087 | 0.07782 | 0.041199 | 0.07782 | -121.9666 | -122.0444 | 0.12817 | 0.14191 | 0.086975 | 0.064086 | 0.009155 | 0.80566 | 121.7514 | 0.050354 | -0.027466 | 122.0764 | 0.050354 | 122.0993 | 0.12817 | -122.0718 | -122.0169 | 121.7743 | 0.050354 | 22.5311 | 0.036621
3357.75 | 122.0261 | -0.086975 | 122.0032 | -0.01976 | 0.001833 | 0.053641 | 0.051947 | 0.0042169 | -0.00963 | -0.0021682 | -0.0023192 | 0.023599 | 0.046053 | -0.013997 | 0.014898 | 0.023751 | 0.0015017 | 22.4213 | 121.9574 | -0.086975 | 121.6827 | 0.75531 | 0 | 0.027466 | -0.073242 | 0.009155 | -0.054932 | -0.054932 | 0.045776 | 0.022888 | 0.027466 | 0 | -0.045777 | -0.32044 | 0.84229 | 0.11444 | 0.086975 | 0.11444 | 0.086975 | 0.032043 | -121.994 | -122.0581 | 0.13275 | 0.11444 | 0.10986 | 0.082398 | 0.07782 | 0.84229 | 121.7697 | 0.10071 | 0 | 122.0444 | 0.064087 | 122.0444 | 0.09613 | -122.0901 | -122.0581 | 121.7697 | 0.032043 | 22.5082 | 0.013733
3359.5156 | 122.0856 | -0.068665 | 121.9757 | -0.0045011 | 0.0020466 | 0.053854 | 0.050024 | -0.0017645 | -0.0083484 | -0.0004592 | -0.0084228 | 0.018686 | 0.045198 | -0.021687 | 0.015966 | 0.026741 | -0.00063445 | 22.5174 | 121.9437 | -0.054932 | 121.8109 | 0.91553 | 0.1236 | 0.16479 | 0.073242 | -0.013733 | -0.009155 | 0.018311 | 0.15564 | 0.13733 | 0.11902 | 0.013733 | -0.032043 | -0.16479 | 0.98419 | 0.23346 | 0.19226 | 0.21973 | 0.17853 | 0.05951 | -121.9894 | -121.9574 | 0.22431 | 0.18768 | 0.20599 | 0.12817 | 0.14648 | 0.97046 | 121.8658 | 0.16479 | 0.027466 | 121.9986 | -0.004578 | 122.0123 | 0.054932 | -122.0306 | -121.9849 | 121.8796 | 0.086976 | 22.5861 | 0.14191
3361.2188 | 122.113 | -0.054932 | 121.9482 | -0.012131 | 0.0022602 | 0.051932 | 0.050451 | -0.0019781 | -0.0074938 | -0.0011002 | -0.005371 | 0.019967 | 0.046053 | -0.022755 | 0.012762 | 0.025673 | -0.0012753 | 22.4625 | 121.9482 | -0.050354 | 121.7468 | 0.85144 | 0.07782 | 0.11444 | 0.032043 | -0.032043 | 0.004578 | 0.009155 | 0.13733 | 0.11902 | 0.11444 | 0.004578 | 0 | -0.20142 | 0.90637 | 0.16937 | 0.13275 | 0.16479 | 0.12817 | 0.05951 | -121.9803 | -121.9391 | 0.19226 | 0.16937 | 0.17395 | 0.10986 | 0.11444 | 0.90179 | 121.7972 | 0.13275 | 0.004577 | 121.9986 | -0.036621 | 122.0032 | 0.022889 | -121.9986 | -121.9437 | 121.8018 | 0.064087 | 22.5174 | 0.086975
3362.9844 | 122.0215 | -0.07782 | 121.9437 | -0.0045011 | 0.00097838 | 0.054282 | 0.050024 | -0.0026191 | -0.0081348 | -0.0021682 | -0.005371 | 0.021249 | 0.044344 | -0.012715 | 0.014043 | 0.025032 | -0.0027707 | 22.5403 | 121.9437 | -0.045776 | 121.7697 | 0.87891 | 0.10071 | 0.13275 | 0.018311 | -0.018311 | -0.013733 | -0.041199 | 0.082397 | 0.050354 | 0.045776 | 0.032044 | 0 | -0.17395 | 0.95673 | 0.21057 | 0.17853 | 0.17853 | 0.14648 | 0.064087 | -121.962 | -121.9849 | 0.16022 | 0.1236 | 0.12817 | 0.059509 | 0.064087 | 0.92468 | 121.8155 | 0.09613 | -0.027466 | 121.9894 | -0.004578 | 122.0215 | 0.059509 | -121.9894 | -121.9574 | 121.8475 | 0.036621 | 22.6181 | 0.096131
3364.6875 | 122.0352 | -0.10986 | 121.994 | -0.0045011 | 0.00097838 | 0.051505 | 0.052588 | 0.0063531 | -0.010912 | -0.0019546 | -0.005371 | 0.023172 | 0.046267 | -0.017842 | 0.01383 | 0.024605 | -0.0027707 | 22.4945 | 121.9757 | -0.082397 | 121.6919 | 0.77362 | 0 | 0.027466 | -0.073242 | 0.009155 | -0.036621 | -0.068665 | 0.036621 | 0.022888 | 0.045776 | 0.027466 | -0.018311 | -0.30212 | 0.88348 | 0.13733 | 0.10986 | 0.10986 | 0.082397 | 0.073242 | -121.9849 | -122.0627 | 0.14648 | 0.15564 | 0.13275 | 0.082397 | 0.059509 | 0.85602 | 121.7743 | 0.073242 | -0.032044 | 122.0581 | 0.045776 | 122.0856 | 0.11902 | -122.0764 | -122.0306 | 121.8018 | 0.041198 | 22.6044 | 0.036621
3366.4531 | 122.1222 | -0.059509 | 121.9391 | -0.012131 | 0.0069598 | 0.054282 | 0.052588 | -0.0026191 | -0.0066394 | -0.0011002 | -0.005371 | 0.020181 | 0.046267 | -0.014851 | 0.016607 | 0.024819 | -0.0031979 | 22.522 | 121.9666 | -0.059509 | 121.7651 | 0.87891 | 0.050354 | 0.10986 | 0.073242 | -0.022888 | -0.041199 | 0.050354 | 0.13275 | 0.10529 | 0.13733 | 0 | 0.027466 | -0.17395 | 0.93841 | 0.16937 | 0.10986 | 0.16937 | 0.10986 | 0.01831 | -121.962 | -121.8887 | 0.19226 | 0.19684 | 0.16479 | 0.17853 | 0.14649 | 0.93841 | 121.8246 | 0.17395 | 0.091553 | 122.0261 | 0.018311 | 122.0261 | 0.036621 | -121.9986 | -121.9803 | 121.8246 | 0.10986 | 22.5815 | 0.13275
3368.2344 | 122.049 | -0.091553 | 121.9849 | -0.0045011 | 0.0052508 | 0.052786 | 0.051947 | -0.00069646 | -0.01198 | -0.0030228 | -0.005371 | 0.021035 | 0.046694 | -0.010365 | 0.014684 | 0.024819 | -0.0034117 | 22.5586 | 121.9803 | -0.07782 | 121.7102 | 0.80109 | 0.032043 | 0.050354 | -0.050354 | 0.013733 | -0.036621 | -0.032043 | 0.054932 | 0.032043 | 0.068665 | 0.013733 | -0.004577 | -0.27466 | 0.89264 | 0.14191 | 0.1236 | 0.12817 | 0.10986 | 0.054932 | -121.9711 | -122.0169 | 0.14649 | 0.16022 | 0.1236 | 0.10529 | 0.068664 | 0.87891 | 121.788 | 0.091553 | 0.004578 | 122.0581 | 0.050354 | 122.0718 | 0.10529 | -122.0627 | -122.0215 | 121.8018 | 0.05951 | 22.6501 | 0.041199
3369.9375 | 121.994 | -0.11444 | 121.9986 | -0.012131 | 0.0048236 | 0.054922 | 0.051733 | 0.0035761 | -0.0070666 | -0.0013138 | -0.0023192 | 0.021463 | 0.045626 | -0.010365 | 0.016393 | 0.026528 | -0.0057615 | 22.5723 | 121.9803 | -0.07782 | 121.6965 | 0.79651 | -0.018311 | 0.013733 | -0.054932 | 0.009155 | -0.036621 | -0.082397 | 0 | -0.027466 | 0.027466 | 0.036621 | -0.01831 | -0.30212 | 0.91095 | 0.12817 | 0.09613 | 0.091553 | 0.059509 | 0.07782 | -121.9894 | -122.081 | 0.11444 | 0.14191 | 0.086975 | 0.064087 | 0.009155 | 0.87433 | 121.7743 | 0.036621 | -0.045776 | 122.0581 | 0.045776 | 122.0947 | 0.1236 | -122.0764 | -122.0352 | 121.8109 | 0.032044 | 22.6868 | 0.059509
3371.7031 | 122.0444 | -0.09613 | 121.9986 | -0.012131 | 0.0067462 | 0.054495 | 0.050024 | 0.0054987 | -0.0077074 | -0.0013138 | -0.0023192 | 0.023385 | 0.043917 | -0.01421 | 0.015966 | 0.025032 | 0.00086095 | 22.6501 | 121.9711 | -0.07782 | 121.7468 | 0.88806 | 0.050354 | 0.086975 | 0.041199 | 0.009155 | -0.032043 | -0.013733 | 0.082397 | 0.045776 | 0.068665 | 0.01831 | -0.027466 | -0.25177 | 0.98419 | 0.1831 | 0.14648 | 0.16479 | 0.12817 | 0.064087 | -121.9894 | -122.0123 | 0.17853 | 0.16479 | 0.14191 | 0.10071 | 0.077819 | 0.96588 | 121.8246 | 0.11444 | 0.01831 | 122.049 | 0.041198 | 122.0673 | 0.10528 | -122.0764 | -122.0306 | 121.843 | 0.082397 | 22.7463 | 0.13733
3373.4531 | 122.0581 | -0.09613 | 121.994 | -0.01976 | 0.0048236 | 0.054282 | 0.051306 | 0.0020807 | -0.0087756 | -0.0038772 | -0.0084228 | 0.021035 | 0.046907 | -0.012074 | 0.017248 | 0.025032 | -0.0027707 | 22.6593 | 121.9757 | -0.073242 | 121.7239 | 0.89722 | 0.045776 | 0.07782 | 0.032043 | 0.009155 | -0.022888 | 0 | 0.082397 | 0.064087 | 0.07782 | 0.022888 | -0.018311 | -0.27008 | 0.99335 | 0.17395 | 0.14191 | 0.15106 | 0.11902 | 0.073242 | -121.9849 | -121.994 | 0.17853 | 0.17395 | 0.16022 | 0.10071 | 0.086975 | 0.97046 | 121.7972 | 0.10528 | 0.022888 | 122.0489 | 0.032043 | 122.0718 | 0.10528 | -122.0673 | -122.0169 | 121.8201 | 0.09613 | 22.7554 | 0.12817
3375.1562 | 122.1222 | -0.064087 | 121.9482 | -0.012131 | 0.0037556 | 0.055991 | 0.051733 | 0.0063531 | -0.0094164 | -0.0025956 | -0.005371 | 0.021035 | 0.044558 | -0.013783 | 0.014257 | 0.026955 | -0.0061887 | 22.6868 | 121.962 | -0.059509 | 121.7743 | 0.94299 | 0.086975 | 0.1236 | 0.073242 | -0.036621 | -0.018311 | 0.050354 | 0.14191 | 0.11902 | 0.14191 | 0.004578 | 0.013733 | -0.17395 | 1.0071 | 0.18768 | 0.15106 | 0.1831 | 0.14648 | 0.045776 | -121.9849 | -121.8979 | 0.20599 | 0.20599 | 0.18311 | 0.16022 | 0.13733 | 1.0025 | 121.8338 | 0.16022 | 0.068665 | 122.0215 | -0.01831 | 122.0261 | 0.027466 | -122.0078 | -121.9666 | 121.8384 | 0.11444 | 22.7509 | 0.13733
3376.9219 | 122.0856 | -0.073242 | 121.962 | -0.012131 | 0.0037556 | 0.053 | 0.051733 | -0.0019781 | -0.0089892 | -0.000673 | -0.0023192 | 0.021035 | 0.045412 | -0.027882 | 0.014471 | 0.024178 | -0.0027707 | 22.8653 | 121.9299 | -0.041199 | 121.756 | 0.93842 | 0.073242 | 0.13275 | 0.054932 | -0.022888 | -0.018311 | 0 | 0.10529 | 0.10071 | 0.091553 | 0.032043 | -0.032043 | -0.20599 | 1.0117 | 0.20599 | 0.14648 | 0.17395 | 0.11444 | 0.054931 | -121.9849 | -121.962 | 0.17853 | 0.16479 | 0.17395 | 0.10986 | 0.11902 | 0.97962 | 121.7972 | 0.1236 | 0.018311 | 121.9711 | -0.004577 | 122.0032 | 0.050354 | -122.0032 | -121.9803 | 121.8292 | 0.073242 | 22.9385 | 0.12817
3378.6875 | 121.9849 | -0.10529 | 121.9803 | -0.012131 | 0.0058918 | 0.056845 | 0.053228 | -0.00026906 | -0.0092028 | 0.0006088 | -0.005371 | 0.022103 | 0.046053 | -0.017415 | 0.01618 | 0.023964 | -0.00042085 | 22.8836 | 121.9894 | -0.07782 | 121.6782 | 0.82855 | -0.013733 | 0.032043 | -0.082397 | 0.009155 | -0.045776 | -0.082397 | 0.004578 | -0.027466 | 0.022888 | 0.027466 | 0.009155 | -0.30212 | 0.93384 | 0.13733 | 0.091553 | 0.10986 | 0.064087 | 0.05951 | -121.9711 | -122.0627 | 0.10986 | 0.12817 | 0.07782 | 0.068664 | 0.01831 | 0.90637 | 121.756 | 0.050354 | -0.036621 | 122.0673 | 0.054931 | 122.0947 | 0.11444 | -122.0581 | -122.0261 | 121.7834 | 0.022889 | 22.9889 | 0.022889
3380.3906 | 122.1359 | -0.073242 | 121.9299 | -0.012131 | 0.0048236 | 0.053854 | 0.051306 | -0.0017645 | -0.008562 | -0.0021682 | -0.011475 | 0.020181 | 0.046694 | -0.014424 | 0.015539 | 0.024819 | -0.0017027 | 22.9477 | 121.9482 | -0.059509 | 121.7926 | 0.97504 | 0.09613 | 0.14191 | 0.082397 | -0.018311 | -0.013733 | 0.064087 | 0.14191 | 0.13275 | 0.15106 | 0.013733 | 0.01831 | -0.13733 | 1.0483 | 0.21515 | 0.16937 | 0.20142 | 0.15564 | 0.059509 | -121.9482 | -121.8658 | 0.21515 | 0.2243 | 0.20599 | 0.16479 | 0.14648 | 1.0345 | 121.8521 | 0.15564 | 0.07782 | 122.0078 | -0.004578 | 122.0215 | 0.054931 | -121.9894 | -121.9437 | 121.8658 | 0.13733 | 23.0209 | 0.15564
3382.1562 | 122.0764 | -0.073242 | 121.9574 | -0.0045011 | 0.0061054 | 0.054282 | 0.050024 | -0.0017645 | -0.0077074 | -0.0008866 | -0.0084228 | 0.020608 | 0.046267 | -0.012929 | 0.013616 | 0.024178 | -0.0031979 | 22.9431 | 121.9391 | -0.059509 | 121.7377 | 0.96588 | 0.07782 | 0.14191 | 0.036621 | -0.022888 | 0 | 0.009155 | 0.10986 | 0.082397 | 0.09613 | 0.013733 | -0.01831 | -0.21973 | 1.0391 | 0.21515 | 0.15106 | 0.20142 | 0.13733 | 0.073242 | -121.9803 | -121.9482 | 0.18311 | 0.16937 | 0.15564 | 0.09613 | 0.082397 | 1.0254 | 121.7972 | 0.10986 | 0.009155 | 121.9986 | -0.022888 | 122.0123 | 0.050354 | -122.0169 | -121.9574 | 121.8109 | 0.082397 | 23.0164 | 0.10986
3383.9219 | 122.1313 | -0.041199 | 121.9482 | -0.01976 | 0.0056782 | 0.053854 | 0.054297 | 0.0016535 | -0.0074938 | 0.0003952 | -0.005371 | 0.021676 | 0.046053 | -0.010579 | 0.01383 | 0.022896 | -0.0034117 | 23.0118 | 121.9528 | -0.059509 | 121.788 | 0.99335 | 0.091553 | 0.14191 | 0.086975 | -0.018311 | 0 | 0.073242 | 0.16479 | 0.1236 | 0.16022 | -0.01831 | 0.004578 | -0.16022 | 1.0345 | 0.18311 | 0.13275 | 0.20142 | 0.15106 | 0.041199 | -121.9666 | -121.875 | 0.20599 | 0.20142 | 0.16479 | 0.16022 | 0.1236 | 1.0529 | 121.8475 | 0.16479 | 0.073242 | 122.0123 | -0.018311 | 121.994 | 0.022888 | -122.0078 | -121.9482 | 121.8292 | 0.11444 | 23.053 | 0.12817
3385.6406 | 122.0764 | -0.068665 | 121.9482 | -0.012131 | 0.0035418 | 0.055136 | 0.049811 | 0.00058534 | -0.0094164 | -0.0013138 | -0.0084228 | 0.023385 | 0.046053 | -0.018055 | 0.015966 | 0.024605 | -0.0029843 | 23.0164 | 121.9299 | -0.041199 | 121.8018 | 0.99792 | 0.15106 | 0.16022 | 0.050354 | 0 | -0.018311 | -0.018311 | 0.10529 | 0.09613 | 0.086975 | 0.027466 | -0.01831 | -0.14648 | 1.0666 | 0.22888 | 0.21973 | 0.20142 | 0.19226 | 0.050354 | -121.9482 | -121.9666 | 0.17395 | 0.15564 | 0.16479 | 0.10529 | 0.11444 | 1.0391 | 121.843 | 0.1236 | 0 | 121.9711 | 0.018311 | 121.9986 | 0.068665 | -121.9894 | -121.9666 | 121.8704 | 0.050354 | 23.085 | 0.11902
3387.4062 | 122.0306 | -0.13275 | 121.994 | -0.012131 | 0.0031146 | 0.052359 | 0.05216 | -0.00026906 | -0.0094164 | -0.0021682 | -0.005371 | 0.02424 | 0.044558 | -0.015706 | 0.016607 | 0.024605 | -0.0014891 | 22.9706 | 121.9894 | -0.082397 | 121.6919 | 0.86517 | 0.027466 | 0.059509 | -0.068665 | 0.009155 | -0.032043 | -0.07782 | 0.041199 | 0.022888 | 0.050354 | 0.050354 | -0.004578 | -0.30212 | 0.99792 | 0.19226 | 0.16022 | 0.14191 | 0.10986 | 0.10071 | -121.9849 | -122.0718 | 0.17395 | 0.18311 | 0.15564 | 0.082397 | 0.054931 | 0.94757 | 121.7743 | 0.073242 | -0.045777 | 122.0718 | 0.041198 | 122.1222 | 0.14191 | -122.0764 | -122.0261 | 121.8246 | 0.054931 | 23.1033 | 0.064086
3389.125 | 122.0261 | -0.091553 | 121.9894 | -0.01976 | 0.0033282 | 0.051077 | 0.053656 | 0.0025079 | -0.0083484 | -0.001741 | -0.005371 | 0.022744 | 0.046053 | -0.0088695 | 0.017461 | 0.0261 | -0.0025571 | 22.9843 | 121.9666 | -0.09613 | 121.6919 | 0.88806 | 0.027466 | 0.064087 | -0.041199 | 0.009155 | -0.054932 | -0.045776 | 0.059509 | 0.041199 | 0.054932 | -0.004577 | -0.022888 | -0.29755 | 0.97962 | 0.15564 | 0.11902 | 0.16022 | 0.1236 | 0.036621 | -121.9803 | -122.0352 | 0.15106 | 0.14649 | 0.13275 | 0.10986 | 0.096131 | 0.98419 | 121.788 | 0.11444 | 0.009156 | 122.0627 | 0.064087 | 122.0581 | 0.10071 | -122.0856 | -122.0444 | 121.7834 | 0.045777 | 23.0759 | 0.050354
3390.8906 | 122.0947 | -0.064087 | 121.9391 | -0.0045011 | 0.0054644 | 0.056631 | 0.049597 | -0.00091006 | -0.0070666 | -0.0049454 | -0.005371 | 0.021035 | 0.046053 | -0.016774 | 0.014898 | 0.024819 | -0.0074705 | 23.0392 | 121.9345 | -0.022888 | 121.8018 | 1.0483 | 0.10986 | 0.16937 | 0.10529 | -0.022888 | -0.004578 | 0.064087 | 0.13733 | 0.12817 | 0.11444 | 0.041199 | -0.004578 | -0.13733 | 1.1124 | 0.23346 | 0.17395 | 0.19226 | 0.13275 | 0.059509 | -121.962 | -121.875 | 0.20142 | 0.17853 | 0.19226 | 0.11902 | 0.13275 | 1.0712 | 121.8246 | 0.14191 | 0.068665 | 121.9574 | -0.01831 | 121.9986 | 0.041199 | -121.962 | -121.9437 | 121.8658 | 0.12817 | 23.1033 | 0.16937
3392.5938 | 121.994 | -0.10986 | 121.9894 | -0.02739 | 0.00461 | 0.054922 | 0.055578 | 0.0050713 | -0.00963 | -0.0038772 | -0.0023192 | 0.02189 | 0.044558 | -0.013569 | 0.018743 | 0.022683 | -0.0023435 | 23.0209 | 121.9986 | -0.086975 | 121.7102 | 0.89722 | 0 | 0.045776 | -0.054932 | 0.009155 | -0.036621 | -0.068665 | 0.013733 | -0.032043 | 0.036621 | 0.022888 | 0.009155 | -0.27924 | 1.0071 | 0.15564 | 0.10986 | 0.13275 | 0.086975 | 0.073242 | -121.9803 | -122.0581 | 0.1236 | 0.14648 | 0.07782 | 0.073242 | 0.004578 | 0.98419 | 121.7972 | 0.050354 | -0.032044 | 122.0856 | 0.045776 | 122.1085 | 0.11902 | -122.0764 | -122.0261 | 121.8201 | 0.041198 | 23.1308 | 0.054931
3394.375 | 122.1405 | -0.068665 | 121.9803 | -0.01976 | -0.0017986 | 0.053 | 0.05216 | 0.0012261 | -0.0098438 | -0.000673 | -0.0023192 | 0.021249 | 0.04648 | -0.021687 | 0.013403 | 0.025246 | -0.0017027 | 23.0667 | 121.9482 | -0.059509 | 121.7972 | 1.0483 | 0.15564 | 0.1831 | 0.086975 | -0.032043 | -0.004578 | 0.054932 | 0.1831 | 0.16479 | 0.13733 | 0.009156 | -0.032044 | -0.18311 | 1.1169 | 0.25177 | 0.22431 | 0.24261 | 0.21515 | 0.064087 | -122.0123 | -121.9254 | 0.25177 | 0.20599 | 0.23346 | 0.14191 | 0.16937 | 1.1078 | 121.8567 | 0.18768 | 0.05951 | 122.0078 | -0.027465 | 122.0169 | 0.036622 | -122.0398 | -121.9849 | 121.8658 | 0.1236 | 23.1354 | 0.15564
3396.1406 | 122.0901 | -0.082397 | 121.9482 | -0.012131 | 0.0037556 | 0.053641 | 0.052801 | -0.0024055 | -0.008562 | -0.0040908 | -0.011475 | 0.01954 | 0.044985 | -0.018269 | 0.012975 | 0.023964 | -0.00020725 | 23.0576 | 121.9666 | -0.054932 | 121.756 | 1.0025 | 0.091553 | 0.13733 | 0.018311 | -0.009155 | -0.009155 | -0.018311 | 0.091553 | 0.068665 | 0.082397 | 0.027465 | 0.018311 | -0.19226 | 1.0849 | 0.21973 | 0.17395 | 0.19226 | 0.14649 | 0.073242 | -121.9574 | -121.9666 | 0.17395 | 0.16479 | 0.15106 | 0.091552 | 0.07782 | 1.0574 | 121.8109 | 0.10071 | -0.009156 | 122.0215 | 0 | 122.049 | 0.073242 | -122.0032 | -121.9574 | 121.8384 | 0.064086 | 23.14 | 0.10071
3397.9062 | 121.9849 | -0.10071 | 121.9894 | -0.0045011 | 0.0026874 | 0.054922 | 0.049597 | -0.0021919 | -0.008562 | -0.0015274 | -0.0023192 | 0.024667 | 0.04648 | -0.014638 | 0.015325 | 0.023964 | -0.0010617 | 23.0667 | 121.9757 | -0.09613 | 121.6873 | 0.92468 | 0.013733 | 0.064087 | -0.054932 | 0.013733 | -0.050354 | -0.068665 | 0.036621 | 0.013733 | 0.027466 | 0.004578 | -0.013733 | -0.30212 | 1.0254 | 0.1648 | 0.11444 | 0.16022 | 0.10986 | 0.050354 | -121.9757 | -122.0581 | 0.13733 | 0.12817 | 0.11444 | 0.07782 | 0.064087 | 1.0208 | 121.7834 | 0.086975 | -0.018311 | 122.0718 | 0.064087 | 122.0764 | 0.11444 | -122.0856 | -122.0398 | 121.788 | 0.032043 | 23.1674 | 0.045776
3399.625 | 122.1359 | -0.036621 | 121.9391 | -0.012131 | 0.006319 | 0.060263 | 0.051306 | -0.00026906 | -0.0077074 | -0.00345 | -0.0023192 | 0.020395 | 0.045412 | -0.016133 | 0.015539 | 0.022042 | -0.0044797 | 23.1583 | 121.9437 | -0.050354 | 121.8155 | 1.0757 | 0.11444 | 0.17395 | 0.10529 | -0.041199 | 0 | 0.064087 | 0.16479 | 0.1236 | 0.14648 | -0.013733 | 0.004578 | -0.1236 | 1.1124 | 0.21057 | 0.15106 | 0.2243 | 0.16479 | 0.036621 | -121.9803 | -121.875 | 0.20142 | 0.18311 | 0.16022 | 0.14648 | 0.1236 | 1.1261 | 121.8658 | 0.16479 | 0.064087 | 121.994 | -0.041199 | 121.9803 | -0.004578 | -121.9894 | -121.9391 | 121.8521 | 0.10071 | 23.1949 | 0.14191
3401.3906 | 122.0032 | -0.10529 | 121.9849 | -0.012131 | 0.0041828 | 0.051932 | 0.05216 | 0.0022943 | -0.0094164 | -0.0002456 | -0.005371 | 0.023599 | 0.045626 | -0.013142 | 0.015325 | 0.025032 | -0.0049069 | 23.0942 | 121.9849 | -0.068665 | 121.6782 | 0.95215 | 0.032043 | 0.054932 | -0.059509 | 0.013733 | -0.045776 | -0.068665 | 0.054932 | 0.009155 | 0.032043 | 0.036621 | 0 | -0.3067 | 1.0574 | 0.16022 | 0.13733 | 0.1236 | 0.10071 | 0.05951 | -121.9711 | -122.0535 | 0.16022 | 0.13733 | 0.11444 | 0.077819 | 0.054931 | 1.0208 | 121.7468 | 0.10071 | -0.022889 | 122.0535 | 0.059509 | 122.0901 | 0.11902 | -122.0535 | -122.0306 | 121.7834 | 0.036621 | 23.1995 | 0.045777
3403.1875 | 122.1451 | -0.07782 | 121.9391 | 0.010757 | 0.0020466 | 0.053641 | 0.050451 | 0.00058534 | -0.0074938 | -0.0019546 | -0.0084228 | 0.020395 | 0.045626 | -0.019337 | 0.014471 | 0.023964 | -0.0072569 | 23.2086 | 121.9162 | -0.050354 | 121.843 | 1.1261 | 0.19226 | 0.20599 | 0.11902 | -0.027466 | -0.018311 | 0.045776 | 0.17853 | 0.16479 | 0.11902 | 0.027466 | -0.022888 | -0.09613 | 1.2039 | 0.28381 | 0.27008 | 0.25635 | 0.24261 | 0.059509 | -121.9666 | -121.8933 | 0.25635 | 0.19684 | 0.24261 | 0.13733 | 0.18311 | 1.1765 | 121.8933 | 0.19684 | 0.064087 | 121.9666 | -0.009155 | 121.994 | 0.050354 | -121.9894 | -121.9574 | 121.9208 | 0.1236 | 23.2864 | 0.19684
3404.9688 | 122.1405 | -0.07782 | 121.9482 | -0.0045011 | 0.0020466 | 0.052786 | 0.04917 | 0.0012261 | -0.008562 | -0.0038772 | -0.0023192 | 0.021249 | 0.046267 | -0.016347 | 0.013189 | 0.022683 | -0.0036253 | 23.1583 | 121.9391 | -0.059509 | 121.7651 | 1.0712 | 0.13275 | 0.18768 | 0.064087 | -0.013733 | -0.009155 | 0.041199 | 0.16479 | 0.15564 | 0.14191 | 0.018311 | -0.009155 | -0.1831 | 1.149 | 0.2655 | 0.21057 | 0.24719 | 0.19226 | 0.068665 | -121.962 | -121.907 | 0.24261 | 0.21973 | 0.23346 | 0.15106 | 0.16479 | 1.1307 | 121.8246 | 0.17395 | 0.050354 | 121.9986 | -0.004578 | 122.0169 | 0.064087 | -122.0078 | -121.9574 | 121.843 | 0.11902 | 23.2361 | 0.14191
3406.75 | 122.0169 | -0.10529 | 121.9757 | 0.0031279 | 0.00076478 | 0.051718 | 0.053228 | -0.00069646 | -0.0083484 | -0.0004592 | -0.0023192 | 0.024667 | 0.044771 | -0.010365 | 0.015752 | 0.025673 | -0.0031979 | 23.1674 | 121.9757 | -0.09613 | 121.669 | 0.9613 | 0.045776 | 0.073242 | -0.068665 | 0.013733 | -0.041199 | -0.068665 | 0.050354 | 0.032043 | 0.041199 | 0.009156 | 0 | -0.3067 | 1.0666 | 0.17853 | 0.15106 | 0.16937 | 0.14191 | 0.064087 | -121.962 | -122.0444 | 0.15564 | 0.14649 | 0.13733 | 0.082398 | 0.073242 | 1.0574 | 121.7651 | 0.091553 | -0.027466 | 122.0718 | 0.054932 | 122.081 | 0.11902 | -122.0718 | -122.0169 | 121.7743 | 0.036621 | 23.2727 | 0.036621
3408.4688 | 122.1542 | -0.050354 | 121.9437 | -0.01976 | 0.00033758 | 0.052145 | 0.049597 | -0.0039007 | -0.010057 | 0.0001816 | -0.0023192 | 0.019113 | 0.044985 | -0.017842 | 0.014684 | 0.023537 | -0.0042661 | 23.2361 | 121.9116 | -0.068665 | 121.8063 | 1.1444 | 0.17853 | 0.21515 | 0.13275 | -0.032043 | -0.013733 | 0.068665 | 0.19226 | 0.17395 | 0.13733 | -0.018311 | -0.032044 | -0.13733 | 1.1948 | 0.2655 | 0.22888 | 0.28381 | 0.24719 | 0.036621 | -121.9757 | -121.875 | 0.24261 | 0.18768 | 0.2243 | 0.15106 | 0.18768 | 1.2131 | 121.875 | 0.20599 | 0.082398 | 121.9803 | -0.01831 | 121.962 | 0.018311 | -122.0123 | -121.9574 | 121.8567 | 0.11902 | 23.2864 | 0.18311
3410.2344 | 122.049 | -0.09613 | 121.9986 | -0.01976 | 0.00461 | 0.051932 | 0.054083 | 0.0052851 | -0.0062122 | -0.0055862 | -0.0084228 | 0.023385 | 0.043917 | -0.012501 | 0.015752 | 0.023751 | -0.0051205 | 23.2361 | 121.9666 | -0.068665 | 121.7606 | 1.0712 | 0.07782 | 0.10986 | 0.018311 | 0.004578 | -0.027466 | -0.018311 | 0.073242 | 0.045776 | 0.064087 | 0.027465 | -0.032043 | -0.23804 | 1.1673 | 0.20599 | 0.17395 | 0.17853 | 0.14649 | 0.068664 | -121.994 | -122.0169 | 0.16937 | 0.16022 | 0.14191 | 0.091553 | 0.073242 | 1.1398 | 121.8292 | 0.10071 | 0.009155 | 122.0352 | 0.032044 | 122.0627 | 0.10071 | -122.0673 | -122.0261 | 121.8567 | 0.077819 | 23.3322 | 0.11444
3411.9375 | 122.0764 | -0.07782 | 121.9711 | -0.0045011 | 0.001192 | 0.053641 | 0.050879 | -0.0024055 | -0.0079212 | -0.001741 | -0.0023192 | 0.018686 | 0.043703 | -0.012288 | 0.012975 | 0.021401 | -0.0010617 | 23.2773 | 121.9162 | -0.068665 | 121.8018 | 1.149 | 0.17395 | 0.19684 | 0.059509 | -0.004578 | -0.018311 | -0.009155 | 0.10529 | 0.10071 | 0.091553 | 0.009155 | -0.054931 | -0.16937 | 1.2268 | 0.27466 | 0.25177 | 0.2655 | 0.24261 | 0.059509 | -121.9757 | -121.9803 | 0.18311 | 0.16937 | 0.17853 | 0.10986 | 0.11902 | 1.2177 | 121.8704 | 0.1236 | 0.009156 | 121.9849 | 0.013733 | 121.994 | 0.073242 | -122.0398 | -121.9894 | 121.8796 | 0.068665 | 23.3551 | 0.13733
3413.7031 | 122.0444 | -0.082397 | 122.0078 | -0.0045011 | 0.0043964 | 0.053427 | 0.052374 | 0.0016535 | -0.0074938 | -0.0011002 | -0.005371 | 0.024667 | 0.045412 | -0.01186 | 0.016821 | 0.024391 | -0.0038389 | 23.2773 | 121.9803 | -0.064087 | 121.7514 | 1.0986 | 0.082397 | 0.1236 | 0.018311 | -0.009155 | -0.032043 | -0.009155 | 0.086975 | 0.045776 | 0.064087 | 0.01831 | -0.027465 | -0.25635 | 1.181 | 0.20599 | 0.16479 | 0.18768 | 0.14648 | 0.050354 | -122.0169 | -122.0169 | 0.16937 | 0.14648 | 0.12817 | 0.09613 | 0.077819 | 1.1627 | 121.8155 | 0.11902 | 0.022888 | 122.0444 | 0.022888 | 122.0627 | 0.073242 | -122.0718 | -122.0398 | 121.8338 | 0.073242 | 23.3597 | 0.10071
3415.4688 | 122.1497 | -0.059509 | 121.9666 | -0.012131 | 0.00076478 | 0.051932 | 0.048529 | -0.0021919 | -0.0087756 | -0.0008866 | -0.0084228 | 0.019113 | 0.043062 | -0.015065 | 0.013403 | 0.024178 | -0.0021299 | 23.3139 | 121.907 | -0.050354 | 121.8246 | 1.2085 | 0.20142 | 0.23346 | 0.14191 | -0.041199 | -0.009155 | 0.054932 | 0.19684 | 0.16479 | 0.15106 | 0.009155 | -0.05951 | -0.14191 | 1.268 | 0.29297 | 0.26093 | 0.28381 | 0.25177 | 0.050354 | -122.0078 | -121.9116 | 0.25635 | 0.21057 | 0.2243 | 0.16022 | 0.17395 | 1.2589 | 121.875 | 0.20599 | 0.064087 | 121.9574 | -0.032044 | 121.9666 | 0.01831 | -122.0169 | -121.9757 | 121.8842 | 0.11444 | 23.3734 | 0.20142
3417.2344 | 122.0078 | -0.11444 | 121.9803 | -0.012131 | 0.00461 | 0.057059 | 0.056006 | 0.0012261 | -0.0072802 | -0.0028092 | -0.005371 | 0.024667 | 0.046694 | -0.014638 | 0.017675 | 0.024178 | -0.0017027 | 23.259 | 122.0169 | -0.073242 | 121.669 | 1.0025 | 0.004578 | 0.068665 | -0.054932 | 0.009155 | -0.050354 | -0.068665 | 0.009155 | -0.018311 | 0.036621 | 0.041199 | 0.036621 | -0.31128 | 1.1169 | 0.18311 | 0.11902 | 0.14191 | 0.07782 | 0.064087 | -121.9711 | -122.049 | 0.1236 | 0.15106 | 0.09613 | 0.086975 | 0.032043 | 1.0757 | 121.7422 | 0.059509 | -0.018311 | 122.0901 | 0.059509 | 122.1313 | 0.1236 | -122.0535 | -122.0306 | 121.7834 | 0.045776 | 23.3734 | 0.059509
3419 | 122.049 | -0.086975 | 121.994 | -0.012131 | 0.00461 | 0.054495 | 0.052801 | 0.0014397 | -0.00963 | -0.0021682 | -0.0023192 | 0.025949 | 0.046694 | -0.012288 | 0.015539 | 0.023964 | -0.0053343 | 23.3276 | 121.962 | -0.054932 | 121.7468 | 1.1215 | 0.10071 | 0.11902 | 0.022888 | 0.013733 | -0.045776 | 0.004578 | 0.10071 | 0.068665 | 0.082397 | 0.032043 | -0.032044 | -0.24719 | 1.2085 | 0.20599 | 0.18768 | 0.17395 | 0.15564 | 0.041199 | -121.9803 | -121.9894 | 0.18768 | 0.16937 | 0.15564 | 0.12817 | 0.11444 | 1.1765 | 121.8018 | 0.14648 | 0.050354 | 122.0169 | 0.059509 | 122.0489 | 0.10071 | -122.049 | -122.0398 | 121.8338 | 0.091553 | 23.4146 | 0.10986
3420.7656 | 122.0306 | -0.091553 | 121.9574 | -0.0045011 | 0.0031146 | 0.053 | 0.054297 | 0.0010125 | -0.0077074 | -0.0015274 | -0.005371 | 0.020181 | 0.042849 | -0.015492 | 0.016821 | 0.022896 | -0.0057615 | 23.3139 | 121.962 | -0.082397 | 121.7331 | 1.0941 | 0.09613 | 0.11444 | -0.009155 | 0 | -0.032043 | -0.022888 | 0.10071 | 0.068665 | 0.086975 | 0.009156 | 0.004578 | -0.2243 | 1.1856 | 0.20599 | 0.18768 | 0.19684 | 0.17853 | 0.05951 | -121.9574 | -121.9803 | 0.19226 | 0.17853 | 0.16022 | 0.11902 | 0.10071 | 1.1765 | 121.8155 | 0.13275 | 0.009155 | 122.0444 | 0.032043 | 122.0535 | 0.091553 | -122.0398 | -121.9894 | 121.8246 | 0.068665 | 23.4055 | 0.082398
3422.4688 | 122.0581 | -0.091553 | 121.9894 | -0.012131 | 0.0014056 | 0.053641 | 0.050451 | 0.00015814 | -0.0089892 | -0.0025956 | -0.005371 | 0.021463 | 0.045198 | -0.013783 | 0.017461 | 0.024391 | -0.0021299 | 23.3231 | 121.962 | -0.082397 | 121.7056 | 1.0895 | 0.086975 | 0.091553 | -0.022888 | 0.022888 | -0.032043 | -0.032043 | 0.082397 | 0.054932 | 0.068665 | 0.009156 | -0.027466 | -0.28381 | 1.181 | 0.18311 | 0.17853 | 0.17395 | 0.16937 | 0.05951 | -121.9666 | -122.0215 | 0.17395 | 0.16022 | 0.14649 | 0.10071 | 0.086975 | 1.1719 | 121.788 | 0.11444 | 0 | 122.0444 | 0.054931 | 122.0535 | 0.11444 | -122.0718 | -122.0215 | 121.7972 | 0.05951 | 23.4146 | 0.068665
3424.2344 | 122.1039 | -0.064087 | 121.9345 | -0.012131 | 0.0037556 | 0.055563 | 0.050665 | -0.00091006 | -0.0094164 | -0.0028092 | -0.0084228 | 0.021463 | 0.043062 | -0.019978 | 0.012975 | 0.028023 | -0.0019163 | 23.3551 | 121.9162 | -0.036621 | 121.7926 | 1.2131 | 0.16022 | 0.21515 | 0.07782 | -0.036621 | -0.009155 | 0.054932 | 0.13733 | 0.10986 | 0.10529 | 0.027466 | -0.01831 | -0.14191 | 1.2772 | 0.27924 | 0.2243 | 0.25177 | 0.19684 | 0.054932 | -121.9711 | -121.8796 | 0.20142 | 0.16937 | 0.17395 | 0.11444 | 0.11902 | 1.2497 | 121.8292 | 0.14648 | 0.064087 | 121.9528 | -0.027466 | 121.9803 | 0.027466 | -121.9711 | -121.9437 | 121.8567 | 0.11902 | 23.4192 | 0.14191
3426.0156 | 122.0993 | -0.068665 | 121.9437 | -0.012131 | 0.0033282 | 0.051718 | 0.049811 | -0.0030463 | -0.0077074 | -0.0045182 | -0.011475 | 0.020181 | 0.042849 | -0.018483 | 0.014471 | 0.023751 | -0.0023435 | 23.4009 | 121.9345 | -0.050354 | 121.8109 | 1.2405 | 0.19684 | 0.2243 | 0.091553 | -0.022888 | 0.004578 | 0.036621 | 0.15564 | 0.14648 | 0.11444 | 0.018311 | -0.009156 | -0.13275 | 1.3092 | 0.29297 | 0.2655 | 0.27466 | 0.24719 | 0.073243 | -121.9666 | -121.907 | 0.22431 | 0.18311 | 0.21515 | 0.10986 | 0.14191 | 1.2909 | 121.8613 | 0.15106 | 0.032043 | 121.9849 | -0.027466 | 122.0032 | 0.045777 | -121.994 | -121.9391 | 121.8796 | 0.10529 | 23.4695 | 0.16022
3427.7812 | 122.0215 | -0.091553 | 121.9849 | -0.0045011 | 0.0052508 | 0.056845 | 0.053869 | 0.0020807 | -0.0072802 | -0.0013138 | -0.0023192 | 0.021676 | 0.042421 | -0.010365 | 0.015539 | 0.025032 | -0.0044797 | 23.3505 | 121.9849 | -0.068665 | 121.669 | 1.0803 | 0.027466 | 0.073242 | -0.050354 | 0.022888 | -0.045776 | -0.054932 | 0.032043 | -0.009155 | 0.027466 | 0.022888 | 0 | -0.31586 | 1.1719 | 0.16479 | 0.11902 | 0.14191 | 0.096131 | 0.045777 | -121.962 | -122.0398 | 0.1236 | 0.11902 | 0.082398 | 0.073242 | 0.036621 | 1.149 | 121.7377 | 0.077819 | -0.009156 | 122.0535 | 0.068664 | 122.0764 | 0.11444 | -122.0535 | -122.0306 | 121.7606 | 0.036621 | 23.4421 | 0.041199
3429.5 | 122.0764 | -0.068665 | 121.962 | -0.012131 | 0.0058918 | 0.055991 | 0.055151 | -0.0013373 | -0.0059986 | -0.00345 | -0.005371 | 0.020608 | 0.042635 | -0.014424 | 0.012975 | 0.023964 | -0.0025571 | 23.3505 | 121.9986 | -0.091553 | 121.7331 | 1.1398 | 0.068665 | 0.12817 | 0.013733 | 0 | -0.018311 | 0.032043 | 0.10986 | 0.091553 | 0.1236 | -0.022888 | 0.036621 | -0.22888 | 1.2085 | 0.19684 | 0.13733 | 0.21973 | 0.16022 | 0.050354 | -121.962 | -121.9299 | 0.17853 | 0.19226 | 0.16022 | 0.14191 | 0.10986 | 1.2314 | 121.8246 | 0.12817 | 0.050354 | 122.0901 | 0.018311 | 122.0673 | 0.068665 | -122.0535 | -121.9803 | 121.8018 | 0.10071 | 23.4192 | 0.082398
3431.2656 | 122.0398 | -0.082397 | 121.962 | -0.0045011 | 0.0058918 | 0.055777 | 0.054937 | 0.0014397 | -0.0066394 | 0.0001816 | -0.005371 | 0.024026 | 0.040499 | -0.012074 | 0.01618 | 0.025246 | -0.0061887 | 23.3826 | 121.9666 | -0.086975 | 121.7331 | 1.2085 | 0.1236 | 0.13733 | 0.041199 | -0.004578 | -0.018311 | -0.013733 | 0.091553 | 0.073242 | 0.064087 | -0.004578 | 0.004578 | -0.22888 | 1.2909 | 0.21973 | 0.20599 | 0.2243 | 0.21057 | 0.064086 | -121.9666 | -121.9757 | 0.17395 | 0.14648 | 0.15564 | 0.082398 | 0.091553 | 1.2955 | 121.8201 | 0.10986 | 0.004578 | 122.0535 | 0.013733 | 122.049 | 0.077819 | -122.0489 | -121.9803 | 121.8155 | 0.068664 | 23.465 | 0.1236
3432.9688 | 122.1176 | -0.064087 | 121.9574 | -0.0045011 | 0.0033282 | 0.053854 | 0.050451 | 0.00079894 | -0.0092028 | -0.0013138 | -0.005371 | 0.01954 | 0.04114 | -0.015065 | 0.013616 | 0.024605 | -0.0076841 | 23.4238 | 121.9025 | -0.041199 | 121.843 | 1.3 | 0.21973 | 0.26093 | 0.12817 | -0.032043 | 0 | 0.036621 | 0.19226 | 0.17395 | 0.12817 | 0.022888 | -0.054931 | -0.11444 | 1.3641 | 0.32501 | 0.28381 | 0.30212 | 0.26093 | 0.064087 | -121.9894 | -121.9208 | 0.25635 | 0.19226 | 0.23804 | 0.12817 | 0.17395 | 1.3412 | 121.8842 | 0.19226 | 0.036621 | 121.9437 | -0.032043 | 121.9666 | 0.032044 | -121.9986 | -121.9574 | 121.907 | 0.10071 | 23.4879 | 0.19226
3434.7344 | 122.049 | -0.10071 | 121.9803 | 0.0031279 | 0.0052508 | 0.050436 | 0.053228 | 0.0027215 | -0.0094164 | -0.0008866 | -0.0084228 | 0.022958 | 0.039858 | -0.0084423 | 0.016393 | 0.02546 | -0.0068295 | 23.41 | 121.9757 | -0.07782 | 121.7377 | 1.1993 | 0.12817 | 0.13275 | 0.009155 | 0.013733 | -0.018311 | -0.022888 | 0.09613 | 0.050354 | 0.07782 | 0.022888 | -0.004578 | -0.24262 | 1.3 | 0.23346 | 0.22888 | 0.21057 | 0.20599 | 0.082397 | -121.9666 | -122.0032 | 0.19684 | 0.17853 | 0.15106 | 0.096131 | 0.068665 | 1.2772 | 121.8155 | 0.11444 | -0.004577 | 122.0535 | 0.032044 | 122.0764 | 0.11444 | -122.0581 | -121.9986 | 121.8384 | 0.07782 | 23.5107 | 0.10986
3436.5 | 122.0306 | -0.10071 | 122.0078 | -0.012131 | 0.006319 | 0.053641 | 0.052588 | 0.00079894 | -0.00963 | -0.0036636 | -0.0023192 | 0.020822 | 0.04178 | -0.016987 | 0.016821 | 0.028023 | -0.00042085 | 23.3871 | 121.9849 | -0.07782 | 121.6736 | 1.1536 | 0.054932 | 0.09613 | -0.041199 | 0.004578 | -0.032043 | -0.041199 | 0.036621 | 0.018311 | 0.045776 | 0.022888 | -0.022888 | -0.33417 | 1.2543 | 0.19684 | 0.15564 | 0.17395 | 0.13275 | 0.068665 | -122.0032 | -122.049 | 0.13733 | 0.14648 | 0.11902 | 0.077819 | 0.050354 | 1.2314 | 121.7514 | 0.068664 | -0.009156 | 122.0627 | 0.036621 | 122.0856 | 0.10529 | -122.0856 | -122.0398 | 121.7743 | 0.059509 | 23.4879 | 0.059509
3438.2812 | 121.9849 | -0.11444 | 121.9849 | -0.012131 | 0.008028 | 0.054282 | 0.053228 | 0.0010125 | -0.0064258 | -0.0015274 | -0.0084228 | 0.022103 | 0.040071 | -0.019764 | 0.01618 | 0.022042 | -0.0023435 | 23.3963 | 121.994 | -0.073242 | 121.6919 | 1.1353 | 0.045776 | 0.086975 | -0.064087 | 0.036621 | -0.050354 | -0.07782 | 0.009155 | -0.032043 | 0.018311 | 0.041199 | 0.009156 | -0.29297 | 1.2497 | 0.20142 | 0.16022 | 0.16022 | 0.11902 | 0.064087 | -121.9482 | -122.0627 | 0.1236 | 0.13275 | 0.082398 | 0.068665 | 0.018311 | 1.2085 | 121.7651 | 0.059509 | -0.027466 | 122.0673 | 0.086975 | 122.1085 | 0.15106 | -122.0581 | -122.0352 | 121.8063 | 0.036621 | 23.5107 | 0.050354
3439.9844 | 122.0444 | -0.086975 | 121.9711 | -0.01976 | 0.0065326 | 0.053854 | 0.054083 | -0.00091006 | -0.0074938 | -0.0019546 | -0.005371 | 0.021249 | 0.04413 | -0.02126 | 0.015325 | 0.026314 | -0.0014891 | 23.4009 | 122.0032 | -0.082397 | 121.6965 | 1.1856 | 0.068665 | 0.11444 | -0.013733 | -0.004578 | -0.036621 | -0.013733 | 0.068665 | 0.041199 | 0.082397 | 0.004578 | 0.032044 | -0.27466 | 1.2726 | 0.20142 | 0.15564 | 0.19684 | 0.15106 | 0.050354 | -121.9757 | -121.9849 | 0.15564 | 0.16937 | 0.12817 | 0.11902 | 0.07782 | 1.268 | 121.7789 | 0.10529 | 0.022888 | 122.0856 | 0.032043 | 122.0901 | 0.082397 | -122.0535 | -122.0078 | 121.7834 | 0.073242 | 23.4879 | 0.073242
3441.75 | 122.1313 | -0.068665 | 121.9574 | -0.012131 | 0.0052508 | 0.054282 | 0.053228 | 0.0035761 | -0.0094164 | -0.0021682 | -0.0084228 | 0.018899 | 0.039644 | -0.0086559 | 0.015539 | 0.025032 | -0.0055479 | 23.4741 | 121.9666 | -0.041199 | 121.7926 | 1.3046 | 0.16479 | 0.2243 | 0.091553 | -0.032043 | -0.018311 | 0.064087 | 0.16022 | 0.14191 | 0.15564 | 0.027466 | 0.009156 | -0.16479 | 1.3733 | 0.29297 | 0.23346 | 0.2655 | 0.20599 | 0.050354 | -121.9894 | -121.8933 | 0.22888 | 0.22431 | 0.21057 | 0.17395 | 0.16022 | 1.3458 | 121.8338 | 0.17853 | 0.082398 | 122.0078 | -0.013732 | 122.0352 | 0.036622 | -121.9986 | -121.9757 | 121.8613 | 0.13275 | 23.5428 | 0.16022
3443.5156 | 122.049 | -0.09613 | 121.9757 | -0.012131 | 0.0039692 | 0.05535 | 0.054083 | 0.0052851 | -0.0081348 | -0.0008866 | -0.0023192 | 0.02189 | 0.03879 | -0.0078015 | 0.015966 | 0.025673 | -0.0057615 | 23.4741 | 121.9894 | -0.073242 | 121.7468 | 1.2772 | 0.13733 | 0.16022 | 0.045776 | 0.018311 | -0.013733 | -0.004578 | 0.082397 | 0.068665 | 0.07782 | 0.022888 | 0.013733 | -0.22888 | 1.3733 | 0.25635 | 0.23346 | 0.23346 | 0.21057 | 0.082397 | -121.9574 | -121.9803 | 0.17853 | 0.17395 | 0.16479 | 0.091553 | 0.082398 | 1.3504 | 121.8201 | 0.09613 | 0.009155 | 122.0627 | 0.032044 | 122.0856 | 0.11444 | -122.0489 | -121.9894 | 121.843 | 0.091552 | 23.5703 | 0.14191
3445.2188 | 122.1497 | -0.064087 | 121.9482 | -0.012131 | -0.00051702 | 0.051932 | 0.049383 | 0.00058534 | -0.0087756 | -0.001741 | -0.005371 | 0.015695 | 0.040499 | -0.014638 | 0.015112 | 0.025887 | -0.0012753 | 23.5016 | 121.9345 | -0.054932 | 121.8063 | 1.3687 | 0.24261 | 0.27008 | 0.1236 | -0.022888 | 0 | 0.064087 | 0.21057 | 0.17853 | 0.14191 | 0.009155 | -0.013733 | -0.14191 | 1.4328 | 0.33417 | 0.3067 | 0.32501 | 0.29755 | 0.064087 | -121.9711 | -121.8842 | 0.27466 | 0.20599 | 0.24261 | 0.14191 | 0.17853 | 1.4236 | 121.8613 | 0.21057 | 0.064087 | 121.9894 | -0.022888 | 121.9986 | 0.041199 | -122.0032 | -121.9482 | 121.8704 | 0.12817 | 23.5657 | 0.18768
3446.9844 | 122.0352 | -0.09613 | 121.994 | -0.012131 | 0.0037556 | 0.054709 | 0.053228 | -0.0015509 | -0.0087756 | 0.0001816 | -0.005371 | 0.024026 | 0.043062 | -0.013997 | 0.016393 | 0.02546 | -0.0014891 | 23.5107 | 122.0078 | -0.059509 | 121.7422 | 1.2817 | 0.13733 | 0.15106 | 0.032043 | 0.004578 | -0.027466 | -0.018311 | 0.073242 | 0.036621 | 0.068665 | 0.036621 | 0.013732 | -0.25177 | 1.3779 | 0.24719 | 0.23346 | 0.21057 | 0.19684 | 0.068664 | -121.9894 | -122.0123 | 0.16937 | 0.16479 | 0.13275 | 0.096131 | 0.064087 | 1.3412 | 121.8018 | 0.10071 | 0.009155 | 122.0673 | 0.032044 | 122.1039 | 0.10071 | -122.0535 | -122.0215 | 121.8384 | 0.077819 | 23.6069 | 0.12817
3448.7656 | 122.081 | -0.091553 | 121.9803 | -0.0045011 | 0.0039692 | 0.054495 | 0.050451 | -0.0019781 | -0.0083484 | -3.1996e-05 | -0.0023192 | 0.017617 | 0.041567 | -0.018055 | 0.014043 | 0.025032 | -0.00084805 | 23.4924 | 121.9116 | -0.045776 | 121.7422 | 1.3092 | 0.17395 | 0.20142 | 0.018311 | -0.013733 | -0.013733 | -0.009155 | 0.10529 | 0.068665 | 0.086975 | 0.045777 | -0.068665 | -0.23804 | 1.4008 | 0.29297 | 0.2655 | 0.24719 | 0.21973 | 0.07782 | -121.994 | -121.9894 | 0.19684 | 0.17853 | 0.16022 | 0.10071 | 0.082398 | 1.355 | 121.788 | 0.11902 | 0.004578 | 121.9574 | 0 | 122.0032 | 0.07782 | -122.0261 | -121.994 | 121.8338 | 0.082398 | 23.584 | 0.10986
3450.4844 | 122.1313 | -0.086975 | 121.9391 | -0.012131 | 0.0022602 | 0.054282 | 0.053015 | 0.0022943 | -0.0070666 | 0.0001816 | -0.005371 | 0.020608 | 0.040712 | -0.012501 | 0.014471 | 0.026955 | -0.0044797 | 23.5336 | 121.9345 | -0.064087 | 121.7926 | 1.3641 | 0.19684 | 0.25635 | 0.054932 | -0.032043 | -0.013733 | 0.036621 | 0.1831 | 0.15564 | 0.13733 | 0.022888 | -0.004578 | -0.14648 | 1.4511 | 0.34332 | 0.28381 | 0.32044 | 0.26093 | 0.073242 | -121.9711 | -121.9025 | 0.27008 | 0.2243 | 0.24261 | 0.15106 | 0.16937 | 1.4282 | 121.8567 | 0.19684 | 0.050354 | 121.9986 | -0.01831 | 122.0215 | 0.054932 | -122.0032 | -121.9528 | 121.8796 | 0.1236 | 23.6206 | 0.14191
3452.25 | 122.0581 | -0.091553 | 121.994 | -0.0045011 | 0.0043964 | 0.053854 | 0.052374 | -0.0026191 | -0.0092028 | -0.0038772 | -0.005371 | 0.021676 | 0.04114 | -0.011647 | 0.016607 | 0.024391 | -0.0017027 | 23.5657 | 121.9757 | -0.086975 | 121.7377 | 1.2772 | 0.14648 | 0.16479 | -0.004578 | 0.004578 | -0.022888 | -0.018311 | 0.082397 | 0.059509 | 0.086975 | 0.004578 | -0.018311 | -0.25635 | 1.3687 | 0.25635 | 0.23804 | 0.25177 | 0.23346 | 0.068665 | -121.9894 | -122.0123 | 0.17395 | 0.17853 | 0.15106 | 0.10986 | 0.082397 | 1.3641 | 121.8246 | 0.10528 | 0.004577 | 122.0627 | 0.027466 | 122.0673 | 0.096131 | -122.081 | -122.0169 | 121.8292 | 0.073242 | 23.6572 | 0.086975
3453.9531 | 122.1313 | -0.054932 | 121.9391 | -0.0045011 | 0.0016192 | 0.054709 | 0.048529 | -0.0024055 | -0.006853 | -0.0030228 | -0.005371 | 0.021249 | 0.042849 | -0.015278 | 0.01383 | 0.024819 | -0.0036253 | 23.6389 | 121.9254 | -0.045776 | 121.8246 | 1.4328 | 0.25177 | 0.28839 | 0.11902 | -0.045776 | -0.013733 | 0.054932 | 0.18768 | 0.16022 | 0.13733 | 0.009156 | -0.013733 | -0.11444 | 1.4877 | 0.34332 | 0.3067 | 0.33417 | 0.29755 | 0.041199 | -121.9849 | -121.8842 | 0.24261 | 0.19226 | 0.21515 | 0.15106 | 0.17395 | 1.4786 | 121.8704 | 0.20142 | 0.068665 | 121.9711 | -0.032043 | 121.9803 | 0.009156 | -121.9849 | -121.9528 | 121.8796 | 0.10986 | 23.6938 | 0.17395
3455.7188 | 122.1085 | -0.041199 | 121.9482 | -0.01976 | 0.0065326 | 0.056631 | 0.05216 | -0.0017645 | -0.0081348 | -0.0008866 | -0.005371 | 0.020608 | 0.038576 | -0.01421 | 0.014898 | 0.023323 | -0.0046933 | 23.671 | 121.9482 | -0.032043 | 121.8063 | 1.4191 | 0.21057 | 0.27466 | 0.11902 | -0.032043 | 0.013733 | 0.054932 | 0.14648 | 0.11902 | 0.13275 | 0.009156 | 0 | -0.14191 | 1.4603 | 0.31586 | 0.25177 | 0.3067 | 0.24261 | 0.054932 | -121.9803 | -121.8933 | 0.18768 | 0.17395 | 0.16022 | 0.11902 | 0.10529 | 1.4511 | 121.8384 | 0.13275 | 0.041199 | 121.9803 | -0.045776 | 121.9894 | 0.009156 | -121.9803 | -121.9345 | 121.8475 | 0.096131 | 23.7122 | 0.16022
3457.4688 | 122.0764 | -0.068665 | 121.9208 | -0.012131 | 0.0039692 | 0.055777 | 0.05152 | 0.0052851 | -0.006853 | -0.0008866 | -0.0084228 | 0.019754 | 0.040285 | -0.012715 | 0.015539 | 0.0261 | -0.0031979 | 23.6435 | 121.9391 | -0.045776 | 121.756 | 1.3596 | 0.16479 | 0.21057 | 0.018311 | 0 | -0.022888 | 0 | 0.10529 | 0.07782 | 0.09613 | 0.022889 | 0.018311 | -0.16479 | 1.4282 | 0.27924 | 0.23346 | 0.25635 | 0.21057 | 0.045777 | -121.9208 | -121.9208 | 0.17395 | 0.16479 | 0.14649 | 0.11902 | 0.10071 | 1.4053 | 121.8018 | 0.12817 | 0.022888 | 121.9849 | 0.022888 | 122.0078 | 0.068665 | -121.9666 | -121.9437 | 121.8246 | 0.068665 | 23.7122 | 0.086976
3459.1719 | 122.0993 | -0.054932 | 121.9345 | -0.01976 | 0.006319 | 0.054068 | 0.052374 | 0.0014397 | -0.0083484 | -0.0011002 | -0.005371 | 0.02189 | 0.040926 | -0.012715 | 0.015539 | 0.025246 | -0.0044797 | 23.7122 | 121.9391 | -0.036621 | 121.8109 | 1.4603 | 0.21057 | 0.2655 | 0.11444 | -0.018311 | 0.009155 | 0.045776 | 0.16022 | 0.13275 | 0.1236 | 0.018311 | 0.004578 | -0.1236 | 1.5152 | 0.32043 | 0.2655 | 0.30212 | 0.24719 | 0.064087 | -121.9528 | -121.8887 | 0.21515 | 0.17853 | 0.18768 | 0.11444 | 0.1236 | 1.4969 | 121.8475 | 0.15106 | 0.036621 | 121.9757 | -0.027466 | 121.994 | 0.036621 | -121.9711 | -121.9254 | 121.8658 | 0.10071 | 23.7671 | 0.16937
3460.9375 | 121.9986 | -0.091553 | 121.9711 | -0.012131 | 0.0086688 | 0.056418 | 0.055151 | -0.0039007 | -0.0070666 | 0.0003952 | -0.0023192 | 0.02189 | 0.041994 | -0.011433 | 0.016821 | 0.022255 | -0.0055479 | 23.7122 | 121.962 | -0.07782 | 121.7331 | 1.3687 | 0.13733 | 0.17395 | 0.004578 | 0.022888 | -0.041199 | -0.032043 | 0.041199 | 0.018311 | 0.050354 | 0.013733 | -0.009155 | -0.23804 | 1.4603 | 0.2655 | 0.22888 | 0.25177 | 0.21515 | 0.050354 | -121.9482 | -122.0032 | 0.13275 | 0.14191 | 0.10986 | 0.091553 | 0.05951 | 1.4465 | 121.8109 | 0.082398 | 0.009156 | 122.0398 | 0.064087 | 122.0535 | 0.11444 | -122.049 | -122.0123 | 121.8246 | 0.05951 | 23.8037 | 0.096131
3462.6562 | 122.0032 | -0.10986 | 122.0169 | -0.012131 | 0.0031146 | 0.051077 | 0.051733 | -0.0034735 | -0.008562 | -0.0021682 | 0.00073235 | 0.020822 | 0.04114 | -0.014638 | 0.017034 | 0.025032 | -0.0049069 | 23.6801 | 121.9711 | -0.086975 | 121.6827 | 1.3275 | 0.12817 | 0.15564 | -0.064087 | 0.009155 | -0.050354 | -0.07782 | 0.022888 | 0.018311 | 0.041199 | 0.022888 | -0.045777 | -0.33417 | 1.4374 | 0.2655 | 0.23804 | 0.24261 | 0.21515 | 0.059509 | -122.0078 | -122.0947 | 0.13275 | 0.15106 | 0.12817 | 0.091553 | 0.068665 | 1.4145 | 121.7697 | 0.073242 | -0.027466 | 122.0581 | 0.059509 | 122.081 | 0.11902 | -122.1039 | -122.0673 | 121.7926 | 0.032043 | 23.79 | 0.045776
3464.4219 | 122.1222 | -0.050354 | 121.9254 | -0.01976 | 0.0054644 | 0.053214 | 0.05152 | -0.0030463 | -0.0064258 | -0.0047318 | -0.0023192 | 0.020181 | 0.040499 | -0.017628 | 0.015539 | 0.025032 | -0.0025571 | 23.8266 | 121.9528 | -0.027466 | 121.8109 | 1.4969 | 0.22888 | 0.27924 | 0.11902 | -0.013733 | -0.004578 | 0.086975 | 0.16022 | 0.13275 | 0.13275 | 0.022888 | 0.027466 | -0.11444 | 1.5472 | 0.32959 | 0.27924 | 0.3067 | 0.25635 | 0.045776 | -121.9391 | -121.8384 | 0.21057 | 0.18311 | 0.18311 | 0.13733 | 0.13733 | 1.5244 | 121.8384 | 0.16479 | 0.091553 | 121.9803 | -0.009155 | 122.0032 | 0.036621 | -121.9528 | -121.9299 | 121.8613 | 0.13733 | 23.877 | 0.16937
3466.1406 | 122.049 | -0.10071 | 121.9666 | -0.012131 | 0.0043964 | 0.05535 | 0.05451 | 0.0012261 | -0.0049304 | -0.001741 | 0.00073235 | 0.021035 | 0.040071 | -0.0078015 | 0.017034 | 0.023751 | -0.00020725 | 23.8083 | 121.994 | -0.07782 | 121.7377 | 1.4191 | 0.16022 | 0.1831 | 0.027466 | 0.022888 | -0.027466 | -0.004578 | 0.091553 | 0.059509 | 0.064087 | 0.022888 | 0.027466 | -0.22888 | 1.5198 | 0.28381 | 0.26093 | 0.26092 | 0.23804 | 0.073242 | -121.9437 | -121.9711 | 0.19226 | 0.1648 | 0.16022 | 0.091553 | 0.086975 | 1.4969 | 121.8155 | 0.11902 | 0.022888 | 122.0718 | 0.050354 | 122.0947 | 0.1236 | -122.0444 | -121.994 | 121.8384 | 0.09613 | 23.909 | 0.12817
3467.9062 | 122.1268 | -0.064087 | 121.9391 | -0.01976 | 0.0035418 | 0.054282 | 0.049597 | -0.0051825 | -0.0070666 | -0.0008866 | -0.005371 | 0.020395 | 0.041994 | -0.019978 | 0.014684 | 0.026528 | -0.0025571 | 23.8632 | 121.907 | -0.050354 | 121.8246 | 1.5381 | 0.28839 | 0.29297 | 0.11444 | -0.032043 | -0.009155 | 0.054932 | 0.18768 | 0.15564 | 0.13733 | 0.013733 | -0.032044 | -0.11444 | 1.6022 | 0.35706 | 0.35248 | 0.34332 | 0.33875 | 0.054932 | -121.9711 | -121.8842 | 0.25177 | 0.20142 | 0.21973 | 0.14648 | 0.16479 | 1.5884 | 121.875 | 0.19684 | 0.064087 | 121.9574 | -0.022888 | 121.9711 | 0.032044 | -121.9894 | -121.9482 | 121.8887 | 0.11902 | 23.9273 | 0.17853
3469.6562 | 121.9986 | -0.10071 | 121.9711 | -0.0045011 | 0.0069598 | 0.055777 | 0.054724 | 0.0010125 | -0.0057848 | -0.0004592 | -0.0023192 | 0.022317 | 0.039217 | -0.019337 | 0.017248 | 0.025673 | -0.0055479 | 23.8403 | 121.9849 | -0.091553 | 121.6736 | 1.3641 | 0.10529 | 0.13733 | -0.07782 | 0.004578 | -0.045776 | -0.068665 | 0.013733 | -0.018311 | 0.032043 | 0.009155 | 0.013733 | -0.29755 | 1.4648 | 0.23804 | 0.20599 | 0.22888 | 0.19684 | 0.054932 | -121.9666 | -122.0398 | 0.11444 | 0.13275 | 0.082397 | 0.077819 | 0.027465 | 1.4557 | 121.7651 | 0.059509 | -0.022889 | 122.0764 | 0.050354 | 122.0856 | 0.10529 | -122.0627 | -122.0169 | 121.7743 | 0.032043 | 23.941 | 0.022888
3471.375 | 122.1176 | -0.050354 | 121.9299 | -0.012131 | 0.0048236 | 0.054495 | 0.053869 | -0.0017645 | -0.0057848 | -0.0002456 | -0.0084228 | 0.021035 | 0.040499 | -0.013997 | 0.015325 | 0.025246 | -0.00042085 | 23.9456 | 121.9849 | -0.050354 | 121.7789 | 1.5198 | 0.2243 | 0.24261 | 0.091553 | -0.018311 | 0.004578 | 0.045776 | 0.16022 | 0.12817 | 0.15106 | 0 | 0.054931 | -0.15106 | 1.5701 | 0.29297 | 0.27466 | 0.29297 | 0.27466 | 0.054932 | -121.9482 | -121.8842 | 0.21057 | 0.20142 | 0.17853 | 0.14648 | 0.1236 | 1.5701 | 121.8292 | 0.15564 | 0.041198 | 122.0352 | -0.022889 | 122.0352 | 0.032043 | -121.9803 | -121.9254 | 121.8292 | 0.09613 | 23.996 | 0.14191
3473.1406 | 122.0032 | -0.10071 | 121.994 | -0.012131 | 0.002901 | 0.053427 | 0.052588 | 0.00079894 | -0.0087756 | 0.0021042 | -0.0023192 | 0.023172 | 0.039003 | -0.010365 | 0.013616 | 0.025673 | -0.0031979 | 23.9594 | 121.9528 | -0.09613 | 121.6736 | 1.4282 | 0.16022 | 0.16022 | -0.07782 | 0.013733 | -0.054932 | -0.068665 | 0.045776 | 0.018311 | 0.027466 | 0.004578 | -0.041199 | -0.32043 | 1.5289 | 0.26093 | 0.26093 | 0.25635 | 0.25635 | 0.045776 | -121.9803 | -122.0627 | 0.14648 | 0.12817 | 0.11902 | 0.082398 | 0.073243 | 1.5244 | 121.7697 | 0.10071 | -0.013733 | 122.049 | 0.068665 | 122.0535 | 0.11444 | -122.0901 | -122.049 | 121.7743 | 0.032043 | 24.0601 | 0.022888
3474.8438 | 122.113 | -0.036621 | 121.9208 | -0.012131 | 0.006319 | 0.057272 | 0.052374 | 0.00079894 | -0.0072802 | 0.001036 | -0.011475 | 0.020181 | 0.040499 | -0.016347 | 0.015752 | 0.024605 | -0.0038389 | 24.0784 | 121.9437 | -0.041199 | 121.7834 | 1.5884 | 0.25177 | 0.28839 | 0.12817 | -0.027466 | 0.004578 | 0.054932 | 0.15564 | 0.14191 | 0.14191 | -0.004578 | 0.022889 | -0.13733 | 1.6251 | 0.32501 | 0.28839 | 0.32959 | 0.29297 | 0.041199 | -121.9482 | -121.8658 | 0.19226 | 0.17853 | 0.17853 | 0.13733 | 0.13733 | 1.6296 | 121.8246 | 0.15106 | 0.050354 | 121.9849 | -0.032044 | 121.9803 | 0.009155 | -121.962 | -121.9162 | 121.8201 | 0.091553 | 24.115 | 0.1648
3476.6094 | 122.0444 | -0.082397 | 121.9803 | -0.012131 | 0.0056782 | 0.052359 | 0.053442 | -0.0015509 | -0.0087756 | 0.0014634 | -0.005371 | 0.022958 | 0.04114 | -0.010792 | 0.015966 | 0.024391 | -0.00042085 | 24.1013 | 121.9711 | -0.073242 | 121.7377 | 1.4923 | 0.19684 | 0.20599 | 0 | 0.013733 | -0.018311 | -0.022888 | 0.10071 | 0.059509 | 0.068665 | 0.009155 | -0.009156 | -0.24262 | 1.5747 | 0.28839 | 0.27924 | 0.27924 | 0.27008 | 0.064086 | -121.9666 | -122.0032 | 0.18311 | 0.15106 | 0.14191 | 0.086976 | 0.07782 | 1.5656 | 121.8109 | 0.11902 | -0.004577 | 122.0444 | 0.032044 | 122.0535 | 0.09613 | -122.0535 | -121.9986 | 121.8201 | 0.059509 | 24.1837 | 0.082397
3478.375 | 122.081 | -0.073242 | 121.962 | -0.012131 | 0.0035418 | 0.055563 | 0.05152 | -0.0024055 | -0.0070666 | -0.0011002 | -0.005371 | 0.018045 | 0.040499 | -0.025319 | 0.014043 | 0.024819 | -0.0044797 | 24.1791 | 121.9574 | -0.059509 | 121.7377 | 1.5564 | 0.21973 | 0.25635 | -0.004578 | -0.009155 | -0.022888 | -0.009155 | 0.10986 | 0.086975 | 0.091553 | 0.013733 | -0.004578 | -0.2243 | 1.6296 | 0.32959 | 0.29297 | 0.31586 | 0.27924 | 0.050354 | -121.9711 | -121.9711 | 0.18311 | 0.16479 | 0.16022 | 0.11444 | 0.10986 | 1.6159 | 121.7972 | 0.13275 | 0.013733 | 122.0169 | 0.013733 | 122.0306 | 0.064087 | -122.0215 | -121.9849 | 121.8109 | 0.064087 | 24.2523 | 0.068664
3480.0781 | 122.0535 | -0.073242 | 121.9574 | -0.0045011 | 0.0067462 | 0.054282 | 0.055151 | 0.00015814 | -0.0079212 | -0.0008866 | -0.005371 | 0.02189 | 0.038362 | -0.010579 | 0.014471 | 0.02311 | -0.0023435 | 24.2111 | 121.962 | -0.073242 | 121.6965 | 1.4969 | 0.13733 | 0.19684 | -0.009155 | 0 | -0.045776 | -0.009155 | 0.073242 | 0.045776 | 0.082397 | 0 | 0.004578 | -0.26093 | 1.5701 | 0.27008 | 0.21057 | 0.27008 | 0.21057 | 0.027466 | -121.9574 | -121.9666 | 0.14648 | 0.15564 | 0.11902 | 0.12817 | 0.091552 | 1.5701 | 121.7697 | 0.11902 | 0.036621 | 122.0352 | 0.045776 | 122.0352 | 0.073242 | -122.0306 | -122.0032 | 121.7697 | 0.064087 | 24.2844 | 0.064087
3481.8438 | 122.049 | -0.086975 | 121.9849 | -0.0045011 | 0.0073872 | 0.053641 | 0.05451 | 0.0046441 | -0.0081348 | -0.0030228 | -0.005371 | 0.022958 | 0.042208 | -0.0097241 | 0.014898 | 0.022683 | -0.0044797 | 24.3347 | 121.9437 | -0.086975 | 121.7377 | 1.5701 | 0.19684 | 0.2243 | 0.018311 | 0.027466 | -0.036621 | -0.013733 | 0.09613 | 0.045776 | 0.07782 | 0 | -0.041198 | -0.24719 | 1.6571 | 0.31128 | 0.28381 | 0.31128 | 0.28381 | 0.050354 | -121.9574 | -121.9986 | 0.1831 | 0.16479 | 0.13275 | 0.11444 | 0.082397 | 1.6571 | 121.8246 | 0.13275 | 0.022888 | 122.0306 | 0.064087 | 122.0306 | 0.11444 | -122.0718 | -122.0215 | 121.8246 | 0.073242 | 24.4217 | 0.10529
3483.6094 | 122.0215 | -0.10071 | 121.9849 | -0.0045011 | 0.0037556 | 0.053641 | 0.054724 | -0.00026906 | -0.0072802 | -0.0021682 | -0.0084228 | 0.021463 | 0.040926 | -0.012715 | 0.015966 | 0.024178 | -0.0025571 | 24.3896 | 121.9849 | -0.086975 | 121.6827 | 1.5244 | 0.16479 | 0.17853 | -0.059509 | 0.022888 | -0.022888 | -0.07782 | 0.045776 | 0.032043 | 0.050354 | 0.013733 | 0 | -0.30212 | 1.6251 | 0.27924 | 0.2655 | 0.2655 | 0.25177 | 0.07782 | -121.962 | -122.0627 | 0.14648 | 0.15106 | 0.13275 | 0.073242 | 0.054931 | 1.6113 | 121.7697 | 0.068664 | -0.054932 | 122.0718 | 0.045776 | 122.0856 | 0.1236 | -122.0718 | -122.0078 | 121.7834 | 0.022888 | 24.4904 | 0.041199
3485.3125 | 122.113 | -0.059509 | 121.9528 | -0.012131 | 0.0065326 | 0.053427 | 0.055151 | -5.5462e-05 | -0.0072802 | -0.0008866 | -0.0023192 | 0.021249 | 0.040499 | -0.011647 | 0.015325 | 0.023537 | -0.0021299 | 24.472 | 121.9666 | -0.07782 | 121.7285 | 1.593 | 0.18768 | 0.24261 | 0.036621 | 0.004578 | -0.022888 | 0.050354 | 0.13733 | 0.10529 | 0.1236 | -0.018311 | 0.013733 | -0.2243 | 1.6525 | 0.30212 | 0.24719 | 0.32044 | 0.2655 | 0.036621 | -121.9482 | -121.9025 | 0.19684 | 0.1831 | 0.16479 | 0.14648 | 0.12817 | 1.6708 | 121.8063 | 0.16022 | 0.073242 | 122.0444 | 0.027466 | 122.0261 | 0.064087 | -122.0306 | -121.9757 | 121.788 | 0.10986 | 24.5316 | 0.09613
3487.0938 | 122.113 | -0.064087 | 121.9437 | -0.01976 | 0.0058918 | 0.054495 | 0.054297 | 0.0010125 | -0.0045032 | 0.0006088 | -0.005371 | 0.019754 | 0.039217 | -0.013997 | 0.015752 | 0.025887 | -0.0034117 | 24.5865 | 121.9803 | -0.054932 | 121.7468 | 1.6342 | 0.21973 | 0.2655 | 0.050354 | -0.004578 | -0.018311 | 0.054932 | 0.13733 | 0.10529 | 0.13275 | 0.009155 | 0.036621 | -0.19684 | 1.6983 | 0.32959 | 0.28381 | 0.32043 | 0.27466 | 0.045776 | -121.9482 | -121.8887 | 0.20142 | 0.19684 | 0.16937 | 0.15106 | 0.1236 | 1.6891 | 121.8018 | 0.15564 | 0.073243 | 122.0352 | 0.013733 | 122.0444 | 0.059509 | -121.9986 | -121.962 | 121.8109 | 0.11902 | 24.6506 | 0.11444
3488.8594 | 122.0032 | -0.12817 | 121.994 | -0.012131 | 0.0037556 | 0.053214 | 0.053015 | -0.00091006 | -0.0083484 | -0.0013138 | -0.005371 | 0.022317 | 0.039431 | -0.0097241 | 0.013189 | 0.021401 | -0.0029843 | 24.6231 | 121.9803 | -0.082397 | 121.669 | 1.5884 | 0.20142 | 0.20599 | -0.068665 | 0.018311 | -0.036621 | -0.07782 | 0.027466 | 0.022888 | 0.027466 | 0.045777 | -0.013733 | -0.32501 | 1.7166 | 0.33417 | 0.32959 | 0.28839 | 0.28381 | 0.091553 | -121.9757 | -122.0718 | 0.15564 | 0.15564 | 0.15106 | 0.064087 | 0.059509 | 1.6708 | 121.7514 | 0.064087 | -0.041199 | 122.0627 | 0.054932 | 122.1085 | 0.14649 | -122.0764 | -122.0306 | 121.7972 | 0.050354 | 24.7513 | 0.059509
3490.5625 | 122.0352 | -0.10529 | 121.9757 | -0.0045011 | 0.0022602 | 0.053641 | 0.050451 | 0.0033623 | -0.0079212 | -0.0013138 | -0.0084228 | 0.020181 | 0.037935 | -0.022755 | 0.014471 | 0.023537 | -0.0046933 | 24.7971 | 121.9574 | -0.073242 | 121.7331 | 1.6617 | 0.26093 | 0.2655 | -0.022888 | -0.013733 | -0.027466 | -0.054932 | 0.059509 | 0.045776 | 0.022888 | 0.032044 | -0.018311 | -0.24262 | 1.767 | 0.37079 | 0.36621 | 0.33874 | 0.33417 | 0.07782 | -121.9894 | -122.0306 | 0.16479 | 0.12817 | 0.15106 | 0.050354 | 0.073242 | 1.7349 | 121.8063 | 0.086975 | -0.027466 | 122.0306 | 0.013733 | 122.0627 | 0.091553 | -122.0489 | -122.0032 | 121.8384 | 0.050354 | 24.9023 | 0.082398
3492.3281 | 122.1359 | -0.064087 | 121.9482 | -0.01976 | 0.0020466 | 0.054282 | 0.048742 | 0.0044305 | -0.008562 | -0.0036636 | -0.005371 | 0.021035 | 0.038362 | -0.016774 | 0.014471 | 0.0261 | -0.0034117 | 24.939 | 121.907 | -0.045776 | 121.8292 | 1.8265 | 0.34332 | 0.35706 | 0.13733 | -0.041199 | -0.004578 | 0.041199 | 0.19226 | 0.16022 | 0.12817 | 0.018311 | -0.041199 | -0.11902 | 1.8906 | 0.42114 | 0.40741 | 0.40283 | 0.3891 | 0.059509 | -121.9894 | -121.907 | 0.25635 | 0.19226 | 0.2243 | 0.13275 | 0.16479 | 1.8723 | 121.875 | 0.19684 | 0.045777 | 121.9528 | -0.036621 | 121.9711 | 0.022888 | -121.994 | -121.9528 | 121.8933 | 0.10529 | 25.0031 | 0.20142
3494.0312 | 122.1039 | -0.050354 | 121.9345 | -0.0045011 | 0.0043964 | 0.054709 | 0.053869 | -0.0017645 | -0.0072802 | -0.0021682 | -0.005371 | 0.020181 | 0.041567 | -0.012715 | 0.016393 | 0.024605 | -0.0044797 | 25.0443 | 121.9162 | -0.041199 | 121.8063 | 1.7944 | 0.29755 | 0.33875 | 0.12817 | -0.041199 | -0.004578 | 0.054932 | 0.14648 | 0.1236 | 0.11902 | 0.009155 | -0.01831 | -0.12817 | 1.8448 | 0.3891 | 0.3479 | 0.37994 | 0.33874 | 0.045776 | -121.9757 | -121.8796 | 0.19684 | 0.16937 | 0.17395 | 0.1236 | 0.12817 | 1.8356 | 121.8475 | 0.15106 | 0.05951 | 121.9574 | -0.036621 | 121.9666 | 0.009155 | -121.9757 | -121.9391 | 121.8567 | 0.10529 | 25.0946 | 0.17853
3495.7969 | 122.0901 | -0.07782 | 121.9437 | -0.01976 | 0.0039692 | 0.054709 | 0.051306 | 0.0012261 | -0.0070666 | 0.0003952 | -0.0023192 | 0.023385 | 0.039431 | -0.013783 | 0.014043 | 0.024605 | -0.0012753 | 25.1083 | 121.907 | -0.059509 | 121.7285 | 1.7487 | 0.25635 | 0.29297 | 0.013733 | 0.004578 | -0.018311 | -0.004578 | 0.11902 | 0.09613 | 0.10071 | 0.018311 | -0.036622 | -0.21515 | 1.8265 | 0.37079 | 0.33417 | 0.35248 | 0.31586 | 0.059509 | -121.9391 | -121.9482 | 0.19684 | 0.17853 | 0.17395 | 0.11902 | 0.11444 | 1.8082 | 121.788 | 0.13733 | 0.013733 | 121.9666 | 0.022889 | 121.9849 | 0.082398 | -122.0032 | -121.962 | 121.8063 | 0.073242 | 25.1862 | 0.091553
3497.5781 | 121.9894 | -0.11902 | 121.9849 | -0.0045011 | 0.0056782 | 0.056418 | 0.054297 | 0.0018671 | -0.0079212 | -0.0002456 | -0.005371 | 0.021676 | 0.040499 | -0.013569 | 0.017675 | 0.023751 | -0.0017027 | 25.2274 | 121.9986 | -0.086975 | 121.6599 | 1.6479 | 0.13733 | 0.17395 | -0.064087 | 0.022888 | -0.054932 | -0.054932 | 0.004578 | -0.032043 | 0.022888 | 0.032044 | 0.013733 | -0.32501 | 1.767 | 0.29297 | 0.25635 | 0.26092 | 0.2243 | 0.064087 | -121.962 | -122.0398 | 0.1236 | 0.14191 | 0.086976 | 0.07782 | 0.022889 | 1.7349 | 121.7468 | 0.05951 | 0 | 122.0856 | 0.07782 | 122.1176 | 0.14191 | -122.0718 | -122.0398 | 121.7789 | 0.064087 | 25.3464 | 0.054932
3499.3438 | 122.081 | -0.059509 | 121.9437 | -0.012131 | 0.0065326 | 0.057272 | 0.053015 | 0.0048577 | -0.0081348 | -0.0008866 | 0.00073235 | 0.020608 | 0.040499 | -0.014638 | 0.014471 | 0.023751 | -0.0061887 | 25.4471 | 121.9391 | -0.032043 | 121.7651 | 1.8585 | 0.27924 | 0.33875 | 0.09613 | -0.032043 | -0.009155 | 0.022888 | 0.12817 | 0.10529 | 0.10529 | 0.027466 | -0.004578 | -0.17853 | 1.918 | 0.39825 | 0.33874 | 0.37079 | 0.31128 | 0.050354 | -121.9757 | -121.9208 | 0.18768 | 0.16479 | 0.16479 | 0.11444 | 0.11444 | 1.8906 | 121.7972 | 0.13733 | 0.032043 | 121.9711 | -0.022888 | 121.9986 | 0.027466 | -121.9757 | -121.9528 | 121.8246 | 0.082397 | 25.5066 | 0.15564
3501.0625 | 121.9986 | -0.10529 | 121.9803 | -0.012131 | 0.0035418 | 0.053 | 0.051733 | -0.0021919 | -0.008562 | -0.000673 | -0.0023192 | 0.02189 | 0.042635 | -0.012074 | 0.016607 | 0.022896 | -0.0042661 | 25.4379 | 121.9666 | -0.091553 | 121.6644 | 1.7303 | 0.20599 | 0.23804 | -0.059509 | 0.032043 | -0.041199 | -0.082397 | 0.032043 | 0.013733 | 0.022888 | 0.013733 | -0.013733 | -0.31586 | 1.8356 | 0.34332 | 0.31128 | 0.32959 | 0.29755 | 0.064087 | -121.9482 | -122.0627 | 0.13733 | 0.12817 | 0.11902 | 0.064087 | 0.054932 | 1.8219 | 121.756 | 0.073242 | -0.041198 | 122.0581 | 0.073242 | 122.0718 | 0.13733 | -122.0718 | -122.0215 | 121.7697 | 0.022889 | 25.5432 | 0.045777
3502.8281 | 122.0673 | -0.09613 | 121.9574 | -0.0045011 | 0.0054644 | 0.055777 | 0.055792 | 0.0025079 | -0.006853 | -0.002382 | -0.005371 | 0.02189 | 0.040499 | -0.012074 | 0.01618 | 0.024605 | -0.0029843 | 25.8041 | 122.0169 | -0.068665 | 121.6965 | 1.7899 | 0.21057 | 0.23804 | 0 | -0.004578 | -0.022888 | -0.013733 | 0.073242 | 0.054932 | 0.073242 | 0.027465 | 0.05951 | -0.26093 | 1.886 | 0.33417 | 0.3067 | 0.3067 | 0.27924 | 0.073242 | -121.962 | -121.9711 | 0.16937 | 0.16937 | 0.15106 | 0.09613 | 0.07782 | 1.8585 | 121.7651 | 0.09613 | 0.009155 | 122.0856 | 0.01831 | 122.113 | 0.091552 | -122.0261 | -121.9803 | 121.7926 | 0.082397 | 25.9003 | 0.09613
3504.5938 | 122.1268 | -0.07782 | 121.9299 | -0.01976 | 0.0048236 | 0.056845 | 0.05152 | 0.00015814 | -0.0083484 | -0.0030228 | -0.005371 | 0.018899 | 0.041353 | -0.016987 | 0.012975 | 0.026741 | -0.0076841 | 26.1337 | 121.9299 | -0.036621 | 121.8246 | 1.9913 | 0.3479 | 0.39368 | 0.10986 | -0.027466 | 0 | 0.059509 | 0.20599 | 0.16479 | 0.14648 | 0.041199 | 0 | -0.10529 | 2.0691 | 0.4715 | 0.42572 | 0.4303 | 0.38452 | 0.07782 | -121.9574 | -121.8704 | 0.28381 | 0.2243 | 0.24261 | 0.14648 | 0.16479 | 2.0279 | 121.8613 | 0.20599 | 0.059509 | 121.9666 | -0.027466 | 122.0078 | 0.050354 | -121.9666 | -121.9299 | 121.9025 | 0.13733 | 26.2115 | 0.18768
3506.3594 | 122.1359 | -0.073242 | 121.9254 | -0.012131 | 0.0035418 | 0.054282 | 0.051306 | -0.00026906 | -0.0074938 | -0.0025956 | -0.0023192 | 0.020608 | 0.040071 | -0.013142 | 0.015752 | 0.025246 | -0.0059751 | 26.358 | 121.9116 | -0.045776 | 121.8155 | 2.0096 | 0.39825 | 0.39368 | 0.11902 | -0.018311 | -0.009155 | 0.059509 | 0.19684 | 0.15564 | 0.13275 | 0.027466 | -0.013733 | -0.10986 | 2.0828 | 0.46692 | 0.4715 | 0.43945 | 0.44403 | 0.064087 | -121.9437 | -121.8658 | 0.27008 | 0.20599 | 0.22888 | 0.14191 | 0.16479 | 2.0554 | 121.8613 | 0.20599 | 0.068664 | 121.9574 | -0.009156 | 121.9849 | 0.054931 | -121.9711 | -121.9345 | 121.8887 | 0.13275 | 26.4313 | 0.19226
3508.0625 | 122.1222 | -0.050354 | 121.9345 | -0.02739 | 0.0084552 | 0.056204 | 0.053656 | 0.0025079 | -0.0092028 | 0.0008224 | -0.0023192 | 0.022103 | 0.037935 | -0.012501 | 0.015325 | 0.023964 | -0.0055479 | 26.5823 | 121.9437 | -0.045776 | 121.7972 | 2.0096 | 0.32501 | 0.35706 | 0.10986 | -0.022888 | -0.004578 | 0.082397 | 0.16479 | 0.10986 | 0.14191 | 0.004578 | 0.009156 | -0.13733 | 2.0599 | 0.40741 | 0.37537 | 0.40283 | 0.37079 | 0.045776 | -121.9574 | -121.8521 | 0.21515 | 0.19226 | 0.16022 | 0.14649 | 0.11444 | 2.0554 | 121.843 | 0.16937 | 0.086975 | 121.9894 | -0.01831 | 121.994 | 0.027466 | -121.9803 | -121.9391 | 121.8475 | 0.13275 | 26.6327 | 0.16022
3509.8281 | 122.0764 | -0.086975 | 121.9345 | -0.0045011 | 0.0056782 | 0.056631 | 0.052801 | -0.0013373 | -0.0049304 | 0.001677 | -0.005371 | 0.019113 | 0.040499 | -0.015065 | 0.015325 | 0.024178 | -0.00063445 | 26.7151 | 121.9162 | -0.041199 | 121.7468 | 1.9684 | 0.28839 | 0.32959 | 0.004578 | -0.022888 | -0.018311 | -0.009155 | 0.11902 | 0.073242 | 0.082397 | 0.045776 | -0.01831 | -0.18768 | 2.0554 | 0.41656 | 0.37537 | 0.37079 | 0.32959 | 0.068664 | -121.9574 | -121.9437 | 0.20599 | 0.16937 | 0.16022 | 0.10071 | 0.091553 | 2.0096 | 121.788 | 0.13733 | 0.009156 | 121.9574 | -0.004577 | 122.0032 | 0.064087 | -121.9757 | -121.9528 | 121.8338 | 0.07782 | 26.8021 | 0.091553
3511.5469 | 122.0581 | -0.091553 | 121.962 | -0.012131 | 0.0039692 | 0.054068 | 0.053442 | 0.0018671 | -0.0077074 | -0.0011002 | -0.0023192 | 0.019754 | 0.04178 | -0.019551 | 0.013616 | 0.025673 | -0.00020725 | 26.9394 | 121.9391 | -0.054932 | 121.7514 | 2.0004 | 0.29755 | 0.34332 | 0.013733 | -0.004578 | -0.022888 | 0 | 0.09613 | 0.086975 | 0.086975 | 0.036621 | -0.022888 | -0.21057 | 2.092 | 0.43488 | 0.3891 | 0.39825 | 0.35248 | 0.068665 | -121.9666 | -121.962 | 0.18768 | 0.17853 | 0.17853 | 0.10986 | 0.10986 | 2.0554 | 121.8063 | 0.11902 | 0.022888 | 121.994 | 0.01831 | 122.0306 | 0.086975 | -122.0169 | -121.9849 | 121.843 | 0.091553 | 27.0309 | 0.10529
3513.3125 | 121.9986 | -0.10986 | 121.9849 | -0.012131 | 0.0048236 | 0.054495 | 0.053442 | 0.00015814 | -0.0070666 | -0.0021682 | -0.0084228 | 0.020395 | 0.04114 | -0.017628 | 0.014684 | 0.02311 | -0.0057615 | 27.2186 | 121.9299 | -0.059509 | 121.7331 | 2.0279 | 0.28839 | 0.32044 | -0.013733 | 0.009155 | -0.045776 | -0.059509 | 0.064087 | 0.022888 | 0.032043 | 0.050354 | -0.054931 | -0.25177 | 2.1378 | 0.4303 | 0.39825 | 0.37994 | 0.3479 | 0.064087 | -121.9757 | -122.0444 | 0.17395 | 0.14191 | 0.13275 | 0.077819 | 0.068664 | 2.0874 | 121.7926 | 0.10986 | -0.013733 | 121.9894 | 0.054931 | 122.0398 | 0.11902 | -122.0444 | -122.0306 | 121.843 | 0.050354 | 27.3285 | 0.09613
3515.0781 | 122.0123 | -0.11444 | 121.9849 | -0.012131 | 0.006319 | 0.051932 | 0.053228 | -0.0026191 | -0.0094164 | -0.0019546 | -0.005371 | 0.021035 | 0.040926 | -0.014424 | 0.014684 | 0.023537 | -0.0019163 | 27.4887 | 121.9345 | -0.059509 | 121.7422 | 2.0782 | 0.31586 | 0.3479 | -0.009155 | 0.004578 | -0.032043 | -0.064087 | 0.059509 | 0.036621 | 0.050354 | 0.054932 | -0.050354 | -0.24261 | 2.1927 | 0.46234 | 0.4303 | 0.40741 | 0.37537 | 0.082398 | -121.9803 | -122.049 | 0.17395 | 0.16479 | 0.15106 | 0.082397 | 0.068664 | 2.1378 | 121.8018 | 0.091552 | -0.032044 | 121.994 | 0.036621 | 122.049 | 0.11902 | -122.0444 | -122.0169 | 121.8567 | 0.050354 | 27.6031 | 0.10529
3516.8594 | 122.0215 | -0.09613 | 122.0032 | -0.012131 | 0.0058918 | 0.056418 | 0.055151 | 0.0012261 | -0.0049304 | 0.0003952 | -0.0084228 | 0.023599 | 0.040499 | -0.0069469 | 0.017461 | 0.022896 | -0.0049069 | 27.7359 | 121.9482 | -0.073242 | 121.7468 | 2.1103 | 0.29297 | 0.31586 | 0.045776 | 0.022888 | -0.032043 | 0.009155 | 0.086975 | 0.045776 | 0.068665 | 0.022888 | -0.054932 | -0.25635 | 2.2064 | 0.41199 | 0.3891 | 0.3891 | 0.36621 | 0.064087 | -121.9803 | -121.994 | 0.1831 | 0.16479 | 0.14191 | 0.10071 | 0.077819 | 2.1835 | 121.8201 | 0.11902 | 0.041198 | 122.0215 | 0.054931 | 122.0444 | 0.11902 | -122.0764 | -122.0352 | 121.843 | 0.10528 | 27.832 | 0.14191
3518.5625 | 122.0306 | -0.091553 | 121.9849 | 0.0031279 | 0.008028 | 0.054495 | 0.053015 | -0.0011237 | -0.0053576 | -0.0015274 | 0.00073235 | 0.021676 | 0.040071 | -0.012288 | 0.015966 | 0.025887 | -0.0021299 | 28.038 | 121.994 | -0.068665 | 121.7285 | 2.1332 | 0.29755 | 0.3067 | 0.009155 | 0.009155 | -0.032043 | -0.013733 | 0.09613 | 0.054932 | 0.082397 | 0.022888 | 0.009156 | -0.25635 | 2.2247 | 0.39825 | 0.3891 | 0.37537 | 0.36621 | 0.05951 | -121.9757 | -121.9986 | 0.18768 | 0.17395 | 0.14649 | 0.11444 | 0.086975 | 2.2018 | 121.7972 | 0.12817 | 0.01831 | 122.0627 | 0.041198 | 122.0856 | 0.10071 | -122.0535 | -122.0169 | 121.8201 | 0.07782 | 28.1296 | 0.10071
3520.3281 | 122.1176 | -0.068665 | 121.9345 | 0.0031279 | 0.0033282 | 0.054922 | 0.049383 | -0.0045417 | -0.0077074 | 0.0006088 | -0.0023192 | 0.019754 | 0.040285 | -0.01656 | 0.014684 | 0.024605 | -0.0019163 | 28.3081 | 121.9299 | -0.054932 | 121.7697 | 2.2476 | 0.36621 | 0.41657 | 0.082397 | -0.045776 | -0.013733 | 0.045776 | 0.17395 | 0.17395 | 0.13733 | 0.013733 | -0.004577 | -0.1648 | 2.3163 | 0.48523 | 0.43488 | 0.4715 | 0.42114 | 0.054932 | -121.9803 | -121.8887 | 0.24261 | 0.20599 | 0.24261 | 0.15106 | 0.18768 | 2.3026 | 121.8246 | 0.18768 | 0.059509 | 121.9849 | -0.032043 | 121.9986 | 0.022889 | -121.9894 | -121.9482 | 121.8384 | 0.11444 | 28.3768 | 0.15106
3522.0469 | 122.1039 | -0.054932 | 121.9711 | -0.01976 | 0.0048236 | 0.054068 | 0.052588 | 0.00015814 | -0.0055712 | 0.0014634 | -0.005371 | 0.018899 | 0.039217 | -0.017842 | 0.012548 | 0.024178 | -0.0014891 | 28.624 | 121.9025 | -0.041199 | 121.8109 | 2.3163 | 0.39368 | 0.42114 | 0.10529 | -0.013733 | -0.009155 | 0.045776 | 0.16937 | 0.14648 | 0.13733 | 0.013733 | -0.068664 | -0.16022 | 2.3712 | 0.47607 | 0.44861 | 0.46234 | 0.43488 | 0.045777 | -121.9849 | -121.9254 | 0.22431 | 0.19226 | 0.20142 | 0.14648 | 0.15564 | 2.3575 | 121.8521 | 0.17853 | 0.054931 | 121.9437 | -0.004578 | 121.9574 | 0.041199 | -122.0123 | -121.9803 | 121.8658 | 0.10071 | 28.6789 | 0.16022
3523.8125 | 121.9711 | -0.11444 | 121.994 | -0.01976 | 0.0099506 | 0.056845 | 0.056219 | 0.0022943 | -0.0055712 | 0.0001816 | -0.0023192 | 0.022531 | 0.040926 | -0.010151 | 0.015325 | 0.022469 | -0.0053343 | 28.8986 | 121.9849 | -0.086975 | 121.6965 | 2.2018 | 0.23804 | 0.2655 | -0.064087 | 0.013733 | -0.045776 | -0.068665 | 0.013733 | -0.018311 | 0.022888 | 0.027466 | -0.009156 | -0.29755 | 2.3163 | 0.37994 | 0.35248 | 0.35248 | 0.32501 | 0.068665 | -121.9803 | -122.0627 | 0.12817 | 0.13733 | 0.09613 | 0.068664 | 0.027465 | 2.2888 | 121.7834 | 0.059509 | -0.022889 | 122.0718 | 0.059509 | 122.0993 | 0.12817 | -122.081 | -122.0398 | 121.8109 | 0.045776 | 29.0131 | 0.050354
3525.5781 | 122.0581 | -0.07782 | 121.9437 | -0.012131 | 0.0033282 | 0.054282 | 0.054083 | 0.00015814 | -0.0066394 | 0.001677 | -0.005371 | 0.022317 | 0.039431 | -0.014424 | 0.017034 | 0.025673 | -0.0031979 | 29.2831 | 121.907 | -0.027466 | 121.7926 | 2.3987 | 0.39825 | 0.4303 | 0.068665 | -0.013733 | -0.009155 | 0.018311 | 0.13733 | 0.10986 | 0.091553 | 0.050354 | -0.036622 | -0.15106 | 2.4765 | 0.50812 | 0.47607 | 0.45776 | 0.42572 | 0.068665 | -121.9574 | -121.9254 | 0.21515 | 0.16937 | 0.18768 | 0.10071 | 0.11902 | 2.4261 | 121.8201 | 0.14648 | 0.027466 | 121.9345 | -0.004578 | 121.9849 | 0.064087 | -121.9711 | -121.9528 | 121.8704 | 0.096131 | 29.361 | 0.14649
3527.3594 | 122.1176 | -0.064087 | 121.9208 | -0.012131 | 0.0073872 | 0.056204 | 0.053442 | -0.0034735 | -0.0070666 | -0.0004592 | -0.005371 | 0.021035 | 0.039644 | -0.022542 | 0.013189 | 0.024605 | -0.0019163 | 29.7958 | 121.9391 | -0.041199 | 121.8063 | 2.449 | 0.38452 | 0.42572 | 0.11902 | -0.018311 | 0 | 0.073242 | 0.15564 | 0.1236 | 0.12817 | 0.022888 | 0.018311 | -0.11444 | 2.5131 | 0.48981 | 0.44861 | 0.46692 | 0.42572 | 0.064087 | -121.9391 | -121.8475 | 0.21973 | 0.19226 | 0.18768 | 0.12817 | 0.1236 | 2.4902 | 121.8475 | 0.15564 | 0.073242 | 121.9803 | -0.018311 | 122.0032 | 0.045776 | -121.962 | -121.9208 | 121.8704 | 0.13733 | 29.8599 | 0.18311
3529.0625 | 121.9849 | -0.12817 | 121.994 | -0.012131 | 0.0078144 | 0.057486 | 0.056433 | -0.0017645 | -0.0059986 | -0.0028092 | -0.0023192 | 0.022958 | 0.041353 | -0.013356 | 0.016821 | 0.021828 | -0.0034117 | 30.0613 | 121.9711 | -0.068665 | 121.6873 | 2.33 | 0.26093 | 0.28381 | -0.068665 | 0.032043 | -0.032043 | -0.086975 | 0.009155 | -0.027466 | 0.036621 | 0.059509 | -0.022889 | -0.3067 | 2.4582 | 0.41199 | 0.3891 | 0.35248 | 0.32959 | 0.096131 | -121.962 | -122.081 | 0.13733 | 0.1648 | 0.10071 | 0.068664 | 0.004577 | 2.3987 | 121.756 | 0.041198 | -0.054932 | 122.0398 | 0.064086 | 122.0993 | 0.16022 | -122.0627 | -122.0261 | 121.8155 | 0.041199 | 30.1895 | 0.059509
3530.8438 | 122.0352 | -0.09613 | 121.9849 | -0.0045011 | 0.008028 | 0.055777 | 0.054724 | -0.00091006 | -0.0070666 | 0.0001816 | -0.0084228 | 0.022531 | 0.041353 | -0.012929 | 0.015752 | 0.023751 | -0.0046933 | 30.4321 | 121.9711 | -0.082397 | 121.7056 | 2.4078 | 0.33875 | 0.34332 | -0.032043 | 0.009155 | -0.041199 | -0.018311 | 0.091553 | 0.064087 | 0.068665 | 0.013733 | -0.013733 | -0.27924 | 2.504 | 0.43945 | 0.43488 | 0.42572 | 0.42114 | 0.054931 | -121.9757 | -122.0032 | 0.18768 | 0.16479 | 0.16022 | 0.10986 | 0.10529 | 2.4902 | 121.788 | 0.13275 | 0.022888 | 122.0535 | 0.050354 | 122.0673 | 0.10528 | -122.0673 | -122.0261 | 121.8018 | 0.077819 | 30.5283 | 0.064087
3532.625 | 122.1222 | -0.059509 | 121.9437 | -0.01976 | 0.0058918 | 0.05535 | 0.048529 | 0.0027215 | -0.0062122 | -0.0019546 | -0.0084228 | 0.019326 | 0.041994 | -0.015278 | 0.015752 | 0.026955 | -0.0034117 | 30.8166 | 121.9025 | -0.041199 | 121.8109 | 2.6321 | 0.46234 | 0.45319 | 0.10529 | -0.027466 | 0 | 0.059509 | 0.19226 | 0.16479 | 0.12817 | 0.01831 | -0.041199 | -0.13275 | 2.6916 | 0.5127 | 0.52185 | 0.49438 | 0.50354 | 0.059509 | -121.9711 | -121.8842 | 0.25177 | 0.18768 | 0.2243 | 0.12817 | 0.16479 | 2.6733 | 121.8521 | 0.19226 | 0.059509 | 121.9437 | -0.027466 | 121.962 | 0.032043 | -121.9849 | -121.9437 | 121.8704 | 0.11902 | 30.8762 | 0.16479
3534.3281 | 122.0718 | -0.073242 | 121.9482 | -0.01976 | 0.0054644 | 0.055136 | 0.053656 | 0.00015814 | -0.0072802 | -0.0025956 | -0.005371 | 0.021035 | 0.040071 | -0.020192 | 0.013403 | 0.024819 | -0.0031979 | 31.041 | 121.9345 | -0.054932 | 121.7468 | 2.5497 | 0.3891 | 0.39368 | 0.009155 | -0.018311 | -0.013733 | -0.004578 | 0.11902 | 0.086975 | 0.086975 | 0.01831 | -0.013733 | -0.20142 | 2.623 | 0.46692 | 0.46234 | 0.44861 | 0.44403 | 0.059509 | -121.9666 | -121.9528 | 0.19226 | 0.16022 | 0.16022 | 0.10071 | 0.10071 | 2.6047 | 121.8018 | 0.13275 | 0.009155 | 121.9894 | -0.004578 | 122.0078 | 0.054931 | -122.0032 | -121.962 | 121.8201 | 0.068664 | 31.1142 | 0.082397
3536.0781 | 121.9894 | -0.10986 | 121.9894 | -0.01976 | 0.0031146 | 0.055563 | 0.052588 | 0.0027215 | -0.0062122 | -0.0011002 | -0.0084228 | 0.02189 | 0.042421 | -0.010579 | 0.01383 | 0.024391 | -0.0064023 | 31.2973 | 121.9345 | -0.07782 | 121.6827 | 2.5497 | 0.33875 | 0.36163 | -0.050354 | 0.036621 | -0.041199 | -0.073242 | 0.041199 | 0.004578 | 0.032043 | 0.032043 | -0.054932 | -0.3067 | 2.6596 | 0.4715 | 0.44861 | 0.43945 | 0.41657 | 0.068664 | -121.9528 | -122.0627 | 0.15106 | 0.14191 | 0.11444 | 0.073242 | 0.045777 | 2.6276 | 121.7606 | 0.082398 | -0.032043 | 122.0123 | 0.07782 | 122.0444 | 0.14648 | -122.0673 | -122.0306 | 121.7926 | 0.036621 | 31.4072 | 0.059509
3537.7812 | 122.0306 | -0.091553 | 121.962 | -0.012131 | 0.0078144 | 0.054922 | 0.055365 | 0.00058534 | -0.0074938 | 0.001036 | -0.0084228 | 0.024453 | 0.041994 | -0.013569 | 0.015325 | 0.023323 | -0.0057615 | 31.7505 | 121.9666 | -0.082397 | 121.7331 | 2.6596 | 0.35706 | 0.37537 | 0.032043 | 0.009155 | -0.018311 | -0.009155 | 0.10071 | 0.073242 | 0.082397 | 0.009156 | 0.004578 | -0.22888 | 2.7512 | 0.46692 | 0.44861 | 0.45776 | 0.43945 | 0.073242 | -121.9528 | -121.9711 | 0.19226 | 0.17395 | 0.16479 | 0.10071 | 0.091553 | 2.742 | 121.8155 | 0.11902 | 0.009156 | 122.049 | 0.027466 | 122.0581 | 0.10071 | -122.0444 | -121.9803 | 121.8246 | 0.082398 | 31.842 | 0.1236
3539.5469 | 122.1176 | -0.059509 | 121.9528 | -0.012131 | 0.0099506 | 0.057272 | 0.054937 | 0.0010125 | -0.0062122 | -0.0021682 | -0.0084228 | 0.020822 | 0.040285 | -0.015065 | 0.015539 | 0.024605 | -0.0034117 | 32.1075 | 121.962 | -0.068665 | 121.7743 | 2.7374 | 0.42114 | 0.42572 | 0.07782 | -0.022888 | -0.009155 | 0.059509 | 0.14648 | 0.1236 | 0.14191 | -0.009156 | 0.009155 | -0.17853 | 2.7969 | 0.48523 | 0.48065 | 0.49438 | 0.48981 | 0.050354 | -121.9757 | -121.8933 | 0.20599 | 0.20142 | 0.1831 | 0.15106 | 0.13275 | 2.8061 | 121.843 | 0.15564 | 0.068664 | 122.0306 | -0.013733 | 122.0215 | 0.036621 | -122.0215 | -121.962 | 121.8338 | 0.11902 | 32.1671 | 0.13733
3541.3125 | 122.1039 | -0.059509 | 121.9482 | -0.012131 | 0.0067462 | 0.05535 | 0.051947 | -0.00069646 | -0.0077074 | 0.0006088 | -0.0023192 | 0.01954 | 0.040926 | -0.016774 | 0.01383 | 0.0261 | -0.0027707 | 32.4738 | 121.9162 | -0.045776 | 121.8063 | 2.8702 | 0.4715 | 0.49439 | 0.10986 | -0.022888 | 0.022888 | 0.050354 | 0.16937 | 0.17395 | 0.11902 | 0.013733 | -0.032043 | -0.14191 | 2.9297 | 0.55389 | 0.53101 | 0.54016 | 0.51727 | 0.082397 | -121.9711 | -121.8979 | 0.22888 | 0.17853 | 0.23346 | 0.096131 | 0.15106 | 2.916 | 121.8521 | 0.14649 | 0.027466 | 121.962 | -0.045776 | 121.9757 | 0.036621 | -121.994 | -121.9254 | 121.8658 | 0.10986 | 32.5333 | 0.16937
3543.0156 | 122.0306 | -0.082397 | 121.994 | -0.012131 | 0.0073872 | 0.055563 | 0.056646 | 0.0012261 | -0.0057848 | 0.0003952 | -0.0084228 | 0.023812 | 0.042635 | -0.0048107 | 0.017248 | 0.024819 | -0.0031979 | 32.7988 | 121.9574 | -0.07782 | 121.7239 | 2.8244 | 0.3891 | 0.3891 | 0.032043 | 0.004578 | -0.041199 | 0 | 0.082397 | 0.050354 | 0.082397 | 0.004577 | -0.036622 | -0.27008 | 2.9068 | 0.4715 | 0.4715 | 0.46692 | 0.46692 | 0.041198 | -121.9894 | -121.994 | 0.16479 | 0.16479 | 0.13275 | 0.1236 | 0.091553 | 2.9022 | 121.8018 | 0.1236 | 0.041199 | 122.0352 | 0.045777 | 122.0398 | 0.086975 | -122.0718 | -122.0352 | 121.8063 | 0.082397 | 32.8812 | 0.11444
3544.7812 | 122.0078 | -0.10529 | 121.9528 | -0.01976 | 0.0099506 | 0.058127 | 0.054724 | -0.00048286 | -0.0062122 | 0.0006088 | -0.005371 | 0.021463 | 0.039431 | -0.015919 | 0.016607 | 0.024178 | -0.0055479 | 33.1146 | 121.9803 | -0.073242 | 121.669 | 2.8244 | 0.32959 | 0.35248 | -0.050354 | 0.009155 | -0.036621 | -0.045776 | 0.041199 | 0.013733 | 0.050354 | 0.032044 | 0.027466 | -0.28381 | 2.9297 | 0.45776 | 0.43488 | 0.42572 | 0.40283 | 0.068665 | -121.9437 | -121.9986 | 0.14649 | 0.15564 | 0.11902 | 0.086975 | 0.050354 | 2.8976 | 121.7422 | 0.07782 | -0.009155 | 122.0535 | 0.045776 | 122.0856 | 0.11444 | -122.0261 | -121.9894 | 121.7743 | 0.05951 | 33.2199 | 0.054932
3546.5469 | 122.0947 | -0.059509 | 121.9849 | -0.0045011 | 0.0067462 | 0.054922 | 0.052588 | 0.0029351 | -0.0057848 | 0.0003952 | -0.005371 | 0.019967 | 0.040071 | -0.017415 | 0.014684 | 0.025246 | -0.0025571 | 33.5129 | 121.9208 | -0.045776 | 121.7926 | 3.0304 | 0.48981 | 0.48523 | 0.07782 | -0.027466 | -0.022888 | 0.036621 | 0.16479 | 0.13733 | 0.10986 | 0.013733 | -0.064087 | -0.19226 | 3.0899 | 0.54474 | 0.54932 | 0.53101 | 0.53558 | 0.036621 | -122.0123 | -121.9482 | 0.2243 | 0.16937 | 0.19684 | 0.13275 | 0.16022 | 3.0762 | 121.8384 | 0.18768 | 0.059509 | 121.9666 | -0.004578 | 121.9803 | 0.032043 | -122.0306 | -122.0078 | 121.8521 | 0.09613 | 33.5724 | 0.13733
3548.25 | 122.0352 | -0.10071 | 121.9986 | -0.01976 | 0.0084552 | 0.056418 | 0.05451 | -0.0015509 | -0.0062122 | -0.0008866 | -0.005371 | 0.020608 | 0.042635 | -0.018696 | 0.017034 | 0.023537 | -0.0064023 | 33.8104 | 121.9803 | -0.086975 | 121.7194 | 2.9709 | 0.39825 | 0.3891 | -0.009155 | 0.018311 | -0.041199 | -0.032043 | 0.07782 | 0.045776 | 0.082397 | 0.013733 | -0.01831 | -0.27924 | 3.0716 | 0.48981 | 0.49896 | 0.47607 | 0.48523 | 0.059509 | -121.9803 | -122.0306 | 0.17853 | 0.18311 | 0.14648 | 0.1236 | 0.086975 | 3.0579 | 121.8063 | 0.11902 | 0.009156 | 122.0673 | 0.05951 | 122.081 | 0.11902 | -122.0856 | -122.0398 | 121.8201 | 0.068665 | 33.9111 | 0.091553
3550.0156 | 122.1268 | -0.059509 | 121.9162 | -0.01976 | 0.010805 | 0.056631 | 0.05451 | -0.0043281 | -0.0042896 | 0.0003952 | -0.0084228 | 0.01954 | 0.040712 | -0.013783 | 0.01618 | 0.024819 | -0.0074705 | 34.1858 | 121.9208 | -0.059509 | 121.8018 | 3.154 | 0.46692 | 0.50354 | 0.11444 | -0.027466 | 0 | 0.073242 | 0.1831 | 0.13275 | 0.14648 | 0 | 0.004577 | -0.11444 | 3.2135 | 0.56305 | 0.52643 | 0.56305 | 0.52643 | 0.059509 | -121.9437 | -121.843 | 0.24261 | 0.20599 | 0.19226 | 0.14648 | 0.13275 | 3.2135 | 121.8613 | 0.1831 | 0.073242 | 121.9803 | -0.027466 | 121.9803 | 0.032043 | -121.9757 | -121.9162 | 121.8613 | 0.13275 | 34.2453 | 0.17395
3551.7812 | 122.0535 | -0.09613 | 121.9574 | -0.0045011 | 0.008028 | 0.054709 | 0.054937 | 0.00037174 | -0.0040758 | 0.0006088 | -0.005371 | 0.021463 | 0.039858 | -0.0095105 | 0.014898 | 0.022469 | -0.0010617 | 34.4742 | 121.9757 | -0.09613 | 121.7056 | 3.0899 | 0.3891 | 0.39368 | -0.050354 | 0.013733 | -0.036621 | -0.032043 | 0.068665 | 0.050354 | 0.064087 | 0 | 0.018311 | -0.25177 | 3.186 | 0.48981 | 0.48523 | 0.48981 | 0.48523 | 0.059509 | -121.9437 | -121.9894 | 0.16479 | 0.16022 | 0.14648 | 0.10071 | 0.086975 | 3.186 | 121.8018 | 0.10529 | 0.004578 | 122.0718 | 0.050354 | 122.0718 | 0.10986 | -122.0535 | -121.994 | 121.8018 | 0.064087 | 34.5703 | 0.045776
3553.5469 | 122.0261 | -0.10071 | 121.9849 | -0.012131 | 0.010805 | 0.055563 | 0.056006 | -0.0013373 | -0.0059986 | -0.0021682 | -0.0023192 | 0.022103 | 0.04178 | -0.012715 | 0.014684 | 0.025246 | -0.0021299 | 34.7672 | 121.9711 | -0.086975 | 121.669 | 3.1494 | 0.37994 | 0.39368 | -0.013733 | 0.009155 | -0.041199 | -0.013733 | 0.059509 | 0.027466 | 0.064087 | 0.013733 | -0.013733 | -0.31586 | 3.2501 | 0.49439 | 0.48065 | 0.48065 | 0.46692 | 0.059509 | -121.9757 | -121.9986 | 0.16022 | 0.1648 | 0.12817 | 0.10529 | 0.068665 | 3.2364 | 121.756 | 0.10071 | 0.027466 | 122.0581 | 0.050354 | 122.0718 | 0.10986 | -122.0718 | -122.0261 | 121.7697 | 0.086975 | 34.8679 | 0.086975
3555.3125 | 122.081 | -0.068665 | 121.962 | -0.01976 | 0.0078144 | 0.054922 | 0.054297 | -0.0019781 | -0.006853 | -3.1996e-05 | -0.005371 | 0.020395 | 0.041567 | -0.021687 | 0.014898 | 0.026741 | -0.0019163 | 35.1471 | 121.9299 | -0.068665 | 121.7331 | 3.2639 | 0.44861 | 0.45776 | 0.027466 | -0.022888 | -0.009155 | 0.004578 | 0.10529 | 0.091553 | 0.086975 | 0 | -0.032043 | -0.22888 | 3.3325 | 0.52643 | 0.51727 | 0.52643 | 0.51727 | 0.05951 | -121.9849 | -121.9574 | 0.17395 | 0.15564 | 0.16022 | 0.09613 | 0.10071 | 3.3325 | 121.8018 | 0.11444 | 0.013733 | 121.9986 | -0.013733 | 121.9986 | 0.045777 | -122.0306 | -121.9711 | 121.8018 | 0.073243 | 35.2158 | 0.096131
3557.0781 | 122.1268 | -0.059509 | 121.9299 | -0.012131 | 0.0076008 | 0.056418 | 0.05152 | -0.0032599 | -0.005144 | 0.0003952 | -0.0084228 | 0.018472 | 0.038149 | -0.010579 | 0.012975 | 0.025246 | -0.0031979 | 35.4996 | 121.8933 | -0.054932 | 121.7697 | 3.3966 | 0.52185 | 0.54016 | 0.10529 | -0.027466 | -0.022888 | 0.050354 | 0.17853 | 0.16479 | 0.14191 | 0.004577 | -0.036621 | -0.16022 | 3.4561 | 0.59967 | 0.58136 | 0.59509 | 0.57678 | 0.036621 | -121.9574 | -121.8796 | 0.23804 | 0.20142 | 0.2243 | 0.16479 | 0.18768 | 3.4515 | 121.8246 | 0.20142 | 0.073242 | 121.9482 | -0.004578 | 121.9528 | 0.032043 | -121.9849 | -121.9528 | 121.8292 | 0.10986 | 35.5591 | 0.16479
3558.7812 | 122.113 | -0.068665 | 121.9208 | -0.01976 | 0.010378 | 0.057272 | 0.05216 | 0.0042169 | -0.0059986 | -0.001741 | -0.0084228 | 0.020608 | 0.042635 | -0.0088695 | 0.013616 | 0.023537 | -0.0017027 | 35.8475 | 121.9482 | -0.064087 | 121.7926 | 3.4607 | 0.50354 | 0.53101 | 0.10986 | -0.027466 | 0.013733 | 0.059509 | 0.15106 | 0.1236 | 0.11902 | 0.004578 | 0.027466 | -0.12817 | 3.5294 | 0.59967 | 0.5722 | 0.59509 | 0.56763 | 0.082398 | -121.9482 | -121.8613 | 0.21973 | 0.18768 | 0.19226 | 0.10529 | 0.10986 | 3.5248 | 121.8567 | 0.13733 | 0.045776 | 122.0123 | -0.041199 | 122.0169 | 0.041199 | -121.9849 | -121.907 | 121.8613 | 0.12817 | 35.9161 | 0.17853
3560.5469 | 122.0306 | -0.073242 | 121.9849 | -0.01976 | 0.0088824 | 0.05535 | 0.055792 | -0.0030463 | -0.0062122 | 0.0012496 | -0.005371 | 0.022744 | 0.042635 | -0.0033153 | 0.016607 | 0.024178 | -0.0096067 | 36.0718 | 121.9482 | -0.07782 | 121.6919 | 3.3829 | 0.4303 | 0.40741 | -0.054932 | 0.009155 | -0.050354 | -0.041199 | 0.073242 | 0.045776 | 0.073242 | -0.004578 | -0.036621 | -0.29297 | 3.4561 | 0.48065 | 0.50354 | 0.48523 | 0.50812 | 0.022888 | -121.9757 | -122.0261 | 0.14648 | 0.14648 | 0.11902 | 0.1236 | 0.09613 | 3.4607 | 121.7697 | 0.1236 | 0.009155 | 122.0261 | 0.059509 | 122.0215 | 0.082397 | -122.0627 | -122.0352 | 121.7651 | 0.032043 | 36.145 | 0.01831
3562.3281 | 122.0398 | -0.09613 | 121.9711 | -0.012131 | 0.012728 | 0.057272 | 0.057074 | -0.0011237 | -0.0045032 | 0.0023178 | -0.011475 | 0.022531 | 0.044344 | -0.01122 | 0.015966 | 0.023964 | -0.0046933 | 36.4105 | 121.9666 | -0.07782 | 121.7468 | 3.511 | 0.46692 | 0.46234 | 0.045776 | 0.009155 | -0.013733 | 0.009155 | 0.10529 | 0.064087 | 0.064087 | 0.01831 | -0.004577 | -0.2243 | 3.6072 | 0.55847 | 0.56305 | 0.54016 | 0.54474 | 0.082397 | -121.962 | -121.962 | 0.20142 | 0.16022 | 0.16022 | 0.07782 | 0.07782 | 3.5889 | 121.8246 | 0.11902 | 0.022888 | 122.0444 | 0.022888 | 122.0627 | 0.10528 | -122.049 | -121.9849 | 121.843 | 0.10528 | 36.5067 | 0.14191
3564.0938 | 122.0032 | -0.10986 | 121.9711 | -0.012131 | 0.0067462 | 0.057272 | 0.052374 | 0.0014397 | -0.0081348 | -0.0013138 | -0.0084228 | 0.019967 | 0.04114 | -0.012929 | 0.014257 | 0.023537 | -0.00084805 | 36.676 | 121.9208 | -0.073242 | 121.7331 | 3.5797 | 0.48523 | 0.49439 | -0.022888 | 0.004578 | -0.036621 | -0.073242 | 0.064087 | 0.036621 | 0.045776 | 0.036621 | -0.050354 | -0.23804 | 3.6896 | 0.60425 | 0.59509 | 0.56763 | 0.55847 | 0.073242 | -121.9666 | -122.0444 | 0.17395 | 0.15564 | 0.14648 | 0.082397 | 0.073242 | 3.653 | 121.8063 | 0.10071 | -0.036621 | 121.994 | 0.041199 | 122.0306 | 0.11444 | -122.0444 | -122.0078 | 121.843 | 0.036621 | 36.7859 | 0.086975
3565.7969 | 122.0627 | -0.068665 | 121.9162 | -0.012131 | 0.0082416 | 0.058127 | 0.053656 | -0.0028327 | -0.0059986 | 0.0014634 | -0.0023192 | 0.021463 | 0.04178 | -0.019337 | 0.014684 | 0.025032 | -0.00084805 | 36.9598 | 121.9116 | -0.045776 | 121.7606 | 3.6942 | 0.50812 | 0.53101 | 0.068665 | -0.013733 | 0 | 0.027466 | 0.11444 | 0.086975 | 0.091553 | 0.022889 | -0.004578 | -0.15564 | 3.7628 | 0.59967 | 0.57678 | 0.57678 | 0.55389 | 0.068665 | -121.9299 | -121.8887 | 0.18311 | 0.16022 | 0.15564 | 0.091553 | 0.086975 | 3.7399 | 121.8063 | 0.11444 | 0.027466 | 121.9574 | -0.013733 | 121.9803 | 0.054932 | -121.962 | -121.9162 | 121.8292 | 0.096131 | 37.0285 | 0.13733
3567.5781 | 122.113 | -0.041199 | 121.9437 | -0.01976 | 0.0093098 | 0.054068 | 0.054297 | -0.0028327 | -0.0062122 | -0.0015274 | -0.0084228 | 0.020181 | 0.039431 | -0.015919 | 0.014257 | 0.025673 | 0.00064735 | 37.175 | 121.9025 | -0.073242 | 121.7468 | 3.7079 | 0.50812 | 0.53558 | 0.054932 | -0.013733 | -0.022888 | 0.022888 | 0.12817 | 0.11902 | 0.11902 | -0.032043 | -0.041199 | -0.19684 | 3.7491 | 0.57678 | 0.54932 | 0.60883 | 0.58136 | 0.018311 | -121.9574 | -121.9208 | 0.16937 | 0.16022 | 0.16022 | 0.14191 | 0.14191 | 3.7811 | 121.8201 | 0.15106 | 0.045776 | 121.9757 | 0.009155 | 121.9437 | 0.027466 | -122.0169 | -121.9666 | 121.788 | 0.064087 | 37.2162 | 0.096131
3569.2656 | 121.9849 | -0.10529 | 121.9711 | -0.02739 | 0.011873 | 0.055777 | 0.055365 | -0.00069646 | -0.005144 | 0.0003952 | -0.0084228 | 0.02424 | 0.040499 | -0.010792 | 0.017034 | 0.021614 | -0.0049069 | 37.3672 | 121.9803 | -0.086975 | 121.6507 | 3.6392 | 0.3891 | 0.41199 | -0.059509 | -0.004578 | -0.050354 | -0.045776 | 0.009155 | -0.009155 | 0.036621 | 0.018311 | 0.009156 | -0.32043 | 3.7445 | 0.51727 | 0.49438 | 0.49896 | 0.47607 | 0.054932 | -121.9757 | -122.0169 | 0.11444 | 0.14191 | 0.096131 | 0.086975 | 0.041199 | 3.7262 | 121.7377 | 0.059509 | 0.004578 | 122.0673 | 0.045776 | 122.0856 | 0.10071 | -122.0581 | -122.0215 | 121.756 | 0.05951 | 37.4725 | 0.045777
3571.0312 | 122.0993 | -0.059509 | 121.9254 | -0.01976 | 0.0095234 | 0.057059 | 0.052374 | -0.0034735 | -0.0066394 | 0.0023178 | -0.0084228 | 0.021249 | 0.03879 | -0.019551 | 0.011694 | 0.025673 | -0.0014891 | 37.6923 | 121.9116 | -0.027466 | 121.8018 | 3.8818 | 0.58594 | 0.5722 | 0.09613 | -0.009155 | -0.032043 | 0.041199 | 0.16479 | 0.15106 | 0.1236 | 0.032043 | -0.013733 | -0.1236 | 3.9413 | 0.63171 | 0.64545 | 0.59967 | 0.6134 | 0.027466 | -121.9345 | -121.8842 | 0.2243 | 0.1831 | 0.21057 | 0.15564 | 0.18311 | 3.9093 | 121.8292 | 0.19684 | 0.073242 | 121.9391 | 0.022888 | 121.9711 | 0.050354 | -121.9528 | -121.9574 | 121.8613 | 0.10071 | 37.7518 | 0.15564
3572.7969 | 122.0261 | -0.091553 | 121.9574 | -0.0045011 | 0.009737 | 0.057486 | 0.053656 | -0.0024055 | -0.0030078 | 0.0035996 | -0.0023192 | 0.023812 | 0.039217 | -0.0063061 | 0.01853 | 0.025032 | -0.0036253 | 37.8799 | 121.9666 | -0.073242 | 121.7331 | 3.8269 | 0.50354 | 0.49439 | 0.004578 | 0.022888 | -0.041199 | -0.009155 | 0.091553 | 0.045776 | 0.073242 | 0.018311 | 0.009156 | -0.2243 | 3.9185 | 0.58594 | 0.59509 | 0.56763 | 0.57678 | 0.050354 | -121.9345 | -121.9666 | 0.18311 | 0.16479 | 0.13733 | 0.11444 | 0.086975 | 3.9001 | 121.8063 | 0.13275 | 0.032044 | 122.0398 | 0.064087 | 122.0581 | 0.11444 | -122.0306 | -121.9986 | 121.8246 | 0.082398 | 37.9715 | 0.096131
3574.5 | 121.9803 | -0.09613 | 121.9757 | -0.0045011 | 0.013369 | 0.057059 | 0.056433 | -0.00026906 | -0.0040758 | 0.0023178 | -0.005371 | 0.02189 | 0.04178 | -0.010792 | 0.015539 | 0.025246 | -0.0049069 | 38.0402 | 121.9666 | -0.091553 | 121.6644 | 3.7994 | 0.42114 | 0.44861 | -0.07782 | 0.018311 | -0.041199 | -0.059509 | 0 | -0.027466 | 0.013733 | 0.004577 | -0.009155 | -0.31128 | 3.8956 | 0.54474 | 0.51727 | 0.54016 | 0.5127 | 0.054931 | -121.9574 | -122.0352 | 0.09613 | 0.10986 | 0.068664 | 0.054932 | 0.013733 | 3.891 | 121.756 | 0.041199 | -0.01831 | 122.0581 | 0.05951 | 122.0627 | 0.11444 | -122.0673 | -122.0169 | 121.7606 | 0.036621 | 38.1363 | 0.01831
3576.2656 | 122.1176 | -0.032043 | 121.907 | -0.0045011 | 0.013796 | 0.060904 | 0.053015 | 0.0035761 | -0.003435 | 0.0006088 | -0.011475 | 0.020181 | 0.041567 | -0.0095105 | 0.015752 | 0.0261 | -0.0036253 | 38.2965 | 121.9116 | -0.059509 | 121.7743 | 3.9871 | 0.56305 | 0.56763 | 0.09613 | -0.022888 | -0.004578 | 0.068665 | 0.15564 | 0.13275 | 0.15564 | -0.027466 | 0.004578 | -0.13275 | 4.0192 | 0.59967 | 0.59509 | 0.62714 | 0.62256 | 0.027465 | -121.9299 | -121.8384 | 0.18768 | 0.18768 | 0.16479 | 0.16022 | 0.13733 | 4.0466 | 121.8338 | 0.16022 | 0.073243 | 121.9711 | -0.01831 | 121.9437 | 0.009155 | -121.9666 | -121.9116 | 121.8063 | 0.10071 | 38.3286 | 0.12817
3578.0469 | 121.9849 | -0.1236 | 121.9528 | -0.0045011 | 0.0076008 | 0.057486 | 0.053656 | 0.0027215 | -0.0049304 | 0.0025314 | -0.0084228 | 0.021035 | 0.04114 | -0.015065 | 0.013403 | 0.024819 | 0.00064735 | 38.443 | 121.9437 | -0.07782 | 121.6782 | 3.9734 | 0.49896 | 0.50354 | -0.036621 | 0 | -0.041199 | -0.059509 | 0.059509 | 0.032043 | 0.022888 | 0.045776 | -0.009155 | -0.27466 | 4.097 | 0.62714 | 0.62256 | 0.58136 | 0.57678 | 0.082397 | -121.9528 | -122.0123 | 0.1831 | 0.14648 | 0.15564 | 0.064087 | 0.073242 | 4.0512 | 121.756 | 0.10071 | -0.01831 | 122.0215 | 0.041199 | 122.0673 | 0.1236 | -122.0306 | -121.994 | 121.8018 | 0.064087 | 38.5666 | 0.086975
3579.75 | 122.1039 | -0.054932 | 121.8979 | -0.0045011 | 0.0093098 | 0.056631 | 0.053228 | -0.00026906 | -0.0049304 | 0.0046676 | -0.0084228 | 0.018899 | 0.041567 | -0.016774 | 0.015752 | 0.025673 | -0.0034117 | 38.6169 | 121.9254 | -0.059509 | 121.7422 | 4.0512 | 0.57678 | 0.56763 | 0.041199 | -0.032043 | -0.022888 | 0.027466 | 0.16022 | 0.15106 | 0.1236 | -0.004577 | 0.027466 | -0.15564 | 4.1061 | 0.62256 | 0.63171 | 0.62714 | 0.63629 | 0.032044 | -121.9299 | -121.8704 | 0.21515 | 0.17853 | 0.20599 | 0.14648 | 0.17395 | 4.1107 | 121.8018 | 0.1831 | 0.050354 | 121.9849 | -0.009155 | 121.9803 | 0.022889 | -121.9574 | -121.9208 | 121.7972 | 0.082398 | 38.6719 | 0.096131
3581.5156 | 121.9894 | -0.11444 | 121.9574 | -0.01976 | 0.012728 | 0.054495 | 0.053869 | -0.00091006 | -0.0066394 | 0.001677 | -0.005371 | 0.022317 | 0.042849 | -0.010792 | 0.013616 | 0.023537 | -0.0012753 | 38.8 | 121.9803 | -0.09613 | 121.6553 | 3.9963 | 0.48981 | 0.4715 | -0.050354 | 0.018311 | -0.036621 | -0.082397 | 0.041199 | 0.013733 | 0.022888 | 0.018311 | 0.022889 | -0.30212 | 4.1107 | 0.58594 | 0.60425 | 0.56763 | 0.58594 | 0.07782 | -121.9391 | -122.0398 | 0.15564 | 0.13733 | 0.12817 | 0.059509 | 0.050354 | 4.0924 | 121.7514 | 0.07782 | -0.045776 | 122.0764 | 0.054932 | 122.0947 | 0.13275 | -122.0535 | -121.994 | 121.7697 | 0.032044 | 38.9145 | 0.064087
3583.2812 | 122.0764 | -0.07782 | 121.9574 | -0.012131 | 0.008028 | 0.0577 | 0.05216 | 0.00037174 | -0.0064258 | 0.0023178 | -0.011475 | 0.019754 | 0.04114 | -0.016133 | 0.012762 | 0.023323 | -0.0031979 | 38.9694 | 121.907 | -0.082397 | 121.7194 | 4.1061 | 0.54016 | 0.56763 | 0.022888 | -0.022888 | -0.009155 | -0.004578 | 0.1236 | 0.10529 | 0.086975 | -0.004577 | -0.050354 | -0.23804 | 4.184 | 0.64545 | 0.61798 | 0.65002 | 0.62256 | 0.068665 | -121.9803 | -121.962 | 0.20142 | 0.16479 | 0.18311 | 0.09613 | 0.11444 | 4.1885 | 121.8018 | 0.13275 | 0.004577 | 121.9894 | -0.013733 | 121.9849 | 0.054932 | -122.0398 | -121.9666 | 121.7972 | 0.073242 | 39.0472 | 0.10071
3584.9844 | 122.0169 | -0.082397 | 121.9437 | -0.012131 | 0.012728 | 0.058554 | 0.055578 | 0.0022943 | -0.0030078 | 0.0038132 | -0.0023192 | 0.022531 | 0.040712 | -0.017201 | 0.014257 | 0.024178 | -0.0021299 | 39.1022 | 121.9894 | -0.07782 | 121.6736 | 4.0741 | 0.46692 | 0.4715 | -0.041199 | 0.018311 | -0.032043 | -0.041199 | 0.036621 | 0.004578 | 0.045776 | 0.004577 | 0.045776 | -0.27008 | 4.1565 | 0.55389 | 0.54932 | 0.54932 | 0.54474 | 0.050354 | -121.9254 | -121.9849 | 0.11902 | 0.12817 | 0.086975 | 0.077819 | 0.036621 | 4.1519 | 121.7514 | 0.068664 | -0.009156 | 122.0673 | 0.050354 | 122.0718 | 0.10071 | -122.0215 | -121.9757 | 121.756 | 0.041198 | 39.1846 | 0.041198
3586.75 | 121.994 | -0.09613 | 121.9666 | -0.01976 | 0.0095234 | 0.056204 | 0.052801 | -0.0036871 | -0.0047168 | 0.001036 | -0.005371 | 0.020395 | 0.039644 | -0.020192 | 0.016607 | 0.024391 | -0.0012753 | 39.2807 | 121.9345 | -0.059509 | 121.669 | 4.1519 | 0.50354 | 0.5127 | -0.041199 | 0.004578 | -0.032043 | -0.064087 | 0.050354 | 0.032043 | 0.027466 | 0.036621 | -0.032044 | -0.29755 | 4.248 | 0.60882 | 0.59967 | 0.5722 | 0.56305 | 0.064087 | -121.962 | -122.0306 | 0.14648 | 0.1236 | 0.12817 | 0.059509 | 0.064086 | 4.2114 | 121.7285 | 0.082397 | -0.032044 | 121.994 | 0.036621 | 122.0306 | 0.10071 | -122.0261 | -121.9986 | 121.7651 | 0.032043 | 39.3768 | 0.054931
3588.5156 | 122.0718 | -0.073242 | 121.9162 | -0.0045011 | 0.012087 | 0.059409 | 0.054297 | 0.00037174 | -0.0059986 | 0.0003952 | -0.0023192 | 0.017617 | 0.041567 | -0.013783 | 0.012762 | 0.024391 | -0.0027707 | 39.4867 | 121.9116 | -0.022888 | 121.7834 | 4.3076 | 0.60883 | 0.61798 | 0.10071 | -0.018311 | 0.009155 | 0.050354 | 0.15106 | 0.1236 | 0.11444 | 0.050354 | -0.004578 | -0.13275 | 4.3808 | 0.69122 | 0.68207 | 0.64087 | 0.63171 | 0.082397 | -121.9345 | -121.8658 | 0.2243 | 0.18768 | 0.19684 | 0.10529 | 0.11444 | 4.3304 | 121.8063 | 0.14191 | 0.041199 | 121.9345 | -0.027466 | 121.9849 | 0.054931 | -121.9391 | -121.907 | 121.8567 | 0.1236 | 39.5599 | 0.17395
3590.2188 | 122.0901 | -0.050354 | 121.9345 | -0.012131 | 0.0123 | 0.059836 | 0.054937 | 0.0012261 | -0.0053576 | -0.0019546 | -0.0023192 | 0.018045 | 0.040712 | -0.012715 | 0.015112 | 0.023537 | -0.0021299 | 39.624 | 121.8979 | -0.032043 | 121.7926 | 4.3442 | 0.60425 | 0.62714 | 0.11444 | -0.022888 | -0.009155 | 0.068665 | 0.16022 | 0.11902 | 0.13733 | 0.018311 | -0.036621 | -0.14191 | 4.3945 | 0.67749 | 0.6546 | 0.65918 | 0.63629 | 0.041199 | -121.9574 | -121.8658 | 0.21057 | 0.18768 | 0.16937 | 0.14648 | 0.12817 | 4.3762 | 121.8246 | 0.16937 | 0.07782 | 121.9299 | -0.013733 | 121.9482 | 0.027466 | -121.9666 | -121.9437 | 121.843 | 0.11902 | 39.6744 | 0.16479
3591.9844 | 122.0535 | -0.073242 | 121.907 | -0.01976 | 0.011232 | 0.055991 | 0.054937 | -0.0026191 | -0.0053576 | 0.0014634 | -0.0023192 | 0.021249 | 0.04178 | -0.018696 | 0.012121 | 0.021828 | -0.0042661 | 39.7247 | 121.9391 | -0.054932 | 121.7331 | 4.3121 | 0.5722 | 0.5722 | 0.018311 | -0.013733 | -0.036621 | -0.004578 | 0.10529 | 0.091553 | 0.082397 | 0.01831 | 0.032044 | -0.17395 | 4.3854 | 0.64545 | 0.64545 | 0.62714 | 0.62714 | 0.036621 | -121.9208 | -121.9116 | 0.17853 | 0.15564 | 0.16479 | 0.11902 | 0.12817 | 4.3671 | 121.788 | 0.14191 | 0.032043 | 121.994 | 0.022888 | 122.0123 | 0.059509 | -121.962 | -121.9437 | 121.8063 | 0.068664 | 39.798 | 0.091553
3593.7656 | 122.0306 | -0.09613 | 121.9345 | -0.02739 | 0.012941 | 0.056845 | 0.055365 | -0.0013373 | -0.0042896 | 0.001036 | -0.0084228 | 0.023172 | 0.042635 | -0.014424 | 0.016393 | 0.023964 | -0.0042661 | 39.8163 | 121.9345 | -0.07782 | 121.6736 | 4.2572 | 0.50354 | 0.51727 | -0.032043 | 0 | -0.036621 | -0.022888 | 0.045776 | 0.036621 | 0.059509 | 0.01831 | 0 | -0.26093 | 4.3533 | 0.6134 | 0.59967 | 0.59509 | 0.58136 | 0.059509 | -121.9345 | -121.9574 | 0.14191 | 0.15564 | 0.13275 | 0.09613 | 0.073242 | 4.335 | 121.7514 | 0.082397 | 0.013733 | 122.0123 | 0.036621 | 122.0306 | 0.09613 | -122.0123 | -121.9711 | 121.7697 | 0.073242 | 39.9124 | 0.064087
3595.5312 | 122.0032 | -0.12817 | 121.9574 | -0.0045011 | 0.009096 | 0.056204 | 0.054937 | -5.5462e-05 | -0.003435 | 0.0018906 | -0.0023192 | 0.021249 | 0.042208 | -0.014638 | 0.016607 | 0.022896 | -0.0029843 | 39.9307 | 121.9711 | -0.082397 | 121.6507 | 4.2984 | 0.53558 | 0.53101 | -0.054932 | 0.027466 | -0.041199 | -0.064087 | 0.045776 | 0.013733 | 0.041199 | 0.045777 | 0.013733 | -0.3067 | 4.4266 | 0.65918 | 0.66376 | 0.6134 | 0.61798 | 0.086975 | -121.9299 | -122.0215 | 0.17395 | 0.16937 | 0.14191 | 0.082398 | 0.054932 | 4.3808 | 121.7331 | 0.086975 | -0.022888 | 122.0535 | 0.068665 | 122.0993 | 0.15564 | -122.0398 | -121.9986 | 121.7789 | 0.064087 | 40.0589 | 0.073242
3597.2969 | 122.1176 | -0.059509 | 121.9208 | -0.012131 | 0.011446 | 0.057059 | 0.050879 | -0.0017645 | -0.0072802 | -0.0008866 | 0.00073235 | 0.020395 | 0.039644 | -0.0082287 | 0.015752 | 0.024819 | -0.0057615 | 40.1276 | 121.907 | -0.050354 | 121.788 | 4.5319 | 0.67749 | 0.65002 | 0.10071 | -0.027466 | -0.004578 | 0.045776 | 0.1831 | 0.15564 | 0.13275 | 0.009155 | -0.013733 | -0.13275 | 4.5914 | 0.70953 | 0.737 | 0.70038 | 0.72784 | 0.054931 | -121.9482 | -121.875 | 0.24261 | 0.19226 | 0.21515 | 0.13733 | 0.16022 | 4.5822 | 121.8384 | 0.18768 | 0.050354 | 121.9574 | -0.022888 | 121.9666 | 0.032043 | -121.9711 | -121.9254 | 121.8475 | 0.10528 | 40.1871 | 0.16022
3599 | 122.0627 | -0.09613 | 121.9208 | -0.0045011 | 0.010591 | 0.0577 | 0.053656 | 0.0010125 | -0.0053576 | -0.0008866 | -0.005371 | 0.020181 | 0.043489 | -0.01891 | 0.014043 | 0.026528 | -0.00084805 | 40.2054 | 121.9345 | -0.050354 | 121.7285 | 4.4495 | 0.60883 | 0.59052 | 0.022888 | -0.018311 | -0.036621 | 0.004578 | 0.10071 | 0.07782 | 0.09613 | 0.045776 | 0.013733 | -0.19226 | 4.5456 | 0.68664 | 0.70496 | 0.64087 | 0.65918 | 0.059509 | -121.9391 | -121.9162 | 0.19684 | 0.19226 | 0.17395 | 0.13275 | 0.11444 | 4.4998 | 121.7789 | 0.13733 | 0.041199 | 121.9849 | 0.01831 | 122.0306 | 0.077819 | -121.9711 | -121.9574 | 121.8246 | 0.10071 | 40.3015 | 0.11902
3600.7812 | 122.1268 | -0.045776 | 121.9299 | -0.01976 | 0.01465 | 0.060049 | 0.053869 | 0.0010125 | -0.00087162 | -0.0002456 | -0.0084228 | 0.020822 | 0.04114 | -0.021901 | 0.014684 | 0.02546 | -0.0057615 | 40.3564 | 121.9437 | -0.041199 | 121.7926 | 4.5364 | 0.63171 | 0.62256 | 0.13275 | -0.009155 | 0.004578 | 0.07782 | 0.16479 | 0.14191 | 0.15564 | 0.004577 | 0.013733 | -0.13733 | 4.5822 | 0.66834 | 0.67749 | 0.66376 | 0.67291 | 0.050354 | -121.9391 | -121.8521 | 0.21057 | 0.20142 | 0.18768 | 0.15106 | 0.13733 | 4.5776 | 121.8338 | 0.16022 | 0.073242 | 121.9849 | -0.013733 | 121.9894 | 0.036621 | -121.9711 | -121.9254 | 121.8384 | 0.1236 | 40.4022 | 0.17853
3602.5 | 122.0169 | -0.091553 | 121.9757 | -0.0045011 | 0.013155 | 0.057486 | 0.053869 | 0.0022943 | -0.0047168 | 0.0014634 | -0.005371 | 0.023599 | 0.043062 | -0.013142 | 0.017675 | 0.023537 | -0.0031979 | 40.3564 | 121.9666 | -0.091553 | 121.6782 | 4.4495 | 0.53101 | 0.53558 | -0.032043 | 0.018311 | -0.041199 | -0.041199 | 0.032043 | 0.013733 | 0.059509 | 0 | -0.009155 | -0.29755 | 4.541 | 0.62714 | 0.62256 | 0.62714 | 0.62256 | 0.050354 | -121.9574 | -122.0169 | 0.1236 | 0.15106 | 0.10529 | 0.10071 | 0.054932 | 4.541 | 121.7697 | 0.073242 | 0 | 122.0581 | 0.05951 | 122.0581 | 0.10986 | -122.0673 | -122.0169 | 121.7697 | 0.050354 | 40.448 | 0.05951
3604.2812 | 122.0215 | -0.082397 | 121.9299 | -0.0045011 | 0.012087 | 0.058768 | 0.054297 | 0.0025079 | -0.0047168 | 0.0014634 | -0.005371 | 0.021249 | 0.039217 | -0.013142 | 0.014898 | 0.024605 | -0.0017027 | 40.4617 | 121.9803 | -0.068665 | 121.6736 | 4.4678 | 0.52643 | 0.53101 | -0.018311 | 0.004578 | -0.032043 | -0.013733 | 0.059509 | 0.009155 | 0.054932 | 0.013732 | 0.050354 | -0.25635 | 4.5502 | 0.6134 | 0.60882 | 0.59967 | 0.59509 | 0.050354 | -121.9254 | -121.9437 | 0.14191 | 0.13733 | 0.091552 | 0.086975 | 0.041198 | 4.5364 | 121.7422 | 0.091552 | 0.01831 | 122.049 | 0.036621 | 122.0627 | 0.086975 | -121.9986 | -121.962 | 121.756 | 0.068664 | 40.5441 | 0.064086
3605.9844 | 122.0215 | -0.086975 | 121.9666 | -0.0045011 | 0.014223 | 0.057486 | 0.055578 | 0.0016535 | -0.003435 | -0.0002456 | -0.005371 | 0.022103 | 0.043489 | -0.015278 | 0.017034 | 0.023537 | -0.0051205 | 40.6082 | 121.9666 | -0.07782 | 121.7148 | 4.5731 | 0.58594 | 0.59509 | 0.032043 | 0.004578 | -0.032043 | 0 | 0.091553 | 0.045776 | 0.068665 | 0.009155 | 0 | -0.25177 | 4.66 | 0.68207 | 0.67291 | 0.67291 | 0.66376 | 0.054932 | -121.962 | -121.9666 | 0.17853 | 0.15564 | 0.13275 | 0.10071 | 0.077819 | 4.6509 | 121.7926 | 0.1236 | 0.032043 | 122.0444 | 0.036621 | 122.0535 | 0.091553 | -122.0444 | -121.9986 | 121.8018 | 0.086975 | 40.6952 | 0.11902
3607.7656 | 122.0856 | -0.059509 | 121.9254 | -0.012131 | 0.011019 | 0.056631 | 0.054937 | -0.0015509 | -0.0062122 | 0.0046676 | -0.0084228 | 0.021035 | 0.043062 | -0.013997 | 0.01383 | 0.024819 | -0.0057615 | 40.7227 | 121.9208 | -0.041199 | 121.7697 | 4.6738 | 0.65918 | 0.67749 | 0.10071 | -0.022888 | -0.018311 | 0.036621 | 0.15106 | 0.10986 | 0.10529 | 0.01831 | -0.004578 | -0.15564 | 4.7333 | 0.737 | 0.71869 | 0.71869 | 0.70038 | 0.041198 | -121.9482 | -121.8887 | 0.21057 | 0.16479 | 0.16937 | 0.1236 | 0.12817 | 4.715 | 121.8109 | 0.16937 | 0.054932 | 121.962 | -0.004577 | 121.9803 | 0.036621 | -121.9666 | -121.9437 | 121.8292 | 0.09613 | 40.7822 | 0.16022
3609.5312 | 122.0947 | -0.059509 | 121.9345 | -0.0045011 | 0.0084552 | 0.057059 | 0.050451 | -0.00026906 | -0.0059986 | 0.0035996 | -0.0023192 | 0.019113 | 0.041567 | -0.01421 | 0.016821 | 0.025032 | -0.0049069 | 40.8051 | 121.9116 | -0.050354 | 121.788 | 4.7195 | 0.71411 | 0.69122 | 0.11902 | -0.013733 | -0.013733 | 0.054932 | 0.18768 | 0.16479 | 0.11444 | 0.009155 | -0.022888 | -0.14648 | 4.7791 | 0.75073 | 0.77362 | 0.74158 | 0.76447 | 0.045776 | -121.9482 | -121.8796 | 0.24719 | 0.17395 | 0.2243 | 0.12817 | 0.17853 | 4.7699 | 121.8384 | 0.20142 | 0.068665 | 121.962 | 0 | 121.9711 | 0.045776 | -121.9849 | -121.9482 | 121.8475 | 0.11444 | 40.8646 | 0.17853
3611.2969 | 122.0306 | -0.10529 | 121.9666 | -0.012131 | 0.0123 | 0.058768 | 0.053656 | -0.00069646 | -0.0064258 | -0.0002456 | -0.005371 | 0.025094 | 0.04178 | -0.011647 | 0.016607 | 0.023537 | -0.0064023 | 40.8279 | 121.9528 | -0.07782 | 121.6965 | 4.5914 | 0.56763 | 0.5722 | -0.041199 | 0.013733 | -0.041199 | -0.027466 | 0.09613 | 0.064087 | 0.064087 | 0.027466 | -0.013733 | -0.27008 | 4.6967 | 0.67749 | 0.67291 | 0.65002 | 0.64545 | 0.064087 | -121.9528 | -121.994 | 0.20142 | 0.16937 | 0.16937 | 0.10529 | 0.10529 | 4.6692 | 121.7743 | 0.13733 | 0.013733 | 122.0306 | 0.054932 | 122.0581 | 0.11902 | -122.0444 | -122.0078 | 121.8018 | 0.07782 | 40.9332 | 0.064087
3613.0156 | 122.0078 | -0.09613 | 121.9574 | -0.02739 | 0.014437 | 0.059195 | 0.055578 | -0.00091006 | -0.003435 | -3.1996e-05 | -0.0084228 | 0.02189 | 0.040499 | -0.011647 | 0.019384 | 0.023751 | -0.0059751 | 40.8966 | 121.9803 | -0.082397 | 121.6599 | 4.6097 | 0.53558 | 0.54474 | -0.041199 | 0.022888 | -0.050354 | -0.022888 | 0.059509 | 0.013733 | 0.054932 | 0.013733 | 0.022889 | -0.29755 | 4.7058 | 0.64087 | 0.63171 | 0.62714 | 0.61798 | 0.045776 | -121.9345 | -121.9803 | 0.15564 | 0.15106 | 0.10986 | 0.10529 | 0.064087 | 4.6921 | 121.7422 | 0.10986 | 0.027466 | 122.0627 | 0.073242 | 122.0764 | 0.11902 | -122.0398 | -122.0078 | 121.756 | 0.073242 | 40.9927 | 0.054931
3614.7812 | 122.0673 | -0.059509 | 121.9437 | -0.012131 | 0.013369 | 0.058554 | 0.052374 | 0.0010125 | -0.003435 | 0.0008224 | -0.005371 | 0.020822 | 0.043703 | -0.019337 | 0.014684 | 0.025887 | -0.0023435 | 41.0248 | 121.9162 | -0.036621 | 121.7651 | 4.8019 | 0.65918 | 0.66834 | 0.10529 | -0.032043 | -0.018311 | 0.045776 | 0.13275 | 0.11444 | 0.10529 | 0.022888 | -0.027466 | -0.17853 | 4.8615 | 0.72784 | 0.71869 | 0.70496 | 0.6958 | 0.041198 | -121.9757 | -121.8979 | 0.19226 | 0.16479 | 0.17395 | 0.1236 | 0.13275 | 4.8386 | 121.8018 | 0.15106 | 0.064087 | 121.9528 | -0.013732 | 121.9757 | 0.027466 | -121.9803 | -121.962 | 121.8246 | 0.10528 | 41.0843 | 0.16479
3616.5625 | 122.0535 | -0.09613 | 121.9528 | -0.012131 | 0.012514 | 0.057272 | 0.055578 | 0.0029351 | -0.0032214 | 0.0012496 | -0.005371 | 0.024667 | 0.04114 | -0.0067333 | 0.015752 | 0.022469 | -0.0029843 | 41.1072 | 121.9528 | -0.07782 | 121.7422 | 4.7241 | 0.62256 | 0.6134 | 0.027466 | -0.004578 | -0.041199 | -0.009155 | 0.091553 | 0.059509 | 0.07782 | 0.01831 | 0 | -0.21057 | 4.8203 | 0.70953 | 0.71869 | 0.69122 | 0.70038 | 0.054931 | -121.9574 | -121.962 | 0.18768 | 0.17395 | 0.15564 | 0.11902 | 0.10071 | 4.8019 | 121.8201 | 0.13275 | 0.032044 | 122.0306 | 0.036621 | 122.049 | 0.091552 | -122.0306 | -121.994 | 121.8384 | 0.086975 | 41.2033 | 0.1236
3618.2812 | 121.9437 | -0.091553 | 121.9803 | -0.02739 | 0.01465 | 0.059409 | 0.056646 | 0.00037174 | -0.0036486 | 0.004454 | -0.011475 | 0.020395 | 0.040712 | -0.019337 | 0.015112 | 0.024391 | -0.0031979 | 41.1392 | 121.9757 | -0.086975 | 121.6553 | 4.6646 | 0.54016 | 0.54474 | -0.091553 | 0.018311 | -0.027466 | -0.041199 | 0.009155 | -0.018311 | 0.032043 | 0.004578 | -0.004578 | -0.32501 | 4.7562 | 0.63629 | 0.63171 | 0.63171 | 0.62714 | 0.064087 | -121.962 | -122.0215 | 0.10071 | 0.1236 | 0.073242 | 0.059509 | 0.009155 | 4.7516 | 121.7422 | 0.036621 | -0.013733 | 122.0627 | 0.045777 | 122.0673 | 0.10986 | -122.0673 | -122.0078 | 121.7468 | 0.050354 | 41.2308 | 0
3620.0469 | 122.0947 | -0.07782 | 121.9254 | -0.0045011 | 0.011873 | 0.05834 | 0.052588 | 0.0016535 | -0.0032214 | -3.1996e-05 | -0.011475 | 0.018045 | 0.040285 | -0.01891 | 0.015325 | 0.026528 | -0.0019163 | 41.2491 | 121.9345 | -0.054932 | 121.7102 | 4.7974 | 0.66834 | 0.67749 | 0.022888 | -0.018311 | -0.022888 | 0.018311 | 0.14191 | 0.12817 | 0.10071 | 0.022888 | 0.009155 | -0.21515 | 4.8752 | 0.75531 | 0.74616 | 0.73242 | 0.72327 | 0.054932 | -121.9437 | -121.907 | 0.21973 | 0.17853 | 0.20599 | 0.1236 | 0.15106 | 4.8523 | 121.7651 | 0.16479 | 0.041199 | 121.9894 | 0.004577 | 122.0123 | 0.059509 | -121.9803 | -121.9482 | 121.788 | 0.096131 | 41.3269 | 0.10071
3621.7969 | 121.9803 | -0.11902 | 121.9666 | -0.012131 | 0.011232 | 0.055991 | 0.056006 | -0.0013373 | -0.0053576 | 0.002745 | -0.005371 | 0.022531 | 0.043276 | -0.017628 | 0.014043 | 0.02546 | -0.0025571 | 41.2903 | 121.9574 | -0.09613 | 121.6461 | 4.7607 | 0.60425 | 0.58136 | -0.054932 | 0.022888 | -0.050354 | -0.086975 | 0.036621 | 0.004578 | 0.032043 | 0.022889 | -0.009156 | -0.32044 | 4.8798 | 0.70038 | 0.72327 | 0.67749 | 0.70038 | 0.068665 | -121.9437 | -122.0535 | 0.15564 | 0.15106 | 0.1236 | 0.082397 | 0.054932 | 4.8569 | 121.7422 | 0.086975 | -0.036621 | 122.0535 | 0.073242 | 122.0764 | 0.14191 | -122.0627 | -122.0169 | 121.7651 | 0.032044 | 41.4093 | 0.064087
3623.5625 | 122.1359 | -0.064087 | 121.9345 | 0.0031279 | 0.009737 | 0.058554 | 0.051947 | -0.0043281 | -0.0057848 | -0.0002456 | -0.0084228 | 0.020608 | 0.041994 | -0.019551 | 0.016607 | 0.02311 | -0.0014891 | 41.3956 | 121.9116 | -0.068665 | 121.7606 | 4.9026 | 0.70038 | 0.71411 | 0.09613 | -0.018311 | -0.013733 | 0.032043 | 0.17853 | 0.15564 | 0.15564 | -0.004578 | -0.022888 | -0.17395 | 4.9667 | 0.7782 | 0.76446 | 0.78278 | 0.76904 | 0.050354 | -121.9528 | -121.9025 | 0.24261 | 0.21973 | 0.21973 | 0.16937 | 0.16937 | 4.9713 | 121.8292 | 0.19226 | 0.045776 | 121.9803 | -0.004578 | 121.9757 | 0.045776 | -122.0032 | -121.9482 | 121.8246 | 0.09613 | 41.4597 | 0.16022
3625.3281 | 122.0169 | -0.09613 | 121.9528 | -0.0045011 | 0.015718 | 0.059195 | 0.055792 | 0.0022943 | -0.0032214 | 0.0006088 | -0.0023192 | 0.021463 | 0.043276 | -0.010365 | 0.01618 | 0.024819 | -0.0027707 | 41.5009 | 121.9345 | -0.073242 | 121.7285 | 4.8706 | 0.63629 | 0.62714 | 0.022888 | 0.009155 | -0.036621 | -0.009155 | 0.086975 | 0.068665 | 0.073242 | 0.022888 | -0.018311 | -0.2243 | 4.9667 | 0.72327 | 0.73242 | 0.70038 | 0.70953 | 0.059509 | -121.9437 | -121.962 | 0.1831 | 0.16937 | 0.16479 | 0.10986 | 0.10529 | 4.9438 | 121.8018 | 0.1236 | 0.027466 | 122.0078 | 0.045776 | 122.0306 | 0.10528 | -122.0261 | -121.9894 | 121.8246 | 0.086975 | 41.597 | 0.11902
3627.0312 | 121.994 | -0.10529 | 121.9574 | -0.01976 | 0.011019 | 0.058768 | 0.052374 | 0.00015814 | -0.0038622 | 0.001036 | -0.0023192 | 0.020608 | 0.040071 | -0.011006 | 0.013616 | 0.024819 | -0.0051205 | 41.5192 | 121.9162 | -0.054932 | 121.7102 | 4.8981 | 0.64545 | 0.64545 | -0.009155 | 0 | -0.032043 | -0.068665 | 0.059509 | 0.032043 | 0.036621 | 0.050354 | -0.041198 | -0.24719 | 5.0034 | 0.75073 | 0.75073 | 0.70038 | 0.70038 | 0.073243 | -121.9574 | -122.0261 | 0.16479 | 0.14191 | 0.13733 | 0.068664 | 0.064086 | 4.953 | 121.7651 | 0.091552 | -0.036622 | 121.9711 | 0.032043 | 122.0215 | 0.10529 | -122.0123 | -121.9894 | 121.8155 | 0.036621 | 41.6245 | 0.096131
3628.7969 | 122.0718 | -0.068665 | 121.9437 | -0.0045011 | 0.011232 | 0.058127 | 0.053015 | -0.0011237 | -0.0059986 | 0.0031722 | 0.00073235 | 0.019113 | 0.040712 | -0.013997 | 0.011694 | 0.024819 | -0.0029843 | 41.6016 | 121.8842 | -0.045776 | 121.7697 | 4.9988 | 0.74158 | 0.737 | 0.073242 | -0.013733 | -0.018311 | 0.013733 | 0.13275 | 0.1236 | 0.10986 | 0.022889 | -0.05951 | -0.17395 | 5.0674 | 0.80566 | 0.81024 | 0.78278 | 0.78735 | 0.050354 | -121.9574 | -121.9299 | 0.20142 | 0.17853 | 0.19226 | 0.12817 | 0.14191 | 5.0446 | 121.8155 | 0.15106 | 0.032044 | 121.9299 | 0.004578 | 121.9528 | 0.054932 | -121.9894 | -121.962 | 121.8384 | 0.082398 | 41.6702 | 0.14191
3630.5625 | 122.0993 | -0.059509 | 121.9391 | -0.01976 | 0.013369 | 0.058127 | 0.056433 | 0.0022943 | -0.0032214 | 0.0038132 | -0.0023192 | 0.02189 | 0.040499 | -0.0037427 | 0.016393 | 0.024819 | -0.0019163 | 41.5924 | 121.9574 | -0.073242 | 121.7148 | 4.9347 | 0.63629 | 0.64545 | 0.054932 | -0.009155 | -0.022888 | 0.050354 | 0.14191 | 0.10529 | 0.14648 | -0.013733 | 0.01831 | -0.2243 | 4.9942 | 0.70496 | 0.6958 | 0.71869 | 0.70953 | 0.036621 | -121.9482 | -121.8887 | 0.20142 | 0.20599 | 0.16479 | 0.16937 | 0.12817 | 5.0079 | 121.788 | 0.16479 | 0.073242 | 122.0306 | 0.013733 | 122.0169 | 0.050354 | -122.0123 | -121.962 | 121.7743 | 0.10986 | 41.6519 | 0.11444
3632.3438 | 122.0352 | -0.10071 | 121.962 | -0.0045011 | 0.014223 | 0.0577 | 0.057287 | 0.0022943 | -0.0032214 | 0.0018906 | -0.005371 | 0.023172 | 0.039431 | -0.012288 | 0.017675 | 0.023751 | 6.346e-06 | 41.6748 | 121.962 | -0.086975 | 121.701 | 4.9438 | 0.64087 | 0.63171 | 0 | 0.013733 | -0.027466 | -0.013733 | 0.09613 | 0.059509 | 0.082397 | 0.013733 | 0 | -0.26093 | 5.0446 | 0.73242 | 0.74158 | 0.71869 | 0.72784 | 0.073242 | -121.9482 | -121.9757 | 0.19684 | 0.18311 | 0.16022 | 0.10986 | 0.086975 | 5.0308 | 121.788 | 0.1236 | 0.013733 | 122.0489 | 0.041199 | 122.0627 | 0.11444 | -122.0489 | -121.9894 | 121.8018 | 0.086975 | 41.7755 | 0.10071
3634.1094 | 121.994 | -0.09613 | 121.9666 | -0.012131 | 0.011232 | 0.0577 | 0.051733 | 0.00079894 | -0.0030078 | 0.0012496 | -0.005371 | 0.020608 | 0.042849 | -0.015492 | 0.014898 | 0.024391 | -0.0023435 | 41.7526 | 121.9162 | -0.041199 | 121.7285 | 5.0217 | 0.69122 | 0.67291 | 0 | 0.013733 | -0.018311 | -0.054932 | 0.073242 | 0.064087 | 0.045776 | 0.054931 | -0.050354 | -0.23804 | 5.1178 | 0.76904 | 0.78735 | 0.71411 | 0.73242 | 0.077819 | -121.9528 | -122.0215 | 0.16937 | 0.14191 | 0.16022 | 0.064087 | 0.082398 | 5.0629 | 121.7697 | 0.091553 | -0.036621 | 121.9574 | 0.032044 | 122.0123 | 0.10986 | -122.0078 | -121.9849 | 121.8246 | 0.041198 | 41.8488 | 0.09613
3635.8125 | 122.0993 | -0.068665 | 121.9345 | 0.0031279 | 0.012728 | 0.057059 | 0.053228 | -0.0041145 | -0.0055712 | 0.0012496 | -0.005371 | 0.018899 | 0.042208 | -0.016133 | 0.014043 | 0.025246 | -0.0021299 | 41.7709 | 121.9391 | -0.07782 | 121.7331 | 5.0446 | 0.737 | 0.70038 | 0.054932 | -0.018311 | -0.018311 | 0.032043 | 0.15106 | 0.14648 | 0.13275 | -0.009155 | 0.004578 | -0.20142 | 5.1132 | 0.76904 | 0.80566 | 0.7782 | 0.81482 | 0.050354 | -121.9528 | -121.9025 | 0.21973 | 0.20142 | 0.21515 | 0.15106 | 0.16479 | 5.1224 | 121.8109 | 0.16937 | 0.050354 | 122.0169 | 0 | 122.0078 | 0.050354 | -122.0123 | -121.9528 | 121.8018 | 0.10071 | 41.8396 | 0.1236
3637.5781 | 122.0901 | -0.073242 | 121.9345 | -0.012131 | 0.010378 | 0.056631 | 0.054297 | -0.0030463 | -0.0038622 | 0.001677 | -0.0084228 | 0.021463 | 0.041567 | -0.018483 | 0.014684 | 0.023323 | -0.0010617 | 41.7984 | 121.9254 | -0.045776 | 121.7377 | 5.072 | 0.77362 | 0.70038 | 0.064087 | -0.013733 | -0.027466 | 0.032043 | 0.16022 | 0.14191 | 0.13275 | 0.027466 | -0.009155 | -0.19684 | 5.1453 | 0.77362 | 0.84686 | 0.74615 | 0.8194 | 0.045776 | -121.9482 | -121.9025 | 0.23346 | 0.20599 | 0.21515 | 0.16022 | 0.16937 | 5.1178 | 121.7834 | 0.18768 | 0.059509 | 121.9711 | 0.013733 | 121.9986 | 0.059509 | -121.9803 | -121.962 | 121.8109 | 0.10529 | 41.8716 | 0.13733
3639.2812 | 122.0673 | -0.059509 | 121.9482 | -0.012131 | 0.0123 | 0.056845 | 0.053656 | 0.0040033 | -0.0047168 | 0.0003952 | -0.005371 | 0.02189 | 0.041353 | -0.014638 | 0.015112 | 0.022896 | -0.0034117 | 41.9266 | 121.8842 | -0.045776 | 121.7743 | 5.1361 | 0.74616 | 0.737 | 0.086975 | -0.022888 | -0.013733 | 0.018311 | 0.15106 | 0.1236 | 0.10986 | 0.013733 | -0.064087 | -0.17395 | 5.1956 | 0.79651 | 0.80566 | 0.78278 | 0.79193 | 0.045776 | -121.9711 | -121.9299 | 0.21057 | 0.16937 | 0.1831 | 0.1236 | 0.13733 | 5.1819 | 121.8201 | 0.16479 | 0.032044 | 121.9299 | -0.009155 | 121.9437 | 0.036621 | -121.994 | -121.962 | 121.8338 | 0.07782 | 41.9861 | 0.14648
3641.0312 | 122.0352 | -0.07782 | 121.9757 | -0.012131 | 0.014437 | 0.058127 | 0.055151 | 0.0010125 | -0.0027942 | 0.0018906 | -0.0084228 | 0.021676 | 0.040926 | -0.0026745 | 0.017034 | 0.025032 | -0.0021299 | 41.9266 | 121.9345 | -0.07782 | 121.7102 | 5.0674 | 0.67291 | 0.64545 | 0.018311 | 0.009155 | -0.032043 | -0.009155 | 0.07782 | 0.059509 | 0.073242 | 0 | -0.041199 | -0.2655 | 5.1453 | 0.72327 | 0.75073 | 0.72327 | 0.75073 | 0.045777 | -121.9666 | -121.9849 | 0.15564 | 0.15106 | 0.13733 | 0.10529 | 0.091552 | 5.1453 | 121.788 | 0.10986 | 0.022888 | 122.0123 | 0.041198 | 122.0123 | 0.086975 | -122.0535 | -122.0078 | 121.788 | 0.068665 | 42.0044 | 0.096131
3642.7969 | 121.9803 | -0.10071 | 121.9574 | -0.01976 | 0.015291 | 0.057913 | 0.05686 | -0.00048286 | -0.0019396 | 0.0023178 | -0.005371 | 0.022744 | 0.04178 | -0.0097241 | 0.016821 | 0.024819 | -0.0025571 | 41.9678 | 121.9391 | -0.086975 | 121.6873 | 5.0812 | 0.64087 | 0.6134 | -0.032043 | 0.041199 | -0.036621 | -0.045776 | 0.050354 | -0.022888 | 0.032043 | 0.013733 | -0.01831 | -0.27008 | 5.1819 | 0.71411 | 0.74158 | 0.70038 | 0.72784 | 0.064087 | -121.9162 | -122.0032 | 0.15106 | 0.13275 | 0.07782 | 0.068664 | 0.013733 | 5.1682 | 121.7743 | 0.086975 | -0.009155 | 122.0261 | 0.07782 | 122.0398 | 0.14191 | -122.0444 | -121.994 | 121.788 | 0.054932 | 42.0685 | 0.068665
3644.5781 | 121.9894 | -0.11902 | 121.9711 | 0.0031279 | 0.011232 | 0.055777 | 0.054724 | -0.0026191 | -0.005144 | 0.001677 | -0.0084228 | 0.02189 | 0.040285 | -0.010579 | 0.014043 | 0.023537 | -0.0017027 | 41.9769 | 121.962 | -0.082397 | 121.6461 | 5.0629 | 0.65002 | 0.61798 | -0.064087 | 0.013733 | -0.050354 | -0.073242 | 0.045776 | 0.013733 | 0.032043 | 0.036622 | -0.009155 | -0.32501 | 5.1819 | 0.737 | 0.76904 | 0.70038 | 0.73242 | 0.068665 | -121.9574 | -122.0444 | 0.16479 | 0.15106 | 0.13275 | 0.082397 | 0.064087 | 5.1453 | 121.7285 | 0.09613 | -0.022888 | 122.0444 | 0.064087 | 122.081 | 0.13275 | -122.0535 | -122.0215 | 121.7651 | 0.045777 | 42.0959 | 0.054932
3646.3594 | 121.9894 | -0.091553 | 121.9528 | -0.0045011 | 0.0095234 | 0.057486 | 0.053869 | 0.00079894 | -0.0057848 | 0.0035996 | -0.005371 | 0.022103 | 0.044558 | -0.012929 | 0.016393 | 0.023751 | -0.0061887 | 42.0136 | 121.9391 | -0.09613 | 121.6507 | 5.0995 | 0.65002 | 0.62714 | -0.054932 | 0.018311 | -0.036621 | -0.091553 | 0.032043 | 0.004578 | 0.027466 | -0.004577 | -0.013733 | -0.30212 | 5.191 | 0.71869 | 0.74158 | 0.72327 | 0.74615 | 0.054932 | -121.9345 | -122.0444 | 0.1236 | 0.11902 | 0.096131 | 0.064087 | 0.041199 | 5.1956 | 121.7468 | 0.068664 | -0.054932 | 122.0352 | 0.054932 | 122.0306 | 0.10986 | -122.049 | -121.9894 | 121.7422 | 0 | 42.1051 | 0.036621
3648.125 | 122.081 | -0.091553 | 121.9162 | -0.012131 | 0.012087 | 0.057486 | 0.053656 | -0.0060371 | -0.003435 | 0.0012496 | -0.0023192 | 0.020608 | 0.042208 | -0.012715 | 0.015325 | 0.022255 | -0.0010617 | 42.1371 | 121.9254 | -0.050354 | 121.7102 | 5.1819 | 0.72327 | 0.70953 | 0.032043 | -0.018311 | -0.022888 | 0.018311 | 0.13733 | 0.11444 | 0.10529 | 0.041199 | 0.009155 | -0.20599 | 5.2734 | 0.80109 | 0.81482 | 0.75989 | 0.77362 | 0.068665 | -121.9345 | -121.8979 | 0.22888 | 0.19684 | 0.20599 | 0.12817 | 0.13733 | 5.2322 | 121.7606 | 0.16022 | 0.041199 | 121.9757 | 0.004577 | 122.0169 | 0.073242 | -121.9666 | -121.9391 | 121.8018 | 0.10986 | 42.2287 | 0.1236
3649.8906 | 122.0901 | -0.036621 | 121.9162 | -0.01976 | 0.016573 | 0.05834 | 0.056006 | -0.0013373 | -0.0027942 | 0.0021042 | -0.005371 | 0.021463 | 0.042849 | -0.014638 | 0.015966 | 0.02546 | -0.0057615 | 42.2104 | 121.9254 | -0.041199 | 121.7422 | 5.2368 | 0.74616 | 0.73242 | 0.09613 | -0.018311 | 0.009155 | 0.082397 | 0.14648 | 0.12817 | 0.15106 | -0.004578 | 0.009155 | -0.17395 | 5.2734 | 0.76904 | 0.78278 | 0.77362 | 0.78735 | 0.045776 | -121.9345 | -121.8338 | 0.18311 | 0.18768 | 0.1648 | 0.14191 | 0.11902 | 5.278 | 121.7834 | 0.13733 | 0.073242 | 121.9666 | -0.027466 | 121.962 | 0.01831 | -121.9574 | -121.907 | 121.7789 | 0.11902 | 42.247 | 0.13275
3651.6406 | 122.0535 | -0.073242 | 121.9345 | -0.0045011 | 0.011873 | 0.057272 | 0.05451 | -0.0013373 | -0.0045032 | 0.0008224 | -0.005371 | 0.021249 | 0.041567 | -0.015706 | 0.012975 | 0.024391 | -0.0027707 | 42.215 | 121.9025 | -0.041199 | 121.7194 | 5.2368 | 0.73242 | 0.73242 | 0.022888 | -0.022888 | -0.018311 | 0.009155 | 0.09613 | 0.086975 | 0.09613 | 0.032043 | -0.032043 | -0.21515 | 5.3101 | 0.80566 | 0.80566 | 0.77362 | 0.77362 | 0.054931 | -121.9574 | -121.9254 | 0.16937 | 0.16937 | 0.16022 | 0.11444 | 0.10529 | 5.278 | 121.7606 | 0.11444 | 0.027466 | 121.9437 | -0.004577 | 121.9757 | 0.050354 | -121.9757 | -121.9528 | 121.7926 | 0.082397 | 42.2882 | 0.09613
3653.3594 | 122.0306 | -0.082397 | 121.9757 | -0.012131 | 0.015291 | 0.059195 | 0.056006 | 0.00015814 | -0.0045032 | 0.0029586 | -0.0023192 | 0.02189 | 0.042635 | -0.0067333 | 0.017248 | 0.023323 | -0.0053343 | 42.2882 | 121.9345 | -0.068665 | 121.7285 | 5.2414 | 0.72784 | 0.67749 | 0.041199 | 0.009155 | -0.018311 | 0.009155 | 0.086975 | 0.050354 | 0.068665 | 0.013732 | -0.041199 | -0.24719 | 5.3238 | 0.75989 | 0.81024 | 0.74616 | 0.79651 | 0.064086 | -121.9666 | -121.9666 | 0.16937 | 0.15106 | 0.13275 | 0.086976 | 0.068665 | 5.3101 | 121.7972 | 0.10529 | 0.027466 | 122.0032 | 0.027466 | 122.0169 | 0.091552 | -122.0444 | -121.994 | 121.8109 | 0.091552 | 42.3706 | 0.1236
3655.1406 | 121.9757 | -0.10529 | 121.962 | -0.012131 | 0.0123 | 0.059195 | 0.054937 | -0.0015509 | -0.0077074 | 0.0021042 | -0.005371 | 0.022531 | 0.040499 | -0.01421 | 0.015325 | 0.022255 | -0.0057615 | 42.2607 | 121.9482 | -0.091553 | 121.6507 | 5.1865 | 0.64545 | 0.64545 | -0.073242 | 0.004578 | -0.054932 | -0.073242 | 0.041199 | 0.018311 | 0.041199 | 0.013733 | -0.013733 | -0.31128 | 5.2917 | 0.75073 | 0.75073 | 0.737 | 0.737 | 0.050354 | -121.9574 | -122.0352 | 0.14649 | 0.14649 | 0.1236 | 0.096131 | 0.073243 | 5.278 | 121.7422 | 0.096131 | -0.01831 | 122.0398 | 0.05951 | 122.0535 | 0.10986 | -122.0535 | -122.0169 | 121.756 | 0.032044 | 42.366 | 0.032044
3656.9062 | 122.0581 | -0.082397 | 121.9254 | -0.0045011 | 0.012941 | 0.061331 | 0.054297 | -0.00026906 | -0.003435 | 0.0023178 | -0.005371 | 0.019326 | 0.042849 | -0.017628 | 0.014257 | 0.024819 | -0.00042085 | 42.3294 | 121.9162 | -0.045776 | 121.701 | 5.2963 | 0.737 | 0.72327 | 0.009155 | -0.013733 | -0.004578 | -0.009155 | 0.10071 | 0.091553 | 0.091553 | 0.036621 | -0.009155 | -0.2243 | 5.3787 | 0.80566 | 0.8194 | 0.76904 | 0.78278 | 0.077819 | -121.9391 | -121.9345 | 0.18311 | 0.17395 | 0.17395 | 0.096131 | 0.096131 | 5.3421 | 121.7468 | 0.10529 | -0.004577 | 121.962 | -0.009155 | 121.9986 | 0.068664 | -121.9711 | -121.9299 | 121.7834 | 0.073242 | 42.4118 | 0.091552
3658.625 | 121.9986 | -0.10529 | 121.9482 | -0.012131 | 0.010591 | 0.057272 | 0.053869 | -0.0019781 | -0.0042896 | -0.0013138 | -0.005371 | 0.021463 | 0.039858 | -0.013142 | 0.014684 | 0.023964 | -0.0023435 | 42.4118 | 121.8796 | -0.041199 | 121.7422 | 5.3329 | 0.74616 | 0.737 | 0.032043 | -0.013733 | -0.032043 | -0.045776 | 0.073242 | 0.041199 | 0.054932 | 0.064087 | -0.068664 | -0.20599 | 5.4382 | 0.84229 | 0.85144 | 0.7782 | 0.78735 | 0.073243 | -121.962 | -121.994 | 0.17853 | 0.16022 | 0.14649 | 0.086975 | 0.073242 | 5.3741 | 121.7834 | 0.10529 | -0.013733 | 121.9208 | 0.01831 | 121.9849 | 0.091553 | -121.9894 | -121.9803 | 121.8475 | 0.05951 | 42.5171 | 0.13733
3660.3906 | 122.1085 | -0.064087 | 121.8979 | -0.012131 | 0.013796 | 0.057272 | 0.053228 | 0.00015814 | -0.0045032 | 0.0018906 | -0.005371 | 0.020822 | 0.042421 | -0.0097241 | 0.014043 | 0.024605 | -0.0031979 | 42.4622 | 121.8887 | -0.041199 | 121.7926 | 5.4474 | 0.82855 | 0.78278 | 0.10986 | -0.013733 | -0.018311 | 0.059509 | 0.20142 | 0.16937 | 0.14191 | 0.022888 | -0.009155 | -0.10528 | 5.5115 | 0.84686 | 0.89264 | 0.82398 | 0.86975 | 0.045776 | -121.9116 | -121.8384 | 0.2655 | 0.20599 | 0.23346 | 0.16022 | 0.18768 | 5.4886 | 121.8338 | 0.21973 | 0.07782 | 121.9299 | 0.004578 | 121.9528 | 0.050354 | -121.9391 | -121.9162 | 121.8567 | 0.1236 | 42.5262 | 0.17395
3662.1562 | 122.0947 | -0.064087 | 121.9025 | -0.0045011 | 0.015932 | 0.060263 | 0.056646 | -0.00069646 | -0.0015124 | 0.0006088 | -0.005371 | 0.018258 | 0.04114 | -0.017842 | 0.014898 | 0.024605 | -0.0027707 | 42.5217 | 121.907 | -0.032043 | 121.7789 | 5.4108 | 0.79193 | 0.76904 | 0.11444 | -0.027466 | -0.004578 | 0.059509 | 0.15564 | 0.13733 | 0.13275 | 0.032044 | 0.004577 | -0.1236 | 5.4749 | 0.83313 | 0.85602 | 0.80109 | 0.82397 | 0.059509 | -121.9299 | -121.843 | 0.21973 | 0.19684 | 0.20142 | 0.13733 | 0.14191 | 5.4428 | 121.8109 | 0.16022 | 0.064087 | 121.9391 | -0.022888 | 121.9711 | 0.036621 | -121.9345 | -121.907 | 121.843 | 0.1236 | 42.5858 | 0.17853
3663.8594 | 122.081 | -0.064087 | 121.9208 | -0.01976 | 0.011873 | 0.057059 | 0.052374 | -0.0021919 | -0.0057848 | 0.002745 | -0.0084228 | 0.020822 | 0.040071 | -0.010365 | 0.014471 | 0.022255 | -0.0010617 | 42.5354 | 121.875 | -0.045776 | 121.7789 | 5.452 | 0.8194 | 0.78735 | 0.09613 | -0.032043 | -0.013733 | 0.045776 | 0.16479 | 0.15564 | 0.1236 | 0.018311 | -0.045776 | -0.14191 | 5.5161 | 0.85144 | 0.88348 | 0.83313 | 0.86517 | 0.050354 | -121.9528 | -121.875 | 0.22888 | 0.18768 | 0.21973 | 0.13733 | 0.16937 | 5.4977 | 121.8246 | 0.17853 | 0.059509 | 121.9208 | -0.01831 | 121.9391 | 0.032044 | -121.9666 | -121.9345 | 121.843 | 0.10986 | 42.5995 | 0.16022
3665.6406 | 121.9757 | -0.13275 | 121.962 | -0.012131 | 0.011873 | 0.057913 | 0.055578 | -0.0017645 | -0.0047168 | 0.0014634 | -0.005371 | 0.023172 | 0.04178 | -0.013783 | 0.015112 | 0.022896 | -0.0038389 | 42.4805 | 121.9574 | -0.10986 | 121.6553 | 5.3192 | 0.68665 | 0.78735 | -0.068665 | 0.004578 | -0.036621 | -0.068665 | 0.041199 | 0.013733 | 0.036621 | 0.022888 | -0.004578 | -0.3067 | 5.452 | 0.9201 | 0.8194 | 0.89722 | 0.79651 | 0.09613 | -121.9574 | -122.0306 | 0.17395 | 0.16937 | 0.14648 | 0.073242 | 0.050354 | 5.4291 | 121.7651 | 0.07782 | -0.032044 | 122.0673 | 0.041199 | 122.0901 | 0.13733 | -122.0718 | -121.9986 | 121.788 | 0.064086 | 42.6132 | 0.064086
3667.4062 | 122.0856 | -0.068665 | 121.8887 | -0.012131 | 0.01465 | 0.060904 | 0.055365 | 0.00079894 | -0.00044442 | 0.003386 | 0.00073235 | 0.021249 | 0.041994 | -0.0060925 | 0.015539 | 0.025246 | 0.00086095 | 42.5583 | 121.9162 | -0.045776 | 121.7697 | 5.4794 | 0.81024 | 0.79193 | 0.1236 | -0.027466 | 0 | 0.064087 | 0.13733 | 0.11902 | 0.13275 | 0.022889 | 0.027466 | -0.11902 | 5.5481 | 0.8606 | 0.87891 | 0.83771 | 0.85602 | 0.068665 | -121.9162 | -121.8246 | 0.20599 | 0.20142 | 0.18768 | 0.13275 | 0.11902 | 5.5252 | 121.8155 | 0.13733 | 0.064087 | 121.962 | -0.027466 | 121.9849 | 0.041199 | -121.9345 | -121.8887 | 121.8384 | 0.13275 | 42.627 | 0.19226
3669.1719 | 121.9666 | -0.11444 | 121.9711 | 0.0031279 | 0.014864 | 0.060904 | 0.057928 | 0.0020807 | -0.0036486 | -3.1996e-05 | -0.0084228 | 0.022103 | 0.042849 | -0.0090833 | 0.015325 | 0.022683 | -0.0021299 | 42.5629 | 121.9666 | -0.09613 | 121.669 | 5.3467 | 0.62256 | 0.64545 | -0.054932 | 0.013733 | -0.041199 | -0.054932 | 0.004578 | -0.018311 | 0.027466 | 0.018311 | -0.004577 | -0.30212 | 5.4611 | 0.75989 | 0.737 | 0.74158 | 0.71869 | 0.073242 | -121.9574 | -122.0261 | 0.11902 | 0.14191 | 0.09613 | 0.068665 | 0.022888 | 5.4428 | 121.7651 | 0.045777 | -0.013733 | 122.0627 | 0.054932 | 122.081 | 0.12817 | -122.0673 | -122.0123 | 121.7834 | 0.059509 | 42.6773 | 0.059509
3670.875 | 122.0169 | -0.091553 | 121.9345 | -0.012131 | 0.016146 | 0.057272 | 0.056219 | -0.0013373 | -0.0045032 | 0.0023178 | -0.005371 | 0.01954 | 0.043489 | -0.016774 | 0.01618 | 0.025032 | -0.010034 | 42.5995 | 121.9437 | -0.07782 | 121.6965 | 5.4108 | 0.737 | 0.72327 | 0 | 0.027466 | -0.018311 | -0.009155 | 0.086975 | 0.059509 | 0.07782 | 0.013733 | 0.009156 | -0.23804 | 5.5023 | 0.81482 | 0.82855 | 0.80109 | 0.81482 | 0.073242 | -121.907 | -121.9437 | 0.17853 | 0.16937 | 0.15106 | 0.096131 | 0.07782 | 5.4886 | 121.7743 | 0.10529 | 0.009156 | 122.0215 | 0.045777 | 122.0352 | 0.11902 | -122.0123 | -121.9528 | 121.788 | 0.082398 | 42.691 | 0.091553
3672.6562 | 122.0215 | -0.10071 | 121.9528 | -0.01976 | 0.017214 | 0.061972 | 0.057715 | -0.0019781 | -0.005144 | 0.0029586 | -0.005371 | 0.022317 | 0.042421 | -0.0092969 | 0.016393 | 0.024391 | -0.0070433 | 42.6956 | 121.9482 | -0.068665 | 121.7056 | 5.4611 | 0.77362 | 0.70496 | 0.027466 | 0.013733 | -0.022888 | -0.022888 | 0.07782 | 0.022888 | 0.068665 | 0.032043 | -0.004578 | -0.24719 | 5.5618 | 0.80566 | 0.87433 | 0.77362 | 0.84229 | 0.07782 | -121.9391 | -121.9757 | 0.17853 | 0.16937 | 0.1236 | 0.091553 | 0.045776 | 5.5298 | 121.7743 | 0.10071 | 0 | 122.0169 | 0.036621 | 122.0489 | 0.11444 | -122.0215 | -121.9757 | 121.8063 | 0.07782 | 42.7963 | 0.12817
3674.4375 | 122.0123 | -0.10071 | 121.9528 | -0.012131 | 0.015078 | 0.058768 | 0.055365 | 0.0022943 | -0.0045032 | 0.0046676 | -0.005371 | 0.022317 | 0.042421 | -0.0075879 | 0.016821 | 0.025246 | -0.00063445 | 42.659 | 121.9574 | -0.086975 | 121.6553 | 5.3879 | 0.71411 | 0.68207 | -0.064087 | 0.004578 | -0.036621 | -0.054932 | 0.064087 | 0.022888 | 0.054932 | 0.013733 | 0.004577 | -0.29755 | 5.4886 | 0.78278 | 0.81482 | 0.76904 | 0.80109 | 0.064087 | -121.9482 | -122.0078 | 0.1648 | 0.15564 | 0.1236 | 0.091553 | 0.059509 | 5.4749 | 121.7422 | 0.10071 | -0.018311 | 122.0444 | 0.041199 | 122.0581 | 0.10529 | -122.0398 | -121.9894 | 121.756 | 0.045776 | 42.7597 | 0.036621
3676.2031 | 122.0627 | -0.059509 | 121.9025 | -0.012131 | 0.013369 | 0.059195 | 0.053228 | -0.0013373 | -0.0027942 | 0.0012496 | -0.005371 | 0.019326 | 0.042208 | -0.012288 | 0.01383 | 0.0261 | -0.0027707 | 42.7185 | 121.9208 | -0.036621 | 121.7239 | 5.571 | 0.74616 | 0.78278 | 0.073242 | -0.027466 | -0.009155 | 0.036621 | 0.10986 | 0.09613 | 0.10529 | 0.022888 | 0.01831 | -0.17853 | 5.6305 | 0.84229 | 0.80566 | 0.8194 | 0.78278 | 0.050354 | -121.9299 | -121.8658 | 0.16937 | 0.16479 | 0.15564 | 0.11444 | 0.10528 | 5.6076 | 121.7606 | 0.11902 | 0.045776 | 121.9574 | -0.018311 | 121.9803 | 0.032043 | -121.9391 | -121.9116 | 121.7834 | 0.09613 | 42.778 | 0.13275
3677.9688 | 121.9711 | -0.091553 | 121.9528 | -0.012131 | 0.016573 | 0.059622 | 0.057074 | 0.0025079 | -0.0012988 | 0.0021042 | -0.005371 | 0.021463 | 0.041353 | -0.0069469 | 0.018957 | 0.024819 | -0.0042661 | 42.7231 | 121.9437 | -0.059509 | 121.6873 | 5.4932 | 0.71869 | 0.70038 | -0.009155 | 0.022888 | -0.045776 | -0.036621 | 0.036621 | 0.009155 | 0.032043 | 0.032044 | -0.009155 | -0.2655 | 5.5847 | 0.79193 | 0.81024 | 0.75989 | 0.7782 | 0.045777 | -121.9299 | -121.9894 | 0.12817 | 0.1236 | 0.10071 | 0.077819 | 0.054931 | 5.5527 | 121.7468 | 0.082397 | 0.009155 | 122.0032 | 0.068664 | 122.0352 | 0.11444 | -122.0123 | -121.9986 | 121.7789 | 0.054932 | 42.8146 | 0.082398
3679.6719 | 122.0535 | -0.064087 | 121.9208 | -0.012131 | 0.015932 | 0.061545 | 0.054297 | -0.00026906 | -0.0040758 | 0.0021042 | -0.005371 | 0.020181 | 0.041994 | -0.015492 | 0.014684 | 0.026955 | -0.0040525 | 42.7505 | 121.8979 | -0.045776 | 121.7285 | 5.603 | 0.80109 | 0.77362 | 0.073242 | -0.022888 | -0.018311 | 0.027466 | 0.12817 | 0.09613 | 0.091553 | 0.018311 | -0.022888 | -0.19226 | 5.6671 | 0.83771 | 0.86517 | 0.8194 | 0.84686 | 0.045776 | -121.9437 | -121.8933 | 0.19226 | 0.15564 | 0.16022 | 0.10986 | 0.11444 | 5.6488 | 121.7743 | 0.14649 | 0.045777 | 121.9437 | -0.004577 | 121.962 | 0.041199 | -121.9666 | -121.9391 | 121.7926 | 0.091553 | 42.8146 | 0.13733
3681.4219 | 122.1085 | -0.073242 | 121.907 | -0.012131 | 0.013369 | 0.0577 | 0.052801 | -0.0021919 | -0.002367 | 0.0046676 | -0.0023192 | 0.01954 | 0.039644 | -0.018269 | 0.014257 | 0.024605 | -0.0049069 | 42.8055 | 121.8979 | -0.059509 | 121.7606 | 5.6259 | 0.84228 | 0.79193 | 0.082397 | -0.032043 | -0.018311 | 0.050354 | 0.1831 | 0.15106 | 0.14648 | 0.013733 | -0.009155 | -0.14648 | 5.6992 | 0.86517 | 0.91553 | 0.85144 | 0.90179 | 0.054931 | -121.9391 | -121.8567 | 0.25635 | 0.21973 | 0.2243 | 0.16479 | 0.16937 | 5.6854 | 121.8201 | 0.20142 | 0.068665 | 121.9574 | -0.013732 | 121.9711 | 0.041199 | -121.9666 | -121.9254 | 121.8338 | 0.1236 | 42.8787 | 0.15564
3683.1875 | 122.0352 | -0.086975 | 121.9208 | -0.012131 | 0.015932 | 0.061118 | 0.058569 | 0.0035761 | -0.0025806 | 0.001677 | -0.005371 | 0.022103 | 0.041353 | -0.012715 | 0.01383 | 0.02311 | -0.0042661 | 42.7597 | 121.9391 | -0.10071 | 121.669 | 5.5206 | 0.72327 | 0.6958 | 0 | 0 | -0.027466 | -0.004578 | 0.07782 | 0.045776 | 0.073242 | -0.013733 | 0.018311 | -0.25177 | 5.6076 | 0.78278 | 0.81024 | 0.79651 | 0.82398 | 0.059509 | -121.9208 | -121.9254 | 0.16479 | 0.16022 | 0.13275 | 0.10071 | 0.073242 | 5.6213 | 121.7697 | 0.10529 | 0.022888 | 122.0398 | 0.027466 | 122.0261 | 0.086975 | -122.0215 | -121.9482 | 121.756 | 0.082397 | 42.8467 | 0.086975
3684.9531 | 121.9803 | -0.10529 | 121.9574 | -0.01976 | 0.014223 | 0.059622 | 0.053869 | -0.0062507 | -0.005144 | 0.001677 | -0.0023192 | 0.019967 | 0.04114 | -0.014851 | 0.013403 | 0.023323 | -0.00084805 | 42.8238 | 121.9254 | -0.068665 | 121.6736 | 5.5756 | 0.7782 | 0.73242 | -0.032043 | 0.018311 | -0.041199 | -0.064087 | 0.041199 | 0.022888 | 0.032043 | 0.036621 | -0.032043 | -0.28381 | 5.6808 | 0.83771 | 0.88348 | 0.80109 | 0.84686 | 0.064087 | -121.9391 | -122.0215 | 0.14649 | 0.13733 | 0.12817 | 0.073242 | 0.064087 | 5.6442 | 121.7422 | 0.082398 | -0.022888 | 121.994 | 0.05951 | 122.0306 | 0.1236 | -122.0261 | -121.9986 | 121.7789 | 0.041199 | 42.9291 | 0.073243
3686.6719 | 122.113 | -0.064087 | 121.907 | -0.0045011 | 0.012087 | 0.057272 | 0.053442 | -0.0045417 | -0.002367 | 0.0012496 | -0.005371 | 0.022531 | 0.042635 | -0.012288 | 0.014257 | 0.02311 | -0.0031979 | 42.8833 | 121.907 | -0.045776 | 121.7651 | 5.7129 | 0.89722 | 0.8606 | 0.1236 | -0.050354 | 0 | 0.07782 | 0.19684 | 0.16937 | 0.14191 | 0.018311 | 0 | -0.14191 | 5.777 | 0.92468 | 0.9613 | 0.90637 | 0.94299 | 0.064087 | -121.9574 | -121.8292 | 0.26093 | 0.20599 | 0.23346 | 0.14191 | 0.16937 | 5.7587 | 121.8109 | 0.19684 | 0.07782 | 121.9528 | -0.050354 | 121.9711 | 0.013733 | -121.9528 | -121.907 | 121.8292 | 0.14191 | 42.9474 | 0.18768
3688.4375 | 122.0398 | -0.086975 | 121.9162 | -0.0045011 | 0.014223 | 0.058554 | 0.053228 | 0.0029351 | -0.0027942 | 0.001677 | 0.00073235 | 0.019754 | 0.043062 | -0.020405 | 0.01383 | 0.024819 | -0.0031979 | 42.8558 | 121.8887 | -0.064087 | 121.7102 | 5.6442 | 0.75989 | 0.78735 | 0.022888 | -0.013733 | -0.022888 | -0.009155 | 0.10071 | 0.082397 | 0.09613 | 0.022888 | -0.027466 | -0.20599 | 5.7312 | 0.87433 | 0.84686 | 0.85144 | 0.82398 | 0.064087 | -121.9299 | -121.9254 | 0.18768 | 0.1831 | 0.16937 | 0.11902 | 0.10528 | 5.7083 | 121.7743 | 0.1236 | 0.013733 | 121.9528 | 0.009155 | 121.9757 | 0.073242 | -121.9803 | -121.9391 | 121.7972 | 0.07782 | 42.9428 | 0.10986
3690.2188 | 122.0535 | -0.086975 | 121.9254 | -0.0045011 | 0.013369 | 0.059836 | 0.055792 | -5.5462e-05 | -0.005144 | 0.0023178 | -0.005371 | 0.022317 | 0.039644 | -0.013142 | 0.01383 | 0.025032 | -0.0017027 | 42.8741 | 121.9208 | -0.068665 | 121.7285 | 5.6671 | 0.8194 | 0.7782 | 0.032043 | -0.009155 | -0.013733 | 0 | 0.11902 | 0.09613 | 0.10071 | 0.01831 | -0.004578 | -0.19684 | 5.7541 | 0.86517 | 0.90637 | 0.84686 | 0.88806 | 0.073242 | -121.9345 | -121.9254 | 0.20599 | 0.18768 | 0.1831 | 0.11444 | 0.10986 | 5.7358 | 121.7972 | 0.13275 | 0.013733 | 121.9894 | 0.004578 | 122.0078 | 0.07782 | -121.994 | -121.9391 | 121.8155 | 0.086975 | 42.9611 | 0.11902
3691.9375 | 121.9711 | -0.091553 | 121.9437 | -0.01976 | 0.017427 | 0.060049 | 0.057928 | 0.0016535 | -0.0042896 | 0.003386 | -0.0023192 | 0.02189 | 0.042635 | -0.012074 | 0.016607 | 0.023323 | -0.0027707 | 42.8787 | 121.9528 | -0.091553 | 121.637 | 5.5664 | 0.69122 | 0.66376 | -0.064087 | 0.018311 | -0.045776 | -0.068665 | -0.009155 | -0.022888 | 0.032043 | 0 | 0.009155 | -0.3067 | 5.658 | 0.75531 | 0.78278 | 0.75531 | 0.78278 | 0.045777 | -121.9254 | -122.0123 | 0.082398 | 0.1236 | 0.068665 | 0.077819 | 0.022888 | 5.658 | 121.7285 | 0.036621 | -0.022889 | 122.0444 | 0.064087 | 122.0444 | 0.10986 | -122.0352 | -121.9894 | 121.7285 | 0.022888 | 42.9703 | 0.027466
3693.6875 | 122.0764 | -0.073242 | 121.9025 | -0.0045011 | 0.017427 | 0.058981 | 0.056006 | -0.0011237 | -0.0025806 | 0.0006088 | -0.005371 | 0.019967 | 0.041994 | -0.018055 | 0.015966 | 0.023751 | -0.0040525 | 42.952 | 121.8979 | -0.018311 | 121.7834 | 5.777 | 0.86975 | 0.8606 | 0.10986 | -0.045776 | -0.004578 | 0.064087 | 0.15564 | 0.11902 | 0.12817 | 0.054931 | -0.004578 | -0.11902 | 5.8502 | 0.93384 | 0.94299 | 0.87891 | 0.88806 | 0.068664 | -121.9482 | -121.8384 | 0.22888 | 0.20142 | 0.19226 | 0.13275 | 0.1236 | 5.7953 | 121.8018 | 0.16022 | 0.068665 | 121.9162 | -0.041198 | 121.9711 | 0.027466 | -121.9208 | -121.907 | 121.8567 | 0.13733 | 43.0252 | 0.18311
3695.4688 | 121.994 | -0.091553 | 121.9482 | -0.0045011 | 0.015505 | 0.059195 | 0.058142 | 0.0042169 | -0.00087162 | 0.0006088 | -0.0023192 | 0.022531 | 0.04413 | -0.013142 | 0.014684 | 0.022255 | -0.0012753 | 42.9016 | 121.962 | -0.07782 | 121.6461 | 5.6259 | 0.71411 | 0.6958 | -0.054932 | 0.018311 | -0.041199 | -0.041199 | 0.036621 | 0 | 0.041199 | 0.013733 | 0.013733 | -0.30212 | 5.7175 | 0.78735 | 0.80566 | 0.77362 | 0.79193 | 0.050354 | -121.9299 | -121.9894 | 0.12817 | 0.13275 | 0.091553 | 0.082398 | 0.041199 | 5.7037 | 121.7239 | 0.07782 | 0 | 122.0398 | 0.05951 | 122.0535 | 0.10986 | -122.0261 | -121.9894 | 121.7377 | 0.050354 | 42.9932 | 0.036621
3697.1719 | 122.0901 | -0.059509 | 121.8979 | -0.01976 | 0.017641 | 0.059409 | 0.056006 | 0.0037897 | -0.0032214 | 0.0021042 | -0.0023192 | 0.020181 | 0.041353 | -0.012929 | 0.014471 | 0.0261 | -0.0055479 | 42.984 | 121.9025 | -0.045776 | 121.756 | 5.777 | 0.8194 | 0.8194 | 0.09613 | -0.036621 | -0.018311 | 0.064087 | 0.16022 | 0.11444 | 0.16022 | 0.013733 | 0.004578 | -0.14191 | 5.8365 | 0.87891 | 0.87891 | 0.86517 | 0.86517 | 0.041198 | -121.9345 | -121.8338 | 0.21973 | 0.21973 | 0.17395 | 0.17853 | 0.13275 | 5.8228 | 121.8018 | 0.17853 | 0.082398 | 121.9482 | -0.01831 | 121.962 | 0.022888 | -121.9437 | -121.9162 | 121.8155 | 0.1236 | 43.0435 | 0.15564
3698.9375 | 122.049 | -0.07782 | 121.9254 | -0.02739 | 0.014223 | 0.060049 | 0.054937 | 0.0044305 | -0.0049304 | 0.003386 | -0.0084228 | 0.020181 | 0.040499 | -0.015065 | 0.013616 | 0.024391 | -0.0038389 | 43.0161 | 121.907 | -0.018311 | 121.7514 | 5.8273 | 0.8194 | 0.82855 | 0.091553 | -0.045776 | -0.009155 | 0.041199 | 0.1236 | 0.10986 | 0.10071 | 0.059509 | -0.018311 | -0.17395 | 5.9052 | 0.90637 | 0.89722 | 0.84686 | 0.83771 | 0.068665 | -121.9711 | -121.8842 | 0.20142 | 0.17853 | 0.18768 | 0.10986 | 0.11902 | 5.8456 | 121.7697 | 0.13275 | 0.050354 | 121.9254 | -0.036621 | 121.9849 | 0.032044 | -121.9437 | -121.9345 | 121.8292 | 0.11902 | 43.0939 | 0.16937
3700.7188 | 122.0901 | -0.054932 | 121.8796 | -0.01976 | 0.017 | 0.058768 | 0.05686 | 0.0050713 | -0.0030078 | 0.004454 | -0.005371 | 0.020181 | 0.043703 | -0.012929 | 0.017034 | 0.025032 | -0.0049069 | 43.0389 | 121.9025 | -0.054932 | 121.7514 | 5.8319 | 0.82855 | 0.82398 | 0.10529 | -0.027466 | -0.004578 | 0.068665 | 0.16937 | 0.1236 | 0.14191 | 0 | 0.022888 | -0.12817 | 5.8868 | 0.87891 | 0.88348 | 0.87891 | 0.88348 | 0.050354 | -121.907 | -121.8109 | 0.22431 | 0.19684 | 0.17853 | 0.14649 | 0.12817 | 5.8868 | 121.8063 | 0.17395 | 0.073243 | 121.9574 | -0.022888 | 121.9574 | 0.027466 | -121.9345 | -121.8842 | 121.8063 | 0.1236 | 43.0939 | 0.16022
3702.4688 | 121.9986 | -0.082397 | 121.9757 | -0.01976 | 0.015291 | 0.059195 | 0.057287 | 0.0037897 | -0.0053576 | 0.0008224 | -0.011475 | 0.022744 | 0.041353 | -0.014638 | 0.015325 | 0.028023 | -0.0044797 | 43.0252 | 121.907 | -0.073242 | 121.6873 | 5.7816 | 0.83313 | 0.74616 | 0.004578 | 0 | -0.009155 | -0.013733 | 0.050354 | 0.027466 | 0.064087 | 0.009155 | -0.068665 | -0.28839 | 5.864 | 0.82855 | 0.91553 | 0.8194 | 0.90637 | 0.073242 | -121.9757 | -121.9894 | 0.13275 | 0.14648 | 0.10986 | 0.073242 | 0.036621 | 5.8548 | 121.7606 | 0.059509 | -0.004578 | 121.9803 | 0.009155 | 121.9894 | 0.082397 | -122.0489 | -121.9849 | 121.7697 | 0.068664 | 43.1076 | 0.086975
3704.25 | 121.9528 | -0.09613 | 121.9391 | 0.0031279 | 0.0123 | 0.058127 | 0.05686 | 0.00015814 | -0.0057848 | 0.0048812 | -0.005371 | 0.020181 | 0.043062 | -0.014638 | 0.015539 | 0.027169 | -0.0061887 | 42.9932 | 121.9345 | -0.086975 | 121.6415 | 5.7495 | 0.78278 | 0.72327 | -0.064087 | 0.018311 | -0.041199 | -0.064087 | 0.054932 | 0.018311 | 0.032043 | 0.009155 | -0.004578 | -0.29755 | 5.8456 | 0.8194 | 0.87891 | 0.81024 | 0.86975 | 0.054931 | -121.9208 | -122.0032 | 0.15106 | 0.12817 | 0.11444 | 0.073242 | 0.05951 | 5.8365 | 121.7285 | 0.096131 | -0.022888 | 122.0215 | 0.05951 | 122.0306 | 0.11444 | -122.0261 | -121.9803 | 121.7377 | 0.032043 | 43.0893 | 0.032043
3705.9844 | 122.049 | -0.073242 | 121.9345 | -0.01976 | 0.01465 | 0.061118 | 0.054724 | -0.0019781 | -0.001726 | -0.0008866 | -0.0084228 | 0.020395 | 0.040499 | -0.019124 | 0.011907 | 0.0261 | -0.00042085 | 43.0298 | 121.875 | -0.064087 | 121.7056 | 5.8685 | 0.82398 | 0.8194 | 0.045776 | -0.027466 | -0.032043 | 0.004578 | 0.10986 | 0.091553 | 0.086975 | 0.009155 | -0.059509 | -0.22888 | 5.9418 | 0.89264 | 0.89722 | 0.88348 | 0.88806 | 0.041199 | -121.962 | -121.9299 | 0.18311 | 0.16022 | 0.16479 | 0.11902 | 0.1236 | 5.9326 | 121.7697 | 0.14191 | 0.036621 | 121.9391 | 0.004577 | 121.9482 | 0.045776 | -121.9986 | -121.9666 | 121.7789 | 0.07782 | 43.103 | 0.11902
3707.7344 | 122.0993 | -0.050354 | 121.9162 | -0.012131 | 0.011446 | 0.057272 | 0.052588 | -0.0021919 | -0.0049304 | -0.0004592 | -0.005371 | 0.020608 | 0.040712 | -0.022114 | 0.011694 | 0.02546 | -0.00084805 | 43.0801 | 121.8887 | -0.050354 | 121.756 | 5.9143 | 0.92468 | 0.86517 | 0.10986 | -0.018311 | -0.004578 | 0.064087 | 0.19226 | 0.16937 | 0.13733 | 0 | -0.027466 | -0.16022 | 5.9647 | 0.91553 | 0.97504 | 0.91553 | 0.97504 | 0.045776 | -121.9345 | -121.8521 | 0.24261 | 0.18768 | 0.21973 | 0.14191 | 0.17395 | 5.9647 | 121.8063 | 0.19684 | 0.068665 | 121.9391 | -0.013733 | 121.9391 | 0.032043 | -121.9666 | -121.9208 | 121.8063 | 0.11444 | 43.1305 | 0.16022
3709.4531 | 121.9574 | -0.11444 | 121.9528 | -0.01976 | 0.017427 | 0.060904 | 0.056006 | 0.00015814 | -0.0038622 | 0.003386 | -0.0023192 | 0.022103 | 0.043062 | -0.010792 | 0.016607 | 0.02546 | -0.0066159 | 43.0298 | 121.9391 | -0.07782 | 121.6278 | 5.7587 | 0.78735 | 0.72784 | -0.073242 | 0.009155 | -0.041199 | -0.064087 | -0.004578 | -0.032043 | 0.013733 | 0.036621 | -0.013733 | -0.32501 | 5.8731 | 0.84229 | 0.9018 | 0.80566 | 0.86517 | 0.073242 | -121.9437 | -122.0169 | 0.10986 | 0.12817 | 0.082398 | 0.054932 | 0.009156 | 5.8365 | 121.7056 | 0.036621 | -0.022888 | 122.0169 | 0.050354 | 122.0535 | 0.1236 | -122.0306 | -121.994 | 121.7422 | 0.050354 | 43.1442 | 0.041199
3711.1875 | 122.0398 | -0.09613 | 121.9254 | -0.012131 | 0.014864 | 0.060263 | 0.053015 | 0.0016535 | -0.0038622 | 0.0048812 | -0.0023192 | 0.020822 | 0.040285 | -0.015065 | 0.015112 | 0.022469 | -0.0042661 | 43.1168 | 121.8842 | -0.050354 | 121.7468 | 5.9509 | 0.85144 | 0.87891 | 0.064087 | -0.013733 | -0.009155 | 0.013733 | 0.14191 | 0.11902 | 0.09613 | 0.045776 | -0.041199 | -0.17853 | 6.0471 | 0.97504 | 0.94757 | 0.92926 | 0.90179 | 0.086975 | -121.9391 | -121.9116 | 0.23804 | 0.19226 | 0.21515 | 0.10528 | 0.12817 | 6.0013 | 121.7972 | 0.15106 | 0.022888 | 121.9345 | -0.004578 | 121.9803 | 0.082397 | -121.9757 | -121.9345 | 121.843 | 0.10986 | 43.2129 | 0.16022
3713 | 121.9803 | -0.10529 | 121.9391 | -0.0045011 | 0.016146 | 0.059836 | 0.056433 | 0.0025079 | -0.0040758 | 0.0038132 | -0.005371 | 0.023172 | 0.04178 | -0.0075879 | 0.014257 | 0.026314 | -0.0059751 | 43.0756 | 121.9482 | -0.10986 | 121.6278 | 5.8044 | 0.78735 | 0.74158 | -0.045776 | 0.004578 | -0.041199 | -0.054932 | 0.022888 | 0.009155 | 0.045776 | -0.004577 | 0.009155 | -0.31128 | 5.9097 | 0.84686 | 0.89264 | 0.85144 | 0.89722 | 0.064087 | -121.9345 | -121.994 | 0.12817 | 0.15106 | 0.11444 | 0.086975 | 0.050354 | 5.9143 | 121.7377 | 0.064087 | -0.013733 | 122.0581 | 0.045777 | 122.0535 | 0.10986 | -122.049 | -121.9803 | 121.7331 | 0.050354 | 43.1808 | 0.05951
3714.7031 | 122.0215 | -0.073242 | 121.9299 | 0.0031279 | 0.018068 | 0.057913 | 0.058783 | 0.0010125 | -0.0049304 | 0.0046676 | -0.0084228 | 0.022531 | 0.043703 | -0.016774 | 0.017034 | 0.024391 | -0.0049069 | 43.103 | 121.9574 | -0.082397 | 121.6599 | 5.8685 | 0.84228 | 0.77362 | -0.022888 | -0.009155 | -0.036621 | 0 | 0.082397 | 0.045776 | 0.086975 | -0.009155 | 0.027465 | -0.27008 | 5.9418 | 0.84686 | 0.91553 | 0.85602 | 0.92468 | 0.036621 | -121.9391 | -121.9299 | 0.15564 | 0.16022 | 0.11902 | 0.1236 | 0.082397 | 5.9509 | 121.7422 | 0.11902 | 0.036621 | 122.0398 | 0.027466 | 122.0306 | 0.064087 | -122.0123 | -121.9666 | 121.7331 | 0.073242 | 43.1763 | 0.050354
3716.4844 | 121.9711 | -0.10071 | 121.994 | -0.012131 | 0.014437 | 0.057486 | 0.053442 | -0.00048286 | -0.0038622 | 0.004454 | -0.005371 | 0.021463 | 0.040712 | -0.01421 | 0.014043 | 0.0261 | -0.0021299 | 43.0573 | 121.9391 | -0.086975 | 121.637 | 5.8731 | 0.85602 | 0.75531 | -0.054932 | 0.013733 | -0.054932 | -0.082397 | 0.041199 | 0.004578 | 0.027466 | 0.013733 | -0.054932 | -0.35706 | 5.9738 | 0.85602 | 0.95673 | 0.84229 | 0.94299 | 0.045776 | -121.9803 | -122.0764 | 0.14191 | 0.12817 | 0.10529 | 0.082398 | 0.05951 | 5.9601 | 121.7239 | 0.096131 | -0.027465 | 122.0261 | 0.068665 | 122.0398 | 0.11444 | -122.081 | -122.049 | 121.7377 | 0.018311 | 43.158 | 0.045776
3718.2344 | 121.994 | -0.09613 | 121.9482 | -0.0045011 | 0.015505 | 0.0577 | 0.056646 | -5.5462e-05 | -1.7024e-05 | 0.0018906 | -0.0023192 | 0.021035 | 0.042635 | -0.016987 | 0.014043 | 0.025673 | -0.0044797 | 43.1168 | 121.9391 | -0.086975 | 121.637 | 5.8731 | 0.81024 | 0.75073 | -0.059509 | 0.009155 | -0.050354 | -0.054932 | 0.059509 | 0.036621 | 0.041199 | 0.009155 | -0.009155 | -0.31128 | 5.9692 | 0.84686 | 0.90637 | 0.83771 | 0.89722 | 0.045776 | -121.9391 | -122.0032 | 0.15564 | 0.13733 | 0.13275 | 0.091553 | 0.086975 | 5.9601 | 121.7239 | 0.10986 | -0.004578 | 122.0261 | 0.059509 | 122.0352 | 0.10528 | -122.0352 | -121.9986 | 121.7331 | 0.041198 | 43.2129 | 0.036621
3720 | 122.0032 | -0.10986 | 121.9574 | -0.01976 | 0.015291 | 0.059622 | 0.054724 | 0.0025079 | -0.0012988 | 0.0012496 | -0.005371 | 0.022103 | 0.042421 | -0.0086559 | 0.014898 | 0.023751 | -0.0027707 | 43.1076 | 121.9391 | -0.10071 | 121.6415 | 5.9097 | 0.84686 | 0.75073 | -0.054932 | 0.004578 | -0.045776 | -0.07782 | 0.054932 | 0.041199 | 0.041199 | 0.009155 | -0.01831 | -0.31586 | 6.0196 | 0.86059 | 0.95673 | 0.85144 | 0.94757 | 0.064087 | -121.9528 | -122.0352 | 0.16479 | 0.15106 | 0.15106 | 0.086975 | 0.086975 | 6.0104 | 121.7422 | 0.10071 | -0.032044 | 122.0398 | 0.050354 | 122.049 | 0.11444 | -122.0581 | -122.0032 | 121.7514 | 0.032043 | 43.2175 | 0.054931
3721.7656 | 121.9482 | -0.10529 | 121.9391 | -0.012131 | 0.019136 | 0.061118 | 0.057715 | 0.00058534 | -0.00023062 | 0.0029586 | -0.0084228 | 0.023172 | 0.043703 | -0.013569 | 0.016393 | 0.023964 | 0.0010745 | 43.1488 | 121.9482 | -0.091553 | 121.6324 | 5.8868 | 0.80109 | 0.74616 | -0.10071 | 0.022888 | -0.045776 | -0.050354 | 0.004578 | -0.018311 | 0.032043 | 0.013733 | 0.009155 | -0.3067 | 5.9921 | 0.85144 | 0.90637 | 0.83771 | 0.89264 | 0.05951 | -121.9162 | -121.9894 | 0.10986 | 0.13733 | 0.086975 | 0.077819 | 0.027465 | 5.9784 | 121.7239 | 0.050354 | -0.004578 | 122.0398 | 0.068664 | 122.0535 | 0.12817 | -122.0306 | -121.9849 | 121.7377 | 0.054932 | 43.2541 | 0.004578
3723.4688 | 122.1085 | -0.064087 | 121.8979 | -0.012131 | 0.012087 | 0.05834 | 0.053656 | -0.0028327 | -0.0032214 | -3.1996e-05 | -0.005371 | 0.019113 | 0.042849 | -0.016133 | 0.014471 | 0.022896 | -0.0027707 | 43.2083 | 121.8796 | -0.041199 | 121.7377 | 6.0974 | 0.92926 | 0.89264 | 0.10986 | -0.004578 | -0.018311 | 0.059509 | 0.19226 | 0.16937 | 0.14191 | 0.022888 | -0.01831 | -0.16022 | 6.1615 | 0.95673 | 0.99335 | 0.93384 | 0.97046 | 0.045776 | -121.9025 | -121.8384 | 0.25635 | 0.20599 | 0.23346 | 0.16022 | 0.18768 | 6.1386 | 121.7789 | 0.21057 | 0.07782 | 121.9208 | 0.013733 | 121.9437 | 0.059509 | -121.9391 | -121.9162 | 121.8018 | 0.1236 | 43.2724 | 0.17395
3725.25 | 121.9666 | -0.10071 | 121.9254 | -0.0045011 | 0.014437 | 0.056204 | 0.054937 | 0.0012261 | -0.0040758 | 0.0035996 | -0.0023192 | 0.020181 | 0.043489 | -0.012288 | 0.014043 | 0.021614 | -0.0038389 | 43.1992 | 121.8933 | -0.07782 | 121.6553 | 6.0104 | 0.90179 | 0.80566 | -0.041199 | 0.004578 | -0.041199 | -0.068665 | 0.059509 | 0.032043 | 0.018311 | 0.022888 | -0.032043 | -0.27008 | 6.1111 | 0.90637 | 1.0025 | 0.88348 | 0.97961 | 0.059509 | -121.9208 | -121.994 | 0.16022 | 0.11902 | 0.13275 | 0.05951 | 0.073242 | 6.0883 | 121.7331 | 0.10071 | -0.027466 | 121.9711 | 0.045777 | 121.994 | 0.10529 | -122.0032 | -121.9666 | 121.756 | 0.032043 | 43.2999 | 0.059509
3727 | 121.9437 | -0.10986 | 121.9345 | -0.0045011 | 0.018709 | 0.06069 | 0.05686 | 0.0016535 | -0.00044442 | 0.0029586 | -0.0023192 | 0.020395 | 0.039858 | -0.011433 | 0.017461 | 0.024391 | -0.00084805 | 43.1808 | 121.9574 | -0.073242 | 121.6232 | 5.9418 | 0.68665 | 0.74616 | -0.091553 | 0.018311 | -0.041199 | -0.064087 | 0.013733 | -0.018311 | 0.050354 | 0.036621 | 0.022888 | -0.31128 | 6.0516 | 0.85602 | 0.79651 | 0.8194 | 0.75989 | 0.068664 | -121.9162 | -121.9986 | 0.1236 | 0.16022 | 0.091552 | 0.091553 | 0.022888 | 6.015 | 121.6965 | 0.054932 | -0.022888 | 122.0306 | 0.05951 | 122.0673 | 0.12817 | -122.0078 | -121.9757 | 121.7331 | 0.045776 | 43.2907 | 0.01831
3728.7031 | 121.9574 | -0.10529 | 121.9299 | -0.0045011 | 0.018068 | 0.060263 | 0.057715 | -0.0024055 | -0.0030078 | 0.004454 | -0.005371 | 0.021035 | 0.042849 | -0.014424 | 0.015539 | 0.023537 | -0.0036253 | 43.222 | 121.9299 | -0.068665 | 121.6736 | 6.0287 | 0.78278 | 0.81482 | -0.004578 | 0.018311 | -0.032043 | -0.045776 | 0.041199 | 0 | 0.045776 | 0.036621 | 0 | -0.25635 | 6.134 | 0.9201 | 0.88806 | 0.88348 | 0.85144 | 0.073243 | -121.9116 | -121.9757 | 0.14649 | 0.15106 | 0.10529 | 0.077819 | 0.032043 | 6.0974 | 121.7422 | 0.073242 | -0.013733 | 121.9986 | 0.050354 | 122.0352 | 0.1236 | -121.9986 | -121.962 | 121.7789 | 0.05951 | 43.3273 | 0.10071
3730.4688 | 121.9803 | -0.11902 | 121.9528 | -0.0045011 | 0.012728 | 0.059195 | 0.056433 | 0.0040033 | -0.0040758 | 0.002745 | -0.0023192 | 0.023812 | 0.043917 | -0.020619 | 0.014898 | 0.027596 | -0.0029843 | 43.1671 | 121.9299 | -0.073242 | 121.6461 | 6.015 | 0.70038 | 0.82855 | -0.054932 | 0.018311 | -0.041199 | -0.054932 | 0.054932 | 0.027466 | 0.059509 | 0.045777 | -0.022888 | -0.3067 | 6.134 | 0.94757 | 0.8194 | 0.90179 | 0.77362 | 0.07782 | -121.9345 | -122.0078 | 0.17395 | 0.17853 | 0.14649 | 0.10071 | 0.068665 | 6.0883 | 121.7194 | 0.096131 | -0.013733 | 122.0032 | 0.05951 | 122.049 | 0.13733 | -122.0261 | -121.994 | 121.7651 | 0.064087 | 43.2861 | 0.064087
3732.2188 | 122.0673 | -0.073242 | 121.8933 | -0.012131 | 0.019564 | 0.061118 | 0.05686 | 0.0020807 | -0.0010852 | 0.0006088 | -0.005371 | 0.019967 | 0.042849 | -0.016133 | 0.015752 | 0.02546 | -0.0061887 | 43.309 | 121.8979 | -0.045776 | 121.7422 | 6.1661 | 0.99792 | 0.89722 | 0.09613 | -0.022888 | -0.013733 | 0.073242 | 0.16022 | 0.1236 | 0.15564 | 0.027466 | 0.004577 | -0.15106 | 6.2393 | 0.97046 | 1.0712 | 0.94299 | 1.0437 | 0.059509 | -121.9162 | -121.8201 | 0.23346 | 0.22888 | 0.19684 | 0.16937 | 0.13733 | 6.2119 | 121.788 | 0.17395 | 0.086975 | 121.9437 | -0.009155 | 121.9711 | 0.050354 | -121.9391 | -121.907 | 121.8155 | 0.14648 | 43.3823 | 0.16937
3733.9844 | 121.994 | -0.09613 | 121.9391 | -0.0045011 | 0.015505 | 0.057913 | 0.055151 | 0.0035761 | -0.0038622 | 0.0040268 | -0.0023192 | 0.021035 | 0.042635 | -0.023396 | 0.017675 | 0.023964 | -0.0044797 | 43.1992 | 121.9116 | -0.073242 | 121.637 | 6.0562 | 0.5722 | 0.75531 | -0.064087 | 0.018311 | -0.050354 | -0.064087 | 0.050354 | 0.032043 | 0.054932 | 0.022888 | -0.027466 | -0.30212 | 6.1523 | 0.85144 | 0.66833 | 0.82855 | 0.64545 | 0.045776 | -121.9208 | -122.0032 | 0.14648 | 0.15106 | 0.12817 | 0.10529 | 0.082397 | 6.1295 | 121.7102 | 0.10071 | -0.013733 | 121.9849 | 0.068665 | 122.0078 | 0.11444 | -122.0123 | -121.9894 | 121.7331 | 0.032043 | 43.2953 | 0.032043
3735.7031 | 122.0764 | -0.059509 | 121.9025 | 0.0031279 | 0.014009 | 0.058127 | 0.05451 | -0.0013373 | -0.0036486 | 0.0038132 | -0.005371 | 0.020395 | 0.042208 | -0.020833 | 0.011907 | 0.024819 | -0.0042661 | 43.2953 | 121.8613 | -0.050354 | 121.756 | 6.2393 | 1.0208 | 0.91095 | 0.10529 | -0.032043 | 0 | 0.036621 | 0.18768 | 0.16022 | 0.13275 | 0.009155 | -0.041199 | -0.14648 | 6.2988 | 0.97046 | 1.0803 | 0.9613 | 1.0712 | 0.059509 | -121.9345 | -121.8658 | 0.24719 | 0.19226 | 0.21973 | 0.13275 | 0.16022 | 6.2897 | 121.8063 | 0.18768 | 0.036621 | 121.9116 | -0.032043 | 121.9208 | 0.027466 | -121.9528 | -121.9025 | 121.8155 | 0.09613 | 43.3548 | 0.16479
3737.4688 | 121.9666 | -0.11902 | 121.9482 | -0.01976 | 0.019777 | 0.059836 | 0.05921 | 0.0029351 | -0.0021532 | 0.0025314 | -0.005371 | 0.022744 | 0.042208 | -0.011433 | 0.014257 | 0.024819 | -0.0046933 | 43.1854 | 121.9528 | -0.07782 | 121.6095 | 6.0562 | 0.90637 | 0.78278 | -0.068665 | 0.009155 | -0.059509 | -0.059509 | 0.004578 | -0.009155 | 0.032043 | 0.041199 | 0.004578 | -0.33874 | 6.1752 | 0.9018 | 1.0254 | 0.8606 | 0.98419 | 0.05951 | -121.9391 | -122.0078 | 0.1236 | 0.15106 | 0.10986 | 0.091552 | 0.050354 | 6.134 | 121.6873 | 0.064087 | 0 | 122.0306 | 0.068664 | 122.0718 | 0.12817 | -122.0261 | -122.0078 | 121.7285 | 0.05951 | 43.3044 | 0.050354
3739.2344 | 122.0901 | -0.064087 | 121.9162 | -0.01976 | 0.013582 | 0.05834 | 0.053228 | -0.0030463 | -0.0053576 | 0.0031722 | -0.005371 | 0.018258 | 0.042208 | -0.018696 | 0.01383 | 0.0261 | -0.0027707 | 43.3044 | 121.843 | -0.045776 | 121.7651 | 6.2942 | 0.97504 | 0.94757 | 0.10529 | -0.032043 | -0.013733 | 0.059509 | 0.1831 | 0.16022 | 0.12817 | 0.018311 | -0.073242 | -0.15106 | 6.3583 | 1.0117 | 1.0391 | 0.99335 | 1.0208 | 0.050354 | -121.9482 | -121.8567 | 0.24719 | 0.19226 | 0.2243 | 0.14191 | 0.17395 | 6.34 | 121.8109 | 0.19684 | 0.073242 | 121.8887 | -0.01831 | 121.907 | 0.032044 | -121.962 | -121.9299 | 121.8292 | 0.1236 | 43.3685 | 0.16937
3741 | 122.081 | -0.073242 | 121.9025 | -0.012131 | 0.017427 | 0.061118 | 0.056646 | 0.00079894 | -0.0021532 | 0.002745 | -0.005371 | 0.023385 | 0.043489 | -0.0095105 | 0.015539 | 0.023537 | -0.0034117 | 43.2541 | 121.9345 | -0.068665 | 121.6919 | 6.2027 | 0.92468 | 0.85602 | 0.064087 | -0.009155 | -0.018311 | 0.045776 | 0.13733 | 0.11444 | 0.15106 | 0.004577 | 0.032043 | -0.21057 | 6.2759 | 0.92926 | 0.99793 | 0.92468 | 0.99335 | 0.054931 | -121.9116 | -121.8567 | 0.21057 | 0.2243 | 0.18768 | 0.16937 | 0.13275 | 6.2714 | 121.7606 | 0.15564 | 0.064087 | 122.0032 | 0.009156 | 122.0078 | 0.064087 | -121.9711 | -121.9208 | 121.7651 | 0.11902 | 43.3273 | 0.13733
3742.7031 | 122.081 | -0.045776 | 121.9162 | -0.0045011 | 0.016787 | 0.058981 | 0.055792 | -0.00026906 | -1.7024e-05 | 0.001677 | -0.005371 | 0.018472 | 0.04114 | -0.013783 | 0.014471 | 0.025032 | -0.0031979 | 43.2907 | 121.8979 | -0.032043 | 121.7377 | 6.2942 | 0.99335 | 0.88806 | 0.09613 | -0.027466 | -0.009155 | 0.059509 | 0.14648 | 0.11902 | 0.11902 | 0.013733 | -0.018311 | -0.17853 | 6.34 | 0.93384 | 1.0391 | 0.92011 | 1.0254 | 0.036621 | -121.9437 | -121.8567 | 0.19226 | 0.16479 | 0.16479 | 0.12817 | 0.12817 | 6.3263 | 121.7697 | 0.15564 | 0.068664 | 121.9299 | -0.018311 | 121.9437 | 0.01831 | -121.9482 | -121.9254 | 121.7834 | 0.10528 | 43.3365 | 0.14191
3744.4688 | 122.0856 | -0.036621 | 121.9025 | -0.012131 | 0.012087 | 0.059622 | 0.055578 | -0.00091006 | -0.0049304 | 0.0021042 | -0.005371 | 0.020395 | 0.039431 | -0.01421 | 0.012121 | 0.021828 | -0.0019163 | 43.309 | 121.8658 | -0.050354 | 121.7697 | 6.3538 | 1.0712 | 0.9613 | 0.13275 | -0.009155 | -0.004578 | 0.032043 | 0.19684 | 0.15106 | 0.13733 | -0.013733 | -0.036621 | -0.13275 | 6.3904 | 0.99793 | 1.1078 | 1.0117 | 1.1215 | 0.032043 | -121.9116 | -121.8704 | 0.23346 | 0.17395 | 0.18768 | 0.14191 | 0.15564 | 6.4041 | 121.8201 | 0.20142 | 0.036621 | 121.9162 | -0.004577 | 121.9025 | 0.027466 | -121.9528 | -121.907 | 121.8063 | 0.068664 | 43.3456 | 0.16937
3746.25 | 122.049 | -0.054932 | 121.9025 | -0.012131 | 0.013796 | 0.05834 | 0.054724 | 0.00015814 | -0.002367 | 0.003386 | -0.014526 | 0.021249 | 0.041994 | -0.013997 | 0.014898 | 0.024605 | -0.0040525 | 43.2404 | 121.875 | -0.050354 | 121.7102 | 6.2531 | 0.97961 | 0.84686 | 0.022888 | -0.013733 | -0.027466 | 0.004578 | 0.10529 | 0.091553 | 0.09613 | 0.004578 | -0.027466 | -0.19226 | 6.308 | 0.9018 | 1.0345 | 0.89722 | 1.03 | 0.027466 | -121.9162 | -121.8979 | 0.16022 | 0.15106 | 0.14649 | 0.1236 | 0.11902 | 6.3034 | 121.7606 | 0.13275 | 0.032044 | 121.9254 | 0.013733 | 121.9299 | 0.041199 | -121.9528 | -121.9299 | 121.7651 | 0.05951 | 43.2953 | 0.07782
3747.9531 | 122.0764 | -0.073242 | 121.907 | -0.0045011 | 0.018496 | 0.060049 | 0.057715 | -0.00069646 | -0.001726 | 0.0063766 | -0.005371 | 0.022531 | 0.042208 | -0.012074 | 0.015325 | 0.024605 | -0.0061887 | 43.2861 | 121.8933 | -0.073242 | 121.7056 | 6.2851 | 1.0117 | 0.91553 | 0.064087 | -0.027466 | -0.013733 | 0.064087 | 0.14648 | 0.11444 | 0.13733 | 0 | -0.013732 | -0.20142 | 6.3583 | 0.98877 | 1.0849 | 0.98877 | 1.0849 | 0.059509 | -121.9345 | -121.843 | 0.21973 | 0.21057 | 0.18768 | 0.15106 | 0.12817 | 6.3583 | 121.7789 | 0.16022 | 0.07782 | 121.9666 | -0.013733 | 121.9666 | 0.045776 | -121.9803 | -121.9208 | 121.7789 | 0.13733 | 43.3594 | 0.13733
3749.7188 | 121.9711 | -0.09613 | 121.9299 | -0.01976 | 0.019564 | 0.058981 | 0.057074 | 0.0014397 | -0.0032214 | 0.0055222 | -0.0084228 | 0.02189 | 0.040712 | -0.0067333 | 0.01618 | 0.024605 | -0.0038389 | 43.2953 | 121.9208 | -0.050354 | 121.6873 | 6.2759 | 0.89264 | 0.85144 | 0.022888 | 0.004578 | -0.027466 | -0.041199 | 0.064087 | 0.013733 | 0.050354 | 0.045776 | -0.009156 | -0.24262 | 6.3721 | 0.94757 | 0.98877 | 0.90179 | 0.94299 | 0.068664 | -121.9254 | -121.9711 | 0.16022 | 0.14648 | 0.10986 | 0.07782 | 0.041199 | 6.3263 | 121.7377 | 0.091553 | -0.013733 | 121.9711 | 0.032044 | 122.0169 | 0.10071 | -121.9803 | -121.9574 | 121.7834 | 0.054931 | 43.3914 | 0.11902
3751.4844 | 122.0306 | -0.07782 | 121.9025 | -0.02739 | 0.017427 | 0.062399 | 0.054937 | -5.5462e-05 | 0.00041018 | 0.0053086 | -0.0023192 | 0.020608 | 0.040071 | -0.016774 | 0.014257 | 0.0261 | -0.0017027 | 43.3136 | 121.8613 | -0.054932 | 121.7148 | 6.3766 | 1.0117 | 0.92468 | 0.091553 | -0.018311 | -0.013733 | 0.027466 | 0.13275 | 0.091553 | 0.10071 | 0.022888 | -0.041199 | -0.18768 | 6.4545 | 1.0025 | 1.0895 | 0.97962 | 1.0666 | 0.064087 | -121.9208 | -121.875 | 0.21057 | 0.17853 | 0.16937 | 0.11444 | 0.10529 | 6.4316 | 121.7697 | 0.14648 | 0.041199 | 121.9162 | -0.004578 | 121.9391 | 0.059509 | -121.9574 | -121.9162 | 121.7926 | 0.10529 | 43.3914 | 0.16937
3753.1875 | 122.0398 | -0.045776 | 121.8796 | -0.012131 | 0.018282 | 0.060263 | 0.053656 | 0.00058534 | -0.0010852 | 0.0008224 | -0.005371 | 0.022317 | 0.040499 | -0.015706 | 0.014684 | 0.025887 | -0.0021299 | 43.2999 | 121.8887 | -0.036621 | 121.7377 | 6.3904 | 1.0254 | 0.90179 | 0.10986 | -0.027466 | -0.013733 | 0.032043 | 0.13275 | 0.10986 | 0.10529 | 0.009155 | 0.009155 | -0.14191 | 6.4362 | 0.94757 | 1.0712 | 0.93841 | 1.062 | 0.032043 | -121.907 | -121.8475 | 0.17853 | 0.15106 | 0.15564 | 0.11902 | 0.1236 | 6.427 | 121.7743 | 0.14648 | 0.045776 | 121.9254 | -0.013733 | 121.9345 | 0.01831 | -121.9162 | -121.8933 | 121.7834 | 0.077819 | 43.3456 | 0.15564
3754.8906 | 121.9803 | -0.09613 | 121.9299 | -0.012131 | 0.019991 | 0.060263 | 0.058783 | 0.0033623 | -0.0010852 | 0.0046676 | -0.005371 | 0.021676 | 0.043489 | -0.015706 | 0.018743 | 0.022896 | -0.0017027 | 43.309 | 121.9162 | -0.059509 | 121.6919 | 6.3217 | 0.99335 | 0.87891 | 0 | 0.018311 | -0.032043 | -0.022888 | 0.050354 | 0.009155 | 0.045776 | 0.036621 | -0.013733 | -0.23804 | 6.4178 | 0.97504 | 1.0895 | 0.93841 | 1.0529 | 0.064087 | -121.9116 | -121.9528 | 0.14648 | 0.14191 | 0.10528 | 0.077819 | 0.041198 | 6.3812 | 121.7514 | 0.082397 | 0.009155 | 121.9757 | 0.050354 | 122.0123 | 0.11444 | -121.9894 | -121.962 | 121.788 | 0.073242 | 43.4052 | 0.09613
3756.6562 | 121.9299 | -0.11444 | 121.9345 | -0.012131 | 0.020204 | 0.060049 | 0.057928 | 0.0016535 | -0.0015124 | 0.0025314 | -0.005371 | 0.023812 | 0.041994 | -0.015706 | 0.016821 | 0.02311 | -0.0010617 | 43.2861 | 121.9162 | -0.082397 | 121.637 | 6.2897 | 0.90637 | 0.78735 | -0.07782 | 0.018311 | -0.045776 | -0.064087 | 0.013733 | -0.045776 | 0.027466 | 0.032044 | -0.01831 | -0.29755 | 6.4041 | 0.9018 | 1.0208 | 0.86975 | 0.98877 | 0.068665 | -121.9162 | -121.9986 | 0.12817 | 0.14191 | 0.068665 | 0.073242 | 0 | 6.3721 | 121.7194 | 0.059509 | -0.018311 | 121.9986 | 0.064087 | 122.0306 | 0.13275 | -122.0169 | -121.9803 | 121.7514 | 0.050354 | 43.4006 | 0.036621
3758.375 | 121.9574 | -0.10071 | 121.9299 | -0.012131 | 0.016146 | 0.058768 | 0.054083 | 0.0018671 | -0.003435 | 0.0048812 | -0.011475 | 0.020822 | 0.042421 | -0.016347 | 0.015752 | 0.024391 | -0.0053343 | 43.2266 | 121.9116 | -0.10529 | 121.6232 | 6.3126 | 0.91095 | 0.85602 | -0.059509 | 0.018311 | -0.054932 | -0.064087 | 0.032043 | 0.018311 | 0.045776 | -0.004578 | -0.018311 | -0.3067 | 6.4133 | 0.95673 | 1.0117 | 0.9613 | 1.0162 | 0.045776 | -121.9116 | -121.994 | 0.13275 | 0.14648 | 0.11902 | 0.10071 | 0.073243 | 6.4178 | 121.7285 | 0.086975 | -0.009155 | 122.0169 | 0.073243 | 122.0123 | 0.11902 | -122.0352 | -121.9849 | 121.7239 | 0.036621 | 43.3273 | 0.041199
3760.1406 | 122.0856 | -0.054932 | 121.8842 | -0.01976 | 0.014223 | 0.058554 | 0.054724 | -0.0011237 | -0.0047168 | 0.0029586 | -0.005371 | 0.020608 | 0.040712 | -0.013997 | 0.014043 | 0.023964 | -0.0036253 | 43.277 | 121.8658 | -0.036621 | 121.7422 | 6.4957 | 1.1124 | 0.97504 | 0.11444 | -0.036621 | -0.032043 | 0.059509 | 0.19226 | 0.16479 | 0.14191 | 0.018311 | -0.01831 | -0.14191 | 6.5506 | 1.03 | 1.1673 | 1.0117 | 1.149 | 0.022889 | -121.9208 | -121.8246 | 0.24719 | 0.19684 | 0.21973 | 0.17395 | 0.19684 | 6.5323 | 121.7789 | 0.2243 | 0.091552 | 121.9025 | -0.004578 | 121.9208 | 0.018311 | -121.9208 | -121.9162 | 121.7972 | 0.11444 | 43.3319 | 0.16937
3761.9062 | 122.081 | -0.073242 | 121.8979 | -0.01976 | 0.020845 | 0.060263 | 0.057501 | 0.0014397 | -0.0040758 | 0.0038132 | -0.005371 | 0.01954 | 0.04114 | -0.0082287 | 0.012975 | 0.023964 | -0.0034117 | 43.309 | 121.8796 | -0.045776 | 121.756 | 6.5048 | 1.03 | 1.0071 | 0.11902 | -0.032043 | -0.004578 | 0.068665 | 0.16937 | 0.13275 | 0.12817 | 0.027466 | -0.01831 | -0.14191 | 6.5781 | 1.0803 | 1.1032 | 1.0529 | 1.0757 | 0.068664 | -121.9299 | -121.8292 | 0.24261 | 0.20142 | 0.20599 | 0.13275 | 0.13733 | 6.5506 | 121.8018 | 0.17395 | 0.073243 | 121.9254 | -0.027465 | 121.9528 | 0.041199 | -121.9437 | -121.9025 | 121.8292 | 0.14191 | 43.3823 | 0.19226
3763.6094 | 121.9574 | -0.10071 | 121.9299 | -0.012131 | 0.020632 | 0.060049 | 0.059424 | -0.0017645 | -0.0027942 | 0.0025314 | 0.00073235 | 0.022103 | 0.04114 | -0.014638 | 0.015539 | 0.024605 | -0.0027707 | 43.2175 | 121.9345 | -0.07782 | 121.6553 | 6.4041 | 0.87433 | 0.86975 | -0.036621 | 0.018311 | -0.022888 | -0.064087 | 0.022888 | -0.009155 | 0.027466 | 0.022888 | 0.004577 | -0.27466 | 6.5048 | 0.97046 | 0.97504 | 0.94757 | 0.95215 | 0.07782 | -121.9116 | -121.994 | 0.1236 | 0.12817 | 0.091553 | 0.050354 | 0.013733 | 6.4819 | 121.7331 | 0.045776 | -0.041199 | 122.0123 | 0.041199 | 122.0352 | 0.11902 | -122.0078 | -121.9528 | 121.756 | 0.036621 | 43.3182 | 0.064087
3765.375 | 122.113 | -0.050354 | 121.8887 | -0.01976 | 0.012941 | 0.058127 | 0.052588 | -0.0028327 | -0.003435 | 0.0031722 | -0.005371 | 0.021035 | 0.043062 | -0.012501 | 0.013403 | 0.024819 | -0.0051205 | 43.277 | 121.8658 | -0.050354 | 121.7514 | 6.5872 | 1.1261 | 1.0483 | 0.14648 | -0.022888 | 0 | 0.050354 | 0.17853 | 0.16937 | 0.13733 | 0 | -0.022888 | -0.13733 | 6.6376 | 1.0986 | 1.1765 | 1.0986 | 1.1765 | 0.050354 | -121.9116 | -121.8384 | 0.22888 | 0.18768 | 0.21973 | 0.13733 | 0.16937 | 6.6376 | 121.8018 | 0.17853 | 0.050354 | 121.9162 | -0.022888 | 121.9162 | 0.027466 | -121.9391 | -121.8887 | 121.8018 | 0.10071 | 43.3273 | 0.19684
3767.1562 | 122.0764 | -0.054932 | 121.9482 | -0.012131 | 0.015932 | 0.057913 | 0.053869 | 0.0012261 | -0.0038622 | 0.0031722 | -0.005371 | 0.018686 | 0.040712 | -0.0075879 | 0.014471 | 0.025887 | -0.0027707 | 43.2495 | 121.8521 | -0.054932 | 121.7468 | 6.5826 | 1.0941 | 1.0345 | 0.10529 | -0.018311 | 0.004578 | 0.054932 | 0.19226 | 0.15106 | 0.15564 | 0 | -0.09613 | -0.20142 | 6.6376 | 1.0895 | 1.149 | 1.0895 | 1.149 | 0.05951 | -121.9666 | -121.8933 | 0.24719 | 0.21057 | 0.20599 | 0.15106 | 0.14648 | 6.6376 | 121.8018 | 0.18768 | 0.050354 | 121.907 | -0.022889 | 121.907 | 0.036621 | -122.0032 | -121.9437 | 121.8018 | 0.10986 | 43.3044 | 0.16022
3768.9219 | 122.081 | -0.041199 | 121.875 | -0.01976 | 0.018496 | 0.061545 | 0.058355 | 0.0029351 | -0.0030078 | 0.0040268 | -0.0084228 | 0.021249 | 0.040499 | -0.015706 | 0.014471 | 0.024819 | -0.0034117 | 43.2907 | 121.8658 | -0.036621 | 121.7331 | 6.5826 | 1.0757 | 1.0117 | 0.10071 | -0.018311 | -0.009155 | 0.068665 | 0.16022 | 0.13275 | 0.13275 | 0.004578 | -0.009155 | -0.14191 | 6.6238 | 1.0529 | 1.1169 | 1.0483 | 1.1124 | 0.032044 | -121.8933 | -121.8063 | 0.20142 | 0.17395 | 0.17395 | 0.14191 | 0.14191 | 6.6193 | 121.7697 | 0.16937 | 0.07782 | 121.9025 | -0.009156 | 121.907 | 0.022888 | -121.9116 | -121.8842 | 121.7743 | 0.10986 | 43.3319 | 0.14191
3770.6406 | 121.9757 | -0.086975 | 121.9208 | -0.012131 | 0.018709 | 0.060477 | 0.057928 | -0.0017645 | -0.00065802 | 0.0038132 | -0.0084228 | 0.022317 | 0.042208 | -0.023182 | 0.017034 | 0.022469 | -0.0049069 | 43.2175 | 121.9437 | -0.091553 | 121.6736 | 6.5002 | 1.0574 | 0.91095 | 0.018311 | 0.013733 | -0.041199 | -0.013733 | 0.091553 | 0.045776 | 0.068665 | -0.004578 | 0.022889 | -0.24719 | 6.5872 | 0.99793 | 1.1444 | 1.0025 | 1.149 | 0.045776 | -121.907 | -121.9345 | 0.17853 | 0.15564 | 0.13275 | 0.10986 | 0.086975 | 6.5918 | 121.7651 | 0.13275 | 0.027466 | 122.0352 | 0.054932 | 122.0306 | 0.10071 | -122.0123 | -121.962 | 121.7606 | 0.073242 | 43.3044 | 0.10529
3772.4062 | 122.0032 | -0.10071 | 121.9162 | -0.01976 | 0.019777 | 0.060049 | 0.058569 | -0.0013373 | 0.00062378 | 0.0042404 | -0.0023192 | 0.020822 | 0.043062 | -0.013569 | 0.016393 | 0.027596 | -0.0040525 | 43.1534 | 121.9528 | -0.07782 | 121.6507 | 6.4819 | 0.98419 | 0.87891 | 0.004578 | -0.013733 | -0.036621 | 0.013733 | 0.073242 | 0.059509 | 0.082397 | 0.022888 | 0.036621 | -0.2655 | 6.5826 | 0.97961 | 1.0849 | 0.95673 | 1.062 | 0.064087 | -121.9299 | -121.9025 | 0.17395 | 0.18311 | 0.16022 | 0.11902 | 0.09613 | 6.5598 | 121.7285 | 0.10986 | 0.050354 | 122.0306 | 0.022888 | 122.0535 | 0.086975 | -121.994 | -121.9528 | 121.7514 | 0.11444 | 43.2541 | 0.10529
3774.1094 | 121.9803 | -0.10529 | 121.9574 | -0.012131 | 0.018496 | 0.059409 | 0.05686 | 0.0035761 | -0.001726 | 0.0042404 | -0.0023192 | 0.021676 | 0.042421 | -0.0071607 | 0.01618 | 0.0261 | -0.00084805 | 43.1076 | 121.9299 | -0.091553 | 121.6049 | 6.4911 | 1.0757 | 0.8606 | -0.054932 | 0.013733 | -0.041199 | -0.064087 | 0.054932 | 0.027466 | 0.045776 | 0.013733 | -0.027465 | -0.35248 | 6.5964 | 0.96588 | 1.181 | 0.95215 | 1.1673 | 0.064087 | -121.9437 | -122.0215 | 0.16022 | 0.15106 | 0.13275 | 0.086975 | 0.068665 | 6.5826 | 121.6965 | 0.096131 | -0.022888 | 122.0215 | 0.054932 | 122.0352 | 0.11902 | -122.049 | -121.9986 | 121.7102 | 0.041199 | 43.2129 | 0.050354
3775.9062 | 122.0947 | -0.059509 | 121.8842 | -0.01976 | 0.015718 | 0.057486 | 0.051947 | 0.0012261 | -0.0042896 | 0.001677 | -0.0084228 | 0.017617 | 0.041353 | -0.0097241 | 0.015539 | 0.024605 | -0.0057615 | 43.2083 | 121.843 | -0.041199 | 121.7514 | 6.72 | 1.1581 | 1.03 | 0.10986 | -0.041199 | -0.004578 | 0.054932 | 0.18768 | 0.16022 | 0.12817 | 0.01831 | -0.041198 | -0.13275 | 6.7795 | 1.0895 | 1.2177 | 1.0712 | 1.1993 | 0.054931 | -121.9254 | -121.8292 | 0.24719 | 0.18768 | 0.21973 | 0.13275 | 0.16479 | 6.7612 | 121.7926 | 0.19226 | 0.05951 | 121.8842 | -0.036621 | 121.9025 | 0.01831 | -121.9254 | -121.8887 | 121.8109 | 0.11444 | 43.2678 | 0.16937
3777.6875 | 121.994 | -0.10529 | 121.9162 | -0.01976 | 0.015718 | 0.058127 | 0.057287 | 0.0048577 | -0.0032214 | 0.0025314 | -0.005371 | 0.023385 | 0.040712 | -0.01186 | 0.016607 | 0.024819 | -0.0046933 | 43.1351 | 121.907 | -0.086975 | 121.6324 | 6.5414 | 1.0254 | 0.9201 | -0.073242 | 0 | -0.059509 | -0.036621 | 0.073242 | 0.032043 | 0.073242 | 0.018311 | -0.009156 | -0.28381 | 6.6467 | 1.0254 | 1.1307 | 1.0071 | 1.1124 | 0.045777 | -121.9162 | -121.9528 | 0.17853 | 0.17853 | 0.13733 | 0.13275 | 0.091552 | 6.6284 | 121.7194 | 0.13275 | 0.022888 | 121.994 | 0.059509 | 122.0123 | 0.10529 | -122.0032 | -121.9757 | 121.7377 | 0.068665 | 43.2404 | 0.032044
3779.4375 | 121.9666 | -0.09613 | 121.9254 | -0.0045011 | 0.019777 | 0.058127 | 0.055578 | 0.00079894 | -0.001726 | 0.0055222 | -0.005371 | 0.021463 | 0.044344 | -0.012715 | 0.019384 | 0.022469 | -0.0068295 | 43.1717 | 121.9116 | -0.07782 | 121.6827 | 6.6193 | 1.1078 | 0.93842 | 0.022888 | 0.018311 | -0.041199 | -0.013733 | 0.082397 | 0.036621 | 0.068665 | 0.01831 | -0.013733 | -0.24262 | 6.7154 | 1.0345 | 1.2039 | 1.0162 | 1.1856 | 0.054931 | -121.907 | -121.9391 | 0.17853 | 0.16479 | 0.13275 | 0.10986 | 0.07782 | 6.6971 | 121.7606 | 0.1236 | 0.027466 | 121.9894 | 0.05951 | 122.0078 | 0.11444 | -122.0032 | -121.9666 | 121.7789 | 0.082397 | 43.2678 | 0.11902
3781.1562 | 121.994 | -0.082397 | 121.907 | -0.0045011 | 0.020204 | 0.060477 | 0.059637 | -0.0034735 | -0.0019396 | 0.0031722 | -0.0084228 | 0.022958 | 0.042421 | -0.013142 | 0.015112 | 0.02546 | -0.0036253 | 43.1396 | 121.9299 | -0.086975 | 121.6187 | 6.5964 | 1.0666 | 0.95215 | -0.013733 | 0.004578 | -0.050354 | 0 | 0.068665 | 0.045776 | 0.082397 | -0.004578 | 0.022889 | -0.28839 | 6.6788 | 1.0345 | 1.149 | 1.0391 | 1.1536 | 0.032043 | -121.9025 | -121.907 | 0.15106 | 0.16479 | 0.12817 | 0.13275 | 0.09613 | 6.6833 | 121.7056 | 0.11902 | 0.050354 | 122.0169 | 0.054932 | 122.0123 | 0.086975 | -121.994 | -121.9574 | 121.701 | 0.082397 | 43.222 | 0.068664
3782.9219 | 121.9528 | -0.091553 | 121.9208 | -0.012131 | 0.014864 | 0.06069 | 0.053228 | -0.0021919 | -0.002367 | 0.003386 | 0.00073235 | 0.020181 | 0.041567 | -0.021473 | 0.01618 | 0.024605 | -0.0031979 | 43.1213 | 121.875 | -0.064087 | 121.6507 | 6.6559 | 1.1124 | 1.0117 | -0.032043 | 0.009155 | -0.041199 | -0.068665 | 0.041199 | 0.018311 | 0.032043 | 0.027466 | -0.045776 | -0.27008 | 6.7474 | 1.1032 | 1.2039 | 1.0757 | 1.1765 | 0.050354 | -121.9116 | -121.9894 | 0.13275 | 0.1236 | 0.10986 | 0.073242 | 0.05951 | 6.72 | 121.7148 | 0.082398 | -0.027466 | 121.9391 | 0.050354 | 121.9666 | 0.10071 | -121.9849 | -121.962 | 121.7422 | 0.022888 | 43.2129 | 0.05951
3784.6719 | 121.9666 | -0.1236 | 121.9437 | -0.012131 | 0.018068 | 0.058768 | 0.058783 | -0.00048286 | -0.0010852 | 0.0018906 | -0.005371 | 0.021249 | 0.043062 | -0.0090833 | 0.014257 | 0.023751 | 0.00021995 | 43.0115 | 121.9025 | -0.086975 | 121.6049 | 6.6238 | 1.1307 | 0.92926 | -0.068665 | 0.004578 | -0.068665 | -0.068665 | 0.032043 | 0.018311 | 0.045776 | 0.036621 | -0.041199 | -0.33875 | 6.7474 | 1.0529 | 1.2543 | 1.0162 | 1.2177 | 0.054931 | -121.9391 | -122.0123 | 0.15564 | 0.16937 | 0.14191 | 0.11444 | 0.086976 | 6.7108 | 121.6919 | 0.10071 | 0 | 121.9894 | 0.073243 | 122.0261 | 0.12817 | -122.0306 | -122.0123 | 121.7285 | 0.054931 | 43.1351 | 0.054931
3786.4375 | 122.0673 | -0.054932 | 121.9162 | -0.012131 | 0.015505 | 0.05834 | 0.054724 | 0.0014397 | -0.0032214 | 0.0053086 | -0.0084228 | 0.020181 | 0.043276 | -0.019337 | 0.013403 | 0.022042 | -0.0031979 | 43.0847 | 121.843 | -0.054932 | 121.7743 | 6.8298 | 1.2268 | 1.1261 | 0.1236 | -0.027466 | -0.013733 | 0.059509 | 0.20599 | 0.16479 | 0.13275 | 0 | -0.073242 | -0.14191 | 6.8848 | 1.181 | 1.2817 | 1.181 | 1.2817 | 0.041199 | -121.9437 | -121.8567 | 0.26093 | 0.18768 | 0.21973 | 0.14648 | 0.17853 | 6.8848 | 121.8292 | 0.21973 | 0.073242 | 121.8979 | -0.013733 | 121.8979 | 0.027466 | -121.9711 | -121.9299 | 121.8292 | 0.11444 | 43.1396 | 0.17853
3788.1406 | 122.0718 | -0.041199 | 121.8842 | -0.01976 | 0.019777 | 0.061331 | 0.05451 | 0.00015814 | -0.00087162 | 0.004454 | -0.0023192 | 0.019113 | 0.042421 | -0.015492 | 0.014257 | 0.025032 | -0.0025571 | 43.1076 | 121.8704 | -0.036621 | 121.7377 | 6.8344 | 1.1673 | 1.062 | 0.11444 | -0.041199 | -0.004578 | 0.073242 | 0.16479 | 0.1236 | 0.13733 | 0.004578 | -0.013733 | -0.14648 | 6.8756 | 1.1032 | 1.2085 | 1.0986 | 1.2039 | 0.036621 | -121.9254 | -121.8109 | 0.20599 | 0.17853 | 0.16479 | 0.14191 | 0.12817 | 6.871 | 121.7743 | 0.16937 | 0.07782 | 121.907 | -0.036621 | 121.9116 | 0 | -121.9208 | -121.8887 | 121.7789 | 0.11444 | 43.1488 | 0.15564
3789.9219 | 121.9254 | -0.09613 | 121.9208 | -0.012131 | 0.0217 | 0.061758 | 0.058996 | 0.0042169 | -0.0025806 | 0.002745 | -0.0084228 | 0.022958 | 0.042208 | -0.018055 | 0.017248 | 0.023323 | -0.0034117 | 42.9932 | 121.9528 | -0.07782 | 121.637 | 6.7154 | 1.0391 | 0.95673 | -0.050354 | 0.013733 | -0.050354 | -0.059509 | 0.027466 | -0.018311 | 0.018311 | 0.01831 | 0.032044 | -0.28381 | 6.8115 | 1.0529 | 1.1353 | 1.0345 | 1.1169 | 0.045776 | -121.907 | -121.9803 | 0.1236 | 0.11444 | 0.077819 | 0.068665 | 0.032043 | 6.7932 | 121.7148 | 0.07782 | -0.009155 | 122.0306 | 0.064087 | 122.049 | 0.10986 | -121.9986 | -121.9711 | 121.7331 | 0.036621 | 43.0893 | 0.045776
3791.7031 | 121.9345 | -0.091553 | 121.9116 | -0.0045011 | 0.022341 | 0.060904 | 0.060705 | 0.0014397 | -0.00065802 | 0.0055222 | -0.005371 | 0.022103 | 0.043703 | -0.011433 | 0.018316 | 0.024605 | -0.0031979 | 43.0069 | 121.9162 | -0.068665 | 121.637 | 6.7245 | 1.1032 | 0.97504 | -0.050354 | 0.018311 | -0.041199 | -0.054932 | 0.018311 | -0.013733 | 0.045776 | 0.022888 | 0.004578 | -0.27466 | 6.8161 | 1.0666 | 1.1948 | 1.0437 | 1.1719 | 0.050354 | -121.8933 | -121.9666 | 0.10986 | 0.13733 | 0.07782 | 0.086975 | 0.027466 | 6.7932 | 121.7056 | 0.05951 | -0.013733 | 121.9849 | 0.05951 | 122.0078 | 0.10986 | -121.9803 | -121.9528 | 121.7285 | 0.036621 | 43.0984 | 0.041199
3793.4062 | 122.0993 | -0.045776 | 121.875 | -0.012131 | 0.018496 | 0.058554 | 0.05451 | -0.0041145 | -0.00087162 | 0.0074448 | -0.011475 | 0.019754 | 0.042208 | -0.019551 | 0.015539 | 0.025246 | -0.0044797 | 43.0344 | 121.8613 | -0.054932 | 121.7422 | 6.9443 | 1.2177 | 1.1353 | 0.14648 | -0.013733 | 0 | 0.054932 | 0.18768 | 0.18768 | 0.14191 | -0.009156 | -0.013733 | -0.13275 | 6.9901 | 1.181 | 1.2634 | 1.1902 | 1.2726 | 0.045776 | -121.8887 | -121.8201 | 0.23346 | 0.18768 | 0.23346 | 0.14191 | 0.18768 | 6.9992 | 121.7972 | 0.18768 | 0.054932 | 121.9162 | -0.013733 | 121.907 | 0.032043 | -121.9299 | -121.875 | 121.788 | 0.10071 | 43.0801 | 0.19226
3795.1562 | 121.9391 | -0.1236 | 121.9162 | -0.0045011 | 0.016146 | 0.0577 | 0.058142 | -5.5462e-05 | -0.003435 | 0.0048812 | 0.00073235 | 0.020181 | 0.039858 | -0.013783 | 0.013616 | 0.023323 | -0.0023435 | 42.9337 | 121.9025 | -0.082397 | 121.6232 | 6.752 | 1.0757 | 0.98419 | -0.059509 | 0.027466 | -0.036621 | -0.07782 | 0.036621 | 0.013733 | 0.022888 | 0.041199 | -0.013733 | -0.29297 | 6.8756 | 1.1078 | 1.1993 | 1.0666 | 1.1581 | 0.086975 | -121.8887 | -121.994 | 0.16022 | 0.14648 | 0.13733 | 0.059509 | 0.050354 | 6.8344 | 121.7056 | 0.073242 | -0.041199 | 121.9849 | 0.064087 | 122.0261 | 0.15106 | -121.9986 | -121.9528 | 121.7468 | 0.045776 | 43.0573 | 0.064087
3796.8594 | 121.962 | -0.10071 | 121.9254 | -0.01976 | 0.020204 | 0.061331 | 0.058355 | 0.0018671 | -0.0021532 | 0.0048812 | -0.005371 | 0.02189 | 0.041567 | -0.0060925 | 0.016821 | 0.022896 | -0.0021299 | 43.0069 | 121.8979 | -0.086975 | 121.6827 | 6.839 | 1.1673 | 0.91553 | 0.018311 | 0.018311 | -0.022888 | -0.018311 | 0.068665 | 0.032043 | 0.064087 | 0.013733 | -0.027466 | -0.24262 | 6.9397 | 1.0162 | 1.268 | 1.0025 | 1.2543 | 0.07782 | -121.907 | -121.9437 | 0.16937 | 0.1648 | 0.13275 | 0.086975 | 0.054931 | 6.926 | 121.7697 | 0.091553 | 0.004577 | 121.9849 | 0.041199 | 121.9986 | 0.11902 | -122.0123 | -121.9482 | 121.7834 | 0.082397 | 43.1076 | 0.11902
3798.625 | 122.0444 | -0.045776 | 121.8842 | -0.012131 | 0.0217 | 0.062399 | 0.056006 | -0.00069646 | 0.00041018 | 0.005095 | -0.005371 | 0.021035 | 0.040712 | -0.0088695 | 0.015325 | 0.025673 | -0.0029843 | 42.8741 | 121.8887 | -0.032043 | 121.7194 | 6.9534 | 1.2863 | 1.0941 | 0.1236 | -0.027466 | -0.009155 | 0.050354 | 0.16022 | 0.1236 | 0.11444 | 0.013733 | 0.004578 | -0.1648 | 6.9992 | 1.1398 | 1.3321 | 1.1261 | 1.3184 | 0.036621 | -121.9116 | -121.8338 | 0.20599 | 0.16022 | 0.16937 | 0.1236 | 0.13275 | 6.9855 | 121.7514 | 0.16937 | 0.059509 | 121.9208 | -0.018311 | 121.9345 | 0.01831 | -121.9162 | -121.8933 | 121.7651 | 0.09613 | 42.9199 | 0.16937
3800.3906 | 121.9757 | -0.1236 | 121.9208 | -0.0045011 | 0.01935 | 0.059836 | 0.057287 | 0.0022943 | -0.00087162 | 0.0046676 | -0.0023192 | 0.022317 | 0.040712 | -0.016987 | 0.015966 | 0.025887 | -0.0042661 | 42.8696 | 121.9299 | -0.091553 | 121.6187 | 6.8298 | 1.1993 | 0.99792 | -0.064087 | 0.018311 | -0.050354 | -0.041199 | 0.068665 | 0.032043 | 0.068665 | 0.032043 | 0.009156 | -0.30212 | 6.9534 | 1.1215 | 1.3229 | 1.0895 | 1.2909 | 0.073242 | -121.9025 | -121.962 | 0.19226 | 0.19226 | 0.15564 | 0.11902 | 0.082397 | 6.9214 | 121.7102 | 0.11902 | 0.009155 | 122.0215 | 0.068665 | 122.0535 | 0.14191 | -122.0123 | -121.9711 | 121.7422 | 0.082397 | 42.9932 | 0.059509
3802.0938 | 121.9391 | -0.09613 | 121.9391 | -0.01976 | 0.022341 | 0.060904 | 0.058996 | 0.0020807 | -0.00087162 | 0.0063766 | -0.005371 | 0.022958 | 0.042421 | -0.012929 | 0.013403 | 0.025673 | -0.0040525 | 42.8558 | 121.9299 | -0.09613 | 121.5958 | 6.8253 | 1.0254 | 1.0025 | -0.036621 | 0.013733 | -0.068665 | -0.059509 | 0.018311 | -0.009155 | 0.036621 | 0 | -0.009155 | -0.34332 | 6.9214 | 1.0986 | 1.1215 | 1.0986 | 1.1215 | 0.027465 | -121.9254 | -121.9986 | 0.11444 | 0.13275 | 0.086975 | 0.10529 | 0.05951 | 6.9214 | 121.6919 | 0.086976 | 0.009156 | 122.0261 | 0.082398 | 122.0261 | 0.10986 | -122.0352 | -122.0078 | 121.6919 | 0.036621 | 42.952 | 0.059509
3803.8594 | 122.0718 | -0.041199 | 121.8796 | -0.012131 | 0.020632 | 0.061545 | 0.054297 | -0.00091006 | -0.0012988 | 0.006163 | -0.005371 | 0.019326 | 0.04114 | -0.012501 | 0.015539 | 0.025673 | -0.0034117 | 42.9245 | 121.8658 | -0.045776 | 121.7377 | 7.0084 | 1.2451 | 1.1215 | 0.10986 | -0.032043 | -0.013733 | 0.082397 | 0.16479 | 0.13275 | 0.15564 | -0.004577 | -0.013733 | -0.14191 | 7.0496 | 1.1627 | 1.2863 | 1.1673 | 1.2909 | 0.027466 | -121.9116 | -121.7972 | 0.20599 | 0.19684 | 0.17395 | 0.16937 | 0.14648 | 7.0541 | 121.7834 | 0.17853 | 0.09613 | 121.9116 | -0.01831 | 121.907 | 0.009156 | -121.9254 | -121.8933 | 121.7789 | 0.1236 | 42.9657 | 0.15106
3805.625 | 121.9894 | -0.10529 | 121.8979 | -0.012131 | 0.019564 | 0.059836 | 0.057287 | 0.00015814 | -1.7024e-05 | 0.0046676 | -0.0023192 | 0.022317 | 0.042849 | -0.019124 | 0.014471 | 0.024178 | -0.0038389 | 42.8696 | 121.907 | -0.073242 | 121.6736 | 6.9489 | 1.1078 | 1.0849 | 0.036621 | 0.027466 | -0.036621 | 0 | 0.091553 | 0.054932 | 0.09613 | 0.032044 | 0.009155 | -0.2243 | 7.0541 | 1.1902 | 1.2131 | 1.1581 | 1.181 | 0.068665 | -121.8704 | -121.8979 | 0.19684 | 0.20142 | 0.16022 | 0.13275 | 0.091553 | 7.0221 | 121.7468 | 0.12817 | 0.036621 | 121.9803 | 0.064087 | 122.0123 | 0.13275 | -121.9711 | -121.9345 | 121.7789 | 0.10529 | 42.9749 | 0.14191
3807.3906 | 121.9986 | -0.10071 | 121.907 | -0.012131 | 0.021273 | 0.061545 | 0.056646 | 0.0018671 | -0.00065802 | 0.003386 | -0.005371 | 0.02189 | 0.041353 | -0.0084423 | 0.015752 | 0.024605 | -0.0025571 | 42.8329 | 121.8979 | -0.082397 | 121.6553 | 6.9901 | 1.3229 | 1.0666 | 0.036621 | 0.009155 | -0.027466 | -0.004578 | 0.082397 | 0.068665 | 0.07782 | 0.018311 | -0.009155 | -0.25177 | 7.0908 | 1.1673 | 1.4236 | 1.149 | 1.4053 | 0.073242 | -121.8979 | -121.9116 | 0.18311 | 0.17853 | 0.16937 | 0.10529 | 0.096131 | 7.0724 | 121.7377 | 0.10986 | 0.022888 | 121.9803 | 0.036621 | 121.9986 | 0.10986 | -121.9894 | -121.9345 | 121.756 | 0.09613 | 42.9337 | 0.13733
3809.0938 | 121.9345 | -0.1236 | 121.9299 | -0.012131 | 0.018923 | 0.059622 | 0.055792 | -5.5462e-05 | -0.0012988 | 0.0025314 | -0.005371 | 0.019967 | 0.041994 | -0.014424 | 0.015752 | 0.023537 | -0.0014891 | 42.778 | 121.8979 | -0.068665 | 121.6187 | 6.9763 | 1.1948 | 1.0071 | -0.036621 | 0.022888 | -0.032043 | -0.082397 | 0.045776 | 0.022888 | 0.041199 | 0.054931 | -0.032044 | -0.31128 | 7.0999 | 1.1307 | 1.3184 | 1.0757 | 1.2634 | 0.091553 | -121.907 | -122.0123 | 0.16937 | 0.16479 | 0.14648 | 0.073242 | 0.054931 | 7.045 | 121.6873 | 0.077819 | -0.050354 | 121.9666 | 0.054931 | 122.0215 | 0.14648 | -121.9986 | -121.962 | 121.7422 | 0.041199 | 42.9016 | 0.086975
3810.8594 | 121.9894 | -0.10529 | 121.9208 | 0.0031279 | 0.021913 | 0.061545 | 0.057501 | -0.0013373 | -0.00065802 | 0.0087264 | -0.0084228 | 0.024026 | 0.043703 | -0.013356 | 0.014684 | 0.023537 | -0.0051205 | 42.7643 | 121.8979 | -0.073242 | 121.6599 | 7.0724 | 1.2131 | 1.0757 | 0.032043 | 0.009155 | -0.050354 | -0.009155 | 0.09613 | 0.054932 | 0.073242 | 0.032044 | -0.022888 | -0.26093 | 7.1777 | 1.181 | 1.3184 | 1.149 | 1.2863 | 0.054932 | -121.9116 | -121.9299 | 0.20142 | 0.17853 | 0.16022 | 0.1236 | 0.10529 | 7.1457 | 121.7331 | 0.14648 | 0.041199 | 121.9711 | 0.059509 | 122.0032 | 0.11444 | -121.994 | -121.9711 | 121.7651 | 0.096131 | 42.8696 | 0.13733
3812.5625 | 122.0627 | -0.050354 | 121.8796 | -0.012131 | 0.022982 | 0.061545 | 0.054937 | -0.0017645 | -0.0010852 | 0.0031722 | -0.0084228 | 0.020181 | 0.041994 | -0.013997 | 0.015966 | 0.02546 | -0.0044797 | 42.7368 | 121.907 | -0.073242 | 121.701 | 7.1091 | 1.3046 | 1.0941 | 0.073242 | -0.013733 | -0.018311 | 0.068665 | 0.15106 | 0.12817 | 0.15106 | -0.022888 | 0.027465 | -0.17853 | 7.1594 | 1.1444 | 1.355 | 1.1673 | 1.3779 | 0.032043 | -121.8933 | -121.8109 | 0.20142 | 0.20142 | 0.17853 | 0.16937 | 0.14649 | 7.1823 | 121.7743 | 0.16937 | 0.086976 | 121.9803 | 0.004578 | 121.9574 | 0.036621 | -121.9528 | -121.8979 | 121.7514 | 0.11902 | 42.7872 | 0.1236
3814.3281 | 121.9894 | -0.07782 | 121.9025 | -0.012131 | 0.022982 | 0.062399 | 0.057287 | 0.0025079 | -0.0010852 | 0.0053086 | -0.0023192 | 0.020395 | 0.042849 | -0.019551 | 0.015752 | 0.024605 | -0.0051205 | 42.7002 | 121.8887 | -0.068665 | 121.6553 | 7.1228 | 1.236 | 1.1078 | 0.022888 | 0.022888 | -0.018311 | -0.004578 | 0.10071 | 0.054932 | 0.082397 | 0.009155 | -0.013733 | -0.24719 | 7.2006 | 1.1856 | 1.3138 | 1.1765 | 1.3046 | 0.059509 | -121.8796 | -121.907 | 0.17853 | 0.16022 | 0.13275 | 0.10071 | 0.073243 | 7.1915 | 121.7239 | 0.11902 | 0.013733 | 121.9574 | 0.041199 | 121.9666 | 0.10071 | -121.9711 | -121.9208 | 121.7331 | 0.073242 | 42.778 | 0.10071
3816.0312 | 122.0947 | -0.064087 | 121.8613 | -0.01976 | 0.015505 | 0.058768 | 0.05152 | -0.0015509 | -0.00087162 | 0.0031722 | -0.005371 | 0.019113 | 0.040071 | -0.01421 | 0.013189 | 0.026955 | -0.0017027 | 42.6727 | 121.8384 | -0.032043 | 121.7239 | 7.2418 | 1.3321 | 1.2131 | 0.12817 | -0.027466 | 0 | 0.045776 | 0.19226 | 0.16022 | 0.1236 | 0.032044 | -0.022888 | -0.13733 | 7.3059 | 1.2772 | 1.3962 | 1.2451 | 1.3641 | 0.064087 | -121.8887 | -121.8155 | 0.25635 | 0.18768 | 0.2243 | 0.1236 | 0.16022 | 7.2739 | 121.756 | 0.19226 | 0.045776 | 121.8704 | -0.027466 | 121.9025 | 0.036621 | -121.8933 | -121.8613 | 121.788 | 0.10986 | 42.7368 | 0.19226
3817.7969 | 122.0673 | -0.068665 | 121.8842 | -0.0045011 | 0.021273 | 0.06304 | 0.057928 | 0.0029351 | 0.00083738 | 0.0042404 | -0.0023192 | 0.021035 | 0.04178 | -0.0069469 | 0.015112 | 0.025673 | -0.0034117 | 42.6498 | 121.8796 | -0.054932 | 121.6919 | 7.1548 | 1.2497 | 1.1993 | 0.09613 | -0.018311 | 0.004578 | 0.054932 | 0.14648 | 0.11444 | 0.14648 | 0.013733 | -0.004577 | -0.19226 | 7.2235 | 1.268 | 1.3184 | 1.2543 | 1.3046 | 0.073243 | -121.9025 | -121.8292 | 0.21515 | 0.21515 | 0.18311 | 0.14191 | 0.10986 | 7.2098 | 121.7468 | 0.14191 | 0.050354 | 121.9345 | -0.022889 | 121.9482 | 0.050354 | -121.9391 | -121.8796 | 121.7606 | 0.1236 | 42.7185 | 0.16479
3819.5625 | 121.9849 | -0.091553 | 121.8979 | -0.01976 | 0.021486 | 0.061118 | 0.058996 | 0.00079894 | -0.0010852 | 0.0035996 | -0.005371 | 0.020181 | 0.041353 | -0.013569 | 0.014898 | 0.025673 | -0.0023435 | 42.6224 | 121.907 | -0.086975 | 121.6187 | 7.0862 | 1.2314 | 1.1444 | -0.009155 | 0 | -0.032043 | -0.004578 | 0.07782 | 0.041199 | 0.082397 | 0.004578 | 0.009155 | -0.27924 | 7.1777 | 1.236 | 1.3229 | 1.2314 | 1.3184 | 0.05951 | -121.8979 | -121.9025 | 0.16937 | 0.17395 | 0.13275 | 0.11444 | 0.073242 | 7.1732 | 121.7056 | 0.10986 | 0.027465 | 121.994 | 0.032043 | 121.9986 | 0.091553 | -121.9849 | -121.9299 | 121.7102 | 0.086975 | 42.7139 | 0.082398
3821.2656 | 121.9528 | -0.10986 | 121.9299 | -0.0045011 | 0.020204 | 0.059836 | 0.056219 | 0.0035761 | -0.00065802 | 0.0040268 | -0.0084228 | 0.022317 | 0.04413 | -0.021473 | 0.012548 | 0.024178 | -0.0019163 | 42.659 | 121.8613 | -0.054932 | 121.6782 | 7.2052 | 1.2222 | 1.181 | 0.009155 | -0.013733 | -0.018311 | -0.050354 | 0.059509 | 0.050354 | 0.050354 | 0.054931 | -0.068665 | -0.25177 | 7.3151 | 1.2909 | 1.3321 | 1.236 | 1.2772 | 0.091552 | -121.9437 | -121.9803 | 0.16937 | 0.16022 | 0.16022 | 0.068665 | 0.068665 | 7.2601 | 121.7331 | 0.07782 | -0.032043 | 121.9162 | 0.004578 | 121.9711 | 0.09613 | -121.9849 | -121.9482 | 121.788 | 0.059509 | 42.7689 | 0.11902
3823.0312 | 122.0215 | -0.054932 | 121.8796 | -0.01976 | 0.022982 | 0.063254 | 0.056006 | -0.00069646 | 0.0019056 | 0.0040268 | -0.005371 | 0.020181 | 0.04114 | -0.019978 | 0.013403 | 0.02546 | -0.0012753 | 42.6132 | 121.8658 | -0.045776 | 121.701 | 7.2784 | 1.3 | 1.2405 | 0.10529 | -0.013733 | -0.013733 | 0.032043 | 0.11902 | 0.10986 | 0.10986 | 0.009156 | -0.013733 | -0.17853 | 7.3334 | 1.2955 | 1.355 | 1.2863 | 1.3458 | 0.041199 | -121.8933 | -121.8475 | 0.17395 | 0.16479 | 0.16479 | 0.1236 | 0.1236 | 7.3242 | 121.7468 | 0.13275 | 0.045776 | 121.9116 | 0 | 121.9208 | 0.041199 | -121.9254 | -121.8933 | 121.756 | 0.086975 | 42.6682 | 0.16022
3824.7969 | 122.0444 | -0.059509 | 121.8796 | -0.012131 | 0.021059 | 0.06304 | 0.055578 | 0.0044305 | 0.0012646 | 0.0046676 | -0.0023192 | 0.020608 | 0.040499 | -0.016347 | 0.014898 | 0.02546 | -0.0034117 | 42.627 | 121.8567 | -0.041199 | 121.7239 | 7.2922 | 1.3367 | 1.2726 | 0.1236 | -0.032043 | -0.018311 | 0.064087 | 0.16022 | 0.14191 | 0.14648 | 0.01831 | -0.022889 | -0.15564 | 7.3517 | 1.3321 | 1.3962 | 1.3138 | 1.3779 | 0.041198 | -121.9116 | -121.8155 | 0.21973 | 0.20599 | 0.20142 | 0.16479 | 0.16022 | 7.3334 | 121.7651 | 0.17853 | 0.082398 | 121.8979 | -0.013732 | 121.9162 | 0.027466 | -121.9208 | -121.8979 | 121.7834 | 0.1236 | 42.6865 | 0.1831
3826.5 | 122.0306 | -0.068665 | 121.843 | -0.01976 | 0.021486 | 0.061972 | 0.057501 | 0.00015814 | 0.0021192 | 0.004454 | -0.005371 | 0.019113 | 0.043276 | -0.018483 | 0.01383 | 0.022683 | -0.0031979 | 42.5949 | 121.8567 | -0.045776 | 121.7148 | 7.3288 | 1.3412 | 1.2039 | 0.091553 | -0.041199 | 0 | 0.027466 | 0.11902 | 0.09613 | 0.10529 | 0.022889 | 0.013732 | -0.12817 | 7.3975 | 1.2726 | 1.4099 | 1.2497 | 1.387 | 0.068665 | -121.8842 | -121.8155 | 0.18768 | 0.17395 | 0.16479 | 0.10529 | 0.09613 | 7.3746 | 121.7606 | 0.11902 | 0.027466 | 121.9025 | -0.041199 | 121.9254 | 0.027466 | -121.8887 | -121.843 | 121.7834 | 0.096131 | 42.6636 | 0.16022
3828.2656 | 121.9711 | -0.091553 | 121.8979 | -0.0045011 | 0.020845 | 0.061972 | 0.059851 | 0.00015814 | 0.00019658 | 0.0055222 | -0.0084228 | 0.021676 | 0.041994 | -0.01122 | 0.015112 | 0.022042 | -0.0051205 | 42.5903 | 121.8842 | -0.082397 | 121.6461 | 7.3151 | 1.2772 | 1.1444 | 0.036621 | 0.018311 | -0.032043 | -0.018311 | 0.086975 | 0.041199 | 0.082397 | 0.009156 | -0.013733 | -0.25177 | 7.4066 | 1.236 | 1.3687 | 1.2268 | 1.3596 | 0.05951 | -121.8796 | -121.9162 | 0.17853 | 0.17395 | 0.13275 | 0.11444 | 0.073242 | 7.3975 | 121.7285 | 0.11902 | 0.013732 | 121.9666 | 0.050354 | 121.9757 | 0.10986 | -121.9803 | -121.9299 | 121.7377 | 0.073242 | 42.6819 | 0.12817
3830.0469 | 121.9574 | -0.091553 | 121.9025 | -0.0045011 | 0.021273 | 0.062613 | 0.056006 | 0.0029351 | -0.0019396 | 0.0072312 | -0.011475 | 0.023385 | 0.042849 | -0.0052381 | 0.016393 | 0.02311 | -0.0029843 | 42.5674 | 121.8658 | -0.068665 | 121.6599 | 7.3517 | 1.3916 | 1.149 | 0.013733 | 0 | -0.027466 | -0.009155 | 0.07782 | 0.032043 | 0.07782 | 0.022888 | -0.036621 | -0.24262 | 7.4432 | 1.2405 | 1.4832 | 1.2177 | 1.4603 | 0.064087 | -121.9025 | -121.9116 | 0.16937 | 0.16937 | 0.1236 | 0.10529 | 0.059509 | 7.4204 | 121.7285 | 0.10529 | 0.018311 | 121.9345 | 0.027466 | 121.9574 | 0.091553 | -121.9711 | -121.9299 | 121.7514 | 0.082398 | 42.659 | 0.10529
3831.75 | 121.9162 | -0.11902 | 121.8979 | -0.012131 | 0.020632 | 0.06069 | 0.057928 | 0.0027215 | -0.00065802 | 0.0048812 | -0.0084228 | 0.022317 | 0.044558 | -0.015065 | 0.014043 | 0.02311 | 0.00021995 | 42.4576 | 121.8933 | -0.091553 | 121.5866 | 7.3013 | 1.181 | 1.1856 | -0.059509 | 0.036621 | -0.050354 | -0.073242 | 0.022888 | 0 | 0.041199 | 0.027466 | -0.004577 | -0.31128 | 7.4204 | 1.3046 | 1.3 | 1.2772 | 1.2726 | 0.068665 | -121.8613 | -121.9711 | 0.14191 | 0.16022 | 0.11902 | 0.091553 | 0.050354 | 7.3929 | 121.6782 | 0.073242 | -0.022888 | 121.9849 | 0.086975 | 122.0123 | 0.15564 | -121.9894 | -121.9482 | 121.7056 | 0.045777 | 42.5766 | 0.05951
3833.5156 | 122.0444 | -0.059509 | 121.8521 | -0.012131 | 0.022982 | 0.061758 | 0.056433 | -0.00048286 | 0.001051 | 0.0065902 | -0.005371 | 0.017404 | 0.04178 | -0.017415 | 0.014043 | 0.025246 | -0.0012753 | 42.5354 | 121.8567 | -0.036621 | 121.7194 | 7.4661 | 1.3367 | 1.2817 | 0.091553 | -0.009155 | -0.018311 | 0.07782 | 0.16022 | 0.14191 | 0.14191 | 0.022888 | 0.004577 | -0.13275 | 7.5256 | 1.3412 | 1.3962 | 1.3184 | 1.3733 | 0.041198 | -121.8613 | -121.7743 | 0.21973 | 0.20142 | 0.20142 | 0.16022 | 0.16022 | 7.5027 | 121.756 | 0.17853 | 0.096131 | 121.8933 | 0.009156 | 121.9162 | 0.050354 | -121.8887 | -121.8704 | 121.7789 | 0.13733 | 42.5949 | 0.15106
3835.2188 | 121.9345 | -0.10071 | 121.8979 | -0.012131 | 0.019564 | 0.059836 | 0.056433 | -0.0047553 | -0.0012988 | 0.0055222 | -0.005371 | 0.021676 | 0.040926 | -0.01891 | 0.012975 | 0.023751 | -0.00063445 | 42.4667 | 121.8613 | -0.073242 | 121.6187 | 7.3975 | 1.3275 | 1.2634 | -0.045776 | 0.004578 | -0.050354 | -0.068665 | 0.054932 | 0.022888 | 0.022888 | 0.027466 | -0.036621 | -0.27924 | 7.4982 | 1.3641 | 1.4282 | 1.3367 | 1.4008 | 0.050354 | -121.8933 | -121.9666 | 0.15564 | 0.1236 | 0.1236 | 0.073242 | 0.073242 | 7.4707 | 121.6919 | 0.10529 | -0.018311 | 121.9345 | 0.054932 | 121.962 | 0.10529 | -121.9711 | -121.9482 | 121.7194 | 0.032043 | 42.5674 | 0.054932
3837 | 121.9711 | -0.086975 | 121.907 | -0.0045011 | 0.022768 | 0.062186 | 0.055578 | 0.0012261 | -0.0015124 | 0.0063766 | -0.005371 | 0.023812 | 0.042421 | -0.013997 | 0.015966 | 0.024178 | -0.0031979 | 42.4713 | 121.8887 | -0.064087 | 121.637 | 7.4158 | 1.4465 | 1.2222 | 0.004578 | 0.018311 | -0.036621 | -0.022888 | 0.086975 | 0.050354 | 0.064087 | 0.022888 | -0.01831 | -0.27008 | 7.5027 | 1.3092 | 1.5335 | 1.2863 | 1.5106 | 0.050354 | -121.8887 | -121.9299 | 0.17395 | 0.15106 | 0.13733 | 0.10071 | 0.086975 | 7.4799 | 121.701 | 0.1236 | 0.013733 | 121.9528 | 0.054932 | 121.9757 | 0.10529 | -121.9711 | -121.9437 | 121.7239 | 0.064087 | 42.5583 | 0.091553
3838.7656 | 122.0535 | -0.059509 | 121.8475 | -0.012131 | 0.022982 | 0.062827 | 0.055578 | 0.0040033 | -0.00087162 | 0.007872 | -0.0023192 | 0.019326 | 0.042421 | -0.017201 | 0.015539 | 0.025032 | -0.0025571 | 42.5125 | 121.8521 | -0.032043 | 121.7194 | 7.5714 | 1.5427 | 1.2726 | 0.10071 | -0.022888 | -0.013733 | 0.068665 | 0.17853 | 0.12817 | 0.12817 | 0.027466 | 0.004578 | -0.12817 | 7.6309 | 1.3321 | 1.6022 | 1.3046 | 1.5747 | 0.045776 | -121.8704 | -121.7789 | 0.23804 | 0.18768 | 0.18768 | 0.14191 | 0.14191 | 7.6035 | 121.7514 | 0.19226 | 0.082398 | 121.8842 | -0.009155 | 121.9116 | 0.036621 | -121.8796 | -121.8613 | 121.7789 | 0.12817 | 42.572 | 0.16022
3840.5312 | 121.9345 | -0.10071 | 121.8979 | -0.01976 | 0.020418 | 0.060263 | 0.056646 | -0.0026191 | 0.00041018 | 0.0055222 | -0.0084228 | 0.020822 | 0.042635 | -0.0082287 | 0.015539 | 0.023537 | -0.0044797 | 42.4026 | 121.8384 | -0.068665 | 121.637 | 7.5806 | 1.3641 | 1.2314 | -0.032043 | 0.013733 | -0.045776 | -0.059509 | 0.045776 | 0.032043 | 0.032043 | 0.032043 | -0.059509 | -0.26093 | 7.6813 | 1.3321 | 1.4648 | 1.3 | 1.4328 | 0.054932 | -121.8842 | -121.9574 | 0.14648 | 0.13275 | 0.13275 | 0.077819 | 0.077819 | 7.6492 | 121.7056 | 0.091552 | -0.013733 | 121.907 | 0.059509 | 121.9391 | 0.11444 | -121.9666 | -121.9437 | 121.7377 | 0.041199 | 42.5034 | 0.068665
3842.3125 | 121.9025 | -0.091553 | 121.8887 | -0.01976 | 0.022341 | 0.061972 | 0.057928 | -0.0013373 | 0.00062378 | 0.004454 | -0.0084228 | 0.024667 | 0.041994 | -0.0067333 | 0.015112 | 0.022896 | -0.0010617 | 42.4164 | 121.8796 | -0.068665 | 121.6049 | 7.5485 | 1.236 | 1.2131 | -0.041199 | 0.027466 | -0.050354 | -0.054932 | 0.032043 | -0.018311 | 0.041199 | 0.022888 | -0.009155 | -0.28381 | 7.6401 | 1.3046 | 1.3275 | 1.2817 | 1.3046 | 0.041199 | -121.8613 | -121.9437 | 0.1236 | 0.13275 | 0.073242 | 0.091553 | 0.032043 | 7.6172 | 121.6736 | 0.082397 | -0.004578 | 121.9482 | 0.07782 | 121.9711 | 0.11902 | -121.9574 | -121.9391 | 121.6965 | 0.036621 | 42.5079 | 0.050354
3844.0156 | 121.9254 | -0.10986 | 121.8887 | -0.0045011 | 0.021486 | 0.059622 | 0.058355 | -0.0030463 | -1.7024e-05 | 0.0063766 | -0.0084228 | 0.020822 | 0.044771 | -0.020833 | 0.012762 | 0.025673 | -0.0014891 | 42.3157 | 121.8613 | -0.073242 | 121.5912 | 7.6401 | 1.3687 | 1.2177 | -0.032043 | 0.009155 | -0.041199 | -0.07782 | 0.041199 | 0.018311 | 0.022888 | 0.036621 | -0.027466 | -0.29755 | 7.7499 | 1.3275 | 1.4786 | 1.2909 | 1.442 | 0.068664 | -121.8796 | -121.9666 | 0.15106 | 0.13275 | 0.12817 | 0.064087 | 0.05951 | 7.7133 | 121.6644 | 0.082398 | -0.036621 | 121.9345 | 0.050354 | 121.9711 | 0.11902 | -121.962 | -121.9299 | 121.7011 | 0.032043 | 42.4255 | 0.07782
3845.7188 | 122.0398 | -0.064087 | 121.8887 | -0.01976 | 0.022341 | 0.060477 | 0.056646 | 0.00015814 | 0.001051 | 0.0063766 | -0.0084228 | 0.018045 | 0.042208 | -0.016347 | 0.014898 | 0.024819 | -0.0019163 | 42.3889 | 121.8475 | -0.059509 | 121.6644 | 7.6859 | 1.3962 | 1.3504 | 0.036621 | 0 | -0.036621 | 0.027466 | 0.12817 | 0.11902 | 0.11902 | 0.004578 | -0.041199 | -0.2243 | 7.7499 | 1.4145 | 1.4603 | 1.4099 | 1.4557 | 0.027466 | -121.8887 | -121.8613 | 0.19226 | 0.18311 | 0.18311 | 0.15564 | 0.15564 | 7.7454 | 121.7239 | 0.1648 | 0.064087 | 121.907 | 0.036621 | 121.9116 | 0.064087 | -121.9482 | -121.9254 | 121.7285 | 0.091553 | 42.453 | 0.10071
3847.4844 | 121.9666 | -0.11902 | 121.8887 | -0.012131 | 0.024691 | 0.059836 | 0.057074 | -0.00048286 | 0.001051 | 0.006163 | -0.005371 | 0.020608 | 0.043276 | -0.011433 | 0.014684 | 0.022469 | -0.0044797 | 42.3248 | 121.9025 | -0.07782 | 121.6187 | 7.6538 | 1.355 | 1.3229 | -0.018311 | 0.004578 | -0.054932 | -0.018311 | 0.10071 | 0.050354 | 0.07782 | 0.041199 | 0.013733 | -0.27008 | 7.7728 | 1.442 | 1.474 | 1.4008 | 1.4328 | 0.064087 | -121.8842 | -121.907 | 0.21973 | 0.19684 | 0.16937 | 0.13275 | 0.10529 | 7.7316 | 121.6965 | 0.15564 | 0.036621 | 121.9803 | 0.05951 | 122.0215 | 0.1236 | -121.9666 | -121.9437 | 121.7377 | 0.10071 | 42.4438 | 0.10071
3849.2656 | 121.9437 | -0.10071 | 121.8796 | -0.012131 | 0.022768 | 0.062827 | 0.057715 | -0.0021919 | 0.00062378 | 0.0065902 | -0.011475 | 0.022103 | 0.041994 | -0.01421 | 0.014684 | 0.023964 | -0.0053343 | 42.5034 | 121.9025 | -0.07782 | 121.5958 | 7.7179 | 1.3504 | 1.2634 | -0.068665 | 0.032043 | -0.036621 | -0.054932 | 0.059509 | 0.027466 | 0.045776 | 0.022888 | 0.022888 | -0.28381 | 7.8186 | 1.3641 | 1.4511 | 1.3412 | 1.4282 | 0.064087 | -121.8475 | -121.9345 | 0.16022 | 0.14648 | 0.12817 | 0.082397 | 0.064087 | 7.7957 | 121.6736 | 0.09613 | -0.018311 | 121.9803 | 0.068664 | 122.0032 | 0.13275 | -121.9574 | -121.9162 | 121.6965 | 0.045776 | 42.6041 | 0.032043
3850.9844 | 121.907 | -0.10986 | 121.907 | -0.012131 | 0.020418 | 0.060049 | 0.058142 | -5.5462e-05 | 0.00019658 | 0.0046676 | -0.005371 | 0.022317 | 0.043703 | -0.018055 | 0.014471 | 0.022255 | -0.0042661 | 42.4438 | 121.8979 | -0.09613 | 121.5866 | 7.7179 | 1.442 | 1.2863 | -0.054932 | 0.018311 | -0.050354 | -0.073242 | 0.027466 | 0.013733 | 0.045776 | 0.013733 | -0.009155 | -0.32043 | 7.8278 | 1.3962 | 1.5518 | 1.3824 | 1.5381 | 0.059509 | -121.8887 | -121.9803 | 0.13733 | 0.15564 | 0.1236 | 0.09613 | 0.064087 | 7.814 | 121.6827 | 0.07782 | -0.022888 | 121.994 | 0.068665 | 122.0078 | 0.12817 | -122.0032 | -121.9574 | 121.6965 | 0.036621 | 42.5537 | 0.054931
3852.7656 | 121.9208 | -0.11902 | 121.8933 | -0.012131 | 0.020845 | 0.060477 | 0.055792 | -0.00069646 | -0.00065802 | 0.0080856 | -0.005371 | 0.019754 | 0.042849 | -0.015065 | 0.014257 | 0.023537 | -0.0019163 | 42.4118 | 121.9025 | -0.068665 | 121.5958 | 7.6904 | 1.3916 | 1.2497 | -0.064087 | 0.018311 | -0.07782 | -0.082397 | 0.036621 | 0.004578 | 0.022888 | 0.050354 | 0.009155 | -0.29755 | 7.8094 | 1.3687 | 1.5106 | 1.3184 | 1.4603 | 0.041199 | -121.875 | -121.9757 | 0.15564 | 0.14191 | 0.1236 | 0.10071 | 0.082398 | 7.7591 | 121.6644 | 0.11444 | -0.004577 | 121.9711 | 0.096131 | 122.0215 | 0.13733 | -121.962 | -121.9711 | 121.7148 | 0.036622 | 42.5308 | 0.054932
3854.5312 | 122.0535 | -0.045776 | 121.8613 | -0.01976 | 0.023409 | 0.063681 | 0.055578 | 0.00058534 | 0.001692 | 0.004454 | -0.0023192 | 0.021035 | 0.041994 | -0.01421 | 0.014898 | 0.024178 | -0.0046933 | 42.4713 | 121.843 | -0.036621 | 121.7148 | 7.901 | 1.6022 | 1.3321 | 0.12817 | -0.032043 | -0.009155 | 0.059509 | 0.17395 | 0.13275 | 0.14191 | 0.009155 | -0.01831 | -0.14648 | 7.9468 | 1.3779 | 1.6479 | 1.3687 | 1.6388 | 0.036621 | -121.8933 | -121.8018 | 0.21973 | 0.18768 | 0.17853 | 0.15106 | 0.14191 | 7.9376 | 121.7514 | 0.1831 | 0.068664 | 121.8796 | -0.022888 | 121.8887 | 0.013733 | -121.8979 | -121.8704 | 121.7606 | 0.10528 | 42.5171 | 0.17395
3856.2344 | 121.9391 | -0.10986 | 121.8933 | -0.012131 | 0.023622 | 0.062827 | 0.060492 | 0.0037897 | 0.0025464 | 0.004454 | -0.0084228 | 0.023172 | 0.043917 | -0.013997 | 0.017034 | 0.024178 | 0.00043375 | 42.3889 | 121.9116 | -0.091553 | 121.582 | 7.6767 | 1.4603 | 1.268 | -0.050354 | 0.009155 | -0.032043 | -0.054932 | 0.009155 | -0.027466 | 0.013733 | 0.01831 | 0.01831 | -0.31128 | 7.7866 | 1.3779 | 1.5701 | 1.3596 | 1.5518 | 0.07782 | -121.8842 | -121.9482 | 0.11902 | 0.1236 | 0.082397 | 0.045776 | 0.004577 | 7.7683 | 121.6736 | 0.041198 | -0.022889 | 122.0032 | 0.041198 | 122.0215 | 0.11902 | -121.9849 | -121.9254 | 121.6919 | 0.054931 | 42.4988 | 0.059509
3858.0156 | 121.9528 | -0.10529 | 121.8933 | -0.0045011 | 0.022341 | 0.060263 | 0.057928 | -0.00048286 | -1.7024e-05 | 0.0068038 | -0.005371 | 0.023172 | 0.040071 | -0.019124 | 0.014898 | 0.022896 | -0.0038389 | 42.3477 | 121.8933 | -0.091553 | 121.5912 | 7.7728 | 1.4603 | 1.236 | -0.064087 | 0.036621 | -0.054932 | -0.050354 | 0.068665 | 0.036621 | 0.064087 | 0.013733 | 0 | -0.30212 | 7.8781 | 1.3412 | 1.5656 | 1.3275 | 1.5518 | 0.050354 | -121.8567 | -121.9437 | 0.17395 | 0.16937 | 0.14191 | 0.11902 | 0.091553 | 7.8644 | 121.6827 | 0.1236 | 0.004578 | 121.9849 | 0.091553 | 121.9986 | 0.14191 | -121.9849 | -121.9482 | 121.6965 | 0.054932 | 42.453 | 0.041199
3859.7969 | 121.9116 | -0.09613 | 121.9116 | -0.01976 | 0.021059 | 0.061758 | 0.058355 | 0.0050713 | 0.0014782 | 0.0072312 | -0.0023192 | 0.020395 | 0.041994 | -0.018269 | 0.01383 | 0.026314 | -0.0019163 | 42.2562 | 121.8979 | -0.10529 | 121.5729 | 7.8369 | 1.4236 | 1.2405 | -0.073242 | 0.027466 | -0.064087 | -0.064087 | 0.027466 | 0.018311 | 0.045776 | -0.009156 | -0.013733 | -0.33875 | 7.933 | 1.3367 | 1.5198 | 1.3458 | 1.5289 | 0.032043 | -121.8842 | -121.9757 | 0.1236 | 0.14191 | 0.11444 | 0.10986 | 0.082398 | 7.9422 | 121.6782 | 0.091553 | 0 | 122.0032 | 0.091553 | 121.994 | 0.1236 | -122.0169 | -121.9757 | 121.669 | 0.032043 | 42.3523 | 0.022888
3861.5 | 122.0078 | -0.073242 | 121.8384 | -0.0045011 | 0.021059 | 0.062186 | 0.055365 | -0.0013373 | 0.00083738 | 0.0046676 | -0.0023192 | 0.019754 | 0.042421 | -0.017201 | 0.011907 | 0.02546 | -0.0027707 | 42.2745 | 121.8613 | -0.036621 | 121.6415 | 7.9514 | 1.5564 | 1.3046 | 0.041199 | -0.032043 | -0.027466 | 0.022888 | 0.14648 | 0.1236 | 0.10529 | 0.036621 | 0.022888 | -0.19684 | 8.0246 | 1.3779 | 1.6296 | 1.3412 | 1.593 | 0.045776 | -121.8704 | -121.8155 | 0.21973 | 0.17853 | 0.19684 | 0.13275 | 0.15106 | 7.988 | 121.6782 | 0.17395 | 0.050354 | 121.8979 | -0.004577 | 121.9345 | 0.041199 | -121.875 | -121.8658 | 121.7148 | 0.09613 | 42.3477 | 0.11444
3863.2656 | 121.9849 | -0.082397 | 121.8842 | -0.01976 | 0.023195 | 0.060904 | 0.057287 | -0.0019781 | 0.00083738 | 0.0070176 | -0.0084228 | 0.020608 | 0.040499 | -0.01656 | 0.014684 | 0.023751 | -0.0057615 | 42.2745 | 121.8292 | -0.041199 | 121.6919 | 8.0521 | 1.5381 | 1.4465 | 0.068665 | -0.013733 | -0.027466 | 0.013733 | 0.13275 | 0.10071 | 0.09613 | 0.041198 | -0.054931 | -0.19226 | 8.1345 | 1.5289 | 1.6205 | 1.4877 | 1.5793 | 0.054931 | -121.8979 | -121.8704 | 0.21515 | 0.17853 | 0.18311 | 0.1236 | 0.12817 | 8.0933 | 121.7331 | 0.16022 | 0.041199 | 121.8704 | 0.013733 | 121.9116 | 0.068664 | -121.9254 | -121.9116 | 121.7743 | 0.09613 | 42.3569 | 0.15106
3865.0469 | 121.9025 | -0.09613 | 121.8979 | 0.0031279 | 0.025972 | 0.062827 | 0.057715 | -0.00091006 | 0.0012646 | 0.0059494 | -0.0084228 | 0.023812 | 0.040926 | -0.015492 | 0.014257 | 0.023537 | -0.0010617 | 42.1875 | 121.8796 | -0.068665 | 121.6003 | 7.9422 | 1.4923 | 1.3092 | -0.054932 | 0.032043 | -0.041199 | -0.068665 | 0.009155 | -0.022888 | 0.027466 | 0.027465 | -0.01831 | -0.29755 | 8.0383 | 1.4053 | 1.5884 | 1.3779 | 1.561 | 0.054931 | -121.8658 | -121.9666 | 0.10528 | 0.1236 | 0.073242 | 0.068665 | 0.018311 | 8.0109 | 121.669 | 0.050354 | -0.027466 | 121.9482 | 0.073242 | 121.9757 | 0.12817 | -121.9666 | -121.9391 | 121.6965 | 0.027465 | 42.2836 | 0.041198
3866.8125 | 122.0444 | -0.050354 | 121.843 | -0.0045011 | 0.022768 | 0.060477 | 0.057074 | 0.00037174 | 0.00062378 | 0.0038132 | -0.005371 | 0.021035 | 0.04178 | -0.012929 | 0.013403 | 0.025887 | -0.00084805 | 42.1783 | 121.843 | -0.054932 | 121.6736 | 8.0841 | 1.6022 | 1.4008 | 0.068665 | -0.022888 | -0.013733 | 0.041199 | 0.16937 | 0.15106 | 0.13733 | -0.004578 | 0 | -0.16937 | 8.1345 | 1.4511 | 1.6525 | 1.4557 | 1.6571 | 0.036621 | -121.8658 | -121.8018 | 0.21973 | 0.18768 | 0.20142 | 0.15106 | 0.16479 | 8.139 | 121.7285 | 0.18311 | 0.054932 | 121.8979 | -0.009155 | 121.8933 | 0.027466 | -121.8979 | -121.8567 | 121.7239 | 0.091553 | 42.2287 | 0.11902
3868.5938 | 121.9803 | -0.09613 | 121.843 | -0.02739 | 0.023195 | 0.061972 | 0.05686 | 0.00079894 | -0.00065802 | 0.0053086 | -0.005371 | 0.021463 | 0.041994 | -0.018055 | 0.014898 | 0.02546 | -0.00020725 | 42.1326 | 121.843 | -0.054932 | 121.6507 | 8.1024 | 1.5518 | 1.3641 | 0.036621 | -0.009155 | -0.041199 | 0 | 0.10071 | 0.082397 | 0.086975 | 0.041198 | 0 | -0.19226 | 8.1985 | 1.4603 | 1.6479 | 1.4191 | 1.6068 | 0.054931 | -121.8521 | -121.843 | 0.19684 | 0.1831 | 0.17853 | 0.12817 | 0.1236 | 8.1573 | 121.7056 | 0.14191 | 0.041199 | 121.8979 | 0.032044 | 121.9391 | 0.086975 | -121.8979 | -121.8842 | 121.7468 | 0.09613 | 42.2287 | 0.13275
3870.3594 | 122.0261 | -0.045776 | 121.8246 | -0.0045011 | 0.025331 | 0.064322 | 0.058355 | -5.5462e-05 | 0.0023328 | 0.0048812 | -0.0023192 | 0.018899 | 0.042635 | -0.01122 | 0.016607 | 0.023323 | -0.0049069 | 42.1234 | 121.8613 | -0.041199 | 121.6965 | 8.1985 | 1.6754 | 1.4282 | 0.10529 | -0.027466 | -0.009155 | 0.07782 | 0.16479 | 0.13733 | 0.16022 | 0.004577 | 0.036621 | -0.12817 | 8.2443 | 1.474 | 1.7212 | 1.4694 | 1.7166 | 0.036621 | -121.8521 | -121.7468 | 0.21057 | 0.20599 | 0.18311 | 0.16937 | 0.14648 | 8.2397 | 121.7377 | 0.17395 | 0.086975 | 121.9025 | -0.018311 | 121.907 | 0.01831 | -121.8658 | -121.8338 | 121.7422 | 0.1236 | 42.1692 | 0.15106
3872.125 | 121.8887 | -0.11444 | 121.907 | -0.012131 | 0.025331 | 0.062827 | 0.059424 | 0.0074213 | 0.0023328 | 0.0091538 | -0.005371 | 0.021676 | 0.043489 | -0.013142 | 0.015325 | 0.024178 | -0.0059751 | 42.0547 | 121.8796 | -0.091553 | 121.5775 | 8.107 | 1.355 | 1.2039 | -0.068665 | 0.018311 | -0.045776 | -0.073242 | 0 | -0.032043 | 0.027466 | 0.022888 | -0.027465 | -0.32959 | 8.2214 | 1.3184 | 1.4694 | 1.2955 | 1.4465 | 0.068665 | -121.8887 | -121.9803 | 0.11444 | 0.14191 | 0.082398 | 0.073242 | 0.013733 | 8.1985 | 121.669 | 0.045776 | -0.027466 | 121.9711 | 0.064087 | 121.994 | 0.13275 | -121.9986 | -121.9528 | 121.6919 | 0.041199 | 42.1692 | 0.045776
3873.9062 | 121.9208 | -0.10071 | 121.8796 | 0.0031279 | 0.02704 | 0.063254 | 0.062201 | 0.0012261 | -0.00065802 | 0.007872 | -0.0023192 | 0.022744 | 0.043703 | -0.015065 | 0.013403 | 0.024605 | -0.0055479 | 42.009 | 121.8567 | -0.07782 | 121.6324 | 8.2123 | 1.5564 | 1.3687 | -0.018311 | 0.018311 | -0.022888 | -0.050354 | 0.036621 | 0.013733 | 0.050354 | 0.022888 | -0.022889 | -0.24719 | 8.313 | 1.4694 | 1.6571 | 1.4465 | 1.6342 | 0.07782 | -121.8613 | -121.9299 | 0.13733 | 0.15106 | 0.11444 | 0.073242 | 0.036621 | 8.2901 | 121.7102 | 0.059509 | -0.027466 | 121.9345 | 0.041199 | 121.9574 | 0.11902 | -121.9574 | -121.9025 | 121.7331 | 0.050354 | 42.1097 | 0.082397
3875.6094 | 121.9299 | -0.09613 | 121.875 | -0.012131 | 0.024691 | 0.062827 | 0.05921 | 0.0025079 | 0.0023328 | 0.0080856 | -0.005371 | 0.02189 | 0.043703 | -0.010792 | 0.016393 | 0.023323 | -0.00020725 | 41.9403 | 121.875 | -0.07782 | 121.5683 | 8.1482 | 1.4145 | 1.3824 | -0.045776 | 0.013733 | -0.050354 | -0.050354 | 0.045776 | 0.004578 | 0.050354 | 0.01831 | 0 | -0.3067 | 8.2443 | 1.4786 | 1.5106 | 1.4603 | 1.4923 | 0.045776 | -121.8613 | -121.9254 | 0.14191 | 0.14648 | 0.10071 | 0.10071 | 0.054932 | 8.226 | 121.6461 | 0.09613 | 0 | 121.9528 | 0.064087 | 121.9711 | 0.10986 | -121.9528 | -121.9254 | 121.6644 | 0.045776 | 42.0364 | 0.050354
3877.3594 | 121.8842 | -0.10986 | 121.9025 | -0.0045011 | 0.025331 | 0.064322 | 0.060064 | -0.0021919 | 0.0014782 | 0.0068038 | -0.0023192 | 0.022103 | 0.041353 | -0.013783 | 0.016393 | 0.024819 | -0.00063445 | 41.8762 | 121.8704 | -0.07782 | 121.5637 | 8.139 | 1.3779 | 1.3824 | -0.091553 | 0.018311 | -0.050354 | -0.059509 | 0.018311 | -0.045776 | 0.018311 | 0.032043 | -0.032044 | -0.33875 | 8.2489 | 1.4923 | 1.4877 | 1.4603 | 1.4557 | 0.059509 | -121.8842 | -121.962 | 0.12817 | 0.12817 | 0.064087 | 0.068665 | 0.004578 | 8.2169 | 121.6415 | 0.068665 | -0.009155 | 121.9482 | 0.068665 | 121.9803 | 0.12817 | -121.9803 | -121.9528 | 121.6736 | 0.050354 | 41.9861 | 0.01831
3879.1406 | 121.8979 | -0.10986 | 121.8842 | -0.012131 | 0.02704 | 0.063254 | 0.060919 | 0.00058534 | 0.0042554 | 0.010008 | -0.005371 | 0.02189 | 0.042635 | -0.0039563 | 0.015966 | 0.024605 | -0.0029843 | 41.835 | 121.8796 | -0.073242 | 121.5637 | 8.139 | 1.5198 | 1.3824 | -0.07782 | 0.018311 | -0.045776 | -0.07782 | 0.013733 | -0.032043 | 0.036621 | 0.036621 | -0.004577 | -0.32043 | 8.2489 | 1.4923 | 1.6296 | 1.4557 | 1.593 | 0.064087 | -121.8658 | -121.962 | 0.1236 | 0.14648 | 0.07782 | 0.082397 | 0.013733 | 8.2123 | 121.637 | 0.059509 | -0.032044 | 121.9528 | 0.064087 | 121.9894 | 0.12817 | -121.9574 | -121.9299 | 121.6736 | 0.032043 | 41.9449 | 0.032043
3880.8438 | 121.962 | -0.09613 | 121.8842 | -0.012131 | 0.025545 | 0.062399 | 0.060064 | 0.0040033 | 0.001051 | 0.006163 | -0.005371 | 0.022531 | 0.042421 | -0.018269 | 0.015539 | 0.024178 | -0.0038389 | 41.8762 | 121.8521 | -0.064087 | 121.6324 | 8.3725 | 1.6067 | 1.474 | 0.027466 | -0.004578 | -0.050354 | -0.009155 | 0.086975 | 0.068665 | 0.068665 | 0.032043 | -0.032043 | -0.25177 | 8.4686 | 1.5701 | 1.7029 | 1.5381 | 1.6708 | 0.045776 | -121.8887 | -121.8933 | 0.1831 | 0.16479 | 0.16479 | 0.11902 | 0.11902 | 8.4366 | 121.6965 | 0.13733 | 0.041199 | 121.9162 | 0.045776 | 121.9482 | 0.091552 | -121.9482 | -121.9345 | 121.7285 | 0.086975 | 41.9724 | 0.1236
3882.625 | 121.9391 | -0.091553 | 121.9162 | -0.012131 | 0.026186 | 0.064536 | 0.060705 | 0.0040033 | 0.0040418 | 0.0065902 | -0.0023192 | 0.021463 | 0.044558 | -0.013783 | 0.01383 | 0.023964 | -0.0027707 | 41.7801 | 121.8567 | -0.068665 | 121.6278 | 8.4732 | 1.5793 | 1.5289 | 0.036621 | -0.004578 | -0.022888 | -0.004578 | 0.09613 | 0.059509 | 0.082397 | 0.022888 | -0.05951 | -0.28839 | 8.5648 | 1.6205 | 1.6708 | 1.5976 | 1.648 | 0.068665 | -121.9208 | -121.9208 | 0.18768 | 0.17395 | 0.15106 | 0.10528 | 0.082397 | 8.5419 | 121.6965 | 0.11902 | 0.01831 | 121.9254 | 0.01831 | 121.9482 | 0.086975 | -121.9849 | -121.9391 | 121.7194 | 0.086975 | 41.8716 | 0.12817
3884.3906 | 121.9849 | -0.07782 | 121.8292 | -0.012131 | 0.025972 | 0.061972 | 0.056006 | 0.00037174 | 0.0019056 | 0.006163 | -0.0084228 | 0.019754 | 0.044344 | -0.022542 | 0.011694 | 0.02546 | -0.0014891 | 41.7114 | 121.8567 | -0.059509 | 121.6278 | 8.3817 | 1.7441 | 1.474 | 0.032043 | -0.009155 | -0.022888 | 0.004578 | 0.11444 | 0.10529 | 0.10529 | 0.018311 | 0.027465 | -0.20142 | 8.4595 | 1.5518 | 1.8219 | 1.5335 | 1.8036 | 0.054932 | -121.8384 | -121.8246 | 0.19226 | 0.18311 | 0.18311 | 0.12817 | 0.12817 | 8.4412 | 121.6873 | 0.13733 | 0.027466 | 121.9162 | 0.013733 | 121.9345 | 0.068665 | -121.8887 | -121.8521 | 121.7056 | 0.082398 | 41.7892 | 0.10986
3886.1562 | 121.9482 | -0.082397 | 121.8475 | -0.01976 | 0.026186 | 0.061118 | 0.057501 | 0.0046441 | -1.7024e-05 | 0.0074448 | -0.005371 | 0.022317 | 0.043703 | -0.012715 | 0.014684 | 0.02546 | -0.0036253 | 41.6885 | 121.8658 | -0.09613 | 121.6003 | 8.4 | 1.593 | 1.4648 | -0.009155 | 0 | -0.032043 | -0.032043 | 0.091553 | 0.050354 | 0.082397 | -0.013733 | 0.018311 | -0.24719 | 8.4824 | 1.5472 | 1.6754 | 1.561 | 1.6891 | 0.050354 | -121.8475 | -121.8796 | 0.17395 | 0.16479 | 0.13275 | 0.11444 | 0.082397 | 8.4961 | 121.6965 | 0.1236 | 0 | 121.962 | 0.032043 | 121.9482 | 0.082397 | -121.9437 | -121.8796 | 121.6827 | 0.050354 | 41.7709 | 0.073242
3887.9375 | 121.9437 | -0.09613 | 121.8796 | -0.02739 | 0.026827 | 0.063895 | 0.058569 | 0.0014397 | 0.0019056 | 0.0070176 | -0.005371 | 0.021249 | 0.043489 | -0.013997 | 0.016607 | 0.023323 | -0.0010617 | 41.6748 | 121.8842 | -0.07782 | 121.6049 | 8.5007 | 1.5244 | 1.4465 | -0.013733 | -0.004578 | -0.036621 | -0.022888 | 0.091553 | 0.059509 | 0.068665 | 0.01831 | 0.004577 | -0.27466 | 8.5968 | 1.5427 | 1.6205 | 1.5244 | 1.6022 | 0.059509 | -121.8842 | -121.9025 | 0.18768 | 0.16479 | 0.15564 | 0.10529 | 0.09613 | 8.5785 | 121.6827 | 0.12817 | 0.013733 | 121.962 | 0.032043 | 121.9803 | 0.091552 | -121.9574 | -121.9162 | 121.701 | 0.073242 | 41.7709 | 0.082397
3889.6562 | 121.8796 | -0.086975 | 121.9025 | -0.012131 | 0.027895 | 0.06539 | 0.060492 | -0.0013373 | 0.0042554 | 0.0063766 | 0.00073235 | 0.020395 | 0.043276 | -0.0086559 | 0.016393 | 0.024391 | -0.0087521 | 41.5695 | 121.9116 | -0.07782 | 121.5637 | 8.5052 | 1.5976 | 1.4648 | -0.064087 | 0.027466 | -0.045776 | -0.064087 | 0.022888 | -0.018311 | 0.022888 | 0.009155 | 0.009155 | -0.33875 | 8.5922 | 1.5518 | 1.6846 | 1.5427 | 1.6754 | 0.041199 | -121.875 | -121.9666 | 0.10986 | 0.10986 | 0.068664 | 0.068664 | 0.027465 | 8.5831 | 121.6415 | 0.068664 | -0.018311 | 121.9894 | 0.073242 | 121.9986 | 0.11444 | -121.9803 | -121.9482 | 121.6507 | 0.022888 | 41.6565 | 0.022888
3891.4219 | 122.0078 | -0.059509 | 121.8246 | -0.01976 | 0.027254 | 0.063895 | 0.057928 | 0.0022943 | 0.0038282 | 0.0085128 | -0.0023192 | 0.022958 | 0.044558 | -0.019124 | 0.013616 | 0.025246 | 0.00021995 | 41.6061 | 121.8292 | -0.050354 | 121.6873 | 8.7936 | 1.7761 | 1.6479 | 0.10986 | -0.018311 | -0.004578 | 0.050354 | 0.15106 | 0.1236 | 0.12817 | 0.009155 | 0.004578 | -0.13733 | 8.8531 | 1.7075 | 1.8356 | 1.6983 | 1.8265 | 0.054931 | -121.843 | -121.7743 | 0.21057 | 0.18768 | 0.1831 | 0.13275 | 0.12817 | 8.844 | 121.7377 | 0.15564 | 0.054932 | 121.8796 | -0.013733 | 121.8887 | 0.041198 | -121.875 | -121.8292 | 121.7468 | 0.10986 | 41.6656 | 0.16937
3893.125 | 121.9986 | -0.054932 | 121.8796 | -0.012131 | 0.02405 | 0.061545 | 0.05686 | 0.00037174 | 0.0031872 | 0.0082992 | -0.0084228 | 0.020395 | 0.042208 | -0.019337 | 0.010626 | 0.027382 | -0.0021299 | 41.5466 | 121.8475 | -0.059509 | 121.6782 | 8.6609 | 1.9135 | 1.6754 | 0.082397 | -0.022888 | -0.013733 | 0.041199 | 0.17395 | 0.13275 | 0.11444 | -0.004577 | -0.032044 | -0.20142 | 8.7158 | 1.7303 | 1.9684 | 1.7349 | 1.973 | 0.041199 | -121.9025 | -121.8384 | 0.22888 | 0.16937 | 0.18768 | 0.12817 | 0.14648 | 8.7204 | 121.7377 | 0.18768 | 0.054932 | 121.907 | -0.009155 | 121.9025 | 0.032044 | -121.9391 | -121.8933 | 121.7331 | 0.096131 | 41.6016 | 0.13733
3894.8906 | 121.9025 | -0.10986 | 121.8658 | -0.012131 | 0.029604 | 0.062186 | 0.059424 | 0.0027215 | 0.0036146 | 0.0080856 | -0.005371 | 0.021463 | 0.043917 | -0.01122 | 0.014684 | 0.025246 | -0.0027707 | 41.4139 | 121.8796 | -0.086975 | 121.5454 | 8.638 | 1.5793 | 1.5335 | -0.041199 | 0 | -0.045776 | -0.068665 | 0.009155 | -0.018311 | 0.050354 | 0.022888 | 0.013733 | -0.32043 | 8.7479 | 1.6434 | 1.6891 | 1.6205 | 1.6663 | 0.064087 | -121.8658 | -121.9345 | 0.11902 | 0.16022 | 0.091552 | 0.09613 | 0.027465 | 8.725 | 121.6324 | 0.054931 | -0.022889 | 121.9666 | 0.045776 | 121.9894 | 0.10986 | -121.9528 | -121.9116 | 121.6553 | 0.041198 | 41.5237 | 0.068664
3896.6562 | 121.8887 | -0.1236 | 121.8979 | -0.0045011 | 0.022554 | 0.061331 | 0.059637 | -0.0028327 | 0.00041018 | 0.010008 | -0.0084228 | 0.020395 | 0.040285 | -0.01656 | 0.014471 | 0.024605 | -0.0046933 | 41.391 | 121.8292 | -0.10071 | 121.5591 | 8.757 | 1.8539 | 1.5427 | -0.064087 | 0.027466 | -0.045776 | -0.07782 | 0.036621 | 0.022888 | 0.027466 | 0.022888 | -0.068664 | -0.33874 | 8.8806 | 1.6663 | 1.9775 | 1.6434 | 1.9547 | 0.07782 | -121.8704 | -121.9757 | 0.16022 | 0.15106 | 0.14648 | 0.073242 | 0.068664 | 8.8577 | 121.6599 | 0.082397 | -0.032044 | 121.9299 | 0.073242 | 121.9528 | 0.15106 | -121.9986 | -121.9437 | 121.6827 | 0.045776 | 41.5146 | 0.059509
3898.4531 | 121.9528 | -0.10986 | 121.8842 | -0.012131 | 0.026186 | 0.062399 | 0.060064 | 0.0031487 | 0.0055372 | 0.0074448 | -0.0084228 | 0.021035 | 0.043062 | -0.0095105 | 0.01383 | 0.022469 | -0.0038389 | 41.3177 | 121.8842 | -0.091553 | 121.582 | 8.7936 | 1.7944 | 1.6067 | -0.054932 | 0.009155 | -0.045776 | -0.041199 | 0.07782 | 0.050354 | 0.073242 | 0.01831 | 0 | -0.30212 | 8.9035 | 1.7166 | 1.9043 | 1.6983 | 1.886 | 0.064087 | -121.875 | -121.9254 | 0.18768 | 0.18311 | 0.16022 | 0.11902 | 0.09613 | 8.8852 | 121.6736 | 0.1236 | 0.004577 | 121.9757 | 0.054931 | 121.994 | 0.11902 | -121.9757 | -121.9299 | 121.6919 | 0.068664 | 41.4276 | 0.054931
3900.1562 | 121.9986 | -0.068665 | 121.8384 | -0.0045011 | 0.024477 | 0.062827 | 0.057287 | 0.0059259 | 0.0038282 | 0.0072312 | -0.0023192 | 0.017617 | 0.043062 | -0.022114 | 0.015112 | 0.024178 | -0.0044797 | 41.3406 | 121.8018 | -0.054932 | 121.6827 | 9.0179 | 1.973 | 1.6617 | 0.10071 | -0.009155 | -0.009155 | 0.041199 | 0.17395 | 0.15106 | 0.12817 | 0.013733 | -0.036621 | -0.15564 | 9.0866 | 1.7303 | 2.0416 | 1.7166 | 2.0279 | 0.05951 | -121.8475 | -121.7972 | 0.24261 | 0.19684 | 0.21973 | 0.13733 | 0.16022 | 9.0729 | 121.7377 | 0.1831 | 0.050354 | 121.8567 | 0 | 121.8704 | 0.05951 | -121.8933 | -121.8475 | 121.7514 | 0.10986 | 41.4093 | 0.16937
3901.9219 | 121.8933 | -0.10529 | 121.8704 | -0.012131 | 0.027254 | 0.061545 | 0.056646 | -0.00026906 | 0.0023328 | 0.009581 | -0.005371 | 0.019113 | 0.042421 | -0.011647 | 0.015752 | 0.024178 | -0.0021299 | 41.1942 | 121.8613 | -0.07782 | 121.5637 | 8.9584 | 1.7578 | 1.5701 | -0.054932 | 0.022888 | -0.064087 | -0.09613 | 0.041199 | 0.009155 | 0.022888 | 0.027466 | -0.009155 | -0.3067 | 9.0637 | 1.6754 | 1.8631 | 1.6479 | 1.8356 | 0.041199 | -121.8475 | -121.9666 | 0.14649 | 0.12817 | 0.11444 | 0.086975 | 0.073242 | 9.0363 | 121.6415 | 0.10529 | -0.032043 | 121.9391 | 0.086975 | 121.9666 | 0.12817 | -121.9482 | -121.9345 | 121.669 | 0.009156 | 41.2994 | 0.050354
3903.6406 | 121.8887 | -0.10986 | 121.8521 | -0.01976 | 0.030031 | 0.063895 | 0.060705 | -0.00048286 | 0.003401 | 0.0059494 | -0.005371 | 0.023385 | 0.043489 | -0.010151 | 0.017034 | 0.024178 | 0.00021995 | 41.1804 | 121.8933 | -0.082397 | 121.5363 | 9.0363 | 1.8494 | 1.6434 | -0.07782 | 0.027466 | -0.041199 | -0.054932 | -0.004578 | -0.027466 | 0.036621 | 0.027466 | 0.041199 | -0.31586 | 9.1461 | 1.7532 | 1.9592 | 1.7258 | 1.9318 | 0.068664 | -121.8246 | -121.907 | 0.10529 | 0.14648 | 0.082397 | 0.07782 | 0.013733 | 9.1187 | 121.6187 | 0.036621 | -0.013733 | 121.9757 | 0.068665 | 122.0032 | 0.13733 | -121.9345 | -121.8933 | 121.6461 | 0.054931 | 41.2903 | 0.032043
3905.4062 | 121.8979 | -0.10986 | 121.875 | -0.012131 | 0.031527 | 0.064749 | 0.059424 | 0.0022943 | 0.0036146 | 0.0093674 | -0.005371 | 0.020608 | 0.043489 | -0.012288 | 0.01618 | 0.024178 | -0.0055479 | 41.1163 | 121.8613 | -0.086975 | 121.5454 | 9.0637 | 1.7166 | 1.5381 | -0.068665 | 0.018311 | -0.050354 | -0.059509 | 0 | -0.027466 | 0.032043 | 0.022888 | -0.013733 | -0.32959 | 9.1736 | 1.6479 | 1.8265 | 1.6251 | 1.8036 | 0.059509 | -121.8567 | -121.9345 | 0.10986 | 0.14191 | 0.082397 | 0.082397 | 0.022888 | 9.1507 | 121.6324 | 0.050354 | -0.009155 | 121.9482 | 0.068665 | 121.9711 | 0.12817 | -121.962 | -121.9254 | 121.6553 | 0.050354 | 41.2262 | 0.041198
3907.1875 | 121.8933 | -0.10071 | 121.8796 | -0.0045011 | 0.024477 | 0.061972 | 0.057715 | -0.0011237 | 0.001692 | 0.0068038 | -0.0023192 | 0.018472 | 0.044985 | -0.012929 | 0.014898 | 0.022896 | -0.0025571 | 41.0614 | 121.843 | -0.064087 | 121.5591 | 9.1049 | 1.8036 | 1.8814 | -0.041199 | 0.013733 | -0.041199 | -0.073242 | 0.050354 | 0.032043 | 0.027466 | 0.036621 | -0.036621 | -0.32043 | 9.2056 | 1.9821 | 1.9043 | 1.9455 | 1.8677 | 0.059509 | -121.8658 | -121.9528 | 0.15106 | 0.12817 | 0.13275 | 0.068665 | 0.073242 | 9.169 | 121.6232 | 0.091553 | -0.032043 | 121.907 | 0.054932 | 121.9437 | 0.11444 | -121.9437 | -121.9208 | 121.6599 | 0.027466 | 41.1621 | 0.059509
3908.9062 | 122.0078 | -0.045776 | 121.8292 | -0.012131 | 0.028963 | 0.065604 | 0.058783 | 0.0022943 | 0.0048962 | 0.010008 | -0.005371 | 0.019326 | 0.042635 | -0.018696 | 0.013616 | 0.025032 | -0.0019163 | 41.0614 | 121.843 | -0.041199 | 121.6736 | 9.2926 | 1.9501 | 1.7532 | 0.10529 | -0.022888 | -0.013733 | 0.054932 | 0.16022 | 0.11902 | 0.11902 | 0.004577 | 0.013733 | -0.15564 | 9.3384 | 1.799 | 1.9958 | 1.7944 | 1.9913 | 0.032043 | -121.8521 | -121.7743 | 0.20599 | 0.16479 | 0.16479 | 0.13275 | 0.13275 | 9.3338 | 121.7148 | 0.17395 | 0.068665 | 121.8842 | -0.009155 | 121.8887 | 0.022888 | -121.8704 | -121.843 | 121.7194 | 0.10071 | 41.1072 | 0.15106
3910.6875 | 122.0215 | -0.045776 | 121.8201 | -0.0045011 | 0.025759 | 0.061331 | 0.058142 | -0.0011237 | 0.0055372 | 0.010008 | -0.005371 | 0.01954 | 0.043917 | -0.021473 | 0.012762 | 0.024391 | -0.0029843 | 40.9698 | 121.8018 | -0.050354 | 121.6919 | 9.375 | 2.092 | 1.8127 | 0.10529 | -0.027466 | -0.009155 | 0.036621 | 0.20142 | 0.15106 | 0.13275 | -0.004578 | -0.01831 | -0.12817 | 9.4208 | 1.8585 | 2.1378 | 1.8631 | 2.1423 | 0.036621 | -121.8475 | -121.7834 | 0.24719 | 0.17853 | 0.19684 | 0.14191 | 0.16022 | 9.4254 | 121.7422 | 0.21057 | 0.045776 | 121.8521 | -0.018311 | 121.8475 | 0.01831 | -121.8704 | -121.8292 | 121.7377 | 0.082397 | 41.0156 | 0.15106
3912.3906 | 121.9986 | -0.068665 | 121.7972 | -0.01976 | 0.028536 | 0.064108 | 0.058569 | -0.00026906 | 0.0055372 | 0.0074448 | -0.0023192 | 0.021249 | 0.041994 | -0.016133 | 0.014471 | 0.026314 | -0.0046933 | 40.9698 | 121.8109 | -0.064087 | 121.6827 | 9.3933 | 2.1378 | 1.8173 | 0.11444 | -0.032043 | -0.004578 | 0.045776 | 0.1831 | 0.15106 | 0.1236 | 0.004578 | 0.013733 | -0.11444 | 9.462 | 1.886 | 2.2064 | 1.8814 | 2.2018 | 0.064087 | -121.8292 | -121.7514 | 0.25177 | 0.19226 | 0.21973 | 0.12817 | 0.15564 | 9.4574 | 121.7468 | 0.18768 | 0.050354 | 121.875 | -0.027465 | 121.8796 | 0.036622 | -121.8613 | -121.8018 | 121.7514 | 0.11444 | 41.0385 | 0.18311
3914.1562 | 121.9849 | -0.041199 | 121.7834 | -0.012131 | 0.030886 | 0.064749 | 0.060492 | -0.00048286 | 0.0068188 | 0.0076584 | -0.005371 | 0.020608 | 0.042208 | -0.0088695 | 0.015325 | 0.023751 | -0.0046933 | 40.947 | 121.8155 | -0.036621 | 121.6827 | 9.3201 | 2.0142 | 1.8539 | 0.11444 | -0.032043 | -0.018311 | 0.054932 | 0.16479 | 0.1236 | 0.14191 | 0.004578 | 0.032044 | -0.10071 | 9.3613 | 1.8951 | 2.0554 | 1.8906 | 2.0508 | 0.022888 | -121.8155 | -121.7285 | 0.20599 | 0.18311 | 0.16479 | 0.16022 | 0.14191 | 9.3567 | 121.7194 | 0.18311 | 0.073243 | 121.8521 | -0.013732 | 121.8567 | 0.009156 | -121.8201 | -121.8018 | 121.7239 | 0.096131 | 40.9882 | 0.15564
3915.9219 | 121.8842 | -0.091553 | 121.8475 | -0.012131 | 0.031099 | 0.06304 | 0.063482 | 0.0014397 | 0.0042554 | 0.010222 | -0.011475 | 0.020822 | 0.043062 | -0.012929 | 0.015752 | 0.022683 | -0.0012753 | 40.6998 | 121.8613 | -0.073242 | 121.55 | 9.3201 | 1.7578 | 1.68 | -0.036621 | 0.013733 | -0.050354 | -0.032043 | 0.041199 | 0.013733 | 0.064087 | 0.018311 | 0.013733 | -0.29755 | 9.4116 | 1.7715 | 1.8494 | 1.7532 | 1.8311 | 0.041199 | -121.8338 | -121.8796 | 0.13275 | 0.15564 | 0.10529 | 0.11444 | 0.064087 | 9.3933 | 121.6232 | 0.091553 | 0.018311 | 121.9345 | 0.064087 | 121.9528 | 0.10529 | -121.9208 | -121.8979 | 121.6415 | 0.05951 | 40.7913 | 0.054932
3917.6406 | 122.0261 | -0.082397 | 121.8201 | -0.0045011 | 0.024904 | 0.063467 | 0.058569 | -0.0019781 | 0.0019056 | 0.0093674 | -0.0084228 | 0.018686 | 0.04178 | -0.021901 | 0.012762 | 0.023751 | -0.0046933 | 40.7776 | 121.7926 | -0.045776 | 121.6736 | 9.5444 | 1.9318 | 1.8951 | 0.13275 | -0.022888 | -0.013733 | 0.059509 | 0.19684 | 0.17395 | 0.14191 | 0.036621 | -0.027465 | -0.14648 | 9.6268 | 1.9775 | 2.0142 | 1.9409 | 1.9775 | 0.068664 | -121.843 | -121.7606 | 0.27924 | 0.2243 | 0.25635 | 0.15564 | 0.18768 | 9.5901 | 121.7194 | 0.21057 | 0.073242 | 121.8384 | -0.009155 | 121.875 | 0.059509 | -121.8658 | -121.8338 | 121.756 | 0.14191 | 40.86 | 0.21515
3919.4062 | 121.8567 | -0.09613 | 121.843 | -0.0045011 | 0.031954 | 0.063467 | 0.06391 | 0.00015814 | 0.0021192 | 0.0097946 | 0.00073235 | 0.021463 | 0.044558 | -0.011433 | 0.017248 | 0.021401 | -0.0076841 | 40.6128 | 121.843 | -0.073242 | 121.5363 | 9.3933 | 1.8127 | 1.7349 | -0.073242 | 0.022888 | -0.041199 | -0.07782 | 0 | -0.013733 | 0.027466 | 0.022888 | 0 | -0.3067 | 9.4894 | 1.8311 | 1.9089 | 1.8082 | 1.886 | 0.054931 | -121.8201 | -121.9208 | 0.09613 | 0.1236 | 0.082397 | 0.068665 | 0.027466 | 9.4666 | 121.6095 | 0.041199 | -0.036621 | 121.9162 | 0.064087 | 121.9391 | 0.11902 | -121.9162 | -121.8842 | 121.6324 | 0.01831 | 40.7089 | 0.022888
3921.1562 | 121.9574 | -0.068665 | 121.8613 | -0.01976 | 0.028749 | 0.061758 | 0.05921 | -0.0032599 | 0.0038282 | 0.0068038 | -0.005371 | 0.021035 | 0.042849 | -0.015065 | 0.013403 | 0.023751 | -0.0046933 | 40.6128 | 121.8063 | -0.045776 | 121.5958 | 9.5215 | 2.0187 | 1.8906 | 0.022888 | -0.004578 | -0.022888 | 0 | 0.09613 | 0.09613 | 0.086975 | 0.022889 | -0.054932 | -0.2655 | 9.5901 | 1.9592 | 2.0874 | 1.9363 | 2.0645 | 0.045777 | -121.8658 | -121.8613 | 0.16479 | 0.15564 | 0.16479 | 0.10986 | 0.11902 | 9.5673 | 121.6415 | 0.11902 | 0.022888 | 121.8521 | 0.01831 | 121.875 | 0.064087 | -121.907 | -121.8842 | 121.6644 | 0.068665 | 40.6815 | 0.091553
3922.8594 | 121.8842 | -0.07782 | 121.843 | -0.012131 | 0.031099 | 0.065604 | 0.06156 | 0.0012261 | 0.0053236 | 0.0074448 | -0.0023192 | 0.022103 | 0.043276 | -0.014638 | 0.017889 | 0.023964 | -0.0031979 | 40.448 | 121.8201 | -0.059509 | 121.5958 | 9.7366 | 1.886 | 1.8082 | 0.022888 | 0.009155 | -0.032043 | -0.022888 | 0.064087 | 0.022888 | 0.064087 | 0.018311 | -0.022889 | -0.24719 | 9.8145 | 1.886 | 1.9638 | 1.8677 | 1.9455 | 0.045777 | -121.8338 | -121.8658 | 0.14191 | 0.14191 | 0.10071 | 0.09613 | 0.054931 | 9.7961 | 121.6553 | 0.09613 | 0.009155 | 121.8796 | 0.041198 | 121.8979 | 0.086975 | -121.9025 | -121.875 | 121.6736 | 0.054932 | 40.5258 | 0.10071
3924.6406 | 121.962 | -0.082397 | 121.7972 | -0.012131 | 0.031954 | 0.064108 | 0.059637 | -0.0030463 | 0.0053236 | 0.010008 | -0.0084228 | 0.022531 | 0.042208 | -0.017842 | 0.017675 | 0.025887 | -0.0049069 | 40.4709 | 121.8384 | -0.073242 | 121.5683 | 9.7321 | 1.7944 | 1.7761 | 0.013733 | 0.009155 | -0.032043 | 0.045776 | 0.11902 | 0.086975 | 0.10529 | 0.009155 | 0.041199 | -0.22888 | 9.8145 | 1.8585 | 1.8768 | 1.8494 | 1.8677 | 0.050354 | -121.788 | -121.7514 | 0.20142 | 0.18768 | 0.16937 | 0.13733 | 0.11902 | 9.8053 | 121.6415 | 0.15106 | 0.077819 | 121.9116 | 0.041198 | 121.9208 | 0.091552 | -121.8704 | -121.8292 | 121.6507 | 0.12817 | 40.5533 | 0.09613
3926.3438 | 121.8338 | -0.10071 | 121.843 | -0.0045011 | 0.032808 | 0.063254 | 0.060919 | 0.0022943 | 0.006178 | 0.010222 | 0.00073235 | 0.022103 | 0.041567 | -0.0067333 | 0.014471 | 0.025246 | -0.0046933 | 40.3839 | 121.8246 | -0.07782 | 121.5134 | 9.8236 | 1.9363 | 1.8311 | -0.073242 | 0.022888 | -0.032043 | -0.073242 | 0.004578 | -0.027466 | 0.018311 | 0.022888 | -0.018311 | -0.32959 | 9.9243 | 1.9318 | 2.037 | 1.9089 | 2.0142 | 0.068665 | -121.8201 | -121.9162 | 0.10529 | 0.11902 | 0.073242 | 0.050354 | 0.004577 | 9.9014 | 121.5912 | 0.036621 | -0.041199 | 121.9025 | 0.054931 | 121.9254 | 0.1236 | -121.9208 | -121.875 | 121.6141 | 0.027466 | 40.4846 | 0.027466
3928.1094 | 122.0123 | -0.068665 | 121.7926 | -0.012131 | 0.026827 | 0.063895 | 0.057501 | -0.0013373 | 0.0053236 | 0.01364 | -0.0084228 | 0.020395 | 0.041994 | -0.017628 | 0.015539 | 0.02311 | -0.0012753 | 40.3656 | 121.7926 | -0.045776 | 121.6507 | 9.993 | 2.1011 | 2.037 | 0.13275 | -0.013733 | 0 | 0.064087 | 0.21057 | 0.17395 | 0.13733 | 0.022889 | 0 | -0.14191 | 10.0616 | 2.1057 | 2.1698 | 2.0828 | 2.1469 | 0.068665 | -121.8063 | -121.7285 | 0.27924 | 0.20599 | 0.24261 | 0.13733 | 0.17395 | 10.0388 | 121.6965 | 0.21057 | 0.064087 | 121.8384 | -0.013733 | 121.8613 | 0.054932 | -121.8384 | -121.7926 | 121.7194 | 0.13275 | 40.4343 | 0.20142
3929.875 | 121.9757 | -0.064087 | 121.8292 | -0.01976 | 0.029604 | 0.063467 | 0.058783 | -0.0019781 | 0.0046826 | 0.010222 | -0.005371 | 0.021035 | 0.043917 | -0.020192 | 0.01383 | 0.024391 | -0.0076841 | 40.3564 | 121.8155 | -0.059509 | 121.6003 | 9.9243 | 2.1561 | 1.8631 | 0.045776 | -0.027466 | -0.027466 | 0.036621 | 0.15106 | 0.13275 | 0.10986 | 0.004578 | -0.013733 | -0.22888 | 9.9884 | 1.9272 | 2.2202 | 1.9226 | 2.2156 | 0.036621 | -121.8567 | -121.7926 | 0.21515 | 0.17395 | 0.19684 | 0.13733 | 0.16022 | 9.9838 | 121.6599 | 0.17853 | 0.064087 | 121.875 | 0 | 121.8796 | 0.036621 | -121.8887 | -121.8567 | 121.6644 | 0.10071 | 40.4205 | 0.10986
3931.5781 | 121.9803 | -0.059509 | 121.7834 | -0.0045011 | 0.032167 | 0.064536 | 0.061133 | 0.0052851 | 0.0085278 | 0.011717 | -0.005371 | 0.020395 | 0.04413 | -0.017415 | 0.01383 | 0.024819 | -0.0042661 | 40.274 | 121.8063 | -0.041199 | 121.637 | 9.9838 | 2.2339 | 1.8723 | 0.091553 | -0.027466 | -0.018311 | 0.064087 | 0.14191 | 0.13275 | 0.15106 | 0.01831 | 0.022888 | -0.14648 | 10.0433 | 1.9318 | 2.2934 | 1.9135 | 2.2751 | 0.041198 | -121.8109 | -121.7194 | 0.20142 | 0.21057 | 0.19226 | 0.16937 | 0.15106 | 10.025 | 121.6782 | 0.16022 | 0.082398 | 121.8475 | -0.009155 | 121.8658 | 0.032043 | -121.8246 | -121.8018 | 121.6965 | 0.1236 | 40.3336 | 0.15106
3933.3438 | 121.8933 | -0.11444 | 121.8475 | -0.012131 | 0.031313 | 0.063254 | 0.059637 | 0.0061395 | 0.0042554 | 0.011504 | -0.0084228 | 0.021249 | 0.04413 | -0.014638 | 0.015539 | 0.023964 | -0.0042661 | 40.1917 | 121.8201 | -0.091553 | 121.5179 | 9.8648 | 2.0645 | 1.8814 | -0.041199 | 0.027466 | -0.059509 | -0.068665 | 0.073242 | 0.032043 | 0.059509 | 0.022888 | -0.027466 | -0.32959 | 9.9792 | 1.9959 | 2.179 | 1.973 | 2.1561 | 0.054932 | -121.8201 | -121.9162 | 0.18768 | 0.17395 | 0.14648 | 0.11902 | 0.091552 | 9.9564 | 121.6095 | 0.13275 | -0.009156 | 121.9116 | 0.086975 | 121.9345 | 0.14191 | -121.9391 | -121.907 | 121.6324 | 0.045776 | 40.3061 | 0.073242
3935.0781 | 121.9803 | -0.041199 | 121.8063 | -0.01976 | 0.030886 | 0.062399 | 0.059637 | -0.0028327 | 0.0059644 | 0.0093674 | -0.005371 | 0.01954 | 0.042421 | -0.017415 | 0.015112 | 0.025032 | -0.0036253 | 40.21 | 121.7606 | -0.041199 | 121.637 | 10.1624 | 2.1469 | 2.0187 | 0.1236 | -0.009155 | -0.009155 | 0.059509 | 0.17395 | 0.15564 | 0.13733 | 0 | -0.045776 | -0.16937 | 10.2036 | 2.0599 | 2.1881 | 2.0599 | 2.1881 | 0.032044 | -121.8155 | -121.7468 | 0.21515 | 0.17853 | 0.19684 | 0.14648 | 0.16479 | 10.2036 | 121.6782 | 0.1831 | 0.068664 | 121.8018 | 0 | 121.8018 | 0.032044 | -121.8475 | -121.8155 | 121.6782 | 0.10071 | 40.2512 | 0.16479
3936.8438 | 121.9986 | -0.050354 | 121.7926 | -0.012131 | 0.032595 | 0.063895 | 0.057287 | -0.00069646 | 0.0051098 | 0.0080856 | -0.0023192 | 0.017831 | 0.039217 | -0.015065 | 0.014898 | 0.023537 | -0.0040525 | 40.1459 | 121.7834 | -0.050354 | 121.6324 | 10.1669 | 2.211 | 1.918 | 0.13275 | -0.027466 | 0 | 0.068665 | 0.1831 | 0.17853 | 0.13733 | 0 | -0.009156 | -0.16022 | 10.2173 | 1.9684 | 2.2614 | 1.9684 | 2.2614 | 0.050354 | -121.8201 | -121.7239 | 0.23346 | 0.18768 | 0.22888 | 0.13733 | 0.17853 | 10.2173 | 121.6827 | 0.1831 | 0.068665 | 121.8338 | -0.027466 | 121.8338 | 0.022888 | -121.843 | -121.7926 | 121.6827 | 0.11902 | 40.1962 | 0.18311
3938.5469 | 121.9437 | -0.07782 | 121.788 | -0.0045011 | 0.031099 | 0.063895 | 0.060064 | -0.00091006 | 0.0042554 | 0.0076584 | -0.0084228 | 0.019967 | 0.041567 | -0.011647 | 0.012762 | 0.02311 | -0.0064023 | 40.0955 | 121.7972 | -0.050354 | 121.5729 | 10.199 | 2.2064 | 1.9409 | 0.036621 | -0.036621 | -0.027466 | -0.009155 | 0.11902 | 0.091553 | 0.10986 | 0.027466 | 0.009155 | -0.21515 | 10.2768 | 2.0187 | 2.2842 | 1.9913 | 2.2568 | 0.050354 | -121.8246 | -121.7972 | 0.19684 | 0.18768 | 0.16937 | 0.13733 | 0.11902 | 10.2493 | 121.6232 | 0.14649 | 0.018311 | 121.8475 | -0.009155 | 121.875 | 0.041199 | -121.8384 | -121.8155 | 121.6507 | 0.068665 | 40.1733 | 0.11444
3940.3125 | 121.9803 | -0.082397 | 121.788 | -0.012131 | 0.031099 | 0.063467 | 0.059637 | -0.0043281 | 0.0063916 | 0.011717 | -0.0084228 | 0.019113 | 0.042421 | -0.0063061 | 0.01383 | 0.021828 | -0.0027707 | 39.9536 | 121.7972 | -0.045776 | 121.5912 | 10.2539 | 2.1103 | 1.9135 | 0.073242 | -0.027466 | -0.013733 | 0.036621 | 0.17853 | 0.16022 | 0.11902 | 0.036621 | 0.009155 | -0.19684 | 10.3363 | 1.9958 | 2.1927 | 1.9592 | 2.1561 | 0.068664 | -121.8155 | -121.7514 | 0.26092 | 0.20142 | 0.24261 | 0.13275 | 0.17395 | 10.2997 | 121.637 | 0.19226 | 0.050354 | 121.843 | -0.013733 | 121.8796 | 0.054931 | -121.8338 | -121.8018 | 121.6736 | 0.11902 | 40.036 | 0.15564
3942.0781 | 121.8979 | -0.091553 | 121.7972 | -0.012131 | 0.036226 | 0.064536 | 0.061346 | 0.0018671 | 0.0055372 | 0.0097946 | -0.0023192 | 0.022531 | 0.044558 | -0.0084423 | 0.017248 | 0.024819 | -0.0072569 | 39.9216 | 121.8201 | -0.073242 | 121.5683 | 10.3592 | 2.1332 | 1.9272 | 0.050354 | 0.004578 | -0.032043 | -0.018311 | 0.10071 | 0.054932 | 0.064087 | 0.018311 | 0.022888 | -0.22888 | 10.4507 | 2.0187 | 2.2247 | 2.0004 | 2.2064 | 0.05951 | -121.7926 | -121.8155 | 0.19226 | 0.15564 | 0.14649 | 0.09613 | 0.086975 | 10.4324 | 121.6415 | 0.13275 | 0.013732 | 121.8933 | 0.036621 | 121.9116 | 0.096131 | -121.8704 | -121.8292 | 121.6599 | 0.073242 | 40.0131 | 0.14191
3943.8594 | 121.9574 | -0.07782 | 121.8063 | -0.012131 | 0.031527 | 0.065176 | 0.057928 | 0.0016535 | 0.0059644 | 0.011931 | -0.005371 | 0.019754 | 0.041567 | -0.019978 | 0.015112 | 0.024819 | -0.0027707 | 39.8346 | 121.7743 | -0.059509 | 121.5912 | 10.4599 | 2.2247 | 1.9958 | 0.045776 | -0.004578 | -0.032043 | 0.036621 | 0.16022 | 0.14191 | 0.11902 | 0.018311 | -0.032043 | -0.21515 | 10.5377 | 2.0737 | 2.3026 | 2.0554 | 2.2842 | 0.045777 | -121.8109 | -121.7697 | 0.23804 | 0.19684 | 0.21973 | 0.15106 | 0.17395 | 10.5194 | 121.6507 | 0.19226 | 0.068664 | 121.8338 | 0.027465 | 121.8521 | 0.073242 | -121.8658 | -121.8384 | 121.669 | 0.11444 | 39.9124 | 0.1236
3945.625 | 121.843 | -0.10071 | 121.7789 | -0.012131 | 0.035585 | 0.064536 | 0.064337 | 0.0025079 | 0.0085278 | 0.013853 | -0.0023192 | 0.022317 | 0.043917 | -0.013356 | 0.016607 | 0.024819 | -0.0061887 | 39.7705 | 121.8246 | -0.086975 | 121.4951 | 10.4416 | 2.1149 | 2.037 | -0.059509 | 0.018311 | -0.045776 | -0.036621 | 0.018311 | -0.009155 | 0.041199 | 0.013733 | 0.045776 | -0.28381 | 10.5423 | 2.1378 | 2.2156 | 2.124 | 2.2018 | 0.054932 | -121.7606 | -121.8155 | 0.11902 | 0.14191 | 0.091553 | 0.086975 | 0.036621 | 10.5286 | 121.582 | 0.064087 | 0.009155 | 121.9116 | 0.064087 | 121.9254 | 0.11902 | -121.8658 | -121.8246 | 121.5958 | 0.064087 | 39.8712 | 0.041199
3947.3281 | 121.9757 | -0.082397 | 121.7743 | -0.01976 | 0.030458 | 0.064108 | 0.060492 | -0.00091006 | 0.0057508 | 0.0093674 | -0.005371 | 0.018258 | 0.043917 | -0.020405 | 0.01383 | 0.023537 | -0.0042661 | 39.743 | 121.7743 | -0.068665 | 121.6003 | 10.6247 | 2.3254 | 2.0966 | 0.073242 | -0.032043 | -0.013733 | 0.050354 | 0.15564 | 0.15564 | 0.13275 | 0.013732 | 0 | -0.17395 | 10.7071 | 2.179 | 2.4078 | 2.1652 | 2.3941 | 0.068664 | -121.8063 | -121.7239 | 0.23804 | 0.21515 | 0.23804 | 0.14648 | 0.16937 | 10.6934 | 121.669 | 0.16937 | 0.064087 | 121.843 | -0.01831 | 121.8567 | 0.050354 | -121.843 | -121.788 | 121.6827 | 0.13275 | 39.8254 | 0.15564
3949.0938 | 121.994 | -0.068665 | 121.7926 | -0.0045011 | 0.031527 | 0.062827 | 0.06156 | -0.0026191 | 0.0070324 | 0.011076 | -0.011475 | 0.019326 | 0.043703 | -0.015278 | 0.014684 | 0.02546 | 0.00086095 | 39.7476 | 121.7285 | -0.050354 | 121.6415 | 10.7117 | 2.3849 | 2.1835 | 0.14191 | -0.032043 | -0.004578 | 0.086975 | 0.21057 | 0.1831 | 0.15106 | 0.018311 | -0.064087 | -0.15106 | 10.7803 | 2.2522 | 2.4536 | 2.2339 | 2.4353 | 0.064087 | -121.8246 | -121.7056 | 0.27924 | 0.21973 | 0.25177 | 0.15564 | 0.18768 | 10.762 | 121.6919 | 0.21515 | 0.091553 | 121.7789 | -0.027465 | 121.7972 | 0.036622 | -121.843 | -121.7972 | 121.7102 | 0.15564 | 39.8163 | 0.21057
3950.875 | 121.9116 | -0.068665 | 121.8018 | -0.01976 | 0.033235 | 0.066672 | 0.060919 | -0.00026906 | 0.0057508 | 0.011076 | -0.0023192 | 0.021249 | 0.043917 | -0.014638 | 0.012975 | 0.022469 | -0.0053343 | 39.6927 | 121.7606 | -0.041199 | 121.5683 | 10.6842 | 2.2064 | 2.1652 | 0.041199 | -0.013733 | 0 | 0.009155 | 0.1236 | 0.086975 | 0.091553 | 0.027466 | -0.041199 | -0.23346 | 10.7529 | 2.2339 | 2.2751 | 2.2064 | 2.2476 | 0.068665 | -121.8155 | -121.7926 | 0.19226 | 0.16022 | 0.15564 | 0.091553 | 0.086975 | 10.7254 | 121.6095 | 0.1236 | 0.009155 | 121.8018 | -0.013733 | 121.8292 | 0.054932 | -121.843 | -121.8018 | 121.637 | 0.07782 | 39.7614 | 0.10986
3952.5781 | 121.9711 | -0.073242 | 121.7743 | -0.02739 | 0.030886 | 0.063254 | 0.058996 | -0.0021919 | 0.0074598 | 0.010863 | -0.005371 | 0.021035 | 0.04413 | -0.016774 | 0.014684 | 0.023964 | -0.0025571 | 39.6103 | 121.7422 | -0.050354 | 121.6141 | 10.6934 | 2.3666 | 2.1469 | 0.10529 | -0.027466 | 0 | 0.064087 | 0.17853 | 0.16937 | 0.14648 | 0.022888 | -0.032043 | -0.16022 | 10.7666 | 2.2202 | 2.4399 | 2.1973 | 2.417 | 0.073242 | -121.8018 | -121.7102 | 0.25177 | 0.21973 | 0.24261 | 0.14648 | 0.16937 | 10.7437 | 121.6644 | 0.17853 | 0.064087 | 121.7926 | -0.027466 | 121.8155 | 0.045776 | -121.8246 | -121.7743 | 121.6873 | 0.13733 | 39.6835 | 0.17853
3954.3594 | 121.9574 | -0.054932 | 121.7651 | -0.012131 | 0.032595 | 0.066245 | 0.061346 | -0.0049689 | 0.0055372 | 0.0093674 | 0.00073235 | 0.020608 | 0.044558 | -0.013783 | 0.012548 | 0.023964 | -0.0034117 | 39.5782 | 121.7514 | -0.054932 | 121.6644 | 10.9177 | 2.417 | 2.2064 | 0.12817 | -0.022888 | -0.004578 | 0.054932 | 0.18768 | 0.17395 | 0.12817 | 0 | -0.013733 | -0.10071 | 10.9726 | 2.2614 | 2.4719 | 2.2614 | 2.4719 | 0.050354 | -121.788 | -121.7102 | 0.24261 | 0.18311 | 0.22888 | 0.13275 | 0.17853 | 10.9726 | 121.7194 | 0.19226 | 0.05951 | 121.8063 | -0.01831 | 121.8063 | 0.032044 | -121.8201 | -121.7697 | 121.7194 | 0.10986 | 39.6332 | 0.18311
3956.0625 | 121.907 | -0.068665 | 121.756 | -0.012131 | 0.033022 | 0.063895 | 0.060919 | -0.0032599 | 0.0053236 | 0.0089402 | -0.005371 | 0.021035 | 0.04178 | -0.020833 | 0.013403 | 0.024178 | -0.0034117 | 39.5462 | 121.7651 | -0.064087 | 121.5729 | 10.9451 | 2.2293 | 2.1744 | 0.004578 | -0.009155 | -0.027466 | -0.004578 | 0.09613 | 0.068665 | 0.073242 | 0.004578 | 0.009156 | -0.18311 | 11.0138 | 2.243 | 2.298 | 2.2385 | 2.2934 | 0.041199 | -121.7651 | -121.7606 | 0.16479 | 0.14191 | 0.13733 | 0.10071 | 0.096131 | 11.0092 | 121.637 | 0.1236 | 0.022888 | 121.8292 | 0.018311 | 121.8338 | 0.05951 | -121.8201 | -121.7834 | 121.6415 | 0.064087 | 39.6149 | 0.073243
3957.8281 | 121.8613 | -0.09613 | 121.7834 | -0.012131 | 0.035799 | 0.064108 | 0.062842 | -0.0011237 | 0.0059644 | 0.010435 | -0.005371 | 0.023385 | 0.045839 | -0.011433 | 0.01618 | 0.021187 | -0.0021299 | 39.4913 | 121.8063 | -0.086975 | 121.5134 | 10.9863 | 2.2522 | 2.0508 | -0.059509 | 0.013733 | -0.027466 | -0.054932 | 0.064087 | 0.032043 | 0.054932 | 0.009155 | 0.022888 | -0.27008 | 11.0825 | 2.1469 | 2.3483 | 2.1378 | 2.3392 | 0.068664 | -121.7697 | -121.8384 | 0.16022 | 0.15106 | 0.12817 | 0.082398 | 0.059509 | 11.0733 | 121.6003 | 0.091553 | -0.027466 | 121.8933 | 0.041199 | 121.9025 | 0.10986 | -121.8704 | -121.8109 | 121.6095 | 0.041198 | 39.5874 | 0.036621
3959.6094 | 121.8933 | -0.059509 | 121.7743 | -0.01976 | 0.033022 | 0.065604 | 0.061773 | -0.0041145 | 0.0048962 | 0.011076 | -0.011475 | 0.020395 | 0.04413 | -0.013569 | 0.014898 | 0.024819 | -0.0066159 | 39.4226 | 121.7239 | -0.036621 | 121.5912 | 11.087 | 2.4582 | 2.2522 | 0.064087 | -0.013733 | -0.022888 | 0.013733 | 0.11444 | 0.09613 | 0.091553 | 0.022888 | -0.050354 | -0.1831 | 11.1465 | 2.3117 | 2.5177 | 2.2888 | 2.4948 | 0.036621 | -121.788 | -121.7606 | 0.17395 | 0.15106 | 0.15564 | 0.11444 | 0.11902 | 11.1237 | 121.6278 | 0.13733 | 0.036621 | 121.7606 | 0.009155 | 121.7834 | 0.045776 | -121.8109 | -121.7972 | 121.6507 | 0.073242 | 39.4821 | 0.1236
3961.375 | 121.9025 | -0.086975 | 121.7377 | -0.012131 | 0.032595 | 0.065817 | 0.061773 | -0.0028327 | 0.0053236 | 0.014494 | -0.005371 | 0.022531 | 0.043489 | -0.02596 | 0.014257 | 0.022255 | -0.0010617 | 39.3494 | 121.756 | -0.045776 | 121.5637 | 11.0184 | 2.4307 | 2.2797 | 0.041199 | 0.013733 | -0.018311 | 0.004578 | 0.09613 | 0.07782 | 0.091553 | 0.041199 | 0.01831 | -0.17395 | 11.1053 | 2.3666 | 2.5177 | 2.3254 | 2.4765 | 0.068664 | -121.7239 | -121.7331 | 0.1831 | 0.17853 | 0.16479 | 0.10986 | 0.096131 | 11.0641 | 121.6095 | 0.11444 | 0.022889 | 121.8018 | 0.032044 | 121.843 | 0.10071 | -121.7834 | -121.756 | 121.6507 | 0.091553 | 39.4363 | 0.12817
3963.0938 | 121.8384 | -0.09613 | 121.8155 | -0.012131 | 0.036867 | 0.064749 | 0.064551 | 0.00079894 | 0.0074598 | 0.011931 | -0.0023192 | 0.022317 | 0.043489 | -0.010365 | 0.017675 | 0.022896 | -0.0036253 | 39.1937 | 121.8155 | -0.082397 | 121.4859 | 10.9817 | 2.2339 | 2.2293 | -0.059509 | 0.018311 | -0.041199 | -0.050354 | 0.009155 | -0.027466 | 0.036621 | 0.013733 | 0 | -0.32959 | 11.0779 | 2.3254 | 2.33 | 2.3117 | 2.3163 | 0.054931 | -121.7972 | -121.8658 | 0.10528 | 0.13275 | 0.068664 | 0.07782 | 0.013733 | 11.0641 | 121.5683 | 0.050354 | -0.009155 | 121.8979 | 0.05951 | 121.9116 | 0.11444 | -121.8979 | -121.8567 | 121.582 | 0.045776 | 39.2899 | 0.036621
3964.875 | 121.9437 | -0.054932 | 121.7514 | -0.012131 | 0.03409 | 0.065604 | 0.057928 | -0.0028327 | 0.0070324 | 0.012144 | -0.005371 | 0.021035 | 0.044344 | -0.018055 | 0.012334 | 0.026314 | -0.00042085 | 39.2624 | 121.7514 | -0.045776 | 121.6415 | 11.3663 | 2.4582 | 2.3712 | 0.10986 | -0.009155 | 0.004578 | 0.073242 | 0.18768 | 0.16479 | 0.1236 | 0.009156 | 0 | -0.10986 | 11.4212 | 2.4261 | 2.5131 | 2.417 | 2.504 | 0.05951 | -121.7606 | -121.6782 | 0.24261 | 0.17853 | 0.21973 | 0.11902 | 0.16022 | 11.412 | 121.6873 | 0.1831 | 0.068664 | 121.7972 | -0.013733 | 121.8063 | 0.045777 | -121.7972 | -121.7468 | 121.6965 | 0.12817 | 39.3173 | 0.16479
3966.5938 | 121.875 | -0.073242 | 121.7651 | -0.0045011 | 0.033663 | 0.067099 | 0.059637 | -0.0026191 | 0.006178 | 0.014067 | -0.0084228 | 0.021463 | 0.044344 | -0.01656 | 0.012975 | 0.022469 | -0.0021299 | 39.0884 | 121.7697 | -0.050354 | 121.5591 | 11.3251 | 2.2797 | 2.2339 | 0.022888 | -0.013733 | -0.018311 | 0 | 0.10071 | 0.086975 | 0.10529 | 0.022888 | 0.004577 | -0.20599 | 11.3983 | 2.3071 | 2.3529 | 2.2842 | 2.33 | 0.054931 | -121.7789 | -121.7651 | 0.17395 | 0.17853 | 0.16022 | 0.1236 | 0.10529 | 11.3754 | 121.6095 | 0.11902 | 0.018311 | 121.8201 | 0.004578 | 121.843 | 0.059509 | -121.8155 | -121.7834 | 121.6324 | 0.073242 | 39.1617 | 0.09613
3968.375 | 121.9482 | -0.045776 | 121.7285 | -0.012131 | 0.036653 | 0.066245 | 0.060705 | 0.0035761 | 0.0091688 | 0.013213 | -0.0084228 | 0.020395 | 0.044771 | -0.018055 | 0.01618 | 0.023964 | -0.00020725 | 39.1388 | 121.756 | -0.041199 | 121.6141 | 11.4395 | 2.5452 | 2.3529 | 0.10986 | -0.022888 | -0.009155 | 0.07782 | 0.16479 | 0.11444 | 0.15564 | 0.004577 | 0.027465 | -0.11444 | 11.4853 | 2.3987 | 2.5909 | 2.3941 | 2.5864 | 0.036621 | -121.7514 | -121.6507 | 0.21057 | 0.20142 | 0.16022 | 0.16479 | 0.1236 | 11.4807 | 121.6553 | 0.17395 | 0.086975 | 121.7972 | -0.013733 | 121.8018 | 0.022888 | -121.7697 | -121.7377 | 121.6599 | 0.1236 | 39.1846 | 0.15564
3970.0938 | 121.8201 | -0.11444 | 121.8201 | -0.01976 | 0.038362 | 0.067953 | 0.064978 | -5.5462e-05 | 0.0089552 | 0.012999 | -0.0023192 | 0.022744 | 0.044558 | -0.014424 | 0.015966 | 0.022683 | -0.0019163 | 39.1708 | 121.7834 | -0.07782 | 121.5042 | 11.3617 | 2.3941 | 2.0645 | -0.050354 | 0.027466 | -0.036621 | -0.064087 | 0.018311 | -0.027466 | 0.027466 | 0.036621 | -0.036621 | -0.31586 | 11.4761 | 2.179 | 2.5085 | 2.1423 | 2.4719 | 0.07782 | -121.7926 | -121.8842 | 0.13275 | 0.14191 | 0.086975 | 0.064087 | 0.009155 | 11.4395 | 121.582 | 0.054932 | -0.027466 | 121.8613 | 0.064087 | 121.8979 | 0.14191 | -121.8979 | -121.8567 | 121.6187 | 0.050354 | 39.2853 | 0.064087
3971.8594 | 121.8796 | -0.091553 | 121.7606 | -0.012131 | 0.036013 | 0.066672 | 0.060492 | -0.00069646 | 0.0081006 | 0.013426 | -0.005371 | 0.018258 | 0.042208 | -0.016987 | 0.01383 | 0.023323 | -0.0038389 | 39.0701 | 121.7651 | -0.045776 | 121.5408 | 11.6547 | 2.5269 | 2.2064 | 0.022888 | -0.022888 | -0.041199 | 0 | 0.11902 | 0.10529 | 0.086975 | 0.045777 | 0.004578 | -0.21973 | 11.7462 | 2.298 | 2.6184 | 2.2522 | 2.5726 | 0.050354 | -121.7834 | -121.7606 | 0.21057 | 0.17853 | 0.19684 | 0.12817 | 0.14649 | 11.7004 | 121.5866 | 0.16022 | 0.041199 | 121.8109 | 0.018311 | 121.8567 | 0.068665 | -121.8063 | -121.8018 | 121.6324 | 0.091553 | 39.1617 | 0.11444
3973.5625 | 121.9437 | -0.064087 | 121.7606 | -0.0045011 | 0.040071 | 0.067313 | 0.060492 | 0.0014397 | 0.0083142 | 0.015135 | -0.005371 | 0.021463 | 0.045412 | -0.01421 | 0.015539 | 0.024178 | -0.0014891 | 39.0381 | 121.7331 | -0.032043 | 121.6049 | 11.9202 | 2.6276 | 2.4261 | 0.11444 | -0.027466 | 0.013733 | 0.091553 | 0.17395 | 0.14648 | 0.13275 | 0.032044 | -0.027466 | -0.15564 | 11.9843 | 2.4902 | 2.6917 | 2.4582 | 2.6596 | 0.07782 | -121.788 | -121.669 | 0.23804 | 0.19684 | 0.21057 | 0.11902 | 0.13275 | 11.9522 | 121.637 | 0.16022 | 0.07782 | 121.7651 | -0.041199 | 121.7972 | 0.036621 | -121.7926 | -121.7468 | 121.669 | 0.15564 | 39.1022 | 0.17853
3975.3281 | 121.7926 | -0.091553 | 121.7606 | -0.01976 | 0.035799 | 0.066672 | 0.059851 | 0.0029351 | 0.0063916 | 0.011504 | -0.0023192 | 0.022744 | 0.042421 | -0.016987 | 0.013403 | 0.023323 | -0.0049069 | 38.8367 | 121.7422 | -0.064087 | 121.5363 | 12.0575 | 2.536 | 2.4033 | -0.013733 | 0.004578 | -0.027466 | -0.050354 | 0.064087 | 0.036621 | 0.022888 | 0.027466 | -0.01831 | -0.2243 | 12.149 | 2.4948 | 2.6276 | 2.4673 | 2.6001 | 0.064087 | -121.756 | -121.8109 | 0.15564 | 0.11444 | 0.12817 | 0.050354 | 0.064087 | 12.1216 | 121.6003 | 0.091553 | -0.022888 | 121.8063 | 0.032044 | 121.8338 | 0.096131 | -121.8246 | -121.788 | 121.6278 | 0.041199 | 38.9282 | 0.07782
3977.0312 | 121.9437 | -0.064087 | 121.7514 | -0.012131 | 0.036653 | 0.06539 | 0.058142 | -0.0049689 | 0.0070324 | 0.011717 | -0.005371 | 0.018258 | 0.042635 | -0.023182 | 0.012975 | 0.02311 | -0.0017027 | 38.8 | 121.7331 | -0.036621 | 121.6278 | 12.2452 | 2.5543 | 2.3529 | 0.12817 | -0.022888 | -0.009155 | 0.059509 | 0.18768 | 0.16479 | 0.11902 | 0.027466 | -0.018311 | -0.1236 | 12.3093 | 2.417 | 2.6184 | 2.3895 | 2.5909 | 0.054932 | -121.7743 | -121.6919 | 0.25177 | 0.18311 | 0.22888 | 0.12817 | 0.17395 | 12.2818 | 121.6644 | 0.19684 | 0.068664 | 121.7697 | -0.013733 | 121.7972 | 0.041199 | -121.788 | -121.7606 | 121.6919 | 0.1236 | 38.8641 | 0.19226
3978.7969 | 121.9116 | -0.073242 | 121.8018 | -0.012131 | 0.036226 | 0.065817 | 0.060705 | -0.00048286 | 0.0081006 | 0.013213 | -0.0084228 | 0.022103 | 0.03879 | -0.010365 | 0.01383 | 0.024819 | -0.0072569 | 38.5757 | 121.7331 | -0.036621 | 121.6095 | 12.2452 | 2.6733 | 2.3895 | 0.068665 | -0.018311 | -0.022888 | 0.013733 | 0.13733 | 0.12817 | 0.10529 | 0.036621 | -0.068665 | -0.19226 | 12.3184 | 2.4628 | 2.7466 | 2.4261 | 2.71 | 0.050354 | -121.8201 | -121.788 | 0.21057 | 0.17853 | 0.20142 | 0.12817 | 0.15106 | 12.2818 | 121.6461 | 0.16022 | 0.036621 | 121.7697 | 0.004577 | 121.8063 | 0.054931 | -121.8384 | -121.8246 | 121.6827 | 0.086975 | 38.649 | 0.14191
3980.5781 | 121.9803 | -0.054932 | 121.8201 | -0.012131 | 0.034731 | 0.066672 | 0.060492 | -0.0045417 | 0.0059644 | 0.010649 | -0.0023192 | 0.018045 | 0.039217 | -0.021046 | 0.012548 | 0.022683 | -0.0087521 | 38.7039 | 121.7468 | -0.054932 | 121.669 | 12.4558 | 2.7466 | 2.4673 | 0.11902 | -0.013733 | 0 | 0.068665 | 0.20142 | 0.16937 | 0.13275 | 0 | -0.073242 | -0.15106 | 12.5107 | 2.5223 | 2.8015 | 2.5223 | 2.8015 | 0.054932 | -121.8338 | -121.7514 | 0.25635 | 0.18768 | 0.22431 | 0.13275 | 0.16937 | 12.5107 | 121.7239 | 0.20142 | 0.068665 | 121.8018 | -0.013733 | 121.8018 | 0.041199 | -121.875 | -121.8201 | 121.7239 | 0.1236 | 38.7589 | 0.17395
3982.2969 | 121.8613 | -0.10529 | 121.8384 | -0.0045011 | 0.037294 | 0.066031 | 0.062201 | -0.00048286 | 0.0087414 | 0.010649 | -0.005371 | 0.022103 | 0.038576 | -0.014851 | 0.014043 | 0.024178 | -0.0023435 | 38.5712 | 121.8201 | -0.064087 | 121.5775 | 12.3596 | 2.5864 | 2.3666 | -0.022888 | 0.013733 | -0.041199 | -0.050354 | 0.064087 | 0.022888 | 0.036621 | 0.041199 | -0.018311 | -0.26093 | 12.4649 | 2.4719 | 2.6917 | 2.4307 | 2.6505 | 0.064087 | -121.8246 | -121.8887 | 0.16937 | 0.14191 | 0.12817 | 0.07782 | 0.064087 | 12.4237 | 121.6415 | 0.10529 | -0.009155 | 121.8842 | 0.054932 | 121.9254 | 0.11902 | -121.9025 | -121.8796 | 121.6827 | 0.054932 | 38.6765 | 0.082398
3984.0625 | 121.9666 | -0.068665 | 121.8018 | -0.012131 | 0.04114 | 0.067313 | 0.064337 | 0.0022943 | 0.0087414 | 0.013853 | -0.0023192 | 0.022531 | 0.040071 | -0.015919 | 0.016821 | 0.023537 | -0.0031979 | 38.562 | 121.8521 | -0.059509 | 121.5912 | 12.5198 | 2.5452 | 2.3392 | 0.018311 | 0.004578 | -0.032043 | 0.045776 | 0.1236 | 0.10529 | 0.1236 | 0.009156 | 0.050354 | -0.21057 | 12.5885 | 2.4078 | 2.6138 | 2.3987 | 2.6047 | 0.036622 | -121.7972 | -121.756 | 0.19226 | 0.19226 | 0.17395 | 0.15564 | 0.13733 | 12.5793 | 121.6507 | 0.15564 | 0.077819 | 121.9116 | 0.036621 | 121.9208 | 0.073243 | -121.8613 | -121.8338 | 121.6599 | 0.11444 | 38.6307 | 0.086976
3985.8281 | 121.907 | -0.091553 | 121.8613 | -0.02739 | 0.036653 | 0.066031 | 0.060705 | -5.5462e-05 | 0.0089552 | 0.014067 | -0.0084228 | 0.01954 | 0.040926 | -0.012074 | 0.01383 | 0.024178 | -0.0038389 | 38.5941 | 121.8109 | -0.059509 | 121.6415 | 12.8494 | 2.7878 | 2.5085 | 0.032043 | -0.013733 | -0.032043 | -0.018311 | 0.10529 | 0.07782 | 0.068665 | 0.032044 | -0.050354 | -0.21973 | 12.941 | 2.6001 | 2.8793 | 2.5681 | 2.8473 | 0.05951 | -121.875 | -121.8796 | 0.19684 | 0.16022 | 0.16937 | 0.10071 | 0.10986 | 12.9089 | 121.7011 | 0.13733 | 0.013732 | 121.8704 | 0.01831 | 121.9025 | 0.07782 | -121.9208 | -121.8933 | 121.7331 | 0.073242 | 38.6856 | 0.1236
3987.6094 | 121.9574 | -0.064087 | 121.8201 | -0.02739 | 0.038149 | 0.067953 | 0.061987 | 0.0016535 | 0.0074598 | 0.010008 | -0.005371 | 0.019113 | 0.039003 | -0.016133 | 0.015325 | 0.025887 | -0.0029843 | 38.4888 | 121.8201 | -0.045776 | 121.6095 | 12.8677 | 2.7283 | 2.4628 | 0.018311 | -0.009155 | 0.009155 | 0.004578 | 0.10529 | 0.091553 | 0.091553 | 0.018311 | 0 | -0.21057 | 12.9318 | 2.5269 | 2.7924 | 2.5085 | 2.774 | 0.073242 | -121.8292 | -121.8155 | 0.16937 | 0.15564 | 0.15564 | 0.082398 | 0.082398 | 12.9135 | 121.6553 | 0.096131 | -0.004577 | 121.8658 | -0.01831 | 121.8842 | 0.054932 | -121.8658 | -121.8109 | 121.6736 | 0.068665 | 38.5529 | 0.082398
3989.3125 | 121.9208 | -0.086975 | 121.8704 | -0.01976 | 0.040926 | 0.069449 | 0.06391 | 0.00058534 | 0.0083142 | 0.012785 | -0.0084228 | 0.022958 | 0.040285 | -0.010365 | 0.014257 | 0.027809 | -0.0031979 | 38.4384 | 121.8658 | -0.073242 | 121.637 | 13.06 | 2.8015 | 2.449 | 0.032043 | 0.009155 | -0.022888 | 0.009155 | 0.10071 | 0.050354 | 0.073242 | 0.013733 | -0.004577 | -0.23346 | 13.147 | 2.536 | 2.8885 | 2.5223 | 2.8748 | 0.064087 | -121.8613 | -121.8613 | 0.18768 | 0.16022 | 0.13733 | 0.09613 | 0.073242 | 13.1332 | 121.7102 | 0.1236 | 0.032043 | 121.9391 | 0.032043 | 121.9528 | 0.09613 | -121.9437 | -121.8933 | 121.7239 | 0.09613 | 38.5254 | 0.11902
3991.0938 | 121.8887 | -0.10529 | 121.8704 | -0.012131 | 0.039431 | 0.067953 | 0.063269 | 0.0029351 | 0.0076734 | 0.014494 | -0.011475 | 0.021035 | 0.036867 | -0.01421 | 0.015752 | 0.023537 | -0.0057615 | 38.5162 | 121.8384 | -0.082397 | 121.582 | 13.1012 | 2.7283 | 2.4216 | -0.041199 | 0.009155 | -0.054932 | -0.068665 | 0.032043 | 0.018311 | 0.027466 | 0.022889 | -0.032043 | -0.28839 | 13.2065 | 2.5269 | 2.8336 | 2.504 | 2.8107 | 0.050354 | -121.8613 | -121.9391 | 0.13733 | 0.13275 | 0.1236 | 0.082398 | 0.073243 | 13.1836 | 121.6644 | 0.086975 | -0.013733 | 121.9208 | 0.064087 | 121.9437 | 0.11444 | -121.9528 | -121.9254 | 121.6873 | 0.036621 | 38.6215 | 0.064087
3992.875 | 121.9849 | -0.086975 | 121.8292 | 0.0031279 | 0.039431 | 0.069235 | 0.062201 | -0.0041145 | 0.0076734 | 0.015776 | -0.005371 | 0.019754 | 0.039431 | -0.01891 | 0.011907 | 0.024605 | -0.0017027 | 38.5849 | 121.8246 | -0.054932 | 121.6324 | 13.1195 | 2.8244 | 2.5085 | 0.022888 | -0.018311 | -0.022888 | 0 | 0.11444 | 0.082397 | 0.10071 | 0.032043 | -0.004578 | -0.19684 | 13.2065 | 2.5955 | 2.9114 | 2.5635 | 2.8793 | 0.064087 | -121.8475 | -121.8292 | 0.20142 | 0.18768 | 0.16937 | 0.1236 | 0.10528 | 13.1744 | 121.6873 | 0.13733 | 0.022888 | 121.8796 | 0.004577 | 121.9116 | 0.068664 | -121.8842 | -121.8521 | 121.7194 | 0.086975 | 38.6719 | 0.10986
3994.5938 | 122.0444 | -0.050354 | 121.8384 | -0.01976 | 0.040926 | 0.067313 | 0.062842 | -0.0045417 | 0.010878 | 0.012144 | -0.0023192 | 0.020822 | 0.040926 | -0.01186 | 0.011053 | 0.025246 | -0.0021299 | 38.7085 | 121.8155 | -0.059509 | 121.6461 | 13.2568 | 2.7512 | 2.5314 | 0.041199 | -0.018311 | -0.018311 | 0.032043 | 0.15106 | 0.13733 | 0.12817 | -0.009155 | -0.022888 | -0.19226 | 13.3072 | 2.5818 | 2.8015 | 2.5909 | 2.8107 | 0.032043 | -121.8567 | -121.8063 | 0.20142 | 0.17853 | 0.18768 | 0.14649 | 0.15564 | 13.3163 | 121.7056 | 0.16937 | 0.050354 | 121.875 | 0 | 121.8658 | 0.032043 | -121.8979 | -121.8567 | 121.6965 | 0.082397 | 38.7588 | 0.091553
3996.3594 | 122.0123 | -0.068665 | 121.8201 | -0.01976 | 0.043703 | 0.069022 | 0.062628 | -0.00091006 | 0.010237 | 0.012999 | -0.005371 | 0.021035 | 0.03879 | -0.0090833 | 0.014471 | 0.024605 | 6.346e-06 | 38.8 | 121.8613 | -0.032043 | 121.6965 | 13.623 | 2.9892 | 2.6871 | 0.10529 | -0.018311 | 0.004578 | 0.068665 | 0.15106 | 0.13733 | 0.1236 | 0.036622 | 0.041199 | -0.1236 | 13.6917 | 2.7557 | 3.0579 | 2.7191 | 3.0212 | 0.073243 | -121.8384 | -121.7514 | 0.21973 | 0.19226 | 0.20599 | 0.11902 | 0.13275 | 13.6551 | 121.7285 | 0.14648 | 0.064087 | 121.8933 | -0.022889 | 121.9299 | 0.050354 | -121.8521 | -121.8155 | 121.7651 | 0.13733 | 38.8687 | 0.17395
3998.125 | 122.0352 | -0.064087 | 121.8521 | -0.012131 | 0.03879 | 0.066672 | 0.061133 | -0.0013373 | 0.010664 | 0.011717 | -0.005371 | 0.020395 | 0.038149 | -0.015278 | 0.012975 | 0.024819 | -0.0014891 | 38.6673 | 121.8155 | -0.032043 | 121.7194 | 13.5864 | 2.8152 | 2.5955 | 0.10071 | -0.004578 | -0.004578 | 0.064087 | 0.17853 | 0.16479 | 0.13733 | 0.032044 | -0.036621 | -0.13275 | 13.6505 | 2.6596 | 2.8793 | 2.6276 | 2.8473 | 0.059509 | -121.8567 | -121.788 | 0.24261 | 0.20142 | 0.22888 | 0.14191 | 0.16937 | 13.6185 | 121.7514 | 0.18311 | 0.068665 | 121.8475 | 0 | 121.8796 | 0.059509 | -121.8842 | -121.8567 | 121.7834 | 0.12817 | 38.7314 | 0.1648
3999.9062 | 121.9299 | -0.09613 | 121.8842 | -0.012131 | 0.045626 | 0.069449 | 0.065619 | 0.0018671 | 0.0083142 | 0.014281 | -0.005371 | 0.022317 | 0.040712 | -0.011647 | 0.015752 | 0.023323 | -0.0055479 | 38.7039 | 121.9025 | -0.082397 | 121.5912 | 13.4354 | 2.5955 | 2.5726 | -0.050354 | 0.027466 | -0.050354 | -0.045776 | -0.004578 | -0.004578 | 0.041199 | 0.013733 | 0.018311 | -0.29297 | 13.5315 | 2.6688 | 2.6917 | 2.655 | 2.6779 | 0.045776 | -121.8567 | -121.9299 | 0.091552 | 0.13733 | 0.091552 | 0.091553 | 0.045776 | 13.5178 | 121.6736 | 0.045776 | 0.004578 | 121.9849 | 0.07782 | 121.9986 | 0.1236 | -121.9666 | -121.9345 | 121.6873 | 0.050354 | 38.8 | 0.045776
4001.6094 | 121.9116 | -0.10529 | 121.9116 | -0.012131 | 0.045412 | 0.068808 | 0.064551 | 0.0025079 | 0.0089552 | 0.018126 | -0.0023192 | 0.022531 | 0.040926 | -0.019337 | 0.015325 | 0.022896 | -0.0036253 | 38.7177 | 121.8979 | -0.091553 | 121.5729 | 13.6276 | 2.7512 | 2.5497 | -0.059509 | 0.032043 | -0.041199 | -0.059509 | 0.018311 | -0.018311 | 0.036621 | 0.013733 | -0.013733 | -0.33875 | 13.7329 | 2.655 | 2.8564 | 2.6413 | 2.8427 | 0.064087 | -121.8796 | -121.9711 | 0.1236 | 0.14191 | 0.086975 | 0.07782 | 0.022888 | 13.7192 | 121.6644 | 0.05951 | -0.01831 | 121.9894 | 0.073242 | 122.0032 | 0.13733 | -122.0032 | -121.9528 | 121.6782 | 0.045777 | 38.8229 | 0.045777
4003.3594 | 122.0169 | -0.059509 | 121.8521 | -0.01976 | 0.045198 | 0.070303 | 0.061987 | 0.0046441 | 0.010023 | 0.014708 | -0.011475 | 0.019754 | 0.040499 | -0.01186 | 0.015752 | 0.0261 | -0.0038389 | 38.8092 | 121.8613 | -0.027466 | 121.701 | 13.884 | 2.9434 | 2.71 | 0.09613 | -0.032043 | -0.018311 | 0.059509 | 0.14648 | 0.12817 | 0.12817 | 0.032043 | 0.009155 | -0.15106 | 13.9435 | 2.7695 | 3.0029 | 2.7374 | 2.9709 | 0.041198 | -121.8842 | -121.7926 | 0.20599 | 0.18768 | 0.18768 | 0.14649 | 0.14649 | 13.9114 | 121.7285 | 0.16479 | 0.07782 | 121.8887 | -0.013732 | 121.9208 | 0.027466 | -121.8796 | -121.8704 | 121.7606 | 0.11902 | 38.8687 | 0.15564
4005.0781 | 121.9391 | -0.091553 | 121.907 | -0.012131 | 0.042208 | 0.065604 | 0.061346 | -0.0019781 | 0.0093824 | 0.014067 | -0.0084228 | 0.01954 | 0.040712 | -0.011433 | 0.015112 | 0.022683 | -0.0031979 | 38.9191 | 121.8384 | -0.059509 | 121.6827 | 13.8611 | 2.9938 | 2.623 | 0.032043 | -0.004578 | -0.027466 | -0.032043 | 0.09613 | 0.045776 | 0.054932 | 0.032044 | -0.068664 | -0.2243 | 13.9526 | 2.7145 | 3.0853 | 2.6825 | 3.0533 | 0.064087 | -121.9116 | -121.9391 | 0.18768 | 0.14649 | 0.13733 | 0.082398 | 0.073242 | 13.9206 | 121.7422 | 0.1236 | -0.004577 | 121.8979 | 0.022888 | 121.9299 | 0.086975 | -121.9666 | -121.9345 | 121.7743 | 0.05951 | 39.0106 | 0.1236
4006.8594 | 122.0032 | -0.073242 | 121.8842 | -0.01976 | 0.042849 | 0.069876 | 0.063482 | 0.00079894 | 0.010237 | 0.017912 | -0.005371 | 0.01954 | 0.040071 | -0.016347 | 0.014471 | 0.024391 | -0.0046933 | 38.8824 | 121.8658 | -0.041199 | 121.6873 | 14.0945 | 3.0029 | 2.7924 | 0.073242 | -0.009155 | -0.022888 | 0.022888 | 0.10529 | 0.10529 | 0.10071 | 0.032043 | -0.01831 | -0.19684 | 14.1678 | 2.8656 | 3.0762 | 2.8336 | 3.0441 | 0.050354 | -121.8933 | -121.8613 | 0.17853 | 0.17395 | 0.17853 | 0.1236 | 0.12817 | 14.1357 | 121.7285 | 0.12817 | 0.045776 | 121.907 | 0.013733 | 121.9391 | 0.064087 | -121.9254 | -121.907 | 121.7606 | 0.09613 | 38.9557 | 0.14648
4008.625 | 121.9666 | -0.09613 | 121.9116 | -0.012131 | 0.044558 | 0.06774 | 0.064764 | 0.0040033 | 0.0089552 | 0.017271 | -0.005371 | 0.022317 | 0.040071 | -0.016133 | 0.015112 | 0.022896 | 0.0010745 | 38.9877 | 121.8887 | -0.091553 | 121.6553 | 14.0854 | 2.8198 | 2.6871 | 0.009155 | 0.009155 | -0.022888 | -0.004578 | 0.082397 | 0.064087 | 0.073242 | 0.004577 | -0.022888 | -0.25635 | 14.1815 | 2.7832 | 2.916 | 2.7786 | 2.9114 | 0.073242 | -121.9025 | -121.9162 | 0.17853 | 0.16937 | 0.16022 | 0.09613 | 0.086975 | 14.1769 | 121.7468 | 0.10528 | 0.01831 | 121.9803 | 0.032043 | 121.9849 | 0.10528 | -122.0032 | -121.9345 | 121.7514 | 0.091552 | 39.0839 | 0.10528
4010.3281 | 121.9803 | -0.082397 | 121.9162 | -0.012131 | 0.044771 | 0.071158 | 0.063055 | 0.00079894 | 0.0093824 | 0.014067 | -0.005371 | 0.023385 | 0.039858 | -0.017842 | 0.01618 | 0.025673 | -0.00084805 | 39.0427 | 121.9025 | -0.07782 | 121.637 | 14.3646 | 2.9617 | 2.7283 | 0.022888 | -0.009155 | -0.022888 | 0 | 0.10529 | 0.064087 | 0.073242 | 0.004577 | -0.013733 | -0.27924 | 14.447 | 2.8107 | 3.0441 | 2.8061 | 3.0396 | 0.059509 | -121.9254 | -121.9162 | 0.18768 | 0.15564 | 0.14648 | 0.09613 | 0.086975 | 14.4424 | 121.7148 | 0.12817 | 0.022888 | 121.9803 | 0.013733 | 121.9849 | 0.073242 | -121.994 | -121.9391 | 121.7194 | 0.082397 | 39.1251 | 0.10528
4012.0938 | 122.0078 | -0.068665 | 121.8979 | -0.012131 | 0.047975 | 0.069449 | 0.066687 | 0.0035761 | 0.010237 | 0.017912 | -0.0084228 | 0.02189 | 0.040712 | -0.014424 | 0.015966 | 0.022896 | -0.00042085 | 38.9694 | 121.9116 | -0.082397 | 121.6232 | 14.5157 | 3.0304 | 2.8427 | 0 | 0 | -0.027466 | 0.018311 | 0.09613 | 0.050354 | 0.10071 | -0.013732 | 0.013733 | -0.27466 | 14.5844 | 2.9114 | 3.0991 | 2.9251 | 3.1128 | 0.041199 | -121.8979 | -121.8796 | 0.16479 | 0.16937 | 0.11902 | 0.12817 | 0.07782 | 14.5981 | 121.7056 | 0.1236 | 0.045777 | 121.994 | 0.027466 | 121.9803 | 0.068665 | -121.9803 | -121.9254 | 121.6919 | 0.086976 | 39.0381 | 0.068665
4013.8594 | 122.0123 | -0.059509 | 121.8979 | -0.01976 | 0.045412 | 0.070517 | 0.062628 | -0.0017645 | 0.011732 | 0.01364 | -0.0023192 | 0.019113 | 0.043276 | -0.020619 | 0.014684 | 0.025887 | -0.0023435 | 39.0244 | 121.8842 | -0.045776 | 121.6965 | 14.5981 | 3.0167 | 2.7649 | 0.068665 | 0 | -0.009155 | 0.009155 | 0.12817 | 0.086975 | 0.10529 | 0.013733 | -0.013733 | -0.20142 | 14.6576 | 2.8244 | 3.0762 | 2.8107 | 3.0624 | 0.050354 | -121.8979 | -121.8887 | 0.18768 | 0.16479 | 0.14648 | 0.11444 | 0.09613 | 14.6439 | 121.7422 | 0.13733 | 0.01831 | 121.9299 | 0.009155 | 121.9437 | 0.059509 | -121.9437 | -121.907 | 121.756 | 0.068664 | 39.0839 | 0.12817
4015.5625 | 122.0352 | -0.068665 | 121.9025 | -0.01976 | 0.046694 | 0.069876 | 0.064978 | -0.0013373 | 0.012373 | 0.016203 | -0.005371 | 0.01954 | 0.040499 | -0.01656 | 0.012975 | 0.023751 | -0.0021299 | 39.1159 | 121.8933 | -0.073242 | 121.6827 | 14.6759 | 3.0579 | 2.8107 | 0.027466 | -0.013733 | -0.027466 | 0.013733 | 0.1236 | 0.09613 | 0.10529 | -0.004577 | -0.009155 | -0.21973 | 14.7446 | 2.8793 | 3.1265 | 2.8839 | 3.1311 | 0.041199 | -121.9162 | -121.8887 | 0.19226 | 0.17395 | 0.16479 | 0.13275 | 0.1236 | 14.7491 | 121.756 | 0.15106 | 0.041199 | 121.9666 | 0.013733 | 121.962 | 0.054932 | -121.9757 | -121.9299 | 121.7514 | 0.082398 | 39.1846 | 0.096131
4017.3281 | 121.9849 | -0.10986 | 121.907 | -0.0045011 | 0.044344 | 0.069876 | 0.066473 | 0.0020807 | 0.009596 | 0.015562 | -0.005371 | 0.023172 | 0.037508 | -0.0063061 | 0.014684 | 0.024178 | -0.0038389 | 39.1983 | 121.9254 | -0.082397 | 121.6141 | 14.4608 | 3.0533 | 2.8381 | -0.059509 | 0.022888 | -0.050354 | -0.050354 | 0.050354 | 0.032043 | 0.054932 | 0.027466 | 0.018311 | -0.29297 | 14.5706 | 2.948 | 3.1631 | 2.9205 | 3.1357 | 0.059509 | -121.8842 | -121.9574 | 0.16022 | 0.16479 | 0.14191 | 0.10529 | 0.082397 | 14.5432 | 121.6965 | 0.10071 | 0 | 122.0078 | 0.073242 | 122.0352 | 0.13275 | -121.9894 | -121.9574 | 121.7239 | 0.059509 | 39.3082 | 0.050354
4019.0938 | 122.0306 | -0.068665 | 121.9025 | -0.01976 | 0.047335 | 0.072226 | 0.064551 | 0.0035761 | 0.011305 | 0.018553 | -0.005371 | 0.018258 | 0.041567 | -0.021473 | 0.014898 | 0.023323 | -0.0038389 | 39.3631 | 121.8704 | -0.064087 | 121.7102 | 14.9689 | 3.1723 | 3.0075 | 0.10071 | -0.009155 | -0.013733 | 0.036621 | 0.13275 | 0.10071 | 0.10986 | 0.004578 | -0.032044 | -0.19226 | 15.0375 | 3.0762 | 3.241 | 3.0716 | 3.2364 | 0.054932 | -121.9116 | -121.8658 | 0.20142 | 0.17853 | 0.16937 | 0.1236 | 0.11444 | 15.033 | 121.7743 | 0.14648 | 0.050354 | 121.9345 | 0.004578 | 121.9391 | 0.05951 | -121.9666 | -121.9162 | 121.7789 | 0.10529 | 39.4318 | 0.16937
4020.8125 | 122.0306 | -0.086975 | 121.9162 | -0.012131 | 0.046266 | 0.070731 | 0.064123 | -0.0011237 | 0.010023 | 0.017271 | -0.0084228 | 0.019754 | 0.040499 | -0.014851 | 0.014471 | 0.022896 | -0.0040525 | 39.4409 | 121.9025 | -0.054932 | 121.6873 | 15.0284 | 3.186 | 2.829 | 0.022888 | -0.009155 | -0.009155 | 0 | 0.10071 | 0.086975 | 0.091553 | 0.032043 | -0.013733 | -0.22888 | 15.1154 | 2.916 | 3.273 | 2.8839 | 3.241 | 0.07782 | -121.9254 | -121.9162 | 0.18768 | 0.17853 | 0.17395 | 0.10071 | 0.09613 | 15.0833 | 121.7422 | 0.10986 | 0.009155 | 121.9574 | 0 | 121.9894 | 0.07782 | -121.9711 | -121.9254 | 121.7743 | 0.086975 | 39.5279 | 0.10986
4022.5781 | 121.9986 | -0.091553 | 121.9254 | -0.012131 | 0.049471 | 0.071371 | 0.070105 | 0.0018671 | 0.012159 | 0.01898 | 0.00073235 | 0.021249 | 0.040285 | -0.016774 | 0.015752 | 0.023537 | -0.0023435 | 39.3768 | 121.9574 | -0.073242 | 121.637 | 15.3214 | 3.1128 | 2.7649 | -0.013733 | 0.009155 | -0.045776 | -0.009155 | 0.064087 | 0.045776 | 0.068665 | 0.018311 | 0.032043 | -0.28839 | 15.4129 | 2.8564 | 3.2043 | 2.8381 | 3.186 | 0.045777 | -121.9162 | -121.9345 | 0.15564 | 0.16022 | 0.13733 | 0.11444 | 0.091552 | 15.3946 | 121.7102 | 0.10986 | 0.036621 | 122.0306 | 0.054931 | 122.049 | 0.10071 | -121.9986 | -121.9711 | 121.7285 | 0.082398 | 39.4684 | 0.07782
4024.3438 | 121.9849 | -0.10071 | 121.9437 | -0.0045011 | 0.047548 | 0.070303 | 0.064978 | 0.0014397 | 0.012159 | 0.020476 | -0.0084228 | 0.022958 | 0.040499 | -0.013997 | 0.012975 | 0.022896 | -0.0083249 | 39.5737 | 121.9345 | -0.082397 | 121.6278 | 15.5136 | 3.0716 | 2.8244 | -0.068665 | 0.022888 | -0.050354 | -0.054932 | 0.059509 | 0.032043 | 0.054932 | 0.018311 | -0.009156 | -0.31586 | 15.6143 | 2.9251 | 3.1723 | 2.9068 | 3.154 | 0.050354 | -121.9208 | -121.9986 | 0.16022 | 0.15564 | 0.13275 | 0.10529 | 0.082397 | 15.596 | 121.7102 | 0.10986 | -0.004578 | 122.0169 | 0.073242 | 122.0352 | 0.1236 | -122.0261 | -121.994 | 121.7285 | 0.045776 | 39.6744 | 0.032043
4026.0625 | 121.9986 | -0.082397 | 121.907 | -0.012131 | 0.050325 | 0.072226 | 0.066046 | 0.0012261 | 0.011519 | 0.01834 | -0.0084228 | 0.02189 | 0.041353 | -0.015065 | 0.017461 | 0.024178 | -0.0042661 | 39.8117 | 121.9208 | -0.054932 | 121.6827 | 15.5914 | 3.2547 | 2.9388 | 0.041199 | 0.009155 | -0.036621 | -0.004578 | 0.09613 | 0.064087 | 0.086975 | 0.027465 | 0.013733 | -0.2243 | 15.6738 | 3.0212 | 3.3371 | 2.9938 | 3.3096 | 0.045776 | -121.8979 | -121.9116 | 0.17853 | 0.16937 | 0.14648 | 0.1236 | 0.10071 | 15.6464 | 121.7377 | 0.13275 | 0.032043 | 121.9757 | 0.045776 | 122.0032 | 0.091552 | -121.962 | -121.9437 | 121.7651 | 0.077819 | 39.8941 | 0.1236
4027.8438 | 122.0032 | -0.09613 | 121.9482 | -0.0045011 | 0.049257 | 0.072653 | 0.066687 | -0.0019781 | 0.011305 | 0.017058 | -0.005371 | 0.020181 | 0.039217 | -0.011006 | 0.014043 | 0.023537 | -0.0040525 | 39.917 | 121.9299 | -0.07782 | 121.637 | 15.683 | 3.0396 | 2.9892 | -0.032043 | 0.018311 | -0.041199 | -0.022888 | 0.082397 | 0.054932 | 0.068665 | 0.01831 | -0.01831 | -0.31128 | 15.7791 | 3.0853 | 3.1357 | 3.067 | 3.1174 | 0.054931 | -121.9299 | -121.9711 | 0.17853 | 0.16479 | 0.15106 | 0.10986 | 0.096131 | 15.7608 | 121.7148 | 0.1236 | 0.018311 | 122.0078 | 0.05951 | 122.0261 | 0.11444 | -122.0261 | -121.9894 | 121.7331 | 0.073242 | 40.0131 | 0.064087
4029.5625 | 121.9711 | -0.10986 | 121.9299 | -0.0045011 | 0.046694 | 0.069235 | 0.062628 | -0.00091006 | 0.012159 | 0.017058 | -0.005371 | 0.01954 | 0.041567 | -0.019764 | 0.012334 | 0.024391 | 0.00021995 | 39.9582 | 121.8842 | -0.073242 | 121.6324 | 15.6281 | 3.1219 | 3.1082 | -0.036621 | 0.013733 | -0.036621 | -0.07782 | 0.050354 | 0.013733 | 0.018311 | 0.036621 | -0.045777 | -0.29755 | 15.7379 | 3.2181 | 3.2318 | 3.1815 | 3.1952 | 0.073242 | -121.9162 | -122.0078 | 0.16022 | 0.12817 | 0.1236 | 0.054932 | 0.050354 | 15.7013 | 121.7056 | 0.086975 | -0.041199 | 121.9574 | 0.050354 | 121.994 | 0.1236 | -122.0032 | -121.9666 | 121.7422 | 0.032043 | 40.0681 | 0.073242
4031.3438 | 121.9666 | -0.11444 | 121.9482 | -0.0045011 | 0.046694 | 0.072867 | 0.062842 | -0.0032599 | 0.013228 | 0.01834 | -0.0023192 | 0.021463 | 0.042421 | -0.019337 | 0.014043 | 0.025246 | -0.0038389 | 39.9719 | 121.9162 | -0.07782 | 121.6049 | 16.0355 | 3.2867 | 3.0853 | -0.059509 | 0.022888 | -0.064087 | -0.059509 | 0.054932 | 0.018311 | 0.050354 | 0.036621 | -0.032043 | -0.34332 | 16.1499 | 3.1998 | 3.4012 | 3.1631 | 3.3646 | 0.050354 | -121.9254 | -122.0078 | 0.16937 | 0.16479 | 0.13275 | 0.11444 | 0.082398 | 16.1133 | 121.6827 | 0.11902 | 0.004578 | 121.994 | 0.086975 | 122.0306 | 0.13733 | -122.0261 | -122.0123 | 121.7194 | 0.054932 | 40.0864 | 0.054932
4033.125 | 122.0901 | -0.064087 | 121.8887 | 0.010757 | 0.046907 | 0.072012 | 0.063055 | -0.00091006 | 0.014296 | 0.018553 | -0.005371 | 0.020608 | 0.039217 | -0.023823 | 0.014043 | 0.024819 | -0.0012753 | 40.242 | 121.8658 | -0.036621 | 121.7606 | 16.3559 | 3.2501 | 3.1174 | 0.12817 | -0.022888 | 0.004578 | 0.050354 | 0.1831 | 0.16937 | 0.14191 | 0.027466 | -0.022888 | -0.12817 | 16.42 | 3.1815 | 3.3142 | 3.154 | 3.2867 | 0.068665 | -121.9116 | -121.8384 | 0.24719 | 0.20599 | 0.23346 | 0.13733 | 0.16479 | 16.3925 | 121.7972 | 0.17853 | 0.045776 | 121.9025 | -0.027466 | 121.9299 | 0.041199 | -121.9254 | -121.8842 | 121.8246 | 0.11444 | 40.3061 | 0.19226
4034.8438 | 122.0947 | -0.036621 | 121.9116 | -0.0045011 | 0.048403 | 0.073935 | 0.062414 | 0.0035761 | 0.012587 | 0.019194 | -0.0023192 | 0.018045 | 0.039644 | -0.019978 | 0.012975 | 0.025032 | -0.0031979 | 40.329 | 121.8521 | -0.054932 | 121.7697 | 16.6534 | 3.4607 | 3.0899 | 0.13275 | -0.022888 | 0 | 0.064087 | 0.20599 | 0.15564 | 0.13275 | -0.018311 | -0.059509 | -0.14191 | 16.6901 | 3.1265 | 3.4973 | 3.1448 | 3.5156 | 0.036621 | -121.9345 | -121.8475 | 0.24262 | 0.16937 | 0.19226 | 0.13275 | 0.15564 | 16.7084 | 121.8246 | 0.20599 | 0.064087 | 121.907 | -0.022888 | 121.8887 | 0.013733 | -121.9666 | -121.9116 | 121.8063 | 0.10071 | 40.3656 | 0.16937
4036.625 | 122.0535 | -0.054932 | 121.9162 | -0.02739 | 0.049684 | 0.070944 | 0.063482 | 0.0042169 | 0.012159 | 0.019194 | -0.005371 | 0.019754 | 0.039431 | -0.015278 | 0.011694 | 0.025246 | -0.0027707 | 40.4663 | 121.8796 | -0.073242 | 121.6965 | 16.6168 | 3.3096 | 3.0579 | 0.045776 | -0.009155 | -0.027466 | 0.022888 | 0.13733 | 0.10986 | 0.1236 | -0.01831 | -0.036621 | -0.21973 | 16.6718 | 3.1128 | 3.3646 | 3.1311 | 3.3829 | 0.027466 | -121.9254 | -121.8933 | 0.19226 | 0.17853 | 0.16479 | 0.15106 | 0.13733 | 16.6901 | 121.7697 | 0.16479 | 0.050354 | 121.9528 | 0.018311 | 121.9345 | 0.045777 | -121.9894 | -121.9437 | 121.7514 | 0.07782 | 40.5212 | 0.10071
4038.3281 | 122.081 | -0.050354 | 121.9025 | -0.01976 | 0.056093 | 0.073935 | 0.065619 | 0.0016535 | 0.015364 | 0.018553 | 0.00073235 | 0.02424 | 0.040926 | -0.014851 | 0.014898 | 0.023751 | -0.0055479 | 40.6723 | 121.9025 | -0.022888 | 121.7697 | 16.7908 | 3.3096 | 3.3371 | 0.10986 | -0.013733 | -0.027466 | 0.073242 | 0.16479 | 0.15106 | 0.12817 | 0.027466 | 0 | -0.13275 | 16.8411 | 3.3875 | 3.36 | 3.36 | 3.3325 | 0.022888 | -121.9162 | -121.8292 | 0.21515 | 0.17853 | 0.20142 | 0.15564 | 0.17853 | 16.8137 | 121.7926 | 0.19226 | 0.10071 | 121.9254 | 0.013733 | 121.9528 | 0.036621 | -121.9254 | -121.9299 | 121.8201 | 0.1236 | 40.7227 | 0.16022
4040.0938 | 121.9528 | -0.11444 | 121.9345 | -0.012131 | 0.053957 | 0.074789 | 0.068182 | -0.0015509 | 0.011732 | 0.020262 | -0.0084228 | 0.024667 | 0.039858 | -0.0086559 | 0.017034 | 0.021614 | -0.0034117 | 40.6494 | 121.9162 | -0.086975 | 121.6553 | 16.983 | 3.2776 | 3.0167 | -0.027466 | 0.004578 | -0.036621 | -0.059509 | 0.032043 | -0.004578 | 0.032043 | 0.027466 | -0.01831 | -0.27924 | 17.0975 | 3.1311 | 3.392 | 3.1036 | 3.3646 | 0.07782 | -121.9299 | -121.994 | 0.14648 | 0.14648 | 0.10986 | 0.068664 | 0.032043 | 17.07 | 121.7422 | 0.068664 | -0.022888 | 122.0032 | 0.041199 | 122.0306 | 0.11902 | -122.0215 | -121.9711 | 121.7697 | 0.054932 | 40.7639 | 0.086975
4041.875 | 122.0444 | -0.054932 | 121.8979 | -0.012131 | 0.052248 | 0.073935 | 0.065405 | -0.00091006 | 0.013441 | 0.020689 | -0.005371 | 0.020181 | 0.040712 | -0.015706 | 0.012121 | 0.024178 | -0.0031979 | 40.8508 | 121.8979 | -0.032043 | 121.7422 | 17.4454 | 3.511 | 3.3051 | 0.10071 | -0.018311 | 0 | 0.059509 | 0.15564 | 0.11902 | 0.12817 | 0.022889 | 0 | -0.15564 | 17.5003 | 3.36 | 3.566 | 3.3371 | 3.5431 | 0.054932 | -121.9162 | -121.8384 | 0.21057 | 0.18311 | 0.17395 | 0.12817 | 0.11902 | 17.4774 | 121.7743 | 0.15564 | 0.059509 | 121.9299 | -0.018311 | 121.9528 | 0.036621 | -121.9299 | -121.8979 | 121.7972 | 0.11444 | 40.9058 | 0.15564
4043.625 | 121.962 | -0.10529 | 121.962 | -0.012131 | 0.052675 | 0.074789 | 0.064978 | -0.0034735 | 0.013014 | 0.01834 | -0.005371 | 0.020395 | 0.04178 | -0.012929 | 0.014898 | 0.025246 | -0.0038389 | 40.892 | 121.9345 | -0.10071 | 121.6278 | 17.5095 | 3.273 | 3.035 | -0.054932 | 0.018311 | -0.050354 | -0.073242 | 0.045776 | 0.018311 | 0.036621 | 0.004578 | -0.027466 | -0.33417 | 17.6147 | 3.1403 | 3.3783 | 3.1357 | 3.3737 | 0.054932 | -121.9437 | -122.0352 | 0.15106 | 0.14191 | 0.1236 | 0.086975 | 0.068665 | 17.6102 | 121.7285 | 0.09613 | -0.022888 | 122.0352 | 0.068665 | 122.0398 | 0.1236 | -122.0627 | -122.0123 | 121.7331 | 0.032044 | 40.9973 | 0.050354
4045.3438 | 122.0123 | -0.09613 | 121.9482 | -0.01976 | 0.054598 | 0.075003 | 0.067755 | 0.0042169 | 0.013441 | 0.021117 | -0.005371 | 0.022317 | 0.040712 | -0.018269 | 0.014898 | 0.023964 | -0.0049069 | 41.1026 | 121.9391 | -0.073242 | 121.6873 | 17.514 | 3.4332 | 3.2501 | 0.050354 | 0.004578 | -0.032043 | 0.009155 | 0.10529 | 0.059509 | 0.082397 | 0.022888 | -0.009155 | -0.26093 | 17.6102 | 3.3463 | 3.5294 | 3.3234 | 3.5065 | 0.064087 | -121.9437 | -121.9391 | 0.20142 | 0.17853 | 0.15564 | 0.11444 | 0.091552 | 17.5873 | 121.7606 | 0.13733 | 0.041198 | 122.0123 | 0.036621 | 122.0352 | 0.10071 | -122.0215 | -121.9803 | 121.7834 | 0.10528 | 41.1987 | 0.14648
4047.1094 | 122.0581 | -0.054932 | 121.9162 | -0.01976 | 0.052034 | 0.075217 | 0.064551 | -0.0019781 | 0.016646 | 0.021117 | -0.0023192 | 0.020608 | 0.040285 | -0.016987 | 0.013189 | 0.023964 | -0.0025571 | 41.2811 | 121.907 | -0.032043 | 121.7468 | 17.8116 | 3.566 | 3.4927 | 0.09613 | -0.018311 | -0.004578 | 0.045776 | 0.14191 | 0.11444 | 0.11444 | 0.022889 | -0.009156 | -0.16937 | 17.8665 | 3.5477 | 3.6209 | 3.5248 | 3.598 | 0.050354 | -121.9345 | -121.8704 | 0.19684 | 0.16937 | 0.16937 | 0.11902 | 0.11902 | 17.8436 | 121.7789 | 0.14649 | 0.050354 | 121.9391 | -0.013733 | 121.962 | 0.036621 | -121.9482 | -121.9208 | 121.8018 | 0.10071 | 41.3361 | 0.15106
4048.8125 | 122.0398 | -0.07782 | 121.907 | -0.012131 | 0.056948 | 0.073935 | 0.068823 | 0.00079894 | 0.013228 | 0.018553 | -0.0084228 | 0.021676 | 0.041567 | -0.01656 | 0.015539 | 0.023537 | -0.0038389 | 41.3773 | 121.9437 | -0.07782 | 121.6599 | 17.6056 | 3.3783 | 3.3234 | 0 | 0.009155 | -0.027466 | 0.013733 | 0.091553 | 0.073242 | 0.10529 | 0 | 0.036622 | -0.24719 | 17.6834 | 3.4012 | 3.4561 | 3.4012 | 3.4561 | 0.050354 | -121.8979 | -121.8933 | 0.16937 | 0.18311 | 0.15106 | 0.13275 | 0.10071 | 17.6834 | 121.7377 | 0.11902 | 0.041199 | 122.0215 | 0.036621 | 122.0215 | 0.086975 | -121.9849 | -121.9345 | 121.7377 | 0.091553 | 41.4551 | 0.07782
4050.5781 | 122.049 | -0.059509 | 121.9208 | -0.02739 | 0.056093 | 0.07543 | 0.067328 | 0.0016535 | 0.013441 | 0.019408 | -0.005371 | 0.020395 | 0.039858 | -0.013783 | 0.01383 | 0.024819 | -0.0031979 | 41.5924 | 121.907 | -0.036621 | 121.7331 | 18.1961 | 3.392 | 3.2639 | 0.09613 | -0.018311 | -0.018311 | 0.027466 | 0.11902 | 0.10529 | 0.10071 | 0.022888 | -0.013733 | -0.18768 | 18.2556 | 3.3234 | 3.4515 | 3.3005 | 3.4286 | 0.041198 | -121.9391 | -121.8933 | 0.17853 | 0.16022 | 0.16479 | 0.11902 | 0.1236 | 18.2327 | 121.7697 | 0.13733 | 0.045777 | 121.9437 | 0 | 121.9666 | 0.041198 | -121.9574 | -121.9391 | 121.7926 | 0.086975 | 41.6519 | 0.15564
4052.3594 | 122.0947 | -0.064087 | 121.9025 | -0.01976 | 0.056948 | 0.076712 | 0.06391 | 0.0037897 | 0.01515 | 0.02133 | -0.0084228 | 0.021035 | 0.039644 | -0.018055 | 0.015325 | 0.023537 | 0.00043375 | 41.684 | 121.9116 | -0.041199 | 121.7606 | 18.2693 | 3.6026 | 3.4882 | 0.10986 | -0.022888 | -0.004578 | 0.059509 | 0.17395 | 0.13275 | 0.12817 | 0.022888 | 0.009155 | -0.14191 | 18.3334 | 3.5522 | 3.6667 | 3.5294 | 3.6438 | 0.059509 | -121.9254 | -121.843 | 0.23804 | 0.19226 | 0.19684 | 0.13275 | 0.13733 | 18.3105 | 121.8018 | 0.17853 | 0.064087 | 121.9528 | -0.01831 | 121.9757 | 0.041199 | -121.9437 | -121.907 | 121.8246 | 0.1236 | 41.748 | 0.17395
4054.0625 | 122.0718 | -0.068665 | 121.907 | -0.01976 | 0.05588 | 0.075858 | 0.0669 | 0.0020807 | 0.014509 | 0.020049 | -0.005371 | 0.019754 | 0.039644 | -0.015065 | 0.011694 | 0.023537 | -0.0031979 | 42.0136 | 121.8842 | -0.032043 | 121.7651 | 18.4067 | 3.479 | 3.4927 | 0.11444 | -0.027466 | 0.009155 | 0.064087 | 0.14648 | 0.13733 | 0.12817 | 0.036622 | -0.022888 | -0.14191 | 18.4753 | 3.5614 | 3.5477 | 3.5248 | 3.511 | 0.07782 | -121.9345 | -121.843 | 0.21515 | 0.19684 | 0.20599 | 0.11902 | 0.12817 | 18.4387 | 121.7972 | 0.13733 | 0.054932 | 121.9162 | -0.036621 | 121.9528 | 0.041199 | -121.9391 | -121.8979 | 121.8338 | 0.13275 | 42.0822 | 0.18311
4055.8438 | 122.0398 | -0.07782 | 121.9254 | -0.012131 | 0.055452 | 0.075003 | 0.064551 | -0.0019781 | 0.013655 | 0.018767 | -0.005371 | 0.021676 | 0.036226 | -0.011647 | 0.013189 | 0.025246 | -0.0036253 | 42.0868 | 121.9025 | -0.041199 | 121.7148 | 18.6676 | 3.5202 | 3.5477 | 0.050354 | -0.009155 | -0.022888 | 0.009155 | 0.11902 | 0.082397 | 0.10071 | 0.036621 | -0.022888 | -0.21057 | 18.7454 | 3.6255 | 3.598 | 3.5889 | 3.5614 | 0.054932 | -121.9345 | -121.9162 | 0.19684 | 0.17853 | 0.16022 | 0.1236 | 0.10528 | 18.7088 | 121.756 | 0.14191 | 0.032043 | 121.9437 | 0.013733 | 121.9803 | 0.068665 | -121.9666 | -121.9482 | 121.7926 | 0.086975 | 42.1646 | 0.12817
4057.5625 | 122.0398 | -0.07782 | 121.9391 | -0.0045011 | 0.057802 | 0.074576 | 0.065405 | 0.0014397 | 0.014509 | 0.020476 | -0.0084228 | 0.021035 | 0.041353 | -0.013569 | 0.013616 | 0.02311 | -0.0040525 | 42.1921 | 121.907 | -0.045776 | 121.7102 | 18.7088 | 3.5797 | 3.4287 | 0.018311 | -0.004578 | -0.018311 | -0.009155 | 0.10071 | 0.091553 | 0.09613 | 0.032044 | -0.032044 | -0.22888 | 18.7866 | 3.5065 | 3.6575 | 3.4744 | 3.6255 | 0.059509 | -121.9437 | -121.9482 | 0.17853 | 0.17395 | 0.16937 | 0.11444 | 0.10986 | 18.7546 | 121.756 | 0.11902 | 0.009156 | 121.9528 | 0.013733 | 121.9849 | 0.073242 | -121.9849 | -121.9574 | 121.788 | 0.068665 | 42.2699 | 0.096131
4059.3281 | 122.1085 | -0.068665 | 121.9025 | -0.012131 | 0.054811 | 0.075003 | 0.065405 | -0.0017645 | 0.015791 | 0.018126 | -0.0084228 | 0.020608 | 0.039003 | -0.011433 | 0.014257 | 0.022683 | -0.0051205 | 42.5491 | 121.8842 | -0.054932 | 121.7926 | 18.8873 | 3.7445 | 3.5522 | 0.1236 | -0.032043 | -0.004578 | 0.064087 | 0.20142 | 0.17395 | 0.1236 | 0.013733 | -0.018311 | -0.10986 | 18.956 | 3.6209 | 3.8132 | 3.6072 | 3.7994 | 0.064087 | -121.9345 | -121.8384 | 0.27008 | 0.19226 | 0.24261 | 0.12817 | 0.17853 | 18.9423 | 121.8475 | 0.20599 | 0.068665 | 121.9391 | -0.027465 | 121.9528 | 0.036622 | -121.9574 | -121.907 | 121.8613 | 0.13275 | 42.6178 | 0.19226
4061.1094 | 121.9711 | -0.10071 | 121.9299 | -0.012131 | 0.060152 | 0.079276 | 0.067541 | 0.0018671 | 0.017714 | 0.021544 | -0.005371 | 0.02424 | 0.041994 | -0.0084423 | 0.014471 | 0.023323 | -0.00020725 | 42.6361 | 121.9528 | -0.082397 | 121.6324 | 19.0338 | 3.5294 | 3.2455 | -0.09613 | 0.009155 | -0.041199 | -0.050354 | -0.004578 | -0.027466 | 0.041199 | 0.018311 | 0.022888 | -0.29755 | 19.1345 | 3.3463 | 3.6301 | 3.3279 | 3.6118 | 0.059509 | -121.9208 | -121.9803 | 0.09613 | 0.14191 | 0.073242 | 0.082398 | 0.013733 | 19.1162 | 121.7148 | 0.036621 | -0.009155 | 122.0352 | 0.050354 | 122.0535 | 0.10986 | -122.0123 | -121.9711 | 121.7331 | 0.050354 | 42.7368 | 0.004578
4062.875 | 121.9666 | -0.10529 | 121.9711 | -0.012131 | 0.058016 | 0.075644 | 0.064337 | -0.0015509 | 0.013014 | 0.02133 | -0.0084228 | 0.023172 | 0.041567 | -0.010151 | 0.01618 | 0.023323 | -0.0017027 | 42.6132 | 121.9299 | -0.09613 | 121.6461 | 19.3268 | 3.5248 | 3.5706 | -0.068665 | 0.027466 | -0.027466 | -0.086975 | 0.041199 | 0.022888 | 0.032043 | 0.009156 | -0.041198 | -0.32501 | 19.4321 | 3.6758 | 3.6301 | 3.6667 | 3.6209 | 0.07782 | -121.9437 | -122.0581 | 0.14649 | 0.13733 | 0.12817 | 0.059509 | 0.050354 | 19.4229 | 121.7422 | 0.068665 | -0.059509 | 122.0261 | 0.054932 | 122.0352 | 0.13275 | -122.0673 | -121.9986 | 121.7514 | 0.018311 | 42.7185 | 0.036621
4064.5781 | 121.962 | -0.091553 | 121.9711 | -0.02739 | 0.059938 | 0.075217 | 0.066687 | 0.0035761 | 0.016646 | 0.024107 | -0.0023192 | 0.022317 | 0.039003 | -0.013997 | 0.016607 | 0.023964 | -0.0034117 | 42.8329 | 121.9299 | -0.07782 | 121.6599 | 19.0338 | 3.4927 | 3.4607 | -0.068665 | 0.032043 | -0.041199 | -0.064087 | 0.018311 | -0.022888 | 0.032043 | 0.013733 | -0.041198 | -0.31128 | 19.1254 | 3.5522 | 3.5843 | 3.5385 | 3.5706 | 0.050354 | -121.9391 | -122.0352 | 0.10986 | 0.1236 | 0.068665 | 0.073242 | 0.018311 | 19.1116 | 121.7377 | 0.05951 | -0.022888 | 122.0078 | 0.073242 | 122.0215 | 0.1236 | -122.049 | -122.0123 | 121.7514 | 0.027466 | 42.9245 | 0.022888
4066.3438 | 122.0444 | -0.082397 | 121.9482 | -0.0045011 | 0.059938 | 0.077567 | 0.068823 | 0.0029351 | 0.016859 | 0.024107 | -0.0023192 | 0.023172 | 0.040499 | -0.0092969 | 0.016393 | 0.02546 | -0.0059751 | 43.1122 | 121.9437 | -0.059509 | 121.6919 | 19.4595 | 3.6301 | 3.5706 | 0.018311 | 0.004578 | -0.036621 | 0.009155 | 0.10071 | 0.07782 | 0.082397 | 0.022888 | -0.004577 | -0.25635 | 19.5419 | 3.653 | 3.7125 | 3.6301 | 3.6896 | 0.045776 | -121.9437 | -121.9391 | 0.18311 | 0.16479 | 0.16022 | 0.11902 | 0.11444 | 19.519 | 121.7514 | 0.13733 | 0.045776 | 122.0032 | 0.041199 | 122.0261 | 0.086975 | -122.0078 | -121.9849 | 121.7743 | 0.091552 | 43.1946 | 0.10071
4068.0469 | 122.0215 | -0.07782 | 121.9666 | -0.012131 | 0.061861 | 0.077353 | 0.066687 | 0.0037897 | 0.01515 | 0.021971 | -0.005371 | 0.022317 | 0.040285 | -0.011647 | 0.016607 | 0.024391 | -0.0025571 | 43.3502 | 121.9528 | -0.064087 | 121.6965 | 19.7388 | 3.685 | 3.6346 | 0.036621 | 0 | -0.018311 | -0.009155 | 0.086975 | 0.059509 | 0.068665 | 0.013733 | -0.013733 | -0.27008 | 19.8166 | 3.7125 | 3.7628 | 3.6987 | 3.7491 | 0.059509 | -121.9666 | -121.9757 | 0.16479 | 0.14649 | 0.13733 | 0.086976 | 0.07782 | 19.8029 | 121.7606 | 0.10529 | 0.009156 | 122.0169 | 0.018311 | 122.0306 | 0.07782 | -122.0306 | -121.9849 | 121.7743 | 0.068665 | 43.428 | 0.11444
4069.8125 | 121.9803 | -0.10529 | 121.9666 | -0.02739 | 0.062929 | 0.07778 | 0.067328 | -0.0013373 | 0.018141 | 0.020262 | -0.0023192 | 0.022317 | 0.04178 | -0.017628 | 0.015539 | 0.0261 | -0.0010617 | 43.4006 | 121.9482 | -0.091553 | 121.6278 | 19.8074 | 3.7033 | 3.6667 | -0.086975 | 0.032043 | -0.036621 | -0.050354 | 0.009155 | -0.018311 | 0.041199 | 0.013733 | -0.018311 | -0.33875 | 19.9127 | 3.772 | 3.8086 | 3.7582 | 3.7949 | 0.068665 | -121.9345 | -122.0169 | 0.11444 | 0.14649 | 0.086975 | 0.07782 | 0.01831 | 19.899 | 121.7194 | 0.045776 | -0.013733 | 122.0398 | 0.068664 | 122.0535 | 0.13733 | -122.0581 | -122.0032 | 121.7331 | 0.054932 | 43.5059 | 0.018311
4071.5781 | 121.9803 | -0.10986 | 121.9711 | -0.01976 | 0.064211 | 0.078848 | 0.064978 | -0.0039007 | 0.019423 | 0.025175 | -0.005371 | 0.020822 | 0.040499 | -0.0099377 | 0.015752 | 0.0261 | -0.0061887 | 43.3777 | 121.9345 | -0.064087 | 121.6736 | 19.9997 | 3.6484 | 3.6026 | -0.018311 | 0.013733 | -0.045776 | -0.054932 | 0.036621 | 0.004578 | 0.045776 | 0.045776 | -0.036621 | -0.29755 | 20.1096 | 3.7125 | 3.7582 | 3.6667 | 3.7125 | 0.064087 | -121.9574 | -122.0261 | 0.14648 | 0.15564 | 0.11444 | 0.091552 | 0.050354 | 20.0638 | 121.7377 | 0.082397 | -0.009156 | 121.9986 | 0.059509 | 122.0444 | 0.1236 | -122.0352 | -122.0169 | 121.7834 | 0.054931 | 43.4875 | 0.091552
4073.2812 | 122.0901 | -0.036621 | 121.9162 | -0.02739 | 0.059725 | 0.075217 | 0.064123 | 0.0031487 | 0.015791 | 0.021758 | -0.005371 | 0.019754 | 0.040712 | -0.010151 | 0.014684 | 0.024605 | -0.0025571 | 43.19 | 121.8887 | -0.045776 | 121.7697 | 20.3568 | 3.891 | 3.8361 | 0.12817 | -0.013733 | -0.009155 | 0.050354 | 0.20142 | 0.16479 | 0.14191 | -0.009155 | -0.027466 | -0.14649 | 20.3934 | 3.8727 | 3.9276 | 3.8818 | 3.9368 | 0.027466 | -121.9299 | -121.8658 | 0.23804 | 0.17853 | 0.20142 | 0.15106 | 0.17395 | 20.4025 | 121.8155 | 0.21057 | 0.059509 | 121.9345 | -0.004578 | 121.9254 | 0.022888 | -121.962 | -121.9254 | 121.8063 | 0.086975 | 43.2266 | 0.1648
4075.0469 | 122.1176 | -0.050354 | 121.9437 | -0.012131 | 0.063784 | 0.079489 | 0.064978 | 0.0027215 | 0.019209 | 0.024321 | -0.005371 | 0.020608 | 0.040712 | -0.013142 | 0.01383 | 0.026528 | -0.0051205 | 43.2587 | 121.907 | -0.032043 | 121.7651 | 20.3659 | 3.9505 | 3.8132 | 0.1236 | -0.027466 | -0.009155 | 0.064087 | 0.16022 | 0.14191 | 0.13733 | 0.018311 | -0.036622 | -0.17853 | 20.4163 | 3.8635 | 4.0009 | 3.8452 | 3.9825 | 0.041199 | -121.9711 | -121.8796 | 0.21057 | 0.18768 | 0.19226 | 0.14648 | 0.15106 | 20.3979 | 121.7972 | 0.16937 | 0.073242 | 121.9391 | -0.018311 | 121.9574 | 0.022888 | -121.9757 | -121.9528 | 121.8155 | 0.11444 | 43.309 | 0.17395
4076.8125 | 122.1039 | -0.041199 | 121.9574 | -0.0045011 | 0.059725 | 0.077353 | 0.063696 | 0.0031487 | 0.014937 | 0.025603 | -0.0023192 | 0.019326 | 0.040071 | -0.018483 | 0.010412 | 0.022469 | -0.0051205 | 43.3411 | 121.8887 | -0.045776 | 121.7926 | 20.2103 | 4.0558 | 3.8086 | 0.11444 | -0.013733 | 0.009155 | 0.041199 | 0.19226 | 0.16937 | 0.13275 | -0.004577 | -0.068664 | -0.16479 | 20.2515 | 3.8498 | 4.097 | 3.8544 | 4.1016 | 0.050354 | -121.9711 | -121.9162 | 0.23346 | 0.17395 | 0.21057 | 0.1236 | 0.16022 | 20.256 | 121.8384 | 0.18311 | 0.032044 | 121.9345 | -0.022888 | 121.9299 | 0.027466 | -122.0032 | -121.9482 | 121.8338 | 0.082398 | 43.3823 | 0.15564
4078.5781 | 122.081 | -0.064087 | 121.9345 | -0.01976 | 0.063784 | 0.077353 | 0.067328 | 0.0012261 | 0.017286 | 0.02133 | -0.0084228 | 0.022958 | 0.039217 | -0.0099377 | 0.015112 | 0.024178 | -0.0023435 | 43.3411 | 121.9711 | -0.073242 | 121.6827 | 20.5032 | 3.8498 | 3.8544 | 0.022888 | 0 | -0.036621 | 0.022888 | 0.10071 | 0.09613 | 0.11902 | -0.009155 | 0.036621 | -0.25177 | 20.5673 | 3.9185 | 3.9139 | 3.9276 | 3.923 | 0.027466 | -121.9345 | -121.9116 | 0.1648 | 0.18311 | 0.16022 | 0.15564 | 0.13275 | 20.5765 | 121.756 | 0.13733 | 0.059509 | 122.0444 | 0.036621 | 122.0352 | 0.064087 | -122.0078 | -121.9711 | 121.7468 | 0.086975 | 43.4052 | 0.086975
4080.375 | 121.994 | -0.091553 | 121.9666 | -0.01976 | 0.066774 | 0.078635 | 0.069037 | -0.00069646 | 0.018355 | 0.022612 | -0.0084228 | 0.021676 | 0.040926 | -0.015919 | 0.014043 | 0.025032 | -0.0042661 | 43.4921 | 121.9849 | -0.082397 | 121.637 | 20.4803 | 3.9368 | 3.9276 | -0.059509 | 0 | -0.036621 | -0.064087 | 0.022888 | -0.018311 | 0.045776 | 0.009156 | 0.01831 | -0.32959 | 20.5719 | 4.0192 | 4.0283 | 4.01 | 4.0192 | 0.054932 | -121.9666 | -122.0306 | 0.11444 | 0.13733 | 0.073242 | 0.082397 | 0.01831 | 20.5627 | 121.7194 | 0.059509 | -0.027466 | 122.0673 | 0.036621 | 122.0764 | 0.091553 | -122.049 | -122.0032 | 121.7285 | 0.027466 | 43.5837 | 0.032044
4082.1562 | 122.1451 | -0.054932 | 121.9345 | -0.01976 | 0.061647 | 0.078207 | 0.064337 | -0.0021919 | 0.019423 | 0.024962 | -0.005371 | 0.020608 | 0.039217 | -0.010365 | 0.012762 | 0.025246 | -0.0042661 | 43.602 | 121.9025 | -0.041199 | 121.7697 | 21.048 | 3.9688 | 3.8773 | 0.1236 | -0.013733 | -0.009155 | 0.07782 | 0.20142 | 0.18768 | 0.15564 | 0.013733 | -0.032043 | -0.1648 | 21.1029 | 3.9322 | 4.0237 | 3.9185 | 4.01 | 0.045777 | -121.9482 | -121.8567 | 0.25635 | 0.21057 | 0.24261 | 0.16479 | 0.19684 | 21.0892 | 121.8109 | 0.21057 | 0.086975 | 121.9437 | -0.004578 | 121.9574 | 0.041199 | -121.9757 | -121.9437 | 121.8246 | 0.13275 | 43.6569 | 0.17853
4083.8594 | 122.0856 | -0.064087 | 121.9299 | -0.02739 | 0.065065 | 0.08013 | 0.065191 | -0.00069646 | 0.017286 | 0.024321 | -0.005371 | 0.020181 | 0.039217 | -0.013142 | 0.015325 | 0.024178 | -0.0046933 | 43.7576 | 121.9208 | -0.022888 | 121.7651 | 21.0251 | 4.0878 | 4.0146 | 0.10986 | -0.009155 | -0.013733 | 0.064087 | 0.15106 | 0.10529 | 0.13275 | 0.041199 | -0.009156 | -0.16479 | 21.0892 | 4.0787 | 4.1519 | 4.0375 | 4.1107 | 0.050354 | -121.9391 | -121.8658 | 0.21515 | 0.19684 | 0.16937 | 0.14648 | 0.11902 | 21.048 | 121.788 | 0.16479 | 0.07782 | 121.9437 | 0.004578 | 121.9849 | 0.054932 | -121.9528 | -121.9437 | 121.8292 | 0.12817 | 43.8217 | 0.17395
4085.625 | 121.9666 | -0.11902 | 121.9757 | -0.01976 | 0.068056 | 0.080985 | 0.069891 | 0.00015814 | 0.018355 | 0.024321 | -0.0084228 | 0.022744 | 0.039217 | -0.018269 | 0.013189 | 0.022042 | -0.00063445 | 43.8583 | 121.9711 | -0.07782 | 121.6782 | 20.9198 | 3.9505 | 3.7491 | -0.054932 | 0.018311 | -0.036621 | -0.07782 | 0.018311 | -0.027466 | 0.018311 | 0.041199 | -0.004578 | -0.29755 | 21.0388 | 3.8681 | 4.0695 | 3.8269 | 4.0283 | 0.082398 | -121.9574 | -122.0535 | 0.13733 | 0.13733 | 0.091553 | 0.054932 | 0.009155 | 20.9976 | 121.756 | 0.054932 | -0.041199 | 122.049 | 0.054932 | 122.0901 | 0.13733 | -122.0535 | -122.0123 | 121.7972 | 0.041199 | 43.9774 | 0.064087
4087.3906 | 121.994 | -0.10529 | 121.9803 | -0.01976 | 0.065279 | 0.077994 | 0.06925 | 0.00037174 | 0.018995 | 0.023039 | -0.0023192 | 0.021676 | 0.040499 | -0.013356 | 0.016821 | 0.022683 | -0.0014891 | 44.0002 | 121.962 | -0.082397 | 121.637 | 21.6248 | 4.1061 | 3.9093 | -0.041199 | 0.032043 | -0.045776 | -0.073242 | 0.036621 | 0.009155 | 0.036621 | 0.022889 | -0.018311 | -0.34332 | 21.73 | 4.0146 | 4.2114 | 3.9917 | 4.1885 | 0.05951 | -121.9482 | -122.0535 | 0.14191 | 0.14191 | 0.11444 | 0.082397 | 0.054931 | 21.7072 | 121.7194 | 0.082397 | -0.027466 | 122.0444 | 0.077819 | 122.0673 | 0.13733 | -122.0627 | -122.0261 | 121.7422 | 0.032044 | 44.1055 | 0.064087
4089.0938 | 122.1451 | -0.064087 | 121.9574 | -0.012131 | 0.065493 | 0.077567 | 0.064551 | -0.00026906 | 0.017927 | 0.022185 | -0.005371 | 0.018899 | 0.037508 | -0.021687 | 0.013189 | 0.023964 | -0.0046933 | 44.1422 | 121.9162 | -0.041199 | 121.7789 | 22.0139 | 4.303 | 4.1611 | 0.13733 | -0.027466 | -0.004578 | 0.073242 | 0.18768 | 0.16022 | 0.13275 | 0.022888 | -0.041198 | -0.17853 | 22.0779 | 4.2252 | 4.3671 | 4.2023 | 4.3442 | 0.059509 | -121.9849 | -121.8842 | 0.25177 | 0.19684 | 0.2243 | 0.13733 | 0.16479 | 22.0551 | 121.8201 | 0.19226 | 0.07782 | 121.9574 | -0.022888 | 121.9803 | 0.036621 | -121.9986 | -121.962 | 121.843 | 0.13733 | 44.2062 | 0.20142
4090.875 | 122.0901 | -0.054932 | 121.9299 | -0.01976 | 0.069979 | 0.081198 | 0.069464 | 0.0027215 | 0.019423 | 0.021971 | -0.0023192 | 0.022103 | 0.040285 | -0.013997 | 0.014043 | 0.024391 | -0.0070433 | 44.2474 | 121.9528 | -0.068665 | 121.7331 | 22.0139 | 4.0375 | 4.2114 | 0.064087 | 0 | -0.009155 | 0.064087 | 0.14648 | 0.12817 | 0.14191 | -0.013733 | 0.022888 | -0.19684 | 22.0688 | 4.2664 | 4.0924 | 4.2801 | 4.1061 | 0.045777 | -121.9299 | -121.8658 | 0.20142 | 0.19684 | 0.18311 | 0.15106 | 0.13733 | 22.0825 | 121.8018 | 0.15564 | 0.073242 | 122.0215 | 0.009155 | 122.0078 | 0.054932 | -121.9986 | -121.9391 | 121.788 | 0.11902 | 44.3024 | 0.11902
4092.6094 | 122.0993 | -0.059509 | 121.9162 | -0.01976 | 0.069551 | 0.083121 | 0.068182 | -0.00091006 | 0.0175 | 0.025389 | -0.0023192 | 0.021249 | 0.040285 | -0.015919 | 0.016821 | 0.023323 | -0.0019163 | 44.4351 | 121.9345 | -0.045776 | 121.7468 | 21.8903 | 4.1931 | 4.01 | 0.091553 | -0.009155 | -0.009155 | 0.073242 | 0.16937 | 0.11444 | 0.15106 | 0.013733 | 0.01831 | -0.16937 | 21.9498 | 4.0695 | 4.2526 | 4.0558 | 4.2389 | 0.050354 | -121.9254 | -121.843 | 0.22888 | 0.21057 | 0.17395 | 0.16022 | 0.1236 | 21.936 | 121.7926 | 0.17853 | 0.082397 | 121.9803 | 0 | 121.994 | 0.050354 | -121.962 | -121.9254 | 121.8063 | 0.13275 | 44.4946 | 0.15106
4094.375 | 121.9986 | -0.1236 | 121.9666 | -0.01976 | 0.065493 | 0.079916 | 0.065832 | -0.0039007 | 0.020491 | 0.027525 | -0.005371 | 0.022103 | 0.040285 | -0.019551 | 0.012334 | 0.022042 | -0.0023435 | 44.426 | 121.9254 | -0.073242 | 121.6553 | 21.9269 | 4.1519 | 3.9688 | -0.036621 | 0.045776 | -0.032043 | -0.068665 | 0.054932 | 0.041199 | 0.022888 | 0.050354 | -0.041199 | -0.31128 | 22.0505 | 4.0924 | 4.2755 | 4.0421 | 4.2252 | 0.091553 | -121.9208 | -122.0352 | 0.17853 | 0.14648 | 0.16479 | 0.054931 | 0.073242 | 22.0001 | 121.7285 | 0.086975 | -0.036622 | 121.9986 | 0.077819 | 122.049 | 0.16937 | -122.0398 | -121.9986 | 121.7789 | 0.054931 | 44.5496 | 0.086975
4096.0781 | 121.9894 | -0.086975 | 121.9574 | -0.012131 | 0.066347 | 0.080771 | 0.065191 | 0.00058534 | 0.018995 | 0.024321 | -0.005371 | 0.022317 | 0.042635 | -0.014851 | 0.015539 | 0.02311 | -0.00042085 | 44.6411 | 121.907 | -0.068665 | 121.7102 | 22.1878 | 4.0283 | 4.216 | -0.018311 | 0 | -0.036621 | -0.054932 | 0.059509 | 0.027466 | 0.027466 | 0.01831 | -0.050354 | -0.24719 | 22.2748 | 4.303 | 4.1153 | 4.2847 | 4.097 | 0.050354 | -121.9574 | -122.0123 | 0.14648 | 0.11444 | 0.11444 | 0.064087 | 0.064087 | 22.2565 | 121.7789 | 0.09613 | -0.018311 | 121.9757 | 0.036621 | 121.994 | 0.086975 | -122.0261 | -121.994 | 121.7972 | 0.032043 | 44.7281 | 0.068664
4097.8438 | 121.9894 | -0.10529 | 121.994 | -0.012131 | 0.070192 | 0.081198 | 0.070318 | 0.0033623 | 0.018995 | 0.022612 | -0.0023192 | 0.022744 | 0.040712 | -0.011647 | 0.01618 | 0.025887 | -0.0023435 | 44.783 | 121.962 | -0.07782 | 121.6827 | 22.1283 | 4.3076 | 4.0466 | 0.004578 | 0.009155 | -0.036621 | -0.036621 | 0.045776 | 0.004578 | 0.041199 | 0.027466 | -0.032044 | -0.31128 | 22.2336 | 4.1519 | 4.4128 | 4.1245 | 4.3854 | 0.068665 | -121.9849 | -122.0306 | 0.15106 | 0.14649 | 0.10986 | 0.07782 | 0.041199 | 22.2061 | 121.7606 | 0.082397 | 0 | 122.0398 | 0.045776 | 122.0673 | 0.11444 | -122.0718 | -122.0306 | 121.788 | 0.068665 | 44.8883 | 0.10986
4099.5469 | 122.0627 | -0.07782 | 121.9528 | -0.012131 | 0.069551 | 0.083334 | 0.064551 | 0.00079894 | 0.018995 | 0.021758 | -0.005371 | 0.019967 | 0.039644 | -0.018696 | 0.013616 | 0.024819 | -0.0066159 | 44.7601 | 121.9025 | -0.041199 | 121.7102 | 22.4808 | 4.2847 | 4.1382 | 0.027466 | -0.018311 | -0.009155 | 0.004578 | 0.11902 | 0.086975 | 0.10071 | 0.036621 | -0.050354 | -0.24262 | 22.5586 | 4.216 | 4.3625 | 4.1794 | 4.3259 | 0.068665 | -121.9711 | -121.9482 | 0.19684 | 0.17853 | 0.16479 | 0.10986 | 0.09613 | 22.522 | 121.7514 | 0.12817 | 0.013733 | 121.9437 | -0.009156 | 121.9803 | 0.059509 | -121.994 | -121.962 | 121.788 | 0.082398 | 44.838 | 0.10529
4101.3281 | 122.113 | -0.059509 | 121.9574 | -0.012131 | 0.070833 | 0.081198 | 0.069677 | 0.0012261 | 0.018568 | 0.024535 | -0.005371 | 0.021676 | 0.039217 | -0.0063061 | 0.015112 | 0.025246 | -0.00084805 | 44.9203 | 121.9345 | -0.054932 | 121.701 | 22.4533 | 4.2618 | 4.184 | 0.064087 | -0.013733 | -0.009155 | 0.041199 | 0.13733 | 0.13275 | 0.12817 | 0.004577 | -0.022888 | -0.25635 | 22.5128 | 4.2435 | 4.3213 | 4.2389 | 4.3167 | 0.050354 | -121.9711 | -121.9162 | 0.19684 | 0.18768 | 0.19226 | 0.13733 | 0.14191 | 22.5082 | 121.756 | 0.14648 | 0.050354 | 121.9894 | -0.004578 | 121.994 | 0.045776 | -122.0123 | -121.9666 | 121.7606 | 0.10071 | 44.9799 | 0.1236
4103.0938 | 121.9894 | -0.11902 | 121.9711 | -0.012131 | 0.06827 | 0.077353 | 0.069464 | 0.0027215 | 0.017286 | 0.02368 | -0.0084228 | 0.019326 | 0.042849 | -0.0084423 | 0.014471 | 0.02311 | -0.0049069 | 45.0256 | 121.9391 | -0.082397 | 121.6507 | 23.0026 | 4.184 | 4.1473 | -0.064087 | 0.036621 | -0.050354 | -0.091553 | 0.041199 | 0.022888 | 0.022888 | 0.036622 | -0.032043 | -0.32043 | 23.1216 | 4.2664 | 4.303 | 4.2297 | 4.2664 | 0.068665 | -121.9345 | -122.0627 | 0.16022 | 0.14191 | 0.14191 | 0.073242 | 0.073242 | 23.085 | 121.7331 | 0.091553 | -0.041199 | 122.0215 | 0.086975 | 122.0581 | 0.15564 | -122.0535 | -122.0215 | 121.7697 | 0.027466 | 45.1447 | 0.054932
4104.875 | 121.9849 | -0.09613 | 121.9894 | -0.012131 | 0.07596 | 0.082053 | 0.068182 | 0.0010125 | 0.021559 | 0.026244 | 0.00073235 | 0.024881 | 0.04114 | -0.0097241 | 0.015966 | 0.021401 | -0.0051205 | 45.0851 | 121.9757 | -0.064087 | 121.637 | 23.0072 | 4.303 | 4.1519 | -0.036621 | 0.004578 | -0.032043 | -0.059509 | 0.022888 | 0.004578 | 0.032043 | 0.032043 | -0.013733 | -0.35248 | 23.1033 | 4.248 | 4.3991 | 4.216 | 4.3671 | 0.064087 | -121.9849 | -122.049 | 0.11902 | 0.12817 | 0.10071 | 0.064086 | 0.036621 | 23.0713 | 121.701 | 0.054931 | -0.027466 | 122.0398 | 0.036621 | 122.0718 | 0.10071 | -122.0535 | -122.0215 | 121.7331 | 0.036621 | 45.1813 | 0.059509
4106.5938 | 122.0627 | -0.073242 | 121.962 | -0.012131 | 0.072329 | 0.081839 | 0.067541 | -5.5462e-05 | 0.020064 | 0.024748 | -0.0023192 | 0.017831 | 0.040071 | -0.015065 | 0.012762 | 0.024819 | -0.0042661 | 45.163 | 121.9025 | -0.032043 | 121.756 | 23.6801 | 4.2068 | 4.454 | 0.082397 | -0.036621 | -0.018311 | 0.027466 | 0.12817 | 0.10986 | 0.10529 | 0.041199 | -0.059509 | -0.20599 | 23.7534 | 4.5273 | 4.2801 | 4.4861 | 4.2389 | 0.054931 | -121.9986 | -121.9345 | 0.20142 | 0.17853 | 0.18311 | 0.1236 | 0.12817 | 23.7122 | 121.788 | 0.14649 | 0.045777 | 121.9345 | -0.01831 | 121.9757 | 0.036621 | -121.994 | -121.9803 | 121.8292 | 0.10071 | 45.2362 | 0.15564
4108.375 | 122.0078 | -0.086975 | 121.9757 | -0.012131 | 0.073824 | 0.083762 | 0.069677 | -0.00026906 | 0.0222 | 0.027098 | -0.005371 | 0.02424 | 0.039644 | -0.0099377 | 0.015112 | 0.023964 | -0.0029843 | 45.3369 | 121.9574 | -0.073242 | 121.7056 | 23.7488 | 4.4769 | 4.4403 | 0 | 0.004578 | -0.032043 | -0.027466 | 0.059509 | 0.009155 | 0.045776 | 0.013733 | -0.018311 | -0.27008 | 23.8358 | 4.5273 | 4.5639 | 4.5135 | 4.5502 | 0.054932 | -121.9711 | -122.0032 | 0.14648 | 0.13275 | 0.09613 | 0.077819 | 0.041198 | 23.822 | 121.7789 | 0.091552 | 0.004577 | 122.0306 | 0.036621 | 122.0444 | 0.091553 | -122.0489 | -122.0078 | 121.7926 | 0.059509 | 45.4239 | 0.086975
4110.0938 | 121.9711 | -0.091553 | 121.9574 | -0.012131 | 0.07596 | 0.083975 | 0.069891 | 0.00015814 | 0.023054 | 0.025603 | -0.0023192 | 0.021676 | 0.041567 | -0.012929 | 0.016821 | 0.024178 | -0.0040525 | 45.4056 | 121.9849 | -0.082397 | 121.6736 | 23.6206 | 4.2801 | 4.3533 | -0.027466 | 0.022888 | -0.045776 | -0.059509 | 0.018311 | -0.018311 | 0.041199 | 0.009156 | 0.027466 | -0.28381 | 23.7122 | 4.4449 | 4.3716 | 4.4357 | 4.3625 | 0.045777 | -121.9345 | -122.0169 | 0.10986 | 0.13275 | 0.073242 | 0.086975 | 0.027465 | 23.703 | 121.756 | 0.064087 | -0.013733 | 122.0673 | 0.068664 | 122.0764 | 0.11444 | -122.0398 | -122.0032 | 121.7651 | 0.032044 | 45.4971 | 0.064087
4111.875 | 122.1039 | -0.07782 | 121.9437 | -0.01976 | 0.075106 | 0.086325 | 0.067328 | 0.0037897 | 0.021132 | 0.025389 | -0.005371 | 0.020608 | 0.038149 | -0.019764 | 0.014257 | 0.025032 | -0.0019163 | 45.6528 | 121.9299 | -0.027466 | 121.7743 | 24.2386 | 4.6097 | 4.4083 | 0.10986 | -0.022888 | -0.009155 | 0.068665 | 0.17395 | 0.13275 | 0.12817 | 0.050354 | -0.013733 | -0.16937 | 24.3164 | 4.4861 | 4.6875 | 4.4357 | 4.6371 | 0.068665 | -121.9666 | -121.875 | 0.25177 | 0.20599 | 0.21057 | 0.13733 | 0.14191 | 24.2661 | 121.8018 | 0.1831 | 0.07782 | 121.9574 | -0.013733 | 122.0078 | 0.054932 | -121.9711 | -121.9528 | 121.8521 | 0.14649 | 45.7306 | 0.18768
4113.5781 | 122.0398 | -0.10529 | 121.9803 | -0.02739 | 0.077455 | 0.084189 | 0.067541 | 0.00015814 | 0.021986 | 0.027525 | -0.005371 | 0.021463 | 0.04114 | -0.0078015 | 0.016821 | 0.025887 | -0.0057615 | 45.5566 | 121.9803 | -0.07782 | 121.6599 | 24.028 | 4.4495 | 4.3991 | -0.013733 | 0.009155 | -0.032043 | -0.022888 | 0.045776 | 0.022888 | 0.073242 | 0.027466 | 0 | -0.32044 | 24.1333 | 4.5044 | 4.5547 | 4.4769 | 4.5273 | 0.073243 | -121.9711 | -122.0032 | 0.15106 | 0.17853 | 0.12817 | 0.10529 | 0.054931 | 24.1058 | 121.7377 | 0.077819 | 0.009155 | 122.0581 | 0.041198 | 122.0856 | 0.11444 | -122.0581 | -122.0123 | 121.7651 | 0.082398 | 45.6619 | 0.091553
4115.3438 | 121.994 | -0.10529 | 121.9894 | -0.012131 | 0.074037 | 0.082693 | 0.067114 | 0.0025079 | 0.021132 | 0.028166 | -0.005371 | 0.022103 | 0.040071 | -0.010792 | 0.014257 | 0.022255 | -0.0040525 | 45.6894 | 121.9894 | -0.07782 | 121.637 | 24.4125 | 4.5044 | 4.4907 | -0.064087 | 0.018311 | -0.068665 | -0.09613 | 0.036621 | 0.013733 | 0.032043 | 0.027466 | 0 | -0.35248 | 24.5178 | 4.5959 | 4.6097 | 4.5685 | 4.5822 | 0.036621 | -121.9711 | -122.0856 | 0.14191 | 0.13733 | 0.11902 | 0.10071 | 0.082398 | 24.4904 | 121.7148 | 0.10529 | -0.027465 | 122.0673 | 0.086976 | 122.0947 | 0.1236 | -122.0673 | -122.0581 | 121.7422 | 0.009156 | 45.7947 | 0.041199
4117.125 | 122.0123 | -0.091553 | 121.9803 | -0.0045011 | 0.076174 | 0.082907 | 0.067114 | 0.0027215 | 0.019636 | 0.025603 | -0.0023192 | 0.021249 | 0.039431 | -0.023823 | 0.012548 | 0.025246 | -0.0059751 | 45.8817 | 121.9437 | -0.050354 | 121.7194 | 24.9481 | 4.5319 | 4.5227 | -0.009155 | 0.018311 | -0.022888 | -0.059509 | 0.068665 | 0.036621 | 0.041199 | 0.041199 | -0.036621 | -0.26093 | 25.0397 | 4.6143 | 4.6234 | 4.5731 | 4.5822 | 0.068665 | -121.962 | -122.0398 | 0.16022 | 0.13275 | 0.12817 | 0.064087 | 0.059509 | 24.9985 | 121.7697 | 0.091553 | -0.036621 | 121.994 | 0.041199 | 122.0352 | 0.10986 | -122.0306 | -122.0032 | 121.8109 | 0.032044 | 45.9732 | 0.082398
4118.8906 | 122.0947 | -0.054932 | 121.9162 | -0.01976 | 0.078524 | 0.086539 | 0.065832 | 0.0012261 | 0.0222 | 0.025603 | -0.0084228 | 0.020822 | 0.040285 | -0.02361 | 0.013616 | 0.023964 | -0.0036253 | 45.9732 | 121.9208 | -0.036621 | 121.7651 | 25.2914 | 4.5593 | 4.6234 | 0.1236 | -0.009155 | -0.009155 | 0.064087 | 0.14648 | 0.1236 | 0.13733 | 0.018311 | 0.004577 | -0.15106 | 25.3464 | 4.6783 | 4.6143 | 4.66 | 4.5959 | 0.045777 | -121.9254 | -121.8521 | 0.20142 | 0.19226 | 0.17853 | 0.14648 | 0.13275 | 25.3281 | 121.8018 | 0.15564 | 0.073242 | 121.9574 | 0 | 121.9757 | 0.045777 | -121.9528 | -121.9254 | 121.8201 | 0.11902 | 46.0281 | 0.17853
4120.6406 | 122.0032 | -0.11444 | 121.9711 | -0.01976 | 0.077242 | 0.081625 | 0.068609 | 0.0022943 | 0.018355 | 0.02603 | -0.005371 | 0.023599 | 0.040499 | -0.014424 | 0.014684 | 0.024819 | -0.0019163 | 46.0098 | 121.9803 | -0.07782 | 121.6461 | 25.5157 | 4.5364 | 4.4449 | -0.054932 | 0.009155 | -0.050354 | -0.059509 | 0.054932 | 0.027466 | 0.041199 | 0.036621 | 0.009156 | -0.32501 | 25.6302 | 4.5593 | 4.6509 | 4.5227 | 4.6143 | 0.064087 | -121.962 | -122.0306 | 0.16937 | 0.15564 | 0.14191 | 0.091553 | 0.07782 | 25.5936 | 121.7239 | 0.10529 | -0.009155 | 122.0581 | 0.059509 | 122.0947 | 0.1236 | -122.049 | -122.0215 | 121.7606 | 0.054932 | 46.1243 | 0.059509
4122.3594 | 122.0856 | -0.068665 | 121.9528 | -0.012131 | 0.077455 | 0.085257 | 0.068396 | -0.00026906 | 0.022627 | 0.028593 | -0.0023192 | 0.01954 | 0.041567 | -0.019124 | 0.015325 | 0.023537 | -0.0049069 | 45.9412 | 121.9437 | -0.045776 | 121.7194 | 25.946 | 4.6783 | 4.5364 | 0.013733 | 0 | -0.013733 | -0.009155 | 0.10986 | 0.082397 | 0.09613 | 0.022889 | -0.009155 | -0.23346 | 26.0147 | 4.6051 | 4.747 | 4.5822 | 4.7241 | 0.054932 | -121.9528 | -121.962 | 0.17853 | 0.16479 | 0.15106 | 0.10986 | 0.09613 | 25.9918 | 121.7651 | 0.1236 | 0.004578 | 121.9894 | 0.013733 | 122.0123 | 0.068665 | -121.9986 | -121.9666 | 121.788 | 0.05951 | 46.0098 | 0.082398
4124.1094 | 122.1039 | -0.059509 | 121.9345 | -0.012131 | 0.07831 | 0.082053 | 0.0669 | -0.0019781 | 0.021132 | 0.02838 | -0.005371 | 0.01954 | 0.040499 | -0.018696 | 0.013189 | 0.024819 | -0.0025571 | 46.2341 | 121.9208 | -0.041199 | 121.7743 | 26.1658 | 4.7974 | 4.9026 | 0.10986 | -0.018311 | 0.009155 | 0.045776 | 0.1831 | 0.14648 | 0.13275 | 0.01831 | -0.013733 | -0.16022 | 26.2253 | 4.9622 | 4.8569 | 4.9438 | 4.8386 | 0.068664 | -121.9528 | -121.8887 | 0.24261 | 0.19226 | 0.20599 | 0.1236 | 0.13733 | 26.207 | 121.8155 | 0.17395 | 0.036621 | 121.962 | -0.027466 | 121.9803 | 0.041198 | -121.9757 | -121.9254 | 121.8338 | 0.10528 | 46.2936 | 0.16937
4125.875 | 122.1085 | -0.082397 | 121.9162 | -0.012131 | 0.079378 | 0.085257 | 0.066473 | 0.0016535 | 0.019636 | 0.027525 | -0.005371 | 0.020395 | 0.038576 | -0.015492 | 0.013403 | 0.023964 | -0.0040525 | 46.2845 | 121.9254 | -0.036621 | 121.7239 | 25.9003 | 4.8248 | 4.747 | 0.045776 | -0.027466 | -0.009155 | 0.027466 | 0.13733 | 0.12817 | 0.10986 | 0.045776 | 0.009155 | -0.19226 | 25.9827 | 4.8294 | 4.9072 | 4.7836 | 4.8615 | 0.073242 | -121.9437 | -121.8887 | 0.21973 | 0.19226 | 0.21057 | 0.11902 | 0.13733 | 25.9369 | 121.7606 | 0.14648 | 0.036621 | 121.962 | -0.018311 | 122.0078 | 0.054931 | -121.9528 | -121.9254 | 121.8063 | 0.10986 | 46.3669 | 0.12817
4127.6094 | 121.994 | -0.10986 | 121.9849 | -0.0045011 | 0.077242 | 0.085898 | 0.066687 | -0.0051825 | 0.0222 | 0.029875 | -0.005371 | 0.022103 | 0.040712 | -0.017201 | 0.014257 | 0.023537 | -0.0036253 | 46.225 | 121.9528 | -0.054932 | 121.669 | 25.7812 | 4.7058 | 4.7287 | -0.027466 | 0.009155 | -0.036621 | -0.059509 | 0.041199 | 0.022888 | 0.018311 | 0.054931 | -0.032043 | -0.31586 | 25.8911 | 4.8386 | 4.8157 | 4.7836 | 4.7607 | 0.073242 | -121.9757 | -122.0444 | 0.15106 | 0.12817 | 0.13275 | 0.054932 | 0.059509 | 25.8362 | 121.7239 | 0.07782 | -0.022888 | 122.0078 | 0.045776 | 122.0627 | 0.11902 | -122.0398 | -122.0215 | 121.7789 | 0.050354 | 46.3348 | 0.082397
4129.375 | 121.9666 | -0.09613 | 121.9803 | -0.012131 | 0.082155 | 0.084402 | 0.070318 | 0.0016535 | 0.021559 | 0.028807 | -0.005371 | 0.02424 | 0.040712 | -0.0084423 | 0.017248 | 0.02311 | -0.0049069 | 46.2708 | 121.962 | -0.07782 | 121.6461 | 25.7629 | 4.6417 | 4.7195 | -0.07782 | 0.018311 | -0.045776 | -0.082397 | 0.004578 | -0.027466 | 0.032043 | 0.01831 | -0.018311 | -0.33417 | 25.8591 | 4.8157 | 4.7379 | 4.7974 | 4.7195 | 0.050354 | -121.962 | -122.0627 | 0.10071 | 0.12817 | 0.068664 | 0.077819 | 0.01831 | 25.8408 | 121.7239 | 0.050354 | -0.036621 | 122.0398 | 0.064087 | 122.0581 | 0.11444 | -122.0581 | -122.0261 | 121.7422 | 0.013733 | 46.3669 | 0.01831
4131.0781 | 122.0078 | -0.11902 | 121.9757 | -0.012131 | 0.081728 | 0.083975 | 0.06925 | -0.00069646 | 0.021132 | 0.027525 | -0.005371 | 0.021463 | 0.042421 | -0.0090833 | 0.014684 | 0.02546 | 0.0012881 | 46.2662 | 121.9482 | -0.09613 | 121.6461 | 26.9714 | 4.8203 | 4.7195 | -0.073242 | 0.022888 | -0.045776 | -0.059509 | 0.041199 | 0.013733 | 0.041199 | 0.022889 | -0.027466 | -0.32959 | 27.0905 | 4.8386 | 4.9393 | 4.8157 | 4.9164 | 0.073243 | -121.9528 | -122.0352 | 0.16022 | 0.16022 | 0.13275 | 0.086975 | 0.059509 | 27.0676 | 121.7422 | 0.086975 | -0.013733 | 122.0444 | 0.068664 | 122.0673 | 0.14191 | -122.0718 | -122.0215 | 121.7651 | 0.05951 | 46.3852 | 0.045777
4132.8594 | 122.0993 | -0.064087 | 121.9528 | -0.02739 | 0.08066 | 0.086966 | 0.067114 | -0.00069646 | 0.02455 | 0.026671 | -0.0023192 | 0.020822 | 0.03879 | -0.016987 | 0.012121 | 0.023751 | -0.0029843 | 46.5546 | 121.8796 | -0.027466 | 121.7743 | 26.5366 | 4.8935 | 4.8523 | 0.10071 | -0.022888 | -0.004578 | 0.027466 | 0.15564 | 0.13733 | 0.12817 | 0.036621 | -0.073242 | -0.17853 | 26.6006 | 4.9164 | 4.9576 | 4.8798 | 4.921 | 0.059509 | -121.9757 | -121.9254 | 0.21973 | 0.19226 | 0.20142 | 0.13275 | 0.14191 | 26.564 | 121.8018 | 0.16022 | 0.032044 | 121.907 | -0.01831 | 121.9437 | 0.041199 | -121.9803 | -121.9574 | 121.8384 | 0.091553 | 46.6187 | 0.1648
4134.5625 | 122.1588 | -0.045776 | 121.9345 | -0.012131 | 0.081514 | 0.085684 | 0.067755 | -0.0026191 | 0.024977 | 0.03073 | -0.005371 | 0.018472 | 0.04178 | -0.020833 | 0.014043 | 0.02311 | -0.0061887 | 46.582 | 121.9116 | -0.036621 | 121.7697 | 26.8158 | 5.0537 | 4.9164 | 0.14191 | -0.036621 | -0.013733 | 0.068665 | 0.20599 | 0.1831 | 0.15564 | 0.009155 | -0.022888 | -0.1648 | 26.8616 | 4.9622 | 5.0995 | 4.953 | 5.0903 | 0.032043 | -121.9711 | -121.8658 | 0.25177 | 0.20142 | 0.22888 | 0.16937 | 0.19684 | 26.8524 | 121.8063 | 0.21973 | 0.082398 | 121.9482 | -0.022888 | 121.9574 | 0.009155 | -121.9711 | -121.9482 | 121.8155 | 0.11444 | 46.6278 | 0.18768
4136.3281 | 122.0627 | -0.068665 | 121.9528 | -0.01976 | 0.082796 | 0.08782 | 0.065405 | 0.00037174 | 0.024122 | 0.031798 | -0.0023192 | 0.021676 | 0.041994 | -0.01186 | 0.012762 | 0.023537 | -0.0029843 | 46.6187 | 121.9391 | -0.041199 | 121.7102 | 27.1271 | 4.9438 | 5.0308 | 0.041199 | -0.018311 | -0.036621 | 0 | 0.10071 | 0.082397 | 0.091553 | 0.027466 | -0.013733 | -0.24262 | 27.1957 | 5.0995 | 5.0125 | 5.072 | 4.985 | 0.032044 | -121.9711 | -121.9528 | 0.16937 | 0.16022 | 0.15106 | 0.12817 | 0.11902 | 27.1683 | 121.7514 | 0.13733 | 0.036621 | 121.9803 | 0.01831 | 122.0078 | 0.050354 | -121.994 | -121.9894 | 121.7789 | 0.068665 | 46.6873 | 0.10986
4138.0938 | 122.1313 | -0.059509 | 121.9162 | 0.0031279 | 0.082155 | 0.087393 | 0.068823 | -0.0036871 | 0.024336 | 0.029448 | -0.0023192 | 0.020822 | 0.040285 | -0.018055 | 0.012334 | 0.023964 | -0.0046933 | 46.5637 | 121.9162 | -0.041199 | 121.7697 | 26.7334 | 5.1819 | 5.0125 | 0.13275 | -0.013733 | -0.009155 | 0.064087 | 0.19684 | 0.17395 | 0.16022 | 0.01831 | 0 | -0.14649 | 26.7929 | 5.072 | 5.2414 | 5.0537 | 5.2231 | 0.050354 | -121.9299 | -121.8521 | 0.25635 | 0.21973 | 0.23346 | 0.16937 | 0.1831 | 26.7746 | 121.8109 | 0.20599 | 0.073242 | 121.9574 | -0.004578 | 121.9757 | 0.045776 | -121.9574 | -121.9254 | 121.8292 | 0.1236 | 46.6232 | 0.19226
4139.875 | 121.9849 | -0.11444 | 121.9849 | -0.012131 | 0.082582 | 0.086111 | 0.067541 | -0.0021919 | 0.023268 | 0.031157 | -0.005371 | 0.022744 | 0.040926 | -0.017842 | 0.012975 | 0.023323 | -0.0017027 | 46.7606 | 121.9528 | -0.082397 | 121.6782 | 26.6647 | 4.9164 | 4.953 | -0.036621 | 0.009155 | -0.054932 | -0.064087 | 0.054932 | 0.009155 | 0.027466 | 0.032044 | -0.032043 | -0.3067 | 26.7792 | 5.0674 | 5.0308 | 5.0354 | 4.9988 | 0.059509 | -121.9757 | -122.049 | 0.16937 | 0.14191 | 0.1236 | 0.082398 | 0.064087 | 26.7471 | 121.7606 | 0.10986 | -0.009155 | 122.0352 | 0.064087 | 122.0673 | 0.1236 | -122.0673 | -122.0398 | 121.7926 | 0.050354 | 46.875 | 0.07782
4141.5781 | 122.1039 | -0.050354 | 121.9299 | -0.01976 | 0.081514 | 0.086966 | 0.069037 | 0.00015814 | 0.022413 | 0.02838 | -0.0084228 | 0.020608 | 0.040499 | -0.013356 | 0.01383 | 0.023323 | -0.0040525 | 46.9025 | 121.9162 | -0.059509 | 121.7468 | 27.4704 | 5.1315 | 5.0491 | 0.091553 | -0.018311 | -0.018311 | 0.050354 | 0.17853 | 0.15564 | 0.13733 | -0.009155 | -0.013733 | -0.18311 | 27.5208 | 5.0995 | 5.1819 | 5.1086 | 5.191 | 0.032043 | -121.9482 | -121.8796 | 0.22888 | 0.18768 | 0.20599 | 0.15564 | 0.17395 | 27.5299 | 121.8063 | 0.19684 | 0.068665 | 121.9757 | 0 | 121.9666 | 0.032043 | -121.9894 | -121.9482 | 121.7972 | 0.10071 | 46.9528 | 0.14191
4143.3594 | 122.113 | -0.064087 | 121.9299 | -0.012131 | 0.087709 | 0.08782 | 0.072455 | 0.00037174 | 0.026686 | 0.030089 | -0.005371 | 0.019967 | 0.040499 | -0.010579 | 0.014684 | 0.023537 | -0.0051205 | 46.907 | 121.9482 | -0.041199 | 121.7606 | 27.0905 | 5.1682 | 4.9667 | 0.07782 | -0.018311 | -0.004578 | 0.068665 | 0.16022 | 0.13275 | 0.14191 | 0.022888 | 0.01831 | -0.16937 | 27.1545 | 5.0308 | 5.2322 | 5.0079 | 5.2094 | 0.059509 | -121.9482 | -121.8613 | 0.2243 | 0.20599 | 0.19684 | 0.14649 | 0.13733 | 27.1317 | 121.8018 | 0.16479 | 0.073243 | 121.9894 | -0.013733 | 122.0123 | 0.045776 | -121.9711 | -121.9345 | 121.8246 | 0.13275 | 46.9711 | 0.14191
4145.1406 | 122.1359 | -0.045776 | 121.9528 | -0.01976 | 0.082369 | 0.085043 | 0.067968 | -0.00048286 | 0.02519 | 0.029234 | -0.005371 | 0.020181 | 0.04178 | -0.015278 | 0.014257 | 0.023537 | -0.0070433 | 47.0123 | 121.8887 | -0.054932 | 121.7743 | 27.4292 | 5.2414 | 5.127 | 0.09613 | -0.013733 | 0 | 0.064087 | 0.17853 | 0.16479 | 0.15564 | -0.009156 | -0.064087 | -0.17853 | 27.475 | 5.1727 | 5.2872 | 5.1819 | 5.2963 | 0.045776 | -121.9666 | -121.8887 | 0.2243 | 0.20142 | 0.21057 | 0.15564 | 0.16479 | 27.4841 | 121.8292 | 0.17853 | 0.064087 | 121.9437 | -0.013733 | 121.9345 | 0.032043 | -122.0078 | -121.9528 | 121.8201 | 0.10986 | 47.0581 | 0.14191
4146.8438 | 122.0947 | -0.064087 | 121.9162 | -0.0045011 | 0.087068 | 0.088675 | 0.06925 | -0.0030463 | 0.026899 | 0.030302 | -0.0084228 | 0.020181 | 0.039644 | -0.014424 | 0.011907 | 0.024178 | 0.00043375 | 47.113 | 121.9254 | -0.027466 | 121.7697 | 27.4017 | 5.2322 | 5.0674 | 0.10986 | -0.018311 | -0.009155 | 0.07782 | 0.15106 | 0.12817 | 0.13733 | 0.036621 | 0.009155 | -0.14649 | 27.4658 | 5.1315 | 5.2963 | 5.0949 | 5.2597 | 0.054932 | -121.9345 | -121.8384 | 0.21515 | 0.20142 | 0.19226 | 0.14648 | 0.13733 | 27.4292 | 121.7972 | 0.16022 | 0.086975 | 121.9528 | -0.009156 | 121.9894 | 0.045776 | -121.9437 | -121.9254 | 121.8338 | 0.14191 | 47.1771 | 0.17395
4148.6094 | 122.1085 | -0.041199 | 121.9208 | -0.01976 | 0.089846 | 0.089743 | 0.069464 | -0.0024055 | 0.030104 | 0.03073 | -0.005371 | 0.021249 | 0.03644 | -0.017201 | 0.015325 | 0.024391 | -0.0057615 | 47.2321 | 121.9208 | -0.050354 | 121.788 | 27.9007 | 5.1407 | 5.2734 | 0.11444 | -0.032043 | 0.004578 | 0.064087 | 0.17395 | 0.13275 | 0.12817 | -0.009155 | 0 | -0.13275 | 27.9419 | 5.3146 | 5.1819 | 5.3238 | 5.191 | 0.045777 | -121.9528 | -121.8567 | 0.21515 | 0.16937 | 0.17395 | 0.1236 | 0.12817 | 27.951 | 121.8384 | 0.16937 | 0.059509 | 121.9711 | -0.036621 | 121.962 | 0.009156 | -121.9711 | -121.9162 | 121.8292 | 0.10529 | 47.2733 | 0.15564
4150.3281 | 122.1085 | -0.073242 | 121.9482 | -0.01976 | 0.085146 | 0.086966 | 0.068609 | -0.0060371 | 0.024977 | 0.031157 | -0.0084228 | 0.020608 | 0.041353 | -0.017201 | 0.013616 | 0.023323 | -0.0089659 | 47.168 | 121.9208 | -0.059509 | 121.7468 | 28.0838 | 5.2322 | 5.365 | 0.091553 | -0.018311 | -0.013733 | 0.054932 | 0.16479 | 0.16022 | 0.12817 | 0.013733 | -0.027466 | -0.20142 | 28.157 | 5.4382 | 5.3055 | 5.4245 | 5.2917 | 0.059509 | -121.9666 | -121.8933 | 0.23804 | 0.20142 | 0.23346 | 0.14191 | 0.17395 | 28.1433 | 121.8063 | 0.17853 | 0.068665 | 121.9803 | -0.004578 | 121.994 | 0.054931 | -122.0078 | -121.962 | 121.8201 | 0.12817 | 47.2412 | 0.16479
4152.0938 | 122.0535 | -0.045776 | 121.9391 | 0.0031279 | 0.087068 | 0.088461 | 0.067755 | -0.0028327 | 0.023909 | 0.029234 | -0.005371 | 0.019967 | 0.040499 | -0.0084423 | 0.012975 | 0.023751 | -0.00042085 | 47.3648 | 121.9299 | -0.059509 | 121.7102 | 28.0884 | 5.3513 | 5.1727 | 0.027466 | 0.004578 | -0.018311 | 0 | 0.10529 | 0.082397 | 0.082397 | -0.013733 | -0.009155 | -0.22888 | 28.1342 | 5.2185 | 5.397 | 5.2322 | 5.4108 | 0.027465 | -121.9345 | -121.9391 | 0.15106 | 0.12817 | 0.12817 | 0.10071 | 0.10071 | 28.1479 | 121.7697 | 0.1236 | 0.018311 | 121.9894 | 0.022889 | 121.9757 | 0.050354 | -121.9986 | -121.9574 | 121.756 | 0.045776 | 47.4106 | 0.073242
4153.875 | 122.0764 | -0.082397 | 121.962 | -0.0045011 | 0.088137 | 0.087607 | 0.070105 | 0.0014397 | 0.026045 | 0.030516 | -0.005371 | 0.022103 | 0.039858 | -0.015492 | 0.012548 | 0.023537 | -0.0066159 | 47.1863 | 121.907 | -0.054932 | 121.7331 | 28.4409 | 5.1315 | 5.3696 | 0.022888 | -0.009155 | -0.041199 | 0 | 0.10986 | 0.07782 | 0.082397 | 0.027465 | -0.054932 | -0.22888 | 28.5233 | 5.452 | 5.2139 | 5.4245 | 5.1865 | 0.041198 | -121.9711 | -121.962 | 0.19226 | 0.16479 | 0.16022 | 0.1236 | 0.11902 | 28.4958 | 121.788 | 0.15106 | 0.041199 | 121.962 | 0.032044 | 121.9894 | 0.073242 | -122.0169 | -122.0032 | 121.8155 | 0.082397 | 47.2687 | 0.10528
4155.6406 | 122.0215 | -0.086975 | 121.9894 | -0.0045011 | 0.091341 | 0.089529 | 0.072027 | 0.0020807 | 0.029463 | 0.033293 | -0.005371 | 0.023172 | 0.040926 | -0.013356 | 0.016821 | 0.024605 | -0.0029843 | 47.4976 | 121.9711 | -0.064087 | 121.6644 | 28.363 | 5.4703 | 5.365 | -0.027466 | 0.018311 | -0.045776 | -0.022888 | 0.045776 | 0.018311 | 0.050354 | 0.022888 | -0.018311 | -0.32501 | 28.45 | 5.452 | 5.5573 | 5.4291 | 5.5344 | 0.041199 | -121.9711 | -122.0123 | 0.13275 | 0.13733 | 0.10529 | 0.09613 | 0.064087 | 28.4271 | 121.7285 | 0.091552 | 0.022888 | 122.0352 | 0.064087 | 122.0581 | 0.10529 | -122.0535 | -122.0352 | 121.7514 | 0.064087 | 47.5845 | 0.059509
4157.3594 | 122.0947 | -0.073242 | 121.9528 | -0.01976 | 0.089632 | 0.085684 | 0.068823 | -0.00091006 | 0.026899 | 0.033293 | -0.0023192 | 0.020608 | 0.039217 | -0.015706 | 0.011907 | 0.024178 | -0.0010617 | 47.4701 | 121.8979 | -0.059509 | 121.7514 | 28.8025 | 5.4382 | 5.4703 | 0.032043 | 0 | -0.018311 | 0.032043 | 0.14191 | 0.13275 | 0.11444 | 0.013733 | -0.054932 | -0.20142 | 28.8757 | 5.5435 | 5.5115 | 5.5298 | 5.4977 | 0.054931 | -121.9528 | -121.9208 | 0.21515 | 0.18768 | 0.20599 | 0.13275 | 0.15106 | 28.862 | 121.8109 | 0.16022 | 0.050354 | 121.9574 | 0.018311 | 121.9711 | 0.073242 | -122.0123 | -121.9711 | 121.8246 | 0.10529 | 47.5433 | 0.10529
4159.0625 | 122.0581 | -0.059509 | 121.962 | -0.012131 | 0.092195 | 0.089957 | 0.069037 | 0.0018671 | 0.027968 | 0.032652 | -0.0084228 | 0.022103 | 0.040071 | -0.010365 | 0.014471 | 0.022683 | -0.0034117 | 47.4518 | 121.9162 | -0.032043 | 121.7148 | 28.9398 | 5.5115 | 5.4199 | 0.064087 | -0.009155 | -0.027466 | 0.013733 | 0.11444 | 0.086975 | 0.09613 | 0.027466 | -0.045776 | -0.24719 | 28.9993 | 5.4794 | 5.571 | 5.452 | 5.5435 | 0.032043 | -121.9711 | -121.9482 | 0.17395 | 0.15564 | 0.14648 | 0.1236 | 0.11444 | 28.9719 | 121.7468 | 0.14191 | 0.041199 | 121.9482 | 0.018311 | 121.9757 | 0.050354 | -121.994 | -121.9894 | 121.7743 | 0.073242 | 47.5113 | 0.1236
4160.8281 | 121.9849 | -0.091553 | 121.9528 | -0.0045011 | 0.095613 | 0.092307 | 0.071173 | -0.0019781 | 0.026686 | 0.033293 | -0.005371 | 0.022958 | 0.041994 | -0.011647 | 0.014684 | 0.0261 | -0.0017027 | 47.731 | 121.994 | -0.073242 | 121.637 | 29.1779 | 5.5161 | 5.5298 | -0.059509 | 0.009155 | -0.036621 | -0.054932 | 0.013733 | -0.018311 | 0.032043 | 0.018311 | 0.041199 | -0.31586 | 29.2694 | 5.6213 | 5.6076 | 5.603 | 5.5893 | 0.054932 | -121.9437 | -122.0078 | 0.10529 | 0.1236 | 0.073242 | 0.068664 | 0.01831 | 29.2511 | 121.7102 | 0.050354 | -0.018311 | 122.0673 | 0.045776 | 122.0856 | 0.10071 | -122.0261 | -121.9894 | 121.7285 | 0.036621 | 47.8226 | 0.032044
4162.5469 | 122.1039 | -0.068665 | 121.9116 | -0.0045011 | 0.090914 | 0.088034 | 0.069464 | 0.00058534 | 0.025404 | 0.033934 | -0.005371 | 0.019754 | 0.040712 | -0.012929 | 0.014043 | 0.024391 | -0.0031979 | 47.8638 | 121.907 | -0.050354 | 121.7331 | 29.2053 | 5.7175 | 5.5298 | 0.045776 | -0.009155 | -0.036621 | 0.036621 | 0.16937 | 0.14191 | 0.13275 | 0.018311 | -0.004578 | -0.17853 | 29.274 | 5.5985 | 5.7861 | 5.5801 | 5.7678 | 0.032044 | -121.9208 | -121.875 | 0.23804 | 0.20142 | 0.21057 | 0.16937 | 0.17853 | 29.2557 | 121.7834 | 0.20599 | 0.073242 | 121.9574 | 0.027466 | 121.9757 | 0.05951 | -121.962 | -121.9482 | 121.8018 | 0.10529 | 47.9324 | 0.11444
4164.3125 | 122.0398 | -0.086975 | 121.9894 | -0.012131 | 0.093691 | 0.087607 | 0.070746 | 0.0022943 | 0.027327 | 0.035216 | 0.00073235 | 0.02424 | 0.040071 | -0.010792 | 0.016821 | 0.022896 | -0.0061887 | 47.9141 | 121.9208 | -0.07782 | 121.7056 | 29.6722 | 5.7541 | 5.4337 | 0.004578 | 0.009155 | -0.027466 | 0.004578 | 0.091553 | 0.050354 | 0.07782 | 0.009155 | -0.068665 | -0.28381 | 29.7592 | 5.5206 | 5.8411 | 5.5115 | 5.8319 | 0.059509 | -121.9803 | -121.9849 | 0.17853 | 0.16479 | 0.13733 | 0.10529 | 0.07782 | 29.7501 | 121.7834 | 0.11902 | 0.032044 | 121.9986 | 0.036621 | 122.0078 | 0.09613 | -122.0673 | -122.0169 | 121.7926 | 0.091553 | 48.0011 | 0.091553
4166.0781 | 122.1405 | -0.059509 | 121.9162 | -0.012131 | 0.094545 | 0.089529 | 0.069677 | -0.0013373 | 0.02989 | 0.033507 | -0.005371 | 0.020395 | 0.041994 | -0.013142 | 0.014043 | 0.025887 | -0.0049069 | 47.9919 | 121.9025 | -0.050354 | 121.7422 | 29.7867 | 5.8548 | 5.6396 | 0.082397 | -0.022888 | -0.032043 | 0.064087 | 0.17395 | 0.16479 | 0.1236 | 0.009155 | -0.013733 | -0.17395 | 29.8462 | 5.6992 | 5.9143 | 5.69 | 5.9052 | 0.027466 | -121.9391 | -121.8521 | 0.23346 | 0.1831 | 0.2243 | 0.15564 | 0.19684 | 29.837 | 121.7926 | 0.20599 | 0.09613 | 121.9528 | 0.009155 | 121.962 | 0.036621 | -121.9666 | -121.9482 | 121.8018 | 0.1236 | 48.0515 | 0.14191
4167.8594 | 122.1176 | -0.064087 | 121.9391 | -0.012131 | 0.097322 | 0.092307 | 0.071173 | 0.0010125 | 0.027327 | 0.034148 | -0.005371 | 0.020822 | 0.040499 | -0.013142 | 0.015966 | 0.02546 | -0.0025571 | 48.0652 | 121.9391 | -0.036621 | 121.7834 | 30.1849 | 5.8548 | 5.603 | 0.11444 | -0.018311 | -0.009155 | 0.064087 | 0.16022 | 0.13733 | 0.14191 | 0.027466 | 0 | -0.15564 | 30.249 | 5.6671 | 5.9189 | 5.6396 | 5.8914 | 0.054932 | -121.9574 | -121.875 | 0.2243 | 0.20599 | 0.20142 | 0.15106 | 0.14648 | 30.2216 | 121.8201 | 0.16937 | 0.073242 | 121.9757 | -0.009156 | 122.0032 | 0.045776 | -121.9757 | -121.9482 | 121.8475 | 0.12817 | 48.1293 | 0.17853
4169.5625 | 121.9666 | -0.10529 | 121.994 | -0.012131 | 0.10117 | 0.092947 | 0.073523 | 0.0012261 | 0.029677 | 0.03372 | -0.0084228 | 0.02189 | 0.039858 | -0.013142 | 0.017675 | 0.024178 | -0.0061887 | 47.9095 | 121.9803 | -0.082397 | 121.6461 | 29.9881 | 5.6946 | 5.603 | -0.07782 | 0.009155 | -0.054932 | -0.050354 | 0.027466 | -0.027466 | 0.041199 | 0.022889 | -0.013733 | -0.3479 | 30.0934 | 5.7083 | 5.7999 | 5.6854 | 5.777 | 0.050354 | -121.9849 | -122.0444 | 0.13275 | 0.14649 | 0.07782 | 0.096131 | 0.027466 | 30.0705 | 121.7285 | 0.082398 | 0.004578 | 122.0627 | 0.064087 | 122.0856 | 0.11444 | -122.0764 | -122.049 | 121.7514 | 0.054932 | 48.0148 | 0.027466
4171.3281 | 122.0123 | -0.091553 | 121.9528 | -0.0045011 | 0.096682 | 0.092093 | 0.067755 | 0.0025079 | 0.027754 | 0.037993 | -0.0084228 | 0.02189 | 0.041567 | -0.016774 | 0.015112 | 0.024819 | -0.0023435 | 48.0972 | 121.9254 | -0.054932 | 121.7239 | 30.1895 | 5.928 | 5.864 | 0 | -0.004578 | -0.013733 | -0.032043 | 0.082397 | 0.059509 | 0.041199 | 0.036621 | -0.027466 | -0.22888 | 30.2811 | 5.9555 | 6.0196 | 5.9189 | 5.983 | 0.07782 | -121.9574 | -121.9849 | 0.17395 | 0.13275 | 0.15106 | 0.054932 | 0.073242 | 30.2444 | 121.7789 | 0.09613 | -0.01831 | 121.9803 | 0.009155 | 122.0169 | 0.086975 | -122.0078 | -121.9666 | 121.8155 | 0.05951 | 48.1888 | 0.091553
4173.0938 | 122.0398 | -0.082397 | 121.9711 | -0.012131 | 0.10095 | 0.091666 | 0.072668 | 0.0022943 | 0.02989 | 0.035643 | -0.0084228 | 0.024026 | 0.039858 | -0.010151 | 0.015325 | 0.024605 | -0.0014891 | 47.8134 | 121.9757 | -0.073242 | 121.6599 | 30.3589 | 5.7907 | 5.7358 | -0.018311 | 0.013733 | -0.045776 | -0.004578 | 0.059509 | 0.032043 | 0.068665 | 0.009155 | 0.004578 | -0.31128 | 30.4413 | 5.8182 | 5.8731 | 5.809 | 5.864 | 0.036621 | -121.9574 | -121.9757 | 0.14191 | 0.15106 | 0.11444 | 0.11444 | 0.077819 | 30.4321 | 121.7331 | 0.10528 | 0.041198 | 122.0489 | 0.059509 | 122.0581 | 0.09613 | -122.0444 | -122.0169 | 121.7422 | 0.077819 | 47.8958 | 0.064086
4174.8594 | 122.0306 | -0.091553 | 121.9849 | -0.01976 | 0.10138 | 0.091879 | 0.071173 | -0.0019781 | 0.02989 | 0.035643 | -0.0023192 | 0.023385 | 0.042208 | -0.010579 | 0.016607 | 0.025032 | -0.0019163 | 48.1796 | 121.9528 | -0.068665 | 121.7056 | 30.9357 | 5.8044 | 6.0608 | 0.018311 | -0.004578 | -0.032043 | -0.018311 | 0.07782 | 0.022888 | 0.068665 | 0.022888 | -0.032043 | -0.27924 | 31.0272 | 6.1523 | 5.896 | 6.1295 | 5.8731 | 0.05951 | -121.9894 | -122.0032 | 0.16937 | 0.16022 | 0.11444 | 0.10071 | 0.054931 | 31.0043 | 121.7743 | 0.10986 | 0.013732 | 122.0215 | 0.027465 | 122.0444 | 0.086975 | -122.0535 | -122.0169 | 121.7972 | 0.073242 | 48.2712 | 0.10986
4176.5625 | 122.0261 | -0.11902 | 121.9986 | -0.01976 | 0.098391 | 0.090598 | 0.070532 | -0.0024055 | 0.031172 | 0.039702 | 0.00073235 | 0.022744 | 0.04413 | -0.016347 | 0.015752 | 0.0261 | -0.0042661 | 47.9462 | 121.9482 | -0.086975 | 121.6461 | 31.105 | 5.9738 | 6.0104 | -0.059509 | 0.027466 | -0.045776 | -0.041199 | 0.059509 | 0.036621 | 0.082397 | 0.032044 | -0.050354 | -0.35248 | 31.2241 | 6.1295 | 6.0928 | 6.0974 | 6.0608 | 0.073243 | -121.9711 | -122.0398 | 0.17853 | 0.20142 | 0.15564 | 0.12817 | 0.082397 | 31.192 | 121.7331 | 0.10528 | 0.004577 | 122.0352 | 0.073242 | 122.0673 | 0.14649 | -122.0856 | -122.0444 | 121.7651 | 0.07782 | 48.0652 | 0.05951
4178.3281 | 121.9894 | -0.10529 | 121.9666 | -0.012131 | 0.10181 | 0.092734 | 0.069037 | 0.0025079 | 0.029036 | 0.033934 | -0.005371 | 0.021463 | 0.043062 | -0.0086559 | 0.012121 | 0.023323 | -0.0029843 | 48.0606 | 121.9437 | -0.07782 | 121.6278 | 31.105 | 5.896 | 6.134 | -0.068665 | 0.022888 | -0.068665 | -0.07782 | 0.032043 | 0.027466 | 0.027466 | 0.027466 | -0.022888 | -0.33875 | 31.2103 | 6.2393 | 6.0013 | 6.2119 | 5.9738 | 0.036621 | -121.9437 | -122.0444 | 0.13733 | 0.13275 | 0.13275 | 0.096131 | 0.096131 | 31.1829 | 121.7056 | 0.10071 | -0.009155 | 122.0215 | 0.091553 | 122.049 | 0.12817 | -122.0444 | -122.0352 | 121.7331 | 0.027466 | 48.1659 | 0.036621
4180.0938 | 122.1039 | -0.054932 | 121.9666 | -0.01976 | 0.10074 | 0.092093 | 0.069464 | -0.0015509 | 0.032026 | 0.035857 | -0.005371 | 0.019326 | 0.040926 | -0.019551 | 0.014257 | 0.024605 | -0.0036253 | 48.1979 | 121.9025 | -0.032043 | 121.7697 | 31.3614 | 6.3538 | 6.1707 | 0.09613 | -0.018311 | -0.022888 | 0.041199 | 0.16479 | 0.15564 | 0.11902 | 0.022889 | -0.064087 | -0.19684 | 31.4163 | 6.2256 | 6.4087 | 6.2027 | 6.3858 | 0.032044 | -121.9849 | -121.9254 | 0.21973 | 0.17395 | 0.21057 | 0.14191 | 0.17853 | 31.3934 | 121.8018 | 0.18768 | 0.064087 | 121.9345 | 0.004577 | 121.9574 | 0.036621 | -121.9986 | -121.9894 | 121.8246 | 0.096131 | 48.2529 | 0.15106
4181.8438 | 121.9986 | -0.086975 | 121.9849 | -0.012131 | 0.10501 | 0.093161 | 0.072668 | -0.00026906 | 0.031813 | 0.036284 | -0.0084228 | 0.024026 | 0.041353 | -0.017628 | 0.016821 | 0.025246 | 0.00086095 | 48.0331 | 121.9574 | -0.07782 | 121.6644 | 31.5079 | 6.0837 | 6.0333 | -0.050354 | 0.018311 | -0.041199 | -0.041199 | 0.022888 | -0.013733 | 0.036621 | 0.009155 | -0.027466 | -0.32043 | 31.5948 | 6.1203 | 6.1707 | 6.1111 | 6.1615 | 0.045776 | -121.9666 | -122.0261 | 0.10986 | 0.1236 | 0.073242 | 0.07782 | 0.027466 | 31.5857 | 121.7422 | 0.064087 | 0 | 122.0352 | 0.05951 | 122.0444 | 0.10529 | -122.0627 | -122.0261 | 121.7514 | 0.045776 | 48.1201 | 0.036621
4183.5625 | 122.1313 | -0.054932 | 121.9208 | -0.012131 | 0.10565 | 0.096152 | 0.070532 | 0.0035761 | 0.032667 | 0.037566 | -0.0084228 | 0.020608 | 0.040071 | -0.011647 | 0.013403 | 0.02546 | -0.00084805 | 48.5184 | 121.9208 | -0.036621 | 121.7606 | 31.9656 | 6.3721 | 6.2531 | 0.10529 | -0.022888 | -0.013733 | 0.07782 | 0.17395 | 0.12817 | 0.15564 | 0.018311 | 0 | -0.16022 | 32.0206 | 6.308 | 6.427 | 6.2897 | 6.4087 | 0.041199 | -121.9437 | -121.843 | 0.22888 | 0.21057 | 0.18311 | 0.16937 | 0.14191 | 32.0023 | 121.7972 | 0.18768 | 0.091553 | 121.9574 | -0.009155 | 121.9757 | 0.032044 | -121.9574 | -121.9345 | 121.8155 | 0.13275 | 48.5733 | 0.16022
4185.3281 | 122.0078 | -0.11444 | 121.9574 | -0.012131 | 0.10629 | 0.09487 | 0.073736 | 0.0022943 | 0.032881 | 0.038634 | -0.0084228 | 0.020608 | 0.042208 | -0.012288 | 0.015325 | 0.024178 | -0.0070433 | 48.436 | 121.9666 | -0.073242 | 121.6827 | 32.1121 | 6.4224 | 6.1981 | -0.013733 | 0.013733 | -0.050354 | -0.036621 | 0.045776 | 0.009155 | 0.054932 | 0.041199 | 0.009156 | -0.27466 | 32.2266 | 6.3126 | 6.5369 | 6.2714 | 6.4957 | 0.064087 | -121.9437 | -121.994 | 0.16022 | 0.16937 | 0.1236 | 0.10529 | 0.059509 | 32.1854 | 121.756 | 0.09613 | 0.013733 | 122.0398 | 0.064087 | 122.081 | 0.12817 | -122.0306 | -122.0078 | 121.7972 | 0.07782 | 48.5504 | 0.10071
4187.0938 | 122.113 | -0.07782 | 121.9437 | -0.0045011 | 0.10608 | 0.093161 | 0.067968 | 0.00058534 | 0.032454 | 0.041197 | 0.00073235 | 0.020822 | 0.04114 | -0.015919 | 0.015752 | 0.025032 | -0.0046933 | 48.3673 | 121.8979 | -0.041199 | 121.7834 | 32.0114 | 6.6513 | 6.3904 | 0.11444 | -0.027466 | -0.009155 | 0.054932 | 0.1831 | 0.16479 | 0.14191 | 0.036621 | -0.045777 | -0.16022 | 32.0892 | 6.4682 | 6.7291 | 6.4316 | 6.6925 | 0.068665 | -121.9711 | -121.8887 | 0.26092 | 0.21973 | 0.24261 | 0.15106 | 0.17395 | 32.0526 | 121.8246 | 0.19226 | 0.064087 | 121.9391 | -0.018311 | 121.9757 | 0.050354 | -121.9849 | -121.9528 | 121.8613 | 0.13275 | 48.4451 | 0.19226
4188.8594 | 122.1085 | -0.059509 | 121.9299 | -0.0045011 | 0.10971 | 0.095724 | 0.069677 | 0.0031487 | 0.035444 | 0.041197 | -0.0084228 | 0.022958 | 0.04114 | -0.018055 | 0.012762 | 0.026741 | -0.0064023 | 48.4039 | 121.9208 | -0.036621 | 121.7651 | 32.1121 | 6.6605 | 6.3171 | 0.1236 | -0.032043 | 0 | 0.07782 | 0.17395 | 0.13275 | 0.14648 | 0.022888 | -0.009156 | -0.16479 | 32.1716 | 6.3766 | 6.72 | 6.3538 | 6.6971 | 0.059509 | -121.962 | -121.8521 | 0.23346 | 0.20599 | 0.19226 | 0.14648 | 0.13275 | 32.1487 | 121.8018 | 0.17395 | 0.07782 | 121.9574 | -0.032043 | 121.9803 | 0.027466 | -121.9666 | -121.9299 | 121.8246 | 0.13733 | 48.4634 | 0.1831
4190.5781 | 121.9757 | -0.10986 | 121.962 | -0.0045011 | 0.11228 | 0.096365 | 0.072668 | 0.0010125 | 0.037581 | 0.035857 | -0.0023192 | 0.022958 | 0.041567 | -0.012715 | 0.015539 | 0.024391 | 0.00086095 | 48.4634 | 121.9803 | -0.059509 | 121.6461 | 32.5836 | 6.5231 | 6.2851 | -0.091553 | 0.018311 | -0.050354 | -0.068665 | 0.022888 | -0.022888 | 0.054932 | 0.050354 | 0.018311 | -0.31586 | 32.6935 | 6.395 | 6.633 | 6.3446 | 6.5826 | 0.059509 | -121.9437 | -122.0306 | 0.13275 | 0.16479 | 0.086975 | 0.10529 | 0.027466 | 32.6431 | 121.7056 | 0.073242 | -0.018311 | 122.0398 | 0.068665 | 122.0901 | 0.12817 | -122.0215 | -122.0123 | 121.756 | 0.041198 | 48.5733 | 0.01831
4192.3594 | 122.0856 | -0.068665 | 121.9116 | -0.02739 | 0.11164 | 0.097861 | 0.073095 | 0.0012261 | 0.037153 | 0.040984 | -0.014526 | 0.021463 | 0.041567 | -0.012929 | 0.01618 | 0.025032 | -0.0057615 | 48.4863 | 121.9666 | -0.064087 | 121.6782 | 32.7942 | 6.6559 | 6.514 | 0.045776 | -0.009155 | -0.022888 | 0.041199 | 0.12817 | 0.10986 | 0.13733 | 0.004578 | 0.054932 | -0.23346 | 32.8629 | 6.5826 | 6.7245 | 6.5781 | 6.72 | 0.045777 | -121.9208 | -121.8704 | 0.19684 | 0.20599 | 0.17853 | 0.16022 | 0.13275 | 32.8583 | 121.7422 | 0.15106 | 0.064087 | 122.0306 | 0.013733 | 122.0352 | 0.05951 | -121.9757 | -121.9345 | 121.7468 | 0.10986 | 48.555 | 0.11444
4194.1406 | 122.1176 | -0.045776 | 121.9254 | -0.0045011 | 0.11377 | 0.097006 | 0.072027 | 0.0012261 | 0.035658 | 0.040984 | -0.0084228 | 0.021035 | 0.041353 | -0.021687 | 0.01618 | 0.025246 | -0.00042085 | 48.8617 | 121.9162 | -0.050354 | 121.7514 | 32.7759 | 6.4957 | 6.5598 | 0.10071 | -0.018311 | -0.004578 | 0.073242 | 0.14648 | 0.1236 | 0.14648 | -0.004578 | -0.009155 | -0.17395 | 32.8217 | 6.6055 | 6.5414 | 6.6101 | 6.546 | 0.041198 | -121.9437 | -121.8521 | 0.19226 | 0.19226 | 0.16937 | 0.15106 | 0.12817 | 32.8262 | 121.8018 | 0.15106 | 0.07782 | 121.9666 | -0.013733 | 121.962 | 0.027465 | -121.9757 | -121.9299 | 121.7972 | 0.11902 | 48.9075 | 0.14648
4195.9062 | 122.0261 | -0.082397 | 121.9849 | -0.0045011 | 0.11142 | 0.095511 | 0.070318 | -0.0017645 | 0.037581 | 0.041624 | -0.0084228 | 0.023172 | 0.043276 | -0.015492 | 0.015325 | 0.023751 | -0.0061887 | 48.7106 | 121.962 | -0.086975 | 121.6873 | 33.1558 | 6.7612 | 6.5872 | 0.022888 | 0.013733 | -0.045776 | -0.004578 | 0.10529 | 0.050354 | 0.086975 | -0.004578 | -0.022888 | -0.29755 | 33.2382 | 6.6696 | 6.8436 | 6.6742 | 6.8481 | 0.036621 | -121.9711 | -121.9894 | 0.18768 | 0.16937 | 0.13275 | 0.13275 | 0.09613 | 33.2428 | 121.7743 | 0.15106 | 0.041198 | 122.0489 | 0.059509 | 122.0444 | 0.09613 | -122.0718 | -122.0306 | 121.7697 | 0.077819 | 48.793 | 0.10528
4197.625 | 121.9849 | -0.10071 | 121.9528 | -0.012131 | 0.11698 | 0.097006 | 0.072455 | -0.0011237 | 0.037153 | 0.044402 | -0.005371 | 0.021463 | 0.041994 | -0.014638 | 0.016821 | 0.024178 | -0.0025571 | 48.7656 | 121.9666 | -0.082397 | 121.6324 | 33.4717 | 6.8619 | 6.5643 | -0.054932 | 0.013733 | -0.036621 | -0.054932 | 0.009155 | -0.004578 | 0.036621 | 0.018311 | 0.013733 | -0.32044 | 33.5724 | 6.665 | 6.9626 | 6.6467 | 6.9443 | 0.064087 | -121.9391 | -122.0078 | 0.10986 | 0.13733 | 0.09613 | 0.073242 | 0.032043 | 33.5541 | 121.7148 | 0.045776 | -0.018311 | 122.049 | 0.050354 | 122.0673 | 0.11444 | -122.0352 | -121.9894 | 121.7331 | 0.045776 | 48.8663 | 0.045776
4199.4062 | 122.0856 | -0.059509 | 121.9208 | -0.01976 | 0.11313 | 0.097433 | 0.069464 | 0.00037174 | 0.034376 | 0.040129 | -0.005371 | 0.019967 | 0.040499 | -0.013997 | 0.014043 | 0.0261 | -0.0019163 | 48.9716 | 121.9116 | -0.050354 | 121.756 | 33.5678 | 6.9122 | 6.7474 | 0.091553 | -0.018311 | -0.018311 | 0.041199 | 0.16022 | 0.14191 | 0.12817 | 0.009155 | -0.009155 | -0.16479 | 33.6273 | 6.8069 | 6.9717 | 6.7978 | 6.9626 | 0.041198 | -121.9391 | -121.8796 | 0.21973 | 0.18768 | 0.20142 | 0.14649 | 0.16022 | 33.6182 | 121.8063 | 0.17853 | 0.05951 | 121.962 | 0 | 121.9711 | 0.041198 | -121.9711 | -121.9391 | 121.8155 | 0.10071 | 49.0311 | 0.15106
4201.1094 | 122.0535 | -0.086975 | 121.9345 | -0.012131 | 0.11463 | 0.095297 | 0.070105 | -0.0019781 | 0.037794 | 0.043974 | -0.011475 | 0.020395 | 0.039431 | -0.021901 | 0.012548 | 0.025673 | -0.0014891 | 49.054 | 121.9345 | -0.041199 | 121.6919 | 33.7051 | 6.5689 | 6.839 | 0.009155 | -0.018311 | -0.027466 | -0.004578 | 0.10529 | 0.086975 | 0.09613 | 0.045776 | 0 | -0.24261 | 33.7921 | 6.926 | 6.6559 | 6.8802 | 6.6101 | 0.059509 | -121.9528 | -121.9391 | 0.19226 | 0.1831 | 0.17395 | 0.1236 | 0.11444 | 33.7463 | 121.7331 | 0.13275 | 0.022888 | 121.9757 | 0.009155 | 122.0215 | 0.068664 | -121.9757 | -121.962 | 121.7789 | 0.082397 | 49.1409 | 0.09613
4202.875 | 122.0306 | -0.10986 | 121.9666 | -0.012131 | 0.11569 | 0.095297 | 0.074164 | 0.0027215 | 0.036085 | 0.042052 | -0.005371 | 0.022103 | 0.040712 | -0.012929 | 0.014898 | 0.022042 | -0.0074705 | 49.1135 | 121.9299 | -0.064087 | 121.6965 | 33.8882 | 6.7795 | 6.8848 | 0.027466 | 0.018311 | -0.027466 | -0.009155 | 0.086975 | 0.064087 | 0.086975 | 0.045776 | -0.036621 | -0.27008 | 33.9981 | 6.9946 | 6.8893 | 6.9489 | 6.8436 | 0.082397 | -121.9482 | -121.9757 | 0.19684 | 0.19684 | 0.17395 | 0.11444 | 0.091553 | 33.9523 | 121.7606 | 0.11444 | 0.018311 | 121.994 | 0.045777 | 122.0398 | 0.12817 | -122.0306 | -121.994 | 121.8063 | 0.10071 | 49.2233 | 0.13733
4204.6562 | 122.0718 | -0.086975 | 121.9574 | 0.0031279 | 0.1189 | 0.098288 | 0.070318 | 0.0010125 | 0.037581 | 0.042906 | -0.0023192 | 0.018045 | 0.039431 | -0.022114 | 0.012121 | 0.023537 | 0.0017153 | 49.2371 | 121.9299 | -0.027466 | 121.7148 | 33.847 | 7.0312 | 6.9992 | 0.054932 | -0.018311 | -0.018311 | 0.009155 | 0.10986 | 0.09613 | 0.09613 | 0.059509 | -0.027465 | -0.24261 | 33.934 | 7.0862 | 7.1182 | 7.0267 | 7.0587 | 0.068664 | -121.9757 | -121.9482 | 0.19684 | 0.1831 | 0.1831 | 0.11444 | 0.11444 | 33.8745 | 121.7422 | 0.12817 | 0.027466 | 121.9574 | 0 | 122.0169 | 0.068664 | -121.9849 | -121.9757 | 121.8018 | 0.09613 | 49.324 | 0.14191
4206.4219 | 122.0215 | -0.10529 | 121.9757 | -0.012131 | 0.1189 | 0.096152 | 0.074164 | 0.0057123 | 0.036726 | 0.044402 | -0.005371 | 0.020608 | 0.041353 | -0.010579 | 0.014684 | 0.023964 | -0.0044797 | 49.1135 | 121.9437 | -0.09613 | 121.6461 | 34.053 | 7.0541 | 7.0679 | -0.045776 | 0.018311 | -0.041199 | -0.054932 | 0.059509 | 0.041199 | 0.064087 | 0.009156 | -0.032043 | -0.32959 | 34.1583 | 7.1732 | 7.1594 | 7.164 | 7.1503 | 0.064087 | -121.9574 | -122.0306 | 0.16479 | 0.16937 | 0.14649 | 0.10529 | 0.082398 | 34.1492 | 121.7422 | 0.10071 | -0.013733 | 122.0398 | 0.05951 | 122.049 | 0.1236 | -122.0718 | -122.0169 | 121.7514 | 0.050354 | 49.2188 | 0.05951
4208.2031 | 122.0901 | -0.059509 | 121.9391 | -0.01976 | 0.11676 | 0.099356 | 0.070532 | -0.0015509 | 0.037153 | 0.040343 | -0.0084228 | 0.020608 | 0.040926 | -0.022542 | 0.011053 | 0.024819 | -0.0064023 | 48.9853 | 121.8979 | -0.050354 | 121.7056 | 33.9844 | 7.0496 | 7.164 | 0.045776 | -0.004578 | -0.022888 | 0.027466 | 0.14648 | 0.14191 | 0.12817 | 0.009155 | -0.041199 | -0.23346 | 34.0439 | 7.2235 | 7.1091 | 7.2144 | 7.0999 | 0.036621 | -121.9437 | -121.9116 | 0.20599 | 0.18768 | 0.20142 | 0.15106 | 0.16479 | 34.0347 | 121.756 | 0.16937 | 0.050354 | 121.9482 | 0.01831 | 121.9574 | 0.054931 | -121.9894 | -121.962 | 121.7651 | 0.086975 | 49.0448 | 0.10528
4209.9062 | 122.0444 | -0.068665 | 121.9345 | -0.01976 | 0.12146 | 0.098929 | 0.070746 | -0.00026906 | 0.040358 | 0.045683 | -0.005371 | 0.020395 | 0.041353 | -0.020833 | 0.013403 | 0.021614 | -0.0051205 | 49.3011 | 121.9025 | -0.050354 | 121.701 | 34.2133 | 7.3013 | 7.0908 | 0.022888 | -0.013733 | -0.013733 | 0 | 0.11902 | 0.086975 | 0.091553 | 0.018311 | -0.032043 | -0.23346 | 34.2819 | 7.1594 | 7.37 | 7.1411 | 7.3517 | 0.054932 | -121.9482 | -121.9345 | 0.18768 | 0.16022 | 0.15564 | 0.10529 | 0.10071 | 34.2636 | 121.7514 | 0.13275 | 0.013733 | 121.9528 | 0 | 121.9711 | 0.054932 | -121.9849 | -121.9482 | 121.7697 | 0.068665 | 49.3698 | 0.091553
4211.6719 | 121.9666 | -0.1236 | 121.9666 | -0.0045011 | 0.12253 | 0.098288 | 0.072241 | -0.0021919 | 0.037794 | 0.045897 | -0.0084228 | 0.021463 | 0.042208 | -0.0075879 | 0.013616 | 0.024178 | -0.0040525 | 49.205 | 121.962 | -0.07782 | 121.6415 | 34.3552 | 7.2418 | 7.3242 | -0.041199 | 0.032043 | -0.064087 | -0.07782 | 0.041199 | 0.013733 | 0.027466 | 0.045776 | -0.004578 | -0.32501 | 34.4788 | 7.4478 | 7.3654 | 7.402 | 7.3196 | 0.059509 | -121.9345 | -122.0444 | 0.16479 | 0.15106 | 0.13733 | 0.091553 | 0.07782 | 34.433 | 121.7194 | 0.10529 | -0.013733 | 122.0398 | 0.09613 | 122.0856 | 0.15564 | -122.0444 | -122.0306 | 121.7651 | 0.045776 | 49.3286 | 0.082397
4213.4531 | 122.0535 | -0.064087 | 121.9299 | -0.012131 | 0.12552 | 0.10085 | 0.073523 | -0.00091006 | 0.038862 | 0.045256 | 0.00073235 | 0.020822 | 0.042635 | -0.013997 | 0.013616 | 0.023537 | -0.0040525 | 49.4064 | 121.8933 | -0.050354 | 121.7148 | 34.6619 | 7.489 | 7.3837 | 0.036621 | -0.009155 | -0.022888 | 0 | 0.09613 | 0.091553 | 0.082397 | 0.013733 | -0.036621 | -0.21515 | 34.726 | 7.4478 | 7.5531 | 7.4341 | 7.5394 | 0.041199 | -121.9391 | -121.9299 | 0.16022 | 0.14648 | 0.15564 | 0.10528 | 0.11444 | 34.7122 | 121.7651 | 0.11902 | 0.022888 | 121.9437 | 0.013733 | 121.9574 | 0.054932 | -121.9803 | -121.9528 | 121.7789 | 0.064087 | 49.4705 | 0.10071
4215.1562 | 122.0673 | -0.07782 | 121.9391 | -0.012131 | 0.12723 | 0.10064 | 0.073523 | 0.00079894 | 0.040358 | 0.047392 | -0.005371 | 0.021463 | 0.040499 | -0.015919 | 0.016393 | 0.023751 | -0.0025571 | 49.5392 | 121.9528 | -0.082397 | 121.6415 | 35.1654 | 7.2739 | 7.338 | -0.004578 | 0.009155 | -0.036621 | 0.027466 | 0.082397 | 0.073242 | 0.09613 | -0.004577 | 0.013733 | -0.29755 | 35.2432 | 7.4158 | 7.3517 | 7.4203 | 7.3563 | 0.041199 | -121.9299 | -121.9116 | 0.16022 | 0.17395 | 0.15106 | 0.13275 | 0.10986 | 35.2478 | 121.7239 | 0.11902 | 0.064087 | 122.0352 | 0.045776 | 122.0306 | 0.086975 | -122.0215 | -121.9757 | 121.7194 | 0.10529 | 49.617 | 0.073242
4216.9219 | 121.9894 | -0.09613 | 121.9574 | -0.0045011 | 0.12787 | 0.10042 | 0.0716 | -0.00091006 | 0.041212 | 0.048888 | -0.0084228 | 0.021676 | 0.041567 | -0.016987 | 0.011694 | 0.025032 | -0.0025571 | 49.7726 | 121.9162 | -0.045776 | 121.7102 | 35.3531 | 7.4799 | 7.2464 | 0.009155 | -0.004578 | -0.036621 | -0.041199 | 0.064087 | 0.041199 | 0.036621 | 0.050354 | -0.041198 | -0.24719 | 35.4492 | 7.3425 | 7.576 | 7.2922 | 7.5256 | 0.059509 | -121.962 | -121.9986 | 0.16022 | 0.13275 | 0.13733 | 0.073242 | 0.07782 | 35.3989 | 121.756 | 0.10071 | -0.004578 | 121.962 | 0.032043 | 122.0123 | 0.091552 | -122.0032 | -121.994 | 121.8063 | 0.054931 | 49.8688 | 0.10528
4218.7031 | 122.0947 | -0.059509 | 121.9254 | 0.0031279 | 0.13172 | 0.10277 | 0.073523 | 0.0027215 | 0.042494 | 0.045042 | -0.005371 | 0.021463 | 0.039431 | -0.016774 | 0.012762 | 0.024391 | -0.0057615 | 49.9146 | 121.9345 | -0.054932 | 121.7194 | 36.1084 | 7.7271 | 7.5989 | 0.09613 | -0.013733 | -0.013733 | 0.059509 | 0.16022 | 0.10986 | 0.14191 | 0.004577 | 0.009155 | -0.20599 | 36.1679 | 7.6584 | 7.7866 | 7.6538 | 7.782 | 0.045776 | -121.9391 | -121.8658 | 0.21973 | 0.20142 | 0.16937 | 0.15564 | 0.1236 | 36.1633 | 121.7743 | 0.17395 | 0.073242 | 121.9894 | 0 | 121.994 | 0.045776 | -121.9803 | -121.9391 | 121.7789 | 0.11902 | 49.9741 | 0.15564
4220.4688 | 122.0169 | -0.09613 | 121.9391 | -0.012131 | 0.13172 | 0.1032 | 0.070746 | -5.5462e-05 | 0.043348 | 0.046538 | -0.0084228 | 0.024453 | 0.041353 | -0.0090833 | 0.014684 | 0.021401 | -0.0036253 | 50.1343 | 121.9391 | -0.054932 | 121.6873 | 35.6689 | 7.8781 | 7.7454 | 0.032043 | 0.018311 | -0.036621 | 0 | 0.10071 | 0.036621 | 0.064087 | 0.041198 | 0 | -0.25177 | 35.7651 | 7.8415 | 7.9742 | 7.8003 | 7.933 | 0.059509 | -121.9208 | -121.9391 | 0.19684 | 0.16022 | 0.13275 | 0.10071 | 0.073242 | 35.7239 | 121.7422 | 0.13733 | 0.036621 | 121.994 | 0.054932 | 122.0352 | 0.11444 | -121.994 | -121.9757 | 121.7834 | 0.09613 | 50.2304 | 0.12817
4222.1719 | 122.0123 | -0.07782 | 121.9437 | -0.012131 | 0.13257 | 0.10256 | 0.073095 | 0.0027215 | 0.043989 | 0.046751 | -0.011475 | 0.021676 | 0.041567 | -0.015278 | 0.015112 | 0.023964 | 0.00064735 | 50.0793 | 121.9299 | -0.068665 | 121.6827 | 36.4517 | 7.6355 | 7.6813 | 0.036621 | 0.018311 | -0.018311 | 0.009155 | 0.10071 | 0.073242 | 0.086975 | 0.009155 | -0.013733 | -0.26093 | 36.5295 | 7.7591 | 7.7133 | 7.7499 | 7.7042 | 0.059509 | -121.9254 | -121.9345 | 0.17853 | 0.16479 | 0.15106 | 0.10529 | 0.091553 | 36.5204 | 121.7514 | 0.11902 | 0.027466 | 121.9986 | 0.036622 | 122.0078 | 0.096131 | -122.0123 | -121.962 | 121.7606 | 0.086975 | 50.1572 | 0.11444
4223.9375 | 121.9574 | -0.091553 | 121.9208 | -0.01976 | 0.13642 | 0.10491 | 0.073309 | 0.0035761 | 0.040999 | 0.049956 | -0.005371 | 0.022531 | 0.043276 | -0.01656 | 0.015325 | 0.026741 | -0.0014891 | 50.3586 | 121.9666 | -0.086975 | 121.6049 | 36.5891 | 7.6492 | 7.7316 | -0.054932 | 0.022888 | -0.054932 | -0.050354 | 0.018311 | -0.009155 | 0.041199 | 0.004578 | 0.045777 | -0.31586 | 36.6806 | 7.8232 | 7.7408 | 7.8186 | 7.7362 | 0.036621 | -121.8979 | -121.9711 | 0.10986 | 0.13275 | 0.082398 | 0.096131 | 0.045777 | 36.676 | 121.6919 | 0.073243 | 0.004578 | 122.0535 | 0.07782 | 122.0581 | 0.11444 | -122.0078 | -121.9757 | 121.6965 | 0.041199 | 50.4501 | 0.036621
4225.7031 | 122.0444 | -0.091553 | 121.9254 | -0.0045011 | 0.13385 | 0.10384 | 0.072241 | -0.0030463 | 0.043562 | 0.050383 | -0.0084228 | 0.019113 | 0.039858 | -0.017842 | 0.01383 | 0.024178 | -0.0061887 | 50.6653 | 121.9162 | -0.050354 | 121.6736 | 37.1658 | 8.0109 | 7.9147 | 0.022888 | -0.022888 | -0.009155 | -0.009155 | 0.10986 | 0.086975 | 0.091553 | 0.041199 | -0.009155 | -0.25177 | 37.2574 | 8.0063 | 8.1024 | 7.9651 | 8.0612 | 0.082398 | -121.9482 | -121.9345 | 0.20142 | 0.18311 | 0.17853 | 0.10071 | 0.09613 | 37.2162 | 121.7239 | 0.11902 | 0 | 121.9666 | -0.013733 | 122.0078 | 0.068665 | -121.9757 | -121.9345 | 121.7651 | 0.082398 | 50.7568 | 0.11444
4227.4844 | 122.0261 | -0.082397 | 121.9528 | -0.02739 | 0.13855 | 0.10641 | 0.074377 | 0.0044305 | 0.046553 | 0.052092 | -0.0084228 | 0.023385 | 0.042849 | -0.013569 | 0.015112 | 0.024391 | -0.0017027 | 50.647 | 121.9299 | -0.068665 | 121.6782 | 37.7563 | 8.194 | 7.8735 | 0.041199 | 0.022888 | -0.022888 | 0 | 0.10071 | 0.064087 | 0.086975 | 0.013732 | -0.022888 | -0.27466 | 37.8387 | 7.9559 | 8.2764 | 7.9422 | 8.2626 | 0.059509 | -121.9299 | -121.9528 | 0.18311 | 0.16937 | 0.14648 | 0.10986 | 0.086975 | 37.825 | 121.7468 | 0.1236 | 0.022888 | 121.9986 | 0.045776 | 122.0123 | 0.10528 | -122.0215 | -121.9757 | 121.7606 | 0.082397 | 50.7294 | 0.1236
4229.2031 | 122.1039 | -0.068665 | 121.9208 | -0.01976 | 0.13941 | 0.10555 | 0.074164 | 0.0014397 | 0.045912 | 0.052946 | -0.0023192 | 0.019754 | 0.041567 | -0.010151 | 0.012334 | 0.024819 | -0.00084805 | 50.7614 | 121.8933 | -0.036621 | 121.7285 | 38.1271 | 8.2764 | 8.0704 | 0.086975 | 0 | -0.022888 | 0.082397 | 0.16022 | 0.12817 | 0.15106 | 0.032044 | -0.027465 | -0.19226 | 38.1958 | 8.139 | 8.345 | 8.107 | 8.313 | 0.045777 | -121.9208 | -121.8384 | 0.22888 | 0.21973 | 0.19684 | 0.17395 | 0.15106 | 38.1638 | 121.7651 | 0.1831 | 0.10528 | 121.9299 | 0.022888 | 121.962 | 0.068665 | -121.9574 | -121.9437 | 121.7972 | 0.15106 | 50.8301 | 0.15564
4230.9844 | 122.0169 | -0.086975 | 121.962 | -0.01976 | 0.13898 | 0.1032 | 0.073309 | 0.0020807 | 0.046553 | 0.048888 | -0.0023192 | 0.023812 | 0.04178 | -0.013997 | 0.012762 | 0.024178 | 0.0015017 | 50.6561 | 121.9391 | -0.07782 | 121.6644 | 37.8662 | 8.4274 | 8.0338 | -0.013733 | 0.022888 | -0.018311 | -0.027466 | 0.091553 | 0.050354 | 0.07782 | 0.009155 | -0.022888 | -0.29755 | 37.9532 | 8.1207 | 8.5144 | 8.1116 | 8.5052 | 0.068664 | -121.9391 | -121.9894 | 0.17853 | 0.16479 | 0.13733 | 0.096131 | 0.068665 | 37.944 | 121.7422 | 0.10986 | -0.009155 | 122.0169 | 0.041199 | 122.0261 | 0.10986 | -122.0398 | -121.9803 | 121.7514 | 0.059509 | 50.7431 | 0.073242
4232.75 | 122.0535 | -0.054932 | 121.9299 | -0.0045011 | 0.14218 | 0.10662 | 0.073523 | 0.0022943 | 0.04698 | 0.053374 | -0.011475 | 0.019326 | 0.039858 | -0.014851 | 0.013616 | 0.025887 | -0.0031979 | 50.9949 | 121.9208 | -0.027466 | 121.7239 | 38.2507 | 8.5968 | 8.3771 | 0.10529 | -0.036621 | -0.004578 | 0.027466 | 0.12817 | 0.11444 | 0.11444 | 0.027466 | -0.009156 | -0.20599 | 38.3057 | 8.432 | 8.6517 | 8.4045 | 8.6243 | 0.050354 | -121.9666 | -121.9025 | 0.18311 | 0.16937 | 0.16937 | 0.11902 | 0.11902 | 38.2782 | 121.7514 | 0.13275 | 0.032044 | 121.9482 | -0.032043 | 121.9757 | 0.018311 | -121.9574 | -121.9345 | 121.7789 | 0.082398 | 51.0498 | 0.16022
4234.5312 | 121.9666 | -0.10529 | 121.9482 | -0.01976 | 0.14325 | 0.10512 | 0.073736 | -0.00069646 | 0.046766 | 0.054655 | -0.0084228 | 0.021676 | 0.041353 | -0.017628 | 0.01148 | 0.025032 | -0.00042085 | 50.8759 | 121.9345 | -0.086975 | 121.6278 | 38.5071 | 8.4457 | 8.2764 | -0.050354 | 0.018311 | -0.027466 | -0.082397 | 0.041199 | 0.018311 | 0.022888 | 0.018311 | -0.013733 | -0.32043 | 38.6124 | 8.3817 | 8.551 | 8.3633 | 8.5327 | 0.07782 | -121.9299 | -122.0306 | 0.14649 | 0.12817 | 0.1236 | 0.050354 | 0.045777 | 38.5941 | 121.7148 | 0.068665 | -0.054931 | 122.0215 | 0.045777 | 122.0398 | 0.1236 | -122.0352 | -121.9757 | 121.7331 | 0.022889 | 50.9811 | 0.054932
4236.2969 | 122.0993 | -0.068665 | 121.907 | -0.012131 | 0.14624 | 0.10641 | 0.074377 | -0.00091006 | 0.050398 | 0.051237 | -0.0084228 | 0.020395 | 0.039644 | -0.014424 | 0.015539 | 0.024819 | -0.0042661 | 51.4069 | 121.9025 | -0.036621 | 121.7377 | 38.4201 | 8.7479 | 8.3496 | 0.09613 | -0.022888 | -0.009155 | 0.073242 | 0.17395 | 0.12817 | 0.14648 | 0.032044 | -0.004577 | -0.16937 | 38.4888 | 8.4183 | 8.8165 | 8.3862 | 8.7845 | 0.05951 | -121.9299 | -121.8338 | 0.24261 | 0.21515 | 0.19684 | 0.15564 | 0.13733 | 38.4567 | 121.7743 | 0.1831 | 0.082397 | 121.9391 | -0.013733 | 121.9711 | 0.045777 | -121.9437 | -121.9162 | 121.8063 | 0.14191 | 51.4755 | 0.16479
4238.0625 | 122.0078 | -0.086975 | 121.9528 | -0.012131 | 0.14795 | 0.10598 | 0.075445 | 0.0020807 | 0.04933 | 0.054869 | -0.005371 | 0.021676 | 0.04178 | -0.011006 | 0.013616 | 0.023537 | -0.0036253 | 51.3519 | 121.9208 | -0.064087 | 121.6782 | 39.3356 | 8.551 | 8.6197 | 0.036621 | 0.004578 | -0.027466 | -0.022888 | 0.10071 | 0.054932 | 0.086975 | 0.022888 | -0.032044 | -0.27466 | 39.4226 | 8.7067 | 8.638 | 8.6838 | 8.6151 | 0.059509 | -121.9482 | -121.9757 | 0.18768 | 0.17395 | 0.14191 | 0.11444 | 0.082398 | 39.3997 | 121.7422 | 0.12817 | 0.004578 | 121.9849 | 0.032044 | 122.0078 | 0.091553 | -122.0169 | -121.9803 | 121.7651 | 0.064087 | 51.4389 | 0.1236
4239.8281 | 122.0718 | -0.059509 | 121.9254 | -0.01976 | 0.15051 | 0.1079 | 0.075659 | 0.0018671 | 0.050184 | 0.053801 | -0.0023192 | 0.019113 | 0.043489 | -0.013997 | 0.015752 | 0.023751 | -0.0034117 | 51.5121 | 121.9025 | -0.064087 | 121.6736 | 39.0015 | 8.9905 | 8.6288 | 0.059509 | -0.004578 | -0.018311 | 0.059509 | 0.14648 | 0.11444 | 0.14191 | -0.004578 | -0.022888 | -0.25177 | 39.061 | 8.6884 | 9.05 | 8.6929 | 9.0546 | 0.041198 | -121.9299 | -121.8658 | 0.20599 | 0.20142 | 0.17395 | 0.16022 | 0.13275 | 39.0656 | 121.7377 | 0.16479 | 0.07782 | 121.9666 | 0.013733 | 121.962 | 0.054931 | -121.9894 | -121.9437 | 121.7331 | 0.11902 | 51.5717 | 0.11902
4241.5312 | 121.9711 | -0.11902 | 121.962 | -0.012131 | 0.15372 | 0.10833 | 0.074804 | 0.0037897 | 0.052534 | 0.053374 | -0.005371 | 0.022744 | 0.041994 | -0.0084423 | 0.012975 | 0.022042 | -0.0040525 | 51.8143 | 121.9299 | -0.07782 | 121.5775 | 38.974 | 9.0179 | 8.7524 | -0.064087 | 0.027466 | -0.050354 | -0.068665 | 0.009155 | -0.018311 | 0.032043 | 0.041199 | -0.032043 | -0.38452 | 39.093 | 8.8715 | 9.137 | 8.8303 | 9.0958 | 0.068665 | -121.9345 | -122.0306 | 0.12817 | 0.15106 | 0.10071 | 0.082397 | 0.032043 | 39.0518 | 121.6553 | 0.059509 | -0.018311 | 122.0078 | 0.07782 | 122.049 | 0.14649 | -122.0398 | -122.0123 | 121.6965 | 0.050354 | 51.9333 | 0.054932
4243.2969 | 122.081 | -0.068665 | 121.9299 | -0.012131 | 0.14881 | 0.10662 | 0.072455 | 0.00079894 | 0.047407 | 0.055296 | -0.0084228 | 0.020822 | 0.040071 | -0.014424 | 0.011266 | 0.023537 | -0.00084805 | 51.6678 | 121.8658 | -0.045776 | 121.6919 | 39.2761 | 9.3567 | 8.8669 | 0.054932 | -0.013733 | -0.032043 | 0.041199 | 0.15564 | 0.13733 | 0.12817 | 0.022889 | -0.064087 | -0.23804 | 39.3448 | 8.9355 | 9.4254 | 8.9127 | 9.4025 | 0.036622 | -121.9437 | -121.8887 | 0.22431 | 0.19684 | 0.20599 | 0.16022 | 0.16937 | 39.3219 | 121.7377 | 0.18768 | 0.073242 | 121.9116 | 0.01831 | 121.9345 | 0.054932 | -121.9757 | -121.962 | 121.7606 | 0.10986 | 51.7365 | 0.1236
4245.0156 | 122.0123 | -0.082397 | 121.9528 | -0.012131 | 0.16632 | 0.11025 | 0.075232 | 0.0037897 | 0.060225 | 0.058287 | -0.005371 | 0.021463 | 0.043276 | -0.0088695 | 0.013189 | 0.021401 | -0.0040525 | 54.2542 | 121.8933 | -0.064087 | 121.6782 | 39.505 | 12.323 | 8.9127 | 0.041199 | 0.018311 | -0.050354 | -0.009155 | 0.09613 | 0.064087 | 0.09613 | 0.01831 | -0.059509 | -0.27466 | 39.5874 | 8.9951 | 12.4054 | 8.9767 | 12.3871 | 0.032043 | -121.9345 | -121.962 | 0.17853 | 0.17853 | 0.14648 | 0.14648 | 0.11444 | 39.5691 | 121.7422 | 0.14648 | 0.041199 | 121.9574 | 0.068665 | 121.9757 | 0.10071 | -122.0169 | -122.0032 | 121.7606 | 0.073242 | 54.3365 | 0.1236
4246.7812 | 122.1222 | -0.064087 | 121.907 | -0.0045011 | 0.14966 | 0.1282 | -0.0085086 | 0.079412 | 0.085005 | -0.0049454 | -0.0084228 | 0.019754 | 0.040285 | -0.01421 | 0.01383 | 0.022896 | -0.0034117 | 79.3533 | 121.8567 | -0.041199 | 43.8995 | 121.8796 | 110.6552 | 99.7009 | 0.13733 | -0.041199 | 0.018311 | 0.054932 | 0.18768 | 0.16022 | 0.13733 | 0.022888 | -0.050354 | -78.0075 | 121.9437 | 99.765 | 110.7193 | 99.7421 | 110.6964 | 0.082398 | -121.9482 | -121.8521 | 0.25177 | 0.20142 | 0.2243 | 0.11902 | 0.14191 | 121.9208 | 43.9407 | 0.16937 | 0.036621 | 121.8979 | -0.05951 | 121.9208 | 0.022888 | -121.9482 | -121.8887 | 43.9636 | 0.11902 | 79.4174 | 0.20142
4248.5 | 122.0306 | -0.068665 | 121.9116 | -0.0045011 | 0.15393 | 0.12969 | -0.0080814 | 0.081121 | 0.086073 | -0.0032364 | 0.00073235 | 0.020181 | 0.04178 | -0.016133 | 0.012548 | 0.022683 | -0.0027707 | 80.0629 | 121.875 | -0.041199 | 44.1925 | 121.7606 | 112.3993 | 100.264 | 0.036621 | -0.009155 | -0.009155 | -0.004578 | 0.10529 | 0.07782 | 0.09613 | 0.027466 | -0.036621 | -77.7191 | 121.8292 | 100.3326 | 112.468 | 100.3052 | 112.4405 | 0.05951 | -121.9208 | -121.9162 | 0.17395 | 0.16479 | 0.14649 | 0.10528 | 0.086975 | 121.8018 | 44.2337 | 0.11444 | 0.004577 | 121.9162 | 0 | 121.9437 | 0.05951 | -121.9528 | -121.9208 | 44.2612 | 0.064087 | 80.1315 | 0.10529
4250.2656 | 121.9437 | -0.10986 | 121.9391 | -0.0045011 | 0.15927 | 0.12948 | -0.0055178 | 0.077703 | 0.089491 | -0.0019546 | -0.0023192 | 0.021035 | 0.040285 | -0.011433 | 0.015539 | 0.024178 | -0.0046933 | 80.246 | 121.9162 | -0.068665 | 44.1101 | 121.6782 | 112.8021 | 100.4242 | -0.091553 | 0.018311 | -0.041199 | -0.07782 | 0.009155 | -0.032043 | 0.022888 | 0.041198 | -0.022888 | -77.829 | 121.788 | 100.5341 | 112.912 | 100.4929 | 112.8708 | 0.068664 | -121.9208 | -122.0169 | 0.11902 | 0.13275 | 0.07782 | 0.064087 | 0.009156 | 121.7468 | 44.1788 | 0.050354 | -0.036621 | 121.9849 | 0.05951 | 122.0261 | 0.12817 | -122.0078 | -121.9803 | 44.22 | 0.032043 | 80.3558 | 0.01831
4252.0312 | 122.0718 | -0.059509 | 121.8704 | -0.012131 | 0.1612 | 0.13119 | -0.0057314 | 0.082189 | 0.088637 | -0.0040908 | -0.005371 | 0.020395 | 0.039858 | -0.016987 | 0.015112 | 0.02546 | -0.0081113 | 80.191 | 121.9254 | -0.064087 | 44.3573 | 121.7972 | 113.269 | 101.1475 | 0.07782 | -0.009155 | -0.018311 | 0.064087 | 0.15106 | 0.11902 | 0.14648 | -0.004578 | 0.054932 | -77.5131 | 121.8567 | 101.207 | 113.3286 | 101.2115 | 113.3331 | 0.041198 | -121.8796 | -121.8063 | 0.21057 | 0.20599 | 0.17853 | 0.16479 | 0.13733 | 121.8613 | 44.4214 | 0.16937 | 0.082398 | 121.9894 | 0.009156 | 121.9849 | 0.050354 | -121.9345 | -121.8887 | 44.4168 | 0.1236 | 80.2505 | 0.13733
4253.7969 | 121.994 | -0.09613 | 121.9437 | -0.012131 | 0.15778 | 0.13247 | -0.0050906 | 0.083044 | 0.088637 | -0.001741 | -0.0084228 | 0.021035 | 0.043276 | -0.013783 | 0.013616 | 0.024178 | 0.0010745 | 80.278 | 121.9116 | -0.082397 | 44.2841 | 121.7285 | 113.4109 | 101.4313 | -0.018311 | 0.032043 | -0.054932 | -0.027466 | 0.082397 | 0.054932 | 0.086975 | 0.013733 | -0.032044 | -77.6596 | 121.8246 | 101.5274 | 113.5071 | 101.5137 | 113.4933 | 0.041198 | -121.9116 | -121.9711 | 0.17853 | 0.1831 | 0.15106 | 0.14191 | 0.10986 | 121.8109 | 44.3665 | 0.13733 | 0.027466 | 121.994 | 0.086975 | 122.0078 | 0.12817 | -122.0261 | -121.9986 | 44.3802 | 0.068664 | 80.3741 | 0.077819
4255.5625 | 121.9437 | -0.11444 | 121.9299 | -0.01976 | 0.15628 | 0.13161 | -0.0063724 | 0.08283 | 0.087568 | -0.0038772 | -0.005371 | 0.021463 | 0.04114 | -0.011647 | 0.012975 | 0.023323 | -0.0096067 | 80.127 | 121.9116 | -0.068665 | 44.2566 | 121.7285 | 113.6719 | 101.4816 | -0.036621 | 0.009155 | -0.050354 | -0.068665 | 0.041199 | 0.018311 | 0.018311 | 0.045776 | -0.018311 | -77.6733 | 121.843 | 101.5961 | 113.7863 | 101.5503 | 113.7405 | 0.064087 | -121.9208 | -121.9986 | 0.15564 | 0.13275 | 0.13275 | 0.068665 | 0.068665 | 121.7972 | 44.3253 | 0.091553 | -0.018311 | 121.9803 | 0.059509 | 122.0261 | 0.1236 | -121.9986 | -121.9803 | 44.371 | 0.045776 | 80.2414 | 0.07782
4257.3281 | 122.0261 | -0.07782 | 121.9345 | -0.01976 | 0.15799 | 0.13354 | -0.0078676 | 0.079626 | 0.086928 | -0.0040908 | -0.0023192 | 0.021249 | 0.040499 | -0.010151 | 0.013189 | 0.023537 | -0.0038389 | 80.1865 | 121.8704 | -0.036621 | 44.4534 | 121.8384 | 113.9877 | 101.8936 | 0.059509 | -0.009155 | -0.009155 | 0 | 0.12817 | 0.11444 | 0.091553 | 0.041199 | -0.064087 | -77.4811 | 121.9162 | 101.9714 | 114.0656 | 101.9302 | 114.0244 | 0.068665 | -121.9437 | -121.9345 | 0.20599 | 0.16937 | 0.19226 | 0.10071 | 0.1236 | 121.875 | 44.4901 | 0.13733 | 0.009155 | 121.907 | 0 | 121.9482 | 0.068665 | -121.9711 | -121.9437 | 44.5312 | 0.07782 | 80.2643 | 0.13733
4259.0312 | 121.9986 | -0.10529 | 121.9254 | 0.0031279 | 0.15949 | 0.13076 | -0.0072268 | 0.081121 | 0.086714 | -0.002382 | -0.0023192 | 0.022531 | 0.040712 | -0.014638 | 0.01618 | 0.024605 | -0.0089659 | 79.8569 | 121.9254 | -0.07782 | 44.3619 | 121.6965 | 114.0244 | 101.889 | -0.054932 | 0.018311 | -0.064087 | -0.059509 | 0.059509 | 0.032043 | 0.054932 | 0.027466 | 0 | -77.5635 | 121.8018 | 101.9943 | 114.1296 | 101.9669 | 114.1022 | 0.041199 | -121.907 | -121.9849 | 0.16479 | 0.16022 | 0.13733 | 0.11902 | 0.09613 | 121.7743 | 44.4397 | 0.1236 | 0.004578 | 122.0032 | 0.082398 | 122.0306 | 0.1236 | -122.0032 | -121.9894 | 44.4672 | 0.045777 | 79.9622 | 0.050354
4260.7969 | 122.0306 | -0.073242 | 121.9162 | -0.01976 | 0.15842 | 0.13247 | -0.0078676 | 0.081976 | 0.089064 | -0.0038772 | -0.0023192 | 0.018045 | 0.04114 | -0.014851 | 0.013189 | 0.023537 | -0.0014891 | 80.0308 | 121.8521 | -0.054932 | 44.4443 | 121.7743 | 114.267 | 102.2964 | 0.013733 | -0.004578 | -0.027466 | -0.013733 | 0.11444 | 0.09613 | 0.091553 | 0.01831 | -0.064087 | -77.4719 | 121.8475 | 102.3697 | 114.3402 | 102.3514 | 114.3219 | 0.045776 | -121.9208 | -121.9299 | 0.18768 | 0.16479 | 0.16937 | 0.11902 | 0.1236 | 121.8292 | 44.4992 | 0.14191 | 0.013733 | 121.907 | 0.022888 | 121.9254 | 0.068664 | -121.9711 | -121.9437 | 44.5175 | 0.059509 | 80.1041 | 0.086975
4262.5781 | 121.9437 | -0.10529 | 121.9391 | -0.012131 | 0.16397 | 0.13524 | -0.003168 | 0.086462 | 0.088637 | -0.0043046 | -0.005371 | 0.020181 | 0.041567 | -0.0090833 | 0.014898 | 0.023964 | -0.0027707 | 80.0262 | 121.9299 | -0.082397 | 44.5221 | 121.7056 | 114.3265 | 102.594 | -0.050354 | 0.027466 | -0.036621 | -0.064087 | 0.018311 | -0.018311 | 0.022888 | 0.022889 | -0.009155 | -77.417 | 121.8109 | 102.6993 | 114.4318 | 102.6764 | 114.4089 | 0.068665 | -121.9116 | -122.0032 | 0.1236 | 0.12817 | 0.086975 | 0.059509 | 0.01831 | 121.788 | 44.6045 | 0.054932 | -0.027466 | 122.0123 | 0.064087 | 122.0352 | 0.13275 | -122.0215 | -121.9757 | 44.6274 | 0.041199 | 80.1315 | 0.054932
4264.3594 | 122.0947 | -0.068665 | 121.8933 | -0.0045011 | 0.16141 | 0.13546 | -0.0074404 | 0.078985 | 0.090345 | -0.0070816 | -0.0023192 | 0.019967 | 0.042635 | -0.01891 | 0.01148 | 0.02311 | -0.0049069 | 80.1498 | 121.8842 | -0.050354 | 44.5175 | 121.8109 | 114.5645 | 102.6535 | 0.064087 | -0.022888 | 0 | 0.036621 | 0.17395 | 0.15564 | 0.13733 | 0.018311 | -0.009156 | -77.3758 | 121.8796 | 102.7222 | 114.6332 | 102.7039 | 114.6149 | 0.068665 | -121.9162 | -121.8567 | 0.24261 | 0.20599 | 0.22431 | 0.13733 | 0.15564 | 121.8613 | 44.5679 | 0.17395 | 0.036621 | 121.9345 | -0.022888 | 121.9528 | 0.045777 | -121.9437 | -121.8933 | 44.5862 | 0.10529 | 80.2185 | 0.13275
4266.1406 | 121.9116 | -0.10071 | 121.9482 | -0.0045011 | 0.16376 | 0.13653 | -0.0063724 | 0.081549 | 0.088637 | -0.0040908 | -0.005371 | 0.021249 | 0.04178 | -0.0084423 | 0.015112 | 0.025246 | -0.0023435 | 80.1819 | 121.9345 | -0.082397 | 44.5312 | 121.6644 | 114.5416 | 102.8412 | -0.082397 | 0.009155 | -0.059509 | -0.054932 | 0.004578 | -0.013733 | 0.032043 | 0.018311 | -0.013733 | -77.417 | 121.7651 | 102.9419 | 114.6423 | 102.9236 | 114.624 | 0.041199 | -121.9391 | -122.0032 | 0.10529 | 0.13275 | 0.086975 | 0.091552 | 0.045776 | 121.7468 | 44.6136 | 0.064087 | 0.004577 | 122.0169 | 0.068664 | 122.0352 | 0.10986 | -122.0306 | -122.0078 | 44.632 | 0.045776 | 80.2826 | 0.018311
4267.9219 | 122.1039 | -0.045776 | 121.8887 | -0.0045011 | 0.16034 | 0.13332 | -0.0061588 | 0.080053 | 0.087782 | -0.0015274 | -0.0084228 | 0.018899 | 0.040285 | -0.019978 | 0.012334 | 0.023964 | -0.0038389 | 80.1361 | 121.8384 | -0.045776 | 44.7006 | 121.8338 | 114.8849 | 103.1891 | 0.10529 | -0.027466 | -0.009155 | 0.054932 | 0.18768 | 0.16937 | 0.15106 | 0 | -0.050354 | -77.1881 | 121.8796 | 103.2349 | 114.9307 | 103.2349 | 114.9307 | 0.036621 | -121.9162 | -121.8338 | 0.23346 | 0.19684 | 0.21515 | 0.16022 | 0.17853 | 121.8796 | 44.7464 | 0.19684 | 0.064087 | 121.8842 | -0.018311 | 121.8842 | 0.01831 | -121.9345 | -121.8979 | 44.7464 | 0.10071 | 80.1819 | 0.15106
4269.6406 | 122.049 | -0.07782 | 121.8979 | -0.012131 | 0.16376 | 0.13781 | -0.007654 | 0.084539 | 0.089277 | -0.0045182 | -0.0023192 | 0.020608 | 0.042849 | -0.017628 | 0.012121 | 0.022255 | -0.0029843 | 80.127 | 121.8521 | -0.045776 | 44.6457 | 121.7606 | 114.9582 | 103.1616 | 0.018311 | -0.009155 | -0.018311 | 0.018311 | 0.13275 | 0.11444 | 0.11444 | 0.032044 | -0.045776 | -77.2522 | 121.8384 | 103.2394 | 115.036 | 103.2074 | 115.004 | 0.059509 | -121.907 | -121.8796 | 0.21057 | 0.19226 | 0.19226 | 0.13275 | 0.13275 | 121.8063 | 44.6915 | 0.15106 | 0.036622 | 121.8979 | 0.009156 | 121.9299 | 0.068665 | -121.9437 | -121.9162 | 44.7235 | 0.096131 | 80.2048 | 0.096131
4271.4062 | 121.9803 | -0.082397 | 121.9025 | -0.0045011 | 0.16525 | 0.13824 | -0.0040224 | 0.084112 | 0.087782 | -0.0025956 | 0.00073235 | 0.020181 | 0.043703 | -0.012929 | 0.014684 | 0.024391 | -0.0027707 | 80.0903 | 121.9116 | -0.082397 | 44.8242 | 121.7651 | 115.0909 | 103.8254 | 0.045776 | 0.027466 | -0.027466 | -0.004578 | 0.091553 | 0.059509 | 0.082397 | 0 | 0.009155 | -77.0782 | 121.8475 | 103.9078 | 115.1733 | 103.9078 | 115.1733 | 0.054931 | -121.875 | -121.907 | 0.17395 | 0.16479 | 0.14191 | 0.10986 | 0.086975 | 121.8475 | 44.9066 | 0.11902 | 0.022888 | 121.994 | 0.054932 | 121.994 | 0.10986 | -121.9849 | -121.9299 | 44.9066 | 0.077819 | 80.1727 | 0.12817
4273.125 | 121.9986 | -0.091553 | 121.9345 | -0.012131 | 0.16419 | 0.13759 | -0.0067996 | 0.081762 | 0.089491 | -0.0021682 | -0.005371 | 0.021676 | 0.042208 | -0.010151 | 0.015325 | 0.02311 | -0.00042085 | 80.1682 | 121.8979 | -0.073242 | 44.7739 | 121.7514 | 115.2145 | 103.4729 | 0.009155 | 0.032043 | -0.045776 | -0.022888 | 0.091553 | 0.064087 | 0.086975 | 0.018311 | -0.036621 | -77.1606 | 121.843 | 103.5645 | 115.3061 | 103.5461 | 115.2878 | 0.045777 | -121.9025 | -121.9574 | 0.18311 | 0.17853 | 0.15564 | 0.13275 | 0.10986 | 121.8246 | 44.8471 | 0.13733 | 0.022888 | 121.9711 | 0.077819 | 121.9894 | 0.1236 | -122.0078 | -121.9803 | 44.8654 | 0.068665 | 80.2597 | 0.10071
4274.9062 | 121.9849 | -0.068665 | 121.907 | -0.01976 | 0.16547 | 0.13909 | -0.0067996 | 0.083258 | 0.0912 | -0.0021682 | -0.0023192 | 0.023385 | 0.04114 | -0.011433 | 0.014684 | 0.024178 | -0.0014891 | 80.0262 | 121.8796 | -0.086975 | 44.8059 | 121.7606 | 115.1184 | 103.7338 | 0.036621 | 0.013733 | -0.027466 | -0.009155 | 0.086975 | 0.050354 | 0.073242 | -0.01831 | -0.027465 | -77.1011 | 121.8292 | 103.8025 | 115.1871 | 103.8208 | 115.2054 | 0.041199 | -121.8933 | -121.9162 | 0.15564 | 0.14191 | 0.11902 | 0.10071 | 0.07782 | 121.8475 | 44.8929 | 0.11444 | 0.018311 | 121.9666 | 0.041199 | 121.9482 | 0.082398 | -121.994 | -121.9345 | 44.8746 | 0.05951 | 80.0949 | 0.10529
4276.6719 | 122.0764 | -0.050354 | 121.9025 | -0.012131 | 0.16846 | 0.14144 | -0.006586 | 0.084967 | 0.092054 | -3.1996e-05 | -0.005371 | 0.019967 | 0.041994 | -0.011647 | 0.015325 | 0.024178 | -0.0019163 | 80.0674 | 121.8933 | -0.036621 | 44.9707 | 121.8018 | 115.2328 | 103.6606 | 0.10071 | -0.022888 | -0.013733 | 0.064087 | 0.16479 | 0.12817 | 0.14191 | 0.013733 | -0.009155 | -76.9318 | 121.8521 | 103.7109 | 115.2832 | 103.6972 | 115.2695 | 0.036621 | -121.9254 | -121.8384 | 0.21515 | 0.19226 | 0.17853 | 0.15564 | 0.14191 | 121.8384 | 45.0073 | 0.17853 | 0.07782 | 121.9299 | -0.009155 | 121.9437 | 0.027466 | -121.9391 | -121.9162 | 45.0211 | 0.11444 | 80.1178 | 0.15106
4278.4375 | 121.9528 | -0.11444 | 121.9391 | 0.0031279 | 0.16675 | 0.13952 | -0.0074404 | 0.081549 | 0.088209 | -0.001741 | -0.011475 | 0.022531 | 0.041353 | -0.017201 | 0.013616 | 0.023323 | -0.0021299 | 79.7516 | 121.9208 | -0.082397 | 44.7876 | 121.7056 | 115.155 | 103.1067 | -0.082397 | 0.018311 | -0.054932 | -0.091553 | 0.027466 | 0.022888 | 0.041199 | 0.032044 | -0.018311 | -77.1515 | 121.8201 | 103.2211 | 115.2695 | 103.1891 | 115.2374 | 0.059509 | -121.9208 | -122.0306 | 0.14191 | 0.15564 | 0.13733 | 0.096131 | 0.07782 | 121.788 | 44.87 | 0.082398 | -0.036621 | 122.0032 | 0.073243 | 122.0352 | 0.13275 | -122.0215 | -121.994 | 44.902 | 0.022888 | 79.866 | 0.032044
4280.1562 | 121.9757 | -0.10529 | 121.9208 | -0.012131 | 0.16867 | 0.14208 | -0.0053042 | 0.08518 | 0.087568 | -0.002382 | -0.005371 | 0.023599 | 0.042421 | -0.0086559 | 0.013189 | 0.024178 | -0.0040525 | 79.5456 | 121.8933 | -0.073242 | 44.989 | 121.7651 | 115.2695 | 103.6697 | 0.032043 | 0.009155 | -0.032043 | -0.027466 | 0.082397 | 0.045776 | 0.082397 | 0.032044 | -0.027465 | -76.9318 | 121.8704 | 103.775 | 115.3748 | 103.743 | 115.3427 | 0.073243 | -121.9116 | -121.9482 | 0.18768 | 0.18768 | 0.15106 | 0.11444 | 0.077819 | 121.8384 | 45.0623 | 0.11444 | 0.004577 | 121.9666 | 0.041198 | 121.9986 | 0.11444 | -121.994 | -121.9528 | 45.0943 | 0.07782 | 79.6509 | 0.13733
4281.9219 | 122.0627 | -0.059509 | 121.8796 | -0.012131 | 0.1691 | 0.14336 | -0.0063724 | 0.083685 | 0.08885 | -0.0043046 | -0.0023192 | 0.020608 | 0.040071 | -0.021046 | 0.014898 | 0.025673 | -0.0042661 | 79.5547 | 121.9025 | -0.050354 | 45.2454 | 121.8201 | 115.3656 | 104.0817 | 0.09613 | -0.018311 | 0.013733 | 0.068665 | 0.15564 | 0.1236 | 0.15564 | 0.009155 | 0.022888 | -76.6342 | 121.8796 | 104.1412 | 115.4251 | 104.1321 | 115.416 | 0.073242 | -121.8979 | -121.8109 | 0.21515 | 0.21515 | 0.1831 | 0.14191 | 0.10986 | 121.8704 | 45.2957 | 0.14191 | 0.054932 | 121.9528 | -0.032044 | 121.962 | 0.041198 | -121.9299 | -121.8658 | 45.3049 | 0.12817 | 79.6143 | 0.15564
4283.6719 | 122.0856 | -0.073242 | 121.9208 | -0.012131 | 0.16867 | 0.14187 | -0.0089358 | 0.084539 | 0.088637 | -0.0045182 | -0.0084228 | 0.02189 | 0.041353 | -0.017415 | 0.012548 | 0.022896 | -0.0034117 | 79.6326 | 121.8933 | -0.041199 | 45.4468 | 121.8063 | 115.4663 | 104.0955 | 0.07782 | -0.022888 | -0.013733 | 0.036621 | 0.1831 | 0.15564 | 0.13733 | 0.032043 | -0.027465 | -76.474 | 121.8796 | 104.1687 | 115.5396 | 104.1367 | 115.5075 | 0.059509 | -121.9437 | -121.8842 | 0.25635 | 0.21057 | 0.22888 | 0.15106 | 0.16937 | 121.8475 | 45.488 | 0.19684 | 0.050354 | 121.9345 | -0.009155 | 121.9666 | 0.050354 | -121.962 | -121.9345 | 45.52 | 0.10986 | 79.7058 | 0.15106
4285.375 | 121.994 | -0.09613 | 121.9208 | -0.01976 | 0.16782 | 0.14229 | -0.0089358 | 0.081121 | 0.0912 | -0.0038772 | -0.005371 | 0.020181 | 0.04178 | -0.015065 | 0.011053 | 0.022042 | -0.0053343 | 79.6921 | 121.8567 | -0.050354 | 45.8542 | 121.8292 | 115.7043 | 104.1229 | 0.050354 | -0.009155 | -0.018311 | -0.027466 | 0.11444 | 0.086975 | 0.07782 | 0.045776 | -0.064087 | -76.0666 | 121.9254 | 104.2191 | 115.8005 | 104.1733 | 115.7547 | 0.077819 | -121.9299 | -121.9482 | 0.21057 | 0.17395 | 0.1831 | 0.096131 | 0.10529 | 121.8796 | 45.9045 | 0.13275 | -0.009155 | 121.907 | 0.009156 | 121.9528 | 0.086975 | -121.9711 | -121.9391 | 45.9503 | 0.068664 | 79.7882 | 0.14648
4287.1406 | 122.0215 | -0.064087 | 121.8887 | -0.012131 | 0.17188 | 0.14422 | -0.0091494 | 0.083471 | 0.089277 | -0.0015274 | -0.005371 | 0.018258 | 0.041353 | -0.013997 | 0.012975 | 0.024391 | -0.0064023 | 79.4769 | 121.8796 | -0.045776 | 45.52 | 121.7834 | 115.773 | 103.6423 | 0.059509 | -0.013733 | -0.018311 | 0.018311 | 0.11902 | 0.09613 | 0.091553 | 0.018311 | -0.009155 | -76.3687 | 121.8475 | 103.7064 | 115.8371 | 103.688 | 115.8188 | 0.045776 | -121.9025 | -121.8704 | 0.18311 | 0.15564 | 0.16022 | 0.10986 | 0.11444 | 121.8292 | 45.5658 | 0.13733 | 0.036622 | 121.9254 | 0.004578 | 121.9437 | 0.050354 | -121.9345 | -121.907 | 45.5841 | 0.082398 | 79.541 | 0.1236
4288.9062 | 121.9894 | -0.082397 | 121.9162 | -0.012131 | 0.16867 | 0.14229 | -0.008295 | 0.083258 | 0.089491 | -0.0049454 | 0.00073235 | 0.020395 | 0.04114 | -0.018055 | 0.011694 | 0.022042 | -0.0059751 | 79.4769 | 121.8521 | -0.054932 | 45.8038 | 121.8155 | 115.8142 | 103.8757 | 0.032043 | 0.004578 | -0.036621 | -0.032043 | 0.091553 | 0.068665 | 0.073242 | 0.027465 | -0.064087 | -76.1124 | 121.8979 | 103.9581 | 115.8966 | 103.9307 | 115.8691 | 0.045776 | -121.9116 | -121.9482 | 0.17395 | 0.15564 | 0.15106 | 0.10986 | 0.10529 | 121.8704 | 45.8588 | 0.12817 | 0.004578 | 121.907 | 0.041199 | 121.9345 | 0.086975 | -121.9711 | -121.9528 | 45.8862 | 0.050354 | 79.5593 | 0.11444
4290.6094 | 121.9299 | -0.1236 | 121.962 | -0.012131 | 0.17166 | 0.14358 | -0.0072268 | 0.084753 | 0.091841 | -0.0025956 | -0.005371 | 0.022103 | 0.041353 | -0.015492 | 0.0093439 | 0.022042 | -0.0031979 | 79.3808 | 121.9116 | -0.073242 | 45.7809 | 121.6827 | 115.7501 | 103.9124 | -0.068665 | 0.018311 | -0.054932 | -0.086975 | 0.022888 | 0.013733 | 0.032043 | 0.050354 | -0.050354 | -76.181 | 121.8063 | 104.0359 | 115.8737 | 103.9856 | 115.8234 | 0.068664 | -121.9437 | -122.0489 | 0.14648 | 0.15564 | 0.13733 | 0.086975 | 0.068665 | 121.756 | 45.8542 | 0.07782 | -0.032043 | 121.9849 | 0.073243 | 122.0352 | 0.14191 | -122.0352 | -122.0169 | 45.9045 | 0.036621 | 79.5044 | 0.054931
4292.375 | 122.0398 | -0.059509 | 121.9116 | -0.012131 | 0.17444 | 0.14956 | -0.0072268 | 0.084967 | 0.090345 | -0.00345 | -0.005371 | 0.020395 | 0.042635 | -0.015706 | 0.014043 | 0.024391 | 0.00043375 | 79.3488 | 121.843 | -0.032043 | 45.8084 | 121.8292 | 115.8646 | 104.0588 | 0.1236 | -0.022888 | -0.009155 | 0.050354 | 0.15564 | 0.1236 | 0.13733 | 0.027466 | -0.068664 | -76.1032 | 121.8887 | 104.1183 | 115.9241 | 104.0909 | 115.8966 | 0.050354 | -121.9345 | -121.8613 | 0.21515 | 0.19684 | 0.1831 | 0.14648 | 0.13275 | 121.8613 | 45.8405 | 0.16479 | 0.059509 | 121.875 | -0.013733 | 121.9025 | 0.036621 | -121.9437 | -121.9208 | 45.8679 | 0.10986 | 79.4083 | 0.1831
4294.1406 | 122.0306 | -0.073242 | 121.8979 | -0.012131 | 0.17401 | 0.14721 | -0.0053042 | 0.084112 | 0.089491 | -0.005159 | -0.005371 | 0.01954 | 0.041994 | -0.011647 | 0.014898 | 0.02311 | -0.0034117 | 79.129 | 121.9254 | -0.07782 | 45.6116 | 121.7285 | 115.4984 | 103.7155 | 0.027466 | 0.013733 | -0.041199 | 0.032043 | 0.11444 | 0.068665 | 0.11902 | -0.004578 | 0.027466 | -76.2863 | 121.8018 | 103.7888 | 115.5716 | 103.7933 | 115.5762 | 0.032043 | -121.8842 | -121.8658 | 0.18768 | 0.19226 | 0.14191 | 0.16022 | 0.10986 | 121.8063 | 45.6894 | 0.15564 | 0.073242 | 122.0032 | 0.054932 | 121.9986 | 0.086975 | -121.9757 | -121.9391 | 45.6848 | 0.10529 | 79.2023 | 0.10071
4295.9062 | 122.0673 | -0.059509 | 121.8613 | -0.01976 | 0.17551 | 0.15105 | -0.0053042 | 0.084539 | 0.092054 | -0.0032364 | -0.0023192 | 0.019754 | 0.04178 | -0.021687 | 0.015325 | 0.024605 | -0.0017027 | 79.1656 | 121.8796 | -0.032043 | 45.932 | 121.8063 | 115.6082 | 103.8208 | 0.10529 | -0.009155 | -0.013733 | 0.07782 | 0.16937 | 0.12817 | 0.14648 | 0.027466 | 0.018311 | -75.9293 | 121.8658 | 103.8803 | 115.6677 | 103.8528 | 115.6403 | 0.045776 | -121.8704 | -121.7834 | 0.22888 | 0.20599 | 0.18768 | 0.16022 | 0.14191 | 121.8384 | 45.9641 | 0.18311 | 0.091553 | 121.9116 | 0.004578 | 121.9391 | 0.050354 | -121.8933 | -121.875 | 45.9915 | 0.13733 | 79.2252 | 0.16479
4297.6719 | 121.9711 | -0.086975 | 121.9299 | -0.01976 | 0.1738 | 0.15063 | -0.0057314 | 0.089025 | 0.087355 | -0.005159 | -0.0084228 | 0.023599 | 0.043062 | -0.012501 | 0.015966 | 0.021828 | -0.0042661 | 78.7445 | 121.8796 | -0.073242 | 46.1609 | 121.7514 | 115.8371 | 103.9536 | 0.022888 | 0.022888 | -0.013733 | 0 | 0.09613 | 0.064087 | 0.073242 | 0.013733 | -0.050354 | -75.769 | 121.8384 | 104.0405 | 115.9241 | 104.0268 | 115.9103 | 0.073242 | -121.907 | -121.9299 | 0.1831 | 0.16022 | 0.15106 | 0.086975 | 0.07782 | 121.8246 | 46.2341 | 0.10986 | 0.013733 | 121.9528 | 0.036621 | 121.9666 | 0.10986 | -122.0032 | -121.9437 | 46.2479 | 0.086975 | 78.8315 | 0.10986
4299.3906 | 121.9849 | -0.091553 | 121.8796 | -0.012131 | 0.17551 | 0.15063 | -0.0070132 | 0.081335 | 0.090345 | -0.0008866 | -0.0023192 | 0.022103 | 0.039644 | -0.013569 | 0.014471 | 0.02311 | -0.0076841 | 79.0283 | 121.8933 | -0.086975 | 46.2845 | 121.7194 | 115.8966 | 103.9536 | -0.018311 | 0.022888 | -0.045776 | -0.022888 | 0.082397 | 0.045776 | 0.068665 | 0.004578 | 0.013733 | -75.5951 | 121.8109 | 104.0451 | 115.9882 | 104.0405 | 115.9836 | 0.045777 | -121.8567 | -121.9025 | 0.17395 | 0.16022 | 0.13733 | 0.11444 | 0.091552 | 121.8063 | 46.3715 | 0.12817 | 0.022888 | 121.9803 | 0.068664 | 121.9849 | 0.11444 | -121.9666 | -121.9254 | 46.376 | 0.068665 | 79.1199 | 0.073242
4301.1562 | 122.0764 | -0.064087 | 121.8658 | -0.012131 | 0.17423 | 0.14913 | -0.0095766 | 0.07984 | 0.088423 | -0.0040908 | -0.0023192 | 0.019113 | 0.043489 | -0.013569 | 0.011266 | 0.025673 | -0.00042085 | 79.097 | 121.8567 | -0.027466 | 46.463 | 121.8567 | 116.0065 | 104.1824 | 0.13733 | -0.022888 | -0.004578 | 0.068665 | 0.21515 | 0.16479 | 0.15564 | 0.036621 | -0.009156 | -75.4028 | 121.9208 | 104.2465 | 116.0706 | 104.2099 | 116.0339 | 0.059509 | -121.8887 | -121.7972 | 0.27924 | 0.21973 | 0.22888 | 0.16022 | 0.16937 | 121.8842 | 46.4905 | 0.21973 | 0.073243 | 121.8842 | -0.01831 | 121.9208 | 0.041199 | -121.8933 | -121.8704 | 46.5271 | 0.13275 | 79.1611 | 0.20142
4302.9219 | 121.9391 | -0.10529 | 121.8979 | -0.012131 | 0.17786 | 0.15105 | -0.0033816 | 0.085821 | 0.090345 | -0.0043046 | -0.0023192 | 0.022531 | 0.043917 | -0.012715 | 0.01383 | 0.022896 | 0.0025699 | 78.9276 | 121.9208 | -0.07782 | 46.6095 | 121.6507 | 115.8142 | 103.9948 | -0.086975 | 0.009155 | -0.054932 | -0.064087 | 0.013733 | -0.027466 | 0.022888 | 0.027466 | 0.022888 | -75.2884 | 121.756 | 104.1 | 115.9195 | 104.0726 | 115.892 | 0.050354 | -121.8887 | -121.962 | 0.11902 | 0.12817 | 0.07782 | 0.07782 | 0.027466 | 121.7285 | 46.6873 | 0.068665 | -0.009155 | 121.9986 | 0.064087 | 122.0261 | 0.11444 | -121.9757 | -121.9528 | 46.7148 | 0.041199 | 79.0329 | 0.018311
4304.6875 | 121.9666 | -0.10071 | 121.9162 | -0.012131 | 0.17786 | 0.15148 | -0.0074404 | 0.08518 | 0.089064 | -0.0043046 | -0.005371 | 0.021676 | 0.040926 | -0.016987 | 0.016607 | 0.022683 | -0.0031979 | 78.8544 | 121.8796 | -0.054932 | 46.582 | 121.756 | 115.9836 | 104.1458 | 0.050354 | -0.009155 | -0.054932 | 0 | 0.082397 | 0.054932 | 0.068665 | 0.045776 | -0.036621 | -75.3342 | 121.8567 | 104.2465 | 116.0843 | 104.2007 | 116.0385 | 0.045776 | -121.9254 | -121.9162 | 0.18311 | 0.16937 | 0.15564 | 0.1236 | 0.10986 | 121.8109 | 46.637 | 0.13733 | 0.054932 | 121.9345 | 0.045777 | 121.9803 | 0.091553 | -121.9711 | -121.9711 | 46.6827 | 0.10071 | 78.9551 | 0.15106
4306.3906 | 122.0261 | -0.082397 | 121.875 | -0.01976 | 0.17829 | 0.15255 | -0.0085086 | 0.086035 | 0.090773 | -0.0032364 | -0.0084228 | 0.01954 | 0.042421 | -0.013569 | 0.013403 | 0.025887 | -0.0044797 | 78.8544 | 121.8613 | -0.041199 | 46.788 | 121.7606 | 115.7135 | 104.1641 | 0.013733 | -0.022888 | -0.027466 | 0.009155 | 0.1236 | 0.09613 | 0.091553 | 0.041198 | -0.013733 | -75.087 | 121.843 | 104.2465 | 115.7959 | 104.2053 | 115.7547 | 0.054931 | -121.8979 | -121.8658 | 0.20599 | 0.17395 | 0.17853 | 0.11902 | 0.1236 | 121.8018 | 46.8292 | 0.15106 | 0.036621 | 121.9025 | 0.004578 | 121.9437 | 0.059509 | -121.9162 | -121.9025 | 46.8704 | 0.091552 | 78.9368 | 0.09613
4308.1562 | 121.9437 | -0.10529 | 121.907 | -0.01976 | 0.17572 | 0.15383 | -0.0057314 | 0.087957 | 0.090132 | -0.0043046 | -0.005371 | 0.021463 | 0.042208 | -0.015492 | 0.013189 | 0.024391 | -0.0012753 | 78.8681 | 121.9116 | -0.082397 | 47.0856 | 121.6782 | 115.892 | 103.3539 | -0.032043 | 0.032043 | -0.032043 | -0.041199 | 0.036621 | 0.009155 | 0.059509 | 0.022889 | 0.004578 | -74.8215 | 121.7834 | 103.4592 | 115.9973 | 103.4363 | 115.9744 | 0.073243 | -121.875 | -121.9482 | 0.14191 | 0.16479 | 0.11444 | 0.091552 | 0.041198 | 121.7606 | 47.168 | 0.068664 | -0.009156 | 121.994 | 0.064086 | 122.0169 | 0.13733 | -121.9894 | -121.9391 | 47.1909 | 0.064087 | 78.9734 | 0.073243
4309.9219 | 122.0169 | -0.073242 | 121.8842 | -0.01976 | 0.17829 | 0.15404 | -0.0085086 | 0.08283 | 0.089705 | -0.0019546 | -0.005371 | 0.021035 | 0.039431 | -0.012501 | 0.01148 | 0.024819 | -0.0019163 | 78.8589 | 121.8613 | -0.027466 | 47.2961 | 121.788 | 116.0156 | 104.0543 | 0.054932 | -0.013733 | -0.018311 | -0.004578 | 0.11444 | 0.10071 | 0.10529 | 0.045776 | -0.022888 | -74.588 | 121.8613 | 104.1275 | 116.0889 | 104.0817 | 116.0431 | 0.054931 | -121.8979 | -121.8887 | 0.18768 | 0.17853 | 0.17395 | 0.1236 | 0.11902 | 121.8155 | 47.3236 | 0.13275 | 0.013733 | 121.8887 | 0.004578 | 121.9345 | 0.059509 | -121.9116 | -121.9025 | 47.3694 | 0.068664 | 78.9322 | 0.12817
4311.625 | 122.0581 | -0.054932 | 121.8796 | 0.0031279 | 0.18128 | 0.15554 | -0.0046634 | 0.086462 | 0.089918 | -0.002382 | -0.005371 | 0.020395 | 0.040926 | -0.01186 | 0.013403 | 0.023537 | -0.0034117 | 78.6758 | 121.8613 | -0.027466 | 47.4289 | 121.8292 | 116.0522 | 104.1046 | 0.12817 | -0.013733 | -0.009155 | 0.07782 | 0.16479 | 0.14191 | 0.13275 | 0.027466 | -0.018311 | -74.4507 | 121.8842 | 104.1595 | 116.1072 | 104.1321 | 116.0797 | 0.045777 | -121.8933 | -121.8018 | 0.21973 | 0.18768 | 0.19684 | 0.14191 | 0.15106 | 121.8567 | 47.4564 | 0.17395 | 0.086975 | 121.8887 | -0.004578 | 121.9162 | 0.041199 | -121.907 | -121.8887 | 47.4838 | 0.13275 | 78.7308 | 0.18311
4313.3906 | 121.9666 | -0.10529 | 121.9116 | -0.01976 | 0.17957 | 0.15639 | -0.0091494 | 0.084753 | 0.088423 | -0.00345 | -0.005371 | 0.019967 | 0.040071 | -0.012929 | 0.012762 | 0.022042 | -0.0061887 | 78.5889 | 121.8567 | -0.054932 | 47.5067 | 121.7743 | 116.0889 | 104.0131 | 0.027466 | 0.004578 | -0.027466 | -0.041199 | 0.086975 | 0.059509 | 0.054932 | 0.050354 | -0.054932 | -74.4049 | 121.8796 | 104.1183 | 116.1942 | 104.068 | 116.1438 | 0.07782 | -121.907 | -121.9528 | 0.19226 | 0.16022 | 0.16479 | 0.082398 | 0.086975 | 121.8292 | 47.5616 | 0.11444 | -0.013733 | 121.9116 | 0.032044 | 121.962 | 0.10986 | -121.9666 | -121.9391 | 47.612 | 0.064087 | 78.6942 | 0.13275
4315.1094 | 122.0398 | -0.073242 | 121.875 | -0.012131 | 0.18448 | 0.15789 | -0.0063724 | 0.08753 | 0.091414 | -0.0060134 | -0.005371 | 0.018472 | 0.041567 | -0.015065 | 0.013616 | 0.023964 | 6.346e-06 | 78.2822 | 121.8567 | -0.032043 | 48.1293 | 121.8292 | 116.0934 | 104.4937 | 0.1236 | -0.022888 | 0 | 0.041199 | 0.14648 | 0.1236 | 0.12817 | 0.041199 | -0.018311 | -73.7457 | 121.9025 | 104.567 | 116.1667 | 104.5258 | 116.1255 | 0.073242 | -121.8979 | -121.8338 | 0.21973 | 0.20142 | 0.19684 | 0.12817 | 0.1236 | 121.8613 | 48.1613 | 0.14648 | 0.041199 | 121.8887 | -0.022888 | 121.9299 | 0.050354 | -121.907 | -121.875 | 48.2025 | 0.11444 | 78.3554 | 0.19684
4316.875 | 122.0215 | -0.07782 | 121.8796 | -0.02739 | 0.18555 | 0.15874 | -0.0072268 | 0.090521 | 0.092482 | -0.0028092 | -0.005371 | 0.022103 | 0.040926 | -0.015706 | 0.013616 | 0.025673 | -0.0029843 | 78.3691 | 121.9162 | -0.064087 | 48.5413 | 121.7194 | 116.0248 | 104.7592 | 0.027466 | 0.009155 | -0.018311 | 0.041199 | 0.13275 | 0.091553 | 0.11902 | 0.013733 | 0.036621 | -73.3383 | 121.7972 | 104.837 | 116.1026 | 104.8233 | 116.0889 | 0.059509 | -121.8704 | -121.8384 | 0.21057 | 0.19684 | 0.16937 | 0.13733 | 0.10986 | 121.7834 | 48.6053 | 0.15106 | 0.05951 | 121.9803 | 0.027466 | 121.994 | 0.086975 | -121.9437 | -121.8979 | 48.6191 | 0.11902 | 78.447 | 0.10529
4318.5781 | 121.9116 | -0.11444 | 121.9162 | -0.0045011 | 0.18768 | 0.16067 | -0.004877 | 0.08753 | 0.091841 | -0.0040908 | -0.0084228 | 0.023812 | 0.040712 | -0.0054517 | 0.014684 | 0.022896 | -0.0031979 | 78.2501 | 121.8933 | -0.086975 | 50.0244 | 121.6461 | 116.0156 | 104.7318 | -0.091553 | 0.013733 | -0.036621 | -0.054932 | 0.022888 | -0.013733 | 0.027466 | 0.027466 | -0.022888 | -71.8918 | 121.7606 | 104.8462 | 116.1301 | 104.8187 | 116.1026 | 0.07782 | -121.9025 | -121.9711 | 0.13733 | 0.14191 | 0.10071 | 0.064087 | 0.022888 | 121.7331 | 50.1114 | 0.059509 | -0.018311 | 121.9803 | 0.050354 | 122.0078 | 0.12817 | -122.0032 | -121.9528 | 50.1389 | 0.059509 | 78.3646 | 0.022888
4320.2969 | 122.0078 | -0.082397 | 121.8933 | -0.012131 | 0.18512 | 0.16131 | -0.007654 | 0.086675 | 0.090345 | -0.0028092 | -0.0023192 | 0.018258 | 0.042208 | -0.016774 | 0.012548 | 0.024819 | -0.0064023 | 78.1311 | 121.8475 | -0.036621 | 49.585 | 121.7651 | 116.1072 | 104.3472 | 0.027466 | -0.004578 | -0.027466 | 0.018311 | 0.1236 | 0.091553 | 0.091553 | 0.045776 | -0.045777 | -72.3083 | 121.8475 | 104.4296 | 116.1896 | 104.3838 | 116.1438 | 0.054931 | -121.8979 | -121.875 | 0.20599 | 0.17395 | 0.17395 | 0.11902 | 0.11902 | 121.8018 | 49.6216 | 0.15106 | 0.045777 | 121.8842 | 0.022888 | 121.9299 | 0.077819 | -121.9299 | -121.9208 | 49.6674 | 0.10071 | 78.2135 | 0.10986
4322.0625 | 121.9345 | -0.10986 | 121.9437 | -0.01976 | 0.2052 | 0.18481 | -0.006586 | 0.089025 | 0.088637 | -0.0030228 | -0.005371 | 0.020395 | 0.043703 | -0.016774 | 0.012334 | 0.025673 | -0.0025571 | 78.9825 | 121.8613 | -0.068665 | 98.0118 | 121.7102 | 114.9078 | 113.1409 | -0.036621 | 0.045776 | -0.036621 | -0.086975 | 0.036621 | 0.022888 | 0.027466 | 0.041198 | -0.082398 | -23.9319 | 121.8201 | 113.2507 | 115.0177 | 113.2095 | 114.9765 | 0.073242 | -121.8979 | -122.0306 | 0.14648 | 0.13733 | 0.13275 | 0.064087 | 0.059509 | 121.7789 | 98.0804 | 0.073242 | -0.050354 | 121.9299 | 0.082397 | 121.9711 | 0.15564 | -122.0123 | -121.9803 | 98.1216 | 0.022888 | 79.0924 | 0.073242
4323.8438 | 122.0581 | -0.073242 | 121.8658 | -0.01976 | 0.21204 | 0.19335 | -0.0067996 | 0.08518 | 0.086714 | -0.0036636 | -0.0084228 | 0.021035 | 0.041994 | -0.015492 | 0.012975 | 0.023751 | -0.0014891 | 79.1611 | 121.8109 | -0.041199 | 109.3277 | 121.8246 | 114.8758 | 114.7247 | 0.11902 | -0.027466 | -0.013733 | 0.054932 | 0.20599 | 0.17853 | 0.15106 | 0.032043 | -0.054932 | -12.5381 | 121.8979 | 114.798 | 114.949 | 114.7659 | 114.917 | 0.059509 | -121.8933 | -121.8109 | 0.27924 | 0.2243 | 0.25177 | 0.16479 | 0.19226 | 121.8658 | 109.3689 | 0.21973 | 0.068665 | 121.8521 | -0.013733 | 121.8842 | 0.045776 | -121.907 | -121.8796 | 109.4009 | 0.12817 | 79.2343 | 0.19226
4325.5625 | 121.9528 | -0.10529 | 121.8933 | -0.01976 | 0.2161 | 0.19164 | -0.005945 | 0.086035 | 0.090986 | -0.0019546 | -0.0023192 | 0.023599 | 0.043062 | -0.0078015 | 0.013189 | 0.02311 | -0.0021299 | 79.0329 | 121.8887 | -0.086975 | 110.1791 | 121.6736 | 115.1916 | 114.8117 | -0.050354 | 0.027466 | -0.045776 | -0.054932 | 0.073242 | 0.027466 | 0.050354 | 0.018311 | -0.004578 | -11.7142 | 121.7789 | 114.917 | 115.2969 | 114.8987 | 115.2786 | 0.05951 | -121.8658 | -121.9482 | 0.17853 | 0.15564 | 0.13275 | 0.09613 | 0.073242 | 121.7606 | 110.2661 | 0.11902 | -0.009156 | 121.9757 | 0.073242 | 121.994 | 0.13275 | -121.9803 | -121.9391 | 110.2844 | 0.050354 | 79.1382 | 0.054932
4327.3281 | 122.0169 | -0.050354 | 121.8704 | -0.012131 | 0.22122 | 0.19634 | -0.0074404 | 0.087316 | 0.088637 | -0.0028092 | -0.005371 | 0.019754 | 0.041994 | -0.017201 | 0.012548 | 0.0261 | -0.0036253 | 79.2526 | 121.8521 | -0.018311 | 110.6277 | 121.8201 | 115.3931 | 115.1138 | 0.10071 | -0.009155 | -0.013733 | 0.064087 | 0.15564 | 0.13275 | 0.13275 | 0.032043 | -0.01831 | -11.2427 | 121.8704 | 115.1642 | 115.4434 | 115.1321 | 115.4114 | 0.036621 | -121.8796 | -121.8063 | 0.20599 | 0.18311 | 0.18311 | 0.14648 | 0.14648 | 121.8384 | 110.6461 | 0.16937 | 0.07782 | 121.8704 | 0.004578 | 121.9025 | 0.041199 | -121.8887 | -121.8842 | 110.6781 | 0.11444 | 79.303 | 0.15106
4329.0938 | 121.8887 | -0.11444 | 121.8704 | -0.02739 | 0.22144 | 0.19826 | -0.0033816 | 0.088171 | 0.089064 | -0.0032364 | -0.0084228 | 0.021676 | 0.041994 | -0.011647 | 0.015325 | 0.023751 | -0.0044797 | 78.9551 | 121.8842 | -0.059509 | 111.058 | 121.6415 | 115.535 | 114.949 | -0.07782 | 0.013733 | -0.059509 | -0.073242 | 0 | -0.032043 | 0.018311 | 0.054932 | 0.013733 | -10.8124 | 121.756 | 115.0635 | 115.6494 | 115.0085 | 115.5945 | 0.054932 | -121.8567 | -121.9437 | 0.11444 | 0.13275 | 0.082398 | 0.07782 | 0.027466 | 121.7011 | 111.1176 | 0.059509 | -0.013733 | 121.9437 | 0.073242 | 121.9986 | 0.12817 | -121.9299 | -121.9299 | 111.1725 | 0.041199 | 79.0695 | 0.036621
4330.7969 | 121.9482 | -0.082397 | 121.8704 | -0.01976 | 0.22251 | 0.19805 | -0.0053042 | 0.089453 | 0.089918 | -0.0028092 | -0.0023192 | 0.022103 | 0.043917 | -0.01186 | 0.014471 | 0.024391 | -0.0025571 | 79.0741 | 121.8613 | -0.059509 | 111.5936 | 121.7239 | 115.7684 | 114.8163 | 0.036621 | 0 | -0.036621 | -0.013733 | 0.10986 | 0.059509 | 0.082397 | 0.022888 | -0.009155 | -10.2768 | 121.8063 | 114.8987 | 115.8508 | 114.8758 | 115.8279 | 0.045776 | -121.8704 | -121.8842 | 0.19226 | 0.16479 | 0.14191 | 0.11902 | 0.09613 | 121.7834 | 111.6531 | 0.14648 | 0.022888 | 121.9208 | 0.036621 | 121.9437 | 0.082397 | -121.9299 | -121.907 | 111.676 | 0.068664 | 79.1565 | 0.11902
4332.5156 | 121.9849 | -0.073242 | 121.8338 | -0.012131 | 0.22208 | 0.1972 | -0.0067996 | 0.085394 | 0.091627 | -0.0019546 | -0.0084228 | 0.021676 | 0.04114 | -0.017201 | 0.012334 | 0.023964 | -0.0023435 | 78.9871 | 121.8613 | -0.054932 | 111.5616 | 121.7514 | 115.8417 | 114.8392 | 0.022888 | 0.004578 | -0.032043 | 0 | 0.11444 | 0.086975 | 0.10529 | 0.01831 | 0.027466 | -10.2722 | 121.8246 | 114.9124 | 115.9149 | 114.8941 | 115.8966 | 0.041199 | -121.8292 | -121.8338 | 0.18768 | 0.17853 | 0.16022 | 0.13733 | 0.11902 | 121.8063 | 111.6165 | 0.14648 | 0.032043 | 121.9162 | 0.036621 | 121.9345 | 0.07782 | -121.8887 | -121.8658 | 111.6348 | 0.073242 | 79.0604 | 0.09613
4334.2812 | 121.9437 | -0.09613 | 121.8796 | -0.01976 | 0.22293 | 0.1989 | -0.006586 | 0.085607 | 0.088423 | -0.0030228 | -0.0084228 | 0.021035 | 0.042635 | -0.023182 | 0.014471 | 0.024391 | -0.0012753 | 78.7537 | 121.8842 | -0.082397 | 111.7172 | 121.6782 | 115.892 | 114.7751 | -0.032043 | 0.032043 | -0.054932 | -0.041199 | 0.086975 | 0.036621 | 0.064087 | 0.013733 | 0.004577 | -10.1624 | 121.7743 | 114.8712 | 115.9882 | 114.8575 | 115.9744 | 0.041198 | -121.8475 | -121.9208 | 0.1831 | 0.16022 | 0.13275 | 0.11902 | 0.091553 | 121.7606 | 111.7996 | 0.14191 | 0.013733 | 121.9666 | 0.086975 | 121.9803 | 0.12817 | -121.962 | -121.9345 | 111.8134 | 0.054931 | 78.8498 | 0.064087
4336.0625 | 121.9528 | -0.09613 | 121.8887 | -0.0045011 | 0.22464 | 0.20019 | -0.0055178 | 0.086675 | 0.087996 | -0.0045182 | -0.005371 | 0.020608 | 0.041567 | -0.0043835 | 0.014043 | 0.025032 | -0.0029843 | 78.9139 | 121.875 | -0.064087 | 112.3535 | 121.7331 | 116.1484 | 114.8895 | 0.009155 | 0.004578 | -0.027466 | -0.013733 | 0.086975 | 0.068665 | 0.086975 | 0.032043 | -0.013733 | -9.5352 | 121.8292 | 114.9857 | 116.2445 | 114.9536 | 116.2125 | 0.068664 | -121.8842 | -121.9025 | 0.1831 | 0.1831 | 0.16479 | 0.11444 | 0.096131 | 121.7972 | 112.4176 | 0.11444 | 0.013733 | 121.9391 | 0.032044 | 121.9711 | 0.10071 | -121.9528 | -121.9162 | 112.4496 | 0.082397 | 79.01 | 0.10528
4337.7812 | 121.9162 | -0.11902 | 121.8933 | -0.012131 | 0.22336 | 0.20061 | -0.0095766 | 0.08518 | 0.08885 | -0.0013138 | 0.00073235 | 0.019326 | 0.040926 | -0.013569 | 0.013616 | 0.024819 | -0.0025571 | 78.9185 | 121.8521 | -0.073242 | 112.0605 | 121.6553 | 115.9882 | 114.6378 | -0.068665 | 0.009155 | -0.054932 | -0.064087 | 0.032043 | 0.022888 | 0.041199 | 0.045777 | -0.041199 | -9.8328 | 121.7743 | 114.7568 | 116.1072 | 114.711 | 116.0614 | 0.064087 | -121.8842 | -121.9574 | 0.15106 | 0.16022 | 0.14191 | 0.096131 | 0.07782 | 121.7285 | 112.1338 | 0.086975 | -0.009155 | 121.9254 | 0.064087 | 121.9711 | 0.12817 | -121.9666 | -121.9482 | 112.1796 | 0.054932 | 79.0375 | 0.050354
4339.5625 | 121.9894 | -0.059509 | 121.8842 | -0.012131 | 0.22464 | 0.20168 | -0.008295 | 0.087103 | 0.08885 | -0.0045182 | -0.0023192 | 0.017831 | 0.043489 | -0.021901 | 0.014257 | 0.023964 | 0.0010745 | 78.9139 | 121.8201 | -0.050354 | 112.3215 | 121.7972 | 116.1575 | 114.917 | 0.064087 | -0.013733 | -0.009155 | 0.009155 | 0.15106 | 0.11444 | 0.10071 | 0.009155 | -0.064087 | -9.5627 | 121.8567 | 114.9765 | 116.217 | 114.9673 | 116.2079 | 0.050354 | -121.8979 | -121.875 | 0.21057 | 0.16022 | 0.17395 | 0.10986 | 0.1236 | 121.8475 | 112.3718 | 0.16022 | 0.01831 | 121.8704 | -0.004578 | 121.8796 | 0.045776 | -121.9345 | -121.8933 | 112.381 | 0.068664 | 78.9734 | 0.1236
4341.3438 | 122.049 | -0.050354 | 121.8384 | -0.012131 | 0.2287 | 0.20531 | -0.005945 | 0.088171 | 0.088637 | -0.001741 | -0.0084228 | 0.019754 | 0.04178 | -0.0097241 | 0.015966 | 0.02311 | -0.0057615 | 78.9688 | 121.8384 | -0.032043 | 112.6053 | 121.7926 | 116.3086 | 114.7705 | 0.10986 | -0.041199 | 0.009155 | 0.073242 | 0.17395 | 0.14191 | 0.13275 | 0.018311 | 0 | -9.2331 | 121.843 | 114.8209 | 116.3589 | 114.8026 | 116.3406 | 0.059509 | -121.8796 | -121.7651 | 0.2243 | 0.18311 | 0.19226 | 0.1236 | 0.13275 | 121.8246 | 112.6373 | 0.16479 | 0.064087 | 121.8704 | -0.050354 | 121.8887 | 0.009155 | -121.8704 | -121.8292 | 112.6556 | 0.1236 | 79.0192 | 0.16022
4343.0469 | 122.0306 | -0.050354 | 121.843 | -0.01976 | 0.22998 | 0.20531 | -0.0044498 | 0.086675 | 0.089491 | -0.00345 | -0.005371 | 0.021249 | 0.040712 | -0.021901 | 0.014043 | 0.024391 | 6.346e-06 | 78.891 | 121.8338 | -0.032043 | 112.0697 | 121.7743 | 116.0706 | 114.6103 | 0.09613 | -0.009155 | -0.013733 | 0.068665 | 0.15564 | 0.12817 | 0.14648 | 0.018311 | -0.009156 | -9.7733 | 121.8246 | 114.6606 | 116.1209 | 114.6423 | 116.1026 | 0.036621 | -121.8521 | -121.7743 | 0.20599 | 0.19684 | 0.17853 | 0.16022 | 0.14191 | 121.8063 | 112.1017 | 0.16937 | 0.082398 | 121.8658 | 0.004578 | 121.8842 | 0.041199 | -121.875 | -121.8567 | 112.1201 | 0.11902 | 78.9413 | 0.14648
4344.8125 | 121.9162 | -0.091553 | 121.8658 | -0.0045011 | 0.23084 | 0.20659 | -0.0057314 | 0.08988 | 0.090986 | -0.0032364 | -0.005371 | 0.021035 | 0.043917 | -0.012929 | 0.014043 | 0.023964 | -0.0038389 | 78.9597 | 121.8887 | -0.07782 | 112.2711 | 121.6461 | 116.098 | 114.5416 | -0.022888 | 0.013733 | -0.041199 | -0.041199 | 0.041199 | 0 | 0.050354 | 0.013733 | 0.022888 | -9.5947 | 121.7377 | 114.6332 | 116.1896 | 114.6194 | 116.1758 | 0.050354 | -121.8521 | -121.907 | 0.13275 | 0.14191 | 0.091553 | 0.091553 | 0.041199 | 121.7239 | 112.3489 | 0.082398 | 0 | 121.9666 | 0.054932 | 121.9803 | 0.10529 | -121.9437 | -121.907 | 112.3627 | 0.050354 | 79.0512 | 0.068665
4346.5312 | 122.0306 | -0.059509 | 121.8246 | -0.0045011 | 0.22656 | 0.20873 | -0.0087222 | 0.088171 | 0.089705 | -0.0036636 | -0.0023192 | 0.01954 | 0.041353 | -0.016774 | 0.010839 | 0.024605 | 0.0010745 | 78.8956 | 121.8018 | -0.027466 | 112.9669 | 121.8567 | 116.4139 | 114.6423 | 0.1236 | -0.022888 | -0.018311 | 0.059509 | 0.18768 | 0.16937 | 0.13275 | 0.032043 | -0.022888 | -8.8577 | 121.9162 | 114.7018 | 116.4734 | 114.6698 | 116.4413 | 0.041198 | -121.8475 | -121.7651 | 0.24719 | 0.19226 | 0.22888 | 0.15106 | 0.18768 | 121.8842 | 112.9944 | 0.20599 | 0.07782 | 121.8292 | -0.004577 | 121.8613 | 0.036621 | -121.8521 | -121.843 | 113.0264 | 0.11902 | 78.9551 | 0.1831
4348.2969 | 121.9116 | -0.10986 | 121.8521 | -0.0045011 | 0.23276 | 0.21151 | -0.0053042 | 0.088812 | 0.089705 | -0.0025956 | 0.00073235 | 0.022744 | 0.043917 | -0.013783 | 0.014471 | 0.025032 | -0.0023435 | 78.8086 | 121.8613 | -0.073242 | 112.8937 | 121.6415 | 116.3223 | 114.5279 | -0.045776 | 0.022888 | -0.045776 | -0.050354 | 0.036621 | -0.013733 | 0.045776 | 0.036621 | 0.009155 | -8.9584 | 121.7514 | 114.6378 | 116.4322 | 114.6011 | 116.3956 | 0.064087 | -121.8292 | -121.9025 | 0.14648 | 0.15564 | 0.09613 | 0.091552 | 0.032043 | 121.7148 | 112.9669 | 0.082397 | -0.004578 | 121.9345 | 0.068664 | 121.9711 | 0.13275 | -121.9254 | -121.8979 | 113.0035 | 0.059509 | 78.9185 | 0.064087
4350 | 121.9345 | -0.091553 | 121.8842 | -0.012131 | 0.23468 | 0.20809 | -0.0061588 | 0.093084 | 0.090559 | -0.0032364 | -0.005371 | 0.023599 | 0.042421 | -0.021046 | 0.014043 | 0.023323 | -0.0074705 | 78.8544 | 121.875 | -0.073242 | 113.3102 | 121.637 | 116.4597 | 114.6194 | -0.018311 | 0.013733 | -0.050354 | -0.032043 | 0.059509 | 0.022888 | 0.068665 | 0.018311 | -0.009155 | -8.5739 | 121.7285 | 114.711 | 116.5512 | 114.6927 | 116.5329 | 0.041199 | -121.8704 | -121.9162 | 0.15106 | 0.16022 | 0.11444 | 0.11902 | 0.073242 | 121.7102 | 113.3835 | 0.10986 | 0.018311 | 121.9482 | 0.064087 | 121.9666 | 0.10529 | -121.9574 | -121.9345 | 113.4018 | 0.05951 | 78.9459 | 0.073242
4351.7656 | 122.0169 | -0.041199 | 121.8613 | -0.012131 | 0.2381 | 0.21279 | -0.0063724 | 0.090948 | 0.0912 | -0.000673 | -0.005371 | 0.022103 | 0.041353 | -0.01891 | 0.014257 | 0.024391 | -0.00042085 | 79.0009 | 121.843 | -0.027466 | 113.7131 | 121.7743 | 116.6702 | 114.7705 | 0.10529 | -0.013733 | -0.013733 | 0.064087 | 0.16937 | 0.1236 | 0.14191 | 0.013733 | -0.01831 | -8.1482 | 121.8155 | 114.8117 | 116.7114 | 114.798 | 116.6977 | 0.027466 | -121.875 | -121.7972 | 0.21057 | 0.18311 | 0.16479 | 0.15564 | 0.13733 | 121.8018 | 113.7405 | 0.18311 | 0.07782 | 121.8704 | 0 | 121.8842 | 0.027466 | -121.8887 | -121.875 | 113.7543 | 0.10529 | 79.0421 | 0.14649
4353.5312 | 121.9299 | -0.086975 | 121.875 | -0.012131 | 0.23639 | 0.21514 | -0.006586 | 0.091589 | 0.089277 | -0.0013138 | -0.0023192 | 0.021249 | 0.040499 | -0.018696 | 0.014471 | 0.022255 | -0.0049069 | 78.8635 | 121.8338 | -0.045776 | 113.7817 | 121.7239 | 116.7023 | 114.5508 | 0.032043 | 0.009155 | -0.045776 | -0.027466 | 0.073242 | 0.032043 | 0.054932 | 0.041199 | -0.041199 | -8.0933 | 121.8109 | 114.6378 | 116.7892 | 114.5966 | 116.748 | 0.041199 | -121.8658 | -121.9025 | 0.16022 | 0.14191 | 0.11902 | 0.10071 | 0.077819 | 121.7697 | 113.8275 | 0.11902 | 0.01831 | 121.8796 | 0.054931 | 121.9208 | 0.09613 | -121.9208 | -121.9208 | 113.8687 | 0.059509 | 78.9505 | 0.11902
4355.2969 | 121.994 | -0.045776 | 121.8338 | -0.012131 | 0.24045 | 0.22069 | -0.0074404 | 0.08988 | 0.090132 | -0.00345 | -0.005371 | 0.019326 | 0.040712 | -0.018269 | 0.012121 | 0.0261 | -0.00063445 | 78.9276 | 121.8201 | 0 | 113.9511 | 121.7651 | 116.8579 | 114.5645 | 0.10071 | -0.032043 | -0.013733 | 0.059509 | 0.15564 | 0.1236 | 0.13275 | 0.045776 | -0.013733 | -7.8827 | 121.8109 | 114.6103 | 116.9037 | 114.5645 | 116.8579 | 0.032043 | -121.8658 | -121.7743 | 0.20142 | 0.17853 | 0.16937 | 0.14648 | 0.13733 | 121.7651 | 113.9511 | 0.16937 | 0.073242 | 121.8201 | -0.01831 | 121.8658 | 0.013733 | -121.8338 | -121.8475 | 113.9969 | 0.10528 | 78.9734 | 0.14648
4357.0156 | 122.0032 | -0.059509 | 121.8292 | -0.01976 | 0.26096 | 0.25081 | -0.010431 | 0.08518 | 0.087996 | -0.0040908 | -0.0084228 | 0.019967 | 0.04178 | -0.01186 | 0.01148 | 0.025246 | -0.0019163 | 78.4515 | 121.8018 | 0.013733 | 114.061 | 121.8109 | 116.9083 | 114.6652 | 0.11444 | -0.018311 | -0.004578 | 0.050354 | 0.19226 | 0.15106 | 0.1236 | 0.073242 | -0.027466 | -7.7682 | 121.8704 | 114.7247 | 116.9678 | 114.6515 | 116.8945 | 0.054931 | -121.8475 | -121.7789 | 0.25177 | 0.1831 | 0.21057 | 0.12817 | 0.15564 | 121.7972 | 114.0472 | 0.19684 | 0.054932 | 121.788 | -0.013733 | 121.8613 | 0.041198 | -121.8155 | -121.8338 | 114.1205 | 0.10986 | 78.511 | 0.17395
4358.7969 | 121.962 | -0.07782 | 121.8155 | -0.01976 | 0.44296 | 0.41103 | -0.0087222 | 0.093511 | 0.088637 | -0.0013138 | -0.011475 | 0.018899 | 0.043276 | -0.012501 | 0.012762 | 0.02311 | -0.00020725 | 78.7399 | 121.788 | 0.027466 | 113.5757 | 121.701 | 116.2399 | 114.1525 | 0.045776 | -0.022888 | 0 | -0.004578 | 0.10986 | 0.091553 | 0.10529 | 0.10529 | -0.027466 | -8.2397 | 121.7789 | 114.2303 | 116.3177 | 114.1251 | 116.2125 | 0.07782 | -121.8384 | -121.8201 | 0.18768 | 0.18311 | 0.16937 | 0.10529 | 0.091553 | 121.6736 | 113.5483 | 0.10986 | -0.004578 | 121.7606 | -0.022888 | 121.8658 | 0.054932 | -121.788 | -121.8155 | 113.6536 | 0.073242 | 78.8177 | 0.1236
4360.5156 | 121.994 | -0.050354 | 121.7972 | -0.02739 | 0.52884 | 0.5093 | -0.0061588 | 0.087957 | 0.088423 | -0.0049454 | -0.0023192 | 0.021249 | 0.040285 | -0.015919 | 0.013189 | 0.023751 | -0.0019163 | 78.3691 | 121.788 | 0.009155 | 111.7767 | 121.7606 | 115.2969 | 113.8 | 0.10986 | -0.009155 | -0.013733 | 0.07782 | 0.16937 | 0.12817 | 0.15106 | 0.059509 | -0.009155 | -10.0204 | 121.8109 | 113.8504 | 115.3473 | 113.7909 | 115.2878 | 0.036621 | -121.8063 | -121.7194 | 0.21973 | 0.20142 | 0.17853 | 0.16479 | 0.14191 | 121.7514 | 111.7676 | 0.18311 | 0.091553 | 121.7789 | 0.004578 | 121.8384 | 0.041199 | -121.788 | -121.8109 | 111.8271 | 0.12817 | 78.4195 | 0.16022
4362.2969 | 121.9986 | -0.054932 | 121.8201 | -0.0045011 | 0.0095234 | 0.0089936 | -0.010004 | -0.0034735 | -0.0079212 | -0.0032364 | -0.005371 | 0.019967 | 0.040499 | -0.020192 | 0.012548 | 0.025673 | -0.0029843 | 3.1357 | 3.2822 | 3.1403 | 3.2089 | 3.4012 | 3.241 | 3.2501 | 0.11902 | -0.013733 | -0.013733 | 0.059509 | 0.1831 | 0.16479 | 0.12817 | 3.1952 | -118.5379 | -118.6111 | 3.4561 | 3.3051 | 3.2959 | 0.10986 | 0.10071 | 0.041199 | -121.8338 | -121.7606 | 0.23804 | 0.18311 | 0.21973 | 0.14191 | 0.17853 | 0.26093 | 0.068664 | 0.19684 | 0.073242 | 0.14191 | 0 | 3.3371 | 0.041199 | -118.6798 | -121.8338 | 3.2639 | 0.11444 | 3.1906 | 0.17395
4364.0625 | 121.9025 | -0.10986 | 121.8887 | -0.01976 | 0.016573 | 0.009848 | -0.0035952 | -0.0032599 | -0.0064258 | -0.00345 | -0.0084228 | 0.021676 | 0.039217 | -0.013356 | 0.010626 | 0.022042 | -0.00063445 | 2.9068 | 3.1403 | 2.9572 | 2.8839 | 2.9892 | 2.8656 | 2.9068 | -0.07782 | 0.036621 | -0.032043 | -0.050354 | 0.013733 | -0.018311 | 0.036621 | 3.067 | -118.7485 | -119.0048 | 3.0991 | 3.0167 | 2.9755 | -0.050354 | -0.091552 | 0.07782 | -121.8521 | -121.9391 | 0.1236 | 0.14648 | 0.091552 | 0.068664 | 0.013732 | 0.032044 | -0.073242 | 0.045776 | -0.018311 | 0.18311 | 0.068664 | 3.2501 | 0.14648 | -118.9316 | -121.9208 | 2.9938 | 0.059509 | 3.0167 | 0.032043
4365.7656 | 122.0261 | -0.073242 | 121.8658 | -0.01976 | 0.013155 | 0.00878 | -0.0095766 | -0.0015509 | -0.0083484 | -0.0021682 | -0.0084228 | 0.020395 | 0.039644 | -0.013569 | 0.011907 | 0.024178 | -0.0081113 | 2.8976 | 3.0991 | 2.9617 | 2.9617 | 3.1219 | 2.9846 | 3.0212 | 0.050354 | -0.022888 | -0.018311 | 0.032043 | 0.15564 | 0.13733 | 0.13733 | 3.035 | -118.7668 | -118.9041 | 3.1952 | 3.0945 | 3.0579 | 0.059509 | 0.022888 | 0.054931 | -121.8887 | -121.8338 | 0.22888 | 0.21057 | 0.21057 | 0.15564 | 0.15564 | 0.16022 | 0 | 0.17395 | 0.050354 | 0.13733 | -0.004577 | 3.1723 | 0.050354 | -118.9041 | -121.8842 | 3.035 | 0.10529 | 2.9709 | 0.1236
4367.5469 | 122.0627 | -0.041199 | 121.8842 | -0.012131 | 0.0093098 | 0.0094208 | -0.0074404 | -0.00091006 | -0.0077074 | -0.0028092 | -0.005371 | 0.019113 | 0.039217 | -0.017628 | 0.01383 | 0.023537 | -0.0044797 | 2.9709 | 3.0808 | 2.9709 | 3.035 | 3.1998 | 3.0487 | 3.067 | 0.12817 | -0.027466 | 0 | 0.059509 | 0.19226 | 0.16479 | 0.13275 | 3.0121 | -118.8034 | -118.8492 | 3.241 | 3.1082 | 3.0899 | 0.096131 | 0.07782 | 0.041199 | -121.9116 | -121.8246 | 0.23346 | 0.17395 | 0.20599 | 0.13275 | 0.16479 | 0.22888 | 0.064087 | 0.19226 | 0.059509 | 0.10986 | -0.027466 | 3.1219 | 0.013733 | -118.9133 | -121.8842 | 3.0762 | 0.10071 | 3.0121 | 0.16937
4369.25 | 121.9757 | -0.086975 | 121.9345 | -0.012131 | 0.013796 | 0.0083526 | -0.0061588 | -0.0021919 | -0.010057 | -0.002382 | -0.0023192 | 0.019967 | 0.04178 | -0.010365 | 0.016821 | 0.022469 | -0.0038389 | 2.9297 | 3.1494 | 2.948 | 2.9251 | 3.0396 | 2.9617 | 2.9434 | -0.018311 | 0.032043 | -0.032043 | -0.013733 | 0.082397 | 0.059509 | 0.082397 | 3.035 | -118.7851 | -119.0094 | 3.1265 | 3.0304 | 3.0487 | -0.004578 | 0.013733 | 0.054932 | -121.9025 | -121.9482 | 0.16937 | 0.16937 | 0.14648 | 0.11444 | 0.091552 | 0.091553 | -0.022888 | 0.11444 | 0.01831 | 0.20142 | 0.064086 | 3.2364 | 0.11902 | -118.9865 | -121.9666 | 3.0121 | 0.073242 | 3.0167 | 0.068664
4371.0156 | 121.9803 | -0.11444 | 121.9162 | -0.0045011 | 0.011232 | 0.010916 | -0.0067996 | -0.0013373 | -0.010271 | -0.0036636 | -0.005371 | 0.022531 | 0.040071 | -0.0088695 | 0.015325 | 0.025246 | -0.0034117 | 2.9068 | 3.1174 | 2.9434 | 2.9114 | 3.0121 | 2.916 | 2.9343 | -0.045776 | 0.018311 | -0.059509 | -0.054932 | 0.086975 | 0.041199 | 0.07782 | 3.0579 | -118.7988 | -119.0048 | 3.1265 | 3.0487 | 3.0304 | -0.009155 | -0.027465 | 0.054932 | -121.8979 | -121.9711 | 0.20142 | 0.19226 | 0.15564 | 0.13733 | 0.10071 | 0.068665 | -0.032043 | 0.14648 | 0.004577 | 0.17395 | 0.07782 | 3.2318 | 0.13275 | -118.9728 | -121.9757 | 3.0258 | 0.059509 | 3.0212 | 0.068665
4372.7188 | 121.994 | -0.073242 | 121.9299 | -0.02739 | 0.015078 | 0.01113 | -0.007654 | -0.00048286 | -0.0092028 | -0.0015274 | -0.005371 | 0.021035 | 0.041353 | -0.01186 | 0.015752 | 0.024178 | -0.0046933 | 2.9114 | 3.0991 | 2.9343 | 2.916 | 3.0624 | 2.9205 | 2.9434 | 0.041199 | 0.018311 | -0.050354 | 0.009155 | 0.10986 | 0.064087 | 0.091553 | 3.0075 | -118.8309 | -119.014 | 3.1357 | 3.0167 | 2.9938 | 0.009155 | -0.013733 | 0.022888 | -121.9116 | -121.9208 | 0.18311 | 0.16479 | 0.13733 | 0.14191 | 0.11444 | 0.12817 | -0.01831 | 0.16022 | 0.059509 | 0.1648 | 0.068665 | 3.1723 | 0.091553 | -118.9957 | -121.9803 | 2.9892 | 0.082397 | 2.9846 | 0.11444
4374.4844 | 122.049 | -0.059509 | 121.9025 | -0.012131 | 0.009096 | 0.010489 | -0.0091494 | -0.00026906 | -0.008562 | -0.0025956 | -0.005371 | 0.018686 | 0.040285 | -0.01186 | 0.012762 | 0.024605 | -0.0017027 | 2.8519 | 3.0121 | 2.8976 | 2.8885 | 3.0258 | 2.8976 | 2.9388 | 0.013733 | -0.004578 | -0.027466 | 0 | 0.10529 | 0.091553 | 0.10529 | 2.9572 | -118.8904 | -119.014 | 3.0853 | 2.9984 | 2.9572 | 0.041199 | 0 | 0.032043 | -121.907 | -121.9025 | 0.16479 | 0.16479 | 0.15106 | 0.13275 | 0.11902 | 0.12817 | -0.009155 | 0.13275 | 0.027466 | 0.11444 | 0.022888 | 3.0716 | 0.054931 | -119.0048 | -121.9299 | 2.948 | 0.059509 | 2.9114 | 0.073242
4376.2031 | 122.0306 | -0.073242 | 121.9162 | -0.012131 | 0.011873 | 0.011984 | -0.0080814 | -0.0015509 | -0.0094164 | -0.0032364 | -0.005371 | 0.019967 | 0.039431 | -0.016347 | 0.014471 | 0.022469 | -0.0074705 | 2.8702 | 3.0396 | 2.916 | 2.916 | 3.0579 | 2.9114 | 2.9663 | 0.027466 | 0 | -0.018311 | -0.004578 | 0.10071 | 0.10071 | 0.091553 | 2.9892 | -118.8766 | -119.0002 | 3.1311 | 3.0396 | 2.9846 | 0.050354 | -0.004578 | 0.054931 | -121.9162 | -121.9208 | 0.17395 | 0.16479 | 0.17395 | 0.10986 | 0.11902 | 0.14191 | 0 | 0.11902 | 0.013733 | 0.1236 | 0.018311 | 3.1128 | 0.073242 | -119.0002 | -121.9345 | 2.9892 | 0.068664 | 2.9434 | 0.10071
4377.9688 | 121.962 | -0.13275 | 121.9482 | -0.012131 | 0.016359 | 0.012412 | -0.0038088 | 0.0029351 | -0.0074938 | -0.0030228 | 0.00073235 | 0.022958 | 0.040712 | -0.012715 | 0.015325 | 0.022683 | -0.0019163 | 2.9114 | 3.0899 | 2.9388 | 2.8748 | 2.9984 | 2.861 | 2.8885 | -0.022888 | 0.022888 | -0.036621 | -0.059509 | 0.032043 | -0.013733 | 0.018311 | 3.0716 | -118.8583 | -119.0735 | 3.1311 | 3.0212 | 2.9938 | -0.050354 | -0.07782 | 0.09613 | -121.9254 | -122.0078 | 0.16479 | 0.15106 | 0.11902 | 0.054932 | 0.022888 | 0.059509 | -0.064087 | 0.068664 | -0.022888 | 0.15106 | 0.059509 | 3.2227 | 0.15564 | -119.0094 | -121.9849 | 3.0075 | 0.073242 | 3.0441 | 0.10986
4379.75 | 121.9711 | -0.10986 | 121.9803 | -0.01976 | 0.009737 | 0.0096344 | -0.0089358 | 0.0014397 | -0.0098438 | -0.001741 | -0.0084228 | 0.021463 | 0.04178 | -0.0082287 | 0.012975 | 0.023323 | -0.0034117 | 2.948 | 3.1677 | 2.9938 | 2.9388 | 3.0716 | 2.9434 | 2.9846 | -0.036621 | 0.022888 | -0.041199 | -0.091553 | 0.036621 | 0.018311 | 0.027466 | 3.1036 | -118.8126 | -119.0414 | 3.1815 | 3.0945 | 3.0533 | -0.009155 | -0.050354 | 0.068664 | -121.9574 | -122.0718 | 0.14648 | 0.13733 | 0.12817 | 0.068665 | 0.05951 | 0.07782 | -0.054931 | 0.07782 | -0.050354 | 0.17395 | 0.064087 | 3.2776 | 0.13275 | -118.9865 | -122.0215 | 3.0487 | 0.01831 | 3.0579 | 0.073242
4381.4531 | 122.0032 | -0.10071 | 121.9666 | -0.0045011 | 0.011232 | 0.0089936 | -0.0063724 | 0.00037174 | -0.00963 | -0.0004592 | -0.005371 | 0.022744 | 0.042421 | -0.020405 | 0.014257 | 0.02311 | -0.0014891 | 2.9663 | 3.1723 | 2.9984 | 2.9343 | 3.0441 | 2.9617 | 2.9846 | -0.064087 | 0.013733 | -0.036621 | -0.050354 | 0.054932 | 0.027466 | 0.059509 | 3.0991 | -118.7943 | -119.0323 | 3.1448 | 3.0853 | 3.0624 | -0.013733 | -0.036621 | 0.064087 | -121.9528 | -122.0169 | 0.15564 | 0.16022 | 0.12817 | 0.09613 | 0.064087 | 0.045776 | -0.064087 | 0.091553 | -0.013733 | 0.17395 | 0.050354 | 3.273 | 0.11444 | -118.9682 | -122.0032 | 3.035 | 0.050354 | 3.067 | 0.036621
4383.2188 | 122.0718 | -0.059509 | 121.9254 | -0.012131 | 0.016146 | 0.012412 | -0.0074404 | -0.00026906 | -0.0070666 | -0.0015274 | -0.011475 | 0.019967 | 0.041567 | -0.018483 | 0.014898 | 0.025246 | -0.00063445 | 2.8519 | 3.0579 | 2.8931 | 2.8564 | 2.9846 | 2.829 | 2.8839 | 0.018311 | -0.009155 | -0.018311 | 0.018311 | 0.11444 | 0.068665 | 0.10071 | 2.9526 | -118.8675 | -119.0689 | 3.0441 | 2.9434 | 2.8885 | -0.009155 | -0.064087 | 0.041198 | -121.9345 | -121.907 | 0.17395 | 0.16022 | 0.12817 | 0.11902 | 0.086976 | 0.091553 | -0.036621 | 0.13275 | 0.036622 | 0.16479 | 0.009156 | 3.1174 | 0.050354 | -119.0323 | -121.9437 | 2.916 | 0.07782 | 2.9114 | 0.07782
4384.9844 | 122.0306 | -0.091553 | 121.9666 | -0.01976 | 0.0123 | 0.0085662 | -0.0067996 | 0.0018671 | -0.0087756 | -0.0021682 | -0.005371 | 0.022744 | 0.040285 | -0.015278 | 0.014898 | 0.025032 | -0.0029843 | 2.9663 | 3.1586 | 2.9938 | 2.9617 | 3.0762 | 2.9846 | 2.9984 | 0.004578 | 0.027466 | -0.022888 | -0.018311 | 0.10529 | 0.054932 | 0.07782 | 3.0853 | -118.808 | -119.0048 | 3.1677 | 3.0899 | 3.0762 | 0.004578 | -0.009155 | 0.068665 | -121.9391 | -121.9849 | 0.19684 | 0.16937 | 0.14649 | 0.10071 | 0.07782 | 0.082398 | -0.032043 | 0.12817 | 0.004577 | 0.16479 | 0.050354 | 3.2501 | 0.11902 | -118.9728 | -121.9894 | 3.0533 | 0.073242 | 3.0579 | 0.096131
4386.7656 | 122.0627 | -0.073242 | 121.9666 | -0.01976 | 0.014009 | 0.01113 | -0.0042362 | 0.0042169 | -0.008562 | -0.0055862 | -0.0023192 | 0.021035 | 0.040071 | -0.0095105 | 0.014257 | 0.0261 | -0.0027707 | 2.8656 | 3.0441 | 2.9068 | 2.8656 | 2.9892 | 2.8473 | 2.8931 | -0.004578 | 0.013733 | -0.018311 | 0.009155 | 0.11444 | 0.07782 | 0.10071 | 2.98 | -118.9224 | -119.101 | 3.0624 | 2.9663 | 2.9205 | -0.013733 | -0.059509 | 0.054931 | -121.9528 | -121.9574 | 0.18768 | 0.17395 | 0.15106 | 0.11902 | 0.096131 | 0.082398 | -0.041198 | 0.13275 | 0.027466 | 0.13733 | 0.032044 | 3.1174 | 0.086975 | -119.0598 | -121.9849 | 2.9388 | 0.082397 | 2.9388 | 0.068664
4388.5 | 122.0901 | -0.082397 | 121.9757 | -0.012131 | 0.014009 | 0.011343 | -0.0067996 | 0.0022943 | -0.0092028 | -0.0036636 | -0.0023192 | 0.020822 | 0.039217 | -0.013356 | 0.015325 | 0.024605 | -0.0017027 | 2.8702 | 3.067 | 2.9022 | 2.8748 | 2.9984 | 2.861 | 2.8931 | 0.027466 | 0 | -0.027466 | 0.018311 | 0.1236 | 0.086975 | 0.12817 | 2.9846 | -118.9087 | -119.101 | 3.0807 | 2.9755 | 2.9434 | -0.009156 | -0.041199 | 0.054931 | -121.9757 | -121.9574 | 0.20599 | 0.21057 | 0.16937 | 0.15564 | 0.11444 | 0.09613 | -0.027466 | 0.15106 | 0.045777 | 0.16479 | 0.027466 | 3.1494 | 0.082397 | -119.0735 | -122.0032 | 2.9572 | 0.10071 | 2.9526 | 0.10986
4390.2656 | 121.9894 | -0.09613 | 121.9803 | -0.012131 | 0.010591 | 0.009848 | -0.0078676 | 0.0012261 | -0.010698 | -0.0025956 | -0.005371 | 0.020608 | 0.039003 | -0.012929 | 0.011907 | 0.0261 | -0.0051205 | 2.9297 | 3.1403 | 2.9846 | 2.9388 | 3.0716 | 2.9617 | 2.9984 | -0.054932 | 0.022888 | -0.050354 | -0.07782 | 0.036621 | 0.013733 | 0.027466 | 3.0807 | -118.84 | -119.0414 | 3.1677 | 3.0945 | 3.0579 | 0.013733 | -0.022888 | 0.045776 | -121.9574 | -122.0581 | 0.13275 | 0.1236 | 0.10986 | 0.07782 | 0.064087 | 0.086975 | -0.045776 | 0.086975 | -0.027466 | 0.15564 | 0.073242 | 3.2364 | 0.11902 | -118.9957 | -122.0306 | 3.035 | 0.01831 | 3.0258 | 0.041198
4392.0312 | 122.1222 | -0.073242 | 121.9482 | -0.012131 | 0.010591 | 0.008139 | -0.008295 | 0.0016535 | -0.00963 | -0.001741 | -0.0084228 | 0.01954 | 0.038576 | -0.019124 | 0.011907 | 0.024819 | -0.0021299 | 2.9251 | 3.0716 | 2.9663 | 2.98 | 3.1036 | 2.9892 | 3.0579 | 0.059509 | -0.004578 | -0.018311 | 0.041199 | 0.17395 | 0.14648 | 0.13733 | 3.0396 | -118.8766 | -118.9682 | 3.1769 | 3.1311 | 3.0624 | 0.091552 | 0.022888 | 0.054931 | -121.9528 | -121.907 | 0.24719 | 0.21057 | 0.21973 | 0.15564 | 0.16479 | 0.13733 | 0.013733 | 0.19226 | 0.05951 | 0.10529 | 0.013733 | 3.1448 | 0.068664 | -118.9819 | -121.9666 | 3.0533 | 0.11444 | 2.9984 | 0.13275
4393.7344 | 122.1268 | -0.050354 | 121.9437 | -0.012131 | 0.011232 | 0.010275 | -0.010004 | 0.00058534 | -0.010485 | -0.0043046 | -0.005371 | 0.019113 | 0.039644 | -0.018269 | 0.014471 | 0.024605 | -0.0049069 | 2.9892 | 3.0853 | 2.9938 | 3.035 | 3.1998 | 3.0762 | 3.0945 | 0.13275 | -0.009155 | 0 | 0.059509 | 0.1831 | 0.17395 | 0.15106 | 3.0441 | -118.8583 | -118.9087 | 3.2501 | 3.1448 | 3.1265 | 0.10071 | 0.082398 | 0.050354 | -121.9528 | -121.8842 | 0.23346 | 0.20142 | 0.2243 | 0.15106 | 0.17395 | 0.20599 | 0.041199 | 0.1831 | 0.059509 | 0.091553 | -0.009155 | 3.1357 | 0.041199 | -118.9499 | -121.9437 | 3.0853 | 0.10986 | 3.0396 | 0.18311
4395.4844 | 122.049 | -0.11902 | 121.994 | -0.0045011 | 0.013369 | 0.01113 | -0.006586 | 0.00015814 | -0.012194 | -0.0004592 | -0.0023192 | 0.020608 | 0.039003 | -0.015065 | 0.01383 | 0.021187 | -0.0038389 | 2.98 | 3.154 | 2.9709 | 2.9663 | 3.0853 | 3.0075 | 3.0029 | -0.004578 | 0.018311 | -0.036621 | -0.022888 | 0.082397 | 0.050354 | 0.073242 | 3.0899 | -118.84 | -119.0277 | 3.2043 | 3.1219 | 3.1265 | 0.032044 | 0.036621 | 0.082398 | -121.9757 | -122.0169 | 0.20142 | 0.19226 | 0.16937 | 0.10986 | 0.086975 | 0.11444 | -0.004577 | 0.11902 | 0.013733 | 0.18311 | 0.054932 | 3.273 | 0.13733 | -119.0231 | -122.0306 | 3.0853 | 0.096131 | 3.0991 | 0.11444
4397.2031 | 122.0169 | -0.10529 | 121.994 | -0.01976 | 0.015718 | 0.011984 | -0.0063724 | 0.0022943 | -0.0081348 | -0.0011002 | -0.0084228 | 0.02189 | 0.040499 | -0.0092969 | 0.016393 | 0.02311 | -0.0044797 | 2.8702 | 3.0899 | 2.8931 | 2.8336 | 2.9388 | 2.8061 | 2.8656 | -0.073242 | 0.022888 | -0.064087 | -0.064087 | 0 | -0.013733 | 0.050354 | 2.9984 | -118.9041 | -119.1605 | 3.0441 | 2.9709 | 2.9114 | -0.027465 | -0.086975 | 0.041199 | -121.9711 | -122.0581 | 0.10529 | 0.15564 | 0.091553 | 0.11444 | 0.050354 | 0.045777 | -0.059509 | 0.064087 | 0 | 0.19684 | 0.086975 | 3.1952 | 0.12817 | -119.101 | -122.0581 | 2.9388 | 0.041199 | 2.9755 | 0.032044
4398.9688 | 122.1405 | -0.054932 | 121.962 | -0.01976 | 0.014864 | 0.011557 | -0.0078676 | 0.0042169 | -0.0066394 | -0.0040908 | -0.0023192 | 0.021463 | 0.039431 | -0.014424 | 0.015325 | 0.024605 | -0.0049069 | 2.916 | 3.0075 | 2.9114 | 2.9343 | 3.0533 | 2.9205 | 2.9572 | 0.1236 | -0.018311 | -0.004578 | 0.07782 | 0.16937 | 0.14191 | 0.14191 | 2.9663 | -118.9545 | -119.0277 | 3.1082 | 3.0121 | 2.9755 | 0.045776 | 0.009155 | 0.050354 | -121.9803 | -121.8842 | 0.22431 | 0.19684 | 0.19684 | 0.14649 | 0.14649 | 0.14191 | 0.022888 | 0.17395 | 0.082398 | 0.09613 | -0.013733 | 3.0624 | 0.036621 | -119.0506 | -121.9666 | 2.9892 | 0.13275 | 2.9709 | 0.17853
4400.75 | 122.0718 | -0.10071 | 121.9803 | -0.01976 | 0.012941 | 0.011343 | -0.0033816 | 0.0033623 | -0.0094164 | -0.0032364 | -0.005371 | 0.023172 | 0.04114 | -0.0054517 | 0.01618 | 0.023537 | -0.0021299 | 2.9617 | 3.1082 | 2.9755 | 2.948 | 3.0899 | 2.9617 | 2.9755 | 0.041199 | 0.022888 | -0.050354 | 0 | 0.091553 | 0.073242 | 0.091553 | 3.0762 | -118.8721 | -119.0323 | 3.1906 | 3.0762 | 3.0624 | 0 | -0.013733 | 0.050354 | -121.9574 | -121.9803 | 0.19226 | 0.19226 | 0.17395 | 0.14191 | 0.1236 | 0.11444 | -0.027466 | 0.14191 | 0.050354 | 0.13275 | 0.073242 | 3.2089 | 0.1236 | -119.0048 | -122.0306 | 3.0487 | 0.10071 | 3.0624 | 0.14191
4402.4688 | 122.1085 | -0.041199 | 121.962 | -0.012131 | 0.013155 | 0.0094208 | -0.0072268 | 0.00037174 | -0.0083484 | -0.0047318 | -0.0084228 | 0.019113 | 0.040712 | -0.015492 | 0.012975 | 0.023964 | 0.0029971 | 2.9022 | 2.98 | 2.8976 | 2.9572 | 3.1036 | 2.9388 | 2.9846 | 0.10071 | -0.013733 | 0.004578 | 0.059509 | 0.14648 | 0.1236 | 0.1236 | 2.9388 | -118.9819 | -119.0048 | 3.1448 | 3.0258 | 2.98 | 0.086975 | 0.041199 | 0.045777 | -121.9757 | -121.9025 | 0.18768 | 0.16479 | 0.16479 | 0.11902 | 0.11902 | 0.20599 | 0.059509 | 0.14191 | 0.054931 | 0.082398 | -0.018311 | 3.0212 | 0.027466 | -119.0643 | -121.9574 | 2.9984 | 0.10071 | 2.9434 | 0.14191
4404.2344 | 122.0581 | -0.10071 | 122.0032 | -0.02739 | 0.0095234 | 0.009848 | -0.0061588 | 0.0033623 | -0.006853 | -0.0036636 | -0.005371 | 0.022744 | 0.040712 | -0.01421 | 0.013403 | 0.022683 | -0.0042661 | 2.9388 | 3.1357 | 2.9846 | 2.9388 | 3.0258 | 2.9663 | 2.98 | -0.054932 | 0.022888 | -0.050354 | -0.059509 | 0.07782 | 0.032043 | 0.073242 | 3.0853 | -118.8675 | -119.0643 | 3.1265 | 3.0808 | 3.067 | -0.004577 | -0.01831 | 0.050354 | -121.9803 | -122.0627 | 0.17853 | 0.17395 | 0.13275 | 0.1236 | 0.082397 | 0.041199 | -0.045776 | 0.12817 | -0.009155 | 0.15106 | 0.073242 | 3.2364 | 0.1236 | -119.0186 | -122.0535 | 3.0396 | 0.041199 | 3.0396 | 0.045776
4406 | 122.1176 | -0.073242 | 122.0078 | -0.012131 | 0.014864 | 0.010703 | -0.0040224 | 0.0040033 | -0.010698 | -0.0028092 | -0.0023192 | 0.021035 | 0.039858 | -0.013142 | 0.014684 | 0.023537 | -0.0017027 | 2.8519 | 3.035 | 2.916 | 2.861 | 2.9617 | 2.829 | 2.8748 | 0.022888 | 0.004578 | -0.032043 | 0.022888 | 0.11444 | 0.086975 | 0.10529 | 2.9892 | -118.9728 | -119.1467 | 3.035 | 2.948 | 2.9022 | -0.041199 | -0.086976 | 0.041199 | -122.0032 | -121.9849 | 0.18768 | 0.17853 | 0.16022 | 0.13733 | 0.11902 | 0.045776 | -0.054932 | 0.14648 | 0.054931 | 0.11902 | 0.036621 | 3.1082 | 0.07782 | -119.0918 | -122.0398 | 2.9343 | 0.09613 | 2.9251 | 0.09613
4407.7188 | 122.1588 | -0.050354 | 121.962 | -0.0045011 | 0.009737 | 0.009848 | -0.0097904 | 0.0018671 | -0.0092028 | -0.0045182 | -0.0084228 | 0.018258 | 0.039217 | -0.027028 | 0.013616 | 0.022896 | -0.0014891 | 2.9617 | 3.0396 | 2.9663 | 3.0258 | 3.2043 | 3.0624 | 3.0808 | 0.12817 | -0.022888 | -0.004578 | 0.041199 | 0.18768 | 0.17395 | 0.13275 | 3.0167 | -118.9224 | -118.9362 | 3.2547 | 3.1311 | 3.1128 | 0.11444 | 0.09613 | 0.045776 | -121.9849 | -121.9208 | 0.23804 | 0.18311 | 0.2243 | 0.13733 | 0.17853 | 0.23804 | 0.059509 | 0.19226 | 0.045777 | 0.073242 | -0.01831 | 3.0899 | 0.027466 | -118.9957 | -121.9666 | 3.0762 | 0.091553 | 3.0121 | 0.17853
4409.4844 | 122.0764 | -0.086975 | 122.0169 | -0.01976 | 0.012728 | 0.010916 | -0.0074404 | 0.0061395 | -0.0092028 | -0.001741 | -0.011475 | 0.021676 | 0.040499 | -0.0071607 | 0.015112 | 0.022255 | -0.0066159 | 2.9388 | 3.1174 | 2.9572 | 2.9251 | 3.0304 | 2.9526 | 2.9617 | 0.004578 | 0.018311 | -0.032043 | -0.018311 | 0.091553 | 0.050354 | 0.091553 | 3.0441 | -118.8995 | -119.0918 | 3.1174 | 3.0487 | 3.0396 | 0.004578 | -0.004577 | 0.054932 | -121.9986 | -122.0352 | 0.17853 | 0.17853 | 0.13733 | 0.1236 | 0.082397 | 0.073243 | -0.032043 | 0.1236 | 0.013732 | 0.16022 | 0.050354 | 3.2043 | 0.10529 | -119.0598 | -122.049 | 3.0121 | 0.068664 | 3.0258 | 0.091553
4411.2031 | 122.0444 | -0.10071 | 121.9849 | -0.0045011 | 0.011446 | 0.010275 | -0.010004 | -0.00048286 | -0.010057 | -0.0013138 | -0.0084228 | 0.020822 | 0.040285 | -0.010579 | 0.013403 | 0.022683 | -0.0081113 | 2.9892 | 3.0762 | 2.9938 | 2.9984 | 3.1403 | 3.0396 | 3.0579 | 0.032043 | -0.004578 | -0.036621 | -0.041199 | 0.086975 | 0.059509 | 0.059509 | 3.0945 | -118.9087 | -118.9865 | 3.241 | 3.1586 | 3.1403 | 0.064087 | 0.045777 | 0.064087 | -121.9894 | -122.0261 | 0.18768 | 0.16022 | 0.16022 | 0.09613 | 0.09613 | 0.14648 | 0.004578 | 0.1236 | -0.004578 | 0.082398 | 0.032043 | 3.1769 | 0.09613 | -118.9911 | -122.0215 | 3.0991 | 0.059509 | 3.0899 | 0.13275
4412.9688 | 122.1451 | -0.054932 | 121.9574 | -0.012131 | 0.0095234 | 0.0089936 | -0.007654 | -0.0021919 | -0.011125 | -0.002382 | -0.0084228 | 0.016977 | 0.040712 | -0.013783 | 0.014471 | 0.023323 | -0.0012753 | 2.9984 | 3.067 | 2.9892 | 3.0533 | 3.186 | 3.067 | 3.0899 | 0.10986 | -0.013733 | -0.013733 | 0.032043 | 0.17853 | 0.16022 | 0.12817 | 3.0441 | -118.8904 | -118.9041 | 3.241 | 3.1448 | 3.1219 | 0.10071 | 0.07782 | 0.041199 | -121.9711 | -121.9254 | 0.23346 | 0.18311 | 0.21515 | 0.14191 | 0.17395 | 0.19684 | 0.064087 | 0.19226 | 0.045776 | 0.07782 | 0 | 3.1219 | 0.041199 | -118.9682 | -121.9711 | 3.1082 | 0.086975 | 3.0533 | 0.16479
4414.7344 | 122.1313 | -0.068665 | 121.9757 | -0.012131 | 0.010378 | 0.011771 | -0.0057314 | -0.00026906 | -0.0081348 | -0.0045182 | -0.0084228 | 0.020181 | 0.039217 | -0.019764 | 0.012121 | 0.022683 | -0.0040525 | 2.8931 | 3.0487 | 2.9343 | 2.9663 | 3.0853 | 2.9755 | 3.0258 | 0.054932 | -0.027466 | -0.022888 | 0.045776 | 0.14648 | 0.13733 | 0.12817 | 3.0029 | -118.927 | -119.0094 | 3.154 | 3.0945 | 3.0441 | 0.091553 | 0.041199 | 0.045777 | -122.0032 | -121.9299 | 0.21515 | 0.19684 | 0.20599 | 0.15106 | 0.16022 | 0.15106 | 0.032044 | 0.16937 | 0.068664 | 0.11444 | -0.004578 | 3.1174 | 0.041199 | -119.0414 | -121.9986 | 3.035 | 0.11444 | 2.9617 | 0.1236
4416.4375 | 122.113 | -0.059509 | 121.9574 | -0.01976 | 0.015718 | 0.012412 | -0.005945 | -0.0015509 | -0.0098438 | -0.0015274 | -0.005371 | 0.019754 | 0.040285 | -0.013356 | 0.015539 | 0.023964 | 0.0027835 | 2.9022 | 2.9846 | 2.8976 | 2.9526 | 3.0808 | 2.9297 | 2.9709 | 0.10986 | -0.018311 | 0.009155 | 0.050354 | 0.15106 | 0.1236 | 0.1236 | 2.9572 | -118.9728 | -119.0048 | 3.1403 | 3.0304 | 2.9892 | 0.073242 | 0.032043 | 0.068664 | -121.9757 | -121.907 | 0.21057 | 0.1831 | 0.1831 | 0.11444 | 0.11444 | 0.18311 | 0.054932 | 0.14191 | 0.041199 | 0.086975 | -0.027466 | 3.0441 | 0.041198 | -119.0598 | -121.9482 | 3.0121 | 0.10986 | 2.9617 | 0.16937
4418.2188 | 122.1542 | -0.068665 | 121.962 | -0.012131 | 0.011232 | 0.0096344 | -0.0078676 | 0.00015814 | -0.010698 | -0.0025956 | -0.0023192 | 0.020395 | 0.036226 | -0.010365 | 0.014043 | 0.022683 | -0.0042661 | 2.9938 | 3.0533 | 2.9755 | 3.0396 | 3.1815 | 3.0853 | 3.0899 | 0.11902 | -0.018311 | -0.009155 | 0.041199 | 0.17395 | 0.14648 | 0.13275 | 3.0441 | -118.9087 | -118.9224 | 3.2501 | 3.1586 | 3.154 | 0.11444 | 0.10986 | 0.05951 | -121.9803 | -121.9208 | 0.24261 | 0.20142 | 0.21515 | 0.14191 | 0.15564 | 0.20599 | 0.064087 | 0.1831 | 0.050354 | 0.07782 | -0.009156 | 3.1219 | 0.050354 | -118.9865 | -121.9711 | 3.1082 | 0.10986 | 3.0624 | 0.18768
4419.9844 | 122.0535 | -0.10529 | 121.9849 | -0.012131 | 0.014864 | 0.010703 | -0.004877 | 0.0022943 | -0.0074938 | -0.0040908 | -0.005371 | 0.024453 | 0.040926 | -0.010365 | 0.015539 | 0.021614 | -0.0046933 | 2.9343 | 3.0716 | 2.948 | 2.9343 | 3.0487 | 2.9205 | 2.9572 | 0.027466 | 0.022888 | -0.041199 | -0.013733 | 0.064087 | 0.022888 | 0.050354 | 3.0533 | -118.9133 | -119.0506 | 3.154 | 3.0624 | 3.0258 | 0.009155 | -0.027466 | 0.064087 | -121.962 | -121.9986 | 0.16937 | 0.15564 | 0.12817 | 0.091553 | 0.064087 | 0.10071 | -0.013733 | 0.10529 | 0.027466 | 0.1236 | 0.064087 | 3.1769 | 0.12817 | -119.0369 | -122.0261 | 3.0396 | 0.091553 | 3.0396 | 0.13275
4421.6875 | 122.0764 | -0.11444 | 122.0032 | -0.0045011 | 0.01166 | 0.010275 | -0.0070132 | 0.0016535 | -0.010271 | -0.0021682 | -0.011475 | 0.022103 | 0.042421 | -0.013356 | 0.013403 | 0.021187 | -0.0061887 | 2.9572 | 3.1448 | 2.9892 | 2.9251 | 3.0258 | 2.9617 | 2.9846 | -0.045776 | 0.027466 | -0.041199 | -0.045776 | 0.064087 | 0.032043 | 0.054932 | 3.1036 | -118.8583 | -119.0781 | 3.1403 | 3.0991 | 3.0762 | -0.004578 | -0.027466 | 0.073242 | -121.9757 | -122.049 | 0.17853 | 0.16937 | 0.14648 | 0.096131 | 0.073242 | 0.036621 | -0.064087 | 0.10529 | -0.004577 | 0.15564 | 0.068665 | 3.2593 | 0.14191 | -119.014 | -122.0444 | 3.0396 | 0.068665 | 3.0716 | 0.068665
4423.4531 | 122.1771 | -0.068665 | 121.9574 | -0.012131 | 0.010805 | 0.010275 | -0.0074404 | -0.00026906 | -0.0092028 | -0.0055862 | -0.0084228 | 0.021463 | 0.040285 | -0.015065 | 0.013616 | 0.024178 | -0.0034117 | 2.9434 | 3.0396 | 2.948 | 2.9984 | 3.1403 | 3.0121 | 3.0579 | 0.10986 | -0.018311 | -0.009155 | 0.07782 | 0.1831 | 0.16937 | 0.14191 | 3.0167 | -118.9178 | -118.959 | 3.2089 | 3.1265 | 3.0808 | 0.10986 | 0.064087 | 0.05951 | -121.9757 | -121.8796 | 0.25177 | 0.21057 | 0.23804 | 0.15106 | 0.17853 | 0.19226 | 0.050354 | 0.19226 | 0.086975 | 0.091553 | -0.009156 | 3.1082 | 0.050354 | -119.0094 | -121.9666 | 3.067 | 0.14649 | 3.0121 | 0.17853
4425.2188 | 122.0627 | -0.10071 | 122.0169 | -0.0045011 | 0.016787 | 0.011343 | -0.003168 | 0.00015814 | -0.005144 | -0.0019546 | -0.011475 | 0.020395 | 0.038149 | -0.0088695 | 0.013403 | 0.025032 | -0.0059751 | 2.8519 | 3.0258 | 2.8702 | 2.8107 | 2.916 | 2.8061 | 2.8519 | -0.045776 | 0.009155 | -0.041199 | -0.050354 | 0.027466 | 0 | 0.045776 | 2.9709 | -118.9911 | -119.2062 | 3.0167 | 2.9526 | 2.9068 | -0.01831 | -0.064087 | 0.059509 | -122.0078 | -122.0673 | 0.12817 | 0.14648 | 0.10071 | 0.086975 | 0.041199 | 0.045777 | -0.059509 | 0.068665 | -0.009155 | 0.15564 | 0.050354 | 3.1265 | 0.10986 | -119.1467 | -122.0581 | 2.9114 | 0.050354 | 2.9526 | 0.054932
4427 | 122.0352 | -0.12817 | 122.0398 | -0.0045011 | 0.01166 | 0.01113 | -0.0095766 | -0.00091006 | -0.0087756 | -0.0015274 | -0.0023192 | 0.022531 | 0.042635 | -0.016774 | 0.01383 | 0.022683 | -0.0076841 | 2.9297 | 3.1403 | 2.9892 | 2.9297 | 3.0441 | 2.9572 | 2.9846 | -0.050354 | 0.018311 | -0.059509 | -0.073242 | 0.032043 | 0.018311 | 0.041199 | 3.1174 | -118.8995 | -119.1101 | 3.1723 | 3.1128 | 3.0853 | -0.004578 | -0.032044 | 0.068665 | -122.0215 | -122.113 | 0.16022 | 0.16937 | 0.14649 | 0.10071 | 0.07782 | 0.054931 | -0.05951 | 0.091552 | -0.013733 | 0.15106 | 0.07782 | 3.2684 | 0.14649 | -119.0506 | -122.0993 | 3.0579 | 0.054932 | 3.0579 | 0.07782
4428.7188 | 122.2046 | -0.059509 | 121.9757 | -0.01976 | 0.010805 | 0.010275 | -0.0095766 | 0.0018671 | -0.010912 | -0.0060134 | -0.011475 | 0.018258 | 0.040926 | -0.016347 | 0.01148 | 0.022896 | -0.0053343 | 2.9617 | 3.0258 | 2.9709 | 3.0075 | 3.1815 | 3.0579 | 3.0716 | 0.13733 | -0.018311 | -0.022888 | 0.073242 | 0.19684 | 0.17395 | 0.14648 | 3.0304 | -118.9499 | -118.9682 | 3.241 | 3.1311 | 3.1174 | 0.10071 | 0.086975 | 0.036621 | -121.994 | -121.9025 | 0.25635 | 0.20599 | 0.23346 | 0.16937 | 0.19684 | 0.21057 | 0.036621 | 0.21973 | 0.09613 | 0.054932 | 0.004577 | 3.0853 | 0.041198 | -119.0048 | -121.9986 | 3.067 | 0.13275 | 3.0212 | 0.19684
4430.4844 | 122.0261 | -0.09613 | 122.0398 | -0.012131 | 0.015932 | 0.0094208 | -0.0050906 | -5.5462e-05 | -0.0092028 | -0.0032364 | -0.005371 | 0.022317 | 0.039858 | -0.015278 | 0.014684 | 0.022683 | -0.0027707 | 2.8839 | 3.0624 | 2.8885 | 2.8381 | 2.9205 | 2.8152 | 2.8519 | -0.073242 | 0.032043 | -0.050354 | -0.082397 | 0 | -0.027466 | 0.018311 | 2.9846 | -118.9774 | -119.2017 | 3.0167 | 2.948 | 2.9114 | -0.036621 | -0.073242 | 0.045776 | -122.0078 | -122.1222 | 0.09613 | 0.11444 | 0.068664 | 0.068665 | 0.022888 | 0.032043 | -0.050354 | 0.050354 | -0.032043 | 0.17395 | 0.082397 | 3.1586 | 0.12817 | -119.1513 | -122.0901 | 2.9343 | 0.013733 | 2.98 | 0.022888
4432.2031 | 122.0078 | -0.09613 | 122.0352 | -0.012131 | 0.014223 | 0.0096344 | -0.0046634 | 0.0025079 | -0.008562 | -0.0008866 | -0.0084228 | 0.022531 | 0.04114 | -0.022114 | 0.013616 | 0.025887 | -0.0038389 | 2.8839 | 3.067 | 2.9068 | 2.8473 | 2.9297 | 2.829 | 2.8564 | -0.091553 | 0.027466 | -0.050354 | -0.082397 | 0.013733 | -0.032043 | 0.036621 | 3.0029 | -118.9682 | -119.1879 | 3.0258 | 2.9526 | 2.9251 | -0.050354 | -0.07782 | 0.045776 | -122.0078 | -122.1176 | 0.10986 | 0.13275 | 0.064087 | 0.086975 | 0.018311 | 0.022888 | -0.059509 | 0.064087 | -0.032043 | 0.16022 | 0.07782 | 3.1631 | 0.1236 | -119.1284 | -122.0856 | 2.9434 | 0.013733 | 2.98 | 0.004577
4433.9688 | 122.1039 | -0.091553 | 122.0123 | -0.012131 | 0.013155 | 0.0089936 | -0.0085086 | 0.0042169 | -0.010271 | -0.0019546 | -0.005371 | 0.022958 | 0.04114 | -0.0099377 | 0.015752 | 0.023323 | -0.0070433 | 2.9709 | 3.1219 | 2.9755 | 2.9434 | 3.0624 | 2.948 | 2.98 | 0.022888 | 0.027466 | -0.018311 | -0.004578 | 0.082397 | 0.050354 | 0.07782 | 3.067 | -118.8904 | -119.0689 | 3.154 | 3.0716 | 3.0396 | 0.004578 | -0.027466 | 0.073242 | -121.9849 | -122.0169 | 0.17395 | 0.16937 | 0.14191 | 0.096131 | 0.068665 | 0.086975 | -0.032044 | 0.10071 | 0.013733 | 0.14648 | 0.045777 | 3.2135 | 0.11902 | -119.0369 | -122.0306 | 3.035 | 0.086975 | 3.0624 | 0.11444
4435.7344 | 122.1359 | -0.059509 | 121.9757 | -0.0045011 | 0.014009 | 0.011771 | -0.0085086 | 0.0016535 | -0.008562 | -0.0019546 | -0.005371 | 0.018686 | 0.03879 | -0.015492 | 0.011907 | 0.024605 | -0.0029843 | 2.8839 | 2.9938 | 2.916 | 2.916 | 3.0441 | 2.9297 | 2.9709 | 0.027466 | -0.013733 | -0.027466 | -0.009155 | 0.10071 | 0.09613 | 0.091553 | 2.9755 | -118.9819 | -119.0598 | 3.1036 | 3.0304 | 2.9892 | 0.054931 | 0.013732 | 0.032043 | -121.9894 | -121.9849 | 0.16022 | 0.15106 | 0.15564 | 0.11902 | 0.1236 | 0.12817 | 0 | 0.12817 | 0.018311 | 0.077819 | 0.013733 | 3.0533 | 0.045776 | -119.0598 | -122.0032 | 2.9755 | 0.050354 | 2.9434 | 0.086975
4437.4375 | 122.0673 | -0.09613 | 122.0398 | -0.012131 | 0.015505 | 0.0094208 | -0.0057314 | 0.0010125 | -0.008562 | -0.0040908 | -0.0084228 | 0.020395 | 0.042849 | -0.012715 | 0.014898 | 0.023964 | -0.0038389 | 2.9388 | 3.0716 | 2.9343 | 2.9068 | 3.0212 | 2.9022 | 2.9297 | -0.004578 | 0.027466 | -0.032043 | -0.054932 | 0.045776 | 0.022888 | 0.041199 | 3.0304 | -118.9682 | -119.133 | 3.1174 | 3.0258 | 2.9984 | -0.004578 | -0.032043 | 0.064087 | -122.0123 | -122.0947 | 0.14191 | 0.13733 | 0.11902 | 0.073242 | 0.054931 | 0.086975 | -0.027466 | 0.077819 | -0.022889 | 0.13733 | 0.059509 | 3.1677 | 0.1236 | -119.1055 | -122.0718 | 3.0029 | 0.041198 | 3.035 | 0.091552
4439.2031 | 122.1954 | -0.054932 | 121.9986 | -0.012131 | 0.011019 | 0.012625 | -0.012354 | 0.0018671 | -0.011766 | -0.001741 | -0.005371 | 0.018899 | 0.037722 | -0.016774 | 0.010839 | 0.024605 | -0.0064023 | 2.9663 | 3.0441 | 2.98 | 3.0396 | 3.1906 | 3.0441 | 3.0853 | 0.10986 | -0.013733 | 0 | 0.050354 | 0.19226 | 0.17853 | 0.13733 | 3.035 | -118.9545 | -118.959 | 3.2455 | 3.1403 | 3.0991 | 0.10528 | 0.064086 | 0.054932 | -122.0123 | -121.9482 | 0.24719 | 0.19226 | 0.23346 | 0.13733 | 0.17853 | 0.21057 | 0.059509 | 0.19226 | 0.050354 | 0.064086 | -0.013733 | 3.0991 | 0.041199 | -119.0186 | -121.9986 | 3.0945 | 0.10529 | 3.0212 | 0.16479
4440.9688 | 122.0673 | -0.10529 | 122.0306 | -0.0045011 | 0.016146 | 0.011557 | -0.0057314 | 0.0040033 | -0.0074938 | -0.0049454 | -0.0084228 | 0.020395 | 0.04114 | -0.011433 | 0.015112 | 0.026314 | -0.00084805 | 2.9388 | 3.0624 | 2.9343 | 2.9251 | 3.035 | 2.9297 | 2.9434 | 0 | 0.022888 | -0.041199 | -0.036621 | 0.050354 | 0.027466 | 0.054932 | 3.0396 | -118.9682 | -119.1055 | 3.1403 | 3.0487 | 3.035 | 0.009155 | -0.004578 | 0.064087 | -122.0078 | -122.0673 | 0.15564 | 0.16022 | 0.13275 | 0.096131 | 0.068665 | 0.10071 | -0.009155 | 0.091553 | 0.004578 | 0.12817 | 0.064087 | 3.1677 | 0.12817 | -119.0964 | -122.0718 | 3.0304 | 0.068665 | 3.0441 | 0.10529
4442.7031 | 122.0856 | -0.10529 | 122.0627 | -0.0045011 | 0.014864 | 0.012198 | -0.0078676 | 0.0016535 | -0.010485 | -0.0013138 | -0.005371 | 0.021676 | 0.040499 | -0.0075879 | 0.014898 | 0.023323 | -0.0023435 | 2.9755 | 3.1219 | 2.9709 | 2.9526 | 3.0579 | 2.9572 | 2.9709 | 0.004578 | 0.027466 | -0.032043 | -0.032043 | 0.10071 | 0.059509 | 0.082397 | 3.0762 | -118.9407 | -119.1101 | 3.1631 | 3.0762 | 3.0624 | 0 | -0.013733 | 0.073243 | -122.0352 | -122.0947 | 0.20599 | 0.18768 | 0.16479 | 0.11444 | 0.091552 | 0.086975 | -0.01831 | 0.13275 | 0 | 0.15106 | 0.059509 | 3.2272 | 0.13275 | -119.0918 | -122.0947 | 3.0579 | 0.073243 | 3.0808 | 0.10986
4444.4688 | 122.0627 | -0.10529 | 122.0352 | -0.0045011 | 0.016573 | 0.011771 | -0.0067996 | 0.0037897 | -0.0079212 | -0.0013138 | -0.0023192 | 0.022531 | 0.040071 | -0.015706 | 0.015752 | 0.0261 | -0.0021299 | 2.8564 | 3.0396 | 2.8931 | 2.8244 | 2.916 | 2.7969 | 2.8473 | -0.073242 | 0.018311 | -0.064087 | -0.059509 | 0.013733 | -0.013733 | 0.036621 | 2.9984 | -118.9957 | -119.2108 | 3.0212 | 2.9526 | 2.9022 | -0.045776 | -0.09613 | 0.041199 | -122.0169 | -122.0947 | 0.11902 | 0.14191 | 0.091553 | 0.10071 | 0.050354 | 0.022889 | -0.068664 | 0.07782 | 0.004578 | 0.14648 | 0.082398 | 3.1448 | 0.1236 | -119.1422 | -122.0993 | 2.9297 | 0.045777 | 2.9617 | 0.032044
4446.2344 | 122.1725 | -0.064087 | 122.0032 | -0.012131 | 0.010378 | 0.01113 | -0.0091494 | -0.0039007 | -0.0094164 | -0.0015274 | -0.0023192 | 0.018258 | 0.041567 | -0.016347 | 0.012121 | 0.025032 | -0.0012753 | 2.9984 | 3.0441 | 2.9984 | 3.0441 | 3.1906 | 3.0808 | 3.0808 | 0.10986 | -0.018311 | -0.013733 | 0.045776 | 0.20142 | 0.16479 | 0.14648 | 3.0624 | -118.959 | -118.959 | 3.2547 | 3.1448 | 3.1448 | 0.082398 | 0.082398 | 0.050354 | -122.0215 | -121.9574 | 0.2655 | 0.21057 | 0.22888 | 0.16022 | 0.17853 | 0.19226 | 0.045776 | 0.21515 | 0.059509 | 0.045776 | -0.004578 | 3.1082 | 0.045776 | -119.0048 | -122.0169 | 3.1082 | 0.10986 | 3.0624 | 0.17395
4448 | 122.2 | -0.064087 | 121.9894 | -0.0045011 | 0.010805 | 0.0096344 | -0.009363 | -0.0028327 | -0.010698 | 0.0008224 | -0.0084228 | 0.018472 | 0.036226 | -0.021046 | 0.01383 | 0.02546 | -0.0064023 | 2.98 | 3.0441 | 2.9892 | 3.0304 | 3.2181 | 3.0762 | 3.1036 | 0.1236 | -0.009155 | -0.004578 | 0.036621 | 0.19226 | 0.16022 | 0.15106 | 3.0533 | -118.9453 | -118.959 | 3.2822 | 3.1677 | 3.1403 | 0.11444 | 0.086975 | 0.059509 | -121.9986 | -121.9528 | 0.25635 | 0.21515 | 0.2243 | 0.15564 | 0.16479 | 0.22888 | 0.041199 | 0.19684 | 0.041199 | 0.054931 | -0.004577 | 3.1082 | 0.054932 | -119.0002 | -121.994 | 3.0945 | 0.10071 | 3.0441 | 0.18768
4449.7031 | 122.1909 | -0.032043 | 122.0032 | -0.0045011 | 0.0093098 | 0.010703 | -0.0074404 | 0.00079894 | -0.0098438 | -0.0030228 | -0.005371 | 0.019113 | 0.039644 | -0.019978 | 0.011053 | 0.022896 | -0.0014891 | 2.9938 | 3.035 | 2.9892 | 3.0441 | 3.1906 | 3.0533 | 3.0991 | 0.13275 | -0.004578 | -0.013733 | 0.059509 | 0.19684 | 0.17395 | 0.13733 | 3.0212 | -118.9682 | -118.959 | 3.2227 | 3.1311 | 3.0853 | 0.10986 | 0.064087 | 0.01831 | -122.0078 | -121.9437 | 0.22888 | 0.16937 | 0.20599 | 0.15106 | 0.18768 | 0.20142 | 0.054931 | 0.21057 | 0.073242 | 0.045776 | 0.009155 | 3.067 | 0.027465 | -119.014 | -122.0169 | 3.0762 | 0.091552 | 3.0258 | 0.16479
4451.4688 | 122.1634 | -0.054932 | 122.0078 | -0.01976 | 0.014864 | 0.010916 | -0.0074404 | 0.00015814 | -0.0083484 | -0.002382 | -0.0084228 | 0.020608 | 0.040071 | -0.017415 | 0.012548 | 0.022255 | -0.0036253 | 2.9297 | 2.9663 | 2.9068 | 2.9343 | 3.0396 | 2.916 | 2.948 | 0.10986 | -0.022888 | -0.027466 | 0.086975 | 0.16022 | 0.13275 | 0.15106 | 2.9617 | -119.0414 | -119.0735 | 3.0945 | 3.0029 | 2.9709 | 0.041199 | 0.009156 | 0.027466 | -122.0306 | -121.9208 | 0.21515 | 0.20599 | 0.18768 | 0.17853 | 0.16022 | 0.13275 | 0.027466 | 0.18768 | 0.11444 | 0.05951 | 0.004578 | 3.0212 | 0.032044 | -119.101 | -122.0352 | 2.9892 | 0.14191 | 2.9846 | 0.16479
4453.1719 | 122.1863 | -0.045776 | 122.0078 | -0.0045011 | 0.015718 | 0.013907 | -0.0042362 | 0.0025079 | -0.0072802 | -0.0021682 | -0.005371 | 0.021463 | 0.039858 | -0.012715 | 0.012548 | 0.023751 | -0.0025571 | 2.8793 | 2.9755 | 2.8976 | 2.916 | 3.0212 | 2.8885 | 2.9526 | 0.09613 | -0.013733 | -0.018311 | 0.068665 | 0.13733 | 0.11444 | 0.15106 | 2.9434 | -119.0323 | -119.0918 | 3.067 | 2.9984 | 2.9343 | 0.054932 | -0.009155 | 0.027465 | -122.0215 | -121.9391 | 0.18311 | 0.19684 | 0.16022 | 0.16937 | 0.13275 | 0.1236 | 0.018311 | 0.15564 | 0.086976 | 0.07782 | 0.004578 | 3.0212 | 0.032043 | -119.1101 | -122.0261 | 2.9617 | 0.11444 | 2.9251 | 0.14191
4454.9688 | 122.0856 | -0.091553 | 122.0352 | -0.012131 | 0.011873 | 0.010489 | -0.0055178 | 0.0027215 | -0.0092028 | -0.00345 | -0.0084228 | 0.018899 | 0.039431 | -0.0099377 | 0.01383 | 0.023537 | -0.0031979 | 2.8381 | 3.0212 | 2.8702 | 2.8244 | 2.9297 | 2.8015 | 2.8564 | -0.036621 | 0.022888 | -0.045776 | -0.045776 | 0.022888 | 0 | 0.050354 | 2.9617 | -119.014 | -119.2108 | 3.0212 | 2.948 | 2.8931 | -0.013733 | -0.068664 | 0.045777 | -122.0123 | -122.081 | 0.11444 | 0.14191 | 0.091553 | 0.09613 | 0.045776 | 0.059509 | -0.045776 | 0.068664 | 0 | 0.15106 | 0.068664 | 3.1128 | 0.11444 | -119.165 | -122.081 | 2.916 | 0.045777 | 2.9297 | 0.054932
4456.7344 | 122.0673 | -0.11902 | 122.0627 | -0.0045011 | 0.0099506 | 0.008139 | -0.0085086 | 0.0010125 | -0.0094164 | -0.0043046 | -0.0084228 | 0.01954 | 0.039858 | -0.012715 | 0.014898 | 0.023323 | -0.0046933 | 2.8976 | 3.1036 | 2.9663 | 2.916 | 3.0441 | 2.9617 | 2.9892 | -0.045776 | 0.041199 | -0.041199 | -0.09613 | 0.036621 | 0.004578 | 0.018311 | 3.0853 | -118.959 | -119.1467 | 3.1631 | 3.1082 | 3.0808 | 0.022888 | -0.004578 | 0.07782 | -122.0215 | -122.1588 | 0.15564 | 0.13733 | 0.1236 | 0.05951 | 0.045777 | 0.077819 | -0.050354 | 0.07782 | -0.054931 | 0.13733 | 0.082398 | 3.2227 | 0.16022 | -119.0964 | -122.1039 | 3.035 | 0.022889 | 3.0167 | 0.073243
4458.4531 | 122.1863 | -0.050354 | 122.0169 | -0.01976 | 0.01465 | 0.011343 | -0.006586 | 0.0016535 | -0.006853 | -0.0030228 | -0.0084228 | 0.019754 | 0.040712 | -0.015492 | 0.013403 | 0.024391 | -0.0029843 | 2.8748 | 2.9388 | 2.8885 | 2.9251 | 3.0533 | 2.9114 | 2.9572 | 0.12817 | -0.032043 | -0.013733 | 0.059509 | 0.16479 | 0.13275 | 0.13733 | 2.9388 | -119.0781 | -119.0918 | 3.1036 | 3.0075 | 2.9617 | 0.068664 | 0.022888 | 0.036621 | -122.049 | -121.9574 | 0.21515 | 0.18768 | 0.18311 | 0.15106 | 0.14648 | 0.1648 | 0.036621 | 0.17853 | 0.073242 | 0.050354 | -0.01831 | 2.9892 | 0.018311 | -119.1284 | -122.0306 | 2.9755 | 0.10986 | 2.9251 | 0.17853
4460.2188 | 122.0764 | -0.1236 | 122.0352 | -0.012131 | 0.015291 | 0.011557 | -0.006586 | 0.0031487 | -0.0092028 | -0.0028092 | -0.005371 | 0.02189 | 0.040926 | -0.017415 | 0.014257 | 0.022896 | -0.0021299 | 2.8152 | 2.9755 | 2.8519 | 2.7832 | 2.9068 | 2.7786 | 2.8244 | -0.050354 | 0.022888 | -0.041199 | -0.036621 | 0.013733 | -0.004578 | 0.045776 | 2.9755 | -119.0598 | -119.252 | 3.0304 | 2.948 | 2.9022 | -0.027466 | -0.073243 | 0.082397 | -122.0123 | -122.0718 | 0.13733 | 0.16937 | 0.11902 | 0.086975 | 0.036621 | 0.054931 | -0.068665 | 0.054932 | 0.004578 | 0.1236 | 0.064087 | 3.0991 | 0.14648 | -119.1833 | -122.0764 | 2.9068 | 0.086975 | 2.9388 | 0.073242
4461.9219 | 122.1725 | -0.054932 | 122.0123 | -0.012131 | 0.015078 | 0.010916 | -0.0053042 | 0.0010125 | -0.0057848 | -0.00345 | -0.005371 | 0.02189 | 0.040499 | -0.013783 | 0.014684 | 0.022469 | -0.0044797 | 2.8152 | 2.9755 | 2.8473 | 2.8244 | 2.9434 | 2.8107 | 2.8473 | 0.041199 | 0.009155 | -0.027466 | 0.045776 | 0.12817 | 0.091553 | 0.1236 | 2.9022 | -119.0369 | -119.1879 | 2.9984 | 2.9022 | 2.8656 | 0 | -0.036621 | 0.027466 | -122.0032 | -121.9666 | 0.18311 | 0.17853 | 0.14649 | 0.15106 | 0.11902 | 0.09613 | -0.022888 | 0.15564 | 0.073242 | 0.12817 | 0.036621 | 3.0304 | 0.064087 | -119.165 | -122.0398 | 2.8793 | 0.10071 | 2.8702 | 0.096131
4463.6875 | 122.1451 | -0.068665 | 122.0078 | -0.0045011 | 0.013155 | 0.010916 | -0.010645 | 0.00037174 | -0.0083484 | -0.0036636 | -0.0084228 | 0.019754 | 0.039858 | -0.011433 | 0.011694 | 0.023964 | -0.0049069 | 2.861 | 2.948 | 2.8793 | 2.8976 | 3.0579 | 2.8839 | 2.9388 | 0.09613 | -0.022888 | -0.013733 | 0.045776 | 0.13275 | 0.11444 | 0.1236 | 2.948 | -119.0598 | -119.1101 | 3.1265 | 3.0075 | 2.9526 | 0.05951 | 0.004578 | 0.054932 | -122.0306 | -121.962 | 0.20142 | 0.19226 | 0.18311 | 0.13733 | 0.12817 | 0.17853 | 0.018311 | 0.14648 | 0.059509 | 0.068665 | -0.009155 | 3.0167 | 0.045777 | -119.1284 | -122.0215 | 2.9663 | 0.11444 | 2.9297 | 0.16479
4465.4531 | 122.1863 | -0.064087 | 122.0032 | -0.012131 | 0.010378 | 0.0092072 | -0.010004 | -0.0017645 | -0.0087756 | -0.005159 | -0.005371 | 0.021676 | 0.041994 | -0.011006 | 0.012121 | 0.025246 | -0.0023435 | 2.8519 | 2.9846 | 2.9022 | 2.9068 | 3.0212 | 2.9068 | 2.9617 | 0.041199 | -0.004578 | -0.022888 | 0.022888 | 0.13275 | 0.1236 | 0.13275 | 2.9663 | -119.0186 | -119.0964 | 3.0853 | 3.0258 | 2.9709 | 0.059509 | 0.004577 | 0.041199 | -122.0078 | -121.9803 | 0.19684 | 0.19684 | 0.18768 | 0.15564 | 0.14648 | 0.11902 | 0.004577 | 0.15564 | 0.045776 | 0.082397 | 0.01831 | 3.0487 | 0.059509 | -119.101 | -122.0261 | 2.9709 | 0.086975 | 2.916 | 0.10529
4467.2188 | 122.0993 | -0.10986 | 122.0444 | -0.012131 | 0.014223 | 0.010703 | -0.0044498 | 0.0048577 | -0.011125 | -0.0032364 | -0.005371 | 0.022958 | 0.04178 | -0.015278 | 0.011907 | 0.02311 | -0.0074705 | 2.9114 | 3.0396 | 2.9022 | 2.916 | 3.0304 | 2.9068 | 2.9205 | 0.032043 | 0 | -0.018311 | -0.004578 | 0.07782 | 0.050354 | 0.073242 | 3.0121 | -119.0048 | -119.1284 | 3.1403 | 3.0304 | 3.0167 | 0.01831 | 0.004577 | 0.091552 | -122.0444 | -122.049 | 0.18768 | 0.18311 | 0.16022 | 0.091553 | 0.068665 | 0.12817 | 0.013733 | 0.096131 | 0.013733 | 0.13733 | 0.018311 | 3.1494 | 0.10986 | -119.1422 | -122.0627 | 3.0258 | 0.10529 | 3.0212 | 0.14191
4468.9844 | 122.1313 | -0.091553 | 122.0398 | -0.012131 | 0.014223 | 0.012198 | -0.0072268 | 0.0014397 | -0.010912 | -0.0036636 | -0.005371 | 0.022103 | 0.039217 | -0.010792 | 0.014257 | 0.023751 | -0.0049069 | 2.9068 | 3.0258 | 2.9297 | 2.9022 | 3.0167 | 2.9068 | 2.9068 | 0.032043 | 0.018311 | -0.036621 | -0.004578 | 0.10986 | 0.059509 | 0.068665 | 3.0212 | -119.014 | -119.1376 | 3.1082 | 2.9984 | 2.9984 | -0.022888 | -0.022888 | 0.054932 | -122.0215 | -122.0444 | 0.20142 | 0.16022 | 0.15106 | 0.10529 | 0.09613 | 0.086976 | -0.027465 | 0.14648 | 0.032043 | 0.096131 | 0.054932 | 3.1174 | 0.10986 | -119.1101 | -122.0764 | 2.9938 | 0.086975 | 2.9984 | 0.1236
4470.6875 | 122.1039 | -0.09613 | 122.0261 | -0.0045011 | 0.014437 | 0.010703 | -0.0057314 | 0.0025079 | -0.010485 | -0.002382 | -0.0023192 | 0.022103 | 0.04114 | -0.01122 | 0.014043 | 0.023537 | -0.0046933 | 2.9114 | 3.0212 | 2.9022 | 2.8885 | 3.0167 | 2.8885 | 2.9297 | 0.018311 | 0.032043 | -0.032043 | 0.009155 | 0.10071 | 0.059509 | 0.086975 | 2.9984 | -119.0048 | -119.1376 | 3.1128 | 3.0258 | 2.9846 | 0.027465 | -0.013733 | 0.064087 | -121.994 | -122.0169 | 0.19684 | 0.1831 | 0.15564 | 0.11902 | 0.091552 | 0.11444 | -0.013733 | 0.13275 | 0.041198 | 0.11902 | 0.064086 | 3.1174 | 0.12817 | -119.1238 | -122.0581 | 2.9846 | 0.10528 | 3.0075 | 0.11444
4472.4531 | 122.1634 | -0.068665 | 122.0306 | -0.012131 | 0.011446 | 0.009848 | -0.0089358 | 0.00079894 | -0.0077074 | -3.1996e-05 | -0.005371 | 0.018899 | 0.040071 | -0.020833 | 0.012548 | 0.025246 | -0.0040525 | 2.8381 | 2.9526 | 2.8931 | 2.8748 | 3.0212 | 2.8885 | 2.9434 | 0.013733 | 0.009155 | -0.013733 | 0 | 0.11444 | 0.10986 | 0.10529 | 2.9617 | -119.0781 | -119.1559 | 3.0899 | 3.0121 | 2.9572 | 0.050354 | -0.004577 | 0.054932 | -122.0215 | -122.0306 | 0.18311 | 0.17395 | 0.17853 | 0.11902 | 0.1236 | 0.12817 | -0.01831 | 0.12817 | 0.013733 | 0.05951 | 0.022888 | 3.0212 | 0.07782 | -119.1376 | -122.0444 | 2.9434 | 0.068665 | 2.9068 | 0.082398
4474.1562 | 122.1405 | -0.07782 | 122.0169 | -0.0045011 | 0.014009 | 0.010703 | -0.0078676 | -0.0053961 | -0.0079212 | -0.0053726 | -0.005371 | 0.018899 | 0.039431 | -0.017628 | 0.014898 | 0.023323 | -0.0034117 | 2.8381 | 2.9251 | 2.8702 | 2.8839 | 3.0212 | 2.861 | 2.916 | 0.086975 | -0.009155 | -0.022888 | 0.022888 | 0.11444 | 0.086975 | 0.10071 | 2.948 | -119.0918 | -119.133 | 3.0991 | 2.9938 | 2.9388 | 0.045777 | -0.009155 | 0.054932 | -122.0261 | -121.994 | 0.19226 | 0.17853 | 0.16479 | 0.1236 | 0.10986 | 0.15106 | 0.013733 | 0.13733 | 0.045776 | 0.054932 | 0.013733 | 3.0029 | 0.068665 | -119.1467 | -122.0398 | 2.9617 | 0.10071 | 2.916 | 0.16479
4475.9219 | 122.1085 | -0.082397 | 122.0261 | -0.012131 | 0.013369 | 0.010062 | -0.0070132 | 0.00015814 | -0.011125 | -0.0021682 | -0.005371 | 0.023385 | 0.038576 | -0.012074 | 0.015752 | 0.024605 | -0.0040525 | 2.916 | 3.0212 | 2.8885 | 2.8839 | 3.0167 | 2.8885 | 2.916 | 0.045776 | 0.013733 | -0.018311 | -0.018311 | 0.10071 | 0.054932 | 0.068665 | 2.9709 | -119.0048 | -119.1422 | 3.0991 | 2.9984 | 2.9709 | 0.027466 | 0 | 0.064086 | -122.0123 | -122.0444 | 0.18311 | 0.15106 | 0.13733 | 0.086976 | 0.073243 | 0.12817 | -0.004578 | 0.11902 | 0 | 0.13275 | 0.032044 | 3.1036 | 0.09613 | -119.1376 | -122.0444 | 2.9663 | 0.064086 | 2.9984 | 0.12817
4477.6875 | 122.0627 | -0.10529 | 122.0398 | -0.012131 | 0.010164 | 0.010916 | -0.009363 | -0.0045417 | -0.01198 | -0.0013138 | -0.0023192 | 0.021249 | 0.039003 | -0.019337 | 0.012975 | 0.02311 | -0.0012753 | 2.8839 | 3.0579 | 2.9205 | 2.8885 | 3.0304 | 2.9068 | 2.9343 | -0.032043 | 0.013733 | -0.036621 | -0.064087 | 0.045776 | 0.032043 | 0.018311 | 3.0258 | -118.9819 | -119.1513 | 3.1357 | 3.0396 | 3.0121 | 0.013733 | -0.013733 | 0.068665 | -122.0261 | -122.1039 | 0.15106 | 0.1236 | 0.13733 | 0.054932 | 0.068664 | 0.10986 | -0.032043 | 0.082397 | -0.027466 | 0.13733 | 0.050354 | 3.1631 | 0.11902 | -119.1193 | -122.0764 | 2.9938 | 0.041199 | 2.9892 | 0.073243
4479.4531 | 122.1039 | -0.086975 | 122.0215 | -0.01976 | 0.010378 | 0.010062 | -0.009363 | -0.0028327 | -0.011766 | -0.0013138 | -0.005371 | 0.018686 | 0.040926 | -0.017842 | 0.012975 | 0.024178 | -0.0010617 | 2.9114 | 2.98 | 2.9068 | 2.9343 | 3.0808 | 2.98 | 3.0029 | 0.050354 | 0 | -0.027466 | -0.041199 | 0.10529 | 0.068665 | 0.082397 | 2.9938 | -119.0414 | -119.0872 | 3.1677 | 3.0899 | 3.067 | 0.096131 | 0.073243 | 0.059509 | -122.0215 | -122.0627 | 0.19226 | 0.16937 | 0.15564 | 0.10986 | 0.096131 | 0.17395 | 0.027466 | 0.13275 | -0.013733 | 0.073243 | 0.027466 | 3.067 | 0.086975 | -119.1147 | -122.049 | 3.0212 | 0.045776 | 2.9984 | 0.13733
4481.1562 | 122.1222 | -0.091553 | 122.0261 | -0.012131 | 0.01465 | 0.010916 | -0.0063724 | 0.0010125 | -0.0087756 | -0.0043046 | -0.0023192 | 0.019113 | 0.04114 | -0.013356 | 0.015966 | 0.024391 | 0.00021995 | 2.8976 | 3.0075 | 2.8885 | 2.8885 | 3.0075 | 2.8702 | 2.916 | 0.036621 | 0.018311 | -0.036621 | -0.013733 | 0.10071 | 0.064087 | 0.068665 | 2.98 | -119.0186 | -119.1376 | 3.0991 | 3.0075 | 2.9617 | 0.027466 | -0.018311 | 0.054932 | -122.0078 | -122.0398 | 0.19226 | 0.16022 | 0.15564 | 0.10529 | 0.10071 | 0.11902 | 0 | 0.13733 | 0.022888 | 0.11902 | 0.054932 | 3.0991 | 0.10986 | -119.1376 | -122.0627 | 2.98 | 0.07782 | 2.9892 | 0.12817
4482.9219 | 122.1359 | -0.073242 | 122.0032 | -0.01976 | 0.012941 | 0.0096344 | -0.008295 | 0.00058534 | -0.011339 | -0.00345 | -0.0023192 | 0.019113 | 0.040285 | -0.019764 | 0.012334 | 0.025032 | -0.0027707 | 2.8015 | 2.916 | 2.8244 | 2.8564 | 2.9938 | 2.8336 | 2.8793 | 0.064087 | -0.018311 | -0.022888 | 0.009155 | 0.11444 | 0.10071 | 0.10071 | 2.8976 | -119.0872 | -119.1467 | 3.067 | 2.9526 | 2.9068 | 0.054931 | 0.009155 | 0.050354 | -122.0215 | -121.994 | 0.18768 | 0.17395 | 0.17395 | 0.1236 | 0.1236 | 0.16937 | 0.032043 | 0.13733 | 0.032043 | 0.091553 | 0.004577 | 2.9892 | 0.054931 | -119.1788 | -122.0261 | 2.9297 | 0.082397 | 2.8748 | 0.13733
4484.6562 | 122.0718 | -0.10529 | 122.0352 | -0.0045011 | 0.014437 | 0.01113 | -0.0053042 | 0.0010125 | -0.0089892 | -0.0011002 | -0.005371 | 0.022958 | 0.041994 | -0.012288 | 0.014471 | 0.023751 | -0.0027707 | 2.7695 | 2.948 | 2.8152 | 2.7374 | 2.829 | 2.7283 | 2.7649 | -0.073242 | 0.009155 | -0.054932 | -0.050354 | 0.018311 | -0.013733 | 0.045776 | 2.9205 | -119.0872 | -119.2978 | 2.9343 | 2.8702 | 2.8336 | -0.050354 | -0.086976 | 0.050354 | -122.0261 | -122.0856 | 0.1236 | 0.15106 | 0.091553 | 0.10071 | 0.041199 | 0.013732 | -0.07782 | 0.073243 | 0.004578 | 0.13275 | 0.064087 | 3.0533 | 0.11444 | -119.22 | -122.0901 | 2.8427 | 0.054932 | 2.8748 | 0.032044
4486.4219 | 122.0581 | -0.10071 | 122.0398 | -0.01976 | 0.015291 | 0.011984 | -0.0055178 | 0.00079894 | -0.0077074 | -0.0008866 | -0.011475 | 0.022103 | 0.04114 | -0.0078015 | 0.014043 | 0.022469 | -0.0066159 | 2.8336 | 2.9526 | 2.8336 | 2.7924 | 2.9068 | 2.7832 | 2.7924 | -0.032043 | 0.027466 | -0.027466 | -0.059509 | 0.018311 | -0.018311 | 0.041199 | 2.9343 | -119.0872 | -119.2474 | 3.0075 | 2.8931 | 2.8839 | -0.041199 | -0.050354 | 0.073242 | -122.0123 | -122.0993 | 0.11902 | 0.14191 | 0.082397 | 0.068665 | 0.009155 | 0.073242 | -0.041199 | 0.045777 | -0.032043 | 0.11902 | 0.054932 | 3.0533 | 0.12817 | -119.2062 | -122.0673 | 2.8931 | 0.041199 | 2.9343 | 0.068665
4488.1406 | 122.1909 | -0.086975 | 122.049 | -0.012131 | 0.0095234 | 0.01113 | -0.009363 | -0.0058233 | -0.010485 | -0.0011002 | -0.005371 | 0.016763 | 0.041353 | -0.012288 | 0.010626 | 0.027809 | -0.00042085 | 2.8015 | 2.9251 | 2.8381 | 2.8519 | 2.9846 | 2.8564 | 2.9022 | 0.036621 | -0.018311 | -0.013733 | 0.009155 | 0.13275 | 0.12817 | 0.12817 | 2.9251 | -119.1238 | -119.1971 | 3.0716 | 2.9892 | 2.9434 | 0.064087 | 0.01831 | 0.073242 | -122.0673 | -122.0398 | 0.21973 | 0.21515 | 0.21515 | 0.14191 | 0.14191 | 0.14648 | 0.013733 | 0.14648 | 0.022888 | 0.086975 | -0.004578 | 3.0121 | 0.068664 | -119.2108 | -122.0627 | 2.9388 | 0.09613 | 2.8885 | 0.1236
4489.9062 | 122.1268 | -0.091553 | 122.0535 | -0.01976 | 0.013369 | 0.012412 | -0.0072268 | 0.0018671 | -0.0089892 | -0.00345 | -0.0023192 | 0.022103 | 0.041567 | -0.015919 | 0.01383 | 0.022896 | -0.0049069 | 2.8656 | 2.9938 | 2.8702 | 2.8519 | 2.9846 | 2.8656 | 2.8839 | 0.027466 | 0.022888 | -0.022888 | -0.013733 | 0.09613 | 0.059509 | 0.10529 | 2.9617 | -119.0598 | -119.2017 | 3.0762 | 2.9755 | 2.9572 | 0.013733 | -0.004577 | 0.068665 | -122.0306 | -122.0673 | 0.18768 | 0.19684 | 0.15106 | 0.12817 | 0.082397 | 0.11444 | -0.01831 | 0.11902 | 0.009155 | 0.1236 | 0.045776 | 3.0853 | 0.11444 | -119.1834 | -122.0764 | 2.9434 | 0.07782 | 2.9572 | 0.11902
4491.6719 | 121.9666 | -0.10986 | 121.9528 | -0.012131 | 0.011019 | 0.0083526 | -0.0089358 | -5.5462e-05 | -0.010698 | -0.0028092 | -0.005371 | 0.021035 | 0.042635 | -0.010365 | 0.012975 | 0.023323 | 6.346e-06 | 8.9447 | 9.0637 | 8.5144 | 8.9127 | 9.0363 | 8.9172 | 8.9539 | -0.059509 | 0.036621 | -0.059509 | -0.059509 | 0.036621 | 0.018311 | 0.054932 | 8.6243 | -112.8891 | -113.0402 | 9.1461 | 9.0637 | 9.0271 | 0.43945 | 0.40283 | 0.050354 | -121.9162 | -122.0123 | 0.14648 | 0.16479 | 0.12817 | 0.11444 | 0.07782 | 0.52185 | 0.39825 | 0.09613 | 0 | 0.54932 | 0.09613 | 9.1736 | 0.14648 | -113.4384 | -122.0123 | 9.0225 | 0.050354 | 9.0546 | 0.050354
4493.375 | 122.0398 | -0.11902 | 121.9894 | -0.012131 | 0.013369 | 0.013266 | -0.0055178 | -0.0011237 | -0.006853 | -3.1996e-05 | -0.0084228 | 0.023172 | 0.043062 | -0.013142 | 0.015539 | 0.023537 | -0.0040525 | 8.9539 | 8.9951 | 8.5144 | 8.8852 | 9.0088 | 8.8623 | 8.8943 | -0.032043 | 0.018311 | -0.027466 | -0.050354 | 0.027466 | -0.018311 | 0.032043 | 8.6334 | -112.9944 | -113.1042 | 9.1278 | 9.0134 | 8.9813 | 0.37994 | 0.3479 | 0.091553 | -121.9711 | -122.0398 | 0.14649 | 0.15106 | 0.10071 | 0.059509 | 0.009155 | 0.49438 | 0.37079 | 0.054932 | -0.022888 | 0.48065 | 0.045777 | 9.1141 | 0.13733 | -113.475 | -122.0169 | 9.0042 | 0.068665 | 9.0729 | 0.086976
4495.1406 | 122.0535 | -0.1236 | 122.0535 | -0.0045011 | 0.010164 | 0.010062 | -0.008295 | -0.0011237 | -0.0077074 | -0.0030228 | -0.0023192 | 0.019967 | 0.042208 | -0.012288 | 0.014043 | 0.024819 | -0.00084805 | 8.9767 | 9.0775 | 8.5327 | 8.9539 | 9.082 | 8.963 | 8.9905 | -0.068665 | 0.018311 | -0.064087 | -0.086975 | 0.032043 | 0.013733 | 0.032043 | 8.6563 | -112.9761 | -113.0997 | 9.2056 | 9.1141 | 9.0866 | 0.45776 | 0.4303 | 0.059509 | -122.0352 | -122.1405 | 0.15564 | 0.15564 | 0.13733 | 0.09613 | 0.07782 | 0.54932 | 0.42114 | 0.09613 | -0.022888 | 0.54474 | 0.082398 | 9.201 | 0.14191 | -113.5208 | -122.1176 | 9.0775 | 0.036621 | 9.1003 | 0.054931
4496.8438 | 122.1817 | -0.064087 | 122.0078 | -0.012131 | 0.010164 | 0.009848 | -0.010004 | 0.00079894 | -0.010698 | -0.0047318 | -0.005371 | 0.018045 | 0.042421 | -0.016987 | 0.010412 | 0.024605 | -0.0038389 | 9.0179 | 8.9996 | 8.5373 | 9.0454 | 9.1965 | 9.0591 | 9.082 | 0.10986 | 0 | 0 | 0.045776 | 0.19684 | 0.16937 | 0.11902 | 8.6014 | -113.0081 | -112.9623 | 9.2606 | 9.1461 | 9.1232 | 0.54474 | 0.52185 | 0.064087 | -122.0078 | -121.962 | 0.26093 | 0.18311 | 0.23346 | 0.11902 | 0.16937 | 0.65918 | 0.50812 | 0.19684 | 0.045776 | 0.46234 | 0 | 9.0637 | 0.064087 | -113.4705 | -122.0078 | 9.1095 | 0.10986 | 9.082 | 0.17395
4498.625 | 122.0535 | -0.10529 | 122.0398 | -0.01976 | 0.0099506 | 0.011771 | -0.006586 | -0.0047553 | -0.0083484 | -0.0032364 | -0.005371 | 0.023172 | 0.044985 | -0.013569 | 0.014898 | 0.022255 | -0.0068295 | 8.9859 | 9.0591 | 8.5373 | 8.9493 | 9.082 | 8.9813 | 8.9905 | -0.068665 | 0.022888 | -0.041199 | -0.082397 | 0.036621 | -0.004578 | 0.027466 | 8.6426 | -112.9807 | -113.0905 | 9.1873 | 9.0958 | 9.0866 | 0.45319 | 0.44403 | 0.064087 | -122.0169 | -122.1222 | 0.14191 | 0.13275 | 0.10071 | 0.068665 | 0.036621 | 0.54474 | 0.41199 | 0.07782 | -0.041198 | 0.52185 | 0.064087 | 9.1644 | 0.12817 | -113.5025 | -122.081 | 9.0546 | 0.022889 | 9.0912 | 0.036621
4500.3281 | 122.1222 | -0.10071 | 122.0535 | -0.012131 | 0.01465 | 0.01113 | -0.0080814 | -0.0021919 | -0.011339 | -0.002382 | -0.0023192 | 0.02189 | 0.043703 | -0.017842 | 0.01618 | 0.023751 | -0.0019163 | 9.0179 | 9.0591 | 8.5464 | 8.9767 | 9.0958 | 8.9722 | 9.0042 | 0.004578 | 0.022888 | -0.050354 | -0.018311 | 0.082397 | 0.059509 | 0.082397 | 8.6472 | -112.9944 | -113.0768 | 9.1965 | 9.1049 | 9.0729 | 0.45776 | 0.42572 | 0.050354 | -122.0306 | -122.0718 | 0.18311 | 0.18311 | 0.16022 | 0.13275 | 0.10986 | 0.54932 | 0.4303 | 0.13275 | 0.032043 | 0.5127 | 0.073242 | 9.1599 | 0.1236 | -113.5071 | -122.1039 | 9.0775 | 0.082397 | 9.1187 | 0.10529
4502.0938 | 122.2321 | -0.086975 | 122.0352 | -0.01976 | 0.012514 | 0.0092072 | -0.010858 | -0.00091006 | -0.0094164 | -0.0021682 | -0.005371 | 0.018472 | 0.041567 | -0.013142 | 0.011053 | 0.024178 | -0.0064023 | 9.0408 | 8.9996 | 8.5556 | 9.082 | 9.2514 | 9.0958 | 9.1049 | 0.10529 | -0.013733 | -0.013733 | 0.045776 | 0.17853 | 0.14648 | 0.13275 | 8.6426 | -113.0356 | -112.9532 | 9.3384 | 9.1919 | 9.1827 | 0.54932 | 0.54016 | 0.073242 | -122.049 | -121.9894 | 0.2655 | 0.21973 | 0.23346 | 0.14648 | 0.16022 | 0.6958 | 0.52643 | 0.19226 | 0.059509 | 0.44403 | 0 | 9.0866 | 0.073242 | -113.4796 | -122.049 | 9.169 | 0.13275 | 9.1278 | 0.19226
4503.8125 | 122.0764 | -0.091553 | 122.081 | -0.012131 | 0.015078 | 0.011984 | -0.0057314 | 0.0012261 | -0.0089892 | -0.0038772 | -0.0023192 | 0.023385 | 0.04178 | -0.014851 | 0.013403 | 0.023751 | -0.0027707 | 8.9401 | 9.0179 | 8.5281 | 8.876 | 8.9584 | 8.8303 | 8.876 | -0.068665 | 0.032043 | -0.068665 | -0.068665 | 0.009155 | -0.022888 | 0.032043 | 8.6197 | -113.0631 | -113.205 | 9.05 | 8.9676 | 8.9218 | 0.3479 | 0.30212 | 0.022888 | -122.049 | -122.1497 | 0.10071 | 0.1236 | 0.068665 | 0.10071 | 0.045777 | 0.4303 | 0.3479 | 0.07782 | 0 | 0.48981 | 0.10071 | 9.1095 | 0.1236 | -113.5529 | -122.1497 | 8.9676 | 0.022888 | 9.0317 | 0.022888
4505.5781 | 122.1771 | -0.059509 | 122.0627 | -0.012131 | 0.0123 | 0.010703 | -0.008295 | -0.00069646 | -0.010698 | -0.0053726 | -0.0084228 | 0.018899 | 0.041567 | -0.016347 | 0.01148 | 0.021828 | 0.0012881 | 8.9584 | 8.9676 | 8.5052 | 8.9722 | 9.0958 | 8.9355 | 8.9905 | 0.041199 | -0.018311 | -0.041199 | -0.009155 | 0.10529 | 0.073242 | 0.09613 | 8.5648 | -113.0951 | -113.0905 | 9.1553 | 9.05 | 8.9951 | 0.48523 | 0.4303 | 0.01831 | -122.081 | -122.0718 | 0.16479 | 0.15564 | 0.13275 | 0.13733 | 0.11444 | 0.59052 | 0.46692 | 0.14649 | 0.032044 | 0.46234 | 0.022888 | 9.0271 | 0.041198 | -113.5574 | -122.1039 | 9.0317 | 0.050354 | 9.0179 | 0.10071
4507.3594 | 122.1817 | -0.086975 | 122.0581 | -0.02739 | 0.011019 | 0.0092072 | -0.0061588 | 0.0025079 | -0.011125 | -0.00345 | -0.005371 | 0.018686 | 0.042421 | -0.020619 | 0.011694 | 0.025887 | -0.00084805 | 8.9493 | 8.9722 | 8.5144 | 8.963 | 9.0866 | 8.9676 | 8.9951 | 0.022888 | -0.004578 | -0.022888 | -0.004578 | 0.10071 | 0.091553 | 0.086975 | 8.6014 | -113.0859 | -113.0951 | 9.1736 | 9.082 | 9.0546 | 0.48065 | 0.45319 | 0.064087 | -122.0627 | -122.0627 | 0.18768 | 0.17395 | 0.17853 | 0.10986 | 0.11444 | 0.5722 | 0.44861 | 0.1236 | 0.01831 | 0.45776 | 0.01831 | 9.0591 | 0.082397 | -113.5437 | -122.081 | 9.05 | 0.082397 | 9.0363 | 0.10986
4509.0781 | 122.1313 | -0.09613 | 122.081 | -0.012131 | 0.012941 | 0.012412 | -0.0044498 | 0.0018671 | -0.0079212 | -0.001741 | -0.0023192 | 0.02189 | 0.043917 | -0.0058789 | 0.014684 | 0.022255 | -0.0010617 | 8.9859 | 9.0408 | 8.5373 | 8.9401 | 9.0591 | 8.8898 | 8.931 | -0.009155 | 0.018311 | -0.041199 | -0.054932 | 0.032043 | -0.013733 | 0.027466 | 8.6334 | -113.0402 | -113.1409 | 9.1553 | 9.0271 | 8.9859 | 0.39368 | 0.35248 | 0.054931 | -122.0627 | -122.1359 | 0.12817 | 0.1236 | 0.082397 | 0.068665 | 0.027466 | 0.52185 | 0.40283 | 0.073242 | -0.013733 | 0.50354 | 0.05951 | 9.137 | 0.11444 | -113.5437 | -122.1222 | 9.0363 | 0.041198 | 9.082 | 0.086975
4510.8438 | 122.0993 | -0.091553 | 122.0718 | -0.012131 | 0.014223 | 0.011771 | -0.004877 | 0.0020807 | -0.00963 | -0.0062272 | -0.011475 | 0.021035 | 0.041994 | -0.0097241 | 0.015325 | 0.022683 | -0.0027707 | 8.9767 | 9.0088 | 8.5236 | 8.9035 | 9.0317 | 8.876 | 8.9081 | -0.036621 | 0.027466 | -0.036621 | -0.059509 | 0.022888 | -0.018311 | 0.041199 | 8.6151 | -113.063 | -113.1683 | 9.1232 | 8.9996 | 8.9676 | 0.38452 | 0.35248 | 0.054932 | -122.0444 | -122.1313 | 0.11444 | 0.13275 | 0.073242 | 0.07782 | 0.01831 | 0.50812 | 0.37994 | 0.059509 | -0.022888 | 0.48523 | 0.064087 | 9.1003 | 0.11902 | -113.5483 | -122.1085 | 8.9951 | 0.032044 | 9.0683 | 0.054932
4512.6094 | 122.1497 | -0.09613 | 122.0856 | -0.01976 | 0.013369 | 0.01113 | -0.0050906 | -0.0011237 | -0.0083484 | -0.00345 | -0.0023192 | 0.020608 | 0.042421 | -0.016987 | 0.01383 | 0.024178 | -0.0038389 | 8.9081 | 8.9676 | 8.4869 | 8.8577 | 8.9813 | 8.8211 | 8.8623 | -0.036621 | 0.032043 | -0.045776 | -0.032043 | 0.059509 | 0.004578 | 0.068665 | 8.5831 | -113.118 | -113.2278 | 9.0775 | 8.9584 | 8.9172 | 0.37537 | 0.33417 | 0.050354 | -122.0535 | -122.1176 | 0.15564 | 0.16479 | 0.10071 | 0.11444 | 0.050354 | 0.49438 | 0.37079 | 0.10528 | 0.013733 | 0.48065 | 0.077819 | 9.0637 | 0.12817 | -113.5986 | -122.1313 | 8.9539 | 0.064087 | 9.0042 | 0.059509
4514.3906 | 122.2137 | -0.073242 | 122.0901 | -0.01976 | 0.0123 | 0.0092072 | -0.010218 | 0.0018671 | -0.0087756 | -0.0021682 | -0.005371 | 0.020181 | 0.043703 | -0.016133 | 0.012975 | 0.025032 | 0.0025699 | 8.9401 | 8.9447 | 8.5007 | 8.9447 | 9.0729 | 8.9401 | 8.9859 | 0.013733 | -0.022888 | -0.022888 | -0.013733 | 0.09613 | 0.091553 | 0.10071 | 8.5739 | -113.1454 | -113.1454 | 9.1461 | 9.0591 | 9.0134 | 0.48523 | 0.43945 | 0.050354 | -122.113 | -122.1039 | 0.16937 | 0.17395 | 0.16479 | 0.1236 | 0.11444 | 0.57221 | 0.44403 | 0.11902 | 0.009155 | 0.44403 | 0 | 9.0179 | 0.050354 | -113.5895 | -122.113 | 9.0179 | 0.059509 | 9.0134 | 0.086975
4516.1094 | 122.2321 | -0.073242 | 122.0581 | -0.0045011 | 0.013582 | 0.009848 | -0.006586 | -0.0030463 | -0.0074938 | -0.0032364 | -0.011475 | 0.019326 | 0.043489 | -0.013356 | 0.012334 | 0.024178 | -0.0023435 | 8.9539 | 8.8989 | 8.4869 | 8.963 | 9.1003 | 8.9355 | 8.9676 | 0.10986 | -0.018311 | 0.004578 | 0.045776 | 0.14191 | 0.11444 | 0.12817 | 8.5602 | -113.1592 | -113.0951 | 9.1736 | 9.0408 | 9.0088 | 0.48065 | 0.44861 | 0.07782 | -122.0764 | -122.0123 | 0.21515 | 0.20142 | 0.18768 | 0.1236 | 0.10986 | 0.6134 | 0.47607 | 0.13733 | 0.041198 | 0.41199 | -0.022889 | 8.9722 | 0.054931 | -113.5712 | -122.0535 | 9.0363 | 0.11902 | 9.0271 | 0.18311
4517.875 | 122.1451 | -0.10529 | 122.113 | -0.01976 | 0.014223 | 0.010062 | -0.0046634 | 0.0027215 | -0.0098438 | -0.0036636 | -0.0023192 | 0.022317 | 0.041353 | -0.010792 | 0.014471 | 0.023751 | -0.00042085 | 8.9813 | 9.0179 | 8.5281 | 8.9401 | 9.0683 | 8.9172 | 8.9401 | 0.022888 | 0.027466 | -0.045776 | -0.013733 | 0.068665 | 0.027466 | 0.054932 | 8.6334 | -113.0951 | -113.1729 | 9.1736 | 9.0454 | 9.0225 | 0.41199 | 0.3891 | 0.05951 | -122.0856 | -122.1268 | 0.17395 | 0.16022 | 0.13275 | 0.10071 | 0.073242 | 0.54016 | 0.41199 | 0.11444 | 0.032043 | 0.48981 | 0.073242 | 9.1232 | 0.13275 | -113.5849 | -122.1588 | 9.0454 | 0.091553 | 9.0866 | 0.12817
4519.6562 | 122.168 | -0.10986 | 122.1039 | -0.0045011 | 0.011873 | 0.010489 | -0.0067996 | -0.00091006 | -0.0083484 | -0.0019546 | -0.005371 | 0.020822 | 0.041567 | -0.017842 | 0.015325 | 0.022683 | -0.0021299 | 8.9813 | 8.9767 | 8.519 | 8.9493 | 9.0683 | 8.9355 | 8.9493 | 0.027466 | 0.004578 | -0.013733 | -0.004578 | 0.086975 | 0.059509 | 0.086975 | 8.6288 | -113.1271 | -113.1546 | 9.1782 | 9.0591 | 9.0454 | 0.4303 | 0.41657 | 0.09613 | -122.0993 | -122.1085 | 0.19684 | 0.19684 | 0.16937 | 0.10071 | 0.073242 | 0.54932 | 0.4303 | 0.10071 | 0.009155 | 0.45776 | 0.018311 | 9.0866 | 0.11444 | -113.5849 | -122.1176 | 9.0591 | 0.10529 | 9.0912 | 0.13733
4521.4219 | 122.1359 | -0.10071 | 122.1039 | -0.01976 | 0.015932 | 0.012198 | -0.0038088 | 0.0020807 | -0.0070666 | -0.0036636 | -0.005371 | 0.021035 | 0.044985 | -0.011433 | 0.015112 | 0.023964 | -0.0029843 | 8.8852 | 8.9951 | 8.4778 | 8.8074 | 8.9401 | 8.7891 | 8.8394 | -0.059509 | 0.018311 | -0.059509 | -0.054932 | 0.032043 | 0 | 0.041199 | 8.5785 | -113.1088 | -113.2965 | 9.0408 | 8.9401 | 8.8898 | 0.36163 | 0.31128 | 0.041199 | -122.0856 | -122.1588 | 0.13275 | 0.14191 | 0.10071 | 0.10071 | 0.059509 | 0.46234 | 0.32959 | 0.091552 | 0.004577 | 0.51727 | 0.07782 | 9.0958 | 0.11902 | -113.6261 | -122.1634 | 8.9081 | 0.045776 | 8.9859 | 0.041199
4523.125 | 122.1313 | -0.10529 | 122.1039 | -0.02739 | 0.014009 | 0.010703 | -0.0078676 | 0.0063531 | -0.0098438 | -0.0049454 | -0.0084228 | 0.021249 | 0.041994 | -0.016133 | 0.011694 | 0.022683 | -0.0040525 | 8.8852 | 8.9584 | 8.4778 | 8.8074 | 8.9172 | 8.7753 | 8.8257 | -0.064087 | 0.027466 | -0.050354 | -0.07782 | 0.032043 | -0.013733 | 0.050354 | 8.5831 | -113.1454 | -113.2965 | 9.0225 | 8.931 | 8.8806 | 0.3479 | 0.29755 | 0.054932 | -122.0764 | -122.1817 | 0.13733 | 0.15564 | 0.091553 | 0.10071 | 0.036621 | 0.43945 | 0.32959 | 0.082397 | -0.027466 | 0.48065 | 0.07782 | 9.0637 | 0.13275 | -113.6261 | -122.1542 | 8.9127 | 0.027466 | 8.9905 | 0.041199
4524.9062 | 122.1451 | -0.09613 | 122.1085 | -0.012131 | 0.015718 | 0.012625 | -0.005945 | -0.00048286 | -0.0087756 | -0.0072952 | -0.005371 | 0.022744 | 0.043489 | -0.0084423 | 0.01383 | 0.02546 | -0.0017027 | 8.8806 | 8.9722 | 8.4686 | 8.8165 | 8.9401 | 8.812 | 8.8303 | -0.032043 | 0.018311 | -0.054932 | -0.041199 | 0.032043 | 0.018311 | 0.054932 | 8.5648 | -113.1363 | -113.2919 | 9.0363 | 8.9264 | 8.9081 | 0.36163 | 0.34332 | 0.041198 | -122.0901 | -122.1497 | 0.12817 | 0.15106 | 0.11444 | 0.10986 | 0.073243 | 0.4715 | 0.3479 | 0.086975 | 0.013733 | 0.50354 | 0.073243 | 9.0683 | 0.11444 | -113.6398 | -122.1634 | 8.9127 | 0.054931 | 8.9767 | 0.064087
4526.6094 | 122.1176 | -0.10986 | 122.1268 | -0.01976 | 0.015932 | 0.011771 | -0.0055178 | 0.0031487 | -0.0098438 | -0.001741 | -0.005371 | 0.023385 | 0.042208 | -0.0056653 | 0.014471 | 0.024605 | -0.0031979 | 8.8806 | 8.9539 | 8.4869 | 8.8028 | 8.9172 | 8.7799 | 8.812 | -0.10986 | 0.032043 | -0.041199 | -0.064087 | 0.004578 | -0.027466 | 0.041199 | 8.5968 | -113.1729 | -113.324 | 9.0271 | 8.9218 | 8.8898 | 0.32501 | 0.29297 | 0.068664 | -122.0947 | -122.1909 | 0.11444 | 0.15106 | 0.082397 | 0.082398 | 0.013733 | 0.4303 | 0.31586 | 0.045777 | -0.022888 | 0.46692 | 0.073242 | 9.0637 | 0.14191 | -113.6398 | -122.168 | 8.9127 | 0.045776 | 8.9905 | 0
4528.375 | 122.2183 | -0.059509 | 122.0901 | -0.012131 | 0.010805 | 0.010275 | -0.0097904 | -0.00091006 | -0.010485 | -0.0011002 | -0.011475 | 0.018258 | 0.042849 | -0.016987 | 0.011907 | 0.0261 | -0.0023435 | 8.9081 | 8.931 | 8.4824 | 8.8989 | 9.0179 | 8.8989 | 8.9401 | 0.009155 | -0.009155 | -0.022888 | -0.009155 | 0.10529 | 0.073242 | 0.086975 | 8.5419 | -113.1592 | -113.1912 | 9.0775 | 8.9996 | 8.9584 | 0.45776 | 0.41657 | 0.036621 | -122.0993 | -122.0993 | 0.16479 | 0.14648 | 0.13275 | 0.10986 | 0.09613 | 0.53558 | 0.41657 | 0.12817 | 0.013733 | 0.44861 | 0.013733 | 8.9905 | 0.050354 | -113.6078 | -122.113 | 8.9584 | 0.050354 | 8.9676 | 0.068664
4530.0938 | 122.1771 | -0.086975 | 122.1268 | -0.0045011 | 0.01465 | 0.011557 | -0.0046634 | 0.0012261 | -0.0092028 | -0.0047318 | -0.005371 | 0.022958 | 0.042849 | -0.0084423 | 0.015752 | 0.022683 | -0.0023435 | 8.9584 | 8.9813 | 8.519 | 8.9355 | 9.0591 | 8.9127 | 8.931 | 0.036621 | -0.004578 | -0.027466 | -0.009155 | 0.091553 | 0.054932 | 0.064087 | 8.606 | -113.1454 | -113.1912 | 9.1461 | 9.0179 | 8.9996 | 0.41199 | 0.39368 | 0.059509 | -122.1313 | -122.1359 | 0.17853 | 0.15106 | 0.14191 | 0.091553 | 0.082398 | 0.54016 | 0.41657 | 0.11902 | 0.018311 | 0.46234 | 0.022888 | 9.0683 | 0.082397 | -113.6078 | -122.1542 | 9.0225 | 0.07782 | 9.0454 | 0.1236
4531.8594 | 122.2549 | -0.07782 | 122.0764 | -0.012131 | 0.010591 | 0.010275 | -0.0080814 | 0.0012261 | -0.010698 | -0.000673 | -0.005371 | 0.017404 | 0.040712 | -0.025319 | 0.01148 | 0.023537 | 0.0019289 | 8.8943 | 8.9264 | 8.4778 | 8.9264 | 9.0591 | 8.931 | 8.9722 | 0.059509 | 0.004578 | -0.027466 | 0.013733 | 0.16022 | 0.13275 | 0.13275 | 8.5556 | -113.15 | -113.15 | 9.137 | 9.05 | 9.0088 | 0.49438 | 0.45319 | 0.050354 | -122.0718 | -122.0627 | 0.23804 | 0.21057 | 0.21057 | 0.16022 | 0.16022 | 0.58136 | 0.44861 | 0.18768 | 0.041199 | 0.44861 | 0.032044 | 9.0042 | 0.082398 | -113.5986 | -122.1039 | 9.0042 | 0.091553 | 8.9722 | 0.13733
4533.6406 | 122.2412 | -0.045776 | 122.0901 | -0.02739 | 0.013369 | 0.011557 | -0.0087222 | 0.0033623 | -0.0092028 | -0.0055862 | -0.005371 | 0.018258 | 0.041567 | -0.012715 | 0.012975 | 0.024391 | -0.0051205 | 8.8898 | 8.8715 | 8.4595 | 8.9127 | 9.0637 | 8.8852 | 8.9127 | 0.10071 | -0.027466 | -0.022888 | 0.045776 | 0.12817 | 0.091553 | 0.11444 | 8.5052 | -113.2187 | -113.1775 | 9.1095 | 8.9584 | 8.931 | 0.45319 | 0.42572 | 0.022888 | -122.1176 | -122.0444 | 0.17395 | 0.16022 | 0.13733 | 0.13733 | 0.11444 | 0.60425 | 0.45319 | 0.15106 | 0.068664 | 0.41199 | -0.004578 | 8.9172 | 0.01831 | -113.6307 | -122.113 | 8.9584 | 0.091552 | 8.9355 | 0.14648
4535.4062 | 122.2 | -0.091553 | 122.1268 | -0.01976 | 0.013796 | 0.0096344 | -0.0053042 | -0.00091006 | -0.0079212 | -0.0032364 | -0.0084228 | 0.022531 | 0.043489 | -0.010792 | 0.01383 | 0.02311 | -0.0076841 | 8.9584 | 8.9722 | 8.5144 | 8.931 | 9.0408 | 8.8943 | 8.9172 | 0.022888 | 0.013733 | -0.041199 | -0.022888 | 0.086975 | 0.064087 | 0.073242 | 8.606 | -113.1546 | -113.1958 | 9.1324 | 9.0088 | 8.9859 | 0.40283 | 0.37994 | 0.050354 | -122.113 | -122.1497 | 0.17853 | 0.16479 | 0.15564 | 0.11444 | 0.10529 | 0.52643 | 0.41656 | 0.12817 | 0.018311 | 0.45776 | 0.054932 | 9.0637 | 0.10529 | -113.6124 | -122.168 | 9.0225 | 0.068665 | 9.05 | 0.11444
4537.1094 | 122.1451 | -0.11444 | 122.168 | -0.01976 | 0.0123 | 0.010916 | -0.004877 | 0.0025079 | -0.0089892 | -0.0021682 | -0.005371 | 0.02189 | 0.040712 | -0.017842 | 0.014043 | 0.023751 | -0.0055479 | 8.9584 | 8.9996 | 8.5144 | 8.8989 | 8.9996 | 8.8486 | 8.8852 | -0.036621 | 0.027466 | -0.036621 | -0.064087 | 0.032043 | -0.004578 | 0.036621 | 8.6288 | -113.1683 | -113.269 | 9.1141 | 8.9996 | 8.963 | 0.37079 | 0.33417 | 0.07782 | -122.1405 | -122.2321 | 0.14648 | 0.15106 | 0.10986 | 0.073242 | 0.032043 | 0.48523 | 0.38452 | 0.068664 | -0.027466 | 0.48523 | 0.064087 | 9.1141 | 0.14191 | -113.6536 | -122.2046 | 9.0134 | 0.050354 | 9.0729 | 0.07782
4538.875 | 122.1451 | -0.10986 | 122.1634 | -0.01976 | 0.01166 | 0.010275 | -0.008295 | 0.00058534 | -0.011766 | -0.00345 | -0.0084228 | 0.020181 | 0.042421 | -0.0060925 | 0.011266 | 0.02311 | -0.0040525 | 8.963 | 9.0546 | 8.5281 | 8.9218 | 9.05 | 8.9447 | 8.9676 | -0.059509 | 0.027466 | -0.068665 | -0.082397 | 0.032043 | -0.004578 | 0.032043 | 8.638 | -113.1088 | -113.2416 | 9.1599 | 9.0775 | 9.0546 | 0.43945 | 0.41657 | 0.041198 | -122.1359 | -122.2458 | 0.14191 | 0.14191 | 0.10529 | 0.10071 | 0.064087 | 0.52185 | 0.39368 | 0.10071 | -0.013732 | 0.52643 | 0.096131 | 9.1644 | 0.13733 | -113.6353 | -122.2321 | 9.0317 | 0.027466 | 9.0729 | 0.050354
4540.6406 | 122.1542 | -0.1236 | 122.1725 | -0.012131 | 0.012941 | 0.008139 | -0.005945 | -0.0030463 | -0.011125 | -0.0040908 | -0.0023192 | 0.021249 | 0.044558 | -0.02126 | 0.014043 | 0.02076 | -0.0044797 | 8.9767 | 9.0637 | 8.5281 | 8.9172 | 9.0683 | 8.9355 | 8.9676 | -0.064087 | 0.027466 | -0.054932 | -0.082397 | 0.027466 | 0.013733 | 0.032043 | 8.6517 | -113.1088 | -113.2553 | 9.1919 | 9.0912 | 9.0591 | 0.43945 | 0.40741 | 0.068664 | -122.1451 | -122.2549 | 0.15106 | 0.15564 | 0.13733 | 0.086975 | 0.068665 | 0.54016 | 0.3891 | 0.082398 | -0.027465 | 0.53558 | 0.082398 | 9.1873 | 0.15106 | -113.6444 | -122.2275 | 9.0408 | 0.041199 | 9.1003 | 0.059509
4542.3438 | 122.2321 | -0.068665 | 122.1176 | -0.012131 | 0.014009 | 0.009848 | -0.0063724 | 0.0031487 | -0.0074938 | -0.002382 | -0.005371 | 0.022317 | 0.04413 | -0.019124 | 0.014257 | 0.024605 | -0.0014891 | 8.8715 | 8.9218 | 8.4549 | 8.8303 | 8.9401 | 8.7845 | 8.844 | -0.004578 | -0.009155 | -0.045776 | -0.004578 | 0.086975 | 0.068665 | 0.09613 | 8.5236 | -113.1958 | -113.2874 | 9.0088 | 8.9127 | 8.8531 | 0.3891 | 0.32959 | 0.022889 | -122.1268 | -122.1222 | 0.15564 | 0.16479 | 0.13733 | 0.14191 | 0.11444 | 0.48523 | 0.37537 | 0.13275 | 0.041198 | 0.46692 | 0.036621 | 8.9905 | 0.05951 | -113.6627 | -122.1634 | 8.8989 | 0.064087 | 8.9401 | 0.064087
4544.1094 | 122.1588 | -0.09613 | 122.1359 | -0.0045011 | 0.014223 | 0.012412 | -0.0063724 | 0.00037174 | -0.0081348 | -0.002382 | -0.005371 | 0.022103 | 0.041353 | -0.0041699 | 0.013403 | 0.024391 | -0.0014891 | 8.8531 | 8.9218 | 8.4686 | 8.7891 | 8.8943 | 8.7616 | 8.7982 | -0.059509 | 0.018311 | -0.073242 | -0.059509 | 0.018311 | -0.004578 | 0.032043 | 8.5648 | -113.2141 | -113.3469 | 8.9905 | 8.8943 | 8.8577 | 0.32959 | 0.29297 | 0.022888 | -122.1176 | -122.1954 | 0.11444 | 0.12817 | 0.091552 | 0.10529 | 0.068664 | 0.42572 | 0.32043 | 0.091553 | 0.013733 | 0.45319 | 0.091553 | 9.0179 | 0.11444 | -113.6673 | -122.2092 | 8.8852 | 0.036621 | 8.9493 | 0.036621
4545.875 | 122.2458 | -0.068665 | 122.0718 | -0.0045011 | 0.012087 | 0.01113 | -0.008295 | -0.0011237 | -0.0083484 | -0.0047318 | -0.005371 | 0.017617 | 0.04178 | -0.017201 | 0.010839 | 0.02546 | -0.00063445 | 8.9035 | 8.8669 | 8.4595 | 8.8806 | 9.0363 | 8.8577 | 8.9218 | 0.073242 | -0.004578 | -0.022888 | 0.013733 | 0.10071 | 0.09613 | 0.09613 | 8.5281 | -113.205 | -113.1912 | 9.1049 | 8.9905 | 8.9264 | 0.46234 | 0.39825 | 0.045777 | -122.0764 | -122.0581 | 0.16937 | 0.16479 | 0.16479 | 0.11902 | 0.11902 | 0.57678 | 0.42114 | 0.1236 | 0.036621 | 0.40741 | 0.01831 | 8.9355 | 0.064087 | -113.6124 | -122.0947 | 8.9493 | 0.082398 | 8.9722 | 0.14191
4547.6562 | 122.1542 | -0.086975 | 122.168 | -0.01976 | 0.015291 | 0.013052 | -0.0061588 | -5.5462e-05 | -0.011553 | -0.0038772 | -0.005371 | 0.021463 | 0.042635 | -0.014851 | 0.015752 | 0.023537 | 6.346e-06 | 8.9127 | 8.9539 | 8.4869 | 8.844 | 8.9584 | 8.7936 | 8.844 | -0.032043 | 0.027466 | -0.064087 | -0.050354 | 0.027466 | -0.018311 | 0.032043 | 8.5739 | -113.2141 | -113.324 | 9.0454 | 8.931 | 8.8806 | 0.35706 | 0.3067 | 0.022888 | -122.1405 | -122.2183 | 0.11444 | 0.11902 | 0.068664 | 0.09613 | 0.045776 | 0.4715 | 0.35706 | 0.091553 | 0.013733 | 0.46692 | 0.091553 | 9.0408 | 0.11444 | -113.681 | -122.2321 | 8.931 | 0.036621 | 8.9996 | 0.054932
4549.4219 | 122.2183 | -0.10071 | 122.1542 | -0.012131 | 0.011873 | 0.010062 | -0.0078676 | 0.0010125 | -0.011553 | -0.0004592 | -0.005371 | 0.021035 | 0.043489 | -0.01122 | 0.015325 | 0.023964 | -0.0074705 | 8.9127 | 9.0088 | 8.4915 | 8.8715 | 8.9859 | 8.8806 | 8.9081 | -0.054932 | 0.018311 | -0.045776 | -0.050354 | 0.054932 | 0.045776 | 0.050354 | 8.5922 | -113.1454 | -113.2828 | 9.0866 | 9.0088 | 8.9813 | 0.41656 | 0.3891 | 0.054932 | -122.1359 | -122.2046 | 0.15564 | 0.15106 | 0.14648 | 0.09613 | 0.091552 | 0.49438 | 0.37994 | 0.10071 | -0.004578 | 0.51727 | 0.064087 | 9.1095 | 0.11902 | -113.6627 | -122.2 | 8.9722 | 0.050354 | 9.0134 | 0.045776
4551.125 | 122.1863 | -0.10529 | 122.1542 | -0.0045011 | 0.010805 | 0.0085662 | -0.004877 | 0.0052851 | -0.010271 | -0.001741 | -0.0023192 | 0.021249 | 0.04178 | -0.019551 | 0.016393 | 0.021614 | 6.346e-06 | 8.9127 | 8.9905 | 8.4869 | 8.8669 | 8.9813 | 8.8852 | 8.8989 | -0.059509 | 0.036621 | -0.059509 | -0.064087 | 0.054932 | 0.027466 | 0.045776 | 8.5922 | -113.1638 | -113.2874 | 9.0866 | 9.0042 | 8.9905 | 0.41199 | 0.39825 | 0.045777 | -122.1176 | -122.2183 | 0.16022 | 0.15106 | 0.13275 | 0.10528 | 0.086975 | 0.49438 | 0.37994 | 0.11444 | -0.004578 | 0.50354 | 0.09613 | 9.0958 | 0.14191 | -113.6673 | -122.2137 | 8.9722 | 0.041199 | 9.0179 | 0.045777
4552.8906 | 122.2687 | -0.068665 | 122.0947 | -0.01976 | 0.0093098 | 0.0096344 | -0.007654 | -0.0019781 | -0.0089892 | -0.0019546 | -0.0023192 | 0.019326 | 0.04178 | -0.024251 | 0.012762 | 0.023964 | -0.0023435 | 8.9767 | 8.931 | 8.4961 | 8.9539 | 9.1187 | 8.9722 | 8.9813 | 0.082397 | -0.013733 | -0.027466 | 0.036621 | 0.14191 | 0.14648 | 0.10529 | 8.5648 | -113.1638 | -113.1409 | 9.1873 | 9.05 | 9.0408 | 0.48523 | 0.47607 | 0.041199 | -122.1085 | -122.0581 | 0.21057 | 0.17395 | 0.21515 | 0.13275 | 0.17395 | 0.62256 | 0.45776 | 0.16937 | 0.064087 | 0.43487 | 0.013733 | 8.9996 | 0.054932 | -113.5986 | -122.1222 | 9.0225 | 0.10529 | 9.0454 | 0.15106
4554.6562 | 122.287 | -0.054932 | 122.113 | -0.012131 | 0.01166 | 0.010703 | -0.010218 | -0.0053961 | -0.010271 | -0.0040908 | -0.0084228 | 0.019967 | 0.042849 | -0.018483 | 0.012334 | 0.023537 | -0.0046933 | 8.9722 | 8.9264 | 8.4915 | 8.9767 | 9.137 | 8.9905 | 9.0271 | 0.13733 | -0.022888 | -0.004578 | 0.050354 | 0.1831 | 0.16022 | 0.13733 | 8.5464 | -113.1866 | -113.1363 | 9.1919 | 9.082 | 9.0454 | 0.53558 | 0.49896 | 0.050354 | -122.1359 | -122.0627 | 0.23804 | 0.19226 | 0.21515 | 0.14191 | 0.16479 | 0.64545 | 0.48523 | 0.18768 | 0.054932 | 0.43488 | -0.01831 | 8.9813 | 0.032044 | -113.6215 | -122.1176 | 9.0317 | 0.10529 | 9.0271 | 0.19226
4556.3594 | 122.1771 | -0.11444 | 122.1725 | -0.0045011 | 0.009737 | 0.0096344 | -0.009363 | -0.00069646 | -0.0098438 | -0.0032364 | -0.0084228 | 0.022317 | 0.042635 | -0.017201 | 0.01148 | 0.023964 | -0.0040525 | 8.9218 | 8.9813 | 8.5007 | 8.8715 | 8.9996 | 8.8715 | 8.9172 | -0.050354 | 0.027466 | -0.036621 | -0.07782 | 0.022888 | 0.004578 | 0.027466 | 8.6151 | -113.1912 | -113.3011 | 9.1141 | 9.0317 | 8.9859 | 0.41657 | 0.37079 | 0.07782 | -122.1451 | -122.2504 | 0.13733 | 0.14191 | 0.11902 | 0.064087 | 0.041199 | 0.49896 | 0.37079 | 0.059509 | -0.041199 | 0.48065 | 0.064087 | 9.0958 | 0.14191 | -113.6719 | -122.2092 | 8.9859 | 0.036621 | 9.0363 | 0.064087
4558.125 | 122.2641 | -0.073242 | 122.1176 | -0.01976 | 0.013582 | 0.011771 | -0.0061588 | 0.0025079 | -0.010698 | -0.0021682 | -0.0084228 | 0.018686 | 0.040285 | -0.01421 | 0.013189 | 0.024605 | -0.0019163 | 8.876 | 8.8257 | 8.4412 | 8.8531 | 8.9996 | 8.8348 | 8.8852 | 0.086975 | -0.013733 | -0.018311 | 0.013733 | 0.11902 | 0.10071 | 0.09613 | 8.5144 | -113.2919 | -113.2645 | 9.0729 | 8.9584 | 8.9081 | 0.44403 | 0.39368 | 0.054931 | -122.1313 | -122.1039 | 0.19226 | 0.16937 | 0.17395 | 0.11444 | 0.11902 | 0.55847 | 0.41199 | 0.13733 | 0.032044 | 0.38452 | 0.004578 | 8.8989 | 0.059509 | -113.6765 | -122.1359 | 8.9264 | 0.086975 | 8.9493 | 0.16022
4559.8438 | 122.1771 | -0.091553 | 122.1542 | -0.02739 | 0.012514 | 0.010275 | -0.0074404 | 0.0012261 | -0.010912 | -0.0036636 | 0.00073235 | 0.022531 | 0.045198 | -0.0069469 | 0.013403 | 0.022255 | -0.0042661 | 8.8943 | 8.9127 | 8.4732 | 8.8394 | 8.963 | 8.8028 | 8.8348 | 0.004578 | 0.009155 | -0.027466 | -0.041199 | 0.032043 | 0.004578 | 0.036621 | 8.5648 | -113.2416 | -113.3148 | 9.0546 | 8.9264 | 8.8943 | 0.36163 | 0.32959 | 0.064087 | -122.1451 | -122.1954 | 0.1236 | 0.12817 | 0.096131 | 0.064087 | 0.032044 | 0.48981 | 0.36621 | 0.059509 | -0.013733 | 0.43945 | 0.036621 | 9.0042 | 0.10071 | -113.681 | -122.1817 | 8.931 | 0.050354 | 8.9859 | 0.096131
4561.6094 | 122.2458 | -0.064087 | 122.1268 | -0.01976 | 0.013155 | 0.010062 | -0.0085086 | 0.0029351 | -0.010698 | -0.0036636 | -0.0084228 | 0.019113 | 0.04413 | -0.016347 | 0.012975 | 0.023323 | -0.0046933 | 8.8394 | 8.8257 | 8.4183 | 8.8303 | 8.9813 | 8.7982 | 8.8623 | 0.07782 | -0.009155 | -0.022888 | 0.018311 | 0.11444 | 0.07782 | 0.09613 | 8.4824 | -113.3011 | -113.2965 | 9.0454 | 8.9264 | 8.8623 | 0.44403 | 0.37994 | 0.041199 | -122.1359 | -122.1085 | 0.17853 | 0.16022 | 0.14191 | 0.11902 | 0.10071 | 0.56305 | 0.41199 | 0.13733 | 0.041199 | 0.40741 | 0.013733 | 8.8898 | 0.054932 | -113.7085 | -122.1497 | 8.8943 | 0.082398 | 8.9035 | 0.14191
4563.3906 | 122.3099 | -0.050354 | 122.113 | -0.012131 | 0.0123 | 0.01348 | -0.004877 | -0.00048286 | -0.010698 | -0.0004592 | -0.0084228 | 0.021463 | 0.042208 | -0.015278 | 0.013616 | 0.02311 | -0.0049069 | 8.8623 | 8.8074 | 8.4045 | 8.8394 | 8.9584 | 8.7845 | 8.8348 | 0.10986 | -0.022888 | -0.018311 | 0.073242 | 0.16479 | 0.11444 | 0.14191 | 8.4549 | -113.3057 | -113.2736 | 9.0088 | 8.8852 | 8.8348 | 0.4303 | 0.37994 | 0.032043 | -122.1359 | -122.0398 | 0.21515 | 0.19226 | 0.16479 | 0.16022 | 0.13275 | 0.55389 | 0.43488 | 0.18311 | 0.091553 | 0.40283 | -0.004577 | 8.8577 | 0.027466 | -113.7085 | -122.1313 | 8.8898 | 0.1236 | 8.9127 | 0.16022
4565.1719 | 122.3007 | -0.064087 | 122.0993 | -0.0045011 | 0.016359 | 0.010275 | -0.006586 | 0.0018671 | -0.0070666 | -0.0013138 | -0.005371 | 0.020395 | 0.042635 | -0.011647 | 0.013403 | 0.024819 | -0.0046933 | 8.7936 | 8.8257 | 8.4 | 8.7799 | 8.9081 | 8.7524 | 8.7936 | 0.068665 | -0.009155 | -0.027466 | 0.054932 | 0.15106 | 0.11444 | 0.13275 | 8.4641 | -113.2736 | -113.3194 | 8.9722 | 8.8577 | 8.8165 | 0.39368 | 0.35248 | 0.036621 | -122.1085 | -122.0444 | 0.21515 | 0.19684 | 0.17853 | 0.16022 | 0.14191 | 0.50812 | 0.37994 | 0.17853 | 0.082398 | 0.42572 | 0.018311 | 8.8898 | 0.054932 | -113.6993 | -122.1268 | 8.844 | 0.11902 | 8.8577 | 0.13275
4566.9531 | 122.1954 | -0.11902 | 122.1634 | -0.01976 | 0.011446 | 0.0094208 | -0.0053042 | 0.0027215 | -0.010057 | -0.001741 | -0.005371 | 0.020822 | 0.041567 | -0.01122 | 0.012334 | 0.024391 | 0.00021995 | 8.8715 | 8.963 | 8.4595 | 8.8211 | 8.9401 | 8.8348 | 8.8531 | -0.064087 | 0.027466 | -0.059509 | -0.073242 | 0.032043 | 0.018311 | 0.045776 | 8.5785 | -113.2004 | -113.3423 | 9.0591 | 8.9722 | 8.9539 | 0.39368 | 0.37537 | 0.05951 | -122.1359 | -122.2366 | 0.15106 | 0.16479 | 0.13733 | 0.10528 | 0.07782 | 0.48065 | 0.36163 | 0.091552 | -0.013733 | 0.50354 | 0.086975 | 9.082 | 0.14649 | -113.7039 | -122.2229 | 8.9401 | 0.045777 | 8.9905 | 0.054932
4568.6562 | 122.1909 | -0.11444 | 122.1542 | -0.012131 | 0.011232 | 0.0089936 | -0.0063724 | -0.0017645 | -0.010057 | -0.005159 | -0.0084228 | 0.022317 | 0.043276 | -0.015492 | 0.013616 | 0.022469 | -0.0031979 | 8.8531 | 8.931 | 8.4549 | 8.812 | 8.9447 | 8.8394 | 8.8486 | -0.064087 | 0.018311 | -0.050354 | -0.09613 | 0.050354 | 0.004578 | 0.032043 | 8.5693 | -113.2233 | -113.3423 | 9.0591 | 8.963 | 8.9539 | 0.39368 | 0.38452 | 0.064087 | -122.1359 | -122.2504 | 0.16479 | 0.14648 | 0.11902 | 0.082397 | 0.054932 | 0.48981 | 0.35706 | 0.10071 | -0.045776 | 0.47607 | 0.068665 | 9.0454 | 0.13275 | -113.6993 | -122.2046 | 8.9264 | 0.018311 | 8.9676 | 0.050354
4570.4375 | 122.2275 | -0.091553 | 122.1634 | -0.01976 | 0.013582 | 0.011557 | -0.0072268 | 0.0048577 | -0.010057 | -0.0036636 | -0.011475 | 0.022744 | 0.041353 | -0.0088695 | 0.015325 | 0.024178 | -0.0036253 | 8.8806 | 8.931 | 8.4549 | 8.8348 | 8.9355 | 8.8348 | 8.8623 | -0.027466 | 0.018311 | -0.045776 | -0.036621 | 0.086975 | 0.036621 | 0.07782 | 8.5464 | -113.2324 | -113.3286 | 9.0271 | 8.9539 | 8.9264 | 0.40741 | 0.37994 | 0.045777 | -122.1451 | -122.2 | 0.17853 | 0.16937 | 0.12817 | 0.1236 | 0.082397 | 0.48065 | 0.37994 | 0.13275 | 0.009155 | 0.47607 | 0.064087 | 9.0225 | 0.10986 | -113.7085 | -122.2092 | 8.9264 | 0.054932 | 8.9722 | 0.064087
4572.2031 | 122.3099 | -0.07782 | 122.1313 | -0.01976 | 0.011446 | 0.010062 | -0.0095766 | -0.00091006 | -0.0081348 | -0.0011002 | -0.0084228 | 0.017831 | 0.042635 | -0.017201 | 0.012334 | 0.023964 | -0.0040525 | 8.8165 | 8.8211 | 8.4137 | 8.8303 | 8.9401 | 8.8211 | 8.876 | 0.054932 | -0.018311 | -0.032043 | 0.027466 | 0.16937 | 0.14191 | 0.11902 | 8.4915 | -113.3102 | -113.3011 | 9.0179 | 8.9539 | 8.8989 | 0.46234 | 0.40741 | 0.045777 | -122.1497 | -122.1039 | 0.24719 | 0.19684 | 0.21973 | 0.15106 | 0.17395 | 0.52643 | 0.41657 | 0.20142 | 0.059509 | 0.40741 | 0.013732 | 8.8989 | 0.059509 | -113.7177 | -122.1634 | 8.9081 | 0.10529 | 8.8943 | 0.13275
4573.9688 | 122.1863 | -0.10529 | 122.1817 | -0.01976 | 0.012514 | 0.012839 | -0.0050906 | 0.0054987 | -0.0098438 | -0.0055862 | -0.005371 | 0.023172 | 0.046053 | -0.014851 | 0.013616 | 0.023323 | -0.00063445 | 8.7433 | 8.8486 | 8.3954 | 8.6884 | 8.7845 | 8.6517 | 8.6929 | -0.059509 | 0.032043 | -0.059509 | -0.054932 | 0.009155 | -0.022888 | 0.027466 | 8.5007 | -113.3331 | -113.4933 | 8.8898 | 8.7982 | 8.757 | 0.29755 | 0.25635 | 0.045777 | -122.1497 | -122.2366 | 0.11444 | 0.13275 | 0.082398 | 0.086975 | 0.036621 | 0.3891 | 0.29297 | 0.068664 | 0.004577 | 0.45319 | 0.091552 | 8.9539 | 0.13733 | -113.7863 | -122.2412 | 8.7936 | 0.050354 | 8.8486 | 0.045777
4575.6875 | 122.3236 | -0.064087 | 122.168 | -0.01976 | 0.010805 | 0.009848 | -0.007654 | -0.0034735 | -0.0092028 | -0.0032364 | -0.005371 | 0.018686 | 0.041353 | -0.021901 | 0.012334 | 0.023751 | -0.0023435 | 8.8806 | 8.8394 | 8.4503 | 8.8943 | 9.0591 | 8.9127 | 8.9218 | 0.10071 | -0.018311 | -0.022888 | 0.054932 | 0.17395 | 0.14648 | 0.13733 | 8.5144 | -113.3286 | -113.2736 | 9.1232 | 8.9859 | 8.9767 | 0.4715 | 0.46234 | 0.041199 | -122.1863 | -122.113 | 0.23804 | 0.20142 | 0.21057 | 0.16022 | 0.16937 | 0.60883 | 0.44403 | 0.19684 | 0.07782 | 0.3891 | 0.004577 | 8.9035 | 0.045776 | -113.7177 | -122.1909 | 8.9584 | 0.11902 | 8.9447 | 0.1648
4577.4531 | 122.2046 | -0.11444 | 122.1771 | -0.012131 | 0.01166 | 0.011557 | -0.0089358 | -0.0019781 | -0.00963 | -0.00345 | -0.0084228 | 0.021249 | 0.043062 | -0.0086559 | 0.014898 | 0.023323 | -0.0044797 | 8.844 | 8.9127 | 8.432 | 8.7753 | 8.8852 | 8.7753 | 8.8028 | -0.054932 | 0.036621 | -0.054932 | -0.073242 | 0.036621 | 0.013733 | 0.041199 | 8.5464 | -113.2645 | -113.4018 | 8.9996 | 8.9172 | 8.8898 | 0.37079 | 0.34332 | 0.059509 | -122.1405 | -122.2504 | 0.15106 | 0.15564 | 0.12817 | 0.096131 | 0.068665 | 0.45319 | 0.34332 | 0.091553 | -0.01831 | 0.48065 | 0.091553 | 9.0271 | 0.15106 | -113.7451 | -122.2321 | 8.8898 | 0.041199 | 8.9584 | 0.059509
4579.1562 | 122.2 | -0.12817 | 122.1725 | -0.012131 | 0.009737 | 0.0089936 | -0.0070132 | 0.0029351 | -0.00963 | -0.0025956 | -0.005371 | 0.021463 | 0.043276 | -0.016774 | 0.011694 | 0.022683 | -0.0049069 | 8.8211 | 8.8898 | 8.4229 | 8.7708 | 8.8943 | 8.7753 | 8.8074 | -0.07782 | 0.032043 | -0.059509 | -0.068665 | 0.036621 | 0.013733 | 0.032043 | 8.551 | -113.2828 | -113.4018 | 9.0225 | 8.9355 | 8.9035 | 0.38452 | 0.35248 | 0.068665 | -122.1405 | -122.2412 | 0.1648 | 0.16022 | 0.14191 | 0.091552 | 0.073242 | 0.4715 | 0.3479 | 0.09613 | -0.009156 | 0.46692 | 0.091552 | 9.0179 | 0.16022 | -113.7497 | -122.2321 | 8.8989 | 0.059509 | 8.9493 | 0.050354
4580.9219 | 122.2504 | -0.086975 | 122.168 | -0.012131 | 0.014223 | 0.010703 | -0.005945 | 0.0018671 | -0.010485 | -0.0045182 | -0.0084228 | 0.022531 | 0.043489 | -0.017842 | 0.014257 | 0.022042 | -0.0034117 | 8.8074 | 8.8257 | 8.4137 | 8.757 | 8.8806 | 8.7433 | 8.7662 | 0.027466 | 0.013733 | -0.041199 | -0.009155 | 0.10071 | 0.059509 | 0.073242 | 8.5007 | -113.3423 | -113.4109 | 8.9676 | 8.8531 | 8.8303 | 0.35248 | 0.32959 | 0.045776 | -122.1542 | -122.1771 | 0.18768 | 0.16022 | 0.14648 | 0.11444 | 0.10071 | 0.46692 | 0.34332 | 0.14191 | 0.032044 | 0.41199 | 0.054932 | 8.9127 | 0.10071 | -113.7543 | -122.2092 | 8.844 | 0.07782 | 8.8943 | 0.11444
4582.7031 | 122.3328 | -0.064087 | 122.1405 | -0.01976 | 0.011019 | 0.010062 | -0.009363 | -0.00048286 | -0.0081348 | -0.0019546 | -0.005371 | 0.018899 | 0.041994 | -0.020405 | 0.012548 | 0.025032 | -0.0023435 | 8.8348 | 8.7662 | 8.4045 | 8.8348 | 9.0088 | 8.8486 | 8.8806 | 0.12817 | -0.009155 | -0.004578 | 0.045776 | 0.20142 | 0.17853 | 0.14648 | 8.4686 | -113.3743 | -113.3057 | 9.0729 | 8.9447 | 8.9127 | 0.47607 | 0.44403 | 0.059509 | -122.1497 | -122.0947 | 0.2655 | 0.21057 | 0.24261 | 0.15106 | 0.18311 | 0.60425 | 0.4303 | 0.20599 | 0.050354 | 0.36163 | -0.004577 | 8.8303 | 0.054932 | -113.736 | -122.1451 | 8.8989 | 0.10986 | 8.8989 | 0.19226
4584.4688 | 122.3282 | -0.054932 | 122.1542 | -0.012131 | 0.011446 | 0.0085662 | -0.011499 | -0.0024055 | -0.0087756 | -0.0021682 | -0.005371 | 0.021249 | 0.041994 | -0.017415 | 0.01148 | 0.022469 | -0.0034117 | 8.844 | 8.7708 | 8.3954 | 8.8531 | 9.0134 | 8.8715 | 8.8669 | 0.12817 | -0.027466 | -0.013733 | 0.036621 | 0.19684 | 0.16022 | 0.1236 | 8.4503 | -113.3835 | -113.3011 | 9.0683 | 8.9218 | 8.9264 | 0.4715 | 0.47607 | 0.041199 | -122.1817 | -122.1176 | 0.25177 | 0.17853 | 0.21515 | 0.13733 | 0.17395 | 0.61798 | 0.45776 | 0.21057 | 0.050354 | 0.37537 | -0.013733 | 8.8257 | 0.027466 | -113.7588 | -122.168 | 8.9081 | 0.091553 | 8.8989 | 0.18311
4586.1719 | 122.2092 | -0.11902 | 122.1954 | -0.01976 | 0.010805 | 0.009848 | -0.0074404 | -5.5462e-05 | -0.010057 | -0.0019546 | -0.005371 | 0.022958 | 0.040499 | -0.014851 | 0.010839 | 0.020974 | -0.0017027 | 8.8348 | 8.8257 | 8.4274 | 8.7845 | 8.9081 | 8.7708 | 8.8165 | -0.004578 | 0.018311 | -0.032043 | -0.073242 | 0.050354 | 0.050354 | 0.027466 | 8.5464 | -113.3698 | -113.4109 | 9.0271 | 8.9355 | 8.8898 | 0.3891 | 0.34332 | 0.086976 | -122.1771 | -122.2687 | 0.16937 | 0.14649 | 0.16937 | 0.059509 | 0.082397 | 0.48065 | 0.35706 | 0.082397 | -0.041199 | 0.39826 | 0.050354 | 8.9447 | 0.13733 | -113.768 | -122.2275 | 8.9035 | 0.045777 | 8.9539 | 0.11444
4587.9375 | 122.3373 | -0.054932 | 122.1451 | -0.01976 | 0.013582 | 0.0092072 | -0.0063724 | 0.0033623 | -0.0083484 | -0.0032364 | -0.0023192 | 0.019113 | 0.039858 | -0.022114 | 0.012334 | 0.024819 | -0.00042085 | 8.7708 | 8.6884 | 8.3496 | 8.7524 | 8.8486 | 8.7021 | 8.7479 | 0.09613 | -0.018311 | -0.004578 | 0.07782 | 0.15106 | 0.13275 | 0.14648 | 8.4045 | -113.4567 | -113.3926 | 8.9035 | 8.8028 | 8.757 | 0.39826 | 0.35248 | 0.050354 | -122.1634 | -122.0673 | 0.20599 | 0.20142 | 0.18768 | 0.15106 | 0.13733 | 0.49896 | 0.40283 | 0.15564 | 0.082398 | 0.33875 | -0.013733 | 8.7433 | 0.036621 | -113.7955 | -122.1497 | 8.8074 | 0.13275 | 8.8257 | 0.15106
4589.7188 | 122.2046 | -0.10529 | 122.1817 | -0.02739 | 0.017 | 0.011557 | -0.0038088 | -0.0013373 | -0.0083484 | -0.0019546 | -0.005371 | 0.023172 | 0.041353 | -0.012929 | 0.015325 | 0.024178 | -0.0014891 | 8.7021 | 8.7479 | 8.3496 | 8.6105 | 8.6975 | 8.5739 | 8.6243 | -0.050354 | 0.013733 | -0.064087 | -0.07782 | 0.013733 | -0.032043 | 0.045776 | 8.4549 | -113.4338 | -113.5712 | 8.8028 | 8.7296 | 8.6792 | 0.27466 | 0.22431 | 0.041199 | -122.168 | -122.2595 | 0.11902 | 0.15106 | 0.073243 | 0.10986 | 0.032044 | 0.3479 | 0.26093 | 0.07782 | -0.013733 | 0.39826 | 0.07782 | 8.8531 | 0.11902 | -113.8321 | -122.2458 | 8.7158 | 0.027466 | 8.8074 | 0.054932
4591.5 | 122.2961 | -0.073242 | 122.1725 | -0.02739 | 0.010378 | 0.011984 | -0.0089358 | 0.00079894 | -0.012621 | -0.00345 | -0.0084228 | 0.019754 | 0.041994 | -0.015919 | 0.010626 | 0.024178 | -0.0057615 | 8.812 | 8.757 | 8.4 | 8.8165 | 8.9447 | 8.8165 | 8.8211 | 0.07782 | -0.013733 | -0.022888 | 0.009155 | 0.14191 | 0.13733 | 0.11444 | 8.4732 | -113.4155 | -113.356 | 9.0179 | 8.8943 | 8.8898 | 0.42114 | 0.41657 | 0.050354 | -122.1863 | -122.1634 | 0.21515 | 0.18768 | 0.21057 | 0.13733 | 0.16022 | 0.54474 | 0.41657 | 0.16479 | 0.032043 | 0.35706 | 0.009155 | 8.8303 | 0.059509 | -113.7726 | -122.1954 | 8.8898 | 0.082397 | 8.8852 | 0.15106
4593.2031 | 122.2961 | -0.082397 | 122.1497 | -0.01976 | 0.010591 | 0.012198 | -0.0070132 | -0.00091006 | -0.0094164 | -0.0036636 | -0.005371 | 0.021463 | 0.043062 | -0.019551 | 0.012121 | 0.022255 | -0.0017027 | 8.7158 | 8.7112 | 8.3405 | 8.6929 | 8.8211 | 8.6838 | 8.7341 | 0.018311 | -0.004578 | -0.027466 | -0.009155 | 0.11902 | 0.091553 | 0.10986 | 8.4229 | -113.4384 | -113.4567 | 8.9035 | 8.8165 | 8.7662 | 0.39368 | 0.34332 | 0.054931 | -122.1542 | -122.1588 | 0.20142 | 0.19226 | 0.17395 | 0.13733 | 0.11902 | 0.48065 | 0.35248 | 0.14649 | 0.018311 | 0.37079 | 0.022888 | 8.7936 | 0.077819 | -113.8092 | -122.1771 | 8.7753 | 0.073242 | 8.7982 | 0.10071
4594.9844 | 122.1771 | -0.10986 | 122.2 | -0.01976 | 0.016146 | 0.010275 | -0.005945 | 0.0048577 | -0.0089892 | -0.0028092 | -0.0084228 | 0.021676 | 0.042635 | -0.014424 | 0.015325 | 0.023537 | -0.00020725 | 8.6929 | 8.7479 | 8.345 | 8.6105 | 8.7021 | 8.551 | 8.5876 | -0.091553 | 0.027466 | -0.054932 | -0.086975 | -0.009155 | -0.032043 | 0.022888 | 8.4549 | -113.4521 | -113.5895 | 8.812 | 8.6975 | 8.6609 | 0.24261 | 0.20599 | 0.054931 | -122.1725 | -122.287 | 0.10071 | 0.13275 | 0.07782 | 0.07782 | 0.022889 | 0.35706 | 0.2655 | 0.045777 | -0.032043 | 0.40283 | 0.082398 | 8.8577 | 0.13733 | -113.855 | -122.2549 | 8.7204 | 0.022888 | 8.8028 | 0.01831
4596.7031 | 122.2092 | -0.10986 | 122.2046 | -0.01976 | 0.014223 | 0.010703 | -0.0061588 | 0.00058534 | -0.0074938 | -0.0049454 | -0.005371 | 0.020822 | 0.039644 | -0.011647 | 0.013189 | 0.024391 | -0.0040525 | 8.6884 | 8.7158 | 8.3313 | 8.6105 | 8.7021 | 8.5693 | 8.6151 | -0.064087 | 0.027466 | -0.041199 | -0.064087 | 0 | -0.022888 | 0.027466 | 8.4412 | -113.4888 | -113.5941 | 8.812 | 8.725 | 8.6792 | 0.28381 | 0.23804 | 0.068664 | -122.1771 | -122.2687 | 0.10986 | 0.13733 | 0.086975 | 0.068665 | 0.018311 | 0.37079 | 0.27924 | 0.041199 | -0.022888 | 0.38452 | 0.068665 | 8.8257 | 0.13733 | -113.8733 | -122.2458 | 8.7204 | 0.045776 | 8.7982 | 0.045776
4598.4688 | 122.287 | -0.10071 | 122.1634 | -0.01976 | 0.010164 | 0.01113 | -0.0097904 | 0.0010125 | -0.00963 | -0.0030228 | -0.005371 | 0.020181 | 0.043276 | -0.012715 | 0.013189 | 0.025032 | -0.0017027 | 8.7753 | 8.7204 | 8.3725 | 8.7891 | 8.9127 | 8.7753 | 8.8074 | 0.064087 | -0.013733 | -0.027466 | 0.004578 | 0.13733 | 0.11444 | 0.091553 | 8.4732 | -113.443 | -113.3743 | 9.0134 | 8.9081 | 8.876 | 0.43487 | 0.40283 | 0.073242 | -122.1771 | -122.1588 | 0.23804 | 0.19226 | 0.21515 | 0.11902 | 0.14191 | 0.54016 | 0.41656 | 0.16479 | 0.032044 | 0.3479 | 0.013733 | 8.8211 | 0.086975 | -113.7909 | -122.1909 | 8.8898 | 0.10529 | 8.876 | 0.1648
4600.1875 | 122.2321 | -0.09613 | 122.2046 | 0.0031279 | 0.01166 | 0.010275 | -0.0044498 | -0.00048286 | -0.010271 | -0.0025956 | -0.0084228 | 0.022531 | 0.043062 | -0.019124 | 0.014257 | 0.021401 | -0.0042661 | 8.7341 | 8.7936 | 8.3679 | 8.6792 | 8.7845 | 8.6609 | 8.6975 | -0.041199 | 0.036621 | -0.041199 | -0.050354 | 0.059509 | 0.027466 | 0.050354 | 8.4641 | -113.4109 | -113.5254 | 8.8806 | 8.7936 | 8.757 | 0.32959 | 0.29297 | 0.054931 | -122.168 | -122.2549 | 0.15564 | 0.14648 | 0.1236 | 0.091553 | 0.068665 | 0.41657 | 0.31128 | 0.10071 | -0.009155 | 0.42572 | 0.07782 | 8.8898 | 0.13275 | -113.8367 | -122.2458 | 8.7753 | 0.045776 | 8.8303 | 0.054931
4601.9531 | 122.3419 | -0.07782 | 122.1542 | -0.0045011 | 0.01166 | 0.010275 | -0.010004 | -0.0021919 | -0.010485 | -0.00345 | -0.0023192 | 0.019113 | 0.043062 | -0.022114 | 0.011907 | 0.02546 | 6.346e-06 | 8.6792 | 8.6838 | 8.3221 | 8.7067 | 8.8348 | 8.6975 | 8.7433 | 0.073242 | -0.004578 | -0.036621 | 0.032043 | 0.16479 | 0.14648 | 0.13275 | 8.4 | -113.4705 | -113.4476 | 8.9127 | 8.8211 | 8.7753 | 0.42114 | 0.37537 | 0.041199 | -122.1588 | -122.1222 | 0.24261 | 0.21057 | 0.2243 | 0.16937 | 0.18311 | 0.5127 | 0.38452 | 0.20142 | 0.068664 | 0.36163 | 0.032043 | 8.7616 | 0.073242 | -113.8321 | -122.1909 | 8.7845 | 0.10986 | 8.757 | 0.15106
4603.6562 | 122.3648 | -0.054932 | 122.1451 | -0.01976 | 0.0099506 | 0.0096344 | -0.0089358 | -0.0030463 | -0.010912 | -0.0032364 | -0.0023192 | 0.017831 | 0.039858 | -0.019337 | 0.010626 | 0.022683 | -0.0029843 | 8.7616 | 8.6792 | 8.345 | 8.7753 | 8.9401 | 8.7753 | 8.7982 | 0.13733 | -0.009155 | -0.018311 | 0.054932 | 0.20142 | 0.17395 | 0.14191 | 8.4 | -113.4659 | -113.3698 | 8.9951 | 8.8532 | 8.8303 | 0.45319 | 0.4303 | 0.036621 | -122.1542 | -122.0901 | 0.25635 | 0.19684 | 0.22888 | 0.16022 | 0.19226 | 0.59509 | 0.4303 | 0.21973 | 0.073243 | 0.33417 | 0.009156 | 8.7341 | 0.045777 | -113.8 | -122.1634 | 8.8303 | 0.10986 | 8.8165 | 0.19226
4605.4219 | 122.3145 | -0.050354 | 122.1771 | -0.012131 | 0.013369 | 0.011984 | -0.0074404 | 0.0025079 | -0.0094164 | -0.0055862 | -0.011475 | 0.020608 | 0.040285 | -0.019978 | 0.012975 | 0.023751 | -0.0072569 | 8.6792 | 8.6105 | 8.2901 | 8.6838 | 8.812 | 8.638 | 8.7021 | 0.10986 | -0.027466 | 0.004578 | 0.041199 | 0.16022 | 0.12817 | 0.12817 | 8.3405 | -113.5666 | -113.4933 | 8.8623 | 8.7524 | 8.6884 | 0.41199 | 0.3479 | 0.054932 | -122.2046 | -122.1359 | 0.21057 | 0.17853 | 0.17853 | 0.1236 | 0.1236 | 0.52185 | 0.39368 | 0.15564 | 0.036621 | 0.32043 | -0.032044 | 8.6609 | 0.022888 | -113.887 | -122.1725 | 8.7341 | 0.091553 | 8.7296 | 0.16022
4607.125 | 122.3419 | -0.073242 | 122.1588 | -0.012131 | 0.010591 | 0.0083526 | -0.0074404 | -0.0011237 | -0.0098438 | -0.0036636 | -0.0084228 | 0.018472 | 0.041994 | -0.02126 | 0.012334 | 0.024178 | -0.0021299 | 8.7433 | 8.7021 | 8.3313 | 8.757 | 8.9035 | 8.7524 | 8.7891 | 0.15106 | -0.022888 | -0.013733 | 0.045776 | 0.19684 | 0.16479 | 0.12817 | 8.4045 | -113.4567 | -113.4018 | 8.9767 | 8.8623 | 8.8257 | 0.45776 | 0.42114 | 0.059509 | -122.1817 | -122.113 | 0.27008 | 0.20142 | 0.23804 | 0.14191 | 0.17853 | 0.5722 | 0.42572 | 0.21057 | 0.059509 | 0.37079 | -0.009155 | 8.7753 | 0.050354 | -113.8275 | -122.1725 | 8.8303 | 0.11902 | 8.8165 | 0.2243
4608.9062 | 122.2595 | -0.11444 | 122.2183 | -0.012131 | 0.011232 | 0.010703 | -0.0072268 | -0.0017645 | -0.01198 | -0.0025956 | -0.0023192 | 0.023599 | 0.040926 | -0.0082287 | 0.012121 | 0.022896 | -0.0042661 | 8.7067 | 8.7708 | 8.345 | 8.6517 | 8.7524 | 8.6472 | 8.6655 | -0.073242 | 0.032043 | -0.064087 | -0.068665 | 0.054932 | 0.018311 | 0.045776 | 8.4595 | -113.4476 | -113.5666 | 8.8669 | 8.7799 | 8.7616 | 0.32043 | 0.30212 | 0.050354 | -122.1863 | -122.287 | 0.16937 | 0.16022 | 0.13275 | 0.10986 | 0.082398 | 0.40741 | 0.3067 | 0.11902 | -0.004578 | 0.42572 | 0.09613 | 8.8852 | 0.14648 | -113.8733 | -122.2824 | 8.7662 | 0.045776 | 8.8211 | 0.041199
4610.625 | 122.2549 | -0.10986 | 122.2092 | -0.0045011 | 0.014437 | 0.0096344 | -0.005945 | -0.00048286 | -0.0083484 | -0.0028092 | -0.0084228 | 0.021035 | 0.043276 | -0.0097241 | 0.014471 | 0.022896 | -0.0042661 | 8.6014 | 8.6472 | 8.2718 | 8.5419 | 8.6609 | 8.5007 | 8.5464 | -0.041199 | 0.027466 | -0.064087 | -0.032043 | 0.045776 | 0.009155 | 0.041199 | 8.3817 | -113.562 | -113.6673 | 8.7708 | 8.6563 | 8.6105 | 0.27466 | 0.22888 | 0.045776 | -122.1817 | -122.2412 | 0.15564 | 0.15106 | 0.11902 | 0.10529 | 0.073242 | 0.3891 | 0.27008 | 0.10986 | 0.032044 | 0.37537 | 0.091553 | 8.757 | 0.13733 | -113.9374 | -122.2733 | 8.6517 | 0.07782 | 8.7112 | 0.068664
4612.4062 | 122.2595 | -0.10071 | 122.2046 | -0.01976 | 0.015718 | 0.013266 | -0.005945 | -5.5462e-05 | -0.008562 | -0.0038772 | -0.0084228 | 0.020608 | 0.043489 | -0.016774 | 0.014898 | 0.02311 | -0.0023435 | 8.7021 | 8.6838 | 8.3176 | 8.6472 | 8.7708 | 8.6197 | 8.6426 | 0.022888 | 0.022888 | -0.050354 | -0.013733 | 0.068665 | 0.027466 | 0.064087 | 8.4183 | -113.5208 | -113.5574 | 8.8715 | 8.7433 | 8.7204 | 0.32501 | 0.30212 | 0.050354 | -122.1817 | -122.2183 | 0.16937 | 0.1648 | 0.12817 | 0.11444 | 0.07782 | 0.45319 | 0.32959 | 0.11902 | 0.036621 | 0.36621 | 0.073242 | 8.7845 | 0.1236 | -113.887 | -122.2549 | 8.7479 | 0.086975 | 8.8028 | 0.1236
4614.125 | 122.2549 | -0.10529 | 122.1954 | -0.01976 | 0.011232 | 0.010275 | -0.0097904 | 0.0020807 | -0.0083484 | -0.002382 | -0.005371 | 0.020822 | 0.043703 | -0.0090833 | 0.013616 | 0.022469 | -0.0019163 | 8.6655 | 8.7387 | 8.3221 | 8.6151 | 8.725 | 8.6105 | 8.6563 | -0.050354 | 0.032043 | -0.050354 | -0.059509 | 0.054932 | 0.022888 | 0.054932 | 8.4274 | -113.4567 | -113.5803 | 8.8303 | 8.7616 | 8.7158 | 0.33417 | 0.28839 | 0.054932 | -122.1634 | -122.2549 | 0.16022 | 0.16022 | 0.12817 | 0.10529 | 0.073242 | 0.40283 | 0.29297 | 0.10529 | -0.009155 | 0.41656 | 0.082397 | 8.844 | 0.13733 | -113.8733 | -122.2458 | 8.7204 | 0.045777 | 8.7708 | 0.054932
4615.9062 | 122.2366 | -0.11444 | 122.2321 | -0.0045011 | 0.011232 | 0.0094208 | -0.0089358 | -5.5462e-05 | -0.0079212 | -0.0043046 | -0.0084228 | 0.018472 | 0.045839 | -0.015065 | 0.014043 | 0.023537 | 0.00021995 | 8.6426 | 8.725 | 8.3267 | 8.606 | 8.7479 | 8.6197 | 8.6517 | -0.054932 | 0.018311 | -0.050354 | -0.07782 | 0.041199 | 0.004578 | 0.013733 | 8.4412 | -113.5071 | -113.6261 | 8.8623 | 8.7662 | 8.7341 | 0.32501 | 0.29297 | 0.064087 | -122.2137 | -122.3099 | 0.15564 | 0.12817 | 0.11902 | 0.064087 | 0.054932 | 0.42114 | 0.27924 | 0.091553 | -0.027466 | 0.39826 | 0.068665 | 8.8394 | 0.13275 | -113.9053 | -122.2824 | 8.7204 | 0.036621 | 8.757 | 0.059509
4617.6875 | 122.2641 | -0.091553 | 122.2137 | -0.0045011 | 0.011232 | 0.00878 | -0.0080814 | -0.0015509 | -0.010057 | -0.0030228 | -0.005371 | 0.020608 | 0.044985 | -0.016774 | 0.012334 | 0.022896 | -0.0023435 | 8.6929 | 8.6563 | 8.3176 | 8.67 | 8.7982 | 8.6884 | 8.7021 | 0.027466 | 0 | -0.036621 | -0.050354 | 0.07782 | 0.045776 | 0.064087 | 8.4091 | -113.5574 | -113.5437 | 8.8898 | 8.7936 | 8.7799 | 0.38452 | 0.37079 | 0.054932 | -122.2137 | -122.2641 | 0.16937 | 0.15564 | 0.13733 | 0.10071 | 0.082397 | 0.48065 | 0.35248 | 0.11444 | -0.013733 | 0.33875 | 0.036621 | 8.7479 | 0.091553 | -113.8962 | -122.2504 | 8.7616 | 0.041199 | 8.7845 | 0.11902
4619.4531 | 122.3282 | -0.07782 | 122.2092 | -0.02739 | 0.015718 | 0.010489 | -0.0055178 | 0.0018671 | -0.0064258 | -0.0062272 | -0.005371 | 0.020395 | 0.042421 | -0.012501 | 0.01383 | 0.02311 | -0.0036253 | 8.5373 | 8.5831 | 8.226 | 8.4915 | 8.6105 | 8.4732 | 8.5144 | 0.009155 | -0.009155 | -0.027466 | 0.009155 | 0.11444 | 0.09613 | 0.10071 | 8.3038 | -113.6261 | -113.7177 | 8.6884 | 8.5922 | 8.551 | 0.28839 | 0.24719 | 0.050354 | -122.2183 | -122.2 | 0.19226 | 0.17853 | 0.17395 | 0.12817 | 0.1236 | 0.38452 | 0.2655 | 0.14191 | 0.036621 | 0.35706 | 0.018311 | 8.6609 | 0.068665 | -113.9832 | -122.2366 | 8.5693 | 0.086975 | 8.6151 | 0.086975
4621.2344 | 122.319 | -0.064087 | 122.1863 | -0.012131 | 0.012728 | 0.009848 | -0.0095766 | 0.0048577 | -0.0081348 | -0.0038772 | -0.0084228 | 0.018899 | 0.043917 | -0.017842 | 0.012548 | 0.023537 | -0.0036253 | 8.5739 | 8.5419 | 8.2306 | 8.5739 | 8.725 | 8.5464 | 8.5876 | 0.068665 | -0.027466 | -0.022888 | 0.013733 | 0.10986 | 0.091553 | 0.091553 | 8.2947 | -113.6444 | -113.6124 | 8.7891 | 8.6517 | 8.6105 | 0.35705 | 0.31586 | 0.041199 | -122.2137 | -122.1725 | 0.17395 | 0.15564 | 0.15564 | 0.11444 | 0.11444 | 0.49438 | 0.34332 | 0.13275 | 0.036621 | 0.31128 | -0.004578 | 8.606 | 0.036621 | -113.9557 | -122.2092 | 8.638 | 0.07782 | 8.638 | 0.13275
4622.9531 | 122.3282 | -0.068665 | 122.168 | -0.012131 | 0.012728 | 0.011343 | -0.0089358 | 0.00058534 | -0.0074938 | -0.0004592 | -0.0023192 | 0.018472 | 0.04178 | -0.020833 | 0.014257 | 0.023964 | -0.0019163 | 8.5785 | 8.5648 | 8.2397 | 8.5602 | 8.6884 | 8.5419 | 8.5968 | 0.032043 | -0.022888 | -0.018311 | 0.009155 | 0.10986 | 0.10071 | 0.091553 | 8.3084 | -113.6032 | -113.6078 | 8.757 | 8.6655 | 8.6105 | 0.35706 | 0.30212 | 0.050354 | -122.1909 | -122.1588 | 0.17853 | 0.16022 | 0.16937 | 0.10986 | 0.11902 | 0.44861 | 0.32043 | 0.12817 | 0.027466 | 0.32501 | -0.004577 | 8.6334 | 0.045777 | -113.9282 | -122.1863 | 8.6288 | 0.07782 | 8.6472 | 0.10071
4624.7188 | 122.2321 | -0.10529 | 122.2229 | -0.01976 | 0.014437 | 0.011343 | -0.0035952 | -0.0026191 | -0.011339 | -0.0036636 | -0.005371 | 0.021463 | 0.043276 | -0.020192 | 0.015112 | 0.024605 | -0.0031979 | 8.5602 | 8.6105 | 8.2443 | 8.4824 | 8.5648 | 8.4229 | 8.4686 | -0.073242 | 0.036621 | -0.07782 | -0.07782 | 0.013733 | -0.027466 | 0.045776 | 8.3496 | -113.6124 | -113.7405 | 8.67 | 8.5739 | 8.5281 | 0.2243 | 0.17853 | 0.027466 | -122.1863 | -122.3007 | 0.11902 | 0.15106 | 0.07782 | 0.1236 | 0.050354 | 0.32043 | 0.23804 | 0.091553 | 0 | 0.36621 | 0.11444 | 8.7158 | 0.14191 | -113.9786 | -122.3007 | 8.5876 | 0.027466 | 8.6655 | 0.032044
4626.4844 | 122.2229 | -0.10986 | 122.2183 | -0.01976 | 0.014009 | 0.009848 | -0.0033816 | 0.0010125 | -0.0094164 | -0.0013138 | -0.0084228 | 0.023172 | 0.043703 | -0.015919 | 0.014898 | 0.023537 | -0.0034117 | 8.5693 | 8.5922 | 8.2443 | 8.5144 | 8.6197 | 8.4778 | 8.4915 | -0.041199 | 0.032043 | -0.036621 | -0.059509 | 0.027466 | 0.004578 | 0.027466 | 8.3542 | -113.6261 | -113.7039 | 8.7296 | 8.6014 | 8.5876 | 0.24719 | 0.23346 | 0.073242 | -122.1863 | -122.2778 | 0.13733 | 0.13733 | 0.11444 | 0.064087 | 0.041199 | 0.37537 | 0.27008 | 0.064087 | -0.022888 | 0.3479 | 0.068664 | 8.7021 | 0.14191 | -113.974 | -122.2549 | 8.6243 | 0.050354 | 8.6792 | 0.068664
4628.1875 | 122.2733 | -0.11902 | 122.2412 | -0.012131 | 0.0123 | 0.0089936 | -0.005945 | -0.00048286 | -0.011553 | -0.0013138 | -0.0023192 | 0.022317 | 0.042849 | -0.011006 | 0.013616 | 0.024605 | -0.0036253 | 8.6197 | 8.6609 | 8.2809 | 8.5785 | 8.6975 | 8.5785 | 8.5922 | -0.032043 | 0.022888 | -0.054932 | -0.032043 | 0.082397 | 0.050354 | 0.073242 | 8.4 | -113.5803 | -113.6627 | 8.8165 | 8.7112 | 8.6975 | 0.31128 | 0.29755 | 0.064087 | -122.2183 | -122.2733 | 0.20142 | 0.19226 | 0.16937 | 0.12817 | 0.10529 | 0.41657 | 0.29755 | 0.13733 | 0.022889 | 0.37994 | 0.07782 | 8.7799 | 0.14191 | -113.9603 | -122.2961 | 8.6975 | 0.086976 | 8.7387 | 0.086976
4629.9531 | 122.3877 | -0.050354 | 122.1817 | -0.0045011 | 0.010378 | 0.010062 | -0.010431 | 0.0037897 | -0.0098438 | -0.0013138 | -0.0023192 | 0.018258 | 0.042208 | -0.018696 | 0.012334 | 0.023537 | -0.0049069 | 8.6243 | 8.5739 | 8.2626 | 8.638 | 8.8074 | 8.6563 | 8.6792 | 0.1236 | -0.009155 | -0.013733 | 0.050354 | 0.19684 | 0.16022 | 0.14648 | 8.313 | -113.6078 | -113.5437 | 8.8577 | 8.7296 | 8.7067 | 0.41657 | 0.39368 | 0.036621 | -122.1909 | -122.1313 | 0.24719 | 0.19684 | 0.21057 | 0.16022 | 0.17395 | 0.54474 | 0.37537 | 0.21057 | 0.064087 | 0.31128 | 0.004578 | 8.6243 | 0.041199 | -113.9191 | -122.1954 | 8.6884 | 0.10071 | 8.6746 | 0.17395
4631.6719 | 122.2275 | -0.10986 | 122.2412 | -0.01976 | 0.015505 | 0.011557 | -0.0074404 | 0.0025079 | -0.011553 | -0.0004592 | -0.005371 | 0.022103 | 0.044344 | -0.013142 | 0.01618 | 0.025673 | -0.0083249 | 8.5373 | 8.5739 | 8.226 | 8.4549 | 8.5739 | 8.4229 | 8.4549 | -0.054932 | 0.027466 | -0.050354 | -0.073242 | 0 | -0.032043 | 0.032043 | 8.3359 | -113.6673 | -113.7863 | 8.6838 | 8.5648 | 8.5327 | 0.22888 | 0.19684 | 0.059509 | -122.2137 | -122.3145 | 0.10986 | 0.14191 | 0.07782 | 0.082397 | 0.018311 | 0.3479 | 0.22888 | 0.050354 | -0.022888 | 0.3479 | 0.07782 | 8.6838 | 0.13733 | -114.0152 | -122.2916 | 8.5648 | 0.036621 | 8.6472 | 0.054931
4633.4375 | 122.374 | -0.073242 | 122.2092 | -0.012131 | 0.0093098 | 0.0096344 | -0.0089358 | 0.0018671 | -0.010698 | -0.0021682 | -0.0084228 | 0.022317 | 0.042421 | -0.01656 | 0.012548 | 0.024178 | -0.0059751 | 8.6197 | 8.5464 | 8.2352 | 8.6197 | 8.7845 | 8.6243 | 8.6563 | 0.12817 | -0.022888 | -0.013733 | 0.054932 | 0.19684 | 0.16937 | 0.13733 | 8.3084 | -113.6627 | -113.5895 | 8.8577 | 8.7296 | 8.6975 | 0.42114 | 0.3891 | 0.059509 | -122.2321 | -122.1542 | 0.27008 | 0.21057 | 0.24261 | 0.15106 | 0.18311 | 0.54932 | 0.38452 | 0.21057 | 0.068665 | 0.31128 | -0.009155 | 8.6197 | 0.050354 | -113.974 | -122.2229 | 8.6929 | 0.12817 | 8.6929 | 0.20142
4635.2188 | 122.3831 | -0.050354 | 122.2137 | -0.02739 | 0.015505 | 0.01113 | -0.0089358 | 0.0022943 | -0.0083484 | -0.0036636 | -0.005371 | 0.019113 | 0.04178 | -0.020192 | 0.012121 | 0.023537 | -0.0046933 | 8.519 | 8.4457 | 8.1711 | 8.4961 | 8.6243 | 8.4549 | 8.519 | 0.11902 | -0.018311 | -0.004578 | 0.091553 | 0.17853 | 0.1236 | 0.13733 | 8.2214 | -113.768 | -113.7177 | 8.6746 | 8.5693 | 8.5052 | 0.3479 | 0.28381 | 0.045776 | -122.2321 | -122.1222 | 0.22888 | 0.18768 | 0.17395 | 0.14191 | 0.12817 | 0.45319 | 0.32501 | 0.18311 | 0.096131 | 0.27466 | -0.013733 | 8.4961 | 0.032043 | -114.0427 | -122.2183 | 8.5464 | 0.14191 | 8.5693 | 0.16937
4636.9375 | 122.3465 | -0.073242 | 122.1863 | -0.012131 | 0.010378 | 0.010275 | -0.0080814 | 0.00058534 | -0.010271 | -0.0019546 | -0.0084228 | 0.018686 | 0.042849 | -0.013783 | 0.010412 | 0.022255 | -0.0029843 | 8.5876 | 8.5464 | 8.2352 | 8.5876 | 8.7204 | 8.5831 | 8.6105 | 0.082397 | 0.009155 | -0.009155 | 0.004578 | 0.15564 | 0.10529 | 0.10071 | 8.3084 | -113.6398 | -113.5986 | 8.7936 | 8.6838 | 8.6563 | 0.37537 | 0.3479 | 0.064087 | -122.1771 | -122.1817 | 0.22888 | 0.17395 | 0.17853 | 0.10986 | 0.11444 | 0.48523 | 0.35248 | 0.16479 | 0.013733 | 0.31128 | 0.01831 | 8.6197 | 0.082397 | -113.9511 | -122.1954 | 8.6609 | 0.07782 | 8.6609 | 0.15564
4638.6875 | 122.2458 | -0.1236 | 122.2275 | -0.01976 | 0.015718 | 0.011771 | -0.005945 | 0.0027215 | -0.0072802 | -0.0040908 | -0.0084228 | 0.022531 | 0.04114 | -0.0063061 | 0.014684 | 0.022255 | -0.0042661 | 8.4457 | 8.5007 | 8.1665 | 8.3771 | 8.4869 | 8.3359 | 8.3908 | -0.054932 | 0.027466 | -0.054932 | -0.068665 | 0.009155 | -0.036621 | 0.041199 | 8.2901 | -113.7268 | -113.8504 | 8.6105 | 8.5144 | 8.4595 | 0.2243 | 0.16937 | 0.068664 | -122.2 | -122.2961 | 0.13275 | 0.16479 | 0.086975 | 0.096131 | 0.018311 | 0.32043 | 0.21057 | 0.064087 | -0.013733 | 0.33417 | 0.082398 | 8.6243 | 0.15106 | -114.061 | -122.2824 | 8.5007 | 0.054931 | 8.5693 | 0.068664
4640.3906 | 122.3145 | -0.082397 | 122.2137 | -0.012131 | 0.013582 | 0.012198 | -0.0067996 | 0.0016535 | -0.0072802 | -0.0025956 | -0.005371 | 0.019754 | 0.044771 | -0.0099377 | 0.013403 | 0.02311 | -0.0081113 | 8.4183 | 8.4686 | 8.1299 | 8.3633 | 8.4778 | 8.3313 | 8.3862 | -0.009155 | 0.009155 | -0.036621 | -0.013733 | 0.073242 | 0.032043 | 0.07782 | 8.2123 | -113.7451 | -113.8504 | 8.5602 | 8.4686 | 8.4137 | 0.25635 | 0.20142 | 0.045776 | -122.2046 | -122.2275 | 0.15564 | 0.16022 | 0.11444 | 0.11444 | 0.068664 | 0.3479 | 0.23346 | 0.10986 | 0.022888 | 0.33875 | 0.045776 | 8.551 | 0.091552 | -114.0839 | -122.2504 | 8.4457 | 0.068664 | 8.5007 | 0.073242
4642.1719 | 122.2458 | -0.10529 | 122.2549 | -0.012131 | 0.015291 | 0.010703 | -0.0055178 | 0.0014397 | -0.0070666 | -0.0060134 | -0.0084228 | 0.022531 | 0.045412 | -0.016347 | 0.014684 | 0.02311 | -0.0038389 | 8.4274 | 8.4869 | 8.139 | 8.3359 | 8.4183 | 8.2809 | 8.345 | -0.068665 | 0.018311 | -0.045776 | -0.068665 | 0.013733 | -0.027466 | 0.036621 | 8.2443 | -113.768 | -113.9191 | 8.5236 | 8.4503 | 8.3862 | 0.20599 | 0.14191 | 0.05951 | -122.2366 | -122.3236 | 0.11902 | 0.14191 | 0.07782 | 0.082397 | 0.01831 | 0.27924 | 0.19684 | 0.059509 | -0.022889 | 0.3479 | 0.064087 | 8.5922 | 0.1236 | -114.1159 | -122.3007 | 8.4412 | 0.036621 | 8.5327 | 0.036621
4643.9375 | 122.3053 | -0.09613 | 122.2458 | -0.012131 | 0.0123 | 0.012412 | -0.0074404 | 0.00037174 | -0.0087756 | -0.0038772 | -0.0084228 | 0.022531 | 0.042208 | -0.013356 | 0.015325 | 0.023323 | -0.0021299 | 8.4961 | 8.4961 | 8.1711 | 8.4595 | 8.5831 | 8.4183 | 8.4549 | 0.032043 | 0.009155 | -0.036621 | -0.022888 | 0.086975 | 0.041199 | 0.059509 | 8.2672 | -113.7497 | -113.7863 | 8.6792 | 8.551 | 8.5144 | 0.28381 | 0.24719 | 0.059509 | -122.2366 | -122.2687 | 0.1831 | 0.15564 | 0.13733 | 0.09613 | 0.07782 | 0.41199 | 0.28839 | 0.1236 | 0.013733 | 0.32501 | 0.045776 | 8.5922 | 0.10528 | -114.0747 | -122.2824 | 8.5556 | 0.073242 | 8.5922 | 0.12817
4645.7188 | 122.2504 | -0.10071 | 122.2458 | -0.012131 | 0.016146 | 0.011984 | -0.005945 | 0.00058534 | -0.0089892 | -0.0032364 | -0.005371 | 0.022531 | 0.044985 | -0.0065197 | 0.014257 | 0.023751 | -0.0042661 | 8.4091 | 8.4412 | 8.1253 | 8.3084 | 8.3954 | 8.2581 | 8.3267 | -0.068665 | 0.013733 | -0.036621 | -0.068665 | 0 | -0.022888 | 0.036621 | 8.226 | -113.8046 | -113.9374 | 8.4961 | 8.4274 | 8.3588 | 0.20142 | 0.13275 | 0.064087 | -122.2321 | -122.3145 | 0.10071 | 0.13733 | 0.07782 | 0.073242 | 0.013733 | 0.27008 | 0.18311 | 0.036621 | -0.032044 | 0.31586 | 0.050354 | 8.5419 | 0.11444 | -114.1205 | -122.2824 | 8.4091 | 0.032043 | 8.5098 | 0.032043
4647.4375 | 122.3923 | -0.054932 | 122.2229 | -0.012131 | 0.01166 | 0.010489 | -0.0097904 | -0.0028327 | -0.0081348 | -0.0019546 | -0.005371 | 0.017831 | 0.042849 | -0.0266 | 0.01148 | 0.023537 | -0.00020725 | 8.5052 | 8.4641 | 8.1711 | 8.5464 | 8.6929 | 8.519 | 8.5648 | 0.11902 | 0.004578 | -0.022888 | 0.054932 | 0.17853 | 0.16022 | 0.13733 | 8.226 | -113.7588 | -113.6765 | 8.7479 | 8.6197 | 8.5739 | 0.39368 | 0.3479 | 0.032044 | -122.2183 | -122.168 | 0.23346 | 0.19226 | 0.21515 | 0.16022 | 0.1831 | 0.52185 | 0.37537 | 0.20142 | 0.07782 | 0.29297 | 0.027466 | 8.519 | 0.05951 | -114.0518 | -122.2458 | 8.6014 | 0.10986 | 8.5602 | 0.17395
4649.1875 | 122.287 | -0.10529 | 122.2458 | -0.012131 | 0.013369 | 0.0094208 | -0.0072268 | 0.0042169 | -0.010698 | -0.005159 | -0.0084228 | 0.023385 | 0.043062 | -0.011433 | 0.014257 | 0.022255 | -0.0023435 | 8.4778 | 8.4686 | 8.1482 | 8.4274 | 8.551 | 8.4 | 8.4183 | 0.013733 | 0.018311 | -0.022888 | -0.022888 | 0.07782 | 0.027466 | 0.054932 | 8.2535 | -113.7772 | -113.8184 | 8.6563 | 8.5236 | 8.5052 | 0.27008 | 0.25177 | 0.082398 | -122.2275 | -122.2687 | 0.18311 | 0.16022 | 0.13275 | 0.07782 | 0.050354 | 0.40283 | 0.27924 | 0.10071 | 0 | 0.32044 | 0.041199 | 8.5739 | 0.1236 | -114.0976 | -122.2687 | 8.5327 | 0.082398 | 8.5831 | 0.11902
4650.9531 | 122.3419 | -0.054932 | 122.2275 | -0.01976 | 0.009737 | 0.011771 | -0.0095766 | 0.00037174 | -0.0083484 | -0.0008866 | -0.0084228 | 0.018472 | 0.042421 | -0.019124 | 0.012121 | 0.023323 | -0.0034117 | 8.5098 | 8.4641 | 8.1757 | 8.4915 | 8.6426 | 8.5098 | 8.5281 | 0.082397 | 0.004578 | -0.032043 | 0.004578 | 0.14191 | 0.11444 | 0.10529 | 8.2306 | -113.7634 | -113.736 | 8.6975 | 8.5831 | 8.5648 | 0.35248 | 0.33417 | 0.022889 | -122.2229 | -122.2229 | 0.19684 | 0.16022 | 0.16937 | 0.13733 | 0.14648 | 0.46692 | 0.31586 | 0.17395 | 0.036621 | 0.28839 | 0.036621 | 8.519 | 0.05951 | -114.0518 | -122.2595 | 8.5464 | 0.05951 | 8.5648 | 0.13733
4652.7344 | 122.3236 | -0.09613 | 122.2504 | -0.01976 | 0.012514 | 0.011343 | -0.0040224 | 0.0037897 | -0.011339 | -0.002382 | -0.0084228 | 0.02189 | 0.040712 | -0.010579 | 0.014043 | 0.02311 | -0.0042661 | 8.4641 | 8.4686 | 8.1665 | 8.4045 | 8.5327 | 8.4 | 8.4091 | 0.032043 | 0.027466 | -0.045776 | -0.027466 | 0.091553 | 0.064087 | 0.091553 | 8.2626 | -113.7817 | -113.8458 | 8.6288 | 8.5052 | 8.4961 | 0.24262 | 0.23346 | 0.050354 | -122.2229 | -122.2778 | 0.18768 | 0.18768 | 0.16022 | 0.13733 | 0.10986 | 0.36621 | 0.23804 | 0.13733 | 0.01831 | 0.30212 | 0.073242 | 8.5648 | 0.1236 | -114.0839 | -122.2961 | 8.5007 | 0.068664 | 8.5602 | 0.12817
4654.5156 | 122.2687 | -0.11444 | 122.2687 | -0.01976 | 0.011019 | 0.0083526 | -0.009363 | -0.00069646 | -0.010485 | -0.0002456 | -0.0084228 | 0.022103 | 0.041994 | -0.019124 | 0.012121 | 0.023323 | -0.0023435 | 8.4137 | 8.5007 | 8.1482 | 8.3954 | 8.519 | 8.4137 | 8.4366 | -0.07782 | 0.032043 | -0.059509 | -0.10071 | 0.032043 | 0.009155 | 0.032043 | 8.2626 | -113.768 | -113.8733 | 8.6334 | 8.551 | 8.5281 | 0.28839 | 0.2655 | 0.054932 | -122.2366 | -122.3694 | 0.14648 | 0.14648 | 0.1236 | 0.091552 | 0.068664 | 0.37079 | 0.24719 | 0.091552 | -0.041199 | 0.35248 | 0.091552 | 8.6151 | 0.14648 | -114.1205 | -122.3282 | 8.5098 | 0.013733 | 8.5281 | 0.036621
4656.2969 | 122.287 | -0.10529 | 122.2458 | -0.02739 | 0.015078 | 0.010703 | -0.0061588 | -0.0017645 | -0.010057 | -0.0021682 | -0.0084228 | 0.022103 | 0.042635 | -0.013569 | 0.01383 | 0.022469 | -0.0019163 | 8.3359 | 8.3817 | 8.075 | 8.2581 | 8.3542 | 8.2214 | 8.2718 | -0.054932 | 0.009155 | -0.041199 | -0.059509 | 0.018311 | 0 | 0.041199 | 8.1802 | -113.8641 | -113.9877 | 8.4595 | 8.3771 | 8.3267 | 0.19684 | 0.14649 | 0.064087 | -122.2366 | -122.3053 | 0.1236 | 0.14649 | 0.10529 | 0.082398 | 0.041199 | 0.27924 | 0.18311 | 0.05951 | -0.01831 | 0.3067 | 0.050354 | 8.4869 | 0.11444 | -114.1708 | -122.287 | 8.3633 | 0.045777 | 8.4412 | 0.050354
4658.0625 | 122.2733 | -0.1236 | 122.2595 | -0.0045011 | 0.015078 | 0.011984 | -0.007654 | 0.0040033 | -0.0098438 | -0.0015274 | -0.005371 | 0.020608 | 0.042208 | -0.015065 | 0.014257 | 0.024819 | -0.0029843 | 8.345 | 8.4 | 8.075 | 8.2626 | 8.3405 | 8.226 | 8.2489 | -0.10071 | 0.032043 | -0.059509 | -0.059509 | 0 | -0.027466 | 0.032043 | 8.1985 | -113.8596 | -113.9969 | 8.464 | 8.3725 | 8.3496 | 0.17395 | 0.15106 | 0.064087 | -122.2275 | -122.319 | 0.1236 | 0.15564 | 0.09613 | 0.091552 | 0.032043 | 0.2655 | 0.18768 | 0.059509 | 0 | 0.32501 | 0.091552 | 8.5236 | 0.15564 | -114.1846 | -122.319 | 8.3862 | 0.064087 | 8.4686 | 0.022888
4659.7656 | 122.4152 | -0.068665 | 122.2229 | 0.0031279 | 0.0086688 | 0.010062 | -0.0089358 | 0.0010125 | -0.00963 | 0.0006088 | -0.0084228 | 0.018258 | 0.041353 | -0.021046 | 0.010626 | 0.026528 | -0.0014891 | 8.432 | 8.3862 | 8.1024 | 8.4412 | 8.5785 | 8.4457 | 8.4869 | 0.10986 | -0.022888 | -0.013733 | 0.050354 | 0.20142 | 0.16479 | 0.15106 | 8.1711 | -113.8367 | -113.7817 | 8.6472 | 8.5556 | 8.5144 | 0.38452 | 0.34332 | 0.054932 | -122.2458 | -122.1725 | 0.27008 | 0.21973 | 0.23346 | 0.16479 | 0.17853 | 0.47607 | 0.33874 | 0.21515 | 0.064087 | 0.28381 | -0.009155 | 8.4549 | 0.045777 | -114.1205 | -122.2366 | 8.5098 | 0.11902 | 8.5007 | 0.17853
4661.5469 | 122.3328 | -0.082397 | 122.2549 | -0.01976 | 0.011873 | 0.0074982 | -0.0085086 | 0.0018671 | -0.010485 | -0.0045182 | -0.0023192 | 0.019113 | 0.042421 | -0.016987 | 0.010412 | 0.023537 | 0.00021995 | 8.4595 | 8.4045 | 8.1436 | 8.4549 | 8.5922 | 8.4549 | 8.4824 | 0.050354 | -0.004578 | -0.041199 | -0.022888 | 0.1236 | 0.082397 | 0.07782 | 8.226 | -113.8504 | -113.8 | 8.6746 | 8.5648 | 8.5373 | 0.33874 | 0.31128 | 0.041198 | -122.2595 | -122.2778 | 0.20599 | 0.16022 | 0.16479 | 0.11902 | 0.1236 | 0.44861 | 0.31128 | 0.16479 | 0.018311 | 0.26093 | 0.036621 | 8.4869 | 0.077819 | -114.1113 | -122.2961 | 8.5373 | 0.059509 | 8.5419 | 0.13275
4663.3125 | 122.4152 | -0.068665 | 122.2229 | -0.02739 | 0.016146 | 0.010703 | -0.005945 | -0.00026906 | -0.011125 | -0.0047318 | -0.0084228 | 0.019967 | 0.041567 | -0.014851 | 0.012762 | 0.023537 | -0.0042661 | 8.3862 | 8.2993 | 8.0475 | 8.3542 | 8.4778 | 8.2993 | 8.3496 | 0.10071 | -0.013733 | -0.018311 | 0.068665 | 0.16479 | 0.12817 | 0.15106 | 8.1161 | -113.9236 | -113.8687 | 8.5464 | 8.4183 | 8.3679 | 0.30212 | 0.25177 | 0.050354 | -122.2366 | -122.1542 | 0.23346 | 0.21973 | 0.19684 | 0.16937 | 0.14649 | 0.4303 | 0.3067 | 0.18311 | 0.086976 | 0.25177 | 0.004578 | 8.3679 | 0.054932 | -114.1754 | -122.2412 | 8.4229 | 0.13733 | 8.4549 | 0.16937
4665.0156 | 122.3831 | -0.064087 | 122.2046 | -0.012131 | 0.012514 | 0.011343 | -0.0087222 | -0.0041145 | -0.010271 | -0.0043046 | -0.0023192 | 0.018899 | 0.042635 | -0.019124 | 0.011694 | 0.025673 | -0.0040525 | 8.3633 | 8.3588 | 8.0658 | 8.3496 | 8.4686 | 8.345 | 8.3862 | 0.041199 | -0.009155 | -0.032043 | 0.013733 | 0.13733 | 0.11444 | 0.11902 | 8.1299 | -113.8458 | -113.855 | 8.5327 | 8.4503 | 8.4091 | 0.32043 | 0.27924 | 0.032044 | -122.2137 | -122.1909 | 0.20142 | 0.18311 | 0.17853 | 0.15106 | 0.14648 | 0.40283 | 0.28381 | 0.16937 | 0.045776 | 0.29297 | 0.022888 | 8.4229 | 0.054932 | -114.1388 | -122.2366 | 8.4137 | 0.07782 | 8.4274 | 0.10529
4666.7969 | 122.3053 | -0.11444 | 122.2733 | -0.012131 | 0.015078 | 0.013266 | -0.004877 | 0.00015814 | -0.0098438 | -0.0028092 | -0.011475 | 0.021463 | 0.042208 | -0.0065197 | 0.013189 | 0.022896 | -0.0023435 | 8.3084 | 8.3588 | 8.0429 | 8.226 | 8.3267 | 8.1848 | 8.2397 | -0.054932 | 0.018311 | -0.050354 | -0.068665 | 0.018311 | -0.018311 | 0.041199 | 8.1573 | -113.9145 | -114.0472 | 8.4412 | 8.3542 | 8.2993 | 0.19684 | 0.14191 | 0.064087 | -122.2549 | -122.3419 | 0.13275 | 0.15564 | 0.09613 | 0.091553 | 0.032043 | 0.28381 | 0.1831 | 0.068665 | -0.018311 | 0.31586 | 0.068665 | 8.4732 | 0.13275 | -114.2303 | -122.3236 | 8.3405 | 0.045776 | 8.4229 | 0.059509
4668.5625 | 122.3969 | -0.050354 | 122.2046 | -0.01976 | 0.014223 | 0.010916 | -0.0070132 | 0.0016535 | -0.010912 | -0.0025956 | -0.005371 | 0.018899 | 0.042208 | -0.020405 | 0.014471 | 0.023323 | -0.0014891 | 8.3267 | 8.2855 | 8.02 | 8.313 | 8.432 | 8.2809 | 8.3313 | 0.091553 | -0.018311 | -0.009155 | 0.054932 | 0.15564 | 0.1236 | 0.13733 | 8.0704 | -113.9191 | -113.8916 | 8.4824 | 8.3817 | 8.3313 | 0.31128 | 0.26092 | 0.041199 | -122.2229 | -122.1497 | 0.20599 | 0.18768 | 0.17395 | 0.14648 | 0.13275 | 0.41199 | 0.29297 | 0.16479 | 0.064087 | 0.2655 | -0.009156 | 8.3359 | 0.032043 | -114.1846 | -122.2137 | 8.3633 | 0.10529 | 8.3771 | 0.14191
4670.2656 | 122.3877 | -0.068665 | 122.2275 | -0.02739 | 0.014223 | 0.012839 | -0.0072268 | 0.0012261 | -0.0083484 | -0.0015274 | -0.005371 | 0.019326 | 0.04178 | -0.012501 | 0.016607 | 0.024178 | -0.0055479 | 8.3267 | 8.2489 | 8.0292 | 8.3313 | 8.4686 | 8.2901 | 8.3405 | 0.1236 | -0.013733 | -0.004578 | 0.059509 | 0.15564 | 0.11902 | 0.13733 | 8.0978 | -113.9786 | -113.8962 | 8.5373 | 8.4091 | 8.3588 | 0.31128 | 0.26093 | 0.064087 | -122.2412 | -122.168 | 0.22431 | 0.20599 | 0.18768 | 0.14191 | 0.1236 | 0.43945 | 0.30212 | 0.16022 | 0.064087 | 0.21973 | -0.009155 | 8.3176 | 0.054932 | -114.1983 | -122.2321 | 8.4 | 0.12817 | 8.3954 | 0.19226
4672.0469 | 122.3785 | -0.073242 | 122.2595 | -0.012131 | 0.011232 | 0.00878 | -0.0095766 | -0.0011237 | -0.0092028 | -0.0064408 | -0.0084228 | 0.019326 | 0.041353 | -0.016987 | 0.011907 | 0.024605 | -0.0034117 | 8.313 | 8.3405 | 8.0429 | 8.2855 | 8.4183 | 8.2718 | 8.3267 | 0.018311 | 0.009155 | -0.032043 | -0.018311 | 0.11444 | 0.073242 | 0.091553 | 8.1162 | -113.9191 | -113.974 | 8.4915 | 8.4 | 8.345 | 0.28381 | 0.22888 | 0.041199 | -122.2504 | -122.2778 | 0.18768 | 0.16479 | 0.14648 | 0.1236 | 0.10529 | 0.37537 | 0.24261 | 0.14648 | 0.013732 | 0.29755 | 0.041198 | 8.4137 | 0.082397 | -114.2166 | -122.2916 | 8.3588 | 0.054931 | 8.3862 | 0.091553
4673.8281 | 122.4106 | -0.064087 | 122.2595 | -0.012131 | 0.011873 | 0.010916 | -0.0097904 | -0.00026906 | -0.0098438 | -0.0013138 | -0.011475 | 0.020181 | 0.042849 | -0.013783 | 0.011907 | 0.023964 | -0.0029843 | 8.3267 | 8.3038 | 8.0383 | 8.3267 | 8.4595 | 8.3359 | 8.3771 | 0.064087 | -0.004578 | -0.027466 | 0.050354 | 0.16022 | 0.13733 | 0.13275 | 8.1024 | -113.9557 | -113.9328 | 8.5236 | 8.4412 | 8.4 | 0.33874 | 0.29755 | 0.036621 | -122.2641 | -122.2092 | 0.2243 | 0.19684 | 0.20142 | 0.16022 | 0.16479 | 0.42114 | 0.28839 | 0.18768 | 0.07782 | 0.2655 | 0.022888 | 8.3679 | 0.059509 | -114.2212 | -122.287 | 8.3908 | 0.11444 | 8.3908 | 0.12817
4675.5469 | 122.438 | -0.082397 | 122.2183 | -0.01976 | 0.011873 | 0.00878 | -0.006586 | -0.00069646 | -0.00963 | -0.0064408 | -0.005371 | 0.020181 | 0.042421 | -0.01421 | 0.010626 | 0.02311 | -0.0044797 | 8.3771 | 8.2993 | 8.0383 | 8.3725 | 8.5144 | 8.3679 | 8.4045 | 0.13733 | -0.027466 | -0.013733 | 0.064087 | 0.19684 | 0.16479 | 0.14648 | 8.1207 | -113.9191 | -113.8458 | 8.5968 | 8.4869 | 8.4503 | 0.36621 | 0.32959 | 0.068664 | -122.2458 | -122.1542 | 0.27924 | 0.22888 | 0.24719 | 0.16022 | 0.17853 | 0.47607 | 0.33417 | 0.21057 | 0.07782 | 0.26093 | -0.013733 | 8.3817 | 0.054931 | -114.18 | -122.2321 | 8.4549 | 0.14648 | 8.4595 | 0.21973
4677.3281 | 122.4472 | -0.054932 | 122.2458 | -0.02739 | 0.009737 | 0.0096344 | -0.010004 | -0.0045417 | -0.011125 | -0.0043046 | -0.0084228 | 0.021249 | 0.039217 | -0.0099377 | 0.011266 | 0.023323 | -0.0034117 | 8.345 | 8.2718 | 8.0383 | 8.3542 | 8.5052 | 8.3771 | 8.4 | 0.12817 | -0.009155 | 0 | 0.07782 | 0.19684 | 0.18768 | 0.14648 | 8.0933 | -113.974 | -113.8916 | 8.5602 | 8.4549 | 8.432 | 0.36163 | 0.33874 | 0.054932 | -122.2549 | -122.168 | 0.25177 | 0.20142 | 0.24261 | 0.14648 | 0.18768 | 0.46692 | 0.31586 | 0.19684 | 0.07782 | 0.23346 | -0.009155 | 8.3267 | 0.045777 | -114.2075 | -122.2458 | 8.4091 | 0.13275 | 8.4 | 0.18311
4679.1094 | 122.374 | -0.068665 | 122.2412 | -0.012131 | 0.010378 | 0.010275 | -0.007654 | 0.0016535 | -0.0094164 | -0.0038772 | -0.005371 | 0.018899 | 0.042635 | -0.018696 | 0.012334 | 0.022469 | 0.00021995 | 8.2397 | 8.1985 | 7.988 | 8.2443 | 8.3771 | 8.2169 | 8.2764 | 0.050354 | -0.013733 | -0.018311 | 0.013733 | 0.10986 | 0.086975 | 0.086975 | 8.0566 | -114.0427 | -113.9969 | 8.4457 | 8.345 | 8.2855 | 0.28839 | 0.22888 | 0.050354 | -122.2549 | -122.2275 | 0.17853 | 0.15564 | 0.15564 | 0.10529 | 0.10529 | 0.3891 | 0.25635 | 0.12817 | 0.032044 | 0.21057 | 0.004578 | 8.2672 | 0.054932 | -114.2532 | -122.2595 | 8.313 | 0.082398 | 8.3084 | 0.11902
4680.8281 | 122.4152 | -0.054932 | 122.2321 | -0.01976 | 0.012941 | 0.012412 | -0.0055178 | -0.0049689 | -0.0083484 | -0.005159 | -0.0084228 | 0.017617 | 0.039858 | -0.0099377 | 0.012975 | 0.024819 | -0.0072569 | 8.2626 | 8.1711 | 7.9651 | 8.2672 | 8.3817 | 8.2169 | 8.2581 | 0.11902 | -0.018311 | -0.013733 | 0.064087 | 0.15564 | 0.13275 | 0.13275 | 8.02 | -114.061 | -113.9648 | 8.4366 | 8.313 | 8.2718 | 0.29297 | 0.25177 | 0.041199 | -122.2504 | -122.168 | 0.21057 | 0.18768 | 0.18768 | 0.14648 | 0.14648 | 0.41657 | 0.30212 | 0.16937 | 0.07782 | 0.20599 | -0.004578 | 8.226 | 0.036621 | -114.267 | -122.2458 | 8.3221 | 0.11902 | 8.3176 | 0.17395
4682.6094 | 122.2961 | -0.12817 | 122.2687 | -0.0045011 | 0.015291 | 0.01113 | -0.0027408 | 0.0046441 | -0.0079212 | -0.0015274 | -0.0084228 | 0.023172 | 0.042208 | -0.019337 | 0.014684 | 0.022255 | -0.0066159 | 8.2809 | 8.2809 | 7.9926 | 8.2169 | 8.3038 | 8.1482 | 8.1985 | -0.032043 | 0.041199 | -0.036621 | -0.045776 | 0.027466 | -0.009155 | 0.050354 | 8.1207 | -113.9877 | -114.0518 | 8.432 | 8.3267 | 8.2764 | 0.20599 | 0.15564 | 0.091553 | -122.2275 | -122.3145 | 0.15564 | 0.17853 | 0.11902 | 0.086975 | 0.027466 | 0.31128 | 0.2243 | 0.064087 | -0.009155 | 0.28839 | 0.07782 | 8.4091 | 0.16937 | -114.2761 | -122.3053 | 8.345 | 0.082398 | 8.4091 | 0.096131
4684.3906 | 122.3465 | -0.11444 | 122.2595 | -0.02739 | 0.013369 | 0.011557 | -0.004877 | 0.0012261 | -0.0077074 | -0.0011002 | -0.005371 | 0.021463 | 0.043703 | -0.013569 | 0.014257 | 0.022255 | -0.0044797 | 8.3084 | 8.2947 | 8.02 | 8.2535 | 8.3633 | 8.2214 | 8.2306 | 0.022888 | 0.036621 | -0.041199 | -0.009155 | 0.09613 | 0.045776 | 0.082397 | 8.1345 | -113.9648 | -114.006 | 8.4778 | 8.345 | 8.3359 | 0.21057 | 0.20142 | 0.073242 | -122.2229 | -122.2687 | 0.21057 | 0.19684 | 0.16022 | 0.1236 | 0.086975 | 0.34332 | 0.23346 | 0.13733 | 0.032044 | 0.27466 | 0.07782 | 8.4091 | 0.15106 | -114.2395 | -122.3007 | 8.3679 | 0.10529 | 8.4229 | 0.13733
4686.1719 | 122.2778 | -0.10529 | 122.2549 | -0.012131 | 0.01465 | 0.01113 | -0.006586 | 0.0063531 | -0.0081348 | -0.0038772 | -0.0084228 | 0.022103 | 0.044558 | -0.0090833 | 0.015752 | 0.023537 | -0.0059751 | 8.2397 | 8.2581 | 7.9834 | 8.1573 | 8.2718 | 8.1161 | 8.139 | -0.041199 | 0.036621 | -0.054932 | -0.064087 | 0.018311 | -0.018311 | 0.032043 | 8.0887 | -113.9969 | -114.0976 | 8.3771 | 8.2443 | 8.2214 | 0.15564 | 0.13275 | 0.050354 | -122.2183 | -122.319 | 0.1236 | 0.13733 | 0.086975 | 0.086975 | 0.036621 | 0.28839 | 0.17395 | 0.073243 | -0.009155 | 0.27466 | 0.091553 | 8.3633 | 0.14191 | -114.2715 | -122.3099 | 8.2626 | 0.041199 | 8.345 | 0.064087
4687.9531 | 122.4289 | -0.068665 | 122.2458 | -0.012131 | 0.012941 | 0.010489 | -0.0072268 | 0.0014397 | -0.011766 | -0.0053726 | -0.0084228 | 0.018472 | 0.041994 | -0.025319 | 0.014043 | 0.024819 | -0.00084805 | 8.2443 | 8.2077 | 7.9788 | 8.2443 | 8.3771 | 8.2443 | 8.2764 | 0.064087 | 0 | -0.054932 | 0.036621 | 0.16479 | 0.14648 | 0.11902 | 8.0475 | -114.0381 | -114.0015 | 8.4457 | 8.345 | 8.313 | 0.29755 | 0.2655 | 0.013733 | -122.2458 | -122.2092 | 0.23346 | 0.18768 | 0.21515 | 0.17395 | 0.20142 | 0.39825 | 0.2655 | 0.21973 | 0.091553 | 0.22888 | 0.054932 | 8.2764 | 0.068665 | -114.267 | -122.3007 | 8.313 | 0.10529 | 8.313 | 0.13275
4689.6719 | 122.3007 | -0.10529 | 122.287 | -0.01976 | 0.012941 | 0.0089936 | -0.0078676 | -0.0013373 | -0.0098438 | -0.0030228 | -0.005371 | 0.019754 | 0.042849 | -0.0090833 | 0.014043 | 0.023964 | -0.0072569 | 8.2764 | 8.3496 | 7.9971 | 8.2077 | 8.3405 | 8.2031 | 8.2214 | -0.059509 | 0.054932 | -0.054932 | -0.064087 | 0.032043 | 0.004578 | 0.045776 | 8.1024 | -113.9374 | -114.0793 | 8.4457 | 8.3267 | 8.3084 | 0.22431 | 0.20599 | 0.050354 | -122.2321 | -122.3511 | 0.13733 | 0.15106 | 0.10986 | 0.10071 | 0.05951 | 0.34332 | 0.21057 | 0.086975 | -0.009155 | 0.35248 | 0.10986 | 8.4549 | 0.16022 | -114.2899 | -122.3419 | 8.313 | 0.041199 | 8.3817 | 0.045777
4691.375 | 122.4243 | -0.064087 | 122.2504 | 0.0031279 | 0.0095234 | 0.010916 | -0.010431 | -5.5462e-05 | -0.00963 | -0.00345 | -0.0084228 | 0.019113 | 0.042635 | -0.017415 | 0.012975 | 0.023537 | -0.0036253 | 8.2901 | 8.2306 | 7.9926 | 8.2947 | 8.4549 | 8.2993 | 8.3221 | 0.10529 | -0.018311 | -0.013733 | 0.045776 | 0.1831 | 0.16022 | 0.1236 | 8.0566 | -114.0198 | -113.9557 | 8.519 | 8.3862 | 8.3633 | 0.32959 | 0.3067 | 0.050354 | -122.2687 | -122.2046 | 0.24719 | 0.18768 | 0.2243 | 0.13733 | 0.17395 | 0.46234 | 0.30212 | 0.19684 | 0.059509 | 0.23804 | -0.004578 | 8.2947 | 0.045776 | -114.2578 | -122.2641 | 8.3588 | 0.10986 | 8.3542 | 0.16937
4693.1562 | 122.3145 | -0.10071 | 122.2778 | -0.0045011 | 0.0123 | 0.009848 | -0.007654 | -5.5462e-05 | -0.0074938 | -0.0057998 | -0.0084228 | 0.021035 | 0.042421 | -0.013142 | 0.011266 | 0.022896 | -0.0061887 | 8.2123 | 8.2581 | 7.9742 | 8.1665 | 8.3038 | 8.1665 | 8.1848 | -0.054932 | 0.032043 | -0.032043 | -0.082397 | 0.050354 | 0.022888 | 0.018311 | 8.075 | -114.0198 | -114.1113 | 8.4045 | 8.2855 | 8.2672 | 0.21057 | 0.19226 | 0.068665 | -122.2458 | -122.3602 | 0.15106 | 0.11902 | 0.1236 | 0.050354 | 0.054931 | 0.32959 | 0.19226 | 0.082397 | -0.050354 | 0.28381 | 0.064086 | 8.3588 | 0.13275 | -114.3036 | -122.3099 | 8.2672 | 0.018311 | 8.313 | 0.045776
4694.875 | 122.4335 | -0.054932 | 122.2412 | -0.01976 | 0.0123 | 0.010062 | -0.0089358 | -0.00048286 | -0.0098438 | -0.0021682 | -0.0084228 | 0.018686 | 0.043062 | -0.018055 | 0.012334 | 0.023751 | -0.0019163 | 8.2535 | 8.1757 | 7.9514 | 8.2672 | 8.4045 | 8.2626 | 8.3084 | 0.14648 | -0.009155 | -0.022888 | 0.054932 | 0.18768 | 0.1831 | 0.15106 | 8.0063 | -114.0656 | -113.974 | 8.4595 | 8.3633 | 8.3176 | 0.35706 | 0.31128 | 0.032044 | -122.2504 | -122.1863 | 0.24261 | 0.20599 | 0.23804 | 0.17395 | 0.20599 | 0.45319 | 0.31586 | 0.21057 | 0.07782 | 0.2243 | 0.013733 | 8.2306 | 0.045777 | -114.2899 | -122.2641 | 8.3221 | 0.10986 | 8.3084 | 0.20142
4696.6406 | 122.4014 | -0.10071 | 122.2366 | -0.01976 | 0.012728 | 0.00878 | -0.0087222 | 0.00037174 | -0.0074938 | -0.0047318 | -0.0084228 | 0.019113 | 0.041994 | -0.014851 | 0.012548 | 0.023751 | -0.0040525 | 8.1573 | 8.139 | 7.9056 | 8.1345 | 8.2489 | 8.1116 | 8.1528 | 0.032043 | -0.004578 | -0.036621 | 0.004578 | 0.11902 | 0.091553 | 0.10071 | 8.0063 | -114.0976 | -114.1022 | 8.3496 | 8.2535 | 8.2123 | 0.24719 | 0.20599 | 0.064087 | -122.2412 | -122.2321 | 0.21973 | 0.20142 | 0.19226 | 0.13733 | 0.12817 | 0.34332 | 0.22888 | 0.15564 | 0.041199 | 0.23346 | 0.032043 | 8.2397 | 0.09613 | -114.3311 | -122.2733 | 8.2352 | 0.10529 | 8.2581 | 0.13275
4698.4062 | 122.4243 | -0.068665 | 122.2504 | -0.02739 | 0.011873 | 0.011771 | -0.0078676 | 0.0025079 | -0.011766 | -0.0053726 | -0.0084228 | 0.018899 | 0.042849 | -0.019337 | 0.014471 | 0.022042 | -0.0044797 | 8.2443 | 8.1619 | 7.9514 | 8.2489 | 8.3771 | 8.226 | 8.2443 | 0.10529 | 0 | -0.018311 | 0.041199 | 0.16479 | 0.16022 | 0.13275 | 8.02 | -114.0884 | -114.0015 | 8.4457 | 8.313 | 8.2947 | 0.29297 | 0.27466 | 0.050354 | -122.2504 | -122.2092 | 0.23346 | 0.20142 | 0.22888 | 0.15106 | 0.17853 | 0.42572 | 0.29755 | 0.18311 | 0.05951 | 0.21057 | 0.018311 | 8.2306 | 0.068665 | -114.299 | -122.2687 | 8.3176 | 0.10986 | 8.313 | 0.17395
4700.1094 | 122.3465 | -0.10529 | 122.2778 | -0.012131 | 0.0123 | 0.010275 | -0.0063724 | 0.00015814 | -0.0092028 | -0.0021682 | -0.005371 | 0.020822 | 0.041994 | -0.0073743 | 0.015325 | 0.02076 | -0.0072569 | 8.1802 | 8.226 | 7.9285 | 8.1345 | 8.2397 | 8.1161 | 8.1482 | -0.032043 | 0.036621 | -0.045776 | -0.036621 | 0.082397 | 0.036621 | 0.07782 | 8.0338 | -114.0518 | -114.1434 | 8.345 | 8.2535 | 8.2214 | 0.21973 | 0.18768 | 0.05951 | -122.2412 | -122.3145 | 0.18768 | 0.18311 | 0.14191 | 0.1236 | 0.082397 | 0.31128 | 0.20599 | 0.12817 | 0.009155 | 0.29755 | 0.082397 | 8.3313 | 0.14191 | -114.3494 | -122.3236 | 8.2397 | 0.068665 | 8.2855 | 0.073243
4701.875 | 122.2961 | -0.11902 | 122.287 | -0.012131 | 0.0099506 | 0.0096344 | -0.007654 | -0.00091006 | -0.010485 | -0.0015274 | -0.0084228 | 0.019754 | 0.04114 | -0.015492 | 0.012762 | 0.021614 | -0.0049069 | 8.1436 | 8.1665 | 7.9285 | 8.107 | 8.2306 | 8.0887 | 8.1299 | -0.022888 | 0.022888 | -0.036621 | -0.07782 | 0.027466 | 0.027466 | 0.027466 | 8.0475 | -114.1205 | -114.18 | 8.3496 | 8.2489 | 8.2077 | 0.20142 | 0.16022 | 0.082398 | -122.2641 | -122.3648 | 0.14649 | 0.14649 | 0.14649 | 0.064087 | 0.064087 | 0.30212 | 0.17853 | 0.064087 | -0.041199 | 0.23804 | 0.059509 | 8.2855 | 0.14191 | -114.3585 | -122.3236 | 8.226 | 0.041199 | 8.2626 | 0.096131
4703.6406 | 122.406 | -0.068665 | 122.2458 | -0.02739 | 0.013369 | 0.0096344 | -0.0097904 | -0.0011237 | -0.0077074 | -0.0057998 | -0.005371 | 0.018258 | 0.041994 | -0.018696 | 0.01148 | 0.024605 | -0.0025571 | 8.107 | 8.0887 | 7.8552 | 8.0887 | 8.1985 | 8.0658 | 8.1116 | 0.032043 | 0 | -0.036621 | 0.018311 | 0.12817 | 0.11902 | 0.10986 | 7.9239 | -114.1571 | -114.1571 | 8.2672 | 8.1802 | 8.1345 | 0.25635 | 0.21057 | 0.032044 | -122.2458 | -122.2275 | 0.19684 | 0.17853 | 0.18768 | 0.14648 | 0.15564 | 0.34332 | 0.23346 | 0.1648 | 0.054932 | 0.23346 | 0.036621 | 8.1573 | 0.068665 | -114.3906 | -122.2824 | 8.1573 | 0.086976 | 8.1757 | 0.10071
4705.3438 | 122.4014 | -0.064087 | 122.2824 | -0.01976 | 0.012087 | 0.010703 | -0.007654 | -0.0041145 | -0.0094164 | -0.0028092 | -0.0084228 | 0.020822 | 0.042635 | -0.015065 | 0.012548 | 0.023751 | -0.0053343 | 8.0795 | 8.0246 | 7.8415 | 8.0704 | 8.2123 | 8.02 | 8.0704 | 0.082397 | -0.022888 | -0.022888 | 0.022888 | 0.12817 | 0.10071 | 0.10986 | 7.9056 | -114.2578 | -114.212 | 8.2764 | 8.1345 | 8.0841 | 0.22888 | 0.17853 | 0.041199 | -122.3053 | -122.2595 | 0.19226 | 0.17395 | 0.1648 | 0.13275 | 0.1236 | 0.37079 | 0.22888 | 0.15106 | 0.045776 | 0.18311 | 0 | 8.0887 | 0.041199 | -114.4409 | -122.3053 | 8.1345 | 0.086975 | 8.1436 | 0.14648
4707.125 | 122.438 | -0.045776 | 122.2549 | -0.01976 | 0.014437 | 0.010062 | -0.007654 | -0.0019781 | -0.010057 | -0.0032364 | -0.005371 | 0.021035 | 0.040071 | -0.01186 | 0.013616 | 0.024605 | -0.0025571 | 8.075 | 7.9926 | 7.7866 | 8.0566 | 8.1802 | 8.0017 | 8.0566 | 0.11444 | -0.018311 | -0.009155 | 0.064087 | 0.16479 | 0.1236 | 0.16022 | 7.8323 | -114.2624 | -114.1983 | 8.226 | 8.1024 | 8.0475 | 0.27008 | 0.21515 | 0.036621 | -122.2733 | -122.1909 | 0.21057 | 0.20599 | 0.16937 | 0.16937 | 0.13275 | 0.39368 | 0.27008 | 0.17395 | 0.073242 | 0.20599 | -0.009156 | 8.0383 | 0.027465 | -114.4684 | -122.2641 | 8.1024 | 0.10986 | 8.1207 | 0.16022
4708.8438 | 122.3145 | -0.11902 | 122.2916 | -0.01976 | 0.014009 | 0.010916 | -0.0067996 | 0.0054987 | -0.0092028 | -0.0032364 | -0.005371 | 0.022531 | 0.042421 | -0.015278 | 0.013189 | 0.022896 | -0.0027707 | 8.0063 | 8.0704 | 7.7911 | 7.9193 | 8.02 | 7.8781 | 7.9422 | -0.059509 | 0.041199 | -0.064087 | -0.068665 | 0.009155 | -0.022888 | 0.050354 | 7.9102 | -114.2212 | -114.3723 | 8.139 | 8.0612 | 7.9971 | 0.15106 | 0.086975 | 0.054932 | -122.2504 | -122.3602 | 0.12817 | 0.16937 | 0.096131 | 0.11444 | 0.041199 | 0.22888 | 0.12817 | 0.073242 | -0.004578 | 0.27924 | 0.10529 | 8.1894 | 0.16022 | -114.5004 | -122.3557 | 8.0383 | 0.050354 | 8.1253 | 0.05951
4710.625 | 122.3648 | -0.10071 | 122.2916 | -0.012131 | 0.013796 | 0.0089936 | -0.0063724 | 0.0035761 | -0.0098438 | -0.005159 | -0.005371 | 0.021676 | 0.043703 | -0.015706 | 0.015325 | 0.023964 | -0.0034117 | 8.107 | 8.1024 | 7.8552 | 8.0566 | 8.1665 | 8.0246 | 8.0383 | 0.022888 | 0.027466 | -0.041199 | -0.009155 | 0.10071 | 0.045776 | 0.082397 | 7.9559 | -114.1891 | -114.2349 | 8.2672 | 8.139 | 8.1253 | 0.18311 | 0.16937 | 0.059509 | -122.2641 | -122.3007 | 0.20142 | 0.18311 | 0.14648 | 0.1236 | 0.086975 | 0.31128 | 0.20142 | 0.14191 | 0.032044 | 0.24719 | 0.068665 | 8.2031 | 0.12817 | -114.4363 | -122.3328 | 8.1573 | 0.091553 | 8.2077 | 0.1236
4712.3438 | 122.3511 | -0.10529 | 122.3145 | -0.012131 | 0.010805 | 0.0074982 | -0.0063724 | -0.00048286 | -0.010698 | -0.0021682 | -0.011475 | 0.02189 | 0.042849 | -0.0080151 | 0.015966 | 0.02311 | -0.0034117 | 8.075 | 8.1299 | 7.8415 | 8.0154 | 8.1207 | 8.0109 | 8.0338 | -0.068665 | 0.013733 | -0.054932 | -0.045776 | 0.054932 | 0.036621 | 0.050354 | 7.9468 | -114.1846 | -114.299 | 8.226 | 8.139 | 8.1161 | 0.19226 | 0.16937 | 0.050354 | -122.3007 | -122.3602 | 0.16022 | 0.15564 | 0.14191 | 0.10529 | 0.091553 | 0.27924 | 0.17395 | 0.10986 | 0.009156 | 0.28839 | 0.068665 | 8.2352 | 0.11902 | -114.473 | -122.3694 | 8.1207 | 0.05951 | 8.1802 | 0.036621
4714.1094 | 122.3328 | -0.10071 | 122.3053 | -0.01976 | 0.015932 | 0.01113 | -0.0057314 | 0.0087029 | -0.00963 | -0.0028092 | -0.005371 | 0.020395 | 0.042635 | -0.012715 | 0.014898 | 0.024178 | -0.0040525 | 7.9605 | 8.0017 | 7.7591 | 7.8735 | 7.9926 | 7.8552 | 7.8827 | -0.068665 | 0.004578 | -0.054932 | -0.07782 | 0.041199 | -0.013733 | 0.045776 | 7.8598 | -114.3036 | -114.4318 | 8.0933 | 7.9834 | 7.9559 | 0.1236 | 0.096131 | 0.045776 | -122.3007 | -122.3831 | 0.14191 | 0.14648 | 0.086975 | 0.10071 | 0.041199 | 0.23346 | 0.11444 | 0.096131 | -0.022888 | 0.24261 | 0.05951 | 8.1024 | 0.10529 | -114.5462 | -122.3602 | 7.9742 | 0.022888 | 8.0612 | 0.032043
4715.875 | 122.4152 | -0.073242 | 122.2961 | -0.01976 | 0.011232 | 0.010703 | -0.009363 | 0.0031487 | -0.012834 | -0.0060134 | -0.005371 | 0.018899 | 0.043276 | -0.020833 | 0.011694 | 0.024819 | -0.0061887 | 8.0017 | 8.0017 | 7.7683 | 7.9742 | 8.1024 | 7.9834 | 8.0246 | 0.018311 | 0.004578 | -0.036621 | 0 | 0.12817 | 0.10071 | 0.10071 | 7.8415 | -114.2944 | -114.3219 | 8.1757 | 8.0978 | 8.0566 | 0.25635 | 0.21515 | 0.036621 | -122.2916 | -122.2961 | 0.20142 | 0.17395 | 0.17395 | 0.13733 | 0.13733 | 0.33417 | 0.20599 | 0.1648 | 0.036621 | 0.23346 | 0.041199 | 8.075 | 0.07782 | -114.5279 | -122.3328 | 8.0475 | 0.073242 | 8.075 | 0.091553
4717.6562 | 122.319 | -0.11444 | 122.2916 | -0.01976 | 0.014864 | 0.012625 | -0.0070132 | 0.0029351 | -0.0087756 | -0.00345 | -0.005371 | 0.022958 | 0.042421 | -0.020405 | 0.012121 | 0.023964 | -0.0072569 | 8.0109 | 8.0246 | 7.7728 | 7.9468 | 8.0154 | 7.8827 | 7.9056 | -0.022888 | 0.041199 | -0.036621 | -0.064087 | 0.032043 | -0.013733 | 0.022888 | 7.8873 | -114.267 | -114.3448 | 8.1299 | 8.02 | 7.9971 | 0.13275 | 0.10986 | 0.07782 | -122.2504 | -122.3557 | 0.14648 | 0.13733 | 0.10071 | 0.059509 | 0.022888 | 0.24261 | 0.17395 | 0.068664 | -0.027466 | 0.25177 | 0.07782 | 8.139 | 0.15564 | -114.5187 | -122.3282 | 8.0612 | 0.050354 | 8.1253 | 0.091553
4719.375 | 122.3785 | -0.10529 | 122.3145 | -0.01976 | 0.014437 | 0.010062 | -0.0070132 | -0.0021919 | -0.00963 | -0.0021682 | -0.0084228 | 0.022317 | 0.041353 | -0.01656 | 0.012762 | 0.025032 | -0.0010617 | 8.0246 | 8.0841 | 7.814 | 7.9697 | 8.0887 | 7.9788 | 7.9834 | -0.041199 | 0.027466 | -0.041199 | -0.032043 | 0.073242 | 0.050354 | 0.073242 | 7.9193 | -114.2303 | -114.3448 | 8.194 | 8.0887 | 8.0841 | 0.16937 | 0.16479 | 0.064087 | -122.287 | -122.3465 | 0.17853 | 0.17853 | 0.15564 | 0.11444 | 0.091553 | 0.27466 | 0.15564 | 0.11444 | 0.009156 | 0.27008 | 0.068665 | 8.1894 | 0.13275 | -114.5004 | -122.3557 | 8.075 | 0.073243 | 8.1299 | 0.064087
4721.1406 | 122.4426 | -0.068665 | 122.2961 | -0.012131 | 0.010591 | 0.010703 | -0.0091494 | -0.00069646 | -0.011766 | -0.0030228 | -0.0084228 | 0.019754 | 0.042635 | -0.014424 | 0.012121 | 0.023751 | -0.0029843 | 8.0612 | 7.988 | 7.782 | 8.0612 | 8.2169 | 8.0795 | 8.0933 | 0.10071 | -0.004578 | -0.022888 | 0.041199 | 0.19684 | 0.16937 | 0.13733 | 7.8506 | -114.3082 | -114.2349 | 8.2855 | 8.1619 | 8.1482 | 0.31128 | 0.29755 | 0.045777 | -122.3007 | -122.2549 | 0.2655 | 0.20599 | 0.23804 | 0.16022 | 0.19226 | 0.43488 | 0.27924 | 0.21973 | 0.064087 | 0.20599 | 0.01831 | 8.0566 | 0.064087 | -114.5142 | -122.319 | 8.1299 | 0.10986 | 8.1299 | 0.16937
4722.9219 | 122.4518 | -0.064087 | 122.2824 | -0.0045011 | 0.0123 | 0.0094208 | -0.010858 | 0.00015814 | -0.011553 | -0.0047318 | -0.0084228 | 0.020395 | 0.041567 | -0.018269 | 0.01148 | 0.022896 | -0.0021299 | 8.0566 | 7.9834 | 7.782 | 8.0658 | 8.1848 | 8.0521 | 8.0704 | 0.091553 | -0.009155 | -0.013733 | 0.045776 | 0.17853 | 0.14191 | 0.13733 | 7.8461 | -114.299 | -114.2166 | 8.2489 | 8.1345 | 8.1162 | 0.28839 | 0.27008 | 0.050354 | -122.2916 | -122.2366 | 0.24261 | 0.20142 | 0.20599 | 0.15106 | 0.15564 | 0.40283 | 0.28381 | 0.19226 | 0.059509 | 0.20142 | 0.004578 | 8.0475 | 0.054932 | -114.5004 | -122.2961 | 8.1299 | 0.10986 | 8.1207 | 0.15564
4724.6406 | 122.3419 | -0.11444 | 122.3099 | -0.01976 | 0.011446 | 0.010275 | -0.0055178 | -0.0013373 | -0.0094164 | -0.0047318 | -0.0084228 | 0.022531 | 0.045626 | -0.017628 | 0.014471 | 0.022683 | -0.0021299 | 7.9697 | 8.0383 | 7.7637 | 7.9285 | 8.0612 | 7.9376 | 7.9514 | -0.054932 | 0.032043 | -0.059509 | -0.07782 | 0.041199 | 0.013733 | 0.022888 | 7.8781 | -114.2715 | -114.3814 | 8.1757 | 8.0658 | 8.0521 | 0.18768 | 0.17395 | 0.054932 | -122.2778 | -122.3877 | 0.15564 | 0.13733 | 0.12817 | 0.082397 | 0.073242 | 0.29755 | 0.1648 | 0.10071 | -0.018311 | 0.27466 | 0.091552 | 8.1528 | 0.14648 | -114.5462 | -122.3694 | 8.0429 | 0.036621 | 8.0841 | 0.059509
4726.4062 | 122.4655 | -0.068665 | 122.2733 | -0.01976 | 0.0084552 | 0.00878 | -0.0080814 | -0.0011237 | -0.012194 | -0.002382 | -0.005371 | 0.019754 | 0.043062 | -0.020833 | 0.010626 | 0.023537 | -0.0010617 | 7.9742 | 7.9193 | 7.7225 | 8.0063 | 8.1253 | 8.0017 | 8.0109 | 0.10986 | -0.013733 | -0.009155 | 0.054932 | 0.19684 | 0.17395 | 0.14648 | 7.7911 | -114.3539 | -114.267 | 8.194 | 8.0795 | 8.0704 | 0.28839 | 0.27924 | 0.05951 | -122.287 | -122.2183 | 0.2655 | 0.21515 | 0.24261 | 0.15564 | 0.1831 | 0.40283 | 0.28381 | 0.20599 | 0.064087 | 0.19684 | -0.004578 | 7.988 | 0.054932 | -114.5508 | -122.2824 | 8.075 | 0.1236 | 8.0429 | 0.17853
4728.1875 | 122.3465 | -0.10986 | 122.287 | -0.02739 | 0.0123 | 0.0077118 | -0.0078676 | 0.0014397 | -0.010485 | -0.002382 | -0.0084228 | 0.023599 | 0.04413 | -0.01122 | 0.013403 | 0.021828 | -0.00084805 | 7.9742 | 8.0292 | 7.7454 | 7.9102 | 8.0154 | 7.9102 | 7.9102 | -0.059509 | 0.045776 | -0.059509 | -0.068665 | 0.041199 | 0.022888 | 0.041199 | 7.8552 | -114.2578 | -114.3768 | 8.1253 | 8.02 | 8.02 | 0.16479 | 0.16479 | 0.050354 | -122.2412 | -122.3557 | 0.15106 | 0.15106 | 0.13275 | 0.10071 | 0.082397 | 0.27008 | 0.16479 | 0.10071 | -0.009156 | 0.28381 | 0.10528 | 8.139 | 0.15564 | -114.5416 | -122.3465 | 8.02 | 0.041198 | 8.0841 | 0.050354
4729.9062 | 122.4426 | -0.064087 | 122.2778 | -0.01976 | 0.009096 | 0.010062 | -0.0087222 | -0.00048286 | -0.0089892 | -0.00345 | -0.0084228 | 0.018686 | 0.041353 | -0.018696 | 0.013403 | 0.024605 | -0.00020725 | 8.0063 | 7.9422 | 7.7454 | 8.0109 | 8.1345 | 7.9971 | 8.0338 | 0.091553 | -0.009155 | -0.018311 | 0.036621 | 0.15564 | 0.13733 | 0.12817 | 7.8094 | -114.3356 | -114.267 | 8.1985 | 8.0978 | 8.0612 | 0.28839 | 0.25177 | 0.045776 | -122.287 | -122.2412 | 0.21973 | 0.19226 | 0.20142 | 0.14649 | 0.15564 | 0.3891 | 0.2655 | 0.17395 | 0.054932 | 0.19684 | 0.009156 | 8.0063 | 0.054932 | -114.5325 | -122.2961 | 8.075 | 0.10071 | 8.0704 | 0.15564
4731.6719 | 122.4152 | -0.086975 | 122.287 | -0.01976 | 0.01166 | 0.011343 | -0.0063724 | 0.0016535 | -0.0074938 | -0.0040908 | -0.0084228 | 0.017831 | 0.041567 | -0.014851 | 0.012121 | 0.022255 | -0.0049069 | 7.869 | 7.8644 | 7.6721 | 7.8735 | 7.9834 | 7.8506 | 7.9056 | 0.013733 | -0.013733 | -0.027466 | 0 | 0.10529 | 0.073242 | 0.091553 | 7.7591 | -114.4226 | -114.4135 | 8.0704 | 7.9926 | 7.9376 | 0.23346 | 0.17853 | 0.059509 | -122.3007 | -122.287 | 0.19226 | 0.17853 | 0.16022 | 0.11902 | 0.10071 | 0.31128 | 0.20142 | 0.13275 | 0.027466 | 0.19226 | 0.013733 | 7.9514 | 0.073242 | -114.6149 | -122.3145 | 7.9605 | 0.086975 | 7.9559 | 0.10071
4733.4375 | 122.4197 | -0.07782 | 122.319 | -0.012131 | 0.015078 | 0.0094208 | -0.0061588 | -0.00091006 | -0.011125 | -0.0040908 | -0.0084228 | 0.022103 | 0.043276 | -0.01186 | 0.012121 | 0.023964 | -0.0042661 | 7.8461 | 7.869 | 7.6309 | 7.7866 | 7.8918 | 7.7362 | 7.7957 | 0.004578 | 0.032043 | -0.036621 | 0.018311 | 0.09613 | 0.059509 | 0.09613 | 7.7087 | -114.4501 | -114.5325 | 7.9697 | 7.8735 | 7.814 | 0.1648 | 0.10529 | 0.041199 | -122.287 | -122.3007 | 0.17395 | 0.17395 | 0.13733 | 0.13275 | 0.09613 | 0.26093 | 0.15564 | 0.13275 | 0.054932 | 0.23804 | 0.068664 | 7.9468 | 0.10986 | -114.6881 | -122.3557 | 7.8644 | 0.096131 | 7.9239 | 0.082398
4735.2031 | 122.3099 | -0.10071 | 122.3282 | -0.01976 | 0.016787 | 0.011343 | -0.0063724 | -5.5462e-05 | -0.0072802 | -0.0019546 | -0.011475 | 0.022744 | 0.043276 | -0.0092969 | 0.013616 | 0.024391 | -0.0014891 | 7.8415 | 7.9056 | 7.6538 | 7.7774 | 7.8552 | 7.7133 | 7.7499 | -0.086975 | 0.018311 | -0.050354 | -0.059509 | 0.022888 | -0.027466 | 0.036621 | 7.7545 | -114.4226 | -114.5508 | 7.9559 | 7.8506 | 7.814 | 0.09613 | 0.059509 | 0.050354 | -122.3099 | -122.3877 | 0.1236 | 0.13733 | 0.073242 | 0.086975 | 0.022888 | 0.20142 | 0.1236 | 0.073242 | -0.009155 | 0.25177 | 0.068665 | 8.0063 | 0.11902 | -114.6744 | -122.3785 | 7.8781 | 0.041199 | 7.9422 | 0.013733
4736.9688 | 122.4747 | -0.054932 | 122.2824 | -0.0045011 | 0.014223 | 0.009848 | -0.0067996 | 0.0040033 | -0.0092028 | -0.0043046 | -0.0084228 | 0.020395 | 0.043062 | -0.018483 | 0.01383 | 0.02311 | -0.0040525 | 7.869 | 7.7957 | 7.6218 | 7.8461 | 7.9651 | 7.814 | 7.8552 | 0.10071 | -0.018311 | 0.009155 | 0.07782 | 0.16479 | 0.10986 | 0.15564 | 7.6767 | -114.4867 | -114.4363 | 8.02 | 7.9102 | 7.869 | 0.23346 | 0.19226 | 0.064087 | -122.3007 | -122.2046 | 0.21973 | 0.21057 | 0.16479 | 0.14649 | 0.10071 | 0.34332 | 0.2243 | 0.15564 | 0.068665 | 0.17395 | -0.027466 | 7.8506 | 0.036621 | -114.6606 | -122.2733 | 7.901 | 0.13275 | 7.9239 | 0.15564
4738.75 | 122.4609 | -0.068665 | 122.2778 | -0.012131 | 0.011232 | 0.009848 | -0.0095766 | 0.0027215 | -0.010912 | -0.00345 | -0.005371 | 0.019754 | 0.042421 | -0.013569 | 0.010412 | 0.023537 | -0.0027707 | 7.8506 | 7.8415 | 7.6538 | 7.869 | 8.0017 | 7.8781 | 7.9147 | 0.07782 | 0.004578 | -0.013733 | 0.027466 | 0.15106 | 0.13275 | 0.1236 | 7.7225 | -114.4363 | -114.4089 | 8.0704 | 7.9834 | 7.9468 | 0.26093 | 0.2243 | 0.054932 | -122.2733 | -122.2504 | 0.21973 | 0.19226 | 0.20142 | 0.13733 | 0.14648 | 0.3479 | 0.21515 | 0.16479 | 0.041199 | 0.18768 | 0.018311 | 7.9102 | 0.073243 | -114.624 | -122.2916 | 7.9376 | 0.096131 | 7.9193 | 0.14649
4740.4531 | 122.4747 | -0.059509 | 122.2824 | -0.0045011 | 0.009737 | 0.010916 | -0.0087222 | -0.0021919 | -0.0074938 | -0.0032364 | -0.0084228 | 0.018899 | 0.042208 | -0.014424 | 0.010412 | 0.02311 | 0.00043375 | 7.9102 | 7.8827 | 7.6675 | 7.9193 | 8.0704 | 7.9239 | 7.9605 | 0.12817 | -0.004578 | -0.009155 | 0.073242 | 0.20142 | 0.16479 | 0.15106 | 7.7271 | -114.3997 | -114.3631 | 8.1299 | 8.02 | 7.9834 | 0.29297 | 0.25635 | 0.050354 | -122.287 | -122.2092 | 0.26093 | 0.21057 | 0.2243 | 0.16022 | 0.17395 | 0.40283 | 0.25177 | 0.21057 | 0.082397 | 0.21515 | 0.004577 | 7.9422 | 0.054931 | -114.6149 | -122.2916 | 7.9788 | 0.13275 | 7.9697 | 0.18768
4742.2188 | 122.4197 | -0.082397 | 122.2961 | -0.012131 | 0.012514 | 0.010489 | -0.0063724 | 0.0016535 | -0.00963 | -0.0021682 | -0.005371 | 0.019326 | 0.041353 | -0.015919 | 0.010839 | 0.024178 | -0.0029843 | 7.8186 | 7.8186 | 7.6218 | 7.8186 | 7.9376 | 7.7911 | 7.8415 | 0.027466 | -0.013733 | -0.032043 | -0.004578 | 0.091553 | 0.082397 | 0.09613 | 7.7042 | -114.4775 | -114.4775 | 8.02 | 7.9239 | 7.8735 | 0.21973 | 0.16937 | 0.050354 | -122.3099 | -122.3007 | 0.17395 | 0.17853 | 0.16479 | 0.12817 | 0.11444 | 0.31586 | 0.19684 | 0.1236 | 0.027465 | 0.19684 | 0.01831 | 7.901 | 0.068664 | -114.6744 | -122.3282 | 7.901 | 0.077819 | 7.901 | 0.10986
4743.9375 | 122.4701 | -0.050354 | 122.2916 | -0.01976 | 0.015718 | 0.012625 | -0.0072268 | 0.0031487 | -0.0089892 | -0.0021682 | -0.005371 | 0.019113 | 0.04178 | -0.015706 | 0.012975 | 0.02311 | -0.0059751 | 7.8278 | 7.7637 | 7.5897 | 7.8186 | 7.9239 | 7.7774 | 7.8094 | 0.10071 | -0.009155 | -0.018311 | 0.07782 | 0.16937 | 0.1236 | 0.14648 | 7.6401 | -114.5279 | -114.473 | 7.9742 | 7.8598 | 7.8278 | 0.21973 | 0.18768 | 0.032043 | -122.3007 | -122.2137 | 0.21973 | 0.19684 | 0.17395 | 0.16479 | 0.14191 | 0.33417 | 0.22888 | 0.18768 | 0.096131 | 0.17395 | 0.009156 | 7.814 | 0.041199 | -114.7018 | -122.3099 | 7.869 | 0.12817 | 7.8781 | 0.15106
4745.7031 | 122.4518 | -0.068665 | 122.2961 | -0.01976 | 0.01166 | 0.010489 | -0.008295 | 0.00037174 | -0.011125 | -0.000673 | -0.0084228 | 0.020395 | 0.043062 | -0.016987 | 0.011694 | 0.023964 | -0.0027707 | 7.814 | 7.8049 | 7.6218 | 7.814 | 7.9285 | 7.814 | 7.8461 | 0.036621 | -0.004578 | -0.022888 | 0.032043 | 0.14648 | 0.1236 | 0.11444 | 7.6904 | -114.4913 | -114.4821 | 7.9971 | 7.9147 | 7.8827 | 0.2243 | 0.19226 | 0.045777 | -122.3007 | -122.2641 | 0.21515 | 0.18311 | 0.19226 | 0.13733 | 0.14648 | 0.3067 | 0.19226 | 0.16937 | 0.054931 | 0.18311 | 0.01831 | 7.8735 | 0.064087 | -114.6744 | -122.319 | 7.8827 | 0.10071 | 7.8827 | 0.10529
4747.4688 | 122.3923 | -0.10986 | 122.3465 | -0.012131 | 0.012087 | 0.0085662 | -0.0061588 | 0.00015814 | -0.0092028 | -0.0036636 | -0.005371 | 0.021676 | 0.040071 | -0.01186 | 0.012548 | 0.022469 | -0.0064023 | 7.8644 | 7.8964 | 7.6584 | 7.8094 | 7.9102 | 7.814 | 7.8186 | -0.041199 | 0.027466 | -0.064087 | -0.032043 | 0.068665 | 0.041199 | 0.07782 | 7.7682 | -114.4501 | -114.537 | 8.02 | 7.9285 | 7.9239 | 0.16022 | 0.15564 | 0.045776 | -122.319 | -122.3785 | 0.17853 | 0.18768 | 0.15106 | 0.14191 | 0.10529 | 0.25177 | 0.15106 | 0.13275 | 0.032044 | 0.23804 | 0.091553 | 8.0063 | 0.13733 | -114.6881 | -122.4106 | 7.9193 | 0.07782 | 7.9742 | 0.068664
4749.1875 | 122.4747 | -0.064087 | 122.2916 | -0.0045011 | 0.010591 | 0.0092072 | -0.0087222 | 0.0018671 | -0.010271 | -0.0030228 | -0.0084228 | 0.018472 | 0.042849 | -0.015065 | 0.013189 | 0.021828 | -0.0061887 | 7.8598 | 7.7957 | 7.6172 | 7.869 | 7.9971 | 7.8598 | 7.8918 | 0.11902 | -0.013733 | -0.022888 | 0.068665 | 0.19226 | 0.15106 | 0.15564 | 7.6813 | -114.4959 | -114.4226 | 8.0612 | 7.9559 | 7.9239 | 0.27466 | 0.24261 | 0.041199 | -122.3053 | -122.2229 | 0.25635 | 0.21973 | 0.21515 | 0.17853 | 0.17395 | 0.37994 | 0.25177 | 0.21515 | 0.091553 | 0.17853 | 0.009155 | 7.8598 | 0.050354 | -114.6744 | -122.3145 | 7.933 | 0.13275 | 7.9239 | 0.18311
4750.9688 | 122.4426 | -0.07782 | 122.3007 | -0.012131 | 0.011019 | 0.010489 | -0.007654 | 0.0054987 | -0.0087756 | -0.0025956 | -0.005371 | 0.018258 | 0.04178 | -0.02126 | 0.013189 | 0.022683 | -0.0040525 | 7.7545 | 7.7087 | 7.5623 | 7.7545 | 7.8644 | 7.7225 | 7.7683 | 0.054932 | 0.004578 | -0.022888 | 0.013733 | 0.10986 | 0.082397 | 0.091553 | 7.6401 | -114.592 | -114.5462 | 7.9422 | 7.8461 | 7.8003 | 0.20599 | 0.16022 | 0.054932 | -122.2961 | -122.287 | 0.18768 | 0.16937 | 0.16022 | 0.11444 | 0.10528 | 0.30212 | 0.19226 | 0.13275 | 0.036621 | 0.14648 | 0.027466 | 7.7866 | 0.082398 | -114.7385 | -122.3236 | 7.8323 | 0.091553 | 7.8323 | 0.13275
4752.6719 | 122.4197 | -0.086975 | 122.2961 | -0.0045011 | 0.013796 | 0.0092072 | -0.0085086 | -0.00069646 | -0.0089892 | -0.0038772 | -0.0084228 | 0.019754 | 0.043703 | -0.014638 | 0.012334 | 0.021401 | -0.00084805 | 7.7499 | 7.7499 | 7.5531 | 7.7408 | 7.8552 | 7.7087 | 7.7728 | 0.032043 | 0.009155 | -0.050354 | 0 | 0.09613 | 0.07782 | 0.10529 | 7.6401 | -114.5462 | -114.5554 | 7.9422 | 7.8598 | 7.7957 | 0.21973 | 0.15564 | 0.036621 | -122.287 | -122.2961 | 0.1831 | 0.19226 | 0.16479 | 0.15564 | 0.12817 | 0.30212 | 0.18768 | 0.14648 | 0.050354 | 0.19684 | 0.059509 | 7.8369 | 0.09613 | -114.743 | -122.3465 | 7.8278 | 0.086975 | 7.8369 | 0.11902
4754.4375 | 122.4152 | -0.07782 | 122.2961 | -0.012131 | 0.0123 | 0.0092072 | -0.008295 | 0.0016535 | -0.0094164 | -0.0030228 | -0.0084228 | 0.022103 | 0.044344 | -0.01891 | 0.01383 | 0.02311 | 6.346e-06 | 7.7499 | 7.7225 | 7.5439 | 7.7271 | 7.8323 | 7.6996 | 7.7499 | 0.018311 | 0.009155 | -0.041199 | -0.013733 | 0.10529 | 0.073242 | 0.086975 | 7.6218 | -114.5737 | -114.5691 | 7.9102 | 7.8278 | 7.7774 | 0.20599 | 0.15564 | 0.036621 | -122.287 | -122.3099 | 0.18311 | 0.16479 | 0.15106 | 0.12817 | 0.11444 | 0.28839 | 0.18311 | 0.14649 | 0.027466 | 0.17853 | 0.050354 | 7.8003 | 0.086975 | -114.7522 | -122.3373 | 7.8049 | 0.064087 | 7.8278 | 0.096131
4756.1562 | 122.3557 | -0.10986 | 122.3328 | -0.01976 | 0.010164 | 0.0096344 | -0.0080814 | 0.0020807 | -0.010912 | -0.0040908 | -0.011475 | 0.024026 | 0.041353 | -0.018696 | 0.013616 | 0.021187 | -0.0010617 | 7.7866 | 7.8232 | 7.6035 | 7.7499 | 7.8506 | 7.7225 | 7.7591 | -0.050354 | 0.027466 | -0.064087 | -0.07782 | 0.036621 | 0.022888 | 0.027466 | 7.7133 | -114.5096 | -114.5828 | 7.9605 | 7.869 | 7.8323 | 0.15564 | 0.11902 | 0.045776 | -122.3053 | -122.4106 | 0.14648 | 0.13733 | 0.13275 | 0.091553 | 0.086975 | 0.24719 | 0.14648 | 0.10071 | -0.013733 | 0.21973 | 0.091553 | 7.933 | 0.13733 | -114.7293 | -122.3969 | 7.8598 | 0.032043 | 7.8964 | 0.059509
4757.9219 | 122.5159 | -0.068665 | 122.2961 | -0.012131 | 0.010805 | 0.0096344 | -0.0067996 | 0.00015814 | -0.010912 | -0.0038772 | -0.005371 | 0.018686 | 0.043703 | -0.022328 | 0.01148 | 0.025246 | -0.0046933 | 7.814 | 7.7271 | 7.5668 | 7.8232 | 7.9651 | 7.814 | 7.8461 | 0.14191 | -0.013733 | -0.027466 | 0.054932 | 0.20142 | 0.16022 | 0.14191 | 7.6355 | -114.5691 | -114.473 | 8.0338 | 7.9147 | 7.8827 | 0.27924 | 0.24719 | 0.041199 | -122.3099 | -122.2412 | 0.27008 | 0.21057 | 0.22888 | 0.16937 | 0.18768 | 0.39825 | 0.25635 | 0.22888 | 0.082398 | 0.16022 | 0.013733 | 7.7957 | 0.054932 | -114.7293 | -122.3236 | 7.8918 | 0.1236 | 7.8827 | 0.21057
4759.6406 | 122.3694 | -0.10986 | 122.3373 | -0.012131 | 0.014437 | 0.010275 | -0.0055178 | 0.00015814 | -0.0092028 | -0.0025956 | -0.0084228 | 0.022531 | 0.042421 | -0.0097241 | 0.013616 | 0.024178 | -0.0031979 | 7.7728 | 7.7637 | 7.5439 | 7.7179 | 7.814 | 7.663 | 7.6813 | 0.009155 | 0.022888 | -0.032043 | -0.041199 | 0.059509 | 0.004578 | 0.050354 | 7.6538 | -114.5737 | -114.6194 | 7.9239 | 7.7911 | 7.7728 | 0.13733 | 0.11902 | 0.07782 | -122.3145 | -122.3785 | 0.16937 | 0.16022 | 0.11444 | 0.082397 | 0.036621 | 0.27008 | 0.17395 | 0.091552 | -0.009156 | 0.21973 | 0.054931 | 7.8735 | 0.13275 | -114.7934 | -122.3694 | 7.8278 | 0.068664 | 7.8827 | 0.11902
4761.4062 | 122.4884 | -0.068665 | 122.3007 | -0.0045011 | 0.011019 | 0.009848 | -0.0097904 | 0.00079894 | -0.0083484 | -0.0064408 | -0.0084228 | 0.020181 | 0.040499 | -0.02596 | 0.012121 | 0.025032 | -0.0036253 | 7.7316 | 7.6904 | 7.5165 | 7.7408 | 7.8735 | 7.7545 | 7.7774 | 0.068665 | -0.004578 | -0.036621 | 0.059509 | 0.16479 | 0.16479 | 0.14191 | 7.5851 | -114.6103 | -114.5599 | 7.9422 | 7.8461 | 7.8232 | 0.26093 | 0.23804 | 0.032044 | -122.3053 | -122.2412 | 0.23346 | 0.21057 | 0.23346 | 0.17853 | 0.20142 | 0.35706 | 0.2243 | 0.20142 | 0.09613 | 0.17395 | 0.032043 | 7.7591 | 0.064087 | -114.7842 | -122.3373 | 7.8094 | 0.12817 | 7.8003 | 0.13733
4763.1719 | 122.4609 | -0.073242 | 122.3053 | -0.012131 | 0.012514 | 0.0092072 | -0.0091494 | -0.00048286 | -0.011766 | -0.0011002 | -0.005371 | 0.020181 | 0.040712 | -0.02126 | 0.012334 | 0.022896 | -0.0061887 | 7.7911 | 7.7179 | 7.5577 | 7.7957 | 7.9102 | 7.7683 | 7.7911 | 0.10071 | 0 | -0.018311 | 0.041199 | 0.16479 | 0.13275 | 0.1236 | 7.6309 | -114.5874 | -114.5096 | 7.9834 | 7.8644 | 7.8415 | 0.23346 | 0.21057 | 0.054931 | -122.3053 | -122.2641 | 0.23804 | 0.19684 | 0.20599 | 0.14191 | 0.15106 | 0.35248 | 0.23804 | 0.18311 | 0.05951 | 0.16022 | 0.018311 | 7.7911 | 0.073242 | -114.7476 | -122.3236 | 7.869 | 0.11444 | 7.8644 | 0.17395
4764.9375 | 122.493 | -0.050354 | 122.3099 | -0.01976 | 0.01465 | 0.012198 | -0.0063724 | 0.00058534 | -0.006853 | -0.0030228 | -0.011475 | 0.021035 | 0.043276 | -0.018055 | 0.014257 | 0.023323 | -0.0031979 | 7.6904 | 7.5851 | 7.4753 | 7.6767 | 7.7911 | 7.6035 | 7.663 | 0.10986 | -0.022888 | 0 | 0.073242 | 0.16479 | 0.13275 | 0.13275 | 7.5256 | -114.7247 | -114.6332 | 7.8415 | 7.7133 | 7.6538 | 0.18768 | 0.12817 | 0.050354 | -122.3328 | -122.2366 | 0.21515 | 0.18311 | 0.18311 | 0.13275 | 0.13275 | 0.31586 | 0.20142 | 0.16479 | 0.073242 | 0.10986 | -0.022888 | 7.6355 | 0.027466 | -114.8346 | -122.3099 | 7.7271 | 0.1236 | 7.7408 | 0.16022
4766.6562 | 122.3648 | -0.10986 | 122.3465 | -0.0045011 | 0.0099506 | 0.012625 | -0.0072268 | 0.0025079 | -0.010485 | -0.0021682 | -0.011475 | 0.020822 | 0.041567 | -0.014424 | 0.012548 | 0.022896 | -0.0027707 | 7.7545 | 7.7271 | 7.5485 | 7.695 | 7.8186 | 7.6813 | 7.7225 | 0 | 0.036621 | -0.041199 | -0.073242 | 0.068665 | 0.027466 | 0.027466 | 7.6584 | -114.6194 | -114.6515 | 7.9285 | 7.8323 | 7.7911 | 0.17395 | 0.13275 | 0.068664 | -122.3099 | -122.4197 | 0.17853 | 0.13733 | 0.13733 | 0.068665 | 0.068665 | 0.27008 | 0.14648 | 0.10986 | -0.032043 | 0.17853 | 0.07782 | 7.8369 | 0.14648 | -114.798 | -122.3877 | 7.8049 | 0.036621 | 7.8644 | 0.10986
4768.4375 | 122.374 | -0.10986 | 122.3282 | -0.02739 | 0.012514 | 0.010275 | -0.0061588 | 0.0010125 | -0.010698 | -0.0047318 | -0.011475 | 0.021463 | 0.044344 | -0.012074 | 0.015325 | 0.022042 | -0.0027707 | 7.7087 | 7.7683 | 7.5073 | 7.6447 | 7.7454 | 7.6492 | 7.6813 | -0.054932 | 0.027466 | -0.054932 | -0.059509 | 0.050354 | 0.018311 | 0.050354 | 7.6172 | -114.5599 | -114.6835 | 7.8552 | 7.7911 | 7.7591 | 0.17395 | 0.14191 | 0.054931 | -122.3007 | -122.3877 | 0.16022 | 0.16022 | 0.12817 | 0.10529 | 0.073243 | 0.23804 | 0.13733 | 0.10529 | -0.004577 | 0.26093 | 0.082398 | 7.8781 | 0.13733 | -114.8209 | -122.3831 | 7.7545 | 0.050354 | 7.8186 | 0.054931
4770.2031 | 122.4518 | -0.073242 | 122.2961 | -0.0045011 | 0.01166 | 0.0094208 | -0.011499 | -0.0013373 | -0.010271 | -0.0015274 | -0.0084228 | 0.018472 | 0.041567 | -0.020833 | 0.012762 | 0.022469 | -0.0031979 | 7.6309 | 7.6126 | 7.4524 | 7.6126 | 7.7271 | 7.5989 | 7.6401 | 0.027466 | -0.009155 | -0.027466 | 0.004578 | 0.13275 | 0.091553 | 0.10529 | 7.5256 | -114.6835 | -114.6835 | 7.8003 | 7.7133 | 7.6721 | 0.18768 | 0.14648 | 0.045776 | -122.3053 | -122.2916 | 0.20599 | 0.17853 | 0.16479 | 0.13275 | 0.11902 | 0.27466 | 0.16022 | 0.16022 | 0.032044 | 0.16022 | 0.018311 | 7.6859 | 0.064087 | -114.8438 | -122.3236 | 7.6859 | 0.07782 | 7.7042 | 0.10071
4771.9844 | 122.438 | -0.086975 | 122.3328 | -0.0045011 | 0.0095234 | 0.0094208 | -0.0089358 | 0.0029351 | -0.010485 | -0.0045182 | -0.0023192 | 0.019326 | 0.04114 | -0.015919 | 0.012975 | 0.022255 | -0.0023435 | 7.6309 | 7.6126 | 7.4387 | 7.6309 | 7.7362 | 7.6035 | 7.663 | 0.022888 | -0.018311 | -0.022888 | 0.004578 | 0.10986 | 0.07782 | 0.086975 | 7.5256 | -114.7202 | -114.7018 | 7.8232 | 7.7499 | 7.6904 | 0.2243 | 0.1648 | 0.064087 | -122.3511 | -122.3282 | 0.19684 | 0.17395 | 0.16479 | 0.10986 | 0.10071 | 0.29755 | 0.19226 | 0.13275 | 0.027466 | 0.17395 | 0.004577 | 7.6996 | 0.068664 | -114.8941 | -122.3557 | 7.7179 | 0.091553 | 7.7179 | 0.10986
4773.7656 | 122.4609 | -0.059509 | 122.319 | -0.012131 | 0.011873 | 0.011984 | -0.0078676 | -0.0041145 | -0.0081348 | -0.0028092 | -0.005371 | 0.020395 | 0.043276 | -0.020192 | 0.014898 | 0.021401 | -0.0014891 | 7.6447 | 7.576 | 7.4249 | 7.6218 | 7.7499 | 7.5806 | 7.6447 | 0.09613 | -0.004578 | -0.022888 | 0.032043 | 0.12817 | 0.07782 | 0.1236 | 7.4844 | -114.743 | -114.6973 | 7.8094 | 7.7042 | 7.6401 | 0.21973 | 0.15564 | 0.036621 | -122.3236 | -122.287 | 0.18768 | 0.1831 | 0.13733 | 0.14648 | 0.10071 | 0.32501 | 0.19684 | 0.15106 | 0.054931 | 0.15106 | 0.01831 | 7.6355 | 0.054931 | -114.8941 | -122.3419 | 7.6813 | 0.091552 | 7.7042 | 0.15564
4775.4688 | 122.4976 | -0.064087 | 122.3145 | -0.01976 | 0.015078 | 0.0094208 | -0.0040224 | 0.0057123 | -0.0083484 | -0.0015274 | -0.014526 | 0.020608 | 0.042208 | -0.020192 | 0.015752 | 0.022896 | -0.00020725 | 7.6035 | 7.5806 | 7.4066 | 7.5989 | 7.7042 | 7.5348 | 7.5851 | 0.082397 | -0.022888 | -0.027466 | 0.059509 | 0.16022 | 0.10071 | 0.15106 | 7.4707 | -114.7339 | -114.7156 | 7.7683 | 7.6492 | 7.5989 | 0.17853 | 0.12817 | 0.036621 | -122.3373 | -122.2549 | 0.2243 | 0.21515 | 0.1648 | 0.17853 | 0.12817 | 0.29755 | 0.19226 | 0.18768 | 0.086975 | 0.17395 | 0.004578 | 7.6447 | 0.041199 | -114.9078 | -122.3419 | 7.663 | 0.1236 | 7.6675 | 0.14648
4777.2344 | 122.4106 | -0.10529 | 122.3373 | -0.01976 | 0.012087 | 0.010489 | -0.0061588 | 0.0020807 | -0.0092028 | -0.0047318 | -0.0023192 | 0.020395 | 0.043703 | -0.01421 | 0.014898 | 0.024178 | -0.0044797 | 7.6721 | 7.6996 | 7.4844 | 7.608 | 7.7133 | 7.6035 | 7.6218 | -0.054932 | 0.036621 | -0.050354 | -0.041199 | 0.064087 | 0.018311 | 0.059509 | 7.5897 | -114.6378 | -114.7293 | 7.8186 | 7.7271 | 7.7087 | 0.13733 | 0.11902 | 0.054932 | -122.3007 | -122.3785 | 0.16937 | 0.16479 | 0.1236 | 0.10986 | 0.068665 | 0.22888 | 0.1236 | 0.11444 | 0.009155 | 0.21515 | 0.086975 | 7.8049 | 0.14191 | -114.8529 | -122.3877 | 7.7133 | 0.064087 | 7.7774 | 0.050354
4778.9531 | 122.4518 | -0.07782 | 122.3145 | -0.0045011 | 0.010805 | 0.0089936 | -0.0072268 | -0.00048286 | -0.010271 | -0.0015274 | -0.005371 | 0.019754 | 0.043489 | -0.013356 | 0.01383 | 0.022469 | -0.0019163 | 7.6035 | 7.5668 | 7.4249 | 7.5943 | 7.7271 | 7.5668 | 7.6035 | 0.045776 | -0.009155 | -0.022888 | 0.013733 | 0.12817 | 0.09613 | 0.10071 | 7.5027 | -114.7476 | -114.7202 | 7.8049 | 7.6813 | 7.6447 | 0.17853 | 0.14191 | 0.054932 | -122.3236 | -122.3007 | 0.20599 | 0.17853 | 0.17395 | 0.1236 | 0.11902 | 0.30212 | 0.16937 | 0.15106 | 0.036621 | 0.14191 | 0.013733 | 7.6447 | 0.068665 | -114.8895 | -122.3373 | 7.6721 | 0.091553 | 7.6813 | 0.1236
4780.7188 | 122.3785 | -0.11444 | 122.3557 | -0.01976 | 0.015718 | 0.011771 | -0.0055178 | 0.0033623 | -0.010057 | -0.0030228 | -0.005371 | 0.023599 | 0.043703 | -0.016774 | 0.012548 | 0.022042 | -0.0036253 | 7.5714 | 7.6126 | 7.3883 | 7.4982 | 7.5897 | 7.457 | 7.5027 | -0.073242 | 0.032043 | -0.059509 | -0.059509 | 0.018311 | -0.027466 | 0.022888 | 7.5027 | -114.743 | -114.8575 | 7.7042 | 7.6172 | 7.5714 | 0.11444 | 0.068664 | 0.054932 | -122.3236 | -122.4152 | 0.13275 | 0.13733 | 0.086975 | 0.082397 | 0.032043 | 0.20142 | 0.10986 | 0.07782 | 0 | 0.2243 | 0.091552 | 7.7271 | 0.14648 | -114.9673 | -122.4152 | 7.6126 | 0.054932 | 7.6859 | 0.041199
4782.4844 | 122.3557 | -0.11444 | 122.3648 | -0.0045011 | 0.014437 | 0.011984 | -0.004877 | 0.0042169 | -0.0079212 | -0.0028092 | -0.0084228 | 0.021249 | 0.042421 | -0.012715 | 0.014471 | 0.021828 | -0.0046933 | 7.5668 | 7.6218 | 7.4158 | 7.5073 | 7.5943 | 7.457 | 7.4982 | -0.086975 | 0.022888 | -0.045776 | -0.073242 | 0 | -0.032043 | 0.018311 | 7.5302 | -114.743 | -114.8575 | 7.7087 | 7.6126 | 7.5714 | 0.082398 | 0.041199 | 0.068665 | -122.3419 | -122.438 | 0.11444 | 0.13275 | 0.082398 | 0.064087 | 0.013733 | 0.17853 | 0.091553 | 0.045776 | -0.027466 | 0.20599 | 0.068664 | 7.7362 | 0.13733 | -114.949 | -122.4106 | 7.6218 | 0.041199 | 7.6813 | 0.027466
4784.25 | 122.4609 | -0.09613 | 122.3282 | -0.012131 | 0.012514 | 0.010062 | -0.0087222 | -0.00048286 | -0.010271 | -0.0043046 | -0.0084228 | 0.021035 | 0.04178 | -0.018696 | 0.014043 | 0.024819 | -0.0051205 | 7.5714 | 7.5165 | 7.3837 | 7.5577 | 7.6904 | 7.5165 | 7.576 | 0.032043 | -0.018311 | -0.022888 | 0.022888 | 0.10071 | 0.09613 | 0.091553 | 7.4799 | -114.8117 | -114.7705 | 7.7866 | 7.6721 | 7.6126 | 0.19226 | 0.13275 | 0.073242 | -122.3465 | -122.3053 | 0.19684 | 0.18768 | 0.19226 | 0.11444 | 0.11902 | 0.3067 | 0.17395 | 0.1236 | 0.045776 | 0.13275 | 0.004577 | 7.6126 | 0.077819 | -114.9445 | -122.3511 | 7.6538 | 0.11902 | 7.6675 | 0.12817
4785.9531 | 122.4655 | -0.073242 | 122.3419 | -0.012131 | 0.013155 | 0.010062 | -0.0085086 | -0.00091006 | -0.0092028 | -0.0013138 | -0.005371 | 0.020395 | 0.041567 | -0.022969 | 0.011266 | 0.024178 | -0.0025571 | 7.5623 | 7.5302 | 7.3746 | 7.5485 | 7.6813 | 7.5119 | 7.5806 | 0.041199 | -0.004578 | -0.032043 | 0.013733 | 0.11902 | 0.086975 | 0.086975 | 7.4478 | -114.8117 | -114.7934 | 7.7545 | 7.6538 | 7.5851 | 0.20599 | 0.13733 | 0.041199 | -122.3465 | -122.3282 | 0.19226 | 0.16022 | 0.16022 | 0.11902 | 0.11902 | 0.3067 | 0.17395 | 0.15106 | 0.045776 | 0.15564 | 0.027465 | 7.6035 | 0.068664 | -114.9673 | -122.374 | 7.6218 | 0.086975 | 7.6355 | 0.11444
4787.7188 | 122.4884 | -0.10071 | 122.3236 | -0.012131 | 0.011232 | 0.0092072 | -0.0085086 | -0.0011237 | -0.010271 | -0.0045182 | -0.005371 | 0.017404 | 0.042635 | -0.0086559 | 0.013616 | 0.023751 | -0.00063445 | 7.5851 | 7.5485 | 7.4066 | 7.5714 | 7.6904 | 7.5623 | 7.5897 | 0.022888 | 0.004578 | -0.018311 | 0.018311 | 0.13733 | 0.11902 | 0.10986 | 7.5073 | -114.7751 | -114.7522 | 7.7911 | 7.6904 | 7.663 | 0.18311 | 0.15564 | 0.082397 | -122.319 | -122.3053 | 0.23804 | 0.21057 | 0.21973 | 0.12817 | 0.13733 | 0.28381 | 0.1648 | 0.15564 | 0.036622 | 0.14191 | 0.022889 | 7.6492 | 0.10529 | -114.917 | -122.3419 | 7.6721 | 0.11902 | 7.6859 | 0.1236
4789.4844 | 122.5342 | -0.068665 | 122.3099 | -0.0045011 | 0.011019 | 0.010062 | -0.0097904 | 0.00058534 | -0.011339 | -0.00345 | -0.011475 | 0.021676 | 0.04114 | -0.016987 | 0.011053 | 0.022683 | -0.0017027 | 7.6492 | 7.5668 | 7.4249 | 7.6492 | 7.8003 | 7.6401 | 7.6767 | 0.14648 | 0 | -0.013733 | 0.045776 | 0.18768 | 0.16022 | 0.14648 | 7.4936 | -114.743 | -114.6606 | 7.869 | 7.7454 | 7.7087 | 0.25177 | 0.21515 | 0.054932 | -122.3099 | -122.2641 | 0.25635 | 0.21515 | 0.22888 | 0.16022 | 0.17395 | 0.37537 | 0.2243 | 0.20142 | 0.059509 | 0.14191 | 0.013733 | 7.6355 | 0.068665 | -114.8849 | -122.3236 | 7.7179 | 0.11444 | 7.7179 | 0.21515
4791.2656 | 122.4335 | -0.10071 | 122.3648 | -0.01976 | 0.01465 | 0.011557 | -0.0067996 | 0.0010125 | -0.011339 | -0.0025956 | -0.0023192 | 0.022744 | 0.043703 | -0.01421 | 0.015325 | 0.022683 | -0.00042085 | 7.6263 | 7.6401 | 7.4295 | 7.5806 | 7.6721 | 7.5623 | 7.5897 | -0.009155 | 0.018311 | -0.050354 | -0.018311 | 0.091553 | 0.050354 | 0.073242 | 7.5302 | -114.7247 | -114.7842 | 7.7728 | 7.6904 | 7.663 | 0.16022 | 0.13275 | 0.050354 | -122.3465 | -122.3831 | 0.19226 | 0.17395 | 0.15106 | 0.1236 | 0.10071 | 0.24262 | 0.15106 | 0.14191 | 0.032043 | 0.21057 | 0.068665 | 7.7408 | 0.11902 | -114.9353 | -122.4152 | 7.6813 | 0.082397 | 7.7271 | 0.091553
4793.0469 | 122.4197 | -0.09613 | 122.3648 | -0.012131 | 0.012728 | 0.010916 | -0.0080814 | 0.0012261 | -0.0094164 | -0.0013138 | -0.0023192 | 0.021035 | 0.043276 | -0.013997 | 0.015539 | 0.023537 | -0.0044797 | 7.5943 | 7.5806 | 7.3929 | 7.5394 | 7.6721 | 7.5165 | 7.5439 | 0.036621 | 0.022888 | -0.045776 | -0.004578 | 0.073242 | 0.045776 | 0.064087 | 7.489 | -114.7842 | -114.8254 | 7.7682 | 7.6401 | 7.6126 | 0.15106 | 0.1236 | 0.050354 | -122.3419 | -122.3694 | 0.16937 | 0.16022 | 0.14191 | 0.10986 | 0.091552 | 0.27924 | 0.14648 | 0.11902 | 0.041198 | 0.18768 | 0.068664 | 7.6767 | 0.11902 | -114.9719 | -122.4106 | 7.6355 | 0.091552 | 7.6904 | 0.13275
4794.75 | 122.5067 | -0.073242 | 122.3145 | -0.0045011 | 0.0093098 | 0.00878 | -0.010218 | -0.0011237 | -0.0081348 | -0.0038772 | -0.0023192 | 0.017831 | 0.042208 | -0.025105 | 0.014471 | 0.024605 | -0.0040525 | 7.5577 | 7.5256 | 7.3746 | 7.5668 | 7.6859 | 7.5439 | 7.6126 | 0.073242 | -0.004578 | -0.022888 | 0.036621 | 0.16479 | 0.15106 | 0.13275 | 7.4478 | -114.7888 | -114.7476 | 7.7591 | 7.6859 | 7.6172 | 0.23804 | 0.16937 | 0.050354 | -122.319 | -122.2778 | 0.23804 | 0.20599 | 0.2243 | 0.15564 | 0.17395 | 0.31128 | 0.19226 | 0.18768 | 0.059509 | 0.15106 | 0.01831 | 7.5989 | 0.068664 | -114.9399 | -122.3373 | 7.6401 | 0.10986 | 7.6309 | 0.14648
4796.5312 | 122.4518 | -0.07782 | 122.3373 | -0.02739 | 0.0093098 | 0.010062 | -0.0078676 | 0.00058534 | -0.0074938 | -0.005159 | -0.005371 | 0.018258 | 0.041994 | -0.013997 | 0.011907 | 0.023751 | -0.0014891 | 7.5119 | 7.4936 | 7.3425 | 7.4936 | 7.6126 | 7.489 | 7.5256 | 0.027466 | 0.004578 | -0.022888 | -0.018311 | 0.10071 | 0.07782 | 0.091553 | 7.4203 | -114.8438 | -114.8438 | 7.6904 | 7.6035 | 7.5668 | 0.18311 | 0.14649 | 0.054932 | -122.3328 | -122.3557 | 0.17853 | 0.16937 | 0.15564 | 0.11444 | 0.10071 | 0.27008 | 0.15106 | 0.1236 | 0.004577 | 0.15106 | 0.027466 | 7.5714 | 0.082398 | -114.9948 | -122.3602 | 7.5714 | 0.059509 | 7.5897 | 0.10529
4798.2344 | 122.4655 | -0.073242 | 122.3099 | -0.012131 | 0.012514 | 0.010275 | -0.008295 | -0.0032599 | -0.0074938 | -0.0047318 | -0.0084228 | 0.020181 | 0.042635 | -0.013142 | 0.011907 | 0.022683 | 0.0010745 | 7.5165 | 7.489 | 7.338 | 7.4844 | 7.6035 | 7.4387 | 7.5256 | 0.009155 | -0.009155 | -0.022888 | -0.009155 | 0.11902 | 0.09613 | 0.086975 | 7.4112 | -114.8209 | -114.8254 | 7.6767 | 7.5989 | 7.5119 | 0.18768 | 0.10071 | 0.050354 | -122.319 | -122.319 | 0.19226 | 0.16022 | 0.16937 | 0.10986 | 0.11902 | 0.2655 | 0.14648 | 0.14191 | 0.013733 | 0.15106 | 0.013733 | 7.5623 | 0.064087 | -114.9719 | -122.3328 | 7.5577 | 0.064087 | 7.5897 | 0.082397
4800.0156 | 122.5159 | -0.064087 | 122.3328 | -0.02739 | 0.010591 | 0.0092072 | -0.0095766 | -0.0043281 | -0.010698 | -0.0040908 | -0.005371 | 0.019754 | 0.039644 | -0.0099377 | 0.011907 | 0.022042 | -0.0012753 | 7.608 | 7.4936 | 7.3654 | 7.6126 | 7.7545 | 7.6126 | 7.6355 | 0.12817 | -0.022888 | -0.004578 | 0.045776 | 0.1831 | 0.14191 | 0.14191 | 7.4295 | -114.8392 | -114.7202 | 7.8186 | 7.6996 | 7.6767 | 0.27008 | 0.24719 | 0.059509 | -122.3557 | -122.287 | 0.24719 | 0.20599 | 0.20599 | 0.14649 | 0.14649 | 0.3891 | 0.24719 | 0.18768 | 0.050354 | 0.12817 | -0.01831 | 7.5577 | 0.041199 | -114.9673 | -122.3373 | 7.6767 | 0.10986 | 7.6721 | 0.19226
4801.7344 | 122.4106 | -0.091553 | 122.3694 | -0.012131 | 0.013155 | 0.010916 | -0.0063724 | 0.0052851 | -0.0077074 | -0.0038772 | -0.011475 | 0.022958 | 0.043489 | -0.01421 | 0.014898 | 0.022469 | -0.0031979 | 7.5302 | 7.5165 | 7.338 | 7.489 | 7.6035 | 7.4341 | 7.457 | 0.032043 | 0.009155 | -0.036621 | -0.018311 | 0.064087 | 0.004578 | 0.059509 | 7.4295 | -114.8529 | -114.8804 | 7.695 | 7.5485 | 7.5256 | 0.11902 | 0.09613 | 0.054932 | -122.3602 | -122.3877 | 0.15564 | 0.15106 | 0.096131 | 0.09613 | 0.041199 | 0.2655 | 0.15106 | 0.10071 | 0.01831 | 0.17853 | 0.045776 | 7.608 | 0.10071 | -115.0314 | -122.406 | 7.5806 | 0.073242 | 7.6218 | 0.1236
4803.5 | 122.4976 | -0.059509 | 122.3373 | -0.012131 | 0.011873 | 0.0096344 | -0.008295 | -0.00091006 | -0.0098438 | -0.0032364 | -0.0023192 | 0.017831 | 0.04413 | -0.016347 | 0.012548 | 0.022896 | -0.0036253 | 7.6035 | 7.5073 | 7.3563 | 7.5897 | 7.7271 | 7.576 | 7.5943 | 0.11902 | 0 | -0.013733 | 0.064087 | 0.16022 | 0.14648 | 0.13733 | 7.4158 | -114.83 | -114.7476 | 7.7866 | 7.6538 | 7.6355 | 0.23804 | 0.21973 | 0.045776 | -122.3373 | -122.2733 | 0.21973 | 0.19684 | 0.20599 | 0.15106 | 0.16022 | 0.37079 | 0.23346 | 0.17395 | 0.07782 | 0.15106 | 0.013733 | 7.5668 | 0.059509 | -114.9811 | -122.3511 | 7.6492 | 0.1236 | 7.663 | 0.17853
4805.2812 | 122.3877 | -0.11902 | 122.3557 | -0.012131 | 0.010164 | 0.0085662 | -0.0074404 | -0.0013373 | -0.010057 | -0.0025956 | -0.005371 | 0.021463 | 0.04114 | -0.016347 | 0.012548 | 0.023323 | -0.0055479 | 7.5165 | 7.576 | 7.3517 | 7.489 | 7.5851 | 7.4844 | 7.5027 | -0.054932 | 0.027466 | -0.059509 | -0.068665 | 0.045776 | 0 | 0.032043 | 7.4707 | -114.7797 | -114.8666 | 7.7042 | 7.6218 | 7.6035 | 0.15106 | 0.13275 | 0.05951 | -122.3282 | -122.4243 | 0.16479 | 0.15106 | 0.11902 | 0.091552 | 0.059509 | 0.23346 | 0.13733 | 0.10528 | -0.009156 | 0.2243 | 0.086975 | 7.695 | 0.14649 | -115.004 | -122.4152 | 7.608 | 0.050354 | 7.6355 | 0.064087
4807.0625 | 122.406 | -0.09613 | 122.3602 | -0.01976 | 0.01465 | 0.011771 | -0.0057314 | 0.00015814 | -0.0074938 | -0.0013138 | -0.0084228 | 0.021676 | 0.043489 | -0.015492 | 0.012975 | 0.022896 | -0.0034117 | 7.4158 | 7.4387 | 7.2372 | 7.3471 | 7.4478 | 7.3196 | 7.3563 | -0.036621 | 0.009155 | -0.050354 | -0.050354 | 0.036621 | 0 | 0.041199 | 7.3334 | -114.9216 | -115.0131 | 7.5439 | 7.4524 | 7.4158 | 0.11902 | 0.082397 | 0.045776 | -122.3511 | -122.4106 | 0.13275 | 0.13733 | 0.09613 | 0.091553 | 0.050354 | 0.21057 | 0.10986 | 0.086975 | 0 | 0.20142 | 0.059509 | 7.5348 | 0.10528 | -115.123 | -122.4106 | 7.4432 | 0.045776 | 7.5119 | 0.059509
4808.7656 | 122.5388 | -0.064087 | 122.3465 | -0.012131 | 0.0095234 | 0.0083526 | -0.0085086 | 0.0010125 | -0.011339 | -0.0038772 | -0.005371 | 0.019326 | 0.042849 | -0.013142 | 0.012548 | 0.024178 | 0.00086095 | 7.5119 | 7.4203 | 7.3059 | 7.5073 | 7.663 | 7.5211 | 7.5485 | 0.1236 | -0.013733 | -0.018311 | 0.059509 | 0.20599 | 0.16022 | 0.14648 | 7.37 | -114.9261 | -114.8392 | 7.7271 | 7.6126 | 7.5851 | 0.24262 | 0.21515 | 0.045776 | -122.3602 | -122.287 | 0.27008 | 0.21057 | 0.2243 | 0.16479 | 0.17853 | 0.35706 | 0.20142 | 0.22431 | 0.07782 | 0.11444 | 0.004578 | 7.4844 | 0.050354 | -115.0406 | -122.3648 | 7.5714 | 0.1236 | 7.576 | 0.18768
4810.5312 | 122.5204 | -0.050354 | 122.3511 | -0.01976 | 0.013796 | 0.010916 | -0.006586 | 0.0029351 | -0.008562 | -0.002382 | -0.0084228 | 0.021463 | 0.042208 | -0.0080151 | 0.012548 | 0.023537 | -0.00042085 | 7.4249 | 7.3563 | 7.2189 | 7.4249 | 7.5348 | 7.3883 | 7.4158 | 0.091553 | -0.018311 | -0.022888 | 0.064087 | 0.15564 | 0.11902 | 0.16022 | 7.2693 | -114.9948 | -114.9261 | 7.5851 | 7.4661 | 7.4387 | 0.19684 | 0.16937 | 0.027466 | -122.3694 | -122.287 | 0.20599 | 0.21057 | 0.16937 | 0.1831 | 0.14191 | 0.31586 | 0.20599 | 0.17853 | 0.086975 | 0.13733 | 0.004577 | 7.4066 | 0.032043 | -115.1321 | -122.374 | 7.4753 | 0.11444 | 7.4753 | 0.14191
4812.2969 | 122.5159 | -0.054932 | 122.3236 | -0.01976 | 0.01465 | 0.012412 | -0.008295 | -0.0011237 | -0.010485 | -0.005159 | -0.011475 | 0.019326 | 0.042849 | -0.013569 | 0.013403 | 0.02546 | 6.346e-06 | 7.4066 | 7.3196 | 7.2098 | 7.3883 | 7.5302 | 7.3471 | 7.402 | 0.10986 | -0.018311 | -0.004578 | 0.07782 | 0.16937 | 0.11902 | 0.13275 | 7.2647 | -115.004 | -114.9353 | 7.5851 | 7.457 | 7.402 | 0.19226 | 0.13733 | 0.050354 | -122.3419 | -122.2458 | 0.22431 | 0.18768 | 0.17395 | 0.13733 | 0.1236 | 0.32043 | 0.17853 | 0.17395 | 0.082398 | 0.10986 | -0.013733 | 7.3746 | 0.036621 | -115.1138 | -122.3282 | 7.4432 | 0.13275 | 7.4615 | 0.16479
4814.0156 | 122.4014 | -0.10986 | 122.3694 | -0.01976 | 0.011019 | 0.0089936 | -0.008295 | 0.0014397 | -0.011553 | -0.0049454 | -0.005371 | 0.020822 | 0.041567 | -0.011647 | 0.014257 | 0.022255 | -0.0057615 | 7.4936 | 7.4615 | 7.3013 | 7.4478 | 7.5714 | 7.4387 | 7.4615 | -0.018311 | 0.013733 | -0.036621 | -0.054932 | 0.045776 | 0.027466 | 0.041199 | 7.4112 | -114.9078 | -114.9216 | 7.6813 | 7.5714 | 7.5485 | 0.16022 | 0.13733 | 0.073242 | -122.3557 | -122.4243 | 0.15564 | 0.15106 | 0.13733 | 0.07782 | 0.064087 | 0.27008 | 0.14648 | 0.082397 | -0.018311 | 0.16022 | 0.050354 | 7.5714 | 0.1236 | -115.0681 | -122.406 | 7.5577 | 0.054931 | 7.6035 | 0.091552
4815.7812 | 122.4884 | -0.073242 | 122.3511 | -0.01976 | 0.012728 | 0.00878 | -0.0091494 | -0.0011237 | -0.008562 | -0.0043046 | -0.0084228 | 0.018899 | 0.040071 | -0.016987 | 0.011907 | 0.023537 | -0.0046933 | 7.3792 | 7.3517 | 7.2235 | 7.3746 | 7.489 | 7.3471 | 7.3975 | 0.027466 | -0.018311 | -0.036621 | 0.009155 | 0.10071 | 0.086975 | 0.086975 | 7.2968 | -114.9994 | -114.9765 | 7.5623 | 7.4707 | 7.4203 | 0.17395 | 0.1236 | 0.036621 | -122.3694 | -122.3419 | 0.17395 | 0.16022 | 0.16022 | 0.1236 | 0.1236 | 0.2655 | 0.15106 | 0.13733 | 0.045776 | 0.12817 | 0.01831 | 7.4249 | 0.054931 | -115.1276 | -122.3877 | 7.4478 | 0.082397 | 7.4524 | 0.10071
4817.5469 | 122.3923 | -0.11444 | 122.3785 | -0.01976 | 0.015291 | 0.011771 | -0.0067996 | 0.0042169 | -0.011125 | -0.0025956 | -0.0084228 | 0.022103 | 0.042208 | -0.0092969 | 0.013616 | 0.022042 | -0.0036253 | 7.3425 | 7.3792 | 7.196 | 7.2784 | 7.3517 | 7.2327 | 7.2693 | -0.073242 | 0.032043 | -0.054932 | -0.059509 | 0.013733 | -0.022888 | 0.036621 | 7.3105 | -114.9994 | -115.1001 | 7.4661 | 7.3837 | 7.3471 | 0.073242 | 0.036621 | 0.059509 | -122.3465 | -122.438 | 0.12817 | 0.15106 | 0.091553 | 0.091553 | 0.032044 | 0.15564 | 0.082397 | 0.068665 | -0.004577 | 0.18311 | 0.086975 | 7.4936 | 0.14648 | -115.1825 | -122.4335 | 7.3929 | 0.054932 | 7.457 | 0.041199
4819.3281 | 122.4701 | -0.073242 | 122.3511 | -0.01976 | 0.013155 | 0.010703 | -0.0070132 | 0.0020807 | -0.010271 | -0.0028092 | -0.005371 | 0.020181 | 0.040712 | -0.015919 | 0.012334 | 0.025673 | -0.0046933 | 7.3837 | 7.3242 | 7.196 | 7.3746 | 7.4936 | 7.3425 | 7.3792 | 0.07782 | -0.013733 | -0.009155 | 0.027466 | 0.11444 | 0.086975 | 0.10529 | 7.2693 | -115.0269 | -114.9765 | 7.5668 | 7.4524 | 7.4158 | 0.18311 | 0.14648 | 0.064087 | -122.3648 | -122.3236 | 0.18768 | 0.17853 | 0.16022 | 0.11444 | 0.09613 | 0.29755 | 0.17853 | 0.1236 | 0.036621 | 0.12817 | -0.004578 | 7.3975 | 0.059509 | -115.155 | -122.3602 | 7.4478 | 0.10071 | 7.457 | 0.15106
4821.1094 | 122.5388 | -0.054932 | 122.3373 | -0.01976 | 0.015078 | 0.011343 | -0.006586 | 0.0016535 | -0.0098438 | 0.0001816 | -0.0084228 | 0.019754 | 0.043917 | -0.022114 | 0.014257 | 0.023751 | 0.00043375 | 7.3837 | 7.2922 | 7.1686 | 7.3654 | 7.4661 | 7.2968 | 7.3654 | 0.1236 | -0.013733 | -0.009155 | 0.082397 | 0.16479 | 0.13275 | 0.14191 | 7.2235 | -115.0452 | -114.9719 | 7.5211 | 7.4203 | 7.3517 | 0.19684 | 0.12817 | 0.045777 | -122.3511 | -122.2549 | 0.21973 | 0.19684 | 0.18768 | 0.15106 | 0.14191 | 0.29755 | 0.19684 | 0.17395 | 0.091552 | 0.1236 | -0.004578 | 7.3471 | 0.041199 | -115.1688 | -122.3465 | 7.4203 | 0.13733 | 7.4387 | 0.17853
4822.8281 | 122.4701 | -0.073242 | 122.3831 | -0.012131 | 0.010591 | 0.009848 | -0.0087222 | -0.00069646 | -0.010057 | -0.0011002 | -0.005371 | 0.018686 | 0.042421 | -0.021687 | 0.01383 | 0.022683 | -0.0012753 | 7.338 | 7.2784 | 7.1732 | 7.3288 | 7.4432 | 7.2876 | 7.3334 | 0.041199 | -0.004578 | -0.032043 | 0.009155 | 0.10986 | 0.082397 | 0.10529 | 7.2464 | -115.1047 | -115.0543 | 7.5165 | 7.4066 | 7.3608 | 0.16022 | 0.11444 | 0.041199 | -122.3877 | -122.374 | 0.18311 | 0.17853 | 0.15564 | 0.13733 | 0.11444 | 0.27008 | 0.15564 | 0.14191 | 0.041198 | 0.10529 | 0.027465 | 7.3517 | 0.068664 | -115.21 | -122.4152 | 7.402 | 0.082397 | 7.4112 | 0.11444
4824.6094 | 122.4609 | -0.091553 | 122.374 | -0.012131 | 0.015078 | 0.0079254 | -0.0061588 | 0.0014397 | -0.0079212 | -0.0057998 | -0.005371 | 0.020395 | 0.043489 | -0.015919 | 0.015325 | 0.024178 | -0.0049069 | 7.283 | 7.3196 | 7.1182 | 7.2327 | 7.3288 | 7.1823 | 7.2327 | 0.009155 | 0.022888 | -0.036621 | -0.018311 | 0.054932 | 0.041199 | 0.082397 | 7.2098 | -115.0543 | -115.1413 | 7.4203 | 7.3242 | 7.2739 | 0.11444 | 0.064087 | 0.054932 | -122.3511 | -122.3923 | 0.14649 | 0.17395 | 0.13275 | 0.11902 | 0.07782 | 0.21057 | 0.11444 | 0.091553 | 0.01831 | 0.20142 | 0.059509 | 7.4112 | 0.11444 | -115.2557 | -122.4106 | 7.3242 | 0.073242 | 7.3746 | 0.10071
4826.375 | 122.4243 | -0.09613 | 122.3969 | -0.012131 | 0.010591 | 0.010489 | -0.0072268 | 0.00058534 | -0.0087756 | -0.005159 | -0.0084228 | 0.020822 | 0.042208 | -0.01656 | 0.012121 | 0.024391 | -0.0036253 | 7.4295 | 7.3746 | 7.2189 | 7.3746 | 7.4936 | 7.3792 | 7.3975 | 0.009155 | 0.013733 | -0.045776 | -0.059509 | 0.059509 | 0.027466 | 0.027466 | 7.3151 | -115.0223 | -115.0223 | 7.5897 | 7.4936 | 7.4753 | 0.17853 | 0.16022 | 0.050354 | -122.3831 | -122.4564 | 0.15564 | 0.1236 | 0.1236 | 0.073242 | 0.073242 | 0.27466 | 0.15564 | 0.10528 | -0.013733 | 0.15564 | 0.059509 | 7.4707 | 0.10986 | -115.1779 | -122.4426 | 7.4707 | 0.036621 | 7.5256 | 0.10528
4828.0781 | 122.4014 | -0.10071 | 122.374 | -0.02739 | 0.015505 | 0.011771 | -0.005945 | 0.0044305 | -0.0092028 | -0.002382 | -0.005371 | 0.023385 | 0.043276 | -0.017842 | 0.01383 | 0.023537 | -0.0023435 | 7.338 | 7.3608 | 7.1548 | 7.2601 | 7.3837 | 7.2235 | 7.2601 | -0.022888 | 0.045776 | -0.036621 | -0.036621 | 0.036621 | -0.013733 | 0.022888 | 7.2556 | -115.0131 | -115.1138 | 7.4844 | 7.3608 | 7.3242 | 0.10529 | 0.068665 | 0.064087 | -122.3282 | -122.4106 | 0.13733 | 0.1236 | 0.086975 | 0.059509 | 0.022888 | 0.22888 | 0.10529 | 0.073242 | 0 | 0.20599 | 0.082397 | 7.4615 | 0.14648 | -115.2191 | -122.4106 | 7.3608 | 0.064087 | 7.4387 | 0.07782
4829.8438 | 122.3923 | -0.11444 | 122.4014 | -0.01976 | 0.015078 | 0.01113 | -0.0070132 | 0.0052851 | -0.0094164 | -0.0036636 | -0.005371 | 0.020395 | 0.041353 | -0.0095105 | 0.011053 | 0.024178 | -0.0014891 | 7.2556 | 7.3059 | 7.0999 | 7.1732 | 7.2784 | 7.1411 | 7.1823 | -0.082397 | 0.032043 | -0.068665 | -0.059509 | 0.009155 | -0.022888 | 0.036621 | 7.2144 | -115.0955 | -115.2283 | 7.3929 | 7.2968 | 7.2556 | 0.082397 | 0.041198 | 0.045776 | -122.3694 | -122.4609 | 0.1236 | 0.15106 | 0.091553 | 0.10529 | 0.045777 | 0.17853 | 0.073242 | 0.07782 | 0.009156 | 0.20599 | 0.10071 | 7.4203 | 0.14648 | -115.3015 | -122.4701 | 7.2876 | 0.054932 | 7.37 | 0.032044
4831.625 | 122.4838 | -0.073242 | 122.3419 | -0.012131 | 0.010591 | 0.0094208 | -0.009363 | -0.00026906 | -0.011125 | -0.0028092 | -0.005371 | 0.019754 | 0.042849 | -0.016347 | 0.012121 | 0.024178 | -0.0057615 | 7.2693 | 7.2418 | 7.1045 | 7.2464 | 7.3792 | 7.2464 | 7.2922 | 0.004578 | 0.004578 | -0.027466 | -0.009155 | 0.10986 | 0.07782 | 0.09613 | 7.1777 | -115.1001 | -115.0955 | 7.4524 | 7.3654 | 7.3196 | 0.18768 | 0.14191 | 0.045776 | -122.3373 | -122.3511 | 0.18311 | 0.16937 | 0.15106 | 0.1236 | 0.10529 | 0.27466 | 0.14191 | 0.13733 | 0.018311 | 0.13733 | 0.032044 | 7.3151 | 0.07782 | -115.2374 | -122.3694 | 7.3196 | 0.064087 | 7.3425 | 0.07782
4833.3906 | 122.4655 | -0.10071 | 122.3694 | -0.012131 | 0.012514 | 0.0089936 | -0.0067996 | -0.0021919 | -0.0092028 | -0.0015274 | -0.011475 | 0.023599 | 0.040499 | -0.015919 | 0.015112 | 0.022255 | -0.0049069 | 7.3563 | 7.3563 | 7.1686 | 7.2876 | 7.3883 | 7.2693 | 7.2922 | 0 | 0.018311 | -0.054932 | -0.004578 | 0.09613 | 0.045776 | 0.064087 | 7.2693 | -115.0131 | -115.0818 | 7.489 | 7.3929 | 7.37 | 0.1236 | 0.10071 | 0.045776 | -122.3511 | -122.374 | 0.19684 | 0.1648 | 0.14648 | 0.11902 | 0.10071 | 0.21973 | 0.11902 | 0.15106 | 0.050354 | 0.18768 | 0.073243 | 7.457 | 0.11902 | -115.2008 | -122.4243 | 7.3883 | 0.09613 | 7.457 | 0.10071
4835.1094 | 122.5433 | -0.064087 | 122.3465 | -0.0045011 | 0.013582 | 0.011557 | -0.0078676 | 0.00015814 | -0.0074938 | -0.0045182 | -0.005371 | 0.019113 | 0.043917 | -0.013569 | 0.014257 | 0.023323 | -0.0019163 | 7.2647 | 7.196 | 7.0633 | 7.2418 | 7.3608 | 7.1915 | 7.2464 | 0.11444 | -0.009155 | -0.027466 | 0.068665 | 0.17853 | 0.14191 | 0.14648 | 7.1274 | -115.1505 | -115.1047 | 7.4249 | 7.3105 | 7.2556 | 0.18311 | 0.12817 | 0.036621 | -122.3557 | -122.2778 | 0.24261 | 0.21057 | 0.20599 | 0.17395 | 0.16937 | 0.29755 | 0.17853 | 0.20599 | 0.096131 | 0.13275 | 0.018311 | 7.2601 | 0.054932 | -115.2832 | -122.374 | 7.3059 | 0.13275 | 7.3288 | 0.17853
4836.875 | 122.4472 | -0.11444 | 122.3969 | -0.01976 | 0.014864 | 0.0092072 | -0.0061588 | 0.0050713 | -0.0089892 | -0.0030228 | -0.005371 | 0.021249 | 0.041994 | -0.0067333 | 0.014684 | 0.022683 | -0.0019163 | 7.2968 | 7.283 | 7.1228 | 7.2556 | 7.3792 | 7.2327 | 7.2556 | 0.027466 | -0.004578 | -0.032043 | -0.018311 | 0.082397 | 0.036621 | 0.064087 | 7.2372 | -115.1138 | -115.1413 | 7.4936 | 7.37 | 7.3471 | 0.13275 | 0.10986 | 0.082398 | -122.4014 | -122.4152 | 0.19684 | 0.17853 | 0.15106 | 0.09613 | 0.068664 | 0.25635 | 0.13275 | 0.11444 | 0.013732 | 0.16022 | 0.027465 | 7.3975 | 0.10986 | -115.274 | -122.4289 | 7.37 | 0.09613 | 7.4112 | 0.14191
4838.5781 | 122.5342 | -0.054932 | 122.3694 | -0.02739 | 0.015078 | 0.010703 | -0.0070132 | 0.0016535 | -0.0098438 | -0.0043046 | -0.0084228 | 0.020395 | 0.040926 | -0.020619 | 0.013616 | 0.024605 | -0.0025571 | 7.2327 | 7.1594 | 7.0404 | 7.2235 | 7.3517 | 7.1777 | 7.2281 | 0.091553 | 0 | -0.018311 | 0.059509 | 0.15564 | 0.12817 | 0.16479 | 7.0953 | -115.21 | -115.1459 | 7.4066 | 7.283 | 7.2327 | 0.18768 | 0.13733 | 0.036621 | -122.3694 | -122.3099 | 0.21057 | 0.21973 | 0.18311 | 0.18311 | 0.14649 | 0.31128 | 0.18311 | 0.17395 | 0.07782 | 0.11902 | 0.018311 | 7.2144 | 0.054932 | -115.329 | -122.3877 | 7.2784 | 0.11444 | 7.2876 | 0.14649
4840.3594 | 122.5571 | -0.064087 | 122.3557 | 0.0031279 | 0.0086688 | 0.010916 | -0.007654 | 0.00037174 | -0.011125 | -0.000673 | -0.011475 | 0.016763 | 0.042421 | -0.022542 | 0.010839 | 0.022683 | 0.00086095 | 7.2968 | 7.2235 | 7.1182 | 7.2922 | 7.457 | 7.3059 | 7.3471 | 0.13733 | -0.004578 | -0.018311 | 0.073242 | 0.19684 | 0.17395 | 0.14648 | 7.1823 | -115.1321 | -115.0635 | 7.5211 | 7.4112 | 7.37 | 0.22888 | 0.18768 | 0.045776 | -122.3602 | -122.2824 | 0.26093 | 0.21057 | 0.23804 | 0.16479 | 0.19226 | 0.33875 | 0.17395 | 0.21515 | 0.091553 | 0.10529 | 0.013733 | 7.2876 | 0.059509 | -115.2374 | -122.374 | 7.3563 | 0.13733 | 7.3608 | 0.20142
4842.0781 | 122.4197 | -0.11902 | 122.3648 | -0.01976 | 0.011232 | 0.0074982 | -0.0095766 | -0.00069646 | -0.010698 | -0.0032364 | -0.0084228 | 0.01954 | 0.040712 | -0.015278 | 0.011907 | 0.02546 | 0.0015017 | 7.2739 | 7.2968 | 7.1411 | 7.2189 | 7.3425 | 7.2098 | 7.2418 | -0.022888 | 0.018311 | -0.073242 | -0.07782 | 0.045776 | 0.027466 | 0.013733 | 7.2601 | -115.0681 | -115.1459 | 7.4615 | 7.3608 | 7.3288 | 0.10071 | 0.068665 | 0.045777 | -122.3465 | -122.4426 | 0.16479 | 0.13275 | 0.14649 | 0.086975 | 0.10071 | 0.20142 | 0.07782 | 0.11902 | -0.004578 | 0.15564 | 0.091553 | 7.4158 | 0.13733 | -115.2237 | -122.438 | 7.338 | 0.041199 | 7.3929 | 0.096131
4843.875 | 122.4335 | -0.10529 | 122.4014 | -0.01976 | 0.013796 | 0.0079254 | -0.0061588 | -5.5462e-05 | -0.008562 | -0.0038772 | -0.0084228 | 0.022531 | 0.041353 | -0.013356 | 0.01148 | 0.023751 | -0.0064023 | 7.2693 | 7.3288 | 7.1274 | 7.1915 | 7.2968 | 7.1823 | 7.2144 | -0.054932 | 0.032043 | -0.059509 | -0.045776 | 0.059509 | 0.013733 | 0.036621 | 7.2327 | -115.0726 | -115.21 | 7.402 | 7.3196 | 7.2876 | 0.086975 | 0.054932 | 0.045777 | -122.3694 | -122.4472 | 0.16479 | 0.14191 | 0.11902 | 0.09613 | 0.073242 | 0.16937 | 0.064087 | 0.11902 | 0.013733 | 0.20142 | 0.091552 | 7.4341 | 0.13733 | -115.274 | -122.4609 | 7.2968 | 0.05951 | 7.3746 | 0.050354
4845.6406 | 122.4014 | -0.11902 | 122.3877 | -0.012131 | 0.013796 | 0.0072846 | -0.010004 | 0.0016535 | -0.010485 | -0.0057998 | -0.0023192 | 0.020608 | 0.042635 | -0.018055 | 0.01148 | 0.023751 | 0.00021995 | 7.2281 | 7.2922 | 7.0999 | 7.1869 | 7.3105 | 7.1823 | 7.2189 | -0.064087 | 0.036621 | -0.041199 | -0.082397 | 0.032043 | 0.009155 | 0.032043 | 7.2189 | -115.0955 | -115.2008 | 7.4295 | 7.338 | 7.3013 | 0.11902 | 0.082397 | 0.07782 | -122.3511 | -122.4701 | 0.15106 | 0.15106 | 0.12817 | 0.073242 | 0.050354 | 0.21057 | 0.086975 | 0.073242 | -0.041198 | 0.19226 | 0.07782 | 7.4112 | 0.15564 | -115.2878 | -122.4289 | 7.3059 | 0.036622 | 7.3471 | 0.054932
4847.3594 | 122.4518 | -0.091553 | 122.3831 | -0.012131 | 0.010164 | 0.010062 | -0.010218 | 0.00037174 | -0.010057 | -0.0015274 | -0.0084228 | 0.020822 | 0.04178 | -0.018269 | 0.013403 | 0.021828 | -0.0059751 | 7.283 | 7.2281 | 7.1091 | 7.2556 | 7.3929 | 7.2647 | 7.2876 | 0.032043 | 0.018311 | -0.018311 | -0.036621 | 0.10529 | 0.045776 | 0.064087 | 7.2006 | -115.155 | -115.1276 | 7.4844 | 7.3792 | 7.3563 | 0.17853 | 0.15564 | 0.073242 | -122.3648 | -122.4197 | 0.19684 | 0.15564 | 0.13733 | 0.082398 | 0.064087 | 0.28381 | 0.14648 | 0.1236 | -0.01831 | 0.11902 | 0.036622 | 7.3196 | 0.10986 | -115.274 | -122.4014 | 7.3471 | 0.054932 | 7.3746 | 0.1236
4849.1562 | 122.5525 | -0.073242 | 122.3373 | -0.012131 | 0.011019 | 0.0085662 | -0.0091494 | -0.0011237 | -0.0098438 | -0.0036636 | 0.00073235 | 0.020395 | 0.042849 | -0.013356 | 0.010839 | 0.023323 | -0.0044797 | 7.2006 | 7.1548 | 7.0404 | 7.2281 | 7.3563 | 7.2281 | 7.2647 | 0.086975 | -0.018311 | -0.041199 | 0.054932 | 0.17395 | 0.16022 | 0.14648 | 7.1136 | -115.1825 | -115.1093 | 7.4295 | 7.338 | 7.3013 | 0.2243 | 0.18768 | 0.032043 | -122.3557 | -122.2824 | 0.24719 | 0.21973 | 0.23346 | 0.18768 | 0.20142 | 0.31586 | 0.18768 | 0.21515 | 0.096131 | 0.11444 | 0.022888 | 7.2281 | 0.054931 | -115.2969 | -122.3785 | 7.3013 | 0.12817 | 7.2739 | 0.16022
4850.9219 | 122.5296 | -0.059509 | 122.3557 | -0.012131 | 0.011446 | 0.010275 | -0.0087222 | -0.0032599 | -0.011125 | -0.0021682 | -0.0084228 | 0.018045 | 0.042635 | -0.022755 | 0.012334 | 0.022683 | -0.0027707 | 7.1823 | 7.164 | 7.0038 | 7.1823 | 7.3059 | 7.1732 | 7.2098 | 0.064087 | 0 | -0.032043 | 0.041199 | 0.16022 | 0.14191 | 0.13275 | 7.0633 | -115.1917 | -115.1733 | 7.3654 | 7.2693 | 7.2327 | 0.20599 | 0.16937 | 0.027466 | -122.3557 | -122.3145 | 0.21973 | 0.19226 | 0.20142 | 0.16479 | 0.17395 | 0.30212 | 0.17853 | 0.19226 | 0.073242 | 0.16022 | 0.032043 | 7.2235 | 0.059509 | -115.3519 | -122.3877 | 7.2418 | 0.10071 | 7.2418 | 0.1236
4852.6875 | 122.4289 | -0.10986 | 122.4152 | -0.012131 | 0.015078 | 0.012412 | -0.0057314 | 0.0010125 | -0.0089892 | -0.0025956 | -0.0084228 | 0.024026 | 0.042208 | -0.011006 | 0.013616 | 0.021187 | -0.0029843 | 7.0908 | 7.132 | 6.9717 | 7.0221 | 7.0953 | 6.9717 | 7.0267 | -0.054932 | 0.032043 | -0.045776 | -0.064087 | 0.013733 | -0.027466 | 0.050354 | 7.0816 | -115.2832 | -115.3931 | 7.2052 | 7.1365 | 7.0816 | 0.054931 | 0 | 0.064087 | -122.3831 | -122.4792 | 0.1236 | 0.16022 | 0.082397 | 0.09613 | 0.01831 | 0.1236 | 0.050354 | 0.059509 | -0.018311 | 0.16022 | 0.077819 | 7.2418 | 0.14191 | -115.4434 | -122.4609 | 7.132 | 0.045776 | 7.2006 | 0.054931
4854.4531 | 122.4747 | -0.10529 | 122.3785 | -0.0045011 | 0.010164 | 0.010916 | -0.0089358 | 0.0010125 | -0.011125 | -0.0045182 | -0.005371 | 0.018899 | 0.042421 | -0.020192 | 0.014898 | 0.022255 | -0.0031979 | 7.2372 | 7.1594 | 7.0541 | 7.2144 | 7.3334 | 7.2189 | 7.2372 | 0.054932 | -0.009155 | -0.032043 | -0.018311 | 0.10529 | 0.07782 | 0.07782 | 7.1594 | -115.2191 | -115.1642 | 7.4387 | 7.3425 | 7.3242 | 0.18311 | 0.16479 | 0.073243 | -122.3877 | -122.3969 | 0.21057 | 0.18311 | 0.18311 | 0.10986 | 0.10986 | 0.27924 | 0.16022 | 0.13733 | 0.013732 | 0.10529 | 0.022888 | 7.2647 | 0.096131 | -115.3244 | -122.4106 | 7.3196 | 0.086975 | 7.3425 | 0.16022
4856.1719 | 122.4792 | -0.09613 | 122.374 | -0.01976 | 0.01465 | 0.009848 | -0.0057314 | 0.0022943 | -0.0077074 | -0.001741 | -0.005371 | 0.021463 | 0.042635 | -0.013997 | 0.013616 | 0.022255 | -0.0036253 | 7.0679 | 7.1091 | 6.926 | 7.0084 | 7.1136 | 6.9717 | 7.0129 | -0.009155 | 0.027466 | -0.050354 | -0.027466 | 0.050354 | 0.009155 | 0.073242 | 7.0221 | -115.2649 | -115.3656 | 7.2098 | 7.1091 | 7.0679 | 0.086975 | 0.045777 | 0.045776 | -122.3465 | -122.4014 | 0.14648 | 0.16937 | 0.10528 | 0.1236 | 0.059509 | 0.18768 | 0.082398 | 0.10071 | 0.022888 | 0.18311 | 0.07782 | 7.2052 | 0.1236 | -115.448 | -122.4243 | 7.1045 | 0.068664 | 7.164 | 0.086975
4857.9375 | 122.5021 | -0.073242 | 122.3877 | -0.012131 | 0.010164 | 0.0089936 | -0.009363 | -0.0034735 | -0.012194 | -0.0038772 | -0.005371 | 0.01954 | 0.041353 | -0.014638 | 0.014043 | 0.022896 | -0.0010617 | 7.2052 | 7.132 | 7.0267 | 7.2052 | 7.3105 | 7.1823 | 7.2006 | 0.068665 | -0.032043 | -0.009155 | 0.013733 | 0.13733 | 0.11902 | 0.10529 | 7.0999 | -115.2557 | -115.1825 | 7.3837 | 7.2739 | 7.2556 | 0.17395 | 0.15564 | 0.064087 | -122.4197 | -122.374 | 0.21057 | 0.17853 | 0.19226 | 0.11444 | 0.12817 | 0.28381 | 0.17853 | 0.14648 | 0.022888 | 0.10529 | -0.022888 | 7.2052 | 0.041199 | -115.361 | -122.3969 | 7.2784 | 0.086975 | 7.2784 | 0.14191
4859.7188 | 122.5571 | -0.041199 | 122.3648 | -0.01976 | 0.0123 | 0.011343 | -0.0061588 | -0.0015509 | -0.0083484 | -0.0060134 | -0.005371 | 0.018686 | 0.040499 | -0.01891 | 0.014684 | 0.023537 | -0.0029843 | 7.0953 | 6.9992 | 6.9122 | 7.077 | 7.1869 | 7.0267 | 7.0587 | 0.11902 | -0.009155 | -0.013733 | 0.068665 | 0.15564 | 0.12817 | 0.15106 | 6.9534 | -115.3656 | -115.2878 | 7.2281 | 7.0999 | 7.0679 | 0.14649 | 0.11444 | 0.027466 | -122.374 | -122.2961 | 0.19684 | 0.19226 | 0.16937 | 0.16479 | 0.14191 | 0.27466 | 0.16479 | 0.16937 | 0.082398 | 0.086976 | 0.004578 | 7.0404 | 0.032044 | -115.4526 | -122.3785 | 7.1182 | 0.10986 | 7.1365 | 0.16022
4861.4844 | 122.4747 | -0.09613 | 122.3923 | -0.01976 | 0.015505 | 0.010489 | -0.0055178 | -0.0049689 | -0.00963 | -0.0057998 | -0.005371 | 0.01954 | 0.043489 | -0.013356 | 0.012121 | 0.024178 | -0.0044797 | 7.0221 | 7.0541 | 6.8802 | 6.9809 | 7.077 | 6.9122 | 6.9717 | -0.027466 | 0.009155 | -0.041199 | -0.013733 | 0.054932 | 0.018311 | 0.07782 | 6.9763 | -115.3381 | -115.4114 | 7.1732 | 7.0679 | 7.0084 | 0.091553 | 0.032043 | 0.054931 | -122.3831 | -122.406 | 0.15106 | 0.17395 | 0.11444 | 0.11902 | 0.05951 | 0.19684 | 0.10071 | 0.096131 | 0.027466 | 0.17395 | 0.050354 | 7.1503 | 0.10528 | -115.5121 | -122.4335 | 7.077 | 0.082397 | 7.1182 | 0.068664
4863.1875 | 122.5021 | -0.064087 | 122.3557 | -0.02739 | 0.014864 | 0.01113 | -0.0070132 | 0.0020807 | -0.00963 | -0.002382 | 0.00073235 | 0.020395 | 0.043276 | -0.022114 | 0.012762 | 0.023751 | -0.0046933 | 7.0541 | 6.9901 | 6.8939 | 7.0587 | 7.1915 | 7.0221 | 7.0724 | 0.11444 | -0.013733 | -0.018311 | 0.045776 | 0.15564 | 0.13275 | 0.13733 | 6.958 | -115.3656 | -115.2969 | 7.2556 | 7.1365 | 7.0862 | 0.17853 | 0.12817 | 0.045776 | -122.3694 | -122.3099 | 0.21973 | 0.20142 | 0.19684 | 0.15564 | 0.15106 | 0.29755 | 0.1648 | 0.17395 | 0.064087 | 0.09613 | 0.004578 | 7.0541 | 0.050354 | -115.4617 | -122.374 | 7.1228 | 0.10986 | 7.1182 | 0.17853
4864.9688 | 122.4701 | -0.073242 | 122.3969 | -0.012131 | 0.015078 | 0.0079254 | -0.0046634 | 0.0035761 | -0.008562 | -0.001741 | -0.005371 | 0.021249 | 0.041994 | -0.013569 | 0.015752 | 0.022469 | -0.0029843 | 7.1182 | 7.1228 | 6.9534 | 7.0724 | 7.1686 | 7.045 | 7.0679 | 0.050354 | 0.013733 | -0.018311 | -0.004578 | 0.09613 | 0.064087 | 0.082397 | 7.0267 | -115.274 | -115.3244 | 7.2418 | 7.1411 | 7.1182 | 0.11444 | 0.091553 | 0.054931 | -122.3831 | -122.4014 | 0.16937 | 0.15564 | 0.13733 | 0.10071 | 0.082398 | 0.21515 | 0.11902 | 0.11444 | 0.013733 | 0.16937 | 0.032044 | 7.196 | 0.086975 | -115.4434 | -122.4152 | 7.1457 | 0.068664 | 7.1915 | 0.1236
4866.7344 | 122.4792 | -0.086975 | 122.4014 | -0.02739 | 0.015078 | 0.011343 | -0.0070132 | 0.0016535 | -0.0083484 | -0.0025956 | -0.011475 | 0.019326 | 0.04178 | -0.013569 | 0.011266 | 0.023964 | -0.0055479 | 7.0038 | 7.045 | 6.8619 | 6.9489 | 7.0587 | 6.9031 | 6.9397 | -0.009155 | 0.018311 | -0.041199 | -0.004578 | 0.07782 | 0.045776 | 0.091553 | 6.9489 | -115.3564 | -115.4526 | 7.1457 | 7.0267 | 6.9901 | 0.07782 | 0.041199 | 0.045776 | -122.3831 | -122.406 | 0.16479 | 0.17853 | 0.13275 | 0.13275 | 0.086975 | 0.19684 | 0.086976 | 0.11902 | 0.036621 | 0.18311 | 0.05951 | 7.132 | 0.10529 | -115.5396 | -122.4426 | 7.0358 | 0.082397 | 7.0908 | 0.07782
4868.4375 | 122.5159 | -0.050354 | 122.3877 | -0.01976 | 0.011446 | 0.010489 | -0.010431 | 0.0027215 | -0.0081348 | -0.0036636 | -0.005371 | 0.016122 | 0.041567 | -0.015492 | 0.01148 | 0.022896 | -0.0061887 | 7.0221 | 6.9946 | 6.8756 | 7.0129 | 7.1365 | 6.9809 | 7.0267 | 0.050354 | -0.009155 | -0.036621 | 0.018311 | 0.1236 | 0.073242 | 0.09613 | 6.926 | -115.3931 | -115.3748 | 7.1869 | 7.077 | 7.0312 | 0.15106 | 0.10529 | 0.013733 | -122.3969 | -122.3694 | 0.17395 | 0.14648 | 0.1236 | 0.13275 | 0.10986 | 0.26093 | 0.13733 | 0.16022 | 0.054932 | 0.11902 | 0.027466 | 7.045 | 0.041199 | -115.5121 | -122.4243 | 7.0633 | 0.068665 | 7.0724 | 0.10071
4870.2188 | 122.4426 | -0.10986 | 122.4106 | -0.01976 | 0.011232 | 0.010275 | -0.010218 | -0.0017645 | -0.011553 | -0.0032364 | -0.0084228 | 0.019967 | 0.041994 | -0.012715 | 0.011694 | 0.022042 | -0.0078977 | 7.0999 | 7.0908 | 6.9489 | 7.0358 | 7.164 | 7.0312 | 7.0633 | -0.022888 | 0.004578 | -0.054932 | -0.064087 | 0.050354 | 0.018311 | 0.022888 | 7.0587 | -115.3198 | -115.3748 | 7.2739 | 7.1732 | 7.1411 | 0.11444 | 0.082397 | 0.054931 | -122.406 | -122.4747 | 0.16022 | 0.13275 | 0.12817 | 0.07782 | 0.073243 | 0.21515 | 0.086975 | 0.10529 | -0.009155 | 0.14191 | 0.05951 | 7.2006 | 0.11444 | -115.4617 | -122.4655 | 7.1457 | 0.045776 | 7.2098 | 0.086975
4871.9375 | 122.4243 | -0.10986 | 122.4014 | -0.01976 | 0.0086688 | 0.0085662 | -0.0087222 | 0.0040033 | -0.011766 | -0.00345 | -0.011475 | 0.02189 | 0.043276 | -0.020192 | 0.012334 | 0.022255 | -0.0064023 | 7.077 | 7.1045 | 6.9077 | 6.9992 | 7.132 | 7.0221 | 7.045 | -0.064087 | 0.036621 | -0.045776 | -0.064087 | 0.050354 | 0.013733 | 0.027466 | 7.0175 | -115.2969 | -115.4022 | 7.2418 | 7.1548 | 7.132 | 0.13733 | 0.11444 | 0.064087 | -122.3648 | -122.4655 | 0.16022 | 0.13733 | 0.1236 | 0.073242 | 0.059509 | 0.2243 | 0.091553 | 0.09613 | -0.018311 | 0.19684 | 0.082397 | 7.2144 | 0.14648 | -115.4938 | -122.4472 | 7.1091 | 0.045776 | 7.1869 | 0.045776
4873.7188 | 122.4197 | -0.10986 | 122.4152 | -0.0045011 | 0.014864 | 0.010489 | -0.0061588 | 0.0029351 | -0.0089892 | -0.0053726 | -0.0084228 | 0.020608 | 0.042635 | -0.012929 | 0.014684 | 0.022683 | -0.0040525 | 6.9992 | 7.0267 | 6.8527 | 6.9077 | 7.0084 | 6.8527 | 6.8893 | -0.059509 | 0.018311 | -0.050354 | -0.07782 | 0.013733 | -0.027466 | 0.032043 | 6.9626 | -115.3885 | -115.5075 | 7.1182 | 6.9992 | 6.9626 | 0.036621 | 0 | 0.059509 | -122.3969 | -122.493 | 0.1236 | 0.14191 | 0.082397 | 0.082397 | 0.022888 | 0.15564 | 0.054932 | 0.064087 | -0.027466 | 0.17395 | 0.068665 | 7.1365 | 0.12817 | -115.5624 | -122.4655 | 7.0175 | 0.032043 | 7.1091 | 0.050354
4875.4219 | 122.5159 | -0.082397 | 122.4014 | -0.01976 | 0.010805 | 0.0096344 | -0.008295 | -0.0030463 | -0.010698 | -0.0032364 | -0.0084228 | 0.019113 | 0.042849 | -0.016987 | 0.012334 | 0.024819 | -0.0029843 | 6.9672 | 6.9626 | 6.8344 | 6.9534 | 7.0724 | 6.9489 | 6.9901 | 0.004578 | -0.009155 | -0.036621 | 0.009155 | 0.11902 | 0.073242 | 0.07782 | 6.9168 | -115.4388 | -115.448 | 7.1548 | 7.0724 | 7.0312 | 0.15564 | 0.11444 | 0.045776 | -122.4106 | -122.3923 | 0.20142 | 0.16022 | 0.15564 | 0.11444 | 0.10986 | 0.23804 | 0.11902 | 0.15564 | 0.045776 | 0.12817 | 0.027466 | 7.045 | 0.073242 | -115.567 | -122.438 | 7.0358 | 0.091552 | 7.0496 | 0.086975
4877.1875 | 122.4838 | -0.10529 | 122.3969 | -0.0045011 | 0.012514 | 0.010916 | -0.0070132 | 0.0016535 | -0.0089892 | -0.0030228 | -0.0023192 | 0.020181 | 0.043917 | -0.015492 | 0.014684 | 0.02076 | -0.0061887 | 7.0541 | 7.0633 | 6.8893 | 6.9855 | 7.0999 | 6.9672 | 6.9763 | 0.022888 | 0.027466 | -0.045776 | -0.013733 | 0.091553 | 0.054932 | 0.09613 | 6.9946 | -115.3336 | -115.4114 | 7.2052 | 7.0816 | 7.0724 | 0.086975 | 0.07782 | 0.05951 | -122.3694 | -122.4106 | 0.19684 | 0.20142 | 0.16022 | 0.14191 | 0.10071 | 0.21057 | 0.096131 | 0.13733 | 0.032043 | 0.17395 | 0.073242 | 7.1686 | 0.13275 | -115.5075 | -122.4426 | 7.0908 | 0.091553 | 7.1594 | 0.12817
4878.9688 | 122.5662 | -0.054932 | 122.3923 | -0.01976 | 0.015078 | 0.011557 | -0.0089358 | -0.0011237 | -0.0077074 | -0.0021682 | -0.005371 | 0.019754 | 0.04178 | -0.0099377 | 0.013403 | 0.02546 | -0.0010617 | 6.9763 | 6.871 | 6.7795 | 6.9397 | 7.0633 | 6.8939 | 6.9534 | 0.10529 | -0.018311 | -0.013733 | 0.07782 | 0.17853 | 0.12817 | 0.14191 | 6.8344 | -115.5212 | -115.4526 | 7.1182 | 7.0084 | 6.9489 | 0.17395 | 0.11444 | 0.041199 | -122.4106 | -122.3145 | 0.23346 | 0.19684 | 0.18311 | 0.15564 | 0.14191 | 0.28381 | 0.16022 | 0.19226 | 0.091553 | 0.091553 | -0.004578 | 6.926 | 0.036621 | -115.6128 | -122.406 | 6.9946 | 0.13275 | 7.0312 | 0.16022
4880.6875 | 122.4335 | -0.11902 | 122.4197 | -0.01976 | 0.009096 | 0.0092072 | -0.009363 | -0.0026191 | -0.011339 | -0.0030228 | -0.0023192 | 0.02189 | 0.042208 | -0.022542 | 0.012548 | 0.026528 | -0.0034117 | 6.9809 | 7.0404 | 6.871 | 6.9305 | 7.0587 | 6.9305 | 6.9763 | -0.068665 | 0.041199 | -0.068665 | -0.086975 | 0.050354 | 0.018311 | 0.013733 | 6.9901 | -115.3793 | -115.4892 | 7.1777 | 7.0953 | 7.0496 | 0.10529 | 0.059509 | 0.050354 | -122.3785 | -122.5067 | 0.16937 | 0.13275 | 0.13733 | 0.082398 | 0.086976 | 0.18768 | 0.059509 | 0.11902 | -0.01831 | 0.16937 | 0.10986 | 7.1594 | 0.16022 | -115.5487 | -122.4884 | 7.0496 | 0.032044 | 7.0999 | 0.050354
4882.4531 | 122.525 | -0.068665 | 122.3877 | -0.012131 | 0.016146 | 0.012198 | -0.0089358 | 0.0031487 | -0.008562 | -0.0040908 | -0.0084228 | 0.018258 | 0.044771 | -0.018696 | 0.012334 | 0.022255 | -0.0044797 | 6.9397 | 6.8756 | 6.7749 | 6.926 | 7.0633 | 6.8802 | 6.9397 | 0.10071 | -0.022888 | -0.022888 | 0.036621 | 0.11902 | 0.086975 | 0.11902 | 6.8436 | -115.5121 | -115.4617 | 7.132 | 7.0084 | 6.9489 | 0.16479 | 0.10529 | 0.045777 | -122.4106 | -122.3511 | 0.18768 | 0.18768 | 0.15564 | 0.14191 | 0.10986 | 0.28839 | 0.15106 | 0.14191 | 0.059509 | 0.10071 | 0 | 6.9443 | 0.045777 | -115.6128 | -122.4106 | 6.9946 | 0.10529 | 7.0084 | 0.16937
4884.2344 | 122.5113 | -0.054932 | 122.4014 | -0.01976 | 0.012514 | 0.0092072 | -0.0097904 | 0.0020807 | -0.011339 | -0.0043046 | -0.011475 | 0.018899 | 0.042208 | -0.017628 | 0.010839 | 0.022896 | -0.0038389 | 6.9031 | 6.839 | 6.7749 | 6.8893 | 7.0084 | 6.871 | 6.9214 | 0.050354 | 0.004578 | -0.018311 | 0.004578 | 0.10529 | 0.091553 | 0.10071 | 6.8298 | -115.5624 | -115.5121 | 7.0633 | 6.9763 | 6.926 | 0.14649 | 0.096131 | 0.036621 | -122.3969 | -122.3969 | 0.16022 | 0.15564 | 0.14649 | 0.11902 | 0.10986 | 0.23346 | 0.11444 | 0.1236 | 0.022889 | 0.064087 | 0.022889 | 6.8939 | 0.05951 | -115.6265 | -122.4197 | 6.9443 | 0.05951 | 6.958 | 0.10529
4886.0156 | 122.5845 | -0.054932 | 122.3831 | -0.0045011 | 0.0088824 | 0.0083526 | -0.0087222 | -0.00069646 | -0.010057 | -0.0040908 | -0.005371 | 0.020822 | 0.041353 | -0.017201 | 0.011266 | 0.021187 | -0.0064023 | 7.0129 | 6.9214 | 6.8253 | 7.0221 | 7.1594 | 7.0084 | 7.0404 | 0.12817 | 0.018311 | -0.013733 | 0.054932 | 0.19226 | 0.16022 | 0.12817 | 6.8802 | -115.4617 | -115.361 | 7.2144 | 7.0953 | 7.0633 | 0.21515 | 0.18311 | 0.041199 | -122.3648 | -122.3282 | 0.24719 | 0.18311 | 0.21515 | 0.14191 | 0.17395 | 0.33417 | 0.19684 | 0.20599 | 0.068665 | 0.096131 | 0.032044 | 6.9763 | 0.073243 | -115.5579 | -122.3969 | 7.077 | 0.10986 | 7.0679 | 0.18311
4887.7344 | 122.5845 | -0.068665 | 122.3877 | -0.01976 | 0.0093098 | 0.010703 | -0.009363 | -0.0015509 | -0.01198 | -0.00345 | -0.005371 | 0.018045 | 0.041353 | -0.018269 | 0.012548 | 0.022683 | -0.00063445 | 6.9809 | 6.8985 | 6.8253 | 6.9855 | 7.1411 | 6.9901 | 7.0084 | 0.12817 | -0.004578 | -0.018311 | 0.054932 | 0.20599 | 0.16479 | 0.13275 | 6.8939 | -115.4892 | -115.4022 | 7.2098 | 7.077 | 7.0587 | 0.18311 | 0.16479 | 0.050354 | -122.3923 | -122.3328 | 0.27466 | 0.20142 | 0.23346 | 0.15106 | 0.18311 | 0.31586 | 0.16022 | 0.22431 | 0.073243 | 0.073243 | 0.013733 | 6.9672 | 0.064087 | -115.5624 | -122.406 | 7.0541 | 0.1236 | 7.0496 | 0.19684
4889.4531 | 122.58 | -0.064087 | 122.3694 | -0.0045011 | 0.010164 | 0.0074982 | -0.0091494 | -0.0013373 | -0.008562 | -0.0028092 | -0.0084228 | 0.020608 | 0.040285 | -0.013356 | 0.012334 | 0.024178 | -0.0017027 | 6.9305 | 6.8802 | 6.7749 | 6.9489 | 7.077 | 6.9397 | 6.9946 | 0.11902 | -0.004578 | -0.022888 | 0.059509 | 0.18768 | 0.16022 | 0.14648 | 6.839 | -115.4892 | -115.4205 | 7.1411 | 7.0587 | 7.0038 | 0.21973 | 0.16479 | 0.041199 | -122.374 | -122.3099 | 0.25177 | 0.21057 | 0.2243 | 0.16937 | 0.1831 | 0.30212 | 0.17395 | 0.21057 | 0.082397 | 0.10529 | 0.01831 | 6.9443 | 0.059509 | -115.5945 | -122.3923 | 7.0129 | 0.1236 | 6.9946 | 0.18311
4891.2344 | 122.4289 | -0.091553 | 122.4289 | -0.012131 | 0.014223 | 0.01113 | -0.004877 | 0.0027215 | -0.0087756 | -0.0028092 | -0.014526 | 0.021463 | 0.04114 | -0.012074 | 0.015325 | 0.022255 | -0.0049069 | 6.8802 | 6.8802 | 6.7291 | 6.7932 | 6.9077 | 6.7383 | 6.7886 | -0.041199 | 0.018311 | -0.036621 | -0.050354 | 0.027466 | -0.018311 | 0.022888 | 6.8207 | -115.5487 | -115.6357 | 6.9992 | 6.8802 | 6.8298 | 0.059509 | 0.009155 | 0.054932 | -122.4106 | -122.4792 | 0.11902 | 0.11444 | 0.073242 | 0.059509 | 0.01831 | 0.17853 | 0.064087 | 0.064087 | -0.013733 | 0.15106 | 0.054932 | 6.9717 | 0.10986 | -115.6998 | -122.4655 | 6.8848 | 0.041199 | 6.9717 | 0.050354
4893 | 122.4838 | -0.10071 | 122.4335 | -0.01976 | 0.011232 | 0.010489 | -0.0074404 | -0.0013373 | -0.010698 | -0.0070816 | -0.0084228 | 0.020822 | 0.041994 | -0.016347 | 0.014471 | 0.024178 | -0.0042661 | 6.9122 | 6.9351 | 6.7749 | 6.8573 | 6.9489 | 6.8527 | 6.8756 | -0.050354 | 0.032043 | -0.059509 | -0.036621 | 0.07782 | 0.022888 | 0.068665 | 6.8756 | -115.4984 | -115.5762 | 7.0496 | 6.9763 | 6.9534 | 0.10071 | 0.07782 | 0.041199 | -122.4014 | -122.4701 | 0.17853 | 0.16937 | 0.1236 | 0.12817 | 0.082397 | 0.17395 | 0.082398 | 0.13733 | 0.022888 | 0.16022 | 0.091552 | 7.0358 | 0.13275 | -115.6586 | -122.493 | 6.958 | 0.064087 | 7.0129 | 0.050354
4894.7656 | 122.438 | -0.09613 | 122.4518 | -0.012131 | 0.015718 | 0.010062 | -0.0055178 | -0.00026906 | -0.0087756 | -0.0038772 | -0.0084228 | 0.022317 | 0.041567 | -0.013783 | 0.015752 | 0.025032 | -0.0042661 | 6.7978 | 6.8161 | 6.6788 | 6.6971 | 6.7978 | 6.6742 | 6.7245 | -0.068665 | 0.032043 | -0.054932 | -0.059509 | 0.009155 | -0.022888 | 0.018311 | 6.7749 | -115.6357 | -115.7547 | 6.8939 | 6.8207 | 6.7703 | 0.045776 | -0.004578 | 0.041198 | -122.4197 | -122.5113 | 0.10528 | 0.11444 | 0.073242 | 0.073243 | 0.032044 | 0.11902 | 0.018311 | 0.064087 | -0.004577 | 0.13733 | 0.086975 | 6.9122 | 0.12817 | -115.773 | -122.5067 | 6.7932 | 0.036621 | 6.8939 | 0.027465
4896.4844 | 122.5754 | -0.07782 | 122.3602 | -0.012131 | 0.0123 | 0.0079254 | -0.011072 | -0.0019781 | -0.011766 | -0.0013138 | -0.005371 | 0.018258 | 0.041353 | -0.020405 | 0.013189 | 0.024391 | -0.0031979 | 6.8481 | 6.8115 | 6.7062 | 6.8573 | 6.9717 | 6.8619 | 6.8985 | 0.07782 | -0.018311 | -0.027466 | 0.054932 | 0.16937 | 0.14648 | 0.14191 | 6.7841 | -115.5487 | -115.5029 | 7.0496 | 6.9763 | 6.9397 | 0.19226 | 0.15564 | 0.050354 | -122.3785 | -122.3053 | 0.24719 | 0.21973 | 0.2243 | 0.16937 | 0.17395 | 0.2655 | 0.15106 | 0.19684 | 0.082398 | 0.10529 | 0.009155 | 6.8893 | 0.059509 | -115.654 | -122.3877 | 6.9351 | 0.13275 | 6.926 | 0.15564
4898.25 | 122.5433 | -0.054932 | 122.3923 | -0.02739 | 0.01465 | 0.009848 | -0.009363 | -0.00026906 | -0.010271 | -0.005159 | -0.005371 | 0.020181 | 0.042849 | -0.014424 | 0.01148 | 0.023323 | -0.0049069 | 6.8115 | 6.7612 | 6.6559 | 6.8115 | 6.926 | 6.7749 | 6.8161 | 0.10529 | -0.004578 | 0.004578 | 0.041199 | 0.14191 | 0.09613 | 0.11902 | 6.7108 | -115.6311 | -115.5808 | 6.9809 | 6.871 | 6.8298 | 0.16022 | 0.11902 | 0.05951 | -122.3969 | -122.3511 | 0.19684 | 0.17395 | 0.15106 | 0.11444 | 0.091552 | 0.27008 | 0.15564 | 0.13733 | 0.036621 | 0.10528 | -0.009156 | 6.8161 | 0.050354 | -115.7364 | -122.3877 | 6.8665 | 0.096131 | 6.8665 | 0.16022
4899.9531 | 122.5616 | -0.07782 | 122.4152 | -0.012131 | 0.011446 | 0.009848 | -0.0080814 | -0.0019781 | -0.010057 | -0.0043046 | -0.0084228 | 0.019754 | 0.042421 | -0.015065 | 0.0087029 | 0.023751 | -0.0044797 | 6.8253 | 6.7886 | 6.6879 | 6.8253 | 6.9397 | 6.8069 | 6.8619 | 0.059509 | -0.009155 | -0.027466 | 0.041199 | 0.15564 | 0.13275 | 0.12817 | 6.7657 | -115.6265 | -115.5899 | 7.0175 | 6.9397 | 6.8848 | 0.17395 | 0.11902 | 0.050354 | -122.4243 | -122.374 | 0.23346 | 0.20599 | 0.21057 | 0.15564 | 0.16022 | 0.25177 | 0.13733 | 0.18311 | 0.068665 | 0.10071 | 0.018311 | 6.8665 | 0.068665 | -115.7272 | -122.4426 | 6.9031 | 0.11902 | 6.9031 | 0.13733
4901.7344 | 122.5296 | -0.068665 | 122.4197 | -0.012131 | 0.012514 | 0.00878 | -0.008295 | 0.0022943 | -0.010698 | -0.0021682 | -0.0023192 | 0.020181 | 0.04178 | -0.019124 | 0.012334 | 0.023964 | -0.0046933 | 6.7703 | 6.7383 | 6.6376 | 6.7612 | 6.871 | 6.7474 | 6.8069 | 0.041199 | -0.018311 | -0.036621 | 0.004578 | 0.11444 | 0.082397 | 0.091553 | 6.7062 | -115.6815 | -115.6586 | 6.9397 | 6.8756 | 6.8161 | 0.16937 | 0.10986 | 0.032044 | -122.4381 | -122.4152 | 0.18311 | 0.16022 | 0.15106 | 0.12817 | 0.11902 | 0.23346 | 0.1236 | 0.15106 | 0.041199 | 0.10071 | 0.01831 | 6.8069 | 0.050354 | -115.7822 | -122.4564 | 6.8298 | 0.073243 | 6.839 | 0.10986
4903.5 | 122.58 | -0.059509 | 122.4289 | -0.012131 | 0.010591 | 0.010489 | -0.0087222 | -0.00048286 | -0.010057 | -0.0030228 | -0.0084228 | 0.01954 | 0.043703 | -0.019978 | 0.01148 | 0.022896 | -0.0055479 | 6.8161 | 6.7657 | 6.6605 | 6.8253 | 6.9397 | 6.8207 | 6.8481 | 0.086975 | -0.022888 | -0.018311 | 0.045776 | 0.17395 | 0.14191 | 0.14191 | 6.72 | -115.6631 | -115.6036 | 6.9992 | 6.9077 | 6.8802 | 0.18768 | 0.16022 | 0.041198 | -122.4518 | -122.3831 | 0.23346 | 0.20142 | 0.20142 | 0.16022 | 0.16022 | 0.27924 | 0.1648 | 0.19226 | 0.064087 | 0.10529 | -0.004577 | 6.8253 | 0.036621 | -115.7684 | -122.4472 | 6.8848 | 0.10528 | 6.8756 | 0.14648
4905.2031 | 122.5342 | -0.09613 | 122.3969 | -0.012131 | 0.012941 | 0.0085662 | -0.0067996 | 0.0037897 | -0.00963 | -0.0019546 | -0.005371 | 0.020395 | 0.040071 | -0.015919 | 0.014043 | 0.025032 | -0.0010617 | 6.7383 | 6.7108 | 6.6193 | 6.7429 | 6.8665 | 6.7154 | 6.752 | 0.041199 | 0.009155 | -0.027466 | 0.018311 | 0.10529 | 0.091553 | 0.091553 | 6.7154 | -115.686 | -115.654 | 6.9626 | 6.8481 | 6.8115 | 0.13275 | 0.09613 | 0.068664 | -122.3877 | -122.3785 | 0.20142 | 0.18768 | 0.18768 | 0.11902 | 0.11902 | 0.24719 | 0.1236 | 0.13275 | 0.045777 | 0.091552 | 0.036621 | 6.8069 | 0.10528 | -115.7776 | -122.4243 | 6.839 | 0.11444 | 6.8344 | 0.13733
4906.9688 | 122.5342 | -0.082397 | 122.4014 | -0.01976 | 0.011232 | 0.010489 | -0.0070132 | -0.00091006 | -0.01198 | -0.0038772 | -0.005371 | 0.020822 | 0.041353 | -0.017415 | 0.012334 | 0.023323 | -0.0034117 | 6.7474 | 6.7017 | 6.633 | 6.7429 | 6.8298 | 6.6971 | 6.7566 | 0.018311 | -0.009155 | -0.041199 | 0.009155 | 0.10986 | 0.073242 | 0.086975 | 6.7154 | -115.6998 | -115.6586 | 6.9122 | 6.839 | 6.7795 | 0.1236 | 0.064087 | 0.041198 | -122.4106 | -122.3923 | 0.19226 | 0.16937 | 0.15564 | 0.12817 | 0.11444 | 0.19684 | 0.10986 | 0.15106 | 0.050354 | 0.068664 | 0.032044 | 6.7841 | 0.073242 | -115.7684 | -122.4426 | 6.8253 | 0.091552 | 6.8298 | 0.10071
4908.75 | 122.5525 | -0.082397 | 122.4289 | -0.01976 | 0.0095234 | 0.0074982 | -0.0087222 | -0.0017645 | -0.0089892 | -0.0015274 | -0.0084228 | 0.020181 | 0.042208 | -0.010579 | 0.010626 | 0.021614 | -0.0029843 | 6.8344 | 6.7337 | 6.6879 | 6.839 | 6.9809 | 6.8298 | 6.8436 | 0.09613 | -0.004578 | -0.027466 | 0.027466 | 0.16022 | 0.1236 | 0.11902 | 6.7703 | -115.6952 | -115.5899 | 7.0633 | 6.926 | 6.9122 | 0.15564 | 0.14191 | 0.054931 | -122.4335 | -122.4014 | 0.24261 | 0.20142 | 0.20599 | 0.14649 | 0.15106 | 0.29297 | 0.15106 | 0.18768 | 0.054932 | 0.045777 | 0.022888 | 6.8161 | 0.077819 | -115.741 | -122.4564 | 6.9214 | 0.10986 | 6.9168 | 0.17853
4910.4688 | 122.5937 | -0.059509 | 122.4014 | -0.012131 | 0.014437 | 0.0096344 | -0.0061588 | 0.0018671 | -0.0072802 | -0.0036636 | -0.011475 | 0.019754 | 0.04114 | -0.015706 | 0.014043 | 0.023323 | 0.00021995 | 6.7429 | 6.6513 | 6.5643 | 6.72 | 6.8161 | 6.6742 | 6.7062 | 0.10529 | -0.004578 | -0.022888 | 0.082397 | 0.16022 | 0.11444 | 0.14648 | 6.6238 | -115.7501 | -115.6815 | 6.8756 | 6.7657 | 6.7337 | 0.14191 | 0.10986 | 0.036621 | -122.406 | -122.319 | 0.21973 | 0.20599 | 0.17395 | 0.16937 | 0.13733 | 0.25177 | 0.15564 | 0.1831 | 0.10528 | 0.086975 | 0.01831 | 6.7108 | 0.054931 | -115.8371 | -122.4243 | 6.7795 | 0.14191 | 6.8024 | 0.16479
4912.2344 | 122.4564 | -0.11444 | 122.4426 | -0.012131 | 0.015505 | 0.0096344 | -0.0078676 | 0.0033623 | -0.0094164 | -0.005159 | -0.0023192 | 0.022744 | 0.04178 | -0.0095105 | 0.015966 | 0.021187 | -0.0049069 | 6.7566 | 6.7612 | 6.6147 | 6.6788 | 6.7749 | 6.6284 | 6.6467 | -0.013733 | 0.032043 | -0.050354 | -0.032043 | 0.032043 | -0.009155 | 0.032043 | 6.7291 | -115.6815 | -115.7639 | 6.8893 | 6.7612 | 6.7429 | 0.032044 | 0.013733 | 0.064087 | -122.4106 | -122.4747 | 0.14648 | 0.14648 | 0.10529 | 0.082397 | 0.041199 | 0.16022 | 0.064087 | 0.082397 | 0.018311 | 0.14648 | 0.082397 | 6.8756 | 0.14648 | -115.8279 | -122.493 | 6.7932 | 0.082398 | 6.871 | 0.10071
4914 | 122.5113 | -0.09613 | 122.4518 | -0.02739 | 0.010378 | 0.0083526 | -0.0074404 | 0.00015814 | -0.010912 | -0.0045182 | -0.005371 | 0.020608 | 0.041994 | -0.018269 | 0.012548 | 0.023751 | -0.0029843 | 6.8207 | 6.752 | 6.6559 | 6.7841 | 6.9168 | 6.7795 | 6.8069 | 0.032043 | 0.004578 | -0.054932 | -0.027466 | 0.10071 | 0.054932 | 0.073242 | 6.752 | -115.6998 | -115.6677 | 7.0129 | 6.9031 | 6.8756 | 0.15106 | 0.1236 | 0.041198 | -122.4472 | -122.4792 | 0.19684 | 0.16937 | 0.15106 | 0.12817 | 0.10986 | 0.26092 | 0.12817 | 0.15564 | 0.027466 | 0.09613 | 0.05951 | 6.8481 | 0.10071 | -115.7959 | -122.5067 | 6.8802 | 0.068664 | 6.9168 | 0.12817
4915.7188 | 122.4976 | -0.091553 | 122.4243 | -0.012131 | 0.014009 | 0.010489 | -0.0061588 | 0.00037174 | -0.0092028 | -0.0030228 | -0.0084228 | 0.021249 | 0.041994 | -0.017842 | 0.014684 | 0.024391 | -0.0019163 | 6.6513 | 6.6788 | 6.5369 | 6.5964 | 6.6879 | 6.5369 | 6.5964 | -0.022888 | 0.022888 | -0.064087 | -0.004578 | 0.059509 | 0.032043 | 0.068665 | 6.6284 | -115.7455 | -115.8279 | 6.7795 | 6.6879 | 6.6284 | 0.05951 | 0 | 0.027466 | -122.4014 | -122.4289 | 0.15106 | 0.16022 | 0.1236 | 0.13275 | 0.09613 | 0.15106 | 0.05951 | 0.1236 | 0.059509 | 0.14191 | 0.086975 | 6.7703 | 0.11444 | -115.8875 | -122.4884 | 6.6879 | 0.086975 | 6.7429 | 0.068665
4917.4844 | 122.5204 | -0.082397 | 122.4014 | -0.01976 | 0.011873 | 0.010703 | -0.0087222 | -0.0032599 | -0.012621 | -0.0045182 | -0.0084228 | 0.018472 | 0.041567 | -0.018055 | 0.013616 | 0.0261 | -0.0029843 | 6.6605 | 6.6467 | 6.5552 | 6.6696 | 6.7703 | 6.633 | 6.6879 | 0.013733 | -0.004578 | -0.018311 | 0.004578 | 0.09613 | 0.068665 | 0.082397 | 6.6376 | -115.7547 | -115.7318 | 6.8527 | 6.7703 | 6.7154 | 0.13275 | 0.07782 | 0.064086 | -122.406 | -122.3969 | 0.17853 | 0.16479 | 0.15106 | 0.10071 | 0.086976 | 0.21515 | 0.11444 | 0.11444 | 0.022889 | 0.091553 | 0.013733 | 6.7291 | 0.077819 | -115.8463 | -122.4197 | 6.752 | 0.086975 | 6.7429 | 0.09613
4919.2031 | 122.5479 | -0.064087 | 122.3877 | -0.0045011 | 0.012514 | 0.010062 | -0.007654 | 0.0010125 | -0.00963 | -0.0030228 | -0.005371 | 0.020181 | 0.040926 | -0.016347 | 0.013403 | 0.02311 | -0.0019163 | 6.665 | 6.5872 | 6.5231 | 6.665 | 6.8024 | 6.633 | 6.6833 | 0.11444 | -0.018311 | -0.022888 | 0.054932 | 0.13733 | 0.11444 | 0.13275 | 6.5872 | -115.8005 | -115.7227 | 6.8665 | 6.7474 | 6.6971 | 0.16022 | 0.10986 | 0.041199 | -122.406 | -122.3328 | 0.20142 | 0.19684 | 0.17853 | 0.15564 | 0.13733 | 0.27924 | 0.14191 | 0.16022 | 0.07782 | 0.064087 | 0.004577 | 6.6513 | 0.045776 | -115.8646 | -122.4106 | 6.7291 | 0.11902 | 6.7291 | 0.17853
4920.9688 | 122.5433 | -0.068665 | 122.4197 | -0.012131 | 0.013582 | 0.010916 | -0.0087222 | 0.0012261 | -0.010271 | -0.002382 | -0.011475 | 0.016977 | 0.041567 | -0.019124 | 0.012334 | 0.024178 | -0.00063445 | 6.6605 | 6.6422 | 6.5506 | 6.665 | 6.7795 | 6.6513 | 6.6925 | 0.036621 | -0.009155 | -0.027466 | 0.009155 | 0.11444 | 0.07782 | 0.091553 | 6.6193 | -115.7776 | -115.7547 | 6.8481 | 6.7612 | 6.72 | 0.14191 | 0.10071 | 0.041199 | -122.4289 | -122.4106 | 0.18311 | 0.16022 | 0.14649 | 0.11902 | 0.10529 | 0.22888 | 0.11444 | 0.14191 | 0.036621 | 0.091553 | 0.018311 | 6.7108 | 0.05951 | -115.8691 | -122.4472 | 6.7337 | 0.07782 | 6.7291 | 0.10529
4922.75 | 122.4884 | -0.10071 | 122.406 | -0.02739 | 0.013155 | 0.010062 | -0.0067996 | 0.0031487 | -0.011339 | -0.0013138 | -0.011475 | 0.022744 | 0.042849 | -0.014638 | 0.013403 | 0.022683 | -0.0049069 | 6.633 | 6.6422 | 6.5002 | 6.5689 | 6.6605 | 6.5186 | 6.5598 | -0.018311 | 0.032043 | -0.036621 | -0.027466 | 0.041199 | -0.009155 | 0.050354 | 6.601 | -115.7639 | -115.8371 | 6.7612 | 6.6605 | 6.6193 | 0.059509 | 0.018311 | 0.064087 | -122.374 | -122.4335 | 0.14191 | 0.15106 | 0.091553 | 0.086975 | 0.027466 | 0.16022 | 0.068665 | 0.07782 | 0.009155 | 0.14191 | 0.068664 | 6.7429 | 0.13275 | -115.9058 | -122.4426 | 6.6696 | 0.073242 | 6.7337 | 0.082397
4924.4531 | 122.5891 | -0.045776 | 122.3969 | -0.02739 | 0.014223 | 0.012839 | -0.0057314 | 0.0022943 | -0.0072802 | -0.0038772 | -0.005371 | 0.020181 | 0.041994 | -0.010151 | 0.012334 | 0.022255 | -0.0029843 | 6.6788 | 6.5918 | 6.5094 | 6.6467 | 6.7474 | 6.5964 | 6.6376 | 0.11902 | -0.013733 | 0 | 0.082397 | 0.17395 | 0.1236 | 0.15106 | 6.5552 | -115.8051 | -115.7501 | 6.7932 | 6.6833 | 6.6422 | 0.12817 | 0.086976 | 0.045776 | -122.4106 | -122.3145 | 0.21973 | 0.19684 | 0.16937 | 0.15106 | 0.1236 | 0.23804 | 0.13733 | 0.17395 | 0.082397 | 0.082398 | -0.013733 | 6.6376 | 0.032043 | -115.8875 | -122.3969 | 6.6925 | 0.12817 | 6.7245 | 0.16479
4926.2344 | 122.5891 | -0.064087 | 122.4152 | -0.012131 | 0.010591 | 0.008139 | -0.0067996 | -0.0013373 | -0.0098438 | -0.0015274 | -0.005371 | 0.020181 | 0.039217 | -0.018269 | 0.01383 | 0.025887 | -0.0066159 | 6.752 | 6.6788 | 6.5872 | 6.7566 | 6.8985 | 6.7703 | 6.7749 | 0.091553 | 0.004578 | -0.013733 | 0.064087 | 0.18768 | 0.15106 | 0.14191 | 6.6513 | -115.7364 | -115.6586 | 6.9626 | 6.839 | 6.8344 | 0.18768 | 0.18311 | 0.050354 | -122.4106 | -122.3511 | 0.25177 | 0.20599 | 0.21515 | 0.15564 | 0.16479 | 0.31128 | 0.16937 | 0.20142 | 0.07782 | 0.091553 | 0.018311 | 6.7429 | 0.068665 | -115.8279 | -122.4289 | 6.8207 | 0.12817 | 6.8161 | 0.15564
4928 | 122.6074 | -0.059509 | 122.4426 | -0.012131 | 0.015078 | 0.0096344 | -0.0061588 | 0.0054987 | -0.0079212 | -0.00345 | -0.011475 | 0.018258 | 0.042635 | -0.01656 | 0.013616 | 0.023537 | -0.00084805 | 6.6559 | 6.5414 | 6.4865 | 6.633 | 6.752 | 6.5781 | 6.6193 | 0.11902 | 0 | -0.004578 | 0.073242 | 0.16022 | 0.12817 | 0.12817 | 6.546 | -115.9012 | -115.8096 | 6.8115 | 6.6788 | 6.6376 | 0.13275 | 0.091553 | 0.054931 | -122.4426 | -122.3694 | 0.21973 | 0.18768 | 0.18768 | 0.13275 | 0.13275 | 0.2655 | 0.14649 | 0.16479 | 0.07782 | 0.054932 | 0.004578 | 6.601 | 0.059509 | -115.9561 | -122.4472 | 6.6925 | 0.13275 | 6.7154 | 0.17853
4929.7656 | 122.5433 | -0.086975 | 122.4197 | -0.01976 | 0.015078 | 0.0085662 | -0.0074404 | -0.00048286 | -0.011125 | -0.002382 | -0.011475 | 0.01954 | 0.041567 | -0.021687 | 0.012334 | 0.02311 | -0.0025571 | 6.6147 | 6.5735 | 6.4819 | 6.6101 | 6.7291 | 6.5689 | 6.6238 | 0.059509 | 0.004578 | -0.027466 | 0.004578 | 0.10529 | 0.091553 | 0.10529 | 6.5689 | -115.8463 | -115.8096 | 6.8161 | 6.7108 | 6.6559 | 0.14191 | 0.086975 | 0.059509 | -122.4152 | -122.4152 | 0.19226 | 0.19226 | 0.17853 | 0.13275 | 0.11902 | 0.24719 | 0.12817 | 0.13275 | 0.032044 | 0.091552 | 0.032044 | 6.6605 | 0.091553 | -115.9378 | -122.4472 | 6.6971 | 0.091553 | 6.7017 | 0.14648
4931.5469 | 122.4792 | -0.10986 | 122.4564 | -0.0045011 | 0.014009 | 0.011343 | -0.0055178 | 0.0025079 | -0.01198 | -0.0025956 | -0.005371 | 0.022958 | 0.043489 | -0.012288 | 0.014684 | 0.023964 | -0.0044797 | 6.6788 | 6.6376 | 6.5231 | 6.5964 | 6.7108 | 6.5414 | 6.5872 | 0.009155 | 0.027466 | -0.045776 | -0.022888 | 0.050354 | 0.013733 | 0.041199 | 6.633 | -115.8188 | -115.86 | 6.8207 | 6.6971 | 6.6513 | 0.064087 | 0.018311 | 0.064087 | -122.4289 | -122.4792 | 0.16022 | 0.15106 | 0.1236 | 0.086975 | 0.059509 | 0.18768 | 0.073243 | 0.09613 | 0.022888 | 0.11444 | 0.073242 | 6.7474 | 0.13733 | -115.9332 | -122.5021 | 6.7062 | 0.086975 | 6.7886 | 0.11902
4933.3125 | 122.5983 | -0.064087 | 122.4014 | -0.012131 | 0.012728 | 0.0094208 | -0.0087222 | -0.0015509 | -0.010698 | -0.0043046 | -0.011475 | 0.017617 | 0.039858 | -0.016347 | 0.012548 | 0.025032 | -0.0021299 | 6.6879 | 6.6376 | 6.5369 | 6.7154 | 6.8527 | 6.6833 | 6.72 | 0.10986 | -0.009155 | -0.022888 | 0.064087 | 0.1831 | 0.16022 | 0.12817 | 6.601 | -115.7639 | -115.686 | 6.9168 | 6.7841 | 6.7474 | 0.18311 | 0.14649 | 0.041199 | -122.4106 | -122.3373 | 0.24719 | 0.19226 | 0.2243 | 0.15106 | 0.1831 | 0.31586 | 0.17853 | 0.20599 | 0.086975 | 0.10071 | 0.013733 | 6.7017 | 0.054932 | -115.8646 | -122.4243 | 6.7795 | 0.12817 | 6.752 | 0.17395
4935.0312 | 122.4838 | -0.10986 | 122.438 | -0.012131 | 0.011019 | 0.009848 | -0.0087222 | -0.00069646 | -0.011125 | -0.0011002 | -0.0084228 | 0.020395 | 0.044344 | -0.015706 | 0.013616 | 0.023537 | -0.0034117 | 6.6376 | 6.6742 | 6.5414 | 6.5918 | 6.72 | 6.5826 | 6.6055 | -0.050354 | 0.018311 | -0.059509 | -0.07782 | 0.050354 | 0.022888 | 0.032043 | 6.6513 | -115.7639 | -115.8463 | 6.8298 | 6.7154 | 6.6925 | 0.064087 | 0.041199 | 0.050354 | -122.4197 | -122.5159 | 0.16022 | 0.14191 | 0.13275 | 0.091552 | 0.082397 | 0.17853 | 0.050354 | 0.10986 | -0.018311 | 0.13275 | 0.07782 | 6.7841 | 0.12817 | -115.8966 | -122.4976 | 6.7017 | 0.032043 | 6.7474 | 0.059509
4936.8281 | 122.5525 | -0.073242 | 122.4106 | -0.01976 | 0.0123 | 0.010916 | -0.008295 | -0.0013373 | -0.011553 | -0.0038772 | -0.0084228 | 0.019113 | 0.042208 | -0.020619 | 0.011053 | 0.025032 | 0.0012881 | 6.5872 | 6.5048 | 6.4407 | 6.5735 | 6.6742 | 6.5323 | 6.5689 | 0.086975 | -0.009155 | -0.009155 | 0.018311 | 0.1236 | 0.091553 | 0.091553 | 6.514 | -115.9058 | -115.8371 | 6.7474 | 6.6422 | 6.6055 | 0.12817 | 0.091553 | 0.064087 | -122.4197 | -122.3923 | 0.19684 | 0.16479 | 0.16479 | 0.10071 | 0.10071 | 0.23346 | 0.13275 | 0.13275 | 0.027466 | 0.064087 | 0 | 6.5781 | 0.064087 | -115.9698 | -122.4197 | 6.6467 | 0.091553 | 6.6605 | 0.16022
4938.5469 | 122.5845 | -0.068665 | 122.4243 | -0.012131 | 0.011019 | 0.0096344 | -0.008295 | 0.0046441 | -0.011553 | -0.0025956 | -0.011475 | 0.020181 | 0.040285 | -0.026814 | 0.01148 | 0.022683 | -0.0029843 | 6.5735 | 6.5506 | 6.4636 | 6.5781 | 6.6788 | 6.5506 | 6.6055 | 0.054932 | 0 | -0.036621 | 0.027466 | 0.14191 | 0.11902 | 0.11902 | 6.5323 | -115.8737 | -115.8463 | 6.7474 | 6.6742 | 6.6193 | 0.14191 | 0.086975 | 0.032044 | -122.4243 | -122.3969 | 0.21057 | 0.18768 | 0.18768 | 0.15564 | 0.15564 | 0.21515 | 0.11444 | 0.17853 | 0.064087 | 0.086975 | 0.036621 | 6.6193 | 0.068665 | -115.9607 | -122.4609 | 6.6467 | 0.096131 | 6.6422 | 0.1236
4940.3125 | 122.493 | -0.09613 | 122.4747 | -0.0045011 | 0.013582 | 0.011557 | -0.0042362 | 0.0022943 | -0.0081348 | -0.006868 | -0.005371 | 0.022317 | 0.040499 | -0.015065 | 0.014257 | 0.023964 | -0.00042085 | 6.6101 | 6.5918 | 6.4636 | 6.5369 | 6.633 | 6.4911 | 6.5186 | 0.004578 | 0.041199 | -0.045776 | -0.036621 | 0.045776 | 0 | 0.050354 | 6.5598 | -115.8829 | -115.9378 | 6.7291 | 6.6147 | 6.5872 | 0.054932 | 0.027466 | 0.050354 | -122.4335 | -122.5113 | 0.14191 | 0.14648 | 0.09613 | 0.09613 | 0.045776 | 0.16937 | 0.073242 | 0.091552 | 0.009155 | 0.12817 | 0.086975 | 6.6879 | 0.13733 | -116.011 | -122.5204 | 6.633 | 0.059509 | 6.7062 | 0.10071
4942.0938 | 122.438 | -0.12817 | 122.4518 | -0.01976 | 0.015932 | 0.011984 | -0.0055178 | -0.00048286 | -0.00963 | -0.0066544 | -0.0084228 | 0.023172 | 0.042421 | -0.012715 | 0.015112 | 0.022896 | -0.0023435 | 6.5231 | 6.5506 | 6.4224 | 6.427 | 6.5048 | 6.3812 | 6.4224 | -0.091553 | 0.036621 | -0.054932 | -0.054932 | 0.004578 | -0.032043 | 0.032043 | 6.5506 | -115.9012 | -116.0248 | 6.633 | 6.5506 | 6.5094 | 0 | -0.041198 | 0.073242 | -122.4152 | -122.5067 | 0.13275 | 0.16022 | 0.096131 | 0.086975 | 0.022889 | 0.082398 | 0.004578 | 0.05951 | 0 | 0.12817 | 0.091553 | 6.6788 | 0.1648 | -116.0294 | -122.5067 | 6.5552 | 0.073242 | 6.6513 | 0.036621
4943.875 | 122.4701 | -0.10986 | 122.4335 | -0.035019 | 0.017641 | 0.01113 | -0.0070132 | 0.0022943 | -0.0098438 | -0.002382 | -0.005371 | 0.019113 | 0.043489 | -0.010151 | 0.014257 | 0.023537 | -0.0038389 | 6.5689 | 6.5735 | 6.4407 | 6.4911 | 6.5918 | 6.4407 | 6.4774 | -0.032043 | 0.045776 | -0.036621 | -0.050354 | 0.036621 | -0.009155 | 0.027466 | 6.5506 | -115.86 | -115.9424 | 6.7017 | 6.5872 | 6.5506 | 0.036621 | 0 | 0.073242 | -122.3877 | -122.4838 | 0.14648 | 0.13733 | 0.10071 | 0.064087 | 0.027466 | 0.15106 | 0.050354 | 0.073242 | -0.013733 | 0.13275 | 0.082397 | 6.6833 | 0.15564 | -115.9927 | -122.4701 | 6.601 | 0.059509 | 6.6788 | 0.07782
4945.5938 | 122.4884 | -0.10071 | 122.4426 | -0.012131 | 0.012941 | 0.011557 | -0.0053042 | 0.0016535 | -0.0089892 | -0.0028092 | -0.0023192 | 0.022958 | 0.042635 | -0.014851 | 0.015112 | 0.026528 | -0.0029843 | 6.4774 | 6.5186 | 6.3721 | 6.3904 | 6.5094 | 6.3629 | 6.4133 | -0.064087 | 0.036621 | -0.064087 | -0.050354 | 0.022888 | -0.013733 | 0.041199 | 6.4728 | -115.9241 | -116.0522 | 6.6101 | 6.514 | 6.4636 | 0.041199 | -0.009155 | 0.036621 | -122.406 | -122.493 | 0.1236 | 0.14191 | 0.086975 | 0.10529 | 0.050354 | 0.13733 | 0.018311 | 0.086975 | 0.013733 | 0.14649 | 0.10071 | 6.6193 | 0.13733 | -116.0706 | -122.5067 | 6.4911 | 0.050354 | 6.5781 | 0.036621
4947.3594 | 122.5113 | -0.091553 | 122.4655 | -0.01976 | 0.010164 | 0.0079254 | -0.006586 | 0.0025079 | -0.011553 | -0.0049454 | -0.005371 | 0.023385 | 0.04178 | -0.01421 | 0.014684 | 0.025246 | -0.0046933 | 6.6055 | 6.6193 | 6.4636 | 6.5414 | 6.6513 | 6.5277 | 6.5506 | -0.013733 | 0.027466 | -0.041199 | -0.013733 | 0.091553 | 0.050354 | 0.086975 | 6.5552 | -115.8463 | -115.9241 | 6.7429 | 6.6422 | 6.6193 | 0.086975 | 0.064087 | 0.050354 | -122.438 | -122.4792 | 0.18311 | 0.17853 | 0.14191 | 0.12817 | 0.091553 | 0.18768 | 0.07782 | 0.13275 | 0.027466 | 0.15564 | 0.068665 | 6.7108 | 0.11902 | -116.0019 | -122.5067 | 6.633 | 0.07782 | 6.6971 | 0.07782
4949.1406 | 122.493 | -0.10071 | 122.4701 | -0.0045011 | 0.014437 | 0.01113 | -0.007654 | 0.0033623 | -0.0079212 | -0.0025956 | -0.005371 | 0.022744 | 0.043276 | -0.013783 | 0.014257 | 0.024605 | -0.0029843 | 6.5552 | 6.5552 | 6.427 | 6.4819 | 6.6101 | 6.4545 | 6.4728 | -0.018311 | 0.018311 | -0.068665 | -0.032043 | 0.054932 | 0.009155 | 0.041199 | 6.5277 | -115.9149 | -115.9882 | 6.7108 | 6.5735 | 6.5552 | 0.045776 | 0.027466 | 0.032043 | -122.4518 | -122.5021 | 0.15564 | 0.14191 | 0.10986 | 0.10986 | 0.07782 | 0.18311 | 0.054932 | 0.1236 | 0.036622 | 0.12817 | 0.086976 | 6.6559 | 0.11902 | -116.0431 | -122.5388 | 6.5826 | 0.068665 | 6.6559 | 0.082397
4950.9219 | 122.4838 | -0.10986 | 122.4564 | -0.01976 | 0.0099506 | 0.0094208 | -0.008295 | -0.0017645 | -0.011553 | -0.0047318 | -0.0084228 | 0.019754 | 0.042208 | -0.019978 | 0.013189 | 0.022896 | -0.0014891 | 6.5369 | 6.5872 | 6.4362 | 6.4957 | 6.6284 | 6.5186 | 6.546 | -0.068665 | 0.022888 | -0.073242 | -0.082397 | 0.032043 | 0.022888 | 0.018311 | 6.546 | -115.8691 | -115.9607 | 6.7383 | 6.6559 | 6.6284 | 0.10986 | 0.082398 | 0.036621 | -122.4335 | -122.5388 | 0.14191 | 0.12817 | 0.13275 | 0.091553 | 0.09613 | 0.19226 | 0.05951 | 0.10529 | -0.009155 | 0.15106 | 0.09613 | 6.6971 | 0.13275 | -116.0202 | -122.5296 | 6.6055 | 0.027466 | 6.6467 | 0.041198
4952.7031 | 122.5296 | -0.091553 | 122.4884 | -0.01976 | 0.015078 | 0.0096344 | -0.0057314 | 0.00058534 | -0.00963 | -0.0043046 | -0.005371 | 0.022103 | 0.044771 | -0.01421 | 0.012975 | 0.025246 | 0.0019289 | 6.5643 | 6.546 | 6.3995 | 6.4957 | 6.633 | 6.4865 | 6.5002 | 0.054932 | 0.027466 | -0.045776 | -0.013733 | 0.082397 | 0.041199 | 0.086975 | 6.4911 | -115.9424 | -115.9927 | 6.7245 | 6.5918 | 6.5781 | 0.10071 | 0.086975 | 0.045777 | -122.4609 | -122.5021 | 0.17395 | 0.17853 | 0.13275 | 0.13275 | 0.086975 | 0.23346 | 0.096131 | 0.12817 | 0.032043 | 0.14648 | 0.073242 | 6.6376 | 0.11902 | -116.0889 | -122.5342 | 6.5872 | 0.07782 | 6.6559 | 0.14649
4954.4219 | 122.5296 | -0.10071 | 122.4472 | -0.0045011 | 0.011873 | 0.0096344 | -0.006586 | 0.0020807 | -0.010485 | -0.0062272 | -0.0023192 | 0.019326 | 0.042208 | -0.012501 | 0.014684 | 0.024178 | -0.0044797 | 6.5552 | 6.5323 | 6.4041 | 6.4865 | 6.6193 | 6.4728 | 6.4865 | 0.022888 | 0.032043 | -0.041199 | -0.013733 | 0.09613 | 0.059509 | 0.073242 | 6.5048 | -115.9149 | -115.9607 | 6.72 | 6.5872 | 6.5735 | 0.082397 | 0.068664 | 0.059509 | -122.4152 | -122.4609 | 0.19684 | 0.17395 | 0.16022 | 0.11444 | 0.10071 | 0.21515 | 0.082397 | 0.13733 | 0.027466 | 0.12817 | 0.073242 | 6.633 | 0.13275 | -116.0431 | -122.4884 | 6.5872 | 0.086975 | 6.6559 | 0.1236
4956.2031 | 122.5662 | -0.091553 | 122.4518 | -0.012131 | 0.013369 | 0.009848 | -0.0067996 | 0.0031487 | -0.0092028 | -0.0043046 | -0.005371 | 0.020608 | 0.041994 | -0.016987 | 0.014257 | 0.025673 | -0.0027707 | 6.4362 | 6.4407 | 6.2942 | 6.3583 | 6.4728 | 6.3217 | 6.3675 | 0.013733 | 0.013733 | -0.041199 | 0 | 0.10986 | 0.054932 | 0.09613 | 6.3858 | -116.011 | -116.0934 | 6.5643 | 6.459 | 6.4133 | 0.073243 | 0.027466 | 0.050354 | -122.438 | -122.4518 | 0.20142 | 0.18768 | 0.14649 | 0.13733 | 0.096131 | 0.17853 | 0.064087 | 0.15106 | 0.041199 | 0.14649 | 0.054932 | 6.5323 | 0.10529 | -116.1575 | -122.493 | 6.4499 | 0.091553 | 6.5277 | 0.10529
4957.9688 | 122.6166 | -0.059509 | 122.4152 | -0.01976 | 0.013796 | 0.01113 | -0.0067996 | 0.0016535 | -0.0087756 | -0.002382 | -0.0023192 | 0.018045 | 0.042421 | -0.018696 | 0.012975 | 0.023964 | 0.0032107 | 6.4407 | 6.3766 | 6.3034 | 6.4316 | 6.546 | 6.4087 | 6.4362 | 0.10529 | 0.013733 | 0.004578 | 0.059509 | 0.16022 | 0.1236 | 0.15106 | 6.3629 | -116.0385 | -115.9836 | 6.6055 | 6.4957 | 6.4682 | 0.13275 | 0.10529 | 0.064087 | -122.4014 | -122.3557 | 0.21973 | 0.21057 | 0.1831 | 0.14648 | 0.11902 | 0.24261 | 0.12817 | 0.15564 | 0.054931 | 0.073242 | 0.009155 | 6.4362 | 0.073242 | -116.1118 | -122.4106 | 6.4911 | 0.11902 | 6.5002 | 0.16479
4959.7031 | 122.5708 | -0.082397 | 122.4564 | -0.01976 | 0.012514 | 0.0083526 | -0.0097904 | 0.0012261 | -0.011339 | -0.0021682 | -0.011475 | 0.017831 | 0.042208 | -0.021687 | 0.012334 | 0.023964 | 0.00086095 | 6.4453 | 6.4224 | 6.3263 | 6.4178 | 6.546 | 6.4133 | 6.4453 | 0.032043 | 0.009155 | -0.009155 | -0.009155 | 0.10986 | 0.082397 | 0.10071 | 6.4087 | -116.0339 | -116.0385 | 6.6284 | 6.5277 | 6.4957 | 0.11902 | 0.086975 | 0.073242 | -122.4472 | -122.4655 | 0.19226 | 0.18311 | 0.16479 | 0.10986 | 0.091552 | 0.21973 | 0.091553 | 0.11902 | 0 | 0.09613 | 0.01831 | 6.5048 | 0.091552 | -116.1301 | -122.4655 | 6.5002 | 0.073242 | 6.5277 | 0.11444
4961.5156 | 122.5433 | -0.082397 | 122.4564 | -0.0045011 | 0.012728 | 0.010062 | -0.0085086 | 0.0020807 | -0.0092028 | -0.000673 | -0.011475 | 0.019967 | 0.04178 | -0.010579 | 0.013403 | 0.024605 | -0.0021299 | 6.5002 | 6.4682 | 6.3766 | 6.427 | 6.5506 | 6.427 | 6.4133 | 0.022888 | 0.018311 | -0.050354 | -0.009155 | 0.10071 | 0.054932 | 0.082397 | 6.459 | -115.9882 | -116.0294 | 6.633 | 6.4957 | 6.5094 | 0.036621 | 0.050354 | 0.032043 | -122.438 | -122.4655 | 0.18311 | 0.16479 | 0.13733 | 0.13275 | 0.10529 | 0.17395 | 0.050354 | 0.15106 | 0.041199 | 0.091553 | 0.068665 | 6.5506 | 0.10071 | -116.0797 | -122.5067 | 6.5094 | 0.073242 | 6.5826 | 0.10528
4963.2188 | 122.5021 | -0.10986 | 122.4655 | -0.012131 | 0.012728 | 0.010703 | -0.005945 | 0.0031487 | -0.008562 | 0.0014634 | -0.0084228 | 0.020822 | 0.043062 | -0.012501 | 0.012334 | 0.02311 | -0.0021299 | 6.3538 | 6.4087 | 6.2622 | 6.2988 | 6.395 | 6.2576 | 6.308 | -0.036621 | 0.022888 | -0.045776 | -0.054932 | 0.018311 | 0 | 0.050354 | 6.3721 | -116.0568 | -116.1667 | 6.5048 | 6.4178 | 6.3675 | 0.045776 | -0.004578 | 0.064087 | -122.4426 | -122.5204 | 0.12817 | 0.16022 | 0.10986 | 0.09613 | 0.045776 | 0.13275 | 0.036621 | 0.064087 | -0.009156 | 0.14648 | 0.068664 | 6.5186 | 0.13275 | -116.2033 | -122.5113 | 6.4087 | 0.054931 | 6.4636 | 0.073242
4964.9531 | 122.6486 | -0.059509 | 122.438 | -0.01976 | 0.0082416 | 0.009848 | -0.010858 | -0.0030463 | -0.0098438 | -0.0025956 | -0.005371 | 0.018472 | 0.043062 | -0.022114 | 0.011053 | 0.022469 | -0.0038389 | 6.4865 | 6.4041 | 6.34 | 6.5002 | 6.6422 | 6.5323 | 6.5369 | 0.10986 | -0.013733 | -0.013733 | 0.054932 | 0.1831 | 0.16022 | 0.13733 | 6.3995 | -116.0339 | -115.9378 | 6.7017 | 6.5964 | 6.5918 | 0.19684 | 0.19226 | 0.045776 | -122.4518 | -122.3831 | 0.24261 | 0.19684 | 0.21973 | 0.15106 | 0.17395 | 0.30212 | 0.16022 | 0.19684 | 0.068665 | 0.064087 | 0 | 6.4636 | 0.045776 | -116.098 | -122.4518 | 6.5598 | 0.11444 | 6.546 | 0.16937
4966.7031 | 122.4747 | -0.10529 | 122.4701 | -0.01976 | 0.014864 | 0.009848 | -0.0061588 | 0.0010125 | -0.0092028 | -0.00345 | -0.0084228 | 0.020395 | 0.043703 | -0.013783 | 0.012334 | 0.023537 | -0.00084805 | 6.3583 | 6.3858 | 6.2485 | 6.2714 | 6.3583 | 6.2256 | 6.2759 | -0.082397 | 0.032043 | -0.068665 | -0.059509 | 0.004578 | -0.022888 | 0.032043 | 6.3538 | -116.0843 | -116.1987 | 6.4636 | 6.3812 | 6.3309 | 0.027466 | -0.022888 | 0.036621 | -122.4381 | -122.5296 | 0.10986 | 0.13733 | 0.082398 | 0.10071 | 0.045777 | 0.10986 | 0.022888 | 0.073243 | 0.009156 | 0.13733 | 0.10071 | 6.4911 | 0.13733 | -116.2216 | -122.5388 | 6.3766 | 0.045777 | 6.4636 | 0.022889
4968.4062 | 122.5479 | -0.10071 | 122.4884 | -0.02739 | 0.013582 | 0.010062 | -0.005945 | 0.0059259 | -0.0094164 | -0.0021682 | -0.0084228 | 0.020395 | 0.040285 | -0.0084423 | 0.014257 | 0.023323 | -0.0038389 | 6.4407 | 6.4362 | 6.308 | 6.3904 | 6.5048 | 6.3583 | 6.3904 | 0.022888 | 0.045776 | -0.036621 | -0.009155 | 0.091553 | 0.050354 | 0.086975 | 6.4087 | -116.0522 | -116.098 | 6.6055 | 6.4911 | 6.459 | 0.082398 | 0.050354 | 0.064087 | -122.4426 | -122.4976 | 0.19226 | 0.18768 | 0.15106 | 0.1236 | 0.086975 | 0.19684 | 0.082398 | 0.12817 | 0.027466 | 0.12817 | 0.082397 | 6.5369 | 0.14648 | -116.1804 | -122.525 | 6.4911 | 0.091553 | 6.5414 | 0.1236
4970.1719 | 122.5067 | -0.10071 | 122.4564 | -0.01976 | 0.015291 | 0.0074982 | -0.008295 | -0.00091006 | -0.011339 | -0.00345 | -0.005371 | 0.020608 | 0.043917 | -0.016774 | 0.013616 | 0.022469 | -0.0027707 | 6.4178 | 6.3904 | 6.2805 | 6.3309 | 6.4682 | 6.3354 | 6.3446 | 0.018311 | 0.032043 | -0.032043 | -0.032043 | 0.059509 | 0.009155 | 0.054932 | 6.3812 | -116.066 | -116.1255 | 6.5689 | 6.4453 | 6.4362 | 0.064086 | 0.054931 | 0.068665 | -122.4243 | -122.4884 | 0.16022 | 0.15564 | 0.10986 | 0.086975 | 0.041198 | 0.18768 | 0.050354 | 0.091552 | 0 | 0.10986 | 0.064086 | 6.4911 | 0.13275 | -116.1758 | -122.4884 | 6.4316 | 0.068665 | 6.5186 | 0.11902
4971.9375 | 122.5067 | -0.10529 | 122.4564 | -0.0045011 | 0.013582 | 0.0085662 | -0.006586 | -0.0021919 | -0.0089892 | -0.0028092 | -0.005371 | 0.019754 | 0.042849 | -0.015492 | 0.014471 | 0.024605 | -0.0057615 | 6.4178 | 6.4774 | 6.3171 | 6.34 | 6.4407 | 6.3354 | 6.3858 | -0.054932 | 0.041199 | -0.054932 | -0.054932 | 0.036621 | 0.013733 | 0.027466 | 6.4224 | -115.979 | -116.1163 | 6.546 | 6.4911 | 6.4407 | 0.068664 | 0.01831 | 0.050354 | -122.4152 | -122.5113 | 0.14191 | 0.13275 | 0.11902 | 0.082398 | 0.068665 | 0.1236 | 0.022888 | 0.091553 | 0 | 0.16022 | 0.096131 | 6.5826 | 0.14649 | -116.1392 | -122.5113 | 6.4453 | 0.050354 | 6.5231 | 0.050354
4973.7344 | 122.58 | -0.082397 | 122.4564 | -0.0045011 | 0.0123 | 0.010062 | -0.010004 | -0.0015509 | -0.010271 | -0.005159 | -0.0084228 | 0.018045 | 0.040285 | -0.019124 | 0.012121 | 0.0261 | -0.0010617 | 6.3263 | 6.2714 | 6.221 | 6.2942 | 6.4453 | 6.2851 | 6.3354 | 0.045776 | 0.004578 | -0.027466 | 0.004578 | 0.10071 | 0.086975 | 0.09613 | 6.3034 | -116.185 | -116.1621 | 6.5277 | 6.4178 | 6.3675 | 0.11444 | 0.064087 | 0.054931 | -122.4518 | -122.4518 | 0.18311 | 0.17853 | 0.16937 | 0.1236 | 0.11444 | 0.2243 | 0.073242 | 0.12817 | 0.032044 | 0.050354 | 0.032044 | 6.3538 | 0.086975 | -116.2354 | -122.4838 | 6.3766 | 0.086975 | 6.4087 | 0.12817
4975.4531 | 122.5204 | -0.10986 | 122.4884 | -0.01976 | 0.015291 | 0.008139 | -0.0053042 | 0.00015814 | -0.011553 | -0.0008866 | -0.005371 | 0.01954 | 0.042208 | -0.013356 | 0.01383 | 0.023323 | -0.0049069 | 6.2942 | 6.308 | 6.1661 | 6.1981 | 6.2988 | 6.1615 | 6.2027 | -0.041199 | 0.027466 | -0.045776 | -0.064087 | 0.032043 | -0.013733 | 0.054932 | 6.2759 | -116.1804 | -116.2903 | 6.4087 | 6.3126 | 6.2714 | 0.036621 | -0.004578 | 0.064087 | -122.4609 | -122.5525 | 0.14191 | 0.16479 | 0.09613 | 0.10071 | 0.032043 | 0.13275 | 0.032043 | 0.077819 | -0.018311 | 0.14191 | 0.073242 | 6.4178 | 0.13733 | -116.3223 | -122.5342 | 6.308 | 0.045776 | 6.4041 | 0.068664
4977.1562 | 122.5159 | -0.09613 | 122.493 | -0.01976 | 0.012728 | 0.011771 | -0.0063724 | 0.0031487 | -0.0077074 | -0.0030228 | -0.0023192 | 0.022531 | 0.043489 | -0.01122 | 0.014043 | 0.026528 | -0.0021299 | 6.2622 | 6.2942 | 6.1798 | 6.1798 | 6.2897 | 6.1615 | 6.2073 | -0.045776 | 0.027466 | -0.036621 | -0.050354 | 0.027466 | -0.018311 | 0.036621 | 6.2759 | -116.1987 | -116.3132 | 6.3858 | 6.3034 | 6.2576 | 0.027465 | -0.018311 | 0.059509 | -122.4655 | -122.5433 | 0.1236 | 0.13275 | 0.077819 | 0.073242 | 0.01831 | 0.10986 | 0 | 0.064087 | -0.013733 | 0.11444 | 0.064087 | 6.3904 | 0.1236 | -116.3132 | -122.5296 | 6.2759 | 0.045776 | 6.3583 | 0.050354
4978.875 | 122.4655 | -0.11902 | 122.4747 | -0.02739 | 0.0123 | 0.012839 | -0.0072268 | 0.0033623 | -0.0064258 | -0.0045182 | -0.0023192 | 0.020822 | 0.042849 | -0.010792 | 0.014043 | 0.024819 | -0.0012753 | 6.2897 | 6.308 | 6.1798 | 6.1844 | 6.2622 | 6.1569 | 6.1935 | -0.086975 | 0.022888 | -0.059509 | -0.059509 | -0.004578 | -0.022888 | 0.036621 | 6.2988 | -116.1667 | -116.2903 | 6.3812 | 6.3126 | 6.2759 | 0.013732 | -0.022889 | 0.05951 | -122.4518 | -122.5342 | 0.11444 | 0.15564 | 0.096131 | 0.09613 | 0.036621 | 0.082397 | 0.004577 | 0.054931 | 0 | 0.12817 | 0.082397 | 6.427 | 0.14191 | -116.2949 | -122.5342 | 6.3034 | 0.05951 | 6.4087 | 0.032044
4980.6094 | 122.6349 | -0.073242 | 122.4289 | -0.01976 | 0.011232 | 0.010489 | -0.010431 | -0.00026906 | -0.010271 | -0.0028092 | -0.005371 | 0.018045 | 0.042421 | -0.01656 | 0.010412 | 0.024819 | -0.00020725 | 6.4087 | 6.3217 | 6.2622 | 6.3995 | 6.5506 | 6.4178 | 6.4316 | 0.12817 | -0.013733 | -0.013733 | 0.041199 | 0.19226 | 0.17395 | 0.14191 | 6.3354 | -116.1072 | -116.0294 | 6.6238 | 6.5048 | 6.4911 | 0.16937 | 0.15564 | 0.059509 | -122.4426 | -122.3877 | 0.2655 | 0.21515 | 0.24719 | 0.15564 | 0.18768 | 0.28839 | 0.13733 | 0.20599 | 0.054932 | 0.059509 | 0 | 6.395 | 0.059509 | -116.1667 | -122.4426 | 6.4728 | 0.11444 | 6.4819 | 0.20142
4982.375 | 122.5708 | -0.082397 | 122.4426 | -0.012131 | 0.012941 | 0.010062 | -0.0085086 | 0.00015814 | -0.011553 | -0.0036636 | -0.0084228 | 0.01954 | 0.040712 | -0.0048107 | 0.0080621 | 0.024605 | -0.0014891 | 6.2805 | 6.2714 | 6.1661 | 6.2531 | 6.3721 | 6.2439 | 6.2942 | 0.032043 | -0.009155 | -0.045776 | -0.004578 | 0.10986 | 0.086975 | 0.091553 | 6.2485 | -116.1713 | -116.1896 | 6.4545 | 6.3766 | 6.3263 | 0.12817 | 0.077819 | 0.036621 | -122.4518 | -122.4472 | 0.19226 | 0.17395 | 0.16937 | 0.13733 | 0.13275 | 0.20599 | 0.086975 | 0.15564 | 0.041198 | 0.10529 | 0.036621 | 6.3538 | 0.073242 | -116.2766 | -122.4884 | 6.3354 | 0.077819 | 6.3629 | 0.11444
4984.0938 | 122.5479 | -0.07782 | 122.4884 | -0.01976 | 0.013796 | 0.0094208 | -0.0038088 | 0.0022943 | -0.0092028 | -0.0002456 | -0.0084228 | 0.021676 | 0.045626 | -0.013997 | 0.012975 | 0.023964 | 0.0010745 | 6.2393 | 6.2531 | 6.1386 | 6.1752 | 6.2622 | 6.1203 | 6.1844 | -0.004578 | 0.022888 | -0.041199 | 0 | 0.059509 | 0.036621 | 0.07782 | 6.2164 | -116.2354 | -116.3132 | 6.34 | 6.2622 | 6.1981 | 0.045776 | -0.018311 | 0.036621 | -122.4655 | -122.4884 | 0.13733 | 0.15564 | 0.11444 | 0.11902 | 0.07782 | 0.1236 | 0.036621 | 0.10071 | 0.041199 | 0.11444 | 0.064087 | 6.3309 | 0.10071 | -116.3498 | -122.5296 | 6.2531 | 0.07782 | 6.3171 | 0.073242
4985.8438 | 122.4976 | -0.1236 | 122.4792 | -0.012131 | 0.009737 | 0.0089936 | -0.0063724 | 0.00079894 | -0.01198 | -0.0004592 | -0.0084228 | 0.022531 | 0.042635 | -0.0082287 | 0.015325 | 0.022683 | -0.00063445 | 6.2988 | 6.3675 | 6.2027 | 6.2576 | 6.3858 | 6.2805 | 6.3263 | -0.064087 | 0.027466 | -0.059509 | -0.068665 | 0.027466 | 0.004578 | 0.036621 | 6.3263 | -116.1118 | -116.2216 | 6.5094 | 6.4499 | 6.4041 | 0.1236 | 0.07782 | 0.064087 | -122.4518 | -122.5479 | 0.15106 | 0.16022 | 0.12817 | 0.09613 | 0.064087 | 0.18311 | 0.054931 | 0.086975 | -0.009156 | 0.16479 | 0.086975 | 6.4911 | 0.15106 | -116.2766 | -122.5388 | 6.3812 | 0.054931 | 6.4224 | 0.059509
4987.5625 | 122.5845 | -0.059509 | 122.4701 | -0.012131 | 0.0078144 | 0.011771 | -0.010645 | 0.0010125 | -0.010271 | -0.0038772 | -0.005371 | 0.017831 | 0.040926 | -0.018269 | 0.011266 | 0.023751 | -0.0059751 | 6.3583 | 6.2851 | 6.2164 | 6.3492 | 6.4819 | 6.3492 | 6.3812 | 0.10071 | 0 | -0.027466 | 0.027466 | 0.16937 | 0.12817 | 0.11902 | 6.2759 | -116.185 | -116.1209 | 6.5414 | 6.4407 | 6.4087 | 0.16479 | 0.13275 | 0.032043 | -122.4701 | -122.4426 | 0.22888 | 0.17853 | 0.18768 | 0.14649 | 0.15564 | 0.2655 | 0.13275 | 0.19684 | 0.054932 | 0.068664 | 0.027466 | 6.3446 | 0.059509 | -116.2537 | -122.4976 | 6.4087 | 0.086975 | 6.4178 | 0.16022
4989.3438 | 122.5388 | -0.091553 | 122.493 | -0.01976 | 0.011232 | 0.00878 | -0.0067996 | 0.00015814 | -0.0087756 | -0.0021682 | -0.0084228 | 0.020608 | 0.040285 | -0.015706 | 0.012975 | 0.021401 | -0.0038389 | 6.3126 | 6.3583 | 6.221 | 6.2302 | 6.34 | 6.2347 | 6.2576 | -0.059509 | 0.045776 | -0.068665 | -0.068665 | 0.054932 | 0.027466 | 0.054932 | 6.3126 | -116.1346 | -116.2628 | 6.4316 | 6.3492 | 6.3263 | 0.036621 | 0.013733 | 0.022888 | -122.4472 | -122.5616 | 0.14649 | 0.14649 | 0.11902 | 0.1236 | 0.096131 | 0.11902 | 0.009156 | 0.1236 | 0 | 0.13733 | 0.11444 | 6.4499 | 0.13733 | -116.272 | -122.5616 | 6.3217 | 0.022888 | 6.4041 | 0.032044
4991.0781 | 122.6486 | -0.050354 | 122.438 | -0.012131 | 0.011446 | 0.00878 | -0.008295 | 0.0020807 | -0.011339 | -0.0036636 | -0.005371 | 0.018045 | 0.04178 | -0.017415 | 0.0099847 | 0.022469 | -0.0017027 | 6.3309 | 6.2256 | 6.1844 | 6.3217 | 6.4819 | 6.3263 | 6.3583 | 0.11444 | -0.022888 | -0.013733 | 0.054932 | 0.19684 | 0.15564 | 0.13733 | 6.2347 | -116.2125 | -116.1163 | 6.5323 | 6.4087 | 6.3766 | 0.17395 | 0.14191 | 0.036621 | -122.4609 | -122.3831 | 0.24719 | 0.18768 | 0.20599 | 0.15106 | 0.16937 | 0.29755 | 0.13733 | 0.21057 | 0.068665 | 0.041199 | -0.009155 | 6.2759 | 0.027466 | -116.2537 | -122.4518 | 6.3721 | 0.10529 | 6.3812 | 0.16479
4992.7969 | 122.5845 | -0.068665 | 122.4518 | -0.012131 | 0.010164 | 0.0089936 | -0.010004 | 0.0046441 | -0.010698 | -0.0070816 | -0.011475 | 0.019967 | 0.040926 | -0.011433 | 0.011266 | 0.022683 | -0.0027707 | 6.2164 | 6.189 | 6.1066 | 6.189 | 6.3034 | 6.1844 | 6.221 | 0.027466 | 0.004578 | -0.045776 | -0.004578 | 0.10986 | 0.091553 | 0.082397 | 6.1752 | -116.2628 | -116.2628 | 6.3721 | 6.2897 | 6.2531 | 0.11444 | 0.07782 | 0.022889 | -122.4472 | -122.4564 | 0.17853 | 0.15106 | 0.16022 | 0.12817 | 0.13733 | 0.19684 | 0.082398 | 0.15564 | 0.041198 | 0.082398 | 0.050354 | 6.2576 | 0.073243 | -116.3452 | -122.4976 | 6.2576 | 0.064087 | 6.2851 | 0.096131
4994.5938 | 122.5479 | -0.10529 | 122.4747 | -0.012131 | 0.014009 | 0.011557 | -0.0080814 | 0.0057123 | -0.011766 | -0.000673 | -0.0023192 | 0.020395 | 0.043276 | -0.0084423 | 0.014684 | 0.022896 | 0.00086095 | 6.2714 | 6.2622 | 6.1478 | 6.2164 | 6.3263 | 6.1981 | 6.2164 | 0.027466 | 0.027466 | -0.050354 | -0.004578 | 0.091553 | 0.073242 | 0.07782 | 6.2531 | -116.2125 | -116.2582 | 6.4316 | 6.3217 | 6.3034 | 0.068665 | 0.050354 | 0.054932 | -122.4472 | -122.4792 | 0.19684 | 0.18311 | 0.17853 | 0.12817 | 0.1236 | 0.17853 | 0.068665 | 0.14191 | 0.045776 | 0.11444 | 0.07782 | 6.3675 | 0.13275 | -116.3269 | -122.525 | 6.3217 | 0.10071 | 6.3766 | 0.13275
4996.4062 | 122.5342 | -0.10071 | 122.5067 | -0.01976 | 0.014864 | 0.010489 | -0.006586 | 0.0016535 | -0.0094164 | -0.0011002 | -0.0084228 | 0.020395 | 0.041994 | -0.014424 | 0.014471 | 0.025032 | -0.0027707 | 6.2668 | 6.2347 | 6.1157 | 6.2027 | 6.3126 | 6.1615 | 6.1844 | 0.041199 | 0.018311 | -0.045776 | -0.009155 | 0.082397 | 0.027466 | 0.073242 | 6.2164 | -116.272 | -116.304 | 6.4133 | 6.2851 | 6.2622 | 0.068664 | 0.045776 | 0.054932 | -122.4884 | -122.5159 | 0.18311 | 0.17395 | 0.12817 | 0.11902 | 0.073242 | 0.19684 | 0.086975 | 0.12817 | 0.036621 | 0.11902 | 0.064087 | 6.3354 | 0.11902 | -116.391 | -122.5525 | 6.3034 | 0.091553 | 6.3675 | 0.14191
4998.125 | 122.6486 | -0.064087 | 122.4472 | -0.012131 | 0.011019 | 0.0085662 | -0.0097904 | -0.0017645 | -0.012621 | -0.00345 | -0.005371 | 0.018899 | 0.041994 | -0.02126 | 0.012762 | 0.025887 | -0.0034117 | 6.2714 | 6.1981 | 6.1157 | 6.2668 | 6.4041 | 6.2714 | 6.2805 | 0.15564 | -0.022888 | -0.032043 | 0.064087 | 0.20599 | 0.15564 | 0.14648 | 6.1798 | -116.2491 | -116.1804 | 6.4682 | 6.3446 | 6.3354 | 0.16479 | 0.15564 | 0.032044 | -122.4701 | -122.3831 | 0.27008 | 0.21057 | 0.21973 | 0.17853 | 0.18768 | 0.28839 | 0.15106 | 0.23804 | 0.09613 | 0.082397 | 0.009155 | 6.2622 | 0.041199 | -116.3315 | -122.4792 | 6.3309 | 0.12817 | 6.3354 | 0.21973
4999.8906 | 122.6395 | -0.054932 | 122.4289 | -0.01976 | 0.015078 | 0.0094208 | -0.0074404 | 0.0018671 | -0.010698 | -0.00345 | -0.005371 | 0.019967 | 0.043062 | -0.013783 | 0.011694 | 0.022683 | -0.0066159 | 6.1935 | 6.0883 | 6.0287 | 6.1386 | 6.2531 | 6.0928 | 6.1386 | 0.11444 | -0.004578 | -0.009155 | 0.073242 | 0.16937 | 0.1236 | 0.15106 | 6.0837 | -116.3406 | -116.2903 | 6.308 | 6.1935 | 6.1478 | 0.10986 | 0.064086 | 0.045777 | -122.4335 | -122.3557 | 0.22431 | 0.20599 | 0.17853 | 0.16022 | 0.13275 | 0.2243 | 0.10986 | 0.17853 | 0.082397 | 0.059509 | 0.004577 | 6.1432 | 0.050354 | -116.4001 | -122.438 | 6.1935 | 0.12817 | 6.2485 | 0.16937
5001.6719 | 122.5159 | -0.09613 | 122.4701 | -0.01976 | 0.011873 | 0.010275 | -0.0089358 | -0.00091006 | -0.011553 | -0.0028092 | -0.005371 | 0.020822 | 0.040285 | -0.0099377 | 0.012762 | 0.022896 | -0.0027707 | 6.2393 | 6.2256 | 6.134 | 6.2119 | 6.3263 | 6.1981 | 6.2164 | -0.009155 | 0.018311 | -0.041199 | -0.064087 | 0.045776 | 0.036621 | 0.027466 | 6.2302 | -116.2445 | -116.2582 | 6.4224 | 6.3126 | 6.2942 | 0.082398 | 0.064087 | 0.054931 | -122.4518 | -122.5342 | 0.14191 | 0.1236 | 0.13275 | 0.068665 | 0.07782 | 0.19226 | 0.07782 | 0.086975 | -0.022888 | 0.091553 | 0.05951 | 6.3217 | 0.11444 | -116.3361 | -122.5113 | 6.308 | 0.032043 | 6.3354 | 0.086975
5003.375 | 122.6257 | -0.068665 | 122.438 | -0.01976 | 0.01166 | 0.010062 | -0.0091494 | 0.0029351 | -0.010912 | -0.0043046 | -0.0023192 | 0.019326 | 0.040926 | -0.015278 | 0.0099847 | 0.021828 | -0.0023435 | 6.1707 | 6.1478 | 6.0516 | 6.1752 | 6.2942 | 6.1844 | 6.2256 | 0.086975 | -0.018311 | -0.041199 | 0.036621 | 0.1831 | 0.15106 | 0.13275 | 6.1203 | -116.2903 | -116.2628 | 6.3629 | 6.2943 | 6.2531 | 0.17395 | 0.13275 | 0.027466 | -122.4564 | -122.4014 | 0.25177 | 0.20142 | 0.21973 | 0.17395 | 0.19226 | 0.24261 | 0.1236 | 0.2243 | 0.07782 | 0.09613 | 0.022888 | 6.2164 | 0.050354 | -116.3864 | -122.4792 | 6.2439 | 0.10529 | 6.2393 | 0.15564
5005.1094 | 122.6212 | -0.082397 | 122.4747 | -0.01976 | 0.010378 | 0.010275 | -0.0080814 | -0.00048286 | -0.010912 | 0.0001816 | -0.005371 | 0.019754 | 0.040499 | -0.0069469 | 0.0089167 | 0.022042 | -0.0029843 | 6.1432 | 6.1249 | 6.0425 | 6.1478 | 6.2576 | 6.134 | 6.1707 | 0.059509 | 0.013733 | -0.027466 | 0.018311 | 0.15564 | 0.12817 | 0.11902 | 6.1249 | -116.3498 | -116.3269 | 6.34 | 6.2531 | 6.2164 | 0.12817 | 0.091553 | 0.054931 | -122.4609 | -122.4564 | 0.23804 | 0.20142 | 0.21057 | 0.14649 | 0.15564 | 0.21515 | 0.10529 | 0.18311 | 0.045777 | 0.082398 | 0.041199 | 6.2073 | 0.09613 | -116.4322 | -122.5021 | 6.2302 | 0.10071 | 6.2256 | 0.14191
5006.8594 | 122.5433 | -0.086975 | 122.5021 | -0.012131 | 0.014009 | 0.00878 | -0.005945 | -5.5462e-05 | -0.011339 | -0.0038772 | -0.0084228 | 0.022744 | 0.04114 | -0.013783 | 0.013616 | 0.021828 | -0.0040525 | 6.1798 | 6.2119 | 6.0699 | 6.134 | 6.221 | 6.1203 | 6.1386 | -0.036621 | 0.022888 | -0.054932 | -0.032043 | 0.086975 | 0.041199 | 0.073242 | 6.1569 | -116.2903 | -116.3681 | 6.308 | 6.2256 | 6.2073 | 0.068665 | 0.050354 | 0.032043 | -122.4792 | -122.5342 | 0.17395 | 0.16022 | 0.12817 | 0.12817 | 0.096131 | 0.15106 | 0.064087 | 0.14191 | 0.022889 | 0.14191 | 0.07782 | 6.2988 | 0.10986 | -116.4322 | -122.5571 | 6.221 | 0.054932 | 6.2668 | 0.050354
5008.5781 | 122.644 | -0.07782 | 122.4609 | -0.012131 | 0.0093098 | 0.008139 | -0.011072 | -0.0039007 | -0.012407 | -0.00345 | -0.011475 | 0.019967 | 0.040926 | -0.016133 | 0.012762 | 0.023537 | -0.0066159 | 6.2119 | 6.134 | 6.0699 | 6.2027 | 6.3446 | 6.2027 | 6.2347 | 0.10071 | -0.018311 | -0.032043 | 0.050354 | 0.17395 | 0.13733 | 0.1236 | 6.1478 | -116.3269 | -116.2582 | 6.4224 | 6.3126 | 6.2805 | 0.16479 | 0.13275 | 0.045777 | -122.4792 | -122.4106 | 0.25177 | 0.20142 | 0.21515 | 0.15564 | 0.16937 | 0.27466 | 0.13275 | 0.20599 | 0.082397 | 0.064087 | 0.013732 | 6.2119 | 0.059509 | -116.391 | -122.493 | 6.2805 | 0.12817 | 6.2897 | 0.17853
5010.3594 | 122.5616 | -0.091553 | 122.493 | -0.012131 | 0.012087 | 0.010703 | -0.004877 | 0.0037897 | -0.012194 | -0.0025956 | -0.0084228 | 0.02189 | 0.041994 | -0.0086559 | 0.014257 | 0.021828 | -0.0040525 | 6.1707 | 6.2027 | 6.0654 | 6.0883 | 6.2027 | 6.0928 | 6.1111 | -0.027466 | 0.022888 | -0.059509 | -0.032043 | 0.09613 | 0.041199 | 0.068665 | 6.1569 | -116.2903 | -116.4047 | 6.2943 | 6.2027 | 6.1844 | 0.045776 | 0.027465 | 0.032044 | -122.4701 | -122.525 | 0.18768 | 0.16022 | 0.13275 | 0.12817 | 0.10071 | 0.13733 | 0.022888 | 0.15564 | 0.027466 | 0.13733 | 0.082397 | 6.2943 | 0.11444 | -116.4276 | -122.5525 | 6.1798 | 0.05951 | 6.2622 | 0.064087
5012.0781 | 122.5113 | -0.09613 | 122.4792 | -0.012131 | 0.014437 | 0.010916 | -0.006586 | 0.0046441 | -0.0083484 | -0.0030228 | 0.00073235 | 0.021035 | 0.043276 | -0.011433 | 0.014684 | 0.024178 | -0.0034117 | 6.1478 | 6.1249 | 6.0013 | 6.0608 | 6.1661 | 6.0242 | 6.0562 | -0.009155 | 0.022888 | -0.045776 | -0.036621 | 0.045776 | 0 | 0.027466 | 6.0974 | -116.3544 | -116.4185 | 6.2622 | 6.1523 | 6.1203 | 0.054931 | 0.022888 | 0.050354 | -122.4564 | -122.5159 | 0.14191 | 0.1236 | 0.09613 | 0.073242 | 0.045776 | 0.16479 | 0.059509 | 0.091552 | 0.009155 | 0.1236 | 0.068664 | 6.221 | 0.11902 | -116.478 | -122.525 | 6.1569 | 0.059509 | 6.2439 | 0.086975
5013.8281 | 122.6028 | -0.086975 | 122.4655 | -0.01976 | 0.014223 | 0.011771 | -0.0050906 | 0.0025079 | -0.0092028 | -0.0025956 | -0.005371 | 0.018472 | 0.040926 | -0.012715 | 0.014257 | 0.022042 | -0.0012753 | 6.0287 | 6.0608 | 5.9143 | 5.9647 | 6.0745 | 5.9143 | 5.9647 | 0.004578 | 0.009155 | -0.045776 | 0.018311 | 0.10986 | 0.059509 | 0.091553 | 6.0013 | -116.4047 | -116.5009 | 6.1615 | 6.0516 | 6.0013 | 0.050354 | 0 | 0.041199 | -122.4564 | -122.4472 | 0.19684 | 0.17853 | 0.14648 | 0.13733 | 0.10528 | 0.16022 | 0.050354 | 0.15564 | 0.064087 | 0.14648 | 0.054931 | 6.1478 | 0.09613 | -116.5512 | -122.5113 | 6.0516 | 0.10529 | 6.1157 | 0.091553
5015.5469 | 122.5296 | -0.10986 | 122.5067 | -0.01976 | 0.012087 | 0.0085662 | -0.0085086 | -0.0043281 | -0.0074938 | -0.0047318 | -0.005371 | 0.020608 | 0.040926 | -0.018483 | 0.011907 | 0.024391 | -0.0012753 | 6.1203 | 6.1752 | 6.0104 | 6.0516 | 6.1798 | 6.0791 | 6.0791 | -0.073242 | 0.022888 | -0.045776 | -0.082397 | 0.045776 | 0.004578 | 0.036621 | 6.1203 | -116.3315 | -116.4551 | 6.2897 | 6.189 | 6.189 | 0.068665 | 0.068665 | 0.064087 | -122.4838 | -122.5891 | 0.15564 | 0.14648 | 0.11444 | 0.082397 | 0.050354 | 0.16937 | 0.041199 | 0.091552 | -0.036621 | 0.1648 | 0.068664 | 6.2851 | 0.13275 | -116.4963 | -122.5525 | 6.1615 | 0.027466 | 6.2302 | 0.036621
5017.2969 | 122.5571 | -0.086975 | 122.4655 | -0.0045011 | 0.01465 | 0.009848 | -0.0072268 | -0.00069646 | -0.0083484 | -0.0045182 | -0.005371 | 0.018472 | 0.043489 | -0.015065 | 0.012548 | 0.022042 | 0.00086095 | 5.9875 | 6.0333 | 5.896 | 5.9189 | 6.0425 | 5.8914 | 5.9418 | -0.022888 | 0.022888 | -0.054932 | -0.018311 | 0.054932 | 0.022888 | 0.059509 | 5.983 | -116.4322 | -116.5466 | 6.1295 | 6.0287 | 5.9784 | 0.045776 | -0.004578 | 0.032043 | -122.4426 | -122.4838 | 0.14191 | 0.14648 | 0.10986 | 0.11444 | 0.07782 | 0.14648 | 0.022888 | 0.10986 | 0.036621 | 0.13733 | 0.07782 | 6.1203 | 0.10986 | -116.5695 | -122.5204 | 6.0059 | 0.068664 | 6.0745 | 0.064087
5019.0156 | 122.5983 | -0.07782 | 122.4518 | -0.01976 | 0.0084552 | 0.0094208 | -0.011713 | -0.00048286 | -0.0098438 | -0.0030228 | -0.0023192 | 0.020181 | 0.04178 | -0.015919 | 0.011907 | 0.022896 | -0.00084805 | 6.0287 | 6.0104 | 5.9326 | 6.015 | 6.1249 | 5.9921 | 6.0333 | 0.018311 | 0 | -0.045776 | -0.013733 | 0.09613 | 0.068665 | 0.091553 | 6.0104 | -116.4413 | -116.4368 | 6.2027 | 6.1111 | 6.0699 | 0.10071 | 0.059509 | 0.032044 | -122.4518 | -122.4655 | 0.17395 | 0.16937 | 0.14649 | 0.13733 | 0.11444 | 0.19226 | 0.082398 | 0.14191 | 0.032043 | 0.07782 | 0.045776 | 6.0883 | 0.07782 | -116.5192 | -122.4976 | 6.0928 | 0.064087 | 6.1066 | 0.096131
5020.7812 | 122.5845 | -0.10071 | 122.4747 | -0.02739 | 0.013369 | 0.01113 | -0.0055178 | 0.0020807 | -0.010698 | -0.0045182 | -0.0084228 | 0.021463 | 0.042421 | -0.017628 | 0.011694 | 0.023751 | -0.0046933 | 5.983 | 6.0196 | 5.8868 | 5.9052 | 6.0104 | 5.8868 | 5.928 | -0.004578 | 0.018311 | -0.041199 | 0.004578 | 0.073242 | 0.054932 | 0.07782 | 5.9875 | -116.4551 | -116.5695 | 6.1111 | 6.0287 | 5.9875 | 0.041199 | 0 | 0.059509 | -122.4564 | -122.4701 | 0.17395 | 0.17853 | 0.15564 | 0.11902 | 0.096131 | 0.1236 | 0.01831 | 0.11444 | 0.045777 | 0.13275 | 0.05951 | 6.1203 | 0.11902 | -116.5878 | -122.5159 | 6.0059 | 0.10529 | 6.0837 | 0.09613
5022.4844 | 122.5983 | -0.064087 | 122.4609 | -0.01976 | 0.015505 | 0.0083526 | -0.0085086 | 0.0020807 | -0.0087756 | -0.0021682 | -0.005371 | 0.019967 | 0.041353 | -0.017201 | 0.011907 | 0.024178 | -0.0040525 | 6.0013 | 5.9647 | 5.9006 | 5.983 | 6.1111 | 5.9555 | 6.015 | 0.054932 | -0.009155 | -0.032043 | 0.004578 | 0.11902 | 0.091553 | 0.09613 | 5.9647 | -116.4963 | -116.478 | 6.1752 | 6.0791 | 6.0196 | 0.11444 | 0.054931 | 0.032044 | -122.4701 | -122.4564 | 0.18311 | 0.16022 | 0.15564 | 0.12817 | 0.1236 | 0.21057 | 0.082397 | 0.15106 | 0.036621 | 0.064087 | 0.022888 | 6.0287 | 0.054932 | -116.5604 | -122.493 | 6.0471 | 0.068665 | 6.0654 | 0.11902
5024.2031 | 122.6624 | -0.054932 | 122.4518 | -0.01976 | 0.01465 | 0.009848 | -0.0074404 | 0.0018671 | -0.00963 | -0.0011002 | -0.005371 | 0.018899 | 0.040499 | -0.022755 | 0.013403 | 0.02311 | -0.0027707 | 6.0013 | 5.9052 | 5.8868 | 6.0059 | 6.1203 | 5.9418 | 6.0059 | 0.11444 | -0.004578 | -0.022888 | 0.050354 | 0.16937 | 0.14191 | 0.1236 | 5.9418 | -116.5466 | -116.4459 | 6.1752 | 6.0608 | 5.9967 | 0.11902 | 0.054931 | 0.032044 | -122.4564 | -122.4014 | 0.22431 | 0.17853 | 0.19684 | 0.14648 | 0.16479 | 0.23346 | 0.11902 | 0.19226 | 0.073242 | 0.01831 | 0.01831 | 5.9601 | 0.050354 | -116.5649 | -122.4747 | 6.0608 | 0.10529 | 6.0562 | 0.16937
5025.9219 | 122.6624 | -0.068665 | 122.4838 | -0.01976 | 0.013155 | 0.010703 | -0.0057314 | 0.0052851 | -0.010485 | -0.0028092 | -0.005371 | 0.02189 | 0.041994 | -0.0090833 | 0.013616 | 0.023964 | -0.0029843 | 5.983 | 5.9509 | 5.8502 | 5.9784 | 6.0791 | 5.9326 | 5.9784 | 0.091553 | -0.027466 | -0.022888 | 0.068665 | 0.15564 | 0.11902 | 0.14648 | 5.9189 | -116.5329 | -116.5054 | 6.1478 | 6.0471 | 6.0013 | 0.12817 | 0.082397 | 0.045777 | -122.5113 | -122.4152 | 0.22431 | 0.21515 | 0.18768 | 0.16937 | 0.14191 | 0.22888 | 0.12817 | 0.17853 | 0.091553 | 0.10071 | -0.004578 | 6.0196 | 0.041199 | -116.6336 | -122.5067 | 6.0471 | 0.13733 | 6.0516 | 0.16022
5027.6562 | 122.5525 | -0.11444 | 122.4976 | -0.01976 | 0.013155 | 0.01113 | -0.0055178 | 0.0020807 | -0.0074938 | -0.0019546 | -0.005371 | 0.021249 | 0.045198 | -0.0078015 | 0.01383 | 0.024819 | -0.0044797 | 5.9647 | 5.9967 | 5.8594 | 5.8731 | 5.9418 | 5.8228 | 5.8823 | -0.054932 | 0.036621 | -0.064087 | -0.064087 | 0 | -0.018311 | 0.036621 | 5.9738 | -116.5009 | -116.6245 | 6.0562 | 5.9967 | 5.9372 | 0.022888 | -0.036621 | 0.050354 | -122.4609 | -122.5616 | 0.11444 | 0.15106 | 0.09613 | 0.10071 | 0.045776 | 0.082397 | 0.013733 | 0.064087 | 0 | 0.13733 | 0.10071 | 6.1111 | 0.15106 | -116.6382 | -122.5616 | 5.9875 | 0.050354 | 6.0791 | 0.059509
5029.375 | 122.5204 | -0.10529 | 122.5067 | -0.012131 | 0.01465 | 0.011557 | -0.0055178 | -0.0017645 | -0.0081348 | -0.0045182 | -0.0084228 | 0.02189 | 0.043276 | -0.011647 | 0.013616 | 0.02076 | -0.0029843 | 5.9326 | 5.9921 | 5.8502 | 5.8502 | 5.9326 | 5.8044 | 5.8548 | -0.07782 | 0.032043 | -0.050354 | -0.068665 | 0.018311 | -0.041199 | 0.041199 | 5.9555 | -116.5146 | -116.6565 | 6.0379 | 5.9601 | 5.9097 | 0.004577 | -0.045777 | 0.054932 | -122.4747 | -122.5754 | 0.1236 | 0.14649 | 0.064087 | 0.091553 | 0.009155 | 0.082397 | 0 | 0.068665 | -0.018311 | 0.14191 | 0.082397 | 6.0974 | 0.13733 | -116.6565 | -122.5571 | 5.9555 | 0.036621 | 6.0379 | 0.027466
5031.0781 | 122.644 | -0.050354 | 122.4792 | -0.012131 | 0.014223 | 0.013266 | -0.0072268 | 0.00058534 | -0.0092028 | -0.0030228 | -0.0084228 | 0.01719 | 0.044344 | -0.013569 | 0.012975 | 0.023751 | -0.0014891 | 5.9784 | 5.8868 | 5.8365 | 5.9509 | 6.0562 | 5.9006 | 5.9418 | 0.1236 | -0.013733 | -0.027466 | 0.068665 | 0.17395 | 0.11902 | 0.14648 | 5.8868 | -116.5924 | -116.5283 | 6.1066 | 5.9921 | 5.9509 | 0.10529 | 0.064087 | 0.022888 | -122.493 | -122.4106 | 0.2243 | 0.19684 | 0.16937 | 0.17395 | 0.14649 | 0.21973 | 0.11444 | 0.20142 | 0.096131 | 0.050354 | 0.013733 | 5.9372 | 0.036621 | -116.6428 | -122.5067 | 6.0013 | 0.11902 | 6.0287 | 0.17395
5032.7969 | 122.6028 | -0.086975 | 122.4747 | -0.012131 | 0.011873 | 0.010275 | -0.009363 | -0.0024055 | -0.010271 | -0.0038772 | -0.005371 | 0.019326 | 0.042421 | -0.015706 | 0.011907 | 0.022896 | -0.0019163 | 6.0608 | 5.9921 | 5.9418 | 6.0608 | 6.1615 | 6.0379 | 6.0654 | 0.07782 | -0.009155 | -0.032043 | 0.013733 | 0.14191 | 0.1236 | 0.10529 | 6.0287 | -116.4825 | -116.4139 | 6.2485 | 6.1523 | 6.1249 | 0.1236 | 0.096131 | 0.054932 | -122.4838 | -122.4609 | 0.22888 | 0.19226 | 0.21057 | 0.13733 | 0.15564 | 0.21973 | 0.11902 | 0.17395 | 0.045776 | 0.050354 | 0.022888 | 6.0791 | 0.07782 | -116.5329 | -122.5067 | 6.1478 | 0.10071 | 6.1478 | 0.16479
5034.5156 | 122.6349 | -0.068665 | 122.4701 | -0.02739 | 0.013582 | 0.011557 | -0.0061588 | 0.0022943 | -0.0074938 | -0.0032364 | -0.0084228 | 0.022317 | 0.043276 | -0.0054517 | 0.012121 | 0.024819 | -0.0053343 | 5.8914 | 5.8868 | 5.8136 | 5.8594 | 5.9738 | 5.8182 | 5.8777 | 0.036621 | 0.009155 | -0.022888 | 0.045776 | 0.13733 | 0.10071 | 0.13733 | 5.8823 | -116.5833 | -116.6107 | 6.0425 | 5.9464 | 5.8868 | 0.064087 | 0.004577 | 0.045777 | -122.4609 | -122.4243 | 0.20599 | 0.20599 | 0.16937 | 0.16022 | 0.1236 | 0.16022 | 0.045776 | 0.16022 | 0.068664 | 0.073242 | 0.032043 | 5.9555 | 0.07782 | -116.6565 | -122.493 | 5.928 | 0.11444 | 5.9601 | 0.10529
5036.3906 | 122.6532 | -0.059509 | 122.493 | -0.0045011 | 0.012941 | 0.0096344 | -0.005945 | 0.0033623 | -0.010057 | -0.0049454 | -0.0084228 | 0.020822 | 0.040071 | -0.01421 | 0.01148 | 0.023751 | -0.0023435 | 5.9418 | 5.8502 | 5.8136 | 5.9143 | 6.0333 | 5.8823 | 5.9189 | 0.09613 | 0.004578 | -0.032043 | 0.068665 | 0.16022 | 0.11902 | 0.14648 | 5.8731 | -116.6428 | -116.5787 | 6.0928 | 5.9784 | 5.9418 | 0.10529 | 0.068664 | 0.027466 | -122.4884 | -122.4243 | 0.21973 | 0.20599 | 0.17853 | 0.17853 | 0.15106 | 0.21973 | 0.10071 | 0.19226 | 0.10071 | 0.036621 | 0.036621 | 5.9097 | 0.064087 | -116.6794 | -122.525 | 5.9738 | 0.12817 | 6.0013 | 0.15564
5038.1406 | 122.5067 | -0.10071 | 122.5159 | -0.01976 | 0.016573 | 0.010703 | -0.0057314 | 0.0018671 | -0.0094164 | -0.00345 | -0.014526 | 0.021035 | 0.042635 | -0.0097241 | 0.01383 | 0.023751 | -0.0055479 | 5.9006 | 5.9372 | 5.8182 | 5.7953 | 5.8868 | 5.777 | 5.809 | -0.086975 | 0.041199 | -0.068665 | -0.064087 | 0.004578 | -0.022888 | 0.027466 | 5.9189 | -116.5787 | -116.7206 | 5.9875 | 5.9097 | 5.8777 | -0.009155 | -0.041198 | 0.032043 | -122.4747 | -122.58 | 0.10529 | 0.12817 | 0.07782 | 0.096131 | 0.045777 | 0.068665 | -0.022888 | 0.073243 | 0.004578 | 0.11902 | 0.10986 | 6.0379 | 0.14191 | -116.6977 | -122.5845 | 5.896 | 0.036621 | 6.0013 | 0.013733
5039.9219 | 122.5525 | -0.11902 | 122.5021 | -0.012131 | 0.010164 | 0.0068574 | -0.0085086 | -0.00026906 | -0.0094164 | -0.002382 | -0.0084228 | 0.021249 | 0.04178 | -0.015706 | 0.010412 | 0.022896 | 0.0017153 | 5.9555 | 6.0104 | 5.8685 | 5.9097 | 6.0287 | 5.9052 | 5.9463 | -0.059509 | 0.036621 | -0.059509 | -0.082397 | 0.036621 | 0.018311 | 0.013733 | 5.9875 | -116.4917 | -116.5924 | 6.1478 | 6.0654 | 6.0242 | 0.07782 | 0.036621 | 0.05951 | -122.4655 | -122.5845 | 0.15564 | 0.13275 | 0.13733 | 0.073242 | 0.07782 | 0.16022 | 0.041199 | 0.09613 | -0.022888 | 0.14191 | 0.09613 | 6.1295 | 0.15564 | -116.6336 | -122.5616 | 6.0287 | 0.036622 | 6.0745 | 0.05951
5041.6562 | 122.612 | -0.068665 | 122.4838 | -0.0045011 | 0.011873 | 0.0089936 | -0.0080814 | -5.5462e-05 | -0.0092028 | -0.0032364 | -0.005371 | 0.018899 | 0.04178 | -0.02126 | 0.012121 | 0.025032 | -0.0042661 | 5.8823 | 5.8456 | 5.7953 | 5.8731 | 5.9875 | 5.8456 | 5.8914 | 0.036621 | 0 | -0.036621 | 0.004578 | 0.10529 | 0.073242 | 0.09613 | 5.864 | -116.6382 | -116.6107 | 6.0562 | 5.9601 | 5.9143 | 0.09613 | 0.050354 | 0.032044 | -122.4838 | -122.4792 | 0.17395 | 0.16479 | 0.14191 | 0.13275 | 0.10986 | 0.19226 | 0.07782 | 0.14191 | 0.041199 | 0.050354 | 0.036621 | 5.9143 | 0.068665 | -116.6885 | -122.5204 | 5.9418 | 0.073243 | 5.9509 | 0.10529
5043.4375 | 122.5754 | -0.082397 | 122.4792 | -0.01976 | 0.015291 | 0.0096344 | -0.006586 | 0.0044305 | -0.010271 | -0.0040908 | -0.011475 | 0.020181 | 0.041567 | -0.012501 | 0.014898 | 0.024605 | 0.00064735 | 5.8319 | 5.8685 | 5.7449 | 5.7678 | 5.8731 | 5.7358 | 5.777 | -0.018311 | 0.022888 | -0.041199 | -0.018311 | 0.073242 | 0.036621 | 0.082397 | 5.8273 | -116.6107 | -116.7114 | 5.9555 | 5.8594 | 5.8182 | 0.032044 | -0.009155 | 0.041198 | -122.4564 | -122.4976 | 0.15564 | 0.16479 | 0.11902 | 0.1236 | 0.07782 | 0.12817 | 0.022888 | 0.11444 | 0.022888 | 0.1236 | 0.064087 | 5.9509 | 0.10528 | -116.7343 | -122.5204 | 5.8502 | 0.064086 | 5.9143 | 0.064086
5045.2188 | 122.5204 | -0.12817 | 122.5113 | -0.01976 | 0.01465 | 0.010489 | -0.0050906 | 0.0048577 | -0.0092028 | -0.00345 | -0.0084228 | 0.021035 | 0.045198 | -0.015919 | 0.012975 | 0.02311 | -0.0019163 | 5.8365 | 5.8868 | 5.7541 | 5.7678 | 5.8319 | 5.7083 | 5.7449 | -0.059509 | 0.018311 | -0.045776 | -0.064087 | 0.018311 | -0.036621 | 0.022888 | 5.8823 | -116.6245 | -116.7435 | 5.9601 | 5.8731 | 5.8365 | -0.009155 | -0.045776 | 0.082398 | -122.493 | -122.5754 | 0.14649 | 0.15106 | 0.091553 | 0.068664 | 0.009155 | 0.07782 | 0.013733 | 0.064087 | -0.018311 | 0.13275 | 0.064087 | 6.015 | 0.14649 | -116.7572 | -122.5571 | 5.896 | 0.064087 | 5.9647 | 0.068665
5047 | 122.5388 | -0.10071 | 122.5021 | -0.02739 | 0.014009 | 0.010703 | -0.007654 | 0.0061395 | -0.0098438 | -0.0055862 | -0.005371 | 0.019326 | 0.043276 | -0.0082287 | 0.011907 | 0.023751 | -0.0023435 | 5.8182 | 5.864 | 5.7404 | 5.7266 | 5.8182 | 5.6854 | 5.7449 | -0.054932 | 0.027466 | -0.050354 | -0.059509 | 0.004578 | -0.013733 | 0.045776 | 5.8411 | -116.6382 | -116.7755 | 5.9189 | 5.8456 | 5.7861 | 0.004578 | -0.054931 | 0.050354 | -122.4747 | -122.5616 | 0.10529 | 0.14648 | 0.086975 | 0.09613 | 0.036621 | 0.07782 | -0.013732 | 0.054932 | -0.009155 | 0.1236 | 0.07782 | 5.9647 | 0.12817 | -116.7618 | -122.5525 | 5.8273 | 0.041199 | 5.9189 | 0.045776
5048.7188 | 122.58 | -0.12817 | 122.5296 | -0.02739 | 0.0123 | 0.0092072 | -0.006586 | 0.00058534 | -0.010271 | -0.0028092 | -0.005371 | 0.022103 | 0.044344 | -0.019978 | 0.013616 | 0.022896 | -0.0038389 | 5.9235 | 5.9463 | 5.8319 | 5.864 | 5.9601 | 5.8685 | 5.8731 | -0.009155 | 0.036621 | -0.059509 | -0.027466 | 0.086975 | 0.050354 | 0.07782 | 5.9601 | -116.5833 | -116.6656 | 6.0883 | 6.0013 | 5.9967 | 0.041199 | 0.036621 | 0.068665 | -122.493 | -122.5571 | 0.21515 | 0.20599 | 0.17853 | 0.13733 | 0.10986 | 0.12817 | 0.032044 | 0.14648 | 0.032043 | 0.11444 | 0.09613 | 6.0745 | 0.1648 | -116.6977 | -122.5891 | 5.9921 | 0.10071 | 6.0516 | 0.11902
5050.4844 | 122.5891 | -0.086975 | 122.5113 | -0.01976 | 0.010805 | 0.0089936 | -0.011286 | 0.0010125 | -0.0094164 | -0.0019546 | -0.0084228 | 0.021676 | 0.042421 | -0.022755 | 0.011053 | 0.02311 | -0.0051205 | 5.9418 | 5.8914 | 5.8136 | 5.928 | 6.0471 | 5.9326 | 5.9555 | 0.045776 | 0.009155 | -0.045776 | -0.018311 | 0.10529 | 0.082397 | 0.07782 | 5.9006 | -116.6199 | -116.5833 | 6.134 | 6.0425 | 6.0196 | 0.14191 | 0.11902 | 0.041199 | -122.5021 | -122.5296 | 0.19226 | 0.16479 | 0.16937 | 0.1236 | 0.12817 | 0.23346 | 0.11444 | 0.15106 | 0.027465 | 0.077819 | 0.054931 | 5.9784 | 0.09613 | -116.6977 | -122.5571 | 6.015 | 0.068664 | 6.0287 | 0.13275
5052.2656 | 122.5845 | -0.10529 | 122.4792 | -0.01976 | 0.012941 | 0.009848 | -0.0057314 | -0.0036871 | -0.0081348 | -0.002382 | -0.0084228 | 0.020608 | 0.040285 | -0.0073743 | 0.013189 | 0.023323 | -0.0010617 | 5.9189 | 5.928 | 5.809 | 5.8365 | 5.9418 | 5.8411 | 5.8548 | 0 | 0.036621 | -0.041199 | -0.013733 | 0.086975 | 0.045776 | 0.068665 | 5.9143 | -116.5512 | -116.6428 | 6.0471 | 5.9601 | 5.9464 | 0.045776 | 0.032043 | 0.064087 | -122.4426 | -122.493 | 0.19226 | 0.17395 | 0.15106 | 0.10986 | 0.086975 | 0.13275 | 0.027466 | 0.12817 | 0.027466 | 0.11902 | 0.07782 | 6.0333 | 0.14191 | -116.6702 | -122.5204 | 5.9418 | 0.091553 | 6.0242 | 0.10529
5054.0625 | 122.6074 | -0.086975 | 122.4838 | -0.0045011 | 0.011019 | 0.00878 | -0.0097904 | 0.0010125 | -0.013475 | -0.0043046 | -0.0084228 | 0.018045 | 0.041353 | -0.017842 | 0.012334 | 0.023964 | -0.00042085 | 5.809 | 5.777 | 5.7358 | 5.7816 | 5.9097 | 5.777 | 5.8136 | 0.018311 | 0.009155 | -0.032043 | -0.022888 | 0.10071 | 0.068665 | 0.091553 | 5.8228 | -116.7068 | -116.7023 | 5.9967 | 5.9006 | 5.864 | 0.07782 | 0.041199 | 0.054932 | -122.4747 | -122.5067 | 0.18768 | 0.17853 | 0.15564 | 0.1236 | 0.10071 | 0.17395 | 0.045776 | 0.13275 | 0.009155 | 0.041199 | 0.041198 | 5.864 | 0.09613 | -116.748 | -122.5159 | 5.8685 | 0.064087 | 5.896 | 0.10529
5055.8438 | 122.5891 | -0.10071 | 122.5296 | -0.0045011 | 0.014223 | 0.0094208 | -0.0072268 | 0.0016535 | -0.010271 | -0.0055862 | -0.005371 | 0.020395 | 0.042421 | -0.016347 | 0.012121 | 0.023964 | -0.0036253 | 5.9006 | 5.896 | 5.7953 | 5.8228 | 5.9189 | 5.8411 | 5.8456 | -0.022888 | 0.018311 | -0.045776 | -0.027466 | 0.086975 | 0.041199 | 0.059509 | 5.896 | -116.6336 | -116.7068 | 6.0196 | 5.9463 | 5.9418 | 0.050354 | 0.045776 | 0.054932 | -122.5113 | -122.5571 | 0.18768 | 0.16022 | 0.14191 | 0.10528 | 0.086975 | 0.1236 | 0.027466 | 0.13275 | 0.01831 | 0.10071 | 0.064087 | 5.9967 | 0.11902 | -116.7343 | -122.5754 | 5.9235 | 0.073242 | 6.0013 | 0.07782
5057.5469 | 122.6624 | -0.059509 | 122.4564 | -0.012131 | 0.015505 | 0.0089936 | -0.0074404 | 0.0025079 | -0.00963 | -0.0043046 | -0.005371 | 0.018472 | 0.040499 | -0.018696 | 0.012334 | 0.024178 | -0.0014891 | 5.8365 | 5.7495 | 5.7037 | 5.8044 | 5.9189 | 5.7541 | 5.8044 | 0.10986 | 0 | -0.022888 | 0.064087 | 0.17395 | 0.1236 | 0.14191 | 5.7632 | -116.7068 | -116.6519 | 5.9784 | 5.864 | 5.8136 | 0.10071 | 0.050354 | 0.036621 | -122.4564 | -122.3923 | 0.23346 | 0.20142 | 0.1831 | 0.16479 | 0.14648 | 0.21515 | 0.10071 | 0.19684 | 0.086975 | 0.045777 | 0.022888 | 5.809 | 0.059509 | -116.7526 | -122.4792 | 5.864 | 0.1236 | 5.896 | 0.16937
5059.3281 | 122.5342 | -0.1236 | 122.5159 | -0.01976 | 0.012514 | 0.0068574 | -0.010858 | -0.0011237 | -0.011553 | -0.0030228 | -0.011475 | 0.020608 | 0.04178 | -0.016774 | 0.01148 | 0.022469 | -0.0044797 | 5.8548 | 5.9509 | 5.777 | 5.8136 | 5.928 | 5.8319 | 5.8548 | -0.07782 | 0.032043 | -0.054932 | -0.09613 | 0.032043 | 0.018311 | 0.022888 | 5.9006 | -116.5649 | -116.7023 | 6.0516 | 5.9784 | 5.9555 | 0.077819 | 0.054931 | 0.068664 | -122.4838 | -122.612 | 0.15564 | 0.14648 | 0.14191 | 0.07782 | 0.073243 | 0.15106 | 0.036621 | 0.086975 | -0.041198 | 0.17395 | 0.086975 | 6.0745 | 0.15564 | -116.7389 | -122.5708 | 5.9372 | 0.027466 | 5.9784 | 0.045776
5061.0469 | 122.5204 | -0.10071 | 122.5067 | -0.012131 | 0.014864 | 0.0092072 | -0.006586 | -5.5462e-05 | -0.0081348 | -0.005159 | -0.005371 | 0.022317 | 0.042849 | -0.013142 | 0.012762 | 0.023537 | -0.0012753 | 5.7816 | 5.8182 | 5.6763 | 5.6854 | 5.7587 | 5.6488 | 5.6763 | -0.082397 | 0.022888 | -0.064087 | -0.054932 | 0.018311 | -0.022888 | 0.036621 | 5.777 | -116.6885 | -116.8213 | 5.8594 | 5.777 | 5.7495 | 0 | -0.027466 | 0.036621 | -122.4838 | -122.5616 | 0.11902 | 0.13733 | 0.07782 | 0.10071 | 0.041199 | 0.082397 | 0.009155 | 0.082398 | 0.009155 | 0.14191 | 0.086975 | 5.9189 | 0.1236 | -116.8304 | -122.5708 | 5.7861 | 0.045776 | 5.8823 | 0.018311
5062.8125 | 122.5571 | -0.09613 | 122.5296 | -0.01976 | 0.013155 | 0.011557 | -0.0070132 | 0.0014397 | -0.0098438 | -0.0064408 | -0.005371 | 0.021463 | 0.04178 | -0.0084423 | 0.011907 | 0.022683 | -0.0029843 | 5.7404 | 5.7907 | 5.6534 | 5.6534 | 5.7724 | 5.6305 | 5.6763 | -0.068665 | 0.036621 | -0.064087 | -0.059509 | 0.027466 | 0.004578 | 0.045776 | 5.7495 | -116.7389 | -116.8762 | 5.8685 | 5.7724 | 5.7266 | 0.022889 | -0.022888 | 0.032043 | -122.493 | -122.5891 | 0.1236 | 0.14191 | 0.10071 | 0.10986 | 0.068665 | 0.11902 | 0 | 0.091553 | 0.004578 | 0.13733 | 0.10071 | 5.8868 | 0.13275 | -116.8762 | -122.5937 | 5.7495 | 0.036621 | 5.8365 | 0.027465
5064.5312 | 122.5479 | -0.10529 | 122.5204 | -0.02739 | 0.010164 | 0.0077118 | -0.0070132 | 0.0037897 | -0.010485 | -0.001741 | -0.005371 | 0.020608 | 0.04178 | -0.012715 | 0.012975 | 0.024605 | 0.0012881 | 5.8411 | 5.896 | 5.7541 | 5.777 | 5.8868 | 5.7724 | 5.8228 | -0.07782 | 0.027466 | -0.059509 | -0.064087 | 0.036621 | 0.018311 | 0.045776 | 5.8594 | -116.6245 | -116.7435 | 5.9921 | 5.928 | 5.8777 | 0.068665 | 0.018311 | 0.045777 | -122.493 | -122.5845 | 0.14191 | 0.15106 | 0.1236 | 0.10528 | 0.07782 | 0.13275 | 0.022889 | 0.09613 | -0.004578 | 0.14191 | 0.086975 | 6.0013 | 0.13275 | -116.7664 | -122.58 | 5.8823 | 0.041199 | 5.9464 | 0.027466
5066.3125 | 122.5525 | -0.09613 | 122.5204 | -0.0045011 | 0.012087 | 0.0089936 | -0.0095766 | 0.0033623 | -0.011125 | -0.00345 | -0.005371 | 0.019326 | 0.040071 | -0.022755 | 0.015325 | 0.023964 | -0.0034117 | 5.8777 | 5.8365 | 5.7541 | 5.8136 | 5.9463 | 5.809 | 5.8548 | 0 | 0.032043 | -0.050354 | -0.064087 | 0.059509 | 0.032043 | 0.050354 | 5.8502 | -116.684 | -116.7068 | 6.0425 | 5.9509 | 5.9052 | 0.10071 | 0.054932 | 0.045776 | -122.4884 | -122.5845 | 0.15564 | 0.14648 | 0.12817 | 0.10071 | 0.082397 | 0.19226 | 0.05951 | 0.10986 | -0.013733 | 0.082398 | 0.082397 | 5.9326 | 0.12817 | -116.7664 | -122.5708 | 5.9097 | 0.032043 | 5.9738 | 0.09613
5068.0312 | 122.5296 | -0.11902 | 122.5067 | -0.01976 | 0.011446 | 0.0094208 | -0.0080814 | 0.00058534 | -0.012194 | -0.0053726 | -0.0084228 | 0.021035 | 0.043917 | -0.024464 | 0.012121 | 0.024391 | -0.0038389 | 5.7953 | 5.864 | 5.7312 | 5.7541 | 5.8731 | 5.7724 | 5.777 | -0.054932 | 0.032043 | -0.059509 | -0.07782 | 0.032043 | 0.004578 | 0.022888 | 5.8502 | -116.6428 | -116.7526 | 5.9921 | 5.896 | 5.8914 | 0.045777 | 0.041199 | 0.05951 | -122.4747 | -122.5845 | 0.15106 | 0.14191 | 0.1236 | 0.082397 | 0.064087 | 0.14191 | 0.022888 | 0.091552 | -0.018311 | 0.13275 | 0.091552 | 5.983 | 0.15106 | -116.7755 | -122.5662 | 5.8731 | 0.041199 | 5.9143 | 0.064087
5069.8281 | 122.6166 | -0.073242 | 122.4976 | -0.01976 | 0.011446 | 0.00878 | -0.0087222 | -0.0034735 | -0.011125 | -0.0015274 | -0.0023192 | 0.021463 | 0.042849 | -0.022328 | 0.012975 | 0.023751 | 6.346e-06 | 5.7312 | 5.7129 | 5.6488 | 5.7129 | 5.8411 | 5.6946 | 5.7541 | 0.032043 | 0.009155 | -0.045776 | -0.009155 | 0.11902 | 0.091553 | 0.082397 | 5.722 | -116.7847 | -116.7847 | 5.9143 | 5.8273 | 5.7678 | 0.10528 | 0.045776 | 0.027466 | -122.4884 | -122.5067 | 0.19226 | 0.15564 | 0.16479 | 0.12817 | 0.13733 | 0.19226 | 0.064087 | 0.16479 | 0.036621 | 0.064087 | 0.054931 | 5.7861 | 0.082397 | -116.8488 | -122.5433 | 5.7861 | 0.064087 | 5.8044 | 0.10529
5071.5469 | 122.5296 | -0.11444 | 122.5433 | -0.0045011 | 0.014223 | 0.0085662 | -0.0095766 | 0.0016535 | -0.010271 | -0.0021682 | -0.0023192 | 0.020181 | 0.04413 | -0.017628 | 0.012121 | 0.020974 | -0.00084805 | 5.7861 | 5.8273 | 5.7083 | 5.7449 | 5.8548 | 5.7541 | 5.7632 | -0.054932 | 0.036621 | -0.073242 | -0.07782 | 0.013733 | 0.004578 | 0.027466 | 5.8228 | -116.716 | -116.7984 | 5.9692 | 5.8777 | 5.8685 | 0.054932 | 0.045776 | 0.041199 | -122.5067 | -122.6212 | 0.12817 | 0.14191 | 0.11902 | 0.10071 | 0.07782 | 0.14648 | 0.036621 | 0.086975 | -0.004578 | 0.11902 | 0.10986 | 5.9418 | 0.15106 | -116.835 | -122.6166 | 5.8594 | 0.036621 | 5.9006 | 0.059509
5073.3281 | 122.6898 | -0.059509 | 122.5021 | -0.01976 | 0.0088824 | 0.007071 | -0.010004 | -0.0015509 | -0.011553 | -0.0021682 | -0.0084228 | 0.019113 | 0.043703 | -0.015492 | 0.0095575 | 0.022469 | -0.00084805 | 5.809 | 5.7404 | 5.6946 | 5.8044 | 5.9418 | 5.809 | 5.864 | 0.14191 | 0.009155 | -0.018311 | 0.054932 | 0.19226 | 0.16022 | 0.15106 | 5.7541 | -116.7618 | -116.6977 | 6.0013 | 5.9235 | 5.8685 | 0.16937 | 0.11444 | 0.041198 | -122.493 | -122.4472 | 0.25177 | 0.21057 | 0.21973 | 0.16937 | 0.17853 | 0.24719 | 0.10986 | 0.21057 | 0.073243 | 0.045776 | 0.027466 | 5.7999 | 0.068664 | -116.8076 | -122.5204 | 5.864 | 0.11444 | 5.8685 | 0.20142
5075.1094 | 122.5342 | -0.11444 | 122.5342 | -0.01976 | 0.014864 | 0.010062 | -0.004877 | 0.0029351 | -0.011125 | -0.0043046 | -0.0084228 | 0.023599 | 0.04413 | -0.0095105 | 0.011907 | 0.024391 | -0.0053343 | 5.6854 | 5.7175 | 5.6122 | 5.603 | 5.6946 | 5.5618 | 5.5984 | -0.064087 | 0.022888 | -0.054932 | -0.064087 | 0 | -0.027466 | 0.036621 | 5.7266 | -116.8167 | -116.9312 | 5.809 | 5.7129 | 5.6763 | -0.013733 | -0.050354 | 0.059509 | -122.5113 | -122.5983 | 0.11444 | 0.15106 | 0.086975 | 0.091553 | 0.027466 | 0.082397 | -0.009156 | 0.054932 | -0.009155 | 0.10529 | 0.07782 | 5.8319 | 0.13733 | -116.922 | -122.5891 | 5.7175 | 0.050354 | 5.7999 | 0.050354
5076.875 | 122.5571 | -0.10529 | 122.5296 | -0.012131 | 0.011019 | 0.0068574 | -0.0091494 | -0.0047553 | -0.011339 | -0.0040908 | -0.0084228 | 0.022317 | 0.040499 | -0.01186 | 0.01148 | 0.022042 | -0.0055479 | 5.7678 | 5.8273 | 5.6763 | 5.7129 | 5.8319 | 5.7404 | 5.7587 | -0.068665 | 0.041199 | -0.064087 | -0.082397 | 0.045776 | 0.004578 | 0.027466 | 5.7816 | -116.7023 | -116.8167 | 5.9372 | 5.864 | 5.8456 | 0.082397 | 0.064086 | 0.041199 | -122.4884 | -122.612 | 0.15106 | 0.13275 | 0.10986 | 0.091553 | 0.068665 | 0.15564 | 0.036621 | 0.10986 | -0.01831 | 0.15106 | 0.10529 | 5.9326 | 0.14649 | -116.8533 | -122.5937 | 5.8182 | 0.022889 | 5.8731 | 0.036621
5078.5938 | 122.6761 | -0.050354 | 122.5021 | -0.01976 | 0.011019 | 0.0085662 | -0.010004 | -0.00091006 | -0.010698 | -0.0021682 | -0.005371 | 0.020181 | 0.042208 | -0.016133 | 0.013403 | 0.024605 | -0.0042661 | 5.7907 | 5.7129 | 5.6671 | 5.7953 | 5.9509 | 5.8044 | 5.8182 | 0.15106 | -0.022888 | -0.018311 | 0.032043 | 0.20142 | 0.16479 | 0.12817 | 5.7175 | -116.7892 | -116.7068 | 6.0013 | 5.8685 | 5.8548 | 0.15106 | 0.13733 | 0.032043 | -122.525 | -122.4701 | 0.25177 | 0.17853 | 0.21515 | 0.14649 | 0.18311 | 0.28381 | 0.12817 | 0.21973 | 0.050354 | 0.045777 | -0.004577 | 5.7632 | 0.027466 | -116.835 | -122.5204 | 5.8456 | 0.082397 | 5.8411 | 0.20142
5080.3125 | 122.5342 | -0.091553 | 122.5296 | -0.01976 | 0.013155 | 0.009848 | -0.0067996 | 0.00079894 | -0.010698 | -0.0011002 | -0.005371 | 0.023599 | 0.04178 | -0.016987 | 0.015112 | 0.024178 | -0.0034117 | 5.6992 | 5.7083 | 5.6122 | 5.6122 | 5.7083 | 5.5801 | 5.6076 | -0.041199 | 0.022888 | -0.064087 | -0.054932 | 0.018311 | -0.032043 | 0.022888 | 5.7037 | -116.8213 | -116.9174 | 5.7999 | 5.6992 | 5.6717 | -0.004578 | -0.032044 | 0.027466 | -122.5067 | -122.5845 | 0.10986 | 0.11444 | 0.05951 | 0.086975 | 0.032044 | 0.09613 | 0 | 0.082398 | 0.009155 | 0.09613 | 0.086975 | 5.7999 | 0.11444 | -116.9174 | -122.5937 | 5.7037 | 0.036621 | 5.7907 | 0.050354
5082.0781 | 122.6349 | -0.059509 | 122.5113 | -0.02739 | 0.016359 | 0.010703 | -0.010004 | -0.0039007 | -0.008562 | -0.0057998 | -0.005371 | 0.017831 | 0.040499 | -0.022542 | 0.014043 | 0.023964 | -0.0021299 | 6.9901 | 6.871 | 6.8115 | 6.9626 | 7.1045 | 6.9397 | 6.9717 | 0.10986 | -0.022888 | -0.027466 | 0.054932 | 0.13275 | 0.09613 | 0.12817 | 6.871 | -115.6403 | -115.5487 | 7.164 | 7.0312 | 6.9992 | 0.16022 | 0.12817 | 0.032043 | -122.5342 | -122.4564 | 0.19226 | 0.18768 | 0.15564 | 0.15564 | 0.1236 | 0.29297 | 0.15106 | 0.16022 | 0.082398 | 0.05951 | 0.004578 | 6.9305 | 0.036621 | -115.6998 | -122.5388 | 7.0221 | 0.11444 | 7.0496 | 0.16937
5083.7969 | 122.5433 | -0.11444 | 122.5342 | -0.02739 | 0.014223 | 0.01113 | -0.0046634 | 0.0025079 | -0.0081348 | -0.00345 | -0.005371 | 0.022317 | 0.043703 | -0.01421 | 0.014684 | 0.023964 | -0.0017027 | 6.9443 | 6.958 | 6.7932 | 6.8436 | 6.926 | 6.7978 | 6.8573 | -0.054932 | 0.036621 | -0.050354 | -0.059509 | 0.009155 | -0.032043 | 0.022888 | 6.9077 | -115.5762 | -115.6906 | 7.0404 | 6.9717 | 6.9122 | 0.064087 | 0.004578 | 0.064087 | -122.4976 | -122.5937 | 0.1236 | 0.13733 | 0.082398 | 0.073242 | 0.018311 | 0.13275 | 0.050354 | 0.059509 | -0.009155 | 0.1648 | 0.086975 | 7.0724 | 0.15106 | -115.741 | -122.5845 | 6.958 | 0.054932 | 7.0587 | 0.059509
5085.5625 | 122.5433 | -0.10071 | 122.5388 | -0.01976 | 0.014437 | 0.0096344 | -0.005945 | 0.0048577 | -0.0098438 | -0.0015274 | -0.0084228 | 0.022958 | 0.043489 | -0.018483 | 0.012975 | 0.022469 | -0.0068295 | 6.9351 | 6.9397 | 6.7841 | 6.839 | 6.9168 | 6.8069 | 6.8436 | -0.07782 | 0.027466 | -0.064087 | -0.059509 | 0.009155 | -0.036621 | 0.036621 | 6.8848 | -115.5991 | -115.6998 | 7.0175 | 6.9443 | 6.9077 | 0.059509 | 0.022888 | 0.036621 | -122.5113 | -122.5983 | 0.10986 | 0.13733 | 0.064087 | 0.10071 | 0.027466 | 0.13275 | 0.054931 | 0.073242 | 0.004578 | 0.15564 | 0.091553 | 7.0404 | 0.12817 | -115.7547 | -122.6028 | 6.9397 | 0.041199 | 7.0358 | 0.022888
5087.3281 | 122.5296 | -0.10071 | 122.5433 | -0.012131 | 0.011446 | 0.00878 | -0.0089358 | 0.0018671 | -0.012621 | -0.0040908 | -0.011475 | 0.020395 | 0.043489 | -0.013569 | 0.011907 | 0.023537 | -0.0046933 | 5.6854 | 5.7266 | 5.6259 | 5.6168 | 5.7449 | 5.6442 | 5.6717 | -0.059509 | 0.050354 | -0.07782 | -0.086975 | 0.032043 | 0.018311 | 0.027466 | 5.7266 | -116.8167 | -116.9266 | 5.8456 | 5.7724 | 5.7449 | 0.045776 | 0.01831 | 0.022888 | -122.493 | -122.6303 | 0.13275 | 0.12817 | 0.11902 | 0.10529 | 0.096131 | 0.11902 | -0.009156 | 0.10986 | -0.009155 | 0.10071 | 0.12817 | 5.8273 | 0.15106 | -116.9174 | -122.6212 | 5.7175 | 0.013733 | 5.7861 | 0.041199
5089.0625 | 122.5571 | -0.10986 | 122.5342 | -0.012131 | 0.011446 | 0.0096344 | -0.010431 | -0.00069646 | -0.0092028 | -0.0021682 | -0.011475 | 0.019113 | 0.041567 | -0.0082287 | 0.01148 | 0.023323 | -0.0027707 | 5.7404 | 5.7037 | 5.6213 | 5.6717 | 5.7953 | 5.6763 | 5.6854 | -0.022888 | 0.004578 | -0.050354 | -0.068665 | 0.059509 | 0.027466 | 0.022888 | 5.7312 | -116.8304 | -116.8625 | 5.9052 | 5.7953 | 5.7861 | 0.064087 | 0.054932 | 0.059509 | -122.5296 | -122.6028 | 0.16937 | 0.13275 | 0.13733 | 0.073242 | 0.07782 | 0.17395 | 0.050354 | 0.10986 | -0.018311 | 0.082397 | 0.054932 | 5.8136 | 0.11444 | -116.9128 | -122.5845 | 5.7816 | 0.041198 | 5.8502 | 0.086975
5090.8438 | 122.6028 | -0.07782 | 122.5067 | -0.01976 | 0.012728 | 0.010916 | -0.0072268 | 0.00058534 | -0.006853 | -0.0047318 | -0.0084228 | 0.020608 | 0.043276 | -0.018269 | 0.012548 | 0.023537 | -0.0061887 | 5.6854 | 5.69 | 5.571 | 5.6259 | 5.7449 | 5.6076 | 5.6351 | 0.027466 | 0.032043 | -0.036621 | -0.013733 | 0.091553 | 0.045776 | 0.064087 | 5.6488 | -116.8167 | -116.8808 | 5.8228 | 5.7129 | 5.6854 | 0.064087 | 0.036621 | 0.041199 | -122.4747 | -122.5204 | 0.16937 | 0.14191 | 0.1236 | 0.10071 | 0.082397 | 0.17395 | 0.054932 | 0.12817 | 0.022888 | 0.11902 | 0.068664 | 5.7678 | 0.10986 | -116.9357 | -122.5433 | 5.7037 | 0.064087 | 5.7632 | 0.10529
5092.5469 | 122.6624 | -0.064087 | 122.5113 | -0.01976 | 0.013155 | 0.012412 | -0.009363 | 0.0037897 | -0.0081348 | -0.0036636 | -0.005371 | 0.019113 | 0.040712 | -0.018696 | 0.012975 | 0.024819 | -0.0021299 | 5.6213 | 5.5252 | 5.4886 | 5.5984 | 5.7266 | 5.5618 | 5.6076 | 0.11444 | -0.004578 | -0.022888 | 0.064087 | 0.17853 | 0.10986 | 0.14648 | 5.5527 | -116.9861 | -116.9128 | 5.7907 | 5.6717 | 5.6259 | 0.11902 | 0.073243 | 0.041199 | -122.5159 | -122.4472 | 0.24261 | 0.21057 | 0.17395 | 0.16937 | 0.13275 | 0.23804 | 0.10986 | 0.20142 | 0.086975 | 0.036622 | 0.01831 | 5.5893 | 0.059509 | -117.0227 | -122.5342 | 5.6625 | 0.12817 | 5.6854 | 0.17853
5094.3281 | 122.5983 | -0.091553 | 122.5159 | -0.012131 | 0.014437 | 0.0085662 | -0.0072268 | -0.0017645 | -0.010485 | -0.001741 | -0.005371 | 0.02189 | 0.042208 | -0.016133 | 0.013189 | 0.025673 | -0.0051205 | 5.6808 | 5.6717 | 5.5756 | 5.6168 | 5.7312 | 5.5984 | 5.6122 | 0.022888 | 0.022888 | -0.064087 | -0.018311 | 0.086975 | 0.059509 | 0.064087 | 5.6671 | -116.8442 | -116.8991 | 5.8228 | 5.7037 | 5.69 | 0.036621 | 0.022888 | 0.027466 | -122.493 | -122.5342 | 0.17853 | 0.15564 | 0.15106 | 0.12817 | 0.1236 | 0.15564 | 0.041198 | 0.15106 | 0.045776 | 0.09613 | 0.086975 | 5.7632 | 0.11444 | -116.9403 | -122.58 | 5.7083 | 0.073242 | 5.7724 | 0.11444
5096.0312 | 122.5662 | -0.11444 | 122.5296 | -0.01976 | 0.013155 | 0.0092072 | -0.0085086 | -0.00026906 | -0.0072802 | -0.00345 | -0.011475 | 0.021249 | 0.043489 | -0.016133 | 0.01383 | 0.024178 | -0.00084805 | 5.5435 | 5.5801 | 5.4657 | 5.4474 | 5.571 | 5.4245 | 5.484 | -0.073242 | 0.036621 | -0.068665 | -0.073242 | 0.022888 | -0.004578 | 0.045776 | 5.5801 | -116.9495 | -117.0822 | 5.6854 | 5.5985 | 5.5389 | 0.018311 | -0.041198 | 0.045776 | -122.493 | -122.6028 | 0.13733 | 0.16022 | 0.10986 | 0.11444 | 0.064087 | 0.10529 | -0.01831 | 0.091553 | -0.004577 | 0.11444 | 0.10529 | 5.6946 | 0.15106 | -117.0639 | -122.5983 | 5.5618 | 0.041199 | 5.658 | 0.041199
5097.7969 | 122.5571 | -0.10071 | 122.5342 | -0.012131 | 0.014437 | 0.010916 | -0.0080814 | 0.0016535 | -0.010485 | -0.001741 | -0.005371 | 0.020395 | 0.042421 | -0.017628 | 0.01148 | 0.023323 | -0.0040525 | 5.6168 | 5.603 | 5.5161 | 5.5252 | 5.6442 | 5.5023 | 5.5435 | -0.018311 | 0.018311 | -0.050354 | -0.045776 | 0.036621 | 0 | 0.041199 | 5.6168 | -116.9312 | -117.009 | 5.7449 | 5.6442 | 5.603 | 0.027466 | -0.013733 | 0.050354 | -122.5159 | -122.58 | 0.13733 | 0.14191 | 0.10071 | 0.091553 | 0.050354 | 0.12817 | 0.009156 | 0.086975 | 0.004578 | 0.086975 | 0.068665 | 5.7037 | 0.11902 | -117.0181 | -122.5845 | 5.6259 | 0.054932 | 5.7175 | 0.082397
5099.5781 | 122.644 | -0.073242 | 122.4976 | -0.01976 | 0.009737 | 0.0094208 | -0.010431 | -0.0011237 | -0.0098438 | -0.00345 | -0.0084228 | 0.019326 | 0.040712 | -0.018696 | 0.010839 | 0.024178 | -0.0017027 | 4.1428 | 4.1702 | 4.1016 | 4.129 | 4.2435 | 4.129 | 4.1565 | 0.018311 | 0.004578 | -0.036621 | -0.009155 | 0.11902 | 0.11444 | 0.10529 | 4.1748 | -118.3273 | -118.3685 | 4.3167 | 4.2297 | 4.2023 | 0.054932 | 0.027466 | 0.036621 | -122.493 | -122.5067 | 0.19226 | 0.17853 | 0.18768 | 0.14191 | 0.15106 | 0.14191 | 0.027466 | 0.15564 | 0.027466 | 0.068665 | 0.041199 | 4.2435 | 0.07782 | -118.396 | -122.5342 | 4.2023 | 0.064087 | 4.216 | 0.091553
5101.3594 | 122.6852 | -0.064087 | 122.4884 | -0.0045011 | 0.010164 | 0.0094208 | -0.011499 | -0.0019781 | -0.012407 | -0.0045182 | -0.005371 | 0.017831 | 0.040499 | -0.020405 | 0.012121 | 0.023751 | -0.0027707 | 4.2435 | 4.2023 | 4.1565 | 4.2389 | 4.3945 | 4.2664 | 4.303 | 0.12817 | -0.004578 | -0.041199 | 0.045776 | 0.19226 | 0.15564 | 0.12817 | 4.2206 | -118.2861 | -118.2495 | 4.4586 | 4.3671 | 4.3304 | 0.14648 | 0.10986 | 0.022888 | -122.493 | -122.4426 | 0.25635 | 0.19226 | 0.21973 | 0.16937 | 0.19684 | 0.23804 | 0.082398 | 0.23346 | 0.086975 | 0.045777 | 0.036621 | 4.2664 | 0.059509 | -118.3319 | -122.5296 | 4.303 | 0.10986 | 4.3076 | 0.19226
5103.0781 | 122.5662 | -0.10529 | 122.525 | -0.01976 | 0.010378 | 0.0092072 | -0.0072268 | 0.0018671 | -0.010485 | -0.0019546 | -0.0084228 | 0.019113 | 0.039217 | -0.017842 | 0.011694 | 0.022255 | -0.0057615 | 4.2114 | 4.2389 | 4.1565 | 4.1565 | 4.2801 | 4.1611 | 4.2068 | -0.036621 | 0.032043 | -0.050354 | -0.082397 | 0.041199 | 0.013733 | 0.032043 | 4.2618 | -118.2861 | -118.3685 | 4.3854 | 4.3121 | 4.2664 | 0.050354 | 0.004578 | 0.054932 | -122.493 | -122.6074 | 0.14649 | 0.13733 | 0.11902 | 0.082397 | 0.064087 | 0.1236 | 0 | 0.091553 | -0.032043 | 0.082398 | 0.082397 | 4.3442 | 0.13733 | -118.3685 | -122.5754 | 4.2618 | 0.022889 | 4.3167 | 0.068665
5104.875 | 122.6166 | -0.082397 | 122.5113 | -0.01976 | 0.012728 | 0.0092072 | -0.007654 | -0.00091006 | -0.0092028 | -0.0028092 | -0.0084228 | 0.020395 | 0.040499 | -0.018483 | 0.013616 | 0.022042 | -0.0027707 | 4.1748 | 4.1885 | 4.1107 | 4.129 | 4.2435 | 4.1107 | 4.1428 | 0.013733 | 0.050354 | -0.059509 | -0.022888 | 0.09613 | 0.059509 | 0.082397 | 4.1931 | -118.3228 | -118.3823 | 4.3259 | 4.2252 | 4.1931 | 0.032043 | 0 | 0.022888 | -122.4609 | -122.5342 | 0.17853 | 0.16479 | 0.14191 | 0.14191 | 0.11902 | 0.13275 | 0.01831 | 0.15564 | 0.036621 | 0.07782 | 0.10986 | 4.2709 | 0.13275 | -118.4006 | -122.5708 | 4.2114 | 0.059509 | 4.2572 | 0.09613
5106.6562 | 122.5479 | -0.1236 | 122.5433 | -0.0045011 | 0.0099506 | 0.0083526 | -0.0087222 | -0.00091006 | -0.012621 | -0.001741 | -0.0023192 | 0.022103 | 0.041567 | -0.015492 | 0.010626 | 0.021828 | -0.0068295 | 4.1794 | 4.2389 | 4.1473 | 4.1245 | 4.2389 | 4.1382 | 4.1656 | -0.059509 | 0.041199 | -0.064087 | -0.07782 | 0.041199 | 0.013733 | 0.041199 | 4.2709 | -118.3044 | -118.4189 | 4.3625 | 4.2892 | 4.2618 | 0.01831 | -0.009155 | 0.059509 | -122.5021 | -122.6212 | 0.16479 | 0.16479 | 0.13733 | 0.10529 | 0.07782 | 0.091553 | -0.022888 | 0.10529 | -0.013733 | 0.091553 | 0.10529 | 4.3625 | 0.16479 | -118.396 | -122.6074 | 4.248 | 0.045776 | 4.303 | 0.064087
5108.3594 | 122.5433 | -0.11444 | 122.5525 | -0.0045011 | 0.015718 | 0.0079254 | -0.0097904 | -0.00048286 | -0.0087756 | -0.0032364 | -0.005371 | 0.020395 | 0.041994 | -0.013142 | 0.013189 | 0.023751 | -0.0034117 | 4.1107 | 4.1428 | 4.0741 | 4.0329 | 4.1473 | 4.0146 | 4.0466 | -0.045776 | 0.027466 | -0.032043 | -0.064087 | 0.022888 | -0.013733 | 0.027466 | 4.1885 | -118.4097 | -118.5196 | 4.2618 | 4.1611 | 4.129 | -0.027466 | -0.05951 | 0.082398 | -122.525 | -122.6166 | 0.13733 | 0.14191 | 0.10071 | 0.059509 | 0.01831 | 0.073242 | -0.041199 | 0.054931 | -0.032044 | 0.068664 | 0.059509 | 4.2572 | 0.14191 | -118.4784 | -122.5845 | 4.1473 | 0.050354 | 4.2252 | 0.068665
5110.1406 | 122.6898 | -0.050354 | 122.4747 | -0.012131 | 0.014437 | 0.0094208 | -0.008295 | 0.0042169 | -0.00963 | -0.0036636 | -0.005371 | 0.019967 | 0.041994 | -0.015919 | 0.010198 | 0.022896 | -0.0034117 | 5.5069 | 5.4108 | 5.3787 | 5.4794 | 5.6076 | 5.4291 | 5.5069 | 0.11444 | -0.022888 | -0.013733 | 0.064087 | 0.17853 | 0.1236 | 0.14191 | 5.4291 | -117.0639 | -116.9952 | 5.658 | 5.5573 | 5.4794 | 0.12817 | 0.050354 | 0.036621 | -122.4976 | -122.4106 | 0.22888 | 0.19226 | 0.17395 | 0.15564 | 0.13733 | 0.22888 | 0.10071 | 0.19226 | 0.07782 | 0.032044 | -0.009155 | 5.4611 | 0.027466 | -117.0959 | -122.4884 | 5.5298 | 0.11444 | 5.5573 | 0.16479
5111.8594 | 122.6852 | -0.064087 | 122.5113 | -0.01976 | 0.012087 | 0.0072846 | -0.010858 | 0.0031487 | -0.0070666 | -0.00345 | -0.011475 | 0.020181 | 0.043703 | -0.011433 | 0.012762 | 0.022042 | -0.0021299 | 5.5847 | 5.5161 | 5.4749 | 5.5893 | 5.7449 | 5.6076 | 5.6396 | 0.10529 | 0 | -0.009155 | 0.045776 | 0.1831 | 0.15564 | 0.13275 | 5.5389 | -116.9952 | -116.922 | 5.809 | 5.7037 | 5.6717 | 0.16479 | 0.13275 | 0.054932 | -122.5113 | -122.4655 | 0.24719 | 0.19684 | 0.21973 | 0.14191 | 0.16479 | 0.27008 | 0.11444 | 0.19226 | 0.054931 | 0.041198 | 0.009155 | 5.5801 | 0.064087 | -117.0364 | -122.5204 | 5.6534 | 0.10986 | 5.6488 | 0.16937
5113.6406 | 122.6898 | -0.064087 | 122.5067 | -0.01976 | 0.010378 | 0.00878 | -0.010218 | -0.0019781 | -0.011125 | -0.0057998 | 0.00073235 | 0.018472 | 0.04178 | -0.018055 | 0.011053 | 0.022469 | -0.00084805 | 5.5389 | 5.4794 | 5.4153 | 5.5115 | 5.6442 | 5.5161 | 5.5801 | 0.086975 | -0.022888 | -0.036621 | 0.041199 | 0.1831 | 0.15106 | 0.15106 | 5.4794 | -117.0273 | -116.9952 | 5.7083 | 5.6442 | 5.5801 | 0.16479 | 0.10071 | 0.027466 | -122.5296 | -122.4655 | 0.24719 | 0.21515 | 0.21515 | 0.18768 | 0.18768 | 0.22888 | 0.096131 | 0.21973 | 0.07782 | 0.064087 | 0.013733 | 5.5435 | 0.041199 | -117.0914 | -122.5433 | 5.5756 | 0.10529 | 5.603 | 0.15106
5115.4219 | 122.699 | -0.068665 | 122.5204 | -0.01976 | 0.010164 | 0.010275 | -0.009363 | -5.5462e-05 | -0.0070666 | -0.0053726 | -0.0084228 | 0.017831 | 0.043062 | -0.017201 | 0.0095575 | 0.023537 | -0.0070433 | 5.5801 | 5.4703 | 5.4565 | 5.5664 | 5.7129 | 5.5664 | 5.5939 | 0.12817 | -0.004578 | -0.018311 | 0.036621 | 0.19684 | 0.17395 | 0.1236 | 5.5252 | -117.0502 | -116.954 | 5.7816 | 5.6625 | 5.6351 | 0.13733 | 0.10986 | 0.050354 | -122.525 | -122.4838 | 0.2655 | 0.19226 | 0.24261 | 0.14191 | 0.19226 | 0.25635 | 0.10986 | 0.21515 | 0.054932 | 0.013733 | 0.013733 | 5.5389 | 0.064087 | -117.0639 | -122.5388 | 5.6351 | 0.10529 | 5.6488 | 0.19684
5117.125 | 122.5571 | -0.11444 | 122.5388 | -0.012131 | 0.014009 | 0.0094208 | -0.0080814 | 0.00079894 | -0.00963 | -0.0028092 | -0.0084228 | 0.023812 | 0.039644 | -0.013142 | 0.013403 | 0.023537 | -0.0085385 | 5.4428 | 5.4749 | 5.3604 | 5.3421 | 5.4153 | 5.3009 | 5.3375 | -0.10071 | 0.045776 | -0.059509 | -0.054932 | -0.009155 | -0.027466 | 0.036621 | 5.4749 | -117.0639 | -117.1967 | 5.5298 | 5.452 | 5.4153 | -0.022889 | -0.05951 | 0.054932 | -122.493 | -122.5937 | 0.10529 | 0.15106 | 0.086975 | 0.09613 | 0.032043 | 0.054931 | -0.018311 | 0.050354 | 0.004577 | 0.11444 | 0.10528 | 5.5893 | 0.16022 | -117.1783 | -122.5983 | 5.4565 | 0.059509 | 5.5573 | 0.013733
5118.8906 | 122.5616 | -0.10986 | 122.5433 | -0.012131 | 0.014864 | 0.010489 | -0.005945 | 0.0033623 | -0.0089892 | -0.0038772 | -0.0084228 | 0.022958 | 0.04178 | -0.0086559 | 0.014043 | 0.023751 | -0.0057615 | 5.4703 | 5.4749 | 5.365 | 5.3604 | 5.4703 | 5.3329 | 5.3696 | -0.050354 | 0.036621 | -0.045776 | -0.068665 | 0.027466 | -0.027466 | 0.013733 | 5.4749 | -117.0685 | -117.1829 | 5.5801 | 5.4794 | 5.4428 | 0.004578 | -0.032043 | 0.064087 | -122.5067 | -122.612 | 0.13733 | 0.1236 | 0.082397 | 0.059509 | 0.01831 | 0.10529 | -0.004577 | 0.073242 | -0.022889 | 0.10986 | 0.082397 | 5.5847 | 0.14648 | -117.1783 | -122.5891 | 5.4703 | 0.041198 | 5.5801 | 0.059509
5120.6562 | 122.5708 | -0.12817 | 122.5159 | -0.012131 | 0.0123 | 0.010916 | -0.0050906 | -0.00069646 | -0.012407 | -0.0013138 | -0.0084228 | 0.020822 | 0.040712 | -0.018696 | 0.013403 | 0.023751 | -0.0034117 | 5.3879 | 5.4245 | 5.3238 | 5.2917 | 5.3833 | 5.2689 | 5.3101 | -0.059509 | 0.027466 | -0.064087 | -0.059509 | 0.004578 | -0.022888 | 0.032043 | 5.452 | -117.0914 | -117.2241 | 5.5115 | 5.4382 | 5.397 | -0.013733 | -0.054932 | 0.064087 | -122.4884 | -122.5754 | 0.13275 | 0.16022 | 0.10529 | 0.09613 | 0.041199 | 0.059509 | -0.032044 | 0.068665 | 0.004578 | 0.10071 | 0.091553 | 5.5527 | 0.15564 | -117.1921 | -122.58 | 5.4199 | 0.068665 | 5.5161 | 0.068665
5122.375 | 122.6395 | -0.091553 | 122.5296 | -0.012131 | 0.013369 | 0.0077118 | -0.0091494 | 0.0033623 | -0.011553 | -0.0032364 | -0.0084228 | 0.018258 | 0.04413 | -0.021473 | 0.011907 | 0.023323 | -0.0038389 | 5.4382 | 5.3925 | 5.3375 | 5.3879 | 5.5252 | 5.397 | 5.4337 | 0.018311 | 0.013733 | -0.045776 | 0.004578 | 0.10986 | 0.068665 | 0.091553 | 5.4291 | -117.1371 | -117.1417 | 5.6168 | 5.5252 | 5.4886 | 0.096131 | 0.05951 | 0.045777 | -122.5159 | -122.525 | 0.20142 | 0.18311 | 0.16022 | 0.13733 | 0.11444 | 0.18768 | 0.050354 | 0.15564 | 0.050354 | 0.054932 | 0.059509 | 5.484 | 0.10529 | -117.1921 | -122.5754 | 5.4794 | 0.096131 | 5.5298 | 0.10986
5124.1562 | 122.612 | -0.10529 | 122.5388 | -0.012131 | 0.0123 | 0.0089936 | -0.0074404 | -0.0015509 | -0.011766 | -0.0008866 | -0.005371 | 0.021035 | 0.041353 | -0.014851 | 0.011694 | 0.023537 | -0.0034117 | 5.5023 | 5.5069 | 5.3879 | 5.4382 | 5.5344 | 5.4245 | 5.4245 | 0.018311 | 0.041199 | -0.064087 | -0.022888 | 0.09613 | 0.054932 | 0.07782 | 5.4932 | -117.0319 | -117.1005 | 5.6396 | 5.5298 | 5.5298 | 0.036622 | 0.036622 | 0.041199 | -122.4976 | -122.5616 | 0.20142 | 0.18311 | 0.16022 | 0.14191 | 0.11902 | 0.14649 | 0.050354 | 0.16022 | 0.041199 | 0.11902 | 0.10529 | 5.6122 | 0.14649 | -117.1509 | -122.6028 | 5.5435 | 0.082398 | 5.6076 | 0.1236
5125.9375 | 122.6028 | -0.10986 | 122.5296 | -0.02739 | 0.012728 | 0.010275 | -0.0070132 | 0.0044305 | -0.0098438 | -0.0049454 | -0.0084228 | 0.021249 | 0.043062 | -0.014424 | 0.012762 | 0.021614 | -0.00063445 | 5.3421 | 5.397 | 5.2597 | 5.2872 | 5.3787 | 5.2597 | 5.2963 | -0.032043 | 0.018311 | -0.054932 | -0.036621 | 0.050354 | 0.009155 | 0.054932 | 5.3696 | -117.1326 | -117.2424 | 5.4886 | 5.4062 | 5.3696 | 0.036621 | 0 | 0.054931 | -122.5113 | -122.5662 | 0.16022 | 0.16479 | 0.11902 | 0.10986 | 0.064087 | 0.11902 | 0.027465 | 0.10529 | 0.018311 | 0.13733 | 0.073243 | 5.5069 | 0.12817 | -117.2699 | -122.5845 | 5.397 | 0.073242 | 5.452 | 0.07782
5127.7188 | 122.5616 | -0.1236 | 122.5616 | -0.035019 | 0.015718 | 0.012412 | -0.006586 | 0.0067803 | -0.011339 | -0.0028092 | -0.005371 | 0.021249 | 0.040071 | -0.011647 | 0.01383 | 0.024178 | -0.00020725 | 5.3558 | 5.3879 | 5.2826 | 5.2551 | 5.3513 | 5.2231 | 5.2505 | -0.068665 | 0.022888 | -0.059509 | -0.068665 | -0.004578 | -0.027466 | 0.045776 | 5.4062 | -117.1738 | -117.3065 | 5.4749 | 5.3741 | 5.3467 | -0.032044 | -0.05951 | 0.064087 | -122.5388 | -122.6303 | 0.11902 | 0.16937 | 0.09613 | 0.10528 | 0.032043 | 0.068664 | -0.027466 | 0.054931 | -0.009156 | 0.10528 | 0.082397 | 5.5115 | 0.14648 | -117.2791 | -122.6212 | 5.3787 | 0.054931 | 5.4794 | 0.054931
5129.5 | 122.5754 | -0.10529 | 122.5342 | -0.012131 | 0.014437 | 0.0085662 | -0.0074404 | -0.00026906 | -0.0089892 | -0.0030228 | -0.005371 | 0.022531 | 0.042635 | -0.012288 | 0.013616 | 0.024178 | -0.0064023 | 5.3055 | 5.3604 | 5.2505 | 5.2505 | 5.3467 | 5.2094 | 5.2505 | -0.041199 | 0.022888 | -0.050354 | -0.054932 | 0.022888 | -0.004578 | 0.027466 | 5.3558 | -117.1738 | -117.2836 | 5.452 | 5.3558 | 5.3146 | 0 | -0.041198 | 0.054932 | -122.5113 | -122.5891 | 0.12817 | 0.13275 | 0.10071 | 0.07782 | 0.045776 | 0.096131 | 0 | 0.073242 | -0.004578 | 0.10986 | 0.073242 | 5.4657 | 0.12817 | -117.2836 | -122.5845 | 5.3558 | 0.050354 | 5.4108 | 0.064087
5131.2188 | 122.5891 | -0.10986 | 122.525 | -0.01976 | 0.0088824 | 0.0085662 | -0.0097904 | -0.0030463 | -0.011766 | -0.0045182 | -0.011475 | 0.018472 | 0.042421 | -0.013356 | 0.0099847 | 0.024178 | -0.0042661 | 5.4749 | 5.4245 | 5.3467 | 5.4382 | 5.5618 | 5.4474 | 5.4703 | 0.018311 | 0.027466 | -0.032043 | -0.041199 | 0.082397 | 0.045776 | 0.054932 | 5.4565 | -117.1005 | -117.0868 | 5.6717 | 5.5801 | 5.5573 | 0.1236 | 0.10071 | 0.07782 | -122.4976 | -122.5662 | 0.19226 | 0.16479 | 0.15564 | 0.086975 | 0.077819 | 0.21515 | 0.091552 | 0.11444 | -0.009156 | 0.07782 | 0.059509 | 5.5344 | 0.13733 | -117.1783 | -122.5571 | 5.5481 | 0.068664 | 5.5847 | 0.12817
5132.9844 | 122.644 | -0.082397 | 122.5296 | -0.01976 | 0.011232 | 0.009848 | -0.0091494 | 0.0022943 | -0.0089892 | -0.0032364 | -0.005371 | 0.016977 | 0.042421 | -0.017628 | 0.0099847 | 0.024605 | -0.0046933 | 5.3375 | 5.3101 | 5.2597 | 5.3101 | 5.4337 | 5.2917 | 5.3558 | 0.036621 | -0.013733 | -0.032043 | -0.004578 | 0.11444 | 0.068665 | 0.091553 | 5.3421 | -117.2195 | -117.2195 | 5.5161 | 5.4382 | 5.3741 | 0.09613 | 0.032043 | 0.050354 | -122.5433 | -122.5342 | 0.19684 | 0.17395 | 0.15106 | 0.1236 | 0.10071 | 0.17395 | 0.050354 | 0.14648 | 0.027465 | 0.050354 | 0.01831 | 5.3925 | 0.068664 | -117.2699 | -122.5616 | 5.3925 | 0.077819 | 5.4199 | 0.11902
5134.7812 | 122.612 | -0.086975 | 122.5616 | -0.01976 | 0.0123 | 0.0092072 | -0.0070132 | 0.0037897 | -0.012407 | -0.0049454 | -0.005371 | 0.019967 | 0.041567 | -0.017842 | 0.012548 | 0.022683 | -0.0076841 | 5.4428 | 5.4474 | 5.3329 | 5.365 | 5.452 | 5.3604 | 5.3787 | -0.009155 | 0.018311 | -0.041199 | -0.027466 | 0.086975 | 0.059509 | 0.073242 | 5.4199 | -117.1143 | -117.1967 | 5.5389 | 5.4657 | 5.4474 | 0.045776 | 0.027466 | 0.045776 | -122.5433 | -122.5891 | 0.17395 | 0.16022 | 0.14648 | 0.11444 | 0.10071 | 0.11902 | 0.032043 | 0.12817 | 0.013733 | 0.11444 | 0.05951 | 5.5344 | 0.10529 | -117.2287 | -122.6028 | 5.452 | 0.059509 | 5.5298 | 0.07782
5136.5625 | 122.6303 | -0.091553 | 122.5616 | -0.012131 | 0.014009 | 0.009848 | -0.0074404 | 0.0037897 | -0.0092028 | -0.0045182 | -0.0084228 | 0.020608 | 0.042208 | -0.011006 | 0.013189 | 0.024178 | -0.0044797 | 5.4153 | 5.3833 | 5.2917 | 5.3329 | 5.4657 | 5.3101 | 5.3513 | 0.041199 | 0.027466 | -0.050354 | -0.009155 | 0.10529 | 0.073242 | 0.082397 | 5.3833 | -117.1783 | -117.2287 | 5.5573 | 5.4428 | 5.4016 | 0.059509 | 0.018311 | 0.041199 | -122.5342 | -122.5708 | 0.19684 | 0.17395 | 0.16479 | 0.13275 | 0.1236 | 0.17395 | 0.041199 | 0.15564 | 0.041199 | 0.091553 | 0.07782 | 5.4749 | 0.11902 | -117.2699 | -122.612 | 5.4245 | 0.082398 | 5.5069 | 0.13275
5138.2812 | 122.6761 | -0.059509 | 122.5204 | -0.01976 | 0.014009 | 0.012412 | -0.010858 | 0.0035761 | -0.010057 | -0.001741 | -0.005371 | 0.020395 | 0.042208 | -0.015065 | 0.011266 | 0.024178 | -0.0046933 | 5.3192 | 5.2368 | 5.2094 | 5.3055 | 5.4428 | 5.2872 | 5.3375 | 0.10529 | -0.018311 | -0.022888 | 0.027466 | 0.15106 | 0.11902 | 0.12817 | 5.2689 | -117.2836 | -117.215 | 5.5023 | 5.397 | 5.3467 | 0.12817 | 0.077819 | 0.036621 | -122.5388 | -122.493 | 0.21057 | 0.18768 | 0.17853 | 0.15106 | 0.14191 | 0.23346 | 0.09613 | 0.17395 | 0.050354 | 0.027465 | 0.004577 | 5.2963 | 0.041198 | -117.3111 | -122.5433 | 5.365 | 0.086975 | 5.3787 | 0.16479
5140.0781 | 122.6349 | -0.10529 | 122.5708 | 0.0031279 | 0.01465 | 0.010703 | -0.0067996 | 0.0037897 | -0.010698 | -0.0008866 | -0.0023192 | 0.020822 | 0.042849 | -0.016347 | 0.014471 | 0.02311 | -0.0042661 | 5.3833 | 5.3833 | 5.2689 | 5.3284 | 5.4291 | 5.3009 | 5.3101 | 0.041199 | 0.041199 | -0.041199 | -0.018311 | 0.091553 | 0.068665 | 0.07782 | 5.3741 | -117.1875 | -117.2424 | 5.5344 | 5.4153 | 5.4062 | 0.041199 | 0.032043 | 0.064087 | -122.5296 | -122.5891 | 0.19684 | 0.18311 | 0.17395 | 0.11902 | 0.10986 | 0.16022 | 0.059509 | 0.13275 | 0.022888 | 0.11444 | 0.082398 | 5.4886 | 0.14649 | -117.3019 | -122.612 | 5.4337 | 0.086975 | 5.4886 | 0.14649
5141.7969 | 122.6852 | -0.050354 | 122.5388 | -0.01976 | 0.014223 | 0.011343 | -0.008295 | 0.0027215 | -0.0077074 | -0.0047318 | -0.005371 | 0.018045 | 0.040712 | -0.017842 | 0.011694 | 0.023537 | -0.0053343 | 5.2917 | 5.2139 | 5.1956 | 5.2917 | 5.4108 | 5.2551 | 5.3146 | 0.10529 | -0.013733 | -0.018311 | 0.054932 | 0.15564 | 0.11902 | 0.11444 | 5.246 | -117.3248 | -117.247 | 5.4611 | 5.365 | 5.3055 | 0.11902 | 0.059509 | 0.032043 | -122.5525 | -122.4838 | 0.20599 | 0.16479 | 0.16937 | 0.13275 | 0.13733 | 0.21515 | 0.09613 | 0.17395 | 0.073243 | 0.01831 | 0.004578 | 5.2643 | 0.036621 | -117.3431 | -122.5571 | 5.3421 | 0.10529 | 5.3421 | 0.15564
5143.5781 | 122.6807 | -0.086975 | 122.5296 | -0.012131 | 0.010591 | 0.0092072 | -0.0089358 | -0.00069646 | -0.010698 | -0.0040908 | -0.005371 | 0.018899 | 0.041994 | -0.016987 | 0.0091303 | 0.022469 | -0.00063445 | 5.3009 | 5.2963 | 5.2048 | 5.2643 | 5.3696 | 5.2597 | 5.3055 | 0.032043 | 0 | -0.041199 | -0.004578 | 0.12817 | 0.10071 | 0.10986 | 5.2917 | -117.2333 | -117.2653 | 5.4565 | 5.3925 | 5.3467 | 0.10071 | 0.054932 | 0.045776 | -122.5296 | -122.5342 | 0.21515 | 0.19684 | 0.18768 | 0.15106 | 0.14191 | 0.16479 | 0.059509 | 0.16937 | 0.036621 | 0.091553 | 0.041199 | 5.3833 | 0.086975 | -117.3248 | -122.5708 | 5.3513 | 0.082397 | 5.3879 | 0.11902
5145.3594 | 122.6166 | -0.10071 | 122.5571 | -0.0045011 | 0.015718 | 0.010916 | -0.0067996 | 0.0033623 | -0.0087756 | -0.0036636 | -0.005371 | 0.020395 | 0.043917 | -0.010792 | 0.013403 | 0.022469 | -0.0051205 | 5.2368 | 5.2551 | 5.1636 | 5.1315 | 5.2414 | 5.1132 | 5.1498 | -0.041199 | 0.013733 | -0.045776 | -0.050354 | 0.027466 | -0.004578 | 0.045776 | 5.2643 | -117.3019 | -117.4255 | 5.3421 | 5.2505 | 5.2139 | -0.013733 | -0.050354 | 0.054932 | -122.5433 | -122.6074 | 0.12817 | 0.14648 | 0.09613 | 0.091552 | 0.041198 | 0.07782 | -0.032043 | 0.073242 | -0.004578 | 0.091553 | 0.059509 | 5.3558 | 0.11444 | -117.3935 | -122.6028 | 5.2322 | 0.050354 | 5.3375 | 0.059509
5147.1562 | 122.5479 | -0.11444 | 122.5525 | -0.01976 | 0.015291 | 0.010916 | -0.0055178 | 0.0020807 | -0.010485 | -0.0028092 | -0.0084228 | 0.021463 | 0.043062 | -0.0088695 | 0.011694 | 0.022255 | -0.0072569 | 5.246 | 5.2551 | 5.1636 | 5.1361 | 5.2185 | 5.1086 | 5.1544 | -0.068665 | 0.032043 | -0.054932 | -0.064087 | 0 | -0.027466 | 0.045776 | 5.278 | -117.2974 | -117.4164 | 5.3329 | 5.2689 | 5.2231 | -0.009155 | -0.054931 | 0.059509 | -122.5204 | -122.6166 | 0.11444 | 0.16022 | 0.086975 | 0.10071 | 0.027466 | 0.054932 | -0.027466 | 0.054932 | -0.009155 | 0.091553 | 0.086975 | 5.3696 | 0.14648 | -117.3889 | -122.6074 | 5.2505 | 0.050354 | 5.3604 | 0.045776
5148.9375 | 122.7219 | -0.050354 | 122.5296 | -0.01976 | 0.011232 | 0.0094208 | -0.010645 | 0.0016535 | -0.00963 | -0.001741 | -0.011475 | 0.018686 | 0.041353 | -0.016347 | 0.011053 | 0.025246 | -0.0040525 | 5.3513 | 5.2734 | 5.2231 | 5.3513 | 5.4977 | 5.3696 | 5.3925 | 0.1236 | -0.013733 | -0.018311 | 0.050354 | 0.1831 | 0.16022 | 0.1236 | 5.2734 | -117.2562 | -117.1783 | 5.5481 | 5.4428 | 5.4199 | 0.16937 | 0.14649 | 0.032043 | -122.5433 | -122.4792 | 0.23346 | 0.17395 | 0.21057 | 0.14191 | 0.17853 | 0.27466 | 0.12817 | 0.20142 | 0.068665 | 0.050354 | 0.004578 | 5.3238 | 0.036621 | -117.3065 | -122.5479 | 5.4016 | 0.10071 | 5.4016 | 0.17395
5150.7188 | 122.7036 | -0.050354 | 122.5433 | -0.02739 | 0.016359 | 0.010062 | -0.0085086 | 0.00079894 | -0.0083484 | -0.0049454 | -0.0084228 | 0.019967 | 0.040926 | -0.012074 | 0.012975 | 0.024178 | -0.0036253 | 5.2734 | 5.159 | 5.1132 | 5.2048 | 5.3375 | 5.191 | 5.2322 | 0.10071 | -0.013733 | -0.018311 | 0.064087 | 0.16937 | 0.10986 | 0.14191 | 5.1636 | -117.3843 | -117.3386 | 5.3879 | 5.2826 | 5.2414 | 0.11902 | 0.07782 | 0.032043 | -122.5571 | -122.4792 | 0.21973 | 0.19226 | 0.16022 | 0.16022 | 0.12817 | 0.2243 | 0.091553 | 0.18768 | 0.082398 | 0.045777 | 0.004578 | 5.2094 | 0.036621 | -117.4301 | -122.5616 | 5.2551 | 0.11444 | 5.3238 | 0.15106
5152.4375 | 122.612 | -0.11444 | 122.5662 | -0.012131 | 0.011446 | 0.010489 | -0.0070132 | 0.00079894 | -0.010698 | -0.0053726 | -0.0084228 | 0.02189 | 0.04178 | -0.022755 | 0.013189 | 0.02311 | -0.0042661 | 5.3009 | 5.3421 | 5.246 | 5.2231 | 5.3375 | 5.2368 | 5.2414 | -0.054932 | 0.032043 | -0.064087 | -0.064087 | 0.045776 | 0.022888 | 0.054932 | 5.3604 | -117.2241 | -117.3431 | 5.452 | 5.3558 | 5.3513 | -0.004578 | -0.009156 | 0.050354 | -122.5342 | -122.6303 | 0.16022 | 0.16937 | 0.13733 | 0.11902 | 0.086975 | 0.091552 | -0.022889 | 0.10986 | 0 | 0.09613 | 0.09613 | 5.4565 | 0.14648 | -117.3203 | -122.6303 | 5.3375 | 0.050354 | 5.4153 | 0.059509
5154.2188 | 122.6212 | -0.09613 | 122.5388 | -0.01976 | 0.015291 | 0.010275 | -0.0072268 | 0.0025079 | -0.0074938 | -0.0032364 | -0.005371 | 0.020181 | 0.039431 | -0.0080151 | 0.011053 | 0.022042 | -0.0049069 | 5.191 | 5.2231 | 5.0949 | 5.1086 | 5.2094 | 5.0858 | 5.1178 | -0.027466 | 0.027466 | -0.050354 | -0.036621 | 0.054932 | 0.018311 | 0.068665 | 5.191 | -117.3157 | -117.4301 | 5.3055 | 5.2139 | 5.1819 | 0.022888 | -0.009156 | 0.045776 | -122.5113 | -122.5754 | 0.15106 | 0.16479 | 0.11444 | 0.11902 | 0.068665 | 0.11444 | 0.013733 | 0.10529 | 0.013733 | 0.12817 | 0.07782 | 5.3192 | 0.1236 | -117.4438 | -122.5891 | 5.2048 | 0.059509 | 5.2872 | 0.068664
5155.9375 | 122.6303 | -0.082397 | 122.5662 | -0.01976 | 0.012941 | 0.010703 | -0.007654 | 0.0046441 | -0.0098438 | -0.0040908 | -0.0023192 | 0.020822 | 0.042635 | -0.015065 | 0.013616 | 0.02311 | -0.0044797 | 5.2917 | 5.2872 | 5.2002 | 5.2277 | 5.3375 | 5.2002 | 5.2368 | 0.022888 | 0.027466 | -0.032043 | -0.004578 | 0.10071 | 0.050354 | 0.073242 | 5.2826 | -117.2791 | -117.3386 | 5.4199 | 5.3192 | 5.2826 | 0.036621 | 0 | 0.050354 | -122.5388 | -122.5708 | 0.18311 | 0.15564 | 0.13275 | 0.10529 | 0.082397 | 0.13733 | 0.027466 | 0.13275 | 0.027465 | 0.086975 | 0.059509 | 5.3696 | 0.10986 | -117.366 | -122.5983 | 5.3101 | 0.077819 | 5.3741 | 0.10528
5157.7188 | 122.6578 | -0.082397 | 122.5525 | -0.012131 | 0.013796 | 0.012412 | -0.0070132 | 0.00015814 | -0.008562 | -0.0032364 | -0.005371 | 0.021249 | 0.042849 | -0.017201 | 0.015752 | 0.024178 | -0.0027707 | 5.1636 | 5.2094 | 5.0858 | 5.0812 | 5.2094 | 5.0629 | 5.1178 | -0.004578 | 0.041199 | -0.032043 | 0.009155 | 0.09613 | 0.064087 | 0.10529 | 5.1682 | -117.3431 | -117.4713 | 5.2917 | 5.2002 | 5.1453 | 0.032044 | -0.022888 | 0.050354 | -122.5113 | -122.5433 | 0.17853 | 0.18768 | 0.14648 | 0.13733 | 0.09613 | 0.1236 | -0.004577 | 0.12817 | 0.041198 | 0.1236 | 0.073242 | 5.2917 | 0.1236 | -117.4667 | -122.5845 | 5.1636 | 0.091552 | 5.246 | 0.077819
5159.5 | 122.7081 | -0.054932 | 122.5296 | -0.012131 | 0.0086688 | 0.008139 | -0.012354 | 0.00037174 | -0.011339 | -0.002382 | -0.0084228 | 0.017831 | 0.043062 | -0.01656 | 0.0097711 | 0.024819 | -0.0025571 | 5.2872 | 5.2231 | 5.1956 | 5.3009 | 5.452 | 5.3055 | 5.3375 | 0.10986 | 0.009155 | -0.009155 | 0.045776 | 0.19684 | 0.16022 | 0.14191 | 5.2505 | -117.3065 | -117.2287 | 5.5069 | 5.3925 | 5.3604 | 0.14191 | 0.10986 | 0.045777 | -122.5204 | -122.4838 | 0.25177 | 0.19684 | 0.21515 | 0.15106 | 0.16937 | 0.25635 | 0.10529 | 0.20599 | 0.054931 | 0.027465 | 0.01831 | 5.278 | 0.064087 | -117.334 | -122.5388 | 5.3558 | 0.10071 | 5.3421 | 0.16479
5161.2812 | 122.7219 | -0.054932 | 122.4792 | -0.0045011 | 0.014437 | 0.0096344 | -0.0089358 | 0.0016535 | -0.0081348 | -0.0049454 | -0.0084228 | 0.018045 | 0.043489 | -0.015065 | 0.011694 | 0.023964 | -0.0025571 | 5.2139 | 5.0903 | 5.0903 | 5.1544 | 5.278 | 5.1132 | 5.1682 | 0.10071 | -0.004578 | -0.018311 | 0.073242 | 0.16479 | 0.12817 | 0.13733 | 5.1453 | -117.3889 | -117.3248 | 5.3329 | 5.2231 | 5.1682 | 0.07782 | 0.022888 | 0.036621 | -122.4838 | -122.406 | 0.21973 | 0.19226 | 0.18311 | 0.15564 | 0.14649 | 0.18768 | 0.064087 | 0.18311 | 0.091553 | 0 | 0.013733 | 5.1453 | 0.050354 | -117.3889 | -122.4976 | 5.2094 | 0.12817 | 5.2689 | 0.15564
5163.0625 | 122.6166 | -0.086975 | 122.5342 | -0.012131 | 0.014223 | 0.010275 | -0.0061588 | 0.0046441 | -0.0092028 | -0.002382 | -0.005371 | 0.020181 | 0.043917 | -0.010365 | 0.012762 | 0.024178 | -0.0036253 | 5.2368 | 5.2277 | 5.1361 | 5.1865 | 5.3055 | 5.159 | 5.1819 | 0.036621 | 0.027466 | -0.041199 | -0.013733 | 0.086975 | 0.027466 | 0.073242 | 5.2231 | -117.3065 | -117.3477 | 5.3925 | 5.2689 | 5.246 | 0.045777 | 0.022889 | 0.045776 | -122.5067 | -122.5479 | 0.17395 | 0.16022 | 0.11444 | 0.11444 | 0.068665 | 0.16937 | 0.050354 | 0.12817 | 0.027466 | 0.091553 | 0.068665 | 5.3146 | 0.11444 | -117.3981 | -122.5754 | 5.2734 | 0.073242 | 5.3238 | 0.1236
5164.8438 | 122.7219 | -0.064087 | 122.525 | -0.02739 | 0.014223 | 0.011984 | -0.0087222 | 0.00079894 | -0.010912 | 0.0001816 | -0.0084228 | 0.01954 | 0.04114 | -0.019551 | 0.012121 | 0.022896 | -0.0019163 | 5.1636 | 5.072 | 5.072 | 5.1361 | 5.2551 | 5.1086 | 5.1407 | 0.10071 | 0 | -0.036621 | 0.064087 | 0.16937 | 0.13275 | 0.13275 | 5.1361 | -117.453 | -117.3889 | 5.3192 | 5.2048 | 5.1727 | 0.068665 | 0.036622 | 0.027466 | -122.525 | -122.4609 | 0.23346 | 0.19684 | 0.19684 | 0.16937 | 0.16937 | 0.18311 | 0.064087 | 0.20599 | 0.10071 | 0 | 0.036621 | 5.1361 | 0.064087 | -117.453 | -122.5616 | 5.2002 | 0.12817 | 5.2277 | 0.1648
5166.5781 | 122.6898 | -0.086975 | 122.5479 | -0.01976 | 0.013796 | 0.010275 | -0.0072268 | 0.0018671 | -0.0092028 | -0.0025956 | -0.0084228 | 0.019113 | 0.04114 | -0.018483 | 0.011907 | 0.023323 | -0.0042661 | 5.0903 | 5.1178 | 5.0171 | 5.0491 | 5.1682 | 5.0262 | 5.0491 | 0.032043 | 0.004578 | -0.041199 | 0.032043 | 0.13733 | 0.10071 | 0.10529 | 5.1041 | -117.4301 | -117.4988 | 5.2551 | 5.1361 | 5.1132 | 0.032043 | 0.009155 | 0.045776 | -122.5433 | -122.5159 | 0.2243 | 0.19226 | 0.18768 | 0.14649 | 0.14191 | 0.15106 | 0.032043 | 0.17853 | 0.073242 | 0.10071 | 0.045777 | 5.2048 | 0.091553 | -117.5308 | -122.5891 | 5.1361 | 0.11902 | 5.1773 | 0.11902
5168.3594 | 122.6349 | -0.082397 | 122.5433 | -0.02739 | 0.013796 | 0.0094208 | -0.0053042 | 0.00015814 | -0.0098438 | -0.0019546 | -0.0084228 | 0.01954 | 0.042635 | -0.012501 | 0.013616 | 0.021401 | -0.0046933 | 5.0995 | 5.1224 | 5.0079 | 5.0217 | 5.1361 | 4.9896 | 5.04 | -0.009155 | 0.032043 | -0.050354 | -0.018311 | 0.073242 | 0.041199 | 0.068665 | 5.0903 | -117.421 | -117.5217 | 5.2185 | 5.1224 | 5.072 | 0.032043 | -0.018311 | 0.032043 | -122.5113 | -122.5616 | 0.15564 | 0.15106 | 0.1236 | 0.11902 | 0.091553 | 0.12817 | 0.013732 | 0.1236 | 0.032043 | 0.11444 | 0.082397 | 5.2048 | 0.11444 | -117.5354 | -122.5937 | 5.1041 | 0.064086 | 5.1819 | 0.073242
5170.0781 | 122.7036 | -0.07782 | 122.5433 | -0.0045011 | 0.010378 | 0.00878 | -0.010218 | 0.00037174 | -0.008562 | -0.0040908 | -0.005371 | 0.018899 | 0.043062 | -0.012929 | 0.010198 | 0.023964 | -0.0023435 | 5.1453 | 5.1178 | 5.0491 | 5.1132 | 5.246 | 5.127 | 5.1819 | 0.041199 | 0.018311 | -0.059509 | 0.009155 | 0.14648 | 0.12817 | 0.10986 | 5.127 | -117.4255 | -117.4301 | 5.3238 | 5.2597 | 5.2048 | 0.13275 | 0.07782 | 0.018311 | -122.525 | -122.5342 | 0.2243 | 0.18768 | 0.20599 | 0.16937 | 0.18768 | 0.19684 | 0.064087 | 0.20599 | 0.068664 | 0.068665 | 0.07782 | 5.1956 | 0.096131 | -117.4942 | -122.6028 | 5.191 | 0.086975 | 5.2231 | 0.11902
5171.8594 | 122.699 | -0.07782 | 122.5754 | -0.01976 | 0.012941 | 0.0085662 | -0.010004 | -0.0015509 | -0.013475 | -0.0045182 | -0.005371 | 0.019113 | 0.041567 | -0.016133 | 0.011053 | 0.022683 | -0.0064023 | 5.2368 | 5.1682 | 5.1224 | 5.2368 | 5.3558 | 5.2277 | 5.2597 | 0.11444 | -0.009155 | -0.013733 | 0.032043 | 0.16937 | 0.15106 | 0.13733 | 5.2002 | -117.4072 | -117.3386 | 5.4337 | 5.3375 | 5.3055 | 0.13733 | 0.10529 | 0.064087 | -122.5845 | -122.5433 | 0.24719 | 0.21515 | 0.22888 | 0.15106 | 0.16479 | 0.23346 | 0.11444 | 0.18311 | 0.045776 | 0.045777 | 0.004578 | 5.246 | 0.068665 | -117.453 | -122.5891 | 5.3146 | 0.10986 | 5.3146 | 0.19226
5173.625 | 122.6852 | -0.068665 | 122.5433 | -0.02739 | 0.011019 | 0.009848 | -0.010004 | 0.00015814 | -0.010271 | -0.0049454 | -0.0023192 | 0.018899 | 0.04114 | -0.016987 | 0.01148 | 0.022896 | -0.0023435 | 5.2185 | 5.159 | 5.0995 | 5.2139 | 5.3329 | 5.2002 | 5.2277 | 0.07782 | 0 | -0.027466 | 0.027466 | 0.16022 | 0.14191 | 0.1236 | 5.1682 | -117.3843 | -117.3294 | 5.4016 | 5.2963 | 5.2689 | 0.12817 | 0.10071 | 0.041199 | -122.5433 | -122.5159 | 0.22888 | 0.19226 | 0.21057 | 0.15106 | 0.16937 | 0.23346 | 0.11444 | 0.18768 | 0.054932 | 0.05951 | 0.027466 | 5.2277 | 0.068665 | -117.4438 | -122.5708 | 5.2826 | 0.096131 | 5.2872 | 0.14649
5175.3281 | 122.6166 | -0.091553 | 122.5754 | -0.01976 | 0.012087 | 0.0085662 | -0.0080814 | 0.00015814 | -0.008562 | -0.0013138 | -0.0084228 | 0.021463 | 0.041353 | -0.010579 | 0.012762 | 0.023323 | -0.0031979 | 5.1727 | 5.2094 | 5.1178 | 5.0903 | 5.1865 | 5.0949 | 5.1041 | -0.068665 | 0.041199 | -0.050354 | -0.064087 | 0.054932 | 0.027466 | 0.041199 | 5.2094 | -117.366 | -117.485 | 5.278 | 5.1956 | 5.1865 | -0.013733 | -0.022888 | 0.041199 | -122.5342 | -122.6395 | 0.14649 | 0.13275 | 0.11902 | 0.091553 | 0.07782 | 0.068664 | -0.027466 | 0.10529 | -0.013733 | 0.091553 | 0.091553 | 5.3009 | 0.13275 | -117.4576 | -122.6257 | 5.1819 | 0.027466 | 5.2643 | 0.022888
5177.1094 | 122.7036 | -0.068665 | 122.5342 | -0.02739 | 0.013796 | 0.011343 | -0.0050906 | 0.0010125 | -0.0077074 | -0.0030228 | -0.005371 | 0.01954 | 0.040285 | -0.010579 | 0.011907 | 0.024819 | -0.00084805 | 5.0629 | 5.0537 | 4.9622 | 5.0125 | 5.1453 | 5.0079 | 5.0446 | 0.07782 | -0.004578 | -0.022888 | 0.045776 | 0.13275 | 0.10529 | 0.12817 | 5.0308 | -117.4805 | -117.5217 | 5.2139 | 5.1132 | 5.0766 | 0.082398 | 0.045777 | 0.045777 | -122.5388 | -122.4884 | 0.20142 | 0.19684 | 0.17395 | 0.15106 | 0.12817 | 0.18311 | 0.050354 | 0.15564 | 0.068664 | 0.091553 | 0.01831 | 5.1224 | 0.064087 | -117.572 | -122.5571 | 5.0812 | 0.11444 | 5.1315 | 0.14649
5178.8281 | 122.7264 | -0.064087 | 122.5159 | -0.012131 | 0.010591 | 0.0089936 | -0.010431 | 0.00037174 | -0.010271 | -0.0025956 | -0.0084228 | 0.019326 | 0.040712 | -0.013356 | 0.010839 | 0.022255 | -0.0051205 | 5.1773 | 5.0995 | 5.0858 | 5.1865 | 5.3558 | 5.2048 | 5.2185 | 0.11902 | 0.013733 | -0.032043 | 0.050354 | 0.20142 | 0.16479 | 0.14191 | 5.1498 | -117.4164 | -117.3294 | 5.4199 | 5.2826 | 5.2689 | 0.13275 | 0.11902 | 0.032044 | -122.5021 | -122.4655 | 0.2655 | 0.20599 | 0.22888 | 0.17395 | 0.19684 | 0.27008 | 0.10071 | 0.23346 | 0.082397 | 0.013733 | 0.045776 | 5.1636 | 0.07782 | -117.4301 | -122.5479 | 5.2505 | 0.11444 | 5.2414 | 0.18311
5180.625 | 122.612 | -0.10529 | 122.5937 | -0.01976 | 0.014009 | 0.0094208 | -0.005945 | 0.0016535 | -0.0098438 | -0.0032364 | -0.0084228 | 0.019326 | 0.041567 | -0.013356 | 0.013189 | 0.023537 | -0.0038389 | 5.1682 | 5.127 | 5.0491 | 5.0903 | 5.2002 | 5.0537 | 5.0903 | 0.032043 | 0.018311 | -0.032043 | -0.018311 | 0.07782 | 0.022888 | 0.068665 | 5.1544 | -117.4667 | -117.5034 | 5.3055 | 5.1956 | 5.159 | 0.041199 | 0.004578 | 0.073243 | -122.5754 | -122.612 | 0.18311 | 0.17395 | 0.12817 | 0.10071 | 0.054931 | 0.15106 | 0.041199 | 0.10986 | 0.013732 | 0.07782 | 0.050354 | 5.2322 | 0.1236 | -117.5446 | -122.6257 | 5.1956 | 0.086975 | 5.2734 | 0.13733
5182.4062 | 122.6074 | -0.10071 | 122.6028 | -0.012131 | 0.013582 | 0.0085662 | -0.0061588 | 0.0031487 | -0.0098438 | -0.0030228 | -0.0023192 | 0.021676 | 0.042421 | -0.016347 | 0.013403 | 0.022255 | -0.0036253 | 5.1224 | 5.1041 | 5.0354 | 5.0354 | 5.1407 | 5.0034 | 5.04 | -0.013733 | 0.018311 | -0.050354 | -0.041199 | 0.027466 | 0 | 0.036621 | 5.1361 | -117.4988 | -117.5674 | 5.2414 | 5.1407 | 5.1041 | 0.004578 | -0.032043 | 0.050354 | -122.5845 | -122.644 | 0.12817 | 0.13733 | 0.10071 | 0.086975 | 0.050354 | 0.10529 | 0 | 0.07782 | 0.009155 | 0.068665 | 0.068665 | 5.2048 | 0.11902 | -117.5674 | -122.6532 | 5.1361 | 0.059509 | 5.2231 | 0.086975
5184.125 | 122.7219 | -0.041199 | 122.5433 | -0.02739 | 0.009737 | 0.0068574 | -0.0095766 | -0.0011237 | -0.0098438 | -0.0047318 | -0.011475 | 0.017404 | 0.043062 | -0.016133 | 0.010412 | 0.023751 | -0.0010617 | 5.1682 | 5.0903 | 5.0583 | 5.159 | 5.3284 | 5.1865 | 5.2094 | 0.10529 | -0.009155 | -0.009155 | 0.041199 | 0.19684 | 0.15106 | 0.12817 | 5.0995 | -117.453 | -117.3843 | 5.3696 | 5.2505 | 5.2277 | 0.15106 | 0.12817 | 0.032044 | -122.5525 | -122.5021 | 0.23804 | 0.16937 | 0.19226 | 0.13733 | 0.16022 | 0.27008 | 0.10071 | 0.20599 | 0.050354 | 0.032043 | 0 | 5.1315 | 0.032044 | -117.485 | -122.5525 | 5.2002 | 0.082398 | 5.2094 | 0.14649
5185.8906 | 122.6349 | -0.12817 | 122.5754 | -0.01976 | 0.013155 | 0.00878 | -0.0074404 | 0.0035761 | -0.011553 | -0.0030228 | -0.005371 | 0.019754 | 0.042635 | -0.019337 | 0.010839 | 0.022255 | -0.0034117 | 5.1224 | 5.1865 | 5.0766 | 5.0491 | 5.1636 | 5.0629 | 5.0858 | -0.054932 | 0.050354 | -0.07782 | -0.064087 | 0.064087 | 0.032043 | 0.050354 | 5.2048 | -117.3889 | -117.5262 | 5.2917 | 5.2139 | 5.191 | 0.009155 | -0.013733 | 0.050354 | -122.525 | -122.6395 | 0.19226 | 0.17853 | 0.16022 | 0.12817 | 0.10986 | 0.086975 | -0.027466 | 0.14191 | 0.013733 | 0.10986 | 0.12817 | 5.3146 | 0.17853 | -117.4988 | -122.6532 | 5.1773 | 0.064087 | 5.2505 | 0.073242
5187.5938 | 122.5845 | -0.10986 | 122.5479 | -0.0045011 | 0.015505 | 0.0092072 | -0.0080814 | 0.0057123 | -0.0077074 | -0.0019546 | -0.0084228 | 0.021463 | 0.043062 | -0.014851 | 0.011907 | 0.025246 | -0.0044797 | 5.0171 | 5.0491 | 4.9393 | 4.9393 | 5.0217 | 4.8889 | 4.9301 | -0.068665 | 0.027466 | -0.064087 | -0.073242 | 0.013733 | -0.018311 | 0.027466 | 5.0491 | -117.4988 | -117.6086 | 5.1315 | 5.04 | 4.9988 | -0.009155 | -0.050354 | 0.045776 | -122.5204 | -122.6212 | 0.1236 | 0.13733 | 0.091552 | 0.091553 | 0.045776 | 0.082397 | 0 | 0.07782 | -0.009155 | 0.10986 | 0.091553 | 5.159 | 0.13733 | -117.6086 | -122.612 | 5.0491 | 0.036621 | 5.127 | 0.041198
5189.3594 | 122.6486 | -0.10529 | 122.5479 | -0.012131 | 0.012514 | 0.0096344 | -0.0072268 | -0.00048286 | -0.011339 | -0.0040908 | -0.005371 | 0.020822 | 0.042849 | -0.02126 | 0.014898 | 0.023323 | -0.0038389 | 5.127 | 5.0949 | 5.0079 | 5.0583 | 5.1727 | 5.04 | 5.0674 | 0.032043 | 0.022888 | -0.041199 | -0.018311 | 0.082397 | 0.050354 | 0.07782 | 5.1132 | -117.453 | -117.4896 | 5.278 | 5.1727 | 5.1453 | 0.059509 | 0.032043 | 0.064087 | -122.525 | -122.5662 | 0.18768 | 0.18311 | 0.15564 | 0.11902 | 0.091553 | 0.16479 | 0.050354 | 0.1236 | 0.022888 | 0.086975 | 0.064087 | 5.2002 | 0.12817 | -117.54 | -122.5891 | 5.1636 | 0.086975 | 5.2322 | 0.13733
5191.1406 | 122.7264 | -0.068665 | 122.5342 | -0.012131 | 0.012087 | 0.0085662 | -0.009363 | 0.0010125 | -0.011339 | -0.0032364 | -0.0023192 | 0.016763 | 0.042421 | -0.021687 | 0.01148 | 0.024819 | -0.0049069 | 5.1498 | 5.0537 | 5.0308 | 5.1453 | 5.278 | 5.1636 | 5.1819 | 0.10986 | 0 | -0.009155 | 0.045776 | 0.17853 | 0.15564 | 0.12817 | 5.0995 | -117.4805 | -117.3889 | 5.3467 | 5.2506 | 5.2322 | 0.15106 | 0.13275 | 0.05951 | -122.5342 | -122.4884 | 0.24719 | 0.19684 | 0.22431 | 0.13733 | 0.16479 | 0.24719 | 0.11444 | 0.18768 | 0.054931 | 0.022888 | 0.009155 | 5.1224 | 0.068665 | -117.5034 | -122.5433 | 5.2139 | 0.11444 | 5.2185 | 0.17853
5192.9062 | 122.6074 | -0.11902 | 122.5937 | -0.012131 | 0.013369 | 0.0085662 | -0.0078676 | 0.0010125 | -0.0083484 | -0.0043046 | -0.0023192 | 0.020608 | 0.041567 | -0.016133 | 0.013403 | 0.02311 | 0.0015017 | 5.0903 | 5.1453 | 5.0446 | 5.0308 | 5.1361 | 5.0308 | 5.0583 | -0.064087 | 0.050354 | -0.050354 | -0.064087 | 0.045776 | 0.018311 | 0.045776 | 5.1636 | -117.4484 | -117.5629 | 5.2551 | 5.1773 | 5.1498 | 0.013733 | -0.013733 | 0.068665 | -122.5433 | -122.6578 | 0.16479 | 0.16479 | 0.13733 | 0.09613 | 0.068665 | 0.091552 | -0.013733 | 0.09613 | -0.013733 | 0.10071 | 0.10071 | 5.2643 | 0.16937 | -117.5491 | -122.644 | 5.1498 | 0.054932 | 5.2094 | 0.054932
5194.625 | 122.6852 | -0.073242 | 122.5662 | -0.012131 | 0.011873 | 0.00878 | -0.0087222 | 0.0033623 | -0.0092028 | -0.0047318 | -0.0023192 | 0.017831 | 0.04178 | -0.016774 | 0.010839 | 0.023323 | -0.00042085 | 5.0034 | 4.9759 | 4.921 | 4.9942 | 5.1315 | 4.953 | 5.0262 | 0.068665 | -0.018311 | -0.027466 | 0.013733 | 0.11444 | 0.07782 | 0.086975 | 4.9942 | -117.5903 | -117.572 | 5.2048 | 5.0995 | 5.0262 | 0.10529 | 0.032044 | 0.045776 | -122.5845 | -122.5525 | 0.18768 | 0.16022 | 0.15106 | 0.11444 | 0.10529 | 0.21057 | 0.073243 | 0.14191 | 0.041199 | 0.054932 | 0.009155 | 5.0491 | 0.054931 | -117.6453 | -122.5937 | 5.0674 | 0.086975 | 5.0766 | 0.14191
5196.4062 | 122.6303 | -0.086975 | 122.6074 | -0.012131 | 0.012087 | 0.0085662 | -0.0070132 | -0.0015509 | -0.011766 | -0.0038772 | -0.0084228 | 0.020822 | 0.042208 | -0.015706 | 0.01148 | 0.021614 | -0.0027707 | 5.0766 | 5.1041 | 5.0125 | 5.0262 | 5.1224 | 5.0217 | 5.0446 | -0.022888 | 0.036621 | -0.054932 | -0.022888 | 0.082397 | 0.045776 | 0.082397 | 5.0995 | -117.5034 | -117.5812 | 5.2093 | 5.1315 | 5.1086 | 0.032044 | 0.009155 | 0.032043 | -122.5708 | -122.6303 | 0.16937 | 0.16937 | 0.13275 | 0.13733 | 0.10071 | 0.10986 | 0.013733 | 0.13733 | 0.032044 | 0.091553 | 0.091553 | 5.191 | 0.1236 | -117.5949 | -122.6624 | 5.1132 | 0.064087 | 5.1636 | 0.064087
5198.1719 | 122.6028 | -0.10986 | 122.5983 | -0.01976 | 0.010591 | 0.00878 | -0.0080814 | 0.0022943 | -0.01198 | -0.0038772 | -0.005371 | 0.019326 | 0.040926 | -0.015065 | 0.0095575 | 0.024819 | -0.0019163 | 5.0491 | 5.1041 | 4.9896 | 4.9896 | 5.1224 | 5.0034 | 5.04 | -0.041199 | 0.041199 | -0.059509 | -0.09613 | 0.027466 | 0.004578 | 0.027466 | 5.0995 | -117.4942 | -117.6086 | 5.2322 | 5.1498 | 5.1132 | 0.050354 | 0.013733 | 0.050354 | -122.5571 | -122.6944 | 0.13733 | 0.13733 | 0.11444 | 0.086975 | 0.064087 | 0.13275 | 0 | 0.086975 | -0.036621 | 0.11444 | 0.10071 | 5.2139 | 0.15106 | -117.6086 | -122.6578 | 5.0995 | 0.013733 | 5.159 | 0.068664
5199.875 | 122.5708 | -0.10071 | 122.58 | -0.0045011 | 0.013582 | 0.010275 | -0.0074404 | 0.0022943 | -0.010485 | -0.0030228 | -0.0023192 | 0.020608 | 0.043062 | -0.013569 | 0.013403 | 0.022469 | -0.0025571 | 4.9942 | 5.0125 | 4.921 | 4.9072 | 4.9988 | 4.8752 | 4.9118 | -0.07782 | 0.022888 | -0.054932 | -0.086975 | 0.004578 | -0.032043 | 0.022888 | 5.0217 | -117.5674 | -117.6727 | 5.0995 | 5.0125 | 4.9759 | -0.009155 | -0.045776 | 0.045776 | -122.5571 | -122.6669 | 0.10529 | 0.1236 | 0.068665 | 0.07782 | 0.022889 | 0.07782 | -0.013732 | 0.05951 | -0.032043 | 0.091553 | 0.07782 | 5.1132 | 0.1236 | -117.659 | -122.6349 | 5.0079 | 0.013733 | 5.0949 | 0.022888
5201.6719 | 122.6898 | -0.064087 | 122.5571 | -0.012131 | 0.012941 | 0.010489 | -0.0063724 | -0.00069646 | -0.00963 | -0.0036636 | -0.0084228 | 0.017831 | 0.040499 | -0.015278 | 0.012975 | 0.023537 | -0.0023435 | 4.9942 | 4.9164 | 4.8843 | 4.9622 | 5.1086 | 4.9484 | 5.0079 | 0.10071 | -0.004578 | -0.022888 | 0.041199 | 0.13733 | 0.10986 | 0.12817 | 4.9484 | -117.6407 | -117.5949 | 5.1727 | 5.072 | 5.0125 | 0.1236 | 0.064087 | 0.041199 | -122.5616 | -122.5159 | 0.20142 | 0.19226 | 0.17395 | 0.15106 | 0.13275 | 0.22431 | 0.07782 | 0.16022 | 0.064087 | 0.032044 | 0.01831 | 4.9805 | 0.059509 | -117.6727 | -122.58 | 5.0262 | 0.10529 | 5.0583 | 0.1648
5203.3906 | 122.6807 | -0.064087 | 122.5616 | -0.01976 | 0.0123 | 0.010489 | -0.010218 | -0.00048286 | -0.010698 | -0.0013138 | -0.0084228 | 0.018686 | 0.040926 | -0.018483 | 0.010412 | 0.022896 | -0.0031979 | 4.9622 | 4.9576 | 4.9026 | 4.9301 | 5.0629 | 4.921 | 4.985 | 0.022888 | -0.013733 | -0.050354 | 0 | 0.10529 | 0.07782 | 0.086975 | 4.9667 | -117.6041 | -117.6315 | 5.127 | 5.0491 | 4.985 | 0.082397 | 0.01831 | 0.013733 | -122.5754 | -122.5616 | 0.16937 | 0.15106 | 0.14191 | 0.13733 | 0.12817 | 0.16022 | 0.027466 | 0.15564 | 0.050354 | 0.054932 | 0.036621 | 5.0217 | 0.050354 | -117.659 | -122.612 | 4.9942 | 0.064087 | 5.0262 | 0.086975
5205.1719 | 122.5983 | -0.09613 | 122.5983 | -0.02739 | 0.012087 | 0.010916 | -0.0085086 | -0.00048286 | -0.011125 | -0.0030228 | -0.005371 | 0.019754 | 0.043062 | -0.022328 | 0.0099847 | 0.023323 | -0.0046933 | 5.0629 | 5.0354 | 4.9713 | 5.0079 | 5.1086 | 4.9759 | 5.0171 | -0.018311 | 0.027466 | -0.045776 | -0.064087 | 0.050354 | 0.032043 | 0.032043 | 5.0674 | -117.5629 | -117.5903 | 5.2048 | 5.1132 | 5.072 | 0.045777 | 0.004578 | 0.050354 | -122.5708 | -122.6624 | 0.14648 | 0.12817 | 0.12817 | 0.077819 | 0.077819 | 0.13733 | 0.036622 | 0.09613 | -0.018311 | 0.064087 | 0.073242 | 5.1315 | 0.1236 | -117.627 | -122.644 | 5.1041 | 0.032043 | 5.159 | 0.077819
5206.9531 | 122.7219 | -0.054932 | 122.5662 | -0.012131 | 0.013369 | 0.0089936 | -0.0067996 | -0.0013373 | -0.010698 | -0.0060134 | -0.005371 | 0.01954 | 0.040926 | -0.014638 | 0.013403 | 0.022469 | -0.0042661 | 4.9255 | 4.8798 | 4.8477 | 4.9118 | 5.0262 | 4.8477 | 4.9255 | 0.086975 | -0.009155 | -0.022888 | 0.045776 | 0.14191 | 0.10529 | 0.14191 | 4.9026 | -117.6865 | -117.6544 | 5.0812 | 4.9805 | 4.9026 | 0.07782 | 0 | 0.032044 | -122.5754 | -122.5204 | 0.19684 | 0.19684 | 0.16022 | 0.16479 | 0.12817 | 0.17853 | 0.064087 | 0.16479 | 0.068664 | 0.032044 | 0.013733 | 4.9347 | 0.045777 | -117.7185 | -122.5891 | 4.9667 | 0.10071 | 4.9805 | 0.14191
5208.6719 | 122.6349 | -0.11902 | 122.5662 | -0.01976 | 0.013155 | 0.0092072 | -0.0095766 | 0.0027215 | -0.00963 | -0.0036636 | -0.0084228 | 0.01954 | 0.043703 | -0.017628 | 0.0093439 | 0.020974 | 0.00064735 | 5.0674 | 4.985 | 4.9438 | 5.0354 | 5.159 | 5.0262 | 5.072 | 0.027466 | 0.036621 | -0.045776 | -0.041199 | 0.07782 | 0.054932 | 0.045776 | 5.0629 | -117.5812 | -117.5308 | 5.278 | 5.191 | 5.1453 | 0.12817 | 0.082397 | 0.073243 | -122.5296 | -122.6074 | 0.19684 | 0.16479 | 0.17395 | 0.091552 | 0.10071 | 0.21515 | 0.091552 | 0.1236 | 0.004577 | 0.041198 | 0.082397 | 5.1041 | 0.15564 | -117.6224 | -122.612 | 5.1544 | 0.07782 | 5.1865 | 0.14649
5210.4375 | 122.7539 | -0.07782 | 122.5433 | -0.012131 | 0.010378 | 0.0085662 | -0.0070132 | -0.0011237 | -0.012194 | -0.0002456 | -0.0084228 | 0.01719 | 0.041353 | -0.018696 | 0.010839 | 0.022896 | -0.0023435 | 4.9805 | 4.9301 | 4.8935 | 4.9667 | 5.1086 | 4.9805 | 5.0217 | 0.073242 | -0.004578 | -0.045776 | 0.027466 | 0.16479 | 0.13733 | 0.14648 | 4.9713 | -117.6132 | -117.5766 | 5.1865 | 5.0995 | 5.0583 | 0.12817 | 0.086975 | 0.032044 | -122.5479 | -122.5159 | 0.24261 | 0.2243 | 0.21515 | 0.19226 | 0.18311 | 0.21515 | 0.073242 | 0.21057 | 0.073242 | 0.036621 | 0.041198 | 5.0079 | 0.073242 | -117.6498 | -122.5891 | 5.0446 | 0.10529 | 5.0583 | 0.15106
5212.2031 | 122.6074 | -0.13733 | 122.5891 | -0.012131 | 0.010805 | 0.0085662 | -0.0074404 | 0.00037174 | -0.010912 | -0.0066544 | -0.005371 | 0.021035 | 0.040926 | -0.012074 | 0.011694 | 0.021401 | -0.0029843 | 4.985 | 5.0308 | 4.921 | 4.9301 | 5.0354 | 4.9484 | 4.9713 | -0.054932 | 0.045776 | -0.073242 | -0.086975 | 0.027466 | 0.004578 | 0.032043 | 5.0583 | -117.5583 | -117.659 | 5.1727 | 5.1086 | 5.0858 | 0.050354 | 0.027466 | 0.064087 | -122.5433 | -122.6761 | 0.16479 | 0.16937 | 0.14191 | 0.10529 | 0.07782 | 0.11444 | 0.009156 | 0.10071 | -0.013733 | 0.10986 | 0.11902 | 5.1682 | 0.18311 | -117.6682 | -122.6624 | 5.0674 | 0.050354 | 5.1224 | 0.082397
5213.9219 | 122.6212 | -0.10529 | 122.5891 | -0.012131 | 0.016146 | 0.010275 | -0.0074404 | 0.0046441 | -0.0098438 | -0.0021682 | -0.0023192 | 0.019754 | 0.041353 | -0.0075879 | 0.013616 | 0.020546 | -0.0027707 | 4.953 | 4.9667 | 4.8614 | 4.866 | 4.9622 | 4.8294 | 4.8523 | -0.032043 | 0.018311 | -0.045776 | -0.054932 | 0.032043 | -0.027466 | 0.027466 | 4.9667 | -117.6224 | -117.7231 | 5.0674 | 4.9576 | 4.9347 | -0.009155 | -0.032043 | 0.05951 | -122.5708 | -122.644 | 0.13733 | 0.13275 | 0.07782 | 0.073242 | 0.01831 | 0.10071 | 0.004578 | 0.077819 | -0.009156 | 0.10529 | 0.064087 | 5.072 | 0.1236 | -117.7277 | -122.6349 | 4.9713 | 0.050354 | 5.0583 | 0.073243
5215.7031 | 122.731 | -0.045776 | 122.5571 | -0.01976 | 0.013582 | 0.010489 | -0.0070132 | -0.0024055 | -0.0074938 | -0.0019546 | -0.005371 | 0.01954 | 0.043489 | -0.012929 | 0.012762 | 0.025887 | -0.0042661 | 4.8752 | 4.8614 | 4.7974 | 4.8706 | 4.985 | 4.8065 | 4.8569 | 0.091553 | 0 | -0.022888 | 0.064087 | 0.16022 | 0.10986 | 0.15106 | 4.8431 | -117.6956 | -117.6865 | 5.0308 | 4.9026 | 4.8523 | 0.05951 | 0.009156 | 0.022888 | -122.5571 | -122.493 | 0.20599 | 0.19684 | 0.15564 | 0.17395 | 0.13275 | 0.18768 | 0.073242 | 0.1831 | 0.086975 | 0.064087 | 0.022888 | 4.9072 | 0.045776 | -117.7597 | -122.58 | 4.9164 | 0.10986 | 4.921 | 0.13733
5217.4844 | 122.699 | -0.064087 | 122.5525 | -0.01976 | 0.015291 | 0.0096344 | -0.0072268 | -0.00048286 | -0.00963 | -0.0038772 | -0.005371 | 0.01954 | 0.044344 | -0.01891 | 0.012762 | 0.022042 | -0.0066159 | 4.8523 | 4.8935 | 4.7974 | 4.7928 | 4.9072 | 4.7607 | 4.8203 | 0.009155 | 0.013733 | -0.045776 | 0.018311 | 0.10986 | 0.082397 | 0.12817 | 4.8614 | -117.659 | -117.7597 | 4.9713 | 4.8843 | 4.8248 | 0.022888 | -0.036621 | 0.018311 | -122.5388 | -122.5342 | 0.17395 | 0.19226 | 0.14648 | 0.17395 | 0.12817 | 0.10986 | -0.004577 | 0.15564 | 0.064087 | 0.096131 | 0.059509 | 4.9576 | 0.07782 | -117.7551 | -122.5983 | 4.8569 | 0.082398 | 4.9164 | 0.073242
5219.2031 | 122.6074 | -0.10986 | 122.6166 | -0.01976 | 0.0099506 | 0.0066436 | -0.0097904 | 0.0010125 | -0.0089892 | -0.0028092 | -0.0084228 | 0.022103 | 0.043062 | -0.016774 | 0.012548 | 0.024605 | 0.00021995 | 4.9393 | 5.0034 | 4.8843 | 4.9072 | 5.0308 | 4.9255 | 4.9301 | -0.059509 | 0.036621 | -0.059509 | -0.073242 | 0.036621 | 0.009155 | 0.027466 | 4.9942 | -117.6132 | -117.7094 | 5.1407 | 5.04 | 5.0354 | 0.045777 | 0.041199 | 0.050354 | -122.58 | -122.6898 | 0.14648 | 0.13733 | 0.11902 | 0.086975 | 0.068664 | 0.14649 | 0.022889 | 0.09613 | -0.013733 | 0.11902 | 0.09613 | 5.1132 | 0.14648 | -117.7322 | -122.6761 | 5.0171 | 0.036621 | 5.0491 | 0.050354
5220.9688 | 122.612 | -0.11444 | 122.5937 | -0.01976 | 0.010805 | 0.0092072 | -0.012781 | 0.0012261 | -0.010698 | -0.0013138 | -0.0084228 | 0.019754 | 0.044558 | -0.014638 | 0.0099847 | 0.02076 | -0.0040525 | 4.953 | 4.9484 | 4.8843 | 4.9026 | 5.0079 | 4.9026 | 4.921 | -0.036621 | 0.013733 | -0.050354 | -0.082397 | 0.054932 | 0.013733 | 0.013733 | 4.9988 | -117.6453 | -117.691 | 5.1224 | 5.0354 | 5.0171 | 0.036621 | 0.018311 | 0.064087 | -122.58 | -122.6761 | 0.16937 | 0.12817 | 0.12817 | 0.064087 | 0.064087 | 0.1236 | 0.018311 | 0.10529 | -0.032043 | 0.064087 | 0.064087 | 5.0629 | 0.12817 | -117.7094 | -122.644 | 5.0171 | 0.032044 | 5.0674 | 0.07782
5222.75 | 122.58 | -0.10071 | 122.6028 | -0.0045011 | 0.016146 | 0.009848 | -0.005945 | 0.0042169 | -0.0092028 | -0.0053726 | -0.0084228 | 0.021463 | 0.04114 | -0.013356 | 0.013189 | 0.022042 | -0.0040525 | 4.8752 | 4.8798 | 4.7882 | 4.7745 | 4.8523 | 4.7287 | 4.7653 | -0.073242 | 0.036621 | -0.064087 | -0.086975 | -0.004578 | -0.041199 | 0.018311 | 4.8889 | -117.7231 | -117.8284 | 4.953 | 4.866 | 4.8294 | -0.022888 | -0.059509 | 0.036621 | -122.5662 | -122.6898 | 0.09613 | 0.11902 | 0.059509 | 0.082398 | 0.022888 | 0.064087 | -0.013733 | 0.059509 | -0.022888 | 0.091553 | 0.10071 | 4.9805 | 0.13733 | -117.8146 | -122.6669 | 4.8752 | 0.013733 | 4.9759 | 0.027466
5224.5312 | 122.6852 | -0.091553 | 122.5525 | -0.012131 | 0.010164 | 0.0085662 | -0.0089358 | -0.0030463 | -0.0083484 | -0.0038772 | -0.011475 | 0.017831 | 0.041994 | -0.024251 | 0.01148 | 0.02311 | -0.0017027 | 4.8569 | 4.8431 | 4.7882 | 4.8248 | 4.9393 | 4.8294 | 4.8706 | 0.022888 | 0 | -0.032043 | -0.013733 | 0.09613 | 0.082397 | 0.082397 | 4.8798 | -117.7094 | -117.7277 | 5.0308 | 4.9622 | 4.921 | 0.082397 | 0.041199 | 0.05951 | -122.5525 | -122.5662 | 0.18768 | 0.17395 | 0.17395 | 0.11444 | 0.11444 | 0.15106 | 0.036621 | 0.12817 | 0.01831 | 0.054932 | 0.032043 | 4.9347 | 0.091553 | -117.7643 | -122.5845 | 4.9164 | 0.07782 | 4.9484 | 0.11444
5226.25 | 122.6578 | -0.082397 | 122.6028 | -0.02739 | 0.014437 | 0.0085662 | -0.007654 | -0.00069646 | -0.011125 | -0.0038772 | -0.005371 | 0.020181 | 0.042208 | -0.016987 | 0.012975 | 0.02076 | -0.0023435 | 4.9301 | 4.9393 | 4.8386 | 4.866 | 4.9576 | 4.8752 | 4.8935 | -0.032043 | 0.018311 | -0.068665 | -0.032043 | 0.091553 | 0.050354 | 0.064087 | 4.921 | -117.6636 | -117.7368 | 5.04 | 4.9759 | 4.9576 | 0.054932 | 0.036621 | 0.013732 | -122.5845 | -122.6349 | 0.17395 | 0.14648 | 0.13275 | 0.13275 | 0.11902 | 0.11902 | 0.027466 | 0.16022 | 0.036622 | 0.10071 | 0.086976 | 5.0217 | 0.10071 | -117.7643 | -122.6715 | 4.9484 | 0.050354 | 5.0125 | 0.050354
5228.0312 | 122.6852 | -0.068665 | 122.5616 | -0.02739 | 0.010805 | 0.01113 | -0.010858 | 0.00079894 | -0.0094164 | -0.0045182 | -0.0084228 | 0.019754 | 0.043703 | -0.017842 | 0.012975 | 0.023537 | -0.0031979 | 4.8386 | 4.7974 | 4.7699 | 4.8019 | 4.9393 | 4.7882 | 4.8523 | 0.036621 | -0.013733 | -0.064087 | -0.004578 | 0.10986 | 0.091553 | 0.091553 | 4.8386 | -117.7643 | -117.7597 | 5.0079 | 4.921 | 4.8569 | 0.082398 | 0.018311 | 0.004578 | -122.5754 | -122.5662 | 0.17853 | 0.16022 | 0.16022 | 0.15564 | 0.15564 | 0.16937 | 0.032044 | 0.17395 | 0.059509 | 0.027466 | 0.050354 | 4.866 | 0.054932 | -117.7917 | -122.6257 | 4.8706 | 0.064087 | 4.9072 | 0.10529
5229.7344 | 122.612 | -0.10529 | 122.612 | -0.0045011 | 0.011232 | 0.0077118 | -0.008295 | -5.5462e-05 | -0.011766 | -0.0043046 | -0.005371 | 0.020608 | 0.042208 | -0.013997 | 0.012334 | 0.023323 | 6.346e-06 | 4.8935 | 4.9255 | 4.8203 | 4.8248 | 4.9576 | 4.8523 | 4.8706 | -0.050354 | 0.027466 | -0.054932 | -0.07782 | 0.027466 | 0 | 0.013733 | 4.9255 | -117.6865 | -117.7872 | 5.0629 | 4.9759 | 4.9576 | 0.050354 | 0.032044 | 0.050354 | -122.5845 | -122.6898 | 0.13275 | 0.11902 | 0.10529 | 0.068665 | 0.054932 | 0.13733 | 0.004578 | 0.082398 | -0.022888 | 0.10529 | 0.082398 | 5.0308 | 0.13275 | -117.7917 | -122.6669 | 4.9301 | 0.027466 | 4.9988 | 0.054932
5231.5156 | 122.6944 | -0.082397 | 122.58 | -0.01976 | 0.013369 | 0.008139 | -0.010218 | -0.0015509 | -0.0089892 | -0.0025956 | -0.011475 | 0.019967 | 0.043276 | -0.018055 | 0.010412 | 0.022896 | -0.0027707 | 4.834 | 4.8065 | 4.7516 | 4.7836 | 4.9026 | 4.7882 | 4.8248 | 0.032043 | -0.004578 | -0.027466 | -0.004578 | 0.11902 | 0.086975 | 0.091553 | 4.834 | -117.7734 | -117.7963 | 4.985 | 4.9072 | 4.8706 | 0.073242 | 0.036621 | 0.054931 | -122.5845 | -122.5845 | 0.20142 | 0.17395 | 0.16937 | 0.11902 | 0.11444 | 0.15106 | 0.032043 | 0.14649 | 0.022888 | 0.054932 | 0.022888 | 4.8889 | 0.077819 | -117.8284 | -122.6074 | 4.866 | 0.077819 | 4.9164 | 0.11444
5233.2188 | 122.7722 | -0.068665 | 122.58 | -0.01976 | 0.0123 | 0.0092072 | -0.011286 | -0.00026906 | -0.0077074 | -0.0025956 | -0.011475 | 0.019754 | 0.040926 | -0.025319 | 0.0095575 | 0.024391 | -0.0036253 | 4.8935 | 4.8248 | 4.8065 | 4.921 | 5.0629 | 4.9072 | 4.9393 | 0.15564 | 0.009155 | -0.018311 | 0.050354 | 0.1831 | 0.14648 | 0.14648 | 4.8752 | -117.7551 | -117.659 | 5.1315 | 5.0079 | 4.9759 | 0.13275 | 0.10071 | 0.050354 | -122.5708 | -122.5296 | 0.25177 | 0.21515 | 0.21515 | 0.16479 | 0.16479 | 0.25635 | 0.11444 | 0.20142 | 0.068665 | 0.01831 | 0.027466 | 4.8935 | 0.07782 | -117.7734 | -122.5983 | 4.9896 | 0.11902 | 4.9622 | 0.22431
5234.9844 | 122.6212 | -0.1236 | 122.6028 | -0.012131 | 0.009737 | 0.0068574 | -0.008295 | 0.00015814 | -0.011553 | -0.0045182 | -0.011475 | 0.021463 | 0.042208 | -0.015706 | 0.014043 | 0.020974 | -0.00020725 | 4.866 | 4.9118 | 4.7928 | 4.8019 | 4.9255 | 4.8203 | 4.8431 | -0.059509 | 0.027466 | -0.07782 | -0.073242 | 0.036621 | -0.004578 | 0.027466 | 4.9164 | -117.691 | -117.8009 | 5.0491 | 4.9667 | 4.9438 | 0.050354 | 0.027465 | 0.045776 | -122.5754 | -122.6761 | 0.16022 | 0.15106 | 0.11902 | 0.10529 | 0.073242 | 0.13275 | 0.009155 | 0.11444 | 0.004578 | 0.11902 | 0.10529 | 5.0354 | 0.15106 | -117.8101 | -122.6807 | 4.9255 | 0.050354 | 4.9896 | 0.064087
5236.7188 | 122.7264 | -0.064087 | 122.5479 | -0.0045011 | 0.014864 | 0.010703 | -0.0067996 | 0.0027215 | -0.0079212 | -0.0015274 | -0.005371 | 0.020822 | 0.039858 | -0.017415 | 0.012762 | 0.022255 | -0.0019163 | 4.7882 | 4.7104 | 4.6967 | 4.7607 | 4.8798 | 4.7195 | 4.7699 | 0.10986 | -0.013733 | -0.013733 | 0.073242 | 0.16022 | 0.12817 | 0.13733 | 4.7607 | -117.8375 | -117.7872 | 4.9438 | 4.834 | 4.7836 | 0.073242 | 0.022888 | 0.050354 | -122.5616 | -122.4747 | 0.2243 | 0.20142 | 0.19226 | 0.15106 | 0.14191 | 0.18311 | 0.064087 | 0.17395 | 0.086975 | 0.013733 | 0 | 4.7745 | 0.050354 | -117.8513 | -122.5616 | 4.8248 | 0.13733 | 4.8523 | 0.17395
5238.5 | 122.731 | -0.082397 | 122.5708 | -0.01976 | 0.010164 | 0.0077118 | -0.010645 | 0.0014397 | -0.010912 | -0.0036636 | -0.005371 | 0.018472 | 0.040712 | -0.016347 | 0.010412 | 0.023537 | -0.0010617 | 4.7928 | 4.7607 | 4.7241 | 4.7745 | 4.8889 | 4.7791 | 4.8111 | 0.018311 | 0 | -0.045776 | 0.022888 | 0.11902 | 0.11444 | 0.10529 | 4.8065 | -117.8101 | -117.7963 | 4.9713 | 4.8935 | 4.8615 | 0.086975 | 0.054932 | 0.036621 | -122.5708 | -122.5479 | 0.20142 | 0.18768 | 0.19684 | 0.15106 | 0.16022 | 0.16479 | 0.050354 | 0.16479 | 0.068664 | 0.036621 | 0.045776 | 4.8431 | 0.082397 | -117.8467 | -122.6166 | 4.8569 | 0.10528 | 4.8752 | 0.10071
5240.2031 | 122.6578 | -0.068665 | 122.6028 | -0.012131 | 0.014009 | 0.0089936 | -0.0091494 | 0.0059259 | -0.011125 | -0.0045182 | -0.0084228 | 0.022744 | 0.043062 | -0.012288 | 0.01383 | 0.020119 | -0.0049069 | 4.834 | 4.8157 | 4.7241 | 4.7928 | 4.9026 | 4.7653 | 4.7928 | 0.050354 | 0.036621 | -0.050354 | 0 | 0.086975 | 0.041199 | 0.073242 | 4.7928 | -117.7872 | -117.8101 | 4.9713 | 4.8615 | 4.834 | 0.068665 | 0.041199 | 0.018311 | -122.5662 | -122.6028 | 0.15564 | 0.14191 | 0.10986 | 0.1236 | 0.091553 | 0.17853 | 0.068665 | 0.13733 | 0.050354 | 0.091553 | 0.086975 | 4.8843 | 0.10529 | -117.8787 | -122.6532 | 4.8615 | 0.068665 | 4.9026 | 0.11902
5241.9844 | 122.6486 | -0.10071 | 122.58 | -0.01976 | 0.015718 | 0.010489 | -0.004877 | 0.0035761 | -0.010485 | -0.0015274 | -0.0084228 | 0.021463 | 0.040285 | -0.0050243 | 0.015112 | 0.024391 | -0.0025571 | 4.7379 | 4.7516 | 4.6555 | 4.66 | 4.747 | 4.6188 | 4.6555 | -0.022888 | 0.022888 | -0.059509 | -0.022888 | 0.054932 | 0.009155 | 0.068665 | 4.7562 | -117.8284 | -117.9199 | 4.8477 | 4.7562 | 4.7195 | 0 | -0.036622 | 0.041199 | -122.5571 | -122.6028 | 0.15564 | 0.16937 | 0.10986 | 0.12817 | 0.068664 | 0.091552 | 0.004577 | 0.11444 | 0.036621 | 0.09613 | 0.082397 | 4.8523 | 0.1236 | -117.9245 | -122.6395 | 4.7607 | 0.07782 | 4.8386 | 0.07782
5243.7656 | 122.7493 | -0.068665 | 122.5845 | -0.012131 | 0.011019 | 0.0077118 | -0.0097904 | -0.00091006 | -0.010057 | -0.0032364 | -0.005371 | 0.020181 | 0.041994 | -0.023823 | 0.012121 | 0.021828 | -0.0051205 | 4.7928 | 4.7424 | 4.7195 | 4.7745 | 4.9164 | 4.7791 | 4.834 | 0.082397 | -0.018311 | -0.036621 | 0.050354 | 0.17853 | 0.14648 | 0.12817 | 4.7882 | -117.8421 | -117.8101 | 4.985 | 4.9026 | 4.8477 | 0.11444 | 0.05951 | 0.032044 | -122.6028 | -122.5342 | 0.24719 | 0.19684 | 0.21515 | 0.1648 | 0.18311 | 0.19684 | 0.054932 | 0.21515 | 0.086975 | 0.022889 | 0.01831 | 4.8111 | 0.050354 | -117.865 | -122.6212 | 4.8431 | 0.11902 | 4.8615 | 0.15106
5245.4688 | 122.6898 | -0.07782 | 122.5891 | -0.0045011 | 0.010591 | 0.00878 | -0.0070132 | 0.0025079 | -0.012407 | -0.0032364 | -0.0023192 | 0.020181 | 0.042421 | -0.020619 | 0.010839 | 0.021401 | -0.0046933 | 4.8477 | 4.7791 | 4.7516 | 4.8431 | 4.9576 | 4.8477 | 4.8523 | 0.054932 | 0.004578 | -0.027466 | -0.013733 | 0.11902 | 0.091553 | 0.086975 | 4.8294 | -117.8101 | -117.746 | 5.0354 | 4.9301 | 4.9255 | 0.10071 | 0.09613 | 0.050354 | -122.5845 | -122.6028 | 0.19684 | 0.16479 | 0.16937 | 0.11444 | 0.11902 | 0.20599 | 0.091553 | 0.14649 | 0.013733 | 0.027466 | 0.032044 | 4.8569 | 0.082398 | -117.8375 | -122.6166 | 4.921 | 0.064087 | 4.9255 | 0.13275
5247.25 | 122.7081 | -0.068665 | 122.5891 | -0.0045011 | 0.013155 | 0.0077118 | -0.0072268 | -0.00069646 | -0.0094164 | -0.0030228 | -0.011475 | 0.018899 | 0.041353 | -0.022969 | 0.0093439 | 0.022683 | -0.0053343 | 4.7241 | 4.6875 | 4.6555 | 4.7058 | 4.8294 | 4.6829 | 4.7333 | 0.022888 | -0.036621 | -0.041199 | -0.009155 | 0.10071 | 0.073242 | 0.091553 | 4.7241 | -117.9016 | -117.8833 | 4.8981 | 4.8019 | 4.7516 | 0.077819 | 0.027465 | 0.027466 | -122.6257 | -122.5983 | 0.16937 | 0.16022 | 0.14191 | 0.13275 | 0.11444 | 0.17395 | 0.050354 | 0.14191 | 0.032044 | 0.032043 | 0.004578 | 4.7562 | 0.032044 | -117.9337 | -122.6303 | 4.7745 | 0.05951 | 4.7928 | 0.091553
5248.9688 | 122.6624 | -0.11902 | 122.5937 | -0.0045011 | 0.01465 | 0.0092072 | -0.005945 | 0.0029351 | -0.010912 | -0.002382 | -0.0084228 | 0.02189 | 0.042208 | -0.010792 | 0.010626 | 0.022255 | -0.0036253 | 4.7699 | 4.7745 | 4.6738 | 4.6921 | 4.7928 | 4.6463 | 4.6829 | 0 | 0.032043 | -0.045776 | -0.027466 | 0.032043 | 0 | 0.036621 | 4.7928 | -117.8192 | -117.9016 | 4.9118 | 4.8019 | 4.7653 | 0.009155 | -0.027466 | 0.073243 | -122.5616 | -122.6212 | 0.15106 | 0.15564 | 0.11902 | 0.082397 | 0.045776 | 0.11902 | 0.018311 | 0.077819 | 0.01831 | 0.10071 | 0.077819 | 4.8935 | 0.15106 | -117.9199 | -122.6395 | 4.8111 | 0.091553 | 4.8889 | 0.11902
5250.75 | 122.7722 | -0.050354 | 122.5708 | -0.02739 | 0.0099506 | 0.008139 | -0.011072 | 0.0020807 | -0.011339 | -0.0043046 | -0.0084228 | 0.018686 | 0.040071 | -0.01891 | 0.010626 | 0.024178 | -0.0034117 | 4.8111 | 4.7379 | 4.6921 | 4.7836 | 4.9347 | 4.8019 | 4.8386 | 0.13275 | 0.018311 | -0.032043 | 0.068665 | 0.20142 | 0.17853 | 0.14648 | 4.7424 | -117.8329 | -117.7872 | 4.985 | 4.8889 | 4.8523 | 0.14648 | 0.10986 | 0.018311 | -122.5525 | -122.5021 | 0.25177 | 0.19684 | 0.22888 | 0.17853 | 0.21057 | 0.24261 | 0.091552 | 0.23346 | 0.10071 | 0.045776 | 0.050354 | 4.7882 | 0.068665 | -117.8787 | -122.6028 | 4.834 | 0.11902 | 4.8614 | 0.18311
5252.4688 | 122.6166 | -0.12817 | 122.6166 | -0.012131 | 0.010164 | 0.0079254 | -0.0097904 | 0.0037897 | -0.010485 | -0.0045182 | -0.0084228 | 0.020608 | 0.04178 | -0.020833 | 0.011694 | 0.022896 | -0.0012753 | 4.747 | 4.8065 | 4.7195 | 4.6967 | 4.8248 | 4.7012 | 4.7424 | -0.064087 | 0.045776 | -0.054932 | -0.07782 | 0.036621 | 0.018311 | 0.032043 | 4.8477 | -117.8101 | -117.9199 | 4.953 | 4.8706 | 4.8294 | 0.022889 | -0.01831 | 0.073242 | -122.5708 | -122.6944 | 0.1648 | 0.16022 | 0.14649 | 0.086975 | 0.073243 | 0.10529 | -0.022888 | 0.091553 | -0.022888 | 0.086976 | 0.10071 | 4.9347 | 0.17395 | -117.897 | -122.6715 | 4.8248 | 0.050354 | 4.8752 | 0.064087
5254.25 | 122.6532 | -0.07782 | 122.5845 | -0.01976 | 0.016146 | 0.012198 | -0.0053042 | 0.00079894 | -0.0094164 | -0.0040908 | -0.0084228 | 0.022103 | 0.042421 | -0.014424 | 0.01383 | 0.022683 | -0.0040525 | 4.7562 | 4.7516 | 4.6646 | 4.7058 | 4.8065 | 4.6738 | 4.7104 | 0.022888 | 0.027466 | -0.059509 | -0.009155 | 0.073242 | 0.027466 | 0.082397 | 4.7424 | -117.8329 | -117.8787 | 4.8843 | 4.7882 | 4.7516 | 0.045776 | 0.009155 | 0.018311 | -122.5571 | -122.5937 | 0.15106 | 0.16022 | 0.10529 | 0.14191 | 0.086975 | 0.14191 | 0.041199 | 0.13275 | 0.050354 | 0.086975 | 0.086975 | 4.8294 | 0.10529 | -117.9199 | -122.644 | 4.7836 | 0.068665 | 4.834 | 0.10071
5256.0312 | 122.6486 | -0.10529 | 122.5983 | -0.012131 | 0.010805 | 0.0094208 | -0.009363 | 0.0033623 | -0.012407 | -0.0019546 | -0.0023192 | 0.020395 | 0.043917 | -0.011006 | 0.014684 | 0.024391 | -0.0031979 | 4.7607 | 4.8157 | 4.7104 | 4.6875 | 4.7699 | 4.6783 | 4.6921 | -0.045776 | 0.022888 | -0.064087 | -0.064087 | 0.050354 | 0.022888 | 0.027466 | 4.8157 | -117.7826 | -117.9108 | 4.8752 | 4.7974 | 4.7836 | -0.01831 | -0.032043 | 0.041199 | -122.5754 | -122.6624 | 0.15564 | 0.13275 | 0.12817 | 0.091553 | 0.086975 | 0.059509 | -0.022888 | 0.11444 | 0 | 0.10529 | 0.086975 | 4.921 | 0.12817 | -117.8879 | -122.6624 | 4.7928 | 0.041199 | 4.866 | 0.05951
5257.75 | 122.6898 | -0.091553 | 122.5983 | -0.0045011 | 0.013582 | 0.010489 | -0.011286 | -0.00091006 | -0.012194 | -0.0030228 | -0.005371 | 0.018258 | 0.042849 | -0.017415 | 0.0097711 | 0.024391 | -0.0029843 | 4.7882 | 4.7012 | 4.6783 | 4.7562 | 4.8981 | 4.7745 | 4.7974 | 0.059509 | -0.004578 | -0.022888 | -0.009155 | 0.11444 | 0.086975 | 0.082397 | 4.7699 | -117.897 | -117.8421 | 4.9896 | 4.8889 | 4.866 | 0.11902 | 0.09613 | 0.068665 | -122.6028 | -122.6074 | 0.20599 | 0.17395 | 0.17853 | 0.10528 | 0.10986 | 0.21973 | 0.07782 | 0.13733 | 0.013733 | 0.022888 | 0.01831 | 4.7928 | 0.086975 | -117.9199 | -122.6212 | 4.8477 | 0.082398 | 4.8798 | 0.15106
5259.5156 | 122.7448 | -0.054932 | 122.5571 | -0.02739 | 0.012514 | 0.0089936 | -0.010004 | -0.00091006 | -0.010698 | -0.0049454 | -0.0084228 | 0.01954 | 0.043703 | -0.020405 | 0.012762 | 0.020974 | -0.0027707 | 4.7699 | 4.6783 | 4.6692 | 4.7607 | 4.9072 | 4.7607 | 4.8065 | 0.12817 | -0.004578 | -0.032043 | 0.050354 | 0.18768 | 0.16479 | 0.11902 | 4.7241 | -117.8787 | -117.7963 | 4.9622 | 4.8615 | 4.8157 | 0.13733 | 0.091553 | 0.022889 | -122.5616 | -122.5067 | 0.24261 | 0.17395 | 0.21973 | 0.15106 | 0.19684 | 0.23804 | 0.091553 | 0.21973 | 0.082397 | 0.009156 | 0.027465 | 4.7333 | 0.050354 | -117.8879 | -122.5891 | 4.8157 | 0.10529 | 4.8248 | 0.18311
5261.2344 | 122.6486 | -0.091553 | 122.5937 | 0.0031279 | 0.012941 | 0.01113 | -0.0057314 | 0.0035761 | -0.0094164 | -0.0038772 | -0.0084228 | 0.021035 | 0.043703 | -0.01891 | 0.014684 | 0.022896 | -0.0036253 | 4.7241 | 4.7058 | 4.6326 | 4.66 | 4.7745 | 4.6509 | 4.6646 | 0.027466 | 0 | -0.050354 | -0.018311 | 0.086975 | 0.036621 | 0.068665 | 4.7241 | -117.8879 | -117.9337 | 4.866 | 4.7562 | 4.7424 | 0.032044 | 0.018311 | 0.041199 | -122.5937 | -122.612 | 0.17853 | 0.16022 | 0.12817 | 0.11902 | 0.086975 | 0.14191 | 0.027466 | 0.13733 | 0.032043 | 0.073243 | 0.050354 | 4.7974 | 0.091553 | -117.9611 | -122.644 | 4.7516 | 0.073242 | 4.8157 | 0.11902
5263.0156 | 122.644 | -0.10529 | 122.6074 | -0.01976 | 0.013155 | 0.0060028 | -0.0089358 | 0.00015814 | -0.01198 | -0.0028092 | -0.0084228 | 0.021035 | 0.043489 | -0.012074 | 0.015112 | 0.022469 | -0.0027707 | 4.715 | 4.7516 | 4.6692 | 4.6371 | 4.747 | 4.6646 | 4.66 | -0.059509 | 0.032043 | -0.064087 | -0.045776 | 0.050354 | 0.027466 | 0.041199 | 4.7745 | -117.8558 | -117.9703 | 4.8523 | 4.7653 | 4.7699 | -0.009155 | -0.004577 | 0.041199 | -122.5754 | -122.6532 | 0.15564 | 0.14649 | 0.13275 | 0.10529 | 0.091553 | 0.07782 | -0.032043 | 0.11444 | 0.018311 | 0.082398 | 0.09613 | 4.8569 | 0.13733 | -117.9382 | -122.6715 | 4.7424 | 0.05951 | 4.8203 | 0.045777
5264.7969 | 122.7173 | -0.086975 | 122.5983 | -0.01976 | 0.010378 | 0.0096344 | -0.010004 | -0.0015509 | -0.010271 | -0.0028092 | -0.0084228 | 0.018899 | 0.042421 | -0.015492 | 0.010412 | 0.023751 | -0.0053343 | 4.6234 | 4.5776 | 4.5502 | 4.5959 | 4.7195 | 4.5822 | 4.6234 | 0.036621 | 0 | -0.045776 | -0.009155 | 0.1236 | 0.091553 | 0.10529 | 4.6371 | -118.0206 | -118.0023 | 4.8065 | 4.7104 | 4.6692 | 0.073242 | 0.032043 | 0.041199 | -122.5983 | -122.6074 | 0.21057 | 0.19226 | 0.17853 | 0.15106 | 0.13733 | 0.16937 | 0.045776 | 0.16937 | 0.036621 | 0.027466 | 0.045776 | 4.6646 | 0.086975 | -118.0481 | -122.644 | 4.6829 | 0.07782 | 4.7104 | 0.1236
5266.5156 | 122.6715 | -0.11444 | 122.5754 | -0.012131 | 0.013369 | 0.011557 | -0.0085086 | -0.0024055 | -0.010698 | -0.0002456 | -0.005371 | 0.021249 | 0.039644 | -0.013142 | 0.012975 | 0.020546 | -0.00042085 | 4.7195 | 4.7058 | 4.6326 | 4.6326 | 4.7516 | 4.6326 | 4.66 | 0.022888 | 0.018311 | -0.041199 | -0.004578 | 0.082397 | 0.050354 | 0.068665 | 4.747 | -117.8696 | -117.9428 | 4.866 | 4.7745 | 4.747 | 0.027466 | 0 | 0.073242 | -122.5571 | -122.58 | 0.19684 | 0.18311 | 0.16479 | 0.10986 | 0.091553 | 0.11902 | 0 | 0.1236 | 0.036621 | 0.073243 | 0.05951 | 4.8203 | 0.13275 | -117.9428 | -122.6166 | 4.747 | 0.10986 | 4.834 | 0.13733
5268.3125 | 122.7676 | -0.068665 | 122.5479 | -0.01976 | 0.010591 | 0.0074982 | -0.009363 | 0.00079894 | -0.01198 | -0.0028092 | -0.005371 | 0.018899 | 0.041994 | -0.020833 | 0.0087029 | 0.025246 | -0.0042661 | 4.6875 | 4.6326 | 4.5868 | 4.6829 | 4.8019 | 4.6921 | 4.7195 | 0.10986 | -0.013733 | -0.045776 | 0.054932 | 0.19226 | 0.17395 | 0.13733 | 4.6555 | -117.9153 | -117.865 | 4.8706 | 4.7882 | 4.7607 | 0.13275 | 0.10529 | 0.022889 | -122.5616 | -122.493 | 0.26093 | 0.20599 | 0.24261 | 0.18311 | 0.21973 | 0.21515 | 0.09613 | 0.23804 | 0.10071 | 0.045776 | 0.032043 | 4.7012 | 0.054932 | -117.9611 | -122.5937 | 4.7516 | 0.1236 | 4.7562 | 0.17853
5270.1094 | 122.6578 | -0.11902 | 122.6166 | -0.01976 | 0.013155 | 0.0077118 | -0.0078676 | -0.0013373 | -0.011125 | -0.0008866 | -0.0084228 | 0.020608 | 0.040926 | -0.020619 | 0.012975 | 0.022255 | -0.0042661 | 4.6829 | 4.7424 | 4.628 | 4.5868 | 4.6967 | 4.6097 | 4.6326 | -0.050354 | 0.027466 | -0.064087 | -0.073242 | 0.054932 | 0.022888 | 0.045776 | 4.747 | -117.8741 | -118.0298 | 4.8157 | 4.7516 | 4.7287 | 0.004577 | -0.018311 | 0.054932 | -122.5891 | -122.6898 | 0.17395 | 0.16479 | 0.14191 | 0.10986 | 0.086975 | 0.068664 | -0.041199 | 0.11902 | -0.009155 | 0.11444 | 0.091553 | 4.8615 | 0.14649 | -117.9886 | -122.6807 | 4.7058 | 0.045777 | 4.8019 | 0.068665
5271.8438 | 122.7539 | -0.086975 | 122.58 | -0.01976 | 0.010805 | 0.0079254 | -0.01214 | 0.0012261 | -0.011125 | -0.0043046 | 0.00073235 | 0.020822 | 0.041567 | -0.017415 | 0.011266 | 0.02311 | -0.0036253 | 4.6326 | 4.6005 | 4.5593 | 4.6234 | 4.7379 | 4.6234 | 4.6646 | 0.050354 | 0 | -0.045776 | 0.045776 | 0.16479 | 0.14191 | 0.12817 | 4.6463 | -117.9794 | -117.9565 | 4.8248 | 4.7516 | 4.7104 | 0.10529 | 0.064087 | 0.041199 | -122.58 | -122.5342 | 0.25177 | 0.21515 | 0.22888 | 0.17395 | 0.18768 | 0.17853 | 0.064087 | 0.21057 | 0.091552 | 0.041199 | 0.045776 | 4.6875 | 0.086975 | -118.0206 | -122.6257 | 4.7104 | 0.13275 | 4.7195 | 0.13733
5273.5781 | 122.7264 | -0.068665 | 122.6257 | -0.01976 | 0.012514 | 0.0079254 | -0.0080814 | 0.0012261 | -0.010057 | -0.0021682 | -0.005371 | 0.021249 | 0.042635 | -0.01891 | 0.010198 | 0.022896 | 0.0015017 | 4.6143 | 4.5868 | 4.5456 | 4.5776 | 4.7012 | 4.5822 | 4.6234 | 0.018311 | -0.004578 | -0.050354 | 0.022888 | 0.1236 | 0.10986 | 0.10986 | 4.6143 | -118.0389 | -118.0481 | 4.7699 | 4.6921 | 4.6509 | 0.07782 | 0.036621 | 0.018311 | -122.6303 | -122.6028 | 0.19226 | 0.17853 | 0.17853 | 0.16022 | 0.16022 | 0.15564 | 0.032044 | 0.17395 | 0.073242 | 0.041199 | 0.045776 | 4.6555 | 0.064087 | -118.0801 | -122.6761 | 4.6463 | 0.091553 | 4.6829 | 0.086976
5275.2969 | 122.699 | -0.054932 | 122.5937 | -0.01976 | 0.010164 | 0.010062 | -0.010218 | -0.00069646 | -0.0092028 | -0.0032364 | -0.005371 | 0.018045 | 0.042635 | -0.023182 | 0.011266 | 0.022683 | -0.0038389 | 4.6005 | 4.5685 | 4.5364 | 4.5776 | 4.6783 | 4.5685 | 4.5959 | 0.027466 | 0.009155 | -0.041199 | 0 | 0.10986 | 0.064087 | 0.091553 | 4.5914 | -118.0252 | -118.0161 | 4.7333 | 4.6509 | 4.6234 | 0.059509 | 0.032043 | 0.013733 | -122.5845 | -122.5937 | 0.16479 | 0.14649 | 0.11902 | 0.13275 | 0.10529 | 0.14191 | 0.041199 | 0.15106 | 0.041199 | 0.032043 | 0.050354 | 4.6234 | 0.064087 | -118.0573 | -122.6349 | 4.6326 | 0.054932 | 4.6555 | 0.082398
5277.0625 | 122.7859 | -0.064087 | 122.5845 | -0.01976 | 0.010591 | 0.0083526 | -0.010858 | 0.00015814 | -0.0098438 | -0.00345 | -0.005371 | 0.020608 | 0.043062 | -0.019124 | 0.0097711 | 0.022255 | -0.0038389 | 4.6692 | 4.5868 | 4.5685 | 4.6692 | 4.7836 | 4.6646 | 4.7058 | 0.12817 | -0.022888 | -0.013733 | 0.054932 | 0.17853 | 0.16022 | 0.14191 | 4.6326 | -117.9977 | -117.9153 | 4.8477 | 4.7699 | 4.7287 | 0.13733 | 0.096131 | 0.050354 | -122.6074 | -122.5296 | 0.24261 | 0.20599 | 0.2243 | 0.15564 | 0.17395 | 0.21515 | 0.10071 | 0.19226 | 0.068665 | 0.018311 | -0.009155 | 4.6509 | 0.041199 | -118.0161 | -122.5983 | 4.7333 | 0.11902 | 4.7333 | 0.19226
5278.7969 | 122.6669 | -0.09613 | 122.5983 | -0.0045011 | 0.012087 | 0.00878 | -0.0072268 | 0.00015814 | -0.011766 | -0.0038772 | -0.011475 | 0.019967 | 0.041567 | -0.022755 | 0.011266 | 0.022255 | -0.0012753 | 4.7012 | 4.6234 | 4.5731 | 4.66 | 4.7836 | 4.6692 | 4.6829 | 0.041199 | 0.009155 | -0.045776 | -0.041199 | 0.082397 | 0.054932 | 0.068665 | 4.6692 | -117.9749 | -117.9382 | 4.8798 | 4.7791 | 4.7653 | 0.10986 | 0.09613 | 0.050354 | -122.5891 | -122.6395 | 0.17853 | 0.16479 | 0.15106 | 0.11444 | 0.10071 | 0.21057 | 0.086975 | 0.12817 | 0.004577 | 0.050354 | 0.054931 | 4.7195 | 0.10528 | -118.0252 | -122.644 | 4.7562 | 0.054931 | 4.7974 | 0.13733
5280.5625 | 122.6303 | -0.10071 | 122.6166 | -0.01976 | 0.011232 | 0.0085662 | -0.0078676 | -0.0024055 | -0.011553 | -0.0025956 | -0.005371 | 0.023599 | 0.040926 | -0.020833 | 0.015325 | 0.022042 | -0.0012753 | 4.6509 | 4.6875 | 4.5959 | 4.5731 | 4.6738 | 4.5776 | 4.5914 | -0.054932 | 0.041199 | -0.07782 | -0.068665 | 0.022888 | 0.009155 | 0.036621 | 4.6967 | -117.9291 | -118.0435 | 4.7745 | 4.6921 | 4.6783 | -0.004577 | -0.01831 | 0.022888 | -122.5754 | -122.6852 | 0.1236 | 0.13733 | 0.10986 | 0.11444 | 0.086975 | 0.07782 | -0.022888 | 0.10071 | 0.009155 | 0.091553 | 0.11902 | 4.7882 | 0.14191 | -118.0206 | -122.6944 | 4.6738 | 0.032043 | 4.7516 | 0.045776
5282.3438 | 122.699 | -0.082397 | 122.5616 | -0.01976 | 0.013369 | 0.0096344 | -0.0080814 | 0.0016535 | -0.010912 | -0.0047318 | -0.011475 | 0.021463 | 0.040499 | -0.018055 | 0.010626 | 0.022469 | -0.0031979 | 4.5547 | 4.5181 | 4.4861 | 4.5273 | 4.6371 | 4.4998 | 4.5639 | 0.022888 | 0.009155 | -0.036621 | 0.009155 | 0.10986 | 0.068665 | 0.10071 | 4.5685 | -118.0435 | -118.0344 | 4.7195 | 4.6463 | 4.5822 | 0.07782 | 0.013733 | 0.045776 | -122.5525 | -122.5525 | 0.19226 | 0.18311 | 0.15106 | 0.13733 | 0.10529 | 0.15106 | 0.041199 | 0.14648 | 0.045776 | 0.032043 | 0.045776 | 4.6005 | 0.091552 | -118.0756 | -122.5983 | 4.6097 | 0.091552 | 4.6371 | 0.10528
5284.0781 | 122.7585 | -0.059509 | 122.5616 | -0.01976 | 0.014437 | 0.011557 | -0.0067996 | -0.0015509 | -0.0092028 | -0.0028092 | -0.005371 | 0.020181 | 0.041353 | -0.012501 | 0.013616 | 0.025673 | -0.0046933 | 4.5639 | 4.4678 | 4.4449 | 4.5319 | 4.6326 | 4.4907 | 4.541 | 0.10529 | -0.018311 | -0.032043 | 0.07782 | 0.15106 | 0.1236 | 0.13733 | 4.5044 | -118.0939 | -118.0298 | 4.6921 | 4.6005 | 4.5502 | 0.096131 | 0.045777 | 0.027466 | -122.58 | -122.4838 | 0.21057 | 0.19684 | 0.1831 | 0.16937 | 0.15564 | 0.18768 | 0.086975 | 0.18311 | 0.10986 | 0.022888 | 0.013732 | 4.5273 | 0.041198 | -118.1168 | -122.5937 | 4.5914 | 0.13733 | 4.6234 | 0.16479
5285.8438 | 122.6257 | -0.1236 | 122.5983 | -0.01976 | 0.011019 | 0.0085662 | -0.010004 | 0.0022943 | -0.012194 | -0.0032364 | -0.011475 | 0.020181 | 0.042421 | -0.019978 | 0.011907 | 0.022683 | -0.0044797 | 4.6326 | 4.6326 | 4.5685 | 4.5685 | 4.6738 | 4.5868 | 4.6005 | -0.032043 | 0.032043 | -0.07782 | -0.064087 | 0.041199 | 0.013733 | 0.022888 | 4.6921 | -117.9657 | -118.0298 | 4.7974 | 4.7241 | 4.7104 | 0.032044 | 0.018311 | 0.045776 | -122.5662 | -122.6624 | 0.16479 | 0.14648 | 0.13733 | 0.10071 | 0.091553 | 0.10529 | 0 | 0.11902 | 0.013733 | 0.064087 | 0.10986 | 4.7562 | 0.15564 | -118.0298 | -122.6761 | 4.6921 | 0.059509 | 4.7562 | 0.091553
5287.5625 | 122.6761 | -0.09613 | 122.6212 | -0.01976 | 0.015078 | 0.010275 | -0.0055178 | 0.00058534 | -0.010271 | -0.0062272 | -0.0084228 | 0.020608 | 0.042421 | -0.0095105 | 0.013616 | 0.023537 | -0.0027707 | 4.628 | 4.6051 | 4.5364 | 4.5547 | 4.6555 | 4.5273 | 4.5456 | 0.027466 | 0.050354 | -0.041199 | -0.009155 | 0.09613 | 0.036621 | 0.07782 | 4.6326 | -118.0161 | -118.0664 | 4.7516 | 4.6417 | 4.6234 | 0.009155 | -0.009155 | 0.054931 | -122.5708 | -122.6303 | 0.19226 | 0.17395 | 0.13275 | 0.11902 | 0.07782 | 0.11902 | 0.018311 | 0.13733 | 0.032044 | 0.068665 | 0.091553 | 4.7012 | 0.14648 | -118.0847 | -122.6624 | 4.6509 | 0.086975 | 4.7241 | 0.1236
5289.2812 | 122.7585 | -0.073242 | 122.5937 | -0.012131 | 0.014437 | 0.0085662 | -0.005945 | 0.0059259 | -0.0070666 | -0.0038772 | -0.0084228 | 0.021035 | 0.040285 | -0.017415 | 0.015752 | 0.023751 | 0.00086095 | 4.4952 | 4.4815 | 4.4357 | 4.4495 | 4.5593 | 4.4174 | 4.4769 | 0.059509 | 0.004578 | -0.032043 | 0.064087 | 0.15106 | 0.10529 | 0.13733 | 4.509 | -118.1122 | -118.1442 | 4.6326 | 4.5502 | 4.4907 | 0.041199 | -0.018311 | 0.041199 | -122.5891 | -122.5296 | 0.2243 | 0.21057 | 0.17853 | 0.16937 | 0.13733 | 0.1236 | 0.013733 | 0.18311 | 0.09613 | 0.045776 | 0.036621 | 4.5547 | 0.07782 | -118.158 | -122.6257 | 4.5227 | 0.13733 | 4.5685 | 0.13275
5291.0156 | 122.7036 | -0.091553 | 122.6166 | -0.012131 | 0.015505 | 0.009848 | -0.005945 | 0.0018671 | -0.010912 | -0.0040908 | -0.011475 | 0.022317 | 0.044344 | -0.01421 | 0.014471 | 0.023537 | -0.0017027 | 4.4861 | 4.5364 | 4.4174 | 4.4037 | 4.5136 | 4.3579 | 4.4174 | 0 | 0.013733 | -0.068665 | 0 | 0.091553 | 0.045776 | 0.086975 | 4.509 | -118.0801 | -118.2129 | 4.6051 | 4.509 | 4.4495 | 0 | -0.059509 | 0.022888 | -122.6028 | -122.6166 | 0.18311 | 0.17853 | 0.13733 | 0.15564 | 0.11444 | 0.096131 | -0.013732 | 0.16022 | 0.068665 | 0.11902 | 0.082398 | 4.628 | 0.10529 | -118.1992 | -122.6852 | 4.4952 | 0.091553 | 4.5776 | 0.091553
5292.7344 | 122.7402 | -0.068665 | 122.6166 | -0.01976 | 0.0093098 | 0.0083526 | -0.010218 | 0.0025079 | -0.012194 | -0.0028092 | -0.005371 | 0.019113 | 0.043062 | -0.022328 | 0.011053 | 0.021401 | -0.0068295 | 4.6371 | 4.541 | 4.5364 | 4.6097 | 4.747 | 4.6097 | 4.6371 | 0.09613 | 0 | -0.032043 | 0.045776 | 0.16479 | 0.12817 | 0.11444 | 4.6051 | -118.0756 | -118.0069 | 4.8157 | 4.7058 | 4.6783 | 0.10071 | 0.073242 | 0.036622 | -122.6166 | -122.5708 | 0.23346 | 0.18311 | 0.19684 | 0.14648 | 0.16022 | 0.21057 | 0.073242 | 0.19684 | 0.077819 | 0.004578 | 0.032043 | 4.6097 | 0.068665 | -118.0801 | -122.6486 | 4.6783 | 0.11444 | 4.7058 | 0.16479
5294.4375 | 122.6852 | -0.086975 | 122.612 | -0.02739 | 0.012728 | 0.010062 | -0.0070132 | 0.0018671 | -0.0094164 | -0.0038772 | -0.0084228 | 0.022744 | 0.041567 | -0.0082287 | 0.013403 | 0.022469 | -0.0049069 | 4.5959 | 4.5547 | 4.4998 | 4.5273 | 4.6417 | 4.509 | 4.5227 | 0.050354 | 0.022888 | -0.045776 | -0.004578 | 0.09613 | 0.064087 | 0.07782 | 4.5868 | -118.0573 | -118.0847 | 4.7287 | 4.6097 | 4.5959 | 0.022888 | 0.009155 | 0.041199 | -122.5891 | -122.6166 | 0.1831 | 0.16479 | 0.15106 | 0.1236 | 0.10986 | 0.14191 | 0.027466 | 0.14191 | 0.041198 | 0.054932 | 0.068664 | 4.6417 | 0.10986 | -118.1122 | -122.6578 | 4.6143 | 0.082397 | 4.6829 | 0.13733
5296.1562 | 122.6303 | -0.11444 | 122.6212 | -0.01976 | 0.016146 | 0.011557 | -0.004877 | 0.0014397 | -0.010057 | -0.001741 | -0.011475 | 0.020395 | 0.04114 | -0.012929 | 0.012548 | 0.022255 | -0.0010617 | 4.4678 | 4.4861 | 4.3762 | 4.3533 | 4.4632 | 4.335 | 4.3762 | -0.073242 | 0.041199 | -0.064087 | -0.064087 | 0.018311 | -0.018311 | 0.027466 | 4.4907 | -118.1351 | -118.2678 | 4.5776 | 4.4907 | 4.4495 | 0 | -0.041199 | 0.050354 | -122.58 | -122.6852 | 0.13275 | 0.14191 | 0.09613 | 0.091553 | 0.045776 | 0.086975 | -0.022888 | 0.082398 | 0 | 0.10986 | 0.10529 | 4.6005 | 0.15564 | -118.2449 | -122.6852 | 4.4678 | 0.050354 | 4.5822 | 0.041199
5297.8906 | 122.7676 | -0.068665 | 122.5937 | -0.012131 | 0.0084552 | 0.008139 | -0.010858 | 0.0033623 | -0.011766 | -0.0038772 | -0.011475 | 0.020822 | 0.041994 | -0.018696 | 0.0099847 | 0.024391 | -0.0025571 | 4.5822 | 4.5136 | 4.4861 | 4.5731 | 4.7379 | 4.5776 | 4.6234 | 0.13733 | -0.013733 | -0.018311 | 0.064087 | 0.19684 | 0.15564 | 0.12817 | 4.5547 | -118.0801 | -118.0206 | 4.8065 | 4.6921 | 4.6463 | 0.13733 | 0.091553 | 0.050354 | -122.6074 | -122.5296 | 0.2655 | 0.19684 | 0.22431 | 0.14649 | 0.17395 | 0.25177 | 0.086975 | 0.21515 | 0.082398 | 0.027466 | 0.004578 | 4.5822 | 0.054932 | -118.1076 | -122.612 | 4.6417 | 0.13275 | 4.6509 | 0.20599
5299.6094 | 122.6761 | -0.10071 | 122.6212 | -0.012131 | 0.015505 | 0.0089936 | -0.0070132 | 0.0031487 | -0.010271 | -0.0057998 | -0.005371 | 0.022531 | 0.042849 | -0.020619 | 0.012334 | 0.022469 | -0.0055479 | 4.4449 | 4.4769 | 4.3716 | 4.3625 | 4.4632 | 4.3259 | 4.3854 | -0.036621 | 0.018311 | -0.041199 | -0.036621 | 0.041199 | 0 | 0.059509 | 4.4724 | -118.1442 | -118.2587 | 4.5639 | 4.4861 | 4.4266 | 0.013733 | -0.045776 | 0.059509 | -122.6028 | -122.6578 | 0.14191 | 0.16022 | 0.10071 | 0.10071 | 0.041199 | 0.091553 | -0.009155 | 0.082398 | 0.004578 | 0.10529 | 0.05951 | 4.5776 | 0.11902 | -118.2495 | -122.6624 | 4.4632 | 0.064087 | 4.5456 | 0.064087
5301.375 | 122.7356 | -0.073242 | 122.5983 | -0.01976 | 0.010805 | 0.0085662 | -0.010218 | 0.0012261 | -0.011339 | -0.0049454 | -0.0084228 | 0.018258 | 0.04114 | -0.024678 | 0.012548 | 0.022896 | -0.0046933 | 4.4907 | 4.4724 | 4.4357 | 4.4449 | 4.5685 | 4.4449 | 4.4815 | 0.022888 | 0.004578 | -0.054932 | -0.009155 | 0.11444 | 0.10529 | 0.09613 | 4.509 | -118.1259 | -118.1534 | 4.6417 | 4.5547 | 4.5181 | 0.045776 | 0.009155 | 0.01831 | -122.5937 | -122.6074 | 0.18768 | 0.16937 | 0.17853 | 0.15106 | 0.16022 | 0.13275 | 0.009155 | 0.16937 | 0.045777 | 0.036621 | 0.05951 | 4.5456 | 0.07782 | -118.1625 | -122.6532 | 4.5181 | 0.064087 | 4.5639 | 0.09613
5303.0938 | 122.7814 | -0.068665 | 122.58 | -0.01976 | 0.0084552 | 0.0079254 | -0.010004 | -0.0028327 | -0.011339 | -0.0055862 | -0.011475 | 0.020181 | 0.039431 | -0.012501 | 0.0095575 | 0.021828 | -0.0038389 | 4.5868 | 4.4998 | 4.4907 | 4.5776 | 4.7195 | 4.5731 | 4.6051 | 0.12817 | -0.013733 | -0.022888 | 0.068665 | 0.1831 | 0.16479 | 0.14191 | 4.5593 | -118.0801 | -118.0023 | 4.7882 | 4.6738 | 4.6417 | 0.11444 | 0.082397 | 0.045777 | -122.5937 | -122.5113 | 0.25177 | 0.21057 | 0.23346 | 0.16479 | 0.18768 | 0.22888 | 0.086975 | 0.20599 | 0.091553 | 0.009155 | 0.009155 | 4.5685 | 0.054932 | -118.0893 | -122.6028 | 4.6463 | 0.13733 | 4.6555 | 0.19684
5304.875 | 122.7859 | -0.073242 | 122.5937 | -0.01976 | 0.011232 | 0.0077118 | -0.0089358 | -0.0026191 | -0.011553 | -0.005159 | 0.00073235 | 0.017617 | 0.039003 | -0.023396 | 0.012121 | 0.021828 | -0.0053343 | 4.5456 | 4.4678 | 4.4357 | 4.5364 | 4.6646 | 4.5319 | 4.5822 | 0.11902 | 0.009155 | -0.032043 | 0.059509 | 0.19226 | 0.16479 | 0.15106 | 4.509 | -118.1259 | -118.0573 | 4.7379 | 4.6555 | 4.6051 | 0.14648 | 0.09613 | 0.041199 | -122.5845 | -122.5342 | 0.2655 | 0.2243 | 0.23804 | 0.18311 | 0.19684 | 0.22888 | 0.10071 | 0.2243 | 0.091552 | 0.032043 | 0.041198 | 4.541 | 0.082397 | -118.158 | -122.6257 | 4.6097 | 0.13275 | 4.6188 | 0.19226
5306.6094 | 122.6349 | -0.10071 | 122.612 | -0.012131 | 0.012514 | 0.010275 | -0.0085086 | 0.0018671 | -0.0098438 | -0.0004592 | -0.005371 | 0.022958 | 0.039858 | -0.010579 | 0.012975 | 0.021187 | -0.0042661 | 4.4815 | 4.4815 | 4.422 | 4.3808 | 4.4907 | 4.3488 | 4.4037 | -0.041199 | 0.022888 | -0.041199 | -0.064087 | 0.032043 | -0.013733 | 0.032043 | 4.5227 | -118.1305 | -118.2312 | 4.5914 | 4.5044 | 4.4495 | -0.01831 | -0.073242 | 0.059509 | -122.5891 | -122.6761 | 0.13275 | 0.13275 | 0.086975 | 0.073242 | 0.027466 | 0.068665 | -0.041199 | 0.073242 | -0.022888 | 0.059509 | 0.064087 | 4.5822 | 0.1236 | -118.19 | -122.6532 | 4.4815 | 0.036621 | 4.5822 | 0.059509
5308.3125 | 122.7448 | -0.064087 | 122.58 | -0.0045011 | 0.01465 | 0.009848 | -0.007654 | -5.5462e-05 | -0.010698 | -0.00345 | -0.0084228 | 0.018472 | 0.040712 | -0.019978 | 0.010839 | 0.021614 | -0.0053343 | 4.454 | 4.3854 | 4.3716 | 4.4037 | 4.5547 | 4.3808 | 4.4449 | 0.064087 | 0 | -0.013733 | 0.022888 | 0.10071 | 0.086975 | 0.091553 | 4.4357 | -118.1946 | -118.1763 | 4.6188 | 4.509 | 4.4449 | 0.073242 | 0.009155 | 0.050354 | -122.58 | -122.5571 | 0.1648 | 0.15564 | 0.15106 | 0.10529 | 0.10071 | 0.18311 | 0.032044 | 0.11444 | 0.036621 | 0.013733 | 0.013733 | 4.4495 | 0.064087 | -118.2083 | -122.5937 | 4.4678 | 0.086975 | 4.5181 | 0.12817
5310.0312 | 122.7173 | -0.068665 | 122.6074 | -0.01976 | 0.011019 | 0.0089936 | -0.0087222 | -0.0017645 | -0.010698 | -0.002382 | -0.0084228 | 0.01954 | 0.043489 | -0.020192 | 0.011266 | 0.023323 | -0.0038389 | 4.5547 | 4.4815 | 4.4586 | 4.5456 | 4.6509 | 4.5319 | 4.5685 | 0.073242 | 0 | -0.036621 | -0.004578 | 0.12817 | 0.10071 | 0.091553 | 4.5273 | -118.1259 | -118.0618 | 4.7195 | 4.6371 | 4.6005 | 0.10986 | 0.073242 | 0.032044 | -122.6074 | -122.612 | 0.19684 | 0.16022 | 0.16937 | 0.12817 | 0.13733 | 0.19226 | 0.086975 | 0.1648 | 0.032043 | 0.022888 | 0.036621 | 4.5502 | 0.068665 | -118.1488 | -122.644 | 4.6143 | 0.064087 | 4.6234 | 0.14191
5311.75 | 122.6395 | -0.11902 | 122.6486 | -0.02739 | 0.017214 | 0.010062 | -0.004877 | 0.00015814 | -0.011553 | -0.0030228 | -0.005371 | 0.021249 | 0.042849 | -0.015278 | 0.01383 | 0.022683 | -0.0049069 | 4.4449 | 4.454 | 4.3808 | 4.3625 | 4.4495 | 4.303 | 4.3533 | -0.064087 | 0.032043 | -0.054932 | -0.054932 | 0.009155 | -0.036621 | 0.027466 | 4.4998 | -118.1946 | -118.2861 | 4.5685 | 4.4724 | 4.422 | -0.027465 | -0.077819 | 0.064087 | -122.6166 | -122.7036 | 0.12817 | 0.14649 | 0.082398 | 0.082398 | 0.018311 | 0.068665 | -0.01831 | 0.064087 | 0 | 0.073243 | 0.086975 | 4.5731 | 0.15106 | -118.2678 | -122.7036 | 4.4815 | 0.064087 | 4.5639 | 0.054932
5313.4688 | 122.6898 | -0.10529 | 122.5937 | -0.01976 | 0.0123 | 0.0094208 | -0.008295 | 0.0044305 | -0.010485 | -0.001741 | -0.0023192 | 0.019967 | 0.042421 | -0.018269 | 0.012762 | 0.023537 | -0.0055479 | 4.5181 | 4.5364 | 4.4357 | 4.4449 | 4.5502 | 4.4495 | 4.4632 | -0.009155 | 0.032043 | -0.045776 | -0.027466 | 0.086975 | 0.045776 | 0.073242 | 4.541 | -118.0573 | -118.1488 | 4.6555 | 4.5685 | 4.5547 | 0.027466 | 0.013733 | 0.05951 | -122.5616 | -122.6212 | 0.19226 | 0.17853 | 0.15106 | 0.11902 | 0.091552 | 0.11444 | 0.009155 | 0.13275 | 0.01831 | 0.10071 | 0.077819 | 4.6417 | 0.13733 | -118.158 | -122.6395 | 4.5502 | 0.07782 | 4.6234 | 0.096131
5315.1719 | 122.6944 | -0.10529 | 122.6212 | -0.01976 | 0.015078 | 0.008139 | -0.0067996 | 0.0054987 | -0.010057 | -0.0049454 | -0.005371 | 0.021676 | 0.04114 | -0.01891 | 0.013189 | 0.024391 | -0.0023435 | 4.3762 | 4.4037 | 4.2892 | 4.2984 | 4.4037 | 4.2801 | 4.3213 | -0.032043 | 0.032043 | -0.068665 | -0.022888 | 0.054932 | 0.013733 | 0.045776 | 4.3945 | -118.2175 | -118.3228 | 4.509 | 4.4266 | 4.3854 | 0.032043 | -0.009156 | 0.036621 | -122.5891 | -122.644 | 0.16022 | 0.15106 | 0.11902 | 0.11444 | 0.082398 | 0.11444 | 0.009155 | 0.1236 | 0.045777 | 0.11444 | 0.10071 | 4.509 | 0.13733 | -118.3319 | -122.6898 | 4.4037 | 0.082398 | 4.4815 | 0.073243
5316.8906 | 122.7127 | -0.086975 | 122.612 | -0.01976 | 0.0123 | 0.00878 | -0.010858 | -0.00069646 | -0.011125 | -0.0072952 | -0.005371 | 0.019967 | 0.043489 | -0.020619 | 0.0097711 | 0.023964 | 0.00064735 | 4.4128 | 4.3854 | 4.3442 | 4.3671 | 4.4998 | 4.3716 | 4.4083 | 0.045776 | 0.004578 | -0.041199 | -0.004578 | 0.10529 | 0.082397 | 0.091553 | 4.4312 | -118.2266 | -118.2449 | 4.5868 | 4.4952 | 4.4586 | 0.064087 | 0.027466 | 0.045776 | -122.6074 | -122.6166 | 0.19226 | 0.17853 | 0.16937 | 0.13275 | 0.1236 | 0.15564 | 0.022888 | 0.14649 | 0.036621 | 0.041199 | 0.045777 | 4.4724 | 0.091553 | -118.2678 | -122.6532 | 4.454 | 0.082397 | 4.4998 | 0.13275
5318.6094 | 122.7356 | -0.050354 | 122.6074 | -0.012131 | 0.01166 | 0.0096344 | -0.0089358 | -0.00091006 | -0.010485 | -0.0025956 | -0.011475 | 0.020822 | 0.038576 | -0.0090833 | 0.0099847 | 0.023964 | -0.0051205 | 4.509 | 4.422 | 4.4312 | 4.4907 | 4.6188 | 4.4952 | 4.5273 | 0.07782 | 0 | -0.045776 | 0.022888 | 0.14648 | 0.11902 | 0.10986 | 4.4815 | -118.1854 | -118.1168 | 4.6692 | 4.5776 | 4.5456 | 0.096131 | 0.064087 | 0.004578 | -122.6074 | -122.5845 | 0.19684 | 0.16022 | 0.16937 | 0.15564 | 0.16479 | 0.18768 | 0.05951 | 0.19226 | 0.068664 | -0.009155 | 0.045776 | 4.4724 | 0.050354 | -118.1763 | -122.6532 | 4.541 | 0.073242 | 4.5593 | 0.12817
5320.3594 | 122.7905 | -0.059509 | 122.5937 | -0.01976 | 0.0095234 | 0.0083526 | -0.0097904 | 0.00058534 | -0.010271 | -0.0028092 | -0.0084228 | 0.020181 | 0.04178 | -0.024678 | 0.011266 | 0.021401 | 0.0012881 | 4.4586 | 4.3854 | 4.3671 | 4.4403 | 4.5776 | 4.4449 | 4.4815 | 0.086975 | -0.013733 | -0.036621 | 0.045776 | 0.16937 | 0.15106 | 0.15106 | 4.4266 | -118.2083 | -118.1534 | 4.6371 | 4.541 | 4.5044 | 0.11444 | 0.07782 | 0.022888 | -122.6074 | -122.5479 | 0.22888 | 0.21057 | 0.21057 | 0.18768 | 0.18768 | 0.21057 | 0.073243 | 0.20599 | 0.082397 | 0.018311 | 0.022888 | 4.4449 | 0.045776 | -118.2266 | -122.6303 | 4.4998 | 0.10528 | 4.5181 | 0.14648
5322.0781 | 122.644 | -0.10986 | 122.6257 | -0.012131 | 0.0086688 | 0.010703 | -0.0097904 | -0.0011237 | -0.013048 | -0.0030228 | -0.0023192 | 0.020822 | 0.042849 | -0.017842 | 0.011907 | 0.019905 | -0.00042085 | 4.4998 | 4.4724 | 4.4128 | 4.422 | 4.5364 | 4.4403 | 4.4632 | -0.018311 | 0.027466 | -0.059509 | -0.059509 | 0.045776 | 0.018311 | 0.022888 | 4.5227 | -118.1534 | -118.2037 | 4.6463 | 4.5731 | 4.5502 | 0.050354 | 0.027466 | 0.050354 | -122.5983 | -122.6852 | 0.15564 | 0.13275 | 0.12817 | 0.082397 | 0.07782 | 0.1236 | 0.009155 | 0.10528 | 0 | 0.059509 | 0.086975 | 4.5822 | 0.13733 | -118.2129 | -122.6852 | 4.5319 | 0.050354 | 4.6097 | 0.091552
5323.7969 | 122.7493 | -0.073242 | 122.5891 | -0.01976 | 0.011873 | 0.0094208 | -0.0095766 | -0.00091006 | -0.00963 | -0.0025956 | -0.0084228 | 0.019326 | 0.040712 | -0.012501 | 0.010626 | 0.02311 | -0.0023435 | 4.3991 | 4.3808 | 4.335 | 4.3671 | 4.4907 | 4.3762 | 4.4174 | 0.041199 | -0.013733 | -0.041199 | 0.013733 | 0.14191 | 0.11902 | 0.11902 | 4.4083 | -118.2083 | -118.222 | 4.5639 | 4.4907 | 4.4495 | 0.082397 | 0.041199 | 0.032043 | -122.6028 | -122.5754 | 0.21515 | 0.19226 | 0.19226 | 0.16022 | 0.16022 | 0.15564 | 0.032043 | 0.18311 | 0.054932 | 0.045776 | 0.027466 | 4.454 | 0.059509 | -118.2541 | -122.6303 | 4.4403 | 0.086975 | 4.4724 | 0.11444
5325.5 | 122.6486 | -0.10986 | 122.6303 | -0.012131 | 0.0099506 | 0.008139 | -0.006586 | -0.0015509 | -0.011553 | -0.0013138 | -0.0023192 | 0.022531 | 0.044558 | -0.014638 | 0.010198 | 0.021828 | -0.0029843 | 4.4403 | 4.4952 | 4.3808 | 4.39 | 4.4998 | 4.3945 | 4.4174 | -0.059509 | 0.050354 | -0.054932 | -0.082397 | 0.027466 | -0.004578 | 0.022888 | 4.4907 | -118.1351 | -118.2404 | 4.6097 | 4.5273 | 4.5044 | 0.036621 | 0.013733 | 0.054931 | -122.58 | -122.7127 | 0.13733 | 0.13275 | 0.10529 | 0.07782 | 0.050354 | 0.11902 | 0.009156 | 0.082398 | -0.027465 | 0.11444 | 0.10529 | 4.6051 | 0.16022 | -118.2495 | -122.6852 | 4.4998 | 0.027466 | 4.5502 | 0.050354
5327.2344 | 122.7402 | -0.082397 | 122.6166 | -0.01976 | 0.010591 | 0.00878 | -0.0097904 | 0.0044305 | -0.01198 | -0.005159 | -0.011475 | 0.020395 | 0.041567 | -0.022542 | 0.011266 | 0.023751 | -0.0044797 | 4.3671 | 4.3442 | 4.303 | 4.3533 | 4.4403 | 4.3304 | 4.3671 | 0.018311 | -0.004578 | -0.041199 | 0.009155 | 0.10071 | 0.068665 | 0.07782 | 4.3854 | -118.2724 | -118.2632 | 4.5227 | 4.4495 | 4.4128 | 0.064086 | 0.027465 | 0.041198 | -122.6212 | -122.6074 | 0.18311 | 0.16022 | 0.15106 | 0.11902 | 0.10986 | 0.13733 | 0.050354 | 0.14191 | 0.050354 | 0.041198 | 0.036621 | 4.4266 | 0.077819 | -118.3136 | -122.6578 | 4.4357 | 0.091552 | 4.4495 | 0.10071
5328.9531 | 122.699 | -0.07782 | 122.6074 | 0.0031279 | 0.012514 | 0.0092072 | -0.0074404 | -0.0028327 | -0.013475 | -0.0043046 | -0.011475 | 0.022103 | 0.040712 | -0.0060925 | 0.011907 | 0.02311 | -0.0076841 | 4.4632 | 4.4449 | 4.3808 | 4.3716 | 4.4998 | 4.3671 | 4.3854 | 0.013733 | 0.036621 | -0.041199 | -0.013733 | 0.082397 | 0.041199 | 0.082397 | 4.4586 | -118.1625 | -118.2358 | 4.5776 | 4.4632 | 4.4449 | 0.004578 | -0.013733 | 0.036621 | -122.5708 | -122.6212 | 0.16022 | 0.16022 | 0.11902 | 0.1236 | 0.082398 | 0.11902 | -0.009155 | 0.1236 | 0.027466 | 0.064087 | 0.07782 | 4.5227 | 0.11444 | -118.2266 | -122.6486 | 4.4495 | 0.064087 | 4.541 | 0.091553
5330.6719 | 122.731 | -0.086975 | 122.5937 | -0.012131 | 0.010805 | 0.0085662 | -0.009363 | -5.5462e-05 | -0.011553 | -0.0049454 | -0.0084228 | 0.018472 | 0.038362 | -0.017628 | 0.011907 | 0.024819 | -0.0019163 | 4.3396 | 4.3076 | 4.2664 | 4.3076 | 4.4403 | 4.3121 | 4.3625 | 0.041199 | 0.004578 | -0.027466 | -0.004578 | 0.09613 | 0.07782 | 0.10071 | 4.3533 | -118.2861 | -118.2861 | 4.5273 | 4.4495 | 4.3991 | 0.096131 | 0.045777 | 0.059509 | -122.5891 | -122.5983 | 0.1831 | 0.18768 | 0.16479 | 0.12817 | 0.10529 | 0.17395 | 0.041199 | 0.1236 | 0.022888 | 0.041199 | 0.032044 | 4.3945 | 0.091553 | -118.3273 | -122.6212 | 4.3945 | 0.082397 | 4.4266 | 0.12817
5332.4062 | 122.7356 | -0.09613 | 122.5983 | -0.01976 | 0.015291 | 0.0092072 | -0.0044498 | 0.0027215 | -0.00963 | -0.0045182 | -0.0084228 | 0.021249 | 0.042635 | -0.019337 | 0.012975 | 0.021828 | -0.0061887 | 4.3121 | 4.3396 | 4.2618 | 4.2618 | 4.3488 | 4.2206 | 4.2755 | 0.036621 | 0.022888 | -0.050354 | 0.036621 | 0.11444 | 0.091553 | 0.11902 | 4.3579 | -118.2587 | -118.3365 | 4.4449 | 4.3716 | 4.3167 | 0.013733 | -0.041199 | 0.045776 | -122.5754 | -122.5616 | 0.21057 | 0.21515 | 0.18768 | 0.16937 | 0.14191 | 0.086975 | 0 | 0.16479 | 0.086975 | 0.07782 | 0.073242 | 4.4357 | 0.11902 | -118.3365 | -122.6486 | 4.3579 | 0.13275 | 4.4083 | 0.13275
5334.1094 | 122.7539 | -0.045776 | 122.612 | -0.01976 | 0.011446 | 0.0092072 | -0.0095766 | 0.00058534 | -0.010485 | -0.0019546 | -0.0084228 | 0.020181 | 0.04114 | -0.018269 | 0.012548 | 0.022469 | -0.0014891 | 4.454 | 4.3716 | 4.3579 | 4.4586 | 4.5822 | 4.4449 | 4.4815 | 0.10529 | -0.018311 | -0.032043 | 0.041199 | 0.16937 | 0.15106 | 0.13275 | 4.4037 | -118.2404 | -118.1534 | 4.628 | 4.5273 | 4.4907 | 0.1236 | 0.086975 | 0.013733 | -122.6303 | -122.5708 | 0.21515 | 0.17853 | 0.19684 | 0.16479 | 0.18311 | 0.2243 | 0.10071 | 0.20142 | 0.073242 | 0.013733 | 0.013732 | 4.4174 | 0.027465 | -118.2541 | -122.644 | 4.5044 | 0.086975 | 4.4998 | 0.15106
5335.8438 | 122.7814 | -0.050354 | 122.5891 | -0.01976 | 0.01465 | 0.010275 | -0.008295 | 0.0014397 | -0.010912 | -0.0032364 | -0.0084228 | 0.019326 | 0.041353 | -0.019551 | 0.011907 | 0.02311 | -0.0029843 | 4.335 | 4.2709 | 4.2389 | 4.2938 | 4.4037 | 4.2664 | 4.3121 | 0.10529 | 0 | -0.027466 | 0.073242 | 0.16022 | 0.1236 | 0.14191 | 4.2892 | -118.3182 | -118.2953 | 4.454 | 4.3625 | 4.3167 | 0.073242 | 0.027465 | 0.022888 | -122.5891 | -122.5159 | 0.21057 | 0.19226 | 0.17395 | 0.16937 | 0.15106 | 0.16479 | 0.054931 | 0.18768 | 0.10071 | 0.032043 | 0.027466 | 4.3213 | 0.050354 | -118.3502 | -122.6166 | 4.3442 | 0.1236 | 4.3854 | 0.15564
5337.5625 | 122.6532 | -0.1236 | 122.6532 | -0.012131 | 0.014437 | 0.0085662 | -0.0080814 | -0.00091006 | -0.0087756 | -0.0025956 | -0.005371 | 0.022103 | 0.040071 | -0.013783 | 0.013189 | 0.022896 | -0.0038389 | 4.4174 | 4.4586 | 4.3533 | 4.3259 | 4.4449 | 4.335 | 4.3488 | -0.064087 | 0.022888 | -0.064087 | -0.086975 | 0.054932 | 0.022888 | 0.045776 | 4.4769 | -118.1946 | -118.3273 | 4.5685 | 4.4724 | 4.4586 | -0.004578 | -0.018311 | 0.059509 | -122.6303 | -122.7402 | 0.17853 | 0.16937 | 0.14648 | 0.10986 | 0.086975 | 0.091552 | -0.027466 | 0.11902 | -0.022888 | 0.10529 | 0.086975 | 4.5822 | 0.14648 | -118.2999 | -122.7173 | 4.4495 | 0.036621 | 4.541 | 0.059509
5339.3281 | 122.7402 | -0.082397 | 122.58 | -0.01976 | 0.015078 | 0.0083526 | -0.006586 | 0.0044305 | -0.0098438 | -0.0038772 | -0.0023192 | 0.02424 | 0.040926 | -0.015492 | 0.015752 | 0.022683 | -0.0051205 | 4.2572 | 4.2892 | 4.2114 | 4.1977 | 4.2984 | 4.1656 | 4.2252 | 0.009155 | 0.004578 | -0.054932 | 0.027466 | 0.09613 | 0.068665 | 0.11444 | 4.2938 | -118.2907 | -118.3823 | 4.3808 | 4.3076 | 4.248 | 0.013733 | -0.045777 | 0.027465 | -122.5754 | -122.5525 | 0.17853 | 0.19684 | 0.15106 | 0.16937 | 0.1236 | 0.086975 | -0.013733 | 0.15106 | 0.082398 | 0.07782 | 0.05951 | 4.3716 | 0.086975 | -118.3685 | -122.6349 | 4.2801 | 0.10986 | 4.3396 | 0.091552
5341.0469 | 122.7539 | -0.064087 | 122.6028 | -0.01976 | 0.013369 | 0.0089936 | -0.0085086 | 0.0022943 | -0.0089892 | -0.0062272 | -0.005371 | 0.021035 | 0.041994 | -0.020619 | 0.01148 | 0.022469 | -0.0029843 | 4.3442 | 4.2526 | 4.2389 | 4.303 | 4.4449 | 4.2892 | 4.3259 | 0.10986 | -0.009155 | -0.032043 | 0.050354 | 0.13733 | 0.11902 | 0.11444 | 4.303 | -118.3502 | -118.2999 | 4.509 | 4.39 | 4.3533 | 0.086975 | 0.050354 | 0.032044 | -122.612 | -122.5525 | 0.20142 | 0.17853 | 0.18311 | 0.14648 | 0.15106 | 0.20599 | 0.064087 | 0.16937 | 0.082397 | 0.013733 | 0.022888 | 4.3167 | 0.054932 | -118.364 | -122.6349 | 4.3671 | 0.11444 | 4.4083 | 0.17395
5342.7969 | 122.7676 | -0.07782 | 122.6212 | -0.0045011 | 0.013796 | 0.012412 | -0.0091494 | 0.0057123 | -0.0092028 | -0.0038772 | -0.005371 | 0.020181 | 0.041353 | -0.018055 | 0.014257 | 0.024819 | -0.0014891 | 4.2892 | 4.2664 | 4.2206 | 4.2343 | 4.335 | 4.1931 | 4.248 | 0.050354 | 0.004578 | -0.045776 | 0.041199 | 0.14648 | 0.086975 | 0.12817 | 4.2984 | -118.3548 | -118.3868 | 4.4128 | 4.3259 | 4.2709 | 0.027466 | -0.027466 | 0.032044 | -122.6166 | -122.58 | 0.2243 | 0.20599 | 0.16479 | 0.17395 | 0.13275 | 0.11444 | 0.013733 | 0.19226 | 0.086975 | 0.045776 | 0.050354 | 4.3442 | 0.082398 | -118.4006 | -122.6669 | 4.3121 | 0.11902 | 4.3671 | 0.12817
5344.5156 | 122.7402 | -0.082397 | 122.6212 | -0.01976 | 0.009737 | 0.0085662 | -0.0085086 | 0.0016535 | -0.010912 | -0.0038772 | -0.0084228 | 0.021035 | 0.040712 | -0.01656 | 0.011907 | 0.022683 | -0.0025571 | 4.2984 | 4.248 | 4.2343 | 4.2801 | 4.3991 | 4.2755 | 4.3167 | 0.032043 | 0.022888 | -0.022888 | -0.009155 | 0.10986 | 0.09613 | 0.091553 | 4.3167 | -118.3731 | -118.3411 | 4.4815 | 4.3991 | 4.3579 | 0.082397 | 0.041199 | 0.059509 | -122.5983 | -122.6303 | 0.19226 | 0.17395 | 0.17853 | 0.11444 | 0.11902 | 0.16479 | 0.045776 | 0.13275 | 0.013733 | 0.013733 | 0.045776 | 4.3304 | 0.10528 | -118.3868 | -122.644 | 4.3625 | 0.073242 | 4.3808 | 0.11444
5346.2344 | 122.7951 | -0.064087 | 122.5891 | -0.01976 | 0.0086688 | 0.00643 | -0.0097904 | 0.00015814 | -0.0070666 | -0.002382 | -0.0084228 | 0.020822 | 0.041994 | -0.014424 | 0.010626 | 0.02311 | -0.0057615 | 4.3579 | 4.3121 | 4.2709 | 4.3625 | 4.4861 | 4.3671 | 4.3991 | 0.11444 | -0.009155 | -0.027466 | 0.045776 | 0.17853 | 0.16937 | 0.14648 | 4.335 | -118.277 | -118.2266 | 4.5502 | 4.4632 | 4.4312 | 0.12817 | 0.09613 | 0.036621 | -122.5983 | -122.5433 | 0.24261 | 0.21057 | 0.23346 | 0.17395 | 0.19684 | 0.21515 | 0.091553 | 0.20599 | 0.073242 | 0.041199 | 0.018311 | 4.3762 | 0.054932 | -118.3182 | -122.6166 | 4.4266 | 0.10986 | 4.422 | 0.17853
5347.9688 | 122.6715 | -0.10071 | 122.6257 | -0.012131 | 0.013582 | 0.010275 | -0.0080814 | 0.0012261 | -0.012407 | -0.0030228 | -0.0084228 | 0.021249 | 0.043703 | -0.013783 | 0.012334 | 0.023964 | -0.0042661 | 4.3762 | 4.3259 | 4.2664 | 4.303 | 4.4266 | 4.2755 | 4.2938 | 0.032043 | 0.036621 | -0.045776 | -0.022888 | 0.068665 | 0.036621 | 0.059509 | 4.3671 | -118.2999 | -118.3228 | 4.5273 | 4.3945 | 4.3762 | 0.027466 | 0.009156 | 0.054932 | -122.5891 | -122.6486 | 0.16937 | 0.16022 | 0.13733 | 0.10528 | 0.082397 | 0.16022 | 0.036622 | 0.11444 | 0.022888 | 0.05951 | 0.082397 | 4.4266 | 0.13733 | -118.3594 | -122.6715 | 4.4037 | 0.07782 | 4.4769 | 0.13275
5349.6875 | 122.6761 | -0.1236 | 122.6257 | -0.01976 | 0.011446 | 0.0094208 | -0.0087222 | 0.0018671 | -0.011339 | -0.0013138 | -0.0084228 | 0.017617 | 0.040712 | -0.01891 | 0.013403 | 0.024178 | -0.0017027 | 4.3991 | 4.3396 | 4.3076 | 4.3533 | 4.4861 | 4.3579 | 4.3762 | 0.009155 | 0.032043 | -0.059509 | -0.045776 | 0.086975 | 0.022888 | 0.036621 | 4.4312 | -118.2861 | -118.2724 | 4.6097 | 4.4998 | 4.4815 | 0.068665 | 0.050354 | 0.064087 | -122.5937 | -122.6715 | 0.21057 | 0.16022 | 0.14648 | 0.09613 | 0.082397 | 0.17853 | 0.045777 | 0.14648 | 0.013733 | 0.032044 | 0.091552 | 4.4632 | 0.15564 | -118.3182 | -122.6852 | 4.4769 | 0.07782 | 4.5227 | 0.13275
5351.4062 | 122.7356 | -0.09613 | 122.6303 | -0.012131 | 0.011232 | 0.0092072 | -0.0080814 | 0.0046441 | -0.0092028 | -0.00345 | -0.005371 | 0.024026 | 0.041994 | -0.012929 | 0.014898 | 0.02311 | -0.0027707 | 4.2389 | 4.2618 | 4.184 | 4.1702 | 4.2755 | 4.1245 | 4.1885 | 0.004578 | 0.022888 | -0.050354 | -0.004578 | 0.086975 | 0.064087 | 0.10071 | 4.2801 | -118.3685 | -118.4601 | 4.3716 | 4.2847 | 4.2206 | 0.004578 | -0.059509 | 0.045776 | -122.6074 | -122.6349 | 0.1831 | 0.19684 | 0.16022 | 0.15106 | 0.11444 | 0.091553 | -0.013733 | 0.13733 | 0.045776 | 0.07782 | 0.073242 | 4.3579 | 0.11902 | -118.4463 | -122.6807 | 4.2664 | 0.091552 | 4.335 | 0.10071
5353.1562 | 122.6532 | -0.11902 | 122.6349 | -0.012131 | 0.012941 | 0.010062 | -0.0095766 | 0.0031487 | -0.010912 | -0.002382 | -0.005371 | 0.019326 | 0.039003 | -0.027028 | 0.012334 | 0.024819 | -0.0044797 | 4.3625 | 4.3396 | 4.2892 | 4.2984 | 4.3945 | 4.2938 | 4.3488 | -0.036621 | 0.036621 | -0.064087 | -0.082397 | 0.050354 | 0.022888 | 0.036621 | 4.4083 | -118.2953 | -118.3365 | 4.5135 | 4.4678 | 4.4128 | 0.059509 | 0.004577 | 0.054932 | -122.5983 | -122.7173 | 0.16937 | 0.15564 | 0.14191 | 0.10071 | 0.086975 | 0.10528 | 0.009155 | 0.11444 | -0.01831 | 0.050354 | 0.10071 | 4.4586 | 0.15564 | -118.3456 | -122.699 | 4.4174 | 0.036622 | 4.4815 | 0.082398
5354.875 | 122.6578 | -0.09613 | 122.6349 | -0.02739 | 0.010591 | 0.010489 | -0.0074404 | 0.0022943 | -0.00963 | -0.0049454 | -0.0023192 | 0.022317 | 0.041353 | -0.013356 | 0.014471 | 0.024391 | -0.0029843 | 4.3625 | 4.3808 | 4.2892 | 4.2572 | 4.3671 | 4.2664 | 4.2892 | -0.064087 | 0.050354 | -0.068665 | -0.068665 | 0.036621 | 0.004578 | 0.041199 | 4.3854 | -118.2541 | -118.3777 | 4.4632 | 4.3854 | 4.3625 | 0 | -0.022889 | 0.027465 | -122.5845 | -122.7036 | 0.13275 | 0.13733 | 0.10071 | 0.10986 | 0.073243 | 0.077819 | -0.032044 | 0.10529 | 0 | 0.091552 | 0.11902 | 4.4769 | 0.14648 | -118.3456 | -122.7036 | 4.3533 | 0.027465 | 4.4586 | 0.032043
5356.5938 | 122.6532 | -0.11902 | 122.6669 | -0.012131 | 0.010591 | 0.0089936 | -0.0091494 | -0.00048286 | -0.010271 | -0.0036636 | -0.011475 | 0.019967 | 0.04413 | -0.013997 | 0.0084893 | 0.023751 | -0.0040525 | 4.2984 | 4.3625 | 4.2572 | 4.2572 | 4.3808 | 4.2709 | 4.3121 | -0.086975 | 0.032043 | -0.050354 | -0.091553 | 0.032043 | 0.004578 | 0.027466 | 4.3762 | -118.3044 | -118.4097 | 4.4998 | 4.4312 | 4.39 | 0.054932 | 0.013733 | 0.068665 | -122.6349 | -122.7585 | 0.15106 | 0.14649 | 0.1236 | 0.07782 | 0.054932 | 0.1236 | 0 | 0.082397 | -0.041199 | 0.10529 | 0.082397 | 4.4815 | 0.15106 | -118.4097 | -122.7173 | 4.3762 | 0.027466 | 4.4174 | 0.032044
5358.3594 | 122.7356 | -0.082397 | 122.6349 | -0.01976 | 0.01166 | 0.0072846 | -0.0095766 | 0.0027215 | -0.010912 | -0.0040908 | -0.0084228 | 0.01954 | 0.041567 | -0.024464 | 0.010839 | 0.023751 | -0.0027707 | 4.3579 | 4.2938 | 4.2664 | 4.335 | 4.4769 | 4.3625 | 4.3762 | 0.045776 | 0.013733 | -0.036621 | -0.009155 | 0.11902 | 0.09613 | 0.10071 | 4.3488 | -118.3411 | -118.2999 | 4.5593 | 4.4586 | 4.4449 | 0.10986 | 0.096131 | 0.045776 | -122.6212 | -122.644 | 0.20142 | 0.18311 | 0.17853 | 0.13733 | 0.13275 | 0.21057 | 0.068665 | 0.15564 | 0.027466 | 0.027466 | 0.050354 | 4.3762 | 0.09613 | -118.3685 | -122.6715 | 4.4174 | 0.073242 | 4.4403 | 0.12817
5360.0625 | 122.6578 | -0.10986 | 122.6166 | -0.012131 | 0.014864 | 0.010703 | -0.0067996 | -0.00069646 | -0.011125 | -0.0040908 | -0.005371 | 0.021463 | 0.042421 | -0.010365 | 0.011694 | 0.023751 | -0.0051205 | 4.248 | 4.2618 | 4.1794 | 4.1565 | 4.248 | 4.1107 | 4.1519 | -0.059509 | 0.036621 | -0.07782 | -0.073242 | 0.018311 | -0.027466 | 0.022888 | 4.2892 | -118.3548 | -118.4601 | 4.3579 | 4.2618 | 4.2206 | -0.027465 | -0.068664 | 0.032043 | -122.58 | -122.6898 | 0.12817 | 0.13275 | 0.082397 | 0.10071 | 0.050354 | 0.068665 | -0.022888 | 0.096131 | 0.004578 | 0.082398 | 0.11444 | 4.3716 | 0.14648 | -118.4372 | -122.6944 | 4.2664 | 0.036621 | 4.3579 | 0.050354
5361.8281 | 122.6807 | -0.09613 | 122.6532 | -0.01976 | 0.013796 | 0.011343 | -0.007654 | 0.0014397 | -0.00963 | -0.0030228 | -0.0023192 | 0.020608 | 0.042849 | -0.012929 | 0.013616 | 0.023323 | -0.0029843 | 4.2892 | 4.2709 | 4.1931 | 4.1885 | 4.3167 | 4.1565 | 4.2023 | -0.004578 | 0.036621 | -0.054932 | -0.050354 | 0.045776 | -0.013733 | 0.050354 | 4.2892 | -118.3823 | -118.4647 | 4.4128 | 4.2984 | 4.2526 | 0.009156 | -0.036621 | 0.041198 | -122.6166 | -122.7036 | 0.14191 | 0.14648 | 0.082397 | 0.10529 | 0.041199 | 0.1236 | -0.004577 | 0.10071 | 0.004578 | 0.07782 | 0.091553 | 4.3671 | 0.13275 | -118.4601 | -122.7081 | 4.2847 | 0.045776 | 4.3854 | 0.091552
5363.5469 | 122.6852 | -0.086975 | 122.6257 | -0.012131 | 0.015078 | 0.010275 | -0.0061588 | 0.00037174 | -0.0092028 | -0.0057998 | -0.005371 | 0.020395 | 0.042849 | -0.013356 | 0.012548 | 0.022255 | -0.0023435 | 4.1885 | 4.2343 | 4.1016 | 4.1016 | 4.2023 | 4.0695 | 4.1153 | -0.036621 | 0.041199 | -0.050354 | -0.050354 | 0.041199 | 0 | 0.064087 | 4.1885 | -118.3914 | -118.5242 | 4.2892 | 4.2023 | 4.1565 | 0.013733 | -0.032043 | 0.036621 | -122.5845 | -122.6761 | 0.12817 | 0.15106 | 0.086975 | 0.11444 | 0.050354 | 0.10071 | 0 | 0.091553 | 0 | 0.13275 | 0.091553 | 4.3213 | 0.12817 | -118.5242 | -122.6761 | 4.1885 | 0.036621 | 4.2755 | 0.050354
5365.2812 | 122.6486 | -0.11902 | 122.6303 | -0.012131 | 0.015291 | 0.010489 | -0.0050906 | 0.0099847 | -0.011125 | -0.00345 | -0.005371 | 0.02189 | 0.041567 | -0.024251 | 0.012762 | 0.023751 | -0.0029843 | 4.1885 | 4.2068 | 4.1382 | 4.097 | 4.1656 | 4.0649 | 4.1061 | -0.10529 | 0.032043 | -0.064087 | -0.073242 | 0.018311 | -0.032043 | 0.032043 | 4.2572 | -118.4235 | -118.5333 | 4.2847 | 4.2252 | 4.184 | -0.032044 | -0.073243 | 0.054932 | -122.5983 | -122.7036 | 0.13733 | 0.15106 | 0.086976 | 0.09613 | 0.032044 | 0.027465 | -0.041199 | 0.082398 | -0.009155 | 0.068664 | 0.09613 | 4.3259 | 0.15106 | -118.4921 | -122.6944 | 4.216 | 0.045777 | 4.3076 | 0.013733
5367 | 122.6532 | -0.1236 | 122.644 | -0.01976 | 0.015932 | 0.0077118 | -0.0061588 | 0.00058534 | -0.0092028 | -0.0038772 | -0.011475 | 0.021035 | 0.041567 | -0.021901 | 0.012762 | 0.02076 | 0.00064735 | 4.1656 | 4.2068 | 4.1061 | 4.0787 | 4.1611 | 4.0329 | 4.0787 | -0.073242 | 0.045776 | -0.07782 | -0.068665 | 0.004578 | -0.027466 | 0.032043 | 4.2297 | -118.4372 | -118.5654 | 4.2847 | 4.2023 | 4.1565 | -0.027466 | -0.073242 | 0.045776 | -122.5983 | -122.7127 | 0.12817 | 0.15564 | 0.09613 | 0.10986 | 0.050354 | 0.054932 | -0.027466 | 0.082398 | 0.009155 | 0.10071 | 0.1236 | 4.3304 | 0.16937 | -118.5379 | -122.7219 | 4.2023 | 0.054931 | 4.2892 | 0.050354
5368.7188 | 122.7951 | -0.064087 | 122.5983 | -0.012131 | 0.012941 | 0.00878 | -0.011713 | 0.0035761 | -0.013262 | -0.0053726 | -0.0084228 | 0.019326 | 0.041567 | -0.016987 | 0.0099847 | 0.022896 | -0.0023435 | 4.2114 | 4.1977 | 4.1611 | 4.1748 | 4.3076 | 4.2023 | 4.2435 | 0.041199 | -0.013733 | -0.036621 | 0.032043 | 0.15106 | 0.1236 | 0.12817 | 4.2252 | -118.4006 | -118.4235 | 4.3716 | 4.3076 | 4.2664 | 0.082397 | 0.041199 | 0.027466 | -122.612 | -122.5662 | 0.21515 | 0.19226 | 0.18768 | 0.1648 | 0.16022 | 0.14648 | 0.013733 | 0.18768 | 0.068664 | 0.036621 | 0.022888 | 4.2618 | 0.050354 | -118.4372 | -122.6349 | 4.2389 | 0.09613 | 4.2755 | 0.10529
5370.4375 | 122.699 | -0.082397 | 122.6303 | -0.012131 | 0.010591 | 0.010062 | -0.010858 | 0.0016535 | -0.013048 | -0.0038772 | -0.011475 | 0.018899 | 0.04114 | -0.017201 | 0.011266 | 0.022683 | -0.0012753 | 4.3121 | 4.248 | 4.216 | 4.2709 | 4.3945 | 4.2847 | 4.3121 | 0.027466 | 0.018311 | -0.045776 | -0.050354 | 0.10071 | 0.059509 | 0.064087 | 4.2984 | -118.3823 | -118.3594 | 4.4769 | 4.3945 | 4.3671 | 0.096131 | 0.068665 | 0.036621 | -122.612 | -122.6807 | 0.18311 | 0.14648 | 0.14191 | 0.10986 | 0.10528 | 0.17853 | 0.054932 | 0.14648 | -0.004578 | 0.032044 | 0.064087 | 4.3304 | 0.10071 | -118.4143 | -122.6761 | 4.3533 | 0.032043 | 4.3945 | 0.10986
5372.1562 | 122.7036 | -0.10986 | 122.6532 | -0.01976 | 0.01166 | 0.0085662 | -0.0067996 | -5.5462e-05 | -0.011339 | -0.0036636 | -0.005371 | 0.021249 | 0.042849 | -0.010579 | 0.010626 | 0.023964 | -0.0012753 | 4.2572 | 4.2938 | 4.2114 | 4.1656 | 4.2801 | 4.1885 | 4.2023 | -0.064087 | 0.036621 | -0.07782 | -0.064087 | 0.059509 | 0.022888 | 0.064087 | 4.3213 | -118.3594 | -118.4875 | 4.39 | 4.3121 | 4.2984 | -0.009155 | -0.022888 | 0.032043 | -122.6166 | -122.7173 | 0.16937 | 0.17395 | 0.13275 | 0.14191 | 0.10071 | 0.068664 | -0.045777 | 0.13733 | 0.013733 | 0.082397 | 0.11444 | 4.4037 | 0.14648 | -118.4418 | -122.731 | 4.2755 | 0.045776 | 4.3671 | 0.045776
5373.8906 | 122.6486 | -0.10529 | 122.644 | -0.01976 | 0.015505 | 0.010062 | -0.0055178 | 0.0012261 | -0.010271 | -0.0021682 | -0.005371 | 0.022744 | 0.043917 | -0.013142 | 0.014684 | 0.021401 | -0.0034117 | 4.1702 | 4.1977 | 4.0924 | 4.0741 | 4.1611 | 4.0329 | 4.0787 | -0.09613 | 0.022888 | -0.064087 | -0.082397 | -0.004578 | -0.036621 | 0.013733 | 4.1977 | -118.4463 | -118.5699 | 4.2664 | 4.184 | 4.1382 | -0.013733 | -0.059509 | 0.041199 | -122.6212 | -122.7264 | 0.10071 | 0.11902 | 0.068665 | 0.07782 | 0.027466 | 0.068665 | -0.01831 | 0.059509 | -0.01831 | 0.10529 | 0.086975 | 4.303 | 0.12817 | -118.5516 | -122.7081 | 4.1794 | 0.022889 | 4.2755 | 0.009156
5375.625 | 122.7173 | -0.11444 | 122.6257 | -0.01976 | 0.011446 | 0.010916 | -0.0087222 | 0.0042169 | -0.00963 | -0.0038772 | -0.0084228 | 0.020608 | 0.042635 | -0.020833 | 0.014043 | 0.02311 | -0.0049069 | 4.2435 | 4.2618 | 4.1565 | 4.1885 | 4.303 | 4.1565 | 4.1748 | 0.022888 | 0.022888 | -0.054932 | -0.013733 | 0.086975 | 0.045776 | 0.073242 | 4.2709 | -118.364 | -118.4372 | 4.4174 | 4.2892 | 4.2709 | 0.018311 | 0 | 0.059509 | -122.6028 | -122.6395 | 0.20142 | 0.18768 | 0.16022 | 0.12817 | 0.10071 | 0.14648 | 0.032044 | 0.14191 | 0.041199 | 0.10529 | 0.07782 | 4.3762 | 0.13733 | -118.4692 | -122.6807 | 4.303 | 0.10071 | 4.3579 | 0.13733
5377.3281 | 122.6898 | -0.09613 | 122.6532 | -0.02739 | 0.014009 | 0.010489 | -0.0074404 | 0.00058534 | -0.012407 | -0.0036636 | -0.005371 | 0.020608 | 0.041567 | -0.020405 | 0.013189 | 0.022896 | -0.0027707 | 4.2252 | 4.1885 | 4.129 | 4.1519 | 4.2709 | 4.1428 | 4.1656 | 0.013733 | 0.032043 | -0.054932 | -0.032043 | 0.054932 | 0.032043 | 0.059509 | 4.2252 | -118.4647 | -118.5013 | 4.3671 | 4.2618 | 4.2389 | 0.036621 | 0.013733 | 0.041198 | -122.6212 | -122.6852 | 0.15106 | 0.15564 | 0.12817 | 0.11444 | 0.086975 | 0.14191 | 0.022889 | 0.10986 | 0.022889 | 0.05951 | 0.086975 | 4.2847 | 0.12817 | -118.5242 | -122.7081 | 4.248 | 0.064087 | 4.3213 | 0.10986
5379.0312 | 122.7539 | -0.064087 | 122.6257 | -0.02739 | 0.011873 | 0.009848 | -0.010431 | -0.00048286 | -0.0092028 | -0.0049454 | -0.011475 | 0.019754 | 0.042421 | -0.016774 | 0.01148 | 0.024605 | -0.0019163 | 4.1519 | 4.1153 | 4.0695 | 4.1153 | 4.248 | 4.1061 | 4.1565 | 0.018311 | 0 | -0.045776 | 0.009155 | 0.10071 | 0.082397 | 0.082397 | 4.1336 | -118.5104 | -118.5104 | 4.3121 | 4.2206 | 4.1702 | 0.086975 | 0.036621 | 0.018311 | -122.6257 | -122.6166 | 0.1648 | 0.14648 | 0.14648 | 0.12817 | 0.12817 | 0.17853 | 0.045776 | 0.14648 | 0.054931 | 0.045776 | 0.045776 | 4.1794 | 0.064087 | -118.5562 | -122.6715 | 4.1794 | 0.073242 | 4.216 | 0.082398
5380.8281 | 122.7036 | -0.091553 | 122.6395 | -0.01976 | 0.014864 | 0.010489 | -0.0070132 | -0.0021919 | -0.0094164 | -0.007936 | -0.011475 | 0.021035 | 0.04178 | -0.0090833 | 0.012975 | 0.022469 | 6.346e-06 | 4.097 | 4.1428 | 4.0375 | 4.0192 | 4.1199 | 4.0009 | 4.0421 | -0.041199 | 0.036621 | -0.059509 | -0.041199 | 0.036621 | -0.009155 | 0.041199 | 4.129 | -118.4967 | -118.6203 | 4.2114 | 4.1336 | 4.0924 | 0.004577 | -0.036622 | 0.032044 | -122.6028 | -122.6807 | 0.12817 | 0.13275 | 0.082398 | 0.10071 | 0.050354 | 0.082397 | -0.018311 | 0.09613 | 0.01831 | 0.10529 | 0.09613 | 4.2343 | 0.12817 | -118.602 | -122.699 | 4.1107 | 0.050354 | 4.1885 | 0.050354
5382.5469 | 122.8088 | -0.054932 | 122.6074 | -0.012131 | 0.010805 | 0.0092072 | -0.0085086 | 0.0010125 | -0.0081348 | -0.0045182 | -0.011475 | 0.019754 | 0.039217 | -0.016133 | 0.011694 | 0.023751 | -0.0034117 | 4.1428 | 4.0512 | 4.0466 | 4.1061 | 4.2297 | 4.0741 | 4.1245 | 0.1236 | 0 | -0.032043 | 0.064087 | 0.16937 | 0.12817 | 0.13733 | 4.1016 | -118.5562 | -118.5013 | 4.2847 | 4.1794 | 4.129 | 0.07782 | 0.027466 | 0.022889 | -122.6074 | -122.5433 | 0.22431 | 0.19226 | 0.18311 | 0.16937 | 0.16022 | 0.18311 | 0.059509 | 0.20142 | 0.09613 | 0.004577 | 0.032043 | 4.1061 | 0.054932 | -118.5608 | -122.6395 | 4.1611 | 0.11902 | 4.1977 | 0.17853
5384.2656 | 122.7356 | -0.073242 | 122.6257 | -0.012131 | 0.010591 | 0.010275 | -0.0095766 | -0.0036871 | -0.008562 | -0.0011002 | -0.014526 | 0.019113 | 0.042421 | -0.017415 | 0.0097711 | 0.021614 | -0.0034117 | 4.1382 | 4.0924 | 4.0741 | 4.0924 | 4.216 | 4.0924 | 4.1382 | 0.036621 | -0.022888 | -0.054932 | -0.004578 | 0.091553 | 0.07782 | 0.082397 | 4.1473 | -118.5333 | -118.5333 | 4.2892 | 4.2114 | 4.1656 | 0.064087 | 0.01831 | 0.01831 | -122.6486 | -122.6303 | 0.16479 | 0.15564 | 0.15106 | 0.13733 | 0.13275 | 0.14191 | 0.01831 | 0.14649 | 0.050354 | 0.01831 | 0.032044 | 4.1656 | 0.050354 | -118.5516 | -122.6807 | 4.1656 | 0.068664 | 4.2114 | 0.10986
5386 | 122.8134 | -0.073242 | 122.6349 | -0.012131 | 0.015505 | 0.011343 | -0.0057314 | 0.0050713 | -0.010912 | -0.0011002 | -0.005371 | 0.01954 | 0.040071 | -0.024464 | 0.012975 | 0.02311 | -0.0053343 | 4.0878 | 4.0741 | 4.0283 | 4.0421 | 4.1473 | 4.01 | 4.0741 | 0.073242 | 0.009155 | -0.009155 | 0.054932 | 0.14191 | 0.11902 | 0.13733 | 4.1016 | -118.5608 | -118.5928 | 4.2206 | 4.1473 | 4.0833 | 0.045777 | -0.01831 | 0.064087 | -122.6257 | -122.58 | 0.21515 | 0.21057 | 0.19226 | 0.14648 | 0.12817 | 0.11902 | 0.013733 | 0.15106 | 0.064087 | 0.045777 | 0.01831 | 4.1473 | 0.082397 | -118.6066 | -122.644 | 4.1153 | 0.12817 | 4.1611 | 0.14648
5387.7031 | 122.8088 | -0.068665 | 122.612 | -0.012131 | 0.0084552 | 0.0083526 | -0.0095766 | -0.0024055 | -0.010698 | -0.0040908 | -0.011475 | 0.018899 | 0.041353 | -0.019337 | 0.0097711 | 0.021401 | -0.0040525 | 4.2343 | 4.1245 | 4.129 | 4.2114 | 4.3762 | 4.2252 | 4.2526 | 0.15106 | -0.009155 | -0.027466 | 0.036621 | 0.19226 | 0.15106 | 0.13275 | 4.1977 | -118.4875 | -118.4006 | 4.4449 | 4.3213 | 4.2938 | 0.1236 | 0.096131 | 0.041199 | -122.6212 | -122.5754 | 0.26093 | 0.20142 | 0.21973 | 0.16022 | 0.17853 | 0.24719 | 0.082398 | 0.21973 | 0.064087 | -0.004577 | 0.018311 | 4.1931 | 0.05951 | -118.483 | -122.6395 | 4.2801 | 0.10529 | 4.303 | 0.21973
5389.4062 | 122.7814 | -0.082397 | 122.6257 | -0.01976 | 0.010805 | 0.010062 | -0.011286 | -0.00048286 | -0.01198 | -0.0047318 | -0.0084228 | 0.020822 | 0.040712 | -0.012288 | 0.0097711 | 0.020333 | -0.0031979 | 4.2252 | 4.1519 | 4.1336 | 4.2252 | 4.3396 | 4.2343 | 4.2526 | 0.10071 | -0.009155 | -0.022888 | 0.036621 | 0.16937 | 0.13733 | 0.1236 | 4.216 | -118.4738 | -118.4006 | 4.422 | 4.335 | 4.3167 | 0.11902 | 0.10071 | 0.059509 | -122.6349 | -122.5891 | 0.25177 | 0.20599 | 0.21973 | 0.14648 | 0.16022 | 0.20599 | 0.091553 | 0.19226 | 0.059509 | 0.018311 | 0.013733 | 4.2343 | 0.073242 | -118.4921 | -122.6486 | 4.3076 | 0.11902 | 4.3076 | 0.18311
5391.1094 | 122.6624 | -0.11902 | 122.644 | -0.012131 | 0.014864 | 0.011557 | -0.0055178 | 0.0035761 | -0.011553 | -0.0049454 | -0.0084228 | 0.022317 | 0.042635 | -0.012288 | 0.013616 | 0.022469 | -0.0042661 | 4.0924 | 4.1336 | 4.0375 | 3.9963 | 4.0787 | 3.9597 | 4.0009 | -0.086975 | 0.041199 | -0.059509 | -0.09613 | -0.018311 | -0.059509 | 0.013733 | 4.1565 | -118.5104 | -118.6478 | 4.1977 | 4.1199 | 4.0787 | -0.036622 | -0.07782 | 0.05951 | -122.6028 | -122.7402 | 0.10071 | 0.13275 | 0.05951 | 0.073242 | 0 | 0.041198 | -0.041199 | 0.041198 | -0.036621 | 0.09613 | 0.10071 | 4.2526 | 0.16022 | -118.6066 | -122.7036 | 4.1153 | 0.022889 | 4.2114 | 0.032044
5392.875 | 122.8088 | -0.068665 | 122.6028 | -0.012131 | 0.016146 | 0.01113 | -0.0072268 | 0.00079894 | -0.010271 | -0.0043046 | -0.005371 | 0.019113 | 0.042849 | -0.018696 | 0.010839 | 0.023964 | -0.0034117 | 4.1245 | 4.0192 | 4.0054 | 4.0695 | 4.1794 | 4.0283 | 4.0741 | 0.11444 | -0.022888 | -0.018311 | 0.07782 | 0.16479 | 0.12817 | 0.16479 | 4.0741 | -118.5837 | -118.5333 | 4.248 | 4.1428 | 4.097 | 0.068665 | 0.022888 | 0.050354 | -122.6257 | -122.525 | 0.23346 | 0.23346 | 0.19684 | 0.18311 | 0.14649 | 0.17395 | 0.064087 | 0.18311 | 0.096131 | 0.013733 | -0.004577 | 4.0878 | 0.045777 | -118.5974 | -122.6212 | 4.1382 | 0.14649 | 4.1931 | 0.18311
5394.5938 | 122.7539 | -0.07782 | 122.6074 | -0.01976 | 0.0076008 | 0.009848 | -0.009363 | 0.0010125 | -0.011125 | -0.0025956 | -0.005371 | 0.017404 | 0.043062 | -0.018696 | 0.010839 | 0.023751 | -0.0057615 | 4.0924 | 4.0878 | 4.0466 | 4.0649 | 4.1794 | 4.0604 | 4.1061 | 0.032043 | 0.009155 | -0.041199 | -0.004578 | 0.12817 | 0.10071 | 0.10071 | 4.1245 | -118.5196 | -118.5425 | 4.2572 | 4.184 | 4.1382 | 0.059509 | 0.013733 | 0.036621 | -122.5983 | -122.612 | 0.20599 | 0.17853 | 0.17853 | 0.14191 | 0.14191 | 0.13275 | 0.01831 | 0.16937 | 0.036621 | 0.041199 | 0.050354 | 4.1657 | 0.086975 | -118.5608 | -122.6486 | 4.1428 | 0.073242 | 4.1702 | 0.10986
5396.3594 | 122.7173 | -0.10071 | 122.6303 | -0.012131 | 0.013796 | 0.0089936 | -0.0055178 | -0.00048286 | -0.0077074 | -0.0057998 | -0.005371 | 0.019967 | 0.040285 | -0.012074 | 0.015112 | 0.022683 | -0.0012753 | 4.1611 | 4.1199 | 4.0558 | 4.0833 | 4.2068 | 4.0787 | 4.097 | 0.036621 | 0.022888 | -0.050354 | -0.013733 | 0.086975 | 0.032043 | 0.068665 | 4.1565 | -118.5104 | -118.5471 | 4.3076 | 4.1977 | 4.1794 | 0.041199 | 0.022888 | 0.050354 | -122.6074 | -122.644 | 0.18768 | 0.16937 | 0.13275 | 0.11902 | 0.082397 | 0.15106 | 0.027466 | 0.13733 | 0.036621 | 0.064087 | 0.073242 | 4.2206 | 0.1236 | -118.5745 | -122.6807 | 4.184 | 0.086975 | 4.2618 | 0.13733
5398.0625 | 122.7859 | -0.054932 | 122.5983 | -0.0045011 | 0.012087 | 0.0096344 | -0.010004 | 0.0029351 | -0.0089892 | -0.0030228 | -0.005371 | 0.018472 | 0.04413 | -0.015065 | 0.010198 | 0.022469 | -0.0034117 | 4.0649 | 3.9825 | 3.9825 | 4.0558 | 4.1885 | 4.0237 | 4.0695 | 0.10071 | -0.013733 | -0.027466 | 0.045776 | 0.14648 | 0.11444 | 0.13275 | 4.0375 | -118.6157 | -118.5425 | 4.2435 | 4.1245 | 4.0787 | 0.086975 | 0.041199 | 0.027466 | -122.612 | -122.5525 | 0.20142 | 0.18768 | 0.16937 | 0.16022 | 0.14191 | 0.20599 | 0.073242 | 0.17395 | 0.073242 | 0 | 0.013733 | 4.0375 | 0.041199 | -118.6157 | -122.6257 | 4.1107 | 0.10071 | 4.1199 | 0.15564
5399.7812 | 122.6944 | -0.10071 | 122.6486 | -0.01976 | 0.011019 | 0.0077118 | -0.006586 | 0.00015814 | -0.010698 | -0.0030228 | -0.011475 | 0.022317 | 0.042421 | -0.015919 | 0.011907 | 0.023323 | -0.0049069 | 4.1565 | 4.1931 | 4.1016 | 4.0512 | 4.1748 | 4.0604 | 4.0924 | -0.059509 | 0.041199 | -0.068665 | -0.064087 | 0.054932 | 0.013733 | 0.041199 | 4.2023 | -118.4555 | -118.5974 | 4.2755 | 4.1931 | 4.1611 | -0.009155 | -0.041198 | 0.032043 | -122.6074 | -122.7127 | 0.15564 | 0.14191 | 0.11444 | 0.10986 | 0.082398 | 0.073243 | -0.050354 | 0.1236 | 0.004578 | 0.091553 | 0.10986 | 4.2938 | 0.14191 | -118.5471 | -122.7173 | 4.1519 | 0.036621 | 4.2572 | 0.041199
5401.5156 | 122.7814 | -0.059509 | 122.612 | -0.012131 | 0.012087 | 0.009848 | -0.006586 | 0.0059259 | -0.011553 | -0.0038772 | -0.011475 | 0.021463 | 0.04178 | -0.0099377 | 0.0099847 | 0.021187 | -0.0029843 | 4.0009 | 4.0283 | 3.9551 | 3.9597 | 4.0787 | 3.9322 | 3.978 | 0.036621 | 0.022888 | -0.036621 | 0.032043 | 0.1236 | 0.068665 | 0.11902 | 4.0146 | -118.5837 | -118.6523 | 4.1382 | 4.0375 | 3.9917 | 0.022888 | -0.022888 | 0.022888 | -122.5891 | -122.58 | 0.1831 | 0.17853 | 0.12817 | 0.15564 | 0.10529 | 0.1236 | 0.004578 | 0.16022 | 0.068664 | 0.073242 | 0.059509 | 4.0878 | 0.082397 | -118.6569 | -122.6486 | 4.0192 | 0.091552 | 4.0604 | 0.09613
5403.2812 | 122.7036 | -0.1236 | 122.6669 | -0.012131 | 0.014864 | 0.0083526 | -0.008295 | -0.0015509 | -0.0087756 | -0.0057998 | -0.005371 | 0.02189 | 0.043062 | -0.013569 | 0.012334 | 0.022896 | 6.346e-06 | 4.1336 | 4.1519 | 4.0833 | 4.0375 | 4.1519 | 4.0558 | 4.0741 | -0.073242 | 0.050354 | -0.059509 | -0.054932 | 0.050354 | 0.018311 | 0.041199 | 4.2068 | -118.515 | -118.6295 | 4.2755 | 4.1977 | 4.1794 | -0.009155 | -0.027466 | 0.064087 | -122.6166 | -122.7219 | 0.17395 | 0.16479 | 0.14191 | 0.10071 | 0.07782 | 0.068665 | -0.045776 | 0.10986 | 0.004577 | 0.068665 | 0.10986 | 4.2755 | 0.17395 | -118.5837 | -122.7264 | 4.1611 | 0.068664 | 4.2572 | 0.050354
5405 | 122.6715 | -0.091553 | 122.6807 | -0.02739 | 0.013369 | 0.010916 | -0.0089358 | 0.0016535 | -0.010271 | -0.0040908 | -0.005371 | 0.019967 | 0.042208 | -0.013142 | 0.014684 | 0.022896 | -0.0029843 | 4.0741 | 4.0833 | 4.01 | 3.9642 | 4.0787 | 3.9413 | 3.9688 | -0.041199 | 0.022888 | -0.045776 | -0.064087 | 0.022888 | -0.022888 | 0.032043 | 4.1016 | -118.5974 | -118.7164 | 4.1702 | 4.0604 | 4.0329 | -0.041199 | -0.068665 | 0.045777 | -122.6578 | -122.7448 | 0.11444 | 0.1236 | 0.068665 | 0.077819 | 0.022888 | 0.068664 | -0.045777 | 0.068664 | -0.018311 | 0.073242 | 0.068664 | 4.1748 | 0.11444 | -118.6707 | -122.7264 | 4.0558 | 0.027466 | 4.1657 | 0.050354
5406.7188 | 122.6807 | -0.10071 | 122.6578 | -0.0045011 | 0.009737 | 0.0074982 | -0.010004 | 0.0016535 | -0.0087756 | -0.0036636 | -0.005371 | 0.020395 | 0.04178 | -0.022969 | 0.01148 | 0.023323 | -0.0012753 | 4.0878 | 4.1245 | 4.0421 | 4.0192 | 4.1656 | 4.0329 | 4.0741 | -0.054932 | 0.050354 | -0.068665 | -0.091553 | 0.032043 | 0.036621 | 0.027466 | 4.1428 | -118.5333 | -118.6386 | 4.2664 | 4.1748 | 4.1336 | 0.032044 | -0.009155 | 0.032043 | -122.6074 | -122.7493 | 0.13275 | 0.12817 | 0.13733 | 0.096131 | 0.10529 | 0.1236 | -0.022888 | 0.10071 | -0.022888 | 0.082398 | 0.11902 | 4.2252 | 0.15106 | -118.6157 | -122.7264 | 4.1199 | 0.009155 | 4.1885 | 0.045776
5408.4375 | 122.7951 | -0.054932 | 122.6257 | -0.0045011 | 0.014223 | 0.013052 | -0.010218 | 0.00079894 | -0.0070666 | -0.0028092 | -0.0084228 | 0.020181 | 0.040712 | -0.0090833 | 0.013189 | 0.022896 | -0.0023435 | 4.0421 | 3.9597 | 3.9368 | 3.9963 | 4.1199 | 3.9734 | 4.0146 | 0.09613 | -0.004578 | -0.027466 | 0.059509 | 0.16022 | 0.11444 | 0.14191 | 3.9917 | -118.6661 | -118.6295 | 4.1748 | 4.0695 | 4.0283 | 0.077819 | 0.036621 | 0.027466 | -122.6303 | -122.5662 | 0.21515 | 0.19684 | 0.16937 | 0.16937 | 0.14191 | 0.18311 | 0.059509 | 0.18768 | 0.086975 | 0.022888 | 0.022888 | 4.0146 | 0.050354 | -118.689 | -122.6532 | 4.0512 | 0.11444 | 4.097 | 0.15106
5410.1562 | 122.7722 | -0.059509 | 122.644 | -0.01976 | 0.012087 | 0.00878 | -0.0072268 | 0.0018671 | -0.010271 | -0.0032364 | -0.0084228 | 0.019326 | 0.042208 | -0.020405 | 0.010626 | 0.023751 | -0.0042661 | 4.0375 | 3.9368 | 3.9505 | 4.0009 | 4.1382 | 4.0054 | 4.0283 | 0.10986 | 0.004578 | -0.036621 | 0.050354 | 0.13733 | 0.10529 | 0.10986 | 4.01 | -118.7073 | -118.6432 | 4.1977 | 4.0878 | 4.0649 | 0.07782 | 0.054932 | 0.022888 | -122.6395 | -122.5937 | 0.19684 | 0.16937 | 0.16479 | 0.14648 | 0.14191 | 0.18768 | 0.050354 | 0.17395 | 0.086975 | -0.013732 | 0.041199 | 3.9963 | 0.064087 | -118.6935 | -122.6807 | 4.0604 | 0.10986 | 4.097 | 0.16937
5411.875 | 122.818 | -0.050354 | 122.6486 | -0.01976 | 0.010591 | 0.0079254 | -0.010004 | 0.00015814 | -0.010057 | -0.0019546 | -0.011475 | 0.020608 | 0.040712 | -0.018055 | 0.0095575 | 0.02311 | -0.0057615 | 4.129 | 4.0421 | 4.0375 | 4.1107 | 4.2572 | 4.129 | 4.1565 | 0.13733 | -0.009155 | -0.022888 | 0.054932 | 0.1831 | 0.16479 | 0.13733 | 4.0878 | -118.6066 | -118.5379 | 4.3076 | 4.2068 | 4.1794 | 0.11902 | 0.091552 | 0.027466 | -122.6578 | -122.5937 | 0.23346 | 0.18768 | 0.21515 | 0.16022 | 0.18768 | 0.21973 | 0.073242 | 0.20599 | 0.07782 | 0.004577 | 0.013733 | 4.0924 | 0.041199 | -118.6111 | -122.6715 | 4.1611 | 0.10529 | 4.1794 | 0.18768
5413.5938 | 122.818 | -0.045776 | 122.5983 | -0.01976 | 0.014223 | 0.009848 | -0.0055178 | 0.0010125 | -0.0089892 | -0.0066544 | -0.005371 | 0.021463 | 0.041994 | -0.013142 | 0.013189 | 0.022469 | -0.0057615 | 4.0329 | 3.9368 | 3.923 | 3.9871 | 4.097 | 3.9413 | 3.9917 | 0.10071 | -0.022888 | -0.027466 | 0.082397 | 0.16479 | 0.10986 | 0.13275 | 3.9688 | -118.6615 | -118.6111 | 4.1428 | 4.0375 | 3.9871 | 0.068664 | 0.01831 | 0.01831 | -122.6212 | -122.5159 | 0.21057 | 0.17853 | 0.15564 | 0.16022 | 0.13733 | 0.17395 | 0.064087 | 0.19226 | 0.10986 | 0.013733 | 0.004578 | 3.9825 | 0.022888 | -118.6752 | -122.6257 | 4.0329 | 0.12817 | 4.0787 | 0.14648
5415.3438 | 122.8134 | -0.054932 | 122.6257 | -0.01976 | 0.014437 | 0.009848 | -0.0080814 | 0.00058534 | -0.0098438 | -0.0036636 | -0.005371 | 0.019754 | 0.043489 | -0.01656 | 0.012975 | 0.023323 | -0.0055479 | 4.0237 | 3.9322 | 3.9093 | 3.9688 | 4.0833 | 3.9459 | 3.9917 | 0.10071 | -0.018311 | -0.041199 | 0.064087 | 0.14648 | 0.11444 | 0.14191 | 3.9642 | -118.6935 | -118.6569 | 4.1382 | 4.0466 | 4.0009 | 0.082397 | 0.036621 | 0.013733 | -122.644 | -122.5616 | 0.20142 | 0.19684 | 0.16937 | 0.18311 | 0.15564 | 0.17395 | 0.059509 | 0.18768 | 0.10529 | 0.022888 | 0.022888 | 3.9871 | 0.036621 | -118.7164 | -122.6669 | 4.0237 | 0.11902 | 4.0787 | 0.15564
5417.0469 | 122.8043 | -0.073242 | 122.644 | -0.012131 | 0.010378 | 0.00878 | -0.0095766 | -0.00048286 | -0.00963 | -0.0047318 | -0.011475 | 0.020822 | 0.04114 | -0.017842 | 0.010626 | 0.022255 | -0.0057615 | 4.1245 | 4.0329 | 4.0146 | 4.1199 | 4.2435 | 4.1199 | 4.1473 | 0.10986 | 0 | -0.027466 | 0.041199 | 0.17395 | 0.14191 | 0.12817 | 4.0878 | -118.6111 | -118.5242 | 4.3167 | 4.2206 | 4.1931 | 0.13275 | 0.10529 | 0.045776 | -122.644 | -122.6028 | 0.24719 | 0.20142 | 0.21515 | 0.15564 | 0.16937 | 0.22888 | 0.10529 | 0.20142 | 0.068665 | 0.018311 | 0.027466 | 4.1061 | 0.073242 | -118.6295 | -122.6715 | 4.1931 | 0.11444 | 4.1977 | 0.18311
5418.7812 | 122.8226 | -0.073242 | 122.6166 | -0.02739 | 0.012941 | 0.0079254 | -0.009363 | -0.00069646 | -0.01198 | -0.0036636 | -0.0084228 | 0.018258 | 0.04413 | -0.021473 | 0.011694 | 0.021828 | -0.0034117 | 4.0787 | 4.0192 | 3.9825 | 4.0512 | 4.1977 | 4.0695 | 4.097 | 0.13275 | -0.022888 | -0.022888 | 0.064087 | 0.19684 | 0.16937 | 0.14648 | 4.0558 | -118.5974 | -118.5654 | 4.2709 | 4.1702 | 4.1428 | 0.11444 | 0.086975 | 0.050354 | -122.6395 | -122.5525 | 0.27008 | 0.21973 | 0.24261 | 0.16937 | 0.19226 | 0.21515 | 0.068664 | 0.21973 | 0.086975 | 0.036621 | 0 | 4.0924 | 0.050354 | -118.634 | -122.6395 | 4.1244 | 0.13733 | 4.1519 | 0.20599
5420.5 | 122.7814 | -0.086975 | 122.644 | -0.01976 | 0.012514 | 0.0094208 | -0.0095766 | -0.0060371 | -0.011553 | -0.0032364 | -0.011475 | 0.018258 | 0.040712 | -0.01421 | 0.010198 | 0.02311 | -0.0027707 | 3.9963 | 3.9642 | 3.9322 | 3.9459 | 4.0604 | 3.9551 | 4.0009 | 0.032043 | 0 | -0.027466 | -0.018311 | 0.11444 | 0.073242 | 0.10071 | 4.0192 | -118.6798 | -118.6981 | 4.1473 | 4.0878 | 4.0421 | 0.068664 | 0.022888 | 0.059509 | -122.644 | -122.6624 | 0.20142 | 0.18768 | 0.16022 | 0.12817 | 0.10071 | 0.12817 | 0.013733 | 0.14191 | 0.009155 | 0.032043 | 0.027466 | 4.0512 | 0.086975 | -118.7119 | -122.6715 | 4.0329 | 0.068664 | 4.0833 | 0.11902
5422.25 | 122.6852 | -0.11902 | 122.6898 | -0.01976 | 0.009096 | 0.007071 | -0.006586 | -0.0028327 | -0.010912 | -0.0055862 | -0.005371 | 0.02189 | 0.041567 | -0.013569 | 0.010626 | 0.019265 | -0.0040525 | 4.0695 | 4.1107 | 4.0009 | 4.01 | 4.097 | 3.9963 | 4.0192 | -0.045776 | 0.032043 | -0.07782 | -0.068665 | 0.027466 | -0.004578 | 0.036621 | 4.1199 | -118.5791 | -118.6798 | 4.216 | 4.1382 | 4.1153 | 0.018311 | -0.004577 | 0.041199 | -122.6578 | -122.7585 | 0.14649 | 0.15564 | 0.11444 | 0.11444 | 0.073242 | 0.096131 | 0.009156 | 0.10529 | 0.009155 | 0.10986 | 0.10986 | 4.2297 | 0.15106 | -118.689 | -122.7676 | 4.129 | 0.050354 | 4.1885 | 0.073243
5423.9531 | 122.6761 | -0.11444 | 122.6624 | -0.01976 | 0.01465 | 0.011771 | -0.0061588 | -0.0043281 | -0.008562 | -0.0032364 | -0.011475 | 0.02189 | 0.042849 | -0.013356 | 0.013616 | 0.023537 | -0.00042085 | 3.9322 | 3.9917 | 3.9093 | 3.8361 | 3.9047 | 3.7994 | 3.8589 | -0.07782 | 0.041199 | -0.059509 | -0.054932 | 0 | -0.041199 | 0.036621 | 4.0237 | -118.6707 | -118.8263 | 4.0192 | 3.9734 | 3.9139 | -0.050354 | -0.10986 | 0.054932 | -122.6212 | -122.7173 | 0.11444 | 0.15106 | 0.073242 | 0.09613 | 0.01831 | -0.004578 | -0.073242 | 0.059509 | 0.004577 | 0.082397 | 0.10071 | 4.1061 | 0.15564 | -118.7531 | -122.7219 | 3.9505 | 0.059509 | 4.0466 | 0.036621
5425.6719 | 122.7722 | -0.07782 | 122.6212 | -0.012131 | 0.01166 | 0.0085662 | -0.010218 | -0.0013373 | -0.010485 | -0.0036636 | -0.005371 | 0.021035 | 0.04413 | -0.025532 | 0.012334 | 0.02311 | -0.0042661 | 3.9734 | 3.9368 | 3.9093 | 3.9276 | 4.0512 | 3.9185 | 3.978 | 0.009155 | 0.013733 | -0.041199 | -0.004578 | 0.12817 | 0.086975 | 0.10529 | 3.9871 | -118.6844 | -118.6935 | 4.129 | 4.0558 | 3.9963 | 0.068664 | 0.009155 | 0.036621 | -122.6074 | -122.6257 | 0.20599 | 0.18311 | 0.16479 | 0.14649 | 0.12817 | 0.14191 | 0.01831 | 0.16937 | 0.036621 | 0.027466 | 0.054932 | 4.0146 | 0.091553 | -118.7119 | -122.6624 | 4.0054 | 0.073242 | 4.0512 | 0.086975
5427.3906 | 122.7539 | -0.082397 | 122.644 | -0.01976 | 0.015291 | 0.009848 | -0.005945 | -0.0053961 | -0.010057 | -0.0057998 | -0.005371 | 0.022103 | 0.04178 | -0.015065 | 0.01383 | 0.022683 | -0.0083249 | 3.9276 | 3.9459 | 3.8589 | 3.8315 | 3.9505 | 3.8086 | 3.8498 | -0.018311 | 0.013733 | -0.050354 | -0.009155 | 0.073242 | 0.050354 | 0.086975 | 3.9413 | -118.6981 | -118.8126 | 4.0329 | 3.9322 | 3.891 | -0.009156 | -0.050354 | 0.032043 | -122.6303 | -122.6532 | 0.15564 | 0.16937 | 0.13275 | 0.13733 | 0.10071 | 0.091552 | -0.027466 | 0.1236 | 0.041199 | 0.086975 | 0.064087 | 4.0283 | 0.09613 | -118.7851 | -122.6944 | 3.9139 | 0.073242 | 4.01 | 0.064086
5429.0938 | 122.8088 | -0.059509 | 122.6395 | -0.0045011 | 0.0093098 | 0.0057892 | -0.010431 | 0.00079894 | -0.010485 | -0.0057998 | -0.0084228 | 0.01954 | 0.040071 | -0.019124 | 0.010412 | 0.023751 | -0.0046933 | 4.01 | 3.9597 | 3.923 | 3.9871 | 4.1061 | 4.0192 | 4.0375 | 0.086975 | -0.009155 | -0.041199 | 0.064087 | 0.16937 | 0.15106 | 0.13733 | 3.9825 | -118.6798 | -118.6523 | 4.1656 | 4.097 | 4.0787 | 0.11444 | 0.09613 | 0.01831 | -122.6486 | -122.5754 | 0.22888 | 0.19684 | 0.21057 | 0.17853 | 0.19226 | 0.1831 | 0.064087 | 0.21057 | 0.10529 | 0.036621 | 0.032044 | 4.0192 | 0.050354 | -118.7164 | -122.6807 | 4.0466 | 0.1236 | 4.0695 | 0.14648
5430.8125 | 122.7356 | -0.09613 | 122.6669 | -0.012131 | 0.014223 | 0.0079254 | -0.0070132 | 0.00037174 | -0.013262 | -0.0049454 | -0.005371 | 0.024026 | 0.04178 | -0.011006 | 0.012334 | 0.024819 | -0.0040525 | 4.0466 | 4.0741 | 3.9688 | 3.9642 | 4.0604 | 3.9597 | 3.9688 | 0.013733 | 0.036621 | -0.050354 | -0.018311 | 0.086975 | 0.059509 | 0.064087 | 4.0649 | -118.5928 | -118.7027 | 4.1565 | 4.0649 | 4.0558 | 0 | -0.009155 | 0.045776 | -122.6303 | -122.6852 | 0.1831 | 0.16022 | 0.15564 | 0.11444 | 0.10986 | 0.091553 | -0.004578 | 0.13733 | 0.032043 | 0.10529 | 0.086975 | 4.1702 | 0.13275 | -118.6981 | -122.7173 | 4.0604 | 0.077819 | 4.1428 | 0.10986
5432.5312 | 122.6944 | -0.10986 | 122.6761 | -0.01976 | 0.015505 | 0.011771 | -0.0070132 | 0.0020807 | -0.010485 | -0.0057998 | -0.005371 | 0.019326 | 0.043062 | -0.013142 | 0.013616 | 0.022255 | -0.0055479 | 3.9139 | 3.9597 | 3.8589 | 3.8177 | 3.9001 | 3.7857 | 3.8132 | -0.10529 | 0.036621 | -0.073242 | -0.045776 | 0.018311 | -0.036621 | 0.032043 | 3.9688 | -118.7164 | -118.8583 | 4.01 | 3.923 | 3.8956 | -0.045777 | -0.073242 | 0.036621 | -122.6395 | -122.7219 | 0.12817 | 0.14191 | 0.073242 | 0.10529 | 0.036621 | 0.041198 | -0.041199 | 0.091553 | 0.027466 | 0.10071 | 0.10986 | 4.0695 | 0.14648 | -118.8171 | -122.7493 | 3.9276 | 0.064087 | 4.0237 | 0.004577
5434.2969 | 122.6807 | -0.10071 | 122.6761 | -0.012131 | 0.010591 | 0.0083526 | -0.0087222 | 0.0033623 | -0.010271 | -0.0002456 | -0.005371 | 0.021676 | 0.040926 | -0.0097241 | 0.01148 | 0.024178 | 0.0032107 | 4.0421 | 4.0192 | 3.9459 | 3.9642 | 4.0833 | 3.9825 | 3.9871 | -0.013733 | 0.018311 | -0.064087 | -0.068665 | 0.045776 | 0.009155 | 0.022888 | 4.0466 | -118.6569 | -118.7119 | 4.184 | 4.0878 | 4.0833 | 0.041199 | 0.036621 | 0.036621 | -122.6578 | -122.7448 | 0.14648 | 0.1236 | 0.10986 | 0.086975 | 0.073242 | 0.13733 | 0.01831 | 0.10986 | -0.004578 | 0.073242 | 0.082398 | 4.1199 | 0.11902 | -118.7302 | -122.7402 | 4.0649 | 0.032043 | 4.1428 | 0.086975
5436.0156 | 122.7219 | -0.10529 | 122.6532 | -0.02739 | 0.015078 | 0.010062 | -0.0061588 | 0.0016535 | -0.010057 | -0.0038772 | -0.005371 | 0.021463 | 0.04178 | -0.011647 | 0.014043 | 0.020546 | -0.0053343 | 3.9963 | 3.9688 | 3.9001 | 3.9322 | 4.0466 | 3.923 | 3.9276 | 0.027466 | 0.027466 | -0.059509 | -0.009155 | 0.091553 | 0.032043 | 0.073242 | 4.0054 | -118.6844 | -118.721 | 4.1519 | 4.0329 | 4.0283 | 0.027466 | 0.022889 | 0.045777 | -122.6257 | -122.6624 | 0.19684 | 0.17853 | 0.13733 | 0.13275 | 0.091552 | 0.14648 | 0.032044 | 0.15106 | 0.050354 | 0.068665 | 0.086975 | 4.0741 | 0.13275 | -118.7531 | -122.7127 | 4.0375 | 0.096131 | 4.1016 | 0.13275
5437.7969 | 122.7036 | -0.1236 | 122.6624 | -0.02739 | 0.013582 | 0.0092072 | -0.0085086 | -0.0039007 | -0.008562 | -0.0036636 | -0.0084228 | 0.022103 | 0.042849 | -0.015065 | 0.014257 | 0.021614 | -0.0025571 | 4.0146 | 4.0512 | 3.9551 | 3.9185 | 4.0329 | 3.9185 | 3.9459 | -0.059509 | 0.041199 | -0.064087 | -0.064087 | 0.050354 | 0.032043 | 0.041199 | 4.0787 | -118.6111 | -118.7439 | 4.1565 | 4.0695 | 4.0421 | -0.009155 | -0.036621 | 0.059509 | -122.6212 | -122.7264 | 0.17395 | 0.16479 | 0.15564 | 0.10529 | 0.09613 | 0.07782 | -0.036621 | 0.11444 | 0 | 0.09613 | 0.10529 | 4.1748 | 0.16479 | -118.7073 | -122.7264 | 4.0421 | 0.059509 | 4.1382 | 0.064087
5439.5 | 122.699 | -0.11444 | 122.6532 | -0.0045011 | 0.010591 | 0.010275 | -0.0067996 | 0.0018671 | -0.011553 | -0.0025956 | -0.0023192 | 0.022317 | 0.042849 | -0.012288 | 0.01148 | 0.022896 | -0.0051205 | 3.8452 | 3.8956 | 3.8223 | 3.7765 | 3.8727 | 3.7445 | 3.7857 | -0.086975 | 0.041199 | -0.064087 | -0.059509 | 0.018311 | -0.022888 | 0.032043 | 3.9368 | -118.7576 | -118.8766 | 3.9871 | 3.9001 | 3.8589 | -0.036621 | -0.07782 | 0.050354 | -122.612 | -122.7127 | 0.13275 | 0.14648 | 0.091553 | 0.09613 | 0.041199 | 0.050354 | -0.045777 | 0.082398 | 0.004578 | 0.073242 | 0.10529 | 4.01 | 0.15564 | -118.8309 | -122.7173 | 3.891 | 0.054932 | 3.9597 | 0.027466
5441.2344 | 122.6715 | -0.09613 | 122.644 | -0.01976 | 0.016146 | 0.010062 | -0.0063724 | 0.0022943 | -0.008562 | -0.0028092 | -0.0084228 | 0.023172 | 0.039644 | -0.016133 | 0.012975 | 0.023537 | -0.0036253 | 3.8864 | 3.9276 | 3.8315 | 3.7765 | 3.8864 | 3.7445 | 3.7949 | -0.09613 | 0.059509 | -0.064087 | -0.086975 | 0 | -0.054932 | 0.022888 | 3.9276 | -118.7164 | -118.8675 | 3.9825 | 3.891 | 3.8406 | -0.036621 | -0.086975 | 0.032043 | -122.5845 | -122.731 | 0.09613 | 0.11902 | 0.041198 | 0.086975 | 0.009155 | 0.054932 | -0.054932 | 0.064087 | -0.022888 | 0.09613 | 0.1236 | 4.0237 | 0.15564 | -118.8126 | -122.7081 | 3.8727 | 0.009155 | 3.9825 | 0
5442.9531 | 122.7997 | -0.059509 | 122.6395 | -0.01976 | 0.014864 | 0.01113 | -0.0089358 | 0.00079894 | -0.008562 | -0.0055862 | -0.0084228 | 0.018045 | 0.041567 | -0.019337 | 0.012548 | 0.025032 | -0.0034117 | 3.9001 | 3.804 | 3.7949 | 3.8635 | 4.0054 | 3.8452 | 3.8818 | 0.1236 | -0.018311 | -0.027466 | 0.068665 | 0.16937 | 0.14191 | 0.12817 | 3.8544 | -118.8354 | -118.7759 | 4.0649 | 3.9413 | 3.9047 | 0.086975 | 0.050354 | 0.032043 | -122.6578 | -122.5708 | 0.22888 | 0.18768 | 0.20142 | 0.15564 | 0.16937 | 0.21057 | 0.068664 | 0.19684 | 0.096131 | 0.009155 | 0.009155 | 3.8635 | 0.041198 | -118.8446 | -122.6669 | 3.923 | 0.12817 | 3.9597 | 0.1831
5444.6875 | 122.7036 | -0.12817 | 122.6944 | -0.012131 | 0.011232 | 0.0083526 | -0.0097904 | 0.0025079 | -0.010698 | -0.002382 | -0.0084228 | 0.023172 | 0.043062 | -0.011433 | 0.011694 | 0.023537 | 0.00064735 | 3.9597 | 4.01 | 3.9139 | 3.9093 | 4.0237 | 3.923 | 3.9413 | -0.059509 | 0.036621 | -0.082397 | -0.086975 | 0.032043 | 0.018311 | 0.032043 | 4.0421 | -118.6844 | -118.7851 | 4.1519 | 4.0695 | 4.0512 | 0.027466 | 0.009156 | 0.045777 | -122.6578 | -122.7814 | 0.16022 | 0.16022 | 0.14649 | 0.11444 | 0.10071 | 0.10986 | -0.004577 | 0.11444 | -0.004578 | 0.096131 | 0.11902 | 4.1382 | 0.1648 | -118.7805 | -122.7768 | 4.0375 | 0.041199 | 4.0878 | 0.068665
5446.3906 | 122.6807 | -0.11902 | 122.6807 | -0.0045011 | 0.015718 | 0.010703 | -0.0053042 | 0.0029351 | -0.01198 | -0.0019546 | -0.005371 | 0.022317 | 0.042849 | -0.016133 | 0.011053 | 0.023964 | -0.0046933 | 3.8589 | 3.8818 | 3.7994 | 3.7491 | 3.8406 | 3.7354 | 3.772 | -0.09613 | 0.050354 | -0.068665 | -0.059509 | 0.018311 | -0.018311 | 0.041199 | 3.9185 | -118.7988 | -118.9316 | 3.9597 | 3.891 | 3.8544 | -0.027465 | -0.064086 | 0.050354 | -122.6303 | -122.7402 | 0.13733 | 0.16022 | 0.10071 | 0.10986 | 0.050354 | 0.041199 | -0.050354 | 0.086976 | 0.009156 | 0.082398 | 0.11902 | 4.0009 | 0.16937 | -118.8812 | -122.7493 | 3.8681 | 0.05951 | 3.978 | 0.022889
5448.125 | 122.7081 | -0.10529 | 122.644 | -0.0045011 | 0.016359 | 0.010062 | -0.0061588 | 0.0025079 | -0.011339 | -0.0066544 | -0.011475 | 0.021249 | 0.041353 | -0.0073743 | 0.012762 | 0.022469 | -0.0014891 | 3.8177 | 3.8635 | 3.772 | 3.7399 | 3.8544 | 3.7262 | 3.772 | -0.036621 | 0.027466 | -0.091553 | -0.041199 | 0.041199 | 0.009155 | 0.036621 | 3.8773 | -118.7805 | -118.9041 | 3.9597 | 3.8773 | 3.8315 | 0 | -0.045777 | 0.013733 | -122.6166 | -122.6852 | 0.14649 | 0.14191 | 0.11444 | 0.12817 | 0.10071 | 0.082397 | -0.032044 | 0.13275 | 0.050354 | 0.091552 | 0.11902 | 3.9688 | 0.13275 | -118.8721 | -122.7356 | 3.8452 | 0.064087 | 3.923 | 0.068665
5449.8438 | 122.7448 | -0.10529 | 122.6715 | -0.01976 | 0.012514 | 0.008139 | -0.006586 | 0.0018671 | -0.011125 | -0.0055862 | -0.0084228 | 0.021676 | 0.041994 | -0.018269 | 0.014043 | 0.023323 | -0.0046933 | 3.9505 | 3.923 | 3.8635 | 3.8727 | 3.9871 | 3.8681 | 3.8818 | 0.036621 | 0.032043 | -0.045776 | -0.004578 | 0.10071 | 0.041199 | 0.073242 | 3.9688 | -118.7485 | -118.7988 | 4.0924 | 3.9871 | 3.9734 | 0.018311 | 0.004578 | 0.05951 | -122.6395 | -122.6761 | 0.20599 | 0.17853 | 0.14649 | 0.11902 | 0.086975 | 0.1236 | 0.009156 | 0.14648 | 0.041198 | 0.05951 | 0.077819 | 4.0283 | 0.13733 | -118.808 | -122.7173 | 3.978 | 0.10071 | 4.0558 | 0.14191
5451.5625 | 122.8271 | -0.07782 | 122.644 | -0.01976 | 0.013155 | 0.0072846 | -0.010004 | 0.00015814 | -0.0098438 | -0.0032364 | -0.0084228 | 0.018045 | 0.040285 | -0.01656 | 0.0095575 | 0.023323 | -0.0046933 | 3.891 | 3.8498 | 3.8177 | 3.8635 | 4.0054 | 3.8773 | 3.9413 | 0.054932 | -0.009155 | -0.054932 | 0.032043 | 0.16479 | 0.15564 | 0.13275 | 3.8956 | -118.7943 | -118.7805 | 4.0833 | 4.0192 | 3.9551 | 0.1236 | 0.059509 | 0.022888 | -122.6532 | -122.612 | 0.24261 | 0.21057 | 0.23346 | 0.18768 | 0.21057 | 0.18768 | 0.045776 | 0.21973 | 0.086975 | 0.032043 | 0.045777 | 3.9276 | 0.068665 | -118.8263 | -122.699 | 3.9413 | 0.10986 | 3.9688 | 0.13275
5453.2969 | 122.7081 | -0.10529 | 122.699 | -0.02739 | 0.015291 | 0.0094208 | -0.0074404 | 0.0018671 | -0.0083484 | -0.0049454 | -0.0023192 | 0.021676 | 0.040499 | -0.012288 | 0.015112 | 0.024605 | -0.0023435 | 3.8956 | 3.9093 | 3.8132 | 3.8132 | 3.923 | 3.7903 | 3.8177 | -0.018311 | 0.022888 | -0.064087 | -0.054932 | 0.032043 | 0 | 0.041199 | 3.9185 | -118.7897 | -118.8858 | 4.0283 | 3.923 | 3.8956 | 0.004578 | -0.022888 | 0.041199 | -122.6761 | -122.7539 | 0.13733 | 0.14649 | 0.10529 | 0.10529 | 0.064087 | 0.10986 | 0 | 0.09613 | 0.009155 | 0.096131 | 0.086975 | 4.0146 | 0.12817 | -118.8858 | -122.7631 | 3.9185 | 0.050354 | 4.0009 | 0.086975
5455.0312 | 122.8088 | -0.068665 | 122.6395 | -0.012131 | 0.009096 | 0.0085662 | -0.0091494 | 0.00015814 | -0.010271 | -0.0053726 | -0.005371 | 0.018258 | 0.043062 | -0.019551 | 0.010412 | 0.023537 | -0.0034117 | 3.8589 | 3.8315 | 3.7994 | 3.8223 | 3.9551 | 3.8406 | 3.8864 | 0.032043 | 0.009155 | -0.036621 | 0.004578 | 0.13733 | 0.11444 | 0.1236 | 3.8681 | -118.808 | -118.8171 | 4.0237 | 3.9551 | 3.9093 | 0.086976 | 0.041199 | 0.032044 | -122.6303 | -122.6349 | 0.20599 | 0.19226 | 0.18311 | 0.16022 | 0.15106 | 0.15564 | 0.022889 | 0.17395 | 0.041199 | 0.032044 | 0.045776 | 3.9001 | 0.07782 | -118.84 | -122.6761 | 3.891 | 0.073243 | 3.9276 | 0.10071
5456.7656 | 122.8088 | -0.07782 | 122.6715 | -0.012131 | 0.011232 | 0.0096344 | -0.009363 | 0.00079894 | -0.011553 | -0.0021682 | -0.011475 | 0.018686 | 0.038576 | -0.016987 | 0.010839 | 0.022896 | -0.0038389 | 3.8727 | 3.8315 | 3.7949 | 3.8361 | 3.9597 | 3.8498 | 3.8864 | 0.059509 | 0.004578 | -0.050354 | 0.004578 | 0.13275 | 0.11902 | 0.12817 | 3.8727 | -118.84 | -118.8354 | 4.0375 | 3.9642 | 3.9276 | 0.091553 | 0.054931 | 0.027466 | -122.6669 | -122.6669 | 0.21057 | 0.20599 | 0.19684 | 0.17853 | 0.16937 | 0.16479 | 0.041199 | 0.18311 | 0.054932 | 0.036621 | 0.054932 | 3.9093 | 0.082398 | -118.8766 | -122.7219 | 3.9139 | 0.082398 | 3.9505 | 0.13733
5458.4688 | 122.7448 | -0.091553 | 122.6669 | -0.012131 | 0.013582 | 0.0094208 | -0.0063724 | 0.0012261 | -0.011339 | -0.0008866 | 0.00073235 | 0.023385 | 0.04114 | -0.020619 | 0.012334 | 0.022255 | -0.0066159 | 3.9001 | 3.8818 | 3.8361 | 3.8406 | 3.9597 | 3.8361 | 3.8544 | 0.032043 | 0.027466 | -0.054932 | -0.004578 | 0.07782 | 0.041199 | 0.09613 | 3.9276 | -118.7851 | -118.8263 | 4.0512 | 3.9459 | 3.9276 | 0.01831 | 0 | 0.036621 | -122.6395 | -122.6715 | 0.16937 | 0.18768 | 0.13275 | 0.15106 | 0.096131 | 0.1236 | 0.004577 | 0.13275 | 0.050354 | 0.045776 | 0.082398 | 3.9734 | 0.11902 | -118.8309 | -122.7219 | 3.9322 | 0.086975 | 3.9917 | 0.1236
5460.1719 | 122.6898 | -0.10986 | 122.6624 | -0.012131 | 0.01465 | 0.0094208 | -0.007654 | 0.0027215 | -0.0077074 | -0.0047318 | -0.0023192 | 0.019113 | 0.042635 | -0.01891 | 0.014684 | 0.022896 | -0.0051205 | 3.8315 | 3.8773 | 3.7674 | 3.7262 | 3.8406 | 3.7125 | 3.7537 | -0.064087 | 0.050354 | -0.059509 | -0.068665 | 0.013733 | -0.036621 | 0.018311 | 3.8773 | -118.7851 | -118.9362 | 3.9505 | 3.8635 | 3.8223 | -0.013733 | -0.054932 | 0.050354 | -122.612 | -122.731 | 0.1236 | 0.12817 | 0.073242 | 0.07782 | 0.022888 | 0.073242 | -0.041199 | 0.073242 | -0.009156 | 0.10986 | 0.10986 | 3.9871 | 0.16022 | -118.895 | -122.7219 | 3.8361 | 0.041198 | 3.9413 | 0.045776
5461.8906 | 122.7814 | -0.050354 | 122.6212 | -0.012131 | 0.014223 | 0.0094208 | -0.0097904 | -0.00069646 | -0.010271 | -0.0036636 | -0.0084228 | 0.01954 | 0.04114 | -0.012288 | 0.011907 | 0.020546 | -0.0034117 | 3.8315 | 3.7399 | 3.7399 | 3.7949 | 3.9505 | 3.7811 | 3.8315 | 0.10071 | 0 | -0.022888 | 0.059509 | 0.14191 | 0.10071 | 0.10071 | 3.7903 | -118.8812 | -118.8263 | 4.0009 | 3.8818 | 3.8315 | 0.091553 | 0.041199 | 0.027466 | -122.6212 | -122.5616 | 0.19226 | 0.15106 | 0.15106 | 0.1236 | 0.1236 | 0.21057 | 0.054932 | 0.16479 | 0.082397 | 0 | 0.022888 | 3.7903 | 0.050354 | -118.8812 | -122.644 | 3.8452 | 0.10986 | 3.8818 | 0.15106
5463.6094 | 122.8088 | -0.073242 | 122.6532 | -0.012131 | 0.010164 | 0.0074982 | -0.010431 | 0.0016535 | -0.00963 | -0.006868 | -0.0084228 | 0.018472 | 0.041994 | -0.020833 | 0.011053 | 0.024605 | -0.0042661 | 3.9322 | 3.8635 | 3.8498 | 3.9322 | 4.0558 | 3.9368 | 3.9551 | 0.10986 | 0.013733 | -0.032043 | 0.041199 | 0.1831 | 0.14191 | 0.13275 | 3.923 | -118.7897 | -118.721 | 4.129 | 4.0283 | 4.01 | 0.10529 | 0.086976 | 0.041199 | -122.6395 | -122.612 | 0.25635 | 0.20599 | 0.21515 | 0.16479 | 0.17395 | 0.20599 | 0.082398 | 0.21515 | 0.073242 | 0.013733 | 0.045776 | 3.9368 | 0.086975 | -118.8034 | -122.6852 | 4.0054 | 0.11444 | 4.0054 | 0.18311
5465.3281 | 122.8455 | -0.064087 | 122.6532 | -0.012131 | 0.0078144 | 0.008139 | -0.0091494 | -0.0034735 | -0.010698 | -0.0032364 | -0.0084228 | 0.018258 | 0.039858 | -0.015919 | 0.0097711 | 0.023323 | -0.0025571 | 3.9001 | 3.8361 | 3.8177 | 3.9139 | 4.0466 | 3.923 | 3.9551 | 0.14648 | -0.018311 | -0.004578 | 0.064087 | 0.20142 | 0.15106 | 0.12817 | 3.8818 | -118.8171 | -118.7393 | 4.1107 | 4.0192 | 3.9871 | 0.13733 | 0.10529 | 0.059509 | -122.6715 | -122.5891 | 0.2655 | 0.19226 | 0.21515 | 0.13275 | 0.15564 | 0.22888 | 0.09613 | 0.20599 | 0.068665 | 0.018311 | -0.013733 | 3.9001 | 0.045776 | -118.8354 | -122.6578 | 3.978 | 0.12817 | 3.9642 | 0.21057
5467.0469 | 122.7676 | -0.091553 | 122.6578 | -0.012131 | 0.012941 | 0.00878 | -0.0091494 | 0.0022943 | -0.012194 | -0.0062272 | -0.0084228 | 0.020181 | 0.040712 | -0.012929 | 0.012762 | 0.021401 | -0.0017027 | 3.9093 | 3.8818 | 3.8132 | 3.8177 | 3.9368 | 3.8086 | 3.8315 | 0.022888 | 0.032043 | -0.041199 | 0 | 0.10071 | 0.059509 | 0.07782 | 3.9047 | -118.7759 | -118.84 | 4.0283 | 3.923 | 3.9001 | 0.018311 | -0.004577 | 0.050354 | -122.6257 | -122.6578 | 0.19226 | 0.16937 | 0.15106 | 0.11902 | 0.10071 | 0.1236 | 0.004578 | 0.14191 | 0.041199 | 0.068665 | 0.073242 | 3.9734 | 0.1236 | -118.8446 | -122.699 | 3.9093 | 0.091553 | 4.0009 | 0.11444
5468.7656 | 122.7722 | -0.086975 | 122.6715 | -0.02739 | 0.013155 | 0.010489 | -0.0095766 | -0.00091006 | -0.010057 | -0.0030228 | -0.005371 | 0.020181 | 0.043917 | -0.019978 | 0.011907 | 0.02311 | -0.0042661 | 3.804 | 3.7445 | 3.7125 | 3.7628 | 3.891 | 3.7399 | 3.7903 | 0.059509 | 0.013733 | -0.032043 | 0.009155 | 0.11444 | 0.07782 | 0.10529 | 3.7994 | -118.927 | -118.9087 | 3.978 | 3.8773 | 3.8269 | 0.07782 | 0.027466 | 0.054932 | -122.6578 | -122.6624 | 0.20142 | 0.19226 | 0.16479 | 0.13733 | 0.10986 | 0.17853 | 0.050354 | 0.14648 | 0.041198 | 0.032044 | 0.045776 | 3.8315 | 0.10071 | -118.959 | -122.7036 | 3.8498 | 0.09613 | 3.891 | 0.14648
5470.4688 | 122.8043 | -0.082397 | 122.6578 | -0.01976 | 0.0099506 | 0.0089936 | -0.011499 | 0.00015814 | -0.0083484 | -0.0036636 | -0.005371 | 0.020395 | 0.041567 | -0.012074 | 0.0095575 | 0.024819 | -0.0049069 | 3.9185 | 3.8315 | 3.8269 | 3.9001 | 4.0192 | 3.9185 | 3.9322 | 0.086975 | -0.013733 | -0.022888 | 0.022888 | 0.14648 | 0.12817 | 0.10986 | 3.9093 | -118.8263 | -118.7576 | 4.1016 | 4.0146 | 4.0009 | 0.10529 | 0.091553 | 0.059509 | -122.6715 | -122.6349 | 0.22888 | 0.19226 | 0.21057 | 0.13275 | 0.15106 | 0.19226 | 0.073242 | 0.16937 | 0.045776 | 0.004578 | 0.009155 | 3.9139 | 0.068664 | -118.8309 | -122.6807 | 3.9825 | 0.10528 | 4.0009 | 0.16937
5472.1719 | 122.7219 | -0.10529 | 122.6807 | -0.01976 | 0.011446 | 0.00878 | -0.0072268 | 0.0031487 | -0.011553 | -0.0043046 | -0.005371 | 0.022744 | 0.04114 | -0.01186 | 0.012334 | 0.02076 | -0.0036253 | 3.8635 | 3.9185 | 3.8452 | 3.7903 | 3.8864 | 3.7903 | 3.8315 | -0.073242 | 0.041199 | -0.064087 | -0.068665 | 0.041199 | 0.009155 | 0.027466 | 3.9505 | -118.7622 | -118.8904 | 3.9917 | 3.9368 | 3.8956 | -0.013733 | -0.054932 | 0.041199 | -122.6395 | -122.7493 | 0.14649 | 0.13275 | 0.11444 | 0.091553 | 0.073242 | 0.041199 | -0.054932 | 0.10529 | -0.004578 | 0.073242 | 0.10529 | 4.0237 | 0.14649 | -118.8354 | -122.7448 | 3.8956 | 0.036621 | 3.9688 | 0.032044
5473.9219 | 122.7036 | -0.09613 | 122.6807 | -0.0045011 | 0.0095234 | 0.0083526 | -0.009363 | -0.0026191 | -0.012834 | -0.0040908 | -0.011475 | 0.020395 | 0.039644 | -0.013356 | 0.0084893 | 0.025673 | -0.0066159 | 3.8406 | 3.8818 | 3.8086 | 3.7674 | 3.9047 | 3.7994 | 3.8223 | -0.050354 | 0.027466 | -0.054932 | -0.082397 | 0.045776 | 0.009155 | 0.032043 | 3.9047 | -118.7988 | -118.9133 | 4.0009 | 3.9185 | 3.8956 | 0.013733 | -0.009156 | 0.041198 | -122.6532 | -122.7631 | 0.14191 | 0.12817 | 0.10528 | 0.086975 | 0.064087 | 0.09613 | -0.041199 | 0.10071 | -0.027465 | 0.073242 | 0.082398 | 3.978 | 0.1236 | -118.8721 | -122.7356 | 3.8635 | 0.013733 | 3.9368 | 0.045776
5475.625 | 122.8317 | -0.041199 | 122.6303 | -0.012131 | 0.015291 | 0.010275 | -0.008295 | 0.0020807 | -0.010485 | -0.0038772 | -0.005371 | 0.020608 | 0.039431 | -0.019337 | 0.014471 | 0.023537 | -0.0046933 | 3.8132 | 3.7125 | 3.7125 | 3.7491 | 3.8589 | 3.717 | 3.772 | 0.09613 | 0 | -0.036621 | 0.07782 | 0.16022 | 0.1236 | 0.13733 | 3.7537 | -118.9178 | -118.8812 | 3.9001 | 3.8132 | 3.7582 | 0.05951 | 0.004578 | 0.004578 | -122.6303 | -122.5525 | 0.20142 | 0.17853 | 0.16479 | 0.17395 | 0.16022 | 0.14648 | 0.036621 | 0.19684 | 0.11444 | 0 | 0.036621 | 3.7537 | 0.041199 | -118.9178 | -122.6669 | 3.7903 | 0.11902 | 3.8544 | 0.13733
5477.375 | 122.7814 | -0.07782 | 122.644 | -0.012131 | 0.011019 | 0.010489 | -0.009363 | 0.00079894 | -0.010485 | -0.0057998 | -0.0084228 | 0.01954 | 0.039217 | -0.019978 | 0.011266 | 0.025032 | -0.0031979 | 3.7628 | 3.6987 | 3.717 | 3.7399 | 3.8727 | 3.717 | 3.7628 | 0.054932 | -0.013733 | -0.036621 | 0.009155 | 0.11902 | 0.086975 | 0.09613 | 3.7949 | -118.9453 | -118.9041 | 3.9505 | 3.8406 | 3.7949 | 0.045776 | 0 | 0.041199 | -122.6578 | -122.6349 | 0.19684 | 0.17395 | 0.16479 | 0.13275 | 0.1236 | 0.15564 | 0.022888 | 0.15564 | 0.045776 | -0.018311 | 0.022888 | 3.7765 | 0.064087 | -118.927 | -122.6807 | 3.8177 | 0.086975 | 3.8406 | 0.13275
5479.1406 | 122.8271 | -0.07782 | 122.6395 | -0.0045011 | 0.009737 | 0.010062 | -0.010858 | -0.0019781 | -0.0074938 | -0.0015274 | -0.0084228 | 0.019754 | 0.037935 | -0.018055 | 0.010839 | 0.021187 | -0.0021299 | 3.8452 | 3.7765 | 3.7582 | 3.8406 | 3.9734 | 3.8544 | 3.8864 | 0.12817 | 0 | -0.027466 | 0.059509 | 0.20142 | 0.16479 | 0.15106 | 3.8361 | -118.8629 | -118.7988 | 4.0512 | 3.9642 | 3.9322 | 0.12817 | 0.09613 | 0.050354 | -122.6395 | -122.58 | 0.27924 | 0.22888 | 0.24261 | 0.17853 | 0.19226 | 0.21515 | 0.082397 | 0.22888 | 0.086975 | 0.01831 | 0.027466 | 3.8544 | 0.07782 | -118.8812 | -122.6669 | 3.9185 | 0.13733 | 3.923 | 0.20599
5480.8594 | 122.7036 | -0.10529 | 122.6807 | -0.02739 | 0.014009 | 0.0092072 | -0.005945 | -0.0026191 | -0.00963 | -0.002382 | -0.0023192 | 0.021249 | 0.040712 | -0.016987 | 0.012334 | 0.020333 | -0.0036253 | 3.8132 | 3.7994 | 3.7308 | 3.7033 | 3.8177 | 3.685 | 3.717 | -0.013733 | 0.036621 | -0.050354 | -0.036621 | 0.032043 | -0.009155 | 0.032043 | 3.8361 | -118.8812 | -118.9774 | 3.923 | 3.8223 | 3.7903 | -0.013733 | -0.045776 | 0.054932 | -122.644 | -122.7173 | 0.13733 | 0.13733 | 0.096131 | 0.082397 | 0.041199 | 0.086975 | -0.027466 | 0.082397 | 0.013733 | 0.068664 | 0.086975 | 3.9047 | 0.14191 | -118.9499 | -122.731 | 3.8086 | 0.068665 | 3.9185 | 0.091553
5482.5625 | 122.8226 | -0.050354 | 122.6624 | -0.01976 | 0.01465 | 0.007071 | -0.0087222 | 0.0054987 | -0.010271 | -0.0011002 | -0.011475 | 0.019967 | 0.042635 | -0.016987 | 0.011694 | 0.02311 | -0.00084805 | 3.7582 | 3.653 | 3.6621 | 3.7262 | 3.8406 | 3.6758 | 3.7491 | 0.10071 | -0.013733 | -0.009155 | 0.068665 | 0.17395 | 0.13275 | 0.13733 | 3.7125 | -119.0094 | -118.9362 | 3.891 | 3.7994 | 3.7262 | 0.086975 | 0.013733 | 0.041199 | -122.6761 | -122.5937 | 0.2243 | 0.18768 | 0.18311 | 0.14648 | 0.14191 | 0.17853 | 0.064087 | 0.1831 | 0.07782 | -0.009155 | -0.004578 | 3.7033 | 0.036621 | -119.0002 | -122.6715 | 3.7765 | 0.11902 | 3.8086 | 0.15106
5484.2656 | 122.8546 | -0.07782 | 122.6486 | -0.01976 | 0.011019 | 0.0072846 | -0.0097904 | 0.0018671 | -0.0087756 | -0.0015274 | -0.0084228 | 0.019326 | 0.04178 | -0.022114 | 0.011907 | 0.024178 | -0.0025571 | 3.8589 | 3.7674 | 3.7765 | 3.8452 | 3.9963 | 3.8315 | 3.8818 | 0.14191 | 0.004578 | -0.032043 | 0.07782 | 0.19226 | 0.16479 | 0.14648 | 3.8544 | -118.8812 | -118.8034 | 4.0741 | 3.9597 | 3.9093 | 0.10529 | 0.054932 | 0.045777 | -122.644 | -122.5708 | 0.27008 | 0.2243 | 0.24261 | 0.17853 | 0.19684 | 0.21973 | 0.068665 | 0.2243 | 0.10986 | -0.009155 | 0.036621 | 3.8452 | 0.082398 | -118.8721 | -122.6807 | 3.923 | 0.15564 | 3.9368 | 0.21973
5485.9688 | 122.7539 | -0.10986 | 122.699 | -0.012131 | 0.011446 | 0.0074982 | -0.0078676 | 0.0018671 | -0.010485 | -0.0011002 | -0.0084228 | 0.021249 | 0.040712 | -0.016347 | 0.010198 | 0.024178 | -0.0012753 | 3.8223 | 3.8635 | 3.7674 | 3.7491 | 3.8544 | 3.7628 | 3.7765 | -0.027466 | 0.050354 | -0.068665 | -0.036621 | 0.064087 | 0.032043 | 0.054932 | 3.8773 | -118.8355 | -118.9499 | 3.9642 | 3.8864 | 3.8727 | 0.009155 | -0.004578 | 0.041198 | -122.6486 | -122.7356 | 0.17395 | 0.16479 | 0.14191 | 0.1236 | 0.10071 | 0.086975 | -0.018311 | 0.13275 | 0.032044 | 0.09613 | 0.11902 | 3.9734 | 0.16022 | -118.9316 | -122.7676 | 3.8589 | 0.073242 | 3.9322 | 0.082397
5487.6875 | 122.7356 | -0.082397 | 122.6761 | -0.01976 | 0.015078 | 0.008139 | -0.0070132 | 0.00058534 | -0.0098438 | -0.0075088 | -0.0084228 | 0.021463 | 0.04178 | -0.0090833 | 0.014257 | 0.023751 | -0.0021299 | 3.8177 | 3.7994 | 3.717 | 3.7537 | 3.8727 | 3.7399 | 3.7582 | 0.041199 | 0.022888 | -0.059509 | -0.004578 | 0.082397 | 0.045776 | 0.07782 | 3.7994 | -118.8766 | -118.9224 | 3.9551 | 3.8406 | 3.8223 | 0.041199 | 0.022888 | 0.022888 | -122.6532 | -122.6807 | 0.16479 | 0.16022 | 0.12817 | 0.13733 | 0.10528 | 0.15564 | 0.036621 | 0.14191 | 0.054931 | 0.082397 | 0.082397 | 3.8818 | 0.10528 | -118.959 | -122.7356 | 3.8361 | 0.077819 | 3.9001 | 0.1236
5489.4062 | 122.8363 | -0.068665 | 122.6303 | -0.01976 | 0.009737 | 0.0092072 | -0.010004 | -0.0021919 | -0.00963 | -0.0038772 | -0.005371 | 0.018686 | 0.04178 | -0.018055 | 0.011266 | 0.024391 | -0.0027707 | 3.7491 | 3.7537 | 3.6896 | 3.7399 | 3.8589 | 3.7582 | 3.7903 | 0.050354 | 0.009155 | -0.054932 | 0.027466 | 0.16479 | 0.13275 | 0.1236 | 3.7582 | -118.8766 | -118.8904 | 3.9276 | 3.8589 | 3.8269 | 0.10071 | 0.068665 | 0.013733 | -122.6212 | -122.6028 | 0.23346 | 0.19226 | 0.20142 | 0.17853 | 0.18768 | 0.16937 | 0.050354 | 0.21973 | 0.082398 | 0.064087 | 0.064087 | 3.8223 | 0.07782 | -118.9407 | -122.6852 | 3.8086 | 0.096131 | 3.8177 | 0.11902
5491.125 | 122.7448 | -0.10529 | 122.6807 | -0.012131 | 0.013155 | 0.0072846 | -0.0080814 | -0.00026906 | -0.0089892 | -0.0013138 | -0.011475 | 0.021676 | 0.041567 | -0.015492 | 0.01383 | 0.02311 | -0.0053343 | 3.8177 | 3.804 | 3.7399 | 3.7399 | 3.8498 | 3.7216 | 3.7537 | 0.022888 | 0.018311 | -0.036621 | -0.009155 | 0.091553 | 0.050354 | 0.07782 | 3.8452 | -118.8766 | -118.9407 | 3.9551 | 3.8589 | 3.8269 | 0.013733 | -0.01831 | 0.068665 | -122.6624 | -122.6898 | 0.19684 | 0.18311 | 0.15564 | 0.11444 | 0.086975 | 0.10986 | 0 | 0.12817 | 0.027466 | 0.064087 | 0.054932 | 3.9093 | 0.1236 | -118.9407 | -122.7173 | 3.8452 | 0.096131 | 3.923 | 0.12817
5492.8281 | 122.8043 | -0.07782 | 122.6578 | -0.0045011 | 0.016146 | 0.010489 | -0.0072268 | 0.0040033 | -0.0094164 | -0.0057998 | -0.0084228 | 0.021463 | 0.040499 | -0.0043835 | 0.012975 | 0.023964 | -0.0064023 | 3.6804 | 3.6987 | 3.6346 | 3.598 | 3.7216 | 3.5751 | 3.6072 | -0.009155 | 0.018311 | -0.054932 | 0.027466 | 0.091553 | 0.059509 | 0.10071 | 3.7125 | -118.959 | -119.0598 | 3.7994 | 3.685 | 3.653 | -0.027466 | -0.05951 | 0.022888 | -122.6395 | -122.6303 | 0.16937 | 0.17853 | 0.13733 | 0.15564 | 0.11444 | 0.086975 | -0.036622 | 0.14649 | 0.082398 | 0.064086 | 0.073243 | 3.7765 | 0.096131 | -119.0231 | -122.7127 | 3.6758 | 0.10529 | 3.7582 | 0.068665
5494.5312 | 122.8317 | -0.064087 | 122.6761 | -0.0045011 | 0.011232 | 0.0085662 | -0.010645 | 0.00037174 | -0.010698 | -0.0066544 | -0.005371 | 0.018686 | 0.039431 | -0.019124 | 0.0095575 | 0.025032 | -0.0034117 | 3.8132 | 3.7445 | 3.7308 | 3.8086 | 3.9551 | 3.8315 | 3.8544 | 0.11902 | 0 | -0.032043 | 0.054932 | 0.18768 | 0.15564 | 0.14191 | 3.7949 | -118.9316 | -118.8675 | 4.0192 | 3.9185 | 3.8956 | 0.1236 | 0.10071 | 0.032044 | -122.6761 | -122.6212 | 0.25177 | 0.20599 | 0.21973 | 0.17395 | 0.18768 | 0.2243 | 0.07782 | 0.21973 | 0.086975 | 0.013733 | 0.032043 | 3.8086 | 0.064087 | -118.9453 | -122.7081 | 3.8727 | 0.11902 | 3.8773 | 0.18311
5496.25 | 122.7585 | -0.10529 | 122.6761 | -0.01976 | 0.012087 | 0.0077118 | -0.0072268 | -0.0021919 | -0.00963 | -0.0040908 | -0.005371 | 0.02189 | 0.039644 | -0.013997 | 0.012762 | 0.021401 | -0.0053343 | 3.7994 | 3.8086 | 3.7399 | 3.7125 | 3.8177 | 3.7354 | 3.7582 | -0.059509 | 0.032043 | -0.050354 | -0.045776 | 0.068665 | 0.041199 | 0.059509 | 3.8452 | -118.8675 | -118.9636 | 3.923 | 3.8635 | 3.8406 | 0.018311 | -0.004577 | 0.054932 | -122.644 | -122.7219 | 0.17395 | 0.16479 | 0.14649 | 0.10986 | 0.091553 | 0.07782 | -0.027466 | 0.11902 | 0.004578 | 0.068665 | 0.082397 | 3.9139 | 0.13733 | -118.9362 | -122.7264 | 3.8177 | 0.05951 | 3.9047 | 0.045777
5497.9688 | 122.7768 | -0.073242 | 122.6532 | -0.012131 | 0.011019 | 0.0092072 | -0.010431 | 0.00079894 | -0.010271 | -0.0015274 | -0.011475 | 0.020608 | 0.041567 | -0.022328 | 0.011266 | 0.02311 | -0.0074705 | 3.8269 | 3.7445 | 3.7216 | 3.7857 | 3.923 | 3.8132 | 3.8315 | 0.059509 | 0.013733 | -0.045776 | 0 | 0.1236 | 0.07782 | 0.07782 | 3.7949 | -118.9087 | -118.8675 | 3.9963 | 3.9047 | 3.8864 | 0.10986 | 0.091552 | 0.027466 | -122.6395 | -122.6532 | 0.19684 | 0.15106 | 0.15106 | 0.1236 | 0.1236 | 0.20142 | 0.064087 | 0.16937 | 0.045776 | 0.022888 | 0.059509 | 3.8177 | 0.086975 | -118.9316 | -122.699 | 3.8589 | 0.073242 | 3.9001 | 0.13275
5499.6719 | 122.7585 | -0.10529 | 122.6807 | -0.012131 | 0.013369 | 0.0077118 | -0.0074404 | 0.0018671 | -0.0098438 | -0.0030228 | -0.0084228 | 0.023385 | 0.039217 | -0.016347 | 0.014684 | 0.024391 | -0.0036253 | 3.7903 | 3.7628 | 3.717 | 3.7033 | 3.8177 | 3.7125 | 3.7216 | 0.032043 | 0.032043 | -0.032043 | -0.013733 | 0.091553 | 0.054932 | 0.086975 | 3.8223 | -118.9178 | -118.9774 | 3.923 | 3.8269 | 3.8177 | 0.004578 | -0.004578 | 0.073243 | -122.6486 | -122.6944 | 0.19684 | 0.19226 | 0.16022 | 0.11902 | 0.086975 | 0.10071 | -0.013733 | 0.1236 | 0.01831 | 0.045776 | 0.064086 | 3.8681 | 0.13733 | -118.9636 | -122.7127 | 3.8086 | 0.091553 | 3.8956 | 0.13733
5501.3906 | 122.8409 | -0.050354 | 122.6532 | -0.012131 | 0.010378 | 0.0066436 | -0.011713 | -5.5462e-05 | -0.0081348 | -0.0049454 | -0.011475 | 0.01954 | 0.039644 | -0.022328 | 0.010412 | 0.021828 | -0.0044797 | 3.804 | 3.7125 | 3.7216 | 3.7903 | 3.9642 | 3.8132 | 3.8406 | 0.1236 | -0.004578 | -0.027466 | 0.045776 | 0.18768 | 0.16479 | 0.12817 | 3.772 | -118.9407 | -118.8629 | 4.0146 | 3.891 | 3.8635 | 0.11902 | 0.091552 | 0.022888 | -122.6578 | -122.6074 | 0.23804 | 0.17853 | 0.21515 | 0.15564 | 0.19226 | 0.24261 | 0.068664 | 0.21515 | 0.073242 | -0.009156 | 0.022888 | 3.7628 | 0.045776 | -118.9316 | -122.6807 | 3.8406 | 0.09613 | 3.8544 | 0.17395
5503.1094 | 122.7585 | -0.09613 | 122.6669 | -0.02739 | 0.011019 | 0.010489 | -0.007654 | 0.0031487 | -0.01198 | -0.0040908 | -0.0023192 | 0.021249 | 0.040712 | -0.019124 | 0.011053 | 0.024605 | -0.0017027 | 3.7674 | 3.7399 | 3.6713 | 3.6942 | 3.8086 | 3.6713 | 3.6987 | 0.032043 | 0.022888 | -0.041199 | -0.009155 | 0.09613 | 0.054932 | 0.086975 | 3.7674 | -118.927 | -118.9728 | 3.9047 | 3.7949 | 3.7674 | 0.027465 | 0 | 0.054931 | -122.644 | -122.6761 | 0.19226 | 0.1831 | 0.15106 | 0.12817 | 0.096131 | 0.13733 | 0.022888 | 0.13733 | 0.032044 | 0.068664 | 0.064087 | 3.8361 | 0.11902 | -118.9957 | -122.7081 | 3.7903 | 0.086975 | 3.8635 | 0.12817
5504.8438 | 122.7951 | -0.07782 | 122.6624 | -0.01976 | 0.011446 | 0.0079254 | -0.010645 | -0.0013373 | -0.010698 | -0.0028092 | -0.005371 | 0.019326 | 0.04178 | -0.013569 | 0.012334 | 0.023537 | -0.0057615 | 3.6896 | 3.653 | 3.6438 | 3.6484 | 3.7628 | 3.6484 | 3.685 | 0.022888 | 0.018311 | -0.050354 | -0.004578 | 0.11444 | 0.082397 | 0.086975 | 3.7216 | -119.0094 | -119.014 | 3.8406 | 3.7628 | 3.7262 | 0.041199 | 0.004577 | 0.027466 | -122.644 | -122.6669 | 0.19226 | 0.16479 | 0.16022 | 0.13733 | 0.13275 | 0.11902 | 0.004577 | 0.16479 | 0.045776 | 0.009155 | 0.068665 | 3.7308 | 0.096131 | -119.0186 | -122.7127 | 3.7262 | 0.073242 | 3.7674 | 0.10071
5506.5625 | 122.7127 | -0.13275 | 122.6669 | -0.012131 | 0.010805 | 0.0085662 | -0.010004 | 0.00015814 | -0.010698 | -0.0049454 | -0.0023192 | 0.018899 | 0.040071 | -0.01186 | 0.011266 | 0.023751 | -0.0021299 | 3.717 | 3.7765 | 3.685 | 3.6758 | 3.8086 | 3.6942 | 3.7033 | -0.059509 | 0.045776 | -0.073242 | -0.091553 | 0.036621 | 0 | 0.041199 | 3.8177 | -118.8904 | -118.9911 | 3.9413 | 3.8361 | 3.8269 | 0.01831 | 0.009155 | 0.059509 | -122.6212 | -122.7585 | 0.16937 | 0.17395 | 0.13275 | 0.11444 | 0.073242 | 0.1236 | -0.009156 | 0.10986 | -0.018311 | 0.091552 | 0.11902 | 3.9093 | 0.17853 | -118.9819 | -122.7402 | 3.8086 | 0.041198 | 3.8498 | 0.073242
5508.2812 | 122.7402 | -0.086975 | 122.6898 | -0.01976 | 0.014437 | 0.011557 | -0.0080814 | 0.0012261 | -0.010057 | -0.0021682 | -0.005371 | 0.022317 | 0.04178 | -0.013783 | 0.012548 | 0.02076 | -0.0044797 | 3.7491 | 3.717 | 3.653 | 3.6621 | 3.7857 | 3.653 | 3.6804 | 0.032043 | 0.009155 | -0.045776 | -0.009155 | 0.07782 | 0.041199 | 0.07782 | 3.7399 | -118.9728 | -119.0277 | 3.8727 | 3.7674 | 3.7399 | 0.027466 | 0 | 0.041199 | -122.6807 | -122.699 | 0.16479 | 0.16479 | 0.12817 | 0.1236 | 0.086975 | 0.13275 | 0.009155 | 0.1236 | 0.036621 | 0.064087 | 0.054931 | 3.804 | 0.09613 | -119.0369 | -122.7356 | 3.7491 | 0.07782 | 3.8361 | 0.11902
5510 | 122.7448 | -0.11902 | 122.7036 | -0.012131 | 0.010805 | 0.01113 | -0.007654 | 0.0022943 | -0.010485 | -0.0030228 | -0.0084228 | 0.021676 | 0.043703 | -0.014851 | 0.010198 | 0.023537 | -0.0010617 | 3.7445 | 3.7949 | 3.6896 | 3.653 | 3.7537 | 3.6575 | 3.6942 | -0.059509 | 0.032043 | -0.07782 | -0.059509 | 0.054932 | 0.018311 | 0.054932 | 3.8086 | -118.9087 | -119.0506 | 3.8727 | 3.8132 | 3.7766 | 0.004578 | -0.032043 | 0.041199 | -122.6715 | -122.7631 | 0.17395 | 0.17395 | 0.13733 | 0.13275 | 0.096131 | 0.064087 | -0.036621 | 0.13275 | 0.018311 | 0.10529 | 0.10986 | 3.9139 | 0.15106 | -119.014 | -122.7814 | 3.772 | 0.05951 | 3.8635 | 0.05951
5511.75 | 122.8043 | -0.086975 | 122.6532 | -0.01976 | 0.012728 | 0.008139 | -0.010431 | -0.0032599 | -0.010912 | -0.0049454 | -0.0084228 | 0.01719 | 0.04178 | -0.014851 | 0.010198 | 0.021828 | -0.0068295 | 3.6621 | 3.6438 | 3.6026 | 3.6209 | 3.7491 | 3.6072 | 3.6575 | 0.009155 | 0.004578 | -0.027466 | -0.009155 | 0.10529 | 0.073242 | 0.11902 | 3.6896 | -119.0094 | -119.0323 | 3.8361 | 3.7445 | 3.6942 | 0.054932 | 0.004578 | 0.059509 | -122.6486 | -122.6624 | 0.19226 | 0.20599 | 0.16022 | 0.14649 | 0.10071 | 0.14648 | 0.018311 | 0.13275 | 0.018311 | 0.041199 | 0.032044 | 3.7308 | 0.091553 | -119.0506 | -122.6807 | 3.7079 | 0.07782 | 3.7491 | 0.09613
5513.4844 | 122.8043 | -0.09613 | 122.6944 | -0.012131 | 0.012728 | 0.008139 | -0.010431 | 0.0037897 | -0.010698 | -0.0057998 | -0.011475 | 0.019967 | 0.042421 | -0.025319 | 0.0093439 | 0.023964 | -0.0038389 | 3.6484 | 3.598 | 3.5797 | 3.6072 | 3.7354 | 3.598 | 3.653 | 0.050354 | -0.004578 | -0.045776 | -0.004578 | 0.10529 | 0.086975 | 0.082397 | 3.6758 | -119.0964 | -119.0872 | 3.8315 | 3.7491 | 3.6942 | 0.073242 | 0.01831 | 0.050354 | -122.699 | -122.699 | 0.20142 | 0.17853 | 0.1831 | 0.12817 | 0.13275 | 0.15564 | 0.027466 | 0.15106 | 0.041198 | 0.01831 | 0.041198 | 3.6942 | 0.091552 | -119.1147 | -122.7402 | 3.7033 | 0.091552 | 3.7445 | 0.14648
5515.2031 | 122.7997 | -0.082397 | 122.7219 | -0.012131 | 0.010591 | 0.0085662 | -0.0091494 | -0.0011237 | -0.0094164 | -0.0043046 | -0.0084228 | 0.019754 | 0.039431 | -0.015065 | 0.010412 | 0.025246 | -0.0017027 | 3.6118 | 3.5797 | 3.5797 | 3.6118 | 3.7354 | 3.5934 | 3.653 | 0.036621 | -0.013733 | -0.036621 | 0.013733 | 0.10986 | 0.086975 | 0.10529 | 3.6621 | -119.1422 | -119.1101 | 3.8177 | 3.7354 | 3.6758 | 0.073242 | 0.013733 | 0.045776 | -122.7356 | -122.7081 | 0.19226 | 0.18768 | 0.16937 | 0.14191 | 0.1236 | 0.15564 | 0.032043 | 0.14648 | 0.050354 | 0 | 0.022888 | 3.6621 | 0.068664 | -119.1422 | -122.7585 | 3.6942 | 0.09613 | 3.6942 | 0.11902
5516.9375 | 122.8592 | -0.064087 | 122.6715 | -0.0045011 | 0.0088824 | 0.0074982 | -0.010645 | 0.00058534 | -0.010912 | -0.0028092 | -0.0084228 | 0.019326 | 0.039858 | -0.01421 | 0.010839 | 0.02311 | -0.0044797 | 3.7628 | 3.6896 | 3.6758 | 3.7445 | 3.8681 | 3.7491 | 3.7857 | 0.10529 | -0.004578 | -0.022888 | 0.032043 | 0.17853 | 0.12817 | 0.1236 | 3.7399 | -118.9819 | -118.927 | 3.9322 | 3.8498 | 3.8132 | 0.10986 | 0.073242 | 0.041199 | -122.6761 | -122.6395 | 0.24261 | 0.18768 | 0.19226 | 0.14648 | 0.15106 | 0.19226 | 0.068665 | 0.20142 | 0.054931 | 0.013733 | 0.01831 | 3.7537 | 0.059509 | -118.9957 | -122.6944 | 3.8086 | 0.09613 | 3.8269 | 0.16937
5518.6406 | 122.7036 | -0.11444 | 122.699 | -0.02739 | 0.015505 | 0.008139 | -0.0046634 | 0.00079894 | -0.0083484 | -0.002382 | -0.0023192 | 0.024026 | 0.040499 | -0.018269 | 0.01383 | 0.020333 | -0.0014891 | 3.598 | 3.6346 | 3.5477 | 3.5156 | 3.6072 | 3.4836 | 3.5202 | -0.064087 | 0.045776 | -0.059509 | -0.054932 | 0 | -0.041199 | 0.027466 | 3.6621 | -119.0643 | -119.1834 | 3.7216 | 3.6346 | 3.598 | -0.027465 | -0.064086 | 0.054932 | -122.6532 | -122.7539 | 0.11444 | 0.14191 | 0.073242 | 0.086975 | 0.01831 | 0.05951 | -0.032043 | 0.059509 | 0.004577 | 0.086976 | 0.10528 | 3.7491 | 0.16022 | -119.1513 | -122.7585 | 3.6301 | 0.059509 | 3.7125 | 0.050354
5520.3594 | 122.8088 | -0.073242 | 122.6807 | -0.01976 | 0.0123 | 0.0092072 | -0.011072 | 0.0014397 | -0.013475 | -0.005159 | -0.005371 | 0.019754 | 0.040499 | -0.019337 | 0.010412 | 0.022896 | -0.0036253 | 3.6301 | 3.566 | 3.5614 | 3.5934 | 3.7262 | 3.5889 | 3.6438 | 0.027466 | 0 | -0.041199 | -0.013733 | 0.10529 | 0.082397 | 0.091553 | 3.6346 | -119.1147 | -119.0872 | 3.7994 | 3.717 | 3.6621 | 0.082398 | 0.027466 | 0.032043 | -122.6807 | -122.6944 | 0.17853 | 0.16479 | 0.15564 | 0.13275 | 0.1236 | 0.16479 | 0.032044 | 0.14649 | 0.027466 | 0.004578 | 0.041199 | 3.6392 | 0.073242 | -119.1193 | -122.7219 | 3.6667 | 0.059509 | 3.7033 | 0.10071
5522.0781 | 122.7127 | -0.10529 | 122.7036 | -0.012131 | 0.012941 | 0.0077118 | -0.009363 | 0.0012261 | -0.012407 | -0.0019546 | -0.005371 | 0.020395 | 0.039217 | -0.0082287 | 0.011907 | 0.021828 | -0.0036253 | 3.6667 | 3.7216 | 3.6438 | 3.6301 | 3.7537 | 3.6438 | 3.6667 | -0.068665 | 0.032043 | -0.068665 | -0.064087 | 0.041199 | 0 | 0.022888 | 3.7491 | -118.9819 | -119.0735 | 3.8589 | 3.772 | 3.7491 | 0.022888 | 0 | 0.036621 | -122.6715 | -122.7676 | 0.14649 | 0.12817 | 0.10529 | 0.091553 | 0.068665 | 0.10986 | -0.013733 | 0.10986 | 0.004578 | 0.07782 | 0.10071 | 3.8269 | 0.13733 | -119.0598 | -122.7722 | 3.7354 | 0.041199 | 3.772 | 0.036621
5523.8438 | 122.7264 | -0.10071 | 122.6852 | -0.0045011 | 0.015932 | 0.010062 | -0.006586 | 0.00015814 | -0.0089892 | -0.0057998 | -0.005371 | 0.021035 | 0.043489 | -0.021473 | 0.01383 | 0.020546 | -0.0012753 | 3.6804 | 3.6621 | 3.6118 | 3.6026 | 3.7216 | 3.5797 | 3.6118 | 0.009155 | 0.027466 | -0.036621 | -0.041199 | 0.045776 | 0.009155 | 0.050354 | 3.7125 | -119.0231 | -119.0826 | 3.8223 | 3.7125 | 3.6804 | 0 | -0.032043 | 0.064087 | -122.6578 | -122.7264 | 0.14648 | 0.15106 | 0.10986 | 0.086975 | 0.045776 | 0.10986 | -0.009155 | 0.082397 | -0.004578 | 0.050354 | 0.064087 | 3.7628 | 0.12817 | -119.0735 | -122.7219 | 3.7033 | 0.059509 | 3.7811 | 0.10986
5525.5469 | 122.8546 | -0.064087 | 122.644 | -0.01976 | 0.013796 | 0.010703 | -0.007654 | 0.00015814 | -0.0081348 | -0.0030228 | -0.011475 | 0.019326 | 0.04178 | -0.018696 | 0.011907 | 0.022255 | -0.0049069 | 3.6163 | 3.5294 | 3.5202 | 3.566 | 3.6942 | 3.5431 | 3.598 | 0.10071 | 0.009155 | -0.041199 | 0.07782 | 0.16479 | 0.12817 | 0.14191 | 3.5843 | -119.1147 | -119.0781 | 3.7582 | 3.6621 | 3.6072 | 0.077819 | 0.022888 | 0.022888 | -122.6349 | -122.5662 | 0.22888 | 0.20599 | 0.19226 | 0.18311 | 0.16937 | 0.17395 | 0.045776 | 0.20599 | 0.11902 | 0.009155 | 0.050354 | 3.5934 | 0.073242 | -119.1238 | -122.6852 | 3.6301 | 0.14191 | 3.6804 | 0.1648
5527.2656 | 122.818 | -0.068665 | 122.6852 | -0.01976 | 0.011446 | 0.010489 | -0.0091494 | 0.0018671 | -0.01198 | -0.0038772 | -0.011475 | 0.019967 | 0.038576 | -0.020405 | 0.011907 | 0.02311 | -0.0055479 | 3.7262 | 3.6438 | 3.6392 | 3.717 | 3.8452 | 3.717 | 3.7399 | 0.091553 | 0 | -0.004578 | 0.036621 | 0.15106 | 0.12817 | 0.11902 | 3.7079 | -119.0414 | -118.9682 | 3.9139 | 3.8086 | 3.7857 | 0.10071 | 0.07782 | 0.064087 | -122.6852 | -122.6486 | 0.21973 | 0.18768 | 0.19684 | 0.1236 | 0.13275 | 0.20599 | 0.07782 | 0.15564 | 0.041199 | 0.004578 | 0.004578 | 3.7125 | 0.068665 | -119.046 | -122.6898 | 3.7857 | 0.10529 | 3.7949 | 0.16022
5528.9844 | 122.8455 | -0.064087 | 122.6669 | -0.012131 | 0.010164 | 0.008139 | -0.010645 | -0.0028327 | -0.013048 | -0.0060134 | -0.011475 | 0.018045 | 0.04178 | -0.013569 | 0.010626 | 0.022042 | -0.0031979 | 3.7216 | 3.6346 | 3.6118 | 3.6987 | 3.8498 | 3.7079 | 3.7308 | 0.13733 | -0.004578 | -0.027466 | 0.054932 | 0.17853 | 0.14648 | 0.13733 | 3.6758 | -119.0323 | -118.9682 | 3.9139 | 3.7949 | 3.772 | 0.11902 | 0.096131 | 0.036621 | -122.6715 | -122.612 | 0.24261 | 0.20142 | 0.21057 | 0.16479 | 0.17395 | 0.23804 | 0.086975 | 0.20599 | 0.082398 | 0.022889 | 0.022888 | 3.6987 | 0.059509 | -119.0552 | -122.6944 | 3.7628 | 0.11902 | 3.7857 | 0.20142
5530.6875 | 122.731 | -0.09613 | 122.6898 | -0.01976 | 0.012514 | 0.009848 | -0.007654 | 0.0022943 | -0.010698 | -0.0057998 | -0.005371 | 0.022744 | 0.041994 | -0.012929 | 0.012334 | 0.022042 | -0.0085385 | 3.6392 | 3.6163 | 3.566 | 3.5431 | 3.6621 | 3.5202 | 3.5477 | -0.018311 | 0.050354 | -0.073242 | -0.050354 | 0.027466 | -0.013733 | 0.022888 | 3.6621 | -119.0735 | -119.1467 | 3.7582 | 3.6438 | 3.6163 | -0.018311 | -0.045776 | 0.022888 | -122.6395 | -122.7402 | 0.1236 | 0.11902 | 0.082397 | 0.09613 | 0.059509 | 0.09613 | -0.022888 | 0.10071 | 0.022888 | 0.050354 | 0.1236 | 3.7125 | 0.14648 | -119.1238 | -122.7631 | 3.6392 | 0.045776 | 3.7354 | 0.077819
5532.4219 | 122.7859 | -0.07782 | 122.699 | -0.012131 | 0.01166 | 0.0085662 | -0.010004 | -0.0051825 | -0.01198 | -0.0043046 | -0.0084228 | 0.01954 | 0.042208 | -0.022328 | 0.01148 | 0.022042 | -0.0040525 | 3.7079 | 3.6484 | 3.6163 | 3.6758 | 3.8086 | 3.6896 | 3.7079 | 0.041199 | 0.032043 | -0.041199 | -0.018311 | 0.10986 | 0.091553 | 0.07782 | 3.6942 | -119.0506 | -119.0231 | 3.8864 | 3.7857 | 3.7674 | 0.091553 | 0.073242 | 0.036621 | -122.6669 | -122.7173 | 0.18768 | 0.15564 | 0.16937 | 0.11902 | 0.13275 | 0.19226 | 0.059509 | 0.15106 | 0.022888 | 0.032043 | 0.073242 | 3.7262 | 0.10986 | -119.0826 | -122.7402 | 3.7537 | 0.059509 | 3.7857 | 0.11902
5534.125 | 122.7081 | -0.10529 | 122.6898 | -0.01976 | 0.013582 | 0.009848 | -0.0050906 | 0.0044305 | -0.010057 | -0.0053726 | -0.0084228 | 0.023172 | 0.041353 | -0.01122 | 0.013616 | 0.021401 | -0.0025571 | 3.6072 | 3.598 | 3.5614 | 3.5156 | 3.6209 | 3.4973 | 3.5156 | -0.050354 | 0.022888 | -0.059509 | -0.050354 | 0 | -0.027466 | 0.018311 | 3.6667 | -119.0918 | -119.1742 | 3.7262 | 3.6209 | 3.6026 | -0.045776 | -0.064087 | 0.045777 | -122.6669 | -122.7402 | 0.10529 | 0.1236 | 0.07782 | 0.07782 | 0.032043 | 0.05951 | -0.045776 | 0.059509 | 0.009155 | 0.036621 | 0.082397 | 3.7033 | 0.12817 | -119.1284 | -122.7493 | 3.6209 | 0.054932 | 3.7125 | 0.054932
5535.8281 | 122.8271 | -0.07782 | 122.6761 | -0.012131 | 0.012728 | 0.0085662 | -0.010431 | -0.00091006 | -0.0094164 | -0.0015274 | -0.011475 | 0.020181 | 0.03879 | -0.022969 | 0.0078485 | 0.022683 | -0.0019163 | 3.6026 | 3.5751 | 3.5522 | 3.5889 | 3.7125 | 3.5934 | 3.6255 | 0.050354 | 0.004578 | -0.036621 | 0.032043 | 0.14648 | 0.13275 | 0.1236 | 3.6301 | -119.101 | -119.0872 | 3.7903 | 3.7033 | 3.6713 | 0.073242 | 0.041199 | 0.041199 | -122.6715 | -122.644 | 0.2243 | 0.20142 | 0.21057 | 0.16022 | 0.16937 | 0.16022 | 0.036621 | 0.18311 | 0.068664 | 0.022888 | 0.041199 | 3.653 | 0.082398 | -119.1238 | -122.7127 | 3.6667 | 0.10986 | 3.6804 | 0.12817
5537.5469 | 122.7264 | -0.11902 | 122.7219 | -0.01976 | 0.010805 | 0.0092072 | -0.010431 | -0.0032599 | -0.010912 | -0.00345 | -0.005371 | 0.02189 | 0.041567 | -0.014851 | 0.010839 | 0.020546 | -0.0055479 | 3.685 | 3.7079 | 3.598 | 3.5797 | 3.6804 | 3.598 | 3.6301 | -0.064087 | 0.041199 | -0.07782 | -0.073242 | 0.036621 | 0.004578 | 0.032043 | 3.717 | -119.014 | -119.1422 | 3.7994 | 3.7491 | 3.717 | 0.032044 | 0 | 0.041199 | -122.6807 | -122.7951 | 0.15564 | 0.15106 | 0.1236 | 0.10986 | 0.082398 | 0.082398 | -0.01831 | 0.11444 | 0.004578 | 0.10986 | 0.11902 | 3.8269 | 0.16022 | -119.1238 | -122.7997 | 3.6987 | 0.045777 | 3.804 | 0.054932
5539.3125 | 122.8683 | -0.07782 | 122.6395 | -0.02739 | 0.010378 | 0.0072846 | -0.009363 | -0.0021919 | -0.010057 | -0.0036636 | -0.0084228 | 0.018472 | 0.04114 | -0.016987 | 0.011053 | 0.022683 | -0.0038389 | 3.6163 | 3.566 | 3.5294 | 3.5797 | 3.717 | 3.6026 | 3.6392 | 0.068665 | 0.009155 | -0.036621 | 0.045776 | 0.16937 | 0.13733 | 0.13733 | 3.6072 | -119.0735 | -119.0598 | 3.7949 | 3.717 | 3.6804 | 0.10986 | 0.073242 | 0.041199 | -122.6303 | -122.5937 | 0.24719 | 0.21515 | 0.21515 | 0.17395 | 0.17395 | 0.18768 | 0.050354 | 0.20599 | 0.082397 | 0.036621 | 0.045776 | 3.6438 | 0.086975 | -119.1101 | -122.6761 | 3.6575 | 0.1236 | 3.6942 | 0.14649
5541.0156 | 122.731 | -0.10986 | 122.6898 | -0.01976 | 0.0095234 | 0.0066436 | -0.0085086 | -0.0013373 | -0.013689 | -0.002382 | -0.005371 | 0.021035 | 0.042421 | -0.016133 | 0.014257 | 0.022255 | -0.0061887 | 3.653 | 3.7216 | 3.598 | 3.5889 | 3.6987 | 3.5889 | 3.6255 | -0.07782 | 0.050354 | -0.064087 | -0.086975 | 0.027466 | 0.013733 | 0.041199 | 3.7079 | -118.9682 | -119.101 | 3.8086 | 3.7354 | 3.6987 | 0.027466 | -0.009155 | 0.045776 | -122.6395 | -122.7768 | 0.13733 | 0.15106 | 0.1236 | 0.10529 | 0.07782 | 0.10071 | -0.009155 | 0.091553 | -0.022888 | 0.1236 | 0.11444 | 3.8315 | 0.16022 | -119.0918 | -122.7539 | 3.6987 | 0.022888 | 3.7628 | 0.032043
5542.7344 | 122.7585 | -0.09613 | 122.6944 | -0.01976 | 0.0093098 | 0.0096344 | -0.010858 | -0.00048286 | -0.010698 | -0.00345 | -0.0084228 | 0.020608 | 0.039644 | -0.02126 | 0.012548 | 0.024391 | -0.0042661 | 3.685 | 3.6026 | 3.598 | 3.6392 | 3.7903 | 3.6575 | 3.6667 | 0.027466 | 0.004578 | -0.059509 | -0.041199 | 0.091553 | 0.054932 | 0.07782 | 3.6942 | -119.0918 | -119.0552 | 3.8864 | 3.7628 | 3.7537 | 0.068665 | 0.05951 | 0.036621 | -122.6898 | -122.7356 | 0.18768 | 0.17395 | 0.15106 | 0.13733 | 0.11444 | 0.19226 | 0.041199 | 0.15106 | 0.01831 | 0.004578 | 0.064087 | 3.6987 | 0.10071 | -119.0964 | -122.7539 | 3.7354 | 0.054931 | 3.7811 | 0.1236
5544.4688 | 122.7448 | -0.091553 | 122.699 | -0.035019 | 0.013369 | 0.0096344 | -0.0067996 | -0.00026906 | -0.0083484 | -0.0040908 | -0.0023192 | 0.022958 | 0.040285 | -0.018269 | 0.015325 | 0.02311 | -0.0059751 | 3.5248 | 3.5431 | 3.4653 | 3.4149 | 3.5294 | 3.3875 | 3.4424 | -0.068665 | 0.036621 | -0.064087 | -0.059509 | 0.036621 | -0.009155 | 0.036621 | 3.5568 | -119.1559 | -119.2841 | 3.6209 | 3.5339 | 3.479 | -0.022888 | -0.07782 | 0.027466 | -122.6624 | -122.7585 | 0.12817 | 0.12817 | 0.082398 | 0.10071 | 0.054932 | 0.064087 | -0.050354 | 0.10071 | 0.004578 | 0.07782 | 0.10071 | 3.6346 | 0.12817 | -119.2337 | -122.7631 | 3.5065 | 0.032044 | 3.6163 | 0.022888
5546.1875 | 122.7448 | -0.11444 | 122.7036 | -0.01976 | 0.013796 | 0.0092072 | -0.0055178 | 0.0065667 | -0.0087756 | -0.0043046 | -0.005371 | 0.022958 | 0.04114 | -0.012074 | 0.012334 | 0.021828 | -0.0021299 | 3.5202 | 3.5339 | 3.4332 | 3.4287 | 3.5339 | 3.4058 | 3.4378 | -0.027466 | 0.041199 | -0.050354 | -0.036621 | 0.032043 | -0.009155 | 0.045776 | 3.5477 | -119.1696 | -119.2749 | 3.6484 | 3.5522 | 3.5202 | 0.004577 | -0.027466 | 0.064087 | -122.6624 | -122.7402 | 0.14648 | 0.16022 | 0.10529 | 0.09613 | 0.041199 | 0.10071 | -0.004578 | 0.082397 | 0.013733 | 0.10071 | 0.091553 | 3.6484 | 0.15564 | -119.2703 | -122.7539 | 3.5431 | 0.07782 | 3.6346 | 0.086975
5547.9219 | 122.7356 | -0.10986 | 122.7127 | -0.012131 | 0.014437 | 0.009848 | -0.0074404 | -0.00069646 | -0.0087756 | -0.0030228 | -0.005371 | 0.020608 | 0.045198 | -0.015492 | 0.01383 | 0.021401 | -0.0017027 | 3.5019 | 3.5614 | 3.4698 | 3.3966 | 3.511 | 3.3737 | 3.4241 | -0.059509 | 0.041199 | -0.073242 | -0.050354 | 0.009155 | -0.009155 | 0.036621 | 3.5797 | -119.1513 | -119.3161 | 3.6209 | 3.5339 | 3.4836 | -0.045777 | -0.096131 | 0.036621 | -122.6715 | -122.7631 | 0.11902 | 0.14648 | 0.10071 | 0.10986 | 0.064087 | 0.041198 | -0.073243 | 0.082397 | 0.022888 | 0.091552 | 0.11444 | 3.6713 | 0.15106 | -119.2429 | -122.7859 | 3.5065 | 0.059509 | 3.6118 | 0.050354
5549.6562 | 122.8455 | -0.059509 | 122.6669 | -0.012131 | 0.008028 | 0.0094208 | -0.0091494 | -5.5462e-05 | -0.010271 | -0.0053726 | -0.005371 | 0.018258 | 0.041567 | -0.017842 | 0.011694 | 0.020333 | -0.0070433 | 3.6621 | 3.5797 | 3.566 | 3.6301 | 3.7811 | 3.6621 | 3.6896 | 0.10986 | 0 | -0.032043 | 0.050354 | 0.17853 | 0.15564 | 0.14191 | 3.6255 | -119.0872 | -119.0369 | 3.8406 | 3.7491 | 3.7216 | 0.1236 | 0.09613 | 0.027466 | -122.6669 | -122.6166 | 0.23804 | 0.20142 | 0.21515 | 0.17395 | 0.18768 | 0.21515 | 0.064087 | 0.21057 | 0.082397 | 0.013733 | 0.032043 | 3.6392 | 0.059509 | -119.101 | -122.699 | 3.6896 | 0.10986 | 3.7216 | 0.16937
5551.3906 | 122.7859 | -0.09613 | 122.7081 | -0.012131 | 0.0123 | 0.010062 | -0.0080814 | 0.0037897 | -0.010698 | -0.000673 | -0.005371 | 0.022531 | 0.041567 | -0.016987 | 0.011694 | 0.021187 | -0.0072569 | 3.6255 | 3.6392 | 3.5614 | 3.5477 | 3.653 | 3.5614 | 3.5751 | -0.013733 | 0.041199 | -0.054932 | -0.013733 | 0.086975 | 0.050354 | 0.07782 | 3.6575 | -119.0689 | -119.1605 | 3.7491 | 3.6713 | 3.6575 | 0.013733 | 0 | 0.041198 | -122.6669 | -122.7219 | 0.1831 | 0.17395 | 0.14648 | 0.13275 | 0.10529 | 0.091553 | -0.013733 | 0.14191 | 0.041199 | 0.07782 | 0.096131 | 3.7354 | 0.13733 | -119.1467 | -122.7631 | 3.6438 | 0.082397 | 3.7216 | 0.082397
5553.0938 | 122.8638 | -0.054932 | 122.6761 | -0.02739 | 0.012941 | 0.010062 | -0.0072268 | -0.00048286 | -0.0077074 | -0.0047318 | -0.0084228 | 0.020608 | 0.042635 | -0.017415 | 0.012975 | 0.02311 | -0.0044797 | 3.5385 | 3.4424 | 3.4515 | 3.4973 | 3.6072 | 3.4744 | 3.5065 | 0.10529 | -0.013733 | -0.027466 | 0.082397 | 0.17395 | 0.11902 | 0.14191 | 3.5065 | -119.2337 | -119.1788 | 3.6621 | 3.5614 | 3.5294 | 0.054932 | 0.022888 | 0.027466 | -122.6898 | -122.5937 | 0.22888 | 0.19684 | 0.17395 | 0.16937 | 0.14649 | 0.15564 | 0.045776 | 0.20142 | 0.10986 | -0.009155 | 0.013733 | 3.4973 | 0.041199 | -119.2245 | -122.7036 | 3.5522 | 0.13733 | 3.5934 | 0.16022
5554.8125 | 122.7356 | -0.13275 | 122.6944 | -0.01976 | 0.011019 | 0.0068574 | -0.009363 | -0.00069646 | -0.011125 | -0.0045182 | -0.0023192 | 0.020181 | 0.042635 | -0.015065 | 0.012121 | 0.02311 | -0.0038389 | 3.5751 | 3.6163 | 3.5431 | 3.5202 | 3.6438 | 3.5477 | 3.5751 | -0.059509 | 0.054932 | -0.07782 | -0.082397 | 0.032043 | 0.009155 | 0.027466 | 3.6758 | -119.0781 | -119.1742 | 3.7765 | 3.7079 | 3.6804 | 0.032043 | 0.004577 | 0.054931 | -122.6395 | -122.7768 | 0.16479 | 0.16022 | 0.14191 | 0.10529 | 0.086975 | 0.10071 | -0.022888 | 0.10986 | -0.004577 | 0.073242 | 0.13275 | 3.7491 | 0.18768 | -119.1513 | -122.7722 | 3.653 | 0.050354 | 3.7079 | 0.073242
5556.5469 | 122.8729 | -0.064087 | 122.6624 | -0.0045011 | 0.015505 | 0.0085662 | -0.0055178 | 0.0027215 | -0.0081348 | -0.0021682 | -0.005371 | 0.021035 | 0.040712 | -0.01656 | 0.011694 | 0.023964 | -0.0036253 | 3.5294 | 3.447 | 3.4287 | 3.4698 | 3.6118 | 3.4607 | 3.5156 | 0.091553 | -0.009155 | -0.022888 | 0.064087 | 0.16937 | 0.11444 | 0.15106 | 3.4927 | -119.2154 | -119.1925 | 3.6758 | 3.5797 | 3.5248 | 0.086975 | 0.032043 | 0.041199 | -122.6715 | -122.5983 | 0.23346 | 0.21515 | 0.17853 | 0.17395 | 0.13733 | 0.1831 | 0.041199 | 0.19226 | 0.086975 | 0.01831 | 0.013733 | 3.511 | 0.054932 | -119.2337 | -122.6852 | 3.5339 | 0.12817 | 3.5934 | 0.15564
5558.3125 | 122.7859 | -0.091553 | 122.699 | -0.02739 | 0.0123 | 0.0092072 | -0.0067996 | -5.5462e-05 | -0.010698 | -0.0053726 | -0.005371 | 0.02189 | 0.039644 | -0.018696 | 0.011907 | 0.023537 | -0.0042661 | 3.5934 | 3.5751 | 3.5156 | 3.5202 | 3.6255 | 3.5065 | 3.5202 | 0.018311 | 0.027466 | -0.054932 | -0.018311 | 0.10529 | 0.041199 | 0.07782 | 3.6072 | -119.1238 | -119.1788 | 3.717 | 3.6118 | 3.598 | 0.004578 | -0.009155 | 0.036621 | -122.6715 | -122.7173 | 0.19684 | 0.16937 | 0.13275 | 0.13275 | 0.096131 | 0.10986 | 0.004578 | 0.16022 | 0.036621 | 0.059509 | 0.082398 | 3.6667 | 0.11902 | -119.1834 | -122.7539 | 3.6118 | 0.073242 | 3.685 | 0.10986
5560.0312 | 122.7493 | -0.10529 | 122.6944 | -0.01976 | 0.013582 | 0.0092072 | -0.0074404 | 0.0035761 | -0.010057 | -0.0060134 | -0.005371 | 0.021249 | 0.042208 | -0.020405 | 0.012762 | 0.023537 | -0.0021299 | 3.4561 | 3.4973 | 3.4103 | 3.3691 | 3.4836 | 3.3508 | 3.3966 | -0.050354 | 0.041199 | -0.054932 | -0.054932 | 0.032043 | -0.018311 | 0.036621 | 3.5156 | -119.1971 | -119.3253 | 3.5889 | 3.5019 | 3.4561 | -0.013733 | -0.059509 | 0.050354 | -122.6532 | -122.7493 | 0.13733 | 0.14191 | 0.086975 | 0.091553 | 0.036621 | 0.073243 | -0.041198 | 0.086975 | 0 | 0.086975 | 0.096131 | 3.6026 | 0.14649 | -119.2841 | -122.7493 | 3.4744 | 0.050354 | 3.5614 | 0.054932
5561.7656 | 122.7722 | -0.10071 | 122.6898 | -0.012131 | 0.016359 | 0.0092072 | -0.007654 | 0.0010125 | -0.0079212 | -0.0036636 | -0.005371 | 0.02189 | 0.041353 | -0.013142 | 0.013403 | 0.021614 | -0.0019163 | 3.4607 | 3.479 | 3.3829 | 3.3646 | 3.479 | 3.36 | 3.392 | -0.022888 | 0.036621 | -0.059509 | -0.022888 | 0.059509 | 0 | 0.054932 | 3.4836 | -119.2108 | -119.3253 | 3.5797 | 3.4927 | 3.4607 | 0.009155 | -0.022889 | 0.041199 | -122.6532 | -122.7127 | 0.16022 | 0.15564 | 0.10071 | 0.11444 | 0.059509 | 0.09613 | -0.018311 | 0.11902 | 0.036621 | 0.09613 | 0.09613 | 3.5797 | 0.13733 | -119.3069 | -122.7493 | 3.4653 | 0.07782 | 3.5614 | 0.07782
5563.4844 | 122.818 | -0.07782 | 122.6715 | -0.012131 | 0.013155 | 0.0083526 | -0.010218 | 0.0027215 | -0.00963 | -0.0036636 | -0.005371 | 0.016977 | 0.042635 | -0.020192 | 0.010839 | 0.022469 | -0.0023435 | 3.4698 | 3.4515 | 3.4332 | 3.447 | 3.5614 | 3.4515 | 3.4973 | 0.036621 | 0 | -0.054932 | 0.018311 | 0.11444 | 0.07782 | 0.082397 | 3.511 | -119.22 | -119.2245 | 3.6392 | 3.5751 | 3.5294 | 0.064086 | 0.01831 | 0.022888 | -122.6715 | -122.6532 | 0.19226 | 0.16022 | 0.15564 | 0.13733 | 0.13275 | 0.12817 | 0.013732 | 0.16937 | 0.073243 | 0.01831 | 0.054932 | 3.5294 | 0.07782 | -119.2383 | -122.7264 | 3.5248 | 0.096131 | 3.5477 | 0.11444
5565.2031 | 122.8226 | -0.064087 | 122.6852 | -0.02739 | 0.012514 | 0.0085662 | -0.0091494 | -0.0026191 | -0.00963 | -0.0030228 | -0.005371 | 0.018258 | 0.041353 | -0.020405 | 0.0082757 | 0.025246 | -0.0021299 | 3.4836 | 3.4515 | 3.4195 | 3.447 | 3.5751 | 3.447 | 3.4927 | 0.045776 | -0.009155 | -0.032043 | 0.004578 | 0.10071 | 0.086975 | 0.091553 | 3.4836 | -119.2337 | -119.2383 | 3.6392 | 3.5568 | 3.511 | 0.073242 | 0.027465 | 0.032044 | -122.6944 | -122.6807 | 0.1648 | 0.15564 | 0.15106 | 0.1236 | 0.11902 | 0.15564 | 0.027465 | 0.13275 | 0.036621 | 0.032043 | 0.022888 | 3.5156 | 0.054932 | -119.2657 | -122.7173 | 3.511 | 0.068665 | 3.5477 | 0.10986
5566.9375 | 122.7631 | -0.10986 | 122.7081 | -0.01976 | 0.015718 | 0.0094208 | -0.005945 | 0.0037897 | -0.0098438 | -0.0025956 | -0.0084228 | 0.022317 | 0.041353 | -0.016347 | 0.013403 | 0.020546 | -0.0038389 | 3.4607 | 3.4698 | 3.392 | 3.36 | 3.4515 | 3.3417 | 3.3691 | -0.027466 | 0.022888 | -0.050354 | -0.018311 | 0.041199 | 0.013733 | 0.064087 | 3.5019 | -119.2383 | -119.3481 | 3.5614 | 3.479 | 3.4515 | -0.022888 | -0.050354 | 0.059509 | -122.6852 | -122.7264 | 0.15106 | 0.17395 | 0.1236 | 0.11444 | 0.064087 | 0.059509 | -0.032044 | 0.091553 | 0.032043 | 0.07782 | 0.073242 | 3.5797 | 0.13275 | -119.3161 | -122.7585 | 3.4698 | 0.091552 | 3.5706 | 0.082397
5568.6562 | 122.8317 | -0.059509 | 122.7127 | -0.0045011 | 0.01465 | 0.00878 | -0.007654 | -0.00091006 | -0.010485 | -0.005159 | -0.0084228 | 0.020395 | 0.04114 | -0.016987 | 0.011053 | 0.023323 | -0.0049069 | 3.4973 | 3.4149 | 3.4058 | 3.4561 | 3.5934 | 3.4241 | 3.4836 | 0.11444 | -0.009155 | -0.027466 | 0.045776 | 0.13275 | 0.09613 | 0.10986 | 3.4653 | -119.2978 | -119.2566 | 3.653 | 3.5431 | 3.4836 | 0.07782 | 0.01831 | 0.032043 | -122.7219 | -122.6669 | 0.19226 | 0.16937 | 0.15564 | 0.13733 | 0.1236 | 0.18768 | 0.050354 | 0.16022 | 0.073242 | 0.009155 | 0.018311 | 3.4744 | 0.050354 | -119.3069 | -122.7402 | 3.5156 | 0.10528 | 3.5568 | 0.17395
5570.375 | 122.8455 | -0.068665 | 122.6898 | -0.02739 | 0.011232 | 0.0094208 | -0.010858 | -0.0011237 | -0.011339 | -0.00345 | -0.0084228 | 0.018472 | 0.041567 | -0.02126 | 0.0093439 | 0.023751 | -0.0055479 | 3.5065 | 3.4698 | 3.447 | 3.4927 | 3.6301 | 3.5065 | 3.566 | 0.073242 | 0.009155 | -0.036621 | 0.045776 | 0.16479 | 0.1236 | 0.1236 | 3.5156 | -119.22 | -119.1971 | 3.6987 | 3.6346 | 3.5751 | 0.11902 | 0.05951 | 0.032044 | -122.6807 | -122.644 | 0.23346 | 0.19226 | 0.19226 | 0.16022 | 0.16022 | 0.18311 | 0.045777 | 0.20142 | 0.082397 | 0.022889 | 0.045776 | 3.5385 | 0.07782 | -119.2429 | -122.7264 | 3.5614 | 0.11444 | 3.5751 | 0.14191
5572.0938 | 122.7173 | -0.09613 | 122.7448 | -0.01976 | 0.013369 | 0.0096344 | -0.004877 | 0.0040033 | -0.008562 | -0.0062272 | -0.0084228 | 0.021676 | 0.044344 | -0.0082287 | 0.012121 | 0.022255 | -0.0040525 | 3.4882 | 3.5065 | 3.4195 | 3.3875 | 3.4744 | 3.3554 | 3.3875 | -0.045776 | 0.041199 | -0.054932 | -0.07782 | 0.022888 | -0.022888 | 0.022888 | 3.5156 | -119.2383 | -119.3573 | 3.5706 | 3.4836 | 3.4515 | -0.032044 | -0.064087 | 0.041198 | -122.7036 | -122.8226 | 0.11902 | 0.11902 | 0.073242 | 0.07782 | 0.032044 | 0.054931 | -0.032044 | 0.07782 | -0.022888 | 0.086975 | 0.096131 | 3.6026 | 0.13733 | -119.3253 | -122.7997 | 3.4836 | 0.01831 | 3.5843 | 0.050354
5573.8281 | 122.8409 | -0.07782 | 122.7127 | -0.012131 | 0.011232 | 0.008139 | -0.011927 | -0.0019781 | -0.010912 | -0.0049454 | -0.0023192 | 0.01954 | 0.040071 | -0.015065 | 0.011053 | 0.023964 | -0.0042661 | 3.5934 | 3.511 | 3.4973 | 3.5706 | 3.6896 | 3.5706 | 3.5889 | 0.10071 | 0 | -0.018311 | 0.032043 | 0.16937 | 0.1236 | 0.12817 | 3.5751 | -119.2017 | -119.1422 | 3.7674 | 3.6667 | 3.6484 | 0.091553 | 0.073243 | 0.059509 | -122.7127 | -122.6807 | 0.24719 | 0.20599 | 0.20142 | 0.14649 | 0.14191 | 0.19226 | 0.073243 | 0.18768 | 0.050354 | 0.013733 | 0.018311 | 3.5889 | 0.07782 | -119.2154 | -122.731 | 3.6484 | 0.10986 | 3.6713 | 0.17853
5575.5469 | 122.8088 | -0.059509 | 122.6807 | -0.01976 | 0.014864 | 0.009848 | -0.0097904 | 0.0035761 | -0.0094164 | -0.005159 | -0.0084228 | 0.017831 | 0.040926 | -0.018696 | 0.011053 | 0.023323 | -0.0010617 | 3.479 | 3.4012 | 3.3966 | 3.4195 | 3.5706 | 3.4058 | 3.4515 | 0.082397 | 0.004578 | -0.032043 | 0.036621 | 0.1236 | 0.086975 | 0.10529 | 3.4561 | -119.2795 | -119.2612 | 3.6301 | 3.511 | 3.4653 | 0.054932 | 0.009156 | 0.027466 | -122.6761 | -122.644 | 0.1831 | 0.16479 | 0.14648 | 0.13733 | 0.11902 | 0.17395 | 0.022889 | 0.15564 | 0.068664 | 0.004578 | 0.036621 | 3.4607 | 0.064087 | -119.2841 | -122.7127 | 3.479 | 0.09613 | 3.5385 | 0.14191
5577.3125 | 122.7356 | -0.10529 | 122.7219 | -0.012131 | 0.011232 | 0.00643 | -0.009363 | 0.0016535 | -0.010485 | -0.00345 | -0.0023192 | 0.022317 | 0.042849 | -0.015919 | 0.0093439 | 0.02076 | -0.0070433 | 3.5156 | 3.5568 | 3.479 | 3.447 | 3.5843 | 3.4744 | 3.5065 | -0.068665 | 0.045776 | -0.064087 | -0.068665 | 0.027466 | -0.009155 | 0.018311 | 3.5843 | -119.165 | -119.2749 | 3.6896 | 3.6118 | 3.5797 | 0.027466 | -0.004578 | 0.041199 | -122.6761 | -122.7905 | 0.13275 | 0.1236 | 0.096131 | 0.082398 | 0.054932 | 0.10529 | -0.032044 | 0.091553 | -0.004578 | 0.07782 | 0.10986 | 3.6621 | 0.15106 | -119.2429 | -122.7859 | 3.5522 | 0.036621 | 3.6209 | 0.036621
5579.0312 | 122.7905 | -0.09613 | 122.7127 | -0.012131 | 0.013155 | 0.0085662 | -0.008295 | -0.0024055 | -0.010698 | -0.0032364 | -0.0084228 | 0.023172 | 0.041994 | -0.010365 | 0.013616 | 0.022255 | -0.0034117 | 3.5202 | 3.4882 | 3.4241 | 3.4424 | 3.5614 | 3.447 | 3.4698 | 0.027466 | 0.032043 | -0.054932 | 0 | 0.086975 | 0.045776 | 0.073242 | 3.5202 | -119.2245 | -119.2703 | 3.6575 | 3.566 | 3.5431 | 0.045777 | 0.022888 | 0.041198 | -122.6807 | -122.7127 | 0.1831 | 0.16937 | 0.14191 | 0.12817 | 0.10071 | 0.13733 | 0.018311 | 0.14191 | 0.054932 | 0.064087 | 0.086975 | 3.5843 | 0.12817 | -119.2886 | -122.7676 | 3.5385 | 0.09613 | 3.6163 | 0.1236
5580.7656 | 122.7402 | -0.12817 | 122.7036 | -0.0045011 | 0.01166 | 0.0060028 | -0.010858 | -0.0026191 | -0.013048 | -0.0038772 | -0.005371 | 0.020181 | 0.04114 | -0.018696 | 0.011694 | 0.022469 | -0.0055479 | 3.5156 | 3.5522 | 3.4744 | 3.4332 | 3.5751 | 3.447 | 3.4836 | -0.082397 | 0.050354 | -0.068665 | -0.07782 | 0.036621 | -0.004578 | 0.032043 | 3.6026 | -119.1513 | -119.2703 | 3.7033 | 3.6118 | 3.5751 | 0.009156 | -0.027466 | 0.059509 | -122.6532 | -122.7814 | 0.1648 | 0.16022 | 0.1236 | 0.10071 | 0.064087 | 0.10071 | -0.041198 | 0.10529 | -0.009155 | 0.07782 | 0.11902 | 3.6804 | 0.17853 | -119.2291 | -122.7722 | 3.5614 | 0.050354 | 3.6438 | 0.045777
5582.4844 | 122.7585 | -0.10986 | 122.7036 | -0.01976 | 0.016146 | 0.010062 | -0.0072268 | 0.00037174 | -0.00963 | -0.0015274 | -0.0084228 | 0.021035 | 0.040926 | -0.017628 | 0.010412 | 0.023537 | -0.0068295 | 3.4149 | 3.4241 | 3.3463 | 3.3005 | 3.4195 | 3.2776 | 3.3234 | -0.041199 | 0.032043 | -0.064087 | -0.050354 | 0.041199 | 0 | 0.036621 | 3.4561 | -119.2795 | -119.4031 | 3.5294 | 3.4332 | 3.3875 | -0.022888 | -0.068664 | 0.045776 | -122.6715 | -122.7539 | 0.15106 | 0.14648 | 0.10986 | 0.10071 | 0.064087 | 0.073243 | -0.045776 | 0.10529 | 0.013733 | 0.07782 | 0.09613 | 3.5339 | 0.14191 | -119.3573 | -122.7676 | 3.4103 | 0.059509 | 3.5248 | 0.068664
5584.2656 | 122.7585 | -0.11444 | 122.7081 | -0.012131 | 0.015078 | 0.00878 | -0.0070132 | 0.0016535 | -0.013262 | -0.002382 | -0.005371 | 0.020395 | 0.043062 | -0.015919 | 0.012121 | 0.022683 | -0.0040525 | 3.5019 | 3.4882 | 3.4103 | 3.4287 | 3.5431 | 3.4103 | 3.4424 | 0.018311 | 0.041199 | -0.059509 | -0.022888 | 0.059509 | 0.013733 | 0.045776 | 3.5248 | -119.22 | -119.2795 | 3.6575 | 3.5568 | 3.5248 | 0.032044 | 0 | 0.054932 | -122.6669 | -122.731 | 0.17395 | 0.16022 | 0.12817 | 0.10528 | 0.073242 | 0.13275 | 0.018311 | 0.11902 | 0.036621 | 0.07782 | 0.10071 | 3.6026 | 0.15564 | -119.2978 | -122.7676 | 3.5431 | 0.091553 | 3.6163 | 0.13275
5585.9844 | 122.8683 | -0.054932 | 122.6898 | -0.01976 | 0.010164 | 0.0077118 | -0.009363 | -0.0019781 | -0.011339 | -0.0032364 | -0.005371 | 0.01719 | 0.040712 | -0.015706 | 0.0097711 | 0.025887 | -0.0031979 | 3.5248 | 3.4424 | 3.4515 | 3.5065 | 3.6713 | 3.5202 | 3.5385 | 0.14191 | -0.004578 | -0.036621 | 0.050354 | 0.19684 | 0.15106 | 0.12817 | 3.5065 | -119.2474 | -119.1833 | 3.7262 | 3.5934 | 3.5751 | 0.086975 | 0.068665 | 0.018311 | -122.6944 | -122.6395 | 0.25177 | 0.18311 | 0.20599 | 0.1648 | 0.18768 | 0.21973 | 0.054932 | 0.23346 | 0.086975 | -0.009155 | 0.032043 | 3.4973 | 0.050354 | -119.2383 | -122.7264 | 3.5614 | 0.10529 | 3.5797 | 0.19684
5587.75 | 122.7768 | -0.09613 | 122.7264 | -0.012131 | 0.011446 | 0.008139 | -0.0095766 | 0.00037174 | -0.010698 | -0.0028092 | -0.0084228 | 0.021249 | 0.040071 | -0.021687 | 0.010839 | 0.023537 | -0.0064023 | 3.5385 | 3.4744 | 3.4515 | 3.5019 | 3.6346 | 3.511 | 3.5339 | 0.032043 | 0.009155 | -0.045776 | -0.032043 | 0.09613 | 0.054932 | 0.064087 | 3.5477 | -119.252 | -119.2245 | 3.7308 | 3.6301 | 3.6072 | 0.082398 | 0.059509 | 0.050354 | -122.7173 | -122.7585 | 0.19226 | 0.16022 | 0.15106 | 0.10986 | 0.10071 | 0.18311 | 0.050354 | 0.14191 | 0.013733 | 0.022888 | 0.054931 | 3.5706 | 0.10528 | -119.2749 | -122.7722 | 3.598 | 0.064087 | 3.6346 | 0.12817
5589.4531 | 122.7951 | -0.10071 | 122.7127 | -0.01976 | 0.010164 | 0.010916 | -0.0091494 | 0.0025079 | -0.0098438 | -0.00345 | -0.0084228 | 0.021249 | 0.04114 | -0.017415 | 0.012334 | 0.023323 | -0.0059751 | 3.5065 | 3.5065 | 3.4378 | 3.4241 | 3.5339 | 3.4241 | 3.4698 | -0.036621 | 0.032043 | -0.059509 | -0.036621 | 0.073242 | 0.036621 | 0.059509 | 3.5385 | -119.2062 | -119.2886 | 3.6346 | 3.5706 | 3.5248 | 0.032044 | -0.013733 | 0.041199 | -122.6807 | -122.7493 | 0.17395 | 0.16022 | 0.13733 | 0.11902 | 0.09613 | 0.096131 | -0.013733 | 0.13275 | 0.022888 | 0.068665 | 0.091552 | 3.6072 | 0.13275 | -119.2749 | -122.7722 | 3.5248 | 0.064087 | 3.6072 | 0.064087
5591.1719 | 122.7905 | -0.10529 | 122.6898 | -0.01976 | 0.015718 | 0.0096344 | -0.0074404 | 0.00079894 | -0.0098438 | -0.0045182 | -0.011475 | 0.022744 | 0.043917 | -0.019764 | 0.013616 | 0.023964 | -0.0049069 | 3.3875 | 3.4012 | 3.3096 | 3.2776 | 3.4103 | 3.2684 | 3.3051 | -0.027466 | 0.041199 | -0.054932 | -0.032043 | 0.036621 | 0.018311 | 0.059509 | 3.4149 | -119.2886 | -119.4122 | 3.5156 | 3.4103 | 3.3737 | -0.004577 | -0.041198 | 0.050354 | -122.6486 | -122.7219 | 0.14191 | 0.16479 | 0.1236 | 0.11444 | 0.073243 | 0.10071 | -0.032043 | 0.091553 | 0.022889 | 0.091553 | 0.096131 | 3.5065 | 0.14649 | -119.3802 | -122.7448 | 3.3829 | 0.073243 | 3.4927 | 0.07782
5592.8906 | 122.7814 | -0.11902 | 122.7173 | -0.01976 | 0.015505 | 0.010062 | -0.006586 | 0.0035761 | -0.008562 | -0.0013138 | -0.005371 | 0.021463 | 0.041353 | -0.016133 | 0.011907 | 0.023751 | -0.0031979 | 3.3554 | 3.3875 | 3.3142 | 3.2776 | 3.3875 | 3.2501 | 3.3142 | -0.022888 | 0.022888 | -0.068665 | -0.027466 | 0.050354 | 0.009155 | 0.050354 | 3.4332 | -119.3298 | -119.4397 | 3.5065 | 3.4332 | 3.3691 | 0 | -0.064087 | 0.050354 | -122.6944 | -122.7448 | 0.16937 | 0.16937 | 0.12817 | 0.11902 | 0.07782 | 0.073242 | -0.036621 | 0.11902 | 0.041199 | 0.073242 | 0.091553 | 3.5065 | 0.14191 | -119.4031 | -122.7859 | 3.3966 | 0.091553 | 3.4744 | 0.096131
5594.625 | 122.7081 | -0.11902 | 122.7356 | -0.01976 | 0.01465 | 0.010916 | -0.0072268 | 0.0014397 | -0.010057 | -0.0028092 | -0.0084228 | 0.021249 | 0.041994 | -0.016774 | 0.012548 | 0.024391 | -0.0049069 | 3.392 | 3.392 | 3.3417 | 3.2822 | 3.3875 | 3.2776 | 3.3051 | -0.091553 | 0.045776 | -0.082397 | -0.07782 | -0.004578 | -0.041199 | 0.009155 | 3.4607 | -119.3436 | -119.4534 | 3.5065 | 3.4241 | 3.3966 | -0.036621 | -0.064087 | 0.036622 | -122.6898 | -122.8134 | 0.11444 | 0.12817 | 0.07782 | 0.091552 | 0.041198 | 0.045776 | -0.059509 | 0.077819 | 0.004577 | 0.050354 | 0.12817 | 3.511 | 0.16479 | -119.3939 | -122.818 | 3.4012 | 0.041199 | 3.511 | 0.027466
5596.375 | 122.8134 | -0.059509 | 122.6898 | -0.01976 | 0.014437 | 0.008139 | -0.009363 | 0.0061395 | -0.010485 | -0.0043046 | -0.0084228 | 0.021463 | 0.043276 | -0.022969 | 0.0095575 | 0.025887 | -0.0066159 | 3.3875 | 3.3691 | 3.3279 | 3.3554 | 3.479 | 3.3417 | 3.4103 | 0.041199 | 0.009155 | -0.050354 | -0.013733 | 0.10071 | 0.07782 | 0.09613 | 3.3875 | -119.3207 | -119.3344 | 3.5385 | 3.4698 | 3.4012 | 0.082397 | 0.013733 | 0.009155 | -122.6807 | -122.7036 | 0.16022 | 0.15564 | 0.13733 | 0.14648 | 0.12817 | 0.15106 | 0.027466 | 0.15106 | 0.036621 | 0.041199 | 0.059509 | 3.4286 | 0.068664 | -119.3619 | -122.7402 | 3.4149 | 0.045776 | 3.447 | 0.10071
5598.0938 | 122.7219 | -0.11444 | 122.7173 | -0.0045011 | 0.013796 | 0.009848 | -0.008295 | -0.00026906 | -0.010698 | -0.0057998 | -0.0084228 | 0.023385 | 0.040712 | -0.0054517 | 0.011694 | 0.023537 | -0.0061887 | 3.4241 | 3.4378 | 3.3417 | 3.3142 | 3.4149 | 3.2913 | 3.3188 | -0.050354 | 0.050354 | -0.059509 | -0.068665 | 0.009155 | -0.027466 | 0.018311 | 3.4561 | -119.2795 | -119.4031 | 3.5294 | 3.4332 | 3.4058 | -0.022888 | -0.050354 | 0.054932 | -122.6669 | -122.7859 | 0.1236 | 0.13275 | 0.086975 | 0.07782 | 0.032043 | 0.073242 | -0.027466 | 0.068664 | -0.009156 | 0.09613 | 0.10986 | 3.5522 | 0.16479 | -119.3756 | -122.7768 | 3.4286 | 0.045776 | 3.5385 | 0.064087
5599.7969 | 122.8043 | -0.073242 | 122.699 | -0.035019 | 0.012728 | 0.0094208 | -0.0095766 | -0.00048286 | -0.011339 | -0.0038772 | -0.005371 | 0.019113 | 0.04178 | -0.025532 | 0.010412 | 0.02311 | -0.0023435 | 3.3829 | 3.36 | 3.3188 | 3.3463 | 3.479 | 3.3371 | 3.392 | 0.009155 | 0 | -0.050354 | 0.013733 | 0.10071 | 0.07782 | 0.082397 | 3.392 | -119.339 | -119.3527 | 3.5522 | 3.4653 | 3.4103 | 0.073242 | 0.01831 | 0.022888 | -122.699 | -122.6852 | 0.17395 | 0.15564 | 0.15106 | 0.13275 | 0.12817 | 0.16022 | 0.027465 | 0.15106 | 0.064087 | 0.041198 | 0.050354 | 3.4332 | 0.073242 | -119.3802 | -122.7493 | 3.4195 | 0.086975 | 3.4561 | 0.082397
5601.5469 | 122.8271 | -0.082397 | 122.7219 | -0.01976 | 0.0095234 | 0.008139 | -0.0097904 | -0.0019781 | -0.010698 | -0.0053726 | -0.0084228 | 0.019113 | 0.041994 | -0.02126 | 0.010839 | 0.02311 | -0.0042661 | 3.3875 | 3.3691 | 3.3371 | 3.3463 | 3.4698 | 3.3463 | 3.4012 | 0.018311 | 0.009155 | -0.041199 | 0.009155 | 0.13275 | 0.10529 | 0.10529 | 3.4195 | -119.3527 | -119.3756 | 3.5522 | 3.4836 | 3.4286 | 0.064087 | 0.009155 | 0.041198 | -122.7127 | -122.7127 | 0.21515 | 0.18768 | 0.18768 | 0.14649 | 0.14649 | 0.13275 | 0.009155 | 0.17395 | 0.050354 | 0.032044 | 0.050354 | 3.4515 | 0.091552 | -119.3848 | -122.7631 | 3.4286 | 0.091552 | 3.4698 | 0.10071
5603.25 | 122.8638 | -0.059509 | 122.7127 | -0.02739 | 0.0084552 | 0.010703 | -0.010218 | 0.0014397 | -0.011339 | -0.0019546 | -0.0023192 | 0.019967 | 0.039858 | -0.019337 | 0.0093439 | 0.022255 | -0.0023435 | 3.5019 | 3.4149 | 3.4103 | 3.4698 | 3.6163 | 3.4927 | 3.5248 | 0.10529 | 0.009155 | -0.027466 | 0.041199 | 0.17395 | 0.14191 | 0.12817 | 3.4698 | -119.2978 | -119.2429 | 3.6758 | 3.5843 | 3.5522 | 0.11444 | 0.082398 | 0.032043 | -122.7036 | -122.6715 | 0.23346 | 0.18768 | 0.20142 | 0.15564 | 0.16937 | 0.20599 | 0.05951 | 0.20142 | 0.068665 | 0.004578 | 0.036621 | 3.4744 | 0.068664 | -119.3024 | -122.7402 | 3.5294 | 0.10071 | 3.5614 | 0.16479
5604.9844 | 122.7585 | -0.10071 | 122.7264 | -0.012131 | 0.013155 | 0.0089936 | -0.008295 | 0.0035761 | -0.011553 | -0.0025956 | -0.0084228 | 0.02189 | 0.037935 | -0.011433 | 0.012548 | 0.021828 | -0.0061887 | 3.4561 | 3.4927 | 3.4103 | 3.3554 | 3.4515 | 3.3829 | 3.392 | -0.068665 | 0.036621 | -0.073242 | -0.068665 | 0.059509 | 0.027466 | 0.041199 | 3.511 | -119.2337 | -119.371 | 3.5522 | 3.4927 | 3.4836 | -0.01831 | -0.027465 | 0.027466 | -122.6898 | -122.7951 | 0.16022 | 0.14191 | 0.12817 | 0.11444 | 0.10071 | 0.041199 | -0.054931 | 0.13275 | 0.004577 | 0.082398 | 0.10986 | 3.5934 | 0.13733 | -119.3161 | -122.7997 | 3.4561 | 0.032043 | 3.5568 | 0.032043
5606.7188 | 122.731 | -0.10071 | 122.7448 | -0.012131 | 0.017427 | 0.0096344 | -0.0063724 | -0.0019781 | -0.0098438 | -0.0064408 | -0.011475 | 0.024026 | 0.041567 | -0.013356 | 0.013403 | 0.022255 | -0.0068295 | 3.3875 | 3.392 | 3.3234 | 3.2684 | 3.3783 | 3.2501 | 3.2822 | -0.054932 | 0.041199 | -0.064087 | -0.086975 | -0.004578 | -0.027466 | 0.027466 | 3.4241 | -119.3527 | -119.4763 | 3.479 | 3.3829 | 3.3508 | -0.041198 | -0.073242 | 0.036621 | -122.7036 | -122.8317 | 0.09613 | 0.12817 | 0.073242 | 0.091553 | 0.036621 | 0.054932 | -0.054931 | 0.059509 | -0.022888 | 0.068665 | 0.10529 | 3.4927 | 0.14191 | -119.4214 | -122.8088 | 3.3691 | 0.013733 | 3.4882 | 0.045776
5608.4531 | 122.7585 | -0.09613 | 122.7127 | -0.012131 | 0.014223 | 0.0089936 | -0.008295 | 0.0033623 | -0.010271 | -0.0025956 | -0.011475 | 0.021035 | 0.04114 | -0.017201 | 0.014471 | 0.02311 | -0.0093931 | 3.4241 | 3.4012 | 3.3371 | 3.3371 | 3.4515 | 3.3096 | 3.3325 | 0 | 0.045776 | -0.050354 | -0.032043 | 0.041199 | 0.013733 | 0.045776 | 3.4332 | -119.3115 | -119.3756 | 3.5477 | 3.4287 | 3.4058 | -0.004577 | -0.027466 | 0.045776 | -122.6669 | -122.7448 | 0.13733 | 0.14191 | 0.10986 | 0.09613 | 0.064087 | 0.11444 | 0 | 0.091553 | 0.018311 | 0.064087 | 0.09613 | 3.4973 | 0.14191 | -119.3756 | -122.7631 | 3.4332 | 0.064087 | 3.5202 | 0.09613
5610.1719 | 122.7768 | -0.10071 | 122.7127 | -0.01976 | 0.011019 | 0.011771 | -0.010004 | 0.00037174 | -0.010057 | -0.0025956 | -0.011475 | 0.019113 | 0.04178 | -0.016347 | 0.0099847 | 0.023537 | -0.0044797 | 3.4927 | 3.4287 | 3.3737 | 3.4241 | 3.566 | 3.4561 | 3.4698 | 0.009155 | 0.032043 | -0.054932 | -0.032043 | 0.07782 | 0.045776 | 0.050354 | 3.4744 | -119.2841 | -119.2886 | 3.6667 | 3.5706 | 3.5568 | 0.096131 | 0.082398 | 0.045776 | -122.6807 | -122.7448 | 0.17853 | 0.15106 | 0.14648 | 0.10529 | 0.10071 | 0.19226 | 0.050354 | 0.13275 | 0.022889 | 0.054932 | 0.086975 | 3.5294 | 0.13275 | -119.339 | -122.7676 | 3.5248 | 0.068665 | 3.5934 | 0.10986
5611.875 | 122.7722 | -0.10986 | 122.699 | -0.01976 | 0.014864 | 0.0092072 | -0.008295 | -0.0039007 | -0.0098438 | -0.0036636 | -0.0084228 | 0.02189 | 0.040712 | -0.012074 | 0.011907 | 0.021828 | -0.0051205 | 3.3096 | 3.3417 | 3.241 | 3.2181 | 3.3371 | 3.1998 | 3.2364 | -0.045776 | 0.032043 | -0.07782 | -0.045776 | 0.041199 | 0.004578 | 0.059509 | 3.3508 | -119.3573 | -119.4809 | 3.447 | 3.3463 | 3.3096 | -0.004578 | -0.041199 | 0.032043 | -122.6669 | -122.7448 | 0.15106 | 0.16937 | 0.11444 | 0.13733 | 0.082398 | 0.09613 | -0.022888 | 0.11902 | 0.032044 | 0.10071 | 0.10986 | 3.4515 | 0.14191 | -119.458 | -122.7768 | 3.3279 | 0.064087 | 3.4195 | 0.064087
5613.5938 | 122.7402 | -0.10529 | 122.7264 | -0.012131 | 0.014223 | 0.0096344 | -0.0087222 | 0.0059259 | -0.00963 | -0.0072952 | -0.011475 | 0.01954 | 0.04178 | -0.01421 | 0.011694 | 0.021401 | -0.0049069 | 3.3829 | 3.3875 | 3.3234 | 3.273 | 3.392 | 3.2455 | 3.2959 | -0.022888 | 0.045776 | -0.050354 | -0.073242 | 0.032043 | -0.013733 | 0.032043 | 3.4287 | -119.339 | -119.4534 | 3.4973 | 3.4012 | 3.3508 | -0.027466 | -0.07782 | 0.054932 | -122.6807 | -122.7997 | 0.13733 | 0.13733 | 0.091553 | 0.082397 | 0.036621 | 0.068665 | -0.050354 | 0.082397 | -0.022888 | 0.064087 | 0.09613 | 3.4927 | 0.15106 | -119.4031 | -122.7768 | 3.3783 | 0.032044 | 3.4882 | 0.082398
5615.3438 | 122.85 | -0.064087 | 122.7081 | -0.01976 | 0.008028 | 0.0079254 | -0.011499 | 0.0016535 | -0.01198 | -0.0021682 | -0.0023192 | 0.018899 | 0.042635 | -0.0266 | 0.011694 | 0.023537 | -0.00042085 | 3.4698 | 3.4149 | 3.36 | 3.447 | 3.5706 | 3.4607 | 3.479 | 0.09613 | 0 | -0.027466 | 0.027466 | 0.16479 | 0.12817 | 0.11444 | 3.4241 | -119.2932 | -119.2612 | 3.6346 | 3.5431 | 3.5248 | 0.11902 | 0.10071 | 0.036621 | -122.7081 | -122.6807 | 0.22888 | 0.17853 | 0.19226 | 0.14191 | 0.15564 | 0.21057 | 0.086975 | 0.19226 | 0.054932 | 0.054932 | 0.027466 | 3.479 | 0.064087 | -119.3481 | -122.7356 | 3.511 | 0.091553 | 3.5339 | 0.16022
5617.0625 | 122.7448 | -0.1236 | 122.7219 | -0.01976 | 0.013582 | 0.0060028 | -0.0061588 | -5.5462e-05 | -0.008562 | -0.0057998 | -0.011475 | 0.021035 | 0.040712 | -0.011433 | 0.012975 | 0.024178 | -0.00020725 | 3.3737 | 3.36 | 3.3005 | 3.273 | 3.3966 | 3.2501 | 3.273 | -0.041199 | 0.041199 | -0.041199 | -0.068665 | 0.018311 | -0.022888 | 0.027466 | 3.4241 | -119.3619 | -119.4489 | 3.5202 | 3.3966 | 3.3737 | -0.027466 | -0.050354 | 0.082397 | -122.6807 | -122.7905 | 0.14191 | 0.15106 | 0.10071 | 0.068665 | 0.018311 | 0.09613 | -0.027466 | 0.05951 | -0.027466 | 0.059509 | 0.082398 | 3.4836 | 0.16479 | -119.4214 | -122.7631 | 3.3966 | 0.054931 | 3.4973 | 0.082397
5618.7969 | 122.9141 | -0.068665 | 122.6898 | -0.01976 | 0.009737 | 0.0096344 | -0.01449 | 0.0014397 | -0.010271 | -0.0025956 | -0.0084228 | 0.019754 | 0.038149 | -0.020192 | 0.0093439 | 0.024819 | -0.0049069 | 3.4424 | 3.3554 | 3.3417 | 3.4103 | 3.5751 | 3.4378 | 3.4607 | 0.13275 | -0.009155 | -0.036621 | 0.064087 | 0.19226 | 0.15564 | 0.14191 | 3.4103 | -119.3344 | -119.2795 | 3.6438 | 3.5294 | 3.5065 | 0.11902 | 0.09613 | 0.032044 | -122.699 | -122.6257 | 0.26093 | 0.21057 | 0.22431 | 0.17853 | 0.19226 | 0.23346 | 0.068664 | 0.22888 | 0.10071 | 0.013733 | 0.027466 | 3.4241 | 0.05951 | -119.3481 | -122.7264 | 3.479 | 0.13275 | 3.511 | 0.20142
5620.5156 | 122.7951 | -0.11444 | 122.7448 | -0.01976 | 0.010805 | 0.0072846 | -0.0087222 | -0.0011237 | -0.012834 | -0.0043046 | -0.005371 | 0.020822 | 0.04114 | -0.017201 | 0.012975 | 0.022683 | -0.0010617 | 3.4241 | 3.4607 | 3.3508 | 3.3417 | 3.4424 | 3.3463 | 3.3691 | -0.059509 | 0.041199 | -0.073242 | -0.050354 | 0.073242 | 0.027466 | 0.059509 | 3.4653 | -119.2841 | -119.4031 | 3.5568 | 3.4836 | 3.4607 | 0.018311 | -0.004578 | 0.041199 | -122.7036 | -122.7951 | 0.18768 | 0.17395 | 0.14191 | 0.13275 | 0.10071 | 0.091553 | -0.009155 | 0.14648 | 0.022888 | 0.10986 | 0.11444 | 3.5751 | 0.15564 | -119.3939 | -122.818 | 3.4561 | 0.064087 | 3.5385 | 0.054932
5622.2969 | 122.818 | -0.073242 | 122.7081 | -0.02739 | 0.0099506 | 0.0072846 | -0.011072 | -0.0019781 | -0.0083484 | -0.0036636 | -0.0084228 | 0.01719 | 0.041353 | -0.026173 | 0.010412 | 0.022896 | -0.0044797 | 3.3325 | 3.3005 | 3.2822 | 3.273 | 3.4103 | 3.2867 | 3.3417 | 0.013733 | 0.009155 | -0.041199 | 0 | 0.10986 | 0.073242 | 0.086975 | 3.3554 | -119.4077 | -119.4351 | 3.4836 | 3.4149 | 3.36 | 0.059509 | 0.004577 | 0.032043 | -122.699 | -122.7081 | 0.18311 | 0.16022 | 0.14648 | 0.12817 | 0.11444 | 0.12817 | -0.009156 | 0.15106 | 0.041199 | 0.01831 | 0.050354 | 3.3737 | 0.082397 | -119.426 | -122.7493 | 3.3463 | 0.073242 | 3.4058 | 0.086975
5624.0156 | 122.8455 | -0.068665 | 122.7402 | -0.01976 | 0.0099506 | 0.0083526 | -0.0091494 | 0.0020807 | -0.0094164 | -0.0053726 | -0.0084228 | 0.019967 | 0.042208 | -0.016987 | 0.0099847 | 0.024178 | -0.0012753 | 3.4607 | 3.3691 | 3.3554 | 3.4195 | 3.5339 | 3.4287 | 3.4561 | 0.086975 | 0.004578 | -0.027466 | 0.009155 | 0.15106 | 0.1236 | 0.1236 | 3.4241 | -119.371 | -119.3207 | 3.6026 | 3.5248 | 3.4973 | 0.10071 | 0.073242 | 0.041199 | -122.7356 | -122.731 | 0.21973 | 0.19226 | 0.19226 | 0.15106 | 0.15106 | 0.17853 | 0.064087 | 0.17853 | 0.036621 | 0.013733 | 0.032044 | 3.4378 | 0.073243 | -119.3848 | -122.7676 | 3.4882 | 0.07782 | 3.5294 | 0.15564
5625.7344 | 122.7585 | -0.1236 | 122.731 | -0.012131 | 0.011446 | 0.0077118 | -0.0074404 | -0.0019781 | -0.011339 | -0.0036636 | -0.005371 | 0.020395 | 0.042208 | -0.01421 | 0.010198 | 0.022255 | -0.0036253 | 3.3875 | 3.4149 | 3.3371 | 3.3142 | 3.4287 | 3.3188 | 3.3508 | -0.050354 | 0.036621 | -0.07782 | -0.07782 | 0.022888 | 0.009155 | 0.027466 | 3.4607 | -119.3161 | -119.4168 | 3.5522 | 3.4744 | 3.4424 | 0.013733 | -0.01831 | 0.045776 | -122.6944 | -122.8088 | 0.14648 | 0.15106 | 0.13275 | 0.10529 | 0.086975 | 0.091553 | -0.022888 | 0.10071 | 0 | 0.07782 | 0.11444 | 3.5385 | 0.16022 | -119.3939 | -122.8088 | 3.4378 | 0.045776 | 3.511 | 0.073242
5627.4531 | 122.7676 | -0.11902 | 122.7264 | -0.012131 | 0.010591 | 0.0072846 | -0.0097904 | -0.0017645 | -0.011766 | -0.0036636 | -0.0084228 | 0.020181 | 0.04114 | -0.01656 | 0.011694 | 0.023323 | -0.0046933 | 3.3966 | 3.4653 | 3.3646 | 3.3279 | 3.4195 | 3.3188 | 3.36 | -0.068665 | 0.050354 | -0.073242 | -0.068665 | 0.036621 | 0 | 0.036621 | 3.4836 | -119.2612 | -119.3985 | 3.5385 | 3.479 | 3.4378 | -0.004578 | -0.045776 | 0.045777 | -122.6761 | -122.7951 | 0.15564 | 0.15564 | 0.11902 | 0.10986 | 0.073242 | 0.054932 | -0.036621 | 0.10986 | 0.004577 | 0.10071 | 0.1236 | 3.5843 | 0.16937 | -119.3619 | -122.7997 | 3.447 | 0.050354 | 3.5156 | 0.050354
5629.1719 | 122.7859 | -0.091553 | 122.7264 | 0.0031279 | 0.015932 | 0.00878 | -0.0063724 | 0.0059259 | -0.0092028 | -0.0025956 | -0.011475 | 0.022958 | 0.042208 | -0.019124 | 0.011053 | 0.022683 | -0.0042661 | 3.3783 | 3.3508 | 3.2822 | 3.2959 | 3.4195 | 3.2776 | 3.3188 | 0.018311 | 0.022888 | -0.050354 | -0.013733 | 0.073242 | 0.022888 | 0.054932 | 3.3737 | -119.3756 | -119.4305 | 3.511 | 3.4103 | 3.3691 | 0.036621 | -0.004578 | 0.041199 | -122.7036 | -122.7402 | 0.16479 | 0.14649 | 0.11444 | 0.10529 | 0.073242 | 0.13733 | 0.013732 | 0.1236 | 0.036621 | 0.068664 | 0.073242 | 3.4424 | 0.11444 | -119.4443 | -122.7768 | 3.3875 | 0.07782 | 3.4698 | 0.10986
5630.9062 | 122.7997 | -0.10529 | 122.7219 | -0.012131 | 0.014223 | 0.0089936 | -0.0074404 | -0.0034735 | -0.0092028 | -0.0038772 | -0.0084228 | 0.020395 | 0.040499 | -0.014424 | 0.012975 | 0.024391 | -0.0059751 | 3.2776 | 3.2776 | 3.2135 | 3.1586 | 3.2684 | 3.1631 | 3.1998 | -0.045776 | 0.032043 | -0.059509 | -0.041199 | 0.036621 | -0.004578 | 0.045776 | 3.3188 | -119.4443 | -119.5633 | 3.3737 | 3.3051 | 3.2684 | -0.013733 | -0.050354 | 0.045777 | -122.6898 | -122.7631 | 0.14191 | 0.15106 | 0.10071 | 0.10528 | 0.054931 | 0.054932 | -0.054932 | 0.09613 | 0.01831 | 0.064087 | 0.091552 | 3.3829 | 0.13733 | -119.5084 | -122.7814 | 3.2639 | 0.064087 | 3.3829 | 0.05951
5632.6406 | 122.8592 | -0.064087 | 122.6898 | -0.01976 | 0.012941 | 0.012198 | -0.0055178 | 0.0016535 | -0.010057 | -0.0043046 | -0.0084228 | 0.019967 | 0.042421 | -0.017628 | 0.012548 | 0.024178 | -0.00084805 | 3.273 | 3.2547 | 3.2181 | 3.2318 | 3.3646 | 3.2272 | 3.2684 | 0.082397 | 0 | -0.036621 | 0.064087 | 0.14191 | 0.11902 | 0.15106 | 3.2822 | -119.4351 | -119.458 | 3.4287 | 3.3325 | 3.2913 | 0.050354 | 0.009155 | 0.027466 | -122.6898 | -122.6257 | 0.20599 | 0.21515 | 0.18311 | 0.18768 | 0.15564 | 0.14648 | 0.013733 | 0.17853 | 0.10071 | 0.036621 | 0.036621 | 3.3188 | 0.064087 | -119.4717 | -122.7264 | 3.2959 | 0.12817 | 3.3371 | 0.14648
5634.3906 | 122.818 | -0.091553 | 122.6898 | -0.02739 | 0.012514 | 0.0085662 | -0.0085086 | -0.00048286 | -0.0092028 | -0.0047318 | -0.005371 | 0.019754 | 0.040926 | -0.01656 | 0.0095575 | 0.02546 | -0.0057615 | 3.3051 | 3.2684 | 3.2455 | 3.2547 | 3.3737 | 3.2547 | 3.2959 | 0.036621 | -0.004578 | -0.036621 | -0.004578 | 0.12817 | 0.073242 | 0.091553 | 3.3371 | -119.4214 | -119.4351 | 3.4653 | 3.3875 | 3.3463 | 0.050354 | 0.009156 | 0.054932 | -122.6944 | -122.6944 | 0.21973 | 0.18311 | 0.16479 | 0.12817 | 0.10986 | 0.12817 | 0.009156 | 0.1648 | 0.032043 | 0.022889 | 0.032043 | 3.36 | 0.086975 | -119.4443 | -122.7264 | 3.3463 | 0.086975 | 3.3966 | 0.12817
5636.0938 | 122.7859 | -0.10986 | 122.7356 | -0.01976 | 0.010591 | 0.009848 | -0.0078676 | 0.00015814 | -0.010912 | -0.0025956 | -0.005371 | 0.021035 | 0.042208 | -0.010365 | 0.012334 | 0.021614 | -0.0027707 | 3.4012 | 3.4058 | 3.3096 | 3.3051 | 3.4103 | 3.3188 | 3.3279 | -0.022888 | 0.036621 | -0.054932 | -0.036621 | 0.068665 | 0.022888 | 0.07782 | 3.4195 | -119.3298 | -119.4305 | 3.5202 | 3.4378 | 3.4286 | 0.018311 | 0.009156 | 0.054931 | -122.699 | -122.7722 | 0.17853 | 0.18768 | 0.13275 | 0.13275 | 0.07782 | 0.10071 | -0.004577 | 0.1236 | 0.018311 | 0.096131 | 0.091553 | 3.5156 | 0.14648 | -119.426 | -122.7905 | 3.4149 | 0.073242 | 3.511 | 0.086975
5637.7969 | 122.8409 | -0.09613 | 122.6944 | -0.01976 | 0.012728 | 0.008139 | -0.0067996 | 0.0014397 | -0.00963 | -0.0030228 | -0.0084228 | 0.019326 | 0.039003 | -0.015065 | 0.011266 | 0.021614 | -0.0070433 | 3.2455 | 3.2867 | 3.1998 | 3.1494 | 3.2867 | 3.1448 | 3.1815 | -0.004578 | 0.022888 | -0.050354 | -0.013733 | 0.091553 | 0.045776 | 0.07782 | 3.2959 | -119.4077 | -119.545 | 3.3829 | 3.2776 | 3.241 | -0.01831 | -0.054932 | 0.045776 | -122.6715 | -122.7081 | 0.18768 | 0.17395 | 0.14191 | 0.12817 | 0.09613 | 0.086975 | -0.050354 | 0.14191 | 0.036621 | 0.086975 | 0.073242 | 3.3829 | 0.11902 | -119.4946 | -122.7448 | 3.2455 | 0.082397 | 3.3417 | 0.091552
5639.5156 | 122.8867 | -0.07782 | 122.6807 | -0.01976 | 0.010805 | 0.00643 | -0.011927 | -0.0017645 | -0.01198 | -0.0047318 | -0.005371 | 0.017617 | 0.041994 | -0.025746 | 0.010626 | 0.022255 | -0.0046933 | 3.3371 | 3.3051 | 3.2547 | 3.3096 | 3.4607 | 3.3371 | 3.3737 | 0.086975 | -0.009155 | -0.036621 | 0.036621 | 0.17853 | 0.13733 | 0.14191 | 3.3325 | -119.3756 | -119.371 | 3.5385 | 3.4515 | 3.4149 | 0.11902 | 0.082397 | 0.041199 | -122.6898 | -122.644 | 0.25635 | 0.21973 | 0.21515 | 0.17853 | 0.17395 | 0.20599 | 0.054931 | 0.21515 | 0.073242 | 0.050354 | 0.027466 | 3.3829 | 0.068665 | -119.426 | -122.7173 | 3.3875 | 0.11444 | 3.4149 | 0.16479
5641.2812 | 122.7493 | -0.10986 | 122.731 | -0.012131 | 0.015718 | 0.0096344 | -0.0055178 | 0.0035761 | -0.010057 | -0.0036636 | -0.005371 | 0.018258 | 0.040285 | -0.013356 | 0.010839 | 0.022469 | -0.0025571 | 3.2455 | 3.2913 | 3.2135 | 3.1311 | 3.2501 | 3.1265 | 3.1494 | -0.073242 | 0.036621 | -0.059509 | -0.064087 | 0.013733 | -0.018311 | 0.036621 | 3.3234 | -119.4397 | -119.5999 | 3.36 | 3.2593 | 3.2364 | -0.064087 | -0.086975 | 0.050354 | -122.6944 | -122.7951 | 0.1236 | 0.14648 | 0.091552 | 0.09613 | 0.041198 | 0.036621 | -0.082397 | 0.073242 | -0.004578 | 0.07782 | 0.09613 | 3.4012 | 0.14648 | -119.5175 | -122.7905 | 3.241 | 0.045776 | 3.3554 | 0.036621
5642.9844 | 122.8409 | -0.054932 | 122.7219 | -0.012131 | 0.013155 | 0.0089936 | -0.0095766 | -0.00048286 | -0.010057 | -0.0028092 | -0.005371 | 0.018045 | 0.040285 | -0.024678 | 0.010412 | 0.023537 | 0.00086095 | 3.3096 | 3.2318 | 3.2043 | 3.241 | 3.3829 | 3.2043 | 3.2639 | 0.09613 | 0.004578 | -0.032043 | 0.027466 | 0.13275 | 0.086975 | 0.10071 | 3.2593 | -119.4901 | -119.4809 | 3.4378 | 3.3188 | 3.2593 | 0.059509 | 0 | 0.022889 | -122.7173 | -122.6944 | 0.18768 | 0.15564 | 0.14191 | 0.13275 | 0.11902 | 0.17853 | 0.036621 | 0.16479 | 0.059509 | 0.027466 | 0.036621 | 3.2867 | 0.05951 | -119.5175 | -122.7539 | 3.2959 | 0.082398 | 3.3646 | 0.15106
5644.7031 | 122.8683 | -0.068665 | 122.7173 | -0.012131 | 0.0088824 | 0.0077118 | -0.012567 | 0.0027215 | -0.011125 | -0.0072952 | -0.005371 | 0.018899 | 0.040712 | -0.022969 | 0.0097711 | 0.025673 | -0.0040525 | 3.3966 | 3.3051 | 3.3051 | 3.3829 | 3.5339 | 3.3875 | 3.4195 | 0.10529 | 0.009155 | -0.041199 | 0.027466 | 0.17395 | 0.15106 | 0.13275 | 3.3737 | -119.4122 | -119.3344 | 3.6026 | 3.4882 | 3.4561 | 0.11444 | 0.082397 | 0.027466 | -122.7081 | -122.6898 | 0.24261 | 0.20142 | 0.21973 | 0.17395 | 0.19226 | 0.22888 | 0.07782 | 0.21515 | 0.068665 | 0 | 0.050354 | 3.3737 | 0.07782 | -119.4122 | -122.7585 | 3.4515 | 0.096131 | 3.4653 | 0.17395
5646.4219 | 122.7997 | -0.10529 | 122.7219 | -0.01976 | 0.013155 | 0.0077118 | -0.0072268 | 0.0040033 | -0.01198 | -0.005159 | -0.011475 | 0.022103 | 0.04114 | -0.011647 | 0.012334 | 0.02076 | -0.0017027 | 3.3554 | 3.3829 | 3.2867 | 3.2822 | 3.3646 | 3.2959 | 3.3005 | -0.041199 | 0.041199 | -0.064087 | -0.036621 | 0.064087 | 0.032043 | 0.082397 | 3.392 | -119.339 | -119.4397 | 3.4698 | 3.4058 | 3.4012 | 0.013733 | 0.009155 | 0.041199 | -122.6807 | -122.7585 | 0.16937 | 0.18768 | 0.13733 | 0.14648 | 0.09613 | 0.07782 | -0.004577 | 0.12817 | 0.027466 | 0.096131 | 0.10529 | 3.4882 | 0.14649 | -119.4351 | -122.7859 | 3.3875 | 0.068665 | 3.4607 | 0.064087
5648.1406 | 122.7402 | -0.10529 | 122.7219 | -0.01976 | 0.015505 | 0.011771 | -0.006586 | 0.0010125 | -0.011125 | -0.0032364 | -0.0084228 | 0.020822 | 0.04114 | -0.015492 | 0.0099847 | 0.022042 | -0.0070433 | 3.2364 | 3.273 | 3.186 | 3.1265 | 3.2135 | 3.1036 | 3.1448 | -0.07782 | 0.032043 | -0.073242 | -0.059509 | 0.009155 | -0.032043 | 0.027466 | 3.2913 | -119.4489 | -119.5953 | 3.3188 | 3.2501 | 3.2089 | -0.041199 | -0.082397 | 0.032044 | -122.6898 | -122.7814 | 0.11444 | 0.13275 | 0.073243 | 0.10071 | 0.041199 | 0.027466 | -0.059509 | 0.082397 | 0.013733 | 0.086975 | 0.10529 | 3.3783 | 0.13733 | -119.5358 | -122.7951 | 3.2318 | 0.045777 | 3.3417 | 0.027466
5649.8594 | 122.8546 | -0.073242 | 122.7036 | -0.01976 | 0.011446 | 0.0092072 | -0.011713 | -0.00026906 | -0.010912 | -0.000673 | -0.0084228 | 0.017831 | 0.042208 | -0.01891 | 0.011053 | 0.020974 | -0.0049069 | 3.3691 | 3.3096 | 3.2867 | 3.3463 | 3.4927 | 3.3691 | 3.3783 | 0.086975 | 0.013733 | -0.027466 | 0.022888 | 0.16937 | 0.13275 | 0.1236 | 3.36 | -119.3939 | -119.3573 | 3.566 | 3.4515 | 3.4424 | 0.091553 | 0.082398 | 0.045776 | -122.6898 | -122.6807 | 0.24261 | 0.19684 | 0.20599 | 0.15106 | 0.16022 | 0.20599 | 0.059509 | 0.19684 | 0.050354 | 0.022888 | 0.041199 | 3.3829 | 0.086975 | -119.4168 | -122.731 | 3.4195 | 0.09613 | 3.4424 | 0.16022
5651.5781 | 122.8134 | -0.09613 | 122.7173 | -0.01976 | 0.013796 | 0.00878 | -0.0074404 | 0.0012261 | -0.010485 | -0.0049454 | -0.0084228 | 0.01954 | 0.040712 | -0.012715 | 0.012121 | 0.022469 | -0.0034117 | 3.2135 | 3.2364 | 3.1586 | 3.1174 | 3.2272 | 3.1082 | 3.1448 | -0.013733 | 0.022888 | -0.050354 | 0.009155 | 0.07782 | 0.054932 | 0.082397 | 3.2547 | -119.4809 | -119.5999 | 3.3234 | 3.241 | 3.2043 | -0.013733 | -0.050354 | 0.045776 | -122.6944 | -122.7081 | 0.17395 | 0.17853 | 0.15106 | 0.13275 | 0.10529 | 0.068665 | -0.041198 | 0.12817 | 0.059509 | 0.07782 | 0.073242 | 3.3325 | 0.11902 | -119.5587 | -122.7676 | 3.2135 | 0.10528 | 3.3096 | 0.082397
5653.3594 | 122.7951 | -0.10071 | 122.7448 | -0.012131 | 0.014864 | 0.008139 | -0.0063724 | -0.0011237 | -0.0089892 | -0.0038772 | -0.0084228 | 0.02189 | 0.039858 | -0.014638 | 0.011694 | 0.022469 | -0.0049069 | 3.3279 | 3.2867 | 3.2272 | 3.2455 | 3.3646 | 3.2364 | 3.2639 | 0.027466 | 0.032043 | -0.045776 | -0.013733 | 0.09613 | 0.054932 | 0.07782 | 3.3279 | -119.458 | -119.4992 | 3.4653 | 3.3646 | 3.3371 | 0.036621 | 0.009155 | 0.054932 | -122.7127 | -122.7585 | 0.19684 | 0.17853 | 0.15564 | 0.1236 | 0.10071 | 0.13733 | 0.01831 | 0.14191 | 0.032043 | 0.059509 | 0.077819 | 3.3875 | 0.13275 | -119.5175 | -122.7905 | 3.3463 | 0.086975 | 3.4287 | 0.12817
5655.0781 | 122.8455 | -0.086975 | 122.7356 | -0.01976 | 0.0099506 | 0.00878 | -0.0078676 | 0.00058534 | -0.010057 | -0.0019546 | -0.0084228 | 0.017617 | 0.041353 | -0.02126 | 0.0091303 | 0.022896 | 0.0029971 | 3.2593 | 3.2364 | 3.1906 | 3.1906 | 3.3325 | 3.1998 | 3.2547 | 0.027466 | -0.004578 | -0.054932 | 0 | 0.10986 | 0.09613 | 0.086975 | 3.2776 | -119.4992 | -119.545 | 3.4195 | 3.3417 | 3.2867 | 0.064087 | 0.009155 | 0.032043 | -122.7402 | -122.7356 | 0.19684 | 0.17395 | 0.1831 | 0.14191 | 0.15106 | 0.14191 | 0 | 0.16479 | 0.054932 | 0.045776 | 0.050354 | 3.3234 | 0.082397 | -119.545 | -122.7905 | 3.2776 | 0.086975 | 3.3463 | 0.11444
5656.7812 | 122.7585 | -0.10986 | 122.7448 | -0.01976 | 0.010378 | 0.0083526 | -0.009363 | -0.0043281 | -0.013475 | -0.005159 | -0.0084228 | 0.021249 | 0.040712 | -0.021687 | 0.011694 | 0.022896 | -0.0021299 | 3.3325 | 3.3188 | 3.2593 | 3.2455 | 3.3737 | 3.2639 | 3.2776 | -0.041199 | 0.027466 | -0.032043 | -0.073242 | 0.050354 | 0.013733 | 0.013733 | 3.3691 | -119.426 | -119.4992 | 3.4836 | 3.3875 | 3.3737 | 0.018311 | 0.004578 | 0.07782 | -122.7173 | -122.818 | 0.16022 | 0.1236 | 0.1236 | 0.045776 | 0.045776 | 0.11444 | -0.013733 | 0.082397 | -0.041199 | 0.05951 | 0.059509 | 3.4286 | 0.13733 | -119.4855 | -122.7768 | 3.3554 | 0.036621 | 3.4424 | 0.068664
5658.5156 | 122.7722 | -0.1236 | 122.7402 | -0.01976 | 0.010378 | 0.0077118 | -0.008295 | -0.00091006 | -0.010057 | -0.0047318 | -0.005371 | 0.01954 | 0.04178 | -0.020833 | 0.012121 | 0.02311 | -0.0010617 | 3.3142 | 3.36 | 3.2639 | 3.2318 | 3.3371 | 3.2547 | 3.2639 | -0.073242 | 0.054932 | -0.068665 | -0.073242 | 0.036621 | 0 | 0.045776 | 3.3875 | -119.3802 | -119.5084 | 3.4607 | 3.3875 | 3.3783 | 0 | -0.009155 | 0.054931 | -122.6852 | -122.8134 | 0.16022 | 0.16937 | 0.1236 | 0.11444 | 0.068665 | 0.073242 | -0.032043 | 0.10529 | -0.004577 | 0.09613 | 0.1236 | 3.4836 | 0.17853 | -119.4763 | -122.8088 | 3.3554 | 0.050354 | 3.4378 | 0.050354
5660.2812 | 122.8775 | -0.054932 | 122.699 | -0.012131 | 0.011232 | 0.00878 | -0.011072 | -0.0041145 | -0.0094164 | -0.0070816 | -0.005371 | 0.018472 | 0.038576 | -0.014851 | 0.010626 | 0.021828 | -0.00020725 | 3.3554 | 3.2822 | 3.2593 | 3.3417 | 3.4882 | 3.3417 | 3.3691 | 0.10986 | 0.018311 | -0.041199 | 0.041199 | 0.17395 | 0.14648 | 0.13275 | 3.3142 | -119.4168 | -119.3573 | 3.5431 | 3.4241 | 3.3966 | 0.10986 | 0.082398 | 0.013733 | -122.6807 | -122.6578 | 0.22888 | 0.18768 | 0.20142 | 0.17395 | 0.18768 | 0.22888 | 0.082398 | 0.21515 | 0.082398 | 0.022889 | 0.05951 | 3.3371 | 0.073243 | -119.4397 | -122.7402 | 3.3966 | 0.096131 | 3.4103 | 0.16479
5661.9844 | 122.818 | -0.10071 | 122.7219 | -0.02739 | 0.013369 | 0.0089936 | -0.0072268 | 0.0016535 | -0.010271 | -0.0045182 | -0.0084228 | 0.020822 | 0.040071 | -0.011647 | 0.012334 | 0.02311 | -0.0040525 | 3.3188 | 3.3051 | 3.2318 | 3.2135 | 3.3508 | 3.2227 | 3.2501 | 0.022888 | 0.018311 | -0.032043 | -0.009155 | 0.082397 | 0.054932 | 0.07782 | 3.3325 | -119.4168 | -119.5084 | 3.4515 | 3.3508 | 3.3234 | 0.01831 | -0.009156 | 0.068665 | -122.7036 | -122.731 | 0.18311 | 0.17853 | 0.15564 | 0.10986 | 0.086975 | 0.11902 | -0.018311 | 0.11444 | 0.022888 | 0.073242 | 0.050354 | 3.4058 | 0.11902 | -119.4901 | -122.7539 | 3.3142 | 0.091553 | 3.4195 | 0.1236
5663.6875 | 122.8912 | -0.073242 | 122.7036 | -0.01976 | 0.016146 | 0.010916 | -0.0080814 | -0.00069646 | -0.012194 | -0.00345 | -0.005371 | 0.019326 | 0.040926 | -0.012715 | 0.011053 | 0.024819 | -0.0055479 | 3.2227 | 3.1357 | 3.1265 | 3.1723 | 3.3005 | 3.154 | 3.2043 | 0.086975 | -0.009155 | -0.004578 | 0.064087 | 0.16479 | 0.1236 | 0.14191 | 3.1998 | -119.5679 | -119.5312 | 3.3737 | 3.2776 | 3.2272 | 0.07782 | 0.027466 | 0.068664 | -122.7127 | -122.6395 | 0.23804 | 0.21515 | 0.19684 | 0.14649 | 0.12817 | 0.17395 | 0.045776 | 0.16937 | 0.068665 | 0.009155 | -0.004577 | 3.2089 | 0.064087 | -119.577 | -122.7081 | 3.2455 | 0.13733 | 3.2959 | 0.16022
5665.4062 | 122.8226 | -0.073242 | 122.7264 | -0.012131 | 0.010378 | 0.0077118 | -0.011072 | 0.0022943 | -0.010271 | -0.005159 | -0.011475 | 0.017831 | 0.040712 | -0.019978 | 0.011694 | 0.023323 | -0.0038389 | 3.2227 | 3.1677 | 3.1586 | 3.1677 | 3.2959 | 3.1723 | 3.2135 | 0.041199 | 0.004578 | -0.054932 | 0.004578 | 0.11444 | 0.07782 | 0.091553 | 3.2318 | -119.5587 | -119.5587 | 3.3691 | 3.2867 | 3.2455 | 0.054932 | 0.013733 | 0.01831 | -122.7219 | -122.7219 | 0.18768 | 0.16479 | 0.15106 | 0.14649 | 0.13275 | 0.13733 | 0.009156 | 0.16937 | 0.05951 | 0.009156 | 0.05951 | 3.241 | 0.07782 | -119.5679 | -122.7814 | 3.241 | 0.07782 | 3.2959 | 0.11444
5667.125 | 122.7951 | -0.11444 | 122.7448 | -0.035019 | 0.011019 | 0.0094208 | -0.007654 | -0.0034735 | -0.012834 | -0.0021682 | -0.0084228 | 0.019754 | 0.040926 | -0.0043835 | 0.011907 | 0.022042 | -0.0053343 | 3.3005 | 3.3279 | 3.2364 | 3.1998 | 3.3142 | 3.2272 | 3.2593 | -0.045776 | 0.041199 | -0.059509 | -0.054932 | 0.054932 | 0.022888 | 0.054932 | 3.3508 | -119.4168 | -119.545 | 3.4286 | 3.3737 | 3.3417 | 0.022888 | -0.009155 | 0.054932 | -122.7036 | -122.7997 | 0.16937 | 0.16937 | 0.13733 | 0.11444 | 0.082397 | 0.07782 | -0.036621 | 0.11444 | 0.004577 | 0.091553 | 0.10071 | 3.4424 | 0.15564 | -119.5084 | -122.8043 | 3.3142 | 0.059509 | 3.4149 | 0.068665
5668.8906 | 122.8546 | -0.07782 | 122.7173 | -0.02739 | 0.0073872 | 0.0083526 | -0.010645 | -0.0017645 | -0.012621 | -0.005159 | -0.005371 | 0.021035 | 0.041567 | -0.015065 | 0.0099847 | 0.022683 | -0.0036253 | 3.3279 | 3.2547 | 3.2272 | 3.2776 | 3.4241 | 3.3005 | 3.3325 | 0.064087 | 0.004578 | -0.041199 | 0.027466 | 0.15564 | 0.10529 | 0.10986 | 3.3051 | -119.4626 | -119.4397 | 3.5019 | 3.4103 | 3.3783 | 0.10529 | 0.073242 | 0.036621 | -122.7127 | -122.6898 | 0.23346 | 0.18768 | 0.18311 | 0.15106 | 0.14649 | 0.19684 | 0.050354 | 0.19684 | 0.068665 | 0.027466 | 0.045777 | 3.3325 | 0.082398 | -119.4901 | -122.7585 | 3.3554 | 0.10529 | 3.4058 | 0.14191
5670.6094 | 122.7539 | -0.11444 | 122.7264 | -0.02739 | 0.01465 | 0.010275 | -0.006586 | 0.0022943 | -0.0081348 | -0.0032364 | -0.0084228 | 0.021676 | 0.040499 | -0.010579 | 0.012762 | 0.02311 | -0.0042661 | 3.2593 | 3.2272 | 3.1631 | 3.1403 | 3.2547 | 3.1174 | 3.1403 | -0.027466 | 0.054932 | -0.073242 | -0.050354 | 0.032043 | -0.018311 | 0.041199 | 3.2776 | -119.4992 | -119.5862 | 3.3691 | 3.2547 | 3.2318 | -0.022888 | -0.045776 | 0.041199 | -122.6715 | -122.7768 | 0.14648 | 0.15564 | 0.09613 | 0.11444 | 0.054931 | 0.091553 | -0.022888 | 0.10529 | 0.022888 | 0.064087 | 0.12817 | 3.3417 | 0.16937 | -119.5633 | -122.7997 | 3.2547 | 0.064087 | 3.3737 | 0.086975
5672.375 | 122.7676 | -0.1236 | 122.7402 | -0.01976 | 0.01166 | 0.0077118 | -0.0095766 | 0.0012261 | -0.012194 | -0.0015274 | -0.011475 | 0.020181 | 0.04178 | -0.016774 | 0.011907 | 0.022255 | -0.0019163 | 3.3188 | 3.2684 | 3.2364 | 3.241 | 3.3691 | 3.2547 | 3.2776 | -0.027466 | 0.013733 | -0.050354 | -0.059509 | 0.050354 | 0.027466 | 0.032043 | 3.36 | -119.4717 | -119.4992 | 3.4927 | 3.4012 | 3.3783 | 0.041199 | 0.018311 | 0.073242 | -122.7264 | -122.7997 | 0.17395 | 0.15564 | 0.15106 | 0.082397 | 0.07782 | 0.13275 | 0.004578 | 0.10071 | -0.009155 | 0.032044 | 0.064087 | 3.392 | 0.13733 | -119.5038 | -122.7905 | 3.3646 | 0.064087 | 3.4424 | 0.09613
5674.0938 | 122.8592 | -0.086975 | 122.731 | -0.01976 | 0.011446 | 0.0077118 | -0.0095766 | -0.0021919 | -0.010912 | -0.001741 | -0.0084228 | 0.01954 | 0.039858 | -0.015919 | 0.012334 | 0.023751 | -0.0046933 | 3.3325 | 3.241 | 3.2227 | 3.2822 | 3.4149 | 3.3005 | 3.3279 | 0.07782 | 0 | -0.041199 | 0.032043 | 0.16022 | 0.13275 | 0.11902 | 3.3096 | -119.4901 | -119.4489 | 3.5019 | 3.4149 | 3.3875 | 0.10529 | 0.07782 | 0.045776 | -122.731 | -122.699 | 0.24719 | 0.20599 | 0.21973 | 0.16022 | 0.17395 | 0.19226 | 0.05951 | 0.20142 | 0.073242 | 0.018311 | 0.041199 | 3.3279 | 0.086975 | -119.5084 | -122.7722 | 3.3691 | 0.11902 | 3.4195 | 0.16479
5675.8281 | 122.7631 | -0.11444 | 122.7585 | -0.012131 | 0.010805 | 0.0092072 | -0.0087222 | -0.00026906 | -0.011339 | -0.0028092 | -0.005371 | 0.020181 | 0.040712 | -0.01421 | 0.011053 | 0.020546 | -0.0036253 | 3.273 | 3.3096 | 3.2043 | 3.1998 | 3.3188 | 3.2089 | 3.2455 | -0.054932 | 0.045776 | -0.064087 | -0.073242 | 0.041199 | 0.013733 | 0.041199 | 3.3188 | -119.4489 | -119.5587 | 3.4332 | 3.36 | 3.3234 | 0.041198 | 0.004577 | 0.050354 | -122.7127 | -122.8317 | 0.15564 | 0.15564 | 0.12817 | 0.10529 | 0.07782 | 0.11444 | -0.004578 | 0.10529 | -0.009155 | 0.10528 | 0.10986 | 3.4241 | 0.16022 | -119.5541 | -122.8226 | 3.3142 | 0.041199 | 3.3875 | 0.059509
5677.5469 | 122.8683 | -0.091553 | 122.7493 | -0.02739 | 0.010164 | 0.009848 | -0.011713 | -0.0030463 | -0.0089892 | -0.0053726 | -0.0023192 | 0.019326 | 0.042635 | -0.018055 | 0.0089167 | 0.022683 | -0.0044797 | 3.3325 | 3.2135 | 3.2227 | 3.2684 | 3.4058 | 3.2776 | 3.3051 | 0.10071 | -0.004578 | -0.045776 | 0.027466 | 0.15106 | 0.12817 | 0.11444 | 3.3142 | -119.5358 | -119.4809 | 3.4973 | 3.3966 | 3.3691 | 0.082398 | 0.054932 | 0.045777 | -122.7539 | -122.7219 | 0.24261 | 0.20599 | 0.21973 | 0.16022 | 0.17395 | 0.18311 | 0.045777 | 0.19684 | 0.073242 | -0.009155 | 0.041198 | 3.3051 | 0.086975 | -119.5267 | -122.7951 | 3.36 | 0.11902 | 3.4241 | 0.19226
5679.3125 | 122.7631 | -0.10529 | 122.7539 | -0.01976 | 0.017214 | 0.0085662 | -0.0072268 | 0.00015814 | -0.0072802 | -0.0032364 | -0.005371 | 0.01954 | 0.042208 | -0.017628 | 0.013189 | 0.022469 | -0.0038389 | 3.2364 | 3.2227 | 3.1403 | 3.1448 | 3.2547 | 3.1219 | 3.1494 | 0 | 0.041199 | -0.054932 | -0.059509 | 0.050354 | 0 | 0.041199 | 3.2455 | -119.5312 | -119.6091 | 3.36 | 3.2547 | 3.2272 | 0.009155 | -0.018311 | 0.050354 | -122.7127 | -122.8134 | 0.15564 | 0.14649 | 0.10529 | 0.096131 | 0.054932 | 0.11444 | 0.004577 | 0.10529 | -0.004577 | 0.082397 | 0.096131 | 3.3279 | 0.14649 | -119.6136 | -122.8088 | 3.2501 | 0.045777 | 3.3417 | 0.10529
5681.0312 | 122.8867 | -0.064087 | 122.7036 | -0.01976 | 0.013582 | 0.0083526 | -0.011499 | 0.0044305 | -0.0077074 | -0.0019546 | -0.005371 | 0.020822 | 0.040071 | -0.017628 | 0.012121 | 0.024178 | -0.0044797 | 3.1677 | 3.0853 | 3.0853 | 3.1265 | 3.2639 | 3.1036 | 3.154 | 0.11902 | 0.004578 | -0.027466 | 0.054932 | 0.16479 | 0.11902 | 0.1236 | 3.1494 | -119.6182 | -119.577 | 3.3279 | 3.2181 | 3.1677 | 0.068665 | 0.018311 | 0.036621 | -122.699 | -122.6486 | 0.22888 | 0.18768 | 0.18311 | 0.15106 | 0.14649 | 0.17853 | 0.041199 | 0.19226 | 0.082398 | 0 | 0.032044 | 3.1494 | 0.068665 | -119.6182 | -122.731 | 3.1906 | 0.11902 | 3.2318 | 0.18311
5682.7656 | 122.8638 | -0.059509 | 122.7264 | -0.02739 | 0.012941 | 0.0085662 | -0.0091494 | -0.00091006 | -0.010057 | -0.002382 | -0.0084228 | 0.018686 | 0.040071 | -0.013356 | 0.0078485 | 0.023323 | -0.0055479 | 3.1815 | 3.0853 | 3.0808 | 3.1311 | 3.2593 | 3.1174 | 3.1448 | 0.073242 | 0.013733 | -0.027466 | 0.013733 | 0.10986 | 0.091553 | 0.09613 | 3.1403 | -119.6411 | -119.5953 | 3.3188 | 3.2043 | 3.1769 | 0.064086 | 0.036621 | 0.032043 | -122.7127 | -122.7127 | 0.16937 | 0.15564 | 0.15106 | 0.1236 | 0.11902 | 0.17853 | 0.050354 | 0.13733 | 0.041199 | 0.004577 | 0.041199 | 3.1448 | 0.073242 | -119.6457 | -122.7539 | 3.1906 | 0.073242 | 3.241 | 0.13275
5684.5312 | 122.8134 | -0.091553 | 122.7402 | -0.012131 | 0.013796 | 0.0085662 | -0.0067996 | 0.0020807 | -0.010057 | -0.0025956 | -0.0084228 | 0.02189 | 0.043917 | -0.016774 | 0.012334 | 0.021614 | -0.0027707 | 3.241 | 3.2272 | 3.154 | 3.1494 | 3.2867 | 3.1494 | 3.1906 | 0.041199 | 0.032043 | -0.073242 | 0 | 0.091553 | 0.050354 | 0.068665 | 3.2455 | -119.5129 | -119.5908 | 3.3783 | 3.2822 | 3.241 | 0.036621 | -0.004578 | 0.018311 | -122.7081 | -122.7402 | 0.18311 | 0.16022 | 0.14191 | 0.14191 | 0.1236 | 0.13275 | -0.004578 | 0.16479 | 0.073242 | 0.073242 | 0.10529 | 3.3188 | 0.1236 | -119.5862 | -122.8134 | 3.241 | 0.091553 | 3.3325 | 0.13275
5686.25 | 122.8317 | -0.091553 | 122.7356 | -0.01976 | 0.01465 | 0.010916 | -0.0061588 | 0.0057123 | -0.011125 | -0.0049454 | -0.011475 | 0.020608 | 0.041567 | -0.019337 | 0.01148 | 0.023964 | -0.0053343 | 3.1265 | 3.1494 | 3.0624 | 3.0258 | 3.1403 | 3.0075 | 3.0487 | -0.018311 | 0.036621 | -0.054932 | 0.004578 | 0.091553 | 0.050354 | 0.091553 | 3.154 | -119.5862 | -119.7098 | 3.2318 | 3.1403 | 3.0991 | -0.013733 | -0.054932 | 0.036621 | -122.699 | -122.731 | 0.18311 | 0.18311 | 0.14191 | 0.14649 | 0.10529 | 0.07782 | -0.036621 | 0.14649 | 0.05951 | 0.086975 | 0.091553 | 3.241 | 0.12817 | -119.6732 | -122.7905 | 3.1174 | 0.096131 | 3.2181 | 0.073242
5687.9688 | 122.7631 | -0.11902 | 122.7448 | -0.0045011 | 0.0084552 | 0.0074982 | -0.0091494 | -0.0011237 | -0.01198 | -0.0025956 | -0.011475 | 0.019754 | 0.041353 | -0.015278 | 0.012334 | 0.022255 | -0.0012753 | 3.2227 | 3.273 | 3.1677 | 3.1448 | 3.2684 | 3.1723 | 3.1998 | -0.045776 | 0.041199 | -0.07782 | -0.091553 | 0.027466 | 0.009155 | 0.032043 | 3.2867 | -119.4717 | -119.5999 | 3.3875 | 3.3188 | 3.2913 | 0.032043 | 0.004577 | 0.041199 | -122.7036 | -122.8363 | 0.14649 | 0.15106 | 0.12817 | 0.10986 | 0.086975 | 0.10071 | -0.022889 | 0.10529 | -0.013733 | 0.10529 | 0.11902 | 3.392 | 0.16022 | -119.577 | -122.8226 | 3.2639 | 0.027466 | 3.3417 | 0.073243
5689.6875 | 122.7676 | -0.10071 | 122.7264 | -0.012131 | 0.014223 | 0.008139 | -0.0053042 | -0.0011237 | -0.0077074 | -0.0053726 | -0.0084228 | 0.023172 | 0.04178 | -0.016774 | 0.010839 | 0.022896 | -0.0055479 | 3.1128 | 3.1448 | 3.0624 | 2.9938 | 3.1036 | 2.9984 | 3.0212 | -0.054932 | 0.045776 | -0.07782 | -0.054932 | 0.009155 | -0.022888 | 0.041199 | 3.1631 | -119.5816 | -119.7327 | 3.2043 | 3.1219 | 3.0991 | -0.041199 | -0.064087 | 0.022888 | -122.6807 | -122.7814 | 0.10986 | 0.14191 | 0.07782 | 0.11902 | 0.054932 | 0.041199 | -0.068665 | 0.086975 | 0.022888 | 0.082397 | 0.1236 | 3.2455 | 0.14648 | -119.664 | -122.8043 | 3.0945 | 0.045776 | 3.2135 | 0.045776
5691.4062 | 122.8363 | -0.07782 | 122.7081 | -0.01976 | 0.010378 | 0.0085662 | -0.013422 | 0.0033623 | -0.010271 | -0.0028092 | -0.011475 | 0.01954 | 0.040712 | -0.012501 | 0.011053 | 0.023751 | -0.0044797 | 3.1586 | 3.1174 | 3.0899 | 3.0991 | 3.2364 | 3.1036 | 3.1494 | 0.013733 | 0.018311 | -0.036621 | -0.013733 | 0.11444 | 0.064087 | 0.07782 | 3.1677 | -119.5908 | -119.6091 | 3.3142 | 3.2272 | 3.1815 | 0.059509 | 0.013733 | 0.041199 | -122.6898 | -122.7219 | 0.19226 | 0.15564 | 0.14191 | 0.11444 | 0.10071 | 0.14648 | 0.009155 | 0.15106 | 0.022888 | 0.027466 | 0.054932 | 3.1952 | 0.096131 | -119.6182 | -122.7448 | 3.1769 | 0.064087 | 3.2364 | 0.091553
5693.1562 | 122.8317 | -0.10529 | 122.7402 | -0.012131 | 0.013796 | 0.008139 | -0.0095766 | 0.0035761 | -0.012407 | -0.0013138 | -0.005371 | 0.021035 | 0.041353 | -0.01656 | 0.012121 | 0.020974 | -0.0051205 | 3.2272 | 3.1998 | 3.1265 | 3.1311 | 3.273 | 3.1311 | 3.1677 | 0.027466 | 0.045776 | -0.036621 | 0.004578 | 0.10529 | 0.059509 | 0.073242 | 3.2318 | -119.5404 | -119.6091 | 3.3783 | 3.273 | 3.2364 | 0.041199 | 0.004578 | 0.068665 | -122.6944 | -122.7356 | 0.21057 | 0.17853 | 0.16479 | 0.10986 | 0.09613 | 0.14648 | 0.004578 | 0.14191 | 0.041199 | 0.073242 | 0.082397 | 3.3051 | 0.15106 | -119.6136 | -122.7768 | 3.2364 | 0.10986 | 3.3325 | 0.13275
5694.8594 | 122.9004 | -0.082397 | 122.7173 | -0.02739 | 0.016573 | 0.0089936 | -0.0091494 | 0.0016535 | -0.00963 | -0.0047318 | -0.0084228 | 0.019113 | 0.039644 | -0.013997 | 0.014257 | 0.025032 | -0.0017027 | 3.1723 | 3.0579 | 3.067 | 3.0762 | 3.2364 | 3.067 | 3.1174 | 0.10071 | 0 | -0.036621 | 0.054932 | 0.16937 | 0.12817 | 0.16022 | 3.1494 | -119.6594 | -119.6411 | 3.3188 | 3.1998 | 3.1494 | 0.050354 | 0 | 0.045776 | -122.7173 | -122.6624 | 0.25177 | 0.24261 | 0.21057 | 0.19684 | 0.1648 | 0.16937 | 0.009155 | 0.20599 | 0.091553 | -0.009156 | 0.036621 | 3.1403 | 0.082397 | -119.6503 | -122.7539 | 3.1586 | 0.13733 | 3.2547 | 0.18311
5696.5625 | 122.8729 | -0.07782 | 122.7219 | -0.012131 | 0.0086688 | 0.0072846 | -0.011499 | -0.00069646 | -0.011553 | -0.0021682 | -0.014526 | 0.017404 | 0.041994 | -0.027028 | 0.0099847 | 0.022042 | -0.0057615 | 3.2593 | 3.1815 | 3.1631 | 3.2181 | 3.3554 | 3.2318 | 3.2639 | 0.086975 | 0.013733 | -0.036621 | 0.032043 | 0.16022 | 0.13275 | 0.11444 | 3.241 | -119.5404 | -119.5038 | 3.4332 | 3.3417 | 3.3096 | 0.10071 | 0.068665 | 0.041199 | -122.7081 | -122.6898 | 0.23804 | 0.19226 | 0.21057 | 0.15106 | 0.16937 | 0.19226 | 0.054932 | 0.19684 | 0.068664 | 0.018311 | 0.050354 | 3.2593 | 0.091553 | -119.5587 | -122.7585 | 3.2959 | 0.10986 | 3.3371 | 0.16479
5698.3281 | 122.8409 | -0.082397 | 122.7219 | -0.01976 | 0.012941 | 0.0074982 | -0.010645 | -0.0051825 | -0.011553 | -0.0040908 | -0.011475 | 0.018472 | 0.040712 | -0.01891 | 0.0084893 | 0.022896 | -0.0023435 | 3.1403 | 3.0853 | 3.0762 | 3.0853 | 3.2135 | 3.0808 | 3.1494 | 0.018311 | 0 | -0.041199 | 0.004578 | 0.11902 | 0.086975 | 0.091553 | 3.1586 | -119.6365 | -119.6365 | 3.2959 | 3.2318 | 3.1631 | 0.073242 | 0.004578 | 0.041198 | -122.7219 | -122.7173 | 0.20142 | 0.17395 | 0.16937 | 0.13275 | 0.12817 | 0.13733 | 0.009155 | 0.16022 | 0.045777 | 0.009155 | 0.041199 | 3.1677 | 0.082397 | -119.6457 | -122.7631 | 3.1677 | 0.086975 | 3.2227 | 0.10071
5700.0312 | 122.8134 | -0.11444 | 122.7448 | -0.01976 | 0.011019 | 0.0062164 | -0.0091494 | 0.0020807 | -0.010912 | -0.00345 | -0.005371 | 0.021249 | 0.039858 | -0.01122 | 0.012121 | 0.020974 | -0.0010617 | 3.2089 | 3.2318 | 3.1586 | 3.1448 | 3.2364 | 3.1448 | 3.1769 | -0.045776 | 0.032043 | -0.073242 | -0.050354 | 0.068665 | 0.022888 | 0.059509 | 3.273 | -119.5129 | -119.5999 | 3.3508 | 3.2913 | 3.2593 | 0.018311 | -0.013733 | 0.041199 | -122.7127 | -122.7951 | 0.18311 | 0.17395 | 0.13733 | 0.13275 | 0.09613 | 0.07782 | -0.013733 | 0.14191 | 0.022888 | 0.073243 | 0.10529 | 3.3463 | 0.14648 | -119.5862 | -122.818 | 3.2593 | 0.064087 | 3.3234 | 0.068665
5701.75 | 122.7676 | -0.10986 | 122.7631 | -0.012131 | 0.014864 | 0.0085662 | -0.0053042 | 0.0022943 | -0.00963 | -0.0013138 | -0.005371 | 0.021249 | 0.044985 | -0.018483 | 0.012121 | 0.023751 | -0.00042085 | 3.1815 | 3.154 | 3.0945 | 3.0716 | 3.1906 | 3.0396 | 3.0808 | -0.009155 | 0.045776 | -0.050354 | -0.045776 | 0.022888 | -0.018311 | 0.036621 | 3.2043 | -119.6091 | -119.6915 | 3.3005 | 3.1906 | 3.1494 | -0.013732 | -0.054931 | 0.059509 | -122.7173 | -122.8088 | 0.13275 | 0.14648 | 0.091552 | 0.086975 | 0.032043 | 0.096131 | -0.022888 | 0.073242 | 0.004578 | 0.05951 | 0.09613 | 3.2639 | 0.15564 | -119.6686 | -122.8134 | 3.1815 | 0.064087 | 3.2913 | 0.10071
5703.4844 | 122.818 | -0.10529 | 122.7081 | -0.012131 | 0.012941 | 0.010062 | -0.0089358 | 0.00015814 | -0.008562 | -0.0032364 | -0.005371 | 0.020181 | 0.040285 | -0.01891 | 0.012975 | 0.022042 | -0.00084805 | 3.2135 | 3.2089 | 3.1448 | 3.1311 | 3.2639 | 3.1311 | 3.1494 | 0.027466 | 0.041199 | -0.041199 | -0.018311 | 0.082397 | 0.045776 | 0.086975 | 3.2501 | -119.4992 | -119.577 | 3.3691 | 3.2547 | 3.2364 | 0.004578 | -0.013732 | 0.064087 | -122.6669 | -122.7264 | 0.18768 | 0.19226 | 0.15106 | 0.12817 | 0.086975 | 0.11902 | -0.013732 | 0.1236 | 0.022888 | 0.064087 | 0.082398 | 3.3142 | 0.14649 | -119.5633 | -122.7493 | 3.2364 | 0.086975 | 3.3188 | 0.13275
5705.25 | 122.7676 | -0.11444 | 122.7768 | -0.01976 | 0.012087 | 0.0094208 | -0.011286 | 0.0033623 | -0.010912 | -0.0025956 | -0.011475 | 0.021249 | 0.04178 | -0.022755 | 0.011694 | 0.021614 | -0.0064023 | 3.1952 | 3.2181 | 3.1403 | 3.1082 | 3.2318 | 3.1174 | 3.1494 | -0.068665 | 0.032043 | -0.07782 | -0.086975 | 0.027466 | 0.013733 | 0.027466 | 3.2547 | -119.5587 | -119.6686 | 3.3463 | 3.2639 | 3.2318 | 0.009155 | -0.022888 | 0.036621 | -122.7448 | -122.8638 | 0.14191 | 0.14191 | 0.12817 | 0.10529 | 0.091553 | 0.091553 | -0.032044 | 0.10529 | -0.009155 | 0.07782 | 0.10986 | 3.3325 | 0.14648 | -119.6365 | -122.8546 | 3.2227 | 0.027466 | 3.3096 | 0.045776
5706.9531 | 122.7585 | -0.09613 | 122.7448 | -0.012131 | 0.015078 | 0.008139 | -0.0080814 | -0.00026906 | -0.0094164 | -0.0064408 | -0.0084228 | 0.022958 | 0.040285 | -0.013569 | 0.013189 | 0.024391 | -0.00063445 | 3.0991 | 3.1311 | 3.0441 | 2.9846 | 3.0533 | 2.948 | 2.9984 | -0.10529 | 0.036621 | -0.068665 | -0.073242 | 0.009155 | -0.027466 | 0.036621 | 3.1403 | -119.6136 | -119.7601 | 3.1494 | 3.0945 | 3.0441 | -0.045776 | -0.09613 | 0.027465 | -122.7081 | -122.818 | 0.10528 | 0.13275 | 0.068664 | 0.10529 | 0.041199 | 0.009156 | -0.059509 | 0.07782 | -0.004577 | 0.086976 | 0.10529 | 3.2272 | 0.13275 | -119.7006 | -122.8134 | 3.0807 | 0.022888 | 3.1952 | -0.009156
5708.6719 | 122.7585 | -0.11444 | 122.7859 | -0.012131 | 0.01166 | 0.0083526 | -0.0095766 | -0.00026906 | -0.014543 | -0.0047318 | -0.011475 | 0.020608 | 0.042208 | -0.015706 | 0.012121 | 0.022469 | -0.00063445 | 3.1723 | 3.2135 | 3.1357 | 3.0808 | 3.2318 | 3.1219 | 3.1448 | -0.054932 | 0.036621 | -0.073242 | -0.091553 | 0.054932 | 0.009155 | 0.018311 | 3.2501 | -119.5724 | -119.7052 | 3.3463 | 3.2593 | 3.2364 | 0.009155 | -0.013733 | 0.041199 | -122.7493 | -122.8775 | 0.16937 | 0.13275 | 0.1236 | 0.091553 | 0.082397 | 0.096131 | -0.054931 | 0.12817 | -0.018311 | 0.07782 | 0.10986 | 3.3279 | 0.15106 | -119.6503 | -122.8592 | 3.1952 | 0.022888 | 3.2867 | 0.059509
5710.375 | 122.7905 | -0.11902 | 122.731 | -0.01976 | 0.013582 | 0.00878 | -0.0063724 | -0.0019781 | -0.011553 | -0.0043046 | -0.0023192 | 0.020608 | 0.040712 | -0.013783 | 0.01148 | 0.021828 | -0.00063445 | 3.0716 | 3.0808 | 2.9938 | 2.9434 | 3.0716 | 2.9434 | 2.98 | -0.050354 | 0.018311 | -0.068665 | -0.045776 | 0.032043 | -0.018311 | 0.045776 | 3.1128 | -119.6503 | -119.7876 | 3.1906 | 3.0991 | 3.0624 | -0.013732 | -0.050354 | 0.050354 | -122.7127 | -122.7768 | 0.15106 | 0.16479 | 0.10071 | 0.11444 | 0.050354 | 0.07782 | -0.050354 | 0.10071 | 0.022889 | 0.086976 | 0.086976 | 3.1998 | 0.13733 | -119.7372 | -122.7997 | 3.0624 | 0.073243 | 3.1906 | 0.068665
5712.0938 | 122.8592 | -0.07782 | 122.7356 | -0.01976 | 0.0099506 | 0.0094208 | -0.0091494 | -0.0015509 | -0.010485 | -0.0028092 | -0.0084228 | 0.019754 | 0.042208 | -0.02126 | 0.010412 | 0.02311 | -0.0044797 | 3.0945 | 3.0716 | 3.0533 | 3.0441 | 3.1769 | 3.0579 | 3.1036 | 0.018311 | 0.027466 | -0.041199 | 0 | 0.10529 | 0.068665 | 0.09613 | 3.1311 | -119.664 | -119.6915 | 3.2547 | 3.1815 | 3.1357 | 0.050354 | 0.004577 | 0.036621 | -122.7081 | -122.7356 | 0.18311 | 0.17395 | 0.14649 | 0.13733 | 0.10986 | 0.1236 | -0.009156 | 0.14649 | 0.041199 | 0.01831 | 0.068665 | 3.1494 | 0.10529 | -119.6823 | -122.7768 | 3.1219 | 0.07782 | 3.1723 | 0.096131
5713.8125 | 122.8226 | -0.086975 | 122.7585 | -0.01976 | 0.011232 | 0.0079254 | -0.0097904 | -0.0036871 | -0.011339 | -0.002382 | -0.011475 | 0.018686 | 0.04114 | -0.026814 | 0.010626 | 0.020974 | -0.0029843 | 3.2318 | 3.1586 | 3.1219 | 3.1723 | 3.2959 | 3.186 | 3.2135 | 0.041199 | 0.027466 | -0.036621 | -0.036621 | 0.10071 | 0.050354 | 0.059509 | 3.2089 | -119.5999 | -119.5862 | 3.3829 | 3.3005 | 3.273 | 0.091553 | 0.064087 | 0.050354 | -122.731 | -122.7951 | 0.18768 | 0.14648 | 0.13733 | 0.09613 | 0.086975 | 0.17395 | 0.050354 | 0.13733 | 0 | 0.036621 | 0.064087 | 3.2455 | 0.11444 | -119.6365 | -122.7951 | 3.2593 | 0.050354 | 3.3188 | 0.12817
5715.5312 | 122.8226 | -0.10529 | 122.7356 | -0.012131 | 0.011873 | 0.00878 | -0.0070132 | 0.0012261 | -0.011339 | -0.0057998 | -0.0084228 | 0.021676 | 0.041567 | -0.019124 | 0.012762 | 0.02076 | -0.0038389 | 3.1998 | 3.1815 | 3.0945 | 3.0899 | 3.2272 | 3.1036 | 3.1082 | 0.013733 | 0.050354 | -0.054932 | -0.018311 | 0.086975 | 0.050354 | 0.082397 | 3.1998 | -119.5541 | -119.6457 | 3.3325 | 3.2135 | 3.2089 | 0.013733 | 0.009156 | 0.050354 | -122.6852 | -122.7539 | 0.19226 | 0.18768 | 0.15564 | 0.13733 | 0.10529 | 0.13275 | -0.004577 | 0.14191 | 0.036621 | 0.086976 | 0.10529 | 3.2867 | 0.15564 | -119.6411 | -122.7905 | 3.1952 | 0.086975 | 3.3051 | 0.11902
5717.2969 | 122.8409 | -0.082397 | 122.7356 | -0.02739 | 0.0123 | 0.0068574 | -0.010218 | -0.0039007 | -0.0087756 | -0.0045182 | -0.011475 | 0.020822 | 0.040712 | -0.020619 | 0.011053 | 0.022896 | -0.0057615 | 3.0762 | 3.0533 | 3.0304 | 3.0304 | 3.1631 | 3.0441 | 3.0899 | 0.018311 | 0 | -0.059509 | -0.004578 | 0.10986 | 0.082397 | 0.10529 | 3.1128 | -119.6823 | -119.7052 | 3.2455 | 3.1723 | 3.1265 | 0.059509 | 0.013732 | 0.022888 | -122.7356 | -122.7402 | 0.19226 | 0.18768 | 0.16479 | 0.16479 | 0.14191 | 0.13275 | 0 | 0.16937 | 0.054931 | 0.022888 | 0.059509 | 3.1357 | 0.082397 | -119.7052 | -122.7951 | 3.1128 | 0.077819 | 3.1586 | 0.10071
5719.0156 | 122.9141 | -0.07782 | 122.7219 | -0.01976 | 0.011232 | 0.007071 | -0.009363 | -0.0026191 | -0.012194 | -0.0036636 | -0.011475 | 0.018686 | 0.040285 | -0.017415 | 0.0089167 | 0.022896 | 0.0012881 | 3.1631 | 3.1174 | 3.0808 | 3.1448 | 3.2867 | 3.1677 | 3.1998 | 0.11902 | -0.013733 | -0.050354 | 0.045776 | 0.18768 | 0.15106 | 0.14191 | 3.1586 | -119.6045 | -119.577 | 3.3646 | 3.2776 | 3.2455 | 0.11902 | 0.086975 | 0.027466 | -122.7356 | -122.6761 | 0.2655 | 0.21973 | 0.22888 | 0.19226 | 0.20142 | 0.20599 | 0.064086 | 0.23804 | 0.09613 | 0.036621 | 0.036621 | 3.1952 | 0.064087 | -119.6411 | -122.7722 | 3.2227 | 0.1236 | 3.241 | 0.19684
5720.75 | 122.7905 | -0.11902 | 122.7448 | -0.012131 | 0.010164 | 0.0094208 | -0.0091494 | -0.00026906 | -0.010057 | -0.0043046 | -0.005371 | 0.021035 | 0.041567 | -0.020833 | 0.010198 | 0.02311 | -0.0017027 | 3.1906 | 3.1723 | 3.1265 | 3.0899 | 3.2043 | 3.1311 | 3.1311 | -0.036621 | 0.041199 | -0.068665 | -0.07782 | 0.045776 | 0.022888 | 0.018311 | 3.2455 | -119.5724 | -119.6548 | 3.3234 | 3.2501 | 3.2501 | 0.004578 | 0.004578 | 0.050354 | -122.7036 | -122.8226 | 0.16479 | 0.13733 | 0.14191 | 0.086976 | 0.091553 | 0.07782 | -0.036621 | 0.11444 | -0.009155 | 0.045776 | 0.10986 | 3.2913 | 0.16022 | -119.6182 | -122.8134 | 3.2089 | 0.041199 | 3.3096 | 0.082398
5722.4688 | 122.905 | -0.064087 | 122.731 | -0.012131 | 0.0088824 | 0.0074982 | -0.0089358 | -0.00026906 | -0.011125 | -0.0040908 | -0.0084228 | 0.019754 | 0.039644 | -0.02126 | 0.0072077 | 0.021401 | -0.0031979 | 3.1998 | 3.0991 | 3.0945 | 3.186 | 3.3188 | 3.1906 | 3.2181 | 0.11902 | 0 | -0.027466 | 0.054932 | 0.20599 | 0.15564 | 0.12817 | 3.1586 | -119.632 | -119.545 | 3.3829 | 3.2822 | 3.2547 | 0.1236 | 0.096131 | 0.036621 | -122.731 | -122.6761 | 0.27008 | 0.19226 | 0.21973 | 0.15564 | 0.18311 | 0.2243 | 0.091553 | 0.23346 | 0.082398 | 0.004578 | 0.027466 | 3.1631 | 0.064087 | -119.6365 | -122.7585 | 3.2501 | 0.11902 | 3.2639 | 0.18311
5724.1719 | 122.7722 | -0.11444 | 122.7631 | -0.01976 | 0.010805 | 0.0062164 | -0.009363 | -0.00048286 | -0.0092028 | -0.0053726 | -0.0084228 | 0.01954 | 0.039644 | -0.019551 | 0.0091303 | 0.020333 | -0.0044797 | 3.1586 | 3.186 | 3.0899 | 3.0762 | 3.1952 | 3.0945 | 3.1357 | -0.045776 | 0.050354 | -0.059509 | -0.064087 | 0.032043 | -0.004578 | 0.018311 | 3.2043 | -119.577 | -119.6869 | 3.3096 | 3.2501 | 3.2089 | 0.045776 | 0.004577 | 0.054932 | -122.7127 | -122.8271 | 0.14648 | 0.13275 | 0.10986 | 0.07782 | 0.054931 | 0.10529 | -0.013733 | 0.091552 | -0.004578 | 0.09613 | 0.10986 | 3.3005 | 0.16479 | -119.6732 | -122.8226 | 3.1906 | 0.050354 | 3.273 | 0.068665
5725.8906 | 122.7676 | -0.09613 | 122.7448 | -0.01976 | 0.015078 | 0.01113 | -0.0061588 | 0.0031487 | -0.010698 | -0.0028092 | -0.0084228 | 0.020181 | 0.042421 | -0.016347 | 0.013403 | 0.022896 | -0.0049069 | 3.1265 | 3.0945 | 3.0441 | 3.0304 | 3.1448 | 2.9984 | 3.0258 | -0.004578 | 0.036621 | -0.059509 | -0.022888 | 0.032043 | -0.018311 | 0.045776 | 3.1403 | -119.6503 | -119.7144 | 3.241 | 3.1219 | 3.0945 | -0.01831 | -0.045776 | 0.036621 | -122.7081 | -122.7676 | 0.12817 | 0.14191 | 0.077819 | 0.10528 | 0.041198 | 0.10071 | -0.013732 | 0.091552 | 0.036621 | 0.050354 | 0.09613 | 3.1906 | 0.13275 | -119.7006 | -122.8043 | 3.1265 | 0.073242 | 3.2227 | 0.091552
5727.6094 | 122.905 | -0.073242 | 122.6944 | -0.01976 | 0.013369 | 0.0083526 | -0.008295 | -0.00069646 | -0.0083484 | -0.0019546 | -0.0084228 | 0.019113 | 0.040499 | -0.015492 | 0.013189 | 0.024391 | -0.0040525 | 3.0853 | 2.9892 | 2.9709 | 3.0212 | 3.1357 | 2.9846 | 3.035 | 0.10986 | -0.004578 | -0.022888 | 0.073242 | 0.16479 | 0.11902 | 0.15106 | 3.0441 | -119.7052 | -119.6732 | 3.2089 | 3.1082 | 3.0579 | 0.064087 | 0.013733 | 0.050354 | -122.699 | -122.6212 | 0.23804 | 0.2243 | 0.19226 | 0.17395 | 0.14191 | 0.16479 | 0.050354 | 0.18768 | 0.09613 | 0.018311 | 0.01831 | 3.0624 | 0.068664 | -119.7235 | -122.7173 | 3.0945 | 0.14648 | 3.1586 | 0.18311
5729.3281 | 122.8043 | -0.11902 | 122.7493 | -0.02739 | 0.010164 | 0.00878 | -0.0097904 | 0.0022943 | -0.011553 | -0.0045182 | -0.011475 | 0.020181 | 0.042635 | -0.019124 | 0.010198 | 0.023323 | -0.0023435 | 3.1586 | 3.1677 | 3.0991 | 3.0533 | 3.1631 | 3.0624 | 3.0899 | -0.059509 | 0.032043 | -0.07782 | -0.050354 | 0.050354 | 0.018311 | 0.059509 | 3.2181 | -119.5816 | -119.696 | 3.2822 | 3.2089 | 3.1815 | -0.009155 | -0.036621 | 0.041199 | -122.7173 | -122.7997 | 0.16937 | 0.17853 | 0.13733 | 0.13733 | 0.096131 | 0.064087 | -0.045776 | 0.12817 | 0.027466 | 0.068665 | 0.10986 | 3.2867 | 0.15106 | -119.6503 | -122.8271 | 3.1723 | 0.068665 | 3.2776 | 0.05951
5731.0625 | 122.8775 | -0.07782 | 122.6944 | -0.02739 | 0.01166 | 0.0085662 | -0.011072 | -0.0011237 | -0.0083484 | -0.0013138 | -0.011475 | 0.020822 | 0.040071 | -0.018055 | 0.010626 | 0.023537 | -0.0076841 | 3.0853 | 2.9709 | 2.9572 | 3.0396 | 3.1769 | 3.0167 | 3.0624 | 0.11444 | 0.013733 | -0.032043 | 0.054932 | 0.15106 | 0.10529 | 0.1236 | 3.035 | -119.7235 | -119.6548 | 3.2547 | 3.1403 | 3.0945 | 0.10529 | 0.05951 | 0.045777 | -122.6807 | -122.6395 | 0.22888 | 0.20142 | 0.18311 | 0.15564 | 0.13733 | 0.21973 | 0.082398 | 0.18311 | 0.086975 | 0.013733 | 0.045776 | 3.0487 | 0.091553 | -119.7372 | -122.7264 | 3.1174 | 0.13275 | 3.1631 | 0.19226
5732.7812 | 122.8134 | -0.09613 | 122.7539 | -0.012131 | 0.013582 | 0.0096344 | -0.0074404 | 0.0014397 | -0.0089892 | -0.0002456 | -0.005371 | 0.022317 | 0.040712 | -0.0095105 | 0.012975 | 0.022255 | -0.0017027 | 3.1403 | 3.1174 | 3.0441 | 3.0533 | 3.1723 | 3.0396 | 3.0579 | 0.036621 | 0.032043 | -0.045776 | -0.018311 | 0.086975 | 0.041199 | 0.050354 | 3.1403 | -119.6365 | -119.7006 | 3.2684 | 3.154 | 3.1357 | 0.013733 | -0.004577 | 0.050354 | -122.7219 | -122.7722 | 0.1831 | 0.14648 | 0.13733 | 0.09613 | 0.086975 | 0.12817 | 0.009156 | 0.13275 | 0.027465 | 0.073243 | 0.077819 | 3.2135 | 0.12817 | -119.7098 | -122.7997 | 3.1494 | 0.077819 | 3.2364 | 0.13275
5734.4844 | 122.9004 | -0.068665 | 122.7356 | -0.01976 | 0.014223 | 0.0083526 | -0.0089358 | -0.0034735 | -0.0087756 | -0.002382 | -0.005371 | 0.018686 | 0.039217 | -0.014424 | 0.011694 | 0.022255 | -0.0017027 | 3.035 | 2.9892 | 2.9526 | 2.9755 | 3.1082 | 2.948 | 3.0075 | 0.07782 | 0.009155 | -0.027466 | 0.059509 | 0.16479 | 0.10071 | 0.12817 | 3.0212 | -119.7464 | -119.7601 | 3.1769 | 3.0762 | 3.0167 | 0.054931 | -0.004578 | 0.041199 | -122.7264 | -122.6761 | 0.23346 | 0.19684 | 0.16937 | 0.15564 | 0.12817 | 0.15564 | 0.022888 | 0.19226 | 0.086975 | 0.036621 | 0.036621 | 3.0579 | 0.07782 | -119.783 | -122.7631 | 3.0441 | 0.12817 | 3.1036 | 0.14649
5736.25 | 122.8958 | -0.050354 | 122.731 | -0.01976 | 0.012728 | 0.010703 | -0.0085086 | 0.00037174 | -0.0087756 | -0.005159 | -0.014526 | 0.020608 | 0.04178 | -0.012288 | 0.012121 | 0.023537 | -0.0025571 | 3.0258 | 2.9938 | 2.9205 | 2.9617 | 3.0899 | 2.9388 | 2.9892 | 0.059509 | -0.004578 | -0.036621 | 0.050354 | 0.16022 | 0.10071 | 0.13733 | 2.9709 | -119.7372 | -119.7693 | 3.1403 | 3.0396 | 2.9892 | 0.068665 | 0.018311 | 0.013733 | -122.7356 | -122.6807 | 0.21057 | 0.18768 | 0.15106 | 0.17395 | 0.13733 | 0.16937 | 0.041199 | 0.19684 | 0.086975 | 0.073242 | 0.032043 | 3.0441 | 0.045776 | -119.8105 | -122.7676 | 3.0121 | 0.10071 | 3.0762 | 0.10986
5737.9531 | 122.9004 | -0.068665 | 122.7631 | -0.0045011 | 0.0099506 | 0.0060028 | -0.010431 | 0.00079894 | -0.0094164 | -0.0040908 | -0.0084228 | 0.017617 | 0.040926 | -0.017201 | 0.0076349 | 0.022469 | -0.00042085 | 3.1769 | 3.0808 | 3.0762 | 3.1265 | 3.3005 | 3.1631 | 3.186 | 0.11902 | -0.004578 | -0.032043 | 0.045776 | 0.18768 | 0.13733 | 0.12817 | 3.1448 | -119.6823 | -119.6365 | 3.3691 | 3.2547 | 3.2318 | 0.10986 | 0.086975 | 0.036622 | -122.7676 | -122.7173 | 0.25635 | 0.19684 | 0.20599 | 0.16022 | 0.16937 | 0.2243 | 0.050354 | 0.21973 | 0.077819 | 0.004578 | 0.027465 | 3.1494 | 0.064087 | -119.6869 | -122.7951 | 3.1952 | 0.11444 | 3.2455 | 0.18768
5739.6719 | 122.7768 | -0.11902 | 122.7676 | -0.012131 | 0.017214 | 0.010275 | -0.0085086 | 0.0065667 | -0.010698 | -0.0043046 | -0.0084228 | 0.019754 | 0.043489 | -0.0071607 | 0.012975 | 0.022255 | -0.0046933 | 3.0624 | 3.0533 | 2.9755 | 2.9434 | 3.0624 | 2.9022 | 2.9388 | -0.064087 | 0.036621 | -0.07782 | -0.07782 | 0.004578 | -0.032043 | 0.018311 | 3.0945 | -119.7144 | -119.8242 | 3.1815 | 3.0579 | 3.0212 | -0.036621 | -0.073242 | 0.041199 | -122.731 | -122.8455 | 0.1236 | 0.13733 | 0.086976 | 0.096131 | 0.045777 | 0.086975 | -0.032044 | 0.082398 | 0 | 0.07782 | 0.11444 | 3.1723 | 0.15564 | -119.7922 | -122.8455 | 3.0624 | 0.041199 | 3.1815 | 0.054932
5741.3906 | 122.8546 | -0.054932 | 122.7402 | -0.012131 | 0.011446 | 0.0077118 | -0.0095766 | -0.0024055 | -0.010485 | -0.0038772 | -0.005371 | 0.01719 | 0.042849 | -0.015065 | 0.010412 | 0.023964 | -0.0025571 | 3.0533 | 3.0121 | 2.9709 | 2.9892 | 3.1036 | 2.9938 | 3.0258 | 0.013733 | 0.009155 | -0.036621 | -0.022888 | 0.10529 | 0.07782 | 0.091553 | 3.0258 | -119.7281 | -119.751 | 3.1586 | 3.0808 | 3.0487 | 0.054932 | 0.022888 | 0.018311 | -122.731 | -122.7631 | 0.16022 | 0.14649 | 0.13275 | 0.12817 | 0.11444 | 0.13275 | 0.018311 | 0.14191 | 0.013733 | 0.041199 | 0.045776 | 3.067 | 0.064087 | -119.7693 | -122.7768 | 3.0441 | 0.032044 | 3.1082 | 0.068665
5743.1406 | 122.905 | -0.050354 | 122.7356 | -0.01976 | 0.010805 | 0.0074982 | -0.01214 | 0.00037174 | -0.0092028 | -0.00345 | -0.0023192 | 0.01954 | 0.041353 | -0.018055 | 0.0084893 | 0.021187 | -0.0029843 | 3.154 | 3.0441 | 3.035 | 3.1128 | 3.2776 | 3.1357 | 3.1586 | 0.10986 | 0.004578 | -0.018311 | 0.054932 | 0.19684 | 0.15106 | 0.14648 | 3.0853 | -119.6915 | -119.6228 | 3.3279 | 3.2089 | 3.186 | 0.1236 | 0.10071 | 0.032043 | -122.731 | -122.6807 | 0.24719 | 0.19684 | 0.20142 | 0.16479 | 0.16937 | 0.24262 | 0.07782 | 0.21515 | 0.073243 | 0.009155 | 0.022889 | 3.0945 | 0.054932 | -119.7006 | -122.7539 | 3.1631 | 0.10529 | 3.2043 | 0.16022
5744.8438 | 122.7905 | -0.09613 | 122.7676 | -0.02739 | 0.014437 | 0.011984 | -0.0089358 | -0.0013373 | -0.008562 | -0.0015274 | -0.005371 | 0.020822 | 0.039858 | -0.016987 | 0.012762 | 0.023323 | -0.0064023 | 3.0899 | 3.0579 | 3.0167 | 3.0075 | 3.1174 | 2.9755 | 2.9892 | 0.004578 | 0.036621 | -0.064087 | -0.041199 | 0.032043 | 0 | 0.041199 | 3.1128 | -119.7098 | -119.7601 | 3.2135 | 3.0853 | 3.0716 | -0.027466 | -0.041199 | 0.032043 | -122.731 | -122.8088 | 0.12817 | 0.13733 | 0.09613 | 0.10529 | 0.064087 | 0.10071 | -0.009156 | 0.09613 | 0.022888 | 0.041198 | 0.10071 | 3.154 | 0.13275 | -119.751 | -122.8317 | 3.1036 | 0.054931 | 3.186 | 0.10071
5746.5625 | 122.85 | -0.082397 | 122.7219 | -0.01976 | 0.011019 | 0.0096344 | -0.008295 | -0.00091006 | -0.010485 | -0.0045182 | -0.005371 | 0.019113 | 0.040071 | -0.024037 | 0.010412 | 0.02311 | -0.0055479 | 3.0258 | 2.9709 | 2.9709 | 2.9892 | 3.0991 | 2.98 | 3.0212 | 0.009155 | 0.004578 | -0.041199 | -0.009155 | 0.10071 | 0.086975 | 0.086975 | 3.0533 | -119.751 | -119.7327 | 3.1815 | 3.1036 | 3.0624 | 0.050354 | 0.009156 | 0.041198 | -122.7173 | -122.731 | 0.18311 | 0.16937 | 0.16937 | 0.12817 | 0.12817 | 0.12817 | 0.018311 | 0.14191 | 0.032044 | 0 | 0.045777 | 3.0533 | 0.086975 | -119.751 | -122.7631 | 3.0716 | 0.073242 | 3.1082 | 0.091552
5748.3438 | 122.7676 | -0.10529 | 122.7997 | -0.02739 | 0.0099506 | 0.00878 | -0.0097904 | 0.00037174 | -0.010698 | -0.0036636 | -0.0023192 | 0.021035 | 0.039858 | -0.018696 | 0.0095575 | 0.022042 | -0.0076841 | 3.0808 | 3.1036 | 3.035 | 2.9984 | 3.1311 | 3.035 | 3.0533 | -0.054932 | 0.045776 | -0.068665 | -0.086975 | 0.036621 | 0.013733 | 0.032043 | 3.1403 | -119.696 | -119.8013 | 3.2364 | 3.1586 | 3.1403 | 0.018311 | 0 | 0.036621 | -122.7539 | -122.8867 | 0.14191 | 0.13733 | 0.11902 | 0.10071 | 0.082398 | 0.096131 | -0.036621 | 0.10529 | -0.01831 | 0.068665 | 0.11444 | 3.2089 | 0.15106 | -119.7647 | -122.8683 | 3.1036 | 0.018311 | 3.186 | 0.050354
5750.0469 | 122.7539 | -0.11902 | 122.7356 | -0.01976 | 0.014223 | 0.0083526 | -0.0078676 | -0.00069646 | -0.008562 | -0.0038772 | -0.005371 | 0.022958 | 0.040499 | -0.015492 | 0.014043 | 0.024391 | -0.00042085 | 2.9892 | 3.0121 | 2.9434 | 2.8702 | 2.9388 | 2.8427 | 2.9022 | -0.073242 | 0.036621 | -0.07782 | -0.068665 | 0.018311 | -0.050354 | 0.041199 | 3.0624 | -119.7235 | -119.8654 | 3.0579 | 3.0212 | 2.9617 | -0.041198 | -0.10071 | 0.041199 | -122.699 | -122.8043 | 0.13733 | 0.16022 | 0.068665 | 0.11902 | 0.027466 | -0.004577 | -0.073242 | 0.096131 | 0.009155 | 0.068665 | 0.11444 | 3.1311 | 0.15564 | -119.7922 | -122.8134 | 2.9892 | 0.050354 | 3.1082 | 0.045777
5751.7656 | 122.8638 | -0.082397 | 122.7356 | -0.012131 | 0.0095234 | 0.0079254 | -0.011072 | -0.00048286 | -0.012834 | -0.0038772 | -0.0084228 | 0.018472 | 0.041994 | -0.016774 | 0.011053 | 0.02311 | -0.0029843 | 3.1357 | 3.0624 | 3.0396 | 3.0945 | 3.2227 | 3.1082 | 3.1219 | 0.064087 | 0.004578 | -0.068665 | -0.004578 | 0.13275 | 0.07782 | 0.09613 | 3.1219 | -119.6732 | -119.6411 | 3.3051 | 3.2043 | 3.1906 | 0.082397 | 0.068664 | 0.013732 | -122.731 | -122.7402 | 0.21515 | 0.17853 | 0.16022 | 0.16479 | 0.14649 | 0.18311 | 0.054931 | 0.20142 | 0.064087 | 0.022888 | 0.073243 | 3.1448 | 0.086975 | -119.696 | -122.8043 | 3.1769 | 0.077819 | 3.2181 | 0.14648
5753.4688 | 122.8821 | -0.064087 | 122.7173 | -0.035019 | 0.013369 | 0.00878 | -0.0078676 | -0.0015509 | -0.011339 | -0.0077224 | -0.011475 | 0.019754 | 0.042421 | -0.01656 | 0.010198 | 0.024605 | -0.0042661 | 3.0396 | 2.916 | 2.9434 | 2.98 | 3.1265 | 2.9617 | 3.0075 | 0.10529 | -0.009155 | -0.022888 | 0.027466 | 0.14648 | 0.09613 | 0.11444 | 3.0075 | -119.8013 | -119.7372 | 3.1906 | 3.0716 | 3.0258 | 0.064087 | 0.018311 | 0.041199 | -122.7264 | -122.6898 | 0.21057 | 0.17853 | 0.16022 | 0.13733 | 0.11902 | 0.18311 | 0.036622 | 0.16937 | 0.050354 | -0.027465 | 0.013733 | 2.98 | 0.054932 | -119.7739 | -122.7402 | 3.0441 | 0.091553 | 3.1036 | 0.16937
5755.1719 | 122.8821 | -0.086975 | 122.7493 | -0.01976 | 0.0099506 | 0.00878 | -0.010431 | 0.00058534 | -0.011125 | -0.0049454 | -0.0023192 | 0.019326 | 0.037935 | -0.01656 | 0.010412 | 0.022042 | -0.0053343 | 3.1311 | 3.0579 | 3.0441 | 3.0853 | 3.2227 | 3.1082 | 3.1357 | 0.068665 | 0.009155 | -0.041199 | 0.018311 | 0.15106 | 0.10986 | 0.10529 | 3.1311 | -119.6915 | -119.664 | 3.3096 | 3.2227 | 3.1952 | 0.091553 | 0.064087 | 0.045776 | -122.7402 | -122.731 | 0.23804 | 0.19226 | 0.19684 | 0.14649 | 0.15106 | 0.17853 | 0.041199 | 0.19226 | 0.05951 | 0.013733 | 0.050354 | 3.1448 | 0.09613 | -119.7052 | -122.7905 | 3.1723 | 0.10529 | 3.2181 | 0.15564
5756.9062 | 122.8134 | -0.10071 | 122.7219 | -0.01976 | 0.014864 | 0.0092072 | -0.005945 | 0.0033623 | -0.011766 | -0.0021682 | -0.0084228 | 0.022103 | 0.042421 | -0.014424 | 0.013189 | 0.021401 | -0.0038389 | 3.0991 | 3.0487 | 2.9938 | 2.9984 | 3.1128 | 2.98 | 3.0029 | 0.027466 | 0.022888 | -0.050354 | -0.018311 | 0.073242 | 0.036621 | 0.054932 | 3.0945 | -119.6732 | -119.7235 | 3.2135 | 3.1036 | 3.0808 | 0.009156 | -0.013732 | 0.050354 | -122.699 | -122.7402 | 0.17395 | 0.15564 | 0.13733 | 0.10529 | 0.086975 | 0.11902 | 0.004578 | 0.1236 | 0.032043 | 0.054932 | 0.073242 | 3.1494 | 0.1236 | -119.7281 | -122.7722 | 3.0991 | 0.082397 | 3.1998 | 0.12817
5758.6406 | 122.9004 | -0.086975 | 122.7402 | -0.0045011 | 0.01166 | 0.0089936 | -0.010645 | -0.0019781 | -0.011339 | -0.0021682 | -0.0023192 | 0.019113 | 0.04178 | -0.022328 | 0.010626 | 0.023323 | -0.0038389 | 3.035 | 3.0029 | 2.9617 | 2.9984 | 3.1357 | 3.0029 | 3.0396 | 0.054932 | 0.009155 | -0.050354 | 0.027466 | 0.14648 | 0.12817 | 0.11444 | 3.0487 | -119.7372 | -119.7418 | 3.2227 | 3.1265 | 3.0899 | 0.07782 | 0.041199 | 0.036621 | -122.731 | -122.7127 | 0.23346 | 0.20142 | 0.21515 | 0.16479 | 0.17853 | 0.17395 | 0.036621 | 0.19684 | 0.07782 | 0.041199 | 0.059509 | 3.0899 | 0.09613 | -119.7784 | -122.7905 | 3.0853 | 0.11444 | 3.1219 | 0.14191
5760.375 | 122.7859 | -0.11444 | 122.7631 | -0.01976 | 0.015505 | 0.0089936 | -0.005945 | 0.00058534 | -0.00963 | -0.0028092 | -0.0084228 | 0.019967 | 0.042208 | -0.01186 | 0.011694 | 0.022042 | -0.0046933 | 2.9526 | 2.9892 | 2.9068 | 2.8564 | 2.9343 | 2.829 | 2.8564 | -0.068665 | 0.036621 | -0.086975 | -0.041199 | 0.013733 | -0.027466 | 0.036621 | 3.0212 | -119.7739 | -119.9066 | 3.0487 | 2.9709 | 2.9434 | -0.050354 | -0.07782 | 0.027466 | -122.7264 | -122.8043 | 0.12817 | 0.15106 | 0.086975 | 0.1236 | 0.059509 | 0.027466 | -0.050354 | 0.10071 | 0.045776 | 0.082398 | 0.1236 | 3.1036 | 0.15106 | -119.8563 | -122.85 | 2.9709 | 0.073242 | 3.067 | 0.045776
5762.1094 | 122.7997 | -0.091553 | 122.7585 | -0.0045011 | 0.012514 | 0.010275 | -0.006586 | 0.0037897 | -0.0094164 | -0.0030228 | -0.005371 | 0.02189 | 0.039858 | -0.01656 | 0.011694 | 0.022042 | -0.0053343 | 3.067 | 3.0167 | 2.9846 | 2.9663 | 3.0762 | 2.9388 | 2.9663 | 0.009155 | 0.036621 | -0.059509 | -0.032043 | 0.059509 | 0.009155 | 0.054932 | 3.0762 | -119.7418 | -119.7922 | 3.1677 | 3.0579 | 3.0304 | -0.01831 | -0.045776 | 0.032044 | -122.7219 | -122.7905 | 0.15106 | 0.14649 | 0.10071 | 0.11444 | 0.068664 | 0.091553 | -0.01831 | 0.11902 | 0.027466 | 0.032044 | 0.09613 | 3.1082 | 0.12817 | -119.7739 | -122.818 | 3.0579 | 0.05951 | 3.1586 | 0.10071
5763.8594 | 122.8226 | -0.10986 | 122.7585 | -0.012131 | 0.010591 | 0.0074982 | -0.0095766 | 0.00037174 | -0.0098438 | -0.0040908 | -0.0084228 | 0.020395 | 0.041567 | -0.011433 | 0.012975 | 0.021614 | -0.0012753 | 3.0899 | 3.1357 | 3.0258 | 2.98 | 3.0853 | 2.9938 | 3.0121 | -0.050354 | 0.036621 | -0.064087 | -0.059509 | 0.059509 | 0.013733 | 0.054932 | 3.1357 | -119.6228 | -119.7784 | 3.1952 | 3.1219 | 3.1036 | -0.013733 | -0.032044 | 0.045776 | -122.7219 | -122.818 | 0.16937 | 0.16479 | 0.1236 | 0.11902 | 0.07782 | 0.059509 | -0.045776 | 0.1236 | 0.004578 | 0.10986 | 0.10071 | 3.2455 | 0.14648 | -119.7327 | -122.8226 | 3.0899 | 0.050354 | 3.1998 | 0.059509
5765.5781 | 122.8134 | -0.11902 | 122.7539 | -0.01976 | 0.010805 | 0.0072846 | -0.011927 | 0.00015814 | -0.011553 | -0.0049454 | -0.0084228 | 0.019326 | 0.042208 | -0.020619 | 0.0093439 | 0.02311 | -0.0053343 | 3.1082 | 3.0258 | 3.0258 | 3.0487 | 3.186 | 3.0808 | 3.0853 | 0.032043 | 0.018311 | -0.054932 | -0.045776 | 0.073242 | 0.041199 | 0.059509 | 3.1448 | -119.7281 | -119.7052 | 3.3051 | 3.2043 | 3.1998 | 0.059509 | 0.054932 | 0.064087 | -122.7356 | -122.7997 | 0.19226 | 0.17853 | 0.16022 | 0.11444 | 0.096131 | 0.16022 | 0.022888 | 0.12817 | 0.009156 | 0 | 0.073243 | 3.1448 | 0.13733 | -119.7281 | -122.8088 | 3.1677 | 0.073243 | 3.2272 | 0.15106
5767.3438 | 122.9141 | -0.064087 | 122.7356 | -0.02739 | 0.013369 | 0.010703 | -0.0067996 | 0.0022943 | -0.010271 | -0.0032364 | -0.0084228 | 0.018899 | 0.041567 | -0.023182 | 0.013403 | 0.023323 | -0.0049069 | 2.9388 | 2.948 | 2.8793 | 2.8793 | 3.0029 | 2.8427 | 2.9022 | 0.054932 | 0.009155 | -0.050354 | 0.041199 | 0.12817 | 0.11444 | 0.14648 | 2.9434 | -119.7876 | -119.8563 | 3.067 | 2.9663 | 2.9068 | 0.022889 | -0.036621 | 0.013733 | -122.7264 | -122.6944 | 0.19226 | 0.21057 | 0.17853 | 0.19684 | 0.16479 | 0.1236 | 0 | 0.17853 | 0.091553 | 0.068665 | 0.059509 | 3.0121 | 0.073242 | -119.8563 | -122.7859 | 2.9434 | 0.10529 | 3.0029 | 0.11902
5769.0625 | 122.8867 | -0.082397 | 122.7264 | -0.012131 | 0.010378 | 0.010062 | -0.011286 | 0.00058534 | -0.010485 | -0.000673 | -0.0084228 | 0.019754 | 0.043062 | -0.018483 | 0.0084893 | 0.023751 | -0.0019163 | 2.9938 | 2.9617 | 2.9251 | 2.9205 | 3.0624 | 2.9434 | 2.9846 | 0.027466 | -0.004578 | -0.032043 | 0.009155 | 0.11902 | 0.10071 | 0.09613 | 3.0075 | -119.7647 | -119.8059 | 3.1448 | 3.067 | 3.0258 | 0.059509 | 0.01831 | 0.050354 | -122.731 | -122.7173 | 0.20142 | 0.17853 | 0.18311 | 0.12817 | 0.13275 | 0.13733 | -0.004578 | 0.15106 | 0.041198 | 0.036621 | 0.027465 | 3.0441 | 0.077819 | -119.8013 | -122.7585 | 3.0029 | 0.091552 | 3.0762 | 0.10986
5770.7812 | 122.85 | -0.091553 | 122.7356 | -0.01976 | 0.01166 | 0.0077118 | -0.009363 | -0.00026906 | -0.0098438 | -0.0045182 | -0.0084228 | 0.017831 | 0.04178 | -0.016774 | 0.011266 | 0.022042 | 0.0012881 | 3.1128 | 3.0075 | 2.9938 | 3.035 | 3.1769 | 3.0624 | 3.0808 | 0.059509 | 0.022888 | -0.032043 | -0.022888 | 0.11902 | 0.091553 | 0.09613 | 3.0853 | -119.7281 | -119.7006 | 3.2684 | 3.1723 | 3.154 | 0.086976 | 0.068665 | 0.05951 | -122.7127 | -122.7585 | 0.21057 | 0.18768 | 0.18311 | 0.12817 | 0.1236 | 0.18311 | 0.041199 | 0.15106 | 0.009155 | 0.013733 | 0.054931 | 3.0991 | 0.11444 | -119.7418 | -122.7676 | 3.1265 | 0.068665 | 3.2043 | 0.15106
5772.5156 | 122.7905 | -0.11444 | 122.7859 | -0.01976 | 0.015932 | 0.008139 | -0.0074404 | 0.0040033 | -0.010271 | -0.0057998 | -0.0023192 | 0.019326 | 0.041353 | -0.013356 | 0.011694 | 0.023323 | -0.0061887 | 2.948 | 2.9663 | 2.8702 | 2.8244 | 2.9114 | 2.7969 | 2.8519 | -0.073242 | 0.036621 | -0.064087 | -0.064087 | 0.009155 | -0.036621 | 0.036621 | 2.9846 | -119.8196 | -119.9615 | 3.0258 | 2.9663 | 2.9114 | -0.01831 | -0.073242 | 0.050354 | -122.7493 | -122.85 | 0.1236 | 0.15106 | 0.07782 | 0.10071 | 0.027466 | 0.041199 | -0.045776 | 0.073242 | 0 | 0.096131 | 0.10071 | 3.0807 | 0.15106 | -119.9158 | -122.85 | 2.9388 | 0.050354 | 3.0624 | 0.041199
5774.2969 | 122.8317 | -0.07782 | 122.7722 | 0.0031279 | 0.01166 | 0.0089936 | -0.007654 | 0.0042169 | -0.011553 | -0.0032364 | -0.005371 | 0.019326 | 0.039217 | -0.0092969 | 0.01148 | 0.022255 | -0.0021299 | 3.0487 | 3.0075 | 2.948 | 2.948 | 3.0762 | 2.948 | 2.9663 | 0.027466 | 0.027466 | -0.041199 | -0.022888 | 0.073242 | 0.032043 | 0.054932 | 3.0258 | -119.7647 | -119.8242 | 3.154 | 3.0441 | 3.0258 | 0.018311 | 0 | 0.036621 | -122.7448 | -122.7951 | 0.15106 | 0.13275 | 0.10986 | 0.096131 | 0.073242 | 0.12817 | 0 | 0.11444 | 0.018311 | 0.059509 | 0.068665 | 3.0853 | 0.10529 | -119.8242 | -122.8134 | 3.0258 | 0.054932 | 3.1265 | 0.10529
5776.0312 | 122.8958 | -0.082397 | 122.7127 | -0.012131 | 0.0123 | 0.0060028 | -0.0097904 | 0.00058534 | -0.010912 | -0.0043046 | -0.005371 | 0.016122 | 0.040712 | -0.021687 | 0.0080621 | 0.022255 | -0.0021299 | 2.9709 | 2.9617 | 2.916 | 2.9251 | 3.0579 | 2.948 | 2.9846 | 0.027466 | 0.032043 | -0.045776 | 0.018311 | 0.1236 | 0.11444 | 0.10071 | 2.9984 | -119.751 | -119.7876 | 3.1403 | 3.067 | 3.0304 | 0.068664 | 0.032043 | 0.036621 | -122.6807 | -122.6944 | 0.20599 | 0.18311 | 0.19684 | 0.14648 | 0.16022 | 0.14191 | 0.009155 | 0.16937 | 0.064087 | 0.045776 | 0.077819 | 3.0441 | 0.11444 | -119.7968 | -122.7585 | 3.0075 | 0.10071 | 3.0533 | 0.10986
5777.7344 | 122.8363 | -0.10071 | 122.7631 | -0.02739 | 0.011232 | 0.0077118 | -0.0087222 | 0.0014397 | -0.01198 | -0.0019546 | -0.0084228 | 0.02189 | 0.040712 | -0.015492 | 0.012762 | 0.023537 | -0.0025571 | 3.0533 | 3.067 | 2.9663 | 2.9617 | 3.0716 | 2.9709 | 2.98 | -0.036621 | 0.022888 | -0.091553 | -0.045776 | 0.073242 | 0.032043 | 0.082397 | 3.067 | -119.696 | -119.8013 | 3.1723 | 3.0808 | 3.0716 | 0.013733 | 0.004577 | 0.009155 | -122.7402 | -122.8088 | 0.17395 | 0.18311 | 0.13275 | 0.17395 | 0.1236 | 0.10529 | -0.004578 | 0.16479 | 0.045777 | 0.10071 | 0.11444 | 3.1677 | 0.1236 | -119.7968 | -122.8546 | 3.0624 | 0.054932 | 3.154 | 0.064087
5779.4531 | 122.7539 | -0.1236 | 122.7676 | -0.02739 | 0.012941 | 0.0077118 | -0.006586 | 0.00058534 | -0.0094164 | -0.0025956 | -0.0023192 | 0.022103 | 0.040712 | -0.0080151 | 0.012548 | 0.02311 | -0.0049069 | 2.9388 | 2.9709 | 2.8702 | 2.8198 | 2.916 | 2.7969 | 2.8244 | -0.09613 | 0.036621 | -0.07782 | -0.082397 | 0.004578 | -0.022888 | 0.032043 | 2.9938 | -119.7968 | -119.9478 | 3.0396 | 2.948 | 2.9205 | -0.045776 | -0.073242 | 0.045776 | -122.731 | -122.85 | 0.12817 | 0.15564 | 0.10071 | 0.10986 | 0.054932 | 0.045777 | -0.050354 | 0.082398 | -0.004577 | 0.10071 | 0.11444 | 3.0945 | 0.16022 | -119.8975 | -122.8455 | 2.9434 | 0.041199 | 3.0624 | 0.027466
5781.1719 | 122.9279 | -0.07782 | 122.7127 | -0.01976 | 0.011019 | 0.0079254 | -0.005945 | 0.0057123 | -0.010912 | -0.0040908 | -0.005371 | 0.019326 | 0.040285 | -0.014424 | 0.013616 | 0.023323 | -0.0049069 | 2.9755 | 2.8793 | 2.8748 | 2.9022 | 3.0258 | 2.8656 | 2.9114 | 0.10071 | -0.009155 | -0.027466 | 0.068665 | 0.15564 | 0.11444 | 0.14191 | 2.9526 | -119.8334 | -119.8105 | 3.1036 | 2.9892 | 2.9434 | 0.036621 | -0.009155 | 0.050354 | -122.7219 | -122.644 | 0.23346 | 0.21973 | 0.19226 | 0.16937 | 0.14191 | 0.15106 | 0.027466 | 0.18311 | 0.096131 | 0.004577 | 0.018311 | 2.9572 | 0.068665 | -119.838 | -122.7402 | 2.98 | 0.14649 | 3.0533 | 0.17853
5782.8906 | 122.8683 | -0.082397 | 122.7859 | -0.01976 | 0.011019 | 0.0083526 | -0.009363 | -0.00026906 | -0.013048 | -0.0047318 | -0.0023192 | 0.017404 | 0.042635 | -0.021687 | 0.0093439 | 0.023964 | -0.0014891 | 2.9434 | 2.9068 | 2.8931 | 2.8931 | 3.0167 | 2.9114 | 2.9434 | 0.022888 | 0.022888 | -0.045776 | -0.004578 | 0.091553 | 0.059509 | 0.082397 | 2.9755 | -119.8792 | -119.8929 | 3.0991 | 3.0258 | 2.9938 | 0.050354 | 0.018311 | 0.036621 | -122.7631 | -122.7905 | 0.17395 | 0.16479 | 0.14191 | 0.12817 | 0.10528 | 0.1236 | 0 | 0.13733 | 0.041198 | 0.013733 | 0.068664 | 2.9892 | 0.10528 | -119.8929 | -122.8317 | 2.9755 | 0.077819 | 3.0258 | 0.10528
5784.6094 | 122.9095 | -0.073242 | 122.7356 | -0.01976 | 0.011232 | 0.0072846 | -0.010004 | 0.00015814 | -0.011553 | -0.002382 | -0.011475 | 0.017617 | 0.043062 | -0.018483 | 0.010626 | 0.022469 | -0.0083249 | 3.0853 | 2.9663 | 2.9663 | 3.035 | 3.1769 | 3.035 | 3.0624 | 0.09613 | -0.009155 | -0.027466 | 0.036621 | 0.16022 | 0.13275 | 0.1236 | 3.0396 | -119.7693 | -119.7006 | 3.2501 | 3.1357 | 3.1082 | 0.09613 | 0.068664 | 0.045776 | -122.7448 | -122.699 | 0.23346 | 0.19684 | 0.20599 | 0.15106 | 0.16022 | 0.21057 | 0.068664 | 0.18768 | 0.064087 | 0 | 0.018311 | 3.0396 | 0.064087 | -119.7693 | -122.7631 | 3.1082 | 0.10986 | 3.1586 | 0.16937
5786.3594 | 122.8638 | -0.07782 | 122.7356 | -0.02739 | 0.0123 | 0.0060028 | -0.0087222 | 0.0020807 | -0.008562 | -0.0060134 | -0.005371 | 0.018045 | 0.041353 | -0.017415 | 0.011266 | 0.021614 | -0.0023435 | 2.948 | 2.8793 | 2.8839 | 2.8793 | 3.0167 | 2.8839 | 2.9343 | 0.032043 | 0.004578 | -0.059509 | -0.004578 | 0.10986 | 0.082397 | 0.086975 | 2.9617 | -119.8563 | -119.8563 | 3.0945 | 3.0121 | 2.9617 | 0.050354 | 0 | 0.018311 | -122.731 | -122.7402 | 0.18768 | 0.16479 | 0.16022 | 0.14648 | 0.14191 | 0.13275 | -0.004578 | 0.16937 | 0.054931 | -0.004578 | 0.064087 | 2.9572 | 0.082398 | -119.8517 | -122.7951 | 2.9572 | 0.073242 | 3.0258 | 0.10986
5788.0781 | 122.818 | -0.10986 | 122.7905 | -0.01976 | 0.011873 | 0.008139 | -0.010004 | -0.0041145 | -0.013262 | -0.002382 | -0.014526 | 0.021035 | 0.042635 | -0.018269 | 0.011266 | 0.021614 | 0.00086095 | 3.0716 | 2.9709 | 2.9709 | 3.0075 | 3.1357 | 3.0212 | 3.0441 | 0.050354 | 0.027466 | -0.032043 | -0.036621 | 0.10071 | 0.050354 | 0.064087 | 3.0807 | -119.8196 | -119.783 | 3.2455 | 3.154 | 3.1311 | 0.073242 | 0.050354 | 0.07782 | -122.7631 | -122.8271 | 0.21057 | 0.17395 | 0.16022 | 0.09613 | 0.082397 | 0.16479 | 0.036621 | 0.13275 | -0.004578 | 0 | 0.059509 | 3.0807 | 0.13733 | -119.8196 | -122.8226 | 3.1174 | 0.073242 | 3.1815 | 0.16022
5789.7969 | 122.9095 | -0.073242 | 122.7448 | -0.01976 | 0.013796 | 0.010275 | -0.0095766 | 0.0037897 | -0.0092028 | -0.0047318 | -0.0084228 | 0.018472 | 0.038576 | -0.01891 | 0.010412 | 0.025673 | -0.0057615 | 2.9388 | 2.8198 | 2.8336 | 2.916 | 3.0258 | 2.8656 | 2.9251 | 0.10529 | 0.009155 | -0.018311 | 0.064087 | 0.16022 | 0.11444 | 0.14191 | 2.9068 | -119.9249 | -119.8288 | 3.0991 | 2.9984 | 2.9388 | 0.091553 | 0.032044 | 0.054931 | -122.7356 | -122.6807 | 0.23346 | 0.21515 | 0.18768 | 0.16022 | 0.13275 | 0.19226 | 0.082398 | 0.17853 | 0.082398 | -0.013733 | 0.027466 | 2.8931 | 0.082397 | -119.9112 | -122.7631 | 2.9892 | 0.13733 | 3.0121 | 0.17853
5791.5 | 122.8363 | -0.10071 | 122.7356 | -0.012131 | 0.011446 | 0.0083526 | -0.008295 | 0.0012261 | -0.011766 | -0.0040908 | -0.005371 | 0.022531 | 0.040285 | -0.01186 | 0.012548 | 0.02076 | -0.0021299 | 3.0121 | 2.9938 | 2.9022 | 2.916 | 3.0487 | 2.9022 | 2.9205 | 0.018311 | 0.036621 | -0.054932 | -0.004578 | 0.091553 | 0.064087 | 0.07782 | 3.0029 | -119.7418 | -119.8196 | 3.1494 | 3.0212 | 3.0029 | 0.01831 | 0 | 0.045776 | -122.699 | -122.7402 | 0.19226 | 0.17853 | 0.1648 | 0.13275 | 0.11902 | 0.14648 | 0.013733 | 0.14649 | 0.050354 | 0.091552 | 0.091553 | 3.0945 | 0.13733 | -119.8334 | -122.7905 | 3.0167 | 0.09613 | 3.1128 | 0.11902
5793.2812 | 122.8134 | -0.10986 | 122.7768 | -0.01976 | 0.01465 | 0.009848 | -0.0072268 | -5.5462e-05 | -0.012621 | 0.001036 | -0.011475 | 0.022103 | 0.043703 | -0.017628 | 0.012121 | 0.020546 | -0.0042661 | 2.9938 | 2.9526 | 2.8839 | 2.8748 | 3.0029 | 2.8656 | 2.8885 | 0 | 0.041199 | -0.073242 | -0.041199 | 0.068665 | -0.004578 | 0.059509 | 2.9938 | -119.8242 | -119.902 | 3.1128 | 2.9984 | 2.9755 | 0.004578 | -0.01831 | 0.036621 | -122.7356 | -122.818 | 0.17853 | 0.16937 | 0.10529 | 0.13275 | 0.068664 | 0.11902 | -0.009155 | 0.14191 | 0.032043 | 0.068665 | 0.11444 | 3.0624 | 0.15106 | -119.8929 | -122.85 | 2.9846 | 0.068664 | 3.1036 | 0.10986
5795 | 122.9095 | -0.073242 | 122.7585 | -0.012131 | 0.013155 | 0.0085662 | -0.010004 | -5.5462e-05 | -0.011125 | -0.0055862 | -0.0084228 | 0.018899 | 0.040499 | -0.013569 | 0.011694 | 0.022255 | -0.0046933 | 2.916 | 2.8244 | 2.8198 | 2.8793 | 3.0304 | 2.8702 | 2.916 | 0.11444 | 0.009155 | -0.022888 | 0.059509 | 0.15106 | 0.12817 | 0.11444 | 2.8931 | -119.9341 | -119.8792 | 3.1036 | 2.9892 | 2.9434 | 0.096131 | 0.050354 | 0.050354 | -122.7493 | -122.699 | 0.2243 | 0.18768 | 0.20142 | 0.13733 | 0.15106 | 0.21057 | 0.059509 | 0.17395 | 0.082397 | 0.004578 | 0.032043 | 2.8976 | 0.082397 | -119.9387 | -122.7814 | 2.9526 | 0.13275 | 2.9892 | 0.18768
5796.7031 | 122.8867 | -0.068665 | 122.7402 | -0.035019 | 0.010164 | 0.0066436 | -0.0097904 | -0.0017645 | -0.010698 | -0.0043046 | -0.0084228 | 0.019326 | 0.040071 | -0.026814 | 0.0091303 | 0.023964 | -0.0059751 | 3.0487 | 2.9617 | 2.9526 | 3.0029 | 3.154 | 3.0075 | 3.035 | 0.10071 | -0.018311 | -0.036621 | 0.045776 | 0.17395 | 0.1236 | 0.1236 | 3.0212 | -119.7784 | -119.7372 | 3.2227 | 3.1036 | 3.0762 | 0.082397 | 0.054931 | 0.032044 | -122.7585 | -122.6944 | 0.24261 | 0.19226 | 0.19226 | 0.16022 | 0.16022 | 0.20142 | 0.050354 | 0.21057 | 0.082397 | 0.009155 | 0.01831 | 3.0304 | 0.050354 | -119.7876 | -122.7768 | 3.0716 | 0.11444 | 3.1174 | 0.16937
5798.4219 | 122.8088 | -0.1236 | 122.7585 | -0.01976 | 0.017427 | 0.0092072 | -0.008295 | 0.0012261 | -0.010271 | -0.0036636 | -0.0084228 | 0.021035 | 0.04114 | -0.015065 | 0.013616 | 0.02076 | -0.0036253 | 2.9892 | 2.9343 | 2.8839 | 2.8931 | 3.0029 | 2.8656 | 2.8839 | 0.009155 | 0.027466 | -0.064087 | -0.013733 | 0.050354 | 0.009155 | 0.045776 | 3.0075 | -119.8242 | -119.8654 | 3.1265 | 3.0075 | 2.9892 | 0 | -0.01831 | 0.059509 | -122.731 | -122.7722 | 0.17395 | 0.16937 | 0.13275 | 0.10986 | 0.073242 | 0.11902 | 0.009155 | 0.11444 | 0.050354 | 0.050354 | 0.091553 | 3.0579 | 0.15106 | -119.8746 | -122.8226 | 3.0167 | 0.10986 | 3.1128 | 0.13275
5800.1406 | 122.9141 | -0.068665 | 122.7173 | -0.02739 | 0.015505 | 0.0068574 | -0.008295 | 0.0035761 | -0.010698 | -0.0032364 | -0.005371 | 0.020822 | 0.039644 | -0.01656 | 0.011907 | 0.023537 | -0.0046933 | 2.8748 | 2.8564 | 2.8107 | 2.8107 | 2.9388 | 2.7832 | 2.8336 | 0.050354 | 0 | -0.041199 | 0.054932 | 0.14648 | 0.09613 | 0.14648 | 2.8793 | -119.8608 | -119.9066 | 3.0075 | 2.9022 | 2.8519 | 0.022888 | -0.027466 | 0.027466 | -122.7173 | -122.6624 | 0.21515 | 0.21515 | 0.16479 | 0.18768 | 0.13733 | 0.12817 | 0 | 0.18768 | 0.096131 | 0.045776 | 0.041199 | 2.9251 | 0.068665 | -119.9066 | -122.7585 | 2.8793 | 0.1236 | 2.9434 | 0.11902
5801.8594 | 122.7905 | -0.10529 | 122.7905 | -0.02739 | 0.013796 | 0.0096344 | -0.0074404 | 0.0050713 | -0.012407 | -0.0049454 | -0.005371 | 0.020181 | 0.040071 | -0.014638 | 0.013403 | 0.022469 | -0.0014891 | 2.9572 | 2.9205 | 2.8656 | 2.8473 | 2.9572 | 2.8061 | 2.8198 | -0.036621 | 0.050354 | -0.059509 | -0.045776 | 0.032043 | -0.027466 | 0.022888 | 2.9709 | -119.87 | -119.9432 | 3.0624 | 2.9251 | 2.9114 | -0.045777 | -0.05951 | 0.045777 | -122.7402 | -122.8363 | 0.13733 | 0.12817 | 0.07782 | 0.082397 | 0.032043 | 0.091552 | -0.018311 | 0.091552 | 0.013733 | 0.054931 | 0.10986 | 3.0258 | 0.15564 | -119.9249 | -122.85 | 2.9526 | 0.05951 | 3.0624 | 0.068665
5803.5625 | 122.9095 | -0.054932 | 122.7173 | -0.012131 | 0.016787 | 0.010275 | -0.006586 | 0.0037897 | -0.010271 | -0.0055862 | -0.005371 | 0.017617 | 0.039003 | -0.01656 | 0.011907 | 0.02311 | -0.0076841 | 2.8885 | 2.8336 | 2.7969 | 2.8107 | 2.9388 | 2.8198 | 2.8427 | 0.073242 | 0.004578 | -0.045776 | 0.068665 | 0.15564 | 0.10071 | 0.14191 | 2.8519 | -119.8837 | -119.9066 | 2.9938 | 2.8976 | 2.8748 | 0.045776 | 0.022888 | 0.009156 | -122.7127 | -122.6486 | 0.21057 | 0.19684 | 0.15564 | 0.18768 | 0.14648 | 0.14191 | 0.013733 | 0.20142 | 0.11444 | 0.036621 | 0.050354 | 2.8885 | 0.05951 | -119.9203 | -122.7631 | 2.8656 | 0.1236 | 2.9434 | 0.12817
5805.3281 | 122.7814 | -0.11444 | 122.7814 | -0.01976 | 0.016146 | 0.0077118 | -0.0055178 | 0.0040033 | -0.00963 | -0.0049454 | -0.0023192 | 0.021463 | 0.041353 | -0.017628 | 0.011694 | 0.022469 | -0.0061887 | 2.8702 | 2.9068 | 2.8198 | 2.7328 | 2.829 | 2.7328 | 2.7878 | -0.068665 | 0.050354 | -0.082397 | -0.068665 | 0.004578 | -0.041199 | 0.032043 | 2.9343 | -119.8746 | -120.0485 | 2.9434 | 2.9022 | 2.8473 | -0.032043 | -0.086975 | 0.032044 | -122.731 | -122.85 | 0.11902 | 0.14648 | 0.073242 | 0.11444 | 0.041198 | 0.009155 | -0.086975 | 0.086975 | 0.013732 | 0.086975 | 0.13275 | 3.0212 | 0.16479 | -119.9615 | -122.8638 | 2.8473 | 0.045776 | 2.9846 | 0.045776
5807.0469 | 122.8821 | -0.07782 | 122.7722 | -0.01976 | 0.0123 | 0.0085662 | -0.011286 | 0.00015814 | -0.0092028 | -0.0025956 | -0.005371 | 0.018258 | 0.04178 | -0.018696 | 0.010198 | 0.024391 | -0.0027707 | 2.9022 | 2.861 | 2.8564 | 2.8427 | 2.9892 | 2.8473 | 2.8793 | 0.022888 | -0.009155 | -0.050354 | -0.009155 | 0.10529 | 0.054932 | 0.09613 | 2.9343 | -119.9112 | -119.9295 | 3.067 | 2.9572 | 2.9251 | 0.022888 | -0.009155 | 0.027466 | -122.7814 | -122.7814 | 0.18311 | 0.17395 | 0.13275 | 0.14648 | 0.10529 | 0.13275 | -0.013733 | 0.15564 | 0.041199 | 0.004578 | 0.041199 | 2.9388 | 0.068665 | -119.9158 | -122.8226 | 2.9205 | 0.068665 | 2.98 | 0.10071
5808.7812 | 122.818 | -0.12817 | 122.8088 | -0.012131 | 0.010591 | 0.0077118 | -0.0080814 | 0.00015814 | -0.011339 | -0.001741 | -0.0084228 | 0.021249 | 0.04114 | -0.014851 | 0.0097711 | 0.02311 | -0.0031979 | 2.9892 | 3.035 | 2.9205 | 2.8839 | 3.0075 | 2.9205 | 2.9297 | -0.064087 | 0.045776 | -0.082397 | -0.068665 | 0.036621 | 0.013733 | 0.041199 | 3.0487 | -119.7739 | -119.9249 | 3.1357 | 3.0579 | 3.0487 | 0.009155 | 0 | 0.045777 | -122.7631 | -122.8775 | 0.1648 | 0.16937 | 0.14191 | 0.1236 | 0.09613 | 0.086975 | -0.036621 | 0.11902 | 0.013732 | 0.11444 | 0.12817 | 3.1631 | 0.17395 | -119.8883 | -122.8912 | 3.0121 | 0.059509 | 3.1174 | 0.064087
5810.5312 | 122.8043 | -0.1236 | 122.7859 | -0.012131 | 0.01465 | 0.00878 | -0.0072268 | 0.0020807 | -0.010485 | -0.0032364 | -0.005371 | 0.022103 | 0.04178 | -0.012288 | 0.012548 | 0.023751 | -0.0070433 | 2.8519 | 2.8839 | 2.7786 | 2.7008 | 2.829 | 2.7191 | 2.7557 | -0.054932 | 0.036621 | -0.073242 | -0.059509 | 0.009155 | -0.022888 | 0.041199 | 2.9022 | -119.902 | -120.0851 | 2.9526 | 2.8793 | 2.8427 | -0.022888 | -0.059509 | 0.050354 | -122.7493 | -122.8455 | 0.13275 | 0.16479 | 0.10071 | 0.11444 | 0.050354 | 0.050354 | -0.077819 | 0.082397 | 0.013733 | 0.10529 | 0.10986 | 3.0075 | 0.16022 | -120.0073 | -122.8592 | 2.8244 | 0.064087 | 2.9755 | 0.068664
5812.3125 | 122.8775 | -0.068665 | 122.7448 | -0.01976 | 0.009737 | 0.0074982 | -0.010858 | 0.0046441 | -0.0094164 | -0.0040908 | -0.005371 | 0.015908 | 0.042421 | -0.027028 | 0.011266 | 0.022896 | 0.00021995 | 2.8748 | 2.8473 | 2.8381 | 2.8244 | 2.9572 | 2.829 | 2.8793 | 0.013733 | 0.018311 | -0.045776 | -0.022888 | 0.09613 | 0.054932 | 0.09613 | 2.9068 | -119.8975 | -119.9203 | 3.0258 | 2.948 | 2.8976 | 0.041198 | -0.009156 | 0.022889 | -122.7264 | -122.7676 | 0.16479 | 0.16479 | 0.1236 | 0.14191 | 0.10071 | 0.11902 | -0.013733 | 0.14191 | 0.022888 | 0.009155 | 0.064087 | 2.916 | 0.086976 | -119.9066 | -122.7905 | 2.8931 | 0.045777 | 2.9434 | 0.082398
5814.0312 | 122.8638 | -0.09613 | 122.7631 | -0.01976 | 0.010164 | 0.00643 | -0.010218 | 0.0020807 | -0.012407 | -0.0047318 | -0.0084228 | 0.01954 | 0.040926 | -0.018696 | 0.0069941 | 0.022683 | 0.00043375 | 3.0075 | 2.9205 | 2.9022 | 2.9526 | 3.0716 | 2.9755 | 2.9892 | 0.054932 | 0.022888 | -0.059509 | -0.013733 | 0.1236 | 0.09613 | 0.07782 | 2.9984 | -119.8425 | -119.8105 | 3.1677 | 3.0853 | 3.0716 | 0.086975 | 0.073242 | 0.036621 | -122.7402 | -122.7768 | 0.21973 | 0.17395 | 0.19226 | 0.13733 | 0.15564 | 0.16937 | 0.050354 | 0.1831 | 0.045776 | 0.01831 | 0.082397 | 3.0167 | 0.11902 | -119.8608 | -122.8226 | 3.0487 | 0.082397 | 3.1036 | 0.15106
5815.8125 | 122.9324 | -0.064087 | 122.731 | -0.01976 | 0.0095234 | 0.0085662 | -0.0085086 | -0.0013373 | -0.010912 | -0.0036636 | -0.005371 | 0.019754 | 0.040499 | -0.019551 | 0.0080621 | 0.020546 | -0.0051205 | 2.916 | 2.8656 | 2.8336 | 2.8839 | 3.0304 | 2.9114 | 2.9617 | 0.068665 | -0.004578 | -0.045776 | 0.045776 | 0.17853 | 0.13733 | 0.12817 | 2.8976 | -119.8654 | -119.8471 | 3.0945 | 3.0258 | 2.9755 | 0.12817 | 0.07782 | 0.018311 | -122.7356 | -122.6852 | 0.24261 | 0.19226 | 0.20142 | 0.17395 | 0.18311 | 0.19684 | 0.050354 | 0.2243 | 0.091552 | 0.032044 | 0.041198 | 2.9297 | 0.059509 | -119.8975 | -122.7768 | 2.948 | 0.10986 | 2.98 | 0.13275
5817.5312 | 122.905 | -0.073242 | 122.7402 | -0.012131 | 0.010378 | 0.0089936 | -0.011499 | -0.0011237 | -0.0098438 | -0.0038772 | -0.0084228 | 0.019326 | 0.04178 | -0.021901 | 0.010198 | 0.023537 | -0.0012753 | 3.0167 | 2.9205 | 2.9068 | 2.9617 | 3.1036 | 2.9663 | 2.9938 | 0.10529 | 0.013733 | -0.032043 | 0.045776 | 0.15564 | 0.11902 | 0.1236 | 2.98 | -119.8196 | -119.7784 | 3.1769 | 3.067 | 3.0396 | 0.086975 | 0.05951 | 0.041199 | -122.7264 | -122.6944 | 0.22888 | 0.19684 | 0.19226 | 0.15564 | 0.15106 | 0.19684 | 0.054932 | 0.18768 | 0.077819 | 0.013733 | 0.045776 | 2.9938 | 0.086975 | -119.8334 | -122.7722 | 3.035 | 0.11902 | 3.0899 | 0.17853
5819.25 | 122.8134 | -0.11902 | 122.7631 | -0.01976 | 0.010805 | 0.008139 | -0.010218 | -0.0024055 | -0.011339 | -0.0043046 | -0.005371 | 0.019113 | 0.041567 | -0.017201 | 0.011053 | 0.02311 | -0.0042661 | 2.9938 | 2.9205 | 2.9068 | 2.9205 | 3.035 | 2.9251 | 2.9572 | -0.018311 | 0.022888 | -0.064087 | -0.045776 | 0.054932 | 0.032043 | 0.036621 | 3.0258 | -119.8425 | -119.8425 | 3.154 | 3.0762 | 3.0441 | 0.050354 | 0.018311 | 0.054932 | -122.7402 | -122.8088 | 0.17395 | 0.15564 | 0.15106 | 0.10071 | 0.09613 | 0.12817 | 0.013733 | 0.11902 | 0.018311 | 0.013733 | 0.086975 | 3.0396 | 0.14191 | -119.8563 | -122.8271 | 3.0396 | 0.073243 | 3.1128 | 0.10071
5820.9688 | 122.7951 | -0.10529 | 122.7951 | -0.01976 | 0.017427 | 0.0074982 | -0.006586 | 0.00015814 | -0.010271 | -0.0032364 | -0.0084228 | 0.021249 | 0.041353 | -0.016774 | 0.014043 | 0.023537 | -0.0089659 | 2.9114 | 2.8976 | 2.8381 | 2.8198 | 2.9434 | 2.7969 | 2.829 | -0.013733 | 0.041199 | -0.054932 | -0.045776 | 0.036621 | -0.009155 | 0.041199 | 2.9434 | -119.8975 | -119.9753 | 3.0487 | 2.9343 | 2.9022 | -0.009156 | -0.041199 | 0.050354 | -122.7539 | -122.8409 | 0.14191 | 0.14649 | 0.096131 | 0.096131 | 0.045777 | 0.10529 | -0.018311 | 0.091553 | 0.009156 | 0.059509 | 0.096131 | 3.0029 | 0.14649 | -119.957 | -122.85 | 2.9251 | 0.05951 | 3.0167 | 0.091553
5822.8125 | 122.9324 | -0.059509 | 122.7493 | -0.02739 | 0.014437 | 0.010062 | -0.0070132 | 0.00037174 | -0.0094164 | -0.0030228 | -0.011475 | 0.018472 | 0.039858 | -0.015492 | 0.013616 | 0.023537 | -0.0042661 | 2.8885 | 2.7786 | 2.7786 | 2.8152 | 2.948 | 2.7878 | 2.8244 | 0.10529 | -0.004578 | -0.036621 | 0.059509 | 0.17395 | 0.11444 | 0.13733 | 2.8381 | -119.9707 | -119.9341 | 3.0075 | 2.8839 | 2.8473 | 0.045777 | 0.009156 | 0.022888 | -122.7539 | -122.6898 | 0.23346 | 0.19684 | 0.17395 | 0.17395 | 0.15106 | 0.16937 | 0.036622 | 0.21057 | 0.09613 | 0 | 0.032043 | 2.8381 | 0.054931 | -119.9707 | -122.7859 | 2.8748 | 0.11902 | 2.948 | 0.16479
5824.6094 | 122.8271 | -0.10071 | 122.7722 | -0.012131 | 0.0088824 | 0.007071 | -0.0095766 | -0.00048286 | -0.010271 | -0.0040908 | -0.005371 | 0.016336 | 0.040285 | -0.022114 | 0.0099847 | 0.021828 | -0.0059751 | 2.9892 | 2.9114 | 2.8839 | 2.916 | 3.0533 | 2.9343 | 2.9572 | 0.032043 | 0.027466 | -0.045776 | -0.036621 | 0.082397 | 0.022888 | 0.059509 | 2.9846 | -119.8608 | -119.8563 | 3.154 | 3.0579 | 3.035 | 0.073242 | 0.050354 | 0.054932 | -122.7448 | -122.8088 | 0.18311 | 0.16022 | 0.1236 | 0.10528 | 0.068664 | 0.16937 | 0.032044 | 0.12817 | 0.009155 | 0.027466 | 0.073242 | 3.0121 | 0.12817 | -119.8883 | -122.818 | 3.0167 | 0.064087 | 3.0899 | 0.13275
5826.3438 | 122.9004 | -0.07782 | 122.7722 | -0.01976 | 0.01166 | 0.0074982 | -0.0095766 | -0.00048286 | -0.011125 | -0.00345 | -0.011475 | 0.020181 | 0.038362 | -0.01891 | 0.010839 | 0.023964 | -0.0031979 | 2.9846 | 2.8976 | 2.8839 | 2.9205 | 3.0899 | 2.948 | 2.9709 | 0.082397 | 0.022888 | -0.045776 | 0.032043 | 0.16937 | 0.1236 | 0.10986 | 2.9617 | -119.8746 | -119.8517 | 3.1677 | 3.0487 | 3.0258 | 0.086975 | 0.064087 | 0.032044 | -122.7493 | -122.7402 | 0.24719 | 0.18768 | 0.20142 | 0.15564 | 0.16937 | 0.20599 | 0.036621 | 0.21515 | 0.077819 | 0.013733 | 0.068664 | 2.9755 | 0.10071 | -119.8883 | -122.818 | 2.9984 | 0.10986 | 3.0624 | 0.16022
5828.125 | 122.8088 | -0.10986 | 122.7722 | -0.01976 | 0.0099506 | 0.0094208 | -0.0087222 | 0.0010125 | -0.010698 | -0.0028092 | -0.005371 | 0.020822 | 0.042421 | -0.015706 | 0.011907 | 0.020333 | -0.0051205 | 2.9617 | 2.9526 | 2.8793 | 2.8564 | 2.9892 | 2.8748 | 2.8702 | -0.041199 | 0.036621 | -0.054932 | -0.07782 | 0.054932 | 0.027466 | 0.032043 | 2.9892 | -119.8196 | -119.9158 | 3.0991 | 2.98 | 2.9846 | -0.009155 | -0.004577 | 0.054931 | -122.7356 | -122.85 | 0.16479 | 0.14191 | 0.13733 | 0.086975 | 0.082398 | 0.10986 | -0.022888 | 0.10986 | -0.022888 | 0.073243 | 0.091553 | 3.0624 | 0.14648 | -119.8929 | -122.8271 | 2.9663 | 0.032043 | 3.0716 | 0.068664
5829.9062 | 122.8546 | -0.10986 | 122.7448 | -0.012131 | 0.014437 | 0.0085662 | -0.0057314 | -0.0011237 | -0.0098438 | -0.00345 | -0.011475 | 0.022744 | 0.040499 | -0.020619 | 0.011907 | 0.021828 | -0.0042661 | 2.9526 | 2.9205 | 2.8519 | 2.829 | 2.9663 | 2.8427 | 2.8427 | 0.022888 | 0.032043 | -0.050354 | -0.018311 | 0.09613 | 0.045776 | 0.07782 | 2.9617 | -119.8242 | -119.9158 | 3.0762 | 2.9526 | 2.9526 | -0.009156 | -0.009156 | 0.059509 | -122.7127 | -122.7631 | 0.20599 | 0.18768 | 0.15564 | 0.12817 | 0.09613 | 0.11444 | -0.022889 | 0.14648 | 0.032043 | 0.068664 | 0.082397 | 3.0304 | 0.14191 | -119.8929 | -122.7951 | 2.9388 | 0.091552 | 3.0624 | 0.13275
5831.625 | 122.8455 | -0.09613 | 122.7814 | -0.01976 | 0.0123 | 0.0062164 | -0.0087222 | -0.0032599 | -0.0089892 | 0.0001816 | -0.005371 | 0.01954 | 0.039431 | -0.021687 | 0.012548 | 0.022896 | -0.0025571 | 2.9388 | 2.9388 | 2.8702 | 2.8336 | 2.9572 | 2.8473 | 2.861 | 0.009155 | 0.041199 | -0.068665 | -0.013733 | 0.082397 | 0.050354 | 0.073242 | 2.9663 | -119.8425 | -119.9478 | 3.0533 | 2.9572 | 2.9434 | -0.009155 | -0.022888 | 0.027465 | -122.7402 | -122.7951 | 0.17853 | 0.16937 | 0.14648 | 0.14191 | 0.11902 | 0.086975 | -0.036621 | 0.15106 | 0.054932 | 0.068665 | 0.10986 | 3.035 | 0.13733 | -119.9112 | -122.85 | 2.9297 | 0.082397 | 3.035 | 0.10528
5833.4062 | 122.7905 | -0.10529 | 122.7631 | -0.012131 | 0.015078 | 0.0083526 | -0.0085086 | 0.00015814 | -0.011125 | -0.0038772 | -0.0084228 | 0.020181 | 0.040926 | -0.021046 | 0.014471 | 0.024819 | -0.0083249 | 2.8702 | 2.8793 | 2.7878 | 2.7603 | 2.8839 | 2.7283 | 2.7695 | -0.041199 | 0.032043 | -0.054932 | -0.054932 | 0.032043 | -0.027466 | 0.022888 | 2.8931 | -119.8837 | -120.0027 | 2.9892 | 2.8748 | 2.8336 | -0.018311 | -0.05951 | 0.050354 | -122.731 | -122.818 | 0.13733 | 0.12817 | 0.07782 | 0.07782 | 0.027466 | 0.09613 | -0.027466 | 0.086975 | 0 | 0.091552 | 0.086975 | 2.9846 | 0.13733 | -119.9753 | -122.818 | 2.8656 | 0.050354 | 2.9755 | 0.064087
5835.125 | 122.9095 | -0.07782 | 122.7448 | -0.02739 | 0.011232 | 0.0068574 | -0.010858 | 0.0065667 | -0.01198 | -0.0019546 | -0.0084228 | 0.016549 | 0.04178 | -0.012929 | 0.010198 | 0.023751 | 0.0012881 | 2.8702 | 2.8244 | 2.7832 | 2.7924 | 2.9343 | 2.8107 | 2.8473 | 0.022888 | 0.004578 | -0.064087 | 0 | 0.13733 | 0.10071 | 0.09613 | 2.861 | -119.9203 | -119.9524 | 3.0121 | 2.9251 | 2.8885 | 0.064087 | 0.027466 | 0.013733 | -122.7402 | -122.7448 | 0.21515 | 0.17395 | 0.17853 | 0.16022 | 0.1648 | 0.15106 | 0.009155 | 0.20142 | 0.064087 | 0.041199 | 0.068665 | 2.9022 | 0.082398 | -119.9615 | -122.8088 | 2.8702 | 0.07782 | 2.948 | 0.10071
5836.9062 | 122.8317 | -0.10986 | 122.8043 | -0.012131 | 0.0099506 | 0.0085662 | -0.008295 | -0.00069646 | -0.01198 | -0.0057998 | -0.005371 | 0.019754 | 0.042208 | -0.017842 | 0.0099847 | 0.021614 | -0.0040525 | 2.9343 | 2.9526 | 2.8656 | 2.8244 | 2.9388 | 2.829 | 2.8748 | -0.054932 | 0.045776 | -0.064087 | -0.064087 | 0.045776 | 0.018311 | 0.041199 | 2.9755 | -119.8517 | -119.9799 | 3.0487 | 2.9846 | 2.9388 | 0.009155 | -0.036622 | 0.045776 | -122.7585 | -122.8683 | 0.15564 | 0.15106 | 0.12817 | 0.10529 | 0.082398 | 0.073242 | -0.041199 | 0.10986 | 0 | 0.086975 | 0.10986 | 3.0624 | 0.15564 | -119.9387 | -122.8683 | 2.9343 | 0.045776 | 3.0441 | 0.054931
5838.6875 | 122.8455 | -0.10071 | 122.7814 | -0.01976 | 0.01465 | 0.0096344 | -0.008295 | 0.00015814 | -0.011125 | -0.0032364 | -0.0084228 | 0.022744 | 0.042635 | -0.018483 | 0.01383 | 0.024178 | -0.0061887 | 2.916 | 2.8702 | 2.8244 | 2.8244 | 2.9343 | 2.8107 | 2.8381 | 0.041199 | 0.027466 | -0.050354 | 0 | 0.073242 | 0.045776 | 0.068665 | 2.9251 | -119.9112 | -119.957 | 3.035 | 2.9388 | 2.9114 | 0.013733 | -0.013733 | 0.050354 | -122.7539 | -122.7814 | 0.17395 | 0.16937 | 0.14648 | 0.11902 | 0.09613 | 0.10986 | 0 | 0.1236 | 0.050354 | 0.045776 | 0.07782 | 2.9709 | 0.12817 | -119.957 | -122.8317 | 2.9251 | 0.10071 | 3.0167 | 0.14191
5840.4219 | 122.8546 | -0.10529 | 122.8088 | -0.0045011 | 0.010591 | 0.0066436 | -0.0085086 | 0.0042169 | -0.011125 | -0.0043046 | -0.0084228 | 0.021463 | 0.040926 | -0.016347 | 0.013616 | 0.022683 | -0.0098203 | 2.9297 | 2.9343 | 2.8473 | 2.829 | 2.9526 | 2.861 | 2.861 | -0.050354 | 0.059509 | -0.064087 | -0.045776 | 0.07782 | 0.022888 | 0.064087 | 2.9526 | -119.8746 | -119.9799 | 3.0579 | 2.9663 | 2.9663 | 0.013733 | 0.013733 | 0.041199 | -122.7493 | -122.8546 | 0.18311 | 0.16937 | 0.12817 | 0.12817 | 0.086975 | 0.10529 | -0.018311 | 0.14191 | 0.018311 | 0.086975 | 0.1236 | 3.0396 | 0.16479 | -119.9615 | -122.8729 | 2.9343 | 0.05951 | 3.035 | 0.054932
5842.2031 | 122.9279 | -0.091553 | 122.7356 | -0.01976 | 0.011232 | 0.0079254 | -0.010858 | -0.0017645 | -0.012194 | -0.0030228 | -0.0023192 | 0.019326 | 0.040499 | -0.019124 | 0.010198 | 0.025032 | -0.0019163 | 2.8564 | 2.8152 | 2.7786 | 2.8015 | 2.9297 | 2.8336 | 2.8702 | 0.045776 | 0.036621 | -0.036621 | 0.009155 | 0.15106 | 0.12817 | 0.12817 | 2.8702 | -119.9203 | -119.9341 | 3.0212 | 2.9617 | 2.9251 | 0.091553 | 0.054932 | 0.054932 | -122.699 | -122.7264 | 0.24261 | 0.21973 | 0.21973 | 0.1648 | 0.1648 | 0.15106 | 0.022889 | 0.18768 | 0.045776 | 0.036622 | 0.073242 | 2.9068 | 0.12817 | -119.957 | -122.7722 | 2.8931 | 0.10071 | 2.948 | 0.13733
5843.9844 | 122.937 | -0.07782 | 122.7493 | -0.0045011 | 0.0099506 | 0.0083526 | -0.010004 | 0.0031487 | -0.010057 | -0.0043046 | -0.0084228 | 0.01954 | 0.039217 | -0.017628 | 0.0097711 | 0.023751 | -0.0027707 | 2.8564 | 2.829 | 2.8015 | 2.8244 | 2.9617 | 2.861 | 2.8793 | 0.068665 | 0.013733 | -0.045776 | 0.022888 | 0.16479 | 0.13275 | 0.12817 | 2.8793 | -119.9203 | -119.9249 | 3.0396 | 2.9572 | 2.9388 | 0.077819 | 0.059509 | 0.032044 | -122.7356 | -122.7264 | 0.24261 | 0.20599 | 0.21057 | 0.17395 | 0.17853 | 0.16022 | 0.022888 | 0.21057 | 0.068664 | 0.027465 | 0.059509 | 2.9068 | 0.091553 | -119.9478 | -122.7951 | 2.9022 | 0.10071 | 2.9343 | 0.14649
5845.7656 | 122.7997 | -0.10071 | 122.7768 | -0.012131 | 0.014223 | 0.0096344 | -0.0085086 | 0.0037897 | -0.010485 | -0.0025956 | -0.0084228 | 0.021676 | 0.040285 | -0.012929 | 0.01148 | 0.022683 | -0.0034117 | 2.8381 | 2.8107 | 2.7557 | 2.7054 | 2.829 | 2.7008 | 2.7145 | -0.041199 | 0.036621 | -0.073242 | -0.073242 | 0.013733 | -0.032043 | 0.032043 | 2.8564 | -119.9661 | -120.0714 | 2.9297 | 2.8152 | 2.8015 | -0.041198 | -0.054931 | 0.027466 | -122.7402 | -122.85 | 0.11444 | 0.13275 | 0.068665 | 0.10529 | 0.041199 | 0.073242 | -0.050354 | 0.086975 | 0 | 0.054932 | 0.10986 | 2.9114 | 0.13733 | -120.0211 | -122.85 | 2.8061 | 0.027466 | 2.9388 | 0.059509
5847.4844 | 122.8226 | -0.10529 | 122.7905 | -0.012131 | 0.014437 | 0.0092072 | -0.0072268 | 0.0035761 | -0.0094164 | -0.0045182 | -0.005371 | 0.02189 | 0.040712 | -0.0084423 | 0.013403 | 0.022469 | -0.0034117 | 2.9114 | 2.861 | 2.7969 | 2.7878 | 2.916 | 2.7924 | 2.8061 | 0.022888 | 0.036621 | -0.050354 | -0.018311 | 0.059509 | 0.022888 | 0.059509 | 2.9022 | -119.9295 | -120.0027 | 3.0212 | 2.9114 | 2.8976 | 0.009155 | -0.004578 | 0.054932 | -122.7539 | -122.8088 | 0.16479 | 0.16479 | 0.12817 | 0.10986 | 0.073242 | 0.11902 | -0.009155 | 0.10986 | 0.032043 | 0.064087 | 0.086975 | 2.9663 | 0.14191 | -119.9936 | -122.8409 | 2.8931 | 0.086975 | 3.0167 | 0.12817
5849.25 | 122.85 | -0.082397 | 122.7722 | -0.02739 | 0.012514 | 0.0089936 | -0.011286 | -0.00091006 | -0.012194 | -0.0040908 | -0.005371 | 0.020822 | 0.03879 | -0.017201 | 0.0089167 | 0.021828 | 0.0025699 | 2.9434 | 2.8519 | 2.8381 | 2.8976 | 3.0258 | 2.9114 | 2.9297 | 0.032043 | 0.022888 | -0.045776 | -0.018311 | 0.11444 | 0.068665 | 0.086975 | 2.9205 | -119.9203 | -119.8746 | 3.1082 | 3.0121 | 2.9938 | 0.091552 | 0.073242 | 0.036621 | -122.7493 | -122.7905 | 0.19684 | 0.16937 | 0.15106 | 0.13275 | 0.11444 | 0.18768 | 0.059509 | 0.16022 | 0.027465 | 0.013733 | 0.068664 | 2.9343 | 0.10528 | -119.9341 | -122.818 | 2.98 | 0.064086 | 3.0258 | 0.11444
5851.0312 | 122.8043 | -0.11902 | 122.7951 | -0.02739 | 0.014009 | 0.0092072 | -0.0087222 | 0.0027215 | -0.008562 | -0.0057998 | -0.0023192 | 0.021035 | 0.040499 | -0.014424 | 0.010626 | 0.023964 | -0.0017027 | 2.7924 | 2.8015 | 2.7328 | 2.6596 | 2.7512 | 2.6413 | 2.6825 | -0.07782 | 0.050354 | -0.082397 | -0.068665 | 0 | -0.027466 | 0.032043 | 2.8519 | -119.9936 | -120.1355 | 2.8702 | 2.8015 | 2.7603 | -0.050354 | -0.091553 | 0.036622 | -122.7448 | -122.8638 | 0.11902 | 0.15106 | 0.091553 | 0.11444 | 0.054931 | 0.018311 | -0.073242 | 0.082397 | 0.013732 | 0.068665 | 0.13275 | 2.9205 | 0.16937 | -120.0623 | -122.8775 | 2.7786 | 0.050354 | 2.9114 | 0.041199
5852.8281 | 122.8226 | -0.10986 | 122.7768 | -0.01976 | 0.0095234 | 0.008139 | -0.011286 | -5.5462e-05 | -0.010057 | -0.0021682 | -0.005371 | 0.020181 | 0.040499 | -0.020833 | 0.011266 | 0.019478 | -0.0049069 | 2.9297 | 2.8748 | 2.8519 | 2.8427 | 2.9755 | 2.8473 | 2.8793 | -0.009155 | 0.041199 | -0.064087 | -0.064087 | 0.050354 | 0.022888 | 0.032043 | 2.9617 | -119.902 | -119.9341 | 3.0853 | 2.9892 | 2.9572 | 0.027465 | -0.004578 | 0.045776 | -122.7356 | -122.8409 | 0.16022 | 0.14191 | 0.13275 | 0.09613 | 0.086975 | 0.1236 | -0.009156 | 0.11444 | 0 | 0.022888 | 0.10529 | 2.9846 | 0.15106 | -119.9249 | -122.8409 | 2.9526 | 0.045776 | 3.0395 | 0.10071
5854.5469 | 122.818 | -0.10986 | 122.7859 | -0.01976 | 0.013582 | 0.0089936 | -0.010431 | 0.0012261 | -0.0094164 | -0.0032364 | -0.005371 | 0.021249 | 0.044344 | -0.016774 | 0.012334 | 0.023323 | -0.0017027 | 2.7557 | 2.8015 | 2.7008 | 2.6321 | 2.7466 | 2.623 | 2.6825 | -0.054932 | 0.054932 | -0.073242 | -0.050354 | 0.018311 | -0.018311 | 0.027466 | 2.8107 | -119.9844 | -120.1538 | 2.8564 | 2.7924 | 2.7328 | -0.018311 | -0.07782 | 0.036621 | -122.731 | -122.8363 | 0.12817 | 0.13733 | 0.091552 | 0.10071 | 0.054931 | 0.045776 | -0.068665 | 0.091553 | 0.022888 | 0.10071 | 0.12817 | 2.9114 | 0.16479 | -120.0851 | -122.8592 | 2.742 | 0.059509 | 2.8656 | 0.054931
5856.3125 | 122.8638 | -0.10071 | 122.7951 | -0.012131 | 0.01166 | 0.0068574 | -0.0085086 | -0.0015509 | -0.011339 | -0.0032364 | -0.005371 | 0.020608 | 0.042208 | -0.013997 | 0.01148 | 0.023537 | -0.0044797 | 2.916 | 2.8793 | 2.8198 | 2.7878 | 2.9297 | 2.8244 | 2.8015 | 0.013733 | 0.036621 | -0.050354 | -0.022888 | 0.09613 | 0.050354 | 0.082397 | 2.9205 | -119.9158 | -120.0073 | 3.0304 | 2.9022 | 2.9251 | -0.01831 | 0.004578 | 0.050354 | -122.7585 | -122.818 | 0.19684 | 0.18311 | 0.15106 | 0.13275 | 0.10071 | 0.10986 | -0.032043 | 0.14648 | 0.027466 | 0.059509 | 0.086975 | 2.98 | 0.13733 | -119.9753 | -122.8455 | 2.8885 | 0.07782 | 3.0167 | 0.11444
5858.0938 | 122.8043 | -0.10529 | 122.7814 | -0.01976 | 0.014864 | 0.008139 | -0.008295 | 0.0020807 | -0.0079212 | -0.0032364 | -0.0084228 | 0.021249 | 0.041994 | -0.022328 | 0.013616 | 0.022255 | -0.0044797 | 2.8107 | 2.8107 | 2.7466 | 2.71 | 2.8381 | 2.6825 | 2.7237 | -0.050354 | 0.036621 | -0.07782 | -0.068665 | 0.009155 | -0.022888 | 0.018311 | 2.8519 | -119.9707 | -120.0714 | 2.9434 | 2.829 | 2.7878 | -0.022888 | -0.064087 | 0.027466 | -122.7448 | -122.85 | 0.11444 | 0.1236 | 0.082398 | 0.096131 | 0.054932 | 0.091553 | -0.036621 | 0.086975 | 0.009155 | 0.064087 | 0.11444 | 2.916 | 0.14191 | -120.0348 | -122.8592 | 2.8152 | 0.036621 | 2.916 | 0.054932
5859.875 | 122.8775 | -0.068665 | 122.7631 | -0.012131 | 0.013369 | 0.00878 | -0.0095766 | 0.0025079 | -0.010485 | -0.005159 | -0.0084228 | 0.017831 | 0.039858 | -0.022969 | 0.0084893 | 0.021614 | 0.00021995 | 2.7832 | 2.742 | 2.7008 | 2.7283 | 2.8793 | 2.7328 | 2.7832 | 0.018311 | 0.013733 | -0.041199 | 0.004578 | 0.10071 | 0.07782 | 0.10071 | 2.7695 | -120.0211 | -120.0348 | 2.948 | 2.8519 | 2.8015 | 0.082397 | 0.032043 | 0.027466 | -122.7493 | -122.7585 | 0.16937 | 0.16937 | 0.14649 | 0.14191 | 0.11902 | 0.17853 | 0.027465 | 0.14191 | 0.045777 | 0.041198 | 0.054932 | 2.8107 | 0.082398 | -120.0623 | -122.8043 | 2.7969 | 0.073243 | 2.8519 | 0.086976
5861.5781 | 122.8317 | -0.11902 | 122.7905 | -0.012131 | 0.012514 | 0.0062164 | -0.011072 | 0.0010125 | -0.011125 | -0.0043046 | -0.0084228 | 0.020822 | 0.042635 | -0.022542 | 0.0095575 | 0.024178 | -0.0044797 | 2.8976 | 2.9114 | 2.8244 | 2.7924 | 2.9114 | 2.8015 | 2.8244 | -0.073242 | 0.050354 | -0.07782 | -0.07782 | 0.041199 | 0 | 0.045776 | 2.9434 | -119.8791 | -119.9982 | 3.0304 | 2.9434 | 2.9205 | 0 | -0.022888 | 0.041199 | -122.7402 | -122.8683 | 0.16022 | 0.16479 | 0.11902 | 0.1236 | 0.07782 | 0.086975 | -0.032044 | 0.11902 | 0 | 0.086975 | 0.12817 | 3.0304 | 0.16937 | -119.9661 | -122.8683 | 2.9114 | 0.041199 | 3.0167 | 0.045777
5863.3438 | 122.8546 | -0.09613 | 122.7905 | -0.012131 | 0.013796 | 0.0077118 | -0.0089358 | -0.00026906 | -0.011766 | -0.0015274 | -0.011475 | 0.021249 | 0.04114 | -0.012501 | 0.0097711 | 0.021828 | 0.0010745 | 2.8976 | 2.8976 | 2.8107 | 2.7832 | 2.9068 | 2.8152 | 2.8061 | -0.004578 | 0.032043 | -0.045776 | -0.027466 | 0.091553 | 0.022888 | 0.07782 | 2.9068 | -119.8929 | -120.0073 | 3.0029 | 2.9022 | 2.9114 | -0.004578 | 0.004578 | 0.050354 | -122.7585 | -122.818 | 0.18768 | 0.17395 | 0.11902 | 0.1236 | 0.068664 | 0.09613 | -0.027466 | 0.13733 | 0.01831 | 0.086975 | 0.077819 | 2.9938 | 0.12817 | -119.9799 | -122.8363 | 2.8793 | 0.068664 | 2.9938 | 0.091552
5865.0625 | 122.8134 | -0.10071 | 122.7905 | -0.0045011 | 0.010164 | 0.010062 | -0.010218 | -0.0013373 | -0.011553 | -0.0049454 | -0.011475 | 0.018686 | 0.039431 | -0.022328 | 0.010412 | 0.02311 | -0.0053343 | 2.9205 | 2.8519 | 2.8381 | 2.8061 | 2.948 | 2.8381 | 2.8519 | -0.022888 | 0.009155 | -0.064087 | -0.073242 | 0.059509 | 0.018311 | 0.032043 | 2.9388 | -119.9387 | -119.9844 | 3.0487 | 2.9526 | 2.9388 | 0.013733 | 0 | 0.036621 | -122.7814 | -122.8638 | 0.16022 | 0.13275 | 0.11902 | 0.09613 | 0.082398 | 0.10986 | -0.032044 | 0.1236 | -0.009155 | 0.013733 | 0.073242 | 2.9526 | 0.10986 | -119.9524 | -122.8546 | 2.9068 | 0.027466 | 3.0212 | 0.07782
5866.8281 | 122.8088 | -0.11902 | 122.7951 | -0.0045011 | 0.011873 | 0.0049346 | -0.0080814 | -0.0047553 | -0.010698 | -0.0025956 | -0.0084228 | 0.019754 | 0.039858 | -0.015492 | 0.0097711 | 0.023537 | -0.0053343 | 2.8793 | 2.8885 | 2.7969 | 2.774 | 2.8976 | 2.8061 | 2.8152 | -0.073242 | 0.045776 | -0.068665 | -0.086975 | 0.032043 | 0 | 0.041199 | 2.916 | -119.9066 | -120.0211 | 3.0167 | 2.9343 | 2.9251 | 0.018311 | 0.009155 | 0.050354 | -122.7493 | -122.8821 | 0.15106 | 0.16022 | 0.11902 | 0.10986 | 0.068665 | 0.10071 | -0.022888 | 0.10071 | -0.01831 | 0.091553 | 0.11444 | 3.0075 | 0.16479 | -119.9982 | -122.8638 | 2.8931 | 0.032044 | 2.9984 | 0.045777
5868.6094 | 122.818 | -0.11444 | 122.7997 | -0.012131 | 0.016359 | 0.0092072 | -0.0078676 | 0.0022943 | -0.0087756 | -0.002382 | -0.0023192 | 0.022317 | 0.042421 | -0.017842 | 0.011053 | 0.022683 | -0.0027707 | 2.7603 | 2.7512 | 2.6779 | 2.6138 | 2.71 | 2.6184 | 2.6505 | -0.059509 | 0.041199 | -0.068665 | -0.068665 | 0.013733 | -0.013733 | 0.027466 | 2.7924 | -120.0485 | -120.1859 | 2.8244 | 2.7649 | 2.7328 | -0.027465 | -0.059509 | 0.045776 | -122.7585 | -122.8683 | 0.12817 | 0.14191 | 0.10071 | 0.096131 | 0.054932 | 0.032044 | -0.064086 | 0.082398 | 0 | 0.073243 | 0.10986 | 2.8656 | 0.15564 | -120.1218 | -122.8683 | 2.7283 | 0.045776 | 2.8748 | 0.054932
5870.3438 | 122.8363 | -0.10071 | 122.8043 | -0.01976 | 0.012087 | 0.0077118 | -0.0078676 | 0.0031487 | -0.011766 | -0.001741 | -0.0023192 | 0.021035 | 0.040926 | -0.015492 | 0.011266 | 0.022896 | -0.0044797 | 2.7374 | 2.7466 | 2.6642 | 2.6321 | 2.7374 | 2.6093 | 2.6505 | -0.027466 | 0.018311 | -0.086975 | -0.054932 | 0.041199 | 0.004578 | 0.050354 | 2.7649 | -120.0577 | -120.1721 | 2.8381 | 2.7512 | 2.71 | -0.013733 | -0.054932 | 0.013733 | -122.7859 | -122.8592 | 0.14191 | 0.15106 | 0.10529 | 0.13733 | 0.091553 | 0.073242 | -0.032044 | 0.12817 | 0.032043 | 0.082397 | 0.10529 | 2.8473 | 0.11902 | -120.1401 | -122.8912 | 2.7328 | 0.045776 | 2.8381 | 0.073242
5872.125 | 122.8363 | -0.10529 | 122.7768 | -0.01976 | 0.0099506 | 0.007071 | -0.010218 | 0.0014397 | -0.010698 | -0.0032364 | -0.011475 | 0.019326 | 0.04178 | -0.02361 | 0.0074213 | 0.023323 | -0.0040525 | 2.9068 | 2.8381 | 2.8015 | 2.8198 | 2.9846 | 2.8564 | 2.8702 | 0.027466 | 0.027466 | -0.054932 | -0.050354 | 0.07782 | 0.054932 | 0.059509 | 2.9068 | -119.9387 | -119.957 | 3.0899 | 2.9755 | 2.9617 | 0.068664 | 0.054931 | 0.050354 | -122.7493 | -122.8271 | 0.18311 | 0.16479 | 0.16022 | 0.11444 | 0.10986 | 0.1831 | 0.01831 | 0.13275 | 0.004578 | 0.036621 | 0.082398 | 2.9434 | 0.13275 | -119.9753 | -122.8317 | 2.9251 | 0.054932 | 3.0121 | 0.13275
5873.9062 | 122.8226 | -0.11444 | 122.7814 | -0.02739 | 0.015291 | 0.0092072 | -0.0055178 | 0.0046441 | -0.010057 | -0.0032364 | -0.0023192 | 0.019967 | 0.041353 | -0.01421 | 0.012975 | 0.023751 | -0.0023435 | 2.8198 | 2.7924 | 2.7237 | 2.6962 | 2.8107 | 2.6779 | 2.7008 | -0.036621 | 0.036621 | -0.050354 | -0.054932 | 0.036621 | -0.018311 | 0.032043 | 2.8381 | -119.989 | -120.0851 | 2.9251 | 2.8152 | 2.7924 | -0.022888 | -0.045777 | 0.064087 | -122.7448 | -122.8363 | 0.15106 | 0.14648 | 0.09613 | 0.082397 | 0.032043 | 0.086975 | -0.027466 | 0.086975 | -0.004578 | 0.068664 | 0.086975 | 2.9068 | 0.15106 | -120.0577 | -122.8317 | 2.8107 | 0.059509 | 2.9343 | 0.07782
5875.6875 | 122.905 | -0.082397 | 122.7448 | -0.02739 | 0.0123 | 0.0079254 | -0.010431 | -0.0024055 | -0.010485 | -0.0040908 | -0.014526 | 0.016763 | 0.040071 | -0.018483 | 0.0091303 | 0.022896 | -0.0029843 | 2.7695 | 2.6962 | 2.6871 | 2.6917 | 2.8564 | 2.7054 | 2.742 | 0.041199 | 0.009155 | -0.045776 | 0.009155 | 0.10986 | 0.086975 | 0.10071 | 2.7695 | -120.0485 | -120.0531 | 2.9388 | 2.8244 | 2.7878 | 0.054931 | 0.01831 | 0.036621 | -122.7356 | -122.7356 | 0.19226 | 0.18311 | 0.16937 | 0.14648 | 0.13275 | 0.16937 | 0.004577 | 0.15564 | 0.054931 | 0.009155 | 0.054931 | 2.7786 | 0.091552 | -120.0577 | -122.7905 | 2.774 | 0.091552 | 2.8519 | 0.1236
5877.4688 | 122.9324 | -0.059509 | 122.7722 | -0.0045011 | 0.008028 | 0.0057892 | -0.010645 | 0.0016535 | -0.011553 | -0.0045182 | -0.011475 | 0.017831 | 0.03879 | -0.015706 | 0.0089167 | 0.021828 | -0.0019163 | 2.8015 | 2.7374 | 2.7283 | 2.7695 | 2.8931 | 2.7878 | 2.8244 | 0.054932 | -0.013733 | -0.032043 | 0.027466 | 0.16937 | 0.13733 | 0.13733 | 2.7878 | -120.0348 | -120.0027 | 2.9526 | 2.8839 | 2.8473 | 0.096131 | 0.05951 | 0.027466 | -122.7859 | -122.7448 | 0.22888 | 0.19684 | 0.19684 | 0.16937 | 0.16937 | 0.1648 | 0.041199 | 0.20142 | 0.059509 | 0.009156 | 0.01831 | 2.7969 | 0.045776 | -120.0439 | -122.8043 | 2.829 | 0.086975 | 2.861 | 0.11444
5879.1875 | 122.8683 | -0.086975 | 122.7768 | -0.012131 | 0.013796 | 0.0085662 | -0.0097904 | 0.0031487 | -0.0094164 | -0.0025956 | -0.005371 | 0.022103 | 0.038149 | -0.015065 | 0.010839 | 0.021187 | -0.0029843 | 2.8564 | 2.8381 | 2.7466 | 2.7695 | 2.861 | 2.7603 | 2.774 | 0.027466 | 0.045776 | -0.059509 | -0.022888 | 0.082397 | 0.050354 | 0.068665 | 2.8336 | -119.9387 | -120.0073 | 2.948 | 2.861 | 2.8473 | 0.027466 | 0.013733 | 0.027466 | -122.731 | -122.7997 | 0.16937 | 0.15564 | 0.13733 | 0.12817 | 0.10986 | 0.11444 | 0.022888 | 0.14191 | 0.036621 | 0.091553 | 0.10528 | 2.9251 | 0.13275 | -120.0302 | -122.8363 | 2.8564 | 0.064087 | 2.9434 | 0.11444
5880.9688 | 122.8455 | -0.073242 | 122.7814 | -0.012131 | 0.0088824 | 0.0079254 | -0.013208 | -0.00048286 | -0.010912 | -0.0053726 | -0.0084228 | 0.01954 | 0.040926 | -0.016347 | 0.0080621 | 0.020974 | -0.00063445 | 2.8931 | 2.8061 | 2.7695 | 2.8198 | 2.9617 | 2.861 | 2.8656 | 0.036621 | 0.022888 | -0.050354 | -0.036621 | 0.09613 | 0.045776 | 0.064087 | 2.8427 | -119.9753 | -119.9615 | 3.035 | 2.9388 | 2.9343 | 0.096131 | 0.091553 | 0.022888 | -122.7585 | -122.818 | 0.16937 | 0.13733 | 0.11902 | 0.11444 | 0.09613 | 0.19226 | 0.050354 | 0.14648 | 0.013733 | 0.036621 | 0.073242 | 2.8793 | 0.09613 | -120.0119 | -122.8317 | 2.8931 | 0.036621 | 2.9663 | 0.10986
5882.7656 | 122.8592 | -0.091553 | 122.7539 | -0.01976 | 0.013582 | 0.0089936 | -0.0080814 | -0.00026906 | -0.010698 | -0.0030228 | -0.011475 | 0.020395 | 0.041994 | -0.013783 | 0.01148 | 0.022896 | -0.0044797 | 2.7374 | 2.7374 | 2.6505 | 2.623 | 2.7328 | 2.5909 | 2.6276 | -0.013733 | 0.027466 | -0.050354 | -0.027466 | 0.064087 | 0.018311 | 0.068665 | 2.742 | -120.0165 | -120.1309 | 2.8244 | 2.7191 | 2.6825 | -0.022889 | -0.05951 | 0.041199 | -122.7264 | -122.7814 | 0.15564 | 0.16022 | 0.10986 | 0.11902 | 0.068665 | 0.082397 | -0.027466 | 0.11444 | 0.022888 | 0.086975 | 0.07782 | 2.829 | 0.11902 | -120.1035 | -122.8043 | 2.7145 | 0.064087 | 2.829 | 0.07782
5884.4844 | 122.9324 | -0.054932 | 122.7448 | -0.02739 | 0.0086688 | 0.0079254 | -0.010431 | -0.0011237 | -0.012194 | -0.0053726 | -0.0084228 | 0.019326 | 0.040499 | -0.02126 | 0.0095575 | 0.022042 | -0.0038389 | 2.8152 | 2.7649 | 2.71 | 2.7512 | 2.8931 | 2.7832 | 2.829 | 0.07782 | 0.009155 | -0.045776 | 0.032043 | 0.17395 | 0.14191 | 0.13733 | 2.7649 | -119.9799 | -119.9936 | 2.948 | 2.8839 | 2.8381 | 0.11902 | 0.073242 | 0.009156 | -122.7356 | -122.7127 | 0.22888 | 0.19226 | 0.19684 | 0.18311 | 0.18768 | 0.18311 | 0.041199 | 0.21973 | 0.077819 | 0.054932 | 0.054931 | 2.8198 | 0.064087 | -120.0348 | -122.7905 | 2.8061 | 0.086975 | 2.8702 | 0.13275
5886.2656 | 122.9279 | -0.059509 | 122.7631 | -0.012131 | 0.012087 | 0.0092072 | -0.0085086 | 0.00037174 | -0.0087756 | -0.0040908 | -0.0084228 | 0.019967 | 0.042208 | -0.015278 | 0.011266 | 0.023323 | -0.0021299 | 2.7374 | 2.6688 | 2.6321 | 2.6688 | 2.7786 | 2.6413 | 2.6917 | 0.086975 | 0.022888 | -0.036621 | 0.050354 | 0.13275 | 0.10529 | 0.13733 | 2.6916 | -120.0943 | -120.0943 | 2.8381 | 2.7512 | 2.7008 | 0.059509 | 0.009155 | 0.022888 | -122.7402 | -122.7127 | 0.19226 | 0.19684 | 0.16479 | 0.17395 | 0.14191 | 0.14648 | 0.036621 | 0.16937 | 0.086975 | 0.036621 | 0.059509 | 2.7283 | 0.082397 | -120.1309 | -122.7997 | 2.7283 | 0.10986 | 2.7969 | 0.14648
5888.0469 | 122.8592 | -0.086975 | 122.7814 | -0.012131 | 0.012728 | 0.0077118 | -0.007654 | 0.0014397 | -0.0083484 | -0.0040908 | -0.0084228 | 0.021035 | 0.040926 | -0.012288 | 0.012334 | 0.02311 | -0.0087521 | 2.861 | 2.7969 | 2.7283 | 2.7283 | 2.8564 | 2.7191 | 2.7603 | 0.032043 | 0.032043 | -0.050354 | -0.013733 | 0.09613 | 0.045776 | 0.073242 | 2.8152 | -119.9844 | -120.0531 | 2.9434 | 2.8473 | 2.8061 | 0.032044 | -0.009155 | 0.036621 | -122.7493 | -122.7951 | 0.1831 | 0.16022 | 0.13275 | 0.1236 | 0.09613 | 0.12817 | 0 | 0.14648 | 0.036621 | 0.068665 | 0.082397 | 2.8839 | 0.11902 | -120.0531 | -122.8317 | 2.8152 | 0.073242 | 2.948 | 0.11902
5889.7656 | 122.9553 | -0.07782 | 122.7356 | -0.01976 | 0.0099506 | 0.0077118 | -0.009363 | 0.0046441 | -0.0092028 | -0.0036636 | -0.005371 | 0.01719 | 0.037508 | -0.020192 | 0.0087029 | 0.022683 | -0.0061887 | 2.7969 | 2.7374 | 2.7008 | 2.7512 | 2.8931 | 2.7832 | 2.8198 | 0.086975 | 0.004578 | -0.036621 | 0.032043 | 0.16937 | 0.14648 | 0.14191 | 2.7786 | -119.9982 | -119.9844 | 2.9709 | 2.8976 | 2.861 | 0.11902 | 0.082397 | 0.041199 | -122.731 | -122.7036 | 0.24719 | 0.21973 | 0.2243 | 0.17853 | 0.18311 | 0.19226 | 0.050354 | 0.20599 | 0.068664 | 0.036621 | 0.041199 | 2.8152 | 0.082398 | -120.0348 | -122.7722 | 2.829 | 0.10986 | 2.8748 | 0.16479
5891.5469 | 122.9736 | -0.068665 | 122.7676 | -0.01976 | 0.010591 | 0.00878 | -0.0097904 | 0.00058534 | -0.011339 | -0.0043046 | -0.005371 | 0.020822 | 0.039644 | -0.015492 | 0.0082757 | 0.023323 | -0.0044797 | 2.8702 | 2.742 | 2.7603 | 2.8061 | 2.9755 | 2.829 | 2.8702 | 0.15564 | 0.009155 | -0.022888 | 0.041199 | 0.1831 | 0.15106 | 0.13275 | 2.829 | -120.0256 | -119.9615 | 3.0441 | 2.9388 | 2.8976 | 0.10986 | 0.068664 | 0.045777 | -122.7585 | -122.7264 | 0.25177 | 0.20142 | 0.21973 | 0.15564 | 0.17395 | 0.21515 | 0.045776 | 0.20599 | 0.064087 | -0.018311 | 0.032043 | 2.8107 | 0.07782 | -120.0073 | -122.7905 | 2.8748 | 0.10986 | 2.9388 | 0.22431
5893.3281 | 122.8546 | -0.11902 | 122.8134 | -0.01976 | 0.012941 | 0.0079254 | -0.007654 | 0.00058534 | -0.011766 | -0.0047318 | -0.011475 | 0.022103 | 0.040926 | -0.01122 | 0.0099847 | 0.020333 | -0.0064023 | 2.8427 | 2.8519 | 2.7695 | 2.7283 | 2.8244 | 2.7328 | 2.774 | -0.068665 | 0.041199 | -0.068665 | -0.07782 | 0.045776 | 0.013733 | 0.054932 | 2.8885 | -119.9615 | -120.0851 | 2.9434 | 2.8931 | 2.8519 | 0.004578 | -0.036621 | 0.050354 | -122.7722 | -122.8912 | 0.16479 | 0.17395 | 0.13275 | 0.1236 | 0.082398 | 0.054932 | -0.041199 | 0.11444 | -0.009155 | 0.082398 | 0.10986 | 2.9709 | 0.16022 | -120.0439 | -122.8821 | 2.8473 | 0.041199 | 2.9617 | 0.050354
5895.1094 | 122.9553 | -0.073242 | 122.7539 | -0.01976 | 0.01465 | 0.0092072 | -0.007654 | 0.00058534 | -0.008562 | -0.0036636 | -0.0084228 | 0.019326 | 0.041567 | -0.014424 | 0.0084893 | 0.023751 | -0.0042661 | 2.7786 | 2.6413 | 2.6276 | 2.6733 | 2.8061 | 2.6688 | 2.6962 | 0.10529 | 0.009155 | -0.032043 | 0.073242 | 0.16479 | 0.1236 | 0.15564 | 2.7008 | -120.1126 | -120.0806 | 2.8793 | 2.7695 | 2.742 | 0.068665 | 0.041199 | 0.041199 | -122.7448 | -122.6807 | 0.23804 | 0.22888 | 0.19684 | 0.18768 | 0.15564 | 0.17853 | 0.045777 | 0.19684 | 0.10529 | 0.013733 | 0.041198 | 2.7145 | 0.082397 | -120.1263 | -122.7859 | 2.7466 | 0.14648 | 2.8519 | 0.17853
5896.875 | 122.8867 | -0.086975 | 122.7585 | -0.01976 | 0.011873 | 0.0085662 | -0.010218 | -5.5462e-05 | -0.0072802 | -0.0038772 | -0.011475 | 0.018472 | 0.041567 | -0.013569 | 0.0093439 | 0.022469 | -0.0036253 | 2.7557 | 2.6962 | 2.6733 | 2.6779 | 2.8061 | 2.6779 | 2.7283 | 0.018311 | 0.004578 | -0.041199 | -0.013733 | 0.10071 | 0.054932 | 0.091553 | 2.7603 | -120.0623 | -120.0806 | 2.8931 | 2.8152 | 2.7649 | 0.054931 | 0.004577 | 0.045776 | -122.7539 | -122.7722 | 0.18768 | 0.17853 | 0.14191 | 0.13275 | 0.096131 | 0.13275 | 0.004577 | 0.14191 | 0.027466 | 0.022888 | 0.045777 | 2.7832 | 0.091553 | -120.0851 | -122.7997 | 2.7649 | 0.073242 | 2.8427 | 0.10529
5898.5938 | 122.8271 | -0.10071 | 122.7905 | -0.02739 | 0.012728 | 0.0089936 | -0.0057314 | 0.0027215 | -0.0074938 | -0.005159 | -0.005371 | 0.022744 | 0.040071 | -0.012501 | 0.013403 | 0.021828 | 0.00064735 | 2.7008 | 2.7237 | 2.6321 | 2.5726 | 2.6688 | 2.5543 | 2.6093 | -0.07782 | 0.027466 | -0.068665 | -0.068665 | 0.004578 | -0.036621 | 0.036621 | 2.7328 | -120.0668 | -120.2179 | 2.7695 | 2.71 | 2.655 | -0.022888 | -0.07782 | 0.032043 | -122.7631 | -122.8592 | 0.10529 | 0.13733 | 0.064087 | 0.10529 | 0.032044 | 0.036621 | -0.059509 | 0.073243 | 0 | 0.091553 | 0.096131 | 2.8244 | 0.12817 | -120.1584 | -122.8592 | 2.6733 | 0.032043 | 2.8015 | 0.022888
5900.3906 | 122.818 | -0.10986 | 122.8043 | -0.02739 | 0.012087 | 0.0077118 | -0.0095766 | -0.0026191 | -0.011125 | -0.000673 | -0.005371 | 0.021676 | 0.04178 | -0.018055 | 0.011053 | 0.021828 | -0.0040525 | 2.7878 | 2.8519 | 2.7374 | 2.7008 | 2.8656 | 2.7512 | 2.7695 | -0.07782 | 0.036621 | -0.073242 | -0.091553 | 0.027466 | -0.004578 | 0.032043 | 2.8473 | -119.9524 | -120.1035 | 2.9755 | 2.8793 | 2.861 | 0.032043 | 0.013733 | 0.036621 | -122.7676 | -122.8958 | 0.13733 | 0.14191 | 0.10529 | 0.10529 | 0.068664 | 0.12817 | -0.036621 | 0.10071 | -0.018311 | 0.11444 | 0.10986 | 2.9617 | 0.14648 | -120.0668 | -122.8775 | 2.8107 | 0.01831 | 2.8976 | 0.032043
5902.1719 | 122.9004 | -0.07782 | 122.7631 | -0.012131 | 0.0099506 | 0.0077118 | -0.010431 | -0.0024055 | -0.011125 | -0.005159 | -0.011475 | 0.01954 | 0.042635 | -0.021687 | 0.0078485 | 0.022683 | -0.0031979 | 2.7466 | 2.6825 | 2.655 | 2.6733 | 2.7969 | 2.6733 | 2.7191 | 0.009155 | 0.009155 | -0.045776 | 0 | 0.10071 | 0.064087 | 0.086975 | 2.7328 | -120.0806 | -120.0897 | 2.8748 | 2.7969 | 2.7512 | 0.064087 | 0.018311 | 0.032044 | -122.7539 | -122.7631 | 0.17853 | 0.16479 | 0.14191 | 0.13275 | 0.10986 | 0.14191 | 0.018311 | 0.14648 | 0.045776 | 0.027466 | 0.054931 | 2.7603 | 0.086975 | -120.108 | -122.8088 | 2.7512 | 0.07782 | 2.8244 | 0.086975
5903.8906 | 122.9736 | -0.064087 | 122.7722 | -0.01976 | 0.011232 | 0.0094208 | -0.0091494 | 0.0037897 | -0.010698 | -0.00345 | -0.011475 | 0.019113 | 0.040285 | -0.020833 | 0.0095575 | 0.022255 | -0.0038389 | 2.8244 | 2.7237 | 2.7191 | 2.7832 | 2.9343 | 2.7878 | 2.8336 | 0.12817 | 0 | -0.045776 | 0.059509 | 0.17853 | 0.14191 | 0.12817 | 2.7832 | -120.0485 | -119.989 | 2.9984 | 2.8976 | 2.8519 | 0.11444 | 0.068665 | 0.018311 | -122.7722 | -122.7127 | 0.24261 | 0.19226 | 0.20599 | 0.17395 | 0.18768 | 0.21515 | 0.064087 | 0.2243 | 0.10528 | 0.004578 | 0.045776 | 2.7878 | 0.064087 | -120.0531 | -122.818 | 2.8473 | 0.1236 | 2.8885 | 0.19226
5905.6719 | 122.8592 | -0.10529 | 122.8226 | -0.012131 | 0.012087 | 0.0085662 | -0.0085086 | 0.0059259 | -0.010912 | -0.0055862 | -0.005371 | 0.021676 | 0.040285 | -0.014424 | 0.01148 | 0.021828 | -0.00084805 | 2.8198 | 2.8152 | 2.7466 | 2.6962 | 2.8061 | 2.71 | 2.7374 | -0.054932 | 0.045776 | -0.054932 | -0.059509 | 0.064087 | 0.027466 | 0.041199 | 2.8519 | -120.0073 | -120.1263 | 2.9114 | 2.8427 | 2.8152 | -0.009155 | -0.036621 | 0.050354 | -122.7768 | -122.8821 | 0.16937 | 0.14649 | 0.13275 | 0.096131 | 0.082398 | 0.059509 | -0.050354 | 0.11902 | -0.004577 | 0.068665 | 0.10071 | 2.9205 | 0.15106 | -120.076 | -122.8775 | 2.8015 | 0.045777 | 2.9251 | 0.050354
5907.4531 | 122.8271 | -0.10071 | 122.7997 | -0.02739 | 0.015505 | 0.0096344 | -0.006586 | 0.0048577 | -0.010271 | -0.0021682 | -0.005371 | 0.022103 | 0.040285 | -0.017628 | 0.012334 | 0.021614 | -0.0027707 | 2.742 | 2.7374 | 2.6596 | 2.6184 | 2.7191 | 2.5909 | 2.623 | -0.041199 | 0.041199 | -0.068665 | -0.059509 | 0.009155 | -0.036621 | 0.036621 | 2.7603 | -120.0623 | -120.1813 | 2.8198 | 2.7237 | 2.6917 | -0.036621 | -0.068665 | 0.032043 | -122.7585 | -122.8592 | 0.10986 | 0.13733 | 0.064087 | 0.10529 | 0.032044 | 0.059509 | -0.041199 | 0.07782 | 0.009156 | 0.07782 | 0.10986 | 2.8381 | 0.14191 | -120.1401 | -122.8683 | 2.7191 | 0.041199 | 2.8427 | 0.059509
5909.1719 | 122.8226 | -0.1236 | 122.8134 | -0.01976 | 0.010591 | 0.0066436 | -0.010645 | -0.00069646 | -0.012194 | -0.0025956 | -0.005371 | 0.020181 | 0.039858 | -0.021046 | 0.010626 | 0.021828 | -0.0023435 | 2.8427 | 2.7832 | 2.7374 | 2.7145 | 2.8702 | 2.7603 | 2.7786 | -0.018311 | 0.036621 | -0.082397 | -0.068665 | 0.059509 | 0.018311 | 0.022888 | 2.861 | -120.0302 | -120.0989 | 2.9938 | 2.9022 | 2.8839 | 0.041198 | 0.022888 | 0.041199 | -122.7768 | -122.8821 | 0.1831 | 0.14648 | 0.14191 | 0.10528 | 0.10071 | 0.13275 | -0.022888 | 0.14191 | 0.013732 | 0.045776 | 0.11902 | 2.9068 | 0.16022 | -120.076 | -122.8958 | 2.8381 | 0.054931 | 2.9663 | 0.10528
5910.9531 | 122.9553 | -0.07782 | 122.7493 | -0.0045011 | 0.011019 | 0.007071 | -0.011072 | -0.0017645 | -0.014116 | -0.0045182 | -0.014526 | 0.018472 | 0.04178 | -0.017201 | 0.011053 | 0.02311 | -0.0055479 | 2.8244 | 2.7237 | 2.7191 | 2.7695 | 2.9388 | 2.8152 | 2.8427 | 0.13275 | -0.009155 | -0.032043 | 0.045776 | 0.19226 | 0.16022 | 0.13275 | 2.7969 | -120.0256 | -119.9799 | 3.0167 | 2.9205 | 2.8931 | 0.1236 | 0.096131 | 0.045777 | -122.7585 | -122.7036 | 0.27008 | 0.21057 | 0.23804 | 0.16479 | 0.19226 | 0.21973 | 0.050354 | 0.2243 | 0.077819 | 0.004578 | 0.022888 | 2.8015 | 0.068665 | -120.0302 | -122.7814 | 2.8473 | 0.1236 | 2.9022 | 0.21057
5912.7344 | 122.818 | -0.10071 | 122.8271 | -0.012131 | 0.015505 | 0.0089936 | -0.0074404 | 0.0014397 | -0.011125 | -0.0030228 | -0.005371 | 0.023385 | 0.039644 | -0.013783 | 0.012121 | 0.022255 | -0.0014891 | 2.7649 | 2.7466 | 2.6367 | 2.6184 | 2.7374 | 2.5864 | 2.623 | -0.032043 | 0.036621 | -0.054932 | -0.054932 | 0.022888 | -0.032043 | 0.022888 | 2.7374 | -120.0806 | -120.2087 | 2.8381 | 2.7237 | 2.6871 | -0.013733 | -0.050354 | 0.045776 | -122.7905 | -122.8821 | 0.1236 | 0.1236 | 0.068665 | 0.07782 | 0.022889 | 0.10071 | -0.018311 | 0.07782 | 0 | 0.10986 | 0.091553 | 2.8473 | 0.13733 | -120.1904 | -122.8821 | 2.7191 | 0.045776 | 2.8656 | 0.068665
5914.4531 | 122.8683 | -0.082397 | 122.7539 | -0.012131 | 0.013582 | 0.010275 | -0.0067996 | -0.0011237 | -0.010057 | -0.0043046 | -0.005371 | 0.019113 | 0.039858 | -0.017415 | 0.011053 | 0.02076 | -0.0044797 | 2.6825 | 2.6871 | 2.5909 | 2.5681 | 2.6733 | 2.5497 | 2.5726 | -0.027466 | 0.041199 | -0.073242 | -0.027466 | 0.064087 | 0.013733 | 0.07782 | 2.6733 | -120.0668 | -120.1859 | 2.7557 | 2.655 | 2.6321 | -0.01831 | -0.041198 | 0.009155 | -122.7127 | -122.7814 | 0.14648 | 0.16022 | 0.09613 | 0.15106 | 0.086975 | 0.082398 | -0.022888 | 0.13733 | 0.045776 | 0.096131 | 0.11444 | 2.7695 | 0.1236 | -120.163 | -122.8271 | 2.6505 | 0.054931 | 2.7649 | 0.054931
5916.2344 | 122.9507 | -0.07782 | 122.7448 | -0.012131 | 0.011232 | 0.007071 | -0.009363 | 0.00037174 | -0.00963 | -0.007936 | -0.005371 | 0.017831 | 0.039003 | -0.013783 | 0.0095575 | 0.023751 | -0.00042085 | 2.7466 | 2.6779 | 2.6642 | 2.6962 | 2.8473 | 2.7374 | 2.7786 | 0.059509 | -0.004578 | -0.036621 | 0.045776 | 0.16479 | 0.14191 | 0.14191 | 2.742 | -120.0668 | -120.0485 | 2.9251 | 2.8564 | 2.8152 | 0.11444 | 0.073242 | 0.041199 | -122.7493 | -122.699 | 0.24261 | 0.21973 | 0.21973 | 0.17853 | 0.17853 | 0.18311 | 0.032043 | 0.20142 | 0.082397 | 0.013732 | 0.032043 | 2.7557 | 0.073242 | -120.0806 | -122.7814 | 2.774 | 0.1236 | 2.8244 | 0.13733
5917.9531 | 122.8683 | -0.11902 | 122.7997 | 0.0031279 | 0.011019 | 0.00878 | -0.0078676 | -0.00026906 | -0.0098438 | -0.0021682 | -0.005371 | 0.018686 | 0.041353 | -0.016347 | 0.010626 | 0.023964 | -0.0064023 | 2.7924 | 2.8061 | 2.7283 | 2.6733 | 2.7786 | 2.7054 | 2.71 | -0.064087 | 0.041199 | -0.073242 | -0.059509 | 0.050354 | 0.013733 | 0.059509 | 2.8473 | -119.9936 | -120.1263 | 2.8976 | 2.829 | 2.8244 | -0.01831 | -0.022888 | 0.045777 | -122.7585 | -122.8592 | 0.16937 | 0.17853 | 0.13275 | 0.13275 | 0.086975 | 0.050354 | -0.054931 | 0.1236 | 0.013733 | 0.07782 | 0.11444 | 2.9251 | 0.16022 | -120.0714 | -122.8729 | 2.7924 | 0.05951 | 2.9114 | 0.054932
5919.75 | 122.9645 | -0.068665 | 122.7722 | -0.01976 | 0.0086688 | 0.0094208 | -0.010004 | -0.0019781 | -0.010057 | -0.0049454 | -0.005371 | 0.019113 | 0.042421 | -0.024464 | 0.01148 | 0.025673 | -0.00084805 | 2.7786 | 2.6871 | 2.6596 | 2.71 | 2.8656 | 2.742 | 2.7832 | 0.09613 | 0.013733 | -0.041199 | 0.050354 | 0.19226 | 0.14648 | 0.14648 | 2.7283 | -120.0851 | -120.0623 | 2.9343 | 2.8519 | 2.8107 | 0.1236 | 0.082397 | 0.027466 | -122.7585 | -122.7219 | 0.26093 | 0.21515 | 0.21515 | 0.18768 | 0.18768 | 0.20599 | 0.050354 | 0.23346 | 0.091553 | 0.027466 | 0.054932 | 2.7557 | 0.082398 | -120.1126 | -122.8134 | 2.7786 | 0.11902 | 2.8473 | 0.16479
5921.5312 | 122.9141 | -0.068665 | 122.8043 | -0.012131 | 0.013796 | 0.00878 | -0.010431 | 0.0010125 | -0.0094164 | -0.0015274 | -0.0084228 | 0.016977 | 0.039003 | -0.019551 | 0.0099847 | 0.02311 | -0.0025571 | 2.7237 | 2.6596 | 2.6184 | 2.623 | 2.7466 | 2.6321 | 2.6642 | 0.018311 | 0.022888 | -0.036621 | -0.013733 | 0.11444 | 0.068665 | 0.10529 | 2.6871 | -120.1447 | -120.1813 | 2.8152 | 2.7329 | 2.7008 | 0.045777 | 0.013733 | 0.032044 | -122.7814 | -122.818 | 0.18311 | 0.17395 | 0.13733 | 0.14191 | 0.10529 | 0.12817 | 0.004578 | 0.15106 | 0.022888 | 0.041199 | 0.059509 | 2.7283 | 0.091553 | -120.1859 | -122.8409 | 2.6917 | 0.054932 | 2.7924 | 0.086976
5923.25 | 122.818 | -0.1236 | 122.7997 | -0.01976 | 0.015291 | 0.008139 | -0.0080814 | -0.0019781 | -0.0098438 | -0.0032364 | -0.0084228 | 0.020608 | 0.04178 | -0.0084423 | 0.012121 | 0.021828 | 0.00064735 | 2.6642 | 2.6733 | 2.5864 | 2.5269 | 2.6047 | 2.504 | 2.5406 | -0.064087 | 0.036621 | -0.082397 | -0.068665 | 0 | -0.041199 | 0.018311 | 2.71 | -120.1263 | -120.2728 | 2.7283 | 2.6642 | 2.6276 | -0.045777 | -0.082398 | 0.041199 | -122.7631 | -122.8683 | 0.1236 | 0.14191 | 0.082397 | 0.10071 | 0.041198 | 0.01831 | -0.05951 | 0.082397 | 0.013732 | 0.086975 | 0.11902 | 2.7969 | 0.16022 | -120.2133 | -122.8821 | 2.6505 | 0.054931 | 2.7878 | 0.059509
5925.0312 | 122.9095 | -0.068665 | 122.7768 | -0.02739 | 0.010164 | 0.0085662 | -0.0085086 | 0.0010125 | -0.0087756 | -0.0028092 | -0.0084228 | 0.01954 | 0.04178 | -0.013142 | 0.011266 | 0.022469 | -0.0031979 | 2.6871 | 2.6093 | 2.5909 | 2.6001 | 2.7649 | 2.5955 | 2.6596 | 0.059509 | -0.004578 | -0.041199 | 0.004578 | 0.10986 | 0.07782 | 0.10529 | 2.6596 | -120.1675 | -120.1767 | 2.8336 | 2.7283 | 2.6642 | 0.068665 | 0.004578 | 0.027466 | -122.7814 | -122.7722 | 0.17853 | 0.17395 | 0.14649 | 0.14649 | 0.11902 | 0.17395 | 0.009156 | 0.15106 | 0.045777 | 0.018311 | 0.036621 | 2.6779 | 0.064087 | -120.1859 | -122.818 | 2.6688 | 0.073243 | 2.7557 | 0.12817
5926.8125 | 122.8638 | -0.10071 | 122.7768 | -0.01976 | 0.011019 | 0.0072846 | -0.0087222 | 0.0014397 | -0.010485 | -0.0038772 | -0.005371 | 0.021035 | 0.04178 | -0.014638 | 0.014684 | 0.021614 | -0.0042661 | 2.7832 | 2.7695 | 2.6779 | 2.6733 | 2.774 | 2.6779 | 2.7054 | -0.041199 | 0.045776 | -0.073242 | -0.036621 | 0.059509 | 0.041199 | 0.068665 | 2.7786 | -120.0073 | -120.1035 | 2.8748 | 2.8061 | 2.7786 | 0.027466 | 0 | 0.027466 | -122.731 | -122.8134 | 0.16022 | 0.16937 | 0.14191 | 0.14191 | 0.11444 | 0.096131 | -0.004577 | 0.13275 | 0.036621 | 0.091553 | 0.11902 | 2.8702 | 0.14648 | -120.0989 | -122.85 | 2.774 | 0.064087 | 2.8839 | 0.059509
5928.5312 | 122.8638 | -0.11444 | 122.7997 | -0.01976 | 0.01166 | 0.0068574 | -0.0072268 | -0.00048286 | -0.011339 | -0.0062272 | -0.011475 | 0.022317 | 0.040712 | -0.01122 | 0.0095575 | 0.022683 | -0.0078977 | 2.7695 | 2.7832 | 2.6779 | 2.6642 | 2.774 | 2.6825 | 2.6962 | -0.036621 | 0.045776 | -0.064087 | -0.054932 | 0.082397 | 0.036621 | 0.068665 | 2.7924 | -120.0165 | -120.1355 | 2.8885 | 2.8107 | 2.7969 | 0.018311 | 0.004578 | 0.050354 | -122.7539 | -122.8546 | 0.19684 | 0.18311 | 0.15106 | 0.13275 | 0.10071 | 0.096131 | -0.013732 | 0.14648 | 0.009155 | 0.10529 | 0.10986 | 2.8976 | 0.16022 | -120.1218 | -122.8638 | 2.7786 | 0.059509 | 2.8839 | 0.07782
5930.3125 | 122.9462 | -0.059509 | 122.7631 | -0.01976 | 0.012514 | 0.009848 | -0.0070132 | 0.0025079 | -0.008562 | -0.0021682 | -0.005371 | 0.01954 | 0.041567 | -0.017415 | 0.013189 | 0.023537 | -0.0036253 | 2.6871 | 2.5909 | 2.5726 | 2.5864 | 2.7374 | 2.5818 | 2.6321 | 0.086975 | 0.018311 | -0.032043 | 0.059509 | 0.15564 | 0.10529 | 0.15106 | 2.6321 | -120.1721 | -120.1767 | 2.7969 | 2.6916 | 2.6413 | 0.059509 | 0.009155 | 0.027466 | -122.7448 | -122.7036 | 0.21515 | 0.21057 | 0.16479 | 0.18311 | 0.13733 | 0.16479 | 0.013733 | 0.18768 | 0.091552 | 0.01831 | 0.050354 | 2.6505 | 0.07782 | -120.1904 | -122.7951 | 2.6459 | 0.11902 | 2.7466 | 0.14648
5932.0938 | 122.905 | -0.073242 | 122.7722 | -0.02739 | 0.013796 | 0.0085662 | -0.0091494 | 0.0042169 | -0.0077074 | -0.0011002 | -0.005371 | 0.020822 | 0.042421 | -0.021687 | 0.013189 | 0.023751 | -0.0057615 | 2.6367 | 2.6276 | 2.5497 | 2.5314 | 2.655 | 2.5131 | 2.5543 | 0.009155 | 0.018311 | -0.041199 | 0.022888 | 0.11902 | 0.082397 | 0.11444 | 2.623 | -120.1447 | -120.2408 | 2.7283 | 2.6276 | 2.5864 | 0.004577 | -0.036621 | 0.032043 | -122.7539 | -122.7493 | 0.19226 | 0.18768 | 0.15564 | 0.15564 | 0.1236 | 0.10528 | -0.018311 | 0.16022 | 0.064087 | 0.077819 | 0.05951 | 2.7008 | 0.091553 | -120.2225 | -122.8134 | 2.6047 | 0.09613 | 2.71 | 0.082397
5933.8906 | 122.8317 | -0.10071 | 122.8134 | -0.01976 | 0.014864 | 0.00878 | -0.0085086 | -0.00026906 | -0.0098438 | -0.0032364 | -0.005371 | 0.021249 | 0.042635 | -0.020619 | 0.012975 | 0.024605 | -0.0087521 | 2.7466 | 2.6962 | 2.6413 | 2.6047 | 2.7191 | 2.5772 | 2.6093 | 0 | 0.036621 | -0.050354 | -0.041199 | 0.041199 | 0 | 0.027466 | 2.742 | -120.1172 | -120.2087 | 2.8198 | 2.71 | 2.6779 | -0.032043 | -0.064087 | 0.050354 | -122.7768 | -122.8546 | 0.14191 | 0.12817 | 0.10071 | 0.07782 | 0.050354 | 0.07782 | -0.036621 | 0.091553 | 0.009155 | 0.054932 | 0.086975 | 2.7969 | 0.13733 | -120.1721 | -122.8638 | 2.7054 | 0.059509 | 2.8473 | 0.10071
5935.6094 | 122.9691 | -0.054932 | 122.7814 | -0.012131 | 0.0099506 | 0.0079254 | -0.010645 | 0.0012261 | -0.0089892 | -0.0045182 | -0.0084228 | 0.01719 | 0.040285 | -0.019978 | 0.0095575 | 0.024391 | -0.0021299 | 2.7878 | 2.6825 | 2.6733 | 2.7466 | 2.9022 | 2.7512 | 2.7832 | 0.12817 | 0.013733 | -0.022888 | 0.050354 | 0.1831 | 0.13733 | 0.14191 | 2.7283 | -120.0989 | -120.0348 | 2.9572 | 2.8381 | 2.8061 | 0.10986 | 0.07782 | 0.032044 | -122.7676 | -122.731 | 0.23804 | 0.19684 | 0.19226 | 0.16479 | 0.16022 | 0.22888 | 0.073242 | 0.20599 | 0.073242 | 0.009155 | 0.036621 | 2.7374 | 0.068665 | -120.108 | -122.8043 | 2.8015 | 0.10529 | 2.8427 | 0.18311
5937.375 | 122.8455 | -0.10986 | 122.7814 | -0.02739 | 0.013369 | 0.0085662 | -0.0074404 | -0.0017645 | -0.0077074 | 0.0001816 | -0.005371 | 0.021249 | 0.040499 | -0.020619 | 0.014043 | 0.023751 | -0.0019163 | 2.6276 | 2.6367 | 2.5497 | 2.4857 | 2.6001 | 2.4811 | 2.5269 | -0.054932 | 0.050354 | -0.068665 | -0.059509 | 0.027466 | -0.004578 | 0.045776 | 2.6596 | -120.1447 | -120.2957 | 2.71 | 2.6367 | 2.5909 | -0.022889 | -0.068665 | 0.041198 | -122.731 | -122.8409 | 0.13733 | 0.15564 | 0.10529 | 0.11444 | 0.064087 | 0.050354 | -0.064087 | 0.096131 | 0.009156 | 0.086975 | 0.11902 | 2.7466 | 0.16022 | -120.2316 | -122.85 | 2.5955 | 0.050354 | 2.7374 | 0.054931
5939.1094 | 122.8088 | -0.13275 | 122.8317 | -0.01976 | 0.015078 | 0.010062 | -0.0095766 | 0.0031487 | -0.0079212 | -0.0032364 | -0.0084228 | 0.024026 | 0.039431 | -0.0086559 | 0.012121 | 0.020119 | -0.0057615 | 2.6733 | 2.6596 | 2.5772 | 2.5406 | 2.655 | 2.5314 | 2.5452 | -0.064087 | 0.054932 | -0.073242 | -0.086975 | 0.022888 | -0.041199 | 0.027466 | 2.71 | -120.1721 | -120.2911 | 2.7878 | 2.6779 | 2.6642 | -0.032043 | -0.045776 | 0.059509 | -122.7768 | -122.9187 | 0.15564 | 0.16022 | 0.091552 | 0.10071 | 0.032043 | 0.07782 | -0.036621 | 0.09613 | -0.013733 | 0.082398 | 0.12817 | 2.7924 | 0.18768 | -120.2545 | -122.905 | 2.6733 | 0.045776 | 2.8061 | 0.068664
5940.8906 | 122.8638 | -0.10071 | 122.8271 | -0.01976 | 0.015505 | 0.010275 | -0.008295 | 0.0016535 | -0.0092028 | -0.0049454 | -0.005371 | 0.020822 | 0.039431 | -0.011433 | 0.012762 | 0.023537 | 6.346e-06 | 2.7512 | 2.7008 | 2.623 | 2.6321 | 2.774 | 2.623 | 2.6642 | 0.022888 | 0.032043 | -0.054932 | -0.018311 | 0.091553 | 0.045776 | 0.073242 | 2.7237 | -120.1263 | -120.195 | 2.8748 | 2.7649 | 2.7237 | 0.041199 | 0 | 0.045776 | -122.7951 | -122.8455 | 0.19226 | 0.17395 | 0.14648 | 0.12817 | 0.10071 | 0.15106 | 0.009155 | 0.14649 | 0.036621 | 0.07782 | 0.086975 | 2.8015 | 0.13275 | -120.2042 | -122.8821 | 2.7328 | 0.082397 | 2.8519 | 0.1236
5942.6719 | 122.9095 | -0.091553 | 122.7905 | -0.01976 | 0.012087 | 0.010062 | -0.0072268 | 0.0027215 | -0.00963 | -0.0028092 | -0.0023192 | 0.020822 | 0.042849 | -0.018696 | 0.01383 | 0.02311 | -0.0055479 | 2.623 | 2.623 | 2.536 | 2.5131 | 2.6276 | 2.4948 | 2.5223 | 0.004578 | 0.004578 | -0.059509 | 0.004578 | 0.09613 | 0.064087 | 0.09613 | 2.6276 | -120.1675 | -120.2774 | 2.7191 | 2.6138 | 2.5864 | -0.013733 | -0.041199 | 0.032044 | -122.7859 | -122.7859 | 0.18768 | 0.18768 | 0.15564 | 0.15564 | 0.1236 | 0.091552 | -0.022888 | 0.15564 | 0.064087 | 0.086975 | 0.064087 | 2.7145 | 0.096131 | -120.2545 | -122.85 | 2.6047 | 0.096131 | 2.7145 | 0.096131
5944.3906 | 122.8043 | -0.11444 | 122.7951 | -0.02739 | 0.013155 | 0.0079254 | -0.0078676 | 0.0016535 | -0.011339 | -0.0055862 | -0.0084228 | 0.022103 | 0.04413 | -0.017415 | 0.011266 | 0.024391 | -0.0021299 | 2.6733 | 2.6642 | 2.6047 | 2.5406 | 2.655 | 2.536 | 2.5543 | -0.068665 | 0.032043 | -0.07782 | -0.054932 | 0.004578 | -0.013733 | 0.018311 | 2.7191 | -120.1309 | -120.2545 | 2.7695 | 2.6688 | 2.6505 | -0.050354 | -0.068664 | 0.036621 | -122.7631 | -122.85 | 0.11902 | 0.13275 | 0.10071 | 0.096131 | 0.064087 | 0.050354 | -0.064087 | 0.082398 | 0.022888 | 0.05951 | 0.10986 | 2.7786 | 0.14648 | -120.1904 | -122.8729 | 2.655 | 0.059509 | 2.7878 | 0.045776
5946.1719 | 122.8912 | -0.10071 | 122.8043 | -0.012131 | 0.012514 | 0.0060028 | -0.0074404 | 0.00015814 | -0.01198 | -0.0019546 | -0.0084228 | 0.020395 | 0.043276 | -0.015706 | 0.012975 | 0.022469 | -0.00084805 | 2.7695 | 2.7466 | 2.6596 | 2.623 | 2.7649 | 2.655 | 2.6596 | -0.013733 | 0.045776 | -0.073242 | -0.027466 | 0.10071 | 0.045776 | 0.07782 | 2.7603 | -120.0577 | -120.1813 | 2.8656 | 2.7603 | 2.7557 | 0 | -0.004578 | 0.027466 | -122.7585 | -122.8317 | 0.20142 | 0.17853 | 0.14648 | 0.15106 | 0.11902 | 0.10529 | -0.036621 | 0.17395 | 0.045776 | 0.086975 | 0.11902 | 2.8473 | 0.14648 | -120.1447 | -122.8775 | 2.7237 | 0.073242 | 2.8702 | 0.086975
5947.9531 | 122.8455 | -0.11902 | 122.7859 | -0.01976 | 0.015291 | 0.0085662 | -0.0070132 | 0.0052851 | -0.0089892 | -0.0036636 | -0.0084228 | 0.019967 | 0.043489 | -0.018696 | 0.010412 | 0.025032 | -0.0010617 | 2.6138 | 2.6321 | 2.5589 | 2.4673 | 2.5726 | 2.4536 | 2.4994 | -0.064087 | 0.045776 | -0.073242 | -0.064087 | 0.004578 | -0.022888 | 0.036621 | 2.6779 | -120.1538 | -120.3186 | 2.6917 | 2.6184 | 2.5726 | -0.059509 | -0.10529 | 0.045777 | -122.7402 | -122.85 | 0.1236 | 0.15564 | 0.096131 | 0.10986 | 0.050354 | 0.013733 | -0.091553 | 0.07782 | 0.009155 | 0.073242 | 0.11902 | 2.7512 | 0.16479 | -120.2271 | -122.8592 | 2.5864 | 0.054932 | 2.7329 | 0.054932
5949.6875 | 122.9599 | -0.073242 | 122.7722 | -0.02739 | 0.0093098 | 0.0083526 | -0.01214 | -0.0026191 | -0.006853 | -0.0070816 | -0.0084228 | 0.017831 | 0.039858 | -0.015919 | 0.0097711 | 0.022255 | -0.0019163 | 2.6825 | 2.6047 | 2.5955 | 2.6001 | 2.7557 | 2.6505 | 2.6825 | 0.059509 | 0.009155 | -0.059509 | 0.018311 | 0.15106 | 0.13733 | 0.1236 | 2.6688 | -120.1675 | -120.1721 | 2.829 | 2.7557 | 2.7237 | 0.086975 | 0.054932 | 0.013733 | -122.7631 | -122.7539 | 0.2243 | 0.19684 | 0.21057 | 0.1831 | 0.19684 | 0.16022 | 0.004578 | 0.21057 | 0.07782 | 0.009155 | 0.068664 | 2.6779 | 0.082397 | -120.1767 | -122.8317 | 2.6733 | 0.091553 | 2.7557 | 0.13275
5951.4531 | 122.9553 | -0.073242 | 122.7905 | -0.02739 | 0.014009 | 0.0089936 | -0.010004 | 0.00079894 | -0.010057 | -0.0021682 | -0.0023192 | 0.019113 | 0.042421 | -0.015492 | 0.0097711 | 0.021401 | -0.0012753 | 2.6917 | 2.6047 | 2.5955 | 2.6184 | 2.7649 | 2.6642 | 2.6917 | 0.059509 | 0.018311 | -0.050354 | 0.018311 | 0.16022 | 0.15106 | 0.13733 | 2.6688 | -120.1859 | -120.1721 | 2.8381 | 2.7649 | 2.7374 | 0.09613 | 0.068665 | 0.022888 | -122.7722 | -122.7722 | 0.23346 | 0.21057 | 0.2243 | 0.18768 | 0.20142 | 0.16937 | 0.022888 | 0.21057 | 0.068665 | 0.009155 | 0.068665 | 2.6779 | 0.091553 | -120.195 | -122.8409 | 2.6917 | 0.091553 | 2.7649 | 0.13275
5953.2344 | 122.9004 | -0.10071 | 122.8134 | -0.012131 | 0.011019 | 0.0083526 | -0.007654 | -0.00091006 | -0.010057 | -0.0032364 | -0.011475 | 0.020395 | 0.040499 | -0.013569 | 0.011053 | 0.020974 | -0.0068295 | 2.7283 | 2.6596 | 2.6001 | 2.6138 | 2.7466 | 2.6093 | 2.6321 | 0.013733 | 0.032043 | -0.059509 | -0.018311 | 0.082397 | 0.041199 | 0.086975 | 2.7008 | -120.1538 | -120.1996 | 2.8473 | 2.7328 | 2.71 | 0.032043 | 0.009155 | 0.041199 | -122.7814 | -122.8317 | 0.18311 | 0.18768 | 0.14191 | 0.14648 | 0.10071 | 0.14648 | 0.013733 | 0.14191 | 0.041198 | 0.059509 | 0.091552 | 2.7603 | 0.13275 | -120.2133 | -122.8729 | 2.7145 | 0.082397 | 2.829 | 0.11444
5954.9531 | 122.8317 | -0.1236 | 122.7814 | -0.012131 | 0.012514 | 0.00643 | -0.010858 | -0.0036871 | -0.010912 | -0.0057998 | -0.005371 | 0.017404 | 0.041353 | -0.013997 | 0.0080621 | 0.023537 | -0.0066159 | 2.7786 | 2.7145 | 2.6642 | 2.6505 | 2.7924 | 2.6825 | 2.6779 | -0.009155 | 0.032043 | -0.054932 | -0.068665 | 0.054932 | 0.018311 | 0.036621 | 2.7878 | -120.0668 | -120.1309 | 2.916 | 2.8015 | 2.8061 | 0.013732 | 0.01831 | 0.068664 | -122.7493 | -122.85 | 0.17853 | 0.16022 | 0.14191 | 0.091553 | 0.073243 | 0.12817 | -0.013733 | 0.10986 | -0.013733 | 0.050354 | 0.086975 | 2.8381 | 0.15564 | -120.1172 | -122.8363 | 2.774 | 0.054931 | 2.9022 | 0.11444
5956.6719 | 122.8775 | -0.09613 | 122.7814 | -0.01976 | 0.012728 | 0.0089936 | -0.007654 | 0.0072077 | -0.00963 | -0.0047318 | -0.0084228 | 0.022317 | 0.043062 | -0.012715 | 0.011266 | 0.021401 | -0.0017027 | 2.6047 | 2.6047 | 2.5314 | 2.4765 | 2.6001 | 2.4673 | 2.504 | -0.022888 | 0.036621 | -0.07782 | -0.032043 | 0.054932 | 0.009155 | 0.068665 | 2.6276 | -120.1767 | -120.3049 | 2.6962 | 2.6001 | 2.5635 | -0.027466 | -0.064087 | 0.01831 | -122.7448 | -122.8134 | 0.15106 | 0.16479 | 0.10528 | 0.14649 | 0.086975 | 0.068665 | -0.054932 | 0.13275 | 0.045777 | 0.073242 | 0.11444 | 2.7008 | 0.13275 | -120.2499 | -122.8592 | 2.5726 | 0.064087 | 2.7008 | 0.073242
5958.4375 | 122.9645 | -0.059509 | 122.7951 | -0.01976 | 0.013155 | 0.0077118 | -0.0080814 | 0.0027215 | -0.011553 | -0.0036636 | -0.005371 | 0.01954 | 0.040285 | -0.013569 | 0.01148 | 0.023751 | -0.0044797 | 2.6642 | 2.5314 | 2.5269 | 2.5452 | 2.6871 | 2.5406 | 2.6001 | 0.11444 | 0.009155 | -0.022888 | 0.050354 | 0.15564 | 0.12817 | 0.13733 | 2.5864 | -120.2637 | -120.2499 | 2.7466 | 2.6596 | 2.6001 | 0.073243 | 0.013733 | 0.036621 | -122.7859 | -122.7448 | 0.21515 | 0.19684 | 0.18768 | 0.16022 | 0.15106 | 0.16022 | 0.018311 | 0.17853 | 0.073242 | 0.004578 | 0.032043 | 2.5909 | 0.068664 | -120.2683 | -122.818 | 2.6047 | 0.10986 | 2.7237 | 0.17395
5960.2188 | 122.8775 | -0.086975 | 122.8043 | -0.01976 | 0.013582 | 0.0077118 | -0.0061588 | 0.0020807 | -0.011339 | -0.0038772 | -0.0084228 | 0.021035 | 0.04178 | -0.012074 | 0.013189 | 0.021187 | -0.0027707 | 2.7145 | 2.6688 | 2.5909 | 2.6138 | 2.7191 | 2.5955 | 2.6321 | 0.032043 | 0.045776 | -0.059509 | -0.009155 | 0.09613 | 0.045776 | 0.07782 | 2.6779 | -120.1355 | -120.1904 | 2.8061 | 2.7191 | 2.6825 | 0.041199 | 0.004578 | 0.027466 | -122.7585 | -122.8134 | 0.1831 | 0.16479 | 0.13275 | 0.13733 | 0.10528 | 0.12817 | 0.022889 | 0.15564 | 0.050354 | 0.07782 | 0.10528 | 2.7557 | 0.13275 | -120.2133 | -122.8638 | 2.7008 | 0.07782 | 2.8015 | 0.11902
5961.9844 | 122.9004 | -0.091553 | 122.7905 | -0.01976 | 0.013155 | 0.0083526 | -0.0067996 | 0.0018671 | -0.010057 | -0.0030228 | -0.0084228 | 0.020822 | 0.04178 | -0.011647 | 0.013616 | 0.023964 | -0.0059751 | 2.5726 | 2.5726 | 2.5085 | 2.4765 | 2.5864 | 2.4445 | 2.4902 | -0.009155 | 0.022888 | -0.064087 | -0.009155 | 0.082397 | 0.041199 | 0.10071 | 2.6001 | -120.2179 | -120.314 | 2.6779 | 2.5818 | 2.536 | -0.018311 | -0.064087 | 0.027466 | -122.7676 | -122.7997 | 0.17395 | 0.19226 | 0.13275 | 0.1648 | 0.10529 | 0.07782 | -0.032044 | 0.14648 | 0.054932 | 0.064087 | 0.086975 | 2.6642 | 0.11444 | -120.282 | -122.8546 | 2.5681 | 0.082398 | 2.6642 | 0.082398
5963.7031 | 122.9736 | -0.054932 | 122.7814 | -0.02739 | 0.011232 | 0.008139 | -0.011927 | 0.0022943 | -0.0098438 | -0.005159 | -0.0084228 | 0.018045 | 0.042849 | -0.026387 | 0.010412 | 0.021401 | -0.00042085 | 2.7512 | 2.6276 | 2.623 | 2.6733 | 2.8381 | 2.7145 | 2.7466 | 0.11444 | 0.018311 | -0.018311 | 0.036621 | 0.18768 | 0.13733 | 0.14648 | 2.6779 | -120.1538 | -120.108 | 2.8931 | 2.8015 | 2.7695 | 0.1236 | 0.091553 | 0.036621 | -122.7631 | -122.7448 | 0.24261 | 0.20142 | 0.19226 | 0.16479 | 0.15564 | 0.21515 | 0.050354 | 0.20599 | 0.054932 | 0.004577 | 0.036622 | 2.6825 | 0.073243 | -120.1584 | -122.7997 | 2.7283 | 0.091553 | 2.8061 | 0.16937
5965.5 | 122.9324 | -0.073242 | 122.7814 | -0.01976 | 0.011232 | 0.0074982 | -0.009363 | -0.0051825 | -0.010698 | -0.0025956 | -0.005371 | 0.018686 | 0.041567 | -0.017628 | 0.010198 | 0.021401 | -0.0012753 | 2.6184 | 2.5681 | 2.5406 | 2.536 | 2.6733 | 2.536 | 2.6047 | 0.036621 | 0.009155 | -0.059509 | -0.009155 | 0.10071 | 0.073242 | 0.086975 | 2.6138 | -120.2133 | -120.2454 | 2.7466 | 2.6779 | 2.6093 | 0.064087 | -0.004577 | 0.013733 | -122.7722 | -122.7905 | 0.17395 | 0.16022 | 0.14648 | 0.14648 | 0.13275 | 0.13275 | -0.004577 | 0.16022 | 0.050354 | 0.027466 | 0.068664 | 2.6413 | 0.082397 | -120.2408 | -122.8409 | 2.6093 | 0.064087 | 2.6917 | 0.10986
5967.2188 | 122.8455 | -0.11902 | 122.8134 | -0.01976 | 0.015078 | 0.0092072 | -0.005945 | 0.0027215 | -0.011339 | -0.00345 | -0.011475 | 0.021676 | 0.040926 | -0.013569 | 0.012121 | 0.021401 | -0.0046933 | 2.5864 | 2.5772 | 2.504 | 2.4307 | 2.5406 | 2.417 | 2.4628 | -0.068665 | 0.059509 | -0.07782 | -0.073242 | 0.004578 | -0.041199 | 0.027466 | 2.623 | -120.2362 | -120.3827 | 2.6596 | 2.5818 | 2.536 | -0.041198 | -0.086975 | 0.041199 | -122.7539 | -122.8867 | 0.1236 | 0.14649 | 0.07782 | 0.10529 | 0.036621 | 0.036621 | -0.073242 | 0.082398 | 0.004578 | 0.073242 | 0.13733 | 2.6962 | 0.17853 | -120.3094 | -122.8912 | 2.5497 | 0.045777 | 2.7054 | 0.050354
5968.9844 | 122.8271 | -0.10529 | 122.8088 | -0.012131 | 0.014437 | 0.0074982 | -0.0067996 | 0.0025079 | -0.010912 | -0.0030228 | -0.005371 | 0.020395 | 0.043062 | -0.0080151 | 0.01148 | 0.02076 | -0.0055479 | 2.6138 | 2.6047 | 2.5452 | 2.4857 | 2.5864 | 2.4445 | 2.4948 | -0.073242 | 0.050354 | -0.082397 | -0.07782 | 0.009155 | -0.032043 | 0.018311 | 2.6505 | -120.2042 | -120.3232 | 2.6917 | 2.6001 | 2.5497 | -0.050354 | -0.10071 | 0.022889 | -122.7585 | -122.8867 | 0.11444 | 0.1236 | 0.073243 | 0.10071 | 0.050354 | 0.041199 | -0.059509 | 0.091552 | 0.004577 | 0.059509 | 0.13275 | 2.71 | 0.15564 | -120.2637 | -122.8912 | 2.5909 | 0.027466 | 2.7191 | 0.032044
5970.7031 | 122.9324 | -0.082397 | 122.7859 | -0.012131 | 0.010805 | 0.0083526 | -0.009363 | 0.00037174 | -0.0077074 | -0.0032364 | -0.0084228 | 0.020181 | 0.039644 | -0.01186 | 0.0091303 | 0.022469 | -0.0014891 | 2.7328 | 2.6321 | 2.623 | 2.6505 | 2.8198 | 2.6825 | 2.6962 | 0.082397 | 0.018311 | -0.045776 | 0.009155 | 0.14648 | 0.11444 | 0.11444 | 2.7054 | -120.1538 | -120.1355 | 2.9022 | 2.7786 | 2.7649 | 0.073242 | 0.059509 | 0.036621 | -122.7676 | -122.7768 | 0.22888 | 0.19684 | 0.19684 | 0.16022 | 0.16022 | 0.19684 | 0.027466 | 0.19226 | 0.054931 | 0.009155 | 0.064087 | 2.7145 | 0.10071 | -120.163 | -122.8317 | 2.7328 | 0.091552 | 2.8152 | 0.16479
5972.4844 | 122.85 | -0.10529 | 122.8134 | -0.012131 | 0.014223 | 0.0096344 | -0.0087222 | 0.0016535 | -0.010912 | -0.005159 | -0.0084228 | 0.021463 | 0.03879 | -0.010365 | 0.012548 | 0.022255 | -0.0076841 | 2.5818 | 2.5635 | 2.4628 | 2.4261 | 2.5452 | 2.4124 | 2.4673 | -0.045776 | 0.027466 | -0.064087 | -0.054932 | 0.036621 | -0.013733 | 0.045776 | 2.5681 | -120.2499 | -120.3873 | 2.6505 | 2.5726 | 2.5177 | 0.004577 | -0.050354 | 0.041199 | -122.7859 | -122.8683 | 0.14191 | 0.15106 | 0.091553 | 0.10986 | 0.050354 | 0.082397 | -0.036622 | 0.10071 | 0.009155 | 0.10071 | 0.091553 | 2.6688 | 0.13275 | -120.3506 | -122.8775 | 2.5314 | 0.050354 | 2.6871 | 0.05951
5974.2031 | 122.8592 | -0.086975 | 122.8043 | -0.012131 | 0.012941 | 0.0074982 | -0.011927 | -0.00069646 | -0.011766 | -0.00345 | -0.0084228 | 0.018045 | 0.040499 | -0.017628 | 0.010198 | 0.023964 | -0.0010617 | 2.7374 | 2.6138 | 2.6138 | 2.6505 | 2.7924 | 2.6825 | 2.6962 | 0.027466 | 0.041199 | -0.050354 | -0.054932 | 0.091553 | 0.050354 | 0.054932 | 2.7008 | -120.1904 | -120.1538 | 2.8793 | 2.7832 | 2.7695 | 0.082397 | 0.068664 | 0.036621 | -122.7631 | -122.8592 | 0.17853 | 0.14191 | 0.13733 | 0.10529 | 0.10071 | 0.17853 | 0.036621 | 0.14191 | -0.004578 | 0 | 0.091553 | 2.7008 | 0.12817 | -120.1904 | -122.8546 | 2.7374 | 0.032043 | 2.8244 | 0.11444
5976 | 122.9874 | -0.07782 | 122.8043 | -0.012131 | 0.0099506 | 0.0083526 | -0.010858 | -0.0028327 | -0.012194 | -0.00345 | -0.0023192 | 0.019967 | 0.039003 | -0.015065 | 0.0093439 | 0.021401 | -0.0023435 | 2.6962 | 2.6001 | 2.5726 | 2.6413 | 2.7878 | 2.6642 | 2.6917 | 0.14191 | 0.009155 | -0.036621 | 0.068665 | 0.19684 | 0.15564 | 0.16022 | 2.6505 | -120.2042 | -120.163 | 2.8656 | 2.7695 | 2.742 | 0.11902 | 0.091553 | 0.041199 | -122.7951 | -122.7356 | 0.27466 | 0.23804 | 0.23346 | 0.19684 | 0.19226 | 0.21515 | 0.068664 | 0.23346 | 0.10529 | 0.027466 | 0.045776 | 2.6779 | 0.086975 | -120.2316 | -122.8409 | 2.7191 | 0.14649 | 2.774 | 0.21973
5977.7344 | 122.9279 | -0.068665 | 122.7951 | -0.012131 | 0.0123 | 0.00878 | -0.010645 | -0.00026906 | -0.010698 | -0.0045182 | -0.005371 | 0.021249 | 0.040712 | -0.01891 | 0.010412 | 0.021187 | -0.0029843 | 2.6138 | 2.4857 | 2.5131 | 2.5314 | 2.6917 | 2.5223 | 2.5681 | 0.11444 | -0.009155 | -0.041199 | 0.045776 | 0.14191 | 0.07782 | 0.10986 | 2.5818 | -120.3094 | -120.2637 | 2.7603 | 2.6367 | 2.5909 | 0.054931 | 0.009155 | 0.027466 | -122.8043 | -122.7493 | 0.21057 | 0.17853 | 0.14649 | 0.15106 | 0.11902 | 0.17853 | 0.01831 | 0.18311 | 0.086975 | -0.027466 | 0.032044 | 2.5543 | 0.05951 | -120.282 | -122.8363 | 2.6001 | 0.11444 | 2.6825 | 0.18311
5979.5156 | 122.905 | -0.073242 | 122.7997 | -0.035019 | 0.013796 | 0.0060028 | -0.0089358 | 0.0054987 | -0.011339 | -0.0060134 | -0.005371 | 0.021035 | 0.040071 | -0.014638 | 0.011266 | 0.023323 | -0.0059751 | 2.6688 | 2.6047 | 2.536 | 2.5589 | 2.6962 | 2.5635 | 2.5772 | 0.032043 | 0.032043 | -0.068665 | -0.018311 | 0.091553 | 0.036621 | 0.068665 | 2.6093 | -120.195 | -120.2408 | 2.7695 | 2.6505 | 2.6367 | 0.041198 | 0.027466 | 0.004577 | -122.7676 | -122.818 | 0.16479 | 0.14191 | 0.10986 | 0.13733 | 0.10529 | 0.16022 | 0.022888 | 0.16022 | 0.050354 | 0.068664 | 0.10071 | 2.6779 | 0.10529 | -120.2637 | -122.8683 | 2.6321 | 0.054931 | 2.742 | 0.10529
5981.2969 | 122.937 | -0.064087 | 122.7814 | -0.01976 | 0.013369 | 0.0085662 | -0.0097904 | 0.0020807 | -0.0089892 | -0.0062272 | -0.011475 | 0.017617 | 0.041353 | -0.018269 | 0.0099847 | 0.024178 | -0.0046933 | 2.6093 | 2.4811 | 2.4811 | 2.5452 | 2.6642 | 2.5223 | 2.5589 | 0.09613 | -0.013733 | -0.032043 | 0.045776 | 0.15106 | 0.11444 | 0.1236 | 2.5452 | -120.3003 | -120.2362 | 2.7283 | 2.623 | 2.5864 | 0.07782 | 0.041199 | 0.032044 | -122.7951 | -122.7356 | 0.21515 | 0.18768 | 0.17853 | 0.15564 | 0.14648 | 0.18311 | 0.064087 | 0.18311 | 0.077819 | 0 | 0.01831 | 2.5452 | 0.050354 | -120.3003 | -122.8134 | 2.6093 | 0.10986 | 2.6733 | 0.16022
5983.0781 | 122.8958 | -0.10071 | 122.8409 | -0.01976 | 0.013796 | 0.0083526 | -0.006586 | 0.00015814 | -0.011553 | -0.0015274 | -0.0084228 | 0.020822 | 0.04178 | -0.0069469 | 0.012548 | 0.022255 | -0.00020725 | 2.6917 | 2.6825 | 2.5818 | 2.5681 | 2.6962 | 2.5864 | 2.6047 | -0.013733 | 0.036621 | -0.059509 | -0.027466 | 0.07782 | 0.032043 | 0.073242 | 2.6825 | -120.1584 | -120.2728 | 2.7969 | 2.7054 | 2.6871 | 0.022888 | 0.004578 | 0.041199 | -122.8043 | -122.8683 | 0.17853 | 0.17395 | 0.13275 | 0.13275 | 0.091552 | 0.11444 | -0.013733 | 0.13733 | 0.032043 | 0.10071 | 0.09613 | 2.7832 | 0.13733 | -120.2591 | -122.9004 | 2.6688 | 0.073242 | 2.7924 | 0.086975
5984.7969 | 122.8363 | -0.1236 | 122.85 | -0.035019 | 0.0093098 | 0.0051484 | -0.011072 | -5.5462e-05 | -0.010485 | -0.0040908 | -0.011475 | 0.01954 | 0.041994 | -0.011433 | 0.010839 | 0.021828 | -0.0051205 | 2.6459 | 2.6596 | 2.5681 | 2.536 | 2.6642 | 2.5681 | 2.5818 | -0.064087 | 0.050354 | -0.086975 | -0.091553 | 0.036621 | 0.013733 | 0.009155 | 2.6917 | -120.1904 | -120.314 | 2.7878 | 2.7054 | 2.6917 | 0.013733 | 0 | 0.036621 | -122.7997 | -122.9416 | 0.16022 | 0.13275 | 0.13733 | 0.09613 | 0.10071 | 0.096131 | -0.032043 | 0.1236 | -0.004578 | 0.091553 | 0.13733 | 2.7832 | 0.17395 | -120.282 | -122.937 | 2.6596 | 0.032043 | 2.7695 | 0.059509
5986.5781 | 122.8867 | -0.10529 | 122.8271 | -0.02739 | 0.015718 | 0.0079254 | -0.0050906 | 0.0046441 | -0.011766 | -0.0040908 | -0.0084228 | 0.020181 | 0.042635 | -0.015706 | 0.013616 | 0.021401 | -0.0023435 | 2.6825 | 2.5955 | 2.5406 | 2.5543 | 2.6825 | 2.5314 | 2.5681 | 0.036621 | 0.036621 | -0.045776 | -0.009155 | 0.086975 | 0.041199 | 0.068665 | 2.6459 | -120.2316 | -120.2728 | 2.7878 | 2.6733 | 2.6367 | 0.027466 | -0.009155 | 0.05951 | -122.7905 | -122.8363 | 0.19226 | 0.17395 | 0.14649 | 0.11444 | 0.086975 | 0.14191 | 0.013733 | 0.13275 | 0.036621 | 0.054932 | 0.082397 | 2.7008 | 0.14191 | -120.2866 | -122.8729 | 2.6596 | 0.096131 | 2.7878 | 0.14191
5988.2969 | 122.9416 | -0.073242 | 122.8134 | -0.012131 | 0.015078 | 0.0092072 | -0.0074404 | 0.0035761 | -0.0087756 | -0.00345 | -0.0023192 | 0.022531 | 0.042849 | -0.016987 | 0.01148 | 0.022042 | -0.0019163 | 2.536 | 2.5085 | 2.4445 | 2.4307 | 2.5497 | 2.4261 | 2.4582 | 0.036621 | 0.013733 | -0.050354 | 0.041199 | 0.13275 | 0.086975 | 0.12817 | 2.5177 | -120.3049 | -120.3827 | 2.623 | 2.5314 | 2.4994 | 0.013733 | -0.018311 | 0.022888 | -122.7997 | -122.7722 | 0.20599 | 0.20142 | 0.16022 | 0.17853 | 0.13733 | 0.10529 | -0.013733 | 0.18311 | 0.091553 | 0.064087 | 0.064087 | 2.5818 | 0.086975 | -120.369 | -122.8638 | 2.504 | 0.11444 | 2.6093 | 0.10986
5990.0938 | 122.8729 | -0.11444 | 122.8088 | -0.012131 | 0.012728 | 0.0072846 | -0.009363 | 0.0031487 | -0.0092028 | -0.0070816 | -0.005371 | 0.021249 | 0.041567 | -0.012288 | 0.012121 | 0.022042 | -0.00063445 | 2.6688 | 2.6642 | 2.5864 | 2.5314 | 2.6413 | 2.5543 | 2.5726 | -0.050354 | 0.045776 | -0.068665 | -0.064087 | 0.050354 | 0.013733 | 0.045776 | 2.7008 | -120.1447 | -120.2774 | 2.7557 | 2.6871 | 2.6688 | -0.013733 | -0.032044 | 0.045776 | -122.7631 | -122.8729 | 0.16479 | 0.16022 | 0.12817 | 0.11444 | 0.082398 | 0.054931 | -0.054932 | 0.11902 | 0.004578 | 0.07782 | 0.11444 | 2.7786 | 0.16022 | -120.2225 | -122.8775 | 2.6459 | 0.050354 | 2.7832 | 0.064087
5991.875 | 122.9141 | -0.086975 | 122.8088 | -0.01976 | 0.011446 | 0.0085662 | -0.010858 | -0.0024055 | -0.0087756 | -0.0030228 | -0.005371 | 0.018686 | 0.039644 | -0.019978 | 0.0087029 | 0.024605 | -0.0034117 | 2.6825 | 2.5726 | 2.5726 | 2.6093 | 2.7603 | 2.6367 | 2.6688 | 0.068665 | 0.027466 | -0.054932 | 0 | 0.1236 | 0.091553 | 0.09613 | 2.6596 | -120.2362 | -120.1996 | 2.8473 | 2.7557 | 2.7237 | 0.09613 | 0.064087 | 0.032043 | -122.7814 | -122.8088 | 0.21057 | 0.1831 | 0.17853 | 0.15106 | 0.14649 | 0.18768 | 0.036621 | 0.17853 | 0.054932 | 0 | 0.082398 | 2.6596 | 0.11444 | -120.2362 | -122.8638 | 2.6962 | 0.086975 | 2.7695 | 0.15564
5993.5938 | 122.8683 | -0.09613 | 122.8088 | -0.012131 | 0.012514 | 0.0077118 | -0.0074404 | 0.0031487 | -0.010698 | -0.005159 | 0.00073235 | 0.021249 | 0.042421 | -0.015065 | 0.011266 | 0.023964 | -0.0019163 | 2.5223 | 2.5177 | 2.4307 | 2.3987 | 2.504 | 2.3804 | 2.4261 | -0.050354 | 0.036621 | -0.073242 | -0.045776 | 0.032043 | 0.009155 | 0.050354 | 2.5269 | -120.2911 | -120.4102 | 2.6001 | 2.5223 | 2.4765 | -0.004578 | -0.050354 | 0.022888 | -122.7722 | -122.8546 | 0.12817 | 0.14648 | 0.10528 | 0.1236 | 0.082397 | 0.073242 | -0.032043 | 0.10529 | 0.027466 | 0.086975 | 0.10986 | 2.6138 | 0.13275 | -120.3781 | -122.8821 | 2.4948 | 0.050354 | 2.6184 | 0.045776
5995.375 | 122.9782 | -0.068665 | 122.7539 | -0.0045011 | 0.0099506 | 0.0066436 | -0.011499 | -0.0013373 | -0.01198 | -0.0066544 | -0.005371 | 0.019967 | 0.040926 | -0.019764 | 0.0076349 | 0.022469 | -0.0027707 | 2.6642 | 2.5452 | 2.5635 | 2.5955 | 2.7695 | 2.6367 | 2.6642 | 0.13733 | 0.018311 | -0.027466 | 0.045776 | 0.19226 | 0.16022 | 0.13275 | 2.6321 | -120.2087 | -120.1584 | 2.8381 | 2.7329 | 2.7054 | 0.10071 | 0.073242 | 0.041199 | -122.7356 | -122.7081 | 0.26093 | 0.20142 | 0.22888 | 0.16022 | 0.18768 | 0.20599 | 0.032043 | 0.21973 | 0.073242 | -0.018311 | 0.045777 | 2.6138 | 0.086976 | -120.1904 | -122.7814 | 2.6642 | 0.11444 | 2.7329 | 0.20599
5997.1562 | 122.9004 | -0.10529 | 122.8271 | -0.012131 | 0.015291 | 0.0085662 | -0.006586 | 0.0037897 | -0.010271 | -0.0062272 | -0.0084228 | 0.023599 | 0.042208 | -0.015706 | 0.013189 | 0.02311 | -0.0040525 | 2.6459 | 2.5772 | 2.5131 | 2.5177 | 2.655 | 2.5314 | 2.536 | 0.032043 | 0.036621 | -0.064087 | -0.022888 | 0.086975 | 0.032043 | 0.086975 | 2.6184 | -120.2499 | -120.3094 | 2.7603 | 2.6413 | 2.6367 | 0.022888 | 0.01831 | 0.041199 | -122.7905 | -122.85 | 0.19226 | 0.19226 | 0.13733 | 0.15106 | 0.09613 | 0.14191 | 0.004577 | 0.15106 | 0.041199 | 0.064086 | 0.10071 | 2.6825 | 0.14191 | -120.314 | -122.8912 | 2.623 | 0.082398 | 2.7512 | 0.13733
5998.9375 | 122.85 | -0.11444 | 122.8226 | -0.01976 | 0.013369 | 0.0083526 | -0.0080814 | 0.0027215 | -0.0087756 | -0.0049454 | -0.0084228 | 0.020395 | 0.042635 | -0.01421 | 0.01148 | 0.021187 | -0.0019163 | 2.5269 | 2.5314 | 2.4124 | 2.3666 | 2.4765 | 2.3529 | 2.3987 | -0.054932 | 0.059509 | -0.068665 | -0.068665 | 0.041199 | -0.018311 | 0.032043 | 2.5269 | -120.2911 | -120.4559 | 2.5909 | 2.5131 | 2.4673 | -0.013733 | -0.05951 | 0.045776 | -122.7631 | -122.8912 | 0.15564 | 0.14648 | 0.09613 | 0.10071 | 0.050354 | 0.064086 | -0.045777 | 0.10986 | 0 | 0.11902 | 0.12817 | 2.6459 | 0.17395 | -120.4102 | -122.8912 | 2.4811 | 0.045776 | 2.6413 | 0.059509
6000.6562 | 122.9691 | -0.068665 | 122.7768 | -0.01976 | 0.012087 | 0.0083526 | -0.0091494 | 0.0037897 | -0.010912 | -0.0038772 | -0.0023192 | 0.018686 | 0.040285 | -0.013569 | 0.010626 | 0.023964 | -0.0025571 | 2.5589 | 2.4536 | 2.417 | 2.4582 | 2.6047 | 2.4582 | 2.504 | 0.10071 | 0.013733 | -0.022888 | 0.064087 | 0.16937 | 0.10071 | 0.16022 | 2.4857 | -120.3232 | -120.3186 | 2.6733 | 2.5726 | 2.5269 | 0.086975 | 0.041199 | 0.045777 | -122.7631 | -122.7127 | 0.23804 | 0.22888 | 0.16937 | 0.1831 | 0.1236 | 0.18768 | 0.041199 | 0.19226 | 0.086975 | 0.036621 | 0.036621 | 2.5223 | 0.082398 | -120.3598 | -122.7997 | 2.5269 | 0.13275 | 2.6276 | 0.16937
6002.4219 | 122.8912 | -0.10071 | 122.8088 | -0.01976 | 0.015291 | 0.0079254 | -0.0067996 | 0.0059259 | -0.0081348 | -0.0021682 | -0.0084228 | 0.021463 | 0.040071 | -0.016347 | 0.011694 | 0.024605 | -0.0036253 | 2.5131 | 2.4994 | 2.4078 | 2.3712 | 2.4948 | 2.3621 | 2.417 | -0.004578 | 0.041199 | -0.054932 | -0.022888 | 0.073242 | 0.027466 | 0.068665 | 2.5085 | -120.3094 | -120.4376 | 2.5955 | 2.5177 | 2.4628 | 0.009155 | -0.045776 | 0.045776 | -122.7676 | -122.8317 | 0.17395 | 0.16937 | 0.12817 | 0.1236 | 0.082398 | 0.086975 | -0.036621 | 0.12817 | 0.032044 | 0.091553 | 0.096131 | 2.6001 | 0.14191 | -120.401 | -122.8638 | 2.4719 | 0.07782 | 2.6138 | 0.09613
6004.125 | 122.8775 | -0.09613 | 122.8455 | -0.01976 | 0.009737 | 0.0089936 | -0.010858 | -0.0013373 | -0.011125 | -0.0045182 | -0.0084228 | 0.020608 | 0.043062 | -0.02126 | 0.0097711 | 0.022896 | -0.0040525 | 2.6688 | 2.5497 | 2.5452 | 2.5864 | 2.71 | 2.6093 | 2.6276 | 0.032043 | 0.027466 | -0.054932 | -0.036621 | 0.091553 | 0.059509 | 0.059509 | 2.6413 | -120.2957 | -120.2591 | 2.8061 | 2.7237 | 2.7054 | 0.082397 | 0.064087 | 0.041198 | -122.818 | -122.8821 | 0.18768 | 0.15564 | 0.15564 | 0.11444 | 0.11444 | 0.16479 | 0.041199 | 0.14649 | 0.018311 | 0.004578 | 0.082398 | 2.6459 | 0.1236 | -120.3003 | -122.9004 | 2.6825 | 0.059509 | 2.7649 | 0.12817
6005.9062 | 122.9233 | -0.091553 | 122.8043 | -0.01976 | 0.01166 | 0.0079254 | -0.011499 | 0.0027215 | -0.0070666 | -0.0028092 | -0.0023192 | 0.01954 | 0.039858 | -0.01421 | 0.0097711 | 0.022683 | 0.00021995 | 2.5497 | 2.504 | 2.4353 | 2.4582 | 2.5955 | 2.4628 | 2.4994 | 0.027466 | 0 | -0.045776 | -0.013733 | 0.10071 | 0.073242 | 0.09613 | 2.5269 | -120.3003 | -120.3461 | 2.6871 | 2.5909 | 2.5543 | 0.064087 | 0.027466 | 0.045777 | -122.8043 | -122.818 | 0.19226 | 0.18768 | 0.16479 | 0.14191 | 0.11902 | 0.16022 | 0.022888 | 0.14648 | 0.032043 | 0.068664 | 0.045776 | 2.5955 | 0.091553 | -120.369 | -122.85 | 2.5497 | 0.07782 | 2.6413 | 0.11902
6007.625 | 122.9416 | -0.07782 | 122.7997 | -0.01976 | 0.01166 | 0.0079254 | -0.0097904 | -0.0021919 | -0.010698 | -0.005159 | -0.011475 | 0.018686 | 0.039003 | -0.016774 | 0.011266 | 0.022683 | -0.0040525 | 2.5452 | 2.4673 | 2.449 | 2.4536 | 2.6047 | 2.4582 | 2.5177 | 0.032043 | 0.009155 | -0.036621 | -0.022888 | 0.10529 | 0.068665 | 0.07782 | 2.5269 | -120.3323 | -120.3461 | 2.6825 | 2.5955 | 2.536 | 0.068664 | 0.009155 | 0.041199 | -122.7905 | -122.8226 | 0.18311 | 0.15564 | 0.14649 | 0.11444 | 0.10529 | 0.15564 | 0.004577 | 0.14191 | 0.013733 | 0.01831 | 0.045776 | 2.5452 | 0.086975 | -120.3506 | -122.8363 | 2.5314 | 0.054932 | 2.623 | 0.10986
6009.3906 | 122.8867 | -0.11444 | 122.7997 | -0.02739 | 0.0123 | 0.008139 | -0.0050906 | -0.0011237 | -0.012407 | -0.0011002 | -0.005371 | 0.023385 | 0.041994 | -0.013997 | 0.01148 | 0.020974 | -0.0023435 | 2.5085 | 2.4948 | 2.4078 | 2.3712 | 2.4765 | 2.3621 | 2.3987 | -0.032043 | 0.027466 | -0.073242 | -0.027466 | 0.059509 | 0.018311 | 0.054932 | 2.5223 | -120.3049 | -120.4285 | 2.5909 | 2.5131 | 2.4765 | -0.009155 | -0.045776 | 0.041199 | -122.7722 | -122.8271 | 0.17395 | 0.16937 | 0.13275 | 0.12817 | 0.091553 | 0.068664 | -0.036621 | 0.13275 | 0.045776 | 0.086975 | 0.10071 | 2.6093 | 0.14191 | -120.3918 | -122.8729 | 2.4857 | 0.086975 | 2.623 | 0.082398
6011.1719 | 122.9004 | -0.09613 | 122.7814 | -0.02739 | 0.011019 | 0.00878 | -0.0063724 | 0.0027215 | -0.010912 | -0.0030228 | -0.011475 | 0.022103 | 0.04178 | -0.013142 | 0.012975 | 0.022683 | -0.0036253 | 2.6321 | 2.5909 | 2.5177 | 2.504 | 2.6367 | 2.504 | 2.5314 | 0.018311 | 0.045776 | -0.050354 | -0.022888 | 0.086975 | 0.045776 | 0.09613 | 2.6138 | -120.1904 | -120.2774 | 2.7328 | 2.6276 | 2.6001 | 0.013733 | -0.013733 | 0.045776 | -122.7356 | -122.8043 | 0.1831 | 0.19226 | 0.14191 | 0.14648 | 0.09613 | 0.11902 | -0.013733 | 0.13733 | 0.027466 | 0.073242 | 0.09613 | 2.6871 | 0.14191 | -120.2637 | -122.8317 | 2.6001 | 0.073242 | 2.7283 | 0.11444
6012.9531 | 122.8867 | -0.10071 | 122.7905 | -0.01976 | 0.012728 | 0.0072846 | -0.0063724 | -0.00069646 | -0.010271 | -0.0011002 | -0.005371 | 0.021249 | 0.04178 | -0.010579 | 0.012121 | 0.021828 | -0.0034117 | 2.6093 | 2.5543 | 2.4857 | 2.4765 | 2.5955 | 2.4811 | 2.5085 | 0.013733 | 0.027466 | -0.054932 | -0.013733 | 0.07782 | 0.027466 | 0.064087 | 2.5864 | -120.2362 | -120.314 | 2.6962 | 2.6093 | 2.5818 | 0.022888 | -0.004578 | 0.045776 | -122.7631 | -122.8043 | 0.17853 | 0.1648 | 0.12817 | 0.11902 | 0.082398 | 0.10986 | -0.009156 | 0.13275 | 0.041199 | 0.068664 | 0.082398 | 2.655 | 0.12817 | -120.3049 | -122.8455 | 2.5772 | 0.086975 | 2.71 | 0.11444
6014.7188 | 122.8775 | -0.10071 | 122.818 | -0.0045011 | 0.016359 | 0.0096344 | -0.0085086 | -0.0015509 | -0.00963 | -0.0047318 | -0.005371 | 0.019754 | 0.040071 | -0.015278 | 0.01383 | 0.021401 | -0.0025571 | 2.4948 | 2.4628 | 2.3895 | 2.3438 | 2.4719 | 2.3438 | 2.3804 | -0.022888 | 0.027466 | -0.068665 | -0.032043 | 0.045776 | 0.009155 | 0.068665 | 2.4902 | -120.3552 | -120.4742 | 2.5726 | 2.4811 | 2.4445 | -0.009155 | -0.045776 | 0.032043 | -122.7905 | -122.85 | 0.14648 | 0.16937 | 0.10986 | 0.13733 | 0.07782 | 0.082398 | -0.045776 | 0.11444 | 0.036622 | 0.073243 | 0.096131 | 2.5635 | 0.12817 | -120.4285 | -122.8867 | 2.4445 | 0.068665 | 2.5955 | 0.07782
6016.4375 | 122.8546 | -0.10529 | 122.818 | -0.02739 | 0.016146 | 0.0089936 | -0.0074404 | -0.0024055 | -0.0098438 | -0.0036636 | -0.011475 | 0.022103 | 0.037935 | -0.012715 | 0.012121 | 0.023751 | -0.0014891 | 2.4902 | 2.504 | 2.4124 | 2.3483 | 2.4582 | 2.3346 | 2.3666 | -0.07782 | 0.059509 | -0.068665 | -0.059509 | 0.013733 | -0.045776 | 0.045776 | 2.5177 | -120.314 | -120.4697 | 2.5635 | 2.4719 | 2.4399 | -0.045777 | -0.07782 | 0.036621 | -122.7585 | -122.8775 | 0.11902 | 0.15106 | 0.05951 | 0.11444 | 0.022889 | 0.045776 | -0.064087 | 0.082398 | 0.009156 | 0.091552 | 0.12817 | 2.6093 | 0.16479 | -120.4056 | -122.8867 | 2.4536 | 0.045777 | 2.5955 | 0.027466
6018.2031 | 122.85 | -0.14191 | 122.8226 | -0.0045011 | 0.011873 | 0.0057892 | -0.012995 | 0.0010125 | -0.010271 | -0.0047318 | -0.0084228 | 0.017831 | 0.040926 | -0.020619 | 0.010626 | 0.022896 | -0.0046933 | 2.6047 | 2.6001 | 2.5131 | 2.4857 | 2.6276 | 2.5452 | 2.5314 | -0.064087 | 0.054932 | -0.07782 | -0.086975 | 0.045776 | 0.004578 | 0.036621 | 2.655 | -120.2225 | -120.3369 | 2.7695 | 2.6733 | 2.6871 | 0.01831 | 0.032043 | 0.064087 | -122.7676 | -122.9095 | 0.18768 | 0.17853 | 0.14649 | 0.11444 | 0.082398 | 0.11444 | -0.027466 | 0.1236 | -0.009155 | 0.086975 | 0.13275 | 2.742 | 0.19684 | -120.3094 | -122.9004 | 2.6276 | 0.054932 | 2.7466 | 0.07782
6019.9844 | 122.937 | -0.059509 | 122.7448 | -0.01976 | 0.012514 | 0.011343 | -0.010858 | -0.0026191 | -0.011553 | -0.0019546 | -0.005371 | 0.019754 | 0.03879 | -0.016774 | 0.0084893 | 0.02311 | -0.0034117 | 2.5131 | 2.3941 | 2.4078 | 2.4445 | 2.6138 | 2.449 | 2.4811 | 0.091553 | -0.004578 | -0.041199 | 0.032043 | 0.14191 | 0.10529 | 0.1236 | 2.4673 | -120.3506 | -120.3003 | 2.6733 | 2.5406 | 2.5085 | 0.073242 | 0.041199 | 0.01831 | -122.7493 | -122.7127 | 0.20142 | 0.1831 | 0.16479 | 0.16479 | 0.14649 | 0.20599 | 0.036621 | 0.18311 | 0.073242 | -0.013733 | 0.036621 | 2.4536 | 0.054931 | -120.3369 | -122.7859 | 2.504 | 0.091552 | 2.5726 | 0.15106
6021.7031 | 122.8546 | -0.10071 | 122.8271 | -0.012131 | 0.010378 | 0.0072846 | -0.009363 | 0.00079894 | -0.0098438 | -0.0028092 | -0.0084228 | 0.019967 | 0.040499 | -0.010365 | 0.0087029 | 0.021828 | -0.0049069 | 2.6459 | 2.5635 | 2.5314 | 2.5177 | 2.6642 | 2.536 | 2.5635 | -0.004578 | 0.036621 | -0.064087 | -0.059509 | 0.054932 | 0.013733 | 0.041199 | 2.6321 | -120.2637 | -120.3094 | 2.7649 | 2.6642 | 2.6367 | 0.032044 | 0.004578 | 0.036621 | -122.7905 | -122.8867 | 0.15564 | 0.14191 | 0.11444 | 0.10529 | 0.07782 | 0.13275 | -0.013733 | 0.11902 | 0.004578 | 0.032044 | 0.10071 | 2.6642 | 0.13733 | -120.2957 | -122.8912 | 2.6184 | 0.041199 | 2.7466 | 0.09613
6023.4844 | 122.9324 | -0.091553 | 122.7997 | -0.012131 | 0.011019 | 0.0068574 | -0.0089358 | 0.00037174 | -0.010057 | -0.0036636 | -0.005371 | 0.017617 | 0.043489 | -0.022542 | 0.0095575 | 0.023323 | -0.0036253 | 2.536 | 2.449 | 2.4307 | 2.4307 | 2.5635 | 2.4353 | 2.4811 | 0.009155 | 0.009155 | -0.050354 | -0.022888 | 0.11444 | 0.082397 | 0.10071 | 2.5223 | -120.3506 | -120.369 | 2.655 | 2.5726 | 2.5269 | 0.050354 | 0.004578 | 0.041199 | -122.7905 | -122.8226 | 0.20599 | 0.19226 | 0.17395 | 0.15106 | 0.13275 | 0.13275 | 0 | 0.16479 | 0.027466 | 0.018311 | 0.059509 | 2.5406 | 0.10071 | -120.369 | -122.85 | 2.5223 | 0.068665 | 2.6276 | 0.10071
6025.2188 | 122.9141 | -0.07782 | 122.8088 | -0.012131 | 0.011232 | 0.0049346 | -0.009363 | 0.0010125 | -0.0081348 | -0.0057998 | -0.0084228 | 0.019326 | 0.038362 | -0.017415 | 0.0095575 | 0.021187 | -0.0051205 | 2.5085 | 2.4445 | 2.4124 | 2.4124 | 2.5635 | 2.449 | 2.4765 | 0.009155 | 0.022888 | -0.054932 | -0.018311 | 0.10529 | 0.073242 | 0.082397 | 2.4902 | -120.3644 | -120.3964 | 2.6413 | 2.5543 | 2.5269 | 0.064086 | 0.036621 | 0.022888 | -122.7859 | -122.8271 | 0.18311 | 0.16022 | 0.15106 | 0.13733 | 0.12817 | 0.15106 | 0 | 0.16022 | 0.036621 | 0.032043 | 0.07782 | 2.5223 | 0.10071 | -120.3964 | -122.8638 | 2.4902 | 0.059509 | 2.5864 | 0.086975
6026.9844 | 122.9324 | -0.07782 | 122.8271 | -0.012131 | 0.013369 | 0.0096344 | -0.0095766 | -0.0030463 | -0.011766 | -0.0060134 | -0.005371 | 0.018472 | 0.040712 | -0.019124 | 0.0084893 | 0.022255 | -0.0031979 | 2.5085 | 2.4078 | 2.4124 | 2.4307 | 2.5543 | 2.4124 | 2.4628 | 0.050354 | 0.022888 | -0.064087 | -0.004578 | 0.091553 | 0.073242 | 0.086975 | 2.4902 | -120.4193 | -120.3964 | 2.6321 | 2.5406 | 2.4902 | 0.050354 | 0 | 0.013733 | -122.8043 | -122.8317 | 0.16937 | 0.16479 | 0.15106 | 0.15106 | 0.13733 | 0.14191 | 0.01831 | 0.15564 | 0.059509 | -0.004578 | 0.086975 | 2.4857 | 0.10071 | -120.4147 | -122.8912 | 2.5085 | 0.073242 | 2.5864 | 0.12817
6028.7031 | 122.9507 | -0.059509 | 122.8043 | -0.01976 | 0.0099506 | 0.0079254 | -0.009363 | 0.0031487 | -0.01198 | -0.0047318 | -0.005371 | 0.019113 | 0.039644 | -0.015278 | 0.010626 | 0.022042 | -0.0040525 | 2.6367 | 2.5177 | 2.5223 | 2.5772 | 2.7054 | 2.5818 | 2.5955 | 0.10529 | 0.009155 | -0.041199 | 0.022888 | 0.16479 | 0.12817 | 0.11444 | 2.5818 | -120.2866 | -120.2271 | 2.7649 | 2.655 | 2.6413 | 0.073242 | 0.059509 | 0.01831 | -122.7951 | -122.7814 | 0.2243 | 0.17395 | 0.18768 | 0.15564 | 0.16937 | 0.1831 | 0.054931 | 0.20599 | 0.064087 | -0.004578 | 0.050354 | 2.5772 | 0.068664 | -120.282 | -122.8455 | 2.6367 | 0.082397 | 2.6962 | 0.16479
6030.4844 | 122.8867 | -0.10529 | 122.8271 | -0.01976 | 0.014223 | 0.0083526 | -0.0057314 | 0.0057123 | -0.0098438 | -0.0028092 | -0.0084228 | 0.022103 | 0.041567 | -0.010579 | 0.011907 | 0.020333 | -0.0040525 | 2.4673 | 2.4399 | 2.3621 | 2.3209 | 2.417 | 2.3026 | 2.3621 | -0.032043 | 0.045776 | -0.068665 | -0.050354 | 0.027466 | -0.004578 | 0.041199 | 2.4673 | -120.3873 | -120.5063 | 2.5223 | 2.4673 | 2.4078 | 0 | -0.05951 | 0.036621 | -122.7814 | -122.8775 | 0.13275 | 0.14649 | 0.10071 | 0.10986 | 0.064087 | 0.054931 | -0.041199 | 0.096131 | 0.018311 | 0.077819 | 0.11444 | 2.5452 | 0.15106 | -120.4651 | -122.8958 | 2.4261 | 0.054932 | 2.5726 | 0.073243
6032.2031 | 122.9691 | -0.064087 | 122.7859 | -0.012131 | 0.009737 | 0.00878 | -0.010858 | -0.00069646 | -0.011766 | -0.0047318 | -0.011475 | 0.016763 | 0.039858 | -0.013356 | 0.0087029 | 0.021828 | -0.0036253 | 2.6184 | 2.4948 | 2.4948 | 2.5497 | 2.6917 | 2.5726 | 2.6001 | 0.1236 | 0.013733 | -0.036621 | 0.054932 | 0.19684 | 0.14648 | 0.13733 | 2.5589 | -120.2911 | -120.2362 | 2.7557 | 2.6642 | 2.6367 | 0.10529 | 0.07782 | 0.027466 | -122.7722 | -122.731 | 0.26093 | 0.20142 | 0.21057 | 0.17395 | 0.18311 | 0.19684 | 0.054932 | 0.23346 | 0.091553 | 0 | 0.050354 | 2.5589 | 0.07782 | -120.2911 | -122.8226 | 2.6138 | 0.11902 | 2.6825 | 0.18768
6033.9844 | 122.9553 | -0.09613 | 122.7722 | -0.01976 | 0.009737 | 0.0083526 | -0.0080814 | -0.0024055 | -0.010912 | -0.0055862 | -0.011475 | 0.01954 | 0.042208 | -0.019978 | 0.0084893 | 0.021401 | -0.0044797 | 2.504 | 2.4399 | 2.4307 | 2.4124 | 2.5314 | 2.4216 | 2.4628 | 0.022888 | 0.009155 | -0.086975 | -0.004578 | 0.1236 | 0.091553 | 0.09613 | 2.5269 | -120.3323 | -120.3598 | 2.6276 | 2.5589 | 2.5177 | 0.032044 | -0.009155 | 0.009155 | -122.7631 | -122.7768 | 0.21973 | 0.19226 | 0.18768 | 0.1831 | 0.17853 | 0.10071 | -0.01831 | 0.21057 | 0.082397 | 0.009155 | 0.09613 | 2.536 | 0.10528 | -120.3415 | -122.8592 | 2.5085 | 0.091552 | 2.6001 | 0.11902
6035.7656 | 122.8867 | -0.10071 | 122.8363 | -0.02739 | 0.0123 | 0.0085662 | -0.0050906 | -0.00069646 | -0.011125 | -0.0028092 | -0.005371 | 0.021035 | 0.040285 | -0.018269 | 0.013616 | 0.020333 | -0.0051205 | 2.4628 | 2.4445 | 2.3529 | 2.3117 | 2.4216 | 2.298 | 2.3483 | -0.032043 | 0.041199 | -0.064087 | -0.054932 | 0.032043 | -0.004578 | 0.045776 | 2.4536 | -120.3918 | -120.5246 | 2.5223 | 2.449 | 2.3987 | -0.004577 | -0.054931 | 0.036621 | -122.7951 | -122.8912 | 0.13275 | 0.14648 | 0.09613 | 0.10986 | 0.059509 | 0.068665 | -0.041198 | 0.09613 | 0.009155 | 0.091553 | 0.10529 | 2.5452 | 0.14191 | -120.4834 | -122.9004 | 2.4124 | 0.045776 | 2.5635 | 0.068665
6037.4844 | 122.9507 | -0.07782 | 122.7768 | -0.012131 | 0.009737 | 0.0077118 | -0.008295 | -0.0049689 | -0.012407 | -0.0025956 | -0.005371 | 0.020395 | 0.039644 | -0.014638 | 0.0091303 | 0.021401 | 0.00064735 | 2.5177 | 2.4445 | 2.4261 | 2.4124 | 2.5543 | 2.4307 | 2.4719 | 0.018311 | 0.004578 | -0.045776 | 0.004578 | 0.14191 | 0.086975 | 0.10529 | 2.504 | -120.3323 | -120.3644 | 2.6321 | 2.5497 | 2.5085 | 0.045777 | 0.004578 | 0.032044 | -122.7722 | -122.7722 | 0.21973 | 0.18311 | 0.16479 | 0.15106 | 0.13275 | 0.12817 | -0.013732 | 0.18768 | 0.050354 | 0.018311 | 0.050354 | 2.5223 | 0.082398 | -120.3506 | -122.8226 | 2.4902 | 0.082398 | 2.5955 | 0.096131
6039.2656 | 122.9691 | -0.073242 | 122.818 | -0.01976 | 0.009096 | 0.0092072 | -0.0087222 | -0.0017645 | -0.00963 | -0.0038772 | -0.005371 | 0.021676 | 0.039644 | -0.015065 | 0.0097711 | 0.022896 | -0.0038389 | 2.6138 | 2.504 | 2.4994 | 2.5452 | 2.7054 | 2.5726 | 2.5955 | 0.10986 | 0.013733 | -0.027466 | 0.050354 | 0.16937 | 0.13733 | 0.13275 | 2.5726 | -120.314 | -120.2728 | 2.7786 | 2.6688 | 2.6459 | 0.09613 | 0.073242 | 0.045776 | -122.8043 | -122.7676 | 0.24261 | 0.20599 | 0.21057 | 0.16022 | 0.16479 | 0.20599 | 0.045776 | 0.19684 | 0.07782 | 0.004577 | 0.041199 | 2.5772 | 0.086975 | -120.3186 | -122.8455 | 2.6184 | 0.1236 | 2.6871 | 0.18311
6041.0625 | 122.9874 | -0.054932 | 122.7768 | -0.02739 | 0.012087 | 0.0089936 | -0.0087222 | 0.0050713 | -0.010271 | -0.0070816 | -0.014526 | 0.018899 | 0.041353 | -0.018483 | 0.011907 | 0.021401 | -0.0027707 | 2.5177 | 2.3666 | 2.3621 | 2.4078 | 2.5223 | 2.3666 | 2.4261 | 0.11902 | -0.009155 | -0.045776 | 0.068665 | 0.16479 | 0.11444 | 0.15106 | 2.417 | -120.4102 | -120.369 | 2.5772 | 2.4811 | 2.4216 | 0.064086 | 0.004577 | 0.009156 | -122.7859 | -122.7081 | 0.21973 | 0.20599 | 0.16937 | 0.19684 | 0.16022 | 0.16022 | 0.045776 | 0.21057 | 0.11444 | 0.004577 | 0.036621 | 2.4216 | 0.045777 | -120.4147 | -122.8226 | 2.4628 | 0.1236 | 2.5726 | 0.17395
6042.8438 | 122.8729 | -0.10071 | 122.818 | -0.012131 | 0.0082416 | 0.0083526 | -0.0097904 | 0.0016535 | -0.013048 | -0.0011002 | -0.005371 | 0.019967 | 0.04114 | -0.015492 | 0.0080621 | 0.021187 | -0.0029843 | 2.6093 | 2.5131 | 2.4857 | 2.5269 | 2.6505 | 2.5406 | 2.5726 | 0.013733 | 0.032043 | -0.059509 | -0.036621 | 0.07782 | 0.045776 | 0.041199 | 2.5864 | -120.3049 | -120.2911 | 2.7512 | 2.6733 | 2.6413 | 0.086975 | 0.054931 | 0.041199 | -122.7859 | -122.8546 | 0.17853 | 0.14191 | 0.14648 | 0.10071 | 0.10528 | 0.1648 | 0.041198 | 0.13733 | 0.022888 | 0.027466 | 0.091552 | 2.6138 | 0.13275 | -120.3323 | -122.8775 | 2.6276 | 0.064087 | 2.71 | 0.11444
6044.5625 | 122.9233 | -0.086975 | 122.7951 | -0.02739 | 0.012514 | 0.00878 | -0.0070132 | -0.0013373 | -0.010698 | -0.0030228 | -0.011475 | 0.02189 | 0.041567 | -0.0075879 | 0.012334 | 0.023751 | -0.0053343 | 2.4536 | 2.4261 | 2.3575 | 2.3026 | 2.4216 | 2.298 | 2.3346 | -0.004578 | 0.041199 | -0.059509 | -0.004578 | 0.073242 | 0.032043 | 0.091553 | 2.4445 | -120.369 | -120.4926 | 2.5085 | 2.4216 | 2.3849 | -0.022888 | -0.059509 | 0.027466 | -122.7539 | -122.7997 | 0.16022 | 0.17853 | 0.11902 | 0.15106 | 0.091552 | 0.064087 | -0.054932 | 0.13275 | 0.054931 | 0.068664 | 0.10071 | 2.5131 | 0.12817 | -120.4376 | -122.8546 | 2.3895 | 0.082397 | 2.5406 | 0.082397
6046.6562 | 122.85 | -0.10986 | 122.8043 | -0.02739 | 0.013796 | 0.0077118 | -0.0061588 | -0.0028327 | -0.0089892 | -0.0021682 | -0.005371 | 0.022103 | 0.04178 | -0.013997 | 0.012762 | 0.022896 | -0.0078977 | 2.4582 | 2.4399 | 2.3483 | 2.298 | 2.3941 | 2.2751 | 2.3071 | -0.068665 | 0.036621 | -0.086975 | -0.054932 | 0.013733 | -0.036621 | 0.018311 | 2.4582 | -120.3644 | -120.5063 | 2.504 | 2.417 | 2.3849 | -0.041199 | -0.073243 | 0.022888 | -122.7676 | -122.8592 | 0.1236 | 0.12817 | 0.073242 | 0.10529 | 0.050354 | 0.045776 | -0.050354 | 0.10071 | 0.032043 | 0.091552 | 0.1236 | 2.5497 | 0.14648 | -120.4559 | -122.8912 | 2.4078 | 0.054931 | 2.5681 | 0.041198
6050.3594 | 122.9919 | -0.073242 | 122.7859 | -0.02739 | 0.011019 | 0.0060028 | -0.011927 | -0.0015509 | -0.010698 | -0.0030228 | -0.005371 | 0.019326 | 0.042421 | -0.019764 | 0.0093439 | 0.022896 | -0.0049069 | 2.5589 | 2.4582 | 2.4673 | 2.4948 | 2.6779 | 2.5452 | 2.5681 | 0.13733 | 0.004578 | -0.045776 | 0.050354 | 0.1831 | 0.15564 | 0.13733 | 2.5406 | -120.3278 | -120.2911 | 2.7512 | 2.6413 | 2.6184 | 0.10071 | 0.07782 | 0.027466 | -122.7814 | -122.7356 | 0.25635 | 0.21057 | 0.22888 | 0.18311 | 0.20142 | 0.21057 | 0.027466 | 0.22888 | 0.09613 | -0.009155 | 0.050354 | 2.5314 | 0.07782 | -120.3186 | -122.8317 | 2.5681 | 0.1236 | 2.6321 | 0.21057
6053.8281 | 122.8683 | -0.10529 | 122.8271 | -0.01976 | 0.011446 | 0.0072846 | -0.009363 | 0.0031487 | -0.01198 | -0.001741 | -0.005371 | 0.01954 | 0.042208 | -0.015065 | 0.011694 | 0.021401 | -0.0019163 | 2.5955 | 2.504 | 2.4536 | 2.4399 | 2.5681 | 2.4719 | 2.4948 | -0.032043 | 0.032043 | -0.054932 | -0.073242 | 0.054932 | 0.013733 | 0.022888 | 2.5589 | -120.3232 | -120.3873 | 2.6733 | 2.6001 | 2.5772 | 0.041199 | 0.018311 | 0.050354 | -122.7951 | -122.9004 | 0.16022 | 0.12817 | 0.11902 | 0.07782 | 0.068665 | 0.11444 | -0.013733 | 0.10986 | -0.01831 | 0.050354 | 0.086975 | 2.6093 | 0.13733 | -120.3735 | -122.8821 | 2.5452 | 0.032044 | 2.7008 | 0.073243
6059.5 | 122.9462 | -0.086975 | 122.7951 | -0.01976 | 0.011446 | 0.0092072 | -0.0087222 | -0.00026906 | -0.011339 | -0.002382 | -0.011475 | 0.017617 | 0.040926 | -0.014851 | 0.0091303 | 0.022255 | -0.0081113 | 2.4811 | 2.4033 | 2.3804 | 2.3712 | 2.5269 | 2.3895 | 2.4307 | 0.013733 | 0 | -0.064087 | 0.022888 | 0.14191 | 0.11444 | 0.11902 | 2.4673 | -120.3918 | -120.4239 | 2.6138 | 2.5177 | 2.4765 | 0.050354 | 0.009155 | 0.022888 | -122.7951 | -122.7722 | 0.22888 | 0.20599 | 0.20142 | 0.18311 | 0.17853 | 0.14648 | -0.009155 | 0.20599 | 0.086975 | 0.022888 | 0.064087 | 2.4902 | 0.086975 | -120.4147 | -122.8592 | 2.4582 | 0.10986 | 2.5681 | 0.10071
6061.2969 | 122.9736 | -0.086975 | 122.8043 | -0.02739 | 0.0123 | 0.00878 | -0.01214 | -0.0039007 | -0.0089892 | -0.0047318 | -0.005371 | 0.019113 | 0.039217 | -0.018269 | 0.0099847 | 0.023323 | -0.0021299 | 2.504 | 2.4033 | 2.3849 | 2.417 | 2.5543 | 2.4307 | 2.4948 | 0.064087 | 0 | -0.041199 | 0.036621 | 0.16937 | 0.13733 | 0.13733 | 2.4719 | -120.401 | -120.3873 | 2.6413 | 2.5818 | 2.5177 | 0.10986 | 0.045776 | 0.045776 | -122.8043 | -122.7676 | 0.25635 | 0.2243 | 0.2243 | 0.17853 | 0.17853 | 0.16937 | 0.032043 | 0.21057 | 0.07782 | 0.01831 | 0.041199 | 2.4902 | 0.086975 | -120.4193 | -122.8455 | 2.504 | 0.1236 | 2.5909 | 0.15106

## Thermal Data
Fire Time | A Position - Middle | C Position - 3' | C Position - Middle | C Position - 7'
-0.4021 | 3.6409 | 3.9559 | 4.556 | 3.9284
0.5979 | 3.738 | 3.9611 | 4.5507 | 3.941
1.5979 | 3.6475 | 3.9573 | 4.55 | 3.9362
2.5979 | 3.7 | 3.963 | 4.5479 | 3.9425
3.5979 | 3.7405 | 3.9643 | 4.5597 | 3.9425
4.5979 | 3.688 | 3.9554 | 4.5687 | 3.9475
5.5979 | 4.073 | 3.9576 | 4.5793 | 3.9766
6.5979 | 4.842 | 3.9645 | 4.6666 | 3.9978
7.5979 | 8.5275 | 4.8342 | 5.3208 | 4.8484
8.5979 | 13.596 | 4.9594 | 5.4494 | 4.8516
9.5979 | 18.2062 | 5.2154 | 5.5669 | 5.0278
10.5979 | 23.4352 | 5.6184 | 5.69 | 5.2665
11.5979 | 27.9588 | 6.6476 | 6.5995 | 6.7185
12.5979 | 34.218 | 7.5121 | 7.3129 | 9.2251
13.5979 | 51.8333 | 9.2282 | 9.3704 | 10.448
14.5979 | 61.1124 | 11.1273 | 10.614 | 11.2809
15.5979 | 67.5981 | 13.3912 | 12.2414 | 13.3954
16.5979 | 74.0906 | 15.7536 | 13.9482 | 15.1328
17.5979 | 83.4092 | 18.057 | 15.9907 | 17.8928
18.5979 | 90.108 | 20.8512 | 18.6105 | 20.8153
19.5979 | 98.175 | 23.2607 | 20.6018 | 23.2965
20.5979 | 126.0742 | 25.8278 | 23.0388 | 25.4147
21.5979 | 156.36 | 27.6436 | 25.4599 | 28.2342
22.5979 | 176.0744 | 29.0546 | 27.9818 | 31.1758
23.5979 | 186.8289 | 32.1857 | 29.3319 | 32.6363
24.5979 | 219.811 | 34.6637 | 31.2022 | 35.6405
25.5979 | 218.1273 | 36.2952 | 33.5293 | 38.2957
26.5979 | 225.4827 | 38.0457 | 35.4005 | 40.2245
27.5979 | 230.3719 | 40.5804 | 37.2474 | 43.5067
28.5979 | 232.3997 | 42.139 | 39.8373 | 45.7267
29.5979 | 253.7704 | 44.9273 | 42.1458 | 46.9069
30.5979 | 278.502 | 47.4585 | 44.1442 | 48.7023
31.5979 | 319.8576 | 49.0158 | 46.3836 | 50.8567
32.5979 | 345.0325 | 50.9928 | 48.2978 | 53.5761
33.5979 | 375.1523 | 52.9725 | 51.1965 | 55.5443
34.5979 | 401.8273 | 55.5081 | 53.0646 | 57.656
35.5979 | 438.6553 | 58.3375 | 55.1507 | 60.2042
36.5979 | 461.7209 | 61.3675 | 48.4112 | 63.4692
37.5979 | 487.3701 | 64.5942 | 52.2764 | 66.3449
38.5979 | 512.5745 | 66.6963 | 62.3377 | 68.9969
39.5979 | 517.2264 | 69.2637 | 64.723 | 71.1486
40.5979 | 552.9983 | 71.4965 | 67.5776 | 74.0782
41.5979 | 573.6097 | 74.1431 | 69.9879 | 76.5935
42.5979 | 591.8185 | 75.9156 | 73.1378 | 78.3769
43.5979 | 589.2465 | 76.907 | 75.4456 | 80.1639
44.5979 | 594.8596 | 79.279 | 77.8032 | 81.5279
45.5979 | 588.5777 | 80.0927 | 79.5894 | 83.5865
46.5979 | 582.0342 | 81.1575 | 81.3001 | 85.2809
47.5979 | 586.237 | 82.1813 | 83.1168 | 87.5917
48.5979 | 572.0841 | 83.6254 | 85.3713 | 89.3684
49.5979 | 560.0943 | 85.704 | 87.5364 | 90.7067
50.5979 | 558.351 | 86.4947 | 89.2572 | 92.3775
51.5979 | 563.7425 | 87.312 | 90.0947 | 93.5341
52.5979 | 558.1713 | 88.7029 | 91.5355 | 95.6632
53.5979 | 561.9051 | 90.2628 | 93.0109 | 97.6343
54.5979 | 549.0326 | 91.9174 | 94.5689 | 98.9122
55.5979 | 545.4347 | 93.6105 | 96.1185 | 99.9333
56.5979 | 554.2109 | 95.0105 | 97.9612 | 100.8165
57.5979 | 534.0569 | 96.4212 | 99.5374 | 102.255
58.5979 | 524.776 | 97.777 | 101.0284 | 104.0595
59.5979 | 515.779 | 99.1975 | 102.305 | 104.7834
60.5979 | 498.0919 | 99.5905 | 103.6766 | 105.3819
61.5979 | 485.2051 | 101.1233 | 104.6999 | 106.6741
62.5979 | 474.2637 | 102.2556 | 105.7047 | 107.5601
63.5979 | 458.4105 | 103.3471 | 106.901 | 108.6586
64.5979 | 444.1928 | 104.2268 | 108.1709 | 109.6212
65.5979 | 432.8178 | 104.8274 | 109.349 | 110.1616
66.5979 | 425.4974 | 105.5748 | 110.1817 | 110.7687
67.5979 | 416.2564 | 106.5013 | 111.3075 | 112.3487
68.5979 | 409.1468 | 107.462 | 112.5644 | 113.8518
69.5979 | 400.1816 | 108.2327 | 113.7575 | 114.6665
70.5979 | 394.5128 | 109.1098 | 115.2078 | 115.1212
71.5979 | 387.7552 | 110.1521 | 115.8769 | 115.672
72.5979 | 382.8252 | 111.3157 | 116.5665 | 117.1084
73.5979 | 377.1385 | 111.7022 | 117.5523 | 118.4188
74.5979 | 370.4996 | 112.7808 | 118.5017 | 119.8411
75.5979 | 363.9785 | 114.4174 | 119.1798 | 120.6846
76.5979 | 360.0879 | 115.125 | 120.0749 | 121.3799
77.5979 | 352.8133 | 116.2179 | 121.1304 | 122.2137
78.5979 | 351.1411 | 117.391 | 121.6155 | 122.4622
79.5979 | 351.6979 | 117.7166 | 122.8282 | 122.612
80.5979 | 354.7259 | 118.1605 | 124.0489 | 122.4889
81.5979 | 351.4456 | 118.6451 | 124.4782 | 123.3096
82.5979 | 346.6037 | 119.3926 | 124.9422 | 123.8053
83.5979 | 344.0043 | 120.2406 | 125.265 | 124.0127
84.6292 | 340.7738 | 121.1386 | 125.7139 | 123.7287
85.5979 | 338.1355 | 120.7631 | 126.3454 | 123.8355
86.5979 | 339.962 | 121.2934 | 126.7323 | 123.955
87.5979 | 337.0264 | 121.7686 | 127.0897 | 124.5177
88.5979 | 336.9518 | 122.0366 | 127.8285 | 125.5962
89.5979 | 338.262 | 122.3213 | 127.9248 | 125.9878
90.5979 | 334.9651 | 122.3811 | 128.3328 | 126.4537
91.5979 | 330.0973 | 123.1117 | 128.8952 | 127.3226
92.5979 | 326.0666 | 123.8809 | 129.501 | 127.9236
93.5979 | 321.385 | 124.7358 | 129.9569 | 128.1887
94.5979 | 318.9501 | 125.4318 | 130.1513 | 128.9093
95.6135 | 317.4945 | 125.11 | 130.3085 | 128.9204
96.5979 | 316.8591 | 124.8871 | 130.6812 | 129.1037
97.5979 | 313.9087 | 124.8607 | 130.9353 | 129.2409
98.5979 | 315.0761 | 124.7862 | 130.9054 | 129.9465
99.5979 | 316.308 | 125.0517 | 131.2553 | 130.176
100.5979 | 315.5429 | 125.402 | 131.1589 | 130.4865
101.5979 | 314.1208 | 125.7679 | 131.2833 | 131.081
102.5979 | 315.3969 | 126.1324 | 131.621 | 131.4246
103.5979 | 321.6148 | 126.5721 | 131.8683 | 131.526
104.5979 | 325.966 | 126.9757 | 132.7699 | 131.6846
105.5979 | 324.7786 | 127.269 | 133.1438 | 132.0838
106.5979 | 325.6348 | 127.7732 | 133.7449 | 132.8964
107.5979 | 324.2463 | 128.4913 | 133.9944 | 133.3526
108.5979 | 322.5654 | 128.3219 | 134.5064 | 133.6457
109.5979 | 319.7671 | 128.7707 | 134.4832 | 133.4916
110.5979 | 317.3474 | 128.9624 | 134.8093 | 133.8376
111.5979 | 314.8347 | 129.3365 | 134.8049 | 133.7165
112.5979 | 312.5196 | 129.8667 | 134.7372 | 133.9451
113.5979 | 311.8071 | 129.476 | 134.7672 | 134.4443
114.5979 | 310.1972 | 129.3915 | 134.7973 | 134.4894
115.5979 | 308.9496 | 129.2748 | 134.8006 | 135.1304
116.5979 | 309.0312 | 129.4642 | 134.6767 | 135.3875
117.5979 | 309.1246 | 129.4942 | 134.5184 | 135.7781
118.5979 | 308.5737 | 129.4941 | 134.471 | 135.0559
119.5979 | 307.9289 | 129.4884 | 134.4628 | 134.5555
120.5979 | 309.3246 | 129.7086 | 134.2289 | 134.2644
121.5979 | 308.0732 | 129.5541 | 134.0849 | 133.9421
122.5979 | 307.6391 | 129.9675 | 134.1368 | 133.7392
123.5979 | 308.3377 | 129.8776 | 134.0547 | 133.9326
124.5979 | 309.7781 | 129.6067 | 134.147 | 133.9003
125.5979 | 312.8956 | 129.329 | 133.9283 | 133.9646
126.5979 | 315.9116 | 129.3138 | 134.0404 | 133.6769
127.5979 | 315.0462 | 129.2891 | 134.0988 | 133.7459
128.5979 | 314.1919 | 129.2424 | 134.0212 | 133.5209
129.5979 | 314.89 | 129.3752 | 135.0617 | 133.668
130.5979 | 315.5102 | 129.6459 | 135.1211 | 133.3931
131.5979 | 316.2513 | 130.0878 | 135.1231 | 133.1609
132.5979 | 316.0774 | 130.446 | 135.3735 | 133.3459
133.5979 | 315.8128 | 130.5067 | 135.5297 | 134.6776
134.5979 | 315.6025 | 130.4501 | 135.7341 | 133.9939
135.5979 | 318.4692 | 131.2211 | 135.8986 | 134.5461
136.5979 | 318.8056 | 131.8989 | 135.8716 | 134.0926
137.5979 | 318.3633 | 132.2865 | 136.724 | 134.3068
138.5979 | 319.7389 | 132.4326 | 137.1852 | 134.448
139.5979 | 320.3725 | 132.4391 | 137.9191 | 134.8743
140.5979 | 317.9418 | 132.6484 | 138.1106 | 134.5472
141.5979 | 318.6559 | 132.7602 | 138.2637 | 135.3686
142.5979 | 320.2915 | 133.2356 | 138.9417 | 135.6392
143.5979 | 318.5351 | 133.4113 | 139.5224 | 136.0242
144.5979 | 316.619 | 133.3617 | 140.1234 | 136.9415
145.5979 | 313.8895 | 134.0977 | 141.338 | 137.7053
146.5979 | 311.2115 | 134.9063 | 140.9984 | 138.4981
147.5979 | 309.7719 | 135.0165 | 141.3311 | 138.8307
148.5979 | 308.0938 | 135.5878 | 141.6025 | 138.4998
149.5979 | 306.1574 | 136.0697 | 141.682 | 138.6507
150.5979 | 302.9559 | 136.4594 | 141.9007 | 138.8825
151.5979 | 302.4388 | 136.7008 | 142.0771 | 138.786
152.5979 | 300.1438 | 136.7862 | 142.0973 | 139.0431
153.5979 | 298.7685 | 136.7812 | 141.8245 | 138.8908
154.5979 | 298.0807 | 136.5292 | 141.7641 | 138.6245
155.5979 | 298.4092 | 136.5591 | 142.3001 | 138.9944
156.5979 | 299.4448 | 136.3227 | 142.5039 | 138.9424
157.5979 | 298.7729 | 136.0993 | 142.6296 | 138.5976
158.5979 | 298.7824 | 136.2551 | 142.6682 | 138.6521
159.5979 | 297.2358 | 136.1433 | 142.4609 | 138.975
160.5979 | 296.6109 | 136.515 | 142.4161 | 139.8665
161.5979 | 298.1543 | 136.5835 | 142.4709 | 139.9884
162.5979 | 296.0137 | 136.8819 | 142.5648 | 139.6789
163.5979 | 296.0063 | 136.9358 | 142.4834 | 140.0891
164.5979 | 293.5331 | 136.8894 | 143.0292 | 140.0364
165.5979 | 294.6773 | 137.1368 | 142.8516 | 140.8319
166.5979 | 292.5745 | 137.7321 | 142.6487 | 141.0574
167.5979 | 290.0227 | 138.0017 | 143.975 | 141.2019
168.5979 | 286.6141 | 138.416 | 144.1227 | 141.7653
169.5979 | 284.6845 | 138.6057 | 144.9409 | 141.9563
170.5979 | 284.5747 | 139.2958 | 145.0838 | 141.6075
171.5979 | 281.8953 | 138.4563 | 145.1087 | 141.614
172.5979 | 280.3069 | 138.2212 | 145.3195 | 143.6109
173.5979 | 278.5301 | 139.1367 | 146.1254 | 143.9013
174.5979 | 277.9357 | 139.029 | 145.975 | 143.8871
175.5979 | 277.0354 | 139.5755 | 146.2956 | 143.7972
176.5979 | 276.9946 | 139.8414 | 146.6342 | 144.514
177.5979 | 275.8385 | 140.191 | 146.6871 | 144.6787
178.5979 | 275.871 | 139.9832 | 146.5852 | 144.6714
179.5979 | 275.8182 | 140.5334 | 147.3382 | 145.2807
180.5979 | 275.9771 | 140.9309 | 147.4613 | 145.5986
181.5979 | 275.5487 | 141.0202 | 148.7607 | 145.734
182.5979 | 276.5689 | 141.1978 | 148.9617 | 145.9374
183.5979 | 278.2878 | 142.2022 | 148.9239 | 145.911
184.5979 | 279.1267 | 142.7429 | 149.3369 | 146.463
185.5979 | 278.0216 | 143.2334 | 149.4412 | 147.2151
186.5979 | 278.4582 | 143.4866 | 149.7681 | 147.1472
187.5979 | 278.8196 | 143.7942 | 150.2746 | 147.2737
188.5979 | 277.5749 | 144.0576 | 150.4825 | 147.8879
189.5979 | 275.5279 | 144.0613 | 151.0319 | 147.8158
190.5979 | 275.3576 | 144.398 | 150.9236 | 148.1828
191.5979 | 276.2804 | 143.9979 | 151.116 | 148.0805
192.5979 | 274.7451 | 144.6232 | 151.3978 | 148.3057
193.5979 | 273.8027 | 144.6578 | 151.4072 | 148.2004
194.5979 | 273.8053 | 144.9551 | 151.7518 | 148.7084
195.5979 | 273.6587 | 145.1323 | 151.9653 | 148.9064
196.5979 | 275.2417 | 145.7985 | 151.7113 | 148.8204
197.5979 | 275.8369 | 146.068 | 151.7784 | 148.9718
198.5979 | 277.1486 | 146.2485 | 151.7744 | 149.0893
199.5979 | 275.1372 | 146.299 | 151.6366 | 150.4226
200.5979 | 273.9607 | 145.8001 | 151.8414 | 151.366
201.5979 | 272.9745 | 146.2421 | 152.0361 | 152.0949
202.5979 | 272.6862 | 146.7366 | 152.7503 | 152.4976
203.5979 | 272.5048 | 146.7766 | 153.5086 | 152.7474
204.5979 | 273.0899 | 147.055 | 153.8501 | 152.4817
205.5979 | 273.3749 | 147.217 | 156.2061 | 153.632
206.5979 | 274.0755 | 147.6328 | 156.3674 | 153.755
207.5979 | 276.0719 | 147.5995 | 156.2576 | 153.6732
208.5979 | 276.1263 | 147.7615 | 156.5248 | 154.9025
209.5979 | 277.6615 | 148.1921 | 156.7752 | 155.0708
210.5979 | 281.1933 | 148.233 | 156.6157 | 155.8778
211.5979 | 283.2946 | 147.9018 | 156.6093 | 155.8639
212.5979 | 282.1868 | 148.4493 | 156.5738 | 155.7797
213.5979 | 284.3666 | 148.763 | 156.8378 | 155.4672
214.5979 | 284.1926 | 148.9125 | 156.8352 | 155.8907
215.5979 | 287.1069 | 149.1162 | 157.2998 | 156.078
216.5979 | 288.3441 | 149.6639 | 157.1984 | 156.1188
217.5979 | 289.2362 | 150.3326 | 157.0956 | 156.0334
218.5979 | 290.346 | 150.2847 | 156.9552 | 155.8094
219.5979 | 292.4237 | 149.9735 | 156.5592 | 155.2115
220.5979 | 293.2536 | 150.2548 | 157.0763 | 156.0008
221.5979 | 294.3171 | 149.9405 | 156.873 | 155.3831
222.5979 | 295.6818 | 150.1912 | 156.4024 | 155.2398
223.5979 | 297.0558 | 150.0683 | 156.1902 | 154.8958
224.5979 | 297.2248 | 149.7256 | 155.9901 | 154.912
225.5979 | 296.3668 | 149.2262 | 155.881 | 154.847
226.5979 | 295.266 | 149.1125 | 155.9231 | 154.9278
227.5979 | 294.539 | 149.1523 | 155.9523 | 155.1413
228.5979 | 293.0433 | 149.1101 | 155.812 | 155.1372
229.5979 | 292.1847 | 150.1804 | 155.942 | 155.205
230.5979 | 292.8373 | 149.6932 | 156.1119 | 156.0548
231.5979 | 295.1148 | 149.8659 | 156.3753 | 156.1765
232.5979 | 295.0255 | 149.7803 | 156.905 | 156.2579
233.5979 | 297.8865 | 150.9518 | 157.2108 | 156.2156
234.5979 | 297.1849 | 150.828 | 158.0326 | 156.8098
235.5979 | 296.3676 | 150.488 | 158.2978 | 156.9842
236.5979 | 299.3681 | 151.3525 | 158.3708 | 156.9377
237.5979 | 299.4312 | 151.5632 | 158.4022 | 156.7608
238.5979 | 299.9987 | 152.1045 | 158.6644 | 156.8144
239.5979 | 302.3637 | 152.8099 | 159.0972 | 156.5964
240.5979 | 304.3102 | 152.6157 | 159.0817 | 156.2914
241.5979 | 307.0221 | 152.5562 | 159.4225 | 156.5399
242.5979 | 308.0808 | 152.2567 | 159.4325 | 156.3657
243.5979 | 311.0177 | 151.9112 | 159.8694 | 156.3879
244.5979 | 312.6487 | 151.7653 | 160.0196 | 156.7574
245.5979 | 315.8672 | 151.594 | 160.132 | 156.5916
246.5979 | 317.2227 | 151.7312 | 159.8646 | 156.4462
247.5979 | 316.8819 | 151.7165 | 160.0628 | 156.99
248.5979 | 316.509 | 151.2 | 159.8376 | 157.1609
249.5979 | 316.705 | 150.9145 | 159.6211 | 156.9963
250.5979 | 319.0523 | 150.4033 | 159.4543 | 156.613
251.5979 | 320.5341 | 150.7169 | 159.7298 | 156.411
252.5979 | 321.9471 | 151.0779 | 159.6289 | 155.8519
253.5979 | 324.565 | 151.3498 | 159.2668 | 155.5198
254.5979 | 326.3526 | 151.6986 | 159.2436 | 155.5239
255.5979 | 326.0263 | 151.7943 | 159.3089 | 155.6649
256.5979 | 326.696 | 151.2418 | 159.4277 | 156.0493
257.5979 | 327.6084 | 151.4273 | 159.4488 | 156.7034
258.5979 | 327.5998 | 151.4915 | 159.6316 | 156.6386
259.5979 | 326.7756 | 152.044 | 159.8288 | 157.3348
260.5979 | 327.0135 | 152.6491 | 159.9086 | 157.7522
261.5979 | 325.601 | 152.8522 | 159.8419 | 157.8932
262.5979 | 324.4829 | 153.1004 | 160.123 | 157.8401
263.5979 | 321.7708 | 153.2125 | 160.3252 | 158.7553
264.5979 | 319.8134 | 153.7936 | 160.3476 | 158.8052
265.6135 | 318.9288 | 154.933 | 160.4231 | 158.8455
266.5979 | 318.0856 | 154.9366 | 161.031 | 159.7236
267.5979 | 319.3693 | 155.0589 | 161.0504 | 159.979
268.5979 | 321.3959 | 155.0939 | 161.197 | 160.4764
269.5979 | 322.3277 | 154.3642 | 161.1301 | 160.8591
270.5979 | 322.0509 | 154.2769 | 161.0519 | 160.5332
271.5979 | 322.3086 | 154.1003 | 161.5239 | 160.2537
272.5979 | 321.3163 | 154.5712 | 161.524 | 159.916
273.5979 | 320.9074 | 154.8547 | 161.7173 | 159.6871
274.5979 | 323.7081 | 154.9689 | 161.6865 | 159.4796
275.5979 | 322.3199 | 154.7661 | 161.5437 | 159.1764
276.5979 | 324.5191 | 154.6824 | 161.5794 | 159.2273
277.5979 | 324.1089 | 154.7626 | 161.5023 | 159.5062
278.5979 | 325.2387 | 154.8674 | 161.3655 | 159.3932
279.5979 | 326.2183 | 154.5193 | 161.2583 | 159.6585
280.5979 | 327.7741 | 154.9263 | 161.643 | 159.7134
281.5979 | 328.7097 | 154.8522 | 161.6748 | 159.4426
282.5979 | 329.7717 | 155.1741 | 161.6182 | 159.5711
283.5979 | 331.6977 | 155.6957 | 161.6159 | 160.1348
284.5979 | 333.09 | 155.3154 | 161.7093 | 159.8845
285.5979 | 334.1576 | 155.4156 | 162.0052 | 159.8235
286.5979 | 334.256 | 155.3918 | 161.7669 | 159.7314
287.5979 | 334.6918 | 155.0353 | 161.8662 | 159.7892
288.5979 | 333.2032 | 155.0954 | 162.5404 | 160.0094
289.5979 | 332.0198 | 154.8412 | 162.6308 | 159.5809
290.5979 | 333.8013 | 154.5989 | 162.7237 | 159.7859
291.5979 | 335.8857 | 153.9804 | 162.8993 | 160.2797
292.5979 | 336.9219 | 154.0192 | 163.1852 | 160.5444
293.5979 | 339.4748 | 153.3634 | 163.3734 | 161.0115
294.5979 | 344.3002 | 153.188 | 163.5862 | 161.3071
295.5979 | 360.0401 | 153.7029 | 164.6417 | 162.0751
296.5979 | 362.7237 | 153.1641 | 165.5335 | 162.4987
297.5979 | 385.0956 | 153.3433 | 166.5362 | 162.9845
298.5979 | 392.8631 | 153.5355 | 166.5901 | 162.6212
299.5979 | 407.1288 | 153.3708 | 166.0564 | 163.0412
300.5979 | 432.8111 | 153.543 | 166.456 | 162.7352
301.5979 | 449.5059 | 153.3985 | 166.4583 | 162.6699
302.5979 | 467.7968 | 153.9122 | 166.3221 | 162.9678
303.5979 | 488.4406 | 154 | 166.2966 | 162.568
304.5979 | 507.1812 | 153.5932 | 166.0578 | 162.9923
305.5979 | 529.9341 | 153.8436 | 166.3863 | 163.1269
306.5979 | 546.3615 | 153.3684 | 166.1238 | 163.376
307.5979 | 559.3237 | 153.4355 | 165.8057 | 163.3423
308.5979 | 572.8534 | 153.636 | 165.8479 | 163.6765
309.5979 | 591.5528 | 153.381 | 166.0912 | 163.8305
310.5979 | 609.2063 | 152.5907 | 166.5713 | 163.7644
311.5979 | 618.4977 | 152.372 | 166.5283 | 163.9114
312.5979 | 639.0754 | 152.449 | 166.6393 | 164.0128
313.5979 | 646.79 | 152.7655 | 167.0515 | 163.9654
314.5979 | 651.7774 | 151.8023 | 166.9195 | 164.1742
315.5979 | 653.7126 | 151.6004 | 166.6674 | 164.4916
316.5979 | 651.8163 | 152.0972 | 166.7446 | 164.0028
317.5979 | 657.2698 | 152.3596 | 166.8978 | 164.0892
318.5979 | 668.6127 | 152.7578 | 166.6987 | 164.2193
319.5979 | 671.5325 | 152.9915 | 166.7386 | 165.1386
320.5979 | 680.8166 | 153.6564 | 166.8509 | 166.0211
321.5979 | 683.4679 | 153.8825 | 166.9507 | 166.481
322.5979 | 685.3236 | 154.488 | 167.0377 | 166.4411
323.5979 | 682.9839 | 154.8088 | 167.5128 | 166.7286
324.6135 | 692.3483 | 154.3296 | 167.3873 | 166.9254
325.5979 | 690.4009 | 154.676 | 167.7772 | 167.7033
326.5979 | 686.8072 | 154.4235 | 167.4614 | 167.6576
327.5979 | 699.3744 | 154.682 | 167.9867 | 168.4505
328.5979 | 699.6288 | 154.4574 | 167.7981 | 168.6398
329.5979 | 707.026 | 154.479 | 167.5156 | 168.7075
330.5979 | 710.8362 | 154.8665 | 167.4396 | 168.8864
331.6135 | 712.0048 | 155.1143 | 167.6641 | 169.0794
332.5979 | 705.1863 | 155.0748 | 168.1843 | 169.7686
333.5979 | 705.0299 | 155.5861 | 168.4282 | 170.1379
334.5979 | 707.4839 | 155.8732 | 168.3909 | 170.282
335.5979 | 710.4258 | 156.3701 | 168.3028 | 170.7517
336.5979 | 716.1159 | 156.4047 | 168.3244 | 171.5649
337.5979 | 715.6165 | 156.4983 | 168.0248 | 172.1254
338.5979 | 721.2584 | 156.6345 | 167.6998 | 172.1692
339.5979 | 724.8515 | 157.1538 | 167.9151 | 172.4658
340.5979 | 726.6148 | 157.1455 | 168.1328 | 171.9998
341.5979 | 726.7537 | 156.6907 | 168.482 | 172.1805
342.5979 | 730.5355 | 156.2641 | 168.8749 | 171.9397
343.5979 | 737.5478 | 156.3327 | 169.9395 | 171.837
344.5979 | 732.8742 | 156.4983 | 169.9434 | 171.981
345.5979 | 743.2464 | 156.4838 | 169.9305 | 171.7176
346.5979 | 743.2143 | 157.0434 | 170.3596 | 171.7847
347.5979 | 738.5133 | 156.8169 | 170.2169 | 172.9142
348.5979 | 740.5622 | 157.1497 | 170.1655 | 172.8373
349.5979 | 736.8056 | 157.7076 | 170.44 | 172.4117
350.5979 | 736.3906 | 158.13 | 170.8126 | 172.6512
351.5979 | 738.2384 | 158.4324 | 170.6093 | 172.1788
352.5979 | 732.058 | 158.0785 | 170.7147 | 172.0532
353.5979 | 734.2403 | 157.766 | 170.7858 | 172.6309
354.5979 | 738.5977 | 158.0301 | 170.4938 | 172.3017
355.5979 | 743.7776 | 158.6875 | 171.016 | 172.6147
356.5979 | 746.1683 | 159.0659 | 170.9325 | 172.4046
357.5979 | 743.3892 | 159.4232 | 171.3034 | 173.0732
358.5979 | 744.5345 | 159.8977 | 171.4882 | 173.5701
359.5979 | 740.2072 | 160.0948 | 171.7872 | 174.0044
360.5979 | 738.4502 | 159.5935 | 172.2809 | 174.6003
361.5979 | 741.7896 | 160.3703 | 172.4084 | 175.4696
362.5979 | 741.7914 | 160.5502 | 172.703 | 175.6375
363.5979 | 743.751 | 160.6516 | 172.9429 | 176.1931
364.5979 | 749.6323 | 160.3977 | 172.9315 | 175.9612
365.5979 | 752.5296 | 160.2324 | 172.8301 | 175.9809
366.5979 | 754.2738 | 160.2769 | 173.0154 | 176.8258
367.5979 | 751.4469 | 159.9759 | 172.997 | 177.1525
368.5979 | 749.2119 | 159.8101 | 172.7704 | 177.7
369.5979 | 751.032 | 159.7496 | 172.7857 | 177.6863
370.5979 | 751.7449 | 159.0451 | 173.1802 | 178.0669
371.5979 | 749.4708 | 159.0315 | 173.4734 | 178.1026
372.5979 | 746.2953 | 159.3875 | 173.8734 | 177.8688
373.5979 | 743.1525 | 159.2761 | 174.0551 | 177.3474
374.5979 | 744.0381 | 159.372 | 174.4871 | 177.8122
375.5979 | 748.7127 | 159.3648 | 174.9711 | 178.3414
376.5979 | 748.4509 | 159.341 | 174.9181 | 178.8781
377.5979 | 743.7362 | 159.0301 | 174.4247 | 179.6333
378.5979 | 747.3181 | 159.4378 | 175.0244 | 180.0094
379.5979 | 748.3451 | 159.9316 | 174.7278 | 180.49
380.5979 | 745.9258 | 160.7392 | 176.0136 | 181.2078
381.5979 | 743.8245 | 160.3556 | 175.8524 | 181.4869
382.5979 | 734.6857 | 160.9216 | 175.6763 | 181.5401
383.5979 | 735.1543 | 160.8167 | 174.942 | 181.4654
384.5979 | 735.1565 | 160.7166 | 175.2846 | 182.0304
385.5979 | 737.8828 | 160.7591 | 175.5739 | 182.5021
386.5979 | 735.6568 | 160.7807 | 175.3034 | 182.7687
387.5979 | 735.8247 | 161.0999 | 175.31 | 183.183
388.5979 | 737.0449 | 161.5767 | 175.7161 | 183.3999
389.5979 | 738.2317 | 162.0806 | 175.5221 | 183.6207
390.5979 | 732.7301 | 162.185 | 175.7363 | 183.4462
391.5979 | 730.0084 | 161.9322 | 176.2117 | 183.4892
392.5979 | 730.8866 | 162.0283 | 176.7904 | 183.6952
393.5979 | 729.3744 | 162.3398 | 176.8438 | 183.206
394.5979 | 732.4416 | 162.2922 | 177.733 | 183.1551
395.5979 | 732.742 | 162.4503 | 177.761 | 183.0397
396.5979 | 727.3923 | 162.6963 | 177.7971 | 183.5007
397.5979 | 730.22 | 162.766 | 178.3423 | 182.9643
398.5979 | 730.5698 | 163.1383 | 178.3202 | 182.5581
399.5979 | 738.0706 | 163.2782 | 178.0912 | 182.0886
400.5979 | 736.6049 | 162.9645 | 177.874 | 181.976
401.5979 | 731.0476 | 163.3378 | 178.0501 | 181.6953
402.5979 | 734.1506 | 163.2997 | 178.0658 | 181.0715
403.5979 | 735.7105 | 162.5594 | 177.9654 | 180.9578
404.5979 | 735.4438 | 162.4512 | 177.871 | 180.405
405.5979 | 739.7368 | 161.7967 | 177.9694 | 179.9238
406.5979 | 730.8752 | 162.3588 | 177.8067 | 180.1227
407.5979 | 735.1473 | 162.9026 | 177.2602 | 180.4552
408.5979 | 732.4279 | 163.2555 | 177.5002 | 180.7443
409.5979 | 733.3076 | 163.5781 | 177.3614 | 180.908
410.5979 | 732.872 | 163.7631 | 177.4537 | 180.8446
411.5979 | 729.1311 | 164.1529 | 177.3624 | 180.4749
412.5979 | 725.0426 | 164.9471 | 177.161 | 180.0049
413.5979 | 728.1649 | 165.2224 | 177.5672 | 179.8899
414.5979 | 728.0987 | 165.1523 | 177.3573 | 180.0382
415.5979 | 732.6262 | 164.8902 | 177.1713 | 179.9314
416.5979 | 734.6347 | 165.2761 | 177.043 | 180.1533
417.5979 | 729.5398 | 164.5342 | 176.9695 | 179.7338
418.5979 | 729.0536 | 164.6346 | 177.2438 | 179.564
419.5979 | 726.409 | 164.6995 | 176.9334 | 179.2436
420.5979 | 728.1074 | 164.6662 | 177.2926 | 179.2909
421.5979 | 724.8408 | 164.9122 | 176.9205 | 179.5424
422.5979 | 720.3729 | 165.4907 | 177.1915 | 180.886
423.5979 | 718.0225 | 164.9848 | 177.3436 | 180.9915
424.5979 | 725.0983 | 165.4678 | 177.1735 | 181.1433
425.5979 | 724.6659 | 165.4443 | 177.6538 | 181.2298
426.5979 | 723.7006 | 165.7722 | 177.8037 | 181.5127
427.5979 | 725.1076 | 166.5156 | 178.0557 | 181.7489
428.5979 | 726.3929 | 166.7235 | 178.5795 | 182.0525
429.5979 | 729.2693 | 166.6721 | 178.9807 | 182.3889
430.5979 | 728.6133 | 166.6304 | 179.4075 | 182.8318
431.5979 | 725.7917 | 167.3954 | 179.325 | 182.3589
432.5979 | 730.8621 | 167.4268 | 178.9952 | 183.0884
433.5979 | 731.5741 | 167.5186 | 178.9833 | 183.1023
434.5979 | 723.6356 | 168.1182 | 179.452 | 182.8345
435.5979 | 729.2737 | 168.0276 | 180.1826 | 182.762
436.5979 | 726.9039 | 168.3597 | 179.8769 | 182.1871
437.5979 | 719.8138 | 168.4574 | 179.7481 | 182.5342
438.5979 | 716.5776 | 169.2241 | 179.7205 | 182.3025
439.5979 | 718.244 | 169.0419 | 179.7187 | 182.5296
440.5979 | 712.0869 | 169.1419 | 179.9016 | 182.2686
441.5979 | 710.2063 | 169.2615 | 179.6367 | 182.6493
442.5979 | 710.1449 | 169.1377 | 179.8384 | 182.7854
443.5979 | 711.1595 | 169.0724 | 179.9007 | 183.0927
444.5979 | 717.7295 | 169.113 | 180.5662 | 182.7946
445.5979 | 715.0595 | 168.834 | 180.6137 | 182.4435
446.5979 | 718.0588 | 168.4017 | 180.6456 | 183.0495
447.5979 | 724.2447 | 168.3698 | 180.5165 | 182.9552
448.5979 | 720.7698 | 169.0833 | 180.6189 | 183.3744
449.5979 | 721.0525 | 169.339 | 180.5268 | 182.6525
450.5979 | 722.4089 | 169.2405 | 180.3902 | 182.3597
451.6135 | 718.2806 | 168.7165 | 180.7046 | 182.5714
452.5979 | 719.0162 | 168.594 | 180.1044 | 182.5408
453.5979 | 721.9492 | 168.7457 | 179.9591 | 182.5727
454.5979 | 723.6167 | 168.3805 | 179.5793 | 182.9946
455.5979 | 714.9903 | 168.3426 | 179.6417 | 182.661
456.5979 | 712.3949 | 168.0442 | 179.0023 | 184.1414
457.5979 | 694.5546 | 167.84 | 178.7933 | 183.8857
458.5979 | 700.5421 | 167.6483 | 179.0066 | 183.5923
459.5979 | 694.5411 | 167.5638 | 179.246 | 183.7829
460.5979 | 680.6315 | 167.4901 | 179.5015 | 183.7661
461.5979 | 668.8542 | 167.2258 | 179.6148 | 184.1818
462.5979 | 670.4744 | 167.1816 | 179.8115 | 183.8536
463.5979 | 674.0597 | 166.9418 | 179.4412 | 183.6674
464.5979 | 676.0557 | 166.9099 | 179.2349 | 183.0862
465.5979 | 666.4551 | 166.9667 | 178.889 | 182.8494
466.5979 | 666.0149 | 167.2698 | 179.0484 | 183.3853
467.5979 | 661.4997 | 167.6444 | 178.9557 | 182.963
468.5979 | 650.2106 | 167.5828 | 179.1384 | 182.805
469.5979 | 662.1581 | 167.8842 | 179.4677 | 182.6669
470.5979 | 671.2559 | 167.9528 | 178.9822 | 182.9183
471.5979 | 673.497 | 168.2644 | 179.0571 | 182.8137
472.5979 | 669.0198 | 168.5289 | 179.7612 | 182.5567
473.5979 | 646.5625 | 168.2517 | 181.4338 | 182.3001
474.5979 | 624.2269 | 168.8183 | 181.3205 | 182.6726
475.5979 | 614.7001 | 168.822 | 180.6888 | 182.9917
476.5979 | 612.7766 | 168.9031 | 180.7082 | 183.4108
477.5979 | 606.1217 | 168.9099 | 181.1674 | 183.356
478.5979 | 583.9327 | 168.8512 | 181.5451 | 183.9838
479.5979 | 573.435 | 168.3988 | 181.8651 | 184.4204
480.5979 | 570.1964 | 168.4346 | 182.2644 | 184.5248
481.5979 | 570.602 | 167.769 | 181.9601 | 184.6107
482.5979 | 570.0676 | 167.7218 | 182.3168 | 184.2903
483.5979 | 562.6333 | 167.1807 | 182.3775 | 184.1075
484.5979 | 561.663 | 166.9823 | 182.1116 | 184.1351
485.5979 | 574.9575 | 167.3476 | 181.9997 | 183.6448
486.5979 | 577.5035 | 167.7145 | 182.1554 | 183.5878
487.5979 | 569.1876 | 168.0319 | 181.7758 | 183.449
488.5979 | 555.9856 | 167.8033 | 182.0142 | 183.3762
489.5979 | 547.3193 | 168.0248 | 182.2185 | 182.9792
490.5979 | 536.8025 | 168.0269 | 182.0338 | 182.7204
491.5979 | 525.9945 | 168.4229 | 181.8809 | 182.8153
492.5979 | 518.0731 | 168.2839 | 181.662 | 182.4828
493.5979 | 512.9839 | 168.7208 | 181.8056 | 181.9323
494.5979 | 507.6512 | 168.0683 | 182.4019 | 182.1013
495.5979 | 505.82 | 168.0746 | 182.0007 | 182.5889
496.5979 | 505.9506 | 168.3728 | 182.0374 | 182.5313
497.5979 | 516.4916 | 168.2269 | 181.8229 | 182.9807
498.5979 | 511.4508 | 167.6129 | 181.6207 | 182.8106
499.5979 | 504.0018 | 167.1904 | 181.457 | 183.0782
500.5979 | 501.4869 | 166.5827 | 181.0934 | 182.8032
501.5979 | 494.532 | 166.3365 | 180.6405 | 182.5664
502.5979 | 486.6909 | 166.4146 | 180.5188 | 182.2964
503.5979 | 483.582 | 166.7433 | 181.3313 | 182.4445
504.5979 | 480.0309 | 167.1133 | 181.1113 | 181.9947
505.5979 | 481.6842 | 167.1922 | 181.4259 | 182.1648
506.5979 | 480.892 | 167.3548 | 181.1707 | 182.1556
507.5979 | 490.8793 | 167.3413 | 181.1467 | 182.3032
508.5979 | 497.2918 | 167.2191 | 181.1985 | 182.1258
509.5979 | 504.0164 | 166.9995 | 181.0737 | 182.6663
510.5979 | 500.7709 | 166.8454 | 181.6864 | 182.3618
511.5979 | 503.503 | 167.3092 | 181.408 | 182.2259
512.5979 | 498.3286 | 167.488 | 181.9613 | 182.1482
513.5979 | 490.3018 | 167.4917 | 181.9512 | 182.131
514.5979 | 483.9029 | 167.2662 | 181.9541 | 182.2869
515.5979 | 477.8523 | 167.2149 | 182.0764 | 182.0753
516.5979 | 479.3797 | 166.5444 | 182.8369 | 182.629
517.5979 | 487.631 | 166.5543 | 182.9346 | 182.6635
518.5979 | 495.0668 | 166.4662 | 183.3451 | 182.7891
519.5979 | 494.9309 | 166.1611 | 183.918 | 182.63
520.5979 | 489.2608 | 167.7559 | 184.4618 | 182.6751
521.5979 | 487.2334 | 167.3753 | 184.9618 | 182.81
522.5979 | 497.2772 | 168.2321 | 185.1251 | 182.842
523.5979 | 498.1801 | 168.6241 | 185.5801 | 183.3076
524.5979 | 502.0067 | 169.1541 | 185.6945 | 183.7236
525.5979 | 495.7386 | 168.7035 | 185.549 | 184.0647
526.5979 | 485.1624 | 168.6646 | 185.5344 | 184.4263
527.5979 | 477.4909 | 169.1225 | 185.2607 | 184.7778
528.5979 | 472.2301 | 168.5259 | 184.9893 | 184.9137
529.5979 | 465.1356 | 168.757 | 185.0473 | 185.5106
530.5979 | 459.1285 | 168.6921 | 185.5589 | 186.0053
531.5979 | 454.4458 | 169.0521 | 185.4546 | 185.8801
532.5979 | 448.0214 | 169.4897 | 185.4309 | 185.8739
533.5979 | 446.1369 | 169.3555 | 185.3049 | 185.9519
534.5979 | 448.6555 | 169.1479 | 185.4993 | 185.7006
535.5979 | 454.1553 | 169.2432 | 186.0952 | 185.5619
536.5979 | 456.527 | 169.2773 | 185.8084 | 185.5954
537.5979 | 454.4186 | 169.4742 | 185.87 | 185.3775
538.5979 | 451.8647 | 169.4171 | 185.8138 | 184.9851
539.5979 | 449.0847 | 169.3826 | 185.3348 | 185.0429
540.5979 | 448.4812 | 169.3073 | 185.2374 | 184.8953
541.5979 | 448.7324 | 168.7015 | 185.2018 | 184.6923
542.5979 | 447.6663 | 168.8063 | 185.0294 | 184.2732
543.5979 | 446.1034 | 169.1244 | 185.0401 | 183.7401
544.5979 | 442.3388 | 168.9882 | 184.7806 | 183.2415
545.5979 | 448.9407 | 169.263 | 184.6477 | 183.1091
546.5979 | 444.8494 | 169.0927 | 184.5982 | 182.7876
547.5979 | 443.8651 | 168.8949 | 184.5898 | 182.6544
548.5979 | 457.4476 | 168.9159 | 184.579 | 182.4904
549.5979 | 464.7256 | 168.681 | 184.6698 | 182.7571
550.5979 | 463.8412 | 168.7692 | 184.6023 | 182.833
551.5979 | 461.9209 | 169.1641 | 184.5196 | 182.2428
552.5979 | 479.3531 | 169.0565 | 184.3526 | 182.1336
553.5979 | 486.6733 | 169.1358 | 184.9767 | 182.3068
554.5979 | 491.0392 | 168.6955 | 184.3975 | 181.8642
555.5979 | 490.5797 | 168.2017 | 184.3321 | 181.7826
556.5979 | 481.7255 | 168.1755 | 183.8982 | 181.4491
557.5979 | 472.6941 | 168.1915 | 184.1508 | 181.484
558.5979 | 465.146 | 168.0506 | 184.1582 | 181.4557
559.5979 | 457.5475 | 168.0813 | 184.0036 | 181.6999
560.5979 | 455.0165 | 168.0087 | 183.8448 | 182.0499
561.5979 | 453.6468 | 168.1133 | 184.0437 | 181.6042
562.5979 | 452.8113 | 168.3515 | 184.0965 | 181.4553
563.5979 | 453.0962 | 168.7305 | 184.1671 | 181.3841
564.6135 | 449.4514 | 169.4664 | 183.9072 | 181.8612
565.5979 | 447.8039 | 169.5798 | 183.8415 | 182.2463
566.5979 | 447.8092 | 169.7414 | 183.9707 | 182.3514
567.5979 | 446.8641 | 170.7387 | 184.0697 | 181.9526
568.5979 | 446.0359 | 170.7201 | 184.1868 | 182.0216
569.5979 | 443.6464 | 171.3476 | 184.2493 | 181.4754
570.5979 | 440.4468 | 171.0594 | 184.5676 | 181.7038
571.5979 | 436.5544 | 171.5507 | 184.6667 | 181.4408
572.5979 | 432.0612 | 171.1606 | 185.1023 | 181.4669
573.5979 | 431.0518 | 171.0655 | 185.3694 | 181.9546
574.5979 | 433.787 | 171.7331 | 184.9677 | 182.2417
575.5979 | 433.2354 | 171.8682 | 184.9323 | 181.7926
576.5979 | 437.3838 | 172.3889 | 185.395 | 182.0826
577.5979 | 440.7647 | 172.8132 | 185.6703 | 181.9562
578.5979 | 442.6669 | 173.2177 | 185.8093 | 182.1676
579.5979 | 442.8128 | 172.6222 | 185.5237 | 182.4071
580.5979 | 449.7069 | 172.7445 | 185.3819 | 182.4887
581.5979 | 456.8196 | 172.7836 | 184.803 | 182.823
582.5979 | 464.0172 | 173.7399 | 185.5206 | 182.8507
583.5979 | 469.591 | 173.9467 | 186.1893 | 183.3411
584.5979 | 475.8058 | 174.3803 | 186.5634 | 183.7188
585.5979 | 474.2841 | 174.2533 | 186.2175 | 183.8724
586.5979 | 475.3097 | 174.3014 | 186.362 | 184.1123
587.5979 | 475.6248 | 173.8874 | 186.5056 | 184.6806
588.5979 | 474.2172 | 173.7697 | 186.395 | 184.697
589.5979 | 469.7147 | 174.2015 | 187.05 | 184.9622
590.5979 | 469.9571 | 174.526 | 187.5125 | 184.3947
591.5979 | 471.2816 | 174.8534 | 187.8084 | 184.9419
592.5979 | 473.068 | 174.6693 | 188.1669 | 185.1775
593.5979 | 473.6414 | 174.8023 | 188.4727 | 185.5429
594.5979 | 474.4787 | 175.3391 | 188.6211 | 186.647
595.5979 | 472.7315 | 175.4907 | 189.3618 | 187.3508
596.5979 | 493.52 | 175.3154 | 189.8092 | 187.9624
597.5979 | 492.7561 | 175.2222 | 189.8646 | 188.7071
598.5979 | 494.6888 | 175.0767 | 189.8112 | 188.3865
599.5979 | 497.9851 | 174.9542 | 189.6945 | 188.7
600.5979 | 508.0136 | 175.0589 | 189.7 | 188.5009
601.5979 | 509.8662 | 175.4275 | 189.2589 | 188.5167
602.5979 | 506.1942 | 175.3648 | 189.678 | 188.2933
603.5979 | 502.8872 | 175.2358 | 189.61 | 188.2876
604.5979 | 505.1203 | 175.322 | 189.3364 | 188.3064
605.5979 | 515.0509 | 175.2609 | 189.012 | 188.8635
606.5979 | 532.5218 | 176.3225 | 189.1195 | 189.1278
607.5979 | 532.9822 | 176.6958 | 189.0987 | 189.4988
608.5979 | 533.8088 | 176.5142 | 189.2755 | 190.2008
609.5979 | 529.0405 | 176.3322 | 189.3828 | 190.2924
610.5979 | 525.2996 | 176.1648 | 189.0435 | 190.7442
611.5979 | 522.591 | 176.4475 | 187.9859 | 190.9461
612.5979 | 513.9855 | 176.2139 | 188.1893 | 191.2788
613.5979 | 506.4518 | 176.8077 | 188.2689 | 191.2125
614.5979 | 502.5208 | 177.3305 | 188.4156 | 190.9496
615.5979 | 499.6822 | 177.1869 | 188.4836 | 191.1091
616.5979 | 497.1611 | 177.2727 | 188.3805 | 190.7371
617.5979 | 508.693 | 177.2111 | 188.263 | 190.653
618.5979 | 507.827 | 177.3972 | 188.3 | 190.4084
619.5979 | 508.9583 | 176.9628 | 188.6353 | 190.5397
620.5979 | 515.1323 | 177.04 | 189.0495 | 190.4427
621.5979 | 520.0292 | 177.1494 | 189.1162 | 190.7362
622.5979 | 526.3475 | 177.5145 | 189.3037 | 191.1686
623.5979 | 539.2792 | 177.9742 | 189.5297 | 191.0932
624.5979 | 539.7284 | 178.4566 | 190.331 | 191.4694
625.5979 | 535.9656 | 178.3336 | 190.109 | 191.7903
626.5979 | 528.3504 | 178.2907 | 190.4944 | 192.0968
627.5979 | 530.176 | 177.9812 | 190.3815 | 192.1746
628.5979 | 534.224 | 177.8361 | 191.7525 | 191.948
629.5979 | 546.1874 | 177.8871 | 191.6202 | 191.6479
630.5979 | 552.4765 | 178.6243 | 192.0998 | 191.2879
631.5979 | 563.1564 | 177.9971 | 192.1259 | 191.6209
632.5979 | 583.2531 | 178.2536 | 192.2068 | 192.1313
633.5979 | 584.7768 | 178.6312 | 191.7558 | 191.6443
634.5979 | 612.6868 | 178.5864 | 191.4003 | 192.139
635.5979 | 601.0772 | 178.6041 | 191.1424 | 192.741
636.5979 | 590.6631 | 179.13 | 191.1718 | 193.1498
637.5979 | 577.8716 | 178.4459 | 190.7141 | 192.9529
638.5979 | 574.2887 | 178.4132 | 190.946 | 192.9469
639.5979 | 561.5219 | 178.6821 | 190.8475 | 192.9186
640.5979 | 546.7064 | 178.4888 | 190.3399 | 192.8448
641.5979 | 539.6448 | 178.598 | 190.0878 | 192.4105
642.5979 | 534.8118 | 178.7355 | 190.012 | 193.0243
643.5979 | 527.5491 | 178.6368 | 189.8653 | 193.1069
644.5979 | 538.3331 | 178.3082 | 189.7581 | 192.7264
645.5979 | 540.8268 | 179.0976 | 189.6895 | 192.0475
646.5979 | 546.1457 | 179.4752 | 189.9426 | 191.9376
647.5979 | 540.8718 | 179.7032 | 189.8759 | 191.9546
648.5979 | 539.3356 | 179.5348 | 190.2469 | 191.9576
649.5979 | 534.325 | 179.9205 | 189.7675 | 191.5299
650.5979 | 527.7584 | 179.4763 | 189.6411 | 191.3572
651.5979 | 528.5106 | 179.8845 | 189.6631 | 190.9108
652.5979 | 520.9082 | 179.8911 | 189.8073 | 190.8266
653.5979 | 514.4786 | 179.9898 | 189.9479 | 190.7638
654.6135 | 510.2106 | 180.475 | 189.4349 | 190.7088
655.5979 | 504.1687 | 180.3043 | 189.0825 | 191.4591
656.5979 | 501.587 | 180.2007 | 189.3948 | 191.4847
657.5979 | 498.899 | 180.8569 | 189.9215 | 191.3486
658.5979 | 496.0439 | 181.7582 | 190.0259 | 191.0651
659.5979 | 490.9089 | 181.5101 | 189.8009 | 190.7746
660.5979 | 487.5155 | 181.7923 | 190.1038 | 190.4937
661.5979 | 486.5258 | 181.8403 | 189.8559 | 190.156
662.5979 | 484.2403 | 182.176 | 189.8026 | 189.8026
663.5979 | 494.7547 | 181.9261 | 189.7721 | 190.3965
664.5979 | 487.0743 | 182.4624 | 190.0778 | 190.706
665.5979 | 483.1558 | 182.2787 | 190.0128 | 190.5822
666.5979 | 482.4056 | 182.019 | 190.8042 | 190.8019
667.5979 | 485.5965 | 182.4649 | 191.1492 | 190.9957
668.5979 | 484.6669 | 182.6593 | 191.7835 | 191.2095
669.5979 | 484.7157 | 182.7013 | 192.2696 | 190.9703
670.5979 | 484.0763 | 182.8033 | 192.3924 | 190.3646
671.5979 | 483.6384 | 183.1458 | 192.6164 | 190.1507
672.5979 | 482.7248 | 183.0559 | 192.6279 | 190.4484
673.5979 | 480.7797 | 182.5987 | 192.4588 | 190.1436
674.5979 | 483.1361 | 182.7651 | 192.3374 | 189.8656
675.5979 | 483.0853 | 182.4626 | 192.5537 | 189.4294
676.5979 | 480.8068 | 182.0795 | 192.6219 | 189.0771
677.5979 | 483.2704 | 182.1223 | 192.4549 | 188.7656
678.5979 | 482.897 | 181.7317 | 192.4774 | 189.3006
679.5979 | 486.7584 | 181.6019 | 192.4528 | 189.5129
680.5979 | 499.8092 | 181.3226 | 192.5135 | 189.3165
681.5979 | 507.4847 | 181.1813 | 192.357 | 188.9494
682.5979 | 504.4846 | 181.1261 | 192.4164 | 188.6275
683.5979 | 499.9717 | 180.9033 | 192.314 | 188.7686
684.5979 | 504.4232 | 180.8039 | 192.1901 | 189.0526
685.5979 | 500.0065 | 180.7933 | 192.2553 | 188.9422
686.5979 | 494.7605 | 181.1446 | 193.059 | 189.7232
687.5979 | 492.252 | 181.5631 | 193.4626 | 190.2666
688.5979 | 495.1259 | 181.179 | 193.4641 | 190.4272
689.5979 | 493.2649 | 181.9404 | 193.7465 | 190.4001
690.5979 | 490.597 | 181.9701 | 193.8607 | 190.9571
691.5979 | 486.3217 | 181.5583 | 193.5883 | 191.568
692.5979 | 481.9486 | 181.1212 | 194.3222 | 192.0109
693.5979 | 480.7801 | 181.1489 | 194.1779 | 191.8083
694.5979 | 479.3941 | 181.0363 | 194.1218 | 191.5221
695.5979 | 475.7648 | 180.8828 | 193.7764 | 191.2602
696.5979 | 478.6764 | 180.4967 | 193.7162 | 190.9255
697.5979 | 477.6753 | 181.056 | 193.9662 | 190.9266
698.5979 | 478.9041 | 181.1795 | 194.3557 | 191.4075
699.5979 | 480.6878 | 181.0107 | 195.0266 | 191.6003
700.5979 | 478.1018 | 180.536 | 194.8584 | 192.0676
701.5979 | 477.9546 | 180.48 | 194.6072 | 191.9963
702.5979 | 481.2618 | 180.6454 | 194.1263 | 192.0777
703.5979 | 496.2457 | 180.6088 | 193.5317 | 191.6735
704.5979 | 493.1021 | 180.3004 | 194.4835 | 191.3208
705.5979 | 494.4665 | 180.6159 | 194.4611 | 192.0095
706.5979 | 493.3379 | 180.7916 | 194.5748 | 191.971
707.5979 | 496.6979 | 181.0568 | 194.8328 | 191.6971
708.5979 | 523.3207 | 181.3929 | 194.4417 | 191.4826
709.5979 | 529.3748 | 181.1435 | 194.413 | 191.6874
710.5979 | 559.1579 | 180.9605 | 194.6048 | 191.826
711.5979 | 554.0574 | 181.2986 | 194.6565 | 192.1611
712.5979 | 548.952 | 181.3588 | 195.0809 | 192.9729
713.5979 | 537.6353 | 180.8563 | 195.1209 | 193.4193
714.5979 | 529.9857 | 180.8829 | 195.1064 | 194.5213
715.5979 | 523.6943 | 180.4821 | 195.689 | 194.2357
716.5979 | 515.7734 | 180.0696 | 196.0893 | 194.9925
717.5979 | 513.3637 | 180.1297 | 196.036 | 195.1574
718.5979 | 511.4216 | 179.5488 | 196.0621 | 194.6866
719.5979 | 509.0876 | 179.3936 | 196.1591 | 194.2054
720.5979 | 510.3351 | 180.3353 | 196.42 | 194.5003
721.5979 | 505.9818 | 180.7031 | 196.4873 | 194.5236
722.5979 | 505.6411 | 180.9764 | 195.6262 | 194.8098
723.5979 | 502.0191 | 181.2716 | 195.6899 | 195.0234
724.5979 | 497.5523 | 181.0155 | 196.1043 | 195.0365
725.5979 | 494.3778 | 180.8907 | 195.7232 | 194.8713
726.5979 | 509.5535 | 180.7044 | 195.8935 | 194.6022
727.5979 | 512.5661 | 181.426 | 195.65 | 195.0367
728.5979 | 518.5387 | 180.7716 | 195.5965 | 194.8131
729.5979 | 508.9318 | 180.8429 | 195.3557 | 194.4343
730.5979 | 500.7088 | 181.0597 | 195.405 | 194.2962
731.5979 | 495.8399 | 180.6989 | 194.8652 | 194.4535
732.5979 | 496.3166 | 181.1356 | 194.8509 | 194.7134
733.5979 | 526.0269 | 181.8272 | 194.8334 | 194.9221
734.5979 | 523.4691 | 182.4709 | 195.441 | 195.8528
735.5979 | 516.2217 | 182.97 | 195.4132 | 195.9233
736.5979 | 514.3635 | 182.9957 | 195.7998 | 195.6018
737.5979 | 515.0012 | 183.0155 | 196.3965 | 195.6607
738.5979 | 506.8198 | 183.3995 | 196.4502 | 195.6787
739.5979 | 495.9017 | 183.6906 | 197.2311 | 195.7428
740.5979 | 486.1555 | 183.8753 | 197.634 | 196.0761
741.5979 | 478.2744 | 183.4467 | 197.6074 | 196.1335
742.5979 | 471.0291 | 183.3458 | 197.6038 | 195.8755
743.5979 | 464.3871 | 183.4223 | 197.6096 | 195.7654
744.5979 | 460.3214 | 183.9773 | 197.586 | 195.7107
745.5979 | 456.0632 | 183.8904 | 197.534 | 195.4997
746.5979 | 451.7516 | 183.9777 | 197.2521 | 194.8995
747.5979 | 447.4959 | 184.2372 | 197.5061 | 194.4896
748.5979 | 444.7387 | 184.6011 | 197.7982 | 195.2272
749.5979 | 444.2768 | 184.7722 | 197.9773 | 195.106
750.6135 | 442.9256 | 185.1369 | 198.9061 | 195.2611
751.5979 | 442.0443 | 185.1433 | 198.8436 | 195.0537
752.6135 | 440.1283 | 185.5024 | 199.0695 | 195.1483
753.5979 | 442.0819 | 186.1879 | 199.1633 | 195.5434
754.6135 | 442.9276 | 186.7776 | 199.2582 | 196.1365
755.5979 | 441.3352 | 187.1184 | 198.6974 | 196.4735
756.6135 | 444.7608 | 186.9901 | 198.889 | 196.475
757.5979 | 448.0028 | 187.6496 | 199.3071 | 196.1129
758.5979 | 449.395 | 187.4578 | 198.501 | 196.0092
759.5979 | 449.052 | 187.4046 | 198.449 | 196.6138
760.5979 | 448.9947 | 187.1186 | 198.335 | 196.8359
761.5979 | 444.1353 | 186.8347 | 198.2967 | 196.7014
762.5979 | 442.2394 | 186.8716 | 197.9406 | 196.8562
763.5979 | 439.5099 | 187.6725 | 198.0247 | 196.4135
764.5979 | 441.1581 | 187.9823 | 197.9427 | 196.8175
765.5979 | 444.5138 | 188.3796 | 198.4034 | 197.0489
766.5979 | 445.7624 | 188.2085 | 198.6292 | 196.6094
767.5979 | 443.876 | 188.9136 | 198.9526 | 196.9798
768.5979 | 444.2023 | 188.2943 | 198.275 | 196.5883
769.5979 | 443.0616 | 188.1554 | 198.4007 | 197.0817
770.5979 | 442.1255 | 188.5395 | 198.1244 | 196.6233
771.5979 | 440.6324 | 188.5843 | 198.1946 | 196.2975
772.5979 | 438.1534 | 188.4722 | 198.2701 | 195.9459
773.5979 | 434.1752 | 189.1737 | 198.8026 | 196.4678
774.5979 | 432.4121 | 188.8638 | 199.0488 | 198.0811
775.5979 | 436.4261 | 188.9053 | 199.0342 | 197.7495
776.6135 | 440.227 | 188.4733 | 199.0292 | 197.7738
777.5979 | 441.5554 | 188.3593 | 200.2106 | 197.7515
778.5979 | 440.4241 | 188.5335 | 200.3574 | 197.4984
779.5979 | 437.4973 | 188.8445 | 200.3679 | 197.9245
780.5979 | 432.572 | 188.4544 | 200.4219 | 198.3038
781.6292 | 431.4923 | 188.1831 | 200.5788 | 198.4749
782.5979 | 434.3951 | 188.9518 | 200.5163 | 198.2153
783.5979 | 436.5662 | 188.618 | 200.3243 | 198.0108
784.5979 | 440.1996 | 188.1954 | 200.2132 | 197.8646
785.5979 | 439.4627 | 188.0002 | 201.6289 | 198.8385
786.5979 | 438.9026 | 187.2701 | 201.3883 | 198.4711
787.5979 | 437.0855 | 186.8062 | 201.4258 | 198.1272
788.5979 | 433.995 | 187.1623 | 201.3002 | 197.7284
789.5979 | 432.6507 | 187.2275 | 201.2183 | 197.5989
790.5979 | 430.723 | 187.8148 | 201.2082 | 197.8944
791.5979 | 428.3199 | 187.2402 | 201.0843 | 198.278
792.5979 | 425.5135 | 186.4554 | 200.9777 | 198.1518
793.5979 | 425.3231 | 185.7355 | 200.5066 | 198.1205
794.5979 | 421.4446 | 185.1762 | 200.1348 | 197.9545
795.5979 | 420.9388 | 186.0663 | 199.9952 | 198.3797
796.5979 | 417.1675 | 186.2328 | 199.8981 | 198.5657
797.5979 | 414.3604 | 186.0804 | 200.0888 | 198.4065
798.5979 | 411.7306 | 186.3239 | 200.3672 | 198.4733
799.5979 | 411.3801 | 186.4528 | 200.0884 | 198.0075
800.5979 | 409.5923 | 187.0021 | 200.2166 | 197.7582
801.5979 | 408.6745 | 186.7298 | 200.0215 | 197.8311
802.5979 | 410.5854 | 187.2431 | 200.0603 | 197.8382
803.5979 | 413.9959 | 186.9674 | 200.143 | 198.7673
804.5979 | 415.6647 | 187.2399 | 200.3864 | 198.5488
805.5979 | 418.065 | 187.1942 | 200.8306 | 198.8094
806.5979 | 418.2255 | 187.1108 | 200.7294 | 200.5889
807.5979 | 416.8933 | 187.089 | 200.711 | 200.7226
808.5979 | 417.6918 | 186.9384 | 200.5708 | 201.2823
809.5979 | 416.1101 | 187.0031 | 200.454 | 201.8593
810.5979 | 414.4573 | 186.5892 | 200.4447 | 201.549
811.5979 | 413.2964 | 187.4294 | 200.6598 | 201.6357
812.5979 | 413.1867 | 186.994 | 200.7712 | 201.4908
813.5979 | 417.1754 | 186.3424 | 200.8045 | 201.2592
814.5979 | 423.3178 | 186.375 | 201.7033 | 201.3193
815.5979 | 423.8396 | 185.8388 | 201.6581 | 201.4169
816.5979 | 426.4692 | 185.7121 | 201.4657 | 201.4872
817.5979 | 424.9161 | 185.7418 | 201.3657 | 201.0777
818.5979 | 423.6483 | 185.8043 | 201.145 | 201.3473
819.5979 | 420.7944 | 185.0435 | 200.8751 | 200.9219
820.5979 | 419.1496 | 184.351 | 200.9058 | 200.7868
821.5979 | 416.9444 | 184.3478 | 200.6341 | 200.5583
822.5979 | 415.4614 | 183.9382 | 200.4739 | 200.1805
823.5979 | 419.7146 | 183.9582 | 200.2922 | 200.018
824.5979 | 420.4772 | 183.4581 | 200.7614 | 199.4042
825.5979 | 419.6174 | 182.6763 | 200.9082 | 200.134
826.5979 | 422.1016 | 182.8132 | 200.7294 | 200.531
827.5979 | 425.2199 | 182.6417 | 201.1711 | 201.0821
828.5979 | 425.3314 | 182.2359 | 201.2458 | 200.8533
829.5979 | 422.8174 | 182.3046 | 201.1929 | 200.5304
830.5979 | 420.736 | 182.414 | 200.9494 | 200.571
831.5979 | 418.0036 | 182.9784 | 200.9283 | 200.3856
832.5979 | 418.9075 | 183.1021 | 201.197 | 200.6611
833.5979 | 416.3163 | 182.9776 | 201.5228 | 200.6046
834.5979 | 411.1306 | 183.8728 | 201.4316 | 200.933
835.5979 | 408.004 | 183.5968 | 201.5724 | 200.3389
836.5979 | 405.7474 | 184.222 | 201.5227 | 200.1614
837.5979 | 404.537 | 184.5966 | 201.5953 | 200.2138
838.5979 | 403.9608 | 185.1011 | 202.055 | 200.1429
839.5979 | 402.5813 | 184.9957 | 202.1128 | 200.3505
840.5979 | 399.6898 | 185.1659 | 202.3266 | 200.1624
841.5979 | 399.6499 | 185.693 | 202.5055 | 200.5705
842.5979 | 398.9905 | 185.7778 | 202.3876 | 200.7097
843.5979 | 396.9528 | 186.0772 | 202.2659 | 200.7048
844.5979 | 395.6774 | 185.9671 | 201.9904 | 200.8245
845.5979 | 394.601 | 185.9075 | 201.893 | 200.6366
846.5979 | 393.5852 | 186.5539 | 201.6548 | 200.1865
847.5979 | 394.7061 | 186.7102 | 201.701 | 200.0083
848.5979 | 392.1356 | 186.0262 | 201.7699 | 200.2487
849.5979 | 390.6905 | 185.6663 | 201.9104 | 200.9771
850.5979 | 388.9243 | 186.3274 | 202.2129 | 200.8806
851.5979 | 392.4154 | 186.8996 | 202.2393 | 201.497
852.5979 | 391.0259 | 187.1798 | 202.3606 | 201.6171
853.5979 | 388.6869 | 187.2895 | 202.1675 | 201.4542
854.5979 | 387.0428 | 187.9024 | 201.9199 | 200.628
855.5979 | 387.2961 | 188.0947 | 201.8615 | 200.1522
856.5979 | 386.7157 | 187.6685 | 201.9618 | 200.2693
857.5979 | 379.9545 | 187.7227 | 202.2011 | 199.8959
858.5979 | 380.1445 | 187.8277 | 202.2105 | 200.0798
859.5979 | 380.1129 | 187.5322 | 202.2316 | 200.0647
860.5979 | 379.6604 | 188.223 | 202.0986 | 199.8633
861.5979 | 380.0001 | 188.363 | 202.163 | 199.1866
862.5979 | 383.3995 | 188.1104 | 202.0352 | 198.792
863.5979 | 381.9222 | 187.374 | 202.3918 | 199.2333
864.5979 | 381.1277 | 187.7617 | 202.2885 | 199.1127
865.5979 | 382.0208 | 188.3002 | 202.0696 | 199.4942
866.5979 | 380.4379 | 188.3275 | 201.9064 | 199.8239
867.5979 | 381.8874 | 188.1511 | 201.9738 | 199.9987
868.5979 | 384.0371 | 188.3744 | 202.3882 | 199.969
869.5979 | 383.9331 | 188.4398 | 202.3839 | 200.3945
870.5979 | 385.2543 | 188.1283 | 202.1112 | 200.1407
871.5979 | 386.9724 | 187.8431 | 202.2186 | 200.8859
872.5979 | 390.7477 | 187.9207 | 202.1401 | 200.6768
873.5979 | 388.8493 | 187.7892 | 201.9127 | 200.5067
874.5979 | 386.7873 | 188.0904 | 202.4075 | 200.1255
875.5979 | 386.2982 | 187.3061 | 202.2711 | 199.7696
876.5979 | 385.4688 | 187.1083 | 202.3207 | 199.6544
877.5979 | 385.568 | 187.1932 | 202.9364 | 199.7202
878.5979 | 386.999 | 187.2308 | 202.9853 | 200.2826
879.5979 | 388.1272 | 187.7692 | 203.0663 | 200.4746
880.5979 | 390.4191 | 188.436 | 203.4795 | 200.5078
881.5979 | 388.8129 | 188.5401 | 203.6131 | 200.9607
882.5979 | 388.0889 | 188.7493 | 203.7702 | 200.8666
883.5979 | 388.4834 | 189.4364 | 203.2889 | 201.222
884.5979 | 391.7602 | 189.4969 | 203.2126 | 200.9517
885.5979 | 390.8576 | 189.3923 | 203.3981 | 201.2788
886.5979 | 390.2159 | 189.8987 | 203.6252 | 201.3372
887.5979 | 393.8667 | 189.8375 | 203.5731 | 201.4434
888.5979 | 391.6951 | 189.669 | 203.6996 | 201.4823
889.5979 | 391.7918 | 189.376 | 203.4822 | 201.9502
890.5979 | 389.8839 | 189.3938 | 203.3508 | 201.5538
891.5979 | 390.3326 | 189.5263 | 203.2069 | 201.616
892.5979 | 391.2079 | 189.573 | 203.4143 | 201.4977
893.5979 | 391.7354 | 190.1521 | 203.3342 | 201.2694
894.5979 | 392.8469 | 190.3773 | 203.6354 | 201.5794
895.5979 | 392.885 | 190.2443 | 203.908 | 201.853
896.5979 | 392.4626 | 190.3961 | 203.9528 | 201.9588
897.5979 | 392.9866 | 190.472 | 203.8464 | 202.5537
898.5979 | 391.7563 | 190.1135 | 203.6333 | 202.8866
899.5979 | 397.8643 | 189.6556 | 203.676 | 202.6907
900.5979 | 399.3891 | 189.3284 | 203.7631 | 202.8599
901.5979 | 397.9532 | 189.1886 | 204.0153 | 202.5387
902.5979 | 397.2492 | 189.8359 | 204.2293 | 202.5314
903.5979 | 399.9532 | 189.6944 | 204.1898 | 202.3631
904.5979 | 397.4974 | 190.2329 | 204.2335 | 202.1956
905.5979 | 400.1613 | 190.6737 | 204.1592 | 202.2746
906.5979 | 402.3378 | 190.4677 | 204.0272 | 202.1069
907.5979 | 401.4502 | 189.6228 | 203.9487 | 201.9458
908.5979 | 402.7582 | 189.71 | 203.7101 | 201.559
909.5979 | 410.539 | 189.7948 | 203.6694 | 201.4899
910.5979 | 410.3355 | 189.3636 | 203.6387 | 201.4139
911.5979 | 409.1386 | 188.9016 | 203.5043 | 201.2899
912.5979 | 410.3778 | 189.0479 | 203.6662 | 201.115
913.5979 | 413.902 | 189.6695 | 204.624 | 201.3078
914.5979 | 418.7713 | 190.5051 | 204.343 | 201.2108
915.5979 | 428.8677 | 190.7633 | 204.2576 | 202.5396
916.5979 | 427.9025 | 190.6394 | 204.6 | 203.0847
917.5979 | 428.0934 | 191.0983 | 204.7058 | 203.926
918.5979 | 431.4948 | 191.3343 | 205.1927 | 204.448
919.5979 | 431.7562 | 191.037 | 205.0821 | 205.5743
920.5979 | 431.3278 | 190.9215 | 206.0649 | 206.1659
921.5979 | 431.2401 | 191.3662 | 206.0378 | 206.5148
922.5979 | 436.3067 | 191.0429 | 206.4211 | 206.6904
923.5979 | 444.7062 | 191.0041 | 206.808 | 206.6764
924.5979 | 450.2256 | 190.3823 | 207.0202 | 206.4999
925.5979 | 451.5971 | 190.5377 | 207.397 | 206.3557
926.5979 | 450.7879 | 190.1662 | 207.1091 | 205.9009
927.5979 | 449.7269 | 190.7801 | 208.2268 | 205.8361
928.5979 | 449.6489 | 191.3215 | 208.3957 | 205.8722
929.5979 | 449.3593 | 191.8638 | 208.6881 | 205.9455
930.5979 | 446.8056 | 191.9584 | 209.6646 | 206.7763
931.5979 | 453.2134 | 191.9352 | 209.9775 | 206.3107
932.5979 | 451.6667 | 192.883 | 210.0718 | 206.5017
933.5979 | 454.2655 | 193.9558 | 210.0177 | 207.158
934.5979 | 452.8805 | 194.4741 | 210.0457 | 207.6902
935.5979 | 457.2377 | 195.0732 | 210.7704 | 207.8827
936.5979 | 453.8817 | 196.526 | 211.699 | 208.1239
937.5979 | 461.0757 | 196.9078 | 211.9537 | 208.7641
938.5979 | 461.3618 | 197.7993 | 211.9563 | 209.1844
939.5979 | 458.5592 | 198.3074 | 212.2889 | 209.4506
940.5979 | 458.3674 | 198.866 | 212.5927 | 209.6315
941.5979 | 459.5966 | 199.0315 | 213.3082 | 210.5372
942.5979 | 465.2819 | 199.2117 | 213.6428 | 210.6399
943.5979 | 466.029 | 199.6974 | 213.7322 | 210.8817
944.5979 | 465.9091 | 200.3676 | 213.9999 | 211.1923
945.5979 | 464.4135 | 200.4531 | 214.5168 | 211.863
946.5979 | 461.1157 | 199.9555 | 214.5509 | 211.8484
947.5979 | 462.8633 | 199.6566 | 214.9517 | 212.1842
948.5979 | 462.1435 | 199.1388 | 214.787 | 212.2529
949.5979 | 467.4352 | 199.1998 | 215.4332 | 212.0556
950.5979 | 466.2599 | 199.8982 | 215.2449 | 212.3852
951.5979 | 469.9795 | 199.526 | 215.2066 | 212.2896
952.5979 | 470.0224 | 199.7394 | 215.0929 | 211.8845
953.5979 | 467.9049 | 200.3772 | 215.2953 | 212.4559
954.5979 | 468.8483 | 200.0591 | 215.1164 | 212.5406
955.5979 | 468.9274 | 200.5677 | 216.0988 | 212.8168
956.5979 | 470.6903 | 201.0893 | 216.4507 | 213.3432
957.5979 | 470.4545 | 201.622 | 216.3989 | 213.503
958.5979 | 472.1744 | 202.1892 | 216.6623 | 213.5879
959.5979 | 470.0793 | 202.4222 | 216.6962 | 213.6302
960.5979 | 466.5583 | 202.4391 | 217.0035 | 214.629
961.5979 | 464.0201 | 202.2531 | 217.3286 | 214.679
962.5979 | 476.3855 | 202.1081 | 217.4257 | 215.2653
963.5979 | 475.6723 | 202.1914 | 218.082 | 215.7714
964.5979 | 476.432 | 202.0157 | 218.7205 | 215.8933
965.5979 | 479.2051 | 202.3395 | 218.4055 | 215.7388
966.5979 | 480.382 | 202.868 | 218.4002 | 215.3428
967.5979 | 477.8915 | 203.5764 | 219.1054 | 215.2717
968.5979 | 475.9019 | 204.3518 | 219.7772 | 215.9871
969.5979 | 476.3815 | 204.7714 | 220.058 | 216.3255
970.5979 | 474.5426 | 205.4358 | 219.9632 | 217.4475
971.5979 | 488.8055 | 206.0183 | 220.9516 | 218.139
972.5979 | 492.4562 | 205.849 | 220.7643 | 218.4881
973.5979 | 492.5846 | 206.0245 | 220.7069 | 218.3086
974.5979 | 492.141 | 206.2281 | 221.5027 | 218.2023
975.5979 | 489.1355 | 205.9746 | 221.0931 | 218.9781
976.5979 | 488.0107 | 206.1142 | 220.9922 | 219.1325
977.5979 | 494.5175 | 206.9524 | 221.2628 | 219.1645
978.5979 | 500.8556 | 207.169 | 221.119 | 218.7806
979.5979 | 503.9899 | 207.657 | 220.6733 | 219.2027
980.5979 | 512.7092 | 208.4558 | 221.219 | 219.7206
981.5979 | 513.8218 | 208.2495 | 221.3706 | 219.8555
982.5979 | 515.3537 | 207.7126 | 221.6155 | 220.1046
983.5979 | 516.8855 | 207.7112 | 221.4851 | 219.9489
984.5979 | 520.7015 | 207.9719 | 221.1875 | 219.7987
985.5979 | 522.2237 | 207.6005 | 221.4408 | 220.3297
986.6135 | 523.0386 | 207.7935 | 221.7502 | 220.429
987.5979 | 533.6302 | 208.119 | 222.6113 | 220.3863
988.5979 | 527.62 | 207.8955 | 222.5959 | 220.6747
989.5979 | 526.6735 | 208.572 | 222.6648 | 220.7488
990.5979 | 526.618 | 209.4414 | 222.9545 | 220.8217
991.5979 | 527.7251 | 209.5453 | 221.8098 | 221.1569
992.5979 | 532.2581 | 209.9871 | 222.1445 | 220.7689
993.5979 | 543.0728 | 210.0591 | 222.1613 | 220.9731
994.5979 | 541.3123 | 209.5648 | 222.8709 | 220.9179
995.5979 | 541.9353 | 209.7046 | 222.5901 | 221.0725
996.5979 | 537.4012 | 209.6473 | 223.0581 | 221.2956
997.5979 | 545.32 | 209.5804 | 223.4418 | 220.9264
998.5979 | 549.8473 | 210.0428 | 223.5229 | 221.1727
999.5979 | 545.1382 | 210.2169 | 223.0285 | 221.674
1000.5979 | 543.6297 | 210.826 | 222.9442 | 221.8626
1001.5979 | 540.9295 | 211.0909 | 223.3056 | 221.6147
1002.5979 | 551.032 | 211.4175 | 223.5354 | 222.0625
1003.5979 | 546.7183 | 212.6024 | 222.8833 | 223.3413
1004.5979 | 547.5668 | 212.6056 | 223.8454 | 223.483
1005.5979 | 546.0061 | 211.808 | 223.8051 | 223.0818
1006.5979 | 549.419 | 211.4782 | 223.7874 | 222.6642
1007.5979 | 547.2336 | 210.7505 | 223.3558 | 222.5158
1008.5979 | 541.9058 | 210.3582 | 222.8597 | 222.5411
1009.5979 | 541.564 | 210.7838 | 223.1062 | 222.3725
1010.5979 | 540.6441 | 211.3817 | 223.254 | 222.1639
1011.5979 | 542.1099 | 211.3338 | 223.2292 | 222.016
1012.5979 | 537.0882 | 211.0751 | 222.9791 | 221.6331
1013.5979 | 533.7157 | 211.5897 | 222.8752 | 222.0912
1014.5979 | 531.6374 | 211.6941 | 222.9213 | 221.881
1015.5979 | 529.578 | 211.7074 | 222.4638 | 222.368
1016.5979 | 529.4322 | 211.3929 | 222.3552 | 222.2543
1017.5979 | 528.7054 | 211.2929 | 222.1113 | 222.1247
1018.5979 | 523.4472 | 212.2611 | 222.4302 | 222.0293
1019.5979 | 523.8967 | 211.3642 | 222.2981 | 222.3903
1020.5979 | 523.1874 | 211.0493 | 222.8254 | 222.6517
1021.5979 | 529.5775 | 210.7293 | 223.2313 | 222.8166
1022.5979 | 532.2929 | 210.8268 | 223.3323 | 222.9731
1023.5979 | 534.9363 | 211.7944 | 223.741 | 223.4032
1024.5979 | 532.5173 | 211.8387 | 224.1558 | 223.5645
1025.5979 | 528.6751 | 211.4657 | 224.5796 | 223.7813
1026.5979 | 531.2863 | 211.8547 | 224.5445 | 223.5203
1027.5979 | 532.1417 | 212.6589 | 224.769 | 223.0864
1028.5979 | 530.8053 | 212.7155 | 225.4018 | 222.9348
1029.5979 | 526.7042 | 212.5891 | 225.2852 | 222.6198
1030.5979 | 526.0177 | 212.8944 | 225.1078 | 222.3254
1031.5979 | 526.8743 | 212.8232 | 224.7946 | 221.6805
1032.5979 | 526.9277 | 212.5202 | 224.5796 | 221.333
1033.5979 | 536.0546 | 212.4551 | 224.3946 | 221.3091
1034.5979 | 536.2166 | 212.1212 | 224.5114 | 220.5391
1035.5979 | 537.2178 | 212.2248 | 225.3461 | 220.34
1036.5979 | 533.2771 | 212.7926 | 225.7577 | 220.7142
1037.5979 | 531.143 | 213.741 | 226.5005 | 221.6606
1038.5979 | 530.2936 | 213.9906 | 227.3198 | 222.0251
1039.5979 | 538.1007 | 214.4871 | 227.6061 | 222.2776
1040.5979 | 541.4406 | 214.3071 | 227.1592 | 222.3803
1041.5979 | 544.0335 | 214.6559 | 226.8922 | 222.0311
1042.5979 | 546.2473 | 215.0524 | 227.2338 | 221.8393
1043.5979 | 556.4086 | 214.6902 | 226.9128 | 222.3525
1044.5979 | 559.6961 | 214.6975 | 226.5115 | 222.6505
1045.5979 | 559.0556 | 214.806 | 226.5981 | 223.0489
1046.5979 | 557.2627 | 215.0413 | 226.651 | 222.7457
1047.5979 | 565.1182 | 214.6983 | 227.3779 | 222.5909
1048.5979 | 567.9188 | 215.2532 | 227.595 | 222.9033
1049.5979 | 573.6722 | 214.7978 | 228.1368 | 223.2676
1050.5979 | 576.3727 | 214.3024 | 227.9641 | 223.5043
1051.5979 | 577.1369 | 213.5802 | 228.1403 | 223.9444
1052.5979 | 582.433 | 213.1779 | 227.831 | 223.7177
1053.5979 | 584.3317 | 213.7342 | 227.7732 | 223.8011
1054.5979 | 589.5129 | 213.3893 | 227.6034 | 223.9503
1055.5979 | 586.9441 | 213.827 | 227.9201 | 224.2817
1056.5979 | 590.4555 | 213.3641 | 227.8662 | 223.9962
1057.5979 | 599.7924 | 213.0748 | 227.5206 | 224.1232
1058.5979 | 603.6784 | 213.3564 | 228.257 | 224.5854
1059.5979 | 607.6555 | 212.6559 | 227.8992 | 224.6656
1060.5979 | 608.7876 | 212.3258 | 227.5141 | 224.6891
1061.5979 | 611.0764 | 212.9072 | 227.5864 | 225.0678
1062.5979 | 615.266 | 213.418 | 227.7152 | 225.667
1063.5979 | 615.473 | 215.1337 | 228.0449 | 224.9686
1064.5979 | 615.1154 | 215.8468 | 228.8479 | 225.398
1065.5979 | 611.4314 | 215.8026 | 228.8699 | 225.868
1066.5979 | 609.1342 | 216.2183 | 229.1873 | 227.0702
1067.5979 | 610.5253 | 216.6051 | 228.888 | 227.4844
1068.5979 | 613.9044 | 216.367 | 229.0223 | 227.7301
1069.5979 | 615.2546 | 216.394 | 229.2887 | 229.1674
1070.5979 | 618.6357 | 216.2284 | 229.2191 | 229.0472
1071.5979 | 620.0664 | 216.4679 | 229.9875 | 229.5175
1072.5979 | 622.6059 | 215.8844 | 229.5925 | 229.6618
1073.5979 | 625.4657 | 216.0034 | 229.7959 | 229.0569
1074.5979 | 622.9654 | 216.0338 | 229.8715 | 229.3273
1075.5979 | 620.243 | 215.8617 | 229.7631 | 229.4561
1076.5979 | 620.5058 | 215.9189 | 229.8271 | 229.5176
1077.5979 | 620.5958 | 216.2073 | 230.0175 | 229.1708
1078.5979 | 624.4431 | 216.3127 | 229.3829 | 228.4279
1079.5979 | 623.278 | 216.2866 | 229.673 | 228.5711
1080.5979 | 621.1309 | 216.2371 | 229.6688 | 228.5741
1081.5979 | 624.3454 | 216.6767 | 229.9702 | 228.1956
1082.5979 | 625.1691 | 216.7584 | 230.9326 | 228.832
1083.5979 | 626.6774 | 217.1578 | 231.0763 | 228.5686
1084.5979 | 628.3715 | 217.5005 | 231.1036 | 228.3065
1085.5979 | 631.0181 | 217.5199 | 230.8664 | 228.0209
1086.5979 | 632.8001 | 217.9657 | 231.213 | 227.7161
1087.5979 | 638.1954 | 217.3875 | 231.5145 | 227.1709
1088.5979 | 637.9264 | 216.8728 | 231.3684 | 226.8521
1089.5979 | 642.5385 | 216.8224 | 231.473 | 227.1156
1090.5979 | 641.1434 | 216.7771 | 231.5605 | 227.0663
1091.6135 | 641.8146 | 216.595 | 232.0211 | 227.534
1092.5979 | 639.8076 | 216.1203 | 231.8475 | 227.3547
1093.5979 | 639.6107 | 216.5291 | 231.9624 | 227.7569
1094.5979 | 638.8655 | 216.1355 | 231.9158 | 227.4553
1095.5979 | 638.9995 | 215.9872 | 231.944 | 227.6398
1096.5979 | 639.9484 | 216.1276 | 231.7808 | 227.3782
1097.5979 | 641.3936 | 216.8854 | 232.3964 | 227.3706
1098.5979 | 644.8578 | 216.9271 | 232.2049 | 227.9829
1099.5979 | 651.2594 | 217.3557 | 232.9669 | 228.2873
1100.5979 | 653.1605 | 218.9007 | 233.5752 | 228.3301
1101.5979 | 654.2931 | 218.2615 | 234.6881 | 229.2507
1102.5979 | 656.4741 | 218.0894 | 234.3824 | 229.2819
1103.5979 | 658.1614 | 218.1207 | 234.2077 | 229.0372
1104.5979 | 658.4123 | 218.633 | 233.605 | 228.9133
1105.5979 | 656.8004 | 219.307 | 234.4069 | 229.3632
1106.5979 | 654.5533 | 219.9839 | 233.3857 | 230.1835
1107.5979 | 658.1659 | 219.779 | 234.1344 | 230.1588
1108.5979 | 661.1924 | 220.1253 | 234.4826 | 230.1449
1109.5979 | 665.3953 | 220.5333 | 234.8649 | 230.642
1110.5979 | 667.3569 | 220.936 | 235.0029 | 230.9453
1111.5979 | 669.0425 | 221.2919 | 235.1321 | 230.6309
1112.5979 | 671.2135 | 221.6342 | 234.6298 | 230.9205
1113.5979 | 673.3992 | 221.6781 | 235.4755 | 231.2127
1114.5979 | 678.0635 | 221.8885 | 235.5603 | 231.5237
1115.5979 | 676.7169 | 222.8308 | 236.3359 | 231.5
1116.5979 | 682.4676 | 222.9987 | 237.0292 | 232.9477
1117.5979 | 685.2352 | 223.3913 | 237.114 | 234.059
1118.5979 | 687.5754 | 223.5768 | 236.3914 | 235.0421
1119.5979 | 684.8221 | 224.4843 | 236.5686 | 234.3785
1120.5979 | 685.5411 | 224.5594 | 237.0788 | 234.4219
1121.5979 | 693.3493 | 224.9 | 237.4166 | 234.5741
1122.5979 | 693.754 | 225.3114 | 237.2176 | 235.3574
1123.5979 | 695.4371 | 225.1877 | 237.3517 | 235.3078
1124.5979 | 699.7615 | 225.0291 | 237.4195 | 235.6039
1125.5979 | 701.1964 | 225.5167 | 237.897 | 235.7728
1126.6135 | 698.9982 | 225.302 | 237.9888 | 235.9039
1127.5979 | 699.0121 | 225.1481 | 238.2323 | 236.3959
1128.5979 | 697.3395 | 225.3757 | 238.2752 | 237.0067
1129.5979 | 698.4391 | 225.6586 | 238.6029 | 237.292
1130.5979 | 704.4767 | 226.0227 | 238.9145 | 237.7164
1131.5979 | 705.4885 | 226.5027 | 239.0642 | 237.8457
1132.5979 | 700.6704 | 226.4299 | 239.1727 | 237.9529
1133.5979 | 698.7176 | 227.1009 | 239.2303 | 237.9148
1134.5979 | 699.9388 | 227.0374 | 239.5632 | 237.574
1135.5979 | 695.3203 | 227.3341 | 239.6663 | 237.5164
1136.5979 | 690.2199 | 227.7201 | 239.5871 | 238.2766
1137.5979 | 684.9502 | 227.4692 | 239.2808 | 238.8892
1138.5979 | 683.5388 | 227.2685 | 239.0924 | 238.6561
1139.5979 | 677.0501 | 228.0956 | 240.0259 | 238.9988
1140.5979 | 676.5746 | 228.1659 | 239.6564 | 238.8707
1141.5979 | 678.9919 | 228.8355 | 239.9667 | 238.9384
1142.5979 | 690.5052 | 228.9262 | 240.8773 | 239.5305
1143.5979 | 688.6425 | 228.9503 | 242.0781 | 239.6572
1144.5979 | 690.3969 | 229.7524 | 243.2811 | 240.1291
1145.5979 | 688.813 | 229.8559 | 244.266 | 241.2944
1146.5979 | 690.2886 | 230.8195 | 244.7724 | 242.1566
1147.5979 | 690.5828 | 232.0618 | 246.4854 | 242.5878
1148.5979 | 686.3907 | 232.8275 | 246.7852 | 243.1741
1149.5979 | 685.5614 | 232.6573 | 247.6319 | 243.4419
1150.5979 | 691.9989 | 232.8714 | 248.2055 | 243.3281
1151.5979 | 689.388 | 232.5541 | 248.8319 | 243.3124
1152.5979 | 689.5328 | 232.7114 | 249.1311 | 243.5346
1153.5979 | 688.9424 | 231.9839 | 249.1018 | 243.5927
1154.5979 | 684.6083 | 232.1418 | 249.3281 | 244.3446
1155.5979 | 680.2011 | 232.1851 | 250.3111 | 245.0545
1156.5979 | 679.2733 | 231.5209 | 250.499 | 245.3396
1157.5979 | 679.6187 | 231.6635 | 250.8712 | 245.7358
1158.5979 | 674.6225 | 231.3596 | 251.2667 | 246.1332
1159.5979 | 669.0986 | 231.8119 | 251.8908 | 246.0975
1160.5979 | 671.3941 | 232.3097 | 251.8329 | 246.2752
1161.5979 | 672.253 | 232.0622 | 252.6068 | 246.1323
1162.5979 | 668.6306 | 232.3031 | 252.9204 | 246.5726
1163.5979 | 666.1359 | 233.1686 | 253.617 | 246.6561
1164.5979 | 663.1186 | 233.3509 | 254.3509 | 248.4975
1165.5979 | 665.6742 | 233.6871 | 255.2074 | 248.8094
1166.5979 | 660.8728 | 233.9982 | 256.1181 | 250.0324
1167.5979 | 658.031 | 234.2575 | 257.031 | 250.2918
1168.5979 | 661.8223 | 234.8565 | 256.8841 | 250.3425
1169.5979 | 660.868 | 235.5772 | 257.1332 | 250.4802
1170.5979 | 657.9332 | 235.9113 | 256.8699 | 250.5506
1171.5979 | 654.5259 | 236.2518 | 256.9012 | 251.3821
1172.5979 | 653.94 | 236.5734 | 257.3163 | 251.5064
1173.5979 | 654.9184 | 237.6729 | 257.1213 | 251.4394
1174.5979 | 657.1444 | 238.0139 | 256.8797 | 252.0195
1175.5979 | 659.2684 | 238.3936 | 256.5707 | 252.2498
1176.5979 | 658.0014 | 238.361 | 256.4555 | 251.7605
1177.5979 | 653.9063 | 238.7399 | 256.43 | 251.6831
1178.5979 | 653.6864 | 239.1464 | 256.2168 | 252.0737
1179.5979 | 652.8436 | 239.5044 | 256.3972 | 252.0445
1180.5979 | 652.992 | 239.9696 | 256.6769 | 252.0068
1181.6135 | 650.9797 | 240.793 | 258.0473 | 252.2222
1182.5979 | 649.6396 | 240.9491 | 258.1064 | 253.1651
1183.5979 | 647.307 | 241.5801 | 258.5686 | 254.3334
1184.5979 | 646.3176 | 242.3439 | 259.8021 | 254.1144
1185.5979 | 643.9624 | 242.6992 | 260.3082 | 254.4222
1186.5979 | 639.5969 | 242.6979 | 260.5324 | 255.5616
1187.5979 | 639.356 | 242.8162 | 260.4168 | 255.5497
1188.5979 | 639.9035 | 242.821 | 260.1888 | 255.6153
1189.5979 | 637.4361 | 241.7187 | 260.94 | 255.7302
1190.5979 | 638.1757 | 241.5867 | 260.748 | 256.0962
1191.5979 | 638.3305 | 241.6138 | 260.1601 | 256.4505
1192.5979 | 636.7484 | 241.204 | 259.9794 | 256.0412
1193.5979 | 636.2199 | 241.3408 | 259.7424 | 255.9722
1194.5979 | 634.9236 | 242.0383 | 260.5406 | 255.3651
1195.5979 | 635.1005 | 242.1319 | 260.9239 | 255.2628
1196.5979 | 636.1595 | 242.6046 | 261.1154 | 255.8936
1197.5979 | 634.5417 | 242.8049 | 261.3336 | 256.3059
1198.5979 | 631.8915 | 243.1488 | 262.5278 | 256.9659
1199.5979 | 633.3845 | 243.3784 | 262.7741 | 257.2613
1200.5979 | 634.6845 | 243.6182 | 262.9324 | 258.1699
1201.5979 | 633.5405 | 243.597 | 262.5893 | 258.2117
1202.5979 | 633.2303 | 244.2672 | 262.3693 | 258.0704
1203.5979 | 632.0464 | 243.5945 | 262.5444 | 259.0622
1204.5979 | 629.9903 | 243.5091 | 262.6859 | 258.1702
1205.5979 | 630.4455 | 243.7157 | 262.1267 | 257.3126
1206.5979 | 632.6975 | 243.6563 | 261.8363 | 256.7736
1207.5979 | 629.7981 | 244.357 | 261.5241 | 256.4075
1208.5979 | 628.0245 | 245.1876 | 261.9518 | 256.9956
1209.5979 | 627.2277 | 244.5679 | 261.3009 | 257.3119
1210.5979 | 626.7691 | 244.7105 | 261.8112 | 257.1699
1211.5979 | 625.0563 | 245.0189 | 262.0324 | 257.0937
1212.5979 | 626.6564 | 245.2288 | 261.5102 | 257.244
1213.5979 | 624.2826 | 245.3359 | 261.7122 | 257.0497
1214.5979 | 625.6897 | 245.1272 | 261.7122 | 257.515
1215.5979 | 623.7066 | 245.2919 | 261.8892 | 257.7257
1216.5979 | 624.7346 | 245.9157 | 262.0257 | 257.9826
1217.5979 | 623.0793 | 245.7892 | 262.0604 | 257.9636
1218.5979 | 623.5459 | 246.2065 | 262.0945 | 258.746
1219.5979 | 621.784 | 246.6906 | 262.6712 | 258.9973
1220.5979 | 621.2937 | 246.9205 | 262.92 | 259.6261
1221.5979 | 620.057 | 247.6624 | 263.1322 | 260.4698
1222.5979 | 617.6046 | 248.394 | 263.0488 | 260.5009
1223.5979 | 618.0179 | 248.9519 | 263.9866 | 259.8619
1224.5979 | 617.6048 | 248.8462 | 264.9386 | 259.3214
1225.5979 | 615.9965 | 249.7495 | 265.2756 | 259.9891
1226.5979 | 617.7021 | 250.677 | 265.7854 | 260.1017
1227.5979 | 617.9612 | 251.313 | 266.1357 | 260.1928
1228.5979 | 617.8812 | 252.1475 | 266.7815 | 260.2055
1229.5979 | 616.2333 | 253.2209 | 267.3447 | 260.1598
1230.5979 | 616.2624 | 254.8405 | 267.8922 | 260.6484
1231.5979 | 617.4415 | 255.9782 | 268.3685 | 260.4295
1232.5979 | 618.4847 | 256.5376 | 269.3113 | 260.9647
1233.5979 | 620.1708 | 256.7892 | 269.8413 | 260.851
1234.5979 | 621.2507 | 258.2483 | 270.6547 | 260.7164
1235.5979 | 622.2104 | 257.835 | 270.8343 | 261.0647
1236.5979 | 621.6704 | 258.4699 | 270.7395 | 261.4348
1237.5979 | 622.2616 | 258.7563 | 270.4739 | 262.4044
1238.5979 | 623.2876 | 258.5997 | 270.3556 | 262.7554
1239.5979 | 624.8423 | 258.6165 | 270.2065 | 262.6575
1240.5979 | 626.6778 | 259.1012 | 270.6125 | 262.8541
1241.6135 | 625.5843 | 259.5899 | 270.4641 | 263.2426
1242.5979 | 624.4094 | 259.1499 | 270.5797 | 263.9793
1243.5979 | 623.5637 | 258.8022 | 271.1398 | 265.1017
1244.5979 | 622.6286 | 258.8951 | 271.2257 | 266.3618
1245.5979 | 622.9652 | 258.9678 | 270.8617 | 266.5592
1246.5979 | 623.3387 | 258.4063 | 271.4399 | 266.8694
1247.5979 | 622.61 | 258.7158 | 271.3845 | 266.7314
1248.5979 | 622.2227 | 258.8652 | 271.0688 | 266.6863
1249.5979 | 622.6649 | 259.0634 | 271.3097 | 266.7326
1250.5979 | 623.9968 | 259.4408 | 271.6052 | 266.4586
1251.5979 | 624.0566 | 259.4064 | 271.4757 | 266.4446
1252.5979 | 624.9936 | 259.8964 | 272.2662 | 266.3185
1253.5979 | 628.4107 | 259.2567 | 272.7548 | 266.1477
1254.5979 | 629.8656 | 259.2048 | 273.474 | 266.3199
1255.5979 | 631.3358 | 259.3631 | 274.053 | 266.3895
1256.5979 | 630.1958 | 259.0995 | 274.1626 | 267.2232
1257.5979 | 626.4095 | 259.2134 | 274.2593 | 268.4053
1258.5979 | 627.2094 | 259.0486 | 273.7694 | 269.0725
1259.5979 | 629.8576 | 259.4142 | 274.2249 | 269.5229
1260.5979 | 632.2453 | 259.8829 | 274.6453 | 269.7389
1261.5979 | 631.6386 | 260.5582 | 274.9602 | 269.634
1262.5979 | 633.6696 | 260.8501 | 275.4125 | 270.4966
1263.5979 | 634.6569 | 261.1576 | 275.9898 | 270.7236
1264.5979 | 633.5293 | 261.3783 | 276.1836 | 271.3834
1265.5979 | 634.5613 | 262.0628 | 275.6818 | 271.3331
1266.5979 | 635.5728 | 262.2457 | 275.3123 | 271.7423
1267.5979 | 635.281 | 262.599 | 274.9775 | 271.6998
1268.5979 | 634.2311 | 263.2436 | 275.0843 | 271.1394
1269.5979 | 634.2854 | 263.1028 | 275.1022 | 270.7671
1270.5979 | 634.5386 | 263.7425 | 275.5174 | 271.1488
1271.5979 | 634.6568 | 264.1269 | 276.4654 | 271.5143
1272.5979 | 635.3922 | 264.6175 | 277.3395 | 271.3406
1273.5979 | 636.501 | 264.6041 | 277.3366 | 271.1156
1274.5979 | 636.3631 | 264.6609 | 277.7515 | 272.3213
1275.5979 | 633.3074 | 265.1199 | 278.5452 | 272.857
1276.5979 | 632.5355 | 265.8398 | 278.7089 | 272.5707
1277.5979 | 633.0446 | 265.6431 | 278.8281 | 272.7852
1278.5979 | 634.6116 | 266.3729 | 279.894 | 272.9886
1279.5979 | 635.0671 | 266.1475 | 279.8718 | 273.3201
1280.5979 | 635.9796 | 267.5303 | 280.1605 | 274.1835
1281.5979 | 635.3051 | 267.7066 | 280.8818 | 274.4834
1282.5979 | 635.3225 | 268.3108 | 281.3546 | 274.6583
1283.5979 | 636.4338 | 268.6742 | 282.1787 | 275.4576
1284.5979 | 638.2294 | 269.3385 | 282.5988 | 275.3914
1285.5979 | 642.5702 | 268.9128 | 282.4419 | 275.6017
1286.5979 | 642.6523 | 268.8439 | 282.1607 | 276.4929
1287.5979 | 641.675 | 270.1969 | 282.271 | 276.1529
1288.5979 | 641.5208 | 270.0857 | 282.7694 | 276.6522
1289.5979 | 641.4345 | 269.8542 | 283.1335 | 276.9447
1290.5979 | 643.5435 | 270.0645 | 282.9377 | 276.6598
1291.5979 | 645.8042 | 271.094 | 282.4254 | 277.1699
1292.5979 | 645.2166 | 270.5473 | 282.157 | 278.2371
1293.5979 | 646.2817 | 270.8179 | 281.9618 | 278.6097
1294.5979 | 647.1293 | 271.8423 | 281.7525 | 277.8455
1295.5979 | 647.7582 | 271.6743 | 281.4193 | 277.6176
1296.5979 | 650.1693 | 272.7776 | 280.8784 | 277.9674
1297.5979 | 652.2776 | 272.6046 | 280.7589 | 277.4735
1298.5979 | 654.3783 | 272.2091 | 280.5351 | 277.0626
1299.5979 | 653.9013 | 273.0124 | 280.6685 | 276.7713
1300.5979 | 653.4811 | 273.4077 | 280.7869 | 276.976
1301.6135 | 653.776 | 273.4366 | 280.5099 | 277.7951
1302.5979 | 655.9414 | 273.1996 | 280.1905 | 277.7404
1303.5979 | 660.6437 | 273.108 | 281.0924 | 277.8224
1304.5979 | 663.7789 | 272.3326 | 280.9532 | 277.3478
1305.5979 | 665.5038 | 272.3648 | 280.6722 | 276.8627
1306.5979 | 666.3975 | 272.8712 | 280.4229 | 276.7895
1307.5979 | 665.77 | 272.782 | 280.358 | 277.1784
1308.5979 | 665.2423 | 272.7847 | 280.5196 | 276.9228
1309.5979 | 666.6918 | 272.6832 | 281.0116 | 276.5288
1310.5979 | 668.2334 | 272.1187 | 281.1291 | 277.0651
1311.5979 | 668.3433 | 272.8948 | 281.3072 | 278.1312
1312.5979 | 667.1952 | 272.8957 | 281.8733 | 278.7146
1313.5979 | 666.0801 | 273.2737 | 282.0585 | 278.8144
1314.5979 | 664.1598 | 273.4845 | 282.0833 | 279.2357
1315.5979 | 666.7179 | 273.4893 | 282.351 | 279.114
1316.5979 | 668.3056 | 273.2451 | 282.5981 | 279.0666
1317.5979 | 668.2049 | 273.3027 | 283.0734 | 279.0331
1318.5979 | 669.119 | 273.3928 | 282.9179 | 279.4228
1319.5979 | 667.8025 | 273.3767 | 282.7834 | 279.5261
1320.5979 | 668.7848 | 273.6935 | 282.6884 | 279.0678
1321.5979 | 667.1741 | 274.0127 | 282.8943 | 279.8489
1322.6135 | 667.7019 | 273.7818 | 282.7611 | 279.9637
1323.5979 | 667.4144 | 273.6175 | 282.5608 | 280.5994
1324.5979 | 664.4787 | 274.0272 | 282.7056 | 280.083
1325.5979 | 665.0286 | 274.5569 | 282.9273 | 279.3636
1326.5979 | 665.9463 | 274.896 | 283.1799 | 279.2475
1327.5979 | 668.062 | 274.8245 | 282.6405 | 278.8112
1328.5979 | 669.0634 | 275.1222 | 282.5898 | 278.7367
1329.5979 | 669.1752 | 275.8047 | 282.6154 | 278.8945
1330.5979 | 668.6753 | 275.8549 | 282.5264 | 279.7935
1331.5979 | 669.3759 | 275.6683 | 283.5122 | 280.0872
1332.5979 | 668.0806 | 275.7369 | 282.9707 | 279.4041
1333.5979 | 670.5934 | 275.7538 | 282.327 | 279.2752
1334.5979 | 670.3163 | 275.3918 | 282.5224 | 278.3911
1335.5979 | 669.495 | 275.1982 | 283.5691 | 278.5691
1336.5979 | 669.6199 | 275.6561 | 285.018 | 279.6404
1337.5979 | 670.9907 | 275.7145 | 285.586 | 280.1228
1338.5979 | 672.3092 | 275.7353 | 286.4772 | 280.689
1339.5979 | 672.3628 | 276.2378 | 286.931 | 280.7458
1340.5979 | 670.087 | 276.3746 | 287.1148 | 281.0883
1341.5979 | 667.8565 | 276.684 | 287.6548 | 281.5146
1342.5979 | 665.7237 | 277.3027 | 288.3534 | 282.1576
1343.5979 | 664.2608 | 277.2119 | 289.065 | 283.0083
1344.5979 | 666.2989 | 277.5382 | 290.0906 | 283.1942
1345.5979 | 665.6723 | 278.5234 | 290.6983 | 283.2578
1346.5979 | 666.0019 | 278.5409 | 291.6268 | 283.2934
1347.5979 | 666.8512 | 278.6172 | 291.3015 | 283.7844
1348.5979 | 666.3929 | 278.7619 | 290.885 | 283.2627
1349.5979 | 665.3034 | 278.6972 | 292.4988 | 282.9387
1350.5979 | 665.7956 | 278.8119 | 293.2596 | 283.4013
1351.5979 | 664.7369 | 278.7731 | 293.8717 | 283.2216
1352.6135 | 664.9 | 278.9316 | 293.5221 | 283.2482
1353.5979 | 668.5389 | 278.9003 | 293.9641 | 282.7574
1354.5979 | 668.4988 | 279.2505 | 293.8827 | 282.1926
1355.5979 | 667.457 | 280.0245 | 293.0351 | 281.8848
1356.5979 | 668.8822 | 280.091 | 292.592 | 281.7491
1357.5979 | 670.4924 | 280.3368 | 292.8956 | 282.8088
1358.5979 | 670.6518 | 280.1946 | 293.4289 | 283.337
1359.6135 | 674.1418 | 279.946 | 293.1642 | 284.2421
1360.6135 | 674.9443 | 279.1745 | 293.0308 | 284.6218
1361.6135 | 676.0235 | 279.3068 | 292.9511 | 284.7601
1362.5979 | 675.8153 | 279.399 | 292.8988 | 284.7807
1363.5979 | 675.1453 | 279.2304 | 292.4772 | 285.5149
1364.5979 | 674.8887 | 279.3247 | 292.1459 | 285.968
1365.5979 | 675.7203 | 280.2149 | 291.8513 | 286.2943
1366.5979 | 678.0928 | 280.5467 | 292.4491 | 286.7867
1367.5979 | 678.7306 | 281.6017 | 292.3241 | 286.8315
1368.5979 | 680.1076 | 282.1847 | 292.478 | 287.4652
1369.5979 | 678.3948 | 282.4625 | 293.0486 | 287.6567
1370.5979 | 679.1666 | 282.424 | 294.9455 | 288.3941
1371.5979 | 677.6526 | 282.3187 | 294.9013 | 288.5507
1372.5979 | 677.8064 | 283.0776 | 294.9397 | 288.4912
1373.5979 | 678.6909 | 282.2729 | 294.5608 | 288.2027
1374.5979 | 678.0581 | 282.1956 | 294.7447 | 287.2879
1375.5979 | 676.8876 | 282.1053 | 294.7652 | 287.0415
1376.5979 | 676.1925 | 282.2056 | 294.4924 | 286.0112
1377.5979 | 672.6125 | 282.555 | 294.3253 | 286.6634
1378.5979 | 671.2125 | 282.7942 | 294.7558 | 286.1738
1379.5979 | 670.2867 | 283.4759 | 295.0301 | 286.3469
1380.5979 | 670.0686 | 283.6747 | 295.1559 | 286.4973
1381.5979 | 668.7428 | 284.0736 | 295.6259 | 286.745
1382.5979 | 670.319 | 284.0389 | 296.0415 | 286.8309
1383.5979 | 671.229 | 283.7143 | 295.62 | 287.5873
1384.5979 | 669.5735 | 284.1102 | 295.9046 | 288.2911
1385.5979 | 670.6914 | 284.2715 | 296.3823 | 288.2009
1386.5979 | 669.807 | 284.2321 | 296.2413 | 287.9276
1387.5979 | 671.5865 | 283.6167 | 295.8963 | 287.3477
1388.5979 | 673.0902 | 282.9778 | 295.6156 | 286.8171
1389.5979 | 672.3208 | 282.6551 | 295.8266 | 286.878
1390.5979 | 674.3824 | 283.3344 | 296.4747 | 287.6907
1391.5979 | 676.0147 | 284.2702 | 297.1488 | 287.5981
1392.5979 | 675.9406 | 283.913 | 297.3257 | 287.2951
1393.5979 | 676.7992 | 284.2001 | 298.0683 | 287.2864
1394.5979 | 678.3294 | 284.1778 | 298.8181 | 287.4647
1395.5979 | 679.4191 | 283.8891 | 299.0881 | 288.426
1396.5979 | 675.8368 | 283.4803 | 299.102 | 288.785
1397.5979 | 673.7496 | 283.6455 | 298.7344 | 288.6201
1398.5979 | 672.4123 | 283.9796 | 298.4709 | 288.1219
1399.5979 | 672.9937 | 284.5434 | 298.5844 | 288.3243
1400.5979 | 670.9382 | 284.4307 | 300.0009 | 289.2556
1401.5979 | 669.7842 | 284.3933 | 300.806 | 289.0921
1402.5979 | 668.6394 | 284.4332 | 301.9221 | 289.7297
1403.5979 | 668.8768 | 284.5678 | 302.3711 | 291.545
1404.5979 | 669.9303 | 284.3433 | 303.3773 | 291.985
1405.5979 | 672.5678 | 285.2077 | 304.8879 | 292.6672
1406.5979 | 677.0525 | 285.4824 | 306.3349 | 292.8653
1407.5979 | 680.0896 | 285.9394 | 306.8505 | 293.03
1408.5979 | 680.9635 | 286.2671 | 307.6647 | 293.6722
1409.5979 | 679.8505 | 286.9911 | 308.7133 | 293.9174
1410.5979 | 681.3849 | 287.1849 | 309.4377 | 294.7686
1411.5979 | 680.4249 | 287.1104 | 310.1674 | 295.0757
1412.6135 | 682.2942 | 288.4278 | 309.6796 | 295.7148
1413.5979 | 683.467 | 288.6169 | 309.4853 | 295.4803
1414.5979 | 682.1727 | 288.8432 | 309.7531 | 295.6588
1415.5979 | 682.2275 | 289.3896 | 310.4632 | 296.3479
1416.5979 | 682.1398 | 289.3988 | 311.1247 | 296.1988
1417.5979 | 682.6645 | 289.9243 | 311.0736 | 295.6192
1418.5979 | 681.7421 | 290.4048 | 311.7571 | 295.2928
1419.5979 | 682.0995 | 291.141 | 311.6525 | 294.7431
1420.5979 | 684.6096 | 291.3596 | 311.0574 | 294.2998
1421.5979 | 683.5461 | 291.7296 | 311.2978 | 294.5857
1422.5979 | 682.2261 | 291.877 | 310.7418 | 294.4456
1423.5979 | 677.4843 | 291.7541 | 310.2303 | 294.2511
1424.5979 | 675.6865 | 292.9217 | 309.9882 | 294.2332
1425.5979 | 677.9648 | 293.0658 | 310.7541 | 294.2821
1426.5979 | 680.2299 | 292.3765 | 311.5103 | 294.1818
1427.5979 | 679.7702 | 292.2193 | 311.6522 | 294.3437
1428.5979 | 680.8819 | 292.802 | 311.9932 | 294.4385
1429.5979 | 682.3701 | 293.175 | 311.6244 | 294.8162
1430.5979 | 681.6876 | 292.9293 | 311.4043 | 294.2558
1431.5979 | 676.6469 | 293.0254 | 311.1815 | 293.6474
1432.5979 | 676.2245 | 292.8573 | 310.4894 | 294.3576
1433.5979 | 676.4476 | 292.9339 | 310.1159 | 293.8961
1434.5979 | 677.4065 | 293.1834 | 309.7245 | 293.4959
1435.5979 | 678.6032 | 293.7729 | 309.2292 | 293.338
1436.5979 | 680.3829 | 294.517 | 309.125 | 293.4447
1437.5979 | 681.8422 | 294.4484 | 309.1447 | 293.563
1438.5979 | 684.9845 | 294.4687 | 308.6786 | 293.5577
1439.5979 | 688.2903 | 294.7655 | 308.7183 | 293.0878
1440.5979 | 689.9034 | 294.5567 | 309.294 | 293.9823
1441.5979 | 691.3199 | 295.4103 | 309.4793 | 293.7665
1442.5979 | 691.9407 | 295.2655 | 309.4119 | 293.6123
1443.5979 | 692.9918 | 295.5552 | 309.9954 | 293.9632
1444.5979 | 689.5601 | 294.3999 | 310.4471 | 293.4432
1445.5979 | 688.4237 | 294.64 | 310.5748 | 293.787
1446.5979 | 684.58 | 294.2862 | 310.2518 | 294.1589
1447.5979 | 684.4342 | 294.0343 | 308.8875 | 293.2872
1448.5979 | 684.5418 | 293.7177 | 308.2027 | 293.2851
1449.5979 | 685.3119 | 293.6169 | 307.8765 | 294.4389
1450.5979 | 685.102 | 293.569 | 307.9217 | 293.698
1451.5979 | 683.9143 | 293.4387 | 308.2872 | 293.8003
1452.5979 | 682.5235 | 293.1482 | 308.8737 | 293.4832
1453.5979 | 682.6772 | 292.9557 | 309.2275 | 293.0287
1454.5979 | 682.3446 | 292.6097 | 309.102 | 293.1126
1455.5979 | 681.3998 | 292.3384 | 309.0637 | 292.9174
1456.5979 | 684.0199 | 291.7863 | 309.593 | 293.0277
1457.5979 | 683.8902 | 292.1507 | 310.1147 | 293.3576
1458.5979 | 685.7468 | 291.6618 | 310.0516 | 292.4139
1459.5979 | 689.4166 | 291.8404 | 310.037 | 291.9963
1460.5979 | 689.6284 | 291.966 | 310.1445 | 292.0541
1461.5979 | 689.7194 | 291.9733 | 310.1341 | 292.2858
1462.5979 | 689.7767 | 292.8362 | 309.7261 | 293.4488
1463.5979 | 689.3995 | 293.3206 | 309.9264 | 294.1308
1464.5979 | 689.4442 | 293.1866 | 310.3137 | 294.0899
1465.5979 | 688.627 | 293.0894 | 309.9129 | 293.5162
1466.5979 | 686.8198 | 292.8461 | 308.8932 | 292.6804
1467.5979 | 684.068 | 293.5688 | 308.7825 | 292.5851
1468.5979 | 684.7664 | 294.002 | 309.1999 | 292.8096
1469.5979 | 686.2966 | 294.4171 | 309.0855 | 293.1053
1470.5979 | 688.8795 | 294.4795 | 308.8242 | 292.8632
1471.5979 | 692.5838 | 294.7756 | 309.9374 | 293.204
1472.5979 | 694.3097 | 294.2015 | 309.9758 | 293.5825
1473.5979 | 695.7332 | 293.9981 | 309.2203 | 293.5744
1474.5979 | 695.333 | 293.7574 | 309.3661 | 294.2205
1475.5979 | 696.2746 | 293.4884 | 309.2709 | 294.4383
1476.5979 | 694.5519 | 293.6525 | 309.2237 | 294.7831
1477.5979 | 691.1693 | 293.2837 | 308.6397 | 294.7523
1478.5979 | 687.9811 | 292.8826 | 308.7303 | 295.1473
1479.5979 | 687.8005 | 292.5636 | 308.2912 | 294.9432
1480.5979 | 687.8651 | 293.5101 | 309.1523 | 294.8458
1481.6135 | 688.0956 | 293.4464 | 308.9329 | 295.2429
1482.5979 | 687.4019 | 293.4014 | 308.6709 | 295.4954
1483.5979 | 687.1939 | 292.6674 | 308.5666 | 295.7723
1484.5979 | 683.1777 | 292.9195 | 308.6323 | 296.1175
1485.5979 | 680.7366 | 293.233 | 308.6239 | 295.8254
1486.5979 | 679.0135 | 293.85 | 308.877 | 295.4147
1487.5979 | 679.916 | 293.6152 | 308.4046 | 295.1868
1488.5979 | 679.4415 | 294.299 | 308.3343 | 295.406
1489.5979 | 681.9873 | 294.1995 | 308.541 | 294.7313
1490.5979 | 682.8638 | 294.4268 | 309.1096 | 296.0563
1491.5979 | 682.6296 | 293.98 | 308.7174 | 297.1444
1492.5979 | 681.8092 | 294.0343 | 308.6813 | 297.4517
1493.5979 | 683.7599 | 294.1759 | 308.6153 | 296.7289
1494.5979 | 681.5315 | 293.9966 | 308.6309 | 296.5164
1495.5979 | 682.1213 | 294.4508 | 308.8612 | 296.611
1496.5979 | 682.1425 | 294.583 | 309.0739 | 295.8534
1497.5979 | 679.3065 | 295.0924 | 308.6509 | 295.4816
1498.5979 | 675.1962 | 295.3458 | 308.7677 | 294.5287
1499.5979 | 671.2851 | 297.2314 | 308.3687 | 295.0927
1500.6135 | 669.1513 | 296.6762 | 309.1529 | 294.8754
1501.5979 | 670.467 | 296.8761 | 309.4131 | 295.8702
1502.5979 | 672.1185 | 297.507 | 310.4835 | 296.4398
1503.5979 | 675.5614 | 297.1598 | 310.9622 | 296.6208
1504.5979 | 675.3881 | 298.3196 | 311.4671 | 296.6337
1505.5979 | 675.7479 | 299.3095 | 310.9437 | 296.3883
1506.5979 | 679.8389 | 298.8682 | 310.9625 | 297.1068
1507.5979 | 680.9707 | 298.4474 | 311.0534 | 297.6441
1508.5979 | 682.187 | 299.4956 | 311.043 | 296.9523
1509.5979 | 681.5023 | 300.266 | 311.4968 | 297.4963
1510.5979 | 683.3417 | 300.871 | 312.2286 | 297.7679
1511.5979 | 680.9224 | 301.0047 | 313.5091 | 299.3026
1512.5979 | 682.4978 | 302.1841 | 314.5345 | 299.9361
1513.5979 | 684.081 | 302.4091 | 315.8183 | 300.2276
1514.5979 | 686.7329 | 303.249 | 316.5822 | 300.1828
1515.5979 | 689.8606 | 303.3501 | 317.0445 | 299.9964
1516.5979 | 693.1903 | 304.2502 | 317.2567 | 300.2499
1517.5979 | 696.5906 | 305.2544 | 317.598 | 299.7191
1518.5979 | 699.3131 | 305.6893 | 318.3571 | 301.6979
1519.5979 | 700.2037 | 306.4475 | 318.7369 | 302.4649
1520.5979 | 697.7508 | 306.6468 | 319.5999 | 302.3814
1521.5979 | 696.3624 | 307.6277 | 319.8754 | 302.9509
1522.5979 | 695.9692 | 307.9383 | 321.3467 | 303.4958
1523.5979 | 696.9407 | 307.8256 | 322.8695 | 305.9649
1524.5979 | 696.8816 | 309.1543 | 322.7977 | 306.5359
1525.5979 | 696.5493 | 309.6369 | 323.4912 | 307.1357
1526.5979 | 697.195 | 310.4237 | 323.8869 | 307.1909
1527.5979 | 696.4227 | 310.5137 | 324.1617 | 307.7149
1528.5979 | 697.4751 | 311.6225 | 324.311 | 306.9169
1529.5979 | 698.0625 | 312.0343 | 323.8276 | 308.3096
1530.5979 | 695.9524 | 311.9339 | 324.3805 | 308.1663
1531.5979 | 693.0213 | 312.5597 | 324.5333 | 308.2616
1532.6135 | 691.4544 | 312.3825 | 324.446 | 309.184
1533.5979 | 694.2855 | 312.0545 | 324.0752 | 308.8214
1534.5979 | 694.5054 | 312.2075 | 324.0982 | 308.3501
1535.5979 | 694.7348 | 312.8896 | 324.408 | 309.2815
1536.5979 | 694.9572 | 313.314 | 323.9109 | 309.6859
1537.5979 | 693.9275 | 313.5398 | 324.2329 | 308.6809
1538.5979 | 692.3749 | 313.9735 | 324.1317 | 308.2641
1539.5979 | 687.7501 | 313.8962 | 323.8108 | 308.1449
1540.5979 | 686.8589 | 313.8499 | 323.763 | 308.409
1541.5979 | 683.7989 | 314.0509 | 323.5404 | 308.6166
1542.5979 | 684.0914 | 314.6945 | 323.7172 | 309.7718
1543.5979 | 684.4488 | 315.1093 | 324.1657 | 310.9512
1544.5979 | 682.8235 | 315.6302 | 324.8455 | 311.1666
1545.5979 | 680.4083 | 316.3986 | 325.8946 | 311.281
1546.5979 | 679.799 | 316.7932 | 327.1521 | 312.1432
1547.5979 | 681.1499 | 316.8884 | 326.7581 | 312.8673
1548.5979 | 682.6335 | 316.635 | 326.9488 | 313.9442
1549.5979 | 686.8428 | 317.4314 | 326.8718 | 314.7757
1550.5979 | 688.9219 | 317.5093 | 327.5033 | 315.5103
1551.5979 | 691.657 | 317.3512 | 327.4511 | 316.5991
1552.5979 | 691.7116 | 317.5451 | 327.7116 | 316.2321
1553.5979 | 691.0502 | 318.3085 | 327.7415 | 315.3916
1554.5979 | 691.7194 | 319.1777 | 328.3215 | 315.2168
1555.5979 | 692.5049 | 319.062 | 327.8559 | 315.3807
1556.5979 | 692.124 | 318.6856 | 327.9308 | 316.1596
1557.5979 | 693.3696 | 319.5169 | 328.7244 | 316.4741
1558.5979 | 693.1554 | 319.5174 | 328.82 | 317.4295
1559.5979 | 691.6636 | 319.1248 | 328.7819 | 317.6362
1560.5979 | 689.1581 | 319.4913 | 329.437 | 317.2802
1561.5979 | 684.4117 | 320.4188 | 329.5865 | 317.36
1562.6135 | 681.7134 | 320.1259 | 329.6644 | 318.0051
1563.5979 | 682.6097 | 320.1877 | 329.1779 | 318.0131
1564.5979 | 680.7505 | 321.5344 | 329.6084 | 318.4195
1565.5979 | 678.8182 | 322.0587 | 328.8254 | 319.3898
1566.5979 | 675.0369 | 322.1355 | 328.8996 | 319.6128
1567.5979 | 672.3231 | 322.1475 | 328.3537 | 319.2371
1568.5979 | 672.7548 | 322.067 | 328.2242 | 319.6358
1569.5979 | 672.3179 | 322.4004 | 329.4064 | 319.6847
1570.5979 | 673.0806 | 322.6901 | 330.0632 | 319.6273
1571.5979 | 673.4336 | 322.7822 | 330.7314 | 319.5856
1572.5979 | 672.948 | 323.1272 | 330.539 | 320.2175
1573.5979 | 674.7966 | 323.7781 | 330.9468 | 319.9568
1574.5979 | 674.7489 | 323.0621 | 330.2842 | 319.5639
1575.5979 | 672.9289 | 323.7545 | 330.3738 | 320.0836
1576.5979 | 668.4023 | 324.2378 | 330.3332 | 319.4301
1577.5979 | 667.247 | 324.0691 | 330.8562 | 320.3745
1578.5979 | 668.2658 | 324.9793 | 331.0535 | 321.2995
1579.5979 | 667.4713 | 325.0975 | 332.7236 | 321.6729
1580.5979 | 667.651 | 325.4555 | 332.6023 | 322.0347
1581.5979 | 666.9269 | 325.3845 | 332.8003 | 322.8435
1582.5979 | 663.1554 | 326.786 | 335.1462 | 323.1418
1583.5979 | 659.9516 | 327.2467 | 334.4742 | 323.8093
1584.5979 | 657.1909 | 327.6793 | 335.2902 | 324.3796
1585.5979 | 658.1148 | 327.7748 | 334.9345 | 324.3517
1586.5979 | 660.0447 | 326.9547 | 334.3206 | 323.9398
1587.5979 | 658.9158 | 326.6569 | 333.7586 | 323.1633
1588.5979 | 656.3655 | 327.3329 | 333.0224 | 322.5722
1589.5979 | 652.9495 | 326.998 | 332.9551 | 323.6722
1590.5979 | 649.694 | 326.6409 | 333.8206 | 324.3932
1591.5979 | 651.5266 | 326.1994 | 334.0165 | 324.6799
1592.5979 | 654.1669 | 326.5483 | 334.8809 | 324.4673
1593.5979 | 657.5236 | 327.1099 | 335.093 | 324.2002
1594.5979 | 658.8028 | 327.4864 | 334.7828 | 324.457
1595.5979 | 658.9686 | 327.6618 | 335.4657 | 323.8704
1596.5979 | 655.9014 | 328.0079 | 336.9732 | 324.3383
1597.5979 | 655.9929 | 327.5739 | 337.3036 | 324.602
1598.5979 | 655.6084 | 328.4751 | 337.5869 | 324.5012
1599.5979 | 655.4519 | 330.0106 | 336.9929 | 324.2172
1600.5979 | 654.3749 | 331.0243 | 337.4939 | 324.3729
1601.5979 | 656.2613 | 331.4146 | 337.4655 | 324.5595
1602.6135 | 658.5676 | 331.9777 | 338.4277 | 324.6383
1603.5979 | 661.3092 | 332.8135 | 338.7134 | 325.4845
1604.5979 | 661.4048 | 333.9836 | 338.0131 | 325.1602
1605.5979 | 664.2546 | 333.804 | 337.3726 | 324.4379
1606.5979 | 662.1907 | 333.7552 | 337.2985 | 324.6231
1607.5979 | 659.2036 | 333.4311 | 336.5353 | 324.3818
1608.5979 | 655.4632 | 333.522 | 337.3343 | 323.5516
1609.5979 | 651.1977 | 333.633 | 337.6395 | 324.4536
1610.5979 | 648.8192 | 333.2895 | 338.1328 | 325.0649
1611.5979 | 649.5505 | 333.6271 | 338.755 | 325.3954
1612.5979 | 649.973 | 333.5381 | 339.0046 | 325.6771
1613.5979 | 651.6491 | 333.7469 | 338.9369 | 327.0275
1614.5979 | 653.6708 | 334.6967 | 338.7456 | 326.3719
1615.5979 | 654.7476 | 334.4341 | 339.7459 | 327.437
1616.5979 | 653.7505 | 334.0248 | 340.9612 | 328.6969
1617.5979 | 654.8037 | 333.7385 | 341.0825 | 329.707
1618.5979 | 657.3311 | 334.1305 | 340.5786 | 329.2698
1619.5979 | 657.3759 | 334.3296 | 340.0981 | 329.4669
1620.5979 | 658.5348 | 335.2215 | 339.8358 | 329.1899
1621.5979 | 660.4219 | 335.4976 | 340.3938 | 329.3601
1622.6135 | 662.8325 | 335.5195 | 340.8932 | 329.907
1623.5979 | 663.7101 | 335.9155 | 340.7543 | 329.717
1624.5979 | 665.2949 | 336.4534 | 341.2005 | 330.0444
1625.5979 | 665.7511 | 336.6309 | 341.897 | 331.0815
1626.5979 | 665.3257 | 336.24 | 341.6944 | 330.4078
1627.6135 | 665.8984 | 336.9583 | 342.9182 | 330.5423
1628.6135 | 666.7408 | 336.8427 | 344.8146 | 333.0702
1629.5979 | 667.5762 | 336.7422 | 344.6869 | 332.7601
1630.6135 | 667.8767 | 337.1513 | 344.3783 | 333.127
1631.6135 | 666.5541 | 337.7794 | 343.9492 | 332.6673
1632.5979 | 668.1197 | 338.0334 | 343.9164 | 333.4218
1633.5979 | 670.7104 | 337.8855 | 343.503 | 332.1732
1634.5979 | 672.8826 | 338.2892 | 343.3539 | 331.556
1635.5979 | 677.3517 | 339.2539 | 343.7476 | 333.0287
1636.5979 | 681.0904 | 339.3274 | 343.9254 | 332.7
1637.5979 | 682.6201 | 339.1579 | 343.6972 | 332.7912
1638.5979 | 681.1762 | 339.5592 | 343.9753 | 332.782
1639.5979 | 680.0565 | 339.6801 | 344.0494 | 332.7747
1640.5979 | 678.418 | 339.3155 | 344.4162 | 332.9712
1641.5979 | 677.606 | 339.1244 | 344.1932 | 332.8862
1642.5979 | 676.5028 | 338.9191 | 344.0368 | 332.9589
1643.5979 | 677.3827 | 339.3153 | 344.0414 | 333.7641
1644.5979 | 676.678 | 339.4658 | 343.7255 | 333.8
1645.5979 | 676.3363 | 339.2935 | 344.0105 | 334.1353
1646.5979 | 674.3468 | 338.6857 | 343.9014 | 333.7656
1647.5979 | 671.9665 | 338.4386 | 343.2398 | 333.1657
1648.5979 | 670.5535 | 338.4216 | 342.8393 | 332.1488
1649.5979 | 670.1726 | 338.8334 | 342.9504 | 332.2135
1650.5979 | 668.2497 | 338.707 | 342.632 | 332.5657
1651.5979 | 669.2655 | 338.3528 | 341.9334 | 332.8473
1652.5979 | 671.1418 | 337.9293 | 341.6288 | 332.3363
1653.5979 | 670.6675 | 339.2422 | 341.5568 | 331.6724
1654.5979 | 668.611 | 339.3241 | 341.6353 | 331.1056
1655.5979 | 666.5609 | 339.3857 | 342.2135 | 331.4373
1656.5979 | 666.2153 | 339.3595 | 342.0756 | 331.9559
1657.5979 | 666.5687 | 340.002 | 341.9602 | 332.4535
1658.5979 | 668.5511 | 340.0534 | 342.4427 | 332.5356
1659.5979 | 669.2927 | 340.6768 | 343.0428 | 333.1746
1660.5979 | 670.0747 | 341.2679 | 343.552 | 333.0682
1661.6135 | 670.0395 | 341.6344 | 343.2731 | 333.4839
1662.5979 | 670.4685 | 342.0391 | 343.7821 | 332.7746
1663.5979 | 669.3838 | 342.5988 | 344.7615 | 333.2455
1664.5979 | 671.2484 | 342.8354 | 344.9827 | 333.8384
1665.5979 | 671.9144 | 343.5628 | 344.8642 | 333.8336
1666.5979 | 670.8269 | 343.7201 | 344.7937 | 334.1799
1667.5979 | 671.6853 | 343.4012 | 344.5995 | 334.7364
1668.5979 | 670.0805 | 343.7676 | 344.2679 | 334.3832
1669.5979 | 667.4121 | 343.355 | 344.4963 | 334.8455
1670.5979 | 665.6437 | 343.7159 | 344.4319 | 334.7908
1671.5979 | 664.5849 | 344.0079 | 344.1988 | 334.2318
1672.5979 | 662.6827 | 344.245 | 344.0895 | 334.2204
1673.5979 | 663.1226 | 344.1074 | 343.4559 | 334.2607
1674.5979 | 662.5104 | 343.9296 | 344.4474 | 335.792
1675.5979 | 663.286 | 343.7904 | 343.9478 | 335.8989
1676.5979 | 662.5945 | 343.0026 | 343.1626 | 334.6861
1677.5979 | 662.8213 | 343.5103 | 342.6111 | 333.9836
1678.5979 | 661.3265 | 343.8181 | 342.4484 | 334.0231
1679.5979 | 663.3717 | 343.6473 | 342.3926 | 333.7125
1680.5979 | 663.97 | 342.9854 | 342.3287 | 333.0641
1681.5979 | 663.8863 | 342.2854 | 342.2571 | 332.5661
1682.5979 | 663.1738 | 342.3088 | 341.8691 | 332.5051
1683.5979 | 663.8179 | 342.4826 | 342.1299 | 331.7495
1684.5979 | 663.2317 | 342.9934 | 342.6483 | 332.8738
1685.5979 | 663.058 | 342.5389 | 343.4138 | 333.0558
1686.5979 | 663.9227 | 342.1615 | 342.6035 | 332.9806
1687.5979 | 663.0089 | 342.3428 | 342.1562 | 333.1314
1688.5979 | 661.8908 | 342.2949 | 341.8098 | 333.1382
1689.5979 | 660.5405 | 342.4463 | 341.3642 | 333.1851
1690.5979 | 660.4953 | 342.2053 | 341.4811 | 333.474
1691.5979 | 659.1967 | 341.8164 | 341.0371 | 333.7681
1692.5979 | 659.0237 | 342.8827 | 340.7509 | 333.2144
1693.5979 | 658.6036 | 342.7275 | 341.2236 | 332.505
1694.5979 | 659.7701 | 342.6306 | 341.2953 | 332.1196
1695.5979 | 659.5703 | 342.936 | 341.7911 | 332.0037
1696.5979 | 661.0037 | 342.7022 | 342.1815 | 332.8577
1697.5979 | 664.2465 | 342.8391 | 342.4335 | 333.6777
1698.5979 | 663.9068 | 343.92 | 343.4922 | 334.0164
1699.5979 | 661.3924 | 343.882 | 343.0919 | 333.7737
1700.5979 | 661.8937 | 343.4855 | 342.9276 | 334.4557
1701.5979 | 661.8182 | 343.0046 | 343.3086 | 334.188
1702.5979 | 662.315 | 342.9266 | 343.1799 | 333.7094
1703.5979 | 661.0091 | 343.0661 | 343.3373 | 334.0935
1704.5979 | 658.9876 | 343.2004 | 343.2146 | 334.1552
1705.5979 | 655.6066 | 344.0336 | 343.4605 | 334.0053
1706.5979 | 655.3661 | 344.4891 | 343.0227 | 333.7217
1707.5979 | 656.234 | 344.2898 | 342.3 | 333.6935
1708.5979 | 655.7237 | 344.6163 | 342.4615 | 333.5575
1709.5979 | 656.1918 | 344.3255 | 342.3323 | 333.6098
1710.5979 | 655.8617 | 344.7145 | 342.8476 | 333.5799
1711.5979 | 657.7975 | 344.7488 | 342.8528 | 333.5284
1712.6135 | 660.2374 | 345.6181 | 343.2419 | 333.9455
1713.5979 | 659.7862 | 346.0015 | 343.4306 | 334.2082
1714.5979 | 660.9271 | 345.9272 | 343.6035 | 334.5321
1715.5979 | 660.4821 | 345.7826 | 344.124 | 334.4814
1716.5979 | 658.6765 | 346.1002 | 344.3558 | 334.4334
1717.5979 | 658.7754 | 346.1387 | 344.1468 | 334.2904
1718.5979 | 660.3955 | 346.8927 | 344.7568 | 334.7971
1719.5979 | 661.7189 | 347.0995 | 344.6202 | 333.9359
1720.5979 | 661.5655 | 347.4362 | 344.6862 | 334.284
1721.5979 | 661.5676 | 347.2309 | 345.088 | 333.5308
1722.5979 | 661.0295 | 347.0279 | 346.2674 | 333.2464
1723.5979 | 659.4069 | 346.8471 | 346.3535 | 333.0182
1724.5979 | 661.5461 | 346.6384 | 346.8051 | 332.8459
1725.5979 | 662.255 | 346.7929 | 346.463 | 332.9494
1726.5979 | 661.9492 | 346.2919 | 345.6361 | 332.6937
1727.5979 | 664.088 | 345.9175 | 344.6551 | 331.6637
1728.5979 | 665.5075 | 346.7963 | 344.2355 | 330.9686
1729.5979 | 666.0098 | 346.2704 | 343.6752 | 330.9837
1730.5979 | 665.8298 | 346.5334 | 343.3319 | 330.4365
1731.5979 | 666.7126 | 346.4508 | 343.3962 | 329.9057
1732.5979 | 666.76 | 346.1056 | 343.1245 | 330.1123
1733.5979 | 666.954 | 346.6743 | 344.3429 | 330.0495
1734.5979 | 666.2863 | 347.3966 | 344.067 | 330.0838
1735.5979 | 664.6727 | 347.3255 | 344.6998 | 331.0351
1736.5979 | 663.2291 | 347.3212 | 345.2449 | 331.2701
1737.5979 | 661.3071 | 347.463 | 345.2284 | 331.2287
1738.5979 | 661.3585 | 346.9338 | 344.8931 | 331.3287
1739.6135 | 661.1444 | 345.8238 | 344.7402 | 331.2742
1740.5979 | 661.6837 | 344.9553 | 344.228 | 331.3803
1741.5979 | 660.7025 | 344.959 | 344.0559 | 331.2516
1742.6135 | 659.1752 | 345.0332 | 343.8597 | 330.4572
1743.5979 | 657.6466 | 345.2296 | 343.8682 | 329.865
1744.5979 | 657.9129 | 345.1972 | 343.9651 | 330.1552
1745.5979 | 657.6356 | 345.9049 | 344.2127 | 330.7346
1746.6135 | 656.0298 | 347.2341 | 344.3722 | 330.6986
1747.5979 | 656.2313 | 347.5086 | 344.9415 | 331.5337
1748.5979 | 658.8487 | 348.7387 | 344.9084 | 332.2425
1749.5979 | 660.8706 | 348.9181 | 344.8507 | 332.1201
1750.5979 | 659.9987 | 349.2477 | 345.5401 | 332.9114
1751.5979 | 659.4921 | 348.9973 | 346.196 | 332.7767
1752.5979 | 660.8873 | 349.1723 | 346.6873 | 333.8377
1753.5979 | 659.9173 | 349.4323 | 347.8343 | 335.7515
1754.6135 | 660.118 | 349.1843 | 348.1279 | 335.4896
1755.5979 | 660.9703 | 349.5595 | 349.2119 | 336.0489
1756.5979 | 660.692 | 349.9858 | 349.3909 | 336.0223
1757.5979 | 660.3051 | 349.8955 | 349.5783 | 335.0815
1758.5979 | 660.841 | 349.4209 | 349.5292 | 334.1975
1759.5979 | 660.8789 | 349.0819 | 349.7903 | 333.5116
1760.5979 | 664.4144 | 349.1232 | 349.6872 | 332.5354
1761.5979 | 668.9435 | 349.8465 | 349.4829 | 331.6819
1762.5979 | 670.3219 | 350.1029 | 349.3653 | 331.3121
1763.5979 | 670.8774 | 350.0878 | 349.9856 | 331.271
1764.5979 | 671.2813 | 349.9366 | 350.0222 | 332.5166
1765.5979 | 672.3571 | 350.0635 | 350.6084 | 333.3126
1766.5979 | 672.782 | 349.9004 | 350.3267 | 332.9714
1767.5979 | 670.0788 | 349.5713 | 350.0539 | 332.5877
1768.5979 | 670.2781 | 349.361 | 350.0425 | 332.6566
1769.5979 | 668.7728 | 349.1139 | 349.7678 | 332.7076
1770.5979 | 669.1085 | 349.5617 | 349.6923 | 333.2412
1771.5979 | 667.0765 | 349.5428 | 349.2501 | 332.6762
1772.5979 | 665.0235 | 349.5766 | 348.3458 | 332.6173
1773.5979 | 665.2876 | 349.0087 | 348.5231 | 331.8632
1774.5979 | 664.637 | 348.4647 | 348.2118 | 332.2017
1775.5979 | 662.5761 | 348.2395 | 347.8702 | 331.7719
1776.5979 | 661.2032 | 347.821 | 347.605 | 332.2258
1777.5979 | 660.0037 | 347.8325 | 347.5408 | 331.9708
1778.5979 | 661.3252 | 347.5306 | 348.0183 | 331.9073
1779.5979 | 661.8412 | 347.5223 | 347.7623 | 332.2594
1780.5979 | 661.7912 | 347.7377 | 347.5027 | 332.9027
1781.5979 | 663.0633 | 347.9467 | 347.3122 | 332.1116
1782.5979 | 662.5418 | 347.8467 | 347.5573 | 332.2415
1783.5979 | 658.8724 | 347.1141 | 346.5542 | 332.0185
1784.5979 | 658.0927 | 346.7872 | 346.5598 | 332.2328
1785.5979 | 657.6983 | 346.8048 | 346.0338 | 331.9794
1786.5979 | 657.1704 | 345.7332 | 345.0741 | 331.7013
1787.5979 | 654.5675 | 346.1169 | 344.8502 | 331.638
1788.5979 | 650.9594 | 345.9317 | 344.6736 | 332.0457
1789.5979 | 649.2962 | 345.6217 | 345.0057 | 331.8907
1790.5979 | 649.543 | 345.8831 | 345.4165 | 332.6841
1791.5979 | 651.3945 | 345.9602 | 344.1759 | 332.4506
1792.5979 | 651.5934 | 346.12 | 343.8747 | 331.7866
1793.5979 | 651.9921 | 345.951 | 343.5548 | 331.6484
1794.5979 | 650.7086 | 345.9383 | 343.3533 | 331.3073
1795.5979 | 654.331 | 345.4099 | 343.8018 | 331.4977
1796.5979 | 655.8928 | 345.1975 | 343.6088 | 331.4981
1797.5979 | 658.1938 | 344.9839 | 343.5997 | 332.5621
1798.5979 | 657.8007 | 345.5699 | 343.6818 | 332.1618
1799.5979 | 657.5446 | 345.7347 | 343.5021 | 331.3932
1800.5979 | 657.7801 | 346.0182 | 344.0656 | 331.405
1801.5979 | 657.7424 | 345.8561 | 343.8969 | 330.817
1802.5979 | 656.6062 | 346.5303 | 344.5011 | 330.6371
1803.5979 | 657.1777 | 346.2409 | 344.5646 | 331.1464
1804.5979 | 654.8113 | 347.3445 | 344.9919 | 331.3834
1805.5979 | 653.344 | 347.2968 | 344.6684 | 330.9479
1806.5979 | 651.4894 | 347.3739 | 344.3712 | 331.3022
1807.5979 | 650.2209 | 347.8557 | 344.2852 | 330.4946
1808.5979 | 648.5089 | 347.6078 | 344.0039 | 329.986
1809.5979 | 647.6571 | 348.2326 | 344.4286 | 331.1461
1810.5979 | 648.4378 | 348.0544 | 344.4241 | 331.3001
1811.5979 | 648.4987 | 348.0116 | 344.4844 | 332.9299
1812.5979 | 647.514 | 347.3852 | 343.8157 | 332.7629
1813.5979 | 646.0617 | 347.1907 | 343.2788 | 333.1225
1814.5979 | 646.9898 | 346.5273 | 342.9328 | 333.6299
1815.5979 | 648.7251 | 346.3397 | 342.0568 | 332.5433
1816.5979 | 650.0985 | 346.4492 | 341.2867 | 331.2501
1817.5979 | 650.0725 | 347.0589 | 341.2953 | 331.319
1818.5979 | 649.5557 | 346.5048 | 341.3688 | 330.5631
1819.5979 | 649.883 | 346.1355 | 341.5505 | 329.751
1820.5979 | 647.468 | 345.4962 | 340.875 | 329.0585
1821.5979 | 646.2042 | 345.6155 | 340.7208 | 328.3959
1822.5979 | 645.7422 | 345.638 | 340.5652 | 327.7984
1823.5979 | 645.885 | 344.8497 | 340.4288 | 327.8568
1824.5979 | 646.4936 | 344.8552 | 340.6654 | 327.8698
1825.5979 | 646.5567 | 344.9294 | 340.0326 | 328.5541
1826.5979 | 647.7889 | 344.3704 | 339.8484 | 329.0572
1827.5979 | 647.8901 | 344.4065 | 339.7567 | 329.3701
1828.5979 | 647.352 | 344.3551 | 339.4796 | 329.8705
1829.5979 | 645.5427 | 343.8401 | 339.5774 | 329.7476
1830.5979 | 647.0313 | 343.2149 | 339.5534 | 329.4206
1831.5979 | 647.8719 | 342.703 | 339.2525 | 329.5017
1832.5979 | 649.3233 | 342.2542 | 339.2433 | 329.3629
1833.5979 | 648.8552 | 342.2676 | 338.9797 | 329.5214
1834.5979 | 648.2985 | 341.7802 | 338.5028 | 329.3878
1835.5979 | 645.729 | 341.4721 | 338.157 | 329.4531
1836.5979 | 642.9811 | 340.9541 | 339.0157 | 329.2306
1837.5979 | 639.9695 | 340.5981 | 338.6865 | 329.6208
1838.5979 | 639.7859 | 340.6862 | 338.6027 | 329.3658
1839.5979 | 638.9847 | 341.2972 | 338.7912 | 329.1638
1840.5979 | 638.5438 | 341.8811 | 338.782 | 329.2913
1841.5979 | 639.3463 | 341.841 | 338.5811 | 329.5799
1842.5979 | 640.0168 | 341.9884 | 338.5987 | 329.2459
1843.5979 | 640.0653 | 341.8871 | 339.4683 | 329.9914
1844.5979 | 639.8424 | 342.0168 | 340.017 | 331.217
1845.5979 | 639.3728 | 341.863 | 340.3445 | 331.8208
1846.5979 | 639.8405 | 342.7513 | 340.9422 | 331.447
1847.5979 | 640.5418 | 342.8072 | 341.0446 | 331.1829
1848.5979 | 640.0604 | 342.7727 | 341.5721 | 331.2191
1849.5979 | 639.7791 | 343.3078 | 341.704 | 331.9176
1850.5979 | 637.3784 | 343.2409 | 341.9551 | 331.8418
1851.5979 | 637.6915 | 343.567 | 341.5934 | 332.2883
1852.5979 | 638.252 | 344.3335 | 341.7237 | 331.8748
1853.5979 | 641.5648 | 344.2308 | 341.5519 | 332.0191
1854.5979 | 640.6719 | 344.1142 | 340.9405 | 330.9059
1855.5979 | 640.8237 | 343.884 | 340.4492 | 330.4444
1856.5979 | 639.9123 | 343.5876 | 340.4631 | 330.1182
1857.5979 | 637.1411 | 343.9434 | 341.0627 | 330.1719
1858.5979 | 635.8267 | 343.6842 | 341.2209 | 330.378
1859.5979 | 632.1707 | 343.9882 | 340.855 | 330.5779
1860.5979 | 632.3268 | 343.9969 | 341.0791 | 330.482
1861.5979 | 632.6583 | 344.1634 | 341.8354 | 331.2043
1862.5979 | 632.8906 | 343.4522 | 341.7427 | 331.235
1863.5979 | 634.3139 | 342.8156 | 341.4195 | 331.2494
1864.5979 | 634.7679 | 342.4463 | 340.4154 | 330.8013
1865.5979 | 635.0307 | 341.959 | 340.5876 | 329.7318
1866.5979 | 635.9104 | 341.7322 | 340.5515 | 328.7112
1867.5979 | 635.6605 | 341.8137 | 340.9785 | 328.3871
1868.5979 | 635.8877 | 341.7368 | 340.5714 | 328.836
1869.5979 | 636.5438 | 341.4942 | 339.8576 | 329.1998
1870.5979 | 637.0154 | 341.435 | 339.2346 | 329.4409
1871.5979 | 637.1324 | 341.4347 | 339.3495 | 328.5546
1872.5979 | 637.1427 | 341.229 | 339.5515 | 328.0735
1873.5979 | 636.5574 | 340.9535 | 339.4786 | 328.2627
1874.5979 | 637.5203 | 340.5298 | 339.3313 | 328.7494
1875.5979 | 636.1484 | 340.2895 | 338.7145 | 328.9256
1876.5979 | 635.5556 | 340.3917 | 339.0634 | 329.3205
1877.5979 | 635.9637 | 340.2013 | 339.1461 | 329.431
1878.5979 | 634.957 | 339.9903 | 338.6237 | 328.7604
1879.5979 | 633.9963 | 339.945 | 338.1191 | 328.6603
1880.5979 | 632.3653 | 339.4872 | 337.4093 | 328.7795
1881.5979 | 632.515 | 339.4658 | 336.9559 | 328.7697
1882.5979 | 633.2965 | 338.756 | 336.9724 | 328.5343
1883.5979 | 633.3025 | 338.6223 | 336.6086 | 328.4238
1884.5979 | 633.8145 | 339.5456 | 336.1588 | 328.5712
1885.5979 | 631.8111 | 339.2427 | 335.9333 | 328.1771
1886.5979 | 632.2877 | 339.3192 | 335.49 | 328.3984
1887.5979 | 632.7514 | 339.3016 | 335.5156 | 327.5865
1888.5979 | 631.7907 | 339.7015 | 335.459 | 327.0291
1889.5979 | 631.3498 | 339.5062 | 336.0094 | 326.9176
1890.5979 | 630.0308 | 339.5643 | 336.3799 | 327.2735
1891.5979 | 629.3673 | 339.404 | 336.2339 | 326.7051
1892.5979 | 631.6885 | 339.1245 | 336.5177 | 326.6657
1893.5979 | 635.6271 | 338.6502 | 335.6171 | 326.7182
1894.5979 | 636.5648 | 338.0186 | 335.368 | 327.063
1895.5979 | 636.5326 | 337.7 | 335.294 | 326.8824
1896.5979 | 635.5347 | 337.7681 | 335.0696 | 326.9871
1897.5979 | 635.9685 | 337.9131 | 334.9379 | 326.3642
1898.5979 | 636.9346 | 337.958 | 335.2479 | 326.1696
1899.5979 | 638.6489 | 338.4439 | 335.3707 | 325.998
1900.5979 | 638.4369 | 338.2198 | 335.4136 | 325.7244
1901.6135 | 636.2129 | 337.9503 | 335.4697 | 326.1631
1902.5979 | 637.163 | 337.765 | 334.9047 | 325.7981
1903.5979 | 641.235 | 338.0981 | 334.7824 | 325.6531
1904.5979 | 643.8669 | 337.8713 | 334.9399 | 326.4686
1905.5979 | 646.3926 | 339.6276 | 336.4345 | 326.5612
1906.5979 | 649.0606 | 340.5568 | 337.2039 | 328.1403
1907.5979 | 652.5815 | 342.3626 | 338.647 | 329.3809
1908.5979 | 657.1117 | 343.6433 | 340.1885 | 329.8429
1909.5979 | 660.5091 | 345.4953 | 340.712 | 329.7925
1910.5979 | 661.1787 | 345.9638 | 341.6206 | 330.8925
1911.5979 | 659.8254 | 346.3794 | 341.9472 | 330.7811
1912.5979 | 657.5771 | 346.1958 | 342.5301 | 331.0647
1913.5979 | 655.5143 | 345.8014 | 342.6907 | 331.0051
1914.5979 | 655.5905 | 345.2187 | 342.4331 | 330.614
1915.5979 | 653.9187 | 344.8407 | 341.5785 | 330.8331
1916.5979 | 649.9362 | 345.3436 | 340.7892 | 330.3034
1917.5979 | 648.8397 | 344.8203 | 339.8562 | 329.4317
1918.5979 | 649.296 | 344.7891 | 339.5168 | 328.5592
1919.5979 | 653.6281 | 344.8378 | 339.4994 | 328.6994
1920.5979 | 660.2476 | 346.8911 | 340.8388 | 330.1677
1921.5979 | 671.4291 | 349.4135 | 342.6353 | 332.3086
1922.5979 | 685.4067 | 351.1831 | 346.3461 | 335.1228
1923.5979 | 692.8405 | 354.4702 | 348.7288 | 336.3314
1924.5979 | 697.3911 | 356.546 | 350.1657 | 337.9725
1925.5979 | 695.803 | 357.4171 | 351.1616 | 338.7558
1926.5979 | 693.7853 | 357.9079 | 351.2533 | 339.894
1927.5979 | 692.9417 | 359.0692 | 352.7082 | 341.1417
1928.5979 | 694.3136 | 359.2437 | 353.2537 | 341.1885
1929.5979 | 692.3476 | 359.7137 | 354.2682 | 341.8582
1930.5979 | 692.2363 | 359.8165 | 354.2412 | 342.8015
1931.5979 | 690.4805 | 359.7967 | 354.541 | 342.6941
1932.5979 | 690.3905 | 359.5593 | 354.2711 | 342.1809
1933.5979 | 687.6245 | 359.6442 | 355.1257 | 342.9074
1934.5979 | 685.3521 | 359.3115 | 355.1917 | 343.2236
1935.5979 | 685.8131 | 360.3461 | 355.0223 | 343.9782
1936.5979 | 686.762 | 361.2715 | 355.7375 | 344.3473
1937.5979 | 689.8393 | 361.6355 | 355.5645 | 344.1854
1938.5979 | 689.3747 | 362.1045 | 355.3796 | 343.8761
1939.5979 | 689.2334 | 363.2789 | 355.7008 | 343.6841
1940.5979 | 692.8186 | 362.945 | 355.8336 | 343.641
1941.5979 | 694.3961 | 363.0954 | 356.1047 | 344.1698
1942.5979 | 692.7314 | 363.2816 | 356.1032 | 344.4262
1943.5979 | 696.1785 | 363.16 | 356.7076 | 345.0569
1944.5979 | 698.4814 | 363.4759 | 357.5665 | 345.1791
1945.5979 | 699.982 | 364.6618 | 358.6547 | 345.6614
1946.5979 | 699.8628 | 365.031 | 358.8785 | 347.4225
1947.5979 | 698.4964 | 364.8453 | 359.2194 | 347.3921
1948.5979 | 697.7698 | 365.3111 | 358.7147 | 347.0635
1949.5979 | 697.4933 | 365.6184 | 358.2592 | 347.4415
1950.5979 | 701.9792 | 365.7045 | 358.0903 | 347.3586
1951.5979 | 705.4532 | 366.2394 | 358.1648 | 347.1829
1952.5979 | 708.3481 | 367.4252 | 358.965 | 346.6315
1953.5979 | 710.4642 | 367.7297 | 359.381 | 346.3233
1954.5979 | 712.382 | 367.9244 | 360.5793 | 346.3052
1955.5979 | 711.6216 | 367.7301 | 361.063 | 346.3271
1956.5979 | 708.019 | 368.4669 | 361.8437 | 347.3614
1957.5979 | 708.4982 | 368.6943 | 361.6716 | 347.4024
1958.5979 | 712.4077 | 369.7906 | 362.4027 | 347.6107
1959.5979 | 713.072 | 370.1733 | 361.5289 | 347.7481
1960.5979 | 713.0453 | 370.5113 | 361.8141 | 346.9881
1961.5979 | 715.3472 | 370.8999 | 362.1516 | 347.1235
1962.5979 | 715.3175 | 371.2271 | 362.7539 | 347.6767
1963.5979 | 713.5907 | 371.9639 | 362.5678 | 348.8945
1964.5979 | 711.644 | 372.3149 | 363.4225 | 349.0587
1965.5979 | 712.444 | 372.2339 | 363.1492 | 349.752
1966.5979 | 712.4636 | 372.4599 | 363.5082 | 349.5439
1967.5979 | 713.8673 | 372.6019 | 363.8818 | 349.3604
1968.5979 | 718.615 | 373.0805 | 363.8417 | 350.4745
1969.5979 | 718.4248 | 372.9833 | 363.87 | 350.2456
1970.5979 | 716.673 | 372.9287 | 364.0264 | 350.0909
1971.5979 | 714.7051 | 372.5521 | 364.4155 | 350.7973
1972.5979 | 711.6692 | 372.656 | 365.3789 | 351.4306
1973.5979 | 711.602 | 372.213 | 365.7217 | 351.3272
1974.5979 | 711.3447 | 372.48 | 365.813 | 352.193
1975.5979 | 710.8655 | 372.763 | 365.4877 | 352.7116
1976.5979 | 711.3294 | 373.4939 | 365.4785 | 352.255
1977.5979 | 713.7314 | 373.6257 | 365.7174 | 352.5827
1978.5979 | 717.4248 | 373.5242 | 366.0241 | 353.3255
1979.5979 | 720.9465 | 374.0655 | 365.9838 | 354.4256
1980.5979 | 722.1353 | 374.7722 | 366.2433 | 354.9386
1981.5979 | 722.8972 | 374.7165 | 366.5488 | 354.8984
1982.5979 | 727.409 | 374.4882 | 366.62 | 355.4006
1983.5979 | 729.1547 | 374.473 | 366.8965 | 355.7457
1984.5979 | 725.8625 | 374.5576 | 366.7773 | 355.852
1985.5979 | 722.5924 | 374.4718 | 366.9527 | 355.4094
1986.5979 | 720.6902 | 373.6706 | 367.1514 | 355.6965
1987.5979 | 719.2317 | 373.3612 | 366.9495 | 355.4712
1988.5979 | 719.9449 | 373.882 | 366.8087 | 355.0417
1989.5979 | 723.5628 | 375.2086 | 367.1738 | 354.1433
1990.5979 | 723.734 | 375.8146 | 367.3284 | 353.6227
1991.5979 | 721.8097 | 375.5193 | 366.7698 | 354.1128
1992.5979 | 717.5145 | 375.8792 | 366.9154 | 353.6227
1993.5979 | 712.2014 | 375.1993 | 366.7651 | 353.711
1994.5979 | 710.2275 | 374.6296 | 366.4141 | 353.0368
1995.5979 | 709.8556 | 373.8097 | 365.8715 | 353.018
1996.5979 | 711.8188 | 374.1843 | 365.77 | 353.0495
1997.5979 | 714.111 | 373.4677 | 365.5662 | 353.1304
1998.5979 | 715.7703 | 373.2527 | 365.4217 | 353.6011
1999.5979 | 713.2526 | 373.3298 | 365.4895 | 353.9196
2000.5979 | 708.0611 | 373.7262 | 365.4533 | 353.0796
2001.5979 | 704.4554 | 373.7427 | 365.1297 | 352.1696
2002.5979 | 700.3634 | 374.5785 | 365.0067 | 353.0437
2003.5979 | 700.1872 | 374.7038 | 365.3611 | 352.9553
2004.5979 | 700.3919 | 375.0321 | 365.3844 | 354.4987
2005.5979 | 700.3874 | 375.6923 | 365.6617 | 355.552
2006.5979 | 699.0865 | 375.82 | 365.8491 | 354.6699
2007.5979 | 698.3394 | 375.8996 | 365.7155 | 354.0657
2008.5979 | 696.7165 | 376.3294 | 366.1192 | 353.5637
2009.5979 | 696.9562 | 376.6158 | 366.3717 | 354.334
2010.5979 | 698.9129 | 376.2276 | 366.5361 | 354.8563
2011.5979 | 698.776 | 376.5262 | 366.4298 | 354.5068
2012.5979 | 699.4949 | 377.2726 | 366.155 | 354.5739
2013.5979 | 700.907 | 377.1921 | 366.2937 | 355.0861
2014.5979 | 701.3155 | 376.8038 | 365.4709 | 354.5868
2015.5979 | 702.7676 | 377.2632 | 365.5331 | 355.1881
2016.5979 | 705.0988 | 377.4978 | 365.703 | 354.8507
2017.5979 | 707.5624 | 377.7523 | 366.1428 | 355.0515
2018.5979 | 707.7455 | 378.0728 | 365.8658 | 355.8711
2019.5979 | 705.1917 | 377.9842 | 365.6113 | 355.0699
2020.5979 | 702.4066 | 378.0999 | 365.7195 | 354.635
2021.5979 | 702.679 | 377.6806 | 365.6176 | 355.2198
2022.5979 | 702.5203 | 378.0725 | 365.521 | 355.7998
2023.5979 | 699.9459 | 378.3557 | 365.5831 | 354.7522
2024.5979 | 696.3625 | 377.9892 | 365.6322 | 355.2736
2025.5979 | 693.622 | 378.0887 | 365.79 | 355.6577
2026.5979 | 693.4553 | 378.7875 | 366.4026 | 356.67
2027.5979 | 696.0757 | 378.7919 | 367.0408 | 356.848
2028.5979 | 696.5742 | 379.3367 | 367.6239 | 357.2377
2029.5979 | 695.0894 | 379.6894 | 368.3238 | 358.0587
2030.5979 | 696.4209 | 379.3037 | 368.4914 | 358.1436
2031.5979 | 698.6811 | 380.4468 | 370.263 | 358.7767
2032.5979 | 698.8991 | 380.3025 | 370.1807 | 360.0406
2033.5979 | 702.61 | 380.5484 | 370.935 | 361.408
2034.5979 | 706.4408 | 381.1215 | 371.7772 | 361.5663
2035.5979 | 708.2288 | 381.5829 | 372.2319 | 362.0809
2036.5979 | 710.2075 | 382.2618 | 372.1675 | 361.6996
2037.5979 | 713.1442 | 382.4318 | 371.9852 | 360.8108
2038.5979 | 712.3569 | 382.5071 | 372.3109 | 360.7592
2039.5979 | 715.5274 | 382.1186 | 372.5837 | 361.305
2040.5979 | 715.2063 | 382.3716 | 372.5385 | 360.6261
2041.5979 | 713.1902 | 382.5981 | 372.8118 | 360.0225
2042.5979 | 714.3172 | 382.8858 | 372.7487 | 359.7892
2043.5979 | 717.5645 | 382.857 | 373.3612 | 360.9575
2044.5979 | 718.1112 | 382.8644 | 373.4637 | 361.6639
2045.5979 | 714.7959 | 383.0049 | 373.9115 | 362.081
2046.5979 | 713.0901 | 382.8157 | 374.1544 | 361.9135
2047.5979 | 710.841 | 382.7386 | 374.448 | 361.4979
2048.5979 | 709.643 | 382.6352 | 374.3718 | 361.6422
2049.5979 | 710.4279 | 383.1268 | 374.0315 | 361.6936
2050.5979 | 713.2414 | 382.725 | 373.8647 | 362.6965
2051.5979 | 714.6121 | 383.3047 | 374.5122 | 362.5559
2052.5979 | 711.1931 | 383.2124 | 374.6355 | 362.4015
2053.5979 | 709.664 | 383.106 | 374.761 | 362.4275
2054.5979 | 706.4961 | 383.3394 | 374.5567 | 362.2885
2055.5979 | 705.3752 | 382.6832 | 375.0324 | 362.1765
2056.5979 | 704.1615 | 382.2396 | 375.2814 | 362.5038
2057.5979 | 705.0438 | 382.0274 | 375.0876 | 362.4989
2058.5979 | 704.4901 | 381.8385 | 374.6531 | 361.8457
2059.5979 | 704.9535 | 382.2096 | 374.005 | 361.7443
2060.5979 | 705.4053 | 382.2879 | 373.6336 | 361.1293
2061.5979 | 708.2394 | 382.1021 | 373.0901 | 361.3362
2062.5979 | 711.0301 | 382.3105 | 372.9576 | 360.6717
2063.5979 | 710.2383 | 382.85 | 372.6941 | 360.0814
2064.5979 | 710.1315 | 383.3718 | 372.7268 | 360.0173
2065.5979 | 711.0132 | 383.3108 | 372.5807 | 360.3483
2066.5979 | 716.4113 | 383.2624 | 372.2766 | 360.0448
2067.5979 | 718.8037 | 383.5386 | 372.6818 | 360.1691
2068.5979 | 720.2606 | 383.2112 | 372.6583 | 360.8533
2069.5979 | 717.6034 | 383.2835 | 372.8512 | 360.9652
2070.5979 | 715.2285 | 383.2442 | 373.7837 | 361.1963
2071.5979 | 713.2908 | 383.1592 | 373.7838 | 361.6295
2072.5979 | 711.6935 | 383.1123 | 374.3377 | 362.9665
2073.5979 | 710.2888 | 383.3628 | 374.1664 | 363.5995
2074.5979 | 710.6346 | 383.3873 | 374.321 | 364.6182
2075.5979 | 712.5271 | 383.5346 | 374.2394 | 365.2401
2076.5979 | 711.8272 | 383.9338 | 375.1453 | 365.7232
2077.5979 | 712.2939 | 384.2967 | 374.7235 | 365.0653
2078.5979 | 711.6639 | 384.3545 | 374.1681 | 364.9263
2079.5979 | 711.5499 | 384.1415 | 373.5943 | 364.5165
2080.5979 | 710.736 | 383.9937 | 372.8998 | 365.0567
2081.5979 | 708.2696 | 384.0837 | 372.2578 | 364.8896
2082.5979 | 709.1138 | 383.7976 | 371.6592 | 364.6187
2083.5979 | 711.274 | 383.4238 | 371.6454 | 364.4131
2084.5979 | 707.6554 | 383.3437 | 371.5939 | 364.6408
2085.5979 | 704.3999 | 383.4033 | 371.3924 | 364.9396
2086.5979 | 704.2209 | 383.5978 | 371.1267 | 364.3009
2087.5979 | 704.754 | 383.0962 | 370.9386 | 363.6451
2088.5979 | 706.0362 | 383.0439 | 370.1739 | 363.1066
2089.5979 | 706.2867 | 382.3795 | 369.587 | 362.7533
2090.5979 | 708.532 | 382.1165 | 369.5909 | 362.6281
2091.5979 | 709.6851 | 381.6663 | 369.7645 | 362.5394
2092.5979 | 710.4918 | 382.1613 | 370.5541 | 362.5209
2093.5979 | 709.8552 | 382.5903 | 370.8749 | 362.6306
2094.5979 | 709.4997 | 382.856 | 371.2836 | 363.5306
2095.5979 | 707.7937 | 382.8391 | 371.5051 | 363.5541
2096.5979 | 705.6432 | 383.0512 | 371.9365 | 363.2546
2097.5979 | 704.7593 | 382.9932 | 372.3072 | 363.6332
2098.5979 | 702.9032 | 383.2148 | 372.5103 | 363.393
2099.5979 | 700.8917 | 382.8493 | 372.6976 | 363.5102
2100.5979 | 701.8255 | 383.2659 | 373.0269 | 363.4377
2101.5979 | 703.5201 | 383.0698 | 373.0303 | 363.484
2102.5979 | 705.3373 | 382.9552 | 373.3391 | 363.8991
2103.5979 | 702.7408 | 382.7904 | 373.6341 | 363.6245
2104.5979 | 700.9993 | 382.6854 | 373.5689 | 363.6848
2105.5979 | 700.655 | 382.6252 | 373.1777 | 363.5113
2106.5979 | 699.4997 | 382.2196 | 373.4334 | 363.3794
2107.5979 | 699.8548 | 382.0816 | 373.3082 | 362.9847
2108.5979 | 700.7026 | 381.9983 | 373.1438 | 363.6983
2109.5979 | 700.615 | 381.8738 | 373.0589 | 363.5532
2110.5979 | 699.2544 | 381.8574 | 373.6808 | 364.2158
2111.5979 | 698.7741 | 381.9711 | 374.3075 | 364.2275
2112.5979 | 701.0546 | 382.6464 | 374.4285 | 365.3485
2113.5979 | 703.9208 | 383.4418 | 374.6071 | 365.981
2114.5979 | 708.7911 | 383.4328 | 374.5383 | 366.1202
2115.5979 | 707.95 | 383.6227 | 374.9785 | 367.2902
2116.5979 | 708.9962 | 383.5488 | 374.5539 | 367.201
2117.5979 | 711.2131 | 383.8275 | 374.9042 | 366.8699
2118.5979 | 712.2897 | 383.6737 | 374.4 | 366.341
2119.5979 | 710.0079 | 383.6364 | 373.8396 | 366.0254
2120.5979 | 706.7304 | 383.9349 | 374.0022 | 365.4681
2121.5979 | 706.2896 | 384.5323 | 374.0477 | 364.77
2122.5979 | 710.4672 | 384.353 | 373.6147 | 364.8685
2123.5979 | 713.4149 | 384.2664 | 373.3755 | 364.745
2124.5979 | 714.4134 | 384.1251 | 373.4151 | 364.3095
2125.5979 | 715.9912 | 383.8933 | 373.4567 | 364.473
2126.5979 | 720.0739 | 383.6084 | 373.7714 | 364.8818
2127.5979 | 720.8931 | 383.4689 | 373.7614 | 364.7907
2128.5979 | 719.0656 | 383.4651 | 374.2562 | 364.4152
2129.5979 | 716.4473 | 382.9864 | 374.2239 | 364.0247
2130.5979 | 712.0987 | 382.9571 | 374.2057 | 363.814
2131.5979 | 711.2123 | 382.9369 | 374.2842 | 363.0909
2132.5979 | 709.8942 | 383.3678 | 374.1653 | 364.4086
2133.5979 | 709.6839 | 383.4924 | 374.6189 | 364.4614
2134.5979 | 709.4984 | 383.3742 | 374.5165 | 365.1994
2135.5979 | 710.75 | 383.3496 | 374.5161 | 365.4533
2136.5979 | 709.8974 | 383.437 | 374.3272 | 364.8855
2137.5979 | 711.5302 | 383.4205 | 374.2678 | 364.5488
2138.5979 | 709.8985 | 383.3944 | 374.6427 | 364.3956
2139.5979 | 708.5355 | 383.4568 | 375.2236 | 365.1296
2140.5979 | 709.7026 | 383.0266 | 375.2715 | 365.2459
2141.5979 | 710.5626 | 383.1139 | 375.5832 | 365.4516
2142.5979 | 711.4288 | 383.0822 | 375.2024 | 365.8108
2143.5979 | 711.2275 | 382.8215 | 375.4342 | 365.7198
2144.5979 | 712.9546 | 382.2695 | 375.2174 | 365.4381
2145.5979 | 713.5154 | 381.9389 | 374.8132 | 365.3076
2146.5979 | 716.3474 | 382.1762 | 374.9751 | 365.5288
2147.5979 | 717.2332 | 382.3942 | 374.4471 | 366.1418
2148.5979 | 716.744 | 382.3309 | 374.1367 | 366.5278
2149.5979 | 715.4148 | 382.3366 | 373.9963 | 366.6456
2150.5979 | 716.5323 | 382.7571 | 374.7489 | 366.7153
2151.5979 | 718.9437 | 382.6857 | 374.7916 | 366.8943
2152.5979 | 722.3824 | 382.9013 | 374.6645 | 366.3084
2153.5979 | 722.2967 | 383.1597 | 374.8519 | 366.2917
2154.5979 | 723.5732 | 383.1307 | 375.348 | 366.478
2155.5979 | 725.0569 | 383.0894 | 375.217 | 366.3544
2156.5979 | 726.5212 | 383.0061 | 375.5723 | 366.3867
2157.6135 | 726.7577 | 383.1644 | 375.6038 | 366.0886
2158.5979 | 728.4194 | 382.5857 | 375.3322 | 366.7531
2159.5979 | 726.5633 | 382.5123 | 376.2823 | 367.4009
2160.5979 | 724.8599 | 382.8798 | 375.965 | 367.183
2161.5979 | 723.3185 | 382.7485 | 376.8112 | 367.2825
2162.5979 | 723.5791 | 382.6125 | 376.3017 | 366.8695
2163.5979 | 720.2686 | 382.8288 | 376.0676 | 367.3382
2164.5979 | 716.2908 | 383.0556 | 376.4185 | 367.3897
2165.5979 | 713.2324 | 383.197 | 376.8452 | 366.9442
2166.5979 | 707.9897 | 383.2159 | 376.8954 | 366.483
2167.5979 | 707.2178 | 384.5456 | 376.7355 | 366.3037
2168.5979 | 706.2593 | 384.9931 | 376.589 | 366.6424
2169.5979 | 710.0033 | 385.0786 | 376.8701 | 367.8277
2170.5979 | 714.1083 | 385.1675 | 377.194 | 368.1127
2171.5979 | 717.5236 | 385.241 | 378.1411 | 368.829
2172.5979 | 716.3085 | 385.2306 | 377.8579 | 368.824
2173.5979 | 712.1673 | 385.1755 | 377.9823 | 369.2804
2174.5979 | 713.952 | 384.8482 | 378.1534 | 370.6242
2175.5979 | 719.3467 | 384.8651 | 378.3184 | 370.5721
2176.5979 | 719.8267 | 384.4586 | 377.8052 | 370.939
2177.5979 | 722.3473 | 384.7307 | 378.056 | 370.7857
2178.5979 | 725.5741 | 384.9607 | 378.7427 | 371.67
2179.5979 | 728.9973 | 384.9277 | 380.1487 | 371.6744
2180.5979 | 730.6701 | 385.0222 | 379.9908 | 372.0887
2181.5979 | 732.8617 | 384.7746 | 379.714 | 371.9614
2182.5979 | 733.186 | 385.5279 | 379.6552 | 372.3222
2183.5979 | 731.4656 | 385.4778 | 379.6839 | 371.9374
2184.5979 | 728.9442 | 385.4839 | 379.249 | 372.2258
2185.5979 | 726.5539 | 385.4203 | 378.9378 | 372.3345
2186.5979 | 723.2887 | 385.4675 | 378.9484 | 372.2043
2187.5979 | 721.984 | 385.6667 | 378.941 | 372.0664
2188.5979 | 717.7164 | 386.0873 | 379.064 | 371.6705
2189.5979 | 715.9692 | 386.1345 | 379.5068 | 372.1314
2190.5979 | 715.1129 | 386.4714 | 379.8326 | 371.9534
2191.5979 | 712.9467 | 387.1957 | 380.4985 | 372.3402
2192.5979 | 710.7565 | 387.8305 | 380.6501 | 372.4567
2193.5979 | 708.4113 | 387.978 | 380.8447 | 373.8793
2194.5979 | 704.9974 | 388.2558 | 381.4115 | 373.8292
2195.5979 | 703.1565 | 388.4281 | 380.9502 | 374.1402
2196.5979 | 705.7653 | 388.2605 | 380.4715 | 373.9744
2197.5979 | 709.1762 | 388.0114 | 380.3735 | 374.2323
2198.5979 | 710.4942 | 387.6633 | 380.1934 | 374.4502
2199.5979 | 710.7951 | 387.541 | 380.2604 | 374.6037
2200.5979 | 710.5387 | 387.1559 | 380.9935 | 374.5229
2201.6135 | 713.1563 | 386.9458 | 381.0032 | 375.0009
2202.5979 | 714.6144 | 386.5012 | 380.8505 | 374.7607
2203.5979 | 713.7822 | 386.4322 | 381.459 | 374.7563
2204.5979 | 714.4901 | 386.378 | 381.8434 | 375.1054
2205.5979 | 717.2188 | 386.3248 | 381.6006 | 374.5107
2206.5979 | 720.799 | 386.2349 | 381.6798 | 375.2721
2207.5979 | 719.6159 | 386.0769 | 381.7025 | 375.1147
2208.5979 | 720.5065 | 386.1271 | 381.4185 | 374.7391
2209.5979 | 725.5758 | 386.247 | 381.2555 | 375.3852
2210.5979 | 730.0915 | 386.4622 | 381.7704 | 375.2566
2211.5979 | 733.5742 | 385.9963 | 381.5287 | 375.0671
2212.5979 | 732.9307 | 385.9603 | 381.5645 | 375.1084
2213.5979 | 732.9654 | 386.1259 | 382.037 | 375.1715
2214.5979 | 737.0921 | 385.9595 | 382.3679 | 375.0227
2215.5979 | 740.936 | 385.9783 | 382.6007 | 374.9142
2216.5979 | 741.6692 | 385.963 | 382.7656 | 375.137
2217.5979 | 741.6667 | 385.9599 | 382.6256 | 375.838
2218.5979 | 740.0979 | 385.7706 | 382.6788 | 375.8308
2219.5979 | 736.958 | 385.6117 | 382.7314 | 375.67
2220.5979 | 731.2563 | 386.3296 | 382.6097 | 375.7717
2221.5979 | 725.367 | 386.1595 | 382.423 | 375.4409
2222.5979 | 721.1527 | 386.3056 | 382.0322 | 375.2048
2223.5979 | 719.2254 | 386.5384 | 381.7996 | 375.0451
2224.5979 | 717.5646 | 387.146 | 381.6021 | 375.7583
2225.5979 | 717.0304 | 387.3505 | 381.996 | 375.8496
2226.5979 | 713.8597 | 387.3838 | 381.9093 | 375.2603
2227.5979 | 712.6658 | 387.4108 | 382.2464 | 375.0334
2228.5979 | 711.8996 | 387.8132 | 382.2523 | 374.227
2229.5979 | 711.7901 | 387.6485 | 382.0163 | 374.3258
2230.5979 | 710.7756 | 387.5509 | 382.0033 | 374.1973
2231.5979 | 710.7915 | 387.3144 | 381.9719 | 374.4218
2232.5979 | 711.085 | 387.4285 | 381.8335 | 374.1445
2233.5979 | 710.1135 | 387.0768 | 381.5165 | 374.0315
2234.5979 | 709.3607 | 387.243 | 381.177 | 373.6672
2235.5979 | 708.8592 | 386.9555 | 380.8616 | 374.3023
2236.5979 | 707.377 | 386.8618 | 380.9651 | 373.7841
2237.5979 | 707.5319 | 387.3661 | 382.1285 | 373.6809
2238.5979 | 707.9645 | 387.4905 | 382.6037 | 374.311
2239.5979 | 708.4861 | 387.5252 | 382.9063 | 374.8498
2240.5979 | 708.4893 | 387.7663 | 382.9885 | 375.2241
2241.5979 | 707.2782 | 387.8314 | 383.5098 | 375.4395
2242.5979 | 704.4824 | 387.8983 | 383.63 | 376.0315
2243.5979 | 702.4668 | 388.1541 | 383.8418 | 376.1227
2244.5979 | 703.4499 | 388.6453 | 383.8706 | 376.7604
2245.5979 | 703.3987 | 388.6118 | 384.1438 | 376.8437
2246.5979 | 702.612 | 388.6996 | 384.6721 | 377.0101
2247.5979 | 701.122 | 388.9651 | 384.4767 | 377.4719
2248.5979 | 700.3489 | 389.1231 | 385.0151 | 378.2447
2249.5979 | 698.7887 | 389.6803 | 384.9387 | 378.7843
2250.5979 | 698.145 | 390.1974 | 384.9691 | 379.0347
2251.5979 | 699.5122 | 390.6574 | 385.5282 | 378.4998
2252.5979 | 702.7295 | 391.3465 | 386.0786 | 378.9183
2253.5979 | 706.5586 | 391.5956 | 385.6853 | 378.5679
2254.5979 | 709.214 | 391.7003 | 385.2399 | 379.2899
2255.5979 | 709.5718 | 392.1392 | 385.6709 | 379.1596
2256.5979 | 708.6965 | 392.4773 | 385.6282 | 379.0076
2257.5979 | 707.1739 | 392.7782 | 385.3846 | 379.3573
2258.5979 | 706.5069 | 393.6906 | 385.9478 | 379.9582
2259.5979 | 708.74 | 394.1052 | 386.345 | 379.8338
2260.5979 | 709.3295 | 394.3835 | 386.5469 | 380.2953
2261.5979 | 710.4438 | 394.3612 | 386.6977 | 380.7086
2262.5979 | 710.6016 | 394.7084 | 386.655 | 381.323
2263.5979 | 713.2975 | 395.0683 | 386.804 | 381.6301
2264.5979 | 713.5035 | 395.5239 | 387.3398 | 382.401
2265.5979 | 710.8908 | 395.5735 | 387.1246 | 382.6759
2266.5979 | 710.3125 | 395.8471 | 386.8344 | 382.814
2267.5979 | 709.0514 | 396.3657 | 386.7054 | 382.4714
2268.5979 | 709.8187 | 396.5553 | 386.6951 | 382.9483
2269.5979 | 715.0973 | 396.5095 | 387.0846 | 382.9401
2270.5979 | 715.5462 | 396.5138 | 387.7102 | 383.1418
2271.5979 | 718.7286 | 396.4786 | 388.1921 | 383.3018
2272.5979 | 717.0707 | 396.3879 | 388.1707 | 382.8775
2273.5979 | 713.7071 | 396.7811 | 388.3746 | 382.4291
2274.5979 | 712.4842 | 396.9538 | 388.6292 | 382.9068
2275.5979 | 712.9314 | 396.93 | 389.0243 | 382.5938
2276.5979 | 713.5649 | 396.8828 | 389.0637 | 382.2663
2277.5979 | 714.9383 | 397.2706 | 389.1626 | 382.114
2278.5979 | 715.2549 | 397.3504 | 389.5695 | 382.4152
2279.5979 | 715.2097 | 397.1092 | 389.7084 | 382.6411
2280.5979 | 714.989 | 396.9008 | 389.6234 | 382.5698
2281.5979 | 714.4007 | 396.8587 | 389.5995 | 382.7061
2282.5979 | 714.6851 | 396.957 | 390.2338 | 382.5221
2283.5979 | 714.4289 | 397.3011 | 390.5585 | 382.6468
2284.5979 | 712.6304 | 397.0375 | 390.4381 | 383.0923
2285.5979 | 711.726 | 397.1809 | 390.4285 | 383.2317
2286.5979 | 710.9153 | 397.1847 | 390.2015 | 383.2588
2287.5979 | 709.4405 | 397.2238 | 389.8648 | 382.9718
2288.5979 | 707.9138 | 397.0795 | 389.874 | 382.3038
2289.5979 | 707.7966 | 396.9462 | 389.7082 | 381.9181
2290.5979 | 708.7631 | 396.9902 | 390.1527 | 381.5495
2291.5979 | 708.463 | 396.8728 | 389.4633 | 381.1826
2292.5979 | 706.749 | 397.1604 | 389.1742 | 380.5718
2293.5979 | 705.2957 | 397.1133 | 388.8145 | 380.0539
2294.5979 | 705.0044 | 396.9915 | 388.8308 | 379.4969
2295.5979 | 708.3236 | 396.9571 | 389.0625 | 379.5957
2296.5979 | 713.1628 | 397.0821 | 388.8089 | 379.5087
2297.5979 | 713.9132 | 396.8615 | 389.1282 | 379.4937
2298.5979 | 714.1161 | 396.5772 | 389.475 | 379.7867
2299.5979 | 715.6185 | 396.3973 | 389.5257 | 379.9103
2300.5979 | 714.8873 | 396.4564 | 389.8965 | 379.9759
2301.5979 | 715.6912 | 396.4132 | 390.3868 | 380.272
2302.6135 | 718.2868 | 396.1423 | 390.2132 | 380.7092
2303.5979 | 720.1247 | 396.088 | 390.0131 | 380.8681
2304.6135 | 720.0536 | 396.1809 | 390.0841 | 381.6516
2305.5979 | 718.9912 | 396.6853 | 390.2227 | 382.0931
2306.5979 | 719.4517 | 396.7401 | 390.2669 | 382.6706
2307.5979 | 720.4903 | 396.5947 | 390.1734 | 382.7837
2308.5979 | 718.2225 | 396.5729 | 390.2253 | 382.4472
2309.5979 | 716.4246 | 396.6562 | 389.9163 | 382.8831
2310.5979 | 713.7175 | 396.9689 | 390.0321 | 383.091
2311.5979 | 714.3292 | 396.9418 | 390.5795 | 383.7686
2312.5979 | 715.7756 | 397.3194 | 390.7903 | 384.311
2313.5979 | 716.0417 | 397.6806 | 391.0545 | 385.1347
2314.5979 | 716.7862 | 397.3587 | 391.2943 | 385.0296
2315.5979 | 716.5132 | 397.6314 | 391.2437 | 385.3063
2316.5979 | 714.6253 | 397.8247 | 391.651 | 385.3453
2317.5979 | 714.8431 | 398.1313 | 391.696 | 386.1678
2318.5979 | 715.9433 | 398.0278 | 391.4423 | 385.7677
2319.5979 | 715.1538 | 398.0179 | 391.8024 | 386.3082
2320.5979 | 715.7078 | 398.3845 | 392.35 | 386.0751
2321.5979 | 716.6112 | 398.6633 | 392.3821 | 386.5186
2322.5979 | 721.0991 | 398.2733 | 392.2202 | 386.4979
2323.5979 | 724.753 | 398.2036 | 392.9444 | 387.2893
2324.5979 | 726.6816 | 398.1294 | 392.6829 | 387.2953
2325.5979 | 725.6541 | 398.0288 | 392.5271 | 386.3397
2326.5979 | 722.5043 | 397.8046 | 392.6059 | 386.3995
2327.5979 | 719.0158 | 397.7812 | 392.8655 | 386.4244
2328.5979 | 715.5871 | 397.8786 | 393.1362 | 387.1552
2329.5979 | 713.1653 | 397.7392 | 393.2015 | 386.7951
2330.5979 | 710.5746 | 397.1726 | 392.9465 | 387.4891
2331.5979 | 708.2799 | 397.273 | 392.9481 | 388.1997
2332.5979 | 708.952 | 397.2482 | 392.7482 | 387.7379
2333.5979 | 710.0602 | 397.3435 | 392.3645 | 387.9654
2334.5979 | 713.7375 | 397.7274 | 392.3745 | 388.481
2335.5979 | 715.4736 | 398.05 | 393.4628 | 388.2499
2336.5979 | 716.2539 | 397.77 | 393.3154 | 388.509
2337.5979 | 716.0394 | 397.7579 | 393.0447 | 388.1364
2338.5979 | 715.4777 | 397.7078 | 392.9863 | 388.2728
2339.5979 | 712.6899 | 397.5278 | 393.1846 | 387.9664
2340.5979 | 711.5226 | 397.5226 | 393.2033 | 387.735
2341.5979 | 713.3031 | 397.5566 | 393.2921 | 387.7592
2342.5979 | 714.4525 | 397.9209 | 393.0884 | 387.8631
2343.5979 | 712.8151 | 397.8762 | 393.5718 | 388.4094
2344.5979 | 713.9093 | 398.235 | 393.7072 | 389.4996
2345.5979 | 715.1974 | 398.5747 | 394.3477 | 389.9113
2346.5979 | 716.3068 | 399.2005 | 394.7024 | 390.1161
2347.5979 | 718.0013 | 399.8318 | 395.7122 | 390.3795
2348.5979 | 719.0876 | 400.3748 | 396.2673 | 390.7902
2349.5979 | 719.5236 | 400.2476 | 396.3428 | 390.7178
2350.5979 | 720.8775 | 400.3189 | 396.4351 | 391.4291
2351.5979 | 725.4675 | 400.5871 | 396.9092 | 391.2408
2352.5979 | 728.0807 | 400.4144 | 397.2936 | 392.2727
2353.5979 | 730.1733 | 400.502 | 397.4407 | 391.8685
2354.5979 | 728.7418 | 400.77 | 397.5854 | 392.6065
2355.5979 | 726.5995 | 401.5409 | 398.1798 | 393.1486
2356.5979 | 728.8852 | 402.298 | 398.7023 | 392.8819
2357.5979 | 732.3415 | 402.5838 | 399.1687 | 393.7664
2358.5979 | 735.8258 | 402.9366 | 399.7707 | 394.5012
2359.5979 | 737.2504 | 403.0647 | 399.7156 | 394.3425
2360.5979 | 735.1264 | 403.0861 | 399.9513 | 394.4877
2361.5979 | 732.9675 | 403.1157 | 400.3859 | 394.7559
2362.5979 | 730.6 | 403.8502 | 401.325 | 395.3991
2363.5979 | 729.9787 | 404.2703 | 401.4471 | 396.2742
2364.6135 | 731.856 | 404.3417 | 401.2796 | 396.9549
2365.5979 | 731.0657 | 404.5072 | 401.3277 | 396.7387
2366.6135 | 729.135 | 404.669 | 401.8442 | 396.5792
2367.5979 | 729.1504 | 404.6007 | 401.9098 | 396.1506
2368.6135 | 726.6052 | 404.9462 | 403.1547 | 396.0241
2369.5979 | 725.8604 | 406.3299 | 403.4472 | 397.1725
2370.5979 | 725.3716 | 406.5721 | 403.9541 | 397.7074
2371.5979 | 723.8688 | 406.6011 | 404.0804 | 398.2166
2372.5979 | 721.7213 | 406.882 | 404.4585 | 398.4979
2373.5979 | 718.9777 | 406.9168 | 404.7394 | 398.4059
2374.5979 | 716.9806 | 407.1203 | 405.289 | 398.3264
2375.5979 | 717.9554 | 407.2169 | 404.9464 | 397.5942
2376.5979 | 715.2379 | 407.5251 | 404.6174 | 398.657
2377.5979 | 711.2745 | 407.6403 | 404.6334 | 398.4168
2378.5979 | 709.6981 | 407.8274 | 404.8923 | 397.7673
2379.5979 | 708.4504 | 408.087 | 404.7935 | 397.5521
2380.5979 | 707.7556 | 408.732 | 404.6676 | 397.2021
2381.5979 | 708.7387 | 408.662 | 404.4132 | 396.4845
2382.5979 | 708.7965 | 408.8685 | 404.4549 | 396.2243
2383.5979 | 708.3462 | 408.8854 | 404.5522 | 396.2042
2384.5979 | 707.1159 | 409.3553 | 404.22 | 396.3294
2385.5979 | 708.5386 | 409.5454 | 404.2997 | 397.4024
2386.5979 | 709.1625 | 409.6368 | 404.1508 | 398.0556
2387.5979 | 710.4008 | 409.3126 | 403.6447 | 398.3108
2388.5979 | 712.611 | 409.6197 | 403.4065 | 398.3149
2389.5979 | 712.5593 | 409.2605 | 402.988 | 398.0372
2390.5979 | 712.3214 | 408.9392 | 402.4171 | 398.7814
2391.5979 | 712.5982 | 408.5587 | 402.1363 | 398.0622
2392.5979 | 710.9076 | 408.3407 | 402.6296 | 398.8996
2393.5979 | 708.4015 | 407.8514 | 402.386 | 399.1285
2394.5979 | 705.6274 | 407.7512 | 401.9624 | 398.6834
2395.5979 | 705.2116 | 407.9533 | 402.5705 | 398.3849
2396.5979 | 703.665 | 407.6489 | 402.3609 | 398.2065
2397.5979 | 701.8959 | 407.8093 | 402.4478 | 397.7871
2398.5979 | 699.9321 | 408.0994 | 402.3909 | 397.5574
2399.5979 | 700.3347 | 407.7286 | 402.5278 | 397.7958
2400.5979 | 700.481 | 407.3591 | 402.3215 | 396.9505
2401.5979 | 702.1504 | 407.3284 | 401.8053 | 397.2293
2402.5979 | 703.2466 | 407.4348 | 402.0021 | 397.3373
2403.5979 | 703.1231 | 406.7741 | 401.935 | 396.7837
2404.5979 | 701.9535 | 406.6345 | 402.1029 | 396.3381
2405.5979 | 702.1134 | 406.8858 | 402.3653 | 396.3864
2406.5979 | 703.3188 | 406.8043 | 402.4698 | 395.7785
2407.5979 | 706.1104 | 407.3668 | 403.0765 | 395.9605
2408.5979 | 707.7212 | 407.599 | 403.3615 | 396.366
2409.5979 | 707.427 | 407.27 | 402.8575 | 396.2649
2410.5979 | 709.0571 | 407.5232 | 402.5318 | 395.5385
2411.5979 | 710.2814 | 407.4027 | 402.3286 | 395.4946
2412.5979 | 711.2225 | 407.2073 | 402.5206 | 394.9858
2413.5979 | 711.6875 | 407.088 | 402.2391 | 394.6571
2414.5979 | 710.7933 | 407.189 | 402.0924 | 394.1725
2415.5979 | 709.5003 | 407.1029 | 402.2311 | 394.5745
2416.5979 | 706.7839 | 406.8626 | 401.945 | 394.2995
2417.5979 | 705.1079 | 406.9367 | 402.2026 | 394.546
2418.5979 | 706.0995 | 406.8184 | 402.0533 | 395.3046
2419.5979 | 709.5325 | 406.4761 | 401.6822 | 396.2007
2420.5979 | 709.2742 | 406.4766 | 401.8857 | 395.5706
2421.5979 | 709.3609 | 406.5227 | 401.7464 | 394.9622
2422.5979 | 710.0185 | 406.7837 | 401.4557 | 394.9059
2423.5979 | 712.4997 | 406.9065 | 401.5144 | 394.6394
2424.5979 | 714.6856 | 407.0509 | 401.1597 | 394.45
2425.5979 | 715.9284 | 407.2513 | 400.9303 | 394.4125
2426.5979 | 720.5834 | 407.2948 | 400.8808 | 393.9958
2427.5979 | 723.3885 | 407.1513 | 400.8803 | 394.7579
2428.5979 | 722.3481 | 407.1264 | 400.7876 | 395.5377
2429.5979 | 721.8491 | 406.8342 | 400.6474 | 395.5495
2430.5979 | 720.9305 | 406.7111 | 400.3514 | 395.6198
2431.5979 | 720.3689 | 407.024 | 400.0655 | 395.994
2432.5979 | 720.3346 | 407.025 | 400.7166 | 397.2671
2433.5979 | 717.8195 | 407.1513 | 400.8912 | 397.4125
2434.6135 | 714.2715 | 407.7386 | 400.9162 | 397.3629
2435.5979 | 712.6141 | 407.9659 | 400.9985 | 397.2097
2436.5979 | 711.3179 | 408.2899 | 400.7776 | 396.9135
2437.5979 | 711.3355 | 408.8139 | 400.54 | 396.331
2438.5979 | 712.7167 | 408.8705 | 400.7348 | 396.2316
2439.5979 | 714.7109 | 408.6288 | 400.5648 | 396.1125
2440.5979 | 715.0082 | 408.6538 | 401.083 | 395.9673
2441.5979 | 714.6208 | 408.2962 | 400.9576 | 396.0867
2442.5979 | 714.0841 | 407.6349 | 400.6463 | 395.9173
2443.5979 | 714.2437 | 407.1475 | 400.1864 | 395.349
2444.5979 | 713.5223 | 407.0387 | 399.7282 | 395.0409
2445.5979 | 714.1523 | 406.7288 | 399.5899 | 395.1592
2446.5979 | 715.7817 | 406.8416 | 399.8501 | 395.9729
2447.5979 | 717.0954 | 407.2253 | 400.4059 | 395.882
2448.5979 | 717.7901 | 407.1268 | 400.8709 | 396.1096
2449.5979 | 720.044 | 406.9557 | 400.7455 | 396.4393
2450.5979 | 721.0379 | 406.8233 | 400.563 | 395.9635
2451.5979 | 720.9166 | 406.7367 | 400.5389 | 396.1267
2452.5979 | 722.8951 | 406.2946 | 400.7513 | 396.0317
2453.5979 | 723.8644 | 405.8225 | 400.5201 | 395.5942
2454.5979 | 723.4696 | 405.6191 | 400.8259 | 396.2105
2455.5979 | 722.3896 | 405.6144 | 401.4252 | 396.3934
2456.5979 | 722.0509 | 405.7892 | 401.2117 | 396.2809
2457.5979 | 721.2409 | 405.8599 | 401.0926 | 395.9177
2458.5979 | 721.4034 | 405.6431 | 401.2691 | 396.2084
2459.5979 | 721.3426 | 405.7357 | 401.5463 | 397.3176
2460.5979 | 721.5694 | 405.8306 | 401.4021 | 397.0857
2461.5979 | 723.0698 | 406.0987 | 401.5704 | 397.1638
2462.5979 | 722.5399 | 405.8109 | 402.2299 | 397.1936
2463.5979 | 720.8769 | 405.7031 | 401.8256 | 397.077
2464.5979 | 718.8122 | 406.2059 | 401.8949 | 397.3695
2465.5979 | 718.1655 | 406.58 | 401.943 | 397.7183
2466.5979 | 717.7975 | 406.8295 | 402.317 | 397.6123
2467.5979 | 717.1292 | 406.2504 | 401.7179 | 397.7586
2468.5979 | 717.0924 | 406.0944 | 401.2982 | 397.4724
2469.5979 | 717.1747 | 406.0674 | 401.432 | 396.8814
2470.5979 | 716.4039 | 406.0994 | 401.0789 | 396.5308
2471.5979 | 715.5111 | 406.0051 | 400.9525 | 396.4936
2472.5979 | 716.5652 | 405.7446 | 400.5609 | 396.0745
2473.5979 | 718.2489 | 405.7853 | 400.3993 | 396.0893
2474.5979 | 719.9144 | 405.7912 | 400.1419 | 395.4501
2475.5979 | 720.6092 | 405.7556 | 399.7934 | 394.9854
2476.5979 | 722.4757 | 406.4505 | 399.6207 | 395.0125
2477.5979 | 723.2544 | 406.4564 | 399.7123 | 395.1494
2478.5979 | 722.4197 | 406.4501 | 400.3223 | 395.5158
2479.5979 | 723.3427 | 406.3347 | 400.8827 | 395.922
2480.5979 | 724.9221 | 406.3686 | 400.6982 | 395.9602
2481.5979 | 729.4141 | 406.9605 | 400.7372 | 396.3514
2482.5979 | 733.957 | 406.6542 | 401.0712 | 396.7159
2483.5979 | 735.2837 | 406.5385 | 401.5942 | 396.9954
2484.6135 | 733.3246 | 406.4408 | 401.7973 | 398.1212
2485.5979 | 731.3923 | 407.0451 | 401.8835 | 398.5652
2486.6135 | 731.577 | 407.4232 | 401.988 | 399.1967
2487.5979 | 733.1384 | 407.8225 | 402.179 | 399.5526
2488.5979 | 734.4092 | 407.8643 | 402.3182 | 399.4939
2489.5979 | 734.8398 | 407.9551 | 402.877 | 400.1085
2490.5979 | 735.6684 | 407.9684 | 404.2658 | 399.9474
2491.5979 | 736.2184 | 407.9358 | 405.1226 | 400.3278
2492.5979 | 735.89 | 407.7035 | 405.297 | 400.734
2493.5979 | 737.3275 | 407.8354 | 405.4709 | 400.9142
2494.5979 | 737.682 | 407.7086 | 405.3868 | 401.845
2495.5979 | 735.5661 | 407.4603 | 404.9027 | 401.7615
2496.5979 | 732.455 | 407.3318 | 404.8974 | 401.3746
2497.5979 | 732.7648 | 407.8797 | 404.9462 | 401.7972
2498.5979 | 733.7679 | 408.1563 | 405.1538 | 401.6943
2499.5979 | 733.7105 | 407.6627 | 405.0187 | 401.8435
2500.5979 | 731.918 | 407.2844 | 404.6727 | 401.6676
2501.5979 | 731.0265 | 407.2488 | 404.3934 | 401.1801
2502.5979 | 730.9666 | 407.2481 | 403.8881 | 400.322
2503.5979 | 731.1899 | 407.0976 | 403.562 | 399.6795
2504.5979 | 731.5629 | 407.2094 | 403.5901 | 399.4669
2505.5979 | 731.9171 | 407.4018 | 403.4726 | 399.9028
2506.5979 | 731.4821 | 407.5659 | 403.7784 | 399.555
2507.5979 | 730.813 | 407.6809 | 403.5704 | 399.2939
2508.5979 | 731.9742 | 407.4895 | 403.4753 | 399.6876
2509.5979 | 733.5312 | 407.5531 | 403.7877 | 400.1481
2510.5979 | 734.6093 | 407.5203 | 404.6244 | 400.7382
2511.5979 | 733.354 | 407.444 | 405.4471 | 401.0312
2512.5979 | 734.6315 | 407.4221 | 406.0942 | 401.3125
2513.5979 | 735.2766 | 407.6675 | 406.6764 | 401.1987
2514.5979 | 736.0315 | 407.3049 | 406.7302 | 402.0931
2515.5979 | 737.5737 | 407.6708 | 407.0449 | 402.6673
2516.5979 | 738.5668 | 407.8782 | 408.0518 | 402.8289
2517.5979 | 739.3534 | 408.0141 | 407.9 | 402.5888
2518.5979 | 736.9331 | 407.6958 | 407.8335 | 403.1301
2519.5979 | 736.4368 | 407.9083 | 407.821 | 403.7748
2520.5979 | 737.287 | 407.9586 | 408.3143 | 403.5028
2521.5979 | 739.9374 | 408.236 | 408.3069 | 403.1889
2522.5979 | 743.5381 | 408.317 | 407.8781 | 403.3135
2523.5979 | 744.6255 | 408.2837 | 408.3609 | 403.4182
2524.5979 | 746.2623 | 408.9048 | 408.1443 | 403.9919
2525.5979 | 747.3164 | 409.1387 | 408.2295 | 404.4454
2526.5979 | 745.7194 | 409.3709 | 408.2372 | 405.1596
2527.5979 | 744.5197 | 410.024 | 408.5345 | 405.5829
2528.5979 | 742.5058 | 410.3431 | 409.3416 | 405.7794
2529.5979 | 739.4304 | 410.8448 | 409.2393 | 405.4564
2530.5979 | 736.5914 | 410.9726 | 408.7976 | 405.1554
2531.5979 | 734.5063 | 411.1175 | 408.2911 | 404.3623
2532.5979 | 733.8276 | 410.7949 | 407.5464 | 404.2066
2533.5979 | 734.0641 | 410.7918 | 407.0333 | 403.6634
2534.5979 | 734.425 | 410.5231 | 407.0341 | 403.4153
2535.5979 | 731.7308 | 410.3831 | 407.1064 | 402.9055
2536.5979 | 728.7756 | 410.4285 | 407.9384 | 402.7832
2537.5979 | 726.9062 | 410.673 | 408.1102 | 403.4306
2538.5979 | 725.2514 | 411.0814 | 408.153 | 403.0687
2539.5979 | 723.7251 | 410.9658 | 408.0008 | 402.6102
2540.5979 | 722.8098 | 410.5914 | 407.7809 | 402.2054
2541.5979 | 720.9981 | 410.4321 | 407.4271 | 402.2975
2542.5979 | 719.4063 | 410.3295 | 407.5188 | 402.1323
2543.5979 | 718.4293 | 410.3623 | 407.842 | 402.7793
2544.5979 | 716.4489 | 410.3738 | 407.4376 | 402.6426
2545.5979 | 716.7625 | 410.8107 | 407.665 | 402.4443
2546.5979 | 717.9931 | 410.908 | 408.0863 | 402.7918
2547.5979 | 719.2042 | 410.9175 | 407.6668 | 402.8264
2548.5979 | 720.4048 | 411.0205 | 407.4427 | 402.7736
2549.5979 | 722.011 | 410.9806 | 407.591 | 402.8871
2550.5979 | 724.0568 | 411.5416 | 407.9526 | 403.2471
2551.5979 | 726.1317 | 411.9149 | 408.0463 | 403.265
2552.5979 | 724.7681 | 411.8286 | 407.8113 | 403.5956
2553.5979 | 722.821 | 412.0095 | 407.3779 | 403.3844
2554.5979 | 721.6617 | 411.8666 | 407.0374 | 403.09
2555.6135 | 721.6959 | 411.8356 | 406.6848 | 403.5548
2556.6135 | 721.1629 | 411.5993 | 406.7895 | 403.3514
2557.6135 | 717.9467 | 411.539 | 406.6408 | 402.9143
2558.5979 | 715.8898 | 411.2502 | 406.3264 | 402.4625
2559.5979 | 715.1653 | 411.268 | 406.244 | 402.7774
2560.5979 | 716.015 | 410.854 | 406.2646 | 402.5805
2561.5979 | 716.6668 | 410.6073 | 406.0956 | 402.4118
2562.5979 | 715.7828 | 410.3417 | 405.8269 | 402.8804
2563.5979 | 715.6718 | 410.1879 | 405.8195 | 403.0758
2564.5979 | 715.9252 | 409.9114 | 405.7001 | 402.7659
2565.5979 | 716.2886 | 410.3164 | 405.6359 | 402.5412
2566.5979 | 715.886 | 410.5582 | 405.7338 | 402.3099
2567.5979 | 715.5603 | 410.6426 | 406.3257 | 402.3649
2568.5979 | 716.7754 | 411.0416 | 406.4724 | 402.0477
2569.5979 | 718.7846 | 411.4844 | 407.3592 | 401.7742
2570.5979 | 719.3874 | 411.4387 | 407.6779 | 401.3755
2571.5979 | 720.1393 | 411.414 | 407.7012 | 401.0201
2572.5979 | 721.5648 | 411.7564 | 408.0962 | 400.919
2573.5979 | 722.3441 | 411.8492 | 407.753 | 401.4117
2574.5979 | 723.1418 | 411.7127 | 408.1005 | 401.8504
2575.5979 | 723.4984 | 411.4859 | 407.877 | 401.914
2576.5979 | 724.516 | 411.3105 | 407.4163 | 402.6027
2577.5979 | 724.56 | 411.5551 | 406.9608 | 402.5321
2578.5979 | 726.1898 | 411.5536 | 407.1818 | 403.0391
2579.5979 | 728.0525 | 411.9475 | 406.9992 | 402.7406
2580.5979 | 728.982 | 412.075 | 406.835 | 402.2293
2581.5979 | 726.8957 | 411.9497 | 407.1768 | 402.2917
2582.5979 | 725.072 | 412.3058 | 407.7706 | 402.1481
2583.5979 | 725.9995 | 413.3812 | 408.1193 | 402.7067
2584.5979 | 727.9516 | 413.2859 | 409.1989 | 402.9115
2585.5979 | 728.4612 | 412.9339 | 409.0761 | 402.3758
2586.5979 | 728.9844 | 413.3362 | 408.968 | 402.2943
2587.5979 | 728.6609 | 413.4636 | 408.9143 | 402.3804
2588.5979 | 728.3042 | 413.9893 | 408.4764 | 402.5033
2589.5979 | 725.2676 | 413.8785 | 408.1076 | 402.3952
2590.5979 | 724.2671 | 414.4932 | 407.953 | 402.608
2591.5979 | 724.1188 | 414.6212 | 408.5405 | 402.4248
2592.5979 | 722.9683 | 414.15 | 408.3769 | 402.4845
2593.5979 | 720.4721 | 414.207 | 408.6065 | 402.5984
2594.5979 | 717.6202 | 414.3474 | 408.7003 | 402.5139
2595.5979 | 714.9468 | 414.1434 | 408.6297 | 402.0105
2596.5979 | 713.6876 | 413.9946 | 408.4402 | 401.5505
2597.5979 | 713.2743 | 413.6457 | 408.6392 | 402.7398
2598.5979 | 713.6649 | 413.6877 | 408.617 | 402.7022
2599.5979 | 714.0066 | 413.2319 | 408.4447 | 402.894
2600.5979 | 714.4774 | 413.2379 | 407.9892 | 402.5902
2601.5979 | 714.3623 | 413.3143 | 407.5282 | 402.0887
2602.5979 | 716.2233 | 412.8313 | 407.0339 | 401.7605
2603.5979 | 718.5155 | 412.6156 | 406.7009 | 401.6031
2604.5979 | 719.3742 | 412.1523 | 406.1938 | 401.0292
2605.5979 | 719.3107 | 411.8514 | 405.729 | 400.6529
2606.5979 | 719.7354 | 412.577 | 405.8612 | 401.2772
2607.5979 | 722.2553 | 412.8654 | 406.3486 | 401.5918
2608.5979 | 723.9478 | 412.7039 | 406.6841 | 401.5849
2609.5979 | 723.9893 | 412.4296 | 406.5843 | 401.9943
2610.5979 | 722.6952 | 412.5385 | 406.7183 | 402.3304
2611.5979 | 722.6412 | 412.8041 | 407.094 | 401.9054
2612.5979 | 724.1779 | 412.9096 | 407.1742 | 402.3519
2613.5979 | 729.1206 | 412.8097 | 407.4718 | 402.5082
2614.5979 | 733.704 | 412.9229 | 407.7414 | 402.765
2615.5979 | 736.1355 | 413.3086 | 408.3808 | 403.353
2616.5979 | 737.0849 | 413.3439 | 408.7649 | 403.9373
2617.5979 | 738.1036 | 413.3208 | 409.3811 | 404.3922
2618.5979 | 738.0276 | 413.6472 | 409.946 | 404.6287
2619.5979 | 740.6223 | 413.848 | 410.5204 | 405.3874
2620.5979 | 743.4078 | 413.8853 | 410.2146 | 405.7899
2621.5979 | 746.0627 | 413.5558 | 409.7512 | 406.0009
2622.5979 | 745.3728 | 413.5728 | 409.6144 | 405.9296
2623.5979 | 742.8519 | 413.5871 | 409.7822 | 406.0442
2624.5979 | 743.1975 | 413.7424 | 410.1456 | 405.8699
2625.5979 | 744.9744 | 414.1517 | 410.6075 | 406.1642
2626.5979 | 746.0358 | 414.3356 | 410.8395 | 407.1025
2627.5979 | 746.5257 | 414.699 | 410.8353 | 407.2919
2628.5979 | 746.2223 | 414.5366 | 410.7944 | 406.9758
2629.5979 | 744.885 | 414.7071 | 411.0079 | 407.2965
2630.5979 | 743.412 | 415.1888 | 411.4898 | 406.8075
2631.5979 | 742.6036 | 415.375 | 412.0189 | 406.7796
2632.5979 | 741.293 | 415.9761 | 412.1003 | 406.3504
2633.5979 | 741.3911 | 416.2354 | 412.22 | 407.37
2634.5979 | 741.8732 | 416.5617 | 412.4346 | 407.4512
2635.5979 | 739.9009 | 416.613 | 412.8918 | 407.1254
2636.5979 | 739.7612 | 416.7681 | 414.3322 | 407.3607
2637.5979 | 740.42 | 417.3451 | 414.1332 | 407.6505
2638.5979 | 740.5168 | 417.4523 | 413.8928 | 407.9042
2639.5979 | 740.6242 | 417.2194 | 413.4675 | 408.4033
2640.5979 | 739.6876 | 417.4539 | 414.1593 | 408.503
2641.5979 | 738.0389 | 417.233 | 413.9308 | 408.6582
2642.5979 | 736.2581 | 416.979 | 414.0049 | 408.8648
2643.5979 | 732.4439 | 417.255 | 413.6724 | 408.6848
2644.5979 | 727.7973 | 416.7946 | 413.2724 | 408.6705
2645.5979 | 723.6279 | 416.4311 | 413.2004 | 409.1696
2646.5979 | 721.2615 | 416.0987 | 412.8981 | 408.9886
2647.5979 | 719.6622 | 415.5794 | 412.3035 | 408.2081
2648.5979 | 718.0366 | 415.6088 | 412.0413 | 408.0397
2649.5979 | 716.961 | 415.755 | 411.422 | 407.8801
2650.5979 | 716.5306 | 415.8206 | 411.3997 | 408.0512
2651.5979 | 716.9197 | 415.557 | 411.3017 | 407.8595
2652.5979 | 718.4453 | 415.8413 | 411.2263 | 408.2286
2653.5979 | 718.5375 | 415.873 | 411.3969 | 408.4112
2654.5979 | 718.5129 | 415.8819 | 411.1848 | 408.0876
2655.5979 | 719.2366 | 415.9302 | 411.2015 | 407.9301
2656.5979 | 720.9785 | 415.8173 | 411.0088 | 407.5254
2657.5979 | 721.5103 | 415.5742 | 410.7763 | 407.1191
2658.5979 | 720.9237 | 415.4413 | 410.7166 | 407.2072
2659.5979 | 721.0966 | 415.8819 | 411.7837 | 407.7501
2660.5979 | 721.6612 | 416.0555 | 411.8184 | 408.2351
2661.5979 | 722.8481 | 416.6623 | 412.272 | 409.0103
2662.5979 | 724.8328 | 416.737 | 412.402 | 409.5635
2663.5979 | 727.2953 | 416.699 | 412.6523 | 410.1245
2664.5979 | 729.8854 | 417.1297 | 413.802 | 410.4347
2665.5979 | 731.8577 | 417.3391 | 414.3392 | 411.3711
2666.5979 | 732.671 | 417.6996 | 414.4281 | 411.6168
2667.5979 | 732.1571 | 417.3312 | 414.2619 | 411.0462
2668.5979 | 732.6802 | 417.2101 | 413.7916 | 410.7402
2669.5979 | 733.6895 | 417.0849 | 413.5706 | 410.2575
2670.5979 | 732.6489 | 417.0512 | 413.4876 | 410.0309
2671.5979 | 730.6149 | 417.0047 | 413.3584 | 409.8165
2672.5979 | 727.8629 | 417.3021 | 412.9871 | 409.0967
2673.5979 | 724.4086 | 417.3356 | 412.6605 | 408.8946
2674.5979 | 720.6403 | 417.1415 | 412.6571 | 408.4855
2675.5979 | 717.3316 | 417.0112 | 412.4646 | 407.7223
2676.5979 | 714.6884 | 416.7403 | 411.8278 | 407.7527
2677.5979 | 711.8788 | 416.6495 | 411.49 | 408.4691
2678.5979 | 710.2141 | 416.4118 | 411.8718 | 408.6041
2679.5979 | 709.4635 | 416.7594 | 411.4286 | 408.345
2680.5979 | 709.9915 | 417.1158 | 411.8131 | 407.8357
2681.5979 | 711.1833 | 417.7435 | 411.6823 | 407.4104
2682.5979 | 712.8034 | 418.4735 | 411.7018 | 407.4017
2683.5979 | 712.8121 | 418.6163 | 412.5794 | 407.5356
2684.5979 | 713.2786 | 418.8595 | 412.3349 | 407.4195
2685.5979 | 713.5437 | 418.9372 | 412.839 | 408.4242
2686.5979 | 714.5474 | 418.8275 | 413.0967 | 408.5133
2687.5979 | 714.8372 | 418.6544 | 413.0415 | 408.489
2688.5979 | 715.3569 | 418.6932 | 412.8482 | 408.2866
2689.5979 | 715.4219 | 418.8532 | 412.6027 | 408.491
2690.5979 | 716.9134 | 418.6558 | 412.3695 | 408.5146
2691.5979 | 719.2017 | 418.7328 | 412.163 | 409.0808
2692.5979 | 719.9963 | 418.8738 | 412.2883 | 409.9101
2693.5979 | 719.3566 | 419.085 | 412.9709 | 409.4844
2694.5979 | 717.6027 | 419.2495 | 412.8196 | 409.5099
2695.5979 | 718.9615 | 419.2212 | 413.2824 | 409.7075
2696.5979 | 723.0226 | 419.2537 | 413.3947 | 409.9371
2697.5979 | 728.7561 | 419.7567 | 415.5443 | 411.6246
2698.5979 | 735.3909 | 419.9139 | 416.2224 | 412.3221
2699.5979 | 743.6989 | 419.6036 | 416.4604 | 412.7022
2700.5979 | 749.3937 | 419.6757 | 416.7011 | 413.432
2701.5979 | 751.6253 | 419.7032 | 416.8759 | 413.8037
2702.5979 | 752.6912 | 420.2159 | 418.8152 | 414.7587
2703.6135 | 753.4527 | 420.9128 | 418.6491 | 414.6793
2704.5979 | 751.2238 | 421.443 | 419.1849 | 414.8812
2705.5979 | 748.7411 | 421.9779 | 419.2311 | 414.881
2706.5979 | 746.266 | 422.2871 | 419.6097 | 415.3432
2707.5979 | 745.6238 | 423.032 | 419.9221 | 415.2551
2708.5979 | 745.2619 | 423.315 | 419.6773 | 415.658
2709.5979 | 742.3295 | 423.2112 | 419.5631 | 416.0285
2710.5979 | 741.9138 | 423.3281 | 419.3981 | 416.3496
2711.5979 | 741.8202 | 423.6107 | 419.4365 | 417.0889
2712.5979 | 743.4658 | 423.8252 | 420.4353 | 416.7402
2713.5979 | 744.1725 | 423.7367 | 420.8872 | 416.3249
2714.5979 | 741.2832 | 423.4998 | 421.2021 | 416.2788
2715.5979 | 738.0586 | 422.8929 | 420.947 | 415.2418
2716.5979 | 737.8174 | 422.3909 | 420.2019 | 414.5158
2717.5979 | 736.4186 | 422.1563 | 419.7149 | 414.1638
2718.6135 | 735.8765 | 421.6751 | 419.3793 | 414.474
2719.5979 | 733.6847 | 421.4532 | 418.9077 | 414.7774
2720.5979 | 733.1153 | 421.1474 | 418.5703 | 414.744
2721.5979 | 730.9619 | 421.0424 | 418.2308 | 415.1784
2722.5979 | 729.6806 | 421.2434 | 418.153 | 415.0216
2723.5979 | 727.075 | 421.6664 | 418.4097 | 415.141
2724.5979 | 726.364 | 421.9904 | 418.1364 | 415.244
2725.5979 | 725.2308 | 422.9875 | 418.5859 | 415.231
2726.5979 | 726.2551 | 423.1751 | 418.2994 | 415.4311
2727.5979 | 727.6312 | 423.4378 | 418.2433 | 415.42
2728.5979 | 728.4636 | 423.8425 | 418.3469 | 416.0316
2729.5979 | 727.9598 | 424.045 | 418.4313 | 416.2935
2730.5979 | 726.0315 | 424.2378 | 418.3112 | 416.1595
2731.5979 | 725.0405 | 425.0271 | 418.8126 | 415.5824
2732.5979 | 725.8062 | 425.2759 | 419.4214 | 415.6958
2733.6135 | 728.0594 | 425.6921 | 419.9109 | 416.6981
2734.5979 | 729.8419 | 425.685 | 420.2584 | 416.7457
2735.5979 | 733.6814 | 426.3322 | 420.9145 | 417.7184
2736.5979 | 736.5675 | 426.4391 | 421.9735 | 418.808
2737.5979 | 739.4429 | 426.7964 | 422.2222 | 419.556
2738.5979 | 741.2651 | 427.0209 | 422.2701 | 419.685
2739.5979 | 742.6608 | 427.0808 | 422.2524 | 420.4491
2740.5979 | 744.1486 | 427.4614 | 422.4734 | 420.9014
2741.5979 | 744.2305 | 427.853 | 422.6863 | 421.1543
2742.5979 | 744.034 | 428.0701 | 422.3757 | 421.5926
2743.5979 | 743.8748 | 428.6917 | 423.1166 | 421.7127
2744.5979 | 747.8415 | 428.7841 | 423.5573 | 422.2264
2745.5979 | 750.0256 | 428.8185 | 423.6936 | 422.6381
2746.5979 | 751.5633 | 428.4665 | 423.8463 | 423.4101
2747.5979 | 752.0591 | 428.446 | 424.1403 | 423.6254
2748.5979 | 753.6736 | 428.882 | 424.959 | 424.2493
2749.5979 | 754.6554 | 429.2364 | 425.4807 | 424.9815
2750.5979 | 758.022 | 429.4827 | 427.2746 | 424.9499
2751.5979 | 759.8555 | 429.6257 | 426.9439 | 424.4172
2752.5979 | 761.5526 | 429.7349 | 426.8877 | 424.2324
2753.5979 | 763.671 | 429.2582 | 427.0872 | 424.3485
2754.5979 | 760.7933 | 428.5987 | 427.0041 | 424.6662
2755.5979 | 757.0857 | 428.4467 | 426.6287 | 424.2142
2756.5979 | 753.3494 | 428.3368 | 426.6279 | 423.8637
2757.5979 | 751.3344 | 427.8168 | 426.1931 | 423.5072
2758.5979 | 749.667 | 428.0747 | 426.1349 | 422.719
2759.5979 | 747.1267 | 428.5244 | 425.6057 | 422.0004
2760.5979 | 745.5781 | 428.8502 | 425.3754 | 422.3875
2761.5979 | 745.0736 | 429.22 | 425.7007 | 422.2565
2762.5979 | 745.3358 | 429.8669 | 425.7289 | 422.0436
2763.5979 | 744.2674 | 430.0761 | 425.9351 | 422.1308
2764.5979 | 742.8942 | 430.3405 | 425.7186 | 422.8568
2765.5979 | 739.0705 | 430.2729 | 425.7933 | 423.0127
2766.5979 | 737.5751 | 430.8659 | 426.1581 | 422.7177
2767.5979 | 736.9291 | 431.1587 | 426.492 | 422.7882
2768.5979 | 735.6492 | 431.4106 | 426.3951 | 422.7015
2769.5979 | 735.2315 | 431.633 | 426.4513 | 423.5886
2770.5979 | 734.0046 | 432.3083 | 426.6591 | 423.5805
2771.5979 | 731.5455 | 433.1118 | 427.5974 | 424.2368
2772.5979 | 731.4663 | 434.035 | 429.5662 | 424.9236
2773.5979 | 734.1859 | 434.8204 | 430.0138 | 424.7314
2774.5979 | 734.9117 | 434.464 | 430.2076 | 424.4086
2775.5979 | 733.5983 | 433.9833 | 430.3718 | 424.4774
2776.5979 | 734.7618 | 434.0271 | 430.0529 | 424.1628
2777.5979 | 733.5129 | 434.1972 | 429.6202 | 423.8131
2778.5979 | 733.7103 | 434.5934 | 429.6889 | 424.6788
2779.5979 | 734.4765 | 434.8604 | 429.4576 | 425.486
2780.5979 | 733.8217 | 435.8721 | 430.901 | 426.1095
2781.5979 | 735.3452 | 436.5578 | 430.9239 | 427.2003
2782.5979 | 739.2732 | 436.5246 | 431.0076 | 427.9183
2783.5979 | 741.4472 | 436.3597 | 431.1771 | 428.2051
2784.5979 | 741.9138 | 436.3316 | 431.2131 | 429.4423
2785.5979 | 741.2734 | 437.3492 | 431.4328 | 429.2605
2786.5979 | 740.3284 | 438.2339 | 432.8886 | 428.8759
2787.5979 | 737.8737 | 438.9636 | 432.612 | 428.705
2788.5979 | 736.5902 | 439.5858 | 433.157 | 428.6085
2789.5979 | 739.1108 | 440.0121 | 433.2794 | 428.777
2790.5979 | 742.0686 | 440.5596 | 434.3816 | 429.1734
2791.5979 | 745.5851 | 441.0404 | 434.7939 | 430.3448
2792.5979 | 746.0999 | 441.0562 | 434.814 | 431.3176
2793.5979 | 747.0852 | 441.9463 | 435.3416 | 431.4207
2794.5979 | 750.4015 | 443.2732 | 435.9043 | 431.4484
2795.5979 | 752.4553 | 443.3876 | 435.8508 | 432.1548
2796.5979 | 754.6173 | 442.869 | 436.0464 | 432.5087
2797.5979 | 755.7735 | 442.5355 | 436.0435 | 432.7656
2798.5979 | 755.6173 | 441.9994 | 435.8337 | 432.8363
2799.5979 | 756.2326 | 441.8466 | 436.0762 | 433.08
2800.5979 | 757.4076 | 442.5555 | 436.8169 | 433.282
2801.5979 | 759.1832 | 443.6844 | 437.3675 | 433.4869
2802.5979 | 760.4641 | 443.5286 | 437.6451 | 434.0081
2803.5979 | 763.1335 | 443.5495 | 437.7049 | 434.4263
2804.5979 | 767.0004 | 443.329 | 437.4926 | 434.5806
2805.5979 | 769.6237 | 443.0612 | 437.7824 | 434.7843
2806.5979 | 769.6926 | 442.6591 | 438.1846 | 434.9221
2807.5979 | 768.3419 | 442.2491 | 438.6119 | 434.92
2808.5979 | 768.17 | 441.7662 | 438.1641 | 435.6207
2809.5979 | 767.925 | 441.3878 | 438.4854 | 434.7943
2810.5979 | 767.7105 | 441.3177 | 438.2112 | 435.1394
2811.5979 | 766.6618 | 441.1138 | 437.6965 | 434.7264
2812.5979 | 766.2406 | 440.9701 | 437.493 | 434.7964
2813.5979 | 764.731 | 440.7688 | 437.5345 | 435.1134
2814.5979 | 763.2403 | 440.4645 | 437.3831 | 435.23
2815.5979 | 761.8165 | 441.0196 | 437.9759 | 435.499
2816.5979 | 760.9813 | 441.2483 | 438.3382 | 435.3142
2817.5979 | 761.4531 | 441.368 | 438.2346 | 435.0265
2818.5979 | 761.3341 | 441.0248 | 437.8652 | 435.423
2819.5979 | 760.7009 | 441.0781 | 438.5591 | 436.2864
2820.5979 | 760.5423 | 440.6305 | 438.408 | 436.5543
2821.5979 | 763.0534 | 440.6098 | 438.4253 | 436.575
2822.5979 | 764.9955 | 440.766 | 439.4162 | 437.135
2823.5979 | 762.6092 | 440.8029 | 439.0755 | 437.1371
2824.5979 | 759.5955 | 440.733 | 439.0938 | 437.5507
2825.5979 | 756.1712 | 440.3214 | 439.1042 | 437.7524
2826.5979 | 754.2344 | 440.3326 | 439.0938 | 437.4688
2827.5979 | 755.6602 | 440.595 | 439.0207 | 437.2076
2828.5979 | 757.5926 | 440.2073 | 439.137 | 437.3349
2829.5979 | 757.7229 | 440.5192 | 439.5657 | 437.5739
2830.5979 | 758.1974 | 440.4069 | 438.9711 | 438.0403
2831.5979 | 761.0885 | 439.9036 | 438.8297 | 438.6826
2832.5979 | 760.7787 | 439.7994 | 439.0039 | 439.063
2833.5979 | 758.6166 | 439.8837 | 439.4061 | 439.3694
2834.5979 | 757.2218 | 440.6401 | 439.6486 | 439.4453
2835.5979 | 757.4958 | 441.0381 | 439.5378 | 439.8306
2836.5979 | 755.7345 | 441.1259 | 439.1437 | 440.1936
2837.5979 | 753.9806 | 441.0135 | 438.7844 | 440.1493
2838.5979 | 752.4046 | 440.6644 | 439.2964 | 439.5689
2839.5979 | 749.8526 | 440.4796 | 439.1167 | 440.4285
2840.5979 | 746.6616 | 439.9099 | 438.9611 | 440.3597
2841.5979 | 744.6569 | 439.1884 | 438.498 | 439.6241
2842.5979 | 744.121 | 438.7665 | 438.2061 | 439.4846
2843.5979 | 746.0362 | 439.1467 | 438.8829 | 439.999
2844.5979 | 749.8431 | 438.6564 | 439.1491 | 440.0451
2845.6135 | 750.5529 | 438.522 | 439.1422 | 440.709
2846.5979 | 752.2339 | 438.4874 | 439.4019 | 440.7449
2847.5979 | 756.0305 | 438.383 | 439.0865 | 441.7383
2848.5979 | 761.2116 | 439.0833 | 439.3486 | 441.6501
2849.5979 | 763.4704 | 439.3768 | 439.8978 | 441.3351
2850.5979 | 766.2831 | 439.7515 | 441.1415 | 442.6935
2851.5979 | 766.6982 | 439.7671 | 441.3914 | 442.7974
2852.5979 | 764.7867 | 439.6374 | 442.742 | 444.2053
2853.5979 | 761.196 | 440.2209 | 442.7816 | 444.314
2854.5979 | 757.8951 | 440.1519 | 442.8934 | 444.1145
2855.6135 | 755.9383 | 439.8951 | 442.6802 | 444.6407
2856.5979 | 754.3315 | 440.1947 | 442.4877 | 444.1607
2857.5979 | 752.4976 | 440.5293 | 442.025 | 443.8743
2858.5979 | 752.1751 | 440.5959 | 441.7906 | 443.1129
2859.5979 | 753.1274 | 440.552 | 441.7489 | 443.6377
2860.5979 | 755.8616 | 441.1308 | 441.7638 | 442.937
2861.5979 | 756.7056 | 440.8088 | 441.731 | 443.7344
2862.5979 | 756.598 | 440.5869 | 441.5163 | 444.1022
2863.5979 | 757.6319 | 440.4244 | 441.2267 | 443.9334
2864.5979 | 757.9658 | 440.4803 | 440.7218 | 444.0351
2865.5979 | 757.5206 | 439.964 | 440.3185 | 444.1982
2866.5979 | 754.6896 | 439.9646 | 440.2111 | 444.0326
2867.5979 | 751.1211 | 440.1194 | 439.8338 | 443.4733
2868.5979 | 749.7051 | 439.9438 | 439.6989 | 443.146
2869.5979 | 746.6835 | 440.0559 | 439.925 | 443.6231
2870.5979 | 742.9373 | 439.7966 | 440.0451 | 442.9237
2871.5979 | 739.1656 | 439.924 | 440.7328 | 442.7602
2872.5979 | 736.4958 | 440.3779 | 441.2615 | 443.1744
2873.5979 | 732.7619 | 440.2686 | 441.3054 | 443.705
2874.5979 | 729.5539 | 440.5226 | 441.0998 | 444.4935
2875.5979 | 728.0008 | 440.8486 | 440.9158 | 443.5349
2876.5979 | 727.332 | 441.0093 | 440.793 | 443.553
2877.5979 | 725.3797 | 441.1539 | 440.3153 | 442.9186
2878.5979 | 724.9721 | 441.5126 | 440.186 | 442.6591
2879.5979 | 724.8128 | 441.6374 | 440.2714 | 442.8876
2880.5979 | 723.441 | 441.648 | 440.3313 | 442.3115
2881.5979 | 721.7225 | 441.9014 | 440.0734 | 441.6171
2882.5979 | 720.2966 | 442.3151 | 440.1942 | 441.9047
2883.5979 | 718.7374 | 442.3735 | 440.3479 | 442.2467
2884.5979 | 718.1574 | 442.5045 | 440.6421 | 442.2104
2885.5979 | 718.1818 | 441.7819 | 440.3251 | 442.6791
2886.5979 | 717.7778 | 440.9956 | 439.8954 | 442.6606
2887.5979 | 719.0837 | 440.5334 | 439.828 | 442.2015
2888.5979 | 719.6505 | 440.1036 | 439.6837 | 441.7181
2889.5979 | 718.9231 | 439.9896 | 439.2123 | 441.0285
2890.5979 | 717.8637 | 439.1849 | 439.5763 | 440.9603
2891.5979 | 716.7942 | 438.6137 | 439.168 | 440.4714
2892.5979 | 717.3584 | 437.988 | 438.9951 | 440.3014
2893.5979 | 718.92 | 437.5983 | 438.911 | 440.3728
2894.5979 | 724.6856 | 437.986 | 439.1573 | 440.632
2895.6135 | 730.7983 | 438.221 | 439.318 | 441.0896
2896.5979 | 735.6614 | 438.8302 | 439.2803 | 441.4595
2897.5979 | 740.9734 | 438.7961 | 441.1197 | 442.9366
2898.5979 | 745.2399 | 439.0046 | 441.4047 | 443.3282
2899.5979 | 749.4026 | 439.1665 | 441.9092 | 444.4857
2900.5979 | 752.4539 | 439.8749 | 442.8254 | 445.2731
2901.5979 | 755.1096 | 440.2147 | 443.3219 | 445.8277
2902.5979 | 757.101 | 440.7814 | 444.6936 | 446.8197
2903.5979 | 756.0214 | 441.388 | 445.4319 | 446.5547
2904.5979 | 752.3043 | 442.1296 | 446.1121 | 446.6798
2905.5979 | 748.3607 | 442.8257 | 446.3139 | 447.3709
2906.5979 | 746.5122 | 443.36 | 445.956 | 446.7501
2907.5979 | 746.4906 | 443.1313 | 446.0308 | 446.9163
2908.5979 | 746.3369 | 443.0412 | 445.7105 | 446.8311
2909.5979 | 744.5364 | 443.0327 | 446.3223 | 446.2626
2910.5979 | 742.397 | 442.9978 | 446.2236 | 446.2607
2911.5979 | 739.1317 | 442.4515 | 445.4937 | 445.772
2912.5979 | 736.6506 | 442.3068 | 445.1323 | 445.7488
2913.5979 | 736.1817 | 442.2352 | 444.6473 | 445.6663
2914.5979 | 736.4197 | 442.1028 | 444.3168 | 446.51
2915.5979 | 736.4024 | 442.0984 | 444.0914 | 445.9138
2916.5979 | 735.3127 | 442.0871 | 443.679 | 446.2067
2917.5979 | 731.1288 | 441.7809 | 443.2656 | 446.2156
2918.5979 | 727.1079 | 441.5863 | 443.3649 | 446.0006
2919.5979 | 723.4789 | 441.1751 | 442.9751 | 445.9259
2920.5979 | 723.113 | 440.6103 | 442.774 | 445.778
2921.5979 | 721.7307 | 439.9412 | 442.2367 | 445.9526
2922.5979 | 720.895 | 440.086 | 442.0218 | 445.42
2923.5979 | 719.8238 | 440.0759 | 441.6287 | 445.5056
2924.5979 | 720.8243 | 439.7971 | 441.057 | 445.5045
2925.5979 | 720.5515 | 440.0829 | 441.004 | 444.9757
2926.5979 | 720.5346 | 439.8771 | 441.6212 | 445.1948
2927.5979 | 719.4471 | 439.8123 | 441.2968 | 444.6365
2928.5979 | 720.0065 | 440.2134 | 441.2199 | 444.4459
2929.5979 | 722.0579 | 441.1514 | 441.6519 | 444.8112
2930.5979 | 727.5522 | 441.2635 | 441.558 | 444.8013
2931.5979 | 733.3622 | 441.5684 | 441.6836 | 445.3188
2932.5979 | 734.1907 | 441.2898 | 442.0077 | 445.7281
2933.5979 | 732.3443 | 441.0383 | 441.9708 | 446.1075
2934.5979 | 731.8877 | 440.9429 | 442.1998 | 446.6754
2935.5979 | 731.1525 | 440.54 | 442.19 | 446.7946
2936.5979 | 731.3646 | 440.3025 | 441.9898 | 447.683
2937.5979 | 732.4982 | 440.3896 | 442.2474 | 446.9854
2938.5979 | 733.1852 | 440.3259 | 441.9775 | 446.3561
2939.5979 | 735.2138 | 440.5404 | 441.9413 | 446.485
2940.5979 | 735.5486 | 440.2053 | 441.6788 | 446.8232
2941.5979 | 736.3809 | 440.2789 | 441.7526 | 446.6744
2942.5979 | 737.7677 | 440.1416 | 441.8042 | 447.3247
2943.5979 | 740.3417 | 439.9235 | 441.8883 | 447.1453
2944.5979 | 741.0569 | 439.7437 | 442.284 | 446.7644
2945.5979 | 741.2805 | 439.9649 | 442.5723 | 446.0969
2946.5979 | 740.9918 | 439.7886 | 442.7218 | 445.8437
2947.5979 | 740.4244 | 439.3731 | 442.6635 | 445.8252
2948.5979 | 738.5336 | 439.2019 | 442.184 | 446.0445
2949.5979 | 734.6745 | 438.668 | 442.0211 | 445.7603
2950.5979 | 731.2535 | 439.202 | 442.3066 | 445.683
2951.5979 | 730.4845 | 438.916 | 442.0082 | 445.3682
2952.5979 | 729.4158 | 438.6803 | 441.979 | 445.4756
2953.5979 | 726.9826 | 438.4764 | 442.2889 | 445.4081
2954.5979 | 726.8223 | 438.2582 | 442.1211 | 445.1326
2955.5979 | 726.5697 | 438.2454 | 441.9432 | 445.6638
2956.5979 | 726.6663 | 438.0371 | 441.6761 | 445.8983
2957.5979 | 726.8125 | 438.0159 | 441.8326 | 445.1579
2958.5979 | 727.2586 | 438.3053 | 442.2128 | 445.3408
2959.5979 | 727.1978 | 438.5844 | 441.7917 | 445.1957
2960.5979 | 727.4413 | 438.7934 | 442.04 | 445.2009
2961.5979 | 727.6944 | 438.465 | 441.521 | 444.8052
2962.5979 | 728.2516 | 438.5478 | 441.5199 | 444.6583
2963.5979 | 729.8285 | 438.8534 | 442.1062 | 444.7012
2964.5979 | 731.1695 | 438.7885 | 442.142 | 444.789
2965.5979 | 732.3235 | 438.5065 | 442.0769 | 444.347
2966.5979 | 734.8619 | 438.179 | 442.0749 | 444.2759
2967.5979 | 735.799 | 437.7992 | 441.8752 | 445.2657
2968.5979 | 735.5118 | 437.6619 | 441.8283 | 445.3648
2969.5979 | 734.7212 | 437.6776 | 441.4014 | 445.201
2970.5979 | 733.4979 | 438.3288 | 440.9719 | 445.1979
2971.5979 | 734.2557 | 438.7819 | 440.5957 | 445.1458
2972.5979 | 735.2405 | 438.9459 | 440.5418 | 444.861
2973.5979 | 734.8118 | 439.0959 | 440.3719 | 444.9505
2974.5979 | 734.8322 | 439.4208 | 440.1952 | 445.0372
2975.5979 | 734.4545 | 439.4411 | 440.2286 | 444.8924
2976.5979 | 734.0214 | 439.5441 | 440.2615 | 444.9593
2977.5979 | 732.411 | 439.9038 | 440.736 | 445.1034
2978.5979 | 731.3145 | 440.414 | 440.7847 | 445.5849
2979.5979 | 732.157 | 440.7762 | 441.0015 | 445.3284
2980.5979 | 734.0851 | 440.779 | 441.1886 | 446.0231
2981.5979 | 736.1302 | 440.531 | 441.036 | 446.5436
2982.5979 | 736.1752 | 440.3607 | 440.939 | 446.4691
2983.5979 | 735.2758 | 440.2834 | 440.841 | 446.341
2984.5979 | 732.6627 | 439.9919 | 440.4064 | 445.5934
2985.5979 | 730.7814 | 440.0316 | 440.2797 | 444.8741
2986.5979 | 730.9236 | 440.1587 | 440.2645 | 444.6908
2987.5979 | 731.1835 | 440.2058 | 440.1222 | 444.0781
2988.5979 | 729.629 | 439.8701 | 439.5734 | 443.2957
2989.5979 | 728.782 | 439.5367 | 439.923 | 443.3321
2990.5979 | 728.2777 | 439.1868 | 440.4394 | 443.7309
2991.5979 | 726.5593 | 439.3595 | 440.2978 | 443.6364
2992.5979 | 724.7011 | 439.2799 | 440.7834 | 444.287
2993.5979 | 722.7013 | 439.1134 | 441.0016 | 444.086
2994.5979 | 721.7229 | 439.0769 | 441.2218 | 444.506
2995.5979 | 721.2535 | 438.8711 | 441.2245 | 445.3795
2996.6135 | 723.3655 | 438.6755 | 441.0494 | 444.9287
2997.5979 | 724.9547 | 438.6049 | 440.7834 | 444.8161
2998.6135 | 726.7119 | 438.1715 | 440.2276 | 445.1048
2999.5979 | 729.9282 | 438.0393 | 440.6955 | 445.8733
3000.5979 | 735.503 | 438.1592 | 441.086 | 446.3528
3001.5979 | 738.5456 | 438.3222 | 441.1902 | 446.8016
3002.5979 | 741.6628 | 438.3169 | 440.8109 | 446.8922
3003.5979 | 745.3463 | 438.0523 | 441.4044 | 447.0886
3004.5979 | 746.027 | 438.105 | 441.5939 | 447.7714
3005.5979 | 747.0526 | 438.2858 | 441.604 | 447.8336
3006.5979 | 747.9703 | 438.1685 | 441.6781 | 447.1891
3007.5979 | 750.3257 | 438.4282 | 442.0343 | 447.7237
3008.5979 | 753.4833 | 438.2628 | 442.0484 | 447.793
3009.5979 | 756.7309 | 438.5219 | 441.913 | 447.5024
3010.5979 | 756.0817 | 438.3186 | 442.0676 | 447.6242
3011.5979 | 754.3737 | 438.1733 | 442.4249 | 448.1931
3012.5979 | 752.8462 | 437.9207 | 442.3543 | 448.0702
3013.5979 | 751.0629 | 437.9451 | 442.3479 | 448.7261
3014.5979 | 750.3875 | 437.7789 | 442.5169 | 448.4639
3015.5979 | 748.846 | 437.6763 | 442.2209 | 448.2899
3016.5979 | 747.0199 | 437.6065 | 442.5005 | 447.668
3017.5979 | 746.3302 | 437.7623 | 442.7132 | 447.8947
3018.5979 | 747.1193 | 437.6877 | 443.344 | 447.9718
3019.5979 | 746.1686 | 437.7697 | 443.4796 | 448.364
3020.5979 | 747.279 | 438.4368 | 443.5381 | 448.113
3021.5979 | 748.1635 | 438.6307 | 443.4014 | 447.8499
3022.5979 | 747.1936 | 438.4313 | 443.6959 | 448.0816
3023.5979 | 745.3432 | 438.1893 | 443.3332 | 447.6346
3024.5979 | 743.6005 | 437.9379 | 443.145 | 447.6929
3025.5979 | 739.6717 | 437.8953 | 442.9468 | 447.7821
3026.5979 | 737.1385 | 438.12 | 442.7866 | 447.1006
3027.5979 | 735.7937 | 437.643 | 442.4972 | 447.0771
3028.5979 | 735.7956 | 437.0339 | 442.2367 | 446.5839
3029.5979 | 735.2613 | 437.0024 | 442.0988 | 446.7447
3030.5979 | 734.8138 | 436.8186 | 441.9299 | 446.7732
3031.5979 | 734.4462 | 436.5838 | 441.5825 | 446.9308
3032.5979 | 731.8386 | 436.2175 | 441.3295 | 446.3631
3033.5979 | 730.5684 | 436.3484 | 441.0625 | 445.909
3034.5979 | 730.5412 | 436.0248 | 440.8156 | 445.6929
3035.5979 | 733.2327 | 435.6765 | 440.399 | 445.014
3036.5979 | 734.0713 | 435.6937 | 439.936 | 444.6747
3037.5979 | 735.8943 | 435.805 | 439.8471 | 444.7983
3038.5979 | 737.116 | 435.4776 | 439.8272 | 444.9657
3039.5979 | 736.6963 | 435.5452 | 439.8624 | 445.0288
3040.5979 | 735.9606 | 435.5162 | 439.4439 | 446.0022
3041.5979 | 734.5169 | 435.7499 | 439.5418 | 445.7232
3042.5979 | 732.5107 | 436.0053 | 439.5205 | 445.5676
3043.5979 | 730.0482 | 435.9855 | 439.4036 | 445.4911
3044.5979 | 728.1174 | 436.2051 | 440.1501 | 445.4304
3045.5979 | 727.4716 | 436.5106 | 440.0906 | 445.254
3046.5979 | 727.8068 | 436.4238 | 439.7272 | 444.7175
3047.5979 | 728.6069 | 436.2437 | 440.3605 | 444.8675
3048.5979 | 729.1378 | 436.1343 | 440.4199 | 444.8781
3049.5979 | 729.8364 | 436.0795 | 440.4988 | 444.833
3050.5979 | 729.1294 | 436.3026 | 440.7779 | 445.2422
3051.5979 | 726.6418 | 435.9932 | 440.8795 | 445.7242
3052.5979 | 724.0475 | 435.8191 | 440.4903 | 445.2107
3053.5979 | 721.8775 | 436.1142 | 440.5465 | 444.8481
3054.5979 | 721.2401 | 436.8627 | 440.9808 | 444.7977
3055.5979 | 722.2564 | 436.9251 | 441.1447 | 444.5749
3056.5979 | 724.2492 | 436.5388 | 441.1812 | 444.8062
3057.5979 | 724.7491 | 436.1217 | 440.7777 | 445.5128
3058.5979 | 725.4893 | 435.8206 | 440.6765 | 445.6852
3059.5979 | 725.3112 | 436.4192 | 440.7868 | 445.7838
3060.5979 | 724.6312 | 436.2125 | 440.7199 | 445.6662
3061.5979 | 725.027 | 436.028 | 440.4064 | 444.9498
3062.5979 | 725.7812 | 436.1122 | 440.284 | 444.7223
3063.5979 | 727.7255 | 436.1707 | 440.7678 | 444.1915
3064.5979 | 728.1479 | 435.9401 | 440.5041 | 443.989
3065.5979 | 728.72 | 435.7337 | 440.0468 | 443.8739
3066.5979 | 726.3192 | 435.4288 | 439.6398 | 443.8774
3067.5979 | 724.967 | 435.1655 | 440.5537 | 443.6859
3068.5979 | 724.8575 | 435.2761 | 440.69 | 443.5843
3069.5979 | 727.501 | 435.8489 | 440.919 | 443.4891
3070.5979 | 728.8953 | 435.7829 | 441.0616 | 443.9355
3071.5979 | 729.2083 | 435.6029 | 440.9805 | 444.1139
3072.5979 | 729.2533 | 435.2972 | 440.5006 | 444.2606
3073.5979 | 730.1423 | 435.1919 | 440.264 | 443.9369
3074.5979 | 728.7274 | 434.892 | 439.873 | 443.4363
3075.5979 | 726.9924 | 435.0172 | 439.5843 | 443.3522
3076.5979 | 726.4448 | 434.9737 | 439.1906 | 443.9687
3077.5979 | 724.1437 | 435.4742 | 439.1428 | 443.4062
3078.5979 | 725.0225 | 435.6792 | 438.9658 | 443.2112
3079.5979 | 722.7849 | 435.3512 | 438.9331 | 442.9361
3080.5979 | 717.4706 | 435.2711 | 438.9625 | 442.9515
3081.5979 | 714.0493 | 435.2656 | 438.9412 | 442.5516
3082.5979 | 714.4607 | 435.6134 | 439.1336 | 442.9458
3083.5979 | 716.2956 | 435.6594 | 439.2531 | 443.1503
3084.5979 | 720.4508 | 435.6439 | 439.1817 | 443.1054
3085.5979 | 722.0456 | 435.4366 | 439.1841 | 443.4821
3086.5979 | 723.0286 | 435.0675 | 438.828 | 443.465
3087.5979 | 726.0445 | 434.7692 | 438.9311 | 443.6355
3088.5979 | 726.3974 | 434.8859 | 438.8734 | 443.4967
3089.5979 | 726.4694 | 434.8721 | 438.6807 | 443.2171
3090.5979 | 726.709 | 434.9553 | 438.43 | 442.9686
3091.5979 | 727.6271 | 434.9495 | 437.9667 | 443.1198
3092.5979 | 728.7657 | 434.7576 | 437.6607 | 442.8521
3093.5979 | 729.8498 | 434.4443 | 437.7677 | 442.9236
3094.5979 | 730.4586 | 434.4381 | 437.8781 | 442.9066
3095.5979 | 730.7293 | 434.3595 | 437.9211 | 442.9264
3096.5979 | 730.3188 | 434.3351 | 437.8949 | 443.3939
3097.5979 | 730.7954 | 434.296 | 437.9061 | 443.8833
3098.5979 | 731.1395 | 434.3693 | 438.0431 | 444.0307
3099.5979 | 731.0026 | 434.0384 | 438.1302 | 444.3097
3100.5979 | 730.1658 | 433.8677 | 437.8807 | 444.0953
3101.5979 | 730.1355 | 433.862 | 438.0968 | 444.0653
3102.5979 | 730.5484 | 434.37 | 438.0583 | 443.7211
3103.5979 | 729.6153 | 434.26 | 438.0895 | 443.4935
3104.5979 | 727.3271 | 434.0802 | 437.8285 | 443.3841
3105.5979 | 725.0817 | 433.753 | 437.7433 | 443.5264
3106.5979 | 721.7669 | 433.9135 | 437.8382 | 442.9126
3107.5979 | 721.9024 | 433.8262 | 437.3543 | 442.4697
3108.5979 | 722.0777 | 433.4491 | 436.9566 | 442.2897
3109.5979 | 720.7896 | 433.0994 | 436.6467 | 441.735
3110.5979 | 718.5369 | 432.8581 | 436.7093 | 441.6842
3111.5979 | 716.9836 | 432.7741 | 436.7509 | 441.7941
3112.5979 | 714.9617 | 433.169 | 436.7048 | 441.4898
3113.5979 | 717.2985 | 433.0861 | 436.5434 | 441.5156
3114.5979 | 719.9507 | 432.9876 | 436.3897 | 441.1212
3115.5979 | 719.7648 | 432.9204 | 436.1885 | 441.2531
3116.5979 | 718.9048 | 432.6817 | 435.9918 | 440.9959
3117.5979 | 718.6568 | 432.5866 | 435.7947 | 441.1771
3118.5979 | 719.4686 | 432.6907 | 435.7839 | 440.9265
3119.5979 | 719.0778 | 432.9467 | 435.6168 | 441.2307
3120.5979 | 716.1083 | 432.8729 | 435.5549 | 441.253
3121.5979 | 712.6563 | 433.0677 | 435.5313 | 440.8817
3122.5979 | 709.2639 | 433.6076 | 435.8114 | 440.3719
3123.5979 | 707.0382 | 434.0426 | 435.8076 | 440.2955
3124.5979 | 707.2006 | 434.2499 | 435.9645 | 440.1894
3125.5979 | 706.9611 | 434.3668 | 436.1373 | 440.1993
3126.5979 | 706.748 | 434.772 | 436.6299 | 440.2022
3127.5979 | 707.7674 | 434.7858 | 436.643 | 440.1789
3128.5979 | 708.6147 | 434.6775 | 436.7359 | 440.0502
3129.5979 | 706.9243 | 434.9437 | 437.1517 | 440.4121
3130.6135 | 704.9127 | 435.1433 | 437.5315 | 440.6071
3131.5979 | 704.8213 | 435.8518 | 438.8202 | 441.0555
3132.5979 | 706.7157 | 436.0771 | 438.9955 | 440.9235
3133.5979 | 707.545 | 435.9477 | 438.8264 | 440.9199
3134.5979 | 709.0897 | 436.0749 | 438.6177 | 440.6554
3135.6135 | 711.2271 | 435.744 | 438.3147 | 440.4918
3136.6135 | 711.6396 | 436.354 | 438.9883 | 440.841
3137.6135 | 710.5403 | 436.8434 | 439.1845 | 441.1884
3138.5979 | 709.0138 | 436.5539 | 439.1494 | 440.8735
3139.5979 | 708.0587 | 436.2501 | 438.6331 | 440.5585
3140.5979 | 709.7375 | 436.4019 | 437.8863 | 440.4341
3141.5979 | 712.1524 | 435.9477 | 437.7973 | 440.3968
3142.5979 | 712.4406 | 436.2444 | 437.8261 | 440.0212
3143.5979 | 711.0653 | 435.9724 | 437.9161 | 440.1454
3144.5979 | 710.6022 | 435.6258 | 437.6813 | 440.3533
3145.5979 | 711.9389 | 436.112 | 437.6545 | 440.1994
3146.5979 | 710.7979 | 435.9619 | 437.6439 | 440.2932
3147.5979 | 709.688 | 435.5016 | 437.246 | 440.4383
3148.5979 | 708.5189 | 435.0437 | 436.8276 | 440.1473
3149.5979 | 709.421 | 434.8621 | 436.5283 | 439.8672
3150.5979 | 710.3787 | 434.5044 | 436.3812 | 439.9306
3151.5979 | 710.0514 | 434.0493 | 435.9381 | 439.6041
3152.5979 | 711.5202 | 433.7113 | 435.5905 | 439.3857
3153.5979 | 711.8261 | 433.6281 | 435.5083 | 439.7096
3154.5979 | 712.7607 | 433.7445 | 435.445 | 439.4585
3155.5979 | 715.7314 | 433.9894 | 435.4784 | 439.0313
3156.5979 | 715.26 | 434.063 | 435.4356 | 438.9181
3157.5979 | 713.3402 | 433.8521 | 435.9372 | 438.66
3158.5979 | 711.3173 | 433.5315 | 435.6094 | 439.1347
3159.5979 | 710.4288 | 433.0458 | 435.9395 | 438.7498
3160.5979 | 709.2413 | 433.1061 | 435.7465 | 438.7022
3161.5979 | 709.3077 | 433.0217 | 435.8907 | 438.5603
3162.5979 | 709.0677 | 432.9615 | 435.6624 | 438.0842
3163.5979 | 707.7941 | 432.6018 | 435.1349 | 438.3549
3164.5979 | 706.9633 | 432.3135 | 434.5864 | 437.908
3165.5979 | 706.6574 | 431.9397 | 434.1587 | 437.4904
3166.5979 | 705.8752 | 431.5048 | 433.8091 | 438.0611
3167.5979 | 704.8214 | 431.5169 | 433.9262 | 437.9662
3168.5979 | 703.3543 | 431.5751 | 433.9171 | 437.5255
3169.5979 | 703.2263 | 431.5097 | 433.7614 | 437.2201
3170.5979 | 701.8222 | 431.5043 | 433.382 | 436.8276
3171.5979 | 699.517 | 431.4986 | 433.1591 | 436.613
3172.5979 | 697.4286 | 431.6318 | 433.2548 | 436.867
3173.5979 | 697.1131 | 431.4441 | 433.4391 | 436.929
3174.5979 | 696.9004 | 431.2686 | 433.7583 | 437.123
3175.5979 | 695.6202 | 431.3403 | 433.9419 | 437.3841
3176.5979 | 694.4218 | 431.4163 | 434.079 | 437.8299
3177.5979 | 694.7967 | 431.3437 | 434.1238 | 437.6191
3178.5979 | 694.1429 | 431.1735 | 433.8111 | 436.9698
3179.5979 | 693.8167 | 431.361 | 433.7054 | 436.3779
3180.5979 | 694.1822 | 431.8955 | 433.7168 | 435.9785
3181.5979 | 693.8685 | 431.7529 | 433.8002 | 435.6386
3182.5979 | 692.9351 | 431.3269 | 433.5962 | 435.6684
3183.5979 | 692.1915 | 430.8477 | 433.284 | 435.4595
3184.5979 | 691.837 | 430.6103 | 432.9414 | 435.3208
3185.5979 | 692.3619 | 430.4979 | 432.7184 | 435.2766
3186.5979 | 692.1022 | 430.4367 | 432.5001 | 435.2226
3187.5979 | 691.7561 | 430.2366 | 432.1635 | 435.1635
3188.5979 | 691.7444 | 430.245 | 431.8108 | 434.9293
3189.5979 | 690.9837 | 430.656 | 431.5987 | 434.7387
3190.5979 | 690.627 | 430.5782 | 431.5279 | 435.5048
3191.5979 | 689.601 | 430.7496 | 431.6473 | 435.2299
3192.5979 | 689.6998 | 430.8359 | 431.7529 | 435.0726
3193.5979 | 689.5829 | 430.6688 | 431.6209 | 434.7998
3194.5979 | 689.9136 | 430.5637 | 431.6091 | 435.2949
3195.5979 | 691.6812 | 430.4029 | 431.4394 | 434.9423
3196.5979 | 692.4375 | 430.2947 | 431.3168 | 434.7116
3197.5979 | 691.8692 | 430.1701 | 431.2008 | 434.3293
3198.5979 | 690.8108 | 430.1703 | 431.0703 | 433.8656
3199.5979 | 690.4016 | 430.0075 | 431.046 | 433.266
3200.5979 | 689.1072 | 429.7193 | 430.7835 | 432.8161
3201.5979 | 687.7534 | 429.61 | 430.5002 | 432.4523
3202.5979 | 685.9342 | 429.7561 | 430.2304 | 432.0662
3203.5979 | 684.3059 | 429.7786 | 429.8139 | 431.7929
3204.5979 | 683.8522 | 429.6922 | 429.5449 | 431.433
3205.5979 | 683.529 | 430.082 | 429.177 | 431.7423
3206.5979 | 676.5108 | 453.5657 | 436.2035 | 433.5603
3207.5979 | 682.1384 | 429.126 | 428.5666 | 431.1195
3208.5979 | 680.0571 | 428.8866 | 428.3845 | 430.6549
3209.5979 | 677.6305 | 428.63 | 428.1694 | 430.6215
3210.5979 | 676.0105 | 428.4863 | 427.9678 | 430.3227
3211.5979 | 677.3286 | 428.5778 | 428.3682 | 430.5299
3212.5979 | 677.3799 | 428.7376 | 428.5325 | 430.3599
3213.5979 | 677.7849 | 429.2849 | 428.7014 | 430.2645
3214.5979 | 678.5895 | 429.2649 | 428.6704 | 430.0834
3215.5979 | 678.6221 | 429.4474 | 428.7592 | 430.0167
3216.5979 | 677.6774 | 429.4123 | 429.0171 | 429.9008
3217.5979 | 676.6007 | 429.2468 | 429.063 | 429.8369
3218.5979 | 675.1906 | 429.2847 | 429.2607 | 429.6562
3219.5979 | 675.4498 | 429.1303 | 429.1921 | 430.0153
3220.5979 | 674.3905 | 429.1556 | 429.041 | 429.8027
3221.5979 | 673.625 | 429.4081 | 428.7738 | 429.4758
3222.5979 | 673.4018 | 429.5121 | 428.69 | 429.4345
3223.5979 | 673.517 | 429.3972 | 428.5841 | 429.4584
3224.5979 | 673.0954 | 429.079 | 428.4985 | 429.4448
3225.5979 | 673.6627 | 428.9989 | 428.1142 | 429.4575
3226.5979 | 673.7985 | 428.9917 | 428.2866 | 429.8237
3227.5979 | 673.7636 | 429.3009 | 428.5512 | 430.1242
3228.5979 | 674.0616 | 429.4121 | 428.336 | 430.043
3229.5979 | 674.3075 | 429.4698 | 428.2514 | 429.5412
3230.5979 | 673.7148 | 429.3717 | 428.1735 | 429.5965
3231.5979 | 674.2057 | 429.9347 | 428.277 | 429.7655
3232.5979 | 674.1479 | 430.2644 | 428.2835 | 429.7173
3233.5979 | 675.0069 | 430.0098 | 428.3937 | 429.5247
3234.5979 | 675.2614 | 429.6869 | 428.0993 | 429.1704
3235.5979 | 675.5482 | 429.3071 | 427.9838 | 428.7499
3236.5979 | 675.006 | 429.1524 | 427.652 | 428.5524
3237.5979 | 673.798 | 429.0906 | 427.3086 | 428.0766
3238.5979 | 673.2454 | 429.2794 | 427.5248 | 427.7611
3239.5979 | 672.484 | 429.1431 | 427.5417 | 427.6139
3240.5979 | 673.2683 | 429.2943 | 427.9753 | 427.5071
3241.5979 | 673.2895 | 429.5216 | 428.208 | 427.6396
3242.5979 | 673.5244 | 429.6315 | 428.6263 | 427.4322
3243.5979 | 672.8938 | 429.2913 | 428.9818 | 427.6395
3244.5979 | 670.8177 | 429.2803 | 428.9611 | 427.4496
3245.5979 | 668.4482 | 429.4393 | 428.8253 | 427.3207
3246.5979 | 666.6495 | 430.1729 | 428.7269 | 427.4687
3247.5979 | 666.0025 | 430.2203 | 428.8551 | 427.9437
3248.5979 | 665.5014 | 429.9663 | 429.0008 | 428.2378
3249.5979 | 665.9405 | 429.6281 | 429.1587 | 428.0681
3250.5979 | 665.8324 | 429.4925 | 429.1154 | 427.906
3251.5979 | 665.8078 | 429.3429 | 429.0482 | 427.7238
3252.5979 | 664.5636 | 429.1143 | 428.895 | 427.4541
3253.5979 | 663.3245 | 428.9267 | 428.7932 | 427.5053
3254.5979 | 663.7112 | 428.9699 | 428.7367 | 427.4224
3255.5979 | 663.7148 | 429.1794 | 428.9448 | 427.3293
3256.5979 | 663.2013 | 429.0409 | 429.0328 | 427.073
3257.5979 | 663.5587 | 428.791 | 428.6495 | 426.6944
3258.5979 | 663.2583 | 428.4866 | 428.2751 | 426.0974
3259.5979 | 663.4795 | 428.1145 | 427.8542 | 425.4711
3260.5979 | 663.0714 | 427.8097 | 427.5395 | 424.8097
3261.5979 | 662.4571 | 427.265 | 427.1409 | 424.33
3262.5979 | 662.3668 | 426.8979 | 426.755 | 423.8927
3263.5979 | 662.774 | 426.5989 | 426.8525 | 423.5262
3264.5979 | 662.3445 | 426.1941 | 426.4752 | 423.0096
3265.5979 | 661.3899 | 425.8562 | 426.0254 | 422.5212
3266.5979 | 662.7091 | 425.592 | 425.731 | 422.6727
3267.5979 | 663.5657 | 425.2987 | 425.4303 | 422.6523
3268.5979 | 664.5632 | 425.112 | 425.4611 | 422.609
3269.5979 | 665.6374 | 425.1649 | 425.376 | 422.5201
3270.5979 | 664.4417 | 425.1026 | 425.4163 | 422.6356
3271.5979 | 663.0415 | 425.1465 | 425.0081 | 422.6361
3272.5979 | 661.9068 | 424.8912 | 424.5455 | 422.44
3273.5979 | 662.415 | 424.569 | 424.3724 | 422.474
3274.5979 | 662.8871 | 424.4825 | 423.941 | 422.518
3275.5979 | 662.996 | 424.7969 | 423.6279 | 422.2379
3276.5979 | 662.6582 | 425.2938 | 423.6216 | 422.164
3277.5979 | 661.5664 | 425.2694 | 423.6807 | 422.0143
3278.5979 | 659.7981 | 425.0988 | 423.4027 | 421.8179
3279.5979 | 659.0886 | 424.8226 | 423.0657 | 421.6352
3280.5979 | 656.8 | 424.2573 | 422.5959 | 421.6231
3281.5979 | 655.684 | 424.0213 | 422.1171 | 421.3161
3282.5979 | 654.5627 | 423.7137 | 421.6743 | 420.9754
3283.5979 | 654.1317 | 423.2561 | 421.2954 | 420.8704
3284.5979 | 656.1236 | 422.7041 | 420.8003 | 420.7909
3285.5979 | 657.4236 | 422.3236 | 420.4685 | 420.6314
3286.5979 | 655.1764 | 422.1033 | 420.1739 | 420.5678
3287.5979 | 654.9042 | 421.7506 | 419.9059 | 420.2941
3288.5979 | 655.0434 | 421.3933 | 419.6841 | 420.5223
3289.5979 | 655.2644 | 421.1425 | 419.5455 | 420.456
3290.5979 | 656.1637 | 421.0574 | 419.2905 | 420.6081
3291.5979 | 655.8429 | 420.8425 | 419.1658 | 420.3833
3292.5979 | 655.3503 | 420.8876 | 419.3112 | 420.7529
3293.5979 | 654.6515 | 421.0403 | 419.6495 | 420.656
3294.5979 | 652.9062 | 420.9495 | 419.6724 | 420.6179
3295.5979 | 652.6805 | 420.5592 | 419.2836 | 420.5847
3296.5979 | 652.1957 | 420.2734 | 418.7856 | 420.0575
3297.5979 | 651.6705 | 420.0968 | 418.4243 | 419.6132
3298.5979 | 650.1205 | 420.0048 | 418.2606 | 419.1814
3299.5979 | 648.2158 | 420.0256 | 418.498 | 419.0625
3300.5979 | 648.3611 | 420.1409 | 418.4595 | 419.0221
3301.5979 | 650.5632 | 420.5388 | 418.4978 | 418.8236
3302.5979 | 650.8139 | 420.3693 | 418.3826 | 418.5123
3303.5979 | 650.8179 | 420.1537 | 418.1978 | 418.2148
3304.5979 | 649.97 | 420.1745 | 418.1553 | 418.3392
3305.5979 | 648.1021 | 419.9062 | 417.934 | 417.9964
3306.5979 | 647.2117 | 419.6961 | 417.7858 | 417.9054
3307.5979 | 647.2598 | 419.5731 | 417.3809 | 417.8141
3308.5979 | 648.1934 | 419.064 | 416.907 | 417.8433
3309.5979 | 650.0063 | 418.9641 | 416.7268 | 417.6753
3310.5979 | 651.4809 | 418.7901 | 416.5208 | 417.5792
3311.5979 | 652.6979 | 418.7423 | 416.3598 | 417.4283
3312.5979 | 653.8572 | 418.6499 | 416.1771 | 417.2538
3313.5979 | 652.9643 | 418.3523 | 416.0425 | 417.0196
3314.5979 | 651.7869 | 418.389 | 415.8744 | 416.8348
3315.5979 | 651.4804 | 418.8645 | 416.0436 | 416.7671
3316.5979 | 651.6142 | 419.1734 | 415.9316 | 416.6342
3317.5979 | 652.2888 | 419.0771 | 415.8016 | 416.4493
3318.5979 | 652.359 | 418.9962 | 415.5149 | 416.124
3319.5979 | 652.7213 | 418.922 | 415.7221 | 416.0274
3320.5979 | 653.8856 | 418.8562 | 416.0732 | 415.9897
3321.5979 | 654.382 | 418.5066 | 415.9934 | 415.8105
3322.5979 | 654.7079 | 418.3972 | 416.0444 | 415.5975
3323.6135 | 654.2244 | 418.5879 | 415.8178 | 415.4942
3324.5979 | 654.1959 | 418.6081 | 415.7501 | 415.3967
3325.5979 | 653.4352 | 418.5785 | 415.4178 | 415.113
3326.5979 | 653.0388 | 418.3674 | 415.4757 | 414.7506
3327.5979 | 652.7481 | 418.1925 | 415.3422 | 414.6529
3328.5979 | 652.6973 | 418.1686 | 415.0675 | 414.4014
3329.5979 | 653.5292 | 417.9962 | 414.7575 | 414.018
3330.5979 | 653.6051 | 417.8403 | 414.3417 | 413.7641
3331.5979 | 654.4944 | 417.7496 | 414.1659 | 413.6474
3332.5979 | 654.1363 | 417.8502 | 414.2266 | 413.6581
3333.5979 | 653.0711 | 417.942 | 414.2383 | 413.608
3334.5979 | 651.7561 | 418.0431 | 414.2822 | 413.5831
3335.5979 | 651.9073 | 418.0566 | 414.1965 | 413.2506
3336.5979 | 650.8699 | 417.9825 | 414.2725 | 412.9651
3337.5979 | 649.95 | 418.1952 | 414.7243 | 413.1504
3338.5979 | 649.7261 | 418.2441 | 415.0357 | 413.1643
3339.5979 | 651.3181 | 418.1195 | 414.9264 | 412.9756
3340.5979 | 653.4244 | 418.0408 | 415.1724 | 412.7447
3341.5979 | 654.5545 | 417.7631 | 415.1115 | 412.5272
3342.5979 | 654.4737 | 417.5092 | 414.875 | 412.3215
3343.5979 | 654.098 | 417.4858 | 414.8115 | 412.1683
3344.5979 | 653.2536 | 417.4095 | 414.7583 | 412.1684
3345.5979 | 653.0551 | 417.5 | 414.7939 | 412.1253
3346.5979 | 652.2622 | 417.5297 | 414.8757 | 412.0186
3347.5979 | 652.1953 | 417.655 | 414.9341 | 411.8738
3348.5979 | 653.9978 | 417.626 | 414.8645 | 411.6085
3349.5979 | 654.5556 | 417.4148 | 414.5847 | 411.3564
3350.5979 | 654.3668 | 417.086 | 414.2346 | 411.1001
3351.5979 | 654.869 | 417.0442 | 413.8492 | 410.8326
3352.5979 | 655.1353 | 416.8265 | 413.5203 | 410.6868
3353.5979 | 655.5406 | 416.5442 | 413.4797 | 410.7288
3354.5979 | 655.5362 | 416.1758 | 413.5314 | 410.7304
3355.5979 | 653.9225 | 415.8619 | 413.2777 | 410.4675
3356.5979 | 652.5575 | 415.5189 | 412.9544 | 410.4174
3357.5979 | 651.7205 | 415.1435 | 412.8019 | 410.3519
3358.5979 | 650.3476 | 414.8147 | 412.6109 | 410.1962
3359.5979 | 648.2871 | 414.5284 | 412.2357 | 410.0615
3360.5979 | 646.9147 | 414.4558 | 412.1016 | 409.8579
3361.5979 | 646.3585 | 414.3683 | 412.0293 | 410.0884
3362.5979 | 644.787 | 414.0996 | 411.768 | 409.7827
3363.5979 | 642.4002 | 413.7901 | 411.6135 | 409.6936
3364.5979 | 641.2565 | 413.5325 | 411.2288 | 409.5523
3365.5979 | 641.8493 | 413.1361 | 410.9011 | 409.4841
3366.5979 | 641.7304 | 412.7753 | 410.6545 | 409.297
3367.5979 | 641.8086 | 412.6391 | 410.511 | 409.1949
3368.5979 | 641.6791 | 412.4347 | 410.4252 | 409.16
3369.5979 | 641.4985 | 412.1353 | 410.0792 | 409.1106
3370.5979 | 641.3751 | 411.84 | 409.7861 | 408.9374
3371.5979 | 640.3705 | 411.5575 | 409.3887 | 408.6067
3372.5979 | 640.1028 | 411.5246 | 409.1625 | 408.6087
3373.5979 | 639.9862 | 411.5077 | 408.9317 | 408.647
3374.5979 | 639.5308 | 411.3736 | 409.1409 | 408.5452
3375.5979 | 638.654 | 411.0984 | 409.1647 | 408.7518
3376.5979 | 638.463 | 410.8751 | 409.0716 | 408.8227
3377.5979 | 638.192 | 410.9323 | 409.0847 | 408.7386
3378.5979 | 638.0606 | 411.3247 | 409.2573 | 408.8228
3379.5979 | 638.8609 | 411.3279 | 409.2752 | 408.7982
3380.5979 | 638.9866 | 411.1538 | 409.1581 | 408.6991
3381.5979 | 639.213 | 411.0337 | 409.0774 | 408.4345
3382.5979 | 639.8926 | 410.9307 | 408.9553 | 408.305
3383.5979 | 639.8603 | 410.7859 | 408.7946 | 408.0341
3384.5979 | 640.9914 | 410.8479 | 408.7258 | 407.7716
3385.5979 | 641.8556 | 410.7301 | 408.5384 | 407.4927
3386.5979 | 642.4049 | 410.554 | 408.3093 | 407.2461
3387.5979 | 642.0282 | 410.2905 | 407.8798 | 407.218
3388.5979 | 641.007 | 410.3482 | 407.5546 | 406.934
3389.5979 | 639.4633 | 410.2307 | 407.4798 | 406.8245
3390.5979 | 637.9891 | 409.9768 | 407.2553 | 406.8196
3391.5979 | 637.3629 | 409.7617 | 407.3504 | 406.6746
3392.5979 | 636.8178 | 409.5791 | 407.3541 | 406.2994
3393.5979 | 637.1626 | 409.4714 | 407.2881 | 406.2363
3394.5979 | 638.6994 | 409.5692 | 407.1526 | 406.2417
3395.5979 | 639.0395 | 409.4082 | 407.1899 | 406.3774
3396.5979 | 638.802 | 409.2442 | 407.0074 | 406.2544
3397.5979 | 637.4136 | 409.0972 | 406.7973 | 406.1257
3398.5979 | 636.2014 | 408.9346 | 406.6938 | 406.0039
3399.5979 | 635.1826 | 408.7148 | 406.45 | 405.8954
3400.5979 | 635.8522 | 408.7214 | 406.1474 | 406.198
3401.5979 | 637.443 | 408.6102 | 405.9825 | 405.9292
3402.5979 | 637.3359 | 408.4159 | 405.7912 | 405.8085
3403.5979 | 637.4729 | 408.249 | 405.6646 | 405.6873
3404.5979 | 638.423 | 408.0359 | 405.6981 | 405.6759
3405.5979 | 640.0424 | 407.6499 | 405.5482 | 405.445
3406.5979 | 640.0747 | 407.3255 | 405.2507 | 405.1398
3407.5979 | 639.1349 | 407.2364 | 404.8252 | 404.958
3408.5979 | 639.5983 | 407.318 | 404.6334 | 404.8976
3409.5979 | 639.296 | 407.1698 | 404.4951 | 404.7719
3410.5979 | 638.5837 | 406.9223 | 404.2164 | 404.611
3411.5979 | 638.3599 | 406.5023 | 403.8556 | 404.4994
3412.5979 | 637.7413 | 406.1815 | 403.6844 | 404.2864
3413.5979 | 637.116 | 406.0876 | 403.5136 | 404.1277
3414.5979 | 637.2098 | 406.1073 | 403.4626 | 404.0002
3415.5979 | 637.5889 | 406.0607 | 403.3686 | 403.8219
3416.5979 | 637.2059 | 406.034 | 403.288 | 403.7105
3417.5979 | 637.3574 | 405.9138 | 403.5112 | 403.9731
3418.5979 | 637.6793 | 405.9481 | 403.7141 | 403.8642
3419.5979 | 637.6297 | 406.2696 | 403.9642 | 403.8367
3420.5979 | 636.971 | 406.2977 | 403.8367 | 403.6096
3421.5979 | 636.149 | 406.4152 | 403.7488 | 403.337
3422.5979 | 635.1829 | 406.4127 | 403.3398 | 403.1782
3423.5979 | 634.544 | 406.3791 | 403.0452 | 403.0339
3424.5979 | 634.1694 | 406.3635 | 403.0022 | 402.7542
3425.5979 | 633.9727 | 406.3175 | 403.0882 | 402.9016
3426.5979 | 633.531 | 406.186 | 403.0894 | 402.9329
3427.5979 | 633.9816 | 406.0425 | 402.9849 | 402.7727
3428.5979 | 634.5601 | 405.9509 | 403.3107 | 402.6003
3429.5979 | 635.1845 | 405.8394 | 403.348 | 402.4917
3430.5979 | 635.6048 | 405.7405 | 403.3683 | 402.2301
3431.5979 | 635.8179 | 405.6579 | 403.2281 | 401.9962
3432.5979 | 635.7878 | 405.614 | 403.0743 | 401.7911
3433.5979 | 635.557 | 405.5066 | 402.9631 | 401.5459
3434.5979 | 635.6876 | 405.423 | 402.7659 | 401.3375
3435.5979 | 635.0559 | 405.2764 | 402.4769 | 401.0431
3436.5979 | 634.8128 | 405.1637 | 402.49 | 400.7859
3437.5979 | 634.6899 | 404.8986 | 402.2487 | 400.5189
3438.5979 | 633.9496 | 404.6966 | 401.8506 | 400.3518
3439.5979 | 633.214 | 404.4922 | 401.5433 | 400.1141
3440.5979 | 632.6882 | 404.4283 | 401.4362 | 399.8797
3441.5979 | 633.0499 | 404.1891 | 401.254 | 400.097
3442.5979 | 633.6384 | 403.9178 | 401.0893 | 399.9148
3443.5979 | 633.0915 | 403.6202 | 400.7683 | 399.5445
3444.5979 | 633.2036 | 403.4278 | 400.5415 | 399.4351
3445.5979 | 632.8451 | 403.2927 | 400.2805 | 399.19
3446.5979 | 632.1673 | 403.1717 | 399.9854 | 398.9463
3447.5979 | 632.309 | 403.0572 | 399.9766 | 398.7596
3448.5979 | 633.3752 | 403.1756 | 400.2606 | 398.7384
3449.5979 | 634.8204 | 403.1394 | 400.2208 | 398.652
3450.5979 | 635.8632 | 403.1892 | 400.1356 | 398.5002
3451.5979 | 636.2402 | 403.0715 | 399.8501 | 398.3137
3452.5979 | 636.5856 | 402.9665 | 399.6179 | 398.0455
3453.5979 | 636.591 | 402.8352 | 399.7784 | 398.0022
3454.5979 | 636.3816 | 402.6982 | 399.6662 | 397.8893
3455.5979 | 635.6025 | 402.6029 | 399.4744 | 397.5257
3456.5979 | 633.9848 | 402.6102 | 399.4869 | 397.29
3457.5979 | 633.9758 | 402.5539 | 399.5307 | 397.1289
3458.5979 | 633.9958 | 402.432 | 399.3833 | 397.0527
3459.5979 | 632.2258 | 402.5368 | 399.3577 | 396.9839
3460.5979 | 629.3509 | 402.3731 | 399.0687 | 396.8943
3461.5979 | 626.3542 | 402.2861 | 398.691 | 396.7362
3462.5979 | 623.7875 | 401.9581 | 398.4867 | 396.4206
3463.5979 | 621.2551 | 401.559 | 398.1531 | 396.0905
3464.5979 | 619.062 | 401.0326 | 397.6863 | 395.793
3465.5979 | 616.4462 | 400.4463 | 397.4225 | 395.3729
3466.5979 | 614.0328 | 399.817 | 397.0761 | 394.8408
3467.5979 | 611.3997 | 399.0865 | 396.3586 | 394.4085
3468.5979 | 609.5273 | 398.4618 | 395.8708 | 394.1471
3469.5979 | 607.8248 | 397.9016 | 395.2695 | 393.5817
3470.5979 | 605.8783 | 397.4223 | 394.6148 | 393.1067
3471.5979 | 604.2692 | 396.7467 | 394.0365 | 392.7179
3472.5979 | 603.1882 | 396.1751 | 393.3753 | 392.2211
3473.5979 | 601.9939 | 395.8162 | 393.2296 | 391.99
3474.5979 | 600.4194 | 395.3722 | 392.8109 | 391.9853
3475.5979 | 598.5824 | 394.846 | 392.3617 | 391.4982
3476.5979 | 596.6592 | 394.3589 | 392.0099 | 391.0071
3477.5979 | 595.713 | 393.8533 | 391.5971 | 390.5109
3478.5979 | 594.6595 | 393.4062 | 391.034 | 390.0684
3479.5979 | 593.37 | 392.9219 | 390.6507 | 389.6475
3480.5979 | 592.3391 | 392.3493 | 390.2322 | 389.268
3481.5979 | 591.685 | 391.7534 | 389.7976 | 388.8517
3482.5979 | 591.0498 | 391.3789 | 389.2033 | 388.6407
3483.5979 | 590.0965 | 390.9327 | 388.9708 | 388.4634
3484.5979 | 589.5654 | 390.6354 | 388.6151 | 388.3998
3485.5979 | 588.9903 | 390.3695 | 388.2676 | 388.6436
3486.5979 | 588.7476 | 390.1905 | 388.0767 | 388.7723
3487.5979 | 588.4972 | 389.947 | 387.8816 | 388.8457
3488.5979 | 586.9955 | 389.6521 | 387.7603 | 388.7255
3489.5979 | 587.0401 | 389.2898 | 387.5479 | 388.6999
3490.5979 | 587.042 | 389.0059 | 387.2693 | 388.5116
3491.5979 | 586.8021 | 388.6881 | 386.9406 | 388.3429
3492.5979 | 586.5257 | 388.4984 | 386.6164 | 388.0931
3493.5979 | 586.0124 | 388.2573 | 386.1021 | 387.8025
3494.5979 | 585.0653 | 388.0696 | 385.8115 | 387.7336
3495.5979 | 584.5132 | 387.7614 | 385.7519 | 387.8287
3496.5979 | 583.9926 | 387.4839 | 385.9883 | 387.8017
3497.5979 | 583.4946 | 387.1713 | 385.7456 | 387.7641
3498.5979 | 583.2216 | 387.0847 | 385.7706 | 387.8136
3499.5979 | 582.6939 | 387.1126 | 385.8814 | 387.7346
3500.5979 | 582.0478 | 387.1482 | 385.9817 | 387.583
3501.5979 | 581.9983 | 387.1638 | 386.0096 | 387.4605
3502.5979 | 581.9992 | 386.9259 | 385.9693 | 387.4337
3503.5979 | 581.8332 | 386.5792 | 385.5603 | 386.9757
3504.5979 | 581.2883 | 386.1989 | 385.2721 | 386.5507
3505.5979 | 580.7333 | 385.763 | 384.7019 | 386.184
3506.5979 | 580.1187 | 385.3232 | 384.5369 | 385.8972
3507.5979 | 579.8084 | 385.0652 | 384.4879 | 385.7088
3508.5979 | 578.8833 | 384.6936 | 384.6612 | 385.5121
3509.5979 | 577.7935 | 384.3341 | 384.6206 | 385.1896
3510.5979 | 576.7594 | 383.9339 | 384.2003 | 385.0231
3511.5979 | 576.331 | 383.6751 | 383.8323 | 384.7298
3512.5979 | 576.4442 | 383.3815 | 383.5586 | 384.4146
3513.5979 | 577.1497 | 383.1422 | 382.9868 | 384.1606
3514.5979 | 577.1974 | 382.9576 | 382.5587 | 384.0634
3515.5979 | 577.8922 | 382.8347 | 382.1215 | 384.1029
3516.5979 | 579.5687 | 382.5872 | 381.8547 | 384.0432
3517.5979 | 581.704 | 382.3184 | 381.7559 | 384.1014
3518.5979 | 584.3072 | 382.2576 | 381.7995 | 384.1049
3519.5979 | 586.3852 | 382.271 | 381.7594 | 383.9954
3520.5979 | 587.4653 | 382.3185 | 381.7798 | 383.9118
3521.5979 | 589.3832 | 382.4444 | 381.874 | 384.1893
3522.5979 | 591.2661 | 382.5355 | 382.012 | 384.3758
3523.5979 | 593.0954 | 382.71 | 382.0467 | 384.3645
3524.5979 | 594.0712 | 382.9766 | 382.4844 | 384.4955
3525.5979 | 594.7797 | 383.2329 | 383.5797 | 384.6269
3526.5979 | 596.2712 | 383.6205 | 383.7843 | 385.0368
3527.5979 | 598.0228 | 383.8589 | 383.8362 | 385.0586
3528.5979 | 598.828 | 384.2158 | 383.8997 | 384.9816
3529.5979 | 599.4537 | 384.5129 | 383.9483 | 385.0702
3530.5979 | 599.5842 | 384.9631 | 384.0011 | 385.1684
3531.5979 | 601.1311 | 385.1599 | 383.943 | 385.1342
3532.5979 | 602.7635 | 385.5386 | 383.908 | 385.2106
3533.5979 | 603.6933 | 385.4575 | 383.7048 | 385.0765
3534.5979 | 604.3775 | 385.3149 | 383.822 | 384.9238
3535.5979 | 604.7371 | 385.2024 | 383.7684 | 384.9423
3536.5979 | 602.8378 | 385.1584 | 383.7241 | 384.9232
3537.5979 | 602.3016 | 384.9993 | 383.7673 | 385.366
3538.5979 | 602.2768 | 385.0441 | 383.9058 | 385.4714
3539.5979 | 602.3321 | 385.0499 | 384.0763 | 385.4027
3540.5979 | 602.4317 | 384.857 | 384.043 | 385.3531
3541.5979 | 602.5313 | 384.7294 | 383.9238 | 385.2558
3542.5979 | 602.6697 | 384.6334 | 383.9041 | 385.1036
3543.5979 | 603.6322 | 384.4886 | 384.3987 | 385.2078
3544.5979 | 605.981 | 384.3579 | 384.3894 | 385.222
3545.5979 | 607.4684 | 384.2832 | 384.2875 | 385.2098
3546.5979 | 608.2559 | 384.1582 | 384.2214 | 385.0476
3547.6135 | 608.3634 | 383.9991 | 384.1305 | 384.9216
3548.5979 | 609.4144 | 383.8155 | 383.9352 | 384.8103
3549.5979 | 610.1323 | 383.6122 | 383.711 | 384.6824
3550.5979 | 609.7046 | 383.4725 | 383.3511 | 384.6283
3551.5979 | 610.7709 | 383.4263 | 383.0737 | 384.4312
3552.5979 | 611.1583 | 383.4773 | 382.9615 | 384.1812
3553.5979 | 610.9997 | 383.4247 | 382.9769 | 384.5875
3554.5979 | 610.7063 | 383.3927 | 382.9865 | 384.5146
3555.5979 | 610.4895 | 383.4731 | 382.999 | 384.4025
3556.5979 | 611.0295 | 383.363 | 383.1037 | 384.5074
3557.5979 | 610.9747 | 383.4147 | 383.2523 | 384.8228
3558.5979 | 610.5168 | 383.2003 | 383.2051 | 384.7989
3559.5979 | 609.5553 | 383.1001 | 383.08 | 384.7203
3560.5979 | 609.8789 | 383.0619 | 382.8258 | 384.7633
3561.5979 | 610.3377 | 382.8783 | 382.6756 | 384.5929
3562.5979 | 609.9441 | 382.6407 | 382.4932 | 384.2467
3563.5979 | 609.3602 | 382.5118 | 382.4534 | 384.0555
3564.5979 | 608.2757 | 382.5187 | 382.2237 | 383.996
3565.5979 | 606.2983 | 382.6161 | 381.9562 | 383.7293
3566.5979 | 605.4976 | 382.6339 | 381.8919 | 383.7543
3567.5979 | 604.7967 | 382.7036 | 381.8425 | 383.6138
3568.5979 | 604.9364 | 382.6464 | 382.1437 | 384.0671
3569.5979 | 604.2568 | 382.5411 | 382.2723 | 384.3368
3570.5979 | 604.8578 | 382.4762 | 382.4323 | 384.1237
3571.5979 | 604.4241 | 382.3517 | 382.8054 | 384.3598
3572.5979 | 604.8052 | 382.3005 | 382.7548 | 384.3896
3573.5979 | 604.3725 | 382.4588 | 382.8728 | 384.4185
3574.6135 | 603.8664 | 382.5546 | 383.3472 | 384.8008
3575.5979 | 605.1353 | 382.5944 | 383.382 | 384.7956
3576.5979 | 605.4896 | 382.6589 | 383.238 | 384.4457
3577.5979 | 604.9124 | 382.5236 | 382.9729 | 384.4095
3578.5979 | 603.7191 | 382.5681 | 382.8311 | 384.4041
3579.5979 | 602.5897 | 382.7904 | 382.8015 | 384.151
3580.5979 | 602.1122 | 382.9351 | 382.8993 | 383.8587
3581.5979 | 601.9407 | 382.8303 | 383.1873 | 383.9607
3582.5979 | 602.1987 | 382.7222 | 382.9264 | 383.9343
3583.5979 | 602.7052 | 382.584 | 382.6112 | 383.675
3584.5979 | 603.574 | 382.4768 | 382.3285 | 383.3582
3585.5979 | 604.5662 | 382.3184 | 382.0234 | 383.0961
3586.5979 | 604.2842 | 382.0754 | 381.7929 | 382.982
3587.5979 | 604.3843 | 381.8718 | 381.5775 | 382.8003
3588.5979 | 604.6421 | 381.7349 | 381.4852 | 382.6369
3589.5979 | 604.5559 | 381.6578 | 381.381 | 382.6101
3590.5979 | 604.2905 | 381.4981 | 381.3402 | 382.6748
3591.5979 | 604.2082 | 381.5074 | 381.3617 | 382.5893
3592.5979 | 604.0321 | 381.5372 | 381.2912 | 382.6069
3593.5979 | 604.5254 | 381.5291 | 381.3469 | 382.5688
3594.5979 | 604.0441 | 381.4662 | 381.3386 | 382.8653
3595.5979 | 603.4728 | 381.5733 | 381.254 | 382.9262
3596.5979 | 602.594 | 381.3866 | 381.3338 | 383.1481
3597.5979 | 601.1069 | 381.2274 | 381.8464 | 383.1577
3598.5979 | 599.6689 | 381.0639 | 381.6535 | 383.2358
3599.5979 | 598.5097 | 381.001 | 381.3959 | 382.9233
3600.5979 | 597.2894 | 380.9117 | 381.1533 | 382.6342
3601.5979 | 596.6641 | 380.8008 | 380.913 | 382.6042
3602.5979 | 596.1424 | 380.6953 | 380.7271 | 382.4276
3603.5979 | 594.7708 | 380.6365 | 380.4661 | 382.0693
3604.6135 | 593.9747 | 380.6839 | 380.2597 | 381.6784
3605.5979 | 594.0488 | 380.5926 | 380.0753 | 381.4567
3606.5979 | 594.3432 | 380.6342 | 379.8474 | 381.5364
3607.5979 | 594.052 | 380.6099 | 379.7723 | 381.2807
3608.5979 | 593.7964 | 380.8263 | 380.1574 | 381.1501
3609.5979 | 593.2036 | 380.8883 | 379.8996 | 381.1493
3610.5979 | 593.1231 | 380.8441 | 379.9375 | 381.019
3611.5979 | 593.5359 | 380.7991 | 379.8235 | 381.007
3612.5979 | 594.4572 | 380.8398 | 379.7317 | 380.7545
3613.5979 | 595.5541 | 380.817 | 379.5466 | 380.4247
3614.5979 | 596.0058 | 380.6774 | 379.3394 | 380.2333
3615.5979 | 595.9798 | 380.6318 | 379.3842 | 379.9925
3616.5979 | 596.052 | 380.6266 | 379.2845 | 379.7542
3617.5979 | 597.2607 | 380.6473 | 379.3621 | 379.5065
3618.5979 | 598.0261 | 380.5424 | 379.1949 | 379.548
3619.5979 | 598.9988 | 380.4713 | 379.1485 | 379.3177
3620.5979 | 599.1686 | 380.6458 | 379.1042 | 379.203
3621.5979 | 598.6674 | 380.7052 | 379.0488 | 379.5685
3622.5979 | 598.2779 | 380.7438 | 378.9752 | 379.5264
3623.5979 | 598.0599 | 380.6265 | 378.7909 | 379.4276
3624.5979 | 598.4538 | 380.5631 | 378.6083 | 379.3812
3625.5979 | 598.0755 | 380.3594 | 378.4206 | 379.2257
3626.5979 | 598.9974 | 380.3756 | 378.2679 | 379.1491
3627.5979 | 599.8493 | 380.2368 | 378.1912 | 379.1388
3628.5979 | 601.035 | 380.15 | 378.0772 | 379.0946
3629.5979 | 601.2221 | 380.0534 | 378.0266 | 378.9171
3630.5979 | 601.1742 | 379.8944 | 378.211 | 378.9044
3631.5979 | 600.6146 | 379.7746 | 378.1304 | 379.1204
3632.5979 | 599.9385 | 379.5744 | 377.9465 | 378.9578
3633.5979 | 599.9624 | 379.4173 | 377.7524 | 378.7568
3634.5979 | 600.5118 | 379.3122 | 377.4876 | 378.596
3635.5979 | 601.5414 | 379.1207 | 377.2686 | 378.297
3636.5979 | 602.9575 | 378.862 | 377.0892 | 378.0243
3637.5979 | 603.9717 | 378.7331 | 377.0346 | 377.9491
3638.5979 | 603.5721 | 378.6529 | 376.9714 | 378.0047
3639.5979 | 602.6343 | 378.5937 | 376.705 | 377.7952
3640.5979 | 601.6029 | 378.6821 | 376.4673 | 377.5522
3641.5979 | 601.2195 | 378.6866 | 376.2927 | 377.3954
3642.5979 | 600.0152 | 378.6007 | 376.2903 | 377.3229
3643.5979 | 598.7511 | 378.6481 | 376.4274 | 377.4958
3644.5979 | 597.9534 | 378.6227 | 376.3914 | 377.434
3645.5979 | 598.8787 | 378.5832 | 376.5274 | 377.3204
3646.5979 | 599.5991 | 378.4894 | 376.4889 | 377.0822
3647.5979 | 600.0298 | 378.3981 | 376.5624 | 376.8888
3648.5979 | 600.4235 | 378.2394 | 376.4817 | 376.9004
3649.5979 | 600.0823 | 378.0313 | 376.2805 | 376.7335
3650.5979 | 600.0758 | 377.828 | 375.9563 | 376.7673
3651.5979 | 599.8924 | 377.8554 | 375.5737 | 376.7827
3652.5979 | 598.7159 | 377.8172 | 375.3235 | 376.7899
3653.5979 | 597.3077 | 377.6011 | 375.259 | 376.7896
3654.5979 | 596.4373 | 377.3971 | 374.7549 | 376.9396
3655.5979 | 595.8538 | 377.4027 | 375.4182 | 376.9649
3656.5979 | 595.9348 | 377.2464 | 375.6573 | 377.755
3657.6135 | 596.417 | 377.0812 | 375.469 | 377.6331
3658.5979 | 596.5077 | 377.08 | 375.2795 | 377.87
3659.5979 | 596.9246 | 377.1557 | 375.1879 | 377.8942
3660.5979 | 596.3856 | 377.0792 | 375.064 | 377.7596
3661.5979 | 596.1389 | 376.9445 | 374.9569 | 377.5169
3662.5979 | 596.1088 | 376.8276 | 374.825 | 377.2644
3663.5979 | 595.9549 | 376.6706 | 374.6065 | 377.3906
3664.5979 | 595.8769 | 376.4738 | 374.4106 | 377.1711
3665.5979 | 595.0197 | 376.36 | 374.313 | 377.1385
3666.5979 | 593.4626 | 376.2192 | 374.2872 | 376.8693
3667.5979 | 592.9055 | 376.0807 | 374.1432 | 376.9496
3668.5979 | 592.7316 | 376.1428 | 374.1425 | 376.9167
3669.5979 | 592.7964 | 376.1487 | 374.0334 | 376.6427
3670.5979 | 592.6426 | 376.112 | 373.9574 | 376.3398
3671.5979 | 591.9272 | 376.0477 | 373.6275 | 375.9972
3672.5979 | 591.209 | 375.9519 | 373.4246 | 375.7585
3673.5979 | 590.489 | 375.8792 | 373.2668 | 375.4596
3674.5979 | 590.4292 | 375.7561 | 373.1675 | 375.3028
3675.5979 | 590.3646 | 375.6651 | 373.1354 | 375.1412
3676.5979 | 590.4058 | 375.5651 | 372.997 | 374.8846
3677.5979 | 590.9135 | 375.437 | 372.829 | 374.6353
3678.5979 | 590.6549 | 375.4239 | 372.8919 | 374.5784
3679.5979 | 590.2131 | 375.3783 | 373.0135 | 374.9355
3680.5979 | 589.873 | 375.3287 | 373.0478 | 374.9506
3681.5979 | 589.8313 | 375.2112 | 373.0838 | 375.1382
3682.5979 | 590.4827 | 375.0353 | 372.9512 | 375.1362
3683.5979 | 591.2753 | 374.8258 | 372.6977 | 374.9321
3684.5979 | 591.3458 | 374.6228 | 372.5032 | 374.6194
3685.6135 | 590.8554 | 374.5025 | 372.3105 | 374.4615
3686.5979 | 590.3408 | 374.4008 | 372.1765 | 374.4688
3687.5979 | 589.8462 | 374.2796 | 372.0818 | 374.277
3688.5979 | 589.4343 | 374.0872 | 371.8953 | 374.3882
3689.5979 | 589.858 | 374.0119 | 371.8188 | 374.2992
3690.5979 | 590.8172 | 373.8993 | 371.6953 | 374.4734
3691.5979 | 591.509 | 373.8829 | 371.5117 | 374.2484
3692.5979 | 592.7573 | 373.8637 | 371.5559 | 374.1119
3693.5979 | 592.6728 | 373.7804 | 371.5296 | 374.1688
3694.6135 | 591.6347 | 373.8378 | 371.4788 | 373.9957
3695.5979 | 591.8764 | 373.844 | 371.644 | 373.9204
3696.5979 | 592.5188 | 373.8367 | 371.6356 | 373.9787
3697.5979 | 592.4471 | 373.7958 | 371.5421 | 373.7592
3698.5979 | 592.7375 | 373.6934 | 371.4231 | 373.5656
3699.5979 | 591.6816 | 373.5572 | 371.2793 | 373.6569
3700.5979 | 591.2227 | 373.5898 | 371.3999 | 373.8996
3701.5979 | 590.5071 | 373.7379 | 371.4787 | 373.8878
3702.5979 | 589.7029 | 373.6914 | 371.4521 | 373.9717
3703.5979 | 589.603 | 373.7059 | 371.6633 | 373.7997
3704.5979 | 590.5507 | 373.6486 | 371.5802 | 373.8693
3705.5979 | 591.5948 | 373.5009 | 371.5243 | 373.7113
3706.5979 | 592.5391 | 373.4072 | 371.4923 | 373.6219
3707.5979 | 593.3289 | 373.316 | 371.4329 | 373.518
3708.5979 | 594.0941 | 373.2229 | 371.3159 | 373.3488
3709.5979 | 594.8311 | 373.1535 | 371.4966 | 373.1414
3710.5979 | 594.2888 | 373.0803 | 371.4707 | 373.2254
3711.5979 | 593.3949 | 372.9847 | 371.4366 | 373.1416
3712.5979 | 593.9586 | 372.9267 | 371.429 | 373.1449
3713.5979 | 594.2506 | 372.7442 | 371.2293 | 372.9592
3714.5979 | 593.7027 | 372.6362 | 371.1137 | 373.0174
3715.5979 | 592.8795 | 372.5721 | 371.0898 | 373.0323
3716.5979 | 591.4441 | 372.4609 | 371.0893 | 373.0127
3717.5979 | 590.7619 | 372.4571 | 371.0929 | 372.9193
3718.5979 | 589.2814 | 372.4849 | 371.3128 | 373.0177
3719.5979 | 587.7449 | 372.3443 | 371.2886 | 373.4415
3720.5979 | 585.9972 | 372.5144 | 371.4792 | 373.6334
3721.5979 | 585.3187 | 372.5799 | 371.7293 | 373.8752
3722.5979 | 584.8517 | 372.6 | 371.7535 | 373.8025
3723.5979 | 584.9645 | 372.6252 | 371.928 | 374.0542
3724.5979 | 586.0433 | 372.9052 | 371.8321 | 374.0561
3725.5979 | 586.9354 | 372.762 | 371.6133 | 374.2929
3726.5979 | 587.9361 | 372.5878 | 371.6944 | 374.261
3727.5979 | 589.3848 | 372.4775 | 371.5738 | 374.0558
3728.5979 | 590.9154 | 372.3944 | 371.4972 | 374.2134
3729.5979 | 590.8217 | 372.3798 | 371.6163 | 374.6667
3730.5979 | 590.2198 | 372.5653 | 371.6462 | 374.6909
3731.5979 | 589.6781 | 372.632 | 371.6044 | 374.591
3732.5979 | 590.2322 | 372.5665 | 371.5918 | 374.6265
3733.5979 | 590.7286 | 372.2979 | 371.4736 | 374.8457
3734.5979 | 591.4481 | 372.0442 | 371.3996 | 374.8767
3735.5979 | 591.5741 | 371.8478 | 371.5084 | 374.6123
3736.5979 | 591.2648 | 371.7106 | 371.5429 | 374.7008
3737.5979 | 591.1148 | 371.6185 | 371.4257 | 374.9364
3738.5979 | 591.0327 | 371.5743 | 371.2839 | 374.6923
3739.5979 | 591.2559 | 371.5095 | 371.1086 | 374.5515
3740.5979 | 591.8414 | 371.3803 | 370.9905 | 374.3211
3741.5979 | 592.2796 | 371.1967 | 370.7497 | 374.2403
3742.5979 | 591.5251 | 371.3078 | 370.5814 | 373.9164
3743.5979 | 590.1385 | 371.3154 | 370.7588 | 374.2013
3744.5979 | 589.1534 | 371.2673 | 370.668 | 374.0985
3745.5979 | 587.6978 | 371.2386 | 370.7289 | 373.8946
3746.5979 | 586.4009 | 371.296 | 370.7364 | 373.9783
3747.5979 | 585.2822 | 371.3159 | 370.6653 | 373.9345
3748.5979 | 584.3981 | 371.2437 | 370.5802 | 373.7388
3749.5979 | 583.3286 | 371.0418 | 370.5962 | 373.4512
3750.5979 | 582.1065 | 370.9895 | 370.6967 | 373.289
3751.5979 | 580.964 | 370.8267 | 370.7866 | 373.1153
3752.5979 | 579.5021 | 370.811 | 370.6796 | 373.1654
3753.5979 | 579.4564 | 370.8183 | 370.6647 | 372.9051
3754.5979 | 580.0337 | 370.7204 | 370.6194 | 372.9813
3755.5979 | 580.0415 | 370.6439 | 370.3328 | 372.9461
3756.5979 | 580.2277 | 370.8131 | 370.3147 | 372.5461
3757.5979 | 579.9901 | 370.8864 | 370.0987 | 372.3241
3758.5979 | 579.8293 | 371.0118 | 370.0791 | 372.1738
3759.5979 | 579.4705 | 370.9011 | 369.9809 | 372.1623
3760.5979 | 578.9385 | 370.7331 | 369.8332 | 372.0133
3761.5979 | 578.6473 | 370.659 | 369.6073 | 371.8786
3762.5979 | 578.7746 | 370.4943 | 369.4172 | 371.8755
3763.5979 | 578.422 | 370.3728 | 369.2215 | 371.7302
3764.5979 | 577.7184 | 370.2169 | 369.219 | 371.4968
3765.5979 | 578.2084 | 370.2941 | 369.2978 | 371.382
3766.5979 | 580.1983 | 370.2417 | 368.9948 | 371.187
3767.5979 | 580.1932 | 370.0557 | 368.6396 | 370.7751
3768.5979 | 581.9513 | 370.0701 | 368.4602 | 370.4435
3769.5979 | 582.8414 | 370.0678 | 368.6519 | 370.423
3770.5979 | 583.5356 | 369.928 | 368.5153 | 370.5754
3771.5979 | 584.1937 | 369.7485 | 368.3838 | 370.4934
3772.5979 | 584.946 | 369.7055 | 368.0907 | 370.3142
3773.5979 | 586.4256 | 369.5241 | 367.9596 | 370.5003
3774.5979 | 587.5363 | 369.4099 | 367.8427 | 370.5706
3775.5979 | 588.0904 | 369.4097 | 367.78 | 370.4535
3776.5979 | 587.4392 | 369.6721 | 367.7497 | 370.4325
3777.5979 | 585.9436 | 369.6921 | 367.7619 | 370.4985
3778.5979 | 585.3535 | 369.6802 | 367.9235 | 370.7731
3779.5979 | 585.3353 | 369.4681 | 367.8881 | 370.8502
3780.5979 | 585.1911 | 369.1613 | 367.6163 | 370.5895
3781.5979 | 584.9139 | 368.8791 | 367.3304 | 370.3964
3782.5979 | 583.9321 | 368.7237 | 367.0837 | 370.2884
3783.5979 | 583.5422 | 368.7083 | 366.9425 | 370.096
3784.5979 | 583.1395 | 368.8478 | 367.1166 | 370.3585
3785.5979 | 583.1674 | 369.0778 | 367.18 | 370.7108
3786.5979 | 583.2941 | 369.1606 | 367.0423 | 370.6044
3787.5979 | 582.9077 | 369.1597 | 366.8597 | 370.5542
3788.5979 | 582.5294 | 369.0771 | 366.6059 | 370.2959
3789.5979 | 582.9 | 369.0214 | 366.336 | 370.0156
3790.5979 | 583.2086 | 368.9328 | 366.192 | 369.8469
3791.5979 | 582.8496 | 368.7821 | 365.9609 | 369.5531
3792.5979 | 582.5093 | 368.7462 | 365.9716 | 369.535
3793.5979 | 582.7583 | 368.9559 | 366.0491 | 369.8831
3794.5979 | 583.0216 | 368.8334 | 365.8989 | 369.7817
3795.5979 | 583.2712 | 368.6056 | 365.6578 | 369.4857
3796.5979 | 583.189 | 368.4294 | 365.4561 | 369.4147
3797.5979 | 583.8558 | 368.3539 | 365.2786 | 369.3253
3798.5979 | 583.9114 | 368.1937 | 365.1685 | 369.1385
3799.5979 | 583.0607 | 368.0149 | 364.8832 | 368.8112
3800.5979 | 582.2874 | 368.0321 | 364.8172 | 368.4555
3801.5979 | 581.479 | 368.0132 | 364.9037 | 368.4607
3802.5979 | 580.2052 | 367.8685 | 365.3469 | 368.473
3803.5979 | 579.7991 | 367.8669 | 365.4823 | 368.6686
3804.5979 | 578.9819 | 368.2218 | 365.714 | 368.7658
3805.5979 | 578.3694 | 368.4331 | 365.9858 | 368.9381
3806.5979 | 577.6481 | 368.4909 | 366.1374 | 369.1336
3807.5979 | 577.7614 | 368.7543 | 366.1855 | 369.1722
3808.5979 | 577.8712 | 368.7189 | 366.1588 | 369.385
3809.5979 | 577.9056 | 368.7098 | 366.3759 | 369.4917
3810.5979 | 578.6279 | 368.7149 | 366.4398 | 369.3308
3811.5979 | 578.8543 | 368.6513 | 366.2229 | 369.1809
3812.5979 | 579.4809 | 368.5457 | 366.215 | 369.234
3813.5979 | 580.2728 | 368.318 | 366.1872 | 369.3473
3814.5979 | 580.4553 | 368.1437 | 366.0523 | 369.345
3815.5979 | 580.7359 | 368.1093 | 366.2134 | 369.5606
3816.5979 | 581.1373 | 367.7986 | 366.2476 | 369.551
3817.5979 | 583.0578 | 367.5066 | 366.1127 | 369.3902
3818.5979 | 584.5651 | 367.2919 | 365.9659 | 369.4178
3819.5979 | 584.9709 | 367.1336 | 365.7555 | 369.1859
3820.5979 | 584.1416 | 366.9747 | 365.5637 | 368.9758
3821.5979 | 583.1951 | 366.9031 | 365.5252 | 368.9047
3822.5979 | 582.3899 | 366.9609 | 365.4429 | 368.9602
3823.5979 | 581.4752 | 366.9634 | 365.8194 | 368.7316
3824.5979 | 581.2025 | 367.0092 | 366.1134 | 369.0269
3825.5979 | 581.1509 | 366.9196 | 365.9432 | 368.9746
3826.5979 | 581.3227 | 366.6844 | 365.6483 | 368.6596
3827.5979 | 581.9964 | 366.4591 | 365.434 | 368.7093
3828.5979 | 583.4838 | 366.2922 | 365.2726 | 368.3719
3829.5979 | 584.0235 | 366.1198 | 365.0308 | 368.1688
3830.5979 | 583.3423 | 366.0273 | 364.9618 | 368.5875
3831.5979 | 582.8917 | 365.933 | 364.9606 | 368.2345
3832.5979 | 583.3883 | 366.0119 | 364.7971 | 368.0423
3833.5979 | 583.7995 | 365.9206 | 364.625 | 367.9482
3834.5979 | 583.9064 | 365.7172 | 364.4695 | 367.8472
3835.5979 | 582.6332 | 365.7054 | 364.4302 | 367.621
3836.5979 | 581.4542 | 365.8158 | 364.4745 | 367.6379
3837.5979 | 580.9447 | 365.7378 | 364.4069 | 367.34
3838.5979 | 580.6072 | 365.6131 | 364.4376 | 367.4381
3839.5979 | 580.9512 | 365.4214 | 364.3369 | 367.6384
3840.5979 | 581.1639 | 365.2163 | 364.2678 | 367.5586
3841.5979 | 581.6276 | 365.068 | 364.2592 | 367.6777
3842.5979 | 581.597 | 364.9568 | 363.9284 | 367.633
3843.5979 | 582.8842 | 364.8003 | 363.6582 | 367.412
3844.5979 | 584.5976 | 364.7382 | 363.8969 | 367.2827
3845.5979 | 585.1846 | 364.684 | 364.0655 | 367.2594
3846.5979 | 585.3706 | 364.5439 | 363.7516 | 367.008
3847.5979 | 584.9962 | 364.3553 | 363.4603 | 366.8875
3848.5979 | 584.6404 | 364.2139 | 363.3108 | 366.5996
3849.5979 | 583.345 | 364.0564 | 363.0942 | 366.2752
3850.5979 | 582.312 | 363.8366 | 362.8208 | 366.1433
3851.5979 | 581.264 | 363.6508 | 362.5576 | 366.1385
3852.5979 | 581.04 | 363.4866 | 362.2457 | 366.166
3853.5979 | 581.8746 | 363.3651 | 362.0258 | 365.7646
3854.5979 | 582.8779 | 363.3119 | 361.9013 | 365.6985
3855.5979 | 583.2886 | 363.3775 | 362.0618 | 365.5073
3856.5979 | 583.9211 | 363.5294 | 362.1486 | 365.3305
3857.5979 | 584.2351 | 363.7426 | 362.1794 | 365.4754
3858.5979 | 583.9664 | 363.7952 | 362.7632 | 365.6279
3859.5979 | 584.2286 | 364.2798 | 363.5172 | 365.7488
3860.5979 | 583.8897 | 364.427 | 363.5527 | 365.778
3861.5979 | 582.8516 | 364.4737 | 363.549 | 366.021
3862.5979 | 581.1213 | 364.5074 | 363.5345 | 366.1657
3863.5979 | 579.1251 | 364.616 | 363.5579 | 366.1146
3864.5979 | 577.9875 | 364.6312 | 363.5352 | 366.0413
3865.5979 | 576.9579 | 364.5011 | 363.4944 | 365.9327
3866.5979 | 576.0286 | 364.3341 | 363.9091 | 365.9938
3867.5979 | 574.6047 | 364.4478 | 363.7897 | 366.0575
3868.5979 | 573.9914 | 364.3196 | 363.5133 | 365.8725
3869.5979 | 574.4321 | 364.1948 | 363.6062 | 365.7885
3870.5979 | 574.2678 | 364.0138 | 363.437 | 366.0026
3871.5979 | 573.9655 | 363.8511 | 363.2434 | 365.8631
3872.5979 | 574.3114 | 363.6755 | 362.9865 | 365.6743
3873.5979 | 575.2417 | 363.5197 | 362.6521 | 365.3955
3874.5979 | 575.9995 | 363.4607 | 362.4448 | 365.3016
3875.5979 | 577.2729 | 363.3818 | 362.2264 | 365.2216
3876.5979 | 577.4485 | 363.2412 | 362.4622 | 365.132
3877.5979 | 576.7731 | 363.0613 | 362.4445 | 365.1804
3878.5979 | 575.8295 | 363.2791 | 362.3525 | 365.212
3879.5979 | 575.0821 | 363.2357 | 362.2274 | 364.972
3880.5979 | 574.0794 | 363.1552 | 362.0383 | 365.1455
3881.5979 | 574.1174 | 362.9675 | 361.7143 | 365.1616
3882.5979 | 574.6801 | 362.7365 | 361.6248 | 364.8097
3883.5979 | 573.9373 | 362.6295 | 361.4378 | 364.5069
3884.5979 | 573.3443 | 362.7172 | 361.2451 | 364.403
3885.5979 | 572.8865 | 362.7049 | 360.9715 | 364.2069
3886.5979 | 572.9321 | 362.5803 | 360.8226 | 363.9305
3887.5979 | 573.4409 | 362.5766 | 360.804 | 363.814
3888.5979 | 574.5424 | 362.3341 | 360.6201 | 363.6122
3889.5979 | 574.7 | 362.1606 | 360.3843 | 363.402
3890.5979 | 573.6119 | 362.3407 | 360.1763 | 363.1359
3891.5979 | 572.1102 | 362.4354 | 360.1674 | 363.0524
3892.5979 | 570.9695 | 362.5904 | 360.1945 | 362.9197
3893.5979 | 570.5549 | 362.5802 | 360.1502 | 362.9752
3894.5979 | 570.8598 | 362.338 | 359.8677 | 362.9884
3895.5979 | 570.7338 | 362.0274 | 359.5774 | 362.817
3896.5979 | 570.1388 | 361.7116 | 359.3095 | 362.5064
3897.5979 | 569.5078 | 361.5324 | 359.1195 | 362.3089
3898.5979 | 569.092 | 361.3279 | 358.8688 | 362.1253
3899.5979 | 568.3384 | 361.1781 | 358.6489 | 361.9954
3900.5979 | 568.2206 | 361.0028 | 358.4336 | 361.6957
3901.5979 | 568.3374 | 360.7405 | 358.2176 | 361.5069
3902.5979 | 568.4699 | 360.4748 | 357.8911 | 361.2472
3903.5979 | 568.1568 | 360.2456 | 357.6668 | 360.9361
3904.5979 | 567.9676 | 360.0028 | 357.3936 | 360.6036
3905.5979 | 568.584 | 359.8307 | 357.1815 | 360.4106
3906.5979 | 570.3136 | 359.6901 | 357.0593 | 360.2209
3907.5979 | 572.8247 | 359.5681 | 356.8536 | 359.9187
3908.5979 | 574.3216 | 359.4696 | 356.6177 | 359.5399
3909.5979 | 574.6678 | 359.557 | 356.7087 | 359.3208
3910.5979 | 575.4401 | 359.6323 | 356.6613 | 359.1676
3911.5979 | 575.4904 | 359.6533 | 356.6323 | 359.0724
3912.5979 | 575.4011 | 359.5077 | 356.7008 | 359.8724
3913.5979 | 574.4842 | 359.409 | 356.7349 | 359.9599
3914.5979 | 573.5741 | 359.4181 | 356.6905 | 360.0811
3915.5979 | 573.0324 | 359.3864 | 356.6117 | 359.9313
3916.5979 | 571.8038 | 359.243 | 356.5834 | 359.8541
3917.5979 | 571.1784 | 359.0671 | 356.3538 | 359.8917
3918.5979 | 570.605 | 358.8625 | 356.3089 | 359.7079
3919.5979 | 570.9 | 358.7729 | 356.2047 | 359.563
3920.5979 | 570.8564 | 358.7486 | 356.1356 | 359.4366
3921.5979 | 571.5749 | 358.7106 | 356.0412 | 359.3724
3922.5979 | 571.9452 | 358.7078 | 356.2005 | 359.6159
3923.5979 | 572.3088 | 358.769 | 356.4101 | 359.6997
3924.5979 | 571.7496 | 358.95 | 356.6889 | 359.7927
3925.5979 | 571.4715 | 359.0718 | 356.6986 | 359.94
3926.5979 | 571.3018 | 359.2443 | 356.8293 | 360.0934
3927.5979 | 571.1809 | 359.2343 | 356.9594 | 360.1703
3928.5979 | 569.8144 | 359.2051 | 357.2905 | 360.3284
3929.5979 | 569.1345 | 359.2714 | 357.3227 | 360.4165
3930.5979 | 568.4722 | 359.3712 | 357.2914 | 360.4166
3931.5979 | 567.1789 | 359.6174 | 357.3542 | 360.7029
3932.5979 | 566.5966 | 359.9645 | 357.3804 | 360.8818
3933.5979 | 567.7623 | 360.0675 | 357.4027 | 360.8703
3934.5979 | 568.387 | 359.9622 | 357.269 | 360.8086
3935.5979 | 568.7202 | 359.7678 | 357.0795 | 360.6016
3936.5979 | 569.1563 | 359.5603 | 356.8872 | 360.2954
3937.5979 | 569.3752 | 359.3265 | 356.6862 | 360.3985
3938.5979 | 569.2079 | 359.3257 | 356.599 | 360.2829
3939.5979 | 568.7691 | 359.34 | 356.556 | 360.098
3940.5979 | 568.3623 | 359.2508 | 356.7339 | 359.8862
3941.5979 | 567.9126 | 359.0748 | 356.7259 | 359.8231
3942.5979 | 567.5198 | 358.6914 | 356.5957 | 359.8202
3943.5979 | 567.5382 | 358.3966 | 356.3551 | 359.6732
3944.5979 | 567.5536 | 358.2376 | 356.1127 | 359.672
3945.5979 | 567.4708 | 358.1446 | 356.1397 | 360.0324
3946.5979 | 567.1797 | 358.0484 | 356.0089 | 359.8497
3947.5979 | 567.6686 | 357.7218 | 355.82 | 359.9041
3948.5979 | 567.8942 | 357.4903 | 355.7229 | 360.2192
3949.5979 | 567.8021 | 357.3349 | 355.7587 | 360.1589
3950.5979 | 567.3892 | 357.1605 | 355.5818 | 359.9354
3951.5979 | 567.0989 | 357.0288 | 355.3909 | 359.7113
3952.5979 | 567.7972 | 356.8554 | 355.0976 | 359.8119
3953.5979 | 568.393 | 356.6378 | 354.743 | 359.6591
3954.5979 | 569.1055 | 356.3956 | 354.427 | 359.3903
3955.5979 | 568.7608 | 356.2704 | 354.2067 | 359.1043
3956.5979 | 568.27 | 356.1945 | 354.0933 | 358.9798
3957.5979 | 567.9207 | 356.2211 | 354.0214 | 358.8941
3958.5979 | 567.9872 | 356.1545 | 353.8973 | 358.7163
3959.5979 | 568.2173 | 356.2076 | 353.8514 | 358.4155
3960.5979 | 568.9511 | 356.1134 | 353.6148 | 358.1917
3961.5979 | 569.2644 | 355.921 | 353.3996 | 358.0827
3962.5979 | 569.5869 | 355.7811 | 353.1841 | 357.8564
3963.5979 | 569.487 | 355.5877 | 352.9663 | 357.7037
3964.6135 | 570.1718 | 355.4051 | 352.8346 | 357.417
3965.5979 | 570.9834 | 355.2254 | 352.7244 | 357.2003
3966.5979 | 571.49 | 355.0092 | 352.5664 | 357.2064
3967.5979 | 571.9839 | 354.9486 | 352.466 | 356.9183
3968.5979 | 572.4594 | 354.9067 | 352.5878 | 356.7638
3969.5979 | 572.7963 | 354.9509 | 352.8839 | 357.2001
3970.5979 | 573.5127 | 354.8717 | 352.9662 | 357.2576
3971.5979 | 574.8064 | 354.6806 | 352.8697 | 357.2713
3972.5979 | 575.8223 | 354.4783 | 352.7126 | 357.5523
3973.5979 | 576.3159 | 354.3733 | 352.528 | 357.6369
3974.5979 | 576.4305 | 354.4931 | 352.4588 | 357.351
3975.5979 | 576.5616 | 355.0125 | 352.5017 | 357.3134
3976.5979 | 576.6928 | 355.2339 | 352.7098 | 357.5241
3977.5979 | 576.2995 | 355.3751 | 353.0583 | 357.6988
3978.5979 | 576.3431 | 355.3363 | 353.3441 | 358.063
3979.5979 | 576.6622 | 355.2508 | 353.4399 | 358.1747
3980.5979 | 577.7507 | 355.171 | 353.3434 | 358.0353
3981.5979 | 578.7523 | 355.0463 | 353.1511 | 357.8873
3982.5979 | 579.359 | 354.813 | 352.8911 | 357.6893
3983.5979 | 579.8058 | 354.6206 | 352.61 | 357.466
3984.5979 | 580.0472 | 354.4481 | 352.4941 | 357.3734
3985.5979 | 579.8046 | 354.3353 | 352.4519 | 357.1208
3986.5979 | 578.9462 | 354.2477 | 352.5211 | 357.152
3987.5979 | 578.0073 | 354.2992 | 352.6673 | 357.259
3988.5979 | 577.3248 | 354.5295 | 352.9881 | 357.2743
3989.5979 | 576.9694 | 354.5267 | 353.2106 | 357.3213
3990.5979 | 576.6371 | 354.4316 | 353.1402 | 357.2258
3991.5979 | 576.5558 | 354.3579 | 352.8668 | 357.0686
3992.5979 | 576.3451 | 354.193 | 352.5581 | 356.7188
3993.5979 | 576.3397 | 354.0424 | 352.2494 | 356.2991
3994.5979 | 576.3106 | 353.8857 | 352.0732 | 356.267
3995.5979 | 576.3521 | 353.8005 | 351.9395 | 356.3492
3996.5979 | 576.1161 | 353.705 | 351.7632 | 356.1557
3997.5979 | 575.6782 | 353.506 | 351.8247 | 356.2194
3998.5979 | 575.0261 | 353.3177 | 351.8435 | 356.3392
3999.5979 | 574.8968 | 353.2467 | 351.7503 | 356.1615
4000.5979 | 574.7714 | 353.3317 | 351.7335 | 356.029
4001.5979 | 574.7828 | 353.3188 | 351.5093 | 356.242
4002.5979 | 574.8899 | 353.1837 | 351.3016 | 356.0072
4003.5979 | 574.8169 | 353.0906 | 351.1391 | 355.7563
4004.5979 | 575.1155 | 353.0094 | 350.9491 | 355.5706
4005.5979 | 575.5768 | 352.8783 | 350.6885 | 355.2498
4006.5979 | 575.6445 | 352.6609 | 350.4537 | 354.8656
4007.5979 | 575.9937 | 352.3975 | 350.2008 | 354.9884
4008.5979 | 575.9634 | 352.2344 | 350.0707 | 354.825
4009.5979 | 575.5533 | 352.2479 | 349.9152 | 354.4961
4010.5979 | 575.4089 | 352.1476 | 349.7122 | 354.4369
4011.5979 | 576.0615 | 352.0715 | 349.5218 | 354.6248
4012.5979 | 576.7725 | 351.9593 | 349.297 | 354.529
4013.5979 | 577.3261 | 351.7933 | 349.1049 | 354.5519
4014.5979 | 577.2545 | 351.7404 | 349.2029 | 355.01
4015.5979 | 576.8135 | 351.9922 | 349.234 | 354.9844
4016.5979 | 576.5596 | 352.0691 | 349.2413 | 354.8133
4017.5979 | 576.3601 | 352.0378 | 349.4983 | 354.6384
4018.5979 | 576.9002 | 352.1617 | 349.8975 | 354.9111
4019.5979 | 577.3179 | 352.5445 | 350.4081 | 355.0899
4020.5979 | 577.103 | 352.7402 | 350.4978 | 355.1393
4021.5979 | 576.3946 | 352.7888 | 350.5043 | 355.2347
4022.5979 | 576.0423 | 352.7689 | 350.5174 | 355.5069
4023.5979 | 576.1789 | 352.7534 | 350.4197 | 355.3779
4024.5979 | 576.6285 | 352.6394 | 350.4207 | 355.2496
4025.5979 | 577.1163 | 352.4404 | 350.2452 | 355.1739
4026.5979 | 577.8194 | 352.2077 | 349.9466 | 354.8786
4027.5979 | 578.2585 | 352.0579 | 349.7429 | 354.6687
4028.5979 | 578.1768 | 352.0529 | 349.6328 | 354.4874
4029.5979 | 578.6537 | 352.0902 | 349.617 | 354.3219
4030.5979 | 578.6428 | 352.0668 | 349.8078 | 354.4069
4031.5979 | 578.1814 | 352.0173 | 349.9272 | 354.6336
4032.5979 | 577.8198 | 351.6911 | 350.1052 | 354.7229
4033.5979 | 577.6076 | 351.4927 | 349.9189 | 354.7682
4034.5979 | 577.3112 | 351.2057 | 349.6671 | 354.6257
4035.5979 | 577.0026 | 350.9999 | 349.5259 | 354.4943
4036.5979 | 577.1372 | 350.8509 | 349.3297 | 354.2698
4037.5979 | 576.7227 | 350.5619 | 349.2314 | 354.002
4038.5979 | 576.3649 | 350.4005 | 349.0402 | 354.0425
4039.5979 | 576.5677 | 350.2095 | 348.949 | 354.0062
4040.5979 | 577.753 | 350.0644 | 348.8412 | 353.8923
4041.5979 | 578.7658 | 349.9446 | 348.6556 | 353.8183
4042.5979 | 579.5898 | 349.8475 | 348.811 | 353.5344
4043.5979 | 579.9383 | 349.9336 | 349.1468 | 353.3995
4044.5979 | 579.6699 | 350.2038 | 349.0788 | 353.8315
4045.5979 | 579.0986 | 350.3418 | 349.1815 | 353.593
4046.5979 | 579.2932 | 350.2907 | 349.0276 | 353.3825
4047.5979 | 579.8532 | 350.1575 | 348.943 | 353.4605
4048.5979 | 579.538 | 350.1142 | 348.8421 | 353.3495
4049.5979 | 579.2256 | 350.0057 | 348.6853 | 353.1224
4050.5979 | 578.9974 | 349.9296 | 348.6176 | 352.9501
4051.5979 | 578.1367 | 349.9521 | 348.6371 | 352.8613
4052.5979 | 577.5058 | 349.9984 | 348.6493 | 352.9884
4053.5979 | 577.3201 | 350.0065 | 348.8773 | 353.0818
4054.5979 | 578.2436 | 349.9626 | 349.0515 | 352.9174
4055.5979 | 579.0329 | 349.7857 | 348.7983 | 352.7304
4056.5979 | 578.9963 | 349.4608 | 348.5328 | 352.4467
4057.5979 | 578.4948 | 349.1406 | 348.2708 | 352.2449
4058.5979 | 578.6014 | 348.9724 | 348.1317 | 352.0414
4059.5979 | 579.2733 | 348.83 | 347.9391 | 352.0102
4060.5979 | 579.4256 | 348.7767 | 347.8372 | 351.831
4061.5979 | 579.3474 | 348.8811 | 347.7721 | 351.6593
4062.5979 | 579.4697 | 348.8273 | 347.967 | 351.874
4063.5979 | 579.3657 | 348.8051 | 348.0791 | 352.0694
4064.5979 | 579.3832 | 348.9695 | 347.9964 | 352.2138
4065.5979 | 579.7944 | 349.1937 | 347.8734 | 352.4738
4066.5979 | 580.5363 | 349.1251 | 347.8846 | 352.3325
4067.5979 | 580.6692 | 349.0016 | 347.9517 | 352.1355
4068.5979 | 580.2741 | 348.9059 | 347.7859 | 352.0876
4069.5979 | 579.111 | 348.8865 | 347.907 | 351.9959
4070.5979 | 577.9312 | 349.163 | 348.2484 | 351.8897
4071.5979 | 577.0906 | 349.316 | 348.111 | 351.7803
4072.5979 | 576.6448 | 349.3108 | 348.2824 | 351.6287
4073.5979 | 576.3351 | 349.2259 | 348.0545 | 351.5138
4074.5979 | 577.004 | 349.139 | 347.9568 | 351.1755
4075.5979 | 577.416 | 349.1069 | 347.6468 | 350.8998
4076.5979 | 577.6634 | 348.917 | 347.2893 | 350.7243
4077.5979 | 577.4541 | 348.8308 | 347.3271 | 350.7143
4078.5979 | 576.724 | 348.9561 | 347.3151 | 350.6372
4079.5979 | 576.027 | 348.9557 | 347.128 | 350.5097
4080.5979 | 575.1526 | 348.8815 | 347.0162 | 350.4324
4081.5979 | 574.6478 | 348.6074 | 346.9564 | 350.2031
4082.5979 | 574.7249 | 348.4222 | 346.7204 | 350.1267
4083.5979 | 574.3251 | 348.2725 | 346.8227 | 350.316
4084.5979 | 573.6143 | 348.1852 | 346.6994 | 350.2071
4085.5979 | 573.1319 | 348.0309 | 346.3847 | 349.8895
4086.5979 | 572.9158 | 347.83 | 346.1603 | 349.8987
4087.5979 | 573.343 | 347.7085 | 346.0108 | 349.8911
4088.5979 | 573.4057 | 347.5519 | 345.7318 | 349.6386
4089.5979 | 573.8265 | 347.3418 | 345.3705 | 349.1703
4090.5979 | 574.6997 | 347.1374 | 345.0722 | 348.9365
4091.5979 | 575.6138 | 346.9444 | 344.7684 | 348.722
4092.5979 | 576.4308 | 346.752 | 344.4213 | 348.4363
4093.5979 | 576.8694 | 346.4482 | 343.9593 | 348.5776
4094.5979 | 577.2347 | 346.3323 | 343.7538 | 348.2659
4095.5979 | 577.7728 | 346.2563 | 343.4809 | 348.1393
4096.5979 | 578.1219 | 346.0643 | 343.4231 | 348.007
4097.5979 | 578.0764 | 345.9032 | 343.2981 | 348.3453
4098.5979 | 577.7784 | 345.7662 | 343.1301 | 348.1598
4099.5979 | 577.4378 | 345.6867 | 343.2718 | 347.9423
4100.5979 | 577.2969 | 345.4662 | 343.164 | 348.2221
4101.5979 | 577.1837 | 345.3037 | 342.9645 | 348.0787
4102.5979 | 577.8238 | 345.3036 | 342.9368 | 348.1408
4103.5979 | 578.029 | 345.1718 | 342.7733 | 348.1193
4104.5979 | 578.1711 | 345.0469 | 342.6734 | 347.8912
4105.5979 | 577.8768 | 344.9186 | 342.517 | 347.6458
4106.5979 | 577.915 | 344.8244 | 342.3672 | 347.4596
4107.5979 | 578.0245 | 344.6914 | 342.1503 | 347.2079
4108.5979 | 577.7966 | 344.5571 | 341.9228 | 346.9381
4109.5979 | 578.198 | 344.4365 | 341.7412 | 347.079
4110.5979 | 578.6953 | 344.3209 | 341.6455 | 347.3338
4111.5979 | 579.0793 | 344.2013 | 341.6176 | 347.1955
4112.5979 | 578.9439 | 344.1257 | 341.6332 | 347.0375
4113.5979 | 578.6992 | 344.1153 | 341.504 | 347.0986
4114.5979 | 578.6023 | 344.073 | 341.528 | 346.9289
4115.5979 | 578.5385 | 343.9291 | 341.5518 | 346.9948
4116.5979 | 578.0653 | 343.8404 | 341.4503 | 346.9522
4117.5979 | 577.2787 | 343.7069 | 341.5367 | 346.8085
4118.5979 | 576.5606 | 343.4847 | 341.4996 | 346.7846
4119.5979 | 575.9712 | 343.4007 | 341.3387 | 346.5688
4120.5979 | 576.282 | 343.2917 | 341.1355 | 346.3564
4121.5979 | 576.0918 | 343.1405 | 340.9115 | 346.0696
4122.5979 | 575.4606 | 342.9956 | 340.6349 | 345.7908
4123.5979 | 575.4296 | 342.9839 | 340.5925 | 345.5492
4124.5979 | 575.4128 | 342.8699 | 340.4193 | 345.5289
4125.5979 | 575.2682 | 342.7456 | 340.2404 | 345.3025
4126.5979 | 575.5112 | 342.5709 | 340.1443 | 345.2585
4127.5979 | 575.959 | 342.421 | 340.117 | 345.2082
4128.5979 | 575.9896 | 342.2338 | 339.8948 | 345.0769
4129.5979 | 576.1329 | 342.0315 | 339.8299 | 344.7718
4130.5979 | 576.6117 | 341.9012 | 339.5722 | 344.6479
4131.5979 | 576.7346 | 341.7528 | 339.3428 | 344.5483
4132.5979 | 576.9819 | 341.5353 | 339.1364 | 344.6696
4133.5979 | 576.7918 | 341.5002 | 339.1548 | 344.5684
4134.5979 | 576.0427 | 341.6398 | 339.2562 | 344.4394
4135.5979 | 574.5491 | 341.6886 | 339.4124 | 344.3116
4136.5979 | 574.2368 | 341.6344 | 339.3436 | 344.2323
4137.5979 | 573.5799 | 341.5298 | 339.3433 | 344.313
4138.5979 | 573.4911 | 341.4057 | 339.4027 | 344.4304
4139.5979 | 573.87 | 341.1966 | 339.3086 | 344.4141
4140.5979 | 574.3282 | 341.309 | 339.4437 | 344.4222
4141.5979 | 574.7231 | 341.5273 | 339.4655 | 344.832
4142.5979 | 575.0681 | 341.5173 | 339.533 | 345.0335
4143.5979 | 575.5219 | 341.512 | 339.7126 | 345.1469
4144.5979 | 575.5014 | 341.7065 | 340.1827 | 345.5017
4145.5979 | 575.3391 | 342.108 | 340.391 | 345.4074
4146.5979 | 575.3557 | 341.9831 | 340.5773 | 345.3671
4147.5979 | 575.7776 | 341.8513 | 340.6426 | 345.4299
4148.5979 | 575.8549 | 341.6982 | 340.5186 | 345.3923
4149.5979 | 575.7476 | 341.4915 | 340.3184 | 345.243
4150.5979 | 576.1632 | 341.329 | 340.1758 | 345.3618
4151.5979 | 576.2116 | 341.1918 | 340.0194 | 345.3456
4152.5979 | 576.4351 | 341.021 | 339.6575 | 344.9823
4153.5979 | 576.8124 | 340.7584 | 339.2021 | 344.5079
4154.5979 | 576.5001 | 340.5604 | 338.7995 | 344.3302
4155.5979 | 576.1687 | 340.4198 | 338.5469 | 344.1885
4156.5979 | 575.7713 | 340.3505 | 338.347 | 343.9016
4157.5979 | 575.1837 | 340.2415 | 338.0879 | 343.4867
4158.5979 | 574.5239 | 340.0852 | 337.8428 | 343.2003
4159.5979 | 573.998 | 339.9525 | 337.6333 | 342.8853
4160.5979 | 573.7388 | 339.8509 | 337.4438 | 342.6661
4161.5979 | 573.3673 | 339.7583 | 337.202 | 342.4725
4162.5979 | 573.5384 | 339.6904 | 336.9975 | 342.2391
4163.5979 | 573.5467 | 339.6444 | 336.8645 | 341.8819
4164.5979 | 573.1433 | 339.63 | 336.8769 | 341.6203
4165.5979 | 572.725 | 339.6649 | 336.769 | 341.7803
4166.5979 | 572.4949 | 339.6841 | 336.7205 | 341.7439
4167.5979 | 572.6211 | 339.725 | 336.6127 | 341.5563
4168.5979 | 572.7672 | 339.7213 | 336.5547 | 341.4072
4169.5979 | 572.5746 | 339.6075 | 336.4466 | 341.3556
4170.5979 | 571.8617 | 339.4677 | 336.3313 | 341.2351
4171.5979 | 571.3567 | 339.3074 | 336.1876 | 340.8136
4172.5979 | 570.9795 | 339.157 | 335.9789 | 340.4819
4173.5979 | 570.9455 | 339.0049 | 335.7424 | 340.2502
4174.5979 | 570.9686 | 338.9701 | 335.5933 | 340.0063
4175.5979 | 571.188 | 338.8375 | 335.5217 | 339.9252
4176.5979 | 570.9992 | 338.7482 | 335.4141 | 339.7994
4177.5979 | 570.9099 | 338.6629 | 335.2923 | 339.6354
4178.5979 | 571.221 | 338.6084 | 335.2339 | 339.4897
4179.5979 | 571.6471 | 338.5341 | 335.1224 | 339.2868
4180.5979 | 571.8908 | 338.3712 | 335.0107 | 339.1179
4181.5979 | 572.6478 | 338.2065 | 334.9191 | 339.097
4182.5979 | 573.5469 | 338.0884 | 334.813 | 339.0053
4183.5979 | 574.1855 | 338.0176 | 334.9377 | 338.9651
4184.5979 | 574.6781 | 337.9462 | 334.846 | 339.2011
4185.5979 | 574.3276 | 338.0384 | 334.925 | 339.3034
4186.5979 | 573.8753 | 338.2409 | 335.137 | 339.578
4187.5979 | 573.7657 | 338.3587 | 335.4143 | 340.0565
4188.5979 | 573.4987 | 338.2489 | 335.6488 | 340.3706
4189.5979 | 572.6558 | 338.128 | 335.7615 | 340.5982
4190.5979 | 571.8379 | 338.0884 | 335.8008 | 340.6671
4191.5979 | 571.6471 | 338.1794 | 335.8715 | 341.0446
4192.5979 | 571.5333 | 338.172 | 335.9784 | 341.2075
4193.5979 | 572.2445 | 338.1214 | 335.8785 | 341.1001
4194.5979 | 573.1324 | 338.0338 | 335.753 | 340.8999
4195.5979 | 573.1263 | 337.9549 | 335.6661 | 340.9501
4196.5979 | 572.7359 | 337.7622 | 335.5591 | 341.0198
4197.5979 | 572.2288 | 337.6585 | 335.3604 | 340.9284
4198.5979 | 571.743 | 337.583 | 335.1394 | 340.7645
4199.5979 | 571.1451 | 337.5123 | 334.9964 | 340.6435
4200.5979 | 570.8046 | 337.4612 | 334.9161 | 340.4369
4201.5979 | 570.8562 | 337.3954 | 334.9518 | 340.3248
4202.5979 | 571.3203 | 337.3403 | 334.8503 | 340.3317
4203.5979 | 571.9331 | 337.2555 | 334.6822 | 340.1532
4204.5979 | 571.7422 | 337.189 | 334.5221 | 339.8573
4205.5979 | 571.501 | 337.012 | 334.3498 | 339.6791
4206.5979 | 571.2539 | 336.8904 | 334.0794 | 339.613
4207.5979 | 570.7017 | 336.8171 | 333.8927 | 339.4927
4208.5979 | 570.1724 | 336.697 | 333.7141 | 339.205
4209.5979 | 570.4079 | 336.4469 | 333.5031 | 338.886
4210.5979 | 570.5525 | 336.2039 | 333.291 | 338.8567
4211.5979 | 570.4346 | 336.0756 | 333.1862 | 338.7793
4212.5979 | 570.4771 | 335.9786 | 333.0531 | 338.5508
4213.5979 | 570.603 | 335.9337 | 332.9751 | 338.3133
4214.5979 | 571.2707 | 335.8146 | 332.7918 | 338.3218
4215.5979 | 571.8766 | 335.7545 | 332.6347 | 338.2147
4216.5979 | 572.3597 | 335.6809 | 332.4414 | 338.0386
4217.5979 | 572.858 | 335.5176 | 332.3207 | 338.0022
4218.5979 | 573.4382 | 335.3647 | 332.2026 | 338.0724
4219.5979 | 573.8953 | 335.1154 | 332.0018 | 338.326
4220.5979 | 573.9364 | 335.0502 | 331.8941 | 338.21
4221.5979 | 573.7312 | 335.0551 | 331.842 | 338.2176
4222.5979 | 573.976 | 334.9829 | 331.9313 | 338.4442
4223.5979 | 574.246 | 334.8309 | 332.2015 | 338.9279
4224.5979 | 574.5012 | 334.7615 | 332.186 | 339.1881
4225.5979 | 574.776 | 334.7716 | 332.1753 | 339.0586
4226.5979 | 574.7678 | 334.8477 | 331.9798 | 339.0585
4227.5979 | 575.0098 | 334.7628 | 332.0393 | 338.9034
4228.5979 | 575.7501 | 334.6828 | 331.8571 | 339.0565
4229.5979 | 576.3657 | 334.5462 | 331.7055 | 338.8772
4230.5979 | 576.3988 | 334.4804 | 331.6164 | 339.0483
4231.5979 | 576.4845 | 334.5764 | 331.7552 | 338.8949
4232.5979 | 576.4672 | 334.6182 | 332.0136 | 338.7319
4233.5979 | 576.442 | 334.5765 | 331.95 | 338.555
4234.5979 | 576.0406 | 334.5084 | 331.8279 | 338.7587
4235.5979 | 575.854 | 334.3944 | 331.7628 | 338.7082
4236.5979 | 575.4987 | 334.3543 | 331.687 | 338.5167
4237.5979 | 574.9417 | 334.2529 | 331.4228 | 338.4484
4238.5979 | 574.9604 | 334.2496 | 331.3734 | 339.0397
4239.5979 | 574.97 | 334.2089 | 331.2217 | 339.0382
4240.5979 | 575.0457 | 334.0969 | 331.0462 | 338.6594
4241.5979 | 574.9939 | 333.9519 | 330.821 | 338.2301
4242.5979 | 574.7112 | 333.8397 | 330.6789 | 337.7769
4243.5979 | 575.0098 | 333.684 | 330.5244 | 337.553
4244.5979 | 575.1311 | 333.6441 | 330.4934 | 337.7125
4245.5979 | 574.9676 | 333.5413 | 330.4234 | 337.6193
4246.5979 | 574.5057 | 333.4261 | 330.3782 | 337.511
4247.5979 | 574.4295 | 333.2608 | 330.4599 | 337.6727
4248.5979 | 574.6681 | 333.2621 | 330.5687 | 337.5977
4249.5979 | 574.8307 | 333.3055 | 330.7971 | 337.507
4250.5979 | 574.6825 | 333.2934 | 331.1523 | 337.7675
4251.5979 | 574.6155 | 333.3938 | 331.2582 | 337.882
4252.5979 | 574.4066 | 333.4943 | 331.3655 | 337.7593
4253.5979 | 574.1607 | 333.3458 | 331.4623 | 337.7075
4254.5979 | 574.0398 | 333.1863 | 331.5312 | 337.7702
4255.5979 | 574.2819 | 333.2686 | 331.6376 | 337.6758
4256.5979 | 574.3443 | 333.2516 | 331.6951 | 337.6258
4257.5979 | 574.1886 | 333.1775 | 331.7753 | 337.9124
4258.5979 | 574.0112 | 333.1262 | 331.6059 | 337.8996
4259.5979 | 573.7306 | 332.8664 | 331.5476 | 337.7501
4260.5979 | 573.6673 | 332.9063 | 331.6681 | 337.85
4261.5979 | 573.6648 | 332.788 | 331.5542 | 337.8849
4262.5979 | 573.6447 | 332.7406 | 331.2867 | 337.6935
4263.5979 | 573.3878 | 332.6288 | 330.9381 | 337.3887
4264.5979 | 573.1542 | 332.4524 | 330.69 | 337.0186
4265.5979 | 572.9557 | 332.3236 | 330.4458 | 336.7399
4266.5979 | 573.1986 | 332.2494 | 330.2451 | 336.529
4267.5979 | 573.4759 | 332.2381 | 330.0813 | 336.2592
4268.5979 | 574.0358 | 332.239 | 329.8799 | 335.8627
4269.5979 | 574.4602 | 332.191 | 329.6644 | 335.4541
4270.5979 | 574.62 | 332.1455 | 329.4303 | 335.0778
4271.5979 | 574.8748 | 332.1 | 329.4611 | 335.2032
4272.5979 | 574.6678 | 332.1086 | 329.7478 | 335.126
4273.5979 | 574.5811 | 331.9076 | 329.7486 | 335.012
4274.5979 | 574.495 | 331.7184 | 329.7096 | 334.9392
4275.5979 | 574.7186 | 331.6728 | 329.6887 | 335.063
4276.5979 | 574.636 | 331.5695 | 329.7163 | 335.1344
4277.5979 | 574.8728 | 331.5737 | 329.6945 | 335.2683
4278.5979 | 574.7219 | 331.5257 | 329.6591 | 335.258
4279.5979 | 574.321 | 331.4282 | 329.5013 | 335.2958
4280.5979 | 574.4532 | 331.5472 | 329.7169 | 335.3415
4281.5979 | 574.7698 | 331.5501 | 329.6068 | 335.3198
4282.5979 | 575.1824 | 331.5243 | 329.4522 | 335.0352
4283.5979 | 575.4977 | 331.4842 | 329.1851 | 334.6866
4284.5979 | 576.3115 | 331.4873 | 329.1075 | 334.5513
4285.5979 | 576.6381 | 331.4498 | 329.328 | 334.6302
4286.5979 | 576.6496 | 331.3775 | 329.2868 | 334.6574
4287.5979 | 576.3971 | 331.2112 | 329.0932 | 334.8358
4288.5979 | 576.4211 | 330.6649 | 328.932 | 334.6215
4289.5979 | 577.1007 | 330.4875 | 328.9309 | 334.5672
4290.5979 | 577.4771 | 330.0824 | 328.7159 | 334.585
4291.5979 | 577.9657 | 329.96 | 328.8066 | 334.6365
4292.5979 | 578.3778 | 330.026 | 328.9005 | 334.5697
4293.5979 | 579.2398 | 329.9807 | 328.753 | 334.4098
4294.5979 | 579.6536 | 329.908 | 328.6374 | 334.2419
4295.5979 | 579.8134 | 329.8273 | 328.4555 | 333.9878
4296.5979 | 580.4801 | 329.7566 | 328.3992 | 334.0888
4297.5979 | 580.9707 | 329.7828 | 328.371 | 334.046
4298.5979 | 581.6347 | 329.8396 | 328.4002 | 334.0437
4299.5979 | 582.4282 | 329.8885 | 328.2787 | 334.0273
4300.5979 | 582.8829 | 329.8571 | 328.5652 | 334.1324
4301.5979 | 583.6627 | 330.1406 | 328.6995 | 334.2259
4302.5979 | 584.3687 | 330.2942 | 328.8381 | 334.3247
4303.5979 | 585.3107 | 330.3779 | 328.8845 | 334.3716
4304.5979 | 586.1422 | 330.51 | 329.0694 | 334.5979
4305.5979 | 586.3642 | 330.7207 | 329.3105 | 334.6449
4306.5979 | 586.8087 | 330.7334 | 329.3785 | 334.5286
4307.5979 | 587.6714 | 330.5598 | 329.3207 | 334.4192
4308.5979 | 588.3495 | 330.3283 | 329.1459 | 334.4137
4309.5979 | 588.682 | 330.0563 | 329.0518 | 334.3108
4310.5979 | 588.9333 | 329.8733 | 328.8895 | 334.4168
4311.5979 | 589.1667 | 329.6407 | 328.4861 | 334.2076
4312.5979 | 589.5651 | 329.4601 | 328.0071 | 333.7793
4313.5979 | 589.5133 | 329.3506 | 327.6893 | 333.4533
4314.5979 | 589.1884 | 329.2098 | 327.4614 | 333.2009
4315.5979 | 589.7553 | 329.0676 | 327.3536 | 332.7709
4316.5979 | 590.7175 | 329.0248 | 327.1415 | 332.5765
4317.5979 | 590.7291 | 328.9103 | 326.8463 | 332.3278
4318.5979 | 591.0956 | 328.809 | 326.638 | 332.1471
4319.5979 | 592.0046 | 328.7467 | 326.4434 | 332.0001
4320.5979 | 592.8102 | 328.6593 | 326.4092 | 331.8284
4321.5979 | 593.282 | 328.6298 | 326.3419 | 331.6657
4322.5979 | 593.7027 | 328.4271 | 326.2996 | 331.8296
4323.5979 | 593.9263 | 328.0962 | 326.2379 | 332.1592
4324.5979 | 593.7153 | 328.0781 | 326.0494 | 332.1776
4325.5979 | 593.703 | 328.3159 | 326.2855 | 332.1585
4326.5979 | 594.1684 | 328.516 | 326.5421 | 332.1596
4327.5979 | 594.2947 | 328.5042 | 326.7868 | 332.3284
4328.5979 | 594.2117 | 328.5325 | 326.9686 | 332.7039
4329.5979 | 593.9342 | 328.441 | 326.9653 | 332.8168
4330.5979 | 593.8545 | 328.2426 | 326.7993 | 332.7669
4331.5979 | 594.079 | 328.1241 | 326.7329 | 332.6124
4332.5979 | 594.592 | 327.9686 | 326.4919 | 332.2939
4333.5979 | 594.972 | 327.8471 | 326.2532 | 332.0225
4334.5979 | 594.9382 | 327.6422 | 325.9159 | 331.7681
4335.5979 | 595.4112 | 327.3893 | 325.5415 | 331.5247
4336.5979 | 596.0198 | 327.0641 | 325.3906 | 331.4069
4337.5979 | 596.1579 | 326.8031 | 325.1071 | 331.232
4338.5979 | 595.6478 | 326.7414 | 324.8993 | 330.9497
4339.5979 | 595.8233 | 326.6883 | 324.8597 | 330.766
4340.5979 | 596.5432 | 326.6122 | 324.7518 | 330.8429
4341.5979 | 596.8309 | 326.5711 | 324.5413 | 330.5978
4342.5979 | 596.5281 | 326.5488 | 324.3256 | 330.2892
4343.5979 | 596.5699 | 326.5432 | 324.2503 | 330.3487
4344.5979 | 597.0629 | 326.533 | 324.0954 | 330.1736
4345.5979 | 597.274 | 326.5432 | 324.0482 | 329.9138
4346.5979 | 597.4355 | 326.6613 | 324.0875 | 329.8043
4347.5979 | 597.3969 | 326.7283 | 324.1836 | 329.7429
4348.5979 | 596.7266 | 326.6704 | 324.1396 | 329.7675
4349.5979 | 596.4562 | 326.5933 | 324.0659 | 329.5556
4350.5979 | 596.6444 | 326.4997 | 323.9329 | 329.3725
4351.5979 | 596.8958 | 326.2691 | 323.7717 | 329.1699
4352.5979 | 597.3803 | 326.0234 | 323.5581 | 328.9806
4353.5979 | 597.6737 | 325.9455 | 323.4681 | 329.0775
4354.5979 | 597.6417 | 325.8535 | 323.4113 | 329.0107
4355.5979 | 597.4314 | 325.4735 | 323.3381 | 328.8256
4356.5979 | 597.9351 | 325.3947 | 323.1992 | 328.7825
4357.5979 | 598.2102 | 325.3823 | 323.0866 | 328.8199
4358.5979 | 598.8065 | 325.3174 | 322.9649 | 328.9997
4359.5979 | 598.9691 | 325.4958 | 323.111 | 329.2395
4360.5979 | 599.517 | 325.5776 | 323.2125 | 329.4282
4361.5979 | 599.7911 | 325.5873 | 323.1819 | 329.365
4362.5979 | 600.1058 | 325.5104 | 323.1659 | 329.4858
4363.5979 | 600.8171 | 325.6556 | 323.6908 | 329.7839
4364.5979 | 601.4465 | 325.7286 | 324.0122 | 329.8371
4365.5979 | 602.2685 | 325.789 | 324.0986 | 329.7611
4366.5979 | 602.572 | 325.4783 | 324.0786 | 329.615
4367.5979 | 602.9295 | 325.4038 | 323.959 | 329.7191
4368.5979 | 602.976 | 325.3334 | 323.7354 | 329.5247
4369.5979 | 603.509 | 325.1816 | 323.7514 | 329.3769
4370.5979 | 604.1029 | 324.8022 | 323.579 | 329.1516
4371.5979 | 604.5457 | 324.5532 | 323.1151 | 328.8648
4372.5979 | 604.9656 | 324.3606 | 322.8847 | 328.8292
4373.5979 | 605.4979 | 324.2262 | 322.6961 | 328.7349
4374.5979 | 605.391 | 324.1029 | 322.4417 | 328.5717
4375.5979 | 605.3478 | 324.0299 | 322.3133 | 328.5853
4376.5979 | 605.5558 | 324.079 | 322.2881 | 328.8085
4377.5979 | 606.2286 | 324.0803 | 321.9962 | 328.6983
4378.5979 | 606.5007 | 324.0813 | 321.7825 | 328.4884
4379.5979 | 607.3963 | 324.0619 | 321.5842 | 328.2917
4380.5979 | 607.6439 | 324.065 | 321.289 | 327.8144
4381.5979 | 607.7808 | 324.0428 | 321.1261 | 327.4526
4382.5979 | 608.6366 | 323.9797 | 320.8169 | 327.2034
4383.5979 | 609.4382 | 323.8557 | 320.5819 | 327.1765
4384.5979 | 609.8327 | 323.5521 | 320.0957 | 327.1811
4385.5979 | 609.8138 | 323.4785 | 320.2522 | 327.1004
4386.5979 | 609.8601 | 323.4485 | 320.3393 | 327.1418
4387.5979 | 610.1416 | 323.4984 | 320.3528 | 327.1873
4388.5979 | 610.9146 | 323.4322 | 320.3253 | 327.1207
4389.5979 | 610.6514 | 323.2607 | 320.0299 | 327.1037
4390.5979 | 610.2596 | 323.2865 | 320.0203 | 326.7238
4391.5979 | 611.049 | 323.4131 | 319.8791 | 327.0333
4392.5979 | 611.2356 | 323.3548 | 319.7275 | 326.8572
4393.5979 | 610.9691 | 323.1939 | 319.4935 | 326.5096
4394.5979 | 610.6307 | 323.0151 | 319.3393 | 326.2861
4395.5979 | 610.7595 | 322.8959 | 319.3846 | 326.2805
4396.5979 | 611.5772 | 322.9259 | 319.3327 | 326.4079
4397.5979 | 612.2714 | 322.8228 | 319.2011 | 326.2678
4398.5979 | 612.958 | 322.7522 | 318.9499 | 325.9821
4399.5979 | 613.9509 | 322.7084 | 318.9397 | 325.76
4400.5979 | 614.5018 | 322.637 | 318.8371 | 325.7332
4401.5979 | 615.2909 | 322.5701 | 318.6947 | 325.8134
4402.5979 | 615.6507 | 322.5503 | 318.5304 | 325.727
4403.5979 | 616.1587 | 322.4585 | 318.409 | 325.525
4404.5979 | 616.2898 | 322.4448 | 318.5296 | 325.6668
4405.5979 | 616.437 | 322.4258 | 318.4999 | 325.7704
4406.5979 | 616.7455 | 322.3757 | 318.439 | 325.7235
4407.5979 | 617.2651 | 322.3429 | 318.375 | 325.6104
4408.5979 | 617.4195 | 322.3844 | 318.5037 | 325.6599
4409.5979 | 618.1877 | 322.2769 | 318.49 | 325.5962
4410.5979 | 618.3265 | 322.225 | 318.5424 | 325.6197
4411.5979 | 617.6954 | 322.1231 | 318.583 | 325.5896
4412.5979 | 617.4377 | 322.0445 | 318.484 | 325.3853
4413.5979 | 616.8224 | 321.9907 | 318.6519 | 325.1822
4414.5979 | 616.2158 | 321.8668 | 318.4407 | 325.0668
4415.5979 | 616.111 | 321.525 | 318.3097 | 324.9618
4416.5979 | 616.3324 | 321.4556 | 318.2906 | 325.2758
4417.5979 | 616.3806 | 321.2615 | 317.9432 | 325.2839
4418.5979 | 616.266 | 321.117 | 317.7885 | 324.9869
4419.5979 | 615.8748 | 320.9864 | 317.4717 | 324.6846
4420.5979 | 615.9967 | 320.9103 | 317.467 | 324.6214
4421.5979 | 615.8615 | 320.8477 | 317.4501 | 324.709
4422.5979 | 615.96 | 320.8059 | 317.3135 | 324.6295
4423.5979 | 616.0177 | 320.7356 | 317.1782 | 324.4839
4424.5979 | 616.3132 | 320.6961 | 316.9743 | 324.3174
4425.5979 | 616.5674 | 320.6294 | 316.8148 | 323.9596
4426.5979 | 616.9723 | 320.5029 | 316.6419 | 323.6047
4427.5979 | 617.208 | 320.198 | 316.3553 | 323.3692
4428.5979 | 617.4582 | 320.0065 | 316.1801 | 323.4248
4429.5979 | 617.5399 | 319.7911 | 316.2443 | 323.5669
4430.5979 | 617.5632 | 319.7011 | 316.1284 | 323.4877
4431.5979 | 617.8212 | 319.543 | 316.0276 | 323.2999
4432.5979 | 617.6586 | 319.4721 | 315.9508 | 323.2303
4433.5979 | 617.5437 | 319.329 | 315.8543 | 323.213
4434.5979 | 618.0924 | 319.2308 | 315.7798 | 323.0412
4435.5979 | 619.1719 | 319.1311 | 315.732 | 322.9608
4436.5979 | 619.6766 | 319.1204 | 315.8693 | 322.9066
4437.5979 | 619.7973 | 319.1093 | 315.9472 | 322.8042
4438.5979 | 619.5085 | 318.9424 | 315.897 | 322.6198
4439.5979 | 619.2598 | 318.8233 | 315.683 | 322.6929
4440.5979 | 619.4311 | 318.7821 | 315.5465 | 322.7789
4441.5979 | 618.8107 | 318.6867 | 315.1878 | 322.7432
4442.5979 | 619.1002 | 318.6034 | 315.1319 | 322.9113
4443.5979 | 619.7648 | 318.6985 | 315.2677 | 322.7669
4444.5979 | 620.1336 | 318.7364 | 315.3823 | 322.6115
4445.5979 | 620.2075 | 318.7733 | 315.4144 | 322.6275
4446.5979 | 620.7033 | 318.7616 | 315.4204 | 322.6553
4447.5979 | 620.3036 | 318.4555 | 315.3623 | 322.5036
4448.5979 | 619.78 | 318.319 | 315.2514 | 322.2471
4449.5979 | 619.1903 | 318.0322 | 315.1286 | 322.2129
4450.5979 | 619.2158 | 318.0124 | 315.1217 | 322.1107
4451.5979 | 619.6726 | 318.0374 | 315.0672 | 322.0071
4452.5979 | 620.2162 | 317.9776 | 314.8857 | 321.8121
4453.5979 | 621.0049 | 317.8632 | 314.7813 | 321.5207
4454.5979 | 621.8856 | 317.8679 | 314.6229 | 321.3034
4455.5979 | 621.8328 | 317.7727 | 314.3961 | 321.0893
4456.5979 | 621.7511 | 317.6208 | 314.2764 | 320.8457
4457.5979 | 621.2232 | 317.6062 | 314.1802 | 320.6709
4458.5979 | 621.0988 | 317.626 | 313.9751 | 320.509
4459.5979 | 621.1168 | 317.5601 | 313.7345 | 320.3629
4460.5979 | 621.2536 | 317.4121 | 313.5159 | 320.3254
4461.5979 | 621.7317 | 317.3044 | 313.4194 | 320.3359
4462.5979 | 621.6934 | 317.191 | 313.1009 | 320.2707
4463.5979 | 621.782 | 317.0271 | 312.9515 | 320.1455
4464.5979 | 621.8943 | 316.8101 | 312.9488 | 320.0129
4465.5979 | 621.8316 | 316.7381 | 312.8959 | 319.8646
4466.5979 | 621.6422 | 316.6427 | 312.9515 | 319.7409
4467.5979 | 621.434 | 316.4273 | 312.754 | 319.6688
4468.5979 | 620.9002 | 316.2726 | 312.6936 | 319.7053
4469.5979 | 620.5042 | 316.3297 | 312.5406 | 319.6351
4470.5979 | 620.4153 | 316.2243 | 312.0855 | 319.4917
4471.5979 | 620.0228 | 316.0454 | 311.7607 | 319.4945
4472.5979 | 619.5178 | 315.8536 | 311.7853 | 319.5706
4473.5979 | 619.1269 | 315.7196 | 311.8689 | 319.6182
4474.5979 | 619.0894 | 315.8627 | 311.9258 | 319.4332
4475.5979 | 618.8572 | 315.8149 | 311.827 | 319.5383
4476.5979 | 618.8011 | 315.8014 | 311.9758 | 319.6892
4477.5979 | 618.3042 | 315.7912 | 311.9623 | 319.6402
4478.5979 | 618.2123 | 315.8131 | 311.9918 | 319.4303
4479.5979 | 617.9355 | 315.8538 | 311.9562 | 319.2445
4480.5979 | 617.5709 | 315.8992 | 311.9398 | 319.1031
4481.5979 | 617.2206 | 315.9093 | 311.7989 | 318.8841
4482.5979 | 617.4194 | 315.8935 | 311.6333 | 318.6938
4483.5979 | 617.1729 | 315.8337 | 311.4144 | 318.4742
4484.5979 | 617.3457 | 315.7755 | 311.2213 | 318.5202
4485.5979 | 617.3877 | 315.7525 | 311.0074 | 318.4345
4486.5979 | 617.4454 | 315.7489 | 310.9133 | 318.209
4487.5979 | 617.6512 | 315.7285 | 310.842 | 318.0888
4488.5979 | 618.0412 | 315.658 | 310.8618 | 317.8846
4489.5979 | 618.0561 | 315.4354 | 310.7651 | 317.802
4490.5979 | 618.2284 | 315.3614 | 310.7818 | 317.9247
4491.5979 | 618.0905 | 315.2282 | 310.6826 | 317.8561
4492.5979 | 618.0584 | 315.0054 | 310.6544 | 317.904
4493.5979 | 617.9425 | 314.7846 | 310.5047 | 317.7222
4494.5979 | 618.3832 | 314.5802 | 310.4593 | 317.5568
4495.5979 | 618.5188 | 314.5515 | 310.4122 | 317.3762
4496.5979 | 618.4674 | 314.5266 | 310.3233 | 317.2348
4497.5979 | 618.9205 | 314.1788 | 310.0576 | 317.2333
4498.5979 | 619.0205 | 314.1057 | 309.6861 | 317.2432
4499.5979 | 618.8106 | 313.95 | 309.5552 | 317.3108
4500.5979 | 618.5343 | 313.7751 | 309.4255 | 317.2815
4501.5979 | 618.8553 | 313.5011 | 309.3916 | 317.1255
4502.5979 | 619.3839 | 313.5042 | 309.2372 | 316.937
4503.5979 | 619.2373 | 313.4016 | 309.1523 | 317.0583
4504.5979 | 619.1885 | 313.3131 | 309.0821 | 317.1927
4505.5979 | 618.8536 | 313.2863 | 309.0043 | 317.0533
4506.5979 | 618.3592 | 313.1879 | 308.9809 | 317.0269
4507.5979 | 618.3259 | 313.2063 | 308.8403 | 316.9926
4508.5979 | 617.6474 | 313.2158 | 308.7844 | 316.8692
4509.5979 | 617.1437 | 313.2015 | 308.6951 | 316.6293
4510.5979 | 616.662 | 313.3051 | 308.6956 | 316.4919
4511.5979 | 616.4247 | 313.342 | 308.696 | 316.2315
4512.5979 | 616.3475 | 313.3625 | 308.6516 | 316.013
4513.5979 | 616.2905 | 313.317 | 308.5797 | 315.8024
4514.5979 | 616.069 | 313.3014 | 308.5416 | 315.6597
4515.5979 | 616.089 | 313.2478 | 308.4154 | 315.4931
4516.5979 | 616.2202 | 313.2574 | 308.4648 | 315.296
4517.5979 | 615.9449 | 313.2647 | 308.5202 | 315.204
4518.5979 | 615.5394 | 313.2902 | 308.6061 | 315.2674
4519.5979 | 616.1689 | 313.3034 | 308.6574 | 315.3356
4520.5979 | 616.866 | 313.3235 | 308.7752 | 315.4716
4521.5979 | 616.9111 | 313.4522 | 308.8582 | 315.4511
4522.5979 | 617.2743 | 313.5982 | 308.6832 | 315.4521
4523.5979 | 616.6777 | 313.732 | 308.8444 | 315.5187
4524.5979 | 616.22 | 313.5006 | 308.6616 | 315.6253
4525.5979 | 616.133 | 313.3374 | 308.8107 | 315.7237
4526.5979 | 616.3244 | 313.1889 | 308.6889 | 315.7858
4527.5979 | 616.6073 | 313.0576 | 308.7371 | 315.7609
4528.5979 | 616.7305 | 312.9256 | 308.5772 | 315.5341
4529.5979 | 617.0123 | 312.6729 | 308.4804 | 315.6058
4530.5979 | 617.1278 | 312.4347 | 308.1559 | 315.3659
4531.5979 | 616.8884 | 312.2325 | 307.7321 | 315.1995
4532.5979 | 616.7823 | 312.1422 | 307.5535 | 314.9009
4533.5979 | 616.4488 | 312.0916 | 307.4949 | 314.7661
4534.5979 | 616.8343 | 312.0367 | 307.2671 | 314.6599
4535.5979 | 616.809 | 311.9129 | 306.9999 | 314.4359
4536.5979 | 617.0649 | 311.891 | 306.7983 | 314.2871
4537.5979 | 617.7999 | 311.7524 | 306.5453 | 314.6316
4538.5979 | 618.503 | 311.7354 | 306.591 | 314.6268
4539.5979 | 618.5116 | 311.8644 | 306.668 | 314.5735
4540.5979 | 617.7608 | 311.7516 | 306.4681 | 314.3826
4541.5979 | 617.1149 | 311.5032 | 306.2398 | 314.4151
4542.5979 | 616.3191 | 311.4139 | 305.9008 | 314.576
4543.5979 | 616.1911 | 311.1036 | 305.9611 | 314.3681
4544.5979 | 616.2767 | 311.096 | 305.9 | 314.0348
4545.5979 | 616.4381 | 310.9307 | 305.8325 | 314.1022
4546.5979 | 616.8688 | 310.7748 | 305.8034 | 313.9237
4547.5979 | 616.62 | 310.6429 | 305.5944 | 313.8459
4548.5979 | 616.8835 | 310.4798 | 305.581 | 313.8512
4549.5979 | 616.6673 | 310.4657 | 305.8541 | 313.9842
4550.5979 | 616.4265 | 310.592 | 305.8802 | 313.9768
4551.5979 | 616.1984 | 310.424 | 306.0438 | 313.9175
4552.5979 | 615.8347 | 310.4035 | 306.419 | 313.9591
4553.5979 | 615.6455 | 310.3179 | 306.8241 | 314.0734
4554.5979 | 615.8556 | 310.242 | 306.9337 | 314.2131
4555.5979 | 615.7808 | 310.1895 | 306.885 | 314.184
4556.5979 | 615.4337 | 310.1229 | 306.8447 | 314.0527
4557.5979 | 614.6366 | 310.1046 | 306.8299 | 313.866
4558.5979 | 613.6923 | 310.112 | 306.6982 | 313.6657
4559.5979 | 612.9227 | 310.128 | 306.6005 | 313.4712
4560.5979 | 613.1818 | 310.1368 | 306.4976 | 313.3421
4561.5979 | 613.9597 | 310.1137 | 306.379 | 313.0838
4562.5979 | 614.4996 | 310.1583 | 306.0159 | 312.7797
4563.5979 | 614.4775 | 310.1592 | 305.9282 | 312.5804
4564.5979 | 614.6677 | 310.1557 | 305.8512 | 312.3928
4565.6135 | 614.5576 | 310.0609 | 305.7932 | 312.2563
4566.5979 | 614.4427 | 309.9159 | 305.758 | 312.1067
4567.5979 | 614.8239 | 309.8484 | 305.6569 | 311.9369
4568.5979 | 615.0728 | 309.8225 | 305.6522 | 312.0106
4569.5979 | 615.6521 | 309.8534 | 305.6716 | 312.2435
4570.5979 | 616.2467 | 309.842 | 305.4956 | 312.1246
4571.5979 | 616.8495 | 309.8821 | 305.4399 | 311.9876
4572.5979 | 617.2739 | 309.9058 | 305.2766 | 312.2012
4573.5979 | 617.294 | 309.8241 | 305.154 | 312.1713
4574.5979 | 617.8747 | 309.7179 | 305.0505 | 312.1674
4575.5979 | 617.8556 | 309.5722 | 304.9416 | 312.0894
4576.5979 | 617.8869 | 309.3049 | 304.9472 | 312.1212
4577.5979 | 618.2993 | 309.0889 | 304.6147 | 312.1056
4578.5979 | 618.2626 | 309.0528 | 304.5439 | 312.0962
4579.5979 | 617.7544 | 309.0621 | 304.5188 | 312.1378
4580.5979 | 617.3469 | 308.9838 | 304.3271 | 312.2953
4581.5979 | 616.9835 | 308.8384 | 304.2917 | 312.3318
4582.5979 | 616.56 | 308.7123 | 304.4272 | 312.6584
4583.5979 | 616.2672 | 308.7215 | 304.5212 | 312.6033
4584.5979 | 615.8064 | 309.0409 | 304.7369 | 312.4796
4585.5979 | 615.5578 | 309.202 | 304.9657 | 312.3799
4586.5979 | 615.8474 | 309.0876 | 305.2205 | 312.3137
4587.5979 | 616.2425 | 308.7254 | 305.3629 | 312.0192
4588.5979 | 615.7257 | 308.6294 | 305.3881 | 312.0142
4589.5979 | 615.1036 | 308.4812 | 305.1936 | 311.8338
4590.5979 | 614.4147 | 308.3007 | 304.9296 | 311.7297
4591.5979 | 614.3381 | 308.1032 | 304.7638 | 311.5568
4592.5979 | 614.7642 | 307.9598 | 304.5731 | 311.4236
4593.5979 | 614.5042 | 307.7857 | 304.3708 | 311.1
4594.5979 | 614.5093 | 307.6751 | 304.1218 | 310.9087
4595.6135 | 614.544 | 307.3623 | 303.9673 | 310.7191
4596.5979 | 614.4632 | 307.4432 | 303.8596 | 310.5421
4597.5979 | 614.4403 | 307.476 | 303.6428 | 310.3625
4598.5979 | 614.4048 | 307.4143 | 303.3804 | 310.1248
4599.5979 | 614.5716 | 307.349 | 303.1604 | 309.9843
4600.5979 | 614.6043 | 307.3088 | 302.7171 | 309.777
4601.5979 | 614.9795 | 306.8837 | 302.5128 | 309.2796
4602.6135 | 614.6044 | 306.5383 | 302.3253 | 309.1628
4603.5979 | 614.561 | 306.5022 | 302.1453 | 309.161
4604.5979 | 614.8223 | 306.3912 | 302.0183 | 309.1491
4605.5979 | 614.3676 | 306.373 | 301.927 | 309.0717
4606.5979 | 614.5766 | 306.396 | 301.9245 | 308.8971
4607.5979 | 614.3102 | 306.4656 | 301.9956 | 308.9105
4608.5979 | 614.6763 | 306.4438 | 301.9305 | 308.9134
4609.5979 | 614.6558 | 306.438 | 301.6851 | 308.6226
4610.5979 | 614.705 | 306.3806 | 301.7396 | 308.5941
4611.5979 | 614.1668 | 306.3735 | 301.6544 | 308.6348
4612.5979 | 614.2612 | 306.3678 | 301.7153 | 308.6578
4613.5979 | 613.9006 | 306.429 | 301.7663 | 308.7396
4614.5979 | 613.8305 | 306.3967 | 301.8205 | 308.7038
4615.5979 | 613.9233 | 306.3585 | 301.7215 | 308.5503
4616.5979 | 613.8959 | 306.3772 | 301.7525 | 308.4594
4617.5979 | 614.2435 | 306.4234 | 301.6742 | 308.3757
4618.5979 | 614.6729 | 306.4052 | 301.4091 | 308.2102
4619.5979 | 614.9725 | 306.4487 | 301.2612 | 307.8894
4620.5979 | 614.9746 | 306.2984 | 301.1886 | 307.8103
4621.5979 | 615.0815 | 306.1476 | 301.298 | 307.7171
4622.5979 | 615.2509 | 306.1313 | 301.1693 | 307.6599
4623.5979 | 615.1634 | 306.0623 | 300.982 | 307.4559
4624.5979 | 614.2619 | 305.8266 | 300.8552 | 307.2898
4625.5979 | 612.8151 | 305.7658 | 300.8306 | 307.2652
4626.5979 | 611.8559 | 305.5896 | 300.852 | 307.2822
4627.5979 | 611.5725 | 305.6584 | 300.9325 | 307.3169
4628.5979 | 611.6761 | 305.7105 | 300.9877 | 307.3487
4629.5979 | 611.8037 | 305.6381 | 300.8409 | 307.2936
4630.5979 | 611.8373 | 305.6067 | 300.6833 | 307.1096
4631.5979 | 611.7685 | 305.6114 | 300.5162 | 306.8445
4632.5979 | 611.6951 | 305.5745 | 300.4105 | 306.7543
4633.5979 | 611.3425 | 305.5152 | 300.3219 | 306.6546
4634.5979 | 611.6189 | 305.3565 | 300.2299 | 306.6057
4635.5979 | 611.5875 | 305.3648 | 300.1173 | 306.4994
4636.5979 | 611.5706 | 305.3478 | 300.1535 | 306.6257
4637.5979 | 611.6618 | 305.3255 | 300.1298 | 306.6996
4638.5979 | 611.8285 | 305.1354 | 300.2254 | 306.7959
4639.5979 | 610.996 | 304.9354 | 300.4548 | 306.8955
4640.5979 | 610.7146 | 304.8607 | 300.5859 | 307.0402
4641.5979 | 610.4741 | 304.8659 | 300.6456 | 307.1028
4642.5979 | 610.3108 | 305.1013 | 300.5448 | 307.1752
4643.5979 | 610.2112 | 305.2577 | 300.8631 | 307.3797
4644.5979 | 610.2401 | 305.4194 | 301.2664 | 307.6786
4645.5979 | 610.1178 | 305.5843 | 301.5619 | 307.9819
4646.5979 | 610.1091 | 305.7012 | 301.7258 | 308.0985
4647.5979 | 609.4079 | 305.8489 | 301.8679 | 308.1945
4648.5979 | 608.8124 | 305.7568 | 301.8597 | 308.293
4649.5979 | 608.627 | 305.5961 | 301.7933 | 308.3006
4650.5979 | 608.7634 | 305.4149 | 301.5838 | 308.2198
4651.5979 | 608.7246 | 305.1864 | 301.376 | 308.0926
4652.5979 | 608.803 | 305.0517 | 301.1234 | 308.011
4653.5979 | 608.9553 | 304.9358 | 300.9853 | 307.8672
4654.5979 | 609.134 | 304.7769 | 300.8779 | 307.6568
4655.5979 | 609.1864 | 304.6603 | 300.79 | 307.4655
4656.5979 | 608.9587 | 304.6588 | 300.6724 | 307.3648
4657.5979 | 608.5773 | 304.6527 | 300.685 | 307.4344
4658.5979 | 607.9358 | 304.5001 | 300.5727 | 307.5631
4659.5979 | 608.2668 | 304.364 | 300.6566 | 307.5079
4660.5979 | 607.8398 | 304.2925 | 300.6376 | 307.4243
4661.5979 | 607.6134 | 304.1548 | 300.7299 | 307.3748
4662.5979 | 607.0163 | 304.0479 | 300.7299 | 307.3642
4663.5979 | 606.7069 | 304.1249 | 300.5619 | 307.2111
4664.5979 | 606.9599 | 304.077 | 300.4676 | 307.0472
4665.5979 | 607.5819 | 304.1152 | 300.4001 | 306.912
4666.5979 | 607.7781 | 304.0189 | 300.2955 | 306.6627
4667.5979 | 608.614 | 304.0775 | 300.1655 | 306.4943
4668.5979 | 609.3615 | 304.0445 | 300.0364 | 306.2319
4669.5979 | 609.89 | 304.0254 | 299.7217 | 306.052
4670.5979 | 609.801 | 303.9764 | 299.4109 | 305.8685
4671.5979 | 609.8898 | 303.8789 | 299.0887 | 305.7926
4672.5979 | 609.4212 | 303.7865 | 299.0602 | 305.7609
4673.5979 | 609.0433 | 303.7836 | 298.8985 | 305.7166
4674.5979 | 609.6398 | 303.7556 | 298.8159 | 305.522
4675.5979 | 609.6847 | 303.691 | 298.6228 | 305.352
4676.5979 | 609.5806 | 303.6959 | 298.3031 | 305.1872
4677.5979 | 609.5979 | 303.7061 | 298.1541 | 305.0724
4678.5979 | 609.4624 | 303.4783 | 297.9341 | 305.0472
4679.5979 | 609.4021 | 303.1877 | 297.6373 | 304.8888
4680.5979 | 609.7993 | 302.9316 | 297.3087 | 304.5525
4681.5979 | 610.1115 | 302.7659 | 296.966 | 304.4229
4682.5979 | 610.2052 | 302.523 | 296.7511 | 304.3587
4683.5979 | 610.0301 | 302.3982 | 296.636 | 304.2728
4684.5979 | 609.5852 | 302.1765 | 296.6778 | 304.1532
4685.5979 | 609.6556 | 302.1424 | 296.5971 | 304.0821
4686.5979 | 609.6682 | 302.1235 | 296.6712 | 303.935
4687.5979 | 609.5716 | 302.1446 | 296.6609 | 303.9026
4688.5979 | 609.8102 | 302.0858 | 296.5989 | 303.7796
4689.5979 | 609.7276 | 301.9931 | 296.5546 | 303.5874
4690.5979 | 609.7261 | 301.9472 | 296.4686 | 303.4346
4691.5979 | 609.8098 | 301.9556 | 296.2664 | 303.1944
4692.5979 | 610.0701 | 301.9718 | 296.0958 | 303.2253
4693.5979 | 610.2338 | 301.9086 | 296.0586 | 303.0977
4694.5979 | 610.2844 | 301.8892 | 295.9315 | 302.9734
4695.5979 | 610.3055 | 301.7226 | 295.8024 | 303.0631
4696.5979 | 609.9166 | 301.5393 | 295.742 | 303.1081
4697.5979 | 609.3074 | 301.5101 | 295.6738 | 303.0109
4698.5979 | 608.5654 | 301.4909 | 295.7497 | 302.9239
4699.5979 | 608.3039 | 301.3056 | 295.7831 | 302.8855
4700.5979 | 608.1215 | 301.2349 | 295.8143 | 302.8316
4701.5979 | 607.9817 | 301.1568 | 295.9569 | 302.7726
4702.5979 | 607.4603 | 301.1253 | 296.0233 | 302.7995
4703.5979 | 606.7629 | 300.9782 | 296.0153 | 302.7632
4704.5979 | 606.7477 | 300.867 | 296.0105 | 302.7242
4705.5979 | 606.6129 | 300.5179 | 295.9945 | 302.7666
4706.5979 | 606.7693 | 300.38 | 295.9491 | 302.622
4707.5979 | 606.5781 | 300.3281 | 295.9221 | 302.5864
4708.5979 | 606.4475 | 300.1357 | 295.9305 | 302.7076
4709.5979 | 606.849 | 299.9299 | 295.8719 | 302.6663
4710.5979 | 607.305 | 299.8544 | 295.7295 | 302.589
4711.5979 | 607.5114 | 299.7768 | 295.8307 | 302.339
4712.5979 | 607.4526 | 299.872 | 295.8482 | 302.4525
4713.5979 | 607.352 | 299.8267 | 295.6907 | 302.3067
4714.5979 | 607.0569 | 299.8378 | 295.6509 | 302.293
4715.5979 | 606.6479 | 299.9044 | 295.5787 | 302.0699
4716.5979 | 606.5502 | 299.7972 | 295.5296 | 301.9305
4717.5979 | 606.444 | 299.7042 | 295.4805 | 301.6665
4718.5979 | 606.2136 | 299.5113 | 295.3668 | 301.3954
4719.5979 | 606.305 | 299.355 | 295.1347 | 301.0873
4720.5979 | 606.2706 | 299.149 | 294.8734 | 300.8924
4721.5979 | 606.2342 | 299.0754 | 294.3615 | 300.7967
4722.5979 | 606.3722 | 299.1428 | 294.123 | 300.8443
4723.5979 | 606.707 | 299.113 | 294.0217 | 300.7727
4724.5979 | 606.3333 | 299.1003 | 293.8339 | 300.6167
4725.5979 | 606.0562 | 299.1292 | 293.7098 | 300.451
4726.5979 | 605.6561 | 299.1288 | 293.6435 | 300.5932
4727.5979 | 605.571 | 299.1703 | 293.4943 | 300.5192
4728.5979 | 605.7179 | 299.1383 | 293.4657 | 300.397
4729.5979 | 605.4192 | 299.029 | 293.396 | 300.46
4730.5979 | 605.4229 | 299.1101 | 293.4246 | 300.4257
4731.5979 | 605.5912 | 299.1313 | 293.8048 | 300.4802
4732.5979 | 605.3287 | 299.3161 | 294.124 | 300.6466
4733.5979 | 605.1259 | 299.4247 | 294.2356 | 300.8242
4734.5979 | 604.9316 | 299.3141 | 294.1584 | 300.8383
4735.5979 | 604.1595 | 299.36 | 294.2739 | 300.7153
4736.5979 | 603.5306 | 299.3464 | 294.1553 | 300.5755
4737.5979 | 603.228 | 299.3182 | 294.0063 | 300.4823
4738.5979 | 603.0056 | 299.3191 | 293.9934 | 300.2058
4739.5979 | 602.9855 | 299.1812 | 293.9227 | 300.0856
4740.5979 | 603.1528 | 299.026 | 293.7392 | 299.849
4741.5979 | 603.3246 | 298.9986 | 293.6253 | 299.6257
4742.5979 | 603.1999 | 298.9441 | 293.4719 | 299.5899
4743.5979 | 602.771 | 298.9055 | 293.3129 | 299.4967
4744.5979 | 602.3699 | 298.8717 | 293.2203 | 299.3971
4745.5979 | 601.7607 | 298.7757 | 293.2207 | 299.3948
4746.5979 | 601.766 | 298.7284 | 293.1936 | 299.3698
4747.5979 | 601.8976 | 298.6909 | 293.0695 | 299.309
4748.5979 | 601.9827 | 298.6366 | 292.9105 | 299.1067
4749.5979 | 601.6689 | 298.6199 | 292.6626 | 298.9835
4750.5979 | 601.5624 | 298.5691 | 292.5572 | 298.7982
4751.5979 | 601.2036 | 298.3255 | 292.5204 | 298.7274
4752.5979 | 600.7244 | 298.1075 | 292.4528 | 298.729
4753.5979 | 600.5335 | 297.7755 | 292.4368 | 298.802
4754.5979 | 600.7322 | 297.5901 | 292.418 | 298.8422
4755.5979 | 601.0246 | 297.3592 | 292.3965 | 298.8136
4756.5979 | 600.9275 | 297.1428 | 292.5141 | 298.8433
4757.5979 | 600.9377 | 297.1395 | 292.5744 | 298.7744
4758.5979 | 600.5164 | 297.0722 | 292.5543 | 298.81
4759.5979 | 600.2587 | 297.0972 | 292.8476 | 298.9806
4760.5979 | 599.8866 | 297.1349 | 293.1244 | 299.0979
4761.5979 | 599.5968 | 297.0652 | 293.247 | 299.2411
4762.5979 | 599.4708 | 297.12 | 293.3653 | 299.3711
4763.5979 | 599.4816 | 297.1205 | 293.4236 | 299.431
4764.5979 | 599.3796 | 297.2249 | 293.4814 | 299.5022
4765.5979 | 599.1708 | 297.1484 | 293.6375 | 299.4495
4766.5979 | 598.9195 | 297.1342 | 293.6181 | 299.6551
4767.5979 | 598.8869 | 297.007 | 293.5002 | 299.7162
4768.5979 | 599.3769 | 297.0324 | 293.4163 | 299.7544
4769.5979 | 599.3287 | 297.0429 | 293.3594 | 299.4359
4770.5979 | 599.0356 | 296.9854 | 293.284 | 299.2313
4771.5979 | 598.8001 | 296.9725 | 293.243 | 299.3476
4772.5979 | 598.5697 | 296.9754 | 293.1526 | 299.2975
4773.5979 | 598.4856 | 296.9685 | 293.1731 | 299.2453
4774.5979 | 598.6096 | 297.0111 | 293.2814 | 299.3443
4775.5979 | 598.8058 | 297.1349 | 293.4358 | 299.5442
4776.5979 | 599.1549 | 297.2257 | 293.5221 | 299.6363
4777.5979 | 599.3764 | 297.3212 | 293.5364 | 299.6568
4778.5979 | 599.4497 | 297.3453 | 293.2906 | 299.6176
4779.5979 | 599.4127 | 297.3223 | 293.2048 | 299.5274
4780.5979 | 599.3508 | 297.2259 | 293.1556 | 299.4253
4781.5979 | 599.0617 | 296.8937 | 293 | 299.1602
4782.6135 | 598.2479 | 296.4501 | 292.773 | 298.951
4783.5979 | 598.1137 | 296.0929 | 292.5396 | 298.8252
4784.5979 | 598.1204 | 295.8576 | 292.4315 | 298.7599
4785.5979 | 598.0675 | 295.9029 | 292.3681 | 298.6816
4786.5979 | 598.0849 | 295.6589 | 292.3191 | 298.5195
4787.5979 | 597.8675 | 295.6052 | 292.2108 | 298.2636
4788.5979 | 598.1437 | 295.4851 | 291.9897 | 298.1231
4789.5979 | 598.3153 | 295.3053 | 291.9284 | 297.9793
4790.5979 | 598.679 | 295.249 | 291.7837 | 297.7147
4791.5979 | 599.0114 | 295.2135 | 291.5563 | 297.4524
4792.5979 | 599.3521 | 295.1461 | 291.5734 | 297.3555
4793.5979 | 599.1397 | 295.1071 | 291.4295 | 297.2056
4794.5979 | 599.434 | 295.1274 | 291.3848 | 297.0829
4795.6135 | 599.263 | 295.1709 | 291.2697 | 296.9044
4796.5979 | 599.2146 | 295.1702 | 291.1684 | 296.7774
4797.5979 | 599.725 | 295.234 | 291.1079 | 296.7804
4798.5979 | 599.6738 | 295.2671 | 290.9925 | 296.7209
4799.5979 | 599.8153 | 295.2012 | 290.8476 | 296.5993
4800.5979 | 599.3697 | 295.174 | 290.7824 | 296.4401
4801.5979 | 599.5345 | 294.8794 | 290.6991 | 296.348
4802.5979 | 600.1176 | 294.8322 | 290.7054 | 296.2053
4803.5979 | 600.0069 | 294.6862 | 290.5494 | 296.0855
4804.5979 | 599.8499 | 294.672 | 290.4797 | 295.8859
4805.6135 | 599.7033 | 294.6621 | 290.1585 | 295.8398
4806.5979 | 599.9207 | 294.5937 | 290.0501 | 295.8435
4807.5979 | 600.0467 | 294.481 | 289.9268 | 295.7905
4808.5979 | 599.8687 | 294.4165 | 289.8357 | 295.6995
4809.5979 | 600.1022 | 294.4089 | 289.7097 | 295.4884
4810.5979 | 600.3562 | 294.42 | 289.6798 | 295.3215
4811.5979 | 600.1892 | 294.4133 | 289.5054 | 295.2628
4812.5979 | 600.1549 | 294.4313 | 289.2715 | 295.0871
4813.5979 | 600.2959 | 294.4114 | 289.0242 | 294.8683
4814.5979 | 600.0374 | 294.3429 | 288.8937 | 294.6629
4815.5979 | 599.6645 | 294.2107 | 288.729 | 294.5196
4816.5979 | 599.249 | 294.1546 | 288.5192 | 294.4322
4817.5979 | 598.3112 | 294.1077 | 288.0922 | 294.3039
4818.5979 | 598.1222 | 294.0649 | 287.7937 | 294.1421
4819.5979 | 597.337 | 293.9372 | 287.6981 | 294.1543
4820.5979 | 596.8464 | 293.8904 | 287.6352 | 294.1732
4821.5979 | 596.5511 | 293.9151 | 287.6271 | 294.0667
4822.5979 | 596.2591 | 293.8281 | 287.6151 | 293.9539
4823.5979 | 596.1905 | 293.8793 | 287.707 | 293.8831
4824.5979 | 596.6654 | 293.8512 | 287.9483 | 293.7872
4825.5979 | 597.2855 | 293.8711 | 287.9198 | 293.6975
4826.5979 | 596.8907 | 293.9247 | 287.8899 | 293.6745
4827.5979 | 596.7457 | 293.936 | 287.9274 | 293.4655
4828.5979 | 596.5962 | 293.9174 | 287.9644 | 293.5525
4829.5979 | 596.2241 | 293.8692 | 287.892 | 293.565
4830.5979 | 595.7986 | 293.8301 | 287.7826 | 293.5172
4831.5979 | 594.6847 | 293.7634 | 287.6022 | 293.3163
4832.5979 | 594.5511 | 293.5555 | 287.565 | 293.3444
4833.5979 | 594.8035 | 293.4085 | 287.526 | 293.3923
4834.5979 | 594.883 | 293.3713 | 287.4991 | 293.4347
4835.5979 | 595.2764 | 293.264 | 287.4336 | 293.5328
4836.5979 | 595.3825 | 293.1451 | 287.3179 | 293.4231
4837.5979 | 595.3865 | 293.123 | 287.3611 | 293.3135
4838.5979 | 595.5199 | 292.9665 | 287.3824 | 293.3076
4839.5979 | 594.8983 | 292.9664 | 287.3707 | 293.1297
4840.5979 | 594.063 | 292.9834 | 287.3617 | 292.9916
4841.5979 | 593.8158 | 293.0066 | 287.3928 | 292.9071
4842.5979 | 593.7283 | 293.0263 | 287.3534 | 292.9523
4843.5979 | 593.7465 | 293.1181 | 287.3124 | 292.8893
4844.5979 | 593.6694 | 293.0983 | 287.2514 | 292.787
4845.5979 | 593.7078 | 293.0742 | 287.1967 | 292.6785
4846.5979 | 593.3735 | 293.0409 | 287.0373 | 292.5839
4847.5979 | 593.1306 | 292.9239 | 286.8447 | 292.5789
4848.5979 | 593.0675 | 292.8004 | 286.8425 | 292.4386
4849.5979 | 593.0239 | 292.7688 | 286.5158 | 292.2538
4850.5979 | 593.0907 | 292.7748 | 286.2852 | 291.8344
4851.5979 | 593.2325 | 292.6306 | 286.1497 | 291.7258
4852.5979 | 593.664 | 292.571 | 285.9955 | 291.7253
4853.5979 | 593.5127 | 292.4353 | 285.8178 | 291.6192
4854.5979 | 593.3829 | 292.2832 | 285.5907 | 291.4747
4855.5979 | 593.4062 | 292.2451 | 285.3709 | 291.3586
4856.5979 | 593.6024 | 292.2391 | 285.2214 | 291.2711
4857.5979 | 593.8132 | 292.0161 | 285.1009 | 291.2699
4858.5979 | 593.9659 | 291.6259 | 284.9085 | 291.2323
4859.5979 | 593.6595 | 291.5178 | 284.8362 | 291.4323
4860.5979 | 593.1879 | 291.3988 | 284.8296 | 291.4788
4861.5979 | 592.4802 | 291.2743 | 285.061 | 291.4986
4862.5979 | 592.4773 | 291.108 | 285.1976 | 291.5556
4863.5979 | 591.8008 | 290.9638 | 285.1544 | 291.5847
4864.5979 | 591.7722 | 290.8834 | 285.1239 | 291.5668
4865.5979 | 591.6697 | 290.7676 | 285.0192 | 291.4636
4866.5979 | 592.2869 | 290.7307 | 285.0909 | 291.2787
4867.5979 | 592.521 | 290.7218 | 285.2182 | 291.2285
4868.5979 | 592.4683 | 290.6975 | 285.3441 | 291.2628
4869.5979 | 592.6411 | 290.7892 | 285.4652 | 291.3078
4870.5979 | 592.4615 | 290.5926 | 285.4862 | 291.1979
4871.5979 | 592.4157 | 290.2639 | 285.2395 | 291.0944
4872.5979 | 592.3386 | 290.1899 | 285.0812 | 290.9572
4873.5979 | 592.1824 | 290.1982 | 284.8946 | 291.0439
4874.5979 | 592.4289 | 290.1478 | 284.6199 | 291.0962
4875.5979 | 592.4488 | 289.9339 | 284.4707 | 290.982
4876.5979 | 591.957 | 289.7152 | 284.6826 | 290.9423
4877.5979 | 591.1557 | 289.6219 | 284.6152 | 290.8578
4878.5979 | 590.3495 | 289.5672 | 284.6802 | 290.7828
4879.5979 | 589.7635 | 289.4408 | 284.6747 | 290.7111
4880.5979 | 589.3204 | 289.2692 | 284.5294 | 290.6736
4881.5979 | 589.3165 | 289.2735 | 284.5277 | 290.6322
4882.5979 | 589.0892 | 289.2564 | 284.5483 | 290.6207
4883.5979 | 588.8218 | 289.1315 | 284.6118 | 290.6192
4884.5979 | 588.3558 | 288.9751 | 284.4096 | 290.6322
4885.5979 | 588.4424 | 288.7857 | 284.3875 | 290.5552
4886.5979 | 588.0169 | 288.7869 | 284.5053 | 290.674
4887.5979 | 588.015 | 288.712 | 284.4755 | 290.7465
4888.5979 | 587.8938 | 288.7602 | 284.4579 | 290.5224
4889.5979 | 587.7207 | 288.7859 | 284.4902 | 290.3579
4890.5979 | 587.4852 | 288.5882 | 284.3814 | 290.2726
4891.5979 | 587.5582 | 288.6015 | 284.3008 | 290.2917
4892.5979 | 587.5767 | 288.6648 | 284.4528 | 290.2157
4893.5979 | 587.5121 | 288.71 | 284.5307 | 290.141
4894.5979 | 587.4234 | 288.7393 | 284.4532 | 290.0843
4895.5979 | 586.9555 | 288.5831 | 284.1767 | 289.91
4896.5979 | 586.618 | 288.4332 | 283.9459 | 289.831
4897.5979 | 585.9985 | 288.3002 | 283.7044 | 289.7555
4898.5979 | 585.832 | 288.2822 | 283.6207 | 289.6022
4899.5979 | 586.2366 | 288.2581 | 283.4729 | 289.4597
4900.5979 | 586.2455 | 288.3785 | 283.3842 | 289.3809
4901.5979 | 586.1874 | 288.2725 | 283.3499 | 289.4401
4902.5979 | 585.3837 | 288.2406 | 283.2705 | 289.3514
4903.5979 | 585.171 | 288.1828 | 283.1978 | 289.1041
4904.5979 | 585.3554 | 288.2518 | 283.2434 | 289.0284
4905.5979 | 585.8258 | 288.2737 | 283.1311 | 288.8879
4906.5979 | 586.1934 | 288.2307 | 283.0015 | 288.9141
4907.5979 | 586.0203 | 288.1028 | 283.126 | 288.9276
4908.5979 | 586.1868 | 288.047 | 283.1661 | 288.9339
4909.5979 | 586.1311 | 288.0058 | 283.2786 | 288.9591
4910.5979 | 586.384 | 288.068 | 283.3495 | 289.0029
4911.5979 | 586.2298 | 288.1843 | 283.3518 | 289.013
4912.5979 | 586.5988 | 288.2642 | 283.4052 | 289.0178
4913.5979 | 586.7261 | 288.3896 | 283.3453 | 289.0308
4914.5979 | 586.9431 | 288.434 | 283.0299 | 288.8492
4915.5979 | 586.8908 | 288.3668 | 282.826 | 288.6856
4916.5979 | 586.7167 | 288.3601 | 282.6387 | 288.5016
4917.5979 | 586.6111 | 288.3369 | 282.4615 | 288.3686
4918.5979 | 586.513 | 288.322 | 282.3187 | 288.3066
4919.5979 | 586.3203 | 288.1638 | 282.1775 | 288.2862
4920.5979 | 585.9149 | 287.8887 | 282.22 | 288.128
4921.5979 | 585.8814 | 287.6761 | 282.1296 | 287.9804
4922.5979 | 585.7289 | 287.3861 | 282.0903 | 287.8334
4923.5979 | 585.2297 | 287.1611 | 282.0743 | 287.8347
4924.5979 | 584.5637 | 287.0387 | 281.9715 | 287.7656
4925.5979 | 584.2674 | 286.9062 | 281.9029 | 287.6539
4926.5979 | 584.3682 | 286.7709 | 281.8731 | 287.5602
4927.5979 | 584.4404 | 286.6621 | 281.6896 | 287.4555
4928.5979 | 584.469 | 286.5542 | 281.5222 | 287.4407
4929.5979 | 584.2464 | 286.4803 | 281.2126 | 287.3581
4930.5979 | 583.2642 | 286.3886 | 280.98 | 287.2338
4931.5979 | 582.5375 | 286.3806 | 280.9981 | 287.1966
4932.5979 | 582.3928 | 286.4032 | 280.9246 | 287.1975
4933.5979 | 582.661 | 286.3224 | 280.8437 | 287.0779
4934.5979 | 582.8326 | 286.267 | 280.7102 | 286.9255
4935.5979 | 582.4901 | 286.3591 | 280.5096 | 286.7874
4936.5979 | 582.2378 | 286.4626 | 280.4005 | 286.6959
4937.5979 | 582.0481 | 286.4236 | 280.4149 | 286.7454
4938.5979 | 581.707 | 286.2864 | 280.42 | 286.6553
4939.5979 | 581.6442 | 286.1301 | 280.3965 | 286.5983
4940.5979 | 581.5555 | 286.1534 | 280.4192 | 286.6274
4941.5979 | 581.8756 | 286.1287 | 280.0761 | 286.5884
4942.5979 | 582.1926 | 286.0052 | 279.8686 | 286.5161
4943.5979 | 582.5437 | 285.9018 | 279.7805 | 286.4351
4944.5979 | 582.1396 | 285.9052 | 279.5535 | 286.4201
4945.5979 | 581.9552 | 285.9264 | 279.4232 | 286.405
4946.5979 | 581.4686 | 285.9276 | 279.2338 | 286.1628
4947.5979 | 581.5662 | 285.9287 | 279.136 | 285.8565
4948.5979 | 581.366 | 285.7476 | 278.9496 | 285.8776
4949.5979 | 581.3112 | 285.6053 | 278.8574 | 285.7573
4950.5979 | 581.1135 | 285.4378 | 278.8684 | 285.7584
4951.5979 | 581.1187 | 285.3001 | 278.9164 | 285.6075
4952.5979 | 581.2101 | 285.2343 | 278.9405 | 285.6945
4953.5979 | 581.2482 | 285.2697 | 278.9723 | 285.6989
4954.5979 | 581.4476 | 285.239 | 279.0773 | 285.6291
4955.5979 | 581.5552 | 285.3151 | 279.1691 | 285.4378
4956.5979 | 581.5757 | 285.4156 | 279.1088 | 285.4197
4957.5979 | 581.4581 | 285.3141 | 278.9484 | 285.2886
4958.5979 | 581.0042 | 285.2315 | 278.7408 | 284.9192
4959.5979 | 580.5513 | 285.3186 | 278.7045 | 284.6807
4960.5979 | 579.9921 | 285.3098 | 278.7256 | 284.6601
4961.5979 | 579.6091 | 285.3089 | 278.6804 | 284.6018
4962.5979 | 579.5768 | 285.3567 | 278.48 | 284.4353
4963.5979 | 579.9804 | 285.4265 | 278.3377 | 284.4668
4964.5979 | 580.0697 | 285.4521 | 278.2107 | 284.5668
4965.5979 | 579.87 | 285.4843 | 278.2393 | 284.6074
4966.5979 | 579.8783 | 285.5252 | 278.3732 | 284.5262
4967.5979 | 579.6505 | 285.5191 | 278.5627 | 284.399
4968.5979 | 579.4381 | 285.5008 | 278.57 | 284.2342
4969.5979 | 579.2382 | 285.1701 | 278.2035 | 284.0679
4970.5979 | 579.4735 | 284.76 | 277.9288 | 284.0961
4971.5979 | 579.9918 | 284.3795 | 277.8781 | 284.0379
4972.5979 | 579.6119 | 284.3216 | 277.601 | 283.9666
4973.5979 | 578.9498 | 284.3523 | 277.3529 | 283.836
4974.5979 | 578.3077 | 284.269 | 277.0413 | 283.631
4975.5979 | 578.029 | 284.2077 | 276.9797 | 283.4345
4976.5979 | 578.1762 | 284.1806 | 276.958 | 283.5051
4977.5979 | 578.1079 | 284.241 | 277.1214 | 283.556
4978.5979 | 578.2394 | 284.2332 | 277.2719 | 283.4947
4979.5979 | 577.7624 | 284.2686 | 277.3197 | 283.361
4980.5979 | 577.334 | 284.2475 | 277.3108 | 283.2603
4981.5979 | 577.2012 | 284.2701 | 277.2614 | 283.0842
4982.5979 | 576.8922 | 284.1924 | 277.2151 | 282.9377
4983.5979 | 575.9297 | 284.0722 | 277.3168 | 282.8761
4984.5979 | 575.5393 | 284.1559 | 277.2425 | 282.7898
4985.5979 | 575.3663 | 284.0099 | 277.2263 | 282.8026
4986.5979 | 575.8399 | 284.0391 | 277.2092 | 282.8927
4987.5979 | 576.3116 | 283.9957 | 277.048 | 282.7174
4988.5979 | 576.5583 | 283.7785 | 276.7961 | 282.6027
4989.5979 | 576.6192 | 283.6809 | 276.6217 | 282.4947
4990.5979 | 576.4002 | 283.6478 | 276.512 | 282.4581
4991.5979 | 576.2511 | 283.6858 | 276.5658 | 282.478
4992.5979 | 576.2317 | 283.619 | 276.6874 | 282.423
4993.5979 | 576.4217 | 283.6339 | 276.6737 | 282.4005
4994.5979 | 576.4345 | 283.5822 | 276.6245 | 282.3125
4995.5979 | 576.3694 | 283.5378 | 276.7174 | 282.2057
4996.5979 | 576.4242 | 283.2989 | 276.7983 | 282.3057
4997.5979 | 575.7769 | 283.0255 | 276.8138 | 282.4177
4998.5979 | 575.5035 | 282.9161 | 276.936 | 282.5503
4999.5979 | 575.3555 | 282.8159 | 277.0457 | 282.5961
5000.5979 | 575.096 | 282.7572 | 277.1327 | 282.5635
5001.5979 | 574.76 | 282.831 | 277.3216 | 282.683
5002.5979 | 574.7342 | 282.8402 | 277.4512 | 282.9137
5003.5979 | 574.9243 | 282.7357 | 277.5467 | 282.9732
5004.5979 | 574.8855 | 282.7652 | 277.6291 | 282.9256
5005.5979 | 574.85 | 282.6471 | 277.6849 | 282.8522
5006.5979 | 574.4163 | 282.6436 | 277.6675 | 282.8429
5007.5979 | 574.3895 | 282.6881 | 277.6356 | 282.8474
5008.5979 | 574.3276 | 282.4546 | 277.4577 | 282.749
5009.5979 | 574.4771 | 282.3626 | 277.0004 | 282.6769
5010.5979 | 574.7967 | 282.3178 | 276.7747 | 282.5606
5011.5979 | 574.7573 | 282.2228 | 276.6683 | 282.3204
5012.5979 | 574.5789 | 282.1221 | 276.5674 | 282.121
5013.5979 | 574.2661 | 282.023 | 276.3294 | 282.0185
5014.5979 | 573.9797 | 281.8872 | 276.1872 | 282.0096
5015.5979 | 573.7295 | 281.6699 | 276.1836 | 282.0287
5016.5979 | 573.4294 | 281.5807 | 276.1183 | 281.9916
5017.5979 | 573.1381 | 281.4326 | 276.1318 | 281.9492
5018.5979 | 572.8845 | 281.4058 | 276.1321 | 281.8983
5019.5979 | 572.6295 | 281.3098 | 276.0753 | 281.9014
5020.5979 | 572.378 | 281.1916 | 275.9687 | 281.7338
5021.5979 | 572.2872 | 280.9653 | 275.6739 | 281.6411
5022.5979 | 572.1688 | 280.8831 | 275.4705 | 281.435
5023.5979 | 572.083 | 280.8601 | 275.3971 | 281.4208
5024.5979 | 572.0353 | 280.7363 | 275.3245 | 281.4213
5025.5979 | 572.1946 | 280.6704 | 275.3703 | 281.3878
5026.5979 | 572.2714 | 280.6867 | 275.2279 | 281.233
5027.5979 | 572.0322 | 280.6587 | 275.1528 | 281.0663
5028.5979 | 572.0772 | 280.7217 | 275.1269 | 280.9719
5029.5979 | 571.9336 | 280.6175 | 275.218 | 280.8935
5030.5979 | 571.9387 | 280.4643 | 275.1228 | 280.8027
5031.5979 | 571.7629 | 280.3772 | 275.0434 | 280.7445
5032.5979 | 571.3447 | 280.275 | 274.9178 | 280.6904
5033.5979 | 571.1066 | 280.1013 | 274.5872 | 280.6336
5034.5979 | 570.7996 | 279.8362 | 274.3963 | 280.4917
5035.5979 | 570.5471 | 279.8451 | 274.1552 | 280.2534
5036.5979 | 570.2454 | 279.8516 | 274.0884 | 280.193
5037.5979 | 569.9983 | 279.8433 | 273.9322 | 280.2026
5038.5979 | 569.7763 | 279.8049 | 273.7869 | 280.1111
5039.5979 | 569.3823 | 279.697 | 273.8424 | 279.976
5040.5979 | 568.9537 | 279.7471 | 273.69 | 279.908
5041.5979 | 569.3735 | 279.522 | 273.5963 | 279.7957
5042.5979 | 569.3566 | 279.4985 | 273.4661 | 279.7087
5043.5979 | 569.2752 | 279.3762 | 273.5107 | 279.8688
5044.5979 | 569.006 | 279.4437 | 273.4444 | 279.9336
5045.5979 | 568.467 | 279.554 | 273.4349 | 279.8965
5046.5979 | 568.3104 | 279.6704 | 273.3995 | 279.8732
5047.5979 | 568.2037 | 279.8187 | 273.5085 | 279.7735
5048.5979 | 567.1993 | 279.7672 | 273.6584 | 279.6807
5049.5979 | 566.8847 | 279.8148 | 273.86 | 279.7302
5050.5979 | 566.909 | 279.7355 | 274.0201 | 279.8742
5051.5979 | 567.2697 | 279.6486 | 274.0251 | 279.9091
5052.5979 | 567.2043 | 279.6964 | 274.0088 | 279.9433
5053.5979 | 567.1519 | 279.6775 | 273.8755 | 279.9053
5054.5979 | 567.204 | 279.6493 | 273.6721 | 279.7546
5055.5979 | 567.4781 | 279.6734 | 273.6344 | 279.565
5056.5979 | 567.4782 | 279.7195 | 273.608 | 279.4657
5057.5979 | 567.0946 | 279.7126 | 273.3737 | 279.3987
5058.5979 | 567.0806 | 279.76 | 273.2183 | 279.3196
5059.5979 | 566.5854 | 279.551 | 273.0683 | 279.1722
5060.5979 | 566.5478 | 279.4197 | 273.0892 | 279.0992
5061.5979 | 566.7512 | 279.251 | 273.055 | 279.1144
5062.5979 | 567.1542 | 279.2393 | 272.9322 | 279.1307
5063.5979 | 567.3151 | 279.1727 | 272.7851 | 279.041
5064.5979 | 567.0923 | 278.9685 | 272.7602 | 279.0077
5065.5979 | 566.9274 | 278.8813 | 272.7844 | 279.1131
5066.5979 | 566.282 | 278.9358 | 272.7537 | 279.1461
5067.5979 | 566.0492 | 278.9622 | 272.7128 | 279.1447
5068.5979 | 565.4966 | 279.0484 | 272.5239 | 279.1629
5069.5979 | 565.3264 | 278.9552 | 272.5287 | 279.0569
5070.5979 | 565.2945 | 278.7639 | 272.4959 | 279.0485
5071.5979 | 565.3843 | 278.6069 | 272.6158 | 278.9783
5072.5979 | 565.3224 | 278.4072 | 272.6355 | 278.725
5073.5979 | 565.0621 | 278.4397 | 272.6031 | 278.4954
5074.5979 | 564.678 | 278.3451 | 272.5826 | 278.3527
5075.5979 | 564.2179 | 278.2705 | 272.5494 | 278.1671
5076.5979 | 564.0691 | 278.3016 | 272.4795 | 278.1048
5077.5979 | 564.2507 | 278.3144 | 272.412 | 277.9931
5078.5979 | 564.2958 | 278.2933 | 272.3084 | 277.834
5079.5979 | 564.3269 | 278.1057 | 272.1164 | 277.6723
5080.5979 | 564.3733 | 277.9424 | 272.0617 | 277.5873
5081.5979 | 564.6012 | 277.9508 | 271.9662 | 277.3983
5082.5979 | 564.9119 | 277.9274 | 271.9881 | 277.274
5083.5979 | 565.225 | 277.8728 | 271.7942 | 277.1285
5084.5979 | 565.3873 | 277.844 | 271.7781 | 277.1082
5085.5979 | 565.1534 | 277.8183 | 271.6663 | 277.2272
5086.5979 | 565.2116 | 277.5184 | 271.3782 | 277.279
5087.5979 | 564.8007 | 277.4539 | 271.2223 | 277.2446
5088.5979 | 564.4639 | 277.4477 | 271.3594 | 277.2525
5089.5979 | 564.2184 | 277.4971 | 271.339 | 277.1698
5090.5979 | 564.1207 | 277.5843 | 271.3433 | 277.1476
5091.5979 | 564.1742 | 277.6257 | 271.1119 | 277.1038
5092.5979 | 564.1614 | 277.6331 | 270.9229 | 277.1182
5093.5979 | 564.3689 | 277.5631 | 270.6553 | 277.0428
5094.5979 | 564.2666 | 277.3442 | 270.5605 | 277.1339
5095.5979 | 563.9541 | 277.1763 | 270.6708 | 277.0687
5096.5979 | 563.3196 | 277.104 | 270.6476 | 277.0534
5097.5979 | 563.4204 | 277.0284 | 270.7641 | 277.0437
5098.5979 | 563.2146 | 276.8964 | 270.8268 | 277.0323
5099.5979 | 562.8264 | 276.8979 | 270.6781 | 277.0414
5100.5979 | 562.6357 | 276.716 | 270.5762 | 277.0833
5101.5979 | 562.6452 | 276.5926 | 270.5826 | 277.0463
5102.5979 | 562.5427 | 276.5425 | 270.6031 | 276.9506
5103.5979 | 562.4095 | 276.5805 | 270.7074 | 276.9677
5104.5979 | 562.1591 | 276.5429 | 270.7626 | 276.894
5105.5979 | 561.8427 | 276.4423 | 270.7203 | 276.8068
5106.5979 | 561.7977 | 276.4391 | 270.602 | 276.7189
5107.5979 | 561.8788 | 276.4682 | 270.616 | 276.6848
5108.5979 | 561.9548 | 276.5207 | 270.5315 | 276.5282
5109.5979 | 561.96 | 276.4681 | 270.3637 | 276.3679
5110.5979 | 561.7682 | 276.2147 | 270.1408 | 276.296
5111.5979 | 561.3548 | 276.1276 | 270.0979 | 276.2664
5112.5979 | 561.1883 | 276.123 | 270.061 | 276.1978
5113.5979 | 560.8253 | 275.9894 | 270.0482 | 276.1394
5114.5979 | 560.5552 | 275.9377 | 270.0931 | 275.9639
5115.5979 | 560.3607 | 275.8444 | 270.0459 | 275.8927
5116.5979 | 560.2911 | 275.769 | 269.915 | 275.8131
5117.5979 | 560.2529 | 275.7848 | 269.858 | 275.7314
5118.5979 | 560.3474 | 275.5727 | 269.6035 | 275.7269
5119.5979 | 560.1027 | 275.5705 | 269.522 | 275.6126
5120.5979 | 559.984 | 275.5964 | 269.5535 | 275.5856
5121.5979 | 559.878 | 275.427 | 269.3463 | 275.5522
5122.5979 | 560.0816 | 275.2333 | 269.0963 | 275.1811
5123.5979 | 559.8641 | 275.1105 | 269.2398 | 275.11
5124.5979 | 559.7082 | 274.8774 | 269.0933 | 274.9527
5125.5979 | 559.6763 | 274.8483 | 269.0993 | 274.7161
5126.5979 | 559.6011 | 274.8372 | 269.0039 | 274.6116
5127.5979 | 559.5752 | 274.7252 | 268.9356 | 274.5372
5128.5979 | 559.2107 | 274.7305 | 268.6301 | 274.5239
5129.5979 | 559.2241 | 274.7163 | 268.4938 | 274.5961
5130.5979 | 559.2202 | 274.7891 | 268.2571 | 274.5389
5131.5979 | 559.0375 | 274.6855 | 268.2379 | 274.4303
5132.5979 | 559.0189 | 274.3543 | 268.3384 | 274.3688
5133.5979 | 558.7266 | 274.0945 | 268.2073 | 274.3421
5134.5979 | 558.3344 | 274.0289 | 267.9355 | 274.277
5135.5979 | 557.8878 | 274.1574 | 267.9772 | 274.2889
5136.5979 | 557.6116 | 274.2342 | 267.9236 | 274.2758
5137.5979 | 557.5406 | 274.2689 | 267.7504 | 274.1877
5138.5979 | 556.9992 | 274.0757 | 267.659 | 274.062
5139.5979 | 556.8461 | 273.9127 | 267.7507 | 274.1019
5140.5979 | 556.6518 | 273.7376 | 267.8422 | 274.196
5141.5979 | 556.4983 | 273.5322 | 267.9388 | 274.1888
5142.5979 | 556.4009 | 273.4886 | 268.1583 | 274.1401
5143.5979 | 556.3442 | 273.5415 | 268.2048 | 274.1723
5144.5979 | 556.3069 | 273.6781 | 268.1788 | 274.2189
5145.5979 | 556.0048 | 273.7485 | 268.1397 | 274.1715
5146.5979 | 555.6362 | 273.7166 | 268.0455 | 273.9516
5147.5979 | 555.4314 | 273.5828 | 267.9467 | 273.8681
5148.5979 | 555.2981 | 273.6165 | 267.6638 | 273.6155
5149.5979 | 555.015 | 273.471 | 267.4697 | 273.5514
5150.5979 | 554.7722 | 273.53 | 267.283 | 273.5052
5151.5979 | 554.5307 | 273.3874 | 267.2217 | 273.5077
5152.5979 | 554.2635 | 273.1653 | 267.2038 | 273.3999
5153.5979 | 554.2128 | 273.2265 | 267.2511 | 273.2622
5154.5979 | 554.4572 | 273.2932 | 267.2996 | 273.1594
5155.5979 | 554.4752 | 273.2994 | 267.289 | 273.0703
5156.5979 | 554.7729 | 273.4081 | 267.1729 | 272.9732
5157.5979 | 554.8123 | 273.5139 | 267.0118 | 272.8096
5158.5979 | 554.5975 | 273.5482 | 267.0626 | 272.707
5159.5979 | 554.4988 | 273.4552 | 267.046 | 272.5281
5160.5979 | 554.4787 | 273.42 | 267.1094 | 272.5607
5161.5979 | 554.204 | 273.5345 | 267.1076 | 272.4854
5162.5979 | 553.9144 | 273.6119 | 267.1689 | 272.416
5163.5979 | 553.5152 | 273.6847 | 267.2037 | 272.3153
5164.5979 | 553.495 | 273.7126 | 267.2186 | 272.3418
5165.5979 | 553.6734 | 273.7372 | 267.2051 | 272.3806
5166.5979 | 553.6129 | 273.7122 | 267.1605 | 272.4277
5167.5979 | 553.3425 | 273.6741 | 267.1475 | 272.3986
5168.5979 | 553.3041 | 273.5539 | 267.124 | 272.4556
5169.5979 | 553.2549 | 273.5991 | 267.1674 | 272.4276
5170.5979 | 552.9738 | 273.7181 | 267.2074 | 272.3324
5171.5979 | 552.6185 | 273.7362 | 267.1653 | 272.1961
5172.5979 | 552.5291 | 273.7399 | 267.1254 | 271.9622
5173.5979 | 552.3297 | 273.7312 | 267.0744 | 271.8248
5174.5979 | 552.0845 | 273.6266 | 267.0432 | 271.7746
5175.5979 | 551.96 | 273.5047 | 267.1878 | 271.8741
5176.5979 | 551.8859 | 273.5466 | 267.211 | 271.9112
5177.5979 | 551.741 | 273.606 | 267.2298 | 271.9272
5178.5979 | 551.9696 | 273.5931 | 267.3062 | 271.8287
5179.5979 | 552.0741 | 273.6042 | 267.3644 | 271.8506
5180.5979 | 551.8107 | 273.4639 | 267.2608 | 271.8359
5181.5979 | 551.0854 | 273.3928 | 267.2205 | 271.6668
5182.5979 | 551.0237 | 273.3599 | 267.1046 | 271.576
5183.5979 | 551.0002 | 273.3515 | 266.9833 | 271.4883
5184.5979 | 550.8673 | 273.3254 | 266.8148 | 271.3835
5185.5979 | 550.8143 | 273.1949 | 266.7145 | 271.3295
5186.5979 | 550.6594 | 273.1697 | 266.638 | 271.3389
5187.5979 | 550.3279 | 273.1885 | 266.5893 | 271.3909
5188.5979 | 550.3006 | 273.1509 | 266.5944 | 271.3837
5189.5979 | 550.3025 | 273.2041 | 266.5423 | 271.4149
5190.5979 | 550.0476 | 273.2543 | 266.5335 | 271.3192
5191.5979 | 550.1796 | 273.3084 | 266.6695 | 271.4101
5192.5979 | 550.7805 | 273.36 | 266.7093 | 271.3594
5193.5979 | 551.1208 | 273.3801 | 266.6759 | 271.2403
5194.5979 | 551.6587 | 273.4072 | 266.8747 | 271.117
5195.5979 | 551.7778 | 273.3964 | 266.8599 | 271.0662
5196.5979 | 551.7805 | 273.2901 | 266.7733 | 270.9872
5197.5979 | 551.4627 | 273.1 | 266.6184 | 270.8064
5198.5979 | 550.9482 | 272.8768 | 266.5339 | 270.6227
5199.5979 | 550.6306 | 272.7116 | 266.5696 | 270.5486
5200.5979 | 550.5005 | 272.7536 | 266.4824 | 270.559
5201.5979 | 550.0387 | 272.7409 | 266.4497 | 270.5954
5202.5979 | 549.8183 | 272.7567 | 266.4714 | 270.4905
5203.5979 | 549.5585 | 272.7978 | 266.3955 | 270.4082
5204.5979 | 549.5045 | 272.5942 | 266.3865 | 270.3758
5205.5979 | 549.4349 | 272.398 | 266.1738 | 270.1882
5206.5979 | 549.37 | 272.1369 | 266.0046 | 270.0064
5207.5979 | 549.2137 | 271.9607 | 265.9996 | 269.841
5208.5979 | 548.9969 | 271.6851 | 265.957 | 269.7567
5209.5979 | 548.8121 | 271.0182 | 265.6857 | 269.8554
5210.5979 | 548.4179 | 270.8759 | 265.3636 | 269.7888
5211.5979 | 548.1296 | 270.7101 | 265.1208 | 269.7338
5212.5979 | 547.8871 | 270.5004 | 264.907 | 269.686
5213.5979 | 547.3652 | 270.3761 | 264.7991 | 269.7101
5214.5979 | 546.7634 | 270.1303 | 264.7524 | 269.7103
5215.5979 | 546.5428 | 270.0428 | 264.6886 | 269.7438
5216.5979 | 546.5063 | 270.104 | 264.676 | 269.7738
5217.5979 | 546.4996 | 270.1482 | 264.5849 | 269.7788
5218.5979 | 546.6599 | 270.1167 | 264.4866 | 269.7591
5219.5979 | 546.55 | 270.2243 | 264.3234 | 269.6385
5220.5979 | 546.5866 | 270.2239 | 264.155 | 269.4083
5221.5979 | 546.8472 | 270.3394 | 263.9207 | 269.3024
5222.5979 | 546.8585 | 270.3928 | 263.8933 | 269.1908
5223.5979 | 546.6197 | 270.445 | 263.7557 | 269.0932
5224.5979 | 546.2393 | 270.505 | 263.6441 | 269.0584
5225.5979 | 545.8728 | 270.3061 | 263.5104 | 268.9875
5226.5979 | 545.3882 | 270.0702 | 263.3006 | 268.9632
5227.5979 | 545.1631 | 269.9836 | 263.196 | 268.8839
5228.5979 | 544.6611 | 270.0023 | 263.2477 | 268.8815
5229.5979 | 544.3026 | 269.949 | 263.2947 | 268.8751
5230.5979 | 544.3667 | 269.8016 | 263.3061 | 268.8497
5231.5979 | 544.3298 | 269.8474 | 263.3124 | 268.7548
5232.5979 | 543.9776 | 269.8088 | 263.4097 | 268.7544
5233.5979 | 543.912 | 269.7116 | 263.3725 | 268.7815
5234.5979 | 543.5978 | 269.7163 | 263.3257 | 268.7341
5235.5979 | 543.0944 | 269.7313 | 263.3659 | 268.7247
5236.5979 | 542.6808 | 269.7401 | 263.2944 | 268.657
5237.5979 | 542.2949 | 269.6616 | 263.3213 | 268.6964
5238.5979 | 542.3184 | 269.5925 | 263.2234 | 268.6906
5239.5979 | 541.9579 | 269.5361 | 262.9907 | 268.6564
5240.5979 | 541.5768 | 269.4061 | 263.0229 | 268.6753
5241.5979 | 541.4835 | 269.2852 | 263.1335 | 268.6819
5242.5979 | 541.488 | 269.3308 | 263.0246 | 268.6998
5243.5979 | 541.1896 | 269.1212 | 263.08 | 268.8017
5244.5979 | 541.101 | 269.0442 | 263.0428 | 268.8448
5245.5979 | 540.8201 | 269.1273 | 263.033 | 268.842
5246.5979 | 540.6863 | 268.955 | 262.9836 | 268.7618
5247.5979 | 540.6614 | 268.736 | 263.0278 | 268.8047
5248.5979 | 540.6138 | 268.5846 | 263.0719 | 268.7952
5249.5979 | 540.5492 | 268.4558 | 263.1931 | 268.7209
5250.5979 | 540.4376 | 268.3605 | 263.3335 | 268.6381
5251.5979 | 540.5242 | 268.3095 | 263.3823 | 268.6714
5252.5979 | 540.6445 | 268.1821 | 263.3098 | 268.6244
5253.5979 | 540.6083 | 268.0262 | 263.3278 | 268.4811
5254.5979 | 540.4277 | 268.0412 | 263.3722 | 268.4284
5255.5979 | 540.4086 | 267.8875 | 263.4563 | 268.3922
5256.5979 | 540.273 | 267.7917 | 263.5013 | 268.3974
5257.5979 | 539.7319 | 267.8187 | 263.4513 | 268.2999
5258.5979 | 539.3461 | 268.038 | 263.3956 | 268.1673
5259.5979 | 539.0474 | 268.219 | 263.4526 | 268.1048
5260.5979 | 538.8518 | 268.3329 | 263.481 | 268.057
5261.5979 | 538.8569 | 268.3899 | 263.3446 | 268.0498
5262.5979 | 538.6956 | 268.4321 | 263.1691 | 268.0748
5263.5979 | 538.2266 | 268.4781 | 263.1891 | 268.092
5264.5979 | 538.1333 | 268.593 | 263.2821 | 268.0789
5265.5979 | 537.7567 | 268.7067 | 263.4075 | 268.1509
5266.5979 | 537.5028 | 268.822 | 263.5242 | 268.2007
5267.5979 | 537.3244 | 268.8976 | 263.6039 | 268.1616
5268.5979 | 537.021 | 268.9401 | 263.6551 | 268.2055
5269.5979 | 536.7887 | 269.0413 | 263.5946 | 268.1504
5270.5979 | 536.7923 | 268.9767 | 263.5573 | 268.0641
5271.5979 | 537.0567 | 269.0793 | 263.5459 | 267.9681
5272.5979 | 537.1862 | 269.0917 | 263.4404 | 267.8316
5273.5979 | 537.306 | 269.146 | 263.3071 | 267.7644
5274.5979 | 537.2382 | 269.1223 | 263.205 | 267.6303
5275.5979 | 537.3771 | 268.994 | 263.0451 | 267.6022
5276.5979 | 537.4961 | 268.9782 | 263.0383 | 267.4776
5277.5979 | 537.3396 | 268.9341 | 262.9335 | 267.3062
5278.5979 | 537.3298 | 268.9047 | 262.7258 | 267.2047
5279.5979 | 537.5289 | 268.888 | 262.7145 | 267.0684
5280.5979 | 537.6597 | 268.8553 | 262.6094 | 267.0454
5281.5979 | 537.6796 | 268.8662 | 262.6546 | 267.0216
5282.5979 | 537.7112 | 268.742 | 262.4529 | 266.8881
5283.5979 | 537.3621 | 268.6723 | 262.1835 | 266.8065
5284.5979 | 537.0896 | 268.3788 | 261.7107 | 266.7055
5285.5979 | 536.7418 | 268.1188 | 261.554 | 266.5051
5286.5979 | 537.1705 | 268.034 | 261.5057 | 266.5004
5287.5979 | 537.3831 | 267.9433 | 261.4234 | 266.362
5288.5979 | 537.3735 | 267.8707 | 261.3622 | 266.2134
5289.5979 | 537.2838 | 267.7423 | 261.3569 | 266.0397
5290.5979 | 537.0077 | 267.6624 | 261.1813 | 265.8984
5291.5979 | 536.7679 | 267.5866 | 261.1415 | 265.8449
5292.5979 | 536.5101 | 267.5215 | 261.1138 | 265.7631
5293.5979 | 536.2337 | 267.4869 | 261.106 | 265.5559
5294.5979 | 535.8589 | 267.4305 | 261.1385 | 265.4274
5295.5979 | 535.4558 | 267.4852 | 260.9651 | 265.4945
5296.5979 | 535.3862 | 267.4103 | 260.756 | 265.4647
5297.5979 | 535.3679 | 267.1371 | 260.8215 | 265.551
5298.5979 | 535.2202 | 266.9694 | 260.8091 | 265.5627
5299.5979 | 534.8727 | 266.8216 | 260.7021 | 265.5286
5300.5979 | 534.754 | 266.8099 | 260.616 | 265.4344
5301.5979 | 534.8027 | 266.8256 | 260.4971 | 265.4637
5302.5979 | 534.7566 | 266.884 | 260.4536 | 265.3296
5303.5979 | 535.0042 | 266.8913 | 260.4541 | 265.2414
5304.5979 | 535.3965 | 266.9598 | 260.4866 | 265.2421
5305.5979 | 535.4979 | 266.9754 | 260.3907 | 265.2018
5306.5979 | 535.7409 | 267.0254 | 260.3878 | 265.1115
5307.5979 | 536.4243 | 267.0298 | 260.3822 | 265.094
5308.5979 | 536.8081 | 266.9841 | 260.1629 | 265.0259
5309.5979 | 536.7096 | 266.9284 | 259.9602 | 264.9997
5310.5979 | 536.3084 | 266.8974 | 259.8186 | 264.9326
5311.5979 | 536.0855 | 266.8818 | 259.6946 | 264.7696
5312.5979 | 535.9283 | 266.906 | 259.7074 | 264.7223
5313.5979 | 535.5234 | 266.9191 | 259.5993 | 264.6664
5314.5979 | 535.1413 | 266.9133 | 259.5915 | 264.593
5315.5979 | 534.922 | 266.908 | 259.7556 | 264.5636
5316.5979 | 534.7934 | 266.7724 | 259.6342 | 264.5834
5317.5979 | 534.7286 | 266.5606 | 259.6172 | 264.4855
5318.5979 | 534.6102 | 266.3466 | 259.3867 | 264.4457
5319.5979 | 534.5013 | 266.1714 | 259.2105 | 264.5298
5320.5979 | 534.2802 | 265.8186 | 259.0494 | 264.456
5321.5979 | 534.1083 | 265.6682 | 258.8466 | 264.2783
5322.5979 | 533.8519 | 265.4279 | 258.8073 | 264.1819
5323.5979 | 533.4925 | 265.1646 | 258.6771 | 263.9596
5324.5979 | 533.5203 | 265.19 | 258.5726 | 263.8155
5325.5979 | 533.3748 | 265.2674 | 258.4278 | 263.8603
5326.5979 | 533.4333 | 265.2405 | 258.3296 | 263.8879
5327.5979 | 533.2811 | 265.2858 | 258.2695 | 263.8436
5328.5979 | 533.3352 | 265.2996 | 258.2407 | 263.8317
5329.5979 | 533.0474 | 265.3157 | 258.1024 | 263.79
5330.5979 | 532.9553 | 265.403 | 257.8438 | 263.8508
5331.5979 | 532.6153 | 265.4296 | 257.7815 | 263.7536
5332.5979 | 532.2193 | 265.4653 | 257.8676 | 263.7312
5333.5979 | 532.1783 | 265.4061 | 257.9225 | 263.7555
5334.5979 | 532.1783 | 265.3274 | 257.8975 | 263.6937
5335.5979 | 532.1706 | 265.2586 | 257.8722 | 263.6416
5336.5979 | 532.1138 | 265.2705 | 257.8308 | 263.6092
5337.5979 | 532.0036 | 265.0971 | 257.9175 | 263.5898
5338.5979 | 531.8986 | 264.7262 | 257.7406 | 263.525
5339.5979 | 531.6613 | 264.5447 | 257.7056 | 263.4423
5340.5979 | 530.9817 | 264.5419 | 257.783 | 263.4162
5341.5979 | 530.8217 | 264.6441 | 257.9547 | 263.4191
5342.5979 | 530.6562 | 264.5887 | 258.0199 | 263.4625
5343.5979 | 530.7988 | 264.4997 | 258.162 | 263.4987
5344.5979 | 531.1673 | 264.3751 | 258.3346 | 263.4372
5345.5979 | 531.0941 | 264.287 | 258.3687 | 263.4456
5346.5979 | 530.9948 | 264.379 | 258.46 | 263.4539
5347.5979 | 530.591 | 264.4777 | 258.4045 | 263.5088
5348.5979 | 530.4198 | 264.558 | 258.3803 | 263.485
5349.5979 | 530.6674 | 264.6255 | 258.1952 | 263.4289
5350.5979 | 530.8933 | 264.673 | 257.9764 | 263.3923
5351.5979 | 530.7274 | 264.7446 | 257.9084 | 263.4077
5352.5979 | 530.6182 | 264.7178 | 257.7584 | 263.4035
5353.5979 | 530.5497 | 264.6291 | 257.4786 | 263.3021
5354.5979 | 530.6604 | 264.4434 | 257.3317 | 263.2324
5355.5979 | 530.3432 | 264.2981 | 257.3318 | 263.2115
5356.5979 | 530.3774 | 264.1185 | 257.3492 | 263.1543
5357.5979 | 530.5288 | 264.0332 | 257.4021 | 262.9353
5358.5979 | 530.701 | 264.1116 | 257.444 | 262.8122
5359.5979 | 530.8157 | 264.1422 | 257.4104 | 262.7494
5360.5979 | 530.4629 | 264.177 | 257.3165 | 262.6193
5361.5979 | 530.4184 | 264.1141 | 257.0437 | 262.5262
5362.5979 | 530.2801 | 264.0679 | 256.8671 | 262.3462
5363.5979 | 530.386 | 263.7722 | 256.7866 | 262.2227
5364.5979 | 530.1438 | 263.5804 | 256.6303 | 262.0032
5365.5979 | 529.9797 | 263.4347 | 256.3646 | 261.8609
5366.5979 | 529.7889 | 263.3087 | 256.2667 | 261.6649
5367.5979 | 529.4305 | 263.3527 | 256.3354 | 261.5094
5368.5979 | 529.177 | 263.38 | 256.3102 | 261.2974
5369.5979 | 528.946 | 263.4064 | 256.0775 | 261.011
5370.5979 | 528.7819 | 263.3304 | 256.0373 | 260.8312
5371.5979 | 528.6854 | 263.3754 | 255.9042 | 260.7927
5372.5979 | 528.6146 | 263.3591 | 255.7522 | 260.8756
5373.5979 | 528.5665 | 263.3176 | 255.6483 | 260.6979
5374.5979 | 528.4516 | 263.3533 | 255.6092 | 260.6059
5375.5979 | 528.1502 | 263.4373 | 255.4286 | 260.6048
5376.5979 | 527.8175 | 263.3932 | 255.4088 | 260.6022
5377.5979 | 527.6862 | 263.4617 | 255.5543 | 260.5786
5378.5979 | 527.6734 | 263.4994 | 255.5729 | 260.5853
5379.5979 | 527.9811 | 263.3905 | 255.725 | 260.6021
5380.5979 | 527.9242 | 263.2656 | 255.7996 | 260.6187
5381.5979 | 527.7268 | 263.343 | 255.7056 | 260.4083
5382.5979 | 527.4724 | 263.4286 | 255.7718 | 260.4887
5383.5979 | 527.2068 | 263.4753 | 255.8275 | 260.5106
5384.5979 | 527.0342 | 263.297 | 255.7699 | 260.4713
5385.5979 | 527.0076 | 263.1189 | 255.8123 | 260.3646
5386.5979 | 526.7716 | 262.8064 | 255.8953 | 260.3006
5387.5979 | 526.6849 | 262.4813 | 255.9433 | 260.3649
5388.5979 | 526.5289 | 262.4268 | 255.9221 | 260.4738
5389.5979 | 526.319 | 262.3034 | 255.8881 | 260.5305
5390.5979 | 526.1662 | 262.1745 | 255.9289 | 260.5948
5391.5979 | 525.8895 | 262.0662 | 255.9078 | 260.4493
5392.5979 | 525.6964 | 262.0451 | 255.9389 | 260.4039
5393.5979 | 525.5628 | 261.9378 | 255.8089 | 260.4203
5394.5979 | 525.4203 | 261.6469 | 255.6554 | 260.3168
5395.5979 | 525.2966 | 261.3376 | 255.5496 | 260.3051
5396.5979 | 525.0968 | 261.1253 | 255.4717 | 260.2741
5397.5979 | 524.6852 | 261.1048 | 255.2732 | 260.1896
5398.5979 | 523.9306 | 260.8597 | 255.1098 | 260.1496
5399.5979 | 523.3808 | 260.77 | 254.962 | 260.0816
5400.5979 | 523.2293 | 260.7206 | 254.9451 | 260.1018
5401.5979 | 522.9202 | 260.7744 | 254.8813 | 260.1593
5402.5979 | 522.9216 | 260.6894 | 254.8462 | 260.021
5403.5979 | 523.1186 | 260.5878 | 254.716 | 259.9364
5404.5979 | 522.9898 | 260.4439 | 254.763 | 259.862
5405.5979 | 522.8148 | 260.4857 | 254.7033 | 259.7899
5406.5979 | 522.6533 | 260.4342 | 254.4719 | 259.7941
5407.5979 | 522.2664 | 260.5299 | 254.3782 | 259.8198
5408.5979 | 521.8153 | 260.6256 | 254.4304 | 259.8883
5409.5979 | 521.4768 | 260.6728 | 254.4998 | 259.7208
5410.5979 | 521.2563 | 260.6931 | 254.6692 | 259.5374
5411.5979 | 521.0593 | 260.8081 | 254.6694 | 259.4147
5412.5979 | 521.0084 | 260.9565 | 254.579 | 259.3221
5413.5979 | 520.8309 | 260.8955 | 254.5108 | 259.3528
5414.5979 | 520.5522 | 261.0125 | 254.625 | 259.3402
5415.5979 | 520.4843 | 261.086 | 254.6161 | 259.2973
5416.5979 | 520.6456 | 260.896 | 254.479 | 259.3274
5417.5979 | 520.5287 | 260.7623 | 254.2663 | 259.2863
5418.5979 | 520.2196 | 260.465 | 254.0967 | 259.2014
5419.5979 | 520.1306 | 260.4664 | 253.9948 | 259.0719
5420.5979 | 520.2143 | 260.1025 | 253.8993 | 258.9993
5421.5979 | 520.3054 | 259.9167 | 253.9133 | 259.0107
5422.5979 | 520.2797 | 259.7916 | 253.8625 | 258.9287
5423.5979 | 520.1293 | 259.7192 | 253.9065 | 258.6816
5424.5979 | 520.1742 | 259.5825 | 253.9359 | 258.5268
5425.5979 | 520.413 | 259.4854 | 253.8222 | 258.3097
5426.5979 | 520.576 | 259.3289 | 253.7251 | 258.2019
5427.5979 | 520.736 | 259.3553 | 253.5681 | 258.0944
5428.5979 | 520.968 | 259.3666 | 253.4613 | 258.1067
5429.5979 | 521.1917 | 259.419 | 253.3222 | 258.0681
5430.5979 | 521.3434 | 259.367 | 253.179 | 258.1416
5431.5979 | 521.3606 | 259.4003 | 253.0667 | 258.1107
5432.5979 | 521.2739 | 259.363 | 253.0392 | 257.9969
5433.5979 | 520.851 | 259.3144 | 253.1104 | 257.9294
5434.5979 | 520.5332 | 259.2043 | 253.2388 | 257.8261
5435.5979 | 520.4172 | 259.2766 | 253.4089 | 257.8536
5436.5979 | 520.1586 | 259.4122 | 253.3925 | 257.9157
5437.5979 | 519.9205 | 259.3967 | 253.2549 | 257.923
5438.5979 | 519.44 | 259.3095 | 253.3089 | 257.9165
5439.5979 | 519.478 | 259.2382 | 253.0995 | 257.7576
5440.5979 | 519.446 | 259.2893 | 252.8903 | 257.4599
5441.5979 | 519.3501 | 259.3634 | 252.5838 | 257.3508
5442.5979 | 519.5212 | 259.3759 | 252.3049 | 257.3547
5443.5979 | 519.2578 | 259.3433 | 251.9322 | 257.297
5444.5979 | 519.1399 | 259.1013 | 252.0658 | 257.3227
5445.5979 | 518.703 | 259.0173 | 252.1145 | 257.4151
5446.5979 | 518.3656 | 258.8599 | 252.105 | 257.3844
5447.5979 | 518.294 | 258.8058 | 252.1255 | 257.4333
5448.5979 | 518.2953 | 258.8307 | 252.3243 | 257.3289
5449.5979 | 518.2258 | 258.8614 | 252.5151 | 257.2287
5450.5979 | 517.4774 | 259.0105 | 252.5081 | 257.2161
5451.5979 | 517.0067 | 258.9051 | 252.5432 | 257.2436
5452.5979 | 516.5938 | 258.8258 | 252.6362 | 257.2155
5453.5979 | 516.6131 | 258.7577 | 252.6358 | 257.1908
5454.5979 | 516.6688 | 258.8024 | 252.5831 | 257.2094
5455.5979 | 516.6481 | 258.9406 | 252.5632 | 257.2607
5456.5979 | 516.3278 | 258.9786 | 252.4778 | 257.1629
5457.5979 | 516.0367 | 259.0208 | 252.4405 | 257.063
5458.5979 | 515.9399 | 259.1124 | 252.4892 | 257.005
5459.5979 | 515.6599 | 259.1934 | 252.3556 | 256.847
5460.5979 | 515.3852 | 259.1286 | 252.3279 | 256.7781
5461.5979 | 515.3679 | 259.1342 | 252.3571 | 256.7756
5462.5979 | 515.1186 | 259.0136 | 252.4845 | 256.7495
5463.5979 | 514.8329 | 258.7871 | 252.4816 | 256.7674
5464.5979 | 514.4489 | 258.5815 | 252.4218 | 256.7047
5465.5979 | 513.8598 | 258.5556 | 252.476 | 256.6446
5466.5979 | 513.6703 | 258.4974 | 252.5526 | 256.7754
5467.5979 | 513.4772 | 258.4246 | 252.6623 | 256.7884
5468.5979 | 513.0938 | 258.3555 | 252.8134 | 256.8773
5469.5979 | 512.9414 | 258.2742 | 252.8925 | 256.9337
5470.5979 | 512.63 | 258.3703 | 253.0175 | 256.901
5471.5979 | 512.2959 | 258.4198 | 252.9775 | 256.9574
5472.5979 | 512.2255 | 258.3598 | 252.8143 | 256.6725
5473.5979 | 512.2895 | 258.167 | 252.803 | 256.4631
5474.5979 | 512.3854 | 258.0999 | 252.7185 | 256.2874
5475.5979 | 512.2737 | 258.1062 | 252.2946 | 256.1656
5476.5979 | 512.2398 | 258.1399 | 252.1135 | 256.0621
5477.5979 | 512.0711 | 258.0512 | 252.0691 | 256.0502
5478.5979 | 511.9539 | 257.9569 | 251.9943 | 256.1582
5479.5979 | 511.9821 | 257.9348 | 251.8053 | 256.1373
5480.5979 | 511.9982 | 257.8819 | 251.678 | 256.0736
5481.5979 | 512.1049 | 257.8681 | 251.529 | 255.9269
5482.5979 | 511.9996 | 257.8213 | 251.4744 | 255.8029
5483.5979 | 512.1476 | 257.7451 | 251.4278 | 255.7667
5484.5979 | 512.5006 | 257.557 | 251.1108 | 255.657
5485.5979 | 512.7524 | 257.2675 | 250.8346 | 255.6076
5486.5979 | 512.7579 | 257.082 | 250.6915 | 255.5665
5487.5979 | 512.4802 | 256.9701 | 250.7171 | 255.2759
5488.5979 | 512.5667 | 256.8598 | 250.7239 | 255.2647
5489.5979 | 512.6545 | 256.7173 | 250.7679 | 255.346
5490.5979 | 512.4565 | 256.8709 | 250.7205 | 255.3109
5491.5979 | 512.334 | 256.9547 | 250.7553 | 255.1886
5492.5979 | 512.1589 | 256.9929 | 250.8107 | 255.1575
5493.5979 | 512.1688 | 257.0158 | 250.8405 | 255.2209
5494.5979 | 511.8154 | 257.0462 | 250.8853 | 255.2537
5495.5979 | 511.4478 | 257.12 | 250.8917 | 255.3215
5496.5979 | 511.1354 | 257.1361 | 250.9232 | 255.3599
5497.5979 | 510.8098 | 257.2217 | 250.9497 | 255.2705
5498.5979 | 510.3971 | 257.2841 | 251.0438 | 255.2899
5499.5979 | 510.6499 | 257.333 | 251.0104 | 255.2864
5500.5979 | 510.8774 | 257.3069 | 251.066 | 255.172
5501.5979 | 511.0114 | 257.2753 | 251.0057 | 255.2631
5502.5979 | 510.9294 | 257.2239 | 250.9832 | 255.2879
5503.5979 | 510.8475 | 257.1788 | 250.8663 | 255.0936
5504.5979 | 510.6276 | 257.2167 | 250.7876 | 254.8718
5505.5979 | 510.6118 | 257.2328 | 250.6682 | 254.7914
5506.5979 | 510.4541 | 257.1611 | 250.54 | 254.7559
5507.5979 | 510.1987 | 257.1617 | 250.4506 | 254.7757
5508.5979 | 509.8736 | 257.1466 | 250.3951 | 254.92
5509.5979 | 509.5792 | 256.8988 | 250.4998 | 254.9327
5510.5979 | 509.4213 | 256.6611 | 250.5528 | 254.8712
5511.5979 | 509.4276 | 256.5909 | 250.6933 | 254.8066
5512.5979 | 508.9804 | 256.5211 | 250.649 | 254.7233
5513.5979 | 508.5124 | 256.314 | 250.6147 | 254.7087
5514.5979 | 508.1325 | 256.0245 | 250.5733 | 254.7664
5515.5979 | 507.9426 | 255.9124 | 250.605 | 254.6424
5516.5979 | 507.59 | 255.7206 | 250.6938 | 254.6776
5517.5979 | 507.4714 | 255.6346 | 250.4647 | 254.5929
5518.5979 | 507.6217 | 255.4601 | 250.166 | 254.3803
5519.5979 | 507.5166 | 255.5222 | 250.1171 | 254.498
5520.5979 | 507.5037 | 255.3558 | 250.1117 | 254.5572
5521.5979 | 507.3738 | 255.2433 | 250.0711 | 254.5492
5522.5979 | 507.2005 | 255.2148 | 249.965 | 254.5423
5523.5979 | 507.3503 | 255.2278 | 249.8995 | 254.4088
5524.5979 | 507.5348 | 255.0756 | 249.8573 | 254.3088
5525.5979 | 507.5865 | 254.9322 | 249.8598 | 254.3356
5526.5979 | 507.5036 | 254.7978 | 249.7318 | 254.1437
5527.5979 | 507.4592 | 254.7664 | 249.6587 | 254.062
5528.5979 | 507.2338 | 254.8189 | 249.644 | 254.0195
5529.5979 | 506.9491 | 254.8737 | 249.6675 | 254.0003
5530.5979 | 506.8393 | 254.9092 | 249.7224 | 253.9549
5531.5979 | 506.9602 | 254.9686 | 249.6673 | 253.9128
5532.5979 | 507.0631 | 255.0413 | 249.5387 | 253.8207
5533.5979 | 507.0701 | 255.1251 | 249.5157 | 253.7958
5534.5979 | 507.2454 | 255.2329 | 249.4479 | 253.7056
5535.5979 | 507.3256 | 255.3483 | 249.409 | 253.6119
5536.5979 | 507.3074 | 255.4068 | 249.1575 | 253.563
5537.5979 | 507.3093 | 255.5012 | 249.2259 | 253.4614
5538.5979 | 506.9253 | 255.6281 | 249.3402 | 253.474
5539.5979 | 506.8795 | 255.6842 | 249.2349 | 253.488
5540.5979 | 506.9335 | 255.7926 | 249.155 | 253.3181
5541.5979 | 506.8643 | 255.8368 | 249.0395 | 253.217
5542.5979 | 506.9441 | 255.7091 | 248.8974 | 253.0798
5543.5979 | 506.9413 | 255.6544 | 248.9103 | 253.1018
5544.5979 | 506.5961 | 255.416 | 248.9045 | 253.0719
5545.5979 | 506.3849 | 255.3928 | 248.9302 | 253.0962
5546.5979 | 506.1084 | 255.4164 | 248.7347 | 253.0736
5547.5979 | 506.0844 | 255.4442 | 248.4785 | 253.068
5548.5979 | 505.9788 | 255.2249 | 248.3871 | 252.9688
5549.5979 | 505.9459 | 255.0036 | 248.4883 | 252.884
5550.5979 | 505.8457 | 254.7941 | 248.5828 | 252.9032
5551.5979 | 505.5456 | 254.6688 | 248.6672 | 252.8543
5552.5979 | 505.4247 | 254.5297 | 248.7929 | 252.8316
5553.5979 | 505.5003 | 254.247 | 248.7078 | 252.7627
5554.5979 | 505.6805 | 254.0923 | 248.7409 | 252.7756
5555.5979 | 505.9327 | 254.0058 | 248.5801 | 252.7144
5556.5979 | 505.8916 | 254.0487 | 248.3391 | 252.7334
5557.5979 | 505.7599 | 253.9946 | 248.4388 | 252.6717
5558.5979 | 505.8138 | 254.1004 | 248.5939 | 252.5733
5559.5979 | 505.337 | 254.2129 | 248.6715 | 252.5667
5560.5979 | 505.0107 | 254.214 | 248.4847 | 252.4385
5561.5979 | 505.1053 | 254.216 | 248.1692 | 252.4756
5562.5979 | 504.8854 | 254.0143 | 248.0526 | 252.4098
5563.5979 | 504.7499 | 253.9611 | 247.9101 | 252.3704
5564.5979 | 504.5082 | 254.0469 | 247.8498 | 252.4569
5565.5979 | 504.2397 | 254.1608 | 247.6166 | 252.4367
5566.5979 | 503.9228 | 254.1431 | 247.466 | 252.4272
5567.5979 | 503.5645 | 253.969 | 247.413 | 252.4439
5568.5979 | 503.581 | 253.8773 | 247.496 | 252.3763
5569.5979 | 503.9274 | 253.7222 | 247.436 | 252.3848
5570.5979 | 504.0354 | 253.5824 | 247.3877 | 252.3422
5571.5979 | 503.6691 | 253.3633 | 247.3841 | 252.2419
5572.5979 | 503.5199 | 253.1702 | 247.5139 | 252.3283
5573.5979 | 503.7832 | 252.9868 | 247.5699 | 252.3791
5574.5979 | 503.8254 | 252.8818 | 247.7157 | 252.1998
5575.5979 | 503.7267 | 252.7118 | 247.688 | 252.0179
5576.5979 | 503.8463 | 252.7725 | 247.6237 | 252.0048
5577.5979 | 504.016 | 252.7238 | 247.5315 | 252.0498
5578.5979 | 504.1288 | 252.8033 | 247.3579 | 252.0099
5579.5979 | 504.0071 | 252.916 | 247.1125 | 251.9632
5580.5979 | 504.0184 | 252.9844 | 246.8688 | 251.8677
5581.5979 | 504.0338 | 253.0583 | 246.7296 | 251.7568
5582.5979 | 503.9794 | 253.0444 | 246.4804 | 251.67
5583.5979 | 503.8012 | 253.0421 | 246.0617 | 251.7001
5584.5979 | 503.8241 | 252.7711 | 245.7786 | 251.7594
5585.5979 | 503.9773 | 252.5833 | 245.7476 | 251.7529
5586.5979 | 503.7662 | 252.474 | 245.6286 | 251.6986
5587.5979 | 503.4836 | 252.4448 | 245.6096 | 251.6736
5588.5979 | 503.1882 | 252.428 | 245.6167 | 251.6769
5589.5979 | 502.8806 | 252.4457 | 245.5443 | 251.4621
5590.5979 | 502.7177 | 252.4298 | 245.5704 | 251.3191
5591.5979 | 502.4496 | 252.2756 | 245.6598 | 251.3694
5592.5979 | 502.3292 | 252.1907 | 245.9504 | 251.5105
5593.5979 | 502.2151 | 252.1306 | 245.9564 | 251.5264
5594.5979 | 502.1298 | 252.0871 | 245.9853 | 251.4964
5595.5979 | 502.1252 | 252.1099 | 245.9568 | 251.4728
5596.5979 | 501.8323 | 251.8445 | 245.8048 | 251.4295
5597.5979 | 501.1016 | 251.7212 | 245.8481 | 251.3866
5598.5979 | 500.3948 | 251.6747 | 245.8681 | 251.269
5599.5979 | 500.1148 | 251.7817 | 245.9324 | 251.1364
5600.5979 | 500.0154 | 251.8895 | 245.8422 | 251.0728
5601.5979 | 500.0447 | 251.9778 | 245.725 | 251.0881
5602.5979 | 499.8545 | 251.9677 | 245.6652 | 251.0632
5603.5979 | 499.6052 | 251.9663 | 245.6892 | 250.791
5604.5979 | 499.4474 | 251.8896 | 245.6863 | 250.5913
5605.5979 | 499.2704 | 251.6294 | 245.5857 | 250.4174
5606.5979 | 499.2497 | 251.3982 | 245.5663 | 250.0546
5607.5979 | 499.3661 | 251.3478 | 245.5754 | 249.8362
5608.5979 | 499.3536 | 251.2065 | 245.6363 | 249.8048
5609.5979 | 499.1806 | 251.138 | 245.7063 | 249.7191
5610.5979 | 499.1146 | 251.0533 | 245.5697 | 249.6144
5611.5979 | 498.7304 | 250.9422 | 245.3547 | 249.5223
5612.5979 | 498.3154 | 250.8162 | 245.1373 | 249.4404
5613.5979 | 498.4847 | 250.7844 | 245.0842 | 249.4829
5614.5979 | 498.5591 | 250.5542 | 245.0428 | 249.4555
5615.5979 | 498.6064 | 250.479 | 245.0068 | 249.4377
5616.5979 | 498.5488 | 250.3937 | 244.9934 | 249.3467
5617.5979 | 498.0974 | 250.4425 | 244.9349 | 249.2988
5618.5979 | 498.2645 | 250.554 | 244.7247 | 249.3471
5619.5979 | 498.0892 | 250.6986 | 244.7406 | 249.2375
5620.5979 | 498.0031 | 250.6927 | 244.6672 | 249.2095
5621.5979 | 498.1195 | 250.6023 | 244.6159 | 249.2432
5622.5979 | 498.1537 | 250.4483 | 244.6598 | 249.2831
5623.5979 | 498.1525 | 250.2416 | 244.6146 | 249.2501
5624.5979 | 498.0516 | 250.245 | 244.6105 | 249.1656
5625.5979 | 498.0009 | 250.2175 | 244.5718 | 249.0542
5626.5979 | 497.8944 | 250.0391 | 244.6335 | 249.025
5627.5979 | 497.6469 | 250.0484 | 244.6461 | 248.8469
5628.5979 | 497.4573 | 249.9847 | 244.4882 | 248.6634
5629.5979 | 497.1536 | 249.7781 | 244.5823 | 248.5599
5630.5979 | 497.0417 | 249.7445 | 244.5916 | 248.4303
5631.5979 | 496.9839 | 249.7793 | 244.4495 | 248.3492
5632.5979 | 496.6095 | 249.81 | 244.4159 | 248.1965
5633.5979 | 496.4424 | 249.7293 | 244.224 | 248.193
5634.5979 | 496.5395 | 249.6718 | 244.1763 | 248.093
5635.5979 | 496.4 | 249.6832 | 244.1416 | 248.1448
5636.5979 | 495.9655 | 249.7356 | 244.1214 | 248.1988
5637.5979 | 495.7373 | 249.8037 | 244.222 | 248.3053
5638.5979 | 495.3766 | 249.7757 | 244.1784 | 248.3944
5639.5979 | 494.9545 | 249.673 | 244.0759 | 248.3151
5640.5979 | 494.4217 | 249.6675 | 243.9735 | 248.2915
5641.5979 | 493.9268 | 249.5749 | 243.7506 | 248.1927
5642.5979 | 493.3593 | 249.2865 | 243.6396 | 248.1771
5643.5979 | 492.9709 | 249.2269 | 243.5643 | 248.2264
5644.5979 | 492.6367 | 249.0716 | 243.426 | 248.0524
5645.6135 | 492.2924 | 248.9596 | 243.262 | 248.019
5646.5979 | 492.2735 | 248.8268 | 243.1519 | 247.9149
5647.5979 | 492.1067 | 248.7919 | 243.2381 | 247.8984
5648.5979 | 491.8591 | 248.7339 | 243.3281 | 247.9545
5649.5979 | 491.4352 | 248.8721 | 243.3342 | 248.0046
5650.5979 | 491.3747 | 248.8924 | 243.2558 | 248.0872
5651.5979 | 491.3466 | 248.7631 | 243.0836 | 248.145
5652.5979 | 491.3158 | 248.6093 | 242.7055 | 247.9532
5653.5979 | 491.0769 | 248.6584 | 242.4498 | 247.8082
5654.5979 | 490.9475 | 248.6131 | 242.2733 | 247.5151
5655.5979 | 490.8071 | 248.3093 | 242.2182 | 247.2761
5656.5979 | 490.7191 | 248.1869 | 242.1896 | 247.1139
5657.5979 | 490.552 | 247.9354 | 242.2134 | 247.0823
5658.5979 | 490.2627 | 247.9116 | 242.2046 | 246.9962
5659.5979 | 489.8758 | 247.7565 | 242.2111 | 247.0334
5660.5979 | 489.5813 | 247.8158 | 242.2797 | 247.0589
5661.5979 | 489.2885 | 247.8808 | 242.3992 | 247.1122
5662.5979 | 489.2169 | 247.9432 | 242.5422 | 247.1782
5663.5979 | 489.0542 | 248.0714 | 242.7182 | 247.2356
5664.5979 | 488.766 | 248.1738 | 242.8104 | 247.2149
5665.5979 | 488.5513 | 248.2356 | 242.8893 | 247.2098
5666.5979 | 488.405 | 248.3704 | 242.9186 | 247.2736
5667.5979 | 488.0879 | 248.411 | 242.8933 | 247.3474
5668.5979 | 487.9409 | 248.4548 | 242.9492 | 247.4828
5669.5979 | 487.8357 | 248.5722 | 242.9334 | 247.4929
5670.5979 | 487.6428 | 248.7359 | 242.7929 | 247.4856
5671.5979 | 487.4977 | 248.8573 | 242.6839 | 247.3934
5672.5979 | 487.4844 | 248.9609 | 242.2908 | 247.222
5673.5979 | 487.3988 | 249.027 | 241.8641 | 247.1127
5674.5979 | 486.996 | 248.8475 | 241.634 | 247.0808
5675.5979 | 486.8001 | 248.5544 | 241.4744 | 247.0718
5676.6135 | 486.5003 | 248.466 | 241.3476 | 247.0534
5677.5979 | 486.0829 | 248.3986 | 241.3023 | 247.0613
5678.5979 | 485.8258 | 248.2801 | 241.3859 | 247.027
5679.5979 | 485.9294 | 248.3286 | 241.4767 | 247.0145
5680.5979 | 485.8804 | 248.3849 | 241.4298 | 246.9675
5681.5979 | 485.6787 | 248.3839 | 241.3114 | 247.0191
5682.5979 | 485.825 | 248.3328 | 241.243 | 247.0365
5683.5979 | 485.5647 | 248.207 | 240.8785 | 246.9522
5684.5979 | 485.2202 | 247.8661 | 240.6216 | 246.9225
5685.5979 | 485.0695 | 247.6129 | 240.6064 | 246.8223
5686.5979 | 485.0129 | 247.4989 | 240.6042 | 246.7202
5687.5979 | 484.9907 | 247.4107 | 240.6788 | 246.6044
5688.5979 | 484.8846 | 247.4088 | 240.6748 | 246.5727
5689.5979 | 484.8703 | 247.2539 | 240.6009 | 246.5556
5690.5979 | 484.7411 | 247.2105 | 240.4894 | 246.5557
5691.5979 | 484.5934 | 247.2737 | 240.4842 | 246.5744
5692.5979 | 484.6411 | 247.3172 | 240.4212 | 246.5546
5693.5979 | 484.6947 | 247.3014 | 240.5165 | 246.5042
5694.5979 | 484.6437 | 247.2655 | 240.6488 | 246.5505
5695.5979 | 484.8903 | 247.2328 | 240.8065 | 246.629
5696.5979 | 485.2029 | 247.1624 | 240.7564 | 246.6638
5697.5979 | 485.215 | 247.1936 | 240.8661 | 246.6525
5698.5979 | 485.25 | 247.3202 | 240.8026 | 246.5799
5699.5979 | 485.3092 | 247.4817 | 240.7481 | 246.4139
5700.5979 | 485.1512 | 247.4493 | 240.7552 | 246.2551
5701.5979 | 485.036 | 247.2531 | 240.6625 | 246.0792
5702.5979 | 485.2622 | 247.1289 | 240.6402 | 245.9655
5703.5979 | 485.5452 | 247.0353 | 240.6243 | 245.9524
5704.5979 | 485.3909 | 247.1197 | 240.5327 | 245.7854
5705.5979 | 485.1752 | 247.1748 | 240.2863 | 245.6429
5706.5979 | 484.9423 | 247.2678 | 240.1018 | 245.5602
5707.5979 | 484.7482 | 247.2408 | 239.9192 | 245.4314
5708.5979 | 484.5668 | 247.2275 | 239.9118 | 245.2895
5709.5979 | 484.107 | 247.2785 | 239.9688 | 245.265
5710.5979 | 484.0389 | 247.3563 | 240.0521 | 245.1691
5711.5979 | 483.8162 | 247.4125 | 240.1574 | 245.2483
5712.5979 | 483.6635 | 247.3568 | 240.0417 | 245.319
5713.5979 | 483.6112 | 247.2958 | 239.6856 | 245.2457
5714.5979 | 483.3035 | 247.3075 | 239.4774 | 245.1086
5715.5979 | 482.9175 | 247.0311 | 239.4439 | 245.0562
5716.5979 | 482.845 | 246.8508 | 239.5365 | 245.0917
5717.5979 | 482.8073 | 246.6187 | 239.5511 | 245.0433
5718.5979 | 482.9094 | 246.3672 | 239.6097 | 244.9113
5719.5979 | 482.898 | 246.3604 | 239.3575 | 244.6459
5720.5979 | 482.7843 | 246.3296 | 239.1758 | 244.5565
5721.5979 | 482.8298 | 246.2221 | 239.0977 | 244.2678
5722.5979 | 482.8001 | 246.2385 | 239.0385 | 244.1474
5723.5979 | 482.852 | 246.1366 | 239.0084 | 244.1766
5724.5979 | 482.8336 | 246.138 | 238.9872 | 244.2076
5725.5979 | 482.6129 | 246.1333 | 238.9513 | 244.2069
5726.5979 | 482.5599 | 246.1529 | 238.9795 | 244.1485
5727.5979 | 482.5922 | 246.2051 | 238.8745 | 244.0998
5728.5979 | 482.6034 | 246.2492 | 238.6476 | 244.0699
5729.5979 | 482.3444 | 246.202 | 238.5087 | 244.076
5730.5979 | 482.2362 | 246.0065 | 238.315 | 244.1324
5731.5979 | 481.8293 | 245.86 | 238.4406 | 243.9909
5732.5979 | 481.4437 | 245.9385 | 238.5863 | 244.0438
5733.5979 | 481.2793 | 245.9968 | 238.7587 | 244.0305
5734.5979 | 481.1998 | 246.0509 | 238.7716 | 243.9797
5735.5979 | 481.2507 | 246.1245 | 238.7298 | 244.0231
5736.5979 | 481.3132 | 246.0427 | 238.5141 | 243.9889
5737.5979 | 481.0189 | 245.9609 | 238.5103 | 244.0705
5738.5979 | 480.8656 | 245.9026 | 238.5772 | 244.089
5739.5979 | 480.7167 | 245.6443 | 238.2656 | 244.069
5740.5979 | 480.3776 | 245.4788 | 238.0774 | 243.9976
5741.5979 | 480.1038 | 245.3066 | 237.8568 | 243.9859
5742.5979 | 480.0427 | 245.1371 | 237.7139 | 243.9983
5743.5979 | 479.9372 | 245.1254 | 237.7496 | 244.0238
5744.5979 | 479.6672 | 244.8569 | 237.5622 | 243.9763
5745.5979 | 479.6669 | 244.8215 | 237.4964 | 243.9884
5746.5979 | 479.4243 | 244.8598 | 237.5414 | 243.9856
5747.5979 | 479.2417 | 244.9089 | 237.6738 | 243.9665
5748.5979 | 479.0898 | 244.8998 | 237.7041 | 243.936
5749.5979 | 478.9857 | 245.0054 | 237.6353 | 243.901
5750.5979 | 478.821 | 245.0903 | 237.6525 | 243.8437
5751.5979 | 478.8179 | 245.0714 | 237.7135 | 243.6768
5752.5979 | 478.7227 | 245.1954 | 237.8686 | 243.5147
5753.5979 | 478.7337 | 245.1439 | 238.0321 | 243.4617
5754.5979 | 478.5662 | 245.1596 | 238.0538 | 243.5059
5755.5979 | 478.5965 | 245.1663 | 238.1398 | 243.5297
5756.5979 | 478.4592 | 245.0114 | 238.2579 | 243.4855
5757.5979 | 478.2077 | 244.9341 | 238.1547 | 243.3262
5758.5979 | 478.1652 | 244.8792 | 238.264 | 243.0325
5759.5979 | 477.8949 | 244.8305 | 238.3568 | 242.8774
5760.5979 | 477.9856 | 244.8228 | 238.2432 | 242.8963
5761.5979 | 477.9154 | 244.8875 | 238.1837 | 242.7704
5762.5979 | 477.8017 | 244.8973 | 238.0172 | 242.6247
5763.5979 | 477.7065 | 244.9396 | 237.7504 | 242.5527
5764.5979 | 477.7077 | 244.7657 | 237.496 | 242.6414
5765.5979 | 477.5828 | 244.6604 | 237.4682 | 242.5682
5766.5979 | 477.4402 | 244.588 | 237.4175 | 242.5861
5767.5979 | 477.1992 | 244.5559 | 237.3101 | 242.577
5768.5979 | 477.0226 | 244.4707 | 237.4547 | 242.3954
5769.5979 | 476.9658 | 244.4665 | 237.2303 | 242.2599
5770.5979 | 476.8697 | 244.462 | 237.1003 | 242.1826
5771.5979 | 476.673 | 244.4697 | 237.0657 | 242.1908
5772.5979 | 476.4803 | 244.3469 | 237.0929 | 242.2592
5773.5979 | 476.3127 | 244.4603 | 236.8211 | 242.257
5774.5979 | 476.0105 | 244.4403 | 236.8848 | 242.2099
5775.5979 | 475.6881 | 244.4481 | 237.106 | 242.1857
5776.5979 | 475.5806 | 244.3026 | 237.2652 | 242.0859
5777.5979 | 475.4691 | 244.3178 | 237.3205 | 242.1569
5778.5979 | 475.5999 | 244.2438 | 237.2927 | 242.2542
5779.5979 | 475.4519 | 244.237 | 237.3373 | 242.3013
5780.5979 | 475.5445 | 244.2935 | 237.2817 | 242.3025
5781.5979 | 475.5209 | 244.2483 | 237.3597 | 242.1587
5782.5979 | 475.5255 | 244.1415 | 237.2712 | 242.0331
5783.5979 | 475.5419 | 244.0359 | 237.0812 | 241.9724
5784.5979 | 475.2379 | 243.8011 | 236.9643 | 241.9437
5785.5979 | 475.1289 | 243.773 | 236.9618 | 241.9464
5786.5979 | 474.7639 | 243.8102 | 237.0376 | 241.9535
5787.5979 | 474.438 | 243.8641 | 237.1977 | 242.0817
5788.5979 | 474.0609 | 243.8725 | 237.0081 | 242.1618
5789.5979 | 473.8398 | 243.9489 | 236.8492 | 242.2061
5790.5979 | 473.6027 | 244.0042 | 236.7722 | 242.2802
5791.5979 | 473.5588 | 243.9874 | 236.7373 | 242.3176
5792.5979 | 473.3579 | 244.0053 | 236.7364 | 242.3409
5793.5979 | 473.4349 | 243.9608 | 236.5616 | 242.2615
5794.5979 | 473.6564 | 243.7759 | 236.5556 | 241.9863
5795.5979 | 473.4321 | 243.4916 | 236.7254 | 241.8799
5796.5979 | 472.9961 | 243.4202 | 236.7024 | 241.67
5797.5979 | 472.6227 | 243.3439 | 236.7973 | 241.5371
5798.5979 | 472.1879 | 243.3923 | 236.8883 | 241.5291
5799.5979 | 471.947 | 243.4947 | 237.0244 | 241.5018
5800.5979 | 471.7276 | 243.46 | 237.0135 | 241.4504
5801.5979 | 471.5199 | 243.4558 | 237.0278 | 241.4051
5802.5979 | 471.7058 | 243.5087 | 237.0377 | 241.3004
5803.5979 | 472.1833 | 243.5858 | 236.9952 | 241.0241
5804.5979 | 472.2855 | 243.6378 | 236.9043 | 240.7323
5805.5979 | 472.3419 | 243.5597 | 236.7901 | 240.542
5806.5979 | 472.34 | 243.6231 | 236.7957 | 240.3916
5807.5979 | 472.2211 | 243.6368 | 236.817 | 240.2061
5808.5979 | 472.1054 | 243.5048 | 236.8799 | 239.9968
5809.5979 | 472.0212 | 243.2591 | 236.8108 | 239.8924
5810.5979 | 471.59 | 243.0593 | 236.7008 | 239.877
5811.5979 | 471.3773 | 243.0101 | 236.5899 | 239.8864
5812.5979 | 471.3154 | 242.9326 | 236.5648 | 239.8665
5813.5979 | 471.225 | 242.7976 | 236.5823 | 239.8461
5814.5979 | 471.0661 | 242.7753 | 236.5541 | 239.7724
5815.5979 | 470.9853 | 242.5878 | 236.4453 | 239.7571
5816.5979 | 470.856 | 242.3534 | 236.395 | 239.554
5817.5979 | 470.6051 | 242.3137 | 236.4167 | 239.5412
5818.5979 | 470.3221 | 242.3251 | 236.4648 | 239.4972
5819.5979 | 470.2335 | 242.4471 | 236.3915 | 239.4801
5820.5979 | 470.5819 | 242.643 | 236.3169 | 239.3335
5821.5979 | 470.7017 | 242.7297 | 236.2118 | 239.3598
5822.5979 | 470.7187 | 242.7461 | 236.091 | 239.3173
5823.5979 | 470.6879 | 242.6722 | 236.0935 | 239.3229
5824.5979 | 470.7657 | 242.709 | 236.1139 | 239.261
5825.5979 | 470.5627 | 242.5911 | 236.0071 | 239.2592
5826.5979 | 470.4981 | 242.4898 | 235.9614 | 239.2686
5827.5979 | 470.6342 | 242.4807 | 235.8119 | 239.2454
5828.5979 | 470.4111 | 242.5381 | 235.6681 | 239.2657
5829.5979 | 470.5548 | 242.5463 | 235.4974 | 239.3734
5830.5979 | 470.6298 | 242.5876 | 235.3942 | 239.1863
5831.5979 | 470.8855 | 242.6522 | 235.3901 | 238.9937
5832.5979 | 470.9201 | 242.669 | 235.4683 | 238.9806
5833.5979 | 470.7304 | 242.8073 | 235.3475 | 239.035
5834.5979 | 470.6757 | 242.7401 | 235.3624 | 238.9814
5835.5979 | 470.3926 | 242.6585 | 235.365 | 239.0052
5836.5979 | 470.0531 | 242.6862 | 235.1531 | 238.9356
5837.5979 | 469.7327 | 242.7199 | 234.9934 | 238.8784
5838.5979 | 469.675 | 242.6748 | 234.8077 | 238.7839
5839.5979 | 469.7369 | 242.6782 | 234.649 | 238.8076
5840.5979 | 469.6767 | 242.706 | 234.4344 | 238.7176
5841.5979 | 469.644 | 242.5112 | 234.2251 | 238.6195
5842.5979 | 469.5784 | 242.2521 | 234.0268 | 238.5997
5843.5979 | 469.75 | 242.0301 | 233.8984 | 238.4864
5844.5979 | 469.7377 | 242.034 | 233.836 | 238.4657
5845.5979 | 469.7839 | 242.0918 | 233.8149 | 238.51
5846.5979 | 469.5926 | 242.0214 | 233.737 | 238.3935
5847.5979 | 469.5629 | 241.7312 | 233.6037 | 238.3187
5848.5979 | 469.2337 | 241.5817 | 233.5988 | 238.2873
5849.5979 | 468.8871 | 241.4462 | 233.5877 | 238.2661
5850.5979 | 468.6836 | 241.3692 | 233.5803 | 238.2562
5851.5979 | 468.6505 | 241.2869 | 233.6338 | 238.3643
5852.5979 | 468.5157 | 241.3628 | 233.7572 | 238.4691
5853.5979 | 468.244 | 241.2644 | 233.8308 | 238.4656
5854.5979 | 467.7108 | 241.0362 | 233.8484 | 238.4336
5855.5979 | 467.1266 | 240.7688 | 233.8248 | 238.4685
5856.6135 | 467.0764 | 240.7368 | 233.883 | 238.4419
5857.5979 | 466.9652 | 240.5004 | 234.0191 | 238.4442
5858.5979 | 466.8363 | 240.3862 | 233.9301 | 238.4277
5859.5979 | 466.7794 | 240.3887 | 233.8963 | 238.3822
5860.5979 | 466.7219 | 240.44 | 233.7786 | 238.4085
5861.5979 | 466.7063 | 240.2652 | 233.7979 | 238.3905
5862.5979 | 466.6288 | 240.2545 | 233.6775 | 238.199
5863.5979 | 466.6171 | 240.2581 | 233.681 | 238.0373
5864.5979 | 466.6436 | 240.2946 | 233.5672 | 238.0205
5865.5979 | 466.7278 | 240.3642 | 233.4841 | 237.8972
5866.5979 | 466.8066 | 240.4768 | 233.4314 | 237.7909
5867.5979 | 466.6449 | 240.553 | 233.5457 | 237.6569
5868.5979 | 466.364 | 240.6138 | 233.6878 | 237.625
5869.5979 | 466.2999 | 240.6179 | 233.8421 | 237.582
5870.5979 | 466.4099 | 240.4992 | 233.924 | 237.5315
5871.5979 | 466.3101 | 240.4862 | 233.8262 | 237.5739
5872.5979 | 466.2606 | 240.6019 | 233.8147 | 237.5595
5873.5979 | 466.3667 | 240.6529 | 233.8937 | 237.5359
5874.5979 | 466.2845 | 240.6397 | 234.0483 | 237.4512
5875.5979 | 466.2492 | 240.7305 | 234.1545 | 237.3179
5876.5979 | 466.3928 | 240.8245 | 234.0837 | 237.1975
5877.5979 | 466.5334 | 240.9261 | 234.0531 | 237.1216
5878.5979 | 466.6587 | 240.8705 | 233.9474 | 237.1456
5879.5979 | 466.8553 | 240.8551 | 233.8715 | 237.1014
5880.5979 | 466.9138 | 240.7891 | 233.733 | 236.9419
5881.5979 | 466.9784 | 240.7412 | 233.8031 | 236.8461
5882.5979 | 466.9751 | 240.6304 | 233.882 | 236.9579
5883.5979 | 467.0195 | 240.5291 | 233.9483 | 236.997
5884.5979 | 466.7774 | 240.4148 | 233.8913 | 237.0279
5885.5979 | 466.4417 | 240.2858 | 233.6838 | 237.0878
5886.5979 | 466.0916 | 240.2975 | 233.5066 | 236.9462
5887.5979 | 466.0147 | 240.276 | 233.4384 | 236.9461
5888.5979 | 465.9448 | 240.2013 | 233.4295 | 236.9873
5889.5979 | 465.8689 | 240.1561 | 233.4031 | 237.0262
5890.5979 | 465.7258 | 240.1493 | 233.3049 | 236.9952
5891.5979 | 465.6639 | 240.1372 | 233.3308 | 236.9097
5892.5979 | 465.8067 | 240.1697 | 233.2479 | 236.9019
5893.5979 | 465.7509 | 240.2796 | 233.1092 | 236.919
5894.5979 | 465.601 | 240.2864 | 233.1874 | 236.9641
5895.5979 | 465.497 | 240.0323 | 233.2624 | 237.0437
5896.5979 | 465.6388 | 239.9978 | 233.2611 | 237.1045
5897.5979 | 465.7408 | 239.6651 | 232.9656 | 237.1103
5898.5979 | 465.6445 | 239.3655 | 232.7462 | 237.0886
5899.5979 | 465.4186 | 239.308 | 232.5173 | 237.0801
5900.5979 | 465.1667 | 239.2488 | 232.3047 | 237.0588
5901.5979 | 464.9416 | 239.2843 | 232.2972 | 237.1601
5902.5979 | 464.6602 | 239.3641 | 232.2615 | 237.1599
5903.5979 | 464.411 | 239.2753 | 232.1913 | 237.182
5904.5979 | 464.1868 | 239.1842 | 232.1218 | 237.1239
5905.5979 | 464.0078 | 239.1774 | 232.096 | 237.1784
5906.5979 | 463.7433 | 239.1489 | 232.1152 | 237.123
5907.5979 | 463.7266 | 239.1623 | 231.9875 | 237.1458
5908.5979 | 463.4936 | 239.1086 | 231.9333 | 237.0597
5909.5979 | 463.5098 | 238.8641 | 231.839 | 237.1883
5910.5979 | 463.5346 | 238.8962 | 231.6791 | 237.1176
5911.5979 | 463.5126 | 238.9163 | 231.6671 | 237.033
5912.5979 | 463.4414 | 239.0053 | 231.6806 | 236.9922
5913.5979 | 463.3877 | 239.086 | 231.7027 | 236.8291
5914.5979 | 463.5174 | 238.8255 | 231.6107 | 236.729
5915.5979 | 463.2577 | 238.5467 | 231.1911 | 236.71
5916.5979 | 463.0748 | 238.1815 | 230.7873 | 236.7516
5917.5979 | 463.0132 | 237.992 | 230.7252 | 236.7878
5918.5979 | 462.7899 | 237.7012 | 230.741 | 236.8781
5919.5979 | 462.6703 | 237.4378 | 230.5458 | 236.8685
5920.5979 | 462.6148 | 237.2269 | 230.4304 | 236.8172
5921.5979 | 462.3523 | 236.8956 | 230.5076 | 236.803
5922.5979 | 462.069 | 236.5889 | 230.1735 | 236.6909
5923.5979 | 461.9004 | 236.3783 | 230.116 | 236.651
5924.5979 | 461.6678 | 236.3305 | 230.226 | 236.6171
5925.5979 | 461.2537 | 236.3006 | 230.1808 | 236.6396
5926.5979 | 461.1345 | 236.2991 | 230.2147 | 236.6628
5927.5979 | 461.0617 | 236.4084 | 230.3498 | 236.6356
5928.5979 | 460.7367 | 236.4657 | 230.4431 | 236.6886
5929.5979 | 460.4608 | 236.6042 | 230.4883 | 236.5731
5930.5979 | 460.2289 | 236.761 | 230.4864 | 236.5322
5931.5979 | 460.0329 | 236.8983 | 230.4059 | 236.4708
5932.5979 | 459.9702 | 236.7982 | 230.4244 | 236.3829
5933.5979 | 459.7919 | 236.7591 | 230.4233 | 236.4275
5934.5979 | 459.5396 | 236.7311 | 230.5981 | 236.3832
5935.5979 | 459.2715 | 236.7634 | 230.7389 | 236.3513
5936.5979 | 458.9261 | 236.6526 | 230.7415 | 236.3247
5937.5979 | 458.7271 | 236.7364 | 230.7473 | 236.1603
5938.5979 | 458.6124 | 236.802 | 230.679 | 235.9709
5939.5979 | 458.5774 | 236.881 | 230.6365 | 235.8638
5940.5979 | 458.5414 | 237.0776 | 230.5417 | 235.8125
5941.5979 | 458.5283 | 237.2199 | 230.529 | 235.7565
5942.5979 | 458.3349 | 237.3491 | 230.4564 | 235.6887
5943.5979 | 458.0522 | 237.4596 | 230.3902 | 235.6065
5944.5979 | 457.6491 | 237.5254 | 230.4162 | 235.493
5945.5979 | 457.5033 | 237.5156 | 230.4459 | 235.5597
5946.6135 | 457.5001 | 237.5561 | 230.4747 | 235.6406
5947.5979 | 457.5691 | 237.5772 | 230.4478 | 235.6154
5948.5979 | 457.4867 | 237.6189 | 230.4064 | 235.6125
5949.5979 | 457.3264 | 237.6387 | 230.3166 | 235.4941
5950.5979 | 456.9237 | 237.6332 | 230.3907 | 235.4378
5951.5979 | 456.6618 | 237.6739 | 230.5084 | 235.2381
5952.5979 | 456.2755 | 237.7938 | 230.4298 | 235.115
5953.5979 | 455.8168 | 237.7778 | 230.1866 | 235.0397
5954.5979 | 455.6563 | 237.8783 | 229.9791 | 234.9463
5955.5979 | 455.5844 | 237.9237 | 229.8577 | 234.8978
5956.5979 | 455.4563 | 237.8022 | 229.8309 | 234.7252
5957.5979 | 455.3525 | 237.7876 | 229.7214 | 234.5251
5958.5979 | 455.1716 | 237.8032 | 229.587 | 234.4431
5959.5979 | 454.9357 | 237.7845 | 229.492 | 234.4793
5960.5979 | 454.7859 | 237.6715 | 229.6123 | 234.4283
5961.5979 | 454.4939 | 237.5689 | 229.6964 | 234.3401
5962.5979 | 454.1544 | 237.5787 | 229.6312 | 234.2618
5963.5979 | 453.889 | 237.6256 | 229.5816 | 234.1846
5964.5979 | 453.5943 | 237.609 | 229.6328 | 234.2261
5965.5979 | 453.2038 | 237.7177 | 229.5371 | 234.2538
5966.5979 | 453.1663 | 237.8165 | 229.5113 | 234.2842
5967.5979 | 452.7855 | 237.9329 | 229.5823 | 234.2963
5968.5979 | 452.5733 | 238.0041 | 229.6825 | 234.3272
5969.5979 | 452.5342 | 238.0086 | 229.7225 | 234.2736
5970.5979 | 452.4895 | 238.0473 | 229.6478 | 234.2366
5971.5979 | 452.2932 | 238.1328 | 229.5645 | 234.2552
5972.5979 | 452.0466 | 238.0993 | 229.5198 | 234.2691
5973.5979 | 451.9299 | 237.9864 | 229.5326 | 234.271
5974.5979 | 451.6776 | 237.9866 | 229.4628 | 234.3177
5975.5979 | 451.4862 | 237.9634 | 229.397 | 234.421
5976.5979 | 451.4335 | 237.9334 | 229.298 | 234.492
5977.5979 | 451.0969 | 237.9554 | 229.1183 | 234.5605
5978.5979 | 450.8118 | 237.5719 | 228.9055 | 234.6078
5979.5979 | 450.4807 | 237.3649 | 228.8749 | 234.4729
5980.5979 | 450.1802 | 237.1286 | 228.9624 | 234.3757
5981.5979 | 449.8298 | 236.7121 | 229.0712 | 234.2755
5982.5979 | 449.2399 | 236.5543 | 229.218 | 234.2039
5983.5979 | 448.6374 | 236.3622 | 229.404 | 234.1929
5984.5979 | 448.2013 | 236.2121 | 229.4523 | 234.257
5985.5979 | 447.8709 | 236.1399 | 229.4037 | 234.1078
5986.5979 | 447.413 | 236.1569 | 229.3358 | 233.9684
5987.5979 | 447.2344 | 236.0737 | 229.2921 | 233.8383
5988.5979 | 446.8912 | 236.0303 | 229.3207 | 233.6033
5989.5979 | 446.6257 | 235.9072 | 229.2654 | 233.5569
5990.5979 | 446.6543 | 235.7973 | 229.185 | 233.495
5991.5979 | 446.6246 | 235.8209 | 229.1661 | 233.4985
5992.5979 | 446.421 | 235.7634 | 229.2736 | 233.5506
5993.5979 | 446.3107 | 235.6698 | 229.3283 | 233.4576
5994.5979 | 446.1147 | 235.7197 | 229.3974 | 233.4473
5995.5979 | 445.9392 | 235.764 | 229.47 | 233.5557
5996.5979 | 445.6167 | 235.6933 | 229.3421 | 233.7015
5997.5979 | 445.3427 | 235.5751 | 229.1891 | 233.6578
5998.5979 | 445.2116 | 235.5766 | 229.1197 | 233.6173
5999.5979 | 445.0378 | 235.6237 | 229.1638 | 233.5517
6000.5979 | 445.0597 | 235.6005 | 228.9579 | 233.5356
6001.5979 | 445.1259 | 235.5405 | 228.9063 | 233.5669
6002.5979 | 445.2245 | 235.4991 | 229.0294 | 233.589
6003.5979 | 445.2385 | 235.5332 | 229.0839 | 233.522
6004.5979 | 445.3357 | 235.4383 | 229.1558 | 233.3689
6005.5979 | 445.2107 | 235.4125 | 229.1171 | 233.2247
6006.5979 | 445.0155 | 235.3264 | 229.1853 | 233.2212
6007.5979 | 444.9406 | 235.2682 | 229.2547 | 233.2502
6008.5979 | 444.9119 | 235.1668 | 229.4113 | 233.1221
6009.5979 | 444.6811 | 235.0167 | 229.3114 | 233.1082
6010.5979 | 444.5269 | 235.0126 | 229.2316 | 232.9606
6011.5979 | 444.3925 | 234.9903 | 229.2966 | 232.7954
6012.5979 | 444.1126 | 234.7784 | 229.217 | 232.7886
6013.5979 | 443.9136 | 234.7259 | 229.2274 | 232.7563
6014.5979 | 443.7123 | 234.624 | 229.1194 | 232.6611
6015.5979 | 443.5712 | 234.5416 | 228.9732 | 232.6117
6016.5979 | 443.7455 | 234.507 | 228.8792 | 232.519
6017.5979 | 443.866 | 234.5713 | 228.787 | 232.5392
6018.5979 | 444.0065 | 234.6077 | 228.7358 | 232.4939
6019.5979 | 444.1466 | 234.5949 | 228.7388 | 232.4763
6020.5979 | 444.2758 | 234.4833 | 228.7525 | 232.4201
6021.5979 | 444.3981 | 234.5233 | 228.7805 | 232.4355
6022.5979 | 444.4954 | 234.4994 | 228.9298 | 232.4107
6023.5979 | 444.2994 | 234.3983 | 228.8251 | 232.3239
6024.5979 | 444.0043 | 234.3272 | 228.7037 | 232.2267
6025.5979 | 443.97 | 234.3273 | 228.7062 | 232.2322
6026.5979 | 444.0531 | 234.2835 | 228.6999 | 232.2376
6027.5979 | 443.9396 | 234.2724 | 228.5378 | 232.3394
6028.5979 | 443.7303 | 234.3065 | 228.3274 | 232.2298
6029.5979 | 443.4431 | 234.2972 | 228.2928 | 232.1185
6030.5979 | 443.0835 | 234.3487 | 228.2536 | 231.9711
6031.5979 | 442.8804 | 234.3833 | 228.2085 | 231.8861
6032.5979 | 442.6886 | 234.4525 | 228.2393 | 231.932
6033.5979 | 442.6312 | 234.4423 | 228.1231 | 231.9225
6034.5979 | 442.4859 | 234.5283 | 228.1011 | 231.922
6035.5979 | 442.4263 | 234.4642 | 228.1727 | 231.8974
6036.5979 | 442.2932 | 234.4823 | 228.2559 | 231.8505
6037.5979 | 442.1139 | 234.3917 | 228.2013 | 231.8413
6038.5979 | 441.8187 | 234.4068 | 228.2798 | 231.7612
6039.5979 | 441.4956 | 234.4562 | 228.3539 | 231.7726
6040.5979 | 441.3245 | 234.5453 | 228.3096 | 231.8654
6041.5979 | 441.1755 | 234.6534 | 228.1864 | 231.803
6042.5979 | 441.0681 | 234.5564 | 227.998 | 231.7098
6043.5979 | 440.9196 | 234.1639 | 227.7444 | 231.6806
6044.5979 | 440.9003 | 234.0563 | 227.5421 | 231.7267
6045.5979 | 440.7883 | 233.9384 | 227.4701 | 231.6909
6046.5979 | 440.6713 | 233.9373 | 227.4443 | 231.6023
6047.5979 | 440.4894 | 233.7739 | 227.4419 | 231.5789
6048.5979 | 440.1797 | 233.7955 | 227.2691 | 231.4942
6049.5979 | 439.9584 | 233.866 | 227.1546 | 231.4194
6050.5979 | 439.6941 | 233.6641 | 226.9267 | 231.373
6051.5979 | 439.3917 | 233.5967 | 226.6989 | 231.3788
6052.5979 | 439.1087 | 233.5617 | 226.5551 | 231.2341
6053.5979 | 438.7658 | 233.4035 | 226.349 | 231.2757
6054.5979 | 438.431 | 233.3442 | 226.2769 | 231.3031
6055.5979 | 438.1825 | 233.3473 | 226.2024 | 231.3013
6056.5979 | 438.0054 | 233.3932 | 226.1728 | 231.2677
6057.5979 | 437.9334 | 233.4937 | 226.2552 | 231.2377
6058.5979 | 437.7774 | 233.5398 | 226.3875 | 231.1336
6059.5979 | 437.5346 | 233.5971 | 226.3962 | 231.0179
6060.5979 | 437.1625 | 233.3814 | 226.2747 | 231.0231